## Process
Weather Normalization and Peak Methodology
1. Objective
The purpose of this workbook is to develop a weather-normalized hourly load profile for the most recent complete year and to calculate coincident and non-coincident peak metrics based on normalized conditions.
Weather normalization removes the impact of unusually hot or cold weather so that load shapes and peak measures reflect typical weather conditions rather than anomalies in the study year.
2. Data Inputs
The analysis uses the following hourly data:
• Actual hourly load for the study year
• Hourly Heating Degree Days (HDD) for the study year
• Hourly Cooling Degree Days (CDD) for the study year
• 10-year average hourly HDD and CDD (normal weather)
• Calendar indicators:
• Weekend flag (1 for Saturday/Sunday, 0 otherwise)
• Hour-of-day indicator variables (H0 through H23)
The same weather station, base temperature, and HDD/CDD calculation method are used for both study-year and normal weather data.
3. Regression Model
Hourly load is modeled using a linear regression estimated on study-year data:
Load_t = Intercept
β_HDD × HDD_t
β_CDD × CDD_t
β_Weekend × Weekend_t
Hour-of-Day Effects (H0–H23)
Where:
• HDD_t and CDD_t measure hourly weather intensity
• Weekend_t captures weekend usage differences
• Hour-of-day indicators capture the typical daily load shape
• Coefficients are estimated once using actual study-year weather
The regression isolates the incremental effect of weather while controlling for recurring calendar patterns.
4. Weather Normalization
Weather-normalized hourly load is calculated by:
• Holding all estimated coefficients constant
• Replacing study-year HDD and CDD with 10-year average hourly HDD and CDD
• Keeping the same calendar structure (hour and weekend indicators)
Normalized Load_t = Intercept
β_HDD × HDD_t
β_CDD × CDD_t
β_Weekend × Weekend_t
Hour-of-Day Effects (H0–H23)
This produces an hourly series representing expected load under normal weather conditions while preserving actual operating patterns.
The regression is not re-estimated using normal weather. Only the weather inputs are replaced.
5. Peak Calculations
All peak metrics are calculated using the weather-normalized hourly load series.
Non-Coincident Peak (NCP)
NCP measures the class' own peak demand, regardless of when the system peaks.
• NCP1: Highest single hourly load in the normalized year
• NCP4: Fourth highest hourly load in the normalized year
• NCP12: Sum of the twelve highest hourly loads in the normalized year
Monthly NCP values are determined by selecting the maximum hourly load within each calendar month.
Coincident Peak (CP)
Coincident peak measures customer load during defined system peak hour(s).
Customer coincident demand is calculated by selecting the weather-normalized load in the identified system peak hour(s), consistent with the applicable cost allocation or rate framework.
6. Validation (Sanity Check)
As a quality check, the difference between study-year predicted load and normalized predicted load equals the weather adjustment implied by the HDD and CDD sensitivities.
This confirms that only weather effects are removed and that structural load characteristics remain unchanged.
7. Output
The resulting weather-normalized hourly load series forms the basis for the Cost Allocation Demand Data

## INPUT_10Yr_Weather
Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | Date | Temp | HDD | CDD | HDD 10 Yr Avg | CDD 10 Yr Avg | Field | Value
2025-01-01 | 1.5 | 16.5 | 0 | 2024-01-01 | -7.2 | 25.2 | 0 | 2023-01-01 | 3 | 15 | 0 | 2022-01-01 | -1.6 | 19.6 | 0 | 2021-01-01 | -3.4 | 21.4 | 0 | 2020-01-01 | -1.1 | 19.1 | 0 | 2019-01-01 | -1.5 | 19.5 | 0 | 2018-01-01 | -23.6 | 41.6 | 0 | 2017-01-01 | -8 | 26 | 0 | 2016-01-01 | -2.5 | 20.5 | 0 | 22.44 | 0
2025-01-01 | 1.8 | 16.2 | 0 | 2024-01-01 | -7.5 | 25.5 | 0 | 2023-01-01 | 3 | 15 | 0 | 2022-01-01 | -1.8 | 19.8 | 0 | 2021-01-01 | -4 | 22 | 0 | 2020-01-01 | -1.5 | 19.5 | 0 | 2019-01-01 | -0.8 | 18.8 | 0 | 2018-01-01 | -23.8 | 41.8 | 0 | 2017-01-01 | -6.8 | 24.8 | 0 | 2016-01-01 | -2.7 | 20.7 | 0 | 22.41 | 0 | Station Name | Ottawa Intl A
2025-01-01 | 1.7 | 16.3 | 0 | 2024-01-01 | -7.5 | 25.5 | 0 | 2023-01-01 | 3 | 15 | 0 | 2022-01-01 | -1.8 | 19.8 | 0 | 2021-01-01 | -4.1 | 22.1 | 0 | 2020-01-01 | -1.5 | 19.5 | 0 | 2019-01-01 | -0.1 | 18.1 | 0 | 2018-01-01 | -24.4 | 42.4 | 0 | 2017-01-01 | -4.9 | 22.9 | 0 | 2016-01-01 | -3.2 | 21.2 | 0 | 22.28 | 0 | Province | Ontario
2025-01-01 | 1.7 | 16.3 | 0 | 2024-01-01 | -8.1 | 26.1 | 0 | 2023-01-01 | 2.6 | 15.4 | 0 | 2022-01-01 | -1.9 | 19.9 | 0 | 2021-01-01 | -4.1 | 22.1 | 0 | 2020-01-01 | -1.1 | 19.1 | 0 | 2019-01-01 | 0.2 | 17.8 | 0 | 2018-01-01 | -25.7 | 43.7 | 0 | 2017-01-01 | -4 | 22 | 0 | 2016-01-01 | -3.4 | 21.4 | 0 | 22.38 | 0 | Latitude | 45°19'00.000" N
2025-01-01 | 1.8 | 16.2 | 0 | 2024-01-01 | -8.1 | 26.1 | 0 | 2023-01-01 | 2.4 | 15.6 | 0 | 2022-01-01 | -1.8 | 19.8 | 0 | 2021-01-01 | -3.8 | 21.8 | 0 | 2020-01-01 | -1.3 | 19.3 | 0 | 2019-01-01 | 0 | 18 | 0 | 2018-01-01 | -26.2 | 44.2 | 0 | 2017-01-01 | -2.9 | 20.9 | 0 | 2016-01-01 | -3.8 | 21.8 | 0 | 22.37 | 0 | Longitude | 75°40'00.000" W
2025-01-01 | 1.4 | 16.6 | 0 | 2024-01-01 | -7.7 | 25.7 | 0 | 2023-01-01 | 2.1 | 15.9 | 0 | 2022-01-01 | -1.7 | 19.7 | 0 | 2021-01-01 | -3.4 | 21.4 | 0 | 2020-01-01 | -1.1 | 19.1 | 0 | 2019-01-01 | -0.4 | 18.4 | 0 | 2018-01-01 | -27.1 | 45.1 | 0 | 2017-01-01 | -3.7 | 21.7 | 0 | 2016-01-01 | -3.6 | 21.6 | 0 | 22.52 | 0 | Elevation (m) | 114.9
2025-01-01 | 0.8 | 17.2 | 0 | 2024-01-01 | -7.3 | 25.3 | 0 | 2023-01-01 | 2 | 16 | 0 | 2022-01-01 | -1.5 | 19.5 | 0 | 2021-01-01 | -3.2 | 21.2 | 0 | 2020-01-01 | -0.9 | 18.9 | 0 | 2019-01-01 | -0.5 | 18.5 | 0 | 2018-01-01 | -27.2 | 45.2 | 0 | 2017-01-01 | -4.2 | 22.2 | 0 | 2016-01-01 | -3.2 | 21.2 | 0 | 22.52 | 0 | Climate ID | 6106001
2025-01-01 | 1.2 | 16.8 | 0 | 2024-01-01 | -7.3 | 25.3 | 0 | 2023-01-01 | 2 | 16 | 0 | 2022-01-01 | -1.4 | 19.4 | 0 | 2021-01-01 | -3.6 | 21.6 | 0 | 2020-01-01 | -0.9 | 18.9 | 0 | 2019-01-01 | -0.5 | 18.5 | 0 | 2018-01-01 | -27.4 | 45.4 | 0 | 2017-01-01 | -5.7 | 23.7 | 0 | 2016-01-01 | -2.6 | 20.6 | 0 | 22.62 | 0 | WMO ID | 71628
2025-01-01 | 1.3 | 16.7 | 0 | 2024-01-01 | -7.3 | 25.3 | 0 | 2023-01-01 | 1.9 | 16.1 | 0 | 2022-01-01 | -1.2 | 19.2 | 0 | 2021-01-01 | -3.2 | 21.2 | 0 | 2020-01-01 | -0.9 | 18.9 | 0 | 2019-01-01 | -0.2 | 18.2 | 0 | 2018-01-01 | -28.6 | 46.6 | 0 | 2017-01-01 | -6.6 | 24.6 | 0 | 2016-01-01 | -2.2 | 20.2 | 0 | 22.7 | 0 | TC ID | YOW
2025-01-01 | 1.4 | 16.6 | 0 | 2024-01-01 | -6.9 | 24.9 | 0 | 2023-01-01 | 1.6 | 16.4 | 0 | 2022-01-01 | -1 | 19 | 0 | 2021-01-01 | -2.6 | 20.6 | 0 | 2020-01-01 | -0.9 | 18.9 | 0 | 2019-01-01 | -0.8 | 18.8 | 0 | 2018-01-01 | -27 | 45 | 0 | 2017-01-01 | -7 | 25 | 0 | 2016-01-01 | -1.7 | 19.7 | 0 | 22.49 | 0
2025-01-01 | 0.5 | 17.5 | 0 | 2024-01-01 | -6.3 | 24.3 | 0 | 2023-01-01 | 1.8 | 16.2 | 0 | 2022-01-01 | -0.8 | 18.8 | 0 | 2021-01-01 | -1.9 | 19.9 | 0 | 2020-01-01 | -0.5 | 18.5 | 0 | 2019-01-01 | -1.8 | 19.8 | 0 | 2018-01-01 | -24.6 | 42.6 | 0 | 2017-01-01 | -7.1 | 25.1 | 0 | 2016-01-01 | -1.1 | 19.1 | 0 | 22.18 | 0
2025-01-01 | 0.1 | 17.9 | 0 | 2024-01-01 | -6.2 | 24.2 | 0 | 2023-01-01 | 2 | 16 | 0 | 2022-01-01 | -0.4 | 18.4 | 0 | 2021-01-01 | -1.1 | 19.1 | 0 | 2020-01-01 | -0.1 | 18.1 | 0 | 2019-01-01 | -3.3 | 21.3 | 0 | 2018-01-01 | -22.9 | 40.9 | 0 | 2017-01-01 | -6.6 | 24.6 | 0 | 2016-01-01 | -0.9 | 18.9 | 0 | 21.94 | 0
2025-01-01 | 0 | 18 | 0 | 2024-01-01 | -5.4 | 23.4 | 0 | 2023-01-01 | 2.4 | 15.6 | 0 | 2022-01-01 | 0.2 | 17.8 | 0 | 2021-01-01 | -0.7 | 18.7 | 0 | 2020-01-01 | 0 | 18 | 0 | 2019-01-01 | -4.4 | 22.4 | 0 | 2018-01-01 | -21.2 | 39.2 | 0 | 2017-01-01 | -5.2 | 23.2 | 0 | 2016-01-01 | -0.7 | 18.7 | 0 | 21.5 | 0
2025-01-01 | 0.1 | 17.9 | 0 | 2024-01-01 | -5.1 | 23.1 | 0 | 2023-01-01 | 2.5 | 15.5 | 0 | 2022-01-01 | 0.8 | 17.2 | 0 | 2021-01-01 | -0.5 | 18.5 | 0 | 2020-01-01 | 0.3 | 17.7 | 0 | 2019-01-01 | -5.4 | 23.4 | 0 | 2018-01-01 | -20.6 | 38.6 | 0 | 2017-01-01 | -4.1 | 22.1 | 0 | 2016-01-01 | -0.7 | 18.7 | 0 | 21.27 | 0
2025-01-01 | 0.1 | 17.9 | 0 | 2024-01-01 | -4.9 | 22.9 | 0 | 2023-01-01 | 2.3 | 15.7 | 0 | 2022-01-01 | 0.8 | 17.2 | 0 | 2021-01-01 | -0.4 | 18.4 | 0 | 2020-01-01 | 0.7 | 17.3 | 0 | 2019-01-01 | -5.9 | 23.9 | 0 | 2018-01-01 | -19.5 | 37.5 | 0 | 2017-01-01 | -3.7 | 21.7 | 0 | 2016-01-01 | -0.8 | 18.8 | 0 | 21.13 | 0
2025-01-01 | 0.1 | 17.9 | 0 | 2024-01-01 | -5.1 | 23.1 | 0 | 2023-01-01 | 1.7 | 16.3 | 0 | 2022-01-01 | 1.2 | 16.8 | 0 | 2021-01-01 | -0.5 | 18.5 | 0 | 2020-01-01 | 0.7 | 17.3 | 0 | 2019-01-01 | -6.4 | 24.4 | 0 | 2018-01-01 | -19.9 | 37.9 | 0 | 2017-01-01 | -3.2 | 21.2 | 0 | 2016-01-01 | -1.1 | 19.1 | 0 | 21.25 | 0
2025-01-01 | 0.2 | 17.8 | 0 | 2024-01-01 | -5.5 | 23.5 | 0 | 2023-01-01 | 1.9 | 16.1 | 0 | 2022-01-01 | 1.2 | 16.8 | 0 | 2021-01-01 | -1 | 19 | 0 | 2020-01-01 | 0.2 | 17.8 | 0 | 2019-01-01 | -7.5 | 25.5 | 0 | 2018-01-01 | -19.4 | 37.4 | 0 | 2017-01-01 | -2.3 | 20.3 | 0 | 2016-01-01 | -1.5 | 19.5 | 0 | 21.37 | 0
2025-01-01 | 0.3 | 17.7 | 0 | 2024-01-01 | -6.8 | 24.8 | 0 | 2023-01-01 | 1.2 | 16.8 | 0 | 2022-01-01 | -0.3 | 18.3 | 0 | 2021-01-01 | -1.2 | 19.2 | 0 | 2020-01-01 | 0.3 | 17.7 | 0 | 2019-01-01 | -9.3 | 27.3 | 0 | 2018-01-01 | -21.2 | 39.2 | 0 | 2017-01-01 | -3.8 | 21.8 | 0 | 2016-01-01 | -1.8 | 19.8 | 0 | 22.26 | 0
2025-01-01 | 0.3 | 17.7 | 0 | 2024-01-01 | -7.5 | 25.5 | 0 | 2023-01-01 | 1.1 | 16.9 | 0 | 2022-01-01 | -1.7 | 19.7 | 0 | 2021-01-01 | -1.4 | 19.4 | 0 | 2020-01-01 | 0.3 | 17.7 | 0 | 2019-01-01 | -10.6 | 28.6 | 0 | 2018-01-01 | -21 | 39 | 0 | 2017-01-01 | -5.8 | 23.8 | 0 | 2016-01-01 | -2.1 | 20.1 | 0 | 22.84 | 0
2025-01-01 | 0.3 | 17.7 | 0 | 2024-01-01 | -8 | 26 | 0 | 2023-01-01 | 0.7 | 17.3 | 0 | 2022-01-01 | -2.3 | 20.3 | 0 | 2021-01-01 | -1.6 | 19.6 | 0 | 2020-01-01 | -0.1 | 18.1 | 0 | 2019-01-01 | -11.1 | 29.1 | 0 | 2018-01-01 | -20.6 | 38.6 | 0 | 2017-01-01 | -4.9 | 22.9 | 0 | 2016-01-01 | -2.3 | 20.3 | 0 | 22.99 | 0
2025-01-01 | 0.1 | 17.9 | 0 | 2024-01-01 | -8.8 | 26.8 | 0 | 2023-01-01 | 0.5 | 17.5 | 0 | 2022-01-01 | -2.5 | 20.5 | 0 | 2021-01-01 | -1.9 | 19.9 | 0 | 2020-01-01 | -0.6 | 18.6 | 0 | 2019-01-01 | -12.2 | 30.2 | 0 | 2018-01-01 | -20.2 | 38.2 | 0 | 2017-01-01 | -4.1 | 22.1 | 0 | 2016-01-01 | -2.3 | 20.3 | 0 | 23.2 | 0
2025-01-01 | -0.1 | 18.1 | 0 | 2024-01-01 | -8.2 | 26.2 | 0 | 2023-01-01 | 0.6 | 17.4 | 0 | 2022-01-01 | -3 | 21 | 0 | 2021-01-01 | -2 | 20 | 0 | 2020-01-01 | -0.6 | 18.6 | 0 | 2019-01-01 | -13 | 31 | 0 | 2018-01-01 | -20.5 | 38.5 | 0 | 2017-01-01 | -3.6 | 21.6 | 0 | 2016-01-01 | -3 | 21 | 0 | 23.34 | 0
2025-01-01 | -0.6 | 18.6 | 0 | 2024-01-01 | -7.4 | 25.4 | 0 | 2023-01-01 | 0.6 | 17.4 | 0 | 2022-01-01 | -4.3 | 22.3 | 0 | 2021-01-01 | -2.2 | 20.2 | 0 | 2020-01-01 | -0.8 | 18.8 | 0 | 2019-01-01 | -14.2 | 32.2 | 0 | 2018-01-01 | -21.4 | 39.4 | 0 | 2017-01-01 | -4.5 | 22.5 | 0 | 2016-01-01 | -2.9 | 20.9 | 0 | 23.77 | 0
2025-01-01 | -0.9 | 18.9 | 0 | 2024-01-01 | -6.7 | 24.7 | 0 | 2023-01-01 | 0.3 | 17.7 | 0 | 2022-01-01 | -5.5 | 23.5 | 0 | 2021-01-01 | -3.2 | 21.2 | 0 | 2020-01-01 | -1 | 19 | 0 | 2019-01-01 | -15.2 | 33.2 | 0 | 2018-01-01 | -22.1 | 40.1 | 0 | 2017-01-01 | -5.8 | 23.8 | 0 | 2016-01-01 | -3.1 | 21.1 | 0 | 24.32 | 0
2025-01-02 | -1.4 | 19.4 | 0 | 2024-01-02 | -6.2 | 24.2 | 0 | 2023-01-02 | 0.2 | 17.8 | 0 | 2022-01-02 | -7 | 25 | 0 | 2021-01-02 | -4 | 22 | 0 | 2020-01-02 | -1.4 | 19.4 | 0 | 2019-01-02 | -16.1 | 34.1 | 0 | 2018-01-02 | -23.3 | 41.3 | 0 | 2017-01-02 | -5.8 | 23.8 | 0 | 2016-01-02 | -3.1 | 21.1 | 0 | 24.81 | 0
2025-01-02 | -1.8 | 19.8 | 0 | 2024-01-02 | -5.8 | 23.8 | 0 | 2023-01-02 | 0.3 | 17.7 | 0 | 2022-01-02 | -8.3 | 26.3 | 0 | 2021-01-02 | -4.2 | 22.2 | 0 | 2020-01-02 | -2 | 20 | 0 | 2019-01-02 | -16.6 | 34.6 | 0 | 2018-01-02 | -24.7 | 42.7 | 0 | 2017-01-02 | -5.7 | 23.7 | 0 | 2016-01-02 | -3.9 | 21.9 | 0 | 25.27 | 0
2025-01-02 | -1.9 | 19.9 | 0 | 2024-01-02 | -5.7 | 23.7 | 0 | 2023-01-02 | 0.4 | 17.6 | 0 | 2022-01-02 | -8.8 | 26.8 | 0 | 2021-01-02 | -4.2 | 22.2 | 0 | 2020-01-02 | -2.8 | 20.8 | 0 | 2019-01-02 | -16.9 | 34.9 | 0 | 2018-01-02 | -25.6 | 43.6 | 0 | 2017-01-02 | -9.1 | 27.1 | 0 | 2016-01-02 | -4.8 | 22.8 | 0 | 25.94 | 0
2025-01-02 | -1.7 | 19.7 | 0 | 2024-01-02 | -6.3 | 24.3 | 0 | 2023-01-02 | 0.6 | 17.4 | 0 | 2022-01-02 | -9.1 | 27.1 | 0 | 2021-01-02 | -4.3 | 22.3 | 0 | 2020-01-02 | -3.5 | 21.5 | 0 | 2019-01-02 | -17.2 | 35.2 | 0 | 2018-01-02 | -24.4 | 42.4 | 0 | 2017-01-02 | -6.8 | 24.8 | 0 | 2016-01-02 | -5.9 | 23.9 | 0 | 25.86 | 0
2025-01-02 | -1.8 | 19.8 | 0 | 2024-01-02 | -6.1 | 24.1 | 0 | 2023-01-02 | 0.5 | 17.5 | 0 | 2022-01-02 | -9.8 | 27.8 | 0 | 2021-01-02 | -4.6 | 22.6 | 0 | 2020-01-02 | -3.7 | 21.7 | 0 | 2019-01-02 | -16.8 | 34.8 | 0 | 2018-01-02 | -25 | 43 | 0 | 2017-01-02 | -9.8 | 27.8 | 0 | 2016-01-02 | -6.7 | 24.7 | 0 | 26.38 | 0
2025-01-02 | -1.9 | 19.9 | 0 | 2024-01-02 | -6.5 | 24.5 | 0 | 2023-01-02 | 0.4 | 17.6 | 0 | 2022-01-02 | -10.3 | 28.3 | 0 | 2021-01-02 | -4.7 | 22.7 | 0 | 2020-01-02 | -3.6 | 21.6 | 0 | 2019-01-02 | -17.1 | 35.1 | 0 | 2018-01-02 | -27 | 45 | 0 | 2017-01-02 | -9.4 | 27.4 | 0 | 2016-01-02 | -6.1 | 24.1 | 0 | 26.62 | 0
2025-01-02 | -1.8 | 19.8 | 0 | 2024-01-02 | -6.8 | 24.8 | 0 | 2023-01-02 | 0.7 | 17.3 | 0 | 2022-01-02 | -10.6 | 28.6 | 0 | 2021-01-02 | -4.5 | 22.5 | 0 | 2020-01-02 | -4.1 | 22.1 | 0 | 2019-01-02 | -17.7 | 35.7 | 0 | 2018-01-02 | -25.3 | 43.3 | 0 | 2017-01-02 | -9.9 | 27.9 | 0 | 2016-01-02 | -5.2 | 23.2 | 0 | 26.52 | 0
2025-01-02 | -2.1 | 20.1 | 0 | 2024-01-02 | -5 | 23 | 0 | 2023-01-02 | 1.4 | 16.6 | 0 | 2022-01-02 | -11.1 | 29.1 | 0 | 2021-01-02 | -4.1 | 22.1 | 0 | 2020-01-02 | -3.8 | 21.8 | 0 | 2019-01-02 | -18.7 | 36.7 | 0 | 2018-01-02 | -26 | 44 | 0 | 2017-01-02 | -9.2 | 27.2 | 0 | 2016-01-02 | -3.3 | 21.3 | 0 | 26.19 | 0
2025-01-02 | -2.4 | 20.4 | 0 | 2024-01-02 | -3.5 | 21.5 | 0 | 2023-01-02 | 1.7 | 16.3 | 0 | 2022-01-02 | -11.6 | 29.6 | 0 | 2021-01-02 | -3.9 | 21.9 | 0 | 2020-01-02 | -3.1 | 21.1 | 0 | 2019-01-02 | -18.4 | 36.4 | 0 | 2018-01-02 | -25.4 | 43.4 | 0 | 2017-01-02 | -10.1 | 28.1 | 0 | 2016-01-02 | -3.1 | 21.1 | 0 | 25.98 | 0
2025-01-02 | -2 | 20 | 0 | 2024-01-02 | -2.5 | 20.5 | 0 | 2023-01-02 | 2.1 | 15.9 | 0 | 2022-01-02 | -11.9 | 29.9 | 0 | 2021-01-02 | -3.5 | 21.5 | 0 | 2020-01-02 | -2.5 | 20.5 | 0 | 2019-01-02 | -17.8 | 35.8 | 0 | 2018-01-02 | -23.6 | 41.6 | 0 | 2017-01-02 | -9.6 | 27.6 | 0 | 2016-01-02 | -2.8 | 20.8 | 0 | 25.41 | 0
2025-01-02 | -1.9 | 19.9 | 0 | 2024-01-02 | -1.7 | 19.7 | 0 | 2023-01-02 | 2.8 | 15.2 | 0 | 2022-01-02 | -11.9 | 29.9 | 0 | 2021-01-02 | -3.1 | 21.1 | 0 | 2020-01-02 | 0.3 | 17.7 | 0 | 2019-01-02 | -16.8 | 34.8 | 0 | 2018-01-02 | -21.7 | 39.7 | 0 | 2017-01-02 | -7.5 | 25.5 | 0 | 2016-01-02 | -2.4 | 20.4 | 0 | 24.39 | 0
2025-01-02 | -1.8 | 19.8 | 0 | 2024-01-02 | -1.1 | 19.1 | 0 | 2023-01-02 | 3.5 | 14.5 | 0 | 2022-01-02 | -11.6 | 29.6 | 0 | 2021-01-02 | -2.5 | 20.5 | 0 | 2020-01-02 | 1.2 | 16.8 | 0 | 2019-01-02 | -15.6 | 33.6 | 0 | 2018-01-02 | -20.5 | 38.5 | 0 | 2017-01-02 | -4.8 | 22.8 | 0 | 2016-01-02 | -2.2 | 20.2 | 0 | 23.54 | 0
2025-01-02 | -1.5 | 19.5 | 0 | 2024-01-02 | -0.7 | 18.7 | 0 | 2023-01-02 | 3.8 | 14.2 | 0 | 2022-01-02 | -11.1 | 29.1 | 0 | 2021-01-02 | -2.2 | 20.2 | 0 | 2020-01-02 | 2.4 | 15.6 | 0 | 2019-01-02 | -15.1 | 33.1 | 0 | 2018-01-02 | -19.1 | 37.1 | 0 | 2017-01-02 | -3.2 | 21.2 | 0 | 2016-01-02 | -2 | 20 | 0 | 22.87 | 0
2025-01-02 | -1.4 | 19.4 | 0 | 2024-01-02 | -0.7 | 18.7 | 0 | 2023-01-02 | 4.1 | 13.9 | 0 | 2022-01-02 | -10.6 | 28.6 | 0 | 2021-01-02 | -1.2 | 19.2 | 0 | 2020-01-02 | 3.1 | 14.9 | 0 | 2019-01-02 | -13.6 | 31.6 | 0 | 2018-01-02 | -16.9 | 34.9 | 0 | 2017-01-02 | -2 | 20 | 0 | 2016-01-02 | -1.9 | 19.9 | 0 | 22.11 | 0
2025-01-02 | -1.5 | 19.5 | 0 | 2024-01-02 | -0.3 | 18.3 | 0 | 2023-01-02 | 4.6 | 13.4 | 0 | 2022-01-02 | -10.5 | 28.5 | 0 | 2021-01-02 | -0.9 | 18.9 | 0 | 2020-01-02 | 3.1 | 14.9 | 0 | 2019-01-02 | -12.9 | 30.9 | 0 | 2018-01-02 | -15 | 33 | 0 | 2017-01-02 | -1.1 | 19.1 | 0 | 2016-01-02 | -1.5 | 19.5 | 0 | 21.6 | 0
2025-01-02 | -1.8 | 19.8 | 0 | 2024-01-02 | 0 | 18 | 0 | 2023-01-02 | 4.4 | 13.6 | 0 | 2022-01-02 | -10.5 | 28.5 | 0 | 2021-01-02 | -0.9 | 18.9 | 0 | 2020-01-02 | 3.2 | 14.8 | 0 | 2019-01-02 | -12.6 | 30.6 | 0 | 2018-01-02 | -13 | 31 | 0 | 2017-01-02 | -1.1 | 19.1 | 0 | 2016-01-02 | -1.2 | 19.2 | 0 | 21.35 | 0
2025-01-02 | -2.1 | 20.1 | 0 | 2024-01-02 | -0.6 | 18.6 | 0 | 2023-01-02 | 2.7 | 15.3 | 0 | 2022-01-02 | -10.6 | 28.6 | 0 | 2021-01-02 | -0.8 | 18.8 | 0 | 2020-01-02 | 3.2 | 14.8 | 0 | 2019-01-02 | -13 | 31 | 0 | 2018-01-02 | -12.8 | 30.8 | 0 | 2017-01-02 | -1.3 | 19.3 | 0 | 2016-01-02 | -1.1 | 19.1 | 0 | 21.64 | 0
2025-01-02 | -2.8 | 20.8 | 0 | 2024-01-02 | -1.7 | 19.7 | 0 | 2023-01-02 | 3.2 | 14.8 | 0 | 2022-01-02 | -11 | 29 | 0 | 2021-01-02 | -2.1 | 20.1 | 0 | 2020-01-02 | 3.5 | 14.5 | 0 | 2019-01-02 | -13.4 | 31.4 | 0 | 2018-01-02 | -8.4 | 26.4 | 0 | 2017-01-02 | -2.2 | 20.2 | 0 | 2016-01-02 | -1 | 19 | 0 | 21.59 | 0
2025-01-02 | -3.3 | 21.3 | 0 | 2024-01-02 | -2 | 20 | 0 | 2023-01-02 | 2.8 | 15.2 | 0 | 2022-01-02 | -11.3 | 29.3 | 0 | 2021-01-02 | -2.4 | 20.4 | 0 | 2020-01-02 | 3.6 | 14.4 | 0 | 2019-01-02 | -13.5 | 31.5 | 0 | 2018-01-02 | -7.7 | 25.7 | 0 | 2017-01-02 | -2.7 | 20.7 | 0 | 2016-01-02 | -1.1 | 19.1 | 0 | 21.76 | 0
2025-01-02 | -3.5 | 21.5 | 0 | 2024-01-02 | -1.8 | 19.8 | 0 | 2023-01-02 | 2.7 | 15.3 | 0 | 2022-01-02 | -11.7 | 29.7 | 0 | 2021-01-02 | -2.6 | 20.6 | 0 | 2020-01-02 | 3.9 | 14.1 | 0 | 2019-01-02 | -13.1 | 31.1 | 0 | 2018-01-02 | -7.3 | 25.3 | 0 | 2017-01-02 | -4.2 | 22.2 | 0 | 2016-01-02 | -1.1 | 19.1 | 0 | 21.87 | 0
2025-01-02 | -3.6 | 21.6 | 0 | 2024-01-02 | -0.9 | 18.9 | 0 | 2023-01-02 | 2.3 | 15.7 | 0 | 2022-01-02 | -12.7 | 30.7 | 0 | 2021-01-02 | -2.4 | 20.4 | 0 | 2020-01-02 | 4.1 | 13.9 | 0 | 2019-01-02 | -13.1 | 31.1 | 0 | 2018-01-02 | -7.2 | 25.2 | 0 | 2017-01-02 | -4.2 | 22.2 | 0 | 2016-01-02 | -1.1 | 19.1 | 0 | 21.88 | 0
2025-01-02 | -3.9 | 21.9 | 0 | 2024-01-02 | -0.7 | 18.7 | 0 | 2023-01-02 | 2.2 | 15.8 | 0 | 2022-01-02 | -13.7 | 31.7 | 0 | 2021-01-02 | -2.5 | 20.5 | 0 | 2020-01-02 | 3.9 | 14.1 | 0 | 2019-01-02 | -12.8 | 30.8 | 0 | 2018-01-02 | -7.2 | 25.2 | 0 | 2017-01-02 | -4 | 22 | 0 | 2016-01-02 | -1.2 | 19.2 | 0 | 21.99 | 0
2025-01-02 | -3.3 | 21.3 | 0 | 2024-01-02 | -0.6 | 18.6 | 0 | 2023-01-02 | 2.1 | 15.9 | 0 | 2022-01-02 | -15 | 33 | 0 | 2021-01-02 | -3.5 | 21.5 | 0 | 2020-01-02 | 3.8 | 14.2 | 0 | 2019-01-02 | -12.7 | 30.7 | 0 | 2018-01-02 | -7.3 | 25.3 | 0 | 2017-01-02 | -4 | 22 | 0 | 2016-01-02 | -1 | 19 | 0 | 22.15 | 0
2025-01-02 | -3.5 | 21.5 | 0 | 2024-01-02 | -0.5 | 18.5 | 0 | 2023-01-02 | 2 | 16 | 0 | 2022-01-02 | -15.4 | 33.4 | 0 | 2021-01-02 | -3.8 | 21.8 | 0 | 2020-01-02 | 3.5 | 14.5 | 0 | 2019-01-02 | -12.7 | 30.7 | 0 | 2018-01-02 | -7.6 | 25.6 | 0 | 2017-01-02 | -3.7 | 21.7 | 0 | 2016-01-02 | -1.5 | 19.5 | 0 | 22.32 | 0
2025-01-03 | -3.8 | 21.8 | 0 | 2024-01-03 | -0.3 | 18.3 | 0 | 2023-01-03 | 1.5 | 16.5 | 0 | 2022-01-03 | -15.9 | 33.9 | 0 | 2021-01-03 | -4.6 | 22.6 | 0 | 2020-01-03 | 3.1 | 14.9 | 0 | 2019-01-03 | -12.8 | 30.8 | 0 | 2018-01-03 | -7.6 | 25.6 | 0 | 2017-01-03 | -3.7 | 21.7 | 0 | 2016-01-03 | -1.1 | 19.1 | 0 | 22.52 | 0
2025-01-03 | -5.1 | 23.1 | 0 | 2024-01-03 | -0.3 | 18.3 | 0 | 2023-01-03 | 1.3 | 16.7 | 0 | 2022-01-03 | -16.6 | 34.6 | 0 | 2021-01-03 | -6.2 | 24.2 | 0 | 2020-01-03 | 3.3 | 14.7 | 0 | 2019-01-03 | -12.9 | 30.9 | 0 | 2018-01-03 | -8 | 26 | 0 | 2017-01-03 | -3.2 | 21.2 | 0 | 2016-01-03 | -1.1 | 19.1 | 0 | 22.88 | 0
2025-01-03 | -5.5 | 23.5 | 0 | 2024-01-03 | -0.2 | 18.2 | 0 | 2023-01-03 | 1 | 17 | 0 | 2022-01-03 | -17.8 | 35.8 | 0 | 2021-01-03 | -5.2 | 23.2 | 0 | 2020-01-03 | 3.1 | 14.9 | 0 | 2019-01-03 | -12.9 | 30.9 | 0 | 2018-01-03 | -8 | 26 | 0 | 2017-01-03 | -3 | 21 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 22.97 | 0
2025-01-03 | -5.6 | 23.6 | 0 | 2024-01-03 | -0.1 | 18.1 | 0 | 2023-01-03 | 0.8 | 17.2 | 0 | 2022-01-03 | -17.4 | 35.4 | 0 | 2021-01-03 | -4.5 | 22.5 | 0 | 2020-01-03 | 3 | 15 | 0 | 2019-01-03 | -12.8 | 30.8 | 0 | 2018-01-03 | -8 | 26 | 0 | 2017-01-03 | -3 | 21 | 0 | 2016-01-03 | -1.3 | 19.3 | 0 | 22.89 | 0
2025-01-03 | -6.1 | 24.1 | 0 | 2024-01-03 | -0.1 | 18.1 | 0 | 2023-01-03 | -0.7 | 18.7 | 0 | 2022-01-03 | -18 | 36 | 0 | 2021-01-03 | -4.4 | 22.4 | 0 | 2020-01-03 | 3 | 15 | 0 | 2019-01-03 | -12.8 | 30.8 | 0 | 2018-01-03 | -8.7 | 26.7 | 0 | 2017-01-03 | -3.2 | 21.2 | 0 | 2016-01-03 | -1.3 | 19.3 | 0 | 23.23 | 0
2025-01-03 | -6.6 | 24.6 | 0 | 2024-01-03 | -0.2 | 18.2 | 0 | 2023-01-03 | -0.6 | 18.6 | 0 | 2022-01-03 | -18.1 | 36.1 | 0 | 2021-01-03 | -5.2 | 23.2 | 0 | 2020-01-03 | 3 | 15 | 0 | 2019-01-03 | -12.5 | 30.5 | 0 | 2018-01-03 | -9.6 | 27.6 | 0 | 2017-01-03 | -3.1 | 21.1 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 23.41 | 0
2025-01-03 | -6.8 | 24.8 | 0 | 2024-01-03 | -0.3 | 18.3 | 0 | 2023-01-03 | -0.5 | 18.5 | 0 | 2022-01-03 | -19.1 | 37.1 | 0 | 2021-01-03 | -5.2 | 23.2 | 0 | 2020-01-03 | 3.4 | 14.6 | 0 | 2019-01-03 | -12.2 | 30.2 | 0 | 2018-01-03 | -9.3 | 27.3 | 0 | 2017-01-03 | -3.3 | 21.3 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 23.45 | 0
2025-01-03 | -7.2 | 25.2 | 0 | 2024-01-03 | -0.3 | 18.3 | 0 | 2023-01-03 | -0.9 | 18.9 | 0 | 2022-01-03 | -18.5 | 36.5 | 0 | 2021-01-03 | -5 | 23 | 0 | 2020-01-03 | 3 | 15 | 0 | 2019-01-03 | -12.1 | 30.1 | 0 | 2018-01-03 | -8.2 | 26.2 | 0 | 2017-01-03 | -3.3 | 21.3 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 23.37 | 0
2025-01-03 | -8 | 26 | 0 | 2024-01-03 | -0.4 | 18.4 | 0 | 2023-01-03 | -0.5 | 18.5 | 0 | 2022-01-03 | -18.8 | 36.8 | 0 | 2021-01-03 | -5.3 | 23.3 | 0 | 2020-01-03 | 3.1 | 14.9 | 0 | 2019-01-03 | -11.4 | 29.4 | 0 | 2018-01-03 | -8 | 26 | 0 | 2017-01-03 | -2.5 | 20.5 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 23.3 | 0
2025-01-03 | -7.7 | 25.7 | 0 | 2024-01-03 | -0.1 | 18.1 | 0 | 2023-01-03 | -0.1 | 18.1 | 0 | 2022-01-03 | -18.3 | 36.3 | 0 | 2021-01-03 | -5 | 23 | 0 | 2020-01-03 | 3.5 | 14.5 | 0 | 2019-01-03 | -11 | 29 | 0 | 2018-01-03 | -7.8 | 25.8 | 0 | 2017-01-03 | -2.2 | 20.2 | 0 | 2016-01-03 | -1.2 | 19.2 | 0 | 22.99 | 0
2025-01-03 | -7.7 | 25.7 | 0 | 2024-01-03 | 0.2 | 17.8 | 0 | 2023-01-03 | 0.3 | 17.7 | 0 | 2022-01-03 | -16.8 | 34.8 | 0 | 2021-01-03 | -4.3 | 22.3 | 0 | 2020-01-03 | 3.6 | 14.4 | 0 | 2019-01-03 | -10.4 | 28.4 | 0 | 2018-01-03 | -7 | 25 | 0 | 2017-01-03 | -1.7 | 19.7 | 0 | 2016-01-03 | -1 | 19 | 0 | 22.48 | 0
2025-01-03 | -7 | 25 | 0 | 2024-01-03 | 0.8 | 17.2 | 0 | 2023-01-03 | 1.2 | 16.8 | 0 | 2022-01-03 | -15.8 | 33.8 | 0 | 2021-01-03 | -3.7 | 21.7 | 0 | 2020-01-03 | 3.9 | 14.1 | 0 | 2019-01-03 | -9.9 | 27.9 | 0 | 2018-01-03 | -8.1 | 26.1 | 0 | 2017-01-03 | -1 | 19 | 0 | 2016-01-03 | -0.6 | 18.6 | 0 | 22.02 | 0
2025-01-03 | -7.6 | 25.6 | 0 | 2024-01-03 | 1.7 | 16.3 | 0 | 2023-01-03 | 1.8 | 16.2 | 0 | 2022-01-03 | -14.7 | 32.7 | 0 | 2021-01-03 | -3.2 | 21.2 | 0 | 2020-01-03 | 4.2 | 13.8 | 0 | 2019-01-03 | -9.1 | 27.1 | 0 | 2018-01-03 | -7.7 | 25.7 | 0 | 2017-01-03 | -0.8 | 18.8 | 0 | 2016-01-03 | -0.8 | 18.8 | 0 | 21.62 | 0
2025-01-03 | -7.5 | 25.5 | 0 | 2024-01-03 | 1.9 | 16.1 | 0 | 2023-01-03 | 2.3 | 15.7 | 0 | 2022-01-03 | -13.6 | 31.6 | 0 | 2021-01-03 | -2.6 | 20.6 | 0 | 2020-01-03 | 4.5 | 13.5 | 0 | 2019-01-03 | -8.2 | 26.2 | 0 | 2018-01-03 | -7.7 | 25.7 | 0 | 2017-01-03 | -0.8 | 18.8 | 0 | 2016-01-03 | -2.8 | 20.8 | 0 | 21.45 | 0
2025-01-03 | -7.9 | 25.9 | 0 | 2024-01-03 | 2.4 | 15.6 | 0 | 2023-01-03 | 2.8 | 15.2 | 0 | 2022-01-03 | -13.1 | 31.1 | 0 | 2021-01-03 | -2.4 | 20.4 | 0 | 2020-01-03 | 4.7 | 13.3 | 0 | 2019-01-03 | -7.4 | 25.4 | 0 | 2018-01-03 | -7.7 | 25.7 | 0 | 2017-01-03 | -0.7 | 18.7 | 0 | 2016-01-03 | -4.2 | 22.2 | 0 | 21.35 | 0
2025-01-03 | -7.5 | 25.5 | 0 | 2024-01-03 | 2.4 | 15.6 | 0 | 2023-01-03 | 2.2 | 15.8 | 0 | 2022-01-03 | -12.8 | 30.8 | 0 | 2021-01-03 | -2.5 | 20.5 | 0 | 2020-01-03 | 4.4 | 13.6 | 0 | 2019-01-03 | -6.5 | 24.5 | 0 | 2018-01-03 | -7.6 | 25.6 | 0 | 2017-01-03 | -0.5 | 18.5 | 0 | 2016-01-03 | -5.5 | 23.5 | 0 | 21.39 | 0
2025-01-03 | -8.1 | 26.1 | 0 | 2024-01-03 | 2 | 16 | 0 | 2023-01-03 | 1.9 | 16.1 | 0 | 2022-01-03 | -13.1 | 31.1 | 0 | 2021-01-03 | -2.6 | 20.6 | 0 | 2020-01-03 | 4 | 14 | 0 | 2019-01-03 | -6.1 | 24.1 | 0 | 2018-01-03 | -7.9 | 25.9 | 0 | 2017-01-03 | -0.3 | 18.3 | 0 | 2016-01-03 | -6.8 | 24.8 | 0 | 21.7 | 0
2025-01-03 | -8.9 | 26.9 | 0 | 2024-01-03 | 1.5 | 16.5 | 0 | 2023-01-03 | 1.8 | 16.2 | 0 | 2022-01-03 | -14.9 | 32.9 | 0 | 2021-01-03 | -2.6 | 20.6 | 0 | 2020-01-03 | 3.5 | 14.5 | 0 | 2019-01-03 | -6.1 | 24.1 | 0 | 2018-01-03 | -7.8 | 25.8 | 0 | 2017-01-03 | -0.1 | 18.1 | 0 | 2016-01-03 | -8.7 | 26.7 | 0 | 22.23 | 0
2025-01-03 | -10 | 28 | 0 | 2024-01-03 | 1.1 | 16.9 | 0 | 2023-01-03 | 1.8 | 16.2 | 0 | 2022-01-03 | -15 | 33 | 0 | 2021-01-03 | -2.6 | 20.6 | 0 | 2020-01-03 | 2.9 | 15.1 | 0 | 2019-01-03 | -5.2 | 23.2 | 0 | 2018-01-03 | -7.9 | 25.9 | 0 | 2017-01-03 | 0 | 18 | 0 | 2016-01-03 | -9.9 | 27.9 | 0 | 22.48 | 0
2025-01-03 | -10 | 28 | 0 | 2024-01-03 | 0.8 | 17.2 | 0 | 2023-01-03 | 2 | 16 | 0 | 2022-01-03 | -16.3 | 34.3 | 0 | 2021-01-03 | -2.6 | 20.6 | 0 | 2020-01-03 | 2.9 | 15.1 | 0 | 2019-01-03 | -5.1 | 23.1 | 0 | 2018-01-03 | -8 | 26 | 0 | 2017-01-03 | 0 | 18 | 0 | 2016-01-03 | -10.7 | 28.7 | 0 | 22.7 | 0
2025-01-03 | -10.1 | 28.1 | 0 | 2024-01-03 | 0.7 | 17.3 | 0 | 2023-01-03 | 1.9 | 16.1 | 0 | 2022-01-03 | -15.6 | 33.6 | 0 | 2021-01-03 | -2.8 | 20.8 | 0 | 2020-01-03 | 2.7 | 15.3 | 0 | 2019-01-03 | -2.3 | 20.3 | 0 | 2018-01-03 | -8.2 | 26.2 | 0 | 2017-01-03 | 0 | 18 | 0 | 2016-01-03 | -11.8 | 29.8 | 0 | 22.55 | 0
2025-01-03 | -10.1 | 28.1 | 0 | 2024-01-03 | 0.5 | 17.5 | 0 | 2023-01-03 | 1.9 | 16.1 | 0 | 2022-01-03 | -16.4 | 34.4 | 0 | 2021-01-03 | -3 | 21 | 0 | 2020-01-03 | 2.5 | 15.5 | 0 | 2019-01-03 | -1.8 | 19.8 | 0 | 2018-01-03 | -8.3 | 26.3 | 0 | 2017-01-03 | 0.1 | 17.9 | 0 | 2016-01-03 | -12.9 | 30.9 | 0 | 22.75 | 0
2025-01-03 | -10.3 | 28.3 | 0 | 2024-01-03 | 0.2 | 17.8 | 0 | 2023-01-03 | 1.8 | 16.2 | 0 | 2022-01-03 | -16 | 34 | 0 | 2021-01-03 | -3.2 | 21.2 | 0 | 2020-01-03 | 2.3 | 15.7 | 0 | 2019-01-03 | -1.6 | 19.6 | 0 | 2018-01-03 | -8.3 | 26.3 | 0 | 2017-01-03 | 0.1 | 17.9 | 0 | 2016-01-03 | -14.1 | 32.1 | 0 | 22.91 | 0
2025-01-03 | -10.6 | 28.6 | 0 | 2024-01-03 | 0 | 18 | 0 | 2023-01-03 | 2 | 16 | 0 | 2022-01-03 | -16.9 | 34.9 | 0 | 2021-01-03 | -3.3 | 21.3 | 0 | 2020-01-03 | 1.3 | 16.7 | 0 | 2019-01-03 | -1.5 | 19.5 | 0 | 2018-01-03 | -8.1 | 26.1 | 0 | 2017-01-03 | 0.2 | 17.8 | 0 | 2016-01-03 | -14.7 | 32.7 | 0 | 23.16 | 0
2025-01-04 | -11.2 | 29.2 | 0 | 2024-01-04 | 0 | 18 | 0 | 2023-01-04 | 1.6 | 16.4 | 0 | 2022-01-04 | -16 | 34 | 0 | 2021-01-04 | -3.3 | 21.3 | 0 | 2020-01-04 | 1.5 | 16.5 | 0 | 2019-01-04 | -1.5 | 19.5 | 0 | 2018-01-04 | -8.1 | 26.1 | 0 | 2017-01-04 | 0.1 | 17.9 | 0 | 2016-01-04 | -15.7 | 33.7 | 0 | 23.26 | 0
2025-01-04 | -12.6 | 30.6 | 0 | 2024-01-04 | -0.1 | 18.1 | 0 | 2023-01-04 | 1 | 17 | 0 | 2022-01-04 | -14.4 | 32.4 | 0 | 2021-01-04 | -3.4 | 21.4 | 0 | 2020-01-04 | 1.3 | 16.7 | 0 | 2019-01-04 | -1.6 | 19.6 | 0 | 2018-01-04 | -8 | 26 | 0 | 2017-01-04 | 0 | 18 | 0 | 2016-01-04 | -16.4 | 34.4 | 0 | 23.42 | 0
2025-01-04 | -13 | 31 | 0 | 2024-01-04 | -0.2 | 18.2 | 0 | 2023-01-04 | 0.6 | 17.4 | 0 | 2022-01-04 | -13.8 | 31.8 | 0 | 2021-01-04 | -3.2 | 21.2 | 0 | 2020-01-04 | 1.1 | 16.9 | 0 | 2019-01-04 | -1.7 | 19.7 | 0 | 2018-01-04 | -8 | 26 | 0 | 2017-01-04 | 0 | 18 | 0 | 2016-01-04 | -17.3 | 35.3 | 0 | 23.55 | 0
2025-01-04 | -12.7 | 30.7 | 0 | 2024-01-04 | -2.5 | 20.5 | 0 | 2023-01-04 | 0.8 | 17.2 | 0 | 2022-01-04 | -13.2 | 31.2 | 0 | 2021-01-04 | -3.4 | 21.4 | 0 | 2020-01-04 | 1 | 17 | 0 | 2019-01-04 | -1.2 | 19.2 | 0 | 2018-01-04 | -8.1 | 26.1 | 0 | 2017-01-04 | 0 | 18 | 0 | 2016-01-04 | -17.9 | 35.9 | 0 | 23.72 | 0
2025-01-04 | -13 | 31 | 0 | 2024-01-04 | -4.9 | 22.9 | 0 | 2023-01-04 | 0.8 | 17.2 | 0 | 2022-01-04 | -12.2 | 30.2 | 0 | 2021-01-04 | -3.3 | 21.3 | 0 | 2020-01-04 | 0.7 | 17.3 | 0 | 2019-01-04 | -0.6 | 18.6 | 0 | 2018-01-04 | -8 | 26 | 0 | 2017-01-04 | 0 | 18 | 0 | 2016-01-04 | -18.3 | 36.3 | 0 | 23.88 | 0
2025-01-04 | -13 | 31 | 0 | 2024-01-04 | -6.4 | 24.4 | 0 | 2023-01-04 | 1 | 17 | 0 | 2022-01-04 | -11.2 | 29.2 | 0 | 2021-01-04 | -3.2 | 21.2 | 0 | 2020-01-04 | 0.5 | 17.5 | 0 | 2019-01-04 | -0.2 | 18.2 | 0 | 2018-01-04 | -7.9 | 25.9 | 0 | 2017-01-04 | -0.1 | 18.1 | 0 | 2016-01-04 | -18.6 | 36.6 | 0 | 23.91 | 0
2025-01-04 | -13.2 | 31.2 | 0 | 2024-01-04 | -7.6 | 25.6 | 0 | 2023-01-04 | 1.2 | 16.8 | 0 | 2022-01-04 | -9.7 | 27.7 | 0 | 2021-01-04 | -3.2 | 21.2 | 0 | 2020-01-04 | 0.4 | 17.6 | 0 | 2019-01-04 | 0.3 | 17.7 | 0 | 2018-01-04 | -8.2 | 26.2 | 0 | 2017-01-04 | -0.3 | 18.3 | 0 | 2016-01-04 | -19.4 | 37.4 | 0 | 23.97 | 0
2025-01-04 | -13.1 | 31.1 | 0 | 2024-01-04 | -9.1 | 27.1 | 0 | 2023-01-04 | 0.8 | 17.2 | 0 | 2022-01-04 | -8.3 | 26.3 | 0 | 2021-01-04 | -3.3 | 21.3 | 0 | 2020-01-04 | 0.2 | 17.8 | 0 | 2019-01-04 | 0.5 | 17.5 | 0 | 2018-01-04 | -8.6 | 26.6 | 0 | 2017-01-04 | -0.5 | 18.5 | 0 | 2016-01-04 | -19.6 | 37.6 | 0 | 24.1 | 0
2025-01-04 | -13 | 31 | 0 | 2024-01-04 | -9.7 | 27.7 | 0 | 2023-01-04 | 1 | 17 | 0 | 2022-01-04 | -7.6 | 25.6 | 0 | 2021-01-04 | -3 | 21 | 0 | 2020-01-04 | 0.1 | 17.9 | 0 | 2019-01-04 | 0.5 | 17.5 | 0 | 2018-01-04 | -9.4 | 27.4 | 0 | 2017-01-04 | -0.5 | 18.5 | 0 | 2016-01-04 | -19.1 | 37.1 | 0 | 24.07 | 0
2025-01-04 | -12.6 | 30.6 | 0 | 2024-01-04 | -9.1 | 27.1 | 0 | 2023-01-04 | 1.2 | 16.8 | 0 | 2022-01-04 | -7 | 25 | 0 | 2021-01-04 | -2.9 | 20.9 | 0 | 2020-01-04 | 0.1 | 17.9 | 0 | 2019-01-04 | 0.9 | 17.1 | 0 | 2018-01-04 | -10.4 | 28.4 | 0 | 2017-01-04 | -0.2 | 18.2 | 0 | 2016-01-04 | -18.3 | 36.3 | 0 | 23.83 | 0
2025-01-04 | -12.3 | 30.3 | 0 | 2024-01-04 | -8.9 | 26.9 | 0 | 2023-01-04 | 1.3 | 16.7 | 0 | 2022-01-04 | -6.7 | 24.7 | 0 | 2021-01-04 | -2.7 | 20.7 | 0 | 2020-01-04 | 0.1 | 17.9 | 0 | 2019-01-04 | 1.2 | 16.8 | 0 | 2018-01-04 | -10.5 | 28.5 | 0 | 2017-01-04 | 0.2 | 17.8 | 0 | 2016-01-04 | -17.1 | 35.1 | 0 | 23.54 | 0
2025-01-04 | -11.9 | 29.9 | 0 | 2024-01-04 | -9 | 27 | 0 | 2023-01-04 | 1.5 | 16.5 | 0 | 2022-01-04 | -5.6 | 23.6 | 0 | 2021-01-04 | -2.5 | 20.5 | 0 | 2020-01-04 | -0.6 | 18.6 | 0 | 2019-01-04 | 1.4 | 16.6 | 0 | 2018-01-04 | -9.8 | 27.8 | 0 | 2017-01-04 | 1.2 | 16.8 | 0 | 2016-01-04 | -16.4 | 34.4 | 0 | 23.17 | 0
2025-01-04 | -11.5 | 29.5 | 0 | 2024-01-04 | -8.8 | 26.8 | 0 | 2023-01-04 | 1.8 | 16.2 | 0 | 2022-01-04 | -4.5 | 22.5 | 0 | 2021-01-04 | -1.9 | 19.9 | 0 | 2020-01-04 | -0.4 | 18.4 | 0 | 2019-01-04 | 1.6 | 16.4 | 0 | 2018-01-04 | -9.3 | 27.3 | 0 | 2017-01-04 | 1.6 | 16.4 | 0 | 2016-01-04 | -15.5 | 33.5 | 0 | 22.69 | 0
2025-01-04 | -11 | 29 | 0 | 2024-01-04 | -8.1 | 26.1 | 0 | 2023-01-04 | 1.9 | 16.1 | 0 | 2022-01-04 | -3.7 | 21.7 | 0 | 2021-01-04 | -1.3 | 19.3 | 0 | 2020-01-04 | -0.4 | 18.4 | 0 | 2019-01-04 | 1.8 | 16.2 | 0 | 2018-01-04 | -8.5 | 26.5 | 0 | 2017-01-04 | 2 | 16 | 0 | 2016-01-04 | -14.9 | 32.9 | 0 | 22.22 | 0
2025-01-04 | -10.6 | 28.6 | 0 | 2024-01-04 | -8.2 | 26.2 | 0 | 2023-01-04 | 1.9 | 16.1 | 0 | 2022-01-04 | -3.3 | 21.3 | 0 | 2021-01-04 | -1.1 | 19.1 | 0 | 2020-01-04 | -0.5 | 18.5 | 0 | 2019-01-04 | 1.9 | 16.1 | 0 | 2018-01-04 | -7.9 | 25.9 | 0 | 2017-01-04 | 2.7 | 15.3 | 0 | 2016-01-04 | -14.6 | 32.6 | 0 | 21.97 | 0
2025-01-04 | -10 | 28 | 0 | 2024-01-04 | -8.3 | 26.3 | 0 | 2023-01-04 | 1.8 | 16.2 | 0 | 2022-01-04 | -2.5 | 20.5 | 0 | 2021-01-04 | -1 | 19 | 0 | 2020-01-04 | -0.8 | 18.8 | 0 | 2019-01-04 | 2 | 16 | 0 | 2018-01-04 | -10.9 | 28.9 | 0 | 2017-01-04 | 0 | 18 | 0 | 2016-01-04 | -14.6 | 32.6 | 0 | 22.43 | 0
2025-01-04 | -9.8 | 27.8 | 0 | 2024-01-04 | -8.9 | 26.9 | 0 | 2023-01-04 | 1.2 | 16.8 | 0 | 2022-01-04 | -2.5 | 20.5 | 0 | 2021-01-04 | -0.9 | 18.9 | 0 | 2020-01-04 | -0.9 | 18.9 | 0 | 2019-01-04 | 1.9 | 16.1 | 0 | 2018-01-04 | -11.6 | 29.6 | 0 | 2017-01-04 | -0.4 | 18.4 | 0 | 2016-01-04 | -15.3 | 33.3 | 0 | 22.72 | 0
2025-01-04 | -10.3 | 28.3 | 0 | 2024-01-04 | -10.4 | 28.4 | 0 | 2023-01-04 | 0.7 | 17.3 | 0 | 2022-01-04 | -2.8 | 20.8 | 0 | 2021-01-04 | -1.1 | 19.1 | 0 | 2020-01-04 | -1 | 19 | 0 | 2019-01-04 | 1.6 | 16.4 | 0 | 2018-01-04 | -11.9 | 29.9 | 0 | 2017-01-04 | -1.6 | 19.6 | 0 | 2016-01-04 | -15.2 | 33.2 | 0 | 23.2 | 0
2025-01-04 | -10 | 28 | 0 | 2024-01-04 | -10.8 | 28.8 | 0 | 2023-01-04 | 0.3 | 17.7 | 0 | 2022-01-04 | -3.5 | 21.5 | 0 | 2021-01-04 | -1.3 | 19.3 | 0 | 2020-01-04 | -0.8 | 18.8 | 0 | 2019-01-04 | 1.6 | 16.4 | 0 | 2018-01-04 | -13.3 | 31.3 | 0 | 2017-01-04 | -2.7 | 20.7 | 0 | 2016-01-04 | -15.1 | 33.1 | 0 | 23.56 | 0
2025-01-04 | -10.2 | 28.2 | 0 | 2024-01-04 | -11.2 | 29.2 | 0 | 2023-01-04 | 0.3 | 17.7 | 0 | 2022-01-04 | -3.5 | 21.5 | 0 | 2021-01-04 | -1.3 | 19.3 | 0 | 2020-01-04 | -1 | 19 | 0 | 2019-01-04 | 1.8 | 16.2 | 0 | 2018-01-04 | -14.9 | 32.9 | 0 | 2017-01-04 | -4.4 | 22.4 | 0 | 2016-01-04 | -16.5 | 34.5 | 0 | 24.09 | 0
2025-01-04 | -9.9 | 27.9 | 0 | 2024-01-04 | -11.2 | 29.2 | 0 | 2023-01-04 | 0.2 | 17.8 | 0 | 2022-01-04 | -2.8 | 20.8 | 0 | 2021-01-04 | -1.5 | 19.5 | 0 | 2020-01-04 | -1.2 | 19.2 | 0 | 2019-01-04 | 1.6 | 16.4 | 0 | 2018-01-04 | -15.1 | 33.1 | 0 | 2017-01-04 | -4.7 | 22.7 | 0 | 2016-01-04 | -16.5 | 34.5 | 0 | 24.11 | 0
2025-01-04 | -9.7 | 27.7 | 0 | 2024-01-04 | -12.2 | 30.2 | 0 | 2023-01-04 | 0.1 | 17.9 | 0 | 2022-01-04 | -1.4 | 19.4 | 0 | 2021-01-04 | -2 | 20 | 0 | 2020-01-04 | -1.7 | 19.7 | 0 | 2019-01-04 | 1.1 | 16.9 | 0 | 2018-01-04 | -15.8 | 33.8 | 0 | 2017-01-04 | -5.9 | 23.9 | 0 | 2016-01-04 | -17.6 | 35.6 | 0 | 24.51 | 0
2025-01-04 | -10.2 | 28.2 | 0 | 2024-01-04 | -12.4 | 30.4 | 0 | 2023-01-04 | -0.4 | 18.4 | 0 | 2022-01-04 | -1.5 | 19.5 | 0 | 2021-01-04 | -2.1 | 20.1 | 0 | 2020-01-04 | -1.9 | 19.9 | 0 | 2019-01-04 | 0.8 | 17.2 | 0 | 2018-01-04 | -17 | 35 | 0 | 2017-01-04 | -6.2 | 24.2 | 0 | 2016-01-04 | -18 | 36 | 0 | 24.89 | 0
2025-01-04 | -10 | 28 | 0 | 2024-01-04 | -12.8 | 30.8 | 0 | 2023-01-04 | -0.9 | 18.9 | 0 | 2022-01-04 | -1.5 | 19.5 | 0 | 2021-01-04 | -2.2 | 20.2 | 0 | 2020-01-04 | -2.1 | 20.1 | 0 | 2019-01-04 | 0.9 | 17.1 | 0 | 2018-01-04 | -18.1 | 36.1 | 0 | 2017-01-04 | -6.7 | 24.7 | 0 | 2016-01-04 | -18.9 | 36.9 | 0 | 25.23 | 0
2025-01-05 | -10.1 | 28.1 | 0 | 2024-01-05 | -13.5 | 31.5 | 0 | 2023-01-05 | -1.3 | 19.3 | 0 | 2022-01-05 | -2.6 | 20.6 | 0 | 2021-01-05 | -2.2 | 20.2 | 0 | 2020-01-05 | -2.5 | 20.5 | 0 | 2019-01-05 | -0.4 | 18.4 | 0 | 2018-01-05 | -19 | 37 | 0 | 2017-01-05 | -7.4 | 25.4 | 0 | 2016-01-05 | -18.6 | 36.6 | 0 | 25.76 | 0
2025-01-05 | -10 | 28 | 0 | 2024-01-05 | -13.7 | 31.7 | 0 | 2023-01-05 | -1.5 | 19.5 | 0 | 2022-01-05 | -3.2 | 21.2 | 0 | 2021-01-05 | -2.2 | 20.2 | 0 | 2020-01-05 | -3 | 21 | 0 | 2019-01-05 | -1.9 | 19.9 | 0 | 2018-01-05 | -20.2 | 38.2 | 0 | 2017-01-05 | -7.6 | 25.6 | 0 | 2016-01-05 | -19.9 | 37.9 | 0 | 26.32 | 0
2025-01-05 | -9.8 | 27.8 | 0 | 2024-01-05 | -13.8 | 31.8 | 0 | 2023-01-05 | -1.2 | 19.2 | 0 | 2022-01-05 | -3.7 | 21.7 | 0 | 2021-01-05 | -2.2 | 20.2 | 0 | 2020-01-05 | -3.4 | 21.4 | 0 | 2019-01-05 | -2.5 | 20.5 | 0 | 2018-01-05 | -20.7 | 38.7 | 0 | 2017-01-05 | -7.7 | 25.7 | 0 | 2016-01-05 | -20.5 | 38.5 | 0 | 26.55 | 0
2025-01-05 | -10.6 | 28.6 | 0 | 2024-01-05 | -14.2 | 32.2 | 0 | 2023-01-05 | -2 | 20 | 0 | 2022-01-05 | -3.7 | 21.7 | 0 | 2021-01-05 | -2.3 | 20.3 | 0 | 2020-01-05 | -4 | 22 | 0 | 2019-01-05 | -2.1 | 20.1 | 0 | 2018-01-05 | -21.9 | 39.9 | 0 | 2017-01-05 | -7.9 | 25.9 | 0 | 2016-01-05 | -21.6 | 39.6 | 0 | 27.03 | 0
2025-01-05 | -11 | 29 | 0 | 2024-01-05 | -13 | 31 | 0 | 2023-01-05 | -2.6 | 20.6 | 0 | 2022-01-05 | -4.4 | 22.4 | 0 | 2021-01-05 | -2.5 | 20.5 | 0 | 2020-01-05 | -5.2 | 23.2 | 0 | 2019-01-05 | -1.2 | 19.2 | 0 | 2018-01-05 | -22.7 | 40.7 | 0 | 2017-01-05 | -8 | 26 | 0 | 2016-01-05 | -23.2 | 41.2 | 0 | 27.38 | 0
2025-01-05 | -11.1 | 29.1 | 0 | 2024-01-05 | -12.2 | 30.2 | 0 | 2023-01-05 | -3 | 21 | 0 | 2022-01-05 | -4.9 | 22.9 | 0 | 2021-01-05 | -2.6 | 20.6 | 0 | 2020-01-05 | -5.8 | 23.8 | 0 | 2019-01-05 | -0.6 | 18.6 | 0 | 2018-01-05 | -23.2 | 41.2 | 0 | 2017-01-05 | -9.6 | 27.6 | 0 | 2016-01-05 | -21.6 | 39.6 | 0 | 27.46 | 0
2025-01-05 | -11.6 | 29.6 | 0 | 2024-01-05 | -11.7 | 29.7 | 0 | 2023-01-05 | -3 | 21 | 0 | 2022-01-05 | -5.5 | 23.5 | 0 | 2021-01-05 | -2.7 | 20.7 | 0 | 2020-01-05 | -7 | 25 | 0 | 2019-01-05 | -0.6 | 18.6 | 0 | 2018-01-05 | -23.7 | 41.7 | 0 | 2017-01-05 | -11.5 | 29.5 | 0 | 2016-01-05 | -24.6 | 42.6 | 0 | 28.19 | 0
2025-01-05 | -11.8 | 29.8 | 0 | 2024-01-05 | -11.3 | 29.3 | 0 | 2023-01-05 | -3.2 | 21.2 | 0 | 2022-01-05 | -6 | 24 | 0 | 2021-01-05 | -2.8 | 20.8 | 0 | 2020-01-05 | -7.5 | 25.5 | 0 | 2019-01-05 | 0.3 | 17.7 | 0 | 2018-01-05 | -24.1 | 42.1 | 0 | 2017-01-05 | -12.7 | 30.7 | 0 | 2016-01-05 | -24.2 | 42.2 | 0 | 28.33 | 0
2025-01-05 | -12.3 | 30.3 | 0 | 2024-01-05 | -10.6 | 28.6 | 0 | 2023-01-05 | -3.2 | 21.2 | 0 | 2022-01-05 | -6.4 | 24.4 | 0 | 2021-01-05 | -2.9 | 20.9 | 0 | 2020-01-05 | -7.5 | 25.5 | 0 | 2019-01-05 | -0.2 | 18.2 | 0 | 2018-01-05 | -24.4 | 42.4 | 0 | 2017-01-05 | -13.2 | 31.2 | 0 | 2016-01-05 | -24.1 | 42.1 | 0 | 28.48 | 0
2025-01-05 | -12.9 | 30.9 | 0 | 2024-01-05 | -10 | 28 | 0 | 2023-01-05 | -3.2 | 21.2 | 0 | 2022-01-05 | -6.2 | 24.2 | 0 | 2021-01-05 | -3 | 21 | 0 | 2020-01-05 | -7.3 | 25.3 | 0 | 2019-01-05 | -0.5 | 18.5 | 0 | 2018-01-05 | -24 | 42 | 0 | 2017-01-05 | -13.7 | 31.7 | 0 | 2016-01-05 | -22.6 | 40.6 | 0 | 28.34 | 0
2025-01-05 | -13.1 | 31.1 | 0 | 2024-01-05 | -9 | 27 | 0 | 2023-01-05 | -2.8 | 20.8 | 0 | 2022-01-05 | -4.9 | 22.9 | 0 | 2021-01-05 | -3 | 21 | 0 | 2020-01-05 | -7.1 | 25.1 | 0 | 2019-01-05 | 0.9 | 17.1 | 0 | 2018-01-05 | -23.5 | 41.5 | 0 | 2017-01-05 | -10.8 | 28.8 | 0 | 2016-01-05 | -18.6 | 36.6 | 0 | 27.19 | 0
2025-01-05 | -13 | 31 | 0 | 2024-01-05 | -7.9 | 25.9 | 0 | 2023-01-05 | -2.6 | 20.6 | 0 | 2022-01-05 | -3.8 | 21.8 | 0 | 2021-01-05 | -3 | 21 | 0 | 2020-01-05 | -6.9 | 24.9 | 0 | 2019-01-05 | 1.4 | 16.6 | 0 | 2018-01-05 | -22.8 | 40.8 | 0 | 2017-01-05 | -8.7 | 26.7 | 0 | 2016-01-05 | -16.6 | 34.6 | 0 | 26.39 | 0
2025-01-05 | -12.7 | 30.7 | 0 | 2024-01-05 | -6.4 | 24.4 | 0 | 2023-01-05 | -2.3 | 20.3 | 0 | 2022-01-05 | -3.1 | 21.1 | 0 | 2021-01-05 | -2.8 | 20.8 | 0 | 2020-01-05 | -6.9 | 24.9 | 0 | 2019-01-05 | 1.6 | 16.4 | 0 | 2018-01-05 | -22.3 | 40.3 | 0 | 2017-01-05 | -7.9 | 25.9 | 0 | 2016-01-05 | -14.4 | 32.4 | 0 | 25.72 | 0
2025-01-05 | -12.5 | 30.5 | 0 | 2024-01-05 | -5.3 | 23.3 | 0 | 2023-01-05 | -2 | 20 | 0 | 2022-01-05 | -2 | 20 | 0 | 2021-01-05 | -2.1 | 20.1 | 0 | 2020-01-05 | -7.1 | 25.1 | 0 | 2019-01-05 | 2.1 | 15.9 | 0 | 2018-01-05 | -22 | 40 | 0 | 2017-01-05 | -7.8 | 25.8 | 0 | 2016-01-05 | -12.3 | 30.3 | 0 | 25.1 | 0
2025-01-05 | -12.5 | 30.5 | 0 | 2024-01-05 | -4.4 | 22.4 | 0 | 2023-01-05 | -2.1 | 20.1 | 0 | 2022-01-05 | -0.5 | 18.5 | 0 | 2021-01-05 | -2 | 20 | 0 | 2020-01-05 | -6.7 | 24.7 | 0 | 2019-01-05 | 2 | 16 | 0 | 2018-01-05 | -22.4 | 40.4 | 0 | 2017-01-05 | -6.8 | 24.8 | 0 | 2016-01-05 | -10.7 | 28.7 | 0 | 24.61 | 0
2025-01-05 | -12.2 | 30.2 | 0 | 2024-01-05 | -3.9 | 21.9 | 0 | 2023-01-05 | -2.2 | 20.2 | 0 | 2022-01-05 | -0.4 | 18.4 | 0 | 2021-01-05 | -1.8 | 19.8 | 0 | 2020-01-05 | -6.2 | 24.2 | 0 | 2019-01-05 | 1.8 | 16.2 | 0 | 2018-01-05 | -22.1 | 40.1 | 0 | 2017-01-05 | -6.4 | 24.4 | 0 | 2016-01-05 | -9.4 | 27.4 | 0 | 24.28 | 0
2025-01-05 | -12.3 | 30.3 | 0 | 2024-01-05 | -4 | 22 | 0 | 2023-01-05 | -2 | 20 | 0 | 2022-01-05 | 2.9 | 15.1 | 0 | 2021-01-05 | -2 | 20 | 0 | 2020-01-05 | -6.9 | 24.9 | 0 | 2019-01-05 | 2 | 16 | 0 | 2018-01-05 | -21.9 | 39.9 | 0 | 2017-01-05 | -6.2 | 24.2 | 0 | 2016-01-05 | -9.5 | 27.5 | 0 | 23.99 | 0
2025-01-05 | -13.4 | 31.4 | 0 | 2024-01-05 | -3.3 | 21.3 | 0 | 2023-01-05 | -1.8 | 19.8 | 0 | 2022-01-05 | 2.5 | 15.5 | 0 | 2021-01-05 | -2.4 | 20.4 | 0 | 2020-01-05 | -8.1 | 26.1 | 0 | 2019-01-05 | 1.4 | 16.6 | 0 | 2018-01-05 | -21.7 | 39.7 | 0 | 2017-01-05 | -6.1 | 24.1 | 0 | 2016-01-05 | -10.5 | 28.5 | 0 | 24.34 | 0
2025-01-05 | -13.5 | 31.5 | 0 | 2024-01-05 | -3 | 21 | 0 | 2023-01-05 | -2 | 20 | 0 | 2022-01-05 | 2.3 | 15.7 | 0 | 2021-01-05 | -2.4 | 20.4 | 0 | 2020-01-05 | -8.4 | 26.4 | 0 | 2019-01-05 | 0.9 | 17.1 | 0 | 2018-01-05 | -21.7 | 39.7 | 0 | 2017-01-05 | -6.3 | 24.3 | 0 | 2016-01-05 | -11.3 | 29.3 | 0 | 24.54 | 0
2025-01-05 | -13.1 | 31.1 | 0 | 2024-01-05 | -2.6 | 20.6 | 0 | 2023-01-05 | -1.6 | 19.6 | 0 | 2022-01-05 | 1.6 | 16.4 | 0 | 2021-01-05 | -2.7 | 20.7 | 0 | 2020-01-05 | -7.6 | 25.6 | 0 | 2019-01-05 | 1.6 | 16.4 | 0 | 2018-01-05 | -22 | 40 | 0 | 2017-01-05 | -6.8 | 24.8 | 0 | 2016-01-05 | -11 | 29 | 0 | 24.42 | 0
2025-01-05 | -14.2 | 32.2 | 0 | 2024-01-05 | -2.2 | 20.2 | 0 | 2023-01-05 | -1.6 | 19.6 | 0 | 2022-01-05 | 1.1 | 16.9 | 0 | 2021-01-05 | -2.7 | 20.7 | 0 | 2020-01-05 | -8.7 | 26.7 | 0 | 2019-01-05 | 0.9 | 17.1 | 0 | 2018-01-05 | -22.7 | 40.7 | 0 | 2017-01-05 | -7.5 | 25.5 | 0 | 2016-01-05 | -10.5 | 28.5 | 0 | 24.81 | 0
2025-01-05 | -14.5 | 32.5 | 0 | 2024-01-05 | -2.1 | 20.1 | 0 | 2023-01-05 | -1.6 | 19.6 | 0 | 2022-01-05 | 1.2 | 16.8 | 0 | 2021-01-05 | -2.7 | 20.7 | 0 | 2020-01-05 | -11 | 29 | 0 | 2019-01-05 | 0.6 | 17.4 | 0 | 2018-01-05 | -23.4 | 41.4 | 0 | 2017-01-05 | -8.8 | 26.8 | 0 | 2016-01-05 | -10.4 | 28.4 | 0 | 25.27 | 0
2025-01-05 | -13.9 | 31.9 | 0 | 2024-01-05 | -2 | 20 | 0 | 2023-01-05 | -1.6 | 19.6 | 0 | 2022-01-05 | 1.8 | 16.2 | 0 | 2021-01-05 | -2.9 | 20.9 | 0 | 2020-01-05 | -10.8 | 28.8 | 0 | 2019-01-05 | 0.6 | 17.4 | 0 | 2018-01-05 | -23.8 | 41.8 | 0 | 2017-01-05 | -9.1 | 27.1 | 0 | 2016-01-05 | -11.9 | 29.9 | 0 | 25.36 | 0
2025-01-05 | -14.5 | 32.5 | 0 | 2024-01-05 | -2.4 | 20.4 | 0 | 2023-01-05 | -1.7 | 19.7 | 0 | 2022-01-05 | 0.9 | 17.1 | 0 | 2021-01-05 | -3 | 21 | 0 | 2020-01-05 | -11.4 | 29.4 | 0 | 2019-01-05 | 0.4 | 17.6 | 0 | 2018-01-05 | -24.2 | 42.2 | 0 | 2017-01-05 | -9.3 | 27.3 | 0 | 2016-01-05 | -7.2 | 25.2 | 0 | 25.24 | 0
2025-01-06 | -15.2 | 33.2 | 0 | 2024-01-06 | -2.7 | 20.7 | 0 | 2023-01-06 | -1.9 | 19.9 | 0 | 2022-01-06 | 0.7 | 17.3 | 0 | 2021-01-06 | -3.2 | 21.2 | 0 | 2020-01-06 | -10.9 | 28.9 | 0 | 2019-01-06 | 0 | 18 | 0 | 2018-01-06 | -24.7 | 42.7 | 0 | 2017-01-06 | -10.4 | 28.4 | 0 | 2016-01-06 | -8.9 | 26.9 | 0 | 25.72 | 0
2025-01-06 | -16.1 | 34.1 | 0 | 2024-01-06 | -3 | 21 | 0 | 2023-01-06 | -2.1 | 20.1 | 0 | 2022-01-06 | 0.4 | 17.6 | 0 | 2021-01-06 | -3.4 | 21.4 | 0 | 2020-01-06 | -11.4 | 29.4 | 0 | 2019-01-06 | -0.2 | 18.2 | 0 | 2018-01-06 | -25.2 | 43.2 | 0 | 2017-01-06 | -11 | 29 | 0 | 2016-01-06 | -8.5 | 26.5 | 0 | 26.05 | 0
2025-01-06 | -16.3 | 34.3 | 0 | 2024-01-06 | -3.3 | 21.3 | 0 | 2023-01-06 | -2.1 | 20.1 | 0 | 2022-01-06 | -0.7 | 18.7 | 0 | 2021-01-06 | -3.4 | 21.4 | 0 | 2020-01-06 | -11.2 | 29.2 | 0 | 2019-01-06 | -0.4 | 18.4 | 0 | 2018-01-06 | -25.3 | 43.3 | 0 | 2017-01-06 | -11.8 | 29.8 | 0 | 2016-01-06 | -9.2 | 27.2 | 0 | 26.37 | 0
2025-01-06 | -17.3 | 35.3 | 0 | 2024-01-06 | -5.1 | 23.1 | 0 | 2023-01-06 | -2.2 | 20.2 | 0 | 2022-01-06 | -2.2 | 20.2 | 0 | 2021-01-06 | -3.4 | 21.4 | 0 | 2020-01-06 | -10.9 | 28.9 | 0 | 2019-01-06 | -0.6 | 18.6 | 0 | 2018-01-06 | -25.5 | 43.5 | 0 | 2017-01-06 | -12.2 | 30.2 | 0 | 2016-01-06 | -9.7 | 27.7 | 0 | 26.91 | 0
2025-01-06 | -17.1 | 35.1 | 0 | 2024-01-06 | -6.6 | 24.6 | 0 | 2023-01-06 | -2.5 | 20.5 | 0 | 2022-01-06 | -3.5 | 21.5 | 0 | 2021-01-06 | -3.4 | 21.4 | 0 | 2020-01-06 | -10.8 | 28.8 | 0 | 2019-01-06 | -0.2 | 18.2 | 0 | 2018-01-06 | -25.6 | 43.6 | 0 | 2017-01-06 | -15 | 33 | 0 | 2016-01-06 | -10.4 | 28.4 | 0 | 27.51 | 0
2025-01-06 | -16.2 | 34.2 | 0 | 2024-01-06 | -8.6 | 26.6 | 0 | 2023-01-06 | -2.4 | 20.4 | 0 | 2022-01-06 | -3.4 | 21.4 | 0 | 2021-01-06 | -2.4 | 20.4 | 0 | 2020-01-06 | -10.7 | 28.7 | 0 | 2019-01-06 | -0.2 | 18.2 | 0 | 2018-01-06 | -25.6 | 43.6 | 0 | 2017-01-06 | -14.7 | 32.7 | 0 | 2016-01-06 | -10.4 | 28.4 | 0 | 27.46 | 0
2025-01-06 | -17 | 35 | 0 | 2024-01-06 | -9.7 | 27.7 | 0 | 2023-01-06 | -2.4 | 20.4 | 0 | 2022-01-06 | -3.9 | 21.9 | 0 | 2021-01-06 | -2.7 | 20.7 | 0 | 2020-01-06 | -10.5 | 28.5 | 0 | 2019-01-06 | -0.2 | 18.2 | 0 | 2018-01-06 | -25.5 | 43.5 | 0 | 2017-01-06 | -15.1 | 33.1 | 0 | 2016-01-06 | -11.8 | 29.8 | 0 | 27.88 | 0
2025-01-06 | -16.8 | 34.8 | 0 | 2024-01-06 | -9.7 | 27.7 | 0 | 2023-01-06 | -2.2 | 20.2 | 0 | 2022-01-06 | -4.2 | 22.2 | 0 | 2021-01-06 | -3 | 21 | 0 | 2020-01-06 | -10.8 | 28.8 | 0 | 2019-01-06 | -1 | 19 | 0 | 2018-01-06 | -25.5 | 43.5 | 0 | 2017-01-06 | -15.4 | 33.4 | 0 | 2016-01-06 | -12.7 | 30.7 | 0 | 28.13 | 0
2025-01-06 | -16.2 | 34.2 | 0 | 2024-01-06 | -9.6 | 27.6 | 0 | 2023-01-06 | -2.4 | 20.4 | 0 | 2022-01-06 | -3.8 | 21.8 | 0 | 2021-01-06 | -3.2 | 21.2 | 0 | 2020-01-06 | -10.5 | 28.5 | 0 | 2019-01-06 | -2.5 | 20.5 | 0 | 2018-01-06 | -25.4 | 43.4 | 0 | 2017-01-06 | -15.8 | 33.8 | 0 | 2016-01-06 | -10.8 | 28.8 | 0 | 28.02 | 0
2025-01-06 | -14.4 | 32.4 | 0 | 2024-01-06 | -9.5 | 27.5 | 0 | 2023-01-06 | -2.2 | 20.2 | 0 | 2022-01-06 | -3.8 | 21.8 | 0 | 2021-01-06 | -3.6 | 21.6 | 0 | 2020-01-06 | -9.9 | 27.9 | 0 | 2019-01-06 | -3.1 | 21.1 | 0 | 2018-01-06 | -25.1 | 43.1 | 0 | 2017-01-06 | -16.1 | 34.1 | 0 | 2016-01-06 | -9.7 | 27.7 | 0 | 27.74 | 0
2025-01-06 | -14.1 | 32.1 | 0 | 2024-01-06 | -9.2 | 27.2 | 0 | 2023-01-06 | -1.8 | 19.8 | 0 | 2022-01-06 | -5.6 | 23.6 | 0 | 2021-01-06 | -3.8 | 21.8 | 0 | 2020-01-06 | -9.6 | 27.6 | 0 | 2019-01-06 | -3.4 | 21.4 | 0 | 2018-01-06 | -24.6 | 42.6 | 0 | 2017-01-06 | -13.6 | 31.6 | 0 | 2016-01-06 | -7.4 | 25.4 | 0 | 27.31 | 0
2025-01-06 | -13.3 | 31.3 | 0 | 2024-01-06 | -9.1 | 27.1 | 0 | 2023-01-06 | -1.7 | 19.7 | 0 | 2022-01-06 | -7.3 | 25.3 | 0 | 2021-01-06 | -3.7 | 21.7 | 0 | 2020-01-06 | -9.3 | 27.3 | 0 | 2019-01-06 | -4.3 | 22.3 | 0 | 2018-01-06 | -24.2 | 42.2 | 0 | 2017-01-06 | -12.6 | 30.6 | 0 | 2016-01-06 | -5.5 | 23.5 | 0 | 27.1 | 0
2025-01-06 | -12.7 | 30.7 | 0 | 2024-01-06 | -8.9 | 26.9 | 0 | 2023-01-06 | -1.1 | 19.1 | 0 | 2022-01-06 | -7.9 | 25.9 | 0 | 2021-01-06 | -3.3 | 21.3 | 0 | 2020-01-06 | -8.9 | 26.9 | 0 | 2019-01-06 | -4 | 22 | 0 | 2018-01-06 | -23.3 | 41.3 | 0 | 2017-01-06 | -10.7 | 28.7 | 0 | 2016-01-06 | -3.1 | 21.1 | 0 | 26.39 | 0
2025-01-06 | -12.1 | 30.1 | 0 | 2024-01-06 | -8.8 | 26.8 | 0 | 2023-01-06 | -0.5 | 18.5 | 0 | 2022-01-06 | -7.7 | 25.7 | 0 | 2021-01-06 | -2.9 | 20.9 | 0 | 2020-01-06 | -8.4 | 26.4 | 0 | 2019-01-06 | -4.2 | 22.2 | 0 | 2018-01-06 | -23.1 | 41.1 | 0 | 2017-01-06 | -10.1 | 28.1 | 0 | 2016-01-06 | -1.4 | 19.4 | 0 | 25.92 | 0
2025-01-06 | -11 | 29 | 0 | 2024-01-06 | -8.4 | 26.4 | 0 | 2023-01-06 | -0.3 | 18.3 | 0 | 2022-01-06 | -7.8 | 25.8 | 0 | 2021-01-06 | -3.1 | 21.1 | 0 | 2020-01-06 | -7.7 | 25.7 | 0 | 2019-01-06 | -4.8 | 22.8 | 0 | 2018-01-06 | -22.2 | 40.2 | 0 | 2017-01-06 | -9.5 | 27.5 | 0 | 2016-01-06 | -0.1 | 18.1 | 0 | 25.49 | 0
2025-01-06 | -10.3 | 28.3 | 0 | 2024-01-06 | -8.5 | 26.5 | 0 | 2023-01-06 | -0.1 | 18.1 | 0 | 2022-01-06 | -8.2 | 26.2 | 0 | 2021-01-06 | -2.9 | 20.9 | 0 | 2020-01-06 | -7.6 | 25.6 | 0 | 2019-01-06 | -5.8 | 23.8 | 0 | 2018-01-06 | -21.3 | 39.3 | 0 | 2017-01-06 | -8.7 | 26.7 | 0 | 2016-01-06 | 0.8 | 17.2 | 0 | 25.26 | 0
2025-01-06 | -10 | 28 | 0 | 2024-01-06 | -9.1 | 27.1 | 0 | 2023-01-06 | 0 | 18 | 0 | 2022-01-06 | -9.3 | 27.3 | 0 | 2021-01-06 | -3.2 | 21.2 | 0 | 2020-01-06 | -7.2 | 25.2 | 0 | 2019-01-06 | -7 | 25 | 0 | 2018-01-06 | -21.8 | 39.8 | 0 | 2017-01-06 | -8.8 | 26.8 | 0 | 2016-01-06 | 0.1 | 17.9 | 0 | 25.63 | 0
2025-01-06 | -9.9 | 27.9 | 0 | 2024-01-06 | -10 | 28 | 0 | 2023-01-06 | 0.1 | 17.9 | 0 | 2022-01-06 | -10.2 | 28.2 | 0 | 2021-01-06 | -3.8 | 21.8 | 0 | 2020-01-06 | -7.5 | 25.5 | 0 | 2019-01-06 | -7.8 | 25.8 | 0 | 2018-01-06 | -21.9 | 39.9 | 0 | 2017-01-06 | -10.8 | 28.8 | 0 | 2016-01-06 | -1.9 | 19.9 | 0 | 26.37 | 0
2025-01-06 | -10 | 28 | 0 | 2024-01-06 | -10.2 | 28.2 | 0 | 2023-01-06 | 0.7 | 17.3 | 0 | 2022-01-06 | -10.7 | 28.7 | 0 | 2021-01-06 | -3.8 | 21.8 | 0 | 2020-01-06 | -7.4 | 25.4 | 0 | 2019-01-06 | -8.9 | 26.9 | 0 | 2018-01-06 | -21.8 | 39.8 | 0 | 2017-01-06 | -11.8 | 29.8 | 0 | 2016-01-06 | -1.7 | 19.7 | 0 | 26.56 | 0
2025-01-06 | -10.7 | 28.7 | 0 | 2024-01-06 | -10.4 | 28.4 | 0 | 2023-01-06 | 1 | 17 | 0 | 2022-01-06 | -11.8 | 29.8 | 0 | 2021-01-06 | -4.2 | 22.2 | 0 | 2020-01-06 | -6.7 | 24.7 | 0 | 2019-01-06 | -9.6 | 27.6 | 0 | 2018-01-06 | -21.8 | 39.8 | 0 | 2017-01-06 | -12.1 | 30.1 | 0 | 2016-01-06 | -4.2 | 22.2 | 0 | 27.05 | 0
2025-01-06 | -10.9 | 28.9 | 0 | 2024-01-06 | -10.6 | 28.6 | 0 | 2023-01-06 | -0.1 | 18.1 | 0 | 2022-01-06 | -12.5 | 30.5 | 0 | 2021-01-06 | -4.6 | 22.6 | 0 | 2020-01-06 | -7.3 | 25.3 | 0 | 2019-01-06 | -10.4 | 28.4 | 0 | 2018-01-06 | -22.1 | 40.1 | 0 | 2017-01-06 | -12.7 | 30.7 | 0 | 2016-01-06 | -4 | 22 | 0 | 27.52 | 0
2025-01-06 | -11.3 | 29.3 | 0 | 2024-01-06 | -10.8 | 28.8 | 0 | 2023-01-06 | -0.4 | 18.4 | 0 | 2022-01-06 | -12.4 | 30.4 | 0 | 2021-01-06 | -4.5 | 22.5 | 0 | 2020-01-06 | -7.7 | 25.7 | 0 | 2019-01-06 | -11.4 | 29.4 | 0 | 2018-01-06 | -22.4 | 40.4 | 0 | 2017-01-06 | -15.2 | 33.2 | 0 | 2016-01-06 | -4.4 | 22.4 | 0 | 28.05 | 0
2025-01-06 | -11.5 | 29.5 | 0 | 2024-01-06 | -10.9 | 28.9 | 0 | 2023-01-06 | -0.9 | 18.9 | 0 | 2022-01-06 | -13.9 | 31.9 | 0 | 2021-01-06 | -4.5 | 22.5 | 0 | 2020-01-06 | -8.4 | 26.4 | 0 | 2019-01-06 | -11.9 | 29.9 | 0 | 2018-01-06 | -22.8 | 40.8 | 0 | 2017-01-06 | -14.7 | 32.7 | 0 | 2016-01-06 | -5.2 | 23.2 | 0 | 28.47 | 0
2025-01-06 | -11.1 | 29.1 | 0 | 2024-01-06 | -10.8 | 28.8 | 0 | 2023-01-06 | -1.7 | 19.7 | 0 | 2022-01-06 | -13 | 31 | 0 | 2021-01-06 | -3.7 | 21.7 | 0 | 2020-01-06 | -4.4 | 22.4 | 0 | 2019-01-06 | -12.7 | 30.7 | 0 | 2018-01-06 | -23.2 | 41.2 | 0 | 2017-01-06 | -14.4 | 32.4 | 0 | 2016-01-06 | -5.4 | 23.4 | 0 | 28.04 | 0
2025-01-07 | -10.9 | 28.9 | 0 | 2024-01-07 | -10.5 | 28.5 | 0 | 2023-01-07 | -2.4 | 20.4 | 0 | 2022-01-07 | -12.2 | 30.2 | 0 | 2021-01-07 | -3.1 | 21.1 | 0 | 2020-01-07 | -4.7 | 22.7 | 0 | 2019-01-07 | -13.2 | 31.2 | 0 | 2018-01-07 | -23.6 | 41.6 | 0 | 2017-01-07 | -15.9 | 33.9 | 0 | 2016-01-07 | -6.1 | 24.1 | 0 | 28.26 | 0
2025-01-07 | -10.8 | 28.8 | 0 | 2024-01-07 | -10.2 | 28.2 | 0 | 2023-01-07 | -3 | 21 | 0 | 2022-01-07 | -12.2 | 30.2 | 0 | 2021-01-07 | -2.8 | 20.8 | 0 | 2020-01-07 | -5.9 | 23.9 | 0 | 2019-01-07 | -13.8 | 31.8 | 0 | 2018-01-07 | -24.1 | 42.1 | 0 | 2017-01-07 | -18.3 | 36.3 | 0 | 2016-01-07 | -5.6 | 23.6 | 0 | 28.67 | 0
2025-01-07 | -10.8 | 28.8 | 0 | 2024-01-07 | -9.8 | 27.8 | 0 | 2023-01-07 | -4 | 22 | 0 | 2022-01-07 | -11.7 | 29.7 | 0 | 2021-01-07 | -2.7 | 20.7 | 0 | 2020-01-07 | -4.4 | 22.4 | 0 | 2019-01-07 | -14.8 | 32.8 | 0 | 2018-01-07 | -25.3 | 43.3 | 0 | 2017-01-07 | -16.4 | 34.4 | 0 | 2016-01-07 | -6.8 | 24.8 | 0 | 28.67 | 0
2025-01-07 | -10.6 | 28.6 | 0 | 2024-01-07 | -9.3 | 27.3 | 0 | 2023-01-07 | -4.5 | 22.5 | 0 | 2022-01-07 | -11.4 | 29.4 | 0 | 2021-01-07 | -2.9 | 20.9 | 0 | 2020-01-07 | -5 | 23 | 0 | 2019-01-07 | -14.9 | 32.9 | 0 | 2018-01-07 | -25.6 | 43.6 | 0 | 2017-01-07 | -18.5 | 36.5 | 0 | 2016-01-07 | -5.8 | 23.8 | 0 | 28.85 | 0
2025-01-07 | -10.5 | 28.5 | 0 | 2024-01-07 | -9 | 27 | 0 | 2023-01-07 | -5.6 | 23.6 | 0 | 2022-01-07 | -11.3 | 29.3 | 0 | 2021-01-07 | -3 | 21 | 0 | 2020-01-07 | -4.5 | 22.5 | 0 | 2019-01-07 | -14.9 | 32.9 | 0 | 2018-01-07 | -25.9 | 43.9 | 0 | 2017-01-07 | -17.8 | 35.8 | 0 | 2016-01-07 | -5.9 | 23.9 | 0 | 28.84 | 0
2025-01-07 | -10.7 | 28.7 | 0 | 2024-01-07 | -8.8 | 26.8 | 0 | 2023-01-07 | -5.7 | 23.7 | 0 | 2022-01-07 | -11.5 | 29.5 | 0 | 2021-01-07 | -3.2 | 21.2 | 0 | 2020-01-07 | -5.2 | 23.2 | 0 | 2019-01-07 | -15.4 | 33.4 | 0 | 2018-01-07 | -26.2 | 44.2 | 0 | 2017-01-07 | -18 | 36 | 0 | 2016-01-07 | -5.9 | 23.9 | 0 | 29.06 | 0
2025-01-07 | -10.7 | 28.7 | 0 | 2024-01-07 | -8.5 | 26.5 | 0 | 2023-01-07 | -6.1 | 24.1 | 0 | 2022-01-07 | -11.7 | 29.7 | 0 | 2021-01-07 | -3.5 | 21.5 | 0 | 2020-01-07 | -5.8 | 23.8 | 0 | 2019-01-07 | -15.7 | 33.7 | 0 | 2018-01-07 | -27 | 45 | 0 | 2017-01-07 | -18.5 | 36.5 | 0 | 2016-01-07 | -6.7 | 24.7 | 0 | 29.42 | 0
2025-01-07 | -10.8 | 28.8 | 0 | 2024-01-07 | -8.4 | 26.4 | 0 | 2023-01-07 | -7 | 25 | 0 | 2022-01-07 | -11.7 | 29.7 | 0 | 2021-01-07 | -3.6 | 21.6 | 0 | 2020-01-07 | -6.1 | 24.1 | 0 | 2019-01-07 | -15.8 | 33.8 | 0 | 2018-01-07 | -27.5 | 45.5 | 0 | 2017-01-07 | -18.7 | 36.7 | 0 | 2016-01-07 | -8.1 | 26.1 | 0 | 29.77 | 0
2025-01-07 | -11.2 | 29.2 | 0 | 2024-01-07 | -8.3 | 26.3 | 0 | 2023-01-07 | -7.3 | 25.3 | 0 | 2022-01-07 | -11.7 | 29.7 | 0 | 2021-01-07 | -4 | 22 | 0 | 2020-01-07 | -6.6 | 24.6 | 0 | 2019-01-07 | -16.1 | 34.1 | 0 | 2018-01-07 | -27.3 | 45.3 | 0 | 2017-01-07 | -20.5 | 38.5 | 0 | 2016-01-07 | -8.4 | 26.4 | 0 | 30.14 | 0
2025-01-07 | -11 | 29 | 0 | 2024-01-07 | -7.9 | 25.9 | 0 | 2023-01-07 | -7.2 | 25.2 | 0 | 2022-01-07 | -11.9 | 29.9 | 0 | 2021-01-07 | -4.2 | 22.2 | 0 | 2020-01-07 | -6.8 | 24.8 | 0 | 2019-01-07 | -15.6 | 33.6 | 0 | 2018-01-07 | -24.1 | 42.1 | 0 | 2017-01-07 | -18.2 | 36.2 | 0 | 2016-01-07 | -7.3 | 25.3 | 0 | 29.42 | 0
2025-01-07 | -10.4 | 28.4 | 0 | 2024-01-07 | -7.6 | 25.6 | 0 | 2023-01-07 | -6.8 | 24.8 | 0 | 2022-01-07 | -12.4 | 30.4 | 0 | 2021-01-07 | -4.2 | 22.2 | 0 | 2020-01-07 | -5.1 | 23.1 | 0 | 2019-01-07 | -14.9 | 32.9 | 0 | 2018-01-07 | -21.9 | 39.9 | 0 | 2017-01-07 | -16.9 | 34.9 | 0 | 2016-01-07 | -5.9 | 23.9 | 0 | 28.61 | 0
2025-01-07 | -9.8 | 27.8 | 0 | 2024-01-07 | -7.2 | 25.2 | 0 | 2023-01-07 | -6.7 | 24.7 | 0 | 2022-01-07 | -10.9 | 28.9 | 0 | 2021-01-07 | -4.4 | 22.4 | 0 | 2020-01-07 | -4.7 | 22.7 | 0 | 2019-01-07 | -13.9 | 31.9 | 0 | 2018-01-07 | -20.7 | 38.7 | 0 | 2017-01-07 | -13.9 | 31.9 | 0 | 2016-01-07 | -5 | 23 | 0 | 27.72 | 0
2025-01-07 | -9 | 27 | 0 | 2024-01-07 | -6.7 | 24.7 | 0 | 2023-01-07 | -6.7 | 24.7 | 0 | 2022-01-07 | -11.2 | 29.2 | 0 | 2021-01-07 | -4.9 | 22.9 | 0 | 2020-01-07 | -3 | 21 | 0 | 2019-01-07 | -13 | 31 | 0 | 2018-01-07 | -18.9 | 36.9 | 0 | 2017-01-07 | -13.7 | 31.7 | 0 | 2016-01-07 | -3.4 | 21.4 | 0 | 27.05 | 0
2025-01-07 | -8.3 | 26.3 | 0 | 2024-01-07 | -6.4 | 24.4 | 0 | 2023-01-07 | -6.7 | 24.7 | 0 | 2022-01-07 | -10.6 | 28.6 | 0 | 2021-01-07 | -5.3 | 23.3 | 0 | 2020-01-07 | -1.4 | 19.4 | 0 | 2019-01-07 | -12.3 | 30.3 | 0 | 2018-01-07 | -16.4 | 34.4 | 0 | 2017-01-07 | -12.8 | 30.8 | 0 | 2016-01-07 | -2.7 | 20.7 | 0 | 26.29 | 0
2025-01-07 | -7.6 | 25.6 | 0 | 2024-01-07 | -5.9 | 23.9 | 0 | 2023-01-07 | -7 | 25 | 0 | 2022-01-07 | -10.9 | 28.9 | 0 | 2021-01-07 | -5.4 | 23.4 | 0 | 2020-01-07 | -0.7 | 18.7 | 0 | 2019-01-07 | -12.3 | 30.3 | 0 | 2018-01-07 | -14.7 | 32.7 | 0 | 2017-01-07 | -11.4 | 29.4 | 0 | 2016-01-07 | -1.2 | 19.2 | 0 | 25.71 | 0
2025-01-07 | -7 | 25 | 0 | 2024-01-07 | -5.8 | 23.8 | 0 | 2023-01-07 | -7 | 25 | 0 | 2022-01-07 | -11.6 | 29.6 | 0 | 2021-01-07 | -5.7 | 23.7 | 0 | 2020-01-07 | -0.7 | 18.7 | 0 | 2019-01-07 | -12 | 30 | 0 | 2018-01-07 | -13.7 | 31.7 | 0 | 2017-01-07 | -11.6 | 29.6 | 0 | 2016-01-07 | -0.1 | 18.1 | 0 | 25.52 | 0
2025-01-07 | -7 | 25 | 0 | 2024-01-07 | -5.7 | 23.7 | 0 | 2023-01-07 | -7.5 | 25.5 | 0 | 2022-01-07 | -12.4 | 30.4 | 0 | 2021-01-07 | -6 | 24 | 0 | 2020-01-07 | -1 | 19 | 0 | 2019-01-07 | -12.1 | 30.1 | 0 | 2018-01-07 | -13 | 31 | 0 | 2017-01-07 | -12.3 | 30.3 | 0 | 2016-01-07 | 0 | 18 | 0 | 25.7 | 0
2025-01-07 | -7.9 | 25.9 | 0 | 2024-01-07 | -5.6 | 23.6 | 0 | 2023-01-07 | -8 | 26 | 0 | 2022-01-07 | -14 | 32 | 0 | 2021-01-07 | -6.5 | 24.5 | 0 | 2020-01-07 | -1.9 | 19.9 | 0 | 2019-01-07 | -11.8 | 29.8 | 0 | 2018-01-07 | -12.5 | 30.5 | 0 | 2017-01-07 | -13.8 | 31.8 | 0 | 2016-01-07 | -1.9 | 19.9 | 0 | 26.39 | 0
2025-01-07 | -8.3 | 26.3 | 0 | 2024-01-07 | -5.2 | 23.2 | 0 | 2023-01-07 | -8.4 | 26.4 | 0 | 2022-01-07 | -14.5 | 32.5 | 0 | 2021-01-07 | -6.5 | 24.5 | 0 | 2020-01-07 | -1.5 | 19.5 | 0 | 2019-01-07 | -11.5 | 29.5 | 0 | 2018-01-07 | -12.3 | 30.3 | 0 | 2017-01-07 | -15.3 | 33.3 | 0 | 2016-01-07 | -3.7 | 21.7 | 0 | 26.72 | 0
2025-01-07 | -9.1 | 27.1 | 0 | 2024-01-07 | -5.4 | 23.4 | 0 | 2023-01-07 | -8.8 | 26.8 | 0 | 2022-01-07 | -14.8 | 32.8 | 0 | 2021-01-07 | -6.3 | 24.3 | 0 | 2020-01-07 | -1.2 | 19.2 | 0 | 2019-01-07 | -11.5 | 29.5 | 0 | 2018-01-07 | -11.8 | 29.8 | 0 | 2017-01-07 | -15.9 | 33.9 | 0 | 2016-01-07 | -3.5 | 21.5 | 0 | 26.83 | 0
2025-01-07 | -10.2 | 28.2 | 0 | 2024-01-07 | -5.5 | 23.5 | 0 | 2023-01-07 | -8.9 | 26.9 | 0 | 2022-01-07 | -15.2 | 33.2 | 0 | 2021-01-07 | -6.2 | 24.2 | 0 | 2020-01-07 | -0.8 | 18.8 | 0 | 2019-01-07 | -11.6 | 29.6 | 0 | 2018-01-07 | -11.2 | 29.2 | 0 | 2017-01-07 | -16.5 | 34.5 | 0 | 2016-01-07 | -4.3 | 22.3 | 0 | 27.04 | 0
2025-01-07 | -11.3 | 29.3 | 0 | 2024-01-07 | -5.7 | 23.7 | 0 | 2023-01-07 | -9 | 27 | 0 | 2022-01-07 | -15.9 | 33.9 | 0 | 2021-01-07 | -6.3 | 24.3 | 0 | 2020-01-07 | -2.2 | 20.2 | 0 | 2019-01-07 | -12.2 | 30.2 | 0 | 2018-01-07 | -10.5 | 28.5 | 0 | 2017-01-07 | -18.3 | 36.3 | 0 | 2016-01-07 | -5.7 | 23.7 | 0 | 27.71 | 0
2025-01-07 | -11.7 | 29.7 | 0 | 2024-01-07 | -5.9 | 23.9 | 0 | 2023-01-07 | -9.1 | 27.1 | 0 | 2022-01-07 | -16.7 | 34.7 | 0 | 2021-01-07 | -6.3 | 24.3 | 0 | 2020-01-07 | -3 | 21 | 0 | 2019-01-07 | -12.3 | 30.3 | 0 | 2018-01-07 | -10.1 | 28.1 | 0 | 2017-01-07 | -18.2 | 36.2 | 0 | 2016-01-07 | -5.2 | 23.2 | 0 | 27.85 | 0
2025-01-07 | -12.3 | 30.3 | 0 | 2024-01-07 | -5.9 | 23.9 | 0 | 2023-01-07 | -9.2 | 27.2 | 0 | 2022-01-07 | -17.2 | 35.2 | 0 | 2021-01-07 | -6.5 | 24.5 | 0 | 2020-01-07 | -2.6 | 20.6 | 0 | 2019-01-07 | -11.8 | 29.8 | 0 | 2018-01-07 | -9.6 | 27.6 | 0 | 2017-01-07 | -18.8 | 36.8 | 0 | 2016-01-07 | -5.3 | 23.3 | 0 | 27.92 | 0
2025-01-08 | -12.8 | 30.8 | 0 | 2024-01-08 | -5.8 | 23.8 | 0 | 2023-01-08 | -10.1 | 28.1 | 0 | 2022-01-08 | -17.9 | 35.9 | 0 | 2021-01-08 | -6.8 | 24.8 | 0 | 2020-01-08 | -2.9 | 20.9 | 0 | 2019-01-08 | -11.4 | 29.4 | 0 | 2018-01-08 | -10.1 | 28.1 | 0 | 2017-01-08 | -17.8 | 35.8 | 0 | 2016-01-08 | -6.1 | 24.1 | 0 | 28.17 | 0
2025-01-08 | -13.4 | 31.4 | 0 | 2024-01-08 | -6 | 24 | 0 | 2023-01-08 | -11.2 | 29.2 | 0 | 2022-01-08 | -18.5 | 36.5 | 0 | 2021-01-08 | -7.5 | 25.5 | 0 | 2020-01-08 | -2.1 | 20.1 | 0 | 2019-01-08 | -11.2 | 29.2 | 0 | 2018-01-08 | -9.3 | 27.3 | 0 | 2017-01-08 | -17.9 | 35.9 | 0 | 2016-01-08 | -8.2 | 26.2 | 0 | 28.53 | 0
2025-01-08 | -14.1 | 32.1 | 0 | 2024-01-08 | -5.9 | 23.9 | 0 | 2023-01-08 | -10.7 | 28.7 | 0 | 2022-01-08 | -19.1 | 37.1 | 0 | 2021-01-08 | -8.6 | 26.6 | 0 | 2020-01-08 | -1.3 | 19.3 | 0 | 2019-01-08 | -10.6 | 28.6 | 0 | 2018-01-08 | -8.6 | 26.6 | 0 | 2017-01-08 | -17.8 | 35.8 | 0 | 2016-01-08 | -8.8 | 26.8 | 0 | 28.55 | 0
2025-01-08 | -14.6 | 32.6 | 0 | 2024-01-08 | -5.6 | 23.6 | 0 | 2023-01-08 | -10.7 | 28.7 | 0 | 2022-01-08 | -19.4 | 37.4 | 0 | 2021-01-08 | -9.1 | 27.1 | 0 | 2020-01-08 | -1.5 | 19.5 | 0 | 2019-01-08 | -9.8 | 27.8 | 0 | 2018-01-08 | -7.5 | 25.5 | 0 | 2017-01-08 | -18.2 | 36.2 | 0 | 2016-01-08 | -6.5 | 24.5 | 0 | 28.29 | 0
2025-01-08 | -15.3 | 33.3 | 0 | 2024-01-08 | -6 | 24 | 0 | 2023-01-08 | -11.5 | 29.5 | 0 | 2022-01-08 | -20.1 | 38.1 | 0 | 2021-01-08 | -9.4 | 27.4 | 0 | 2020-01-08 | -1.5 | 19.5 | 0 | 2019-01-08 | -9.1 | 27.1 | 0 | 2018-01-08 | -7.2 | 25.2 | 0 | 2017-01-08 | -17.6 | 35.6 | 0 | 2016-01-08 | -7.3 | 25.3 | 0 | 28.5 | 0
2025-01-08 | -15.9 | 33.9 | 0 | 2024-01-08 | -5.8 | 23.8 | 0 | 2023-01-08 | -12.4 | 30.4 | 0 | 2022-01-08 | -21.3 | 39.3 | 0 | 2021-01-08 | -9.9 | 27.9 | 0 | 2020-01-08 | -2.2 | 20.2 | 0 | 2019-01-08 | -8.4 | 26.4 | 0 | 2018-01-08 | -6.7 | 24.7 | 0 | 2017-01-08 | -17.3 | 35.3 | 0 | 2016-01-08 | -6.9 | 24.9 | 0 | 28.68 | 0
2025-01-08 | -15.9 | 33.9 | 0 | 2024-01-08 | -6.2 | 24.2 | 0 | 2023-01-08 | -12.4 | 30.4 | 0 | 2022-01-08 | -21.2 | 39.2 | 0 | 2021-01-08 | -11 | 29 | 0 | 2020-01-08 | -2.5 | 20.5 | 0 | 2019-01-08 | -7.1 | 25.1 | 0 | 2018-01-08 | -6.1 | 24.1 | 0 | 2017-01-08 | -17 | 35 | 0 | 2016-01-08 | -8.6 | 26.6 | 0 | 28.8 | 0
2025-01-08 | -16 | 34 | 0 | 2024-01-08 | -5.9 | 23.9 | 0 | 2023-01-08 | -10.9 | 28.9 | 0 | 2022-01-08 | -21.8 | 39.8 | 0 | 2021-01-08 | -11.9 | 29.9 | 0 | 2020-01-08 | -2.5 | 20.5 | 0 | 2019-01-08 | -4.6 | 22.6 | 0 | 2018-01-08 | -8.6 | 26.6 | 0 | 2017-01-08 | -16.2 | 34.2 | 0 | 2016-01-08 | -8.3 | 26.3 | 0 | 28.67 | 0
2025-01-08 | -16.1 | 34.1 | 0 | 2024-01-08 | -6.2 | 24.2 | 0 | 2023-01-08 | -10.6 | 28.6 | 0 | 2022-01-08 | -22.4 | 40.4 | 0 | 2021-01-08 | -12.2 | 30.2 | 0 | 2020-01-08 | -2.1 | 20.1 | 0 | 2019-01-08 | -4.4 | 22.4 | 0 | 2018-01-08 | -8.8 | 26.8 | 0 | 2017-01-08 | -15.3 | 33.3 | 0 | 2016-01-08 | -7.5 | 25.5 | 0 | 28.56 | 0
2025-01-08 | -15.9 | 33.9 | 0 | 2024-01-08 | -5.7 | 23.7 | 0 | 2023-01-08 | -10 | 28 | 0 | 2022-01-08 | -21 | 39 | 0 | 2021-01-08 | -11.1 | 29.1 | 0 | 2020-01-08 | -2.2 | 20.2 | 0 | 2019-01-08 | -3.8 | 21.8 | 0 | 2018-01-08 | -7.8 | 25.8 | 0 | 2017-01-08 | -14.6 | 32.6 | 0 | 2016-01-08 | -6.8 | 24.8 | 0 | 27.89 | 0
2025-01-08 | -15.6 | 33.6 | 0 | 2024-01-08 | -4.9 | 22.9 | 0 | 2023-01-08 | -9.6 | 27.6 | 0 | 2022-01-08 | -19.2 | 37.2 | 0 | 2021-01-08 | -10.5 | 28.5 | 0 | 2020-01-08 | -2.5 | 20.5 | 0 | 2019-01-08 | -3.5 | 21.5 | 0 | 2018-01-08 | -4.2 | 22.2 | 0 | 2017-01-08 | -14.2 | 32.2 | 0 | 2016-01-08 | -5.7 | 23.7 | 0 | 26.99 | 0
2025-01-08 | -15.2 | 33.2 | 0 | 2024-01-08 | -3.7 | 21.7 | 0 | 2023-01-08 | -9 | 27 | 0 | 2022-01-08 | -17.8 | 35.8 | 0 | 2021-01-08 | -9.3 | 27.3 | 0 | 2020-01-08 | -2.6 | 20.6 | 0 | 2019-01-08 | -2.9 | 20.9 | 0 | 2018-01-08 | -3.6 | 21.6 | 0 | 2017-01-08 | -13.5 | 31.5 | 0 | 2016-01-08 | -4.6 | 22.6 | 0 | 26.22 | 0
2025-01-08 | -14.7 | 32.7 | 0 | 2024-01-08 | -3 | 21 | 0 | 2023-01-08 | -8.2 | 26.2 | 0 | 2022-01-08 | -15.8 | 33.8 | 0 | 2021-01-08 | -8.1 | 26.1 | 0 | 2020-01-08 | -2.7 | 20.7 | 0 | 2019-01-08 | -1.8 | 19.8 | 0 | 2018-01-08 | -1.9 | 19.9 | 0 | 2017-01-08 | -12.9 | 30.9 | 0 | 2016-01-08 | -3.3 | 21.3 | 0 | 25.24 | 0
2025-01-08 | -14.3 | 32.3 | 0 | 2024-01-08 | -2.3 | 20.3 | 0 | 2023-01-08 | -6.7 | 24.7 | 0 | 2022-01-08 | -13.9 | 31.9 | 0 | 2021-01-08 | -7.3 | 25.3 | 0 | 2020-01-08 | -3 | 21 | 0 | 2019-01-08 | 1.1 | 16.9 | 0 | 2018-01-08 | -1.7 | 19.7 | 0 | 2017-01-08 | -12.6 | 30.6 | 0 | 2016-01-08 | -2.4 | 20.4 | 0 | 24.31 | 0
2025-01-08 | -13.2 | 31.2 | 0 | 2024-01-08 | -2 | 20 | 0 | 2023-01-08 | -5.8 | 23.8 | 0 | 2022-01-08 | -13.6 | 31.6 | 0 | 2021-01-08 | -6.5 | 24.5 | 0 | 2020-01-08 | -3.8 | 21.8 | 0 | 2019-01-08 | 0.5 | 17.5 | 0 | 2018-01-08 | -1.2 | 19.2 | 0 | 2017-01-08 | -13.4 | 31.4 | 0 | 2016-01-08 | -2.1 | 20.1 | 0 | 24.11 | 0
2025-01-08 | -12.7 | 30.7 | 0 | 2024-01-08 | -2.1 | 20.1 | 0 | 2023-01-08 | -5.1 | 23.1 | 0 | 2022-01-08 | -13.4 | 31.4 | 0 | 2021-01-08 | -6.2 | 24.2 | 0 | 2020-01-08 | -5.4 | 23.4 | 0 | 2019-01-08 | 0.1 | 17.9 | 0 | 2018-01-08 | -0.9 | 18.9 | 0 | 2017-01-08 | -13.5 | 31.5 | 0 | 2016-01-08 | -2 | 20 | 0 | 24.12 | 0
2025-01-08 | -12.3 | 30.3 | 0 | 2024-01-08 | -2.4 | 20.4 | 0 | 2023-01-08 | -5.2 | 23.2 | 0 | 2022-01-08 | -14.3 | 32.3 | 0 | 2021-01-08 | -6.4 | 24.4 | 0 | 2020-01-08 | -7.5 | 25.5 | 0 | 2019-01-08 | 0.1 | 17.9 | 0 | 2018-01-08 | -0.4 | 18.4 | 0 | 2017-01-08 | -13.6 | 31.6 | 0 | 2016-01-08 | -2.3 | 20.3 | 0 | 24.43 | 0
2025-01-08 | -12 | 30 | 0 | 2024-01-08 | -2.4 | 20.4 | 0 | 2023-01-08 | -5.7 | 23.7 | 0 | 2022-01-08 | -14.1 | 32.1 | 0 | 2021-01-08 | -7.8 | 25.8 | 0 | 2020-01-08 | -9.1 | 27.1 | 0 | 2019-01-08 | -0.4 | 18.4 | 0 | 2018-01-08 | 0.1 | 17.9 | 0 | 2017-01-08 | -14.5 | 32.5 | 0 | 2016-01-08 | -3 | 21 | 0 | 24.89 | 0
2025-01-08 | -11.5 | 29.5 | 0 | 2024-01-08 | -2.5 | 20.5 | 0 | 2023-01-08 | -5.8 | 23.8 | 0 | 2022-01-08 | -14.1 | 32.1 | 0 | 2021-01-08 | -9.1 | 27.1 | 0 | 2020-01-08 | -10 | 28 | 0 | 2019-01-08 | -0.3 | 18.3 | 0 | 2018-01-08 | 0.4 | 17.6 | 0 | 2017-01-08 | -15.4 | 33.4 | 0 | 2016-01-08 | -3.7 | 21.7 | 0 | 25.2 | 0
2025-01-08 | -11.4 | 29.4 | 0 | 2024-01-08 | -3.1 | 21.1 | 0 | 2023-01-08 | -6.3 | 24.3 | 0 | 2022-01-08 | -14 | 32 | 0 | 2021-01-08 | -8.7 | 26.7 | 0 | 2020-01-08 | -11.4 | 29.4 | 0 | 2019-01-08 | -0.3 | 18.3 | 0 | 2018-01-08 | 0.7 | 17.3 | 0 | 2017-01-08 | -16.3 | 34.3 | 0 | 2016-01-08 | -3.5 | 21.5 | 0 | 25.43 | 0
2025-01-08 | -11.4 | 29.4 | 0 | 2024-01-08 | -3 | 21 | 0 | 2023-01-08 | -6.2 | 24.2 | 0 | 2022-01-08 | -14.5 | 32.5 | 0 | 2021-01-08 | -8.9 | 26.9 | 0 | 2020-01-08 | -12.1 | 30.1 | 0 | 2019-01-08 | -0.3 | 18.3 | 0 | 2018-01-08 | 1 | 17 | 0 | 2017-01-08 | -17.4 | 35.4 | 0 | 2016-01-08 | -3.5 | 21.5 | 0 | 25.63 | 0
2025-01-08 | -11.7 | 29.7 | 0 | 2024-01-08 | -3.5 | 21.5 | 0 | 2023-01-08 | -6 | 24 | 0 | 2022-01-08 | -14.3 | 32.3 | 0 | 2021-01-08 | -8.7 | 26.7 | 0 | 2020-01-08 | -12.9 | 30.9 | 0 | 2019-01-08 | -0.4 | 18.4 | 0 | 2018-01-08 | 0.1 | 17.9 | 0 | 2017-01-08 | -18.1 | 36.1 | 0 | 2016-01-08 | -3.6 | 21.6 | 0 | 25.91 | 0
2025-01-08 | -12.1 | 30.1 | 0 | 2024-01-08 | -3.3 | 21.3 | 0 | 2023-01-08 | -5.9 | 23.9 | 0 | 2022-01-08 | -13.8 | 31.8 | 0 | 2021-01-08 | -7.2 | 25.2 | 0 | 2020-01-08 | -13.5 | 31.5 | 0 | 2019-01-08 | -0.5 | 18.5 | 0 | 2018-01-08 | -0.2 | 18.2 | 0 | 2017-01-08 | -19.6 | 37.6 | 0 | 2016-01-08 | -3.7 | 21.7 | 0 | 25.98 | 0
2025-01-08 | -12.5 | 30.5 | 0 | 2024-01-08 | -3.2 | 21.2 | 0 | 2023-01-08 | -5.5 | 23.5 | 0 | 2022-01-08 | -13.4 | 31.4 | 0 | 2021-01-08 | -7.6 | 25.6 | 0 | 2020-01-08 | -14.1 | 32.1 | 0 | 2019-01-08 | -0.3 | 18.3 | 0 | 2018-01-08 | -0.5 | 18.5 | 0 | 2017-01-08 | -19.8 | 37.8 | 0 | 2016-01-08 | -3 | 21 | 0 | 25.99 | 0
2025-01-09 | -13.1 | 31.1 | 0 | 2024-01-09 | -3.4 | 21.4 | 0 | 2023-01-09 | -4.8 | 22.8 | 0 | 2022-01-09 | -12.8 | 30.8 | 0 | 2021-01-09 | -9 | 27 | 0 | 2020-01-09 | -14.7 | 32.7 | 0 | 2019-01-09 | -0.3 | 18.3 | 0 | 2018-01-09 | -0.3 | 18.3 | 0 | 2017-01-09 | -20.6 | 38.6 | 0 | 2016-01-09 | -2.5 | 20.5 | 0 | 26.15 | 0
2025-01-09 | -13.6 | 31.6 | 0 | 2024-01-09 | -3.5 | 21.5 | 0 | 2023-01-09 | -5 | 23 | 0 | 2022-01-09 | -11.9 | 29.9 | 0 | 2021-01-09 | -8.2 | 26.2 | 0 | 2020-01-09 | -15.1 | 33.1 | 0 | 2019-01-09 | -0.2 | 18.2 | 0 | 2018-01-09 | 0 | 18 | 0 | 2017-01-09 | -21.1 | 39.1 | 0 | 2016-01-09 | -2.1 | 20.1 | 0 | 26.07 | 0
2025-01-09 | -13.6 | 31.6 | 0 | 2024-01-09 | -3.8 | 21.8 | 0 | 2023-01-09 | -5 | 23 | 0 | 2022-01-09 | -11.5 | 29.5 | 0 | 2021-01-09 | -8.1 | 26.1 | 0 | 2020-01-09 | -15.5 | 33.5 | 0 | 2019-01-09 | -0.3 | 18.3 | 0 | 2018-01-09 | -0.3 | 18.3 | 0 | 2017-01-09 | -21 | 39 | 0 | 2016-01-09 | -1.8 | 19.8 | 0 | 26.09 | 0
2025-01-09 | -13.5 | 31.5 | 0 | 2024-01-09 | -4 | 22 | 0 | 2023-01-09 | -4.8 | 22.8 | 0 | 2022-01-09 | -10.6 | 28.6 | 0 | 2021-01-09 | -8.5 | 26.5 | 0 | 2020-01-09 | -16.1 | 34.1 | 0 | 2019-01-09 | 0 | 18 | 0 | 2018-01-09 | -0.3 | 18.3 | 0 | 2017-01-09 | -22.4 | 40.4 | 0 | 2016-01-09 | -1.8 | 19.8 | 0 | 26.2 | 0
2025-01-09 | -13.6 | 31.6 | 0 | 2024-01-09 | -4.4 | 22.4 | 0 | 2023-01-09 | -4.8 | 22.8 | 0 | 2022-01-09 | -9.8 | 27.8 | 0 | 2021-01-09 | -8.3 | 26.3 | 0 | 2020-01-09 | -16.4 | 34.4 | 0 | 2019-01-09 | 0.2 | 17.8 | 0 | 2018-01-09 | -0.6 | 18.6 | 0 | 2017-01-09 | -24.1 | 42.1 | 0 | 2016-01-09 | -1.2 | 19.2 | 0 | 26.3 | 0
2025-01-09 | -13.8 | 31.8 | 0 | 2024-01-09 | -4.7 | 22.7 | 0 | 2023-01-09 | -4.9 | 22.9 | 0 | 2022-01-09 | -8.9 | 26.9 | 0 | 2021-01-09 | -7.9 | 25.9 | 0 | 2020-01-09 | -16.9 | 34.9 | 0 | 2019-01-09 | -0.1 | 18.1 | 0 | 2018-01-09 | -0.4 | 18.4 | 0 | 2017-01-09 | -23.8 | 41.8 | 0 | 2016-01-09 | -0.5 | 18.5 | 0 | 26.19 | 0
2025-01-09 | -14.4 | 32.4 | 0 | 2024-01-09 | -4.9 | 22.9 | 0 | 2023-01-09 | -4.7 | 22.7 | 0 | 2022-01-09 | -7.8 | 25.8 | 0 | 2021-01-09 | -7.2 | 25.2 | 0 | 2020-01-09 | -17.7 | 35.7 | 0 | 2019-01-09 | 0.2 | 17.8 | 0 | 2018-01-09 | -0.8 | 18.8 | 0 | 2017-01-09 | -21.1 | 39.1 | 0 | 2016-01-09 | -0.2 | 18.2 | 0 | 25.86 | 0
2025-01-09 | -14.6 | 32.6 | 0 | 2024-01-09 | -5.1 | 23.1 | 0 | 2023-01-09 | -4.4 | 22.4 | 0 | 2022-01-09 | -7 | 25 | 0 | 2021-01-09 | -6.9 | 24.9 | 0 | 2020-01-09 | -18.3 | 36.3 | 0 | 2019-01-09 | 0.1 | 17.9 | 0 | 2018-01-09 | -1.1 | 19.1 | 0 | 2017-01-09 | -20.4 | 38.4 | 0 | 2016-01-09 | 0.3 | 17.7 | 0 | 25.74 | 0
2025-01-09 | -14.3 | 32.3 | 0 | 2024-01-09 | -5.1 | 23.1 | 0 | 2023-01-09 | -4 | 22 | 0 | 2022-01-09 | -6.5 | 24.5 | 0 | 2021-01-09 | -7.3 | 25.3 | 0 | 2020-01-09 | -18.2 | 36.2 | 0 | 2019-01-09 | 0.1 | 17.9 | 0 | 2018-01-09 | -1.5 | 19.5 | 0 | 2017-01-09 | -18.7 | 36.7 | 0 | 2016-01-09 | 0.3 | 17.7 | 0 | 25.52 | 0
2025-01-09 | -14.1 | 32.1 | 0 | 2024-01-09 | -5 | 23 | 0 | 2023-01-09 | -3.5 | 21.5 | 0 | 2022-01-09 | -2.3 | 20.3 | 0 | 2021-01-09 | -8 | 26 | 0 | 2020-01-09 | -17.5 | 35.5 | 0 | 2019-01-09 | 0.2 | 17.8 | 0 | 2018-01-09 | -1.7 | 19.7 | 0 | 2017-01-09 | -17.3 | 35.3 | 0 | 2016-01-09 | 1.2 | 16.8 | 0 | 24.8 | 0
2025-01-09 | -12.8 | 30.8 | 0 | 2024-01-09 | -5 | 23 | 0 | 2023-01-09 | -2.8 | 20.8 | 0 | 2022-01-09 | -1.6 | 19.6 | 0 | 2021-01-09 | -7.3 | 25.3 | 0 | 2020-01-09 | -16 | 34 | 0 | 2019-01-09 | 0.4 | 17.6 | 0 | 2018-01-09 | -2.1 | 20.1 | 0 | 2017-01-09 | -16.1 | 34.1 | 0 | 2016-01-09 | 1 | 17 | 0 | 24.23 | 0
2025-01-09 | -11.9 | 29.9 | 0 | 2024-01-09 | -5.4 | 23.4 | 0 | 2023-01-09 | -2.2 | 20.2 | 0 | 2022-01-09 | -0.4 | 18.4 | 0 | 2021-01-09 | -6.7 | 24.7 | 0 | 2020-01-09 | -15.5 | 33.5 | 0 | 2019-01-09 | 0.6 | 17.4 | 0 | 2018-01-09 | -2.4 | 20.4 | 0 | 2017-01-09 | -14 | 32 | 0 | 2016-01-09 | 1.6 | 16.4 | 0 | 23.63 | 0
2025-01-09 | -10.7 | 28.7 | 0 | 2024-01-09 | -5.7 | 23.7 | 0 | 2023-01-09 | -1.9 | 19.9 | 0 | 2022-01-09 | 0.5 | 17.5 | 0 | 2021-01-09 | -5.5 | 23.5 | 0 | 2020-01-09 | -14.2 | 32.2 | 0 | 2019-01-09 | 1 | 17 | 0 | 2018-01-09 | -2.9 | 20.9 | 0 | 2017-01-09 | -12.2 | 30.2 | 0 | 2016-01-09 | 1.8 | 16.2 | 0 | 22.98 | 0
2025-01-09 | -9 | 27 | 0 | 2024-01-09 | -6.1 | 24.1 | 0 | 2023-01-09 | -1.7 | 19.7 | 0 | 2022-01-09 | 1.2 | 16.8 | 0 | 2021-01-09 | -4.2 | 22.2 | 0 | 2020-01-09 | -13.8 | 31.8 | 0 | 2019-01-09 | 1.2 | 16.8 | 0 | 2018-01-09 | -2.3 | 20.3 | 0 | 2017-01-09 | -10.7 | 28.7 | 0 | 2016-01-09 | 3.3 | 14.7 | 0 | 22.21 | 0
2025-01-09 | -7.5 | 25.5 | 0 | 2024-01-09 | -6.4 | 24.4 | 0 | 2023-01-09 | -1.3 | 19.3 | 0 | 2022-01-09 | 1.6 | 16.4 | 0 | 2021-01-09 | -2.2 | 20.2 | 0 | 2020-01-09 | -13 | 31 | 0 | 2019-01-09 | 0.7 | 17.3 | 0 | 2018-01-09 | -2 | 20 | 0 | 2017-01-09 | -7.9 | 25.9 | 0 | 2016-01-09 | 3.5 | 14.5 | 0 | 21.45 | 0
2025-01-09 | -6.9 | 24.9 | 0 | 2024-01-09 | -6.5 | 24.5 | 0 | 2023-01-09 | -1.2 | 19.2 | 0 | 2022-01-09 | 2.4 | 15.6 | 0 | 2021-01-09 | -1.7 | 19.7 | 0 | 2020-01-09 | -12.6 | 30.6 | 0 | 2019-01-09 | 0.2 | 17.8 | 0 | 2018-01-09 | -1.9 | 19.9 | 0 | 2017-01-09 | -6.4 | 24.4 | 0 | 2016-01-09 | 3.5 | 14.5 | 0 | 21.11 | 0
2025-01-09 | -6.7 | 24.7 | 0 | 2024-01-09 | -6.4 | 24.4 | 0 | 2023-01-09 | -1.3 | 19.3 | 0 | 2022-01-09 | 1.2 | 16.8 | 0 | 2021-01-09 | -3.1 | 21.1 | 0 | 2020-01-09 | -13.1 | 31.1 | 0 | 2019-01-09 | -0.4 | 18.4 | 0 | 2018-01-09 | -2.1 | 20.1 | 0 | 2017-01-09 | -6.7 | 24.7 | 0 | 2016-01-09 | 3.6 | 14.4 | 0 | 21.5 | 0
2025-01-09 | -7.1 | 25.1 | 0 | 2024-01-09 | -6.3 | 24.3 | 0 | 2023-01-09 | -1.3 | 19.3 | 0 | 2022-01-09 | 0.8 | 17.2 | 0 | 2021-01-09 | -4.3 | 22.3 | 0 | 2020-01-09 | -13.1 | 31.1 | 0 | 2019-01-09 | -0.7 | 18.7 | 0 | 2018-01-09 | -3.8 | 21.8 | 0 | 2017-01-09 | -7.1 | 25.1 | 0 | 2016-01-09 | 3.7 | 14.3 | 0 | 21.92 | 0
2025-01-09 | -7.3 | 25.3 | 0 | 2024-01-09 | -6 | 24 | 0 | 2023-01-09 | -1 | 19 | 0 | 2022-01-09 | 0.1 | 17.9 | 0 | 2021-01-09 | -5 | 23 | 0 | 2020-01-09 | -13 | 31 | 0 | 2019-01-09 | -1.2 | 19.2 | 0 | 2018-01-09 | -4.7 | 22.7 | 0 | 2017-01-09 | -7.5 | 25.5 | 0 | 2016-01-09 | 3.8 | 14.2 | 0 | 22.18 | 0
2025-01-09 | -7.7 | 25.7 | 0 | 2024-01-09 | -5.3 | 23.3 | 0 | 2023-01-09 | -0.8 | 18.8 | 0 | 2022-01-09 | -0.9 | 18.9 | 0 | 2021-01-09 | -5.3 | 23.3 | 0 | 2020-01-09 | -12.6 | 30.6 | 0 | 2019-01-09 | -1.4 | 19.4 | 0 | 2018-01-09 | -8.1 | 26.1 | 0 | 2017-01-09 | -7.5 | 25.5 | 0 | 2016-01-09 | 3.6 | 14.4 | 0 | 22.6 | 0
2025-01-09 | -8.8 | 26.8 | 0 | 2024-01-09 | -4.9 | 22.9 | 0 | 2023-01-09 | -0.5 | 18.5 | 0 | 2022-01-09 | -2.8 | 20.8 | 0 | 2021-01-09 | -6.2 | 24.2 | 0 | 2020-01-09 | -12.7 | 30.7 | 0 | 2019-01-09 | -1.7 | 19.7 | 0 | 2018-01-09 | -7 | 25 | 0 | 2017-01-09 | -7.1 | 25.1 | 0 | 2016-01-09 | 3.5 | 14.5 | 0 | 22.82 | 0
2025-01-09 | -9.1 | 27.1 | 0 | 2024-01-09 | -3.2 | 21.2 | 0 | 2023-01-09 | -0.4 | 18.4 | 0 | 2022-01-09 | -4.3 | 22.3 | 0 | 2021-01-09 | -7.3 | 25.3 | 0 | 2020-01-09 | -12.3 | 30.3 | 0 | 2019-01-09 | -1.7 | 19.7 | 0 | 2018-01-09 | -10.9 | 28.9 | 0 | 2017-01-09 | -7 | 25 | 0 | 2016-01-09 | 3.1 | 14.9 | 0 | 23.31 | 0
2025-01-09 | -9.8 | 27.8 | 0 | 2024-01-09 | -2 | 20 | 0 | 2023-01-09 | -2.1 | 20.1 | 0 | 2022-01-09 | -5.8 | 23.8 | 0 | 2021-01-09 | -8.7 | 26.7 | 0 | 2020-01-09 | -11.6 | 29.6 | 0 | 2019-01-09 | -2.4 | 20.4 | 0 | 2018-01-09 | -8.7 | 26.7 | 0 | 2017-01-09 | -7.7 | 25.7 | 0 | 2016-01-09 | 3.2 | 14.8 | 0 | 23.56 | 0
2025-01-09 | -10.2 | 28.2 | 0 | 2024-01-09 | -1.5 | 19.5 | 0 | 2023-01-09 | -2.9 | 20.9 | 0 | 2022-01-09 | -6.8 | 24.8 | 0 | 2021-01-09 | -9.3 | 27.3 | 0 | 2020-01-09 | -11.2 | 29.2 | 0 | 2019-01-09 | -3 | 21 | 0 | 2018-01-09 | -11.6 | 29.6 | 0 | 2017-01-09 | -7.2 | 25.2 | 0 | 2016-01-09 | 3.1 | 14.9 | 0 | 24.06 | 0
2025-01-10 | -10.6 | 28.6 | 0 | 2024-01-10 | 0 | 18 | 0 | 2023-01-10 | -3.6 | 21.6 | 0 | 2022-01-10 | -8.3 | 26.3 | 0 | 2021-01-10 | -9.2 | 27.2 | 0 | 2020-01-10 | -10.9 | 28.9 | 0 | 2019-01-10 | -3.4 | 21.4 | 0 | 2018-01-10 | -11 | 29 | 0 | 2017-01-10 | -6.6 | 24.6 | 0 | 2016-01-10 | 2.6 | 15.4 | 0 | 24.1 | 0
2025-01-10 | -11.3 | 29.3 | 0 | 2024-01-10 | 0.4 | 17.6 | 0 | 2023-01-10 | -5.1 | 23.1 | 0 | 2022-01-10 | -9.6 | 27.6 | 0 | 2021-01-10 | -8.4 | 26.4 | 0 | 2020-01-10 | -10.2 | 28.2 | 0 | 2019-01-10 | -3.2 | 21.2 | 0 | 2018-01-10 | -13.8 | 31.8 | 0 | 2017-01-10 | -6 | 24 | 0 | 2016-01-10 | 2.6 | 15.4 | 0 | 24.46 | 0
2025-01-10 | -11.8 | 29.8 | 0 | 2024-01-10 | 0.9 | 17.1 | 0 | 2023-01-10 | -6.3 | 24.3 | 0 | 2022-01-10 | -10.8 | 28.8 | 0 | 2021-01-10 | -10.1 | 28.1 | 0 | 2020-01-10 | -9.6 | 27.6 | 0 | 2019-01-10 | -4 | 22 | 0 | 2018-01-10 | -14.2 | 32.2 | 0 | 2017-01-10 | -6 | 24 | 0 | 2016-01-10 | 2.6 | 15.4 | 0 | 24.93 | 0
2025-01-10 | -12.3 | 30.3 | 0 | 2024-01-10 | 1.3 | 16.7 | 0 | 2023-01-10 | -6.6 | 24.6 | 0 | 2022-01-10 | -11.9 | 29.9 | 0 | 2021-01-10 | -10.1 | 28.1 | 0 | 2020-01-10 | -9 | 27 | 0 | 2019-01-10 | -5 | 23 | 0 | 2018-01-10 | -15.2 | 33.2 | 0 | 2017-01-10 | -6.4 | 24.4 | 0 | 2016-01-10 | 2.7 | 15.3 | 0 | 25.25 | 0
2025-01-10 | -12.5 | 30.5 | 0 | 2024-01-10 | 1.4 | 16.6 | 0 | 2023-01-10 | -8 | 26 | 0 | 2022-01-10 | -13.9 | 31.9 | 0 | 2021-01-10 | -9.1 | 27.1 | 0 | 2020-01-10 | -8.2 | 26.2 | 0 | 2019-01-10 | -5.8 | 23.8 | 0 | 2018-01-10 | -13.5 | 31.5 | 0 | 2017-01-10 | -6.5 | 24.5 | 0 | 2016-01-10 | 2.8 | 15.2 | 0 | 25.33 | 0
2025-01-10 | -12.8 | 30.8 | 0 | 2024-01-10 | 1.6 | 16.4 | 0 | 2023-01-10 | -8.2 | 26.2 | 0 | 2022-01-10 | -14.1 | 32.1 | 0 | 2021-01-10 | -10.7 | 28.7 | 0 | 2020-01-10 | -7.7 | 25.7 | 0 | 2019-01-10 | -6.6 | 24.6 | 0 | 2018-01-10 | -13.8 | 31.8 | 0 | 2017-01-10 | -6.4 | 24.4 | 0 | 2016-01-10 | 2.5 | 15.5 | 0 | 25.62 | 0
2025-01-10 | -12.9 | 30.9 | 0 | 2024-01-10 | 1.4 | 16.6 | 0 | 2023-01-10 | -9.3 | 27.3 | 0 | 2022-01-10 | -13.1 | 31.1 | 0 | 2021-01-10 | -10.1 | 28.1 | 0 | 2020-01-10 | -7.3 | 25.3 | 0 | 2019-01-10 | -7.3 | 25.3 | 0 | 2018-01-10 | -15.3 | 33.3 | 0 | 2017-01-10 | -6.8 | 24.8 | 0 | 2016-01-10 | 2.2 | 15.8 | 0 | 25.85 | 0
2025-01-10 | -13.5 | 31.5 | 0 | 2024-01-10 | 1.6 | 16.4 | 0 | 2023-01-10 | -9.1 | 27.1 | 0 | 2022-01-10 | -12.7 | 30.7 | 0 | 2021-01-10 | -10.4 | 28.4 | 0 | 2020-01-10 | -6.7 | 24.7 | 0 | 2019-01-10 | -8 | 26 | 0 | 2018-01-10 | -15.1 | 33.1 | 0 | 2017-01-10 | -6.9 | 24.9 | 0 | 2016-01-10 | 1.8 | 16.2 | 0 | 25.9 | 0
2025-01-10 | -13.2 | 31.2 | 0 | 2024-01-10 | 2.1 | 15.9 | 0 | 2023-01-10 | -9.1 | 27.1 | 0 | 2022-01-10 | -13.4 | 31.4 | 0 | 2021-01-10 | -10.3 | 28.3 | 0 | 2020-01-10 | -5.7 | 23.7 | 0 | 2019-01-10 | -8.3 | 26.3 | 0 | 2018-01-10 | -12.9 | 30.9 | 0 | 2017-01-10 | -7.2 | 25.2 | 0 | 2016-01-10 | 2 | 16 | 0 | 25.6 | 0
2025-01-10 | -12.5 | 30.5 | 0 | 2024-01-10 | 2.7 | 15.3 | 0 | 2023-01-10 | -8.9 | 26.9 | 0 | 2022-01-10 | -12.5 | 30.5 | 0 | 2021-01-10 | -10.5 | 28.5 | 0 | 2020-01-10 | 0.5 | 17.5 | 0 | 2019-01-10 | -8.9 | 26.9 | 0 | 2018-01-10 | -11.6 | 29.6 | 0 | 2017-01-10 | -6.9 | 24.9 | 0 | 2016-01-10 | 2 | 16 | 0 | 24.66 | 0
2025-01-10 | -11.6 | 29.6 | 0 | 2024-01-10 | 4.2 | 13.8 | 0 | 2023-01-10 | -8.8 | 26.8 | 0 | 2022-01-10 | -12.5 | 30.5 | 0 | 2021-01-10 | -9.1 | 27.1 | 0 | 2020-01-10 | 2.5 | 15.5 | 0 | 2019-01-10 | -9.1 | 27.1 | 0 | 2018-01-10 | -11.4 | 29.4 | 0 | 2017-01-10 | -6.4 | 24.4 | 0 | 2016-01-10 | 2.1 | 15.9 | 0 | 24.01 | 0
2025-01-10 | -10.2 | 28.2 | 0 | 2024-01-10 | 4.1 | 13.9 | 0 | 2023-01-10 | -8.5 | 26.5 | 0 | 2022-01-10 | -12.3 | 30.3 | 0 | 2021-01-10 | -8.7 | 26.7 | 0 | 2020-01-10 | 2.4 | 15.6 | 0 | 2019-01-10 | -9 | 27 | 0 | 2018-01-10 | -10.2 | 28.2 | 0 | 2017-01-10 | -5.5 | 23.5 | 0 | 2016-01-10 | 2.4 | 15.6 | 0 | 23.55 | 0
2025-01-10 | -8.8 | 26.8 | 0 | 2024-01-10 | 4.8 | 13.2 | 0 | 2023-01-10 | -8.2 | 26.2 | 0 | 2022-01-10 | -12.1 | 30.1 | 0 | 2021-01-10 | -8.7 | 26.7 | 0 | 2020-01-10 | 2.7 | 15.3 | 0 | 2019-01-10 | -9.2 | 27.2 | 0 | 2018-01-10 | -9.1 | 27.1 | 0 | 2017-01-10 | -4.6 | 22.6 | 0 | 2016-01-10 | 2.8 | 15.2 | 0 | 23.04 | 0
2025-01-10 | -7.9 | 25.9 | 0 | 2024-01-10 | 4.5 | 13.5 | 0 | 2023-01-10 | -8.1 | 26.1 | 0 | 2022-01-10 | -12.3 | 30.3 | 0 | 2021-01-10 | -8.7 | 26.7 | 0 | 2020-01-10 | 3.2 | 14.8 | 0 | 2019-01-10 | -9.2 | 27.2 | 0 | 2018-01-10 | -5.6 | 23.6 | 0 | 2017-01-10 | -4.2 | 22.2 | 0 | 2016-01-10 | 3.1 | 14.9 | 0 | 22.52 | 0
2025-01-10 | -7.2 | 25.2 | 0 | 2024-01-10 | 3.9 | 14.1 | 0 | 2023-01-10 | -8 | 26 | 0 | 2022-01-10 | -12.1 | 30.1 | 0 | 2021-01-10 | -7.6 | 25.6 | 0 | 2020-01-10 | 3.4 | 14.6 | 0 | 2019-01-10 | -8.9 | 26.9 | 0 | 2018-01-10 | -4.8 | 22.8 | 0 | 2017-01-10 | -4.2 | 22.2 | 0 | 2016-01-10 | 2.9 | 15.1 | 0 | 22.26 | 0
2025-01-10 | -6.5 | 24.5 | 0 | 2024-01-10 | 3.2 | 14.8 | 0 | 2023-01-10 | -8 | 26 | 0 | 2022-01-10 | -12.2 | 30.2 | 0 | 2021-01-10 | -7.3 | 25.3 | 0 | 2020-01-10 | 3.3 | 14.7 | 0 | 2019-01-10 | -9.5 | 27.5 | 0 | 2018-01-10 | -4.5 | 22.5 | 0 | 2017-01-10 | -5.3 | 23.3 | 0 | 2016-01-10 | 3 | 15 | 0 | 22.38 | 0
2025-01-10 | -7.1 | 25.1 | 0 | 2024-01-10 | 2.4 | 15.6 | 0 | 2023-01-10 | -8.6 | 26.6 | 0 | 2022-01-10 | -13 | 31 | 0 | 2021-01-10 | -7.3 | 25.3 | 0 | 2020-01-10 | 3.4 | 14.6 | 0 | 2019-01-10 | -10.5 | 28.5 | 0 | 2018-01-10 | -4.3 | 22.3 | 0 | 2017-01-10 | -5.8 | 23.8 | 0 | 2016-01-10 | 3.2 | 14.8 | 0 | 22.76 | 0
2025-01-10 | -7.6 | 25.6 | 0 | 2024-01-10 | 1.6 | 16.4 | 0 | 2023-01-10 | -9.6 | 27.6 | 0 | 2022-01-10 | -14 | 32 | 0 | 2021-01-10 | -7.3 | 25.3 | 0 | 2020-01-10 | 3.2 | 14.8 | 0 | 2019-01-10 | -11.3 | 29.3 | 0 | 2018-01-10 | -4.4 | 22.4 | 0 | 2017-01-10 | -5.1 | 23.1 | 0 | 2016-01-10 | 3.4 | 14.6 | 0 | 23.11 | 0
2025-01-10 | -8.7 | 26.7 | 0 | 2024-01-10 | 0.7 | 17.3 | 0 | 2023-01-10 | -9.5 | 27.5 | 0 | 2022-01-10 | -14.9 | 32.9 | 0 | 2021-01-10 | -8.4 | 26.4 | 0 | 2020-01-10 | 3.1 | 14.9 | 0 | 2019-01-10 | -12.2 | 30.2 | 0 | 2018-01-10 | -4.3 | 22.3 | 0 | 2017-01-10 | -4.2 | 22.2 | 0 | 2016-01-10 | 4.2 | 13.8 | 0 | 23.42 | 0
2025-01-10 | -8.1 | 26.1 | 0 | 2024-01-10 | -0.1 | 18.1 | 0 | 2023-01-10 | -10.4 | 28.4 | 0 | 2022-01-10 | -15.2 | 33.2 | 0 | 2021-01-10 | -8.5 | 26.5 | 0 | 2020-01-10 | 3.4 | 14.6 | 0 | 2019-01-10 | -12.7 | 30.7 | 0 | 2018-01-10 | -4.4 | 22.4 | 0 | 2017-01-10 | -3.5 | 21.5 | 0 | 2016-01-10 | 5.8 | 12.2 | 0 | 23.37 | 0
2025-01-10 | -8 | 26 | 0 | 2024-01-10 | -2 | 20 | 0 | 2023-01-10 | -9.8 | 27.8 | 0 | 2022-01-10 | -16.4 | 34.4 | 0 | 2021-01-10 | -9.8 | 27.8 | 0 | 2020-01-10 | 3.1 | 14.9 | 0 | 2019-01-10 | -13.2 | 31.2 | 0 | 2018-01-10 | -4.3 | 22.3 | 0 | 2017-01-10 | -2 | 20 | 0 | 2016-01-10 | 6.1 | 11.9 | 0 | 23.63 | 0
2025-01-10 | -7.9 | 25.9 | 0 | 2024-01-10 | -3.7 | 21.7 | 0 | 2023-01-10 | -10.1 | 28.1 | 0 | 2022-01-10 | -17.6 | 35.6 | 0 | 2021-01-10 | -9.4 | 27.4 | 0 | 2020-01-10 | 3.1 | 14.9 | 0 | 2019-01-10 | -13.6 | 31.6 | 0 | 2018-01-10 | -4.1 | 22.1 | 0 | 2017-01-10 | -1.4 | 19.4 | 0 | 2016-01-10 | 2.1 | 15.9 | 0 | 24.26 | 0
2025-01-10 | -8.3 | 26.3 | 0 | 2024-01-10 | -4.4 | 22.4 | 0 | 2023-01-10 | -10.8 | 28.8 | 0 | 2022-01-10 | -18.6 | 36.6 | 0 | 2021-01-10 | -9 | 27 | 0 | 2020-01-10 | 3.1 | 14.9 | 0 | 2019-01-10 | -14 | 32 | 0 | 2018-01-10 | -4.1 | 22.1 | 0 | 2017-01-10 | -0.6 | 18.6 | 0 | 2016-01-10 | -0.8 | 18.8 | 0 | 24.75 | 0
2025-01-10 | -8 | 26 | 0 | 2024-01-10 | -4.9 | 22.9 | 0 | 2023-01-10 | -11.4 | 29.4 | 0 | 2022-01-10 | -20 | 38 | 0 | 2021-01-10 | -7.8 | 25.8 | 0 | 2020-01-10 | 3 | 15 | 0 | 2019-01-10 | -14.6 | 32.6 | 0 | 2018-01-10 | -3.4 | 21.4 | 0 | 2017-01-10 | 0.1 | 17.9 | 0 | 2016-01-10 | -2 | 20 | 0 | 24.9 | 0
2025-01-11 | -8.3 | 26.3 | 0 | 2024-01-11 | -5.2 | 23.2 | 0 | 2023-01-11 | -12 | 30 | 0 | 2022-01-11 | -21.3 | 39.3 | 0 | 2021-01-11 | -7.1 | 25.1 | 0 | 2020-01-11 | 3 | 15 | 0 | 2019-01-11 | -15.5 | 33.5 | 0 | 2018-01-11 | -2.3 | 20.3 | 0 | 2017-01-11 | 0.7 | 17.3 | 0 | 2016-01-11 | -3.9 | 21.9 | 0 | 25.19 | 0
2025-01-11 | -7.9 | 25.9 | 0 | 2024-01-11 | -5.2 | 23.2 | 0 | 2023-01-11 | -12.9 | 30.9 | 0 | 2022-01-11 | -22.4 | 40.4 | 0 | 2021-01-11 | -6.2 | 24.2 | 0 | 2020-01-11 | 3 | 15 | 0 | 2019-01-11 | -17.2 | 35.2 | 0 | 2018-01-11 | -0.8 | 18.8 | 0 | 2017-01-11 | 1 | 17 | 0 | 2016-01-11 | -5.5 | 23.5 | 0 | 25.41 | 0
2025-01-11 | -7.5 | 25.5 | 0 | 2024-01-11 | -5.3 | 23.3 | 0 | 2023-01-11 | -14 | 32 | 0 | 2022-01-11 | -23.3 | 41.3 | 0 | 2021-01-11 | -5.7 | 23.7 | 0 | 2020-01-11 | 2.7 | 15.3 | 0 | 2019-01-11 | -18.1 | 36.1 | 0 | 2018-01-11 | 1.1 | 16.9 | 0 | 2017-01-11 | 1.5 | 16.5 | 0 | 2016-01-11 | -5.9 | 23.9 | 0 | 25.45 | 0
2025-01-11 | -7.5 | 25.5 | 0 | 2024-01-11 | -5.8 | 23.8 | 0 | 2023-01-11 | -13.4 | 31.4 | 0 | 2022-01-11 | -24 | 42 | 0 | 2021-01-11 | -5.6 | 23.6 | 0 | 2020-01-11 | 2.1 | 15.9 | 0 | 2019-01-11 | -18.8 | 36.8 | 0 | 2018-01-11 | 1.8 | 16.2 | 0 | 2017-01-11 | 1.9 | 16.1 | 0 | 2016-01-11 | -6.7 | 24.7 | 0 | 25.6 | 0
2025-01-11 | -7.7 | 25.7 | 0 | 2024-01-11 | -6.2 | 24.2 | 0 | 2023-01-11 | -13.3 | 31.3 | 0 | 2022-01-11 | -24.7 | 42.7 | 0 | 2021-01-11 | -5.7 | 23.7 | 0 | 2020-01-11 | 2.3 | 15.7 | 0 | 2019-01-11 | -19.5 | 37.5 | 0 | 2018-01-11 | 2.7 | 15.3 | 0 | 2017-01-11 | 3.6 | 14.4 | 0 | 2016-01-11 | -7.7 | 25.7 | 0 | 25.62 | 0
2025-01-11 | -8 | 26 | 0 | 2024-01-11 | -7 | 25 | 0 | 2023-01-11 | -14.7 | 32.7 | 0 | 2022-01-11 | -25.3 | 43.3 | 0 | 2021-01-11 | -6 | 24 | 0 | 2020-01-11 | 2.1 | 15.9 | 0 | 2019-01-11 | -20.1 | 38.1 | 0 | 2018-01-11 | 2.9 | 15.1 | 0 | 2017-01-11 | 3.6 | 14.4 | 0 | 2016-01-11 | -9.2 | 27.2 | 0 | 26.17 | 0
2025-01-11 | -7.6 | 25.6 | 0 | 2024-01-11 | -8.5 | 26.5 | 0 | 2023-01-11 | -15.1 | 33.1 | 0 | 2022-01-11 | -25.6 | 43.6 | 0 | 2021-01-11 | -5.6 | 23.6 | 0 | 2020-01-11 | 2.6 | 15.4 | 0 | 2019-01-11 | -20.7 | 38.7 | 0 | 2018-01-11 | 2.9 | 15.1 | 0 | 2017-01-11 | 3.3 | 14.7 | 0 | 2016-01-11 | -10 | 28 | 0 | 26.43 | 0
2025-01-11 | -7.5 | 25.5 | 0 | 2024-01-11 | -7.6 | 25.6 | 0 | 2023-01-11 | -15 | 33 | 0 | 2022-01-11 | -26.4 | 44.4 | 0 | 2021-01-11 | -5.4 | 23.4 | 0 | 2020-01-11 | 3.8 | 14.2 | 0 | 2019-01-11 | -21.3 | 39.3 | 0 | 2018-01-11 | 4.2 | 13.8 | 0 | 2017-01-11 | 3.3 | 14.7 | 0 | 2016-01-11 | -10.8 | 28.8 | 0 | 26.27 | 0
2025-01-11 | -7.3 | 25.3 | 0 | 2024-01-11 | -6.8 | 24.8 | 0 | 2023-01-11 | -15 | 33 | 0 | 2022-01-11 | -26.5 | 44.5 | 0 | 2021-01-11 | -5.1 | 23.1 | 0 | 2020-01-11 | 5.5 | 12.5 | 0 | 2019-01-11 | -21.4 | 39.4 | 0 | 2018-01-11 | 4.8 | 13.2 | 0 | 2017-01-11 | 3.8 | 14.2 | 0 | 2016-01-11 | -11.3 | 29.3 | 0 | 25.93 | 0
2025-01-11 | -6.9 | 24.9 | 0 | 2024-01-11 | -7 | 25 | 0 | 2023-01-11 | -13.1 | 31.1 | 0 | 2022-01-11 | -25.7 | 43.7 | 0 | 2021-01-11 | -4.7 | 22.7 | 0 | 2020-01-11 | 6.7 | 11.3 | 0 | 2019-01-11 | -20.4 | 38.4 | 0 | 2018-01-11 | 4.7 | 13.3 | 0 | 2017-01-11 | 3.5 | 14.5 | 0 | 2016-01-11 | -11.1 | 29.1 | 0 | 25.4 | 0
2025-01-11 | -6.5 | 24.5 | 0 | 2024-01-11 | -6.5 | 24.5 | 0 | 2023-01-11 | -11.4 | 29.4 | 0 | 2022-01-11 | -25 | 43 | 0 | 2021-01-11 | -4 | 22 | 0 | 2020-01-11 | 7.4 | 10.6 | 0 | 2019-01-11 | -19.8 | 37.8 | 0 | 2018-01-11 | 5.4 | 12.6 | 0 | 2017-01-11 | 3.6 | 14.4 | 0 | 2016-01-11 | -10.5 | 28.5 | 0 | 24.73 | 0
2025-01-11 | -5.8 | 23.8 | 0 | 2024-01-11 | -6.1 | 24.1 | 0 | 2023-01-11 | -10.1 | 28.1 | 0 | 2022-01-11 | -24.2 | 42.2 | 0 | 2021-01-11 | -1.7 | 19.7 | 0 | 2020-01-11 | 7.9 | 10.1 | 0 | 2019-01-11 | -18.3 | 36.3 | 0 | 2018-01-11 | 6.5 | 11.5 | 0 | 2017-01-11 | 3.7 | 14.3 | 0 | 2016-01-11 | -10.3 | 28.3 | 0 | 23.84 | 0
2025-01-11 | -6 | 24 | 0 | 2024-01-11 | -5.7 | 23.7 | 0 | 2023-01-11 | -8.7 | 26.7 | 0 | 2022-01-11 | -23 | 41 | 0 | 2021-01-11 | 0.8 | 17.2 | 0 | 2020-01-11 | 8.3 | 9.7 | 0 | 2019-01-11 | -17.8 | 35.8 | 0 | 2018-01-11 | 7 | 11 | 0 | 2017-01-11 | 3.6 | 14.4 | 0 | 2016-01-11 | -9.9 | 27.9 | 0 | 23.14 | 0
2025-01-11 | -5.1 | 23.1 | 0 | 2024-01-11 | -5.6 | 23.6 | 0 | 2023-01-11 | -8.8 | 26.8 | 0 | 2022-01-11 | -22.2 | 40.2 | 0 | 2021-01-11 | 1.1 | 16.9 | 0 | 2020-01-11 | 6.2 | 11.8 | 0 | 2019-01-11 | -16.6 | 34.6 | 0 | 2018-01-11 | 7.1 | 10.9 | 0 | 2017-01-11 | 4.2 | 13.8 | 0 | 2016-01-11 | -9.5 | 27.5 | 0 | 22.92 | 0
2025-01-11 | -4.4 | 22.4 | 0 | 2024-01-11 | -6.4 | 24.4 | 0 | 2023-01-11 | -8.3 | 26.3 | 0 | 2022-01-11 | -21.2 | 39.2 | 0 | 2021-01-11 | 0.6 | 17.4 | 0 | 2020-01-11 | 2.7 | 15.3 | 0 | 2019-01-11 | -16.4 | 34.4 | 0 | 2018-01-11 | 6.3 | 11.7 | 0 | 2017-01-11 | 4.1 | 13.9 | 0 | 2016-01-11 | -9.2 | 27.2 | 0 | 23.22 | 0
2025-01-11 | -4.3 | 22.3 | 0 | 2024-01-11 | -6.3 | 24.3 | 0 | 2023-01-11 | -8.9 | 26.9 | 0 | 2022-01-11 | -20.6 | 38.6 | 0 | 2021-01-11 | 0.3 | 17.7 | 0 | 2020-01-11 | 2.2 | 15.8 | 0 | 2019-01-11 | -15.7 | 33.7 | 0 | 2018-01-11 | 6.2 | 11.8 | 0 | 2017-01-11 | 3.5 | 14.5 | 0 | 2016-01-11 | -9.1 | 27.1 | 0 | 23.27 | 0
2025-01-11 | -4.4 | 22.4 | 0 | 2024-01-11 | -6.3 | 24.3 | 0 | 2023-01-11 | -9.2 | 27.2 | 0 | 2022-01-11 | -20.3 | 38.3 | 0 | 2021-01-11 | 0.2 | 17.8 | 0 | 2020-01-11 | 1.8 | 16.2 | 0 | 2019-01-11 | -15.3 | 33.3 | 0 | 2018-01-11 | 6.2 | 11.8 | 0 | 2017-01-11 | 3.4 | 14.6 | 0 | 2016-01-11 | -9.5 | 27.5 | 0 | 23.34 | 0
2025-01-11 | -5.9 | 23.9 | 0 | 2024-01-11 | -6.4 | 24.4 | 0 | 2023-01-11 | -9.4 | 27.4 | 0 | 2022-01-11 | -20.3 | 38.3 | 0 | 2021-01-11 | -0.1 | 18.1 | 0 | 2020-01-11 | 1.8 | 16.2 | 0 | 2019-01-11 | -16.6 | 34.6 | 0 | 2018-01-11 | 6.3 | 11.7 | 0 | 2017-01-11 | 3.3 | 14.7 | 0 | 2016-01-11 | -9.8 | 27.8 | 0 | 23.71 | 0
2025-01-11 | -7.2 | 25.2 | 0 | 2024-01-11 | -6.4 | 24.4 | 0 | 2023-01-11 | -9.6 | 27.6 | 0 | 2022-01-11 | -21.6 | 39.6 | 0 | 2021-01-11 | 0.1 | 17.9 | 0 | 2020-01-11 | 1.6 | 16.4 | 0 | 2019-01-11 | -16.2 | 34.2 | 0 | 2018-01-11 | 6.3 | 11.7 | 0 | 2017-01-11 | 2.8 | 15.2 | 0 | 2016-01-11 | -10.4 | 28.4 | 0 | 24.06 | 0
2025-01-11 | -8.1 | 26.1 | 0 | 2024-01-11 | -6.7 | 24.7 | 0 | 2023-01-11 | -9.6 | 27.6 | 0 | 2022-01-11 | -19.7 | 37.7 | 0 | 2021-01-11 | 0.3 | 17.7 | 0 | 2020-01-11 | 1.1 | 16.9 | 0 | 2019-01-11 | -16.8 | 34.8 | 0 | 2018-01-11 | 6.1 | 11.9 | 0 | 2017-01-11 | 2.3 | 15.7 | 0 | 2016-01-11 | -11.8 | 29.8 | 0 | 24.29 | 0
2025-01-11 | -7.5 | 25.5 | 0 | 2024-01-11 | -6.4 | 24.4 | 0 | 2023-01-11 | -9.5 | 27.5 | 0 | 2022-01-11 | -19 | 37 | 0 | 2021-01-11 | 0.2 | 17.8 | 0 | 2020-01-11 | 0.8 | 17.2 | 0 | 2019-01-11 | -16.7 | 34.7 | 0 | 2018-01-11 | 6.3 | 11.7 | 0 | 2017-01-11 | 4.2 | 13.8 | 0 | 2016-01-11 | -11.9 | 29.9 | 0 | 23.95 | 0
2025-01-11 | -7.8 | 25.8 | 0 | 2024-01-11 | -6.4 | 24.4 | 0 | 2023-01-11 | -9.3 | 27.3 | 0 | 2022-01-11 | -18.4 | 36.4 | 0 | 2021-01-11 | 0.1 | 17.9 | 0 | 2020-01-11 | -0.2 | 18.2 | 0 | 2019-01-11 | -16.2 | 34.2 | 0 | 2018-01-11 | 7.2 | 10.8 | 0 | 2017-01-11 | 4.7 | 13.3 | 0 | 2016-01-11 | -12.2 | 30.2 | 0 | 23.85 | 0
2025-01-11 | -9.4 | 27.4 | 0 | 2024-01-11 | -6.3 | 24.3 | 0 | 2023-01-11 | -9.1 | 27.1 | 0 | 2022-01-11 | -17.7 | 35.7 | 0 | 2021-01-11 | 0.1 | 17.9 | 0 | 2020-01-11 | -0.5 | 18.5 | 0 | 2019-01-11 | -15.6 | 33.6 | 0 | 2018-01-11 | 7.2 | 10.8 | 0 | 2017-01-11 | 5 | 13 | 0 | 2016-01-11 | -12.9 | 30.9 | 0 | 23.92 | 0
2025-01-11 | -8 | 26 | 0 | 2024-01-11 | -6.3 | 24.3 | 0 | 2023-01-11 | -9 | 27 | 0 | 2022-01-11 | -15.9 | 33.9 | 0 | 2021-01-11 | 0 | 18 | 0 | 2020-01-11 | -1.6 | 19.6 | 0 | 2019-01-11 | -15.9 | 33.9 | 0 | 2018-01-11 | 7.2 | 10.8 | 0 | 2017-01-11 | 5.5 | 12.5 | 0 | 2016-01-11 | -13.2 | 31.2 | 0 | 23.72 | 0
2025-01-12 | -9.4 | 27.4 | 0 | 2024-01-12 | -6.2 | 24.2 | 0 | 2023-01-12 | -8.7 | 26.7 | 0 | 2022-01-12 | -15.1 | 33.1 | 0 | 2021-01-12 | -0.4 | 18.4 | 0 | 2020-01-12 | -2.4 | 20.4 | 0 | 2019-01-12 | -16.1 | 34.1 | 0 | 2018-01-12 | 8.1 | 9.9 | 0 | 2017-01-12 | 5.7 | 12.3 | 0 | 2016-01-12 | -14.8 | 32.8 | 0 | 23.93 | 0
2025-01-12 | -8.2 | 26.2 | 0 | 2024-01-12 | -6.3 | 24.3 | 0 | 2023-01-12 | -8.4 | 26.4 | 0 | 2022-01-12 | -15.8 | 33.8 | 0 | 2021-01-12 | -0.5 | 18.5 | 0 | 2020-01-12 | -2.4 | 20.4 | 0 | 2019-01-12 | -16.3 | 34.3 | 0 | 2018-01-12 | 9.2 | 8.8 | 0 | 2017-01-12 | 5.7 | 12.3 | 0 | 2016-01-12 | -13.2 | 31.2 | 0 | 23.62 | 0
2025-01-12 | -7.8 | 25.8 | 0 | 2024-01-12 | -6.2 | 24.2 | 0 | 2023-01-12 | -8.2 | 26.2 | 0 | 2022-01-12 | -16 | 34 | 0 | 2021-01-12 | -0.9 | 18.9 | 0 | 2020-01-12 | -2.9 | 20.9 | 0 | 2019-01-12 | -17 | 35 | 0 | 2018-01-12 | 9.3 | 8.7 | 0 | 2017-01-12 | 5.7 | 12.3 | 0 | 2016-01-12 | -14.2 | 32.2 | 0 | 23.82 | 0
2025-01-12 | -10.4 | 28.4 | 0 | 2024-01-12 | -6.6 | 24.6 | 0 | 2023-01-12 | -7.9 | 25.9 | 0 | 2022-01-12 | -15.9 | 33.9 | 0 | 2021-01-12 | -1 | 19 | 0 | 2020-01-12 | -3.6 | 21.6 | 0 | 2019-01-12 | -17.4 | 35.4 | 0 | 2018-01-12 | 10 | 8 | 0 | 2017-01-12 | 5.7 | 12.3 | 0 | 2016-01-12 | -13.7 | 31.7 | 0 | 24.08 | 0
2025-01-12 | -8.9 | 26.9 | 0 | 2024-01-12 | -6.6 | 24.6 | 0 | 2023-01-12 | -7.7 | 25.7 | 0 | 2022-01-12 | -16 | 34 | 0 | 2021-01-12 | -1.4 | 19.4 | 0 | 2020-01-12 | -4 | 22 | 0 | 2019-01-12 | -18.2 | 36.2 | 0 | 2018-01-12 | 10.3 | 7.7 | 0 | 2017-01-12 | 4.7 | 13.3 | 0 | 2016-01-12 | -12.8 | 30.8 | 0 | 24.06 | 0
2025-01-12 | -9.7 | 27.7 | 0 | 2024-01-12 | -6.8 | 24.8 | 0 | 2023-01-12 | -7.7 | 25.7 | 0 | 2022-01-12 | -15.5 | 33.5 | 0 | 2021-01-12 | -1.4 | 19.4 | 0 | 2020-01-12 | -4.5 | 22.5 | 0 | 2019-01-12 | -18.3 | 36.3 | 0 | 2018-01-12 | 10.5 | 7.5 | 0 | 2017-01-12 | 4.5 | 13.5 | 0 | 2016-01-12 | -11.6 | 29.6 | 0 | 24.05 | 0
2025-01-12 | -10.4 | 28.4 | 0 | 2024-01-12 | -7.8 | 25.8 | 0 | 2023-01-12 | -7.5 | 25.5 | 0 | 2022-01-12 | -14.7 | 32.7 | 0 | 2021-01-12 | -1.5 | 19.5 | 0 | 2020-01-12 | -5.2 | 23.2 | 0 | 2019-01-12 | -18.3 | 36.3 | 0 | 2018-01-12 | 10.7 | 7.3 | 0 | 2017-01-12 | 4.8 | 13.2 | 0 | 2016-01-12 | -13.5 | 31.5 | 0 | 24.34 | 0
2025-01-12 | -7.6 | 25.6 | 0 | 2024-01-12 | -8.2 | 26.2 | 0 | 2023-01-12 | -7.2 | 25.2 | 0 | 2022-01-12 | -14.2 | 32.2 | 0 | 2021-01-12 | -1.6 | 19.6 | 0 | 2020-01-12 | -5.8 | 23.8 | 0 | 2019-01-12 | -19.2 | 37.2 | 0 | 2018-01-12 | 11.2 | 6.8 | 0 | 2017-01-12 | 3.2 | 14.8 | 0 | 2016-01-12 | -13.2 | 31.2 | 0 | 24.26 | 0
2025-01-12 | -7.2 | 25.2 | 0 | 2024-01-12 | -9.9 | 27.9 | 0 | 2023-01-12 | -6.8 | 24.8 | 0 | 2022-01-12 | -13.4 | 31.4 | 0 | 2021-01-12 | -1.6 | 19.6 | 0 | 2020-01-12 | -6 | 24 | 0 | 2019-01-12 | -20.1 | 38.1 | 0 | 2018-01-12 | 11.3 | 6.7 | 0 | 2017-01-12 | 3.2 | 14.8 | 0 | 2016-01-12 | -12.2 | 30.2 | 0 | 24.27 | 0
2025-01-12 | -6.8 | 24.8 | 0 | 2024-01-12 | -8.6 | 26.6 | 0 | 2023-01-12 | -6.2 | 24.2 | 0 | 2022-01-12 | -11.8 | 29.8 | 0 | 2021-01-12 | -1.5 | 19.5 | 0 | 2020-01-12 | -6.6 | 24.6 | 0 | 2019-01-12 | -18.3 | 36.3 | 0 | 2018-01-12 | 11.9 | 6.1 | 0 | 2017-01-12 | 3.9 | 14.1 | 0 | 2016-01-12 | -10.9 | 28.9 | 0 | 23.49 | 0
2025-01-12 | -6.4 | 24.4 | 0 | 2024-01-12 | -7.6 | 25.6 | 0 | 2023-01-12 | -5.7 | 23.7 | 0 | 2022-01-12 | -11.3 | 29.3 | 0 | 2021-01-12 | -0.8 | 18.8 | 0 | 2020-01-12 | -7.8 | 25.8 | 0 | 2019-01-12 | -17.3 | 35.3 | 0 | 2018-01-12 | 11.4 | 6.6 | 0 | 2017-01-12 | 3.5 | 14.5 | 0 | 2016-01-12 | -9.5 | 27.5 | 0 | 23.15 | 0
2025-01-12 | -6.1 | 24.1 | 0 | 2024-01-12 | -6.5 | 24.5 | 0 | 2023-01-12 | -5.5 | 23.5 | 0 | 2022-01-12 | -10.7 | 28.7 | 0 | 2021-01-12 | -0.4 | 18.4 | 0 | 2020-01-12 | -8.6 | 26.6 | 0 | 2019-01-12 | -16.6 | 34.6 | 0 | 2018-01-12 | 11.5 | 6.5 | 0 | 2017-01-12 | 2.6 | 15.4 | 0 | 2016-01-12 | -8.7 | 26.7 | 0 | 22.9 | 0
2025-01-12 | -5.4 | 23.4 | 0 | 2024-01-12 | -6.1 | 24.1 | 0 | 2023-01-12 | -5.3 | 23.3 | 0 | 2022-01-12 | -10.8 | 28.8 | 0 | 2021-01-12 | 0 | 18 | 0 | 2020-01-12 | -8.8 | 26.8 | 0 | 2019-01-12 | -15.6 | 33.6 | 0 | 2018-01-12 | 11.2 | 6.8 | 0 | 2017-01-12 | 2.4 | 15.6 | 0 | 2016-01-12 | -8.1 | 26.1 | 0 | 22.65 | 0
2025-01-12 | -5.2 | 23.2 | 0 | 2024-01-12 | -5.4 | 23.4 | 0 | 2023-01-12 | -4.9 | 22.9 | 0 | 2022-01-12 | -9.7 | 27.7 | 0 | 2021-01-12 | 0.2 | 17.8 | 0 | 2020-01-12 | -8.4 | 26.4 | 0 | 2019-01-12 | -14.8 | 32.8 | 0 | 2018-01-12 | 4.2 | 13.8 | 0 | 2017-01-12 | 2.4 | 15.6 | 0 | 2016-01-12 | -7.8 | 25.8 | 0 | 22.94 | 0
2025-01-12 | -4.7 | 22.7 | 0 | 2024-01-12 | -5.5 | 23.5 | 0 | 2023-01-12 | -4.5 | 22.5 | 0 | 2022-01-12 | -10.2 | 28.2 | 0 | 2021-01-12 | 0.5 | 17.5 | 0 | 2020-01-12 | -8.8 | 26.8 | 0 | 2019-01-12 | -13.7 | 31.7 | 0 | 2018-01-12 | 1.8 | 16.2 | 0 | 2017-01-12 | 2 | 16 | 0 | 2016-01-12 | -7.4 | 25.4 | 0 | 23.05 | 0
2025-01-12 | -4.5 | 22.5 | 0 | 2024-01-12 | -5.7 | 23.7 | 0 | 2023-01-12 | -4 | 22 | 0 | 2022-01-12 | -9.4 | 27.4 | 0 | 2021-01-12 | 0.7 | 17.3 | 0 | 2020-01-12 | -8.6 | 26.6 | 0 | 2019-01-12 | -13.5 | 31.5 | 0 | 2018-01-12 | -0.4 | 18.4 | 0 | 2017-01-12 | 1.3 | 16.7 | 0 | 2016-01-12 | -7 | 25 | 0 | 23.11 | 0
2025-01-12 | -4.5 | 22.5 | 0 | 2024-01-12 | -5.4 | 23.4 | 0 | 2023-01-12 | -3.4 | 21.4 | 0 | 2022-01-12 | -8 | 26 | 0 | 2021-01-12 | 0.7 | 17.3 | 0 | 2020-01-12 | -8.6 | 26.6 | 0 | 2019-01-12 | -13.8 | 31.8 | 0 | 2018-01-12 | -3.3 | 21.3 | 0 | 2017-01-12 | 0.6 | 17.4 | 0 | 2016-01-12 | -6.6 | 24.6 | 0 | 23.23 | 0
2025-01-12 | -4.4 | 22.4 | 0 | 2024-01-12 | -6.2 | 24.2 | 0 | 2023-01-12 | -3.2 | 21.2 | 0 | 2022-01-12 | -7.2 | 25.2 | 0 | 2021-01-12 | 0.1 | 17.9 | 0 | 2020-01-12 | -9.3 | 27.3 | 0 | 2019-01-12 | -15.6 | 33.6 | 0 | 2018-01-12 | -7 | 25 | 0 | 2017-01-12 | 0.2 | 17.8 | 0 | 2016-01-12 | -6.6 | 24.6 | 0 | 23.92 | 0
2025-01-12 | -5.5 | 23.5 | 0 | 2024-01-12 | -6.4 | 24.4 | 0 | 2023-01-12 | -2.8 | 20.8 | 0 | 2022-01-12 | -6.8 | 24.8 | 0 | 2021-01-12 | -0.4 | 18.4 | 0 | 2020-01-12 | -9.5 | 27.5 | 0 | 2019-01-12 | -16.1 | 34.1 | 0 | 2018-01-12 | -8.4 | 26.4 | 0 | 2017-01-12 | 0 | 18 | 0 | 2016-01-12 | -6.2 | 24.2 | 0 | 24.21 | 0
2025-01-12 | -5.7 | 23.7 | 0 | 2024-01-12 | -6.2 | 24.2 | 0 | 2023-01-12 | -2.6 | 20.6 | 0 | 2022-01-12 | -6.7 | 24.7 | 0 | 2021-01-12 | -0.6 | 18.6 | 0 | 2020-01-12 | -9.7 | 27.7 | 0 | 2019-01-12 | -16.4 | 34.4 | 0 | 2018-01-12 | -9.7 | 27.7 | 0 | 2017-01-12 | -0.5 | 18.5 | 0 | 2016-01-12 | -4.9 | 22.9 | 0 | 24.3 | 0
2025-01-12 | -5.2 | 23.2 | 0 | 2024-01-12 | -6.3 | 24.3 | 0 | 2023-01-12 | -2.2 | 20.2 | 0 | 2022-01-12 | -6.8 | 24.8 | 0 | 2021-01-12 | -0.7 | 18.7 | 0 | 2020-01-12 | -10.1 | 28.1 | 0 | 2019-01-12 | -16.5 | 34.5 | 0 | 2018-01-12 | -10.7 | 28.7 | 0 | 2017-01-12 | -1.2 | 19.2 | 0 | 2016-01-12 | -3.5 | 21.5 | 0 | 24.32 | 0
2025-01-12 | -5.8 | 23.8 | 0 | 2024-01-12 | -6.3 | 24.3 | 0 | 2023-01-12 | -1.9 | 19.9 | 0 | 2022-01-12 | -6.8 | 24.8 | 0 | 2021-01-12 | -0.9 | 18.9 | 0 | 2020-01-12 | -10.6 | 28.6 | 0 | 2019-01-12 | -16.4 | 34.4 | 0 | 2018-01-12 | -11.1 | 29.1 | 0 | 2017-01-12 | -1.9 | 19.9 | 0 | 2016-01-12 | -5.1 | 23.1 | 0 | 24.68 | 0
2025-01-12 | -5.6 | 23.6 | 0 | 2024-01-12 | -5.9 | 23.9 | 0 | 2023-01-12 | -1.7 | 19.7 | 0 | 2022-01-12 | -6.8 | 24.8 | 0 | 2021-01-12 | -1.1 | 19.1 | 0 | 2020-01-12 | -11 | 29 | 0 | 2019-01-12 | -16.6 | 34.6 | 0 | 2018-01-12 | -11.4 | 29.4 | 0 | 2017-01-12 | -2.6 | 20.6 | 0 | 2016-01-12 | -5.7 | 23.7 | 0 | 24.84 | 0
2025-01-12 | -5.7 | 23.7 | 0 | 2024-01-12 | -6.8 | 24.8 | 0 | 2023-01-12 | -1.1 | 19.1 | 0 | 2022-01-12 | -7.1 | 25.1 | 0 | 2021-01-12 | -1.3 | 19.3 | 0 | 2020-01-12 | -11.1 | 29.1 | 0 | 2019-01-12 | -17.9 | 35.9 | 0 | 2018-01-12 | -11.9 | 29.9 | 0 | 2017-01-12 | -2.9 | 20.9 | 0 | 2016-01-12 | -6.3 | 24.3 | 0 | 25.21 | 0
2025-01-13 | -5.6 | 23.6 | 0 | 2024-01-13 | -6.7 | 24.7 | 0 | 2023-01-13 | -1.2 | 19.2 | 0 | 2022-01-13 | -6.9 | 24.9 | 0 | 2021-01-13 | -1.8 | 19.8 | 0 | 2020-01-13 | -11.1 | 29.1 | 0 | 2019-01-13 | -18 | 36 | 0 | 2018-01-13 | -12.6 | 30.6 | 0 | 2017-01-13 | -3.3 | 21.3 | 0 | 2016-01-13 | -7.2 | 25.2 | 0 | 25.44 | 0
2025-01-13 | -5.6 | 23.6 | 0 | 2024-01-13 | -5.6 | 23.6 | 0 | 2023-01-13 | -1.2 | 19.2 | 0 | 2022-01-13 | -7.4 | 25.4 | 0 | 2021-01-13 | -1.9 | 19.9 | 0 | 2020-01-13 | -11.2 | 29.2 | 0 | 2019-01-13 | -17 | 35 | 0 | 2018-01-13 | -13 | 31 | 0 | 2017-01-13 | -3.5 | 21.5 | 0 | 2016-01-13 | -8.1 | 26.1 | 0 | 25.45 | 0
2025-01-13 | -5.5 | 23.5 | 0 | 2024-01-13 | -5.4 | 23.4 | 0 | 2023-01-13 | -1.2 | 19.2 | 0 | 2022-01-13 | -7.8 | 25.8 | 0 | 2021-01-13 | -2.1 | 20.1 | 0 | 2020-01-13 | -11.6 | 29.6 | 0 | 2019-01-13 | -17.4 | 35.4 | 0 | 2018-01-13 | -13.3 | 31.3 | 0 | 2017-01-13 | -3.8 | 21.8 | 0 | 2016-01-13 | -9.5 | 27.5 | 0 | 25.76 | 0
2025-01-13 | -5.3 | 23.3 | 0 | 2024-01-13 | -5.2 | 23.2 | 0 | 2023-01-13 | -1.4 | 19.4 | 0 | 2022-01-13 | -7.9 | 25.9 | 0 | 2021-01-13 | -2.5 | 20.5 | 0 | 2020-01-13 | -11.1 | 29.1 | 0 | 2019-01-13 | -17.5 | 35.5 | 0 | 2018-01-13 | -13.9 | 31.9 | 0 | 2017-01-13 | -3.4 | 21.4 | 0 | 2016-01-13 | -10.3 | 28.3 | 0 | 25.85 | 0
2025-01-13 | -5.3 | 23.3 | 0 | 2024-01-13 | -4.8 | 22.8 | 0 | 2023-01-13 | -1.5 | 19.5 | 0 | 2022-01-13 | -8 | 26 | 0 | 2021-01-13 | -2.6 | 20.6 | 0 | 2020-01-13 | -10.9 | 28.9 | 0 | 2019-01-13 | -16.6 | 34.6 | 0 | 2018-01-13 | -13.9 | 31.9 | 0 | 2017-01-13 | -2.8 | 20.8 | 0 | 2016-01-13 | -11.4 | 29.4 | 0 | 25.78 | 0
2025-01-13 | -5.3 | 23.3 | 0 | 2024-01-13 | -5 | 23 | 0 | 2023-01-13 | -2.1 | 20.1 | 0 | 2022-01-13 | -8.1 | 26.1 | 0 | 2021-01-13 | -2.6 | 20.6 | 0 | 2020-01-13 | -10.3 | 28.3 | 0 | 2019-01-13 | -17.1 | 35.1 | 0 | 2018-01-13 | -15.2 | 33.2 | 0 | 2017-01-13 | -2.3 | 20.3 | 0 | 2016-01-13 | -12.4 | 30.4 | 0 | 26.04 | 0
2025-01-13 | -5.3 | 23.3 | 0 | 2024-01-13 | -4.7 | 22.7 | 0 | 2023-01-13 | -2.6 | 20.6 | 0 | 2022-01-13 | -8.2 | 26.2 | 0 | 2021-01-13 | -2.2 | 20.2 | 0 | 2020-01-13 | -9.8 | 27.8 | 0 | 2019-01-13 | -17.1 | 35.1 | 0 | 2018-01-13 | -15.3 | 33.3 | 0 | 2017-01-13 | -5 | 23 | 0 | 2016-01-13 | -13.1 | 31.1 | 0 | 26.33 | 0
2025-01-13 | -5.3 | 23.3 | 0 | 2024-01-13 | -3.8 | 21.8 | 0 | 2023-01-13 | -2.9 | 20.9 | 0 | 2022-01-13 | -8.8 | 26.8 | 0 | 2021-01-13 | -2.2 | 20.2 | 0 | 2020-01-13 | -9.6 | 27.6 | 0 | 2019-01-13 | -16.7 | 34.7 | 0 | 2018-01-13 | -16 | 34 | 0 | 2017-01-13 | -5.9 | 23.9 | 0 | 2016-01-13 | -13.9 | 31.9 | 0 | 26.51 | 0
2025-01-13 | -5.1 | 23.1 | 0 | 2024-01-13 | -3.1 | 21.1 | 0 | 2023-01-13 | -3.2 | 21.2 | 0 | 2022-01-13 | -9.6 | 27.6 | 0 | 2021-01-13 | -2 | 20 | 0 | 2020-01-13 | -9.8 | 27.8 | 0 | 2019-01-13 | -16.5 | 34.5 | 0 | 2018-01-13 | -16.7 | 34.7 | 0 | 2017-01-13 | -6.5 | 24.5 | 0 | 2016-01-13 | -14.4 | 32.4 | 0 | 26.69 | 0
2025-01-13 | -4.6 | 22.6 | 0 | 2024-01-13 | -1.7 | 19.7 | 0 | 2023-01-13 | -3.4 | 21.4 | 0 | 2022-01-13 | -9.8 | 27.8 | 0 | 2021-01-13 | -1.8 | 19.8 | 0 | 2020-01-13 | -9.4 | 27.4 | 0 | 2019-01-13 | -15.7 | 33.7 | 0 | 2018-01-13 | -17.3 | 35.3 | 0 | 2017-01-13 | -7 | 25 | 0 | 2016-01-13 | -14.2 | 32.2 | 0 | 26.49 | 0
2025-01-13 | -3.9 | 21.9 | 0 | 2024-01-13 | -0.9 | 18.9 | 0 | 2023-01-13 | -3.4 | 21.4 | 0 | 2022-01-13 | -9.5 | 27.5 | 0 | 2021-01-13 | -1.2 | 19.2 | 0 | 2020-01-13 | -8.9 | 26.9 | 0 | 2019-01-13 | -14.5 | 32.5 | 0 | 2018-01-13 | -17.1 | 35.1 | 0 | 2017-01-13 | -7.9 | 25.9 | 0 | 2016-01-13 | -14 | 32 | 0 | 26.13 | 0
2025-01-13 | -3.2 | 21.2 | 0 | 2024-01-13 | -1 | 19 | 0 | 2023-01-13 | -3.5 | 21.5 | 0 | 2022-01-13 | -9 | 27 | 0 | 2021-01-13 | -0.6 | 18.6 | 0 | 2020-01-13 | -8.7 | 26.7 | 0 | 2019-01-13 | -13.1 | 31.1 | 0 | 2018-01-13 | -17 | 35 | 0 | 2017-01-13 | -7.6 | 25.6 | 0 | 2016-01-13 | -13.2 | 31.2 | 0 | 25.69 | 0
2025-01-13 | -2.6 | 20.6 | 0 | 2024-01-13 | -1.1 | 19.1 | 0 | 2023-01-13 | -4.3 | 22.3 | 0 | 2022-01-13 | -8.6 | 26.6 | 0 | 2021-01-13 | -0.2 | 18.2 | 0 | 2020-01-13 | -8.4 | 26.4 | 0 | 2019-01-13 | -12.7 | 30.7 | 0 | 2018-01-13 | -16.7 | 34.7 | 0 | 2017-01-13 | -7.4 | 25.4 | 0 | 2016-01-13 | -13 | 31 | 0 | 25.5 | 0
2025-01-13 | -2.1 | 20.1 | 0 | 2024-01-13 | -0.5 | 18.5 | 0 | 2023-01-13 | -4.6 | 22.6 | 0 | 2022-01-13 | -7.8 | 25.8 | 0 | 2021-01-13 | 0 | 18 | 0 | 2020-01-13 | -8.2 | 26.2 | 0 | 2019-01-13 | -12.3 | 30.3 | 0 | 2018-01-13 | -16.1 | 34.1 | 0 | 2017-01-13 | -8.3 | 26.3 | 0 | 2016-01-13 | -12.4 | 30.4 | 0 | 25.23 | 0
2025-01-13 | -0.9 | 18.9 | 0 | 2024-01-13 | 1.6 | 16.4 | 0 | 2023-01-13 | -5 | 23 | 0 | 2022-01-13 | -7.7 | 25.7 | 0 | 2021-01-13 | 0.6 | 17.4 | 0 | 2020-01-13 | -7.9 | 25.9 | 0 | 2019-01-13 | -11.8 | 29.8 | 0 | 2018-01-13 | -15.9 | 33.9 | 0 | 2017-01-13 | -8.6 | 26.6 | 0 | 2016-01-13 | -11.6 | 29.6 | 0 | 24.72 | 0
2025-01-13 | 0 | 18 | 0 | 2024-01-13 | 1.6 | 16.4 | 0 | 2023-01-13 | -5 | 23 | 0 | 2022-01-13 | -7.5 | 25.5 | 0 | 2021-01-13 | 0.3 | 17.7 | 0 | 2020-01-13 | -7.6 | 25.6 | 0 | 2019-01-13 | -11.9 | 29.9 | 0 | 2018-01-13 | -15.5 | 33.5 | 0 | 2017-01-13 | -9.2 | 27.2 | 0 | 2016-01-13 | -11.6 | 29.6 | 0 | 24.64 | 0
2025-01-13 | -0.3 | 18.3 | 0 | 2024-01-13 | 0.9 | 17.1 | 0 | 2023-01-13 | -5.1 | 23.1 | 0 | 2022-01-13 | -7.6 | 25.6 | 0 | 2021-01-13 | -0.3 | 18.3 | 0 | 2020-01-13 | -7.3 | 25.3 | 0 | 2019-01-13 | -11.8 | 29.8 | 0 | 2018-01-13 | -15.7 | 33.7 | 0 | 2017-01-13 | -10.1 | 28.1 | 0 | 2016-01-13 | -11.7 | 29.7 | 0 | 24.9 | 0
2025-01-13 | -0.4 | 18.4 | 0 | 2024-01-13 | 0.2 | 17.8 | 0 | 2023-01-13 | -5.5 | 23.5 | 0 | 2022-01-13 | -7.5 | 25.5 | 0 | 2021-01-13 | -0.4 | 18.4 | 0 | 2020-01-13 | -7.2 | 25.2 | 0 | 2019-01-13 | -12.1 | 30.1 | 0 | 2018-01-13 | -16.3 | 34.3 | 0 | 2017-01-13 | -11.1 | 29.1 | 0 | 2016-01-13 | -12.9 | 30.9 | 0 | 25.32 | 0
2025-01-13 | -0.9 | 18.9 | 0 | 2024-01-13 | -0.2 | 18.2 | 0 | 2023-01-13 | -5.9 | 23.9 | 0 | 2022-01-13 | -7.4 | 25.4 | 0 | 2021-01-13 | -0.4 | 18.4 | 0 | 2020-01-13 | -7.1 | 25.1 | 0 | 2019-01-13 | -12.2 | 30.2 | 0 | 2018-01-13 | -17.1 | 35.1 | 0 | 2017-01-13 | -11.7 | 29.7 | 0 | 2016-01-13 | -13.6 | 31.6 | 0 | 25.65 | 0
2025-01-13 | -1.3 | 19.3 | 0 | 2024-01-13 | -0.7 | 18.7 | 0 | 2023-01-13 | -6 | 24 | 0 | 2022-01-13 | -7.4 | 25.4 | 0 | 2021-01-13 | -0.5 | 18.5 | 0 | 2020-01-13 | -7.1 | 25.1 | 0 | 2019-01-13 | -12.1 | 30.1 | 0 | 2018-01-13 | -17.5 | 35.5 | 0 | 2017-01-13 | -13.1 | 31.1 | 0 | 2016-01-13 | -14 | 32 | 0 | 25.97 | 0
2025-01-13 | -1.5 | 19.5 | 0 | 2024-01-13 | -0.7 | 18.7 | 0 | 2023-01-13 | -6.3 | 24.3 | 0 | 2022-01-13 | -7.5 | 25.5 | 0 | 2021-01-13 | -0.2 | 18.2 | 0 | 2020-01-13 | -7 | 25 | 0 | 2019-01-13 | -13 | 31 | 0 | 2018-01-13 | -17.4 | 35.4 | 0 | 2017-01-13 | -12.9 | 30.9 | 0 | 2016-01-13 | -15.8 | 33.8 | 0 | 26.23 | 0
2025-01-13 | -2 | 20 | 0 | 2024-01-13 | -1.2 | 19.2 | 0 | 2023-01-13 | -6.8 | 24.8 | 0 | 2022-01-13 | -7.5 | 25.5 | 0 | 2021-01-13 | 0 | 18 | 0 | 2020-01-13 | -6.9 | 24.9 | 0 | 2019-01-13 | -14.7 | 32.7 | 0 | 2018-01-13 | -18.2 | 36.2 | 0 | 2017-01-13 | -13.4 | 31.4 | 0 | 2016-01-13 | -16.7 | 34.7 | 0 | 26.74 | 0
2025-01-13 | -2.2 | 20.2 | 0 | 2024-01-13 | -2.6 | 20.6 | 0 | 2023-01-13 | -7.3 | 25.3 | 0 | 2022-01-13 | -7.6 | 25.6 | 0 | 2021-01-13 | 0 | 18 | 0 | 2020-01-13 | -6.8 | 24.8 | 0 | 2019-01-13 | -15.7 | 33.7 | 0 | 2018-01-13 | -18.4 | 36.4 | 0 | 2017-01-13 | -14.1 | 32.1 | 0 | 2016-01-13 | -15.7 | 33.7 | 0 | 27.04 | 0
2025-01-13 | -2.7 | 20.7 | 0 | 2024-01-13 | -3.3 | 21.3 | 0 | 2023-01-13 | -7.9 | 25.9 | 0 | 2022-01-13 | -7.4 | 25.4 | 0 | 2021-01-13 | 0 | 18 | 0 | 2020-01-13 | -7.1 | 25.1 | 0 | 2019-01-13 | -16.3 | 34.3 | 0 | 2018-01-13 | -19.5 | 37.5 | 0 | 2017-01-13 | -14.7 | 32.7 | 0 | 2016-01-13 | -14.7 | 32.7 | 0 | 27.36 | 0
2025-01-14 | -3 | 21 | 0 | 2024-01-14 | -3.8 | 21.8 | 0 | 2023-01-14 | -8.8 | 26.8 | 0 | 2022-01-14 | -7.4 | 25.4 | 0 | 2021-01-14 | 0 | 18 | 0 | 2020-01-14 | -7.1 | 25.1 | 0 | 2019-01-14 | -18 | 36 | 0 | 2018-01-14 | -20 | 38 | 0 | 2017-01-14 | -15.4 | 33.4 | 0 | 2016-01-14 | -14.1 | 32.1 | 0 | 27.76 | 0
2025-01-14 | -3.4 | 21.4 | 0 | 2024-01-14 | -4.1 | 22.1 | 0 | 2023-01-14 | -10.1 | 28.1 | 0 | 2022-01-14 | -7.2 | 25.2 | 0 | 2021-01-14 | 0 | 18 | 0 | 2020-01-14 | -7.4 | 25.4 | 0 | 2019-01-14 | -18.3 | 36.3 | 0 | 2018-01-14 | -20.9 | 38.9 | 0 | 2017-01-14 | -15.6 | 33.6 | 0 | 2016-01-14 | -14.3 | 32.3 | 0 | 28.13 | 0
2025-01-14 | -4.2 | 22.2 | 0 | 2024-01-14 | -4.6 | 22.6 | 0 | 2023-01-14 | -10.6 | 28.6 | 0 | 2022-01-14 | -7 | 25 | 0 | 2021-01-14 | -0.2 | 18.2 | 0 | 2020-01-14 | -7.6 | 25.6 | 0 | 2019-01-14 | -18.1 | 36.1 | 0 | 2018-01-14 | -21.3 | 39.3 | 0 | 2017-01-14 | -16.3 | 34.3 | 0 | 2016-01-14 | -14.2 | 32.2 | 0 | 28.41 | 0
2025-01-14 | -4.5 | 22.5 | 0 | 2024-01-14 | -5.2 | 23.2 | 0 | 2023-01-14 | -11.5 | 29.5 | 0 | 2022-01-14 | -7.1 | 25.1 | 0 | 2021-01-14 | -0.3 | 18.3 | 0 | 2020-01-14 | -8.1 | 26.1 | 0 | 2019-01-14 | -17.6 | 35.6 | 0 | 2018-01-14 | -22.4 | 40.4 | 0 | 2017-01-14 | -17.2 | 35.2 | 0 | 2016-01-14 | -13.6 | 31.6 | 0 | 28.75 | 0
2025-01-14 | -4.7 | 22.7 | 0 | 2024-01-14 | -4.6 | 22.6 | 0 | 2023-01-14 | -11.9 | 29.9 | 0 | 2022-01-14 | -7.1 | 25.1 | 0 | 2021-01-14 | -0.4 | 18.4 | 0 | 2020-01-14 | -8.2 | 26.2 | 0 | 2019-01-14 | -19.2 | 37.2 | 0 | 2018-01-14 | -23.1 | 41.1 | 0 | 2017-01-14 | -19.7 | 37.7 | 0 | 2016-01-14 | -15.7 | 33.7 | 0 | 29.46 | 0
2025-01-14 | -5 | 23 | 0 | 2024-01-14 | -4.5 | 22.5 | 0 | 2023-01-14 | -12.7 | 30.7 | 0 | 2022-01-14 | -8.9 | 26.9 | 0 | 2021-01-14 | -0.5 | 18.5 | 0 | 2020-01-14 | -8.4 | 26.4 | 0 | 2019-01-14 | -19 | 37 | 0 | 2018-01-14 | -23.7 | 41.7 | 0 | 2017-01-14 | -20.3 | 38.3 | 0 | 2016-01-14 | -15.3 | 33.3 | 0 | 29.83 | 0
2025-01-14 | -5.3 | 23.3 | 0 | 2024-01-14 | -4.7 | 22.7 | 0 | 2023-01-14 | -12.9 | 30.9 | 0 | 2022-01-14 | -10.3 | 28.3 | 0 | 2021-01-14 | -0.6 | 18.6 | 0 | 2020-01-14 | -9.3 | 27.3 | 0 | 2019-01-14 | -18.7 | 36.7 | 0 | 2018-01-14 | -24.3 | 42.3 | 0 | 2017-01-14 | -20.4 | 38.4 | 0 | 2016-01-14 | -15.3 | 33.3 | 0 | 30.18 | 0
2025-01-14 | -5.4 | 23.4 | 0 | 2024-01-14 | -5.3 | 23.3 | 0 | 2023-01-14 | -13.3 | 31.3 | 0 | 2022-01-14 | -13 | 31 | 0 | 2021-01-14 | -0.5 | 18.5 | 0 | 2020-01-14 | -9.2 | 27.2 | 0 | 2019-01-14 | -19.4 | 37.4 | 0 | 2018-01-14 | -24.9 | 42.9 | 0 | 2017-01-14 | -19.7 | 37.7 | 0 | 2016-01-14 | -14.7 | 32.7 | 0 | 30.54 | 0
2025-01-14 | -5.6 | 23.6 | 0 | 2024-01-14 | -5.4 | 23.4 | 0 | 2023-01-14 | -13.4 | 31.4 | 0 | 2022-01-14 | -15 | 33 | 0 | 2021-01-14 | -0.5 | 18.5 | 0 | 2020-01-14 | -8.7 | 26.7 | 0 | 2019-01-14 | -20.6 | 38.6 | 0 | 2018-01-14 | -26.8 | 44.8 | 0 | 2017-01-14 | -19.1 | 37.1 | 0 | 2016-01-14 | -14.8 | 32.8 | 0 | 30.99 | 0
2025-01-14 | -6 | 24 | 0 | 2024-01-14 | -5.5 | 23.5 | 0 | 2023-01-14 | -13 | 31 | 0 | 2022-01-14 | -16.4 | 34.4 | 0 | 2021-01-14 | -0.6 | 18.6 | 0 | 2020-01-14 | -8.1 | 26.1 | 0 | 2019-01-14 | -18.3 | 36.3 | 0 | 2018-01-14 | -23.5 | 41.5 | 0 | 2017-01-14 | -18.3 | 36.3 | 0 | 2016-01-14 | -13.8 | 31.8 | 0 | 30.35 | 0
2025-01-14 | -6.2 | 24.2 | 0 | 2024-01-14 | -4.3 | 22.3 | 0 | 2023-01-14 | -12.2 | 30.2 | 0 | 2022-01-14 | -16.7 | 34.7 | 0 | 2021-01-14 | -0.3 | 18.3 | 0 | 2020-01-14 | -7.7 | 25.7 | 0 | 2019-01-14 | -16.1 | 34.1 | 0 | 2018-01-14 | -20.7 | 38.7 | 0 | 2017-01-14 | -16.5 | 34.5 | 0 | 2016-01-14 | -12.5 | 30.5 | 0 | 29.32 | 0
2025-01-14 | -6 | 24 | 0 | 2024-01-14 | -3.2 | 21.2 | 0 | 2023-01-14 | -11.1 | 29.1 | 0 | 2022-01-14 | -17.2 | 35.2 | 0 | 2021-01-14 | -0.1 | 18.1 | 0 | 2020-01-14 | -7.7 | 25.7 | 0 | 2019-01-14 | -12.9 | 30.9 | 0 | 2018-01-14 | -19.5 | 37.5 | 0 | 2017-01-14 | -15.5 | 33.5 | 0 | 2016-01-14 | -10.7 | 28.7 | 0 | 28.39 | 0
2025-01-14 | -5.7 | 23.7 | 0 | 2024-01-14 | -3.2 | 21.2 | 0 | 2023-01-14 | -10.6 | 28.6 | 0 | 2022-01-14 | -17.3 | 35.3 | 0 | 2021-01-14 | 0 | 18 | 0 | 2020-01-14 | -7.2 | 25.2 | 0 | 2019-01-14 | -11.4 | 29.4 | 0 | 2018-01-14 | -18.6 | 36.6 | 0 | 2017-01-14 | -14.7 | 32.7 | 0 | 2016-01-14 | -9 | 27 | 0 | 27.77 | 0
2025-01-14 | -5.1 | 23.1 | 0 | 2024-01-14 | -4.9 | 22.9 | 0 | 2023-01-14 | -10.2 | 28.2 | 0 | 2022-01-14 | -16.8 | 34.8 | 0 | 2021-01-14 | 0 | 18 | 0 | 2020-01-14 | -6.5 | 24.5 | 0 | 2019-01-14 | -10.3 | 28.3 | 0 | 2018-01-14 | -17.7 | 35.7 | 0 | 2017-01-14 | -13.5 | 31.5 | 0 | 2016-01-14 | -7.7 | 25.7 | 0 | 27.27 | 0
2025-01-14 | -5.2 | 23.2 | 0 | 2024-01-14 | -5.4 | 23.4 | 0 | 2023-01-14 | -9.3 | 27.3 | 0 | 2022-01-14 | -16.8 | 34.8 | 0 | 2021-01-14 | 0.1 | 17.9 | 0 | 2020-01-14 | -5.8 | 23.8 | 0 | 2019-01-14 | -9.6 | 27.6 | 0 | 2018-01-14 | -16.9 | 34.9 | 0 | 2017-01-14 | -12.7 | 30.7 | 0 | 2016-01-14 | -6.9 | 24.9 | 0 | 26.85 | 0
2025-01-14 | -4.9 | 22.9 | 0 | 2024-01-14 | -4.2 | 22.2 | 0 | 2023-01-14 | -8.2 | 26.2 | 0 | 2022-01-14 | -16.9 | 34.9 | 0 | 2021-01-14 | 0.3 | 17.7 | 0 | 2020-01-14 | -6 | 24 | 0 | 2019-01-14 | -8.9 | 26.9 | 0 | 2018-01-14 | -16.2 | 34.2 | 0 | 2017-01-14 | -12.3 | 30.3 | 0 | 2016-01-14 | -6.7 | 24.7 | 0 | 26.4 | 0
2025-01-14 | -5.1 | 23.1 | 0 | 2024-01-14 | -5 | 23 | 0 | 2023-01-14 | -9 | 27 | 0 | 2022-01-14 | -17.1 | 35.1 | 0 | 2021-01-14 | 0.3 | 17.7 | 0 | 2020-01-14 | -6.1 | 24.1 | 0 | 2019-01-14 | -8.3 | 26.3 | 0 | 2018-01-14 | -16.5 | 34.5 | 0 | 2017-01-14 | -12.4 | 30.4 | 0 | 2016-01-14 | -6.6 | 24.6 | 0 | 26.58 | 0
2025-01-14 | -5.5 | 23.5 | 0 | 2024-01-14 | -5.4 | 23.4 | 0 | 2023-01-14 | -12.3 | 30.3 | 0 | 2022-01-14 | -18.3 | 36.3 | 0 | 2021-01-14 | 0.1 | 17.9 | 0 | 2020-01-14 | -6.5 | 24.5 | 0 | 2019-01-14 | -9 | 27 | 0 | 2018-01-14 | -17.6 | 35.6 | 0 | 2017-01-14 | -12.4 | 30.4 | 0 | 2016-01-14 | -7.4 | 25.4 | 0 | 27.43 | 0
2025-01-14 | -5.8 | 23.8 | 0 | 2024-01-14 | -5.6 | 23.6 | 0 | 2023-01-14 | -14 | 32 | 0 | 2022-01-14 | -19.3 | 37.3 | 0 | 2021-01-14 | -0.1 | 18.1 | 0 | 2020-01-14 | -6.8 | 24.8 | 0 | 2019-01-14 | -8.8 | 26.8 | 0 | 2018-01-14 | -20.4 | 38.4 | 0 | 2017-01-14 | -12.2 | 30.2 | 0 | 2016-01-14 | -6.9 | 24.9 | 0 | 27.99 | 0
2025-01-14 | -6.5 | 24.5 | 0 | 2024-01-14 | -6 | 24 | 0 | 2023-01-14 | -12.2 | 30.2 | 0 | 2022-01-14 | -19.9 | 37.9 | 0 | 2021-01-14 | -0.2 | 18.2 | 0 | 2020-01-14 | -7.1 | 25.1 | 0 | 2019-01-14 | -8.6 | 26.6 | 0 | 2018-01-14 | -20.6 | 38.6 | 0 | 2017-01-14 | -12.2 | 30.2 | 0 | 2016-01-14 | -9.2 | 27.2 | 0 | 28.25 | 0
2025-01-14 | -7.5 | 25.5 | 0 | 2024-01-14 | -7.1 | 25.1 | 0 | 2023-01-14 | -13.1 | 31.1 | 0 | 2022-01-14 | -20.5 | 38.5 | 0 | 2021-01-14 | -0.3 | 18.3 | 0 | 2020-01-14 | -7.2 | 25.2 | 0 | 2019-01-14 | -8.2 | 26.2 | 0 | 2018-01-14 | -21 | 39 | 0 | 2017-01-14 | -12.1 | 30.1 | 0 | 2016-01-14 | -9.1 | 27.1 | 0 | 28.61 | 0
2025-01-14 | -7.6 | 25.6 | 0 | 2024-01-14 | -8.1 | 26.1 | 0 | 2023-01-14 | -14.4 | 32.4 | 0 | 2022-01-14 | -21.1 | 39.1 | 0 | 2021-01-14 | -0.3 | 18.3 | 0 | 2020-01-14 | -7.4 | 25.4 | 0 | 2019-01-14 | -8 | 26 | 0 | 2018-01-14 | -21.7 | 39.7 | 0 | 2017-01-14 | -11.8 | 29.8 | 0 | 2016-01-14 | -10.2 | 28.2 | 0 | 29.06 | 0
2025-01-14 | -8 | 26 | 0 | 2024-01-14 | -8.1 | 26.1 | 0 | 2023-01-14 | -14.7 | 32.7 | 0 | 2022-01-14 | -21.7 | 39.7 | 0 | 2021-01-14 | -0.4 | 18.4 | 0 | 2020-01-14 | -7.3 | 25.3 | 0 | 2019-01-14 | -8 | 26 | 0 | 2018-01-14 | -22.3 | 40.3 | 0 | 2017-01-14 | -11.1 | 29.1 | 0 | 2016-01-14 | -9.3 | 27.3 | 0 | 29.09 | 0
2025-01-14 | -8.3 | 26.3 | 0 | 2024-01-14 | -8.3 | 26.3 | 0 | 2023-01-14 | -15.7 | 33.7 | 0 | 2022-01-14 | -22.4 | 40.4 | 0 | 2021-01-14 | -0.3 | 18.3 | 0 | 2020-01-14 | -7.2 | 25.2 | 0 | 2019-01-14 | -7.6 | 25.6 | 0 | 2018-01-14 | -22.8 | 40.8 | 0 | 2017-01-14 | -9.3 | 27.3 | 0 | 2016-01-14 | -10 | 28 | 0 | 29.19 | 0
2025-01-15 | -8.6 | 26.6 | 0 | 2024-01-15 | -8 | 26 | 0 | 2023-01-15 | -16.1 | 34.1 | 0 | 2022-01-15 | -23.1 | 41.1 | 0 | 2021-01-15 | -0.5 | 18.5 | 0 | 2020-01-15 | -7 | 25 | 0 | 2019-01-15 | -7.2 | 25.2 | 0 | 2018-01-15 | -23.2 | 41.2 | 0 | 2017-01-15 | -6.5 | 24.5 | 0 | 2016-01-15 | -11.1 | 29.1 | 0 | 29.13 | 0
2025-01-15 | -9.9 | 27.9 | 0 | 2024-01-15 | -7.5 | 25.5 | 0 | 2023-01-15 | -15.7 | 33.7 | 0 | 2022-01-15 | -23.7 | 41.7 | 0 | 2021-01-15 | -0.7 | 18.7 | 0 | 2020-01-15 | -6.7 | 24.7 | 0 | 2019-01-15 | -6.7 | 24.7 | 0 | 2018-01-15 | -23.6 | 41.6 | 0 | 2017-01-15 | -6.8 | 24.8 | 0 | 2016-01-15 | -11.7 | 29.7 | 0 | 29.3 | 0
2025-01-15 | -10.8 | 28.8 | 0 | 2024-01-15 | -8.9 | 26.9 | 0 | 2023-01-15 | -15.8 | 33.8 | 0 | 2022-01-15 | -24.2 | 42.2 | 0 | 2021-01-15 | -0.8 | 18.8 | 0 | 2020-01-15 | -6.5 | 24.5 | 0 | 2019-01-15 | -6.3 | 24.3 | 0 | 2018-01-15 | -24.2 | 42.2 | 0 | 2017-01-15 | -9.5 | 27.5 | 0 | 2016-01-15 | -12.4 | 30.4 | 0 | 29.94 | 0
2025-01-15 | -11.2 | 29.2 | 0 | 2024-01-15 | -10.3 | 28.3 | 0 | 2023-01-15 | -15 | 33 | 0 | 2022-01-15 | -25.2 | 43.2 | 0 | 2021-01-15 | -0.8 | 18.8 | 0 | 2020-01-15 | -6.1 | 24.1 | 0 | 2019-01-15 | -5.9 | 23.9 | 0 | 2018-01-15 | -23.8 | 41.8 | 0 | 2017-01-15 | -10.2 | 28.2 | 0 | 2016-01-15 | -13.5 | 31.5 | 0 | 30.2 | 0
2025-01-15 | -11.2 | 29.2 | 0 | 2024-01-15 | -9.8 | 27.8 | 0 | 2023-01-15 | -15.6 | 33.6 | 0 | 2022-01-15 | -25.3 | 43.3 | 0 | 2021-01-15 | -1.8 | 19.8 | 0 | 2020-01-15 | -5.7 | 23.7 | 0 | 2019-01-15 | -5.6 | 23.6 | 0 | 2018-01-15 | -24.1 | 42.1 | 0 | 2017-01-15 | -10.5 | 28.5 | 0 | 2016-01-15 | -14 | 32 | 0 | 30.36 | 0
2025-01-15 | -10.4 | 28.4 | 0 | 2024-01-15 | -10 | 28 | 0 | 2023-01-15 | -16.5 | 34.5 | 0 | 2022-01-15 | -25.9 | 43.9 | 0 | 2021-01-15 | -1.2 | 19.2 | 0 | 2020-01-15 | -5 | 23 | 0 | 2019-01-15 | -5.4 | 23.4 | 0 | 2018-01-15 | -24.1 | 42.1 | 0 | 2017-01-15 | -10.1 | 28.1 | 0 | 2016-01-15 | -13.4 | 31.4 | 0 | 30.2 | 0
2025-01-15 | -10 | 28 | 0 | 2024-01-15 | -10.6 | 28.6 | 0 | 2023-01-15 | -15.2 | 33.2 | 0 | 2022-01-15 | -26.5 | 44.5 | 0 | 2021-01-15 | -1.6 | 19.6 | 0 | 2020-01-15 | -4.4 | 22.4 | 0 | 2019-01-15 | -5.4 | 23.4 | 0 | 2018-01-15 | -23.8 | 41.8 | 0 | 2017-01-15 | -10.3 | 28.3 | 0 | 2016-01-15 | -13.9 | 31.9 | 0 | 30.17 | 0
2025-01-15 | -9.9 | 27.9 | 0 | 2024-01-15 | -11.4 | 29.4 | 0 | 2023-01-15 | -16.7 | 34.7 | 0 | 2022-01-15 | -26.6 | 44.6 | 0 | 2021-01-15 | -2 | 20 | 0 | 2020-01-15 | -4 | 22 | 0 | 2019-01-15 | -5.9 | 23.9 | 0 | 2018-01-15 | -23.5 | 41.5 | 0 | 2017-01-15 | -10.6 | 28.6 | 0 | 2016-01-15 | -13.8 | 31.8 | 0 | 30.44 | 0
2025-01-15 | -9.7 | 27.7 | 0 | 2024-01-15 | -11.6 | 29.6 | 0 | 2023-01-15 | -15.4 | 33.4 | 0 | 2022-01-15 | -26.6 | 44.6 | 0 | 2021-01-15 | -2.1 | 20.1 | 0 | 2020-01-15 | -3.9 | 21.9 | 0 | 2019-01-15 | -6.2 | 24.2 | 0 | 2018-01-15 | -22.6 | 40.6 | 0 | 2017-01-15 | -9.8 | 27.8 | 0 | 2016-01-15 | -13.5 | 31.5 | 0 | 30.14 | 0
2025-01-15 | -9.6 | 27.6 | 0 | 2024-01-15 | -11 | 29 | 0 | 2023-01-15 | -13.8 | 31.8 | 0 | 2022-01-15 | -25.8 | 43.8 | 0 | 2021-01-15 | -1.9 | 19.9 | 0 | 2020-01-15 | -3.5 | 21.5 | 0 | 2019-01-15 | -6.1 | 24.1 | 0 | 2018-01-15 | -21.8 | 39.8 | 0 | 2017-01-15 | -9.2 | 27.2 | 0 | 2016-01-15 | -12.6 | 30.6 | 0 | 29.53 | 0
2025-01-15 | -9.5 | 27.5 | 0 | 2024-01-15 | -9.5 | 27.5 | 0 | 2023-01-15 | -12.8 | 30.8 | 0 | 2022-01-15 | -25 | 43 | 0 | 2021-01-15 | -1.5 | 19.5 | 0 | 2020-01-15 | -2.5 | 20.5 | 0 | 2019-01-15 | -5.4 | 23.4 | 0 | 2018-01-15 | -19.9 | 37.9 | 0 | 2017-01-15 | -8.8 | 26.8 | 0 | 2016-01-15 | -11.4 | 29.4 | 0 | 28.63 | 0
2025-01-15 | -8.9 | 26.9 | 0 | 2024-01-15 | -8.8 | 26.8 | 0 | 2023-01-15 | -11.5 | 29.5 | 0 | 2022-01-15 | -23.9 | 41.9 | 0 | 2021-01-15 | -1.1 | 19.1 | 0 | 2020-01-15 | -0.8 | 18.8 | 0 | 2019-01-15 | -4.3 | 22.3 | 0 | 2018-01-15 | -18.5 | 36.5 | 0 | 2017-01-15 | -8.3 | 26.3 | 0 | 2016-01-15 | -10.6 | 28.6 | 0 | 27.67 | 0
2025-01-15 | -8 | 26 | 0 | 2024-01-15 | -7.8 | 25.8 | 0 | 2023-01-15 | -10.4 | 28.4 | 0 | 2022-01-15 | -22.6 | 40.6 | 0 | 2021-01-15 | -0.1 | 18.1 | 0 | 2020-01-15 | 0.5 | 17.5 | 0 | 2019-01-15 | -4 | 22 | 0 | 2018-01-15 | -17 | 35 | 0 | 2017-01-15 | -8.1 | 26.1 | 0 | 2016-01-15 | -10.3 | 28.3 | 0 | 26.78 | 0
2025-01-15 | -7.6 | 25.6 | 0 | 2024-01-15 | -7.4 | 25.4 | 0 | 2023-01-15 | -9.6 | 27.6 | 0 | 2022-01-15 | -21.5 | 39.5 | 0 | 2021-01-15 | 0.7 | 17.3 | 0 | 2020-01-15 | -0.1 | 18.1 | 0 | 2019-01-15 | -3.6 | 21.6 | 0 | 2018-01-15 | -16.9 | 34.9 | 0 | 2017-01-15 | -7.7 | 25.7 | 0 | 2016-01-15 | -9.9 | 27.9 | 0 | 26.36 | 0
2025-01-15 | -7.2 | 25.2 | 0 | 2024-01-15 | -7.4 | 25.4 | 0 | 2023-01-15 | -8.8 | 26.8 | 0 | 2022-01-15 | -20.2 | 38.2 | 0 | 2021-01-15 | 0.6 | 17.4 | 0 | 2020-01-15 | -0.1 | 18.1 | 0 | 2019-01-15 | -2.9 | 20.9 | 0 | 2018-01-15 | -16.3 | 34.3 | 0 | 2017-01-15 | -7.7 | 25.7 | 0 | 2016-01-15 | -9.7 | 27.7 | 0 | 25.97 | 0
2025-01-15 | -7.5 | 25.5 | 0 | 2024-01-15 | -7.2 | 25.2 | 0 | 2023-01-15 | -8.7 | 26.7 | 0 | 2022-01-15 | -20 | 38 | 0 | 2021-01-15 | 0.6 | 17.4 | 0 | 2020-01-15 | -0.4 | 18.4 | 0 | 2019-01-15 | -2.6 | 20.6 | 0 | 2018-01-15 | -16.1 | 34.1 | 0 | 2017-01-15 | -7.7 | 25.7 | 0 | 2016-01-15 | -9.1 | 27.1 | 0 | 25.87 | 0
2025-01-15 | -7.8 | 25.8 | 0 | 2024-01-15 | -7.7 | 25.7 | 0 | 2023-01-15 | -9.1 | 27.1 | 0 | 2022-01-15 | -20.9 | 38.9 | 0 | 2021-01-15 | 0.2 | 17.8 | 0 | 2020-01-15 | -0.8 | 18.8 | 0 | 2019-01-15 | -2.5 | 20.5 | 0 | 2018-01-15 | -16 | 34 | 0 | 2017-01-15 | -7.3 | 25.3 | 0 | 2016-01-15 | -9.1 | 27.1 | 0 | 26.1 | 0
2025-01-15 | -9.7 | 27.7 | 0 | 2024-01-15 | -8.9 | 26.9 | 0 | 2023-01-15 | -9.9 | 27.9 | 0 | 2022-01-15 | -22.1 | 40.1 | 0 | 2021-01-15 | 0.2 | 17.8 | 0 | 2020-01-15 | -0.5 | 18.5 | 0 | 2019-01-15 | -2.9 | 20.9 | 0 | 2018-01-15 | -16.4 | 34.4 | 0 | 2017-01-15 | -8.5 | 26.5 | 0 | 2016-01-15 | -9.2 | 27.2 | 0 | 26.79 | 0
2025-01-15 | -9.7 | 27.7 | 0 | 2024-01-15 | -9.7 | 27.7 | 0 | 2023-01-15 | -10.2 | 28.2 | 0 | 2022-01-15 | -21.9 | 39.9 | 0 | 2021-01-15 | -0.1 | 18.1 | 0 | 2020-01-15 | -0.7 | 18.7 | 0 | 2019-01-15 | -3.1 | 21.1 | 0 | 2018-01-15 | -16.6 | 34.6 | 0 | 2017-01-15 | -9.8 | 27.8 | 0 | 2016-01-15 | -9.3 | 27.3 | 0 | 27.11 | 0
2025-01-15 | -10.2 | 28.2 | 0 | 2024-01-15 | -10.4 | 28.4 | 0 | 2023-01-15 | -12.3 | 30.3 | 0 | 2022-01-15 | -23.3 | 41.3 | 0 | 2021-01-15 | -0.3 | 18.3 | 0 | 2020-01-15 | -1.3 | 19.3 | 0 | 2019-01-15 | -2.4 | 20.4 | 0 | 2018-01-15 | -16.5 | 34.5 | 0 | 2017-01-15 | -9.5 | 27.5 | 0 | 2016-01-15 | -9.6 | 27.6 | 0 | 27.58 | 0
2025-01-15 | -11.1 | 29.1 | 0 | 2024-01-15 | -11.4 | 29.4 | 0 | 2023-01-15 | -12.8 | 30.8 | 0 | 2022-01-15 | -23.1 | 41.1 | 0 | 2021-01-15 | -0.1 | 18.1 | 0 | 2020-01-15 | -1.6 | 19.6 | 0 | 2019-01-15 | -1.6 | 19.6 | 0 | 2018-01-15 | -17 | 35 | 0 | 2017-01-15 | -10.8 | 28.8 | 0 | 2016-01-15 | -9.7 | 27.7 | 0 | 27.92 | 0
2025-01-15 | -10.5 | 28.5 | 0 | 2024-01-15 | -12.1 | 30.1 | 0 | 2023-01-15 | -12.4 | 30.4 | 0 | 2022-01-15 | -23.8 | 41.8 | 0 | 2021-01-15 | -0.1 | 18.1 | 0 | 2020-01-15 | -1.6 | 19.6 | 0 | 2019-01-15 | -1.3 | 19.3 | 0 | 2018-01-15 | -16.5 | 34.5 | 0 | 2017-01-15 | -11.7 | 29.7 | 0 | 2016-01-15 | -9.4 | 27.4 | 0 | 27.94 | 0
2025-01-15 | -9.7 | 27.7 | 0 | 2024-01-15 | -11.4 | 29.4 | 0 | 2023-01-15 | -14.3 | 32.3 | 0 | 2022-01-15 | -23.2 | 41.2 | 0 | 2021-01-15 | 0 | 18 | 0 | 2020-01-15 | -1.8 | 19.8 | 0 | 2019-01-15 | -0.9 | 18.9 | 0 | 2018-01-15 | -16.1 | 34.1 | 0 | 2017-01-15 | -11.1 | 29.1 | 0 | 2016-01-15 | -9.3 | 27.3 | 0 | 27.78 | 0
2025-01-15 | -9.9 | 27.9 | 0 | 2024-01-15 | -10.8 | 28.8 | 0 | 2023-01-15 | -12.9 | 30.9 | 0 | 2022-01-15 | -25 | 43 | 0 | 2021-01-15 | 0 | 18 | 0 | 2020-01-15 | -2.1 | 20.1 | 0 | 2019-01-15 | -0.8 | 18.8 | 0 | 2018-01-15 | -15.6 | 33.6 | 0 | 2017-01-15 | -10.9 | 28.9 | 0 | 2016-01-15 | -8.9 | 26.9 | 0 | 27.69 | 0
2025-01-16 | -9 | 27 | 0 | 2024-01-16 | -10.9 | 28.9 | 0 | 2023-01-16 | -12.2 | 30.2 | 0 | 2022-01-16 | -25.8 | 43.8 | 0 | 2021-01-16 | -0.4 | 18.4 | 0 | 2020-01-16 | -1.9 | 19.9 | 0 | 2019-01-16 | -1.1 | 19.1 | 0 | 2018-01-16 | -15.3 | 33.3 | 0 | 2017-01-16 | -11.1 | 29.1 | 0 | 2016-01-16 | -8.3 | 26.3 | 0 | 27.6 | 0
2025-01-16 | -9.1 | 27.1 | 0 | 2024-01-16 | -11.4 | 29.4 | 0 | 2023-01-16 | -14.7 | 32.7 | 0 | 2022-01-16 | -25 | 43 | 0 | 2021-01-16 | -0.6 | 18.6 | 0 | 2020-01-16 | -2 | 20 | 0 | 2019-01-16 | -1.3 | 19.3 | 0 | 2018-01-16 | -15.2 | 33.2 | 0 | 2017-01-16 | -12 | 30 | 0 | 2016-01-16 | -8.1 | 26.1 | 0 | 27.94 | 0
2025-01-16 | -8.1 | 26.1 | 0 | 2024-01-16 | -11.3 | 29.3 | 0 | 2023-01-16 | -13.4 | 31.4 | 0 | 2022-01-16 | -26.4 | 44.4 | 0 | 2021-01-16 | -0.6 | 18.6 | 0 | 2020-01-16 | -2.1 | 20.1 | 0 | 2019-01-16 | -1.8 | 19.8 | 0 | 2018-01-16 | -15.1 | 33.1 | 0 | 2017-01-16 | -10.6 | 28.6 | 0 | 2016-01-16 | -7.8 | 25.8 | 0 | 27.72 | 0
2025-01-16 | -7.1 | 25.1 | 0 | 2024-01-16 | -11.2 | 29.2 | 0 | 2023-01-16 | -13.2 | 31.2 | 0 | 2022-01-16 | -25.4 | 43.4 | 0 | 2021-01-16 | -0.4 | 18.4 | 0 | 2020-01-16 | -2 | 20 | 0 | 2019-01-16 | -2 | 20 | 0 | 2018-01-16 | -15 | 33 | 0 | 2017-01-16 | -10.4 | 28.4 | 0 | 2016-01-16 | -7.6 | 25.6 | 0 | 27.43 | 0
2025-01-16 | -6.9 | 24.9 | 0 | 2024-01-16 | -11.3 | 29.3 | 0 | 2023-01-16 | -13.2 | 31.2 | 0 | 2022-01-16 | -27.5 | 45.5 | 0 | 2021-01-16 | -0.5 | 18.5 | 0 | 2020-01-16 | -2.2 | 20.2 | 0 | 2019-01-16 | -2 | 20 | 0 | 2018-01-16 | -14.9 | 32.9 | 0 | 2017-01-16 | -10.3 | 28.3 | 0 | 2016-01-16 | -7.5 | 25.5 | 0 | 27.63 | 0
2025-01-16 | -6.9 | 24.9 | 0 | 2024-01-16 | -11.5 | 29.5 | 0 | 2023-01-16 | -14.4 | 32.4 | 0 | 2022-01-16 | -25.1 | 43.1 | 0 | 2021-01-16 | -0.7 | 18.7 | 0 | 2020-01-16 | -2.2 | 20.2 | 0 | 2019-01-16 | -2.1 | 20.1 | 0 | 2018-01-16 | -14.9 | 32.9 | 0 | 2017-01-16 | -10.2 | 28.2 | 0 | 2016-01-16 | -7.6 | 25.6 | 0 | 27.56 | 0
2025-01-16 | -6.8 | 24.8 | 0 | 2024-01-16 | -10.8 | 28.8 | 0 | 2023-01-16 | -16.5 | 34.5 | 0 | 2022-01-16 | -26.7 | 44.7 | 0 | 2021-01-16 | -0.7 | 18.7 | 0 | 2020-01-16 | -2.2 | 20.2 | 0 | 2019-01-16 | -2.2 | 20.2 | 0 | 2018-01-16 | -14.9 | 32.9 | 0 | 2017-01-16 | -10.9 | 28.9 | 0 | 2016-01-16 | -7.6 | 25.6 | 0 | 27.93 | 0
2025-01-16 | -7 | 25 | 0 | 2024-01-16 | -10.8 | 28.8 | 0 | 2023-01-16 | -15.5 | 33.5 | 0 | 2022-01-16 | -26.3 | 44.3 | 0 | 2021-01-16 | -0.5 | 18.5 | 0 | 2020-01-16 | -2.3 | 20.3 | 0 | 2019-01-16 | -1.9 | 19.9 | 0 | 2018-01-16 | -14.8 | 32.8 | 0 | 2017-01-16 | -9.1 | 27.1 | 0 | 2016-01-16 | -7.3 | 25.3 | 0 | 27.55 | 0
2025-01-16 | -7.5 | 25.5 | 0 | 2024-01-16 | -10.6 | 28.6 | 0 | 2023-01-16 | -16.9 | 34.9 | 0 | 2022-01-16 | -26.4 | 44.4 | 0 | 2021-01-16 | -0.3 | 18.3 | 0 | 2020-01-16 | -2.6 | 20.6 | 0 | 2019-01-16 | -1.7 | 19.7 | 0 | 2018-01-16 | -15.7 | 33.7 | 0 | 2017-01-16 | -8.6 | 26.6 | 0 | 2016-01-16 | -7.1 | 25.1 | 0 | 27.74 | 0
2025-01-16 | -7.2 | 25.2 | 0 | 2024-01-16 | -10.3 | 28.3 | 0 | 2023-01-16 | -15 | 33 | 0 | 2022-01-16 | -24.1 | 42.1 | 0 | 2021-01-16 | -0.3 | 18.3 | 0 | 2020-01-16 | -2.6 | 20.6 | 0 | 2019-01-16 | -1.2 | 19.2 | 0 | 2018-01-16 | -14.8 | 32.8 | 0 | 2017-01-16 | -5.3 | 23.3 | 0 | 2016-01-16 | -6.8 | 24.8 | 0 | 26.76 | 0
2025-01-16 | -6.8 | 24.8 | 0 | 2024-01-16 | -9.4 | 27.4 | 0 | 2023-01-16 | -13.4 | 31.4 | 0 | 2022-01-16 | -21.8 | 39.8 | 0 | 2021-01-16 | -0.1 | 18.1 | 0 | 2020-01-16 | -2.3 | 20.3 | 0 | 2019-01-16 | -1 | 19 | 0 | 2018-01-16 | -14.1 | 32.1 | 0 | 2017-01-16 | -2 | 20 | 0 | 2016-01-16 | -6.3 | 24.3 | 0 | 25.72 | 0
2025-01-16 | -6.2 | 24.2 | 0 | 2024-01-16 | -8.9 | 26.9 | 0 | 2023-01-16 | -11.3 | 29.3 | 0 | 2022-01-16 | -19.2 | 37.2 | 0 | 2021-01-16 | 0 | 18 | 0 | 2020-01-16 | -2.3 | 20.3 | 0 | 2019-01-16 | -2.8 | 20.8 | 0 | 2018-01-16 | -13.3 | 31.3 | 0 | 2017-01-16 | -0.5 | 18.5 | 0 | 2016-01-16 | -5.8 | 23.8 | 0 | 25.03 | 0
2025-01-16 | -5.4 | 23.4 | 0 | 2024-01-16 | -8.8 | 26.8 | 0 | 2023-01-16 | -9.1 | 27.1 | 0 | 2022-01-16 | -17.4 | 35.4 | 0 | 2021-01-16 | 0 | 18 | 0 | 2020-01-16 | -2.5 | 20.5 | 0 | 2019-01-16 | -3 | 21 | 0 | 2018-01-16 | -12.4 | 30.4 | 0 | 2017-01-16 | 1 | 17 | 0 | 2016-01-16 | -5.6 | 23.6 | 0 | 24.32 | 0
2025-01-16 | -4.6 | 22.6 | 0 | 2024-01-16 | -8.3 | 26.3 | 0 | 2023-01-16 | -7 | 25 | 0 | 2022-01-16 | -16.1 | 34.1 | 0 | 2021-01-16 | 0.1 | 17.9 | 0 | 2020-01-16 | -3.8 | 21.8 | 0 | 2019-01-16 | -5.1 | 23.1 | 0 | 2018-01-16 | -12 | 30 | 0 | 2017-01-16 | 2 | 16 | 0 | 2016-01-16 | -4.9 | 22.9 | 0 | 23.97 | 0
2025-01-16 | -4.2 | 22.2 | 0 | 2024-01-16 | -8.1 | 26.1 | 0 | 2023-01-16 | -4.9 | 22.9 | 0 | 2022-01-16 | -15.2 | 33.2 | 0 | 2021-01-16 | 0.2 | 17.8 | 0 | 2020-01-16 | -4.7 | 22.7 | 0 | 2019-01-16 | -7.6 | 25.6 | 0 | 2018-01-16 | -11.8 | 29.8 | 0 | 2017-01-16 | 2.8 | 15.2 | 0 | 2016-01-16 | -3.9 | 21.9 | 0 | 23.74 | 0
2025-01-16 | -3.9 | 21.9 | 0 | 2024-01-16 | -8.2 | 26.2 | 0 | 2023-01-16 | -3.7 | 21.7 | 0 | 2022-01-16 | -14.9 | 32.9 | 0 | 2021-01-16 | 0.2 | 17.8 | 0 | 2020-01-16 | -5.5 | 23.5 | 0 | 2019-01-16 | -9.3 | 27.3 | 0 | 2018-01-16 | -11.6 | 29.6 | 0 | 2017-01-16 | 2.8 | 15.2 | 0 | 2016-01-16 | -3 | 21 | 0 | 23.71 | 0
2025-01-16 | -4.4 | 22.4 | 0 | 2024-01-16 | -8.3 | 26.3 | 0 | 2023-01-16 | -3.8 | 21.8 | 0 | 2022-01-16 | -14.6 | 32.6 | 0 | 2021-01-16 | 0 | 18 | 0 | 2020-01-16 | -6.8 | 24.8 | 0 | 2019-01-16 | -10.4 | 28.4 | 0 | 2018-01-16 | -11.1 | 29.1 | 0 | 2017-01-16 | 2.3 | 15.7 | 0 | 2016-01-16 | -3.5 | 21.5 | 0 | 24.06 | 0
2025-01-16 | -5 | 23 | 0 | 2024-01-16 | -9.2 | 27.2 | 0 | 2023-01-16 | -5.6 | 23.6 | 0 | 2022-01-16 | -17.3 | 35.3 | 0 | 2021-01-16 | -0.2 | 18.2 | 0 | 2020-01-16 | -7.8 | 25.8 | 0 | 2019-01-16 | -12.1 | 30.1 | 0 | 2018-01-16 | -11.5 | 29.5 | 0 | 2017-01-16 | 1.2 | 16.8 | 0 | 2016-01-16 | -3.5 | 21.5 | 0 | 25.1 | 0
2025-01-16 | -6 | 24 | 0 | 2024-01-16 | -13.1 | 31.1 | 0 | 2023-01-16 | -5.5 | 23.5 | 0 | 2022-01-16 | -17.7 | 35.7 | 0 | 2021-01-16 | -0.4 | 18.4 | 0 | 2020-01-16 | -9.3 | 27.3 | 0 | 2019-01-16 | -13.1 | 31.1 | 0 | 2018-01-16 | -12.9 | 30.9 | 0 | 2017-01-16 | 0.1 | 17.9 | 0 | 2016-01-16 | -3.5 | 21.5 | 0 | 26.14 | 0
2025-01-16 | -6.3 | 24.3 | 0 | 2024-01-16 | -11.5 | 29.5 | 0 | 2023-01-16 | -6.3 | 24.3 | 0 | 2022-01-16 | -17.4 | 35.4 | 0 | 2021-01-16 | -0.4 | 18.4 | 0 | 2020-01-16 | -11.2 | 29.2 | 0 | 2019-01-16 | -14 | 32 | 0 | 2018-01-16 | -11.9 | 29.9 | 0 | 2017-01-16 | -0.7 | 18.7 | 0 | 2016-01-16 | -3.6 | 21.6 | 0 | 26.33 | 0
2025-01-16 | -6.4 | 24.4 | 0 | 2024-01-16 | -13.7 | 31.7 | 0 | 2023-01-16 | -9.3 | 27.3 | 0 | 2022-01-16 | -17.7 | 35.7 | 0 | 2021-01-16 | -0.3 | 18.3 | 0 | 2020-01-16 | -12.3 | 30.3 | 0 | 2019-01-16 | -14.8 | 32.8 | 0 | 2018-01-16 | -14.4 | 32.4 | 0 | 2017-01-16 | -1.5 | 19.5 | 0 | 2016-01-16 | -4.9 | 22.9 | 0 | 27.53 | 0
2025-01-16 | -6.5 | 24.5 | 0 | 2024-01-16 | -12.4 | 30.4 | 0 | 2023-01-16 | -8.3 | 26.3 | 0 | 2022-01-16 | -17.4 | 35.4 | 0 | 2021-01-16 | -0.3 | 18.3 | 0 | 2020-01-16 | -13.5 | 31.5 | 0 | 2019-01-16 | -16 | 34 | 0 | 2018-01-16 | -12.4 | 30.4 | 0 | 2017-01-16 | -2.4 | 20.4 | 0 | 2016-01-16 | -5.4 | 23.4 | 0 | 27.46 | 0
2025-01-16 | -6.5 | 24.5 | 0 | 2024-01-16 | -12.3 | 30.3 | 0 | 2023-01-16 | -8.6 | 26.6 | 0 | 2022-01-16 | -17.6 | 35.6 | 0 | 2021-01-16 | -0.4 | 18.4 | 0 | 2020-01-16 | -14.1 | 32.1 | 0 | 2019-01-16 | -16.8 | 34.8 | 0 | 2018-01-16 | -12.5 | 30.5 | 0 | 2017-01-16 | -3 | 21 | 0 | 2016-01-16 | -5.8 | 23.8 | 0 | 27.76 | 0
2025-01-16 | -6.5 | 24.5 | 0 | 2024-01-16 | -13.3 | 31.3 | 0 | 2023-01-16 | -11.2 | 29.2 | 0 | 2022-01-16 | -17.2 | 35.2 | 0 | 2021-01-16 | -0.2 | 18.2 | 0 | 2020-01-16 | -15.2 | 33.2 | 0 | 2019-01-16 | -18.3 | 36.3 | 0 | 2018-01-16 | -12.4 | 30.4 | 0 | 2017-01-16 | -3.7 | 21.7 | 0 | 2016-01-16 | -6.7 | 24.7 | 0 | 28.47 | 0
2025-01-17 | -6.7 | 24.7 | 0 | 2024-01-17 | -14.5 | 32.5 | 0 | 2023-01-17 | -12.6 | 30.6 | 0 | 2022-01-17 | -16.5 | 34.5 | 0 | 2021-01-17 | -0.2 | 18.2 | 0 | 2020-01-17 | -16.2 | 34.2 | 0 | 2019-01-17 | -17.9 | 35.9 | 0 | 2018-01-17 | -16.2 | 34.2 | 0 | 2017-01-17 | -3.9 | 21.9 | 0 | 2016-01-17 | -8.3 | 26.3 | 0 | 29.3 | 0
2025-01-17 | -7 | 25 | 0 | 2024-01-17 | -15.1 | 33.1 | 0 | 2023-01-17 | -11.2 | 29.2 | 0 | 2022-01-17 | -16 | 34 | 0 | 2021-01-17 | -0.1 | 18.1 | 0 | 2020-01-17 | -17.1 | 35.1 | 0 | 2019-01-17 | -18.6 | 36.6 | 0 | 2018-01-17 | -15 | 33 | 0 | 2017-01-17 | -6 | 24 | 0 | 2016-01-17 | -10.2 | 28.2 | 0 | 29.63 | 0
2025-01-17 | -6.9 | 24.9 | 0 | 2024-01-17 | -15.8 | 33.8 | 0 | 2023-01-17 | -12.4 | 30.4 | 0 | 2022-01-17 | -15.6 | 33.6 | 0 | 2021-01-17 | 0 | 18 | 0 | 2020-01-17 | -17.9 | 35.9 | 0 | 2019-01-17 | -20.7 | 38.7 | 0 | 2018-01-17 | -17.5 | 35.5 | 0 | 2017-01-17 | -6.1 | 24.1 | 0 | 2016-01-17 | -11.6 | 29.6 | 0 | 30.45 | 0
2025-01-17 | -7.2 | 25.2 | 0 | 2024-01-17 | -15.2 | 33.2 | 0 | 2023-01-17 | -11.8 | 29.8 | 0 | 2022-01-17 | -14.6 | 32.6 | 0 | 2021-01-17 | 0.1 | 17.9 | 0 | 2020-01-17 | -18.6 | 36.6 | 0 | 2019-01-17 | -21.6 | 39.6 | 0 | 2018-01-17 | -15.1 | 33.1 | 0 | 2017-01-17 | -5.8 | 23.8 | 0 | 2016-01-17 | -13.4 | 31.4 | 0 | 30.32 | 0
2025-01-17 | -7.8 | 25.8 | 0 | 2024-01-17 | -15.2 | 33.2 | 0 | 2023-01-17 | -12.6 | 30.6 | 0 | 2022-01-17 | -13.5 | 31.5 | 0 | 2021-01-17 | 0.1 | 17.9 | 0 | 2020-01-17 | -19.2 | 37.2 | 0 | 2019-01-17 | -21.7 | 39.7 | 0 | 2018-01-17 | -14.2 | 32.2 | 0 | 2017-01-17 | -6.7 | 24.7 | 0 | 2016-01-17 | -13.8 | 31.8 | 0 | 30.46 | 0
2025-01-17 | -7.3 | 25.3 | 0 | 2024-01-17 | -16.1 | 34.1 | 0 | 2023-01-17 | -13.7 | 31.7 | 0 | 2022-01-17 | -11.9 | 29.9 | 0 | 2021-01-17 | -0.1 | 18.1 | 0 | 2020-01-17 | -19.7 | 37.7 | 0 | 2019-01-17 | -22.7 | 40.7 | 0 | 2018-01-17 | -13.3 | 31.3 | 0 | 2017-01-17 | -5.5 | 23.5 | 0 | 2016-01-17 | -16.1 | 34.1 | 0 | 30.64 | 0
2025-01-17 | -7 | 25 | 0 | 2024-01-17 | -16.7 | 34.7 | 0 | 2023-01-17 | -13.7 | 31.7 | 0 | 2022-01-17 | -10.1 | 28.1 | 0 | 2021-01-17 | -0.5 | 18.5 | 0 | 2020-01-17 | -20.2 | 38.2 | 0 | 2019-01-17 | -23 | 41 | 0 | 2018-01-17 | -13.4 | 31.4 | 0 | 2017-01-17 | -8.1 | 26.1 | 0 | 2016-01-17 | -16.1 | 34.1 | 0 | 30.88 | 0
2025-01-17 | -7.2 | 25.2 | 0 | 2024-01-17 | -16.4 | 34.4 | 0 | 2023-01-17 | -13.4 | 31.4 | 0 | 2022-01-17 | -8.3 | 26.3 | 0 | 2021-01-17 | -0.6 | 18.6 | 0 | 2020-01-17 | -20.6 | 38.6 | 0 | 2019-01-17 | -23.3 | 41.3 | 0 | 2018-01-17 | -13.1 | 31.1 | 0 | 2017-01-17 | -9.1 | 27.1 | 0 | 2016-01-17 | -13.6 | 31.6 | 0 | 30.56 | 0
2025-01-17 | -6.9 | 24.9 | 0 | 2024-01-17 | -15.3 | 33.3 | 0 | 2023-01-17 | -14.8 | 32.8 | 0 | 2022-01-17 | -6.5 | 24.5 | 0 | 2021-01-17 | -1.1 | 19.1 | 0 | 2020-01-17 | -20.8 | 38.8 | 0 | 2019-01-17 | -23.2 | 41.2 | 0 | 2018-01-17 | -12.9 | 30.9 | 0 | 2017-01-17 | -8.9 | 26.9 | 0 | 2016-01-17 | -13.6 | 31.6 | 0 | 30.4 | 0
2025-01-17 | -6.3 | 24.3 | 0 | 2024-01-17 | -14.8 | 32.8 | 0 | 2023-01-17 | -12.5 | 30.5 | 0 | 2022-01-17 | -7 | 25 | 0 | 2021-01-17 | -1.4 | 19.4 | 0 | 2020-01-17 | -20.5 | 38.5 | 0 | 2019-01-17 | -21.8 | 39.8 | 0 | 2018-01-17 | -12.2 | 30.2 | 0 | 2017-01-17 | -5.3 | 23.3 | 0 | 2016-01-17 | -12.4 | 30.4 | 0 | 29.42 | 0
2025-01-17 | -5.3 | 23.3 | 0 | 2024-01-17 | -13.9 | 31.9 | 0 | 2023-01-17 | -10.9 | 28.9 | 0 | 2022-01-17 | -6.3 | 24.3 | 0 | 2021-01-17 | -1.4 | 19.4 | 0 | 2020-01-17 | -19.7 | 37.7 | 0 | 2019-01-17 | -19.9 | 37.9 | 0 | 2018-01-17 | -11.5 | 29.5 | 0 | 2017-01-17 | -3.6 | 21.6 | 0 | 2016-01-17 | -11.7 | 29.7 | 0 | 28.42 | 0
2025-01-17 | -4.4 | 22.4 | 0 | 2024-01-17 | -12.9 | 30.9 | 0 | 2023-01-17 | -7.2 | 25.2 | 0 | 2022-01-17 | -5.7 | 23.7 | 0 | 2021-01-17 | -2.1 | 20.1 | 0 | 2020-01-17 | -19.1 | 37.1 | 0 | 2019-01-17 | -18.2 | 36.2 | 0 | 2018-01-17 | -10.2 | 28.2 | 0 | 2017-01-17 | -1.4 | 19.4 | 0 | 2016-01-17 | -10.5 | 28.5 | 0 | 27.17 | 0
2025-01-17 | -3.5 | 21.5 | 0 | 2024-01-17 | -12.2 | 30.2 | 0 | 2023-01-17 | -5.5 | 23.5 | 0 | 2022-01-17 | -5.3 | 23.3 | 0 | 2021-01-17 | -2.6 | 20.6 | 0 | 2020-01-17 | -18.4 | 36.4 | 0 | 2019-01-17 | -16.8 | 34.8 | 0 | 2018-01-17 | -8.9 | 26.9 | 0 | 2017-01-17 | -0.9 | 18.9 | 0 | 2016-01-17 | -9.2 | 27.2 | 0 | 26.33 | 0
2025-01-17 | -2.7 | 20.7 | 0 | 2024-01-17 | -11.3 | 29.3 | 0 | 2023-01-17 | -5 | 23 | 0 | 2022-01-17 | -4.5 | 22.5 | 0 | 2021-01-17 | -2.8 | 20.8 | 0 | 2020-01-17 | -17.4 | 35.4 | 0 | 2019-01-17 | -15.3 | 33.3 | 0 | 2018-01-17 | -7.1 | 25.1 | 0 | 2017-01-17 | -0.5 | 18.5 | 0 | 2016-01-17 | -8.2 | 26.2 | 0 | 25.48 | 0
2025-01-17 | -2.2 | 20.2 | 0 | 2024-01-17 | -11 | 29 | 0 | 2023-01-17 | -4.3 | 22.3 | 0 | 2022-01-17 | -4.9 | 22.9 | 0 | 2021-01-17 | -2.8 | 20.8 | 0 | 2020-01-17 | -16.4 | 34.4 | 0 | 2019-01-17 | -14.2 | 32.2 | 0 | 2018-01-17 | -5.9 | 23.9 | 0 | 2017-01-17 | -1.2 | 19.2 | 0 | 2016-01-17 | -8.1 | 26.1 | 0 | 25.1 | 0
2025-01-17 | -1.9 | 19.9 | 0 | 2024-01-17 | -10.3 | 28.3 | 0 | 2023-01-17 | -4.3 | 22.3 | 0 | 2022-01-17 | -4.6 | 22.6 | 0 | 2021-01-17 | -3.3 | 21.3 | 0 | 2020-01-17 | -16.5 | 34.5 | 0 | 2019-01-17 | -13.8 | 31.8 | 0 | 2018-01-17 | -5.5 | 23.5 | 0 | 2017-01-17 | -1.3 | 19.3 | 0 | 2016-01-17 | -7.7 | 25.7 | 0 | 24.92 | 0
2025-01-17 | -2.1 | 20.1 | 0 | 2024-01-17 | -10.4 | 28.4 | 0 | 2023-01-17 | -3.7 | 21.7 | 0 | 2022-01-17 | -5.5 | 23.5 | 0 | 2021-01-17 | -3.9 | 21.9 | 0 | 2020-01-17 | -16.3 | 34.3 | 0 | 2019-01-17 | -14.9 | 32.9 | 0 | 2018-01-17 | -5.8 | 23.8 | 0 | 2017-01-17 | -1.9 | 19.9 | 0 | 2016-01-17 | -7.4 | 25.4 | 0 | 25.19 | 0
2025-01-17 | -2.2 | 20.2 | 0 | 2024-01-17 | -9.4 | 27.4 | 0 | 2023-01-17 | -3.9 | 21.9 | 0 | 2022-01-17 | -6.9 | 24.9 | 0 | 2021-01-17 | -4.2 | 22.2 | 0 | 2020-01-17 | -17.2 | 35.2 | 0 | 2019-01-17 | -15.1 | 33.1 | 0 | 2018-01-17 | -6.3 | 24.3 | 0 | 2017-01-17 | -2.2 | 20.2 | 0 | 2016-01-17 | -7.4 | 25.4 | 0 | 25.48 | 0
2025-01-17 | -1.9 | 19.9 | 0 | 2024-01-17 | -9.2 | 27.2 | 0 | 2023-01-17 | -3.9 | 21.9 | 0 | 2022-01-17 | -7 | 25 | 0 | 2021-01-17 | -4.2 | 22.2 | 0 | 2020-01-17 | -17.9 | 35.9 | 0 | 2019-01-17 | -15.7 | 33.7 | 0 | 2018-01-17 | -6.8 | 24.8 | 0 | 2017-01-17 | -2.7 | 20.7 | 0 | 2016-01-17 | -7.7 | 25.7 | 0 | 25.7 | 0
2025-01-17 | -1.5 | 19.5 | 0 | 2024-01-17 | -9.8 | 27.8 | 0 | 2023-01-17 | -3.9 | 21.9 | 0 | 2022-01-17 | -6.7 | 24.7 | 0 | 2021-01-17 | -4.8 | 22.8 | 0 | 2020-01-17 | -18 | 36 | 0 | 2019-01-17 | -16 | 34 | 0 | 2018-01-17 | -7.2 | 25.2 | 0 | 2017-01-17 | -3.1 | 21.1 | 0 | 2016-01-17 | -7.4 | 25.4 | 0 | 25.84 | 0
2025-01-17 | -1 | 19 | 0 | 2024-01-17 | -10 | 28 | 0 | 2023-01-17 | -3.7 | 21.7 | 0 | 2022-01-17 | -7.2 | 25.2 | 0 | 2021-01-17 | -5.1 | 23.1 | 0 | 2020-01-17 | -17.7 | 35.7 | 0 | 2019-01-17 | -16.3 | 34.3 | 0 | 2018-01-17 | -7.5 | 25.5 | 0 | 2017-01-17 | -3 | 21 | 0 | 2016-01-17 | -7.3 | 25.3 | 0 | 25.88 | 0
2025-01-17 | -0.7 | 18.7 | 0 | 2024-01-17 | -10.4 | 28.4 | 0 | 2023-01-17 | -3.7 | 21.7 | 0 | 2022-01-17 | -7.5 | 25.5 | 0 | 2021-01-17 | -5 | 23 | 0 | 2020-01-17 | -17.7 | 35.7 | 0 | 2019-01-17 | -16.5 | 34.5 | 0 | 2018-01-17 | -7.6 | 25.6 | 0 | 2017-01-17 | -3.4 | 21.4 | 0 | 2016-01-17 | -7.3 | 25.3 | 0 | 25.98 | 0
2025-01-17 | -0.3 | 18.3 | 0 | 2024-01-17 | -10.9 | 28.9 | 0 | 2023-01-17 | -3.5 | 21.5 | 0 | 2022-01-17 | -7.3 | 25.3 | 0 | 2021-01-17 | -5.2 | 23.2 | 0 | 2020-01-17 | -17.8 | 35.8 | 0 | 2019-01-17 | -16.3 | 34.3 | 0 | 2018-01-17 | -6.8 | 24.8 | 0 | 2017-01-17 | -3.9 | 21.9 | 0 | 2016-01-17 | -7 | 25 | 0 | 25.9 | 0
2025-01-17 | 0.2 | 17.8 | 0 | 2024-01-17 | -11.2 | 29.2 | 0 | 2023-01-17 | -3.6 | 21.6 | 0 | 2022-01-17 | -8.2 | 26.2 | 0 | 2021-01-17 | -5.8 | 23.8 | 0 | 2020-01-17 | -18.8 | 36.8 | 0 | 2019-01-17 | -16.2 | 34.2 | 0 | 2018-01-17 | -7.4 | 25.4 | 0 | 2017-01-17 | -4.1 | 22.1 | 0 | 2016-01-17 | -6.8 | 24.8 | 0 | 26.19 | 0
2025-01-18 | 0.4 | 17.6 | 0 | 2024-01-18 | -11.3 | 29.3 | 0 | 2023-01-18 | -3.5 | 21.5 | 0 | 2022-01-18 | -9.1 | 27.1 | 0 | 2021-01-18 | -6.9 | 24.9 | 0 | 2020-01-18 | -18.1 | 36.1 | 0 | 2019-01-18 | -16 | 34 | 0 | 2018-01-18 | -7.7 | 25.7 | 0 | 2017-01-18 | -4.4 | 22.4 | 0 | 2016-01-18 | -7.1 | 25.1 | 0 | 26.37 | 0
2025-01-18 | 0.4 | 17.6 | 0 | 2024-01-18 | -12.2 | 30.2 | 0 | 2023-01-18 | -3.3 | 21.3 | 0 | 2022-01-18 | -10.1 | 28.1 | 0 | 2021-01-18 | -7.3 | 25.3 | 0 | 2020-01-18 | -18.9 | 36.9 | 0 | 2019-01-18 | -16.3 | 34.3 | 0 | 2018-01-18 | -7 | 25 | 0 | 2017-01-18 | -4.7 | 22.7 | 0 | 2016-01-18 | -7.2 | 25.2 | 0 | 26.66 | 0
2025-01-18 | 0.2 | 17.8 | 0 | 2024-01-18 | -12 | 30 | 0 | 2023-01-18 | -3.1 | 21.1 | 0 | 2022-01-18 | -10.1 | 28.1 | 0 | 2021-01-18 | -7.6 | 25.6 | 0 | 2020-01-18 | -18.7 | 36.7 | 0 | 2019-01-18 | -16.1 | 34.1 | 0 | 2018-01-18 | -6.7 | 24.7 | 0 | 2017-01-18 | -4.7 | 22.7 | 0 | 2016-01-18 | -7.2 | 25.2 | 0 | 26.6 | 0
2025-01-18 | 0 | 18 | 0 | 2024-01-18 | -11.8 | 29.8 | 0 | 2023-01-18 | -3.1 | 21.1 | 0 | 2022-01-18 | -10 | 28 | 0 | 2021-01-18 | -8.1 | 26.1 | 0 | 2020-01-18 | -18.2 | 36.2 | 0 | 2019-01-18 | -15.7 | 33.7 | 0 | 2018-01-18 | -6.1 | 24.1 | 0 | 2017-01-18 | -4.7 | 22.7 | 0 | 2016-01-18 | -7.1 | 25.1 | 0 | 26.48 | 0
2025-01-18 | 0.3 | 17.7 | 0 | 2024-01-18 | -11.7 | 29.7 | 0 | 2023-01-18 | -2.8 | 20.8 | 0 | 2022-01-18 | -11.1 | 29.1 | 0 | 2021-01-18 | -8.9 | 26.9 | 0 | 2020-01-18 | -18.1 | 36.1 | 0 | 2019-01-18 | -15.7 | 33.7 | 0 | 2018-01-18 | -6 | 24 | 0 | 2017-01-18 | -4.6 | 22.6 | 0 | 2016-01-18 | -7.4 | 25.4 | 0 | 26.6 | 0
2025-01-18 | 0.5 | 17.5 | 0 | 2024-01-18 | -11.7 | 29.7 | 0 | 2023-01-18 | -2.6 | 20.6 | 0 | 2022-01-18 | -12.2 | 30.2 | 0 | 2021-01-18 | -10.2 | 28.2 | 0 | 2020-01-18 | -17.5 | 35.5 | 0 | 2019-01-18 | -15.8 | 33.8 | 0 | 2018-01-18 | -5.9 | 23.9 | 0 | 2017-01-18 | -4.6 | 22.6 | 0 | 2016-01-18 | -8.1 | 26.1 | 0 | 26.81 | 0
2025-01-18 | 0.5 | 17.5 | 0 | 2024-01-18 | -11.6 | 29.6 | 0 | 2023-01-18 | -2.3 | 20.3 | 0 | 2022-01-18 | -13.7 | 31.7 | 0 | 2021-01-18 | -10.2 | 28.2 | 0 | 2020-01-18 | -17 | 35 | 0 | 2019-01-18 | -15.6 | 33.6 | 0 | 2018-01-18 | -6 | 24 | 0 | 2017-01-18 | -4.5 | 22.5 | 0 | 2016-01-18 | -8.7 | 26.7 | 0 | 26.91 | 0
2025-01-18 | 0.4 | 17.6 | 0 | 2024-01-18 | -11.6 | 29.6 | 0 | 2023-01-18 | -2.4 | 20.4 | 0 | 2022-01-18 | -14.9 | 32.9 | 0 | 2021-01-18 | -10 | 28 | 0 | 2020-01-18 | -16.8 | 34.8 | 0 | 2019-01-18 | -15.4 | 33.4 | 0 | 2018-01-18 | -6 | 24 | 0 | 2017-01-18 | -4.2 | 22.2 | 0 | 2016-01-18 | -9.4 | 27.4 | 0 | 27.03 | 0
2025-01-18 | 1.1 | 16.9 | 0 | 2024-01-18 | -12 | 30 | 0 | 2023-01-18 | -2.3 | 20.3 | 0 | 2022-01-18 | -15.6 | 33.6 | 0 | 2021-01-18 | -9.9 | 27.9 | 0 | 2020-01-18 | -17.1 | 35.1 | 0 | 2019-01-18 | -15.2 | 33.2 | 0 | 2018-01-18 | -6.1 | 24.1 | 0 | 2017-01-18 | -4.1 | 22.1 | 0 | 2016-01-18 | -11.9 | 29.9 | 0 | 27.31 | 0
2025-01-18 | 1.9 | 16.1 | 0 | 2024-01-18 | -11.5 | 29.5 | 0 | 2023-01-18 | -2 | 20 | 0 | 2022-01-18 | -15.5 | 33.5 | 0 | 2021-01-18 | -10 | 28 | 0 | 2020-01-18 | -16.3 | 34.3 | 0 | 2019-01-18 | -14.7 | 32.7 | 0 | 2018-01-18 | -6 | 24 | 0 | 2017-01-18 | -3.8 | 21.8 | 0 | 2016-01-18 | -13 | 31 | 0 | 27.09 | 0
2025-01-18 | 1.3 | 16.7 | 0 | 2024-01-18 | -10.2 | 28.2 | 0 | 2023-01-18 | -1.7 | 19.7 | 0 | 2022-01-18 | -15.5 | 33.5 | 0 | 2021-01-18 | -10.2 | 28.2 | 0 | 2020-01-18 | -15.3 | 33.3 | 0 | 2019-01-18 | -14 | 32 | 0 | 2018-01-18 | -5.7 | 23.7 | 0 | 2017-01-18 | -3.4 | 21.4 | 0 | 2016-01-18 | -12.9 | 30.9 | 0 | 26.76 | 0
2025-01-18 | 1.2 | 16.8 | 0 | 2024-01-18 | -10 | 28 | 0 | 2023-01-18 | -1.4 | 19.4 | 0 | 2022-01-18 | -15.7 | 33.7 | 0 | 2021-01-18 | -9.5 | 27.5 | 0 | 2020-01-18 | -14.9 | 32.9 | 0 | 2019-01-18 | -13.5 | 31.5 | 0 | 2018-01-18 | -5.3 | 23.3 | 0 | 2017-01-18 | -3.1 | 21.1 | 0 | 2016-01-18 | -13.5 | 31.5 | 0 | 26.57 | 0
2025-01-18 | 1 | 17 | 0 | 2024-01-18 | -9.2 | 27.2 | 0 | 2023-01-18 | -1.4 | 19.4 | 0 | 2022-01-18 | -15.5 | 33.5 | 0 | 2021-01-18 | -8.7 | 26.7 | 0 | 2020-01-18 | -14.6 | 32.6 | 0 | 2019-01-18 | -12.6 | 30.6 | 0 | 2018-01-18 | -5.2 | 23.2 | 0 | 2017-01-18 | -2.7 | 20.7 | 0 | 2016-01-18 | -13.7 | 31.7 | 0 | 26.26 | 0
2025-01-18 | 0.6 | 17.4 | 0 | 2024-01-18 | -8.3 | 26.3 | 0 | 2023-01-18 | -0.7 | 18.7 | 0 | 2022-01-18 | -14.9 | 32.9 | 0 | 2021-01-18 | -8.5 | 26.5 | 0 | 2020-01-18 | -14.2 | 32.2 | 0 | 2019-01-18 | -11.8 | 29.8 | 0 | 2018-01-18 | -4.9 | 22.9 | 0 | 2017-01-18 | -2.4 | 20.4 | 0 | 2016-01-18 | -13.4 | 31.4 | 0 | 25.85 | 0
2025-01-18 | 0.6 | 17.4 | 0 | 2024-01-18 | -8 | 26 | 0 | 2023-01-18 | -0.2 | 18.2 | 0 | 2022-01-18 | -14.8 | 32.8 | 0 | 2021-01-18 | -8.7 | 26.7 | 0 | 2020-01-18 | -14.6 | 32.6 | 0 | 2019-01-18 | -11.2 | 29.2 | 0 | 2018-01-18 | -4.7 | 22.7 | 0 | 2017-01-18 | -2.5 | 20.5 | 0 | 2016-01-18 | -13.1 | 31.1 | 0 | 25.72 | 0
2025-01-18 | 0.6 | 17.4 | 0 | 2024-01-18 | -7.6 | 25.6 | 0 | 2023-01-18 | 0.4 | 17.6 | 0 | 2022-01-18 | -15.1 | 33.1 | 0 | 2021-01-18 | -8.4 | 26.4 | 0 | 2020-01-18 | -14.5 | 32.5 | 0 | 2019-01-18 | -9.8 | 27.8 | 0 | 2018-01-18 | -4.7 | 22.7 | 0 | 2017-01-18 | -2.3 | 20.3 | 0 | 2016-01-18 | -13 | 31 | 0 | 25.44 | 0
2025-01-18 | 0.3 | 17.7 | 0 | 2024-01-18 | -7.6 | 25.6 | 0 | 2023-01-18 | 0.6 | 17.4 | 0 | 2022-01-18 | -15.8 | 33.8 | 0 | 2021-01-18 | -9.1 | 27.1 | 0 | 2020-01-18 | -14.7 | 32.7 | 0 | 2019-01-18 | -9.1 | 27.1 | 0 | 2018-01-18 | -4.7 | 22.7 | 0 | 2017-01-18 | -2.2 | 20.2 | 0 | 2016-01-18 | -13.7 | 31.7 | 0 | 25.6 | 0
2025-01-18 | 0.2 | 17.8 | 0 | 2024-01-18 | -7.9 | 25.9 | 0 | 2023-01-18 | -0.6 | 18.6 | 0 | 2022-01-18 | -16.3 | 34.3 | 0 | 2021-01-18 | -11.6 | 29.6 | 0 | 2020-01-18 | -14.8 | 32.8 | 0 | 2019-01-18 | -9.1 | 27.1 | 0 | 2018-01-18 | -4.9 | 22.9 | 0 | 2017-01-18 | -1.9 | 19.9 | 0 | 2016-01-18 | -13.9 | 31.9 | 0 | 26.08 | 0
2025-01-18 | 0.4 | 17.6 | 0 | 2024-01-18 | -11.3 | 29.3 | 0 | 2023-01-18 | -1 | 19 | 0 | 2022-01-18 | -17.1 | 35.1 | 0 | 2021-01-18 | -12.9 | 30.9 | 0 | 2020-01-18 | -14.8 | 32.8 | 0 | 2019-01-18 | -9.3 | 27.3 | 0 | 2018-01-18 | -5.1 | 23.1 | 0 | 2017-01-18 | -1.6 | 19.6 | 0 | 2016-01-18 | -14.2 | 32.2 | 0 | 26.69 | 0
2025-01-18 | 0.5 | 17.5 | 0 | 2024-01-18 | -10.7 | 28.7 | 0 | 2023-01-18 | -2.2 | 20.2 | 0 | 2022-01-18 | -18.9 | 36.9 | 0 | 2021-01-18 | -11.8 | 29.8 | 0 | 2020-01-18 | -15.2 | 33.2 | 0 | 2019-01-18 | -11.1 | 29.1 | 0 | 2018-01-18 | -5.1 | 23.1 | 0 | 2017-01-18 | -1.8 | 19.8 | 0 | 2016-01-18 | -14.6 | 32.6 | 0 | 27.09 | 0
2025-01-18 | -1 | 19 | 0 | 2024-01-18 | -8.9 | 26.9 | 0 | 2023-01-18 | -1.2 | 19.2 | 0 | 2022-01-18 | -19.2 | 37.2 | 0 | 2021-01-18 | -12.9 | 30.9 | 0 | 2020-01-18 | -15.6 | 33.6 | 0 | 2019-01-18 | -9.8 | 27.8 | 0 | 2018-01-18 | -5.2 | 23.2 | 0 | 2017-01-18 | -1.8 | 19.8 | 0 | 2016-01-18 | -15.3 | 33.3 | 0 | 27.09 | 0
2025-01-18 | -2.7 | 20.7 | 0 | 2024-01-18 | -10.6 | 28.6 | 0 | 2023-01-18 | -3 | 21 | 0 | 2022-01-18 | -20 | 38 | 0 | 2021-01-18 | -14.9 | 32.9 | 0 | 2020-01-18 | -15.1 | 33.1 | 0 | 2019-01-18 | -11.9 | 29.9 | 0 | 2018-01-18 | -5.1 | 23.1 | 0 | 2017-01-18 | -1.7 | 19.7 | 0 | 2016-01-18 | -15.8 | 33.8 | 0 | 28.08 | 0
2025-01-18 | -4.5 | 22.5 | 0 | 2024-01-18 | -12.6 | 30.6 | 0 | 2023-01-18 | -2.3 | 20.3 | 0 | 2022-01-18 | -19.6 | 37.6 | 0 | 2021-01-18 | -13.7 | 31.7 | 0 | 2020-01-18 | -14.9 | 32.9 | 0 | 2019-01-18 | -12.9 | 30.9 | 0 | 2018-01-18 | -5 | 23 | 0 | 2017-01-18 | -1.3 | 19.3 | 0 | 2016-01-18 | -15.9 | 33.9 | 0 | 28.27 | 0
2025-01-18 | -5.7 | 23.7 | 0 | 2024-01-18 | -11.7 | 29.7 | 0 | 2023-01-18 | -3.1 | 21.1 | 0 | 2022-01-18 | -19.4 | 37.4 | 0 | 2021-01-18 | -13.3 | 31.3 | 0 | 2020-01-18 | -15 | 33 | 0 | 2019-01-18 | -15.2 | 33.2 | 0 | 2018-01-18 | -4.9 | 22.9 | 0 | 2017-01-18 | -1 | 19 | 0 | 2016-01-18 | -16.3 | 34.3 | 0 | 28.56 | 0
2025-01-19 | -7.4 | 25.4 | 0 | 2024-01-19 | -9.5 | 27.5 | 0 | 2023-01-19 | -4.8 | 22.8 | 0 | 2022-01-19 | -17.4 | 35.4 | 0 | 2021-01-19 | -13.2 | 31.2 | 0 | 2020-01-19 | -14.7 | 32.7 | 0 | 2019-01-19 | -17.3 | 35.3 | 0 | 2018-01-19 | -5 | 23 | 0 | 2017-01-19 | -0.3 | 18.3 | 0 | 2016-01-19 | -16.6 | 34.6 | 0 | 28.62 | 0
2025-01-19 | -9 | 27 | 0 | 2024-01-19 | -10.7 | 28.7 | 0 | 2023-01-19 | -5.1 | 23.1 | 0 | 2022-01-19 | -16.6 | 34.6 | 0 | 2021-01-19 | -14.8 | 32.8 | 0 | 2020-01-19 | -14.3 | 32.3 | 0 | 2019-01-19 | -19.3 | 37.3 | 0 | 2018-01-19 | -5.1 | 23.1 | 0 | 2017-01-19 | 0 | 18 | 0 | 2016-01-19 | -17.3 | 35.3 | 0 | 29.22 | 0
2025-01-19 | -10.1 | 28.1 | 0 | 2024-01-19 | -12.1 | 30.1 | 0 | 2023-01-19 | -3.6 | 21.6 | 0 | 2022-01-19 | -17.2 | 35.2 | 0 | 2021-01-19 | -14.1 | 32.1 | 0 | 2020-01-19 | -13.6 | 31.6 | 0 | 2019-01-19 | -20.5 | 38.5 | 0 | 2018-01-19 | -5 | 23 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.6 | 35.6 | 0 | 29.36 | 0
2025-01-19 | -11 | 29 | 0 | 2024-01-19 | -13.2 | 31.2 | 0 | 2023-01-19 | -2.9 | 20.9 | 0 | 2022-01-19 | -16.7 | 34.7 | 0 | 2021-01-19 | -14 | 32 | 0 | 2020-01-19 | -13 | 31 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | -5.2 | 23.2 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.9 | 35.9 | 0 | 29.52 | 0
2025-01-19 | -11 | 29 | 0 | 2024-01-19 | -14 | 32 | 0 | 2023-01-19 | -1.9 | 19.9 | 0 | 2022-01-19 | -16.2 | 34.2 | 0 | 2021-01-19 | -14.7 | 32.7 | 0 | 2020-01-19 | -12.5 | 30.5 | 0 | 2019-01-19 | -22.3 | 40.3 | 0 | 2018-01-19 | -5.1 | 23.1 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.8 | 35.8 | 0 | 29.53 | 0
2025-01-19 | -11.2 | 29.2 | 0 | 2024-01-19 | -14.6 | 32.6 | 0 | 2023-01-19 | -1.6 | 19.6 | 0 | 2022-01-19 | -15.9 | 33.9 | 0 | 2021-01-19 | -15.3 | 33.3 | 0 | 2020-01-19 | -12 | 30 | 0 | 2019-01-19 | -23 | 41 | 0 | 2018-01-19 | -5.1 | 23.1 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.8 | 35.8 | 0 | 29.63 | 0
2025-01-19 | -11.8 | 29.8 | 0 | 2024-01-19 | -15.7 | 33.7 | 0 | 2023-01-19 | -1.8 | 19.8 | 0 | 2022-01-19 | -15.5 | 33.5 | 0 | 2021-01-19 | -15.7 | 33.7 | 0 | 2020-01-19 | -12.2 | 30.2 | 0 | 2019-01-19 | -23.6 | 41.6 | 0 | 2018-01-19 | -5 | 23 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.9 | 35.9 | 0 | 29.9 | 0
2025-01-19 | -13.3 | 31.3 | 0 | 2024-01-19 | -16.6 | 34.6 | 0 | 2023-01-19 | -1.8 | 19.8 | 0 | 2022-01-19 | -15.4 | 33.4 | 0 | 2021-01-19 | -15.3 | 33.3 | 0 | 2020-01-19 | -12.4 | 30.4 | 0 | 2019-01-19 | -23.9 | 41.9 | 0 | 2018-01-19 | -4.9 | 22.9 | 0 | 2017-01-19 | 0.1 | 17.9 | 0 | 2016-01-19 | -17.7 | 35.7 | 0 | 30.12 | 0
2025-01-19 | -14.7 | 32.7 | 0 | 2024-01-19 | -17.4 | 35.4 | 0 | 2023-01-19 | -2 | 20 | 0 | 2022-01-19 | -15.5 | 33.5 | 0 | 2021-01-19 | -14.9 | 32.9 | 0 | 2020-01-19 | -12.8 | 30.8 | 0 | 2019-01-19 | -24.2 | 42.2 | 0 | 2018-01-19 | -4.7 | 22.7 | 0 | 2017-01-19 | 0.2 | 17.8 | 0 | 2016-01-19 | -17.8 | 35.8 | 0 | 30.38 | 0
2025-01-19 | -14.8 | 32.8 | 0 | 2024-01-19 | -17.2 | 35.2 | 0 | 2023-01-19 | -1.7 | 19.7 | 0 | 2022-01-19 | -15.4 | 33.4 | 0 | 2021-01-19 | -13.4 | 31.4 | 0 | 2020-01-19 | -12.1 | 30.1 | 0 | 2019-01-19 | -23.7 | 41.7 | 0 | 2018-01-19 | -4.6 | 22.6 | 0 | 2017-01-19 | 0.5 | 17.5 | 0 | 2016-01-19 | -17.6 | 35.6 | 0 | 30 | 0
2025-01-19 | -14.3 | 32.3 | 0 | 2024-01-19 | -16.9 | 34.9 | 0 | 2023-01-19 | -1.6 | 19.6 | 0 | 2022-01-19 | -14.8 | 32.8 | 0 | 2021-01-19 | -12.4 | 30.4 | 0 | 2020-01-19 | -11.7 | 29.7 | 0 | 2019-01-19 | -23.2 | 41.2 | 0 | 2018-01-19 | -4.3 | 22.3 | 0 | 2017-01-19 | 0.6 | 17.4 | 0 | 2016-01-19 | -17 | 35 | 0 | 29.56 | 0
2025-01-19 | -13.4 | 31.4 | 0 | 2024-01-19 | -16.2 | 34.2 | 0 | 2023-01-19 | -1.4 | 19.4 | 0 | 2022-01-19 | -14 | 32 | 0 | 2021-01-19 | -10.6 | 28.6 | 0 | 2020-01-19 | -12.1 | 30.1 | 0 | 2019-01-19 | -22.6 | 40.6 | 0 | 2018-01-19 | -3.7 | 21.7 | 0 | 2017-01-19 | 0.9 | 17.1 | 0 | 2016-01-19 | -15.8 | 33.8 | 0 | 28.89 | 0
2025-01-19 | -13 | 31 | 0 | 2024-01-19 | -15.8 | 33.8 | 0 | 2023-01-19 | -1.2 | 19.2 | 0 | 2022-01-19 | -13.8 | 31.8 | 0 | 2021-01-19 | -8.5 | 26.5 | 0 | 2020-01-19 | -11.3 | 29.3 | 0 | 2019-01-19 | -21.7 | 39.7 | 0 | 2018-01-19 | -3.3 | 21.3 | 0 | 2017-01-19 | 1.2 | 16.8 | 0 | 2016-01-19 | -14.8 | 32.8 | 0 | 28.22 | 0
2025-01-19 | -12.9 | 30.9 | 0 | 2024-01-19 | -15.3 | 33.3 | 0 | 2023-01-19 | -1 | 19 | 0 | 2022-01-19 | -13.1 | 31.1 | 0 | 2021-01-19 | -8 | 26 | 0 | 2020-01-19 | -11.4 | 29.4 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | -3 | 21 | 0 | 2017-01-19 | 1.4 | 16.6 | 0 | 2016-01-19 | -13.4 | 31.4 | 0 | 27.82 | 0
2025-01-19 | -12.8 | 30.8 | 0 | 2024-01-19 | -14.7 | 32.7 | 0 | 2023-01-19 | -0.9 | 18.9 | 0 | 2022-01-19 | -12.4 | 30.4 | 0 | 2021-01-19 | -7.6 | 25.6 | 0 | 2020-01-19 | -10.6 | 28.6 | 0 | 2019-01-19 | -21 | 39 | 0 | 2018-01-19 | -2.6 | 20.6 | 0 | 2017-01-19 | 1.6 | 16.4 | 0 | 2016-01-19 | -11.9 | 29.9 | 0 | 27.29 | 0
2025-01-19 | -12.1 | 30.1 | 0 | 2024-01-19 | -13.9 | 31.9 | 0 | 2023-01-19 | -1.2 | 19.2 | 0 | 2022-01-19 | -12.2 | 30.2 | 0 | 2021-01-19 | -8 | 26 | 0 | 2020-01-19 | -10 | 28 | 0 | 2019-01-19 | -20.7 | 38.7 | 0 | 2018-01-19 | -2.3 | 20.3 | 0 | 2017-01-19 | 1.7 | 16.3 | 0 | 2016-01-19 | -10.9 | 28.9 | 0 | 26.96 | 0
2025-01-19 | -11.8 | 29.8 | 0 | 2024-01-19 | -14.7 | 32.7 | 0 | 2023-01-19 | -1.5 | 19.5 | 0 | 2022-01-19 | -11.3 | 29.3 | 0 | 2021-01-19 | -8.2 | 26.2 | 0 | 2020-01-19 | -9.8 | 27.8 | 0 | 2019-01-19 | -20.7 | 38.7 | 0 | 2018-01-19 | -1.9 | 19.9 | 0 | 2017-01-19 | 1.7 | 16.3 | 0 | 2016-01-19 | -10.6 | 28.6 | 0 | 26.88 | 0
2025-01-19 | -11.9 | 29.9 | 0 | 2024-01-19 | -14.9 | 32.9 | 0 | 2023-01-19 | -2.1 | 20.1 | 0 | 2022-01-19 | -10.4 | 28.4 | 0 | 2021-01-19 | -8.2 | 26.2 | 0 | 2020-01-19 | -10.4 | 28.4 | 0 | 2019-01-19 | -20.9 | 38.9 | 0 | 2018-01-19 | -1.3 | 19.3 | 0 | 2017-01-19 | 1.6 | 16.4 | 0 | 2016-01-19 | -10.5 | 28.5 | 0 | 26.9 | 0
2025-01-19 | -11.7 | 29.7 | 0 | 2024-01-19 | -16.2 | 34.2 | 0 | 2023-01-19 | -2.4 | 20.4 | 0 | 2022-01-19 | -10.4 | 28.4 | 0 | 2021-01-19 | -8.9 | 26.9 | 0 | 2020-01-19 | -10.3 | 28.3 | 0 | 2019-01-19 | -21.3 | 39.3 | 0 | 2018-01-19 | -0.9 | 18.9 | 0 | 2017-01-19 | 2 | 16 | 0 | 2016-01-19 | -10.5 | 28.5 | 0 | 27.06 | 0
2025-01-19 | -11.7 | 29.7 | 0 | 2024-01-19 | -16.2 | 34.2 | 0 | 2023-01-19 | -2.8 | 20.8 | 0 | 2022-01-19 | -10.3 | 28.3 | 0 | 2021-01-19 | -8.6 | 26.6 | 0 | 2020-01-19 | -11.1 | 29.1 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | -1.1 | 19.1 | 0 | 2017-01-19 | 1.1 | 16.9 | 0 | 2016-01-19 | -10.8 | 28.8 | 0 | 27.3 | 0
2025-01-19 | -11.6 | 29.6 | 0 | 2024-01-19 | -16.2 | 34.2 | 0 | 2023-01-19 | -3.9 | 21.9 | 0 | 2022-01-19 | -7.2 | 25.2 | 0 | 2021-01-19 | -8.8 | 26.8 | 0 | 2020-01-19 | -11.5 | 29.5 | 0 | 2019-01-19 | -21.7 | 39.7 | 0 | 2018-01-19 | -1 | 19 | 0 | 2017-01-19 | 0.9 | 17.1 | 0 | 2016-01-19 | -11.2 | 29.2 | 0 | 27.22 | 0
2025-01-19 | -11.9 | 29.9 | 0 | 2024-01-19 | -16.5 | 34.5 | 0 | 2023-01-19 | -4.3 | 22.3 | 0 | 2022-01-19 | -5.4 | 23.4 | 0 | 2021-01-19 | -11.1 | 29.1 | 0 | 2020-01-19 | -11.6 | 29.6 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | -0.9 | 18.9 | 0 | 2017-01-19 | 0.9 | 17.1 | 0 | 2016-01-19 | -11.4 | 29.4 | 0 | 27.37 | 0
2025-01-19 | -12.5 | 30.5 | 0 | 2024-01-19 | -16.8 | 34.8 | 0 | 2023-01-19 | -4.3 | 22.3 | 0 | 2022-01-19 | -3.9 | 21.9 | 0 | 2021-01-19 | -10.4 | 28.4 | 0 | 2020-01-19 | -12.5 | 30.5 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | -0.4 | 18.4 | 0 | 2017-01-19 | 0.6 | 17.4 | 0 | 2016-01-19 | -11.3 | 29.3 | 0 | 27.3 | 0
2025-01-19 | -12.9 | 30.9 | 0 | 2024-01-19 | -17.4 | 35.4 | 0 | 2023-01-19 | -4 | 22 | 0 | 2022-01-19 | -7.3 | 25.3 | 0 | 2021-01-19 | -10.8 | 28.8 | 0 | 2020-01-19 | -13.6 | 31.6 | 0 | 2019-01-19 | -21.5 | 39.5 | 0 | 2018-01-19 | 0 | 18 | 0 | 2017-01-19 | 0.7 | 17.3 | 0 | 2016-01-19 | -11.4 | 29.4 | 0 | 27.82 | 0
2025-01-20 | -13.4 | 31.4 | 0 | 2024-01-20 | -17.5 | 35.5 | 0 | 2023-01-20 | -3.8 | 21.8 | 0 | 2022-01-20 | -10.1 | 28.1 | 0 | 2021-01-20 | -10.5 | 28.5 | 0 | 2020-01-20 | -14.3 | 32.3 | 0 | 2019-01-20 | -21.2 | 39.2 | 0 | 2018-01-20 | 0.3 | 17.7 | 0 | 2017-01-20 | 0.4 | 17.6 | 0 | 2016-01-20 | -11.2 | 29.2 | 0 | 28.13 | 0
2025-01-20 | -14 | 32 | 0 | 2024-01-20 | -17.1 | 35.1 | 0 | 2023-01-20 | -3.4 | 21.4 | 0 | 2022-01-20 | -12.2 | 30.2 | 0 | 2021-01-20 | -10.9 | 28.9 | 0 | 2020-01-20 | -14.6 | 32.6 | 0 | 2019-01-20 | -21.2 | 39.2 | 0 | 2018-01-20 | -0.4 | 18.4 | 0 | 2017-01-20 | 0.5 | 17.5 | 0 | 2016-01-20 | -10.2 | 28.2 | 0 | 28.35 | 0
2025-01-20 | -15 | 33 | 0 | 2024-01-20 | -17 | 35 | 0 | 2023-01-20 | -3.5 | 21.5 | 0 | 2022-01-20 | -13.9 | 31.9 | 0 | 2021-01-20 | -10.7 | 28.7 | 0 | 2020-01-20 | -15.4 | 33.4 | 0 | 2019-01-20 | -21 | 39 | 0 | 2018-01-20 | 1 | 17 | 0 | 2017-01-20 | 0.5 | 17.5 | 0 | 2016-01-20 | -10.2 | 28.2 | 0 | 28.52 | 0
2025-01-20 | -15.7 | 33.7 | 0 | 2024-01-20 | -16.8 | 34.8 | 0 | 2023-01-20 | -3.4 | 21.4 | 0 | 2022-01-20 | -16 | 34 | 0 | 2021-01-20 | -10.8 | 28.8 | 0 | 2020-01-20 | -15.6 | 33.6 | 0 | 2019-01-20 | -20.5 | 38.5 | 0 | 2018-01-20 | 1.3 | 16.7 | 0 | 2017-01-20 | 0.4 | 17.6 | 0 | 2016-01-20 | -10.5 | 28.5 | 0 | 28.76 | 0
2025-01-20 | -16.4 | 34.4 | 0 | 2024-01-20 | -16.4 | 34.4 | 0 | 2023-01-20 | -3.2 | 21.2 | 0 | 2022-01-20 | -17.3 | 35.3 | 0 | 2021-01-20 | -10.1 | 28.1 | 0 | 2020-01-20 | -17.5 | 35.5 | 0 | 2019-01-20 | -19.5 | 37.5 | 0 | 2018-01-20 | 1.9 | 16.1 | 0 | 2017-01-20 | 0.2 | 17.8 | 0 | 2016-01-20 | -10.8 | 28.8 | 0 | 28.91 | 0
2025-01-20 | -17.4 | 35.4 | 0 | 2024-01-20 | -16.2 | 34.2 | 0 | 2023-01-20 | -3 | 21 | 0 | 2022-01-20 | -18.2 | 36.2 | 0 | 2021-01-20 | -10.3 | 28.3 | 0 | 2020-01-20 | -17.7 | 35.7 | 0 | 2019-01-20 | -18.9 | 36.9 | 0 | 2018-01-20 | 2.1 | 15.9 | 0 | 2017-01-20 | 0.2 | 17.8 | 0 | 2016-01-20 | -11 | 29 | 0 | 29.04 | 0
2025-01-20 | -18.4 | 36.4 | 0 | 2024-01-20 | -15.9 | 33.9 | 0 | 2023-01-20 | -2.8 | 20.8 | 0 | 2022-01-20 | -19.7 | 37.7 | 0 | 2021-01-20 | -9.1 | 27.1 | 0 | 2020-01-20 | -18.4 | 36.4 | 0 | 2019-01-20 | -18.4 | 36.4 | 0 | 2018-01-20 | 2.1 | 15.9 | 0 | 2017-01-20 | 0.2 | 17.8 | 0 | 2016-01-20 | -11.3 | 29.3 | 0 | 29.17 | 0
2025-01-20 | -18.8 | 36.8 | 0 | 2024-01-20 | -15.7 | 33.7 | 0 | 2023-01-20 | -2.8 | 20.8 | 0 | 2022-01-20 | -20.2 | 38.2 | 0 | 2021-01-20 | -9.2 | 27.2 | 0 | 2020-01-20 | -18.2 | 36.2 | 0 | 2019-01-20 | -19.2 | 37.2 | 0 | 2018-01-20 | 2.1 | 15.9 | 0 | 2017-01-20 | 0.3 | 17.7 | 0 | 2016-01-20 | -11.6 | 29.6 | 0 | 29.33 | 0
2025-01-20 | -19.7 | 37.7 | 0 | 2024-01-20 | -15.4 | 33.4 | 0 | 2023-01-20 | -2.6 | 20.6 | 0 | 2022-01-20 | -20.9 | 38.9 | 0 | 2021-01-20 | -9.5 | 27.5 | 0 | 2020-01-20 | -18.1 | 36.1 | 0 | 2019-01-20 | -19.2 | 37.2 | 0 | 2018-01-20 | 1.8 | 16.2 | 0 | 2017-01-20 | 0.8 | 17.2 | 0 | 2016-01-20 | -11.5 | 29.5 | 0 | 29.43 | 0
2025-01-20 | -18.3 | 36.3 | 0 | 2024-01-20 | -15.1 | 33.1 | 0 | 2023-01-20 | -2.5 | 20.5 | 0 | 2022-01-20 | -20.5 | 38.5 | 0 | 2021-01-20 | -10.3 | 28.3 | 0 | 2020-01-20 | -17.4 | 35.4 | 0 | 2019-01-20 | -19.2 | 37.2 | 0 | 2018-01-20 | 2.2 | 15.8 | 0 | 2017-01-20 | 0.7 | 17.3 | 0 | 2016-01-20 | -11 | 29 | 0 | 29.14 | 0
2025-01-20 | -17.9 | 35.9 | 0 | 2024-01-20 | -14.7 | 32.7 | 0 | 2023-01-20 | -2.3 | 20.3 | 0 | 2022-01-20 | -19.9 | 37.9 | 0 | 2021-01-20 | -10.7 | 28.7 | 0 | 2020-01-20 | -16.4 | 34.4 | 0 | 2019-01-20 | -18.9 | 36.9 | 0 | 2018-01-20 | 2.4 | 15.6 | 0 | 2017-01-20 | 0.7 | 17.3 | 0 | 2016-01-20 | -10.2 | 28.2 | 0 | 28.79 | 0
2025-01-20 | -17.3 | 35.3 | 0 | 2024-01-20 | -14 | 32 | 0 | 2023-01-20 | -1.9 | 19.9 | 0 | 2022-01-20 | -19.3 | 37.3 | 0 | 2021-01-20 | -11.3 | 29.3 | 0 | 2020-01-20 | -15.2 | 33.2 | 0 | 2019-01-20 | -19 | 37 | 0 | 2018-01-20 | 2.6 | 15.4 | 0 | 2017-01-20 | 1 | 17 | 0 | 2016-01-20 | -8.9 | 26.9 | 0 | 28.33 | 0
2025-01-20 | -16.5 | 34.5 | 0 | 2024-01-20 | -13 | 31 | 0 | 2023-01-20 | -1.6 | 19.6 | 0 | 2022-01-20 | -18.5 | 36.5 | 0 | 2021-01-20 | -10.9 | 28.9 | 0 | 2020-01-20 | -14.1 | 32.1 | 0 | 2019-01-20 | -19 | 37 | 0 | 2018-01-20 | 3.3 | 14.7 | 0 | 2017-01-20 | 1.2 | 16.8 | 0 | 2016-01-20 | -8.4 | 26.4 | 0 | 27.75 | 0
2025-01-20 | -15.9 | 33.9 | 0 | 2024-01-20 | -12.6 | 30.6 | 0 | 2023-01-20 | -1.3 | 19.3 | 0 | 2022-01-20 | -17.9 | 35.9 | 0 | 2021-01-20 | -10.7 | 28.7 | 0 | 2020-01-20 | -12.5 | 30.5 | 0 | 2019-01-20 | -18 | 36 | 0 | 2018-01-20 | 4.4 | 13.6 | 0 | 2017-01-20 | 1 | 17 | 0 | 2016-01-20 | -6.7 | 24.7 | 0 | 27.02 | 0
2025-01-20 | -15.6 | 33.6 | 0 | 2024-01-20 | -12.1 | 30.1 | 0 | 2023-01-20 | -1.3 | 19.3 | 0 | 2022-01-20 | -17.9 | 35.9 | 0 | 2021-01-20 | -10.4 | 28.4 | 0 | 2020-01-20 | -11 | 29 | 0 | 2019-01-20 | -17.5 | 35.5 | 0 | 2018-01-20 | 4.4 | 13.6 | 0 | 2017-01-20 | 1.1 | 16.9 | 0 | 2016-01-20 | -6.2 | 24.2 | 0 | 26.65 | 0
2025-01-20 | -15.3 | 33.3 | 0 | 2024-01-20 | -12 | 30 | 0 | 2023-01-20 | -1.3 | 19.3 | 0 | 2022-01-20 | -17.8 | 35.8 | 0 | 2021-01-20 | -11 | 29 | 0 | 2020-01-20 | -10.2 | 28.2 | 0 | 2019-01-20 | -17.6 | 35.6 | 0 | 2018-01-20 | 5.1 | 12.9 | 0 | 2017-01-20 | 0.8 | 17.2 | 0 | 2016-01-20 | -5.7 | 23.7 | 0 | 26.5 | 0
2025-01-20 | -14.9 | 32.9 | 0 | 2024-01-20 | -11.7 | 29.7 | 0 | 2023-01-20 | -1.4 | 19.4 | 0 | 2022-01-20 | -18.9 | 36.9 | 0 | 2021-01-20 | -11.8 | 29.8 | 0 | 2020-01-20 | -10.5 | 28.5 | 0 | 2019-01-20 | -18.5 | 36.5 | 0 | 2018-01-20 | 5 | 13 | 0 | 2017-01-20 | 0.9 | 17.1 | 0 | 2016-01-20 | -6.3 | 24.3 | 0 | 26.81 | 0
2025-01-20 | -15.4 | 33.4 | 0 | 2024-01-20 | -11.7 | 29.7 | 0 | 2023-01-20 | -1.7 | 19.7 | 0 | 2022-01-20 | -19.5 | 37.5 | 0 | 2021-01-20 | -13.3 | 31.3 | 0 | 2020-01-20 | -12 | 30 | 0 | 2019-01-20 | -19.4 | 37.4 | 0 | 2018-01-20 | 4.9 | 13.1 | 0 | 2017-01-20 | 1 | 17 | 0 | 2016-01-20 | -8 | 26 | 0 | 27.51 | 0
2025-01-20 | -16.9 | 34.9 | 0 | 2024-01-20 | -11.9 | 29.9 | 0 | 2023-01-20 | -1.8 | 19.8 | 0 | 2022-01-20 | -21.1 | 39.1 | 0 | 2021-01-20 | -12.9 | 30.9 | 0 | 2020-01-20 | -12.9 | 30.9 | 0 | 2019-01-20 | -20.2 | 38.2 | 0 | 2018-01-20 | 3.6 | 14.4 | 0 | 2017-01-20 | 0.8 | 17.2 | 0 | 2016-01-20 | -9.1 | 27.1 | 0 | 28.24 | 0
2025-01-20 | -17.9 | 35.9 | 0 | 2024-01-20 | -12.1 | 30.1 | 0 | 2023-01-20 | -2.2 | 20.2 | 0 | 2022-01-20 | -20.1 | 38.1 | 0 | 2021-01-20 | -14.8 | 32.8 | 0 | 2020-01-20 | -13.4 | 31.4 | 0 | 2019-01-20 | -20.8 | 38.8 | 0 | 2018-01-20 | 3.3 | 14.7 | 0 | 2017-01-20 | 0.8 | 17.2 | 0 | 2016-01-20 | -9.5 | 27.5 | 0 | 28.67 | 0
2025-01-20 | -17.5 | 35.5 | 0 | 2024-01-20 | -12.6 | 30.6 | 0 | 2023-01-20 | -2.1 | 20.1 | 0 | 2022-01-20 | -21.9 | 39.9 | 0 | 2021-01-20 | -16.1 | 34.1 | 0 | 2020-01-20 | -14.1 | 32.1 | 0 | 2019-01-20 | -21.2 | 39.2 | 0 | 2018-01-20 | 2.6 | 15.4 | 0 | 2017-01-20 | 0.5 | 17.5 | 0 | 2016-01-20 | -10.3 | 28.3 | 0 | 29.27 | 0
2025-01-20 | -18.5 | 36.5 | 0 | 2024-01-20 | -12.9 | 30.9 | 0 | 2023-01-20 | -2.2 | 20.2 | 0 | 2022-01-20 | -23.7 | 41.7 | 0 | 2021-01-20 | -17.5 | 35.5 | 0 | 2020-01-20 | -17.8 | 35.8 | 0 | 2019-01-20 | -21.6 | 39.6 | 0 | 2018-01-20 | 2.2 | 15.8 | 0 | 2017-01-20 | 0.4 | 17.6 | 0 | 2016-01-20 | -11.2 | 29.2 | 0 | 30.28 | 0
2025-01-20 | -16.4 | 34.4 | 0 | 2024-01-20 | -13.1 | 31.1 | 0 | 2023-01-20 | -2.4 | 20.4 | 0 | 2022-01-20 | -22 | 40 | 0 | 2021-01-20 | -17.5 | 35.5 | 0 | 2020-01-20 | -15 | 33 | 0 | 2019-01-20 | -21.5 | 39.5 | 0 | 2018-01-20 | 2 | 16 | 0 | 2017-01-20 | 0.3 | 17.7 | 0 | 2016-01-20 | -11.9 | 29.9 | 0 | 29.75 | 0
2025-01-20 | -16.6 | 34.6 | 0 | 2024-01-20 | -13.2 | 31.2 | 0 | 2023-01-20 | -2.2 | 20.2 | 0 | 2022-01-20 | -23.4 | 41.4 | 0 | 2021-01-20 | -15.7 | 33.7 | 0 | 2020-01-20 | -16.3 | 34.3 | 0 | 2019-01-20 | -21.9 | 39.9 | 0 | 2018-01-20 | 1.4 | 16.6 | 0 | 2017-01-20 | 0.3 | 17.7 | 0 | 2016-01-20 | -13.4 | 31.4 | 0 | 30.1 | 0
2025-01-21 | -15.9 | 33.9 | 0 | 2024-01-21 | -14.1 | 32.1 | 0 | 2023-01-21 | -3 | 21 | 0 | 2022-01-21 | -24.8 | 42.8 | 0 | 2021-01-21 | -16.2 | 34.2 | 0 | 2020-01-21 | -16.7 | 34.7 | 0 | 2019-01-21 | -22.5 | 40.5 | 0 | 2018-01-21 | 1.1 | 16.9 | 0 | 2017-01-21 | 0.1 | 17.9 | 0 | 2016-01-21 | -12.2 | 30.2 | 0 | 30.42 | 0
2025-01-21 | -16.3 | 34.3 | 0 | 2024-01-21 | -14.8 | 32.8 | 0 | 2023-01-21 | -2.9 | 20.9 | 0 | 2022-01-21 | -24.8 | 42.8 | 0 | 2021-01-21 | -14.2 | 32.2 | 0 | 2020-01-21 | -17.2 | 35.2 | 0 | 2019-01-21 | -22.7 | 40.7 | 0 | 2018-01-21 | 0.4 | 17.6 | 0 | 2017-01-21 | 0.3 | 17.7 | 0 | 2016-01-21 | -13.1 | 31.1 | 0 | 30.53 | 0
2025-01-21 | -16 | 34 | 0 | 2024-01-21 | -15.1 | 33.1 | 0 | 2023-01-21 | -2.7 | 20.7 | 0 | 2022-01-21 | -24.7 | 42.7 | 0 | 2021-01-21 | -13.4 | 31.4 | 0 | 2020-01-21 | -16.2 | 34.2 | 0 | 2019-01-21 | -23 | 41 | 0 | 2018-01-21 | 0.5 | 17.5 | 0 | 2017-01-21 | 0.2 | 17.8 | 0 | 2016-01-21 | -13.6 | 31.6 | 0 | 30.4 | 0
2025-01-21 | -16.5 | 34.5 | 0 | 2024-01-21 | -15.4 | 33.4 | 0 | 2023-01-21 | -3 | 21 | 0 | 2022-01-21 | -25.2 | 43.2 | 0 | 2021-01-21 | -13.3 | 31.3 | 0 | 2020-01-21 | -16.6 | 34.6 | 0 | 2019-01-21 | -23.2 | 41.2 | 0 | 2018-01-21 | -0.1 | 18.1 | 0 | 2017-01-21 | 0.2 | 17.8 | 0 | 2016-01-21 | -14.3 | 32.3 | 0 | 30.74 | 0
2025-01-21 | -17.8 | 35.8 | 0 | 2024-01-21 | -16 | 34 | 0 | 2023-01-21 | -3.1 | 21.1 | 0 | 2022-01-21 | -25.9 | 43.9 | 0 | 2021-01-21 | -13.8 | 31.8 | 0 | 2020-01-21 | -18.1 | 36.1 | 0 | 2019-01-21 | -23.1 | 41.1 | 0 | 2018-01-21 | -0.4 | 18.4 | 0 | 2017-01-21 | 0 | 18 | 0 | 2016-01-21 | -12.4 | 30.4 | 0 | 31.06 | 0
2025-01-21 | -19 | 37 | 0 | 2024-01-21 | -17.4 | 35.4 | 0 | 2023-01-21 | -3.7 | 21.7 | 0 | 2022-01-21 | -26.8 | 44.8 | 0 | 2021-01-21 | -13.1 | 31.1 | 0 | 2020-01-21 | -18.1 | 36.1 | 0 | 2019-01-21 | -23 | 41 | 0 | 2018-01-21 | -0.6 | 18.6 | 0 | 2017-01-21 | -0.2 | 18.2 | 0 | 2016-01-21 | -13.7 | 31.7 | 0 | 31.56 | 0
2025-01-21 | -19.1 | 37.1 | 0 | 2024-01-21 | -17.9 | 35.9 | 0 | 2023-01-21 | -6 | 24 | 0 | 2022-01-21 | -26.5 | 44.5 | 0 | 2021-01-21 | -12 | 30 | 0 | 2020-01-21 | -18.7 | 36.7 | 0 | 2019-01-21 | -23.1 | 41.1 | 0 | 2018-01-21 | -0.6 | 18.6 | 0 | 2017-01-21 | -0.2 | 18.2 | 0 | 2016-01-21 | -14.7 | 32.7 | 0 | 31.88 | 0
2025-01-21 | -19.6 | 37.6 | 0 | 2024-01-21 | -17.8 | 35.8 | 0 | 2023-01-21 | -6.9 | 24.9 | 0 | 2022-01-21 | -27.7 | 45.7 | 0 | 2021-01-21 | -11.8 | 29.8 | 0 | 2020-01-21 | -18.4 | 36.4 | 0 | 2019-01-21 | -23.5 | 41.5 | 0 | 2018-01-21 | -1.3 | 19.3 | 0 | 2017-01-21 | -0.2 | 18.2 | 0 | 2016-01-21 | -16.5 | 34.5 | 0 | 32.37 | 0
2025-01-21 | -19.6 | 37.6 | 0 | 2024-01-21 | -18.4 | 36.4 | 0 | 2023-01-21 | -7.4 | 25.4 | 0 | 2022-01-21 | -27.9 | 45.9 | 0 | 2021-01-21 | -11.3 | 29.3 | 0 | 2020-01-21 | -18.2 | 36.2 | 0 | 2019-01-21 | -24.2 | 42.2 | 0 | 2018-01-21 | -1.5 | 19.5 | 0 | 2017-01-21 | -0.2 | 18.2 | 0 | 2016-01-21 | -14.9 | 32.9 | 0 | 32.36 | 0
2025-01-21 | -17.7 | 35.7 | 0 | 2024-01-21 | -17 | 35 | 0 | 2023-01-21 | -7 | 25 | 0 | 2022-01-21 | -27.6 | 45.6 | 0 | 2021-01-21 | -11.1 | 29.1 | 0 | 2020-01-21 | -17 | 35 | 0 | 2019-01-21 | -24.4 | 42.4 | 0 | 2018-01-21 | -1.1 | 19.1 | 0 | 2017-01-21 | 0.1 | 17.9 | 0 | 2016-01-21 | -13.4 | 31.4 | 0 | 31.62 | 0
2025-01-21 | -15.7 | 33.7 | 0 | 2024-01-21 | -15.5 | 33.5 | 0 | 2023-01-21 | -6.9 | 24.9 | 0 | 2022-01-21 | -23.4 | 41.4 | 0 | 2021-01-21 | -10.5 | 28.5 | 0 | 2020-01-21 | -14.5 | 32.5 | 0 | 2019-01-21 | -24.1 | 42.1 | 0 | 2018-01-21 | -0.5 | 18.5 | 0 | 2017-01-21 | 0.3 | 17.7 | 0 | 2016-01-21 | -12.3 | 30.3 | 0 | 30.31 | 0
2025-01-21 | -14.6 | 32.6 | 0 | 2024-01-21 | -14.3 | 32.3 | 0 | 2023-01-21 | -6 | 24 | 0 | 2022-01-21 | -21.8 | 39.8 | 0 | 2021-01-21 | -10.3 | 28.3 | 0 | 2020-01-21 | -12 | 30 | 0 | 2019-01-21 | -23.4 | 41.4 | 0 | 2018-01-21 | -0.4 | 18.4 | 0 | 2017-01-21 | 0.6 | 17.4 | 0 | 2016-01-21 | -10.7 | 28.7 | 0 | 29.29 | 0
2025-01-21 | -13.8 | 31.8 | 0 | 2024-01-21 | -13.4 | 31.4 | 0 | 2023-01-21 | -4.5 | 22.5 | 0 | 2022-01-21 | -20.5 | 38.5 | 0 | 2021-01-21 | -9.8 | 27.8 | 0 | 2020-01-21 | -10.6 | 28.6 | 0 | 2019-01-21 | -22.8 | 40.8 | 0 | 2018-01-21 | 0.6 | 17.4 | 0 | 2017-01-21 | 0.9 | 17.1 | 0 | 2016-01-21 | -9.4 | 27.4 | 0 | 28.33 | 0
2025-01-21 | -12.7 | 30.7 | 0 | 2024-01-21 | -12.3 | 30.3 | 0 | 2023-01-21 | -3.7 | 21.7 | 0 | 2022-01-21 | -19.4 | 37.4 | 0 | 2021-01-21 | -8.6 | 26.6 | 0 | 2020-01-21 | -7.9 | 25.9 | 0 | 2019-01-21 | -21 | 39 | 0 | 2018-01-21 | 0.8 | 17.2 | 0 | 2017-01-21 | 1 | 17 | 0 | 2016-01-21 | -8.3 | 26.3 | 0 | 27.21 | 0
2025-01-21 | -11.9 | 29.9 | 0 | 2024-01-21 | -11.8 | 29.8 | 0 | 2023-01-21 | -3.2 | 21.2 | 0 | 2022-01-21 | -18.6 | 36.6 | 0 | 2021-01-21 | -7 | 25 | 0 | 2020-01-21 | -7.4 | 25.4 | 0 | 2019-01-21 | -19 | 37 | 0 | 2018-01-21 | 1.1 | 16.9 | 0 | 2017-01-21 | 1.3 | 16.7 | 0 | 2016-01-21 | -7.8 | 25.8 | 0 | 26.43 | 0
2025-01-21 | -11.8 | 29.8 | 0 | 2024-01-21 | -11.3 | 29.3 | 0 | 2023-01-21 | -2.9 | 20.9 | 0 | 2022-01-21 | -18.1 | 36.1 | 0 | 2021-01-21 | -7.1 | 25.1 | 0 | 2020-01-21 | -6.9 | 24.9 | 0 | 2019-01-21 | -18 | 36 | 0 | 2018-01-21 | 1 | 17 | 0 | 2017-01-21 | 1.7 | 16.3 | 0 | 2016-01-21 | -7.7 | 25.7 | 0 | 26.11 | 0
2025-01-21 | -11.9 | 29.9 | 0 | 2024-01-21 | -10.5 | 28.5 | 0 | 2023-01-21 | -2.6 | 20.6 | 0 | 2022-01-21 | -18.2 | 36.2 | 0 | 2021-01-21 | -6.8 | 24.8 | 0 | 2020-01-21 | -6.7 | 24.7 | 0 | 2019-01-21 | -18.2 | 36.2 | 0 | 2018-01-21 | 0.8 | 17.2 | 0 | 2017-01-21 | 1.8 | 16.2 | 0 | 2016-01-21 | -7.9 | 25.9 | 0 | 26.02 | 0
2025-01-21 | -12.8 | 30.8 | 0 | 2024-01-21 | -11.4 | 29.4 | 0 | 2023-01-21 | -2.9 | 20.9 | 0 | 2022-01-21 | -19.1 | 37.1 | 0 | 2021-01-21 | -7.3 | 25.3 | 0 | 2020-01-21 | -6.6 | 24.6 | 0 | 2019-01-21 | -18.4 | 36.4 | 0 | 2018-01-21 | 0.2 | 17.8 | 0 | 2017-01-21 | 2 | 16 | 0 | 2016-01-21 | -8.9 | 26.9 | 0 | 26.52 | 0
2025-01-21 | -13 | 31 | 0 | 2024-01-21 | -11.9 | 29.9 | 0 | 2023-01-21 | -2.8 | 20.8 | 0 | 2022-01-21 | -20.5 | 38.5 | 0 | 2021-01-21 | -7.8 | 25.8 | 0 | 2020-01-21 | -6.5 | 24.5 | 0 | 2019-01-21 | -18.5 | 36.5 | 0 | 2018-01-21 | -0.2 | 18.2 | 0 | 2017-01-21 | 2 | 16 | 0 | 2016-01-21 | -10.1 | 28.1 | 0 | 26.93 | 0
2025-01-21 | -15.3 | 33.3 | 0 | 2024-01-21 | -12.5 | 30.5 | 0 | 2023-01-21 | -2.9 | 20.9 | 0 | 2022-01-21 | -21.8 | 39.8 | 0 | 2021-01-21 | -8 | 26 | 0 | 2020-01-21 | -5.6 | 23.6 | 0 | 2019-01-21 | -18.7 | 36.7 | 0 | 2018-01-21 | -1.2 | 19.2 | 0 | 2017-01-21 | 1.8 | 16.2 | 0 | 2016-01-21 | -9.7 | 27.7 | 0 | 27.39 | 0
2025-01-21 | -14.5 | 32.5 | 0 | 2024-01-21 | -12.8 | 30.8 | 0 | 2023-01-21 | -3.2 | 21.2 | 0 | 2022-01-21 | -22.8 | 40.8 | 0 | 2021-01-21 | -7.9 | 25.9 | 0 | 2020-01-21 | -5.4 | 23.4 | 0 | 2019-01-21 | -19.2 | 37.2 | 0 | 2018-01-21 | -1.9 | 19.9 | 0 | 2017-01-21 | 1.3 | 16.7 | 0 | 2016-01-21 | -9.1 | 27.1 | 0 | 27.55 | 0
2025-01-21 | -14.6 | 32.6 | 0 | 2024-01-21 | -13.1 | 31.1 | 0 | 2023-01-21 | -3.5 | 21.5 | 0 | 2022-01-21 | -23.5 | 41.5 | 0 | 2021-01-21 | -7.8 | 25.8 | 0 | 2020-01-21 | -5 | 23 | 0 | 2019-01-21 | -20 | 38 | 0 | 2018-01-21 | -1.9 | 19.9 | 0 | 2017-01-21 | 1.7 | 16.3 | 0 | 2016-01-21 | -9.2 | 27.2 | 0 | 27.69 | 0
2025-01-21 | -15.3 | 33.3 | 0 | 2024-01-21 | -13.5 | 31.5 | 0 | 2023-01-21 | -3.6 | 21.6 | 0 | 2022-01-21 | -24 | 42 | 0 | 2021-01-21 | -3.9 | 21.9 | 0 | 2020-01-21 | -4.7 | 22.7 | 0 | 2019-01-21 | -20.4 | 38.4 | 0 | 2018-01-21 | -2.4 | 20.4 | 0 | 2017-01-21 | 1.2 | 16.8 | 0 | 2016-01-21 | -9.8 | 27.8 | 0 | 27.64 | 0
2025-01-21 | -15.8 | 33.8 | 0 | 2024-01-21 | -12.6 | 30.6 | 0 | 2023-01-21 | -3 | 21 | 0 | 2022-01-21 | -24.3 | 42.3 | 0 | 2021-01-21 | -6.3 | 24.3 | 0 | 2020-01-21 | -4.5 | 22.5 | 0 | 2019-01-21 | -21.2 | 39.2 | 0 | 2018-01-21 | -2.5 | 20.5 | 0 | 2017-01-21 | 1.2 | 16.8 | 0 | 2016-01-21 | -8.7 | 26.7 | 0 | 27.77 | 0
2025-01-22 | -16.5 | 34.5 | 0 | 2024-01-22 | -12.1 | 30.1 | 0 | 2023-01-22 | -3.6 | 21.6 | 0 | 2022-01-22 | -25.9 | 43.9 | 0 | 2021-01-22 | -4.9 | 22.9 | 0 | 2020-01-22 | -4.5 | 22.5 | 0 | 2019-01-22 | -21.4 | 39.4 | 0 | 2018-01-22 | -2.6 | 20.6 | 0 | 2017-01-22 | 0.6 | 17.4 | 0 | 2016-01-22 | -8.8 | 26.8 | 0 | 27.97 | 0
2025-01-22 | -17.6 | 35.6 | 0 | 2024-01-22 | -12.1 | 30.1 | 0 | 2023-01-22 | -3.8 | 21.8 | 0 | 2022-01-22 | -26.7 | 44.7 | 0 | 2021-01-22 | -3.9 | 21.9 | 0 | 2020-01-22 | -4.7 | 22.7 | 0 | 2019-01-22 | -21.9 | 39.9 | 0 | 2018-01-22 | -3.5 | 21.5 | 0 | 2017-01-22 | 1.2 | 16.8 | 0 | 2016-01-22 | -8.6 | 26.6 | 0 | 28.16 | 0
2025-01-22 | -18.2 | 36.2 | 0 | 2024-01-22 | -11 | 29 | 0 | 2023-01-22 | -3.7 | 21.7 | 0 | 2022-01-22 | -27.9 | 45.9 | 0 | 2021-01-22 | -2.8 | 20.8 | 0 | 2020-01-22 | -4.9 | 22.9 | 0 | 2019-01-22 | -22.6 | 40.6 | 0 | 2018-01-22 | -4.2 | 22.2 | 0 | 2017-01-22 | 0.9 | 17.1 | 0 | 2016-01-22 | -8.4 | 26.4 | 0 | 28.28 | 0
2025-01-22 | -18.7 | 36.7 | 0 | 2024-01-22 | -10.6 | 28.6 | 0 | 2023-01-22 | -3.5 | 21.5 | 0 | 2022-01-22 | -27.1 | 45.1 | 0 | 2021-01-22 | -2.7 | 20.7 | 0 | 2020-01-22 | -4.6 | 22.6 | 0 | 2019-01-22 | -22.6 | 40.6 | 0 | 2018-01-22 | -5.1 | 23.1 | 0 | 2017-01-22 | 1 | 17 | 0 | 2016-01-22 | -8.5 | 26.5 | 0 | 28.24 | 0
2025-01-22 | -18.7 | 36.7 | 0 | 2024-01-22 | -9.2 | 27.2 | 0 | 2023-01-22 | -3.6 | 21.6 | 0 | 2022-01-22 | -27 | 45 | 0 | 2021-01-22 | -2.1 | 20.1 | 0 | 2020-01-22 | -4.3 | 22.3 | 0 | 2019-01-22 | -23.1 | 41.1 | 0 | 2018-01-22 | -5.8 | 23.8 | 0 | 2017-01-22 | 1.1 | 16.9 | 0 | 2016-01-22 | -9.3 | 27.3 | 0 | 28.2 | 0
2025-01-22 | -18.8 | 36.8 | 0 | 2024-01-22 | -8.2 | 26.2 | 0 | 2023-01-22 | -3.4 | 21.4 | 0 | 2022-01-22 | -29.1 | 47.1 | 0 | 2021-01-22 | -3.3 | 21.3 | 0 | 2020-01-22 | -4.4 | 22.4 | 0 | 2019-01-22 | -23.6 | 41.6 | 0 | 2018-01-22 | -6.2 | 24.2 | 0 | 2017-01-22 | 1.1 | 16.9 | 0 | 2016-01-22 | -9.8 | 27.8 | 0 | 28.57 | 0
2025-01-22 | -19.4 | 37.4 | 0 | 2024-01-22 | -6.9 | 24.9 | 0 | 2023-01-22 | -3.5 | 21.5 | 0 | 2022-01-22 | -27.9 | 45.9 | 0 | 2021-01-22 | -4.7 | 22.7 | 0 | 2020-01-22 | -4.9 | 22.9 | 0 | 2019-01-22 | -24.2 | 42.2 | 0 | 2018-01-22 | -6.7 | 24.7 | 0 | 2017-01-22 | 1.2 | 16.8 | 0 | 2016-01-22 | -10.7 | 28.7 | 0 | 28.77 | 0
2025-01-22 | -19.6 | 37.6 | 0 | 2024-01-22 | -7 | 25 | 0 | 2023-01-22 | -3.5 | 21.5 | 0 | 2022-01-22 | -28.4 | 46.4 | 0 | 2021-01-22 | -5.1 | 23.1 | 0 | 2020-01-22 | -7.3 | 25.3 | 0 | 2019-01-22 | -25.2 | 43.2 | 0 | 2018-01-22 | -7.5 | 25.5 | 0 | 2017-01-22 | 0.5 | 17.5 | 0 | 2016-01-22 | -10.9 | 28.9 | 0 | 29.4 | 0
2025-01-22 | -20.4 | 38.4 | 0 | 2024-01-22 | -7.1 | 25.1 | 0 | 2023-01-22 | -3.1 | 21.1 | 0 | 2022-01-22 | -29.2 | 47.2 | 0 | 2021-01-22 | -5.7 | 23.7 | 0 | 2020-01-22 | -7.7 | 25.7 | 0 | 2019-01-22 | -24.9 | 42.9 | 0 | 2018-01-22 | -7.4 | 25.4 | 0 | 2017-01-22 | 0.1 | 17.9 | 0 | 2016-01-22 | -12.4 | 30.4 | 0 | 29.78 | 0
2025-01-22 | -18.4 | 36.4 | 0 | 2024-01-22 | -6 | 24 | 0 | 2023-01-22 | -2.4 | 20.4 | 0 | 2022-01-22 | -27.1 | 45.1 | 0 | 2021-01-22 | -6.2 | 24.2 | 0 | 2020-01-22 | -6.4 | 24.4 | 0 | 2019-01-22 | -23.1 | 41.1 | 0 | 2018-01-22 | -7.5 | 25.5 | 0 | 2017-01-22 | 0.2 | 17.8 | 0 | 2016-01-22 | -10.7 | 28.7 | 0 | 28.76 | 0
2025-01-22 | -16.5 | 34.5 | 0 | 2024-01-22 | -4.2 | 22.2 | 0 | 2023-01-22 | -1.8 | 19.8 | 0 | 2022-01-22 | -24 | 42 | 0 | 2021-01-22 | -6.8 | 24.8 | 0 | 2020-01-22 | -5.3 | 23.3 | 0 | 2019-01-22 | -20.7 | 38.7 | 0 | 2018-01-22 | -7.2 | 25.2 | 0 | 2017-01-22 | 0.4 | 17.6 | 0 | 2016-01-22 | -9.2 | 27.2 | 0 | 27.53 | 0
2025-01-22 | -14.9 | 32.9 | 0 | 2024-01-22 | -2.8 | 20.8 | 0 | 2023-01-22 | -1.5 | 19.5 | 0 | 2022-01-22 | -21.9 | 39.9 | 0 | 2021-01-22 | -6.9 | 24.9 | 0 | 2020-01-22 | -3.5 | 21.5 | 0 | 2019-01-22 | -18.9 | 36.9 | 0 | 2018-01-22 | -6.5 | 24.5 | 0 | 2017-01-22 | 1 | 17 | 0 | 2016-01-22 | -7.5 | 25.5 | 0 | 26.34 | 0
2025-01-22 | -12.9 | 30.9 | 0 | 2024-01-22 | -2 | 20 | 0 | 2023-01-22 | -1.2 | 19.2 | 0 | 2022-01-22 | -20.1 | 38.1 | 0 | 2021-01-22 | -6.9 | 24.9 | 0 | 2020-01-22 | -1.2 | 19.2 | 0 | 2019-01-22 | -17.4 | 35.4 | 0 | 2018-01-22 | -5.9 | 23.9 | 0 | 2017-01-22 | 1.4 | 16.6 | 0 | 2016-01-22 | -6.8 | 24.8 | 0 | 25.3 | 0
2025-01-22 | -11.5 | 29.5 | 0 | 2024-01-22 | -1.6 | 19.6 | 0 | 2023-01-22 | -0.8 | 18.8 | 0 | 2022-01-22 | -18.9 | 36.9 | 0 | 2021-01-22 | -6.6 | 24.6 | 0 | 2020-01-22 | 0.8 | 17.2 | 0 | 2019-01-22 | -16.2 | 34.2 | 0 | 2018-01-22 | -5.7 | 23.7 | 0 | 2017-01-22 | 1.8 | 16.2 | 0 | 2016-01-22 | -6.2 | 24.2 | 0 | 24.49 | 0
2025-01-22 | -11.1 | 29.1 | 0 | 2024-01-22 | -1.9 | 19.9 | 0 | 2023-01-22 | -0.8 | 18.8 | 0 | 2022-01-22 | -18.1 | 36.1 | 0 | 2021-01-22 | -7.1 | 25.1 | 0 | 2020-01-22 | 1.2 | 16.8 | 0 | 2019-01-22 | -14.8 | 32.8 | 0 | 2018-01-22 | -5.4 | 23.4 | 0 | 2017-01-22 | 1.9 | 16.1 | 0 | 2016-01-22 | -5.9 | 23.9 | 0 | 24.2 | 0
2025-01-22 | -10.3 | 28.3 | 0 | 2024-01-22 | -3.1 | 21.1 | 0 | 2023-01-22 | -0.8 | 18.8 | 0 | 2022-01-22 | -17.7 | 35.7 | 0 | 2021-01-22 | -7.2 | 25.2 | 0 | 2020-01-22 | 1 | 17 | 0 | 2019-01-22 | -14.4 | 32.4 | 0 | 2018-01-22 | -5.4 | 23.4 | 0 | 2017-01-22 | 1.9 | 16.1 | 0 | 2016-01-22 | -5.4 | 23.4 | 0 | 24.14 | 0
2025-01-22 | -11.1 | 29.1 | 0 | 2024-01-22 | -2.6 | 20.6 | 0 | 2023-01-22 | -1 | 19 | 0 | 2022-01-22 | -17.4 | 35.4 | 0 | 2021-01-22 | -7.4 | 25.4 | 0 | 2020-01-22 | -0.6 | 18.6 | 0 | 2019-01-22 | -14 | 32 | 0 | 2018-01-22 | -6.4 | 24.4 | 0 | 2017-01-22 | 1.9 | 16.1 | 0 | 2016-01-22 | -5.8 | 23.8 | 0 | 24.44 | 0
2025-01-22 | -11.5 | 29.5 | 0 | 2024-01-22 | -3.1 | 21.1 | 0 | 2023-01-22 | -1.2 | 19.2 | 0 | 2022-01-22 | -16.8 | 34.8 | 0 | 2021-01-22 | -7.7 | 25.7 | 0 | 2020-01-22 | -1.4 | 19.4 | 0 | 2019-01-22 | -14.8 | 32.8 | 0 | 2018-01-22 | -6.7 | 24.7 | 0 | 2017-01-22 | 1.4 | 16.6 | 0 | 2016-01-22 | -6.8 | 24.8 | 0 | 24.86 | 0
2025-01-22 | -12.1 | 30.1 | 0 | 2024-01-22 | -2.9 | 20.9 | 0 | 2023-01-22 | -1.4 | 19.4 | 0 | 2022-01-22 | -17.1 | 35.1 | 0 | 2021-01-22 | -8.1 | 26.1 | 0 | 2020-01-22 | -1.9 | 19.9 | 0 | 2019-01-22 | -15.3 | 33.3 | 0 | 2018-01-22 | -7.1 | 25.1 | 0 | 2017-01-22 | 1.4 | 16.6 | 0 | 2016-01-22 | -7.4 | 25.4 | 0 | 25.19 | 0
2025-01-22 | -11.3 | 29.3 | 0 | 2024-01-22 | -2.8 | 20.8 | 0 | 2023-01-22 | -1.5 | 19.5 | 0 | 2022-01-22 | -17.1 | 35.1 | 0 | 2021-01-22 | -8.3 | 26.3 | 0 | 2020-01-22 | -2 | 20 | 0 | 2019-01-22 | -14.9 | 32.9 | 0 | 2018-01-22 | -7.2 | 25.2 | 0 | 2017-01-22 | 1.2 | 16.8 | 0 | 2016-01-22 | -9.4 | 27.4 | 0 | 25.33 | 0
2025-01-22 | -11.5 | 29.5 | 0 | 2024-01-22 | -2.6 | 20.6 | 0 | 2023-01-22 | -1.6 | 19.6 | 0 | 2022-01-22 | -17.9 | 35.9 | 0 | 2021-01-22 | -8.9 | 26.9 | 0 | 2020-01-22 | -2.2 | 20.2 | 0 | 2019-01-22 | -14.8 | 32.8 | 0 | 2018-01-22 | -7.2 | 25.2 | 0 | 2017-01-22 | 0.8 | 17.2 | 0 | 2016-01-22 | -8.3 | 26.3 | 0 | 25.42 | 0
2025-01-22 | -11.1 | 29.1 | 0 | 2024-01-22 | -2.4 | 20.4 | 0 | 2023-01-22 | -1.7 | 19.7 | 0 | 2022-01-22 | -17.6 | 35.6 | 0 | 2021-01-22 | -9.3 | 27.3 | 0 | 2020-01-22 | -2.5 | 20.5 | 0 | 2019-01-22 | -14.6 | 32.6 | 0 | 2018-01-22 | -6.5 | 24.5 | 0 | 2017-01-22 | 0.5 | 17.5 | 0 | 2016-01-22 | -8.1 | 26.1 | 0 | 25.33 | 0
2025-01-22 | -10.8 | 28.8 | 0 | 2024-01-22 | -1.9 | 19.9 | 0 | 2023-01-22 | -2.3 | 20.3 | 0 | 2022-01-22 | -17.9 | 35.9 | 0 | 2021-01-22 | -9.8 | 27.8 | 0 | 2020-01-22 | -2.9 | 20.9 | 0 | 2019-01-22 | -14.5 | 32.5 | 0 | 2018-01-22 | -5.9 | 23.9 | 0 | 2017-01-22 | 0.3 | 17.7 | 0 | 2016-01-22 | -9.1 | 27.1 | 0 | 25.48 | 0
2025-01-22 | -10.9 | 28.9 | 0 | 2024-01-22 | -1.7 | 19.7 | 0 | 2023-01-22 | -2.1 | 20.1 | 0 | 2022-01-22 | -17.2 | 35.2 | 0 | 2021-01-22 | -10.6 | 28.6 | 0 | 2020-01-22 | -2.8 | 20.8 | 0 | 2019-01-22 | -14.5 | 32.5 | 0 | 2018-01-22 | -5.6 | 23.6 | 0 | 2017-01-22 | -0.2 | 18.2 | 0 | 2016-01-22 | -10.2 | 28.2 | 0 | 25.58 | 0
2025-01-23 | -11.1 | 29.1 | 0 | 2024-01-23 | -1.7 | 19.7 | 0 | 2023-01-23 | -2 | 20 | 0 | 2022-01-23 | -16.9 | 34.9 | 0 | 2021-01-23 | -11.8 | 29.8 | 0 | 2020-01-23 | -2.5 | 20.5 | 0 | 2019-01-23 | -14.9 | 32.9 | 0 | 2018-01-23 | -5.2 | 23.2 | 0 | 2017-01-23 | -0.9 | 18.9 | 0 | 2016-01-23 | -10.5 | 28.5 | 0 | 25.75 | 0
2025-01-23 | -11.3 | 29.3 | 0 | 2024-01-23 | -1.4 | 19.4 | 0 | 2023-01-23 | -2.4 | 20.4 | 0 | 2022-01-23 | -18.1 | 36.1 | 0 | 2021-01-23 | -12.8 | 30.8 | 0 | 2020-01-23 | -2.4 | 20.4 | 0 | 2019-01-23 | -14.6 | 32.6 | 0 | 2018-01-23 | -4.3 | 22.3 | 0 | 2017-01-23 | -1.5 | 19.5 | 0 | 2016-01-23 | -11.4 | 29.4 | 0 | 26.02 | 0
2025-01-23 | -10.8 | 28.8 | 0 | 2024-01-23 | -1.3 | 19.3 | 0 | 2023-01-23 | -2.8 | 20.8 | 0 | 2022-01-23 | -19.2 | 37.2 | 0 | 2021-01-23 | -14.1 | 32.1 | 0 | 2020-01-23 | -2.2 | 20.2 | 0 | 2019-01-23 | -14.6 | 32.6 | 0 | 2018-01-23 | -4.3 | 22.3 | 0 | 2017-01-23 | -1.9 | 19.9 | 0 | 2016-01-23 | -11.7 | 29.7 | 0 | 26.29 | 0
2025-01-23 | -10.8 | 28.8 | 0 | 2024-01-23 | -1.4 | 19.4 | 0 | 2023-01-23 | -2.7 | 20.7 | 0 | 2022-01-23 | -19.2 | 37.2 | 0 | 2021-01-23 | -14.3 | 32.3 | 0 | 2020-01-23 | -2.7 | 20.7 | 0 | 2019-01-23 | -14.3 | 32.3 | 0 | 2018-01-23 | -4.2 | 22.2 | 0 | 2017-01-23 | -2.1 | 20.1 | 0 | 2016-01-23 | -12.3 | 30.3 | 0 | 26.4 | 0
2025-01-23 | -10.9 | 28.9 | 0 | 2024-01-23 | -1.6 | 19.6 | 0 | 2023-01-23 | -2.6 | 20.6 | 0 | 2022-01-23 | -20.1 | 38.1 | 0 | 2021-01-23 | -14.2 | 32.2 | 0 | 2020-01-23 | -3.5 | 21.5 | 0 | 2019-01-23 | -13.2 | 31.2 | 0 | 2018-01-23 | -4.1 | 22.1 | 0 | 2017-01-23 | -2.3 | 20.3 | 0 | 2016-01-23 | -13.3 | 31.3 | 0 | 26.58 | 0
2025-01-23 | -10.9 | 28.9 | 0 | 2024-01-23 | -1.8 | 19.8 | 0 | 2023-01-23 | -2.6 | 20.6 | 0 | 2022-01-23 | -18.7 | 36.7 | 0 | 2021-01-23 | -15 | 33 | 0 | 2020-01-23 | -3.7 | 21.7 | 0 | 2019-01-23 | -12.2 | 30.2 | 0 | 2018-01-23 | -3.8 | 21.8 | 0 | 2017-01-23 | -2.7 | 20.7 | 0 | 2016-01-23 | -14 | 32 | 0 | 26.54 | 0
2025-01-23 | -10.8 | 28.8 | 0 | 2024-01-23 | -2 | 20 | 0 | 2023-01-23 | -2.6 | 20.6 | 0 | 2022-01-23 | -18.1 | 36.1 | 0 | 2021-01-23 | -16.1 | 34.1 | 0 | 2020-01-23 | -3.7 | 21.7 | 0 | 2019-01-23 | -11.8 | 29.8 | 0 | 2018-01-23 | -3.4 | 21.4 | 0 | 2017-01-23 | -2.9 | 20.9 | 0 | 2016-01-23 | -13.9 | 31.9 | 0 | 26.53 | 0
2025-01-23 | -10.4 | 28.4 | 0 | 2024-01-23 | -2.1 | 20.1 | 0 | 2023-01-23 | -2.5 | 20.5 | 0 | 2022-01-23 | -17.4 | 35.4 | 0 | 2021-01-23 | -16.9 | 34.9 | 0 | 2020-01-23 | -4.4 | 22.4 | 0 | 2019-01-23 | -12 | 30 | 0 | 2018-01-23 | -2.8 | 20.8 | 0 | 2017-01-23 | -2.9 | 20.9 | 0 | 2016-01-23 | -14.2 | 32.2 | 0 | 26.56 | 0
2025-01-23 | -10.5 | 28.5 | 0 | 2024-01-23 | -2.3 | 20.3 | 0 | 2023-01-23 | -2.6 | 20.6 | 0 | 2022-01-23 | -12.3 | 30.3 | 0 | 2021-01-23 | -18.1 | 36.1 | 0 | 2020-01-23 | -5 | 23 | 0 | 2019-01-23 | -11.5 | 29.5 | 0 | 2018-01-23 | -2.1 | 20.1 | 0 | 2017-01-23 | -2.5 | 20.5 | 0 | 2016-01-23 | -14.8 | 32.8 | 0 | 26.17 | 0
2025-01-23 | -10.2 | 28.2 | 0 | 2024-01-23 | -2.1 | 20.1 | 0 | 2023-01-23 | -2.4 | 20.4 | 0 | 2022-01-23 | -11.9 | 29.9 | 0 | 2021-01-23 | -17.1 | 35.1 | 0 | 2020-01-23 | -4.4 | 22.4 | 0 | 2019-01-23 | -10.8 | 28.8 | 0 | 2018-01-23 | -1.6 | 19.6 | 0 | 2017-01-23 | -2.2 | 20.2 | 0 | 2016-01-23 | -13.6 | 31.6 | 0 | 25.63 | 0
2025-01-23 | -9.6 | 27.6 | 0 | 2024-01-23 | -2.1 | 20.1 | 0 | 2023-01-23 | -1.7 | 19.7 | 0 | 2022-01-23 | -12.8 | 30.8 | 0 | 2021-01-23 | -16.4 | 34.4 | 0 | 2020-01-23 | -3 | 21 | 0 | 2019-01-23 | -10.2 | 28.2 | 0 | 2018-01-23 | -1.3 | 19.3 | 0 | 2017-01-23 | -1.9 | 19.9 | 0 | 2016-01-23 | -12.6 | 30.6 | 0 | 25.16 | 0
2025-01-23 | -9 | 27 | 0 | 2024-01-23 | -2.8 | 20.8 | 0 | 2023-01-23 | -1.6 | 19.6 | 0 | 2022-01-23 | -14.9 | 32.9 | 0 | 2021-01-23 | -15.8 | 33.8 | 0 | 2020-01-23 | -1.4 | 19.4 | 0 | 2019-01-23 | -9.8 | 27.8 | 0 | 2018-01-23 | -0.7 | 18.7 | 0 | 2017-01-23 | -1.6 | 19.6 | 0 | 2016-01-23 | -10.8 | 28.8 | 0 | 24.84 | 0
2025-01-23 | -8.4 | 26.4 | 0 | 2024-01-23 | -2.9 | 20.9 | 0 | 2023-01-23 | -1.1 | 19.1 | 0 | 2022-01-23 | -13.4 | 31.4 | 0 | 2021-01-23 | -15.3 | 33.3 | 0 | 2020-01-23 | -0.3 | 18.3 | 0 | 2019-01-23 | -8.8 | 26.8 | 0 | 2018-01-23 | -0.3 | 18.3 | 0 | 2017-01-23 | -1.5 | 19.5 | 0 | 2016-01-23 | -10 | 28 | 0 | 24.2 | 0
2025-01-23 | -7.8 | 25.8 | 0 | 2024-01-23 | -2.8 | 20.8 | 0 | 2023-01-23 | -0.5 | 18.5 | 0 | 2022-01-23 | -13.3 | 31.3 | 0 | 2021-01-23 | -14.4 | 32.4 | 0 | 2020-01-23 | 0.8 | 17.2 | 0 | 2019-01-23 | -8 | 26 | 0 | 2018-01-23 | 0.1 | 17.9 | 0 | 2017-01-23 | -1 | 19 | 0 | 2016-01-23 | -9.1 | 27.1 | 0 | 23.6 | 0
2025-01-23 | -7.1 | 25.1 | 0 | 2024-01-23 | -2.9 | 20.9 | 0 | 2023-01-23 | -0.6 | 18.6 | 0 | 2022-01-23 | -13.8 | 31.8 | 0 | 2021-01-23 | -13.9 | 31.9 | 0 | 2020-01-23 | 1.3 | 16.7 | 0 | 2019-01-23 | -7.7 | 25.7 | 0 | 2018-01-23 | 0.2 | 17.8 | 0 | 2017-01-23 | -1 | 19 | 0 | 2016-01-23 | -8.6 | 26.6 | 0 | 23.41 | 0
2025-01-23 | -6.2 | 24.2 | 0 | 2024-01-23 | -3 | 21 | 0 | 2023-01-23 | -0.9 | 18.9 | 0 | 2022-01-23 | -14.3 | 32.3 | 0 | 2021-01-23 | -13.5 | 31.5 | 0 | 2020-01-23 | 1.5 | 16.5 | 0 | 2019-01-23 | -7.4 | 25.4 | 0 | 2018-01-23 | 0.2 | 17.8 | 0 | 2017-01-23 | -1.5 | 19.5 | 0 | 2016-01-23 | -8.3 | 26.3 | 0 | 23.34 | 0
2025-01-23 | -5.9 | 23.9 | 0 | 2024-01-23 | -3.2 | 21.2 | 0 | 2023-01-23 | -1.4 | 19.4 | 0 | 2022-01-23 | -15.3 | 33.3 | 0 | 2021-01-23 | -13.6 | 31.6 | 0 | 2020-01-23 | 1.3 | 16.7 | 0 | 2019-01-23 | -7.4 | 25.4 | 0 | 2018-01-23 | 0.1 | 17.9 | 0 | 2017-01-23 | -1.6 | 19.6 | 0 | 2016-01-23 | -8.5 | 26.5 | 0 | 23.55 | 0
2025-01-23 | -6.1 | 24.1 | 0 | 2024-01-23 | -3.3 | 21.3 | 0 | 2023-01-23 | -1.2 | 19.2 | 0 | 2022-01-23 | -16.6 | 34.6 | 0 | 2021-01-23 | -14.4 | 32.4 | 0 | 2020-01-23 | 0.2 | 17.8 | 0 | 2019-01-23 | -7.3 | 25.3 | 0 | 2018-01-23 | 0.3 | 17.7 | 0 | 2017-01-23 | -1.7 | 19.7 | 0 | 2016-01-23 | -9.4 | 27.4 | 0 | 23.95 | 0
2025-01-23 | -6.5 | 24.5 | 0 | 2024-01-23 | -3.9 | 21.9 | 0 | 2023-01-23 | -1.3 | 19.3 | 0 | 2022-01-23 | -17.1 | 35.1 | 0 | 2021-01-23 | -14.4 | 32.4 | 0 | 2020-01-23 | -0.8 | 18.8 | 0 | 2019-01-23 | -6.8 | 24.8 | 0 | 2018-01-23 | 0.6 | 17.4 | 0 | 2017-01-23 | -1.7 | 19.7 | 0 | 2016-01-23 | -11.1 | 29.1 | 0 | 24.3 | 0
2025-01-23 | -6.1 | 24.1 | 0 | 2024-01-23 | -4.4 | 22.4 | 0 | 2023-01-23 | -1.5 | 19.5 | 0 | 2022-01-23 | -19.1 | 37.1 | 0 | 2021-01-23 | -14.2 | 32.2 | 0 | 2020-01-23 | -1 | 19 | 0 | 2019-01-23 | -6.5 | 24.5 | 0 | 2018-01-23 | 2.9 | 15.1 | 0 | 2017-01-23 | -2.1 | 20.1 | 0 | 2016-01-23 | -12.7 | 30.7 | 0 | 24.47 | 0
2025-01-23 | -6.3 | 24.3 | 0 | 2024-01-23 | -5.1 | 23.1 | 0 | 2023-01-23 | -1.4 | 19.4 | 0 | 2022-01-23 | -20.1 | 38.1 | 0 | 2021-01-23 | -14.6 | 32.6 | 0 | 2020-01-23 | -1.5 | 19.5 | 0 | 2019-01-23 | -5.4 | 23.4 | 0 | 2018-01-23 | 2.9 | 15.1 | 0 | 2017-01-23 | -2.4 | 20.4 | 0 | 2016-01-23 | -13.6 | 31.6 | 0 | 24.75 | 0
2025-01-23 | -6.4 | 24.4 | 0 | 2024-01-23 | -6.5 | 24.5 | 0 | 2023-01-23 | -1.5 | 19.5 | 0 | 2022-01-23 | -20.4 | 38.4 | 0 | 2021-01-23 | -15 | 33 | 0 | 2020-01-23 | -1.4 | 19.4 | 0 | 2019-01-23 | -4.4 | 22.4 | 0 | 2018-01-23 | 2.4 | 15.6 | 0 | 2017-01-23 | -2.7 | 20.7 | 0 | 2016-01-23 | -14.9 | 32.9 | 0 | 25.08 | 0
2025-01-23 | -7 | 25 | 0 | 2024-01-23 | -7 | 25 | 0 | 2023-01-23 | -1.4 | 19.4 | 0 | 2022-01-23 | -18.7 | 36.7 | 0 | 2021-01-23 | -15.6 | 33.6 | 0 | 2020-01-23 | -2.3 | 20.3 | 0 | 2019-01-23 | -3.1 | 21.1 | 0 | 2018-01-23 | 2 | 16 | 0 | 2017-01-23 | -3.1 | 21.1 | 0 | 2016-01-23 | -14.3 | 32.3 | 0 | 25.05 | 0
2025-01-23 | -9.2 | 27.2 | 0 | 2024-01-23 | -7.9 | 25.9 | 0 | 2023-01-23 | -1.6 | 19.6 | 0 | 2022-01-23 | -21.9 | 39.9 | 0 | 2021-01-23 | -16.1 | 34.1 | 0 | 2020-01-23 | -4.2 | 22.2 | 0 | 2019-01-23 | -2.3 | 20.3 | 0 | 2018-01-23 | 0.1 | 17.9 | 0 | 2017-01-23 | -3.2 | 21.2 | 0 | 2016-01-23 | -15.1 | 33.1 | 0 | 26.14 | 0
2025-01-24 | -10.1 | 28.1 | 0 | 2024-01-24 | -8.7 | 26.7 | 0 | 2023-01-24 | -1.6 | 19.6 | 0 | 2022-01-24 | -22.4 | 40.4 | 0 | 2021-01-24 | -16.7 | 34.7 | 0 | 2020-01-24 | -3.4 | 21.4 | 0 | 2019-01-24 | -1.3 | 19.3 | 0 | 2018-01-24 | -3.6 | 21.6 | 0 | 2017-01-24 | -3.2 | 21.2 | 0 | 2016-01-24 | -15 | 33 | 0 | 26.6 | 0
2025-01-24 | -12.2 | 30.2 | 0 | 2024-01-24 | -9.5 | 27.5 | 0 | 2023-01-24 | -1.4 | 19.4 | 0 | 2022-01-24 | -22.8 | 40.8 | 0 | 2021-01-24 | -16.9 | 34.9 | 0 | 2020-01-24 | -3.5 | 21.5 | 0 | 2019-01-24 | -0.4 | 18.4 | 0 | 2018-01-24 | -6.1 | 24.1 | 0 | 2017-01-24 | -3.2 | 21.2 | 0 | 2016-01-24 | -15.8 | 33.8 | 0 | 27.18 | 0
2025-01-24 | -11.6 | 29.6 | 0 | 2024-01-24 | -10 | 28 | 0 | 2023-01-24 | -1 | 19 | 0 | 2022-01-24 | -23.8 | 41.8 | 0 | 2021-01-24 | -17.3 | 35.3 | 0 | 2020-01-24 | -2.5 | 20.5 | 0 | 2019-01-24 | 2.8 | 15.2 | 0 | 2018-01-24 | -7.5 | 25.5 | 0 | 2017-01-24 | -3.1 | 21.1 | 0 | 2016-01-24 | -14.8 | 32.8 | 0 | 26.88 | 0
2025-01-24 | -13.2 | 31.2 | 0 | 2024-01-24 | -10.8 | 28.8 | 0 | 2023-01-24 | -0.7 | 18.7 | 0 | 2022-01-24 | -25.1 | 43.1 | 0 | 2021-01-24 | -17.7 | 35.7 | 0 | 2020-01-24 | -3.3 | 21.3 | 0 | 2019-01-24 | 3.3 | 14.7 | 0 | 2018-01-24 | -8.6 | 26.6 | 0 | 2017-01-24 | -3.1 | 21.1 | 0 | 2016-01-24 | -15.4 | 33.4 | 0 | 27.46 | 0
2025-01-24 | -14.6 | 32.6 | 0 | 2024-01-24 | -10.8 | 28.8 | 0 | 2023-01-24 | -0.6 | 18.6 | 0 | 2022-01-24 | -24.8 | 42.8 | 0 | 2021-01-24 | -18.1 | 36.1 | 0 | 2020-01-24 | -2.6 | 20.6 | 0 | 2019-01-24 | 3.3 | 14.7 | 0 | 2018-01-24 | -9.9 | 27.9 | 0 | 2017-01-24 | -2.9 | 20.9 | 0 | 2016-01-24 | -15.7 | 33.7 | 0 | 27.67 | 0
2025-01-24 | -15.6 | 33.6 | 0 | 2024-01-24 | -10.8 | 28.8 | 0 | 2023-01-24 | -0.6 | 18.6 | 0 | 2022-01-24 | -24.1 | 42.1 | 0 | 2021-01-24 | -18.2 | 36.2 | 0 | 2020-01-24 | -2.6 | 20.6 | 0 | 2019-01-24 | 3.4 | 14.6 | 0 | 2018-01-24 | -10.3 | 28.3 | 0 | 2017-01-24 | -2.5 | 20.5 | 0 | 2016-01-24 | -16.3 | 34.3 | 0 | 27.76 | 0
2025-01-24 | -17.1 | 35.1 | 0 | 2024-01-24 | -10.4 | 28.4 | 0 | 2023-01-24 | -1.3 | 19.3 | 0 | 2022-01-24 | -26.9 | 44.9 | 0 | 2021-01-24 | -18.6 | 36.6 | 0 | 2020-01-24 | -2.2 | 20.2 | 0 | 2019-01-24 | 3.4 | 14.6 | 0 | 2018-01-24 | -11.3 | 29.3 | 0 | 2017-01-24 | -2.3 | 20.3 | 0 | 2016-01-24 | -17 | 35 | 0 | 28.37 | 0
2025-01-24 | -17.4 | 35.4 | 0 | 2024-01-24 | -10.1 | 28.1 | 0 | 2023-01-24 | -1.2 | 19.2 | 0 | 2022-01-24 | -28.2 | 46.2 | 0 | 2021-01-24 | -18.5 | 36.5 | 0 | 2020-01-24 | -1.7 | 19.7 | 0 | 2019-01-24 | 3.2 | 14.8 | 0 | 2018-01-24 | -12 | 30 | 0 | 2017-01-24 | -2.3 | 20.3 | 0 | 2016-01-24 | -17.3 | 35.3 | 0 | 28.55 | 0
2025-01-24 | -18.6 | 36.6 | 0 | 2024-01-24 | -9.8 | 27.8 | 0 | 2023-01-24 | -0.7 | 18.7 | 0 | 2022-01-24 | -27.7 | 45.7 | 0 | 2021-01-24 | -18.7 | 36.7 | 0 | 2020-01-24 | -1.3 | 19.3 | 0 | 2019-01-24 | 2.7 | 15.3 | 0 | 2018-01-24 | -12.3 | 30.3 | 0 | 2017-01-24 | -2.6 | 20.6 | 0 | 2016-01-24 | -17.1 | 35.1 | 0 | 28.61 | 0
2025-01-24 | -17.6 | 35.6 | 0 | 2024-01-24 | -9.4 | 27.4 | 0 | 2023-01-24 | -0.6 | 18.6 | 0 | 2022-01-24 | -25 | 43 | 0 | 2021-01-24 | -18.1 | 36.1 | 0 | 2020-01-24 | -1.4 | 19.4 | 0 | 2019-01-24 | 2 | 16 | 0 | 2018-01-24 | -12.6 | 30.6 | 0 | 2017-01-24 | -2.5 | 20.5 | 0 | 2016-01-24 | -15.8 | 33.8 | 0 | 28.1 | 0
2025-01-24 | -15.5 | 33.5 | 0 | 2024-01-24 | -9.1 | 27.1 | 0 | 2023-01-24 | -0.5 | 18.5 | 0 | 2022-01-24 | -21.8 | 39.8 | 0 | 2021-01-24 | -17.1 | 35.1 | 0 | 2020-01-24 | -0.6 | 18.6 | 0 | 2019-01-24 | 0.6 | 17.4 | 0 | 2018-01-24 | -11.7 | 29.7 | 0 | 2017-01-24 | -2.8 | 20.8 | 0 | 2016-01-24 | -13.4 | 31.4 | 0 | 27.19 | 0
2025-01-24 | -14.5 | 32.5 | 0 | 2024-01-24 | -8.8 | 26.8 | 0 | 2023-01-24 | -0.4 | 18.4 | 0 | 2022-01-24 | -19.4 | 37.4 | 0 | 2021-01-24 | -15.9 | 33.9 | 0 | 2020-01-24 | 0.1 | 17.9 | 0 | 2019-01-24 | 0 | 18 | 0 | 2018-01-24 | -10.8 | 28.8 | 0 | 2017-01-24 | -2.9 | 20.9 | 0 | 2016-01-24 | -11.3 | 29.3 | 0 | 26.39 | 0
2025-01-24 | -12.9 | 30.9 | 0 | 2024-01-24 | -8.6 | 26.6 | 0 | 2023-01-24 | 0.5 | 17.5 | 0 | 2022-01-24 | -17.1 | 35.1 | 0 | 2021-01-24 | -14.6 | 32.6 | 0 | 2020-01-24 | 0.9 | 17.1 | 0 | 2019-01-24 | -0.9 | 18.9 | 0 | 2018-01-24 | -10.1 | 28.1 | 0 | 2017-01-24 | -2.8 | 20.8 | 0 | 2016-01-24 | -9.3 | 27.3 | 0 | 25.49 | 0
2025-01-24 | -12 | 30 | 0 | 2024-01-24 | -8.7 | 26.7 | 0 | 2023-01-24 | 1.1 | 16.9 | 0 | 2022-01-24 | -15.9 | 33.9 | 0 | 2021-01-24 | -13 | 31 | 0 | 2020-01-24 | 0.9 | 17.1 | 0 | 2019-01-24 | -1.2 | 19.2 | 0 | 2018-01-24 | -9.1 | 27.1 | 0 | 2017-01-24 | -2.6 | 20.6 | 0 | 2016-01-24 | -7.9 | 25.9 | 0 | 24.84 | 0
2025-01-24 | -11.7 | 29.7 | 0 | 2024-01-24 | -8.7 | 26.7 | 0 | 2023-01-24 | 1.3 | 16.7 | 0 | 2022-01-24 | -15.9 | 33.9 | 0 | 2021-01-24 | -11.7 | 29.7 | 0 | 2020-01-24 | 1.3 | 16.7 | 0 | 2019-01-24 | -2 | 20 | 0 | 2018-01-24 | -8.9 | 26.9 | 0 | 2017-01-24 | -2.6 | 20.6 | 0 | 2016-01-24 | -6.8 | 24.8 | 0 | 24.57 | 0
2025-01-24 | -11.7 | 29.7 | 0 | 2024-01-24 | -8.2 | 26.2 | 0 | 2023-01-24 | 1.1 | 16.9 | 0 | 2022-01-24 | -14.7 | 32.7 | 0 | 2021-01-24 | -10.9 | 28.9 | 0 | 2020-01-24 | 1.1 | 16.9 | 0 | 2019-01-24 | -3.4 | 21.4 | 0 | 2018-01-24 | -8.5 | 26.5 | 0 | 2017-01-24 | -2.4 | 20.4 | 0 | 2016-01-24 | -6.4 | 24.4 | 0 | 24.4 | 0
2025-01-24 | -12.2 | 30.2 | 0 | 2024-01-24 | -8.1 | 26.1 | 0 | 2023-01-24 | -1.1 | 19.1 | 0 | 2022-01-24 | -14.7 | 32.7 | 0 | 2021-01-24 | -10.9 | 28.9 | 0 | 2020-01-24 | 0.8 | 17.2 | 0 | 2019-01-24 | -4.1 | 22.1 | 0 | 2018-01-24 | -8.9 | 26.9 | 0 | 2017-01-24 | -2.4 | 20.4 | 0 | 2016-01-24 | -6.2 | 24.2 | 0 | 24.78 | 0
2025-01-24 | -12.7 | 30.7 | 0 | 2024-01-24 | -8 | 26 | 0 | 2023-01-24 | -1 | 19 | 0 | 2022-01-24 | -14.4 | 32.4 | 0 | 2021-01-24 | -12.7 | 30.7 | 0 | 2020-01-24 | -0.1 | 18.1 | 0 | 2019-01-24 | -4.5 | 22.5 | 0 | 2018-01-24 | -9.9 | 27.9 | 0 | 2017-01-24 | -2.8 | 20.8 | 0 | 2016-01-24 | -7.2 | 25.2 | 0 | 25.33 | 0
2025-01-24 | -15.4 | 33.4 | 0 | 2024-01-24 | -7.8 | 25.8 | 0 | 2023-01-24 | -2 | 20 | 0 | 2022-01-24 | -15.4 | 33.4 | 0 | 2021-01-24 | -13.7 | 31.7 | 0 | 2020-01-24 | -0.6 | 18.6 | 0 | 2019-01-24 | -4.8 | 22.8 | 0 | 2018-01-24 | -10.2 | 28.2 | 0 | 2017-01-24 | -3 | 21 | 0 | 2016-01-24 | -7.5 | 25.5 | 0 | 26.04 | 0
2025-01-24 | -16.1 | 34.1 | 0 | 2024-01-24 | -7.6 | 25.6 | 0 | 2023-01-24 | -2.7 | 20.7 | 0 | 2022-01-24 | -15.4 | 33.4 | 0 | 2021-01-24 | -13.5 | 31.5 | 0 | 2020-01-24 | -1.5 | 19.5 | 0 | 2019-01-24 | -5 | 23 | 0 | 2018-01-24 | -10.6 | 28.6 | 0 | 2017-01-24 | -3 | 21 | 0 | 2016-01-24 | -7.4 | 25.4 | 0 | 26.28 | 0
2025-01-24 | -15.5 | 33.5 | 0 | 2024-01-24 | -6.6 | 24.6 | 0 | 2023-01-24 | -3.5 | 21.5 | 0 | 2022-01-24 | -15.3 | 33.3 | 0 | 2021-01-24 | -14.4 | 32.4 | 0 | 2020-01-24 | -1.5 | 19.5 | 0 | 2019-01-24 | -5.8 | 23.8 | 0 | 2018-01-24 | -11 | 29 | 0 | 2017-01-24 | -3.2 | 21.2 | 0 | 2016-01-24 | -8.1 | 26.1 | 0 | 26.49 | 0
2025-01-24 | -14.7 | 32.7 | 0 | 2024-01-24 | -6.2 | 24.2 | 0 | 2023-01-24 | -4.4 | 22.4 | 0 | 2022-01-24 | -15.2 | 33.2 | 0 | 2021-01-24 | -14.2 | 32.2 | 0 | 2020-01-24 | -1.9 | 19.9 | 0 | 2019-01-24 | -6.8 | 24.8 | 0 | 2018-01-24 | -11.6 | 29.6 | 0 | 2017-01-24 | -3.2 | 21.2 | 0 | 2016-01-24 | -8.8 | 26.8 | 0 | 26.7 | 0
2025-01-24 | -18.6 | 36.6 | 0 | 2024-01-24 | -5.3 | 23.3 | 0 | 2023-01-24 | -5.6 | 23.6 | 0 | 2022-01-24 | -15.3 | 33.3 | 0 | 2021-01-24 | -14.8 | 32.8 | 0 | 2020-01-24 | -1.9 | 19.9 | 0 | 2019-01-24 | -8.1 | 26.1 | 0 | 2018-01-24 | -12.5 | 30.5 | 0 | 2017-01-24 | -3.2 | 21.2 | 0 | 2016-01-24 | -9.1 | 27.1 | 0 | 27.44 | 0
2025-01-24 | -19.6 | 37.6 | 0 | 2024-01-24 | -4.3 | 22.3 | 0 | 2023-01-24 | -6.5 | 24.5 | 0 | 2022-01-24 | -15.6 | 33.6 | 0 | 2021-01-24 | -14.5 | 32.5 | 0 | 2020-01-24 | -1.5 | 19.5 | 0 | 2019-01-24 | -9.1 | 27.1 | 0 | 2018-01-24 | -13.1 | 31.1 | 0 | 2017-01-24 | -3.3 | 21.3 | 0 | 2016-01-24 | -8.6 | 26.6 | 0 | 27.61 | 0
2025-01-25 | -18.5 | 36.5 | 0 | 2024-01-25 | -4 | 22 | 0 | 2023-01-25 | -8 | 26 | 0 | 2022-01-25 | -15.4 | 33.4 | 0 | 2021-01-25 | -16.2 | 34.2 | 0 | 2020-01-25 | -1.4 | 19.4 | 0 | 2019-01-25 | -10.2 | 28.2 | 0 | 2018-01-25 | -13.9 | 31.9 | 0 | 2017-01-25 | -3.4 | 21.4 | 0 | 2016-01-25 | -8.2 | 26.2 | 0 | 27.92 | 0
2025-01-25 | -19.8 | 37.8 | 0 | 2024-01-25 | -3.7 | 21.7 | 0 | 2023-01-25 | -8.3 | 26.3 | 0 | 2022-01-25 | -15.4 | 33.4 | 0 | 2021-01-25 | -16.7 | 34.7 | 0 | 2020-01-25 | -1.4 | 19.4 | 0 | 2019-01-25 | -10.3 | 28.3 | 0 | 2018-01-25 | -14.6 | 32.6 | 0 | 2017-01-25 | -3.4 | 21.4 | 0 | 2016-01-25 | -7.8 | 25.8 | 0 | 28.14 | 0
2025-01-25 | -18.3 | 36.3 | 0 | 2024-01-25 | -3.4 | 21.4 | 0 | 2023-01-25 | -10.4 | 28.4 | 0 | 2022-01-25 | -15.3 | 33.3 | 0 | 2021-01-25 | -16.8 | 34.8 | 0 | 2020-01-25 | -1.4 | 19.4 | 0 | 2019-01-25 | -11.8 | 29.8 | 0 | 2018-01-25 | -15.4 | 33.4 | 0 | 2017-01-25 | -3.5 | 21.5 | 0 | 2016-01-25 | -7.5 | 25.5 | 0 | 28.38 | 0
2025-01-25 | -18.4 | 36.4 | 0 | 2024-01-25 | -3 | 21 | 0 | 2023-01-25 | -10.2 | 28.2 | 0 | 2022-01-25 | -15.3 | 33.3 | 0 | 2021-01-25 | -15.5 | 33.5 | 0 | 2020-01-25 | -1.7 | 19.7 | 0 | 2019-01-25 | -11.1 | 29.1 | 0 | 2018-01-25 | -15.8 | 33.8 | 0 | 2017-01-25 | -3.4 | 21.4 | 0 | 2016-01-25 | -7.3 | 25.3 | 0 | 28.17 | 0
2025-01-25 | -17.8 | 35.8 | 0 | 2024-01-25 | -2.8 | 20.8 | 0 | 2023-01-25 | -10.6 | 28.6 | 0 | 2022-01-25 | -15.6 | 33.6 | 0 | 2021-01-25 | -15.3 | 33.3 | 0 | 2020-01-25 | -1.8 | 19.8 | 0 | 2019-01-25 | -10.9 | 28.9 | 0 | 2018-01-25 | -16.4 | 34.4 | 0 | 2017-01-25 | -3.6 | 21.6 | 0 | 2016-01-25 | -7 | 25 | 0 | 28.18 | 0
2025-01-25 | -17 | 35 | 0 | 2024-01-25 | -2.9 | 20.9 | 0 | 2023-01-25 | -10.5 | 28.5 | 0 | 2022-01-25 | -15.5 | 33.5 | 0 | 2021-01-25 | -16.9 | 34.9 | 0 | 2020-01-25 | -2 | 20 | 0 | 2019-01-25 | -10.9 | 28.9 | 0 | 2018-01-25 | -16.9 | 34.9 | 0 | 2017-01-25 | -3.5 | 21.5 | 0 | 2016-01-25 | -6.6 | 24.6 | 0 | 28.27 | 0
2025-01-25 | -16.1 | 34.1 | 0 | 2024-01-25 | -2.9 | 20.9 | 0 | 2023-01-25 | -10.2 | 28.2 | 0 | 2022-01-25 | -15.3 | 33.3 | 0 | 2021-01-25 | -15.9 | 33.9 | 0 | 2020-01-25 | -2.1 | 20.1 | 0 | 2019-01-25 | -11.2 | 29.2 | 0 | 2018-01-25 | -17.2 | 35.2 | 0 | 2017-01-25 | -3.4 | 21.4 | 0 | 2016-01-25 | -6.6 | 24.6 | 0 | 28.09 | 0
2025-01-25 | -15.8 | 33.8 | 0 | 2024-01-25 | -2.7 | 20.7 | 0 | 2023-01-25 | -10.5 | 28.5 | 0 | 2022-01-25 | -15.4 | 33.4 | 0 | 2021-01-25 | -17.8 | 35.8 | 0 | 2020-01-25 | -2.4 | 20.4 | 0 | 2019-01-25 | -11.2 | 29.2 | 0 | 2018-01-25 | -17.4 | 35.4 | 0 | 2017-01-25 | -3.3 | 21.3 | 0 | 2016-01-25 | -6.7 | 24.7 | 0 | 28.32 | 0
2025-01-25 | -16.1 | 34.1 | 0 | 2024-01-25 | -2.5 | 20.5 | 0 | 2023-01-25 | -10.7 | 28.7 | 0 | 2022-01-25 | -15.5 | 33.5 | 0 | 2021-01-25 | -16.2 | 34.2 | 0 | 2020-01-25 | -2.5 | 20.5 | 0 | 2019-01-25 | -11 | 29 | 0 | 2018-01-25 | -17.3 | 35.3 | 0 | 2017-01-25 | -3.3 | 21.3 | 0 | 2016-01-25 | -6.7 | 24.7 | 0 | 28.18 | 0
2025-01-25 | -15.1 | 33.1 | 0 | 2024-01-25 | -2.4 | 20.4 | 0 | 2023-01-25 | -10.3 | 28.3 | 0 | 2022-01-25 | -14.9 | 32.9 | 0 | 2021-01-25 | -13.9 | 31.9 | 0 | 2020-01-25 | -2 | 20 | 0 | 2019-01-25 | -10.5 | 28.5 | 0 | 2018-01-25 | -16.7 | 34.7 | 0 | 2017-01-25 | -2.9 | 20.9 | 0 | 2016-01-25 | -6 | 24 | 0 | 27.47 | 0
2025-01-25 | -12.6 | 30.6 | 0 | 2024-01-25 | -2 | 20 | 0 | 2023-01-25 | -10 | 28 | 0 | 2022-01-25 | -14.3 | 32.3 | 0 | 2021-01-25 | -11.8 | 29.8 | 0 | 2020-01-25 | -1.4 | 19.4 | 0 | 2019-01-25 | -8.1 | 26.1 | 0 | 2018-01-25 | -15.7 | 33.7 | 0 | 2017-01-25 | -2.6 | 20.6 | 0 | 2016-01-25 | -4.2 | 22.2 | 0 | 26.27 | 0
2025-01-25 | -9.6 | 27.6 | 0 | 2024-01-25 | -1.4 | 19.4 | 0 | 2023-01-25 | -10.1 | 28.1 | 0 | 2022-01-25 | -12.8 | 30.8 | 0 | 2021-01-25 | -10.6 | 28.6 | 0 | 2020-01-25 | -0.8 | 18.8 | 0 | 2019-01-25 | -3.7 | 21.7 | 0 | 2018-01-25 | -14.6 | 32.6 | 0 | 2017-01-25 | -1.9 | 19.9 | 0 | 2016-01-25 | -2.6 | 20.6 | 0 | 24.81 | 0
2025-01-25 | -7.9 | 25.9 | 0 | 2024-01-25 | -0.8 | 18.8 | 0 | 2023-01-25 | -10.5 | 28.5 | 0 | 2022-01-25 | -12 | 30 | 0 | 2021-01-25 | -9.6 | 27.6 | 0 | 2020-01-25 | -0.1 | 18.1 | 0 | 2019-01-25 | -3 | 21 | 0 | 2018-01-25 | -13.2 | 31.2 | 0 | 2017-01-25 | -1.3 | 19.3 | 0 | 2016-01-25 | -1.3 | 19.3 | 0 | 23.97 | 0
2025-01-25 | -6.8 | 24.8 | 0 | 2024-01-25 | -0.4 | 18.4 | 0 | 2023-01-25 | -10.8 | 28.8 | 0 | 2022-01-25 | -11 | 29 | 0 | 2021-01-25 | -8.6 | 26.6 | 0 | 2020-01-25 | 0.1 | 17.9 | 0 | 2019-01-25 | -3.2 | 21.2 | 0 | 2018-01-25 | -12.2 | 30.2 | 0 | 2017-01-25 | -0.8 | 18.8 | 0 | 2016-01-25 | -0.8 | 18.8 | 0 | 23.45 | 0
2025-01-25 | -6.3 | 24.3 | 0 | 2024-01-25 | -0.2 | 18.2 | 0 | 2023-01-25 | -10.4 | 28.4 | 0 | 2022-01-25 | -10.5 | 28.5 | 0 | 2021-01-25 | -8 | 26 | 0 | 2020-01-25 | -0.4 | 18.4 | 0 | 2019-01-25 | -4.6 | 22.6 | 0 | 2018-01-25 | -11.8 | 29.8 | 0 | 2017-01-25 | -0.5 | 18.5 | 0 | 2016-01-25 | -1.6 | 19.6 | 0 | 23.43 | 0
2025-01-25 | -6.5 | 24.5 | 0 | 2024-01-25 | -0.1 | 18.1 | 0 | 2023-01-25 | -10.6 | 28.6 | 0 | 2022-01-25 | -10.6 | 28.6 | 0 | 2021-01-25 | -7.5 | 25.5 | 0 | 2020-01-25 | -0.4 | 18.4 | 0 | 2019-01-25 | -5 | 23 | 0 | 2018-01-25 | -10.9 | 28.9 | 0 | 2017-01-25 | -0.1 | 18.1 | 0 | 2016-01-25 | -1.9 | 19.9 | 0 | 23.36 | 0
2025-01-25 | -6.3 | 24.3 | 0 | 2024-01-25 | -0.1 | 18.1 | 0 | 2023-01-25 | -10.5 | 28.5 | 0 | 2022-01-25 | -11.4 | 29.4 | 0 | 2021-01-25 | -7.6 | 25.6 | 0 | 2020-01-25 | -0.4 | 18.4 | 0 | 2019-01-25 | -6.2 | 24.2 | 0 | 2018-01-25 | -10.7 | 28.7 | 0 | 2017-01-25 | 0.1 | 17.9 | 0 | 2016-01-25 | -1.6 | 19.6 | 0 | 23.47 | 0
2025-01-25 | -6.2 | 24.2 | 0 | 2024-01-25 | 0 | 18 | 0 | 2023-01-25 | -10.3 | 28.3 | 0 | 2022-01-25 | -12.8 | 30.8 | 0 | 2021-01-25 | -7.8 | 25.8 | 0 | 2020-01-25 | 0.1 | 17.9 | 0 | 2019-01-25 | -7.7 | 25.7 | 0 | 2018-01-25 | -11.1 | 29.1 | 0 | 2017-01-25 | 0.2 | 17.8 | 0 | 2016-01-25 | -1.8 | 19.8 | 0 | 23.74 | 0
2025-01-25 | -6.3 | 24.3 | 0 | 2024-01-25 | 0 | 18 | 0 | 2023-01-25 | -10.2 | 28.2 | 0 | 2022-01-25 | -14.3 | 32.3 | 0 | 2021-01-25 | -7.9 | 25.9 | 0 | 2020-01-25 | 0 | 18 | 0 | 2019-01-25 | -9 | 27 | 0 | 2018-01-25 | -11.1 | 29.1 | 0 | 2017-01-25 | 0.1 | 17.9 | 0 | 2016-01-25 | -1.9 | 19.9 | 0 | 24.06 | 0
2025-01-25 | -6.2 | 24.2 | 0 | 2024-01-25 | 0 | 18 | 0 | 2023-01-25 | -10.2 | 28.2 | 0 | 2022-01-25 | -15.7 | 33.7 | 0 | 2021-01-25 | -8 | 26 | 0 | 2020-01-25 | 0.1 | 17.9 | 0 | 2019-01-25 | -10.3 | 28.3 | 0 | 2018-01-25 | -11.6 | 29.6 | 0 | 2017-01-25 | -0.1 | 18.1 | 0 | 2016-01-25 | -3 | 21 | 0 | 24.5 | 0
2025-01-25 | -6.1 | 24.1 | 0 | 2024-01-25 | -0.1 | 18.1 | 0 | 2023-01-25 | -9.8 | 27.8 | 0 | 2022-01-25 | -15 | 33 | 0 | 2021-01-25 | -8 | 26 | 0 | 2020-01-25 | 0.2 | 17.8 | 0 | 2019-01-25 | -11.4 | 29.4 | 0 | 2018-01-25 | -13.1 | 31.1 | 0 | 2017-01-25 | 0.2 | 17.8 | 0 | 2016-01-25 | -2.4 | 20.4 | 0 | 24.55 | 0
2025-01-25 | -5.5 | 23.5 | 0 | 2024-01-25 | -0.2 | 18.2 | 0 | 2023-01-25 | -9.2 | 27.2 | 0 | 2022-01-25 | -15.8 | 33.8 | 0 | 2021-01-25 | -8.2 | 26.2 | 0 | 2020-01-25 | 0.3 | 17.7 | 0 | 2019-01-25 | -11.9 | 29.9 | 0 | 2018-01-25 | -13.2 | 31.2 | 0 | 2017-01-25 | 0.7 | 17.3 | 0 | 2016-01-25 | -3.7 | 21.7 | 0 | 24.67 | 0
2025-01-25 | -5 | 23 | 0 | 2024-01-25 | -0.3 | 18.3 | 0 | 2023-01-25 | -8.8 | 26.8 | 0 | 2022-01-25 | -17.2 | 35.2 | 0 | 2021-01-25 | -8.1 | 26.1 | 0 | 2020-01-25 | 0.2 | 17.8 | 0 | 2019-01-25 | -12.1 | 30.1 | 0 | 2018-01-25 | -14.8 | 32.8 | 0 | 2017-01-25 | 0.4 | 17.6 | 0 | 2016-01-25 | -4.3 | 22.3 | 0 | 25 | 0
2025-01-25 | -5.3 | 23.3 | 0 | 2024-01-25 | -0.5 | 18.5 | 0 | 2023-01-25 | -8.4 | 26.4 | 0 | 2022-01-25 | -18 | 36 | 0 | 2021-01-25 | -7.9 | 25.9 | 0 | 2020-01-25 | 0 | 18 | 0 | 2019-01-25 | -12.5 | 30.5 | 0 | 2018-01-25 | -15.1 | 33.1 | 0 | 2017-01-25 | 0.2 | 17.8 | 0 | 2016-01-25 | -4.9 | 22.9 | 0 | 25.24 | 0
2025-01-26 | -5.1 | 23.1 | 0 | 2024-01-26 | -0.5 | 18.5 | 0 | 2023-01-26 | -7.9 | 25.9 | 0 | 2022-01-26 | -19.1 | 37.1 | 0 | 2021-01-26 | -8 | 26 | 0 | 2020-01-26 | 0.1 | 17.9 | 0 | 2019-01-26 | -13.1 | 31.1 | 0 | 2018-01-26 | -15 | 33 | 0 | 2017-01-26 | 0.2 | 17.8 | 0 | 2016-01-26 | -4 | 22 | 0 | 25.24 | 0
2025-01-26 | -4 | 22 | 0 | 2024-01-26 | -0.6 | 18.6 | 0 | 2023-01-26 | -7.3 | 25.3 | 0 | 2022-01-26 | -20.3 | 38.3 | 0 | 2021-01-26 | -7.8 | 25.8 | 0 | 2020-01-26 | 0.1 | 17.9 | 0 | 2019-01-26 | -13.7 | 31.7 | 0 | 2018-01-26 | -15.7 | 33.7 | 0 | 2017-01-26 | 0.3 | 17.7 | 0 | 2016-01-26 | -3.5 | 21.5 | 0 | 25.25 | 0
2025-01-26 | -3.6 | 21.6 | 0 | 2024-01-26 | -0.8 | 18.8 | 0 | 2023-01-26 | -6.9 | 24.9 | 0 | 2022-01-26 | -22 | 40 | 0 | 2021-01-26 | -7.6 | 25.6 | 0 | 2020-01-26 | 0.1 | 17.9 | 0 | 2019-01-26 | -13.9 | 31.9 | 0 | 2018-01-26 | -16.5 | 34.5 | 0 | 2017-01-26 | 0.3 | 17.7 | 0 | 2016-01-26 | -6.3 | 24.3 | 0 | 25.72 | 0
2025-01-26 | -2.9 | 20.9 | 0 | 2024-01-26 | -1.1 | 19.1 | 0 | 2023-01-26 | -6.4 | 24.4 | 0 | 2022-01-26 | -22.6 | 40.6 | 0 | 2021-01-26 | -7.4 | 25.4 | 0 | 2020-01-26 | 0 | 18 | 0 | 2019-01-26 | -14.7 | 32.7 | 0 | 2018-01-26 | -16.9 | 34.9 | 0 | 2017-01-26 | 0.2 | 17.8 | 0 | 2016-01-26 | -4.7 | 22.7 | 0 | 25.65 | 0
2025-01-26 | -2.3 | 20.3 | 0 | 2024-01-26 | -1.2 | 19.2 | 0 | 2023-01-26 | -5.8 | 23.8 | 0 | 2022-01-26 | -23.1 | 41.1 | 0 | 2021-01-26 | -7.5 | 25.5 | 0 | 2020-01-26 | 0 | 18 | 0 | 2019-01-26 | -15.6 | 33.6 | 0 | 2018-01-26 | -16.9 | 34.9 | 0 | 2017-01-26 | 0.1 | 17.9 | 0 | 2016-01-26 | -4 | 22 | 0 | 25.63 | 0
2025-01-26 | -2.4 | 20.4 | 0 | 2024-01-26 | -1.2 | 19.2 | 0 | 2023-01-26 | -5.5 | 23.5 | 0 | 2022-01-26 | -23.3 | 41.3 | 0 | 2021-01-26 | -7.7 | 25.7 | 0 | 2020-01-26 | 0 | 18 | 0 | 2019-01-26 | -16.5 | 34.5 | 0 | 2018-01-26 | -17.2 | 35.2 | 0 | 2017-01-26 | 0.2 | 17.8 | 0 | 2016-01-26 | -2.9 | 20.9 | 0 | 25.65 | 0
2025-01-26 | -2.5 | 20.5 | 0 | 2024-01-26 | -1.3 | 19.3 | 0 | 2023-01-26 | -5.3 | 23.3 | 0 | 2022-01-26 | -24.7 | 42.7 | 0 | 2021-01-26 | -7.6 | 25.6 | 0 | 2020-01-26 | 0.1 | 17.9 | 0 | 2019-01-26 | -17.2 | 35.2 | 0 | 2018-01-26 | -17.5 | 35.5 | 0 | 2017-01-26 | 0.2 | 17.8 | 0 | 2016-01-26 | 0 | 18 | 0 | 25.58 | 0
2025-01-26 | -2.5 | 20.5 | 0 | 2024-01-26 | -1 | 19 | 0 | 2023-01-26 | -5.4 | 23.4 | 0 | 2022-01-26 | -27.3 | 45.3 | 0 | 2021-01-26 | -7.5 | 25.5 | 0 | 2020-01-26 | 0 | 18 | 0 | 2019-01-26 | -17.2 | 35.2 | 0 | 2018-01-26 | -18.2 | 36.2 | 0 | 2017-01-26 | 0.3 | 17.7 | 0 | 2016-01-26 | 0.3 | 17.7 | 0 | 25.85 | 0
2025-01-26 | -2.5 | 20.5 | 0 | 2024-01-26 | -0.6 | 18.6 | 0 | 2023-01-26 | -6.3 | 24.3 | 0 | 2022-01-26 | -26.5 | 44.5 | 0 | 2021-01-26 | -7.3 | 25.3 | 0 | 2020-01-26 | 0.1 | 17.9 | 0 | 2019-01-26 | -18.6 | 36.6 | 0 | 2018-01-26 | -17.8 | 35.8 | 0 | 2017-01-26 | 0.5 | 17.5 | 0 | 2016-01-26 | 0.8 | 17.2 | 0 | 25.82 | 0
2025-01-26 | -2.4 | 20.4 | 0 | 2024-01-26 | -0.4 | 18.4 | 0 | 2023-01-26 | -6.9 | 24.9 | 0 | 2022-01-26 | -25.7 | 43.7 | 0 | 2021-01-26 | -7 | 25 | 0 | 2020-01-26 | 0.2 | 17.8 | 0 | 2019-01-26 | -18.1 | 36.1 | 0 | 2018-01-26 | -15.5 | 33.5 | 0 | 2017-01-26 | 0.4 | 17.6 | 0 | 2016-01-26 | 1.3 | 16.7 | 0 | 25.41 | 0
2025-01-26 | -3.8 | 21.8 | 0 | 2024-01-26 | -0.1 | 18.1 | 0 | 2023-01-26 | -7.2 | 25.2 | 0 | 2022-01-26 | -22.7 | 40.7 | 0 | 2021-01-26 | -6.4 | 24.4 | 0 | 2020-01-26 | 0.3 | 17.7 | 0 | 2019-01-26 | -16.3 | 34.3 | 0 | 2018-01-26 | -13.7 | 31.7 | 0 | 2017-01-26 | 0.3 | 17.7 | 0 | 2016-01-26 | 2.1 | 15.9 | 0 | 24.75 | 0
2025-01-26 | -3.6 | 21.6 | 0 | 2024-01-26 | 0 | 18 | 0 | 2023-01-26 | -6.7 | 24.7 | 0 | 2022-01-26 | -20.8 | 38.8 | 0 | 2021-01-26 | -5.7 | 23.7 | 0 | 2020-01-26 | 0.3 | 17.7 | 0 | 2019-01-26 | -14.9 | 32.9 | 0 | 2018-01-26 | -11.2 | 29.2 | 0 | 2017-01-26 | 0.3 | 17.7 | 0 | 2016-01-26 | 2.9 | 15.1 | 0 | 23.94 | 0
2025-01-26 | -2.8 | 20.8 | 0 | 2024-01-26 | 0.4 | 17.6 | 0 | 2023-01-26 | -6.8 | 24.8 | 0 | 2022-01-26 | -19.5 | 37.5 | 0 | 2021-01-26 | -4.7 | 22.7 | 0 | 2020-01-26 | 0.3 | 17.7 | 0 | 2019-01-26 | -14.2 | 32.2 | 0 | 2018-01-26 | -9.2 | 27.2 | 0 | 2017-01-26 | -0.1 | 18.1 | 0 | 2016-01-26 | 3.4 | 14.6 | 0 | 23.32 | 0
2025-01-26 | -2.6 | 20.6 | 0 | 2024-01-26 | 0.9 | 17.1 | 0 | 2023-01-26 | -6.3 | 24.3 | 0 | 2022-01-26 | -19 | 37 | 0 | 2021-01-26 | -4.5 | 22.5 | 0 | 2020-01-26 | 0.4 | 17.6 | 0 | 2019-01-26 | -13.5 | 31.5 | 0 | 2018-01-26 | -7.8 | 25.8 | 0 | 2017-01-26 | -0.3 | 18.3 | 0 | 2016-01-26 | 3.7 | 14.3 | 0 | 22.9 | 0
2025-01-26 | -2.2 | 20.2 | 0 | 2024-01-26 | 0.9 | 17.1 | 0 | 2023-01-26 | -5.9 | 23.9 | 0 | 2022-01-26 | -18.3 | 36.3 | 0 | 2021-01-26 | -4.5 | 22.5 | 0 | 2020-01-26 | 0.3 | 17.7 | 0 | 2019-01-26 | -13 | 31 | 0 | 2018-01-26 | -7 | 25 | 0 | 2017-01-26 | -0.1 | 18.1 | 0 | 2016-01-26 | 4.5 | 13.5 | 0 | 22.53 | 0
2025-01-26 | -2.6 | 20.6 | 0 | 2024-01-26 | 1 | 17 | 0 | 2023-01-26 | -5.2 | 23.2 | 0 | 2022-01-26 | -18 | 36 | 0 | 2021-01-26 | -4.4 | 22.4 | 0 | 2020-01-26 | 0.6 | 17.4 | 0 | 2019-01-26 | -12.2 | 30.2 | 0 | 2018-01-26 | -6.5 | 24.5 | 0 | 2017-01-26 | -0.3 | 18.3 | 0 | 2016-01-26 | 5 | 13 | 0 | 22.26 | 0
2025-01-26 | -3.2 | 21.2 | 0 | 2024-01-26 | 1.4 | 16.6 | 0 | 2023-01-26 | -5 | 23 | 0 | 2022-01-26 | -18 | 36 | 0 | 2021-01-26 | -4.3 | 22.3 | 0 | 2020-01-26 | 0.8 | 17.2 | 0 | 2019-01-26 | -12.5 | 30.5 | 0 | 2018-01-26 | -6.3 | 24.3 | 0 | 2017-01-26 | -0.4 | 18.4 | 0 | 2016-01-26 | 4.8 | 13.2 | 0 | 22.27 | 0
2025-01-26 | -4.5 | 22.5 | 0 | 2024-01-26 | 1.4 | 16.6 | 0 | 2023-01-26 | -4.6 | 22.6 | 0 | 2022-01-26 | -20.3 | 38.3 | 0 | 2021-01-26 | -5.1 | 23.1 | 0 | 2020-01-26 | 0.9 | 17.1 | 0 | 2019-01-26 | -15.5 | 33.5 | 0 | 2018-01-26 | -7.5 | 25.5 | 0 | 2017-01-26 | -0.3 | 18.3 | 0 | 2016-01-26 | 3.9 | 14.1 | 0 | 23.16 | 0
2025-01-26 | -5.5 | 23.5 | 0 | 2024-01-26 | 1.3 | 16.7 | 0 | 2023-01-26 | -5.2 | 23.2 | 0 | 2022-01-26 | -20.3 | 38.3 | 0 | 2021-01-26 | -5.5 | 23.5 | 0 | 2020-01-26 | 1.2 | 16.8 | 0 | 2019-01-26 | -15.2 | 33.2 | 0 | 2018-01-26 | -8.6 | 26.6 | 0 | 2017-01-26 | 0 | 18 | 0 | 2016-01-26 | 3.2 | 14.8 | 0 | 23.46 | 0
2025-01-26 | -6.8 | 24.8 | 0 | 2024-01-26 | 1.2 | 16.8 | 0 | 2023-01-26 | -5.5 | 23.5 | 0 | 2022-01-26 | -22.3 | 40.3 | 0 | 2021-01-26 | -5.8 | 23.8 | 0 | 2020-01-26 | 1.3 | 16.7 | 0 | 2019-01-26 | -15.9 | 33.9 | 0 | 2018-01-26 | -9.1 | 27.1 | 0 | 2017-01-26 | 0 | 18 | 0 | 2016-01-26 | 3.3 | 14.7 | 0 | 23.96 | 0
2025-01-26 | -6.3 | 24.3 | 0 | 2024-01-26 | 1 | 17 | 0 | 2023-01-26 | -5.5 | 23.5 | 0 | 2022-01-26 | -21.5 | 39.5 | 0 | 2021-01-26 | -6 | 24 | 0 | 2020-01-26 | 1.2 | 16.8 | 0 | 2019-01-26 | -16 | 34 | 0 | 2018-01-26 | -9.7 | 27.7 | 0 | 2017-01-26 | 0.2 | 17.8 | 0 | 2016-01-26 | 3.1 | 14.9 | 0 | 23.95 | 0
2025-01-26 | -5.7 | 23.7 | 0 | 2024-01-26 | 0.5 | 17.5 | 0 | 2023-01-26 | -7.3 | 25.3 | 0 | 2022-01-26 | -22.3 | 40.3 | 0 | 2021-01-26 | -5.7 | 23.7 | 0 | 2020-01-26 | 1 | 17 | 0 | 2019-01-26 | -15.9 | 33.9 | 0 | 2018-01-26 | -10.8 | 28.8 | 0 | 2017-01-26 | 0.1 | 17.9 | 0 | 2016-01-26 | 2.8 | 15.2 | 0 | 24.33 | 0
2025-01-26 | -4.7 | 22.7 | 0 | 2024-01-26 | 0.6 | 17.4 | 0 | 2023-01-26 | -8 | 26 | 0 | 2022-01-26 | -21.8 | 39.8 | 0 | 2021-01-26 | -5.7 | 23.7 | 0 | 2020-01-26 | 0.8 | 17.2 | 0 | 2019-01-26 | -16.3 | 34.3 | 0 | 2018-01-26 | -10.9 | 28.9 | 0 | 2017-01-26 | 0.4 | 17.6 | 0 | 2016-01-26 | 1.3 | 16.7 | 0 | 24.43 | 0
2025-01-26 | -4.1 | 22.1 | 0 | 2024-01-26 | 0.4 | 17.6 | 0 | 2023-01-26 | -8.1 | 26.1 | 0 | 2022-01-26 | -23.5 | 41.5 | 0 | 2021-01-26 | -5.7 | 23.7 | 0 | 2020-01-26 | 0.8 | 17.2 | 0 | 2019-01-26 | -15.8 | 33.8 | 0 | 2018-01-26 | -11.3 | 29.3 | 0 | 2017-01-26 | 0.4 | 17.6 | 0 | 2016-01-26 | 0.6 | 17.4 | 0 | 24.63 | 0
2025-01-27 | -3.9 | 21.9 | 0 | 2024-01-27 | 0.4 | 17.6 | 0 | 2023-01-27 | -7.1 | 25.1 | 0 | 2022-01-27 | -23 | 41 | 0 | 2021-01-27 | -5.6 | 23.6 | 0 | 2020-01-27 | 0.7 | 17.3 | 0 | 2019-01-27 | -16 | 34 | 0 | 2018-01-27 | -11.6 | 29.6 | 0 | 2017-01-27 | 0.5 | 17.5 | 0 | 2016-01-27 | 0.3 | 17.7 | 0 | 24.53 | 0
2025-01-27 | -4.1 | 22.1 | 0 | 2024-01-27 | 0.3 | 17.7 | 0 | 2023-01-27 | -7.7 | 25.7 | 0 | 2022-01-27 | -23.4 | 41.4 | 0 | 2021-01-27 | -5.3 | 23.3 | 0 | 2020-01-27 | 0.7 | 17.3 | 0 | 2019-01-27 | -16.2 | 34.2 | 0 | 2018-01-27 | -12.2 | 30.2 | 0 | 2017-01-27 | 0.3 | 17.7 | 0 | 2016-01-27 | -0.8 | 18.8 | 0 | 24.84 | 0
2025-01-27 | -4.2 | 22.2 | 0 | 2024-01-27 | 0.2 | 17.8 | 0 | 2023-01-27 | -8.8 | 26.8 | 0 | 2022-01-27 | -24.7 | 42.7 | 0 | 2021-01-27 | -5 | 23 | 0 | 2020-01-27 | 0.7 | 17.3 | 0 | 2019-01-27 | -16.2 | 34.2 | 0 | 2018-01-27 | -12.1 | 30.1 | 0 | 2017-01-27 | 0.1 | 17.9 | 0 | 2016-01-27 | -1.8 | 19.8 | 0 | 25.18 | 0
2025-01-27 | -5.1 | 23.1 | 0 | 2024-01-27 | 0.1 | 17.9 | 0 | 2023-01-27 | -9.4 | 27.4 | 0 | 2022-01-27 | -24 | 42 | 0 | 2021-01-27 | -5.2 | 23.2 | 0 | 2020-01-27 | 0.4 | 17.6 | 0 | 2019-01-27 | -16 | 34 | 0 | 2018-01-27 | -12.3 | 30.3 | 0 | 2017-01-27 | 0.1 | 17.9 | 0 | 2016-01-27 | -2.6 | 20.6 | 0 | 25.4 | 0
2025-01-27 | -5 | 23 | 0 | 2024-01-27 | 0 | 18 | 0 | 2023-01-27 | -10.1 | 28.1 | 0 | 2022-01-27 | -24.2 | 42.2 | 0 | 2021-01-27 | -5.2 | 23.2 | 0 | 2020-01-27 | 0.3 | 17.7 | 0 | 2019-01-27 | -15.2 | 33.2 | 0 | 2018-01-27 | -11.6 | 29.6 | 0 | 2017-01-27 | 0 | 18 | 0 | 2016-01-27 | -3 | 21 | 0 | 25.4 | 0
2025-01-27 | -4.7 | 22.7 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -10.3 | 28.3 | 0 | 2022-01-27 | -24.6 | 42.6 | 0 | 2021-01-27 | -5.5 | 23.5 | 0 | 2020-01-27 | 0.3 | 17.7 | 0 | 2019-01-27 | -14.3 | 32.3 | 0 | 2018-01-27 | -10.9 | 28.9 | 0 | 2017-01-27 | -0.3 | 18.3 | 0 | 2016-01-27 | -4.3 | 22.3 | 0 | 25.47 | 0
2025-01-27 | -5 | 23 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -10.2 | 28.2 | 0 | 2022-01-27 | -22.4 | 40.4 | 0 | 2021-01-27 | -7.8 | 25.8 | 0 | 2020-01-27 | 0.3 | 17.7 | 0 | 2019-01-27 | -13.1 | 31.1 | 0 | 2018-01-27 | -10.6 | 28.6 | 0 | 2017-01-27 | -0.8 | 18.8 | 0 | 2016-01-27 | -5.1 | 23.1 | 0 | 25.48 | 0
2025-01-27 | -5.5 | 23.5 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -10.9 | 28.9 | 0 | 2022-01-27 | -22.3 | 40.3 | 0 | 2021-01-27 | -6.8 | 24.8 | 0 | 2020-01-27 | 0.2 | 17.8 | 0 | 2019-01-27 | -11.8 | 29.8 | 0 | 2018-01-27 | -9.9 | 27.9 | 0 | 2017-01-27 | -1 | 19 | 0 | 2016-01-27 | -6.6 | 24.6 | 0 | 25.47 | 0
2025-01-27 | -4.5 | 22.5 | 0 | 2024-01-27 | -0.2 | 18.2 | 0 | 2023-01-27 | -10.9 | 28.9 | 0 | 2022-01-27 | -20.8 | 38.8 | 0 | 2021-01-27 | -6.2 | 24.2 | 0 | 2020-01-27 | 0.3 | 17.7 | 0 | 2019-01-27 | -11.3 | 29.3 | 0 | 2018-01-27 | -9.4 | 27.4 | 0 | 2017-01-27 | -1 | 19 | 0 | 2016-01-27 | -7.2 | 25.2 | 0 | 25.12 | 0
2025-01-27 | -3.9 | 21.9 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -10.3 | 28.3 | 0 | 2022-01-27 | -19.5 | 37.5 | 0 | 2021-01-27 | -6.6 | 24.6 | 0 | 2020-01-27 | 0.4 | 17.6 | 0 | 2019-01-27 | -10.4 | 28.4 | 0 | 2018-01-27 | -8.6 | 26.6 | 0 | 2017-01-27 | -1.4 | 19.4 | 0 | 2016-01-27 | -7.5 | 25.5 | 0 | 24.79 | 0
2025-01-27 | -3.1 | 21.1 | 0 | 2024-01-27 | 0.3 | 17.7 | 0 | 2023-01-27 | -9.7 | 27.7 | 0 | 2022-01-27 | -11.8 | 29.8 | 0 | 2021-01-27 | -6.8 | 24.8 | 0 | 2020-01-27 | 0.6 | 17.4 | 0 | 2019-01-27 | -5.3 | 23.3 | 0 | 2018-01-27 | -6.6 | 24.6 | 0 | 2017-01-27 | -1.3 | 19.3 | 0 | 2016-01-27 | -7.2 | 25.2 | 0 | 23.09 | 0
2025-01-27 | -1.9 | 19.9 | 0 | 2024-01-27 | 0.4 | 17.6 | 0 | 2023-01-27 | -8.8 | 26.8 | 0 | 2022-01-27 | -10.2 | 28.2 | 0 | 2021-01-27 | -6.7 | 24.7 | 0 | 2020-01-27 | 0.8 | 17.2 | 0 | 2019-01-27 | -3.4 | 21.4 | 0 | 2018-01-27 | -2.9 | 20.9 | 0 | 2017-01-27 | -0.9 | 18.9 | 0 | 2016-01-27 | -6.5 | 24.5 | 0 | 22.01 | 0
2025-01-27 | -0.5 | 18.5 | 0 | 2024-01-27 | 0.5 | 17.5 | 0 | 2023-01-27 | -8.3 | 26.3 | 0 | 2022-01-27 | -8.9 | 26.9 | 0 | 2021-01-27 | -5.5 | 23.5 | 0 | 2020-01-27 | 1 | 17 | 0 | 2019-01-27 | -5.5 | 23.5 | 0 | 2018-01-27 | 5.7 | 12.3 | 0 | 2017-01-27 | -0.9 | 18.9 | 0 | 2016-01-27 | -6.5 | 24.5 | 0 | 20.89 | 0
2025-01-27 | 0.4 | 17.6 | 0 | 2024-01-27 | 0.7 | 17.3 | 0 | 2023-01-27 | -7.4 | 25.4 | 0 | 2022-01-27 | -7.4 | 25.4 | 0 | 2021-01-27 | -4.5 | 22.5 | 0 | 2020-01-27 | 1.1 | 16.9 | 0 | 2019-01-27 | -5 | 23 | 0 | 2018-01-27 | 6 | 12 | 0 | 2017-01-27 | -0.8 | 18.8 | 0 | 2016-01-27 | -6.2 | 24.2 | 0 | 20.31 | 0
2025-01-27 | 0.7 | 17.3 | 0 | 2024-01-27 | 1.1 | 16.9 | 0 | 2023-01-27 | -6.5 | 24.5 | 0 | 2022-01-27 | -6.8 | 24.8 | 0 | 2021-01-27 | -4.1 | 22.1 | 0 | 2020-01-27 | 1.1 | 16.9 | 0 | 2019-01-27 | -5 | 23 | 0 | 2018-01-27 | 6.5 | 11.5 | 0 | 2017-01-27 | -1.3 | 19.3 | 0 | 2016-01-27 | -5.8 | 23.8 | 0 | 20.01 | 0
2025-01-27 | 0.9 | 17.1 | 0 | 2024-01-27 | 1.1 | 16.9 | 0 | 2023-01-27 | -6 | 24 | 0 | 2022-01-27 | -6.5 | 24.5 | 0 | 2021-01-27 | -5.1 | 23.1 | 0 | 2020-01-27 | 1.1 | 16.9 | 0 | 2019-01-27 | -6 | 24 | 0 | 2018-01-27 | 6.6 | 11.4 | 0 | 2017-01-27 | -1.2 | 19.2 | 0 | 2016-01-27 | -5.5 | 23.5 | 0 | 20.06 | 0
2025-01-27 | 0 | 18 | 0 | 2024-01-27 | 1 | 17 | 0 | 2023-01-27 | -5.8 | 23.8 | 0 | 2022-01-27 | -6.4 | 24.4 | 0 | 2021-01-27 | -5.6 | 23.6 | 0 | 2020-01-27 | 0.3 | 17.7 | 0 | 2019-01-27 | -7.9 | 25.9 | 0 | 2018-01-27 | 6.3 | 11.7 | 0 | 2017-01-27 | -1.3 | 19.3 | 0 | 2016-01-27 | -5.6 | 23.6 | 0 | 20.5 | 0
2025-01-27 | -0.4 | 18.4 | 0 | 2024-01-27 | 0.8 | 17.2 | 0 | 2023-01-27 | -6.2 | 24.2 | 0 | 2022-01-27 | -5.9 | 23.9 | 0 | 2021-01-27 | -6 | 24 | 0 | 2020-01-27 | -0.1 | 18.1 | 0 | 2019-01-27 | -8.7 | 26.7 | 0 | 2018-01-27 | 5.8 | 12.2 | 0 | 2017-01-27 | -1.4 | 19.4 | 0 | 2016-01-27 | -6.5 | 24.5 | 0 | 20.86 | 0
2025-01-27 | -0.4 | 18.4 | 0 | 2024-01-27 | 0.6 | 17.4 | 0 | 2023-01-27 | -6 | 24 | 0 | 2022-01-27 | -5.9 | 23.9 | 0 | 2021-01-27 | -6.1 | 24.1 | 0 | 2020-01-27 | -0.2 | 18.2 | 0 | 2019-01-27 | -10.4 | 28.4 | 0 | 2018-01-27 | 4.9 | 13.1 | 0 | 2017-01-27 | -1.7 | 19.7 | 0 | 2016-01-27 | -7.9 | 25.9 | 0 | 21.31 | 0
2025-01-27 | -0.4 | 18.4 | 0 | 2024-01-27 | 0.4 | 17.6 | 0 | 2023-01-27 | -5.6 | 23.6 | 0 | 2022-01-27 | -6.2 | 24.2 | 0 | 2021-01-27 | -6.1 | 24.1 | 0 | 2020-01-27 | -0.5 | 18.5 | 0 | 2019-01-27 | -11.4 | 29.4 | 0 | 2018-01-27 | 4.8 | 13.2 | 0 | 2017-01-27 | -1.9 | 19.9 | 0 | 2016-01-27 | -9.1 | 27.1 | 0 | 21.6 | 0
2025-01-27 | -1.6 | 19.6 | 0 | 2024-01-27 | 0.2 | 17.8 | 0 | 2023-01-27 | -4.2 | 22.2 | 0 | 2022-01-27 | -6 | 24 | 0 | 2021-01-27 | -6.3 | 24.3 | 0 | 2020-01-27 | -0.5 | 18.5 | 0 | 2019-01-27 | -12.6 | 30.6 | 0 | 2018-01-27 | 4.8 | 13.2 | 0 | 2017-01-27 | -1.8 | 19.8 | 0 | 2016-01-27 | -10.7 | 28.7 | 0 | 21.87 | 0
2025-01-27 | -2.3 | 20.3 | 0 | 2024-01-27 | 0 | 18 | 0 | 2023-01-27 | -3.5 | 21.5 | 0 | 2022-01-27 | -4.8 | 22.8 | 0 | 2021-01-27 | -6.5 | 24.5 | 0 | 2020-01-27 | -0.8 | 18.8 | 0 | 2019-01-27 | -14.4 | 32.4 | 0 | 2018-01-27 | 4.6 | 13.4 | 0 | 2017-01-27 | -1.8 | 19.8 | 0 | 2016-01-27 | -10 | 28 | 0 | 21.95 | 0
2025-01-27 | -2.1 | 20.1 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -3.6 | 21.6 | 0 | 2022-01-27 | -4.3 | 22.3 | 0 | 2021-01-27 | -6.7 | 24.7 | 0 | 2020-01-27 | -1.1 | 19.1 | 0 | 2019-01-27 | -16.3 | 34.3 | 0 | 2018-01-27 | 4.6 | 13.4 | 0 | 2017-01-27 | -1.9 | 19.9 | 0 | 2016-01-27 | -9.8 | 27.8 | 0 | 22.13 | 0
2025-01-27 | -1.7 | 19.7 | 0 | 2024-01-27 | -0.1 | 18.1 | 0 | 2023-01-27 | -4 | 22 | 0 | 2022-01-27 | -4.2 | 22.2 | 0 | 2021-01-27 | -6.8 | 24.8 | 0 | 2020-01-27 | -1.2 | 19.2 | 0 | 2019-01-27 | -18.9 | 36.9 | 0 | 2018-01-27 | 4.5 | 13.5 | 0 | 2017-01-27 | -2.5 | 20.5 | 0 | 2016-01-27 | -9.3 | 27.3 | 0 | 22.42 | 0
2025-01-28 | -1.6 | 19.6 | 0 | 2024-01-28 | -0.1 | 18.1 | 0 | 2023-01-28 | -3.3 | 21.3 | 0 | 2022-01-28 | -4.4 | 22.4 | 0 | 2021-01-28 | -7 | 25 | 0 | 2020-01-28 | -1.4 | 19.4 | 0 | 2019-01-28 | -18.8 | 36.8 | 0 | 2018-01-28 | 4.1 | 13.9 | 0 | 2017-01-28 | -2.3 | 20.3 | 0 | 2016-01-28 | -9.1 | 27.1 | 0 | 22.39 | 0
2025-01-28 | -6.1 | 24.1 | 0 | 2024-01-28 | -0.2 | 18.2 | 0 | 2023-01-28 | -1.9 | 19.9 | 0 | 2022-01-28 | -4.4 | 22.4 | 0 | 2021-01-28 | -7.5 | 25.5 | 0 | 2020-01-28 | -1.9 | 19.9 | 0 | 2019-01-28 | -18.8 | 36.8 | 0 | 2018-01-28 | 4 | 14 | 0 | 2017-01-28 | -2.4 | 20.4 | 0 | 2016-01-28 | -7.1 | 25.1 | 0 | 22.63 | 0
2025-01-28 | -6.6 | 24.6 | 0 | 2024-01-28 | -0.1 | 18.1 | 0 | 2023-01-28 | -2 | 20 | 0 | 2022-01-28 | -5.3 | 23.3 | 0 | 2021-01-28 | -8.5 | 26.5 | 0 | 2020-01-28 | -1.9 | 19.9 | 0 | 2019-01-28 | -19.9 | 37.9 | 0 | 2018-01-28 | 2.8 | 15.2 | 0 | 2017-01-28 | -2.2 | 20.2 | 0 | 2016-01-28 | -6.7 | 24.7 | 0 | 23.04 | 0
2025-01-28 | -8.6 | 26.6 | 0 | 2024-01-28 | -0.2 | 18.2 | 0 | 2023-01-28 | -2.3 | 20.3 | 0 | 2022-01-28 | -9.4 | 27.4 | 0 | 2021-01-28 | -9.3 | 27.3 | 0 | 2020-01-28 | -2 | 20 | 0 | 2019-01-28 | -20.5 | 38.5 | 0 | 2018-01-28 | 1.2 | 16.8 | 0 | 2017-01-28 | -2.9 | 20.9 | 0 | 2016-01-28 | -5.9 | 23.9 | 0 | 23.99 | 0
2025-01-28 | -10.8 | 28.8 | 0 | 2024-01-28 | -0.3 | 18.3 | 0 | 2023-01-28 | -2.3 | 20.3 | 0 | 2022-01-28 | -12.1 | 30.1 | 0 | 2021-01-28 | -10 | 28 | 0 | 2020-01-28 | -2.4 | 20.4 | 0 | 2019-01-28 | -21.8 | 39.8 | 0 | 2018-01-28 | 0.6 | 17.4 | 0 | 2017-01-28 | -3.9 | 21.9 | 0 | 2016-01-28 | -5.1 | 23.1 | 0 | 24.81 | 0
2025-01-28 | -13.9 | 31.9 | 0 | 2024-01-28 | -0.3 | 18.3 | 0 | 2023-01-28 | -1.8 | 19.8 | 0 | 2022-01-28 | -14.8 | 32.8 | 0 | 2021-01-28 | -11.5 | 29.5 | 0 | 2020-01-28 | -2.8 | 20.8 | 0 | 2019-01-28 | -22.5 | 40.5 | 0 | 2018-01-28 | 0.3 | 17.7 | 0 | 2017-01-28 | -4.6 | 22.6 | 0 | 2016-01-28 | -4.4 | 22.4 | 0 | 25.63 | 0
2025-01-28 | -15.3 | 33.3 | 0 | 2024-01-28 | -0.5 | 18.5 | 0 | 2023-01-28 | -1 | 19 | 0 | 2022-01-28 | -16.7 | 34.7 | 0 | 2021-01-28 | -11.9 | 29.9 | 0 | 2020-01-28 | -3.2 | 21.2 | 0 | 2019-01-28 | -22.7 | 40.7 | 0 | 2018-01-28 | 0.2 | 17.8 | 0 | 2017-01-28 | -5.7 | 23.7 | 0 | 2016-01-28 | -3.6 | 21.6 | 0 | 26.04 | 0
2025-01-28 | -16.2 | 34.2 | 0 | 2024-01-28 | -0.5 | 18.5 | 0 | 2023-01-28 | -0.6 | 18.6 | 0 | 2022-01-28 | -17.9 | 35.9 | 0 | 2021-01-28 | -12.2 | 30.2 | 0 | 2020-01-28 | -3.6 | 21.6 | 0 | 2019-01-28 | -25.1 | 43.1 | 0 | 2018-01-28 | -0.5 | 18.5 | 0 | 2017-01-28 | -5.7 | 23.7 | 0 | 2016-01-28 | -3.4 | 21.4 | 0 | 26.57 | 0
2025-01-28 | -16.7 | 34.7 | 0 | 2024-01-28 | -0.5 | 18.5 | 0 | 2023-01-28 | -0.2 | 18.2 | 0 | 2022-01-28 | -19.1 | 37.1 | 0 | 2021-01-28 | -12.1 | 30.1 | 0 | 2020-01-28 | -4.2 | 22.2 | 0 | 2019-01-28 | -24.2 | 42.2 | 0 | 2018-01-28 | -0.6 | 18.6 | 0 | 2017-01-28 | -4.7 | 22.7 | 0 | 2016-01-28 | -2.7 | 20.7 | 0 | 26.5 | 0
2025-01-28 | -16.2 | 34.2 | 0 | 2024-01-28 | -0.4 | 18.4 | 0 | 2023-01-28 | -0.4 | 18.4 | 0 | 2022-01-28 | -19.1 | 37.1 | 0 | 2021-01-28 | -11.9 | 29.9 | 0 | 2020-01-28 | -4 | 22 | 0 | 2019-01-28 | -24.1 | 42.1 | 0 | 2018-01-28 | 0.7 | 17.3 | 0 | 2017-01-28 | -3.4 | 21.4 | 0 | 2016-01-28 | -1.9 | 19.9 | 0 | 26.07 | 0
2025-01-28 | -15.7 | 33.7 | 0 | 2024-01-28 | -0.1 | 18.1 | 0 | 2023-01-28 | 0.1 | 17.9 | 0 | 2022-01-28 | -18.2 | 36.2 | 0 | 2021-01-28 | -12 | 30 | 0 | 2020-01-28 | -3.7 | 21.7 | 0 | 2019-01-28 | -23.9 | 41.9 | 0 | 2018-01-28 | 1.8 | 16.2 | 0 | 2017-01-28 | -2.2 | 20.2 | 0 | 2016-01-28 | -2.3 | 20.3 | 0 | 25.62 | 0
2025-01-28 | -14.6 | 32.6 | 0 | 2024-01-28 | 0.2 | 17.8 | 0 | 2023-01-28 | -0.1 | 18.1 | 0 | 2022-01-28 | -17.5 | 35.5 | 0 | 2021-01-28 | -12.2 | 30.2 | 0 | 2020-01-28 | -3.1 | 21.1 | 0 | 2019-01-28 | -22.9 | 40.9 | 0 | 2018-01-28 | 2.3 | 15.7 | 0 | 2017-01-28 | -1.4 | 19.4 | 0 | 2016-01-28 | -1.6 | 19.6 | 0 | 25.09 | 0
2025-01-28 | -14.2 | 32.2 | 0 | 2024-01-28 | 0.8 | 17.2 | 0 | 2023-01-28 | -1.1 | 19.1 | 0 | 2022-01-28 | -17.1 | 35.1 | 0 | 2021-01-28 | -12.5 | 30.5 | 0 | 2020-01-28 | -3 | 21 | 0 | 2019-01-28 | -21.6 | 39.6 | 0 | 2018-01-28 | 2.8 | 15.2 | 0 | 2017-01-28 | -1.1 | 19.1 | 0 | 2016-01-28 | -1.6 | 19.6 | 0 | 24.86 | 0
2025-01-28 | -13.6 | 31.6 | 0 | 2024-01-28 | 1.2 | 16.8 | 0 | 2023-01-28 | -0.4 | 18.4 | 0 | 2022-01-28 | -16 | 34 | 0 | 2021-01-28 | -12.5 | 30.5 | 0 | 2020-01-28 | -3.2 | 21.2 | 0 | 2019-01-28 | -21.1 | 39.1 | 0 | 2018-01-28 | 2.2 | 15.8 | 0 | 2017-01-28 | -0.7 | 18.7 | 0 | 2016-01-28 | -1.5 | 19.5 | 0 | 24.56 | 0
2025-01-28 | -13 | 31 | 0 | 2024-01-28 | 1.4 | 16.6 | 0 | 2023-01-28 | -0.4 | 18.4 | 0 | 2022-01-28 | -15.3 | 33.3 | 0 | 2021-01-28 | -11.9 | 29.9 | 0 | 2020-01-28 | -3.5 | 21.5 | 0 | 2019-01-28 | -19.7 | 37.7 | 0 | 2018-01-28 | 2.6 | 15.4 | 0 | 2017-01-28 | -0.3 | 18.3 | 0 | 2016-01-28 | -1.4 | 19.4 | 0 | 24.15 | 0
2025-01-28 | -12.5 | 30.5 | 0 | 2024-01-28 | 1.6 | 16.4 | 0 | 2023-01-28 | -0.1 | 18.1 | 0 | 2022-01-28 | -15.1 | 33.1 | 0 | 2021-01-28 | -12.5 | 30.5 | 0 | 2020-01-28 | -3.7 | 21.7 | 0 | 2019-01-28 | -20.1 | 38.1 | 0 | 2018-01-28 | 1.5 | 16.5 | 0 | 2017-01-28 | 0.2 | 17.8 | 0 | 2016-01-28 | -1.4 | 19.4 | 0 | 24.21 | 0
2025-01-28 | -11.9 | 29.9 | 0 | 2024-01-28 | 1.4 | 16.6 | 0 | 2023-01-28 | -0.9 | 18.9 | 0 | 2022-01-28 | -15.2 | 33.2 | 0 | 2021-01-28 | -12.9 | 30.9 | 0 | 2020-01-28 | -3.8 | 21.8 | 0 | 2019-01-28 | -19.7 | 37.7 | 0 | 2018-01-28 | 0.6 | 17.4 | 0 | 2017-01-28 | -0.1 | 18.1 | 0 | 2016-01-28 | -1.2 | 19.2 | 0 | 24.37 | 0
2025-01-28 | -11.6 | 29.6 | 0 | 2024-01-28 | 1 | 17 | 0 | 2023-01-28 | -1.4 | 19.4 | 0 | 2022-01-28 | -16.1 | 34.1 | 0 | 2021-01-28 | -13.9 | 31.9 | 0 | 2020-01-28 | -4.1 | 22.1 | 0 | 2019-01-28 | -19.8 | 37.8 | 0 | 2018-01-28 | 0 | 18 | 0 | 2017-01-28 | -0.3 | 18.3 | 0 | 2016-01-28 | -1 | 19 | 0 | 24.72 | 0
2025-01-28 | -11.8 | 29.8 | 0 | 2024-01-28 | 0.7 | 17.3 | 0 | 2023-01-28 | -1.6 | 19.6 | 0 | 2022-01-28 | -17.5 | 35.5 | 0 | 2021-01-28 | -14.6 | 32.6 | 0 | 2020-01-28 | -4.3 | 22.3 | 0 | 2019-01-28 | -20.2 | 38.2 | 0 | 2018-01-28 | -0.4 | 18.4 | 0 | 2017-01-28 | -0.6 | 18.6 | 0 | 2016-01-28 | -0.9 | 18.9 | 0 | 25.12 | 0
2025-01-28 | -11.9 | 29.9 | 0 | 2024-01-28 | 0.8 | 17.2 | 0 | 2023-01-28 | -1.9 | 19.9 | 0 | 2022-01-28 | -18.4 | 36.4 | 0 | 2021-01-28 | -15.2 | 33.2 | 0 | 2020-01-28 | -4.6 | 22.6 | 0 | 2019-01-28 | -20.2 | 38.2 | 0 | 2018-01-28 | -0.8 | 18.8 | 0 | 2017-01-28 | -0.7 | 18.7 | 0 | 2016-01-28 | -1.1 | 19.1 | 0 | 25.4 | 0
2025-01-28 | -11.2 | 29.2 | 0 | 2024-01-28 | 0.6 | 17.4 | 0 | 2023-01-28 | -2.3 | 20.3 | 0 | 2022-01-28 | -18.5 | 36.5 | 0 | 2021-01-28 | -15.4 | 33.4 | 0 | 2020-01-28 | -4.6 | 22.6 | 0 | 2019-01-28 | -19.7 | 37.7 | 0 | 2018-01-28 | -2.2 | 20.2 | 0 | 2017-01-28 | -0.9 | 18.9 | 0 | 2016-01-28 | -1.1 | 19.1 | 0 | 25.53 | 0
2025-01-28 | -11.6 | 29.6 | 0 | 2024-01-28 | 0.6 | 17.4 | 0 | 2023-01-28 | -2.8 | 20.8 | 0 | 2022-01-28 | -19.1 | 37.1 | 0 | 2021-01-28 | -16.2 | 34.2 | 0 | 2020-01-28 | -4.8 | 22.8 | 0 | 2019-01-28 | -19.7 | 37.7 | 0 | 2018-01-28 | -3.8 | 21.8 | 0 | 2017-01-28 | -1.4 | 19.4 | 0 | 2016-01-28 | -0.7 | 18.7 | 0 | 25.95 | 0
2025-01-28 | -11.9 | 29.9 | 0 | 2024-01-28 | 0.6 | 17.4 | 0 | 2023-01-28 | -3.2 | 21.2 | 0 | 2022-01-28 | -19.7 | 37.7 | 0 | 2021-01-28 | -16.6 | 34.6 | 0 | 2020-01-28 | -5.5 | 23.5 | 0 | 2019-01-28 | -19.5 | 37.5 | 0 | 2018-01-28 | -5 | 23 | 0 | 2017-01-28 | -1.5 | 19.5 | 0 | 2016-01-28 | -0.8 | 18.8 | 0 | 26.31 | 0
2025-01-28 | -11.8 | 29.8 | 0 | 2024-01-28 | 0.5 | 17.5 | 0 | 2023-01-28 | -3.5 | 21.5 | 0 | 2022-01-28 | -21 | 39 | 0 | 2021-01-28 | -17.1 | 35.1 | 0 | 2020-01-28 | -6.6 | 24.6 | 0 | 2019-01-28 | -19 | 37 | 0 | 2018-01-28 | -5.7 | 23.7 | 0 | 2017-01-28 | -1.6 | 19.6 | 0 | 2016-01-28 | -0.6 | 18.6 | 0 | 26.64 | 0
2025-01-29 | -11.7 | 29.7 | 0 | 2024-01-29 | 0.2 | 17.8 | 0 | 2023-01-29 | -4.2 | 22.2 | 0 | 2022-01-29 | -21 | 39 | 0 | 2021-01-29 | -17.9 | 35.9 | 0 | 2020-01-29 | -8.2 | 26.2 | 0 | 2019-01-29 | -18.7 | 36.7 | 0 | 2018-01-29 | -6.6 | 24.6 | 0 | 2017-01-29 | -1.7 | 19.7 | 0 | 2016-01-29 | 0.1 | 17.9 | 0 | 26.97 | 0
2025-01-29 | -12.5 | 30.5 | 0 | 2024-01-29 | -0.2 | 18.2 | 0 | 2023-01-29 | -4.8 | 22.8 | 0 | 2022-01-29 | -21.4 | 39.4 | 0 | 2021-01-29 | -18.2 | 36.2 | 0 | 2020-01-29 | -8.8 | 26.8 | 0 | 2019-01-29 | -18.8 | 36.8 | 0 | 2018-01-29 | -7.3 | 25.3 | 0 | 2017-01-29 | -1.9 | 19.9 | 0 | 2016-01-29 | 0.4 | 17.6 | 0 | 27.35 | 0
2025-01-29 | -12.8 | 30.8 | 0 | 2024-01-29 | -0.6 | 18.6 | 0 | 2023-01-29 | -5.1 | 23.1 | 0 | 2022-01-29 | -22 | 40 | 0 | 2021-01-29 | -18.5 | 36.5 | 0 | 2020-01-29 | -9.5 | 27.5 | 0 | 2019-01-29 | -18.8 | 36.8 | 0 | 2018-01-29 | -7.9 | 25.9 | 0 | 2017-01-29 | -2.3 | 20.3 | 0 | 2016-01-29 | 0.2 | 17.8 | 0 | 27.73 | 0
2025-01-29 | -12.8 | 30.8 | 0 | 2024-01-29 | -1.2 | 19.2 | 0 | 2023-01-29 | -5.4 | 23.4 | 0 | 2022-01-29 | -22.4 | 40.4 | 0 | 2021-01-29 | -18.5 | 36.5 | 0 | 2020-01-29 | -9.6 | 27.6 | 0 | 2019-01-29 | -18.8 | 36.8 | 0 | 2018-01-29 | -8.6 | 26.6 | 0 | 2017-01-29 | -2.2 | 20.2 | 0 | 2016-01-29 | -0.4 | 18.4 | 0 | 27.99 | 0
2025-01-29 | -13.1 | 31.1 | 0 | 2024-01-29 | -1.4 | 19.4 | 0 | 2023-01-29 | -5.3 | 23.3 | 0 | 2022-01-29 | -21.9 | 39.9 | 0 | 2021-01-29 | -19.1 | 37.1 | 0 | 2020-01-29 | -10.8 | 28.8 | 0 | 2019-01-29 | -18.6 | 36.6 | 0 | 2018-01-29 | -9.3 | 27.3 | 0 | 2017-01-29 | -3 | 21 | 0 | 2016-01-29 | -0.7 | 18.7 | 0 | 28.32 | 0
2025-01-29 | -12.9 | 30.9 | 0 | 2024-01-29 | -1.5 | 19.5 | 0 | 2023-01-29 | -5.7 | 23.7 | 0 | 2022-01-29 | -22.7 | 40.7 | 0 | 2021-01-29 | -18.8 | 36.8 | 0 | 2020-01-29 | -11.6 | 29.6 | 0 | 2019-01-29 | -18.3 | 36.3 | 0 | 2018-01-29 | -9.8 | 27.8 | 0 | 2017-01-29 | -4.1 | 22.1 | 0 | 2016-01-29 | -0.8 | 18.8 | 0 | 28.62 | 0
2025-01-29 | -12.9 | 30.9 | 0 | 2024-01-29 | -1.5 | 19.5 | 0 | 2023-01-29 | -5.9 | 23.9 | 0 | 2022-01-29 | -23.4 | 41.4 | 0 | 2021-01-29 | -19.4 | 37.4 | 0 | 2020-01-29 | -12.3 | 30.3 | 0 | 2019-01-29 | -18.1 | 36.1 | 0 | 2018-01-29 | -10.8 | 28.8 | 0 | 2017-01-29 | -5.9 | 23.9 | 0 | 2016-01-29 | -1.2 | 19.2 | 0 | 29.14 | 0
2025-01-29 | -12.8 | 30.8 | 0 | 2024-01-29 | -1.7 | 19.7 | 0 | 2023-01-29 | -6.3 | 24.3 | 0 | 2022-01-29 | -24.1 | 42.1 | 0 | 2021-01-29 | -19.5 | 37.5 | 0 | 2020-01-29 | -12.2 | 30.2 | 0 | 2019-01-29 | -18 | 36 | 0 | 2018-01-29 | -11.1 | 29.1 | 0 | 2017-01-29 | -6.8 | 24.8 | 0 | 2016-01-29 | -1.5 | 19.5 | 0 | 29.4 | 0
2025-01-29 | -13 | 31 | 0 | 2024-01-29 | -1.9 | 19.9 | 0 | 2023-01-29 | -6.5 | 24.5 | 0 | 2022-01-29 | -23.2 | 41.2 | 0 | 2021-01-29 | -19.4 | 37.4 | 0 | 2020-01-29 | -12.2 | 30.2 | 0 | 2019-01-29 | -17.3 | 35.3 | 0 | 2018-01-29 | -11.6 | 29.6 | 0 | 2017-01-29 | -5.7 | 23.7 | 0 | 2016-01-29 | -1.4 | 19.4 | 0 | 29.22 | 0
2025-01-29 | -12.7 | 30.7 | 0 | 2024-01-29 | -2.1 | 20.1 | 0 | 2023-01-29 | -7.6 | 25.6 | 0 | 2022-01-29 | -22.2 | 40.2 | 0 | 2021-01-29 | -18.9 | 36.9 | 0 | 2020-01-29 | -12.2 | 30.2 | 0 | 2019-01-29 | -16.5 | 34.5 | 0 | 2018-01-29 | -11.4 | 29.4 | 0 | 2017-01-29 | -5.6 | 23.6 | 0 | 2016-01-29 | -1.4 | 19.4 | 0 | 29.06 | 0
2025-01-29 | -11.9 | 29.9 | 0 | 2024-01-29 | -2.2 | 20.2 | 0 | 2023-01-29 | -8.7 | 26.7 | 0 | 2022-01-29 | -19.9 | 37.9 | 0 | 2021-01-29 | -17.4 | 35.4 | 0 | 2020-01-29 | -11.5 | 29.5 | 0 | 2019-01-29 | -15.7 | 33.7 | 0 | 2018-01-29 | -10.2 | 28.2 | 0 | 2017-01-29 | -4.7 | 22.7 | 0 | 2016-01-29 | -3.5 | 21.5 | 0 | 28.57 | 0
2025-01-29 | -10.5 | 28.5 | 0 | 2024-01-29 | -2.3 | 20.3 | 0 | 2023-01-29 | -8.9 | 26.9 | 0 | 2022-01-29 | -18.1 | 36.1 | 0 | 2021-01-29 | -15.9 | 33.9 | 0 | 2020-01-29 | -10.7 | 28.7 | 0 | 2019-01-29 | -14.4 | 32.4 | 0 | 2018-01-29 | -9.4 | 27.4 | 0 | 2017-01-29 | -4.5 | 22.5 | 0 | 2016-01-29 | -5.5 | 23.5 | 0 | 28.02 | 0
2025-01-29 | -9.9 | 27.9 | 0 | 2024-01-29 | -2.2 | 20.2 | 0 | 2023-01-29 | -8.6 | 26.6 | 0 | 2022-01-29 | -17 | 35 | 0 | 2021-01-29 | -14.6 | 32.6 | 0 | 2020-01-29 | -9.4 | 27.4 | 0 | 2019-01-29 | -13.1 | 31.1 | 0 | 2018-01-29 | -9 | 27 | 0 | 2017-01-29 | -3.9 | 21.9 | 0 | 2016-01-29 | -6.3 | 24.3 | 0 | 27.4 | 0
2025-01-29 | -9.2 | 27.2 | 0 | 2024-01-29 | -2.2 | 20.2 | 0 | 2023-01-29 | -8 | 26 | 0 | 2022-01-29 | -16 | 34 | 0 | 2021-01-29 | -13.3 | 31.3 | 0 | 2020-01-29 | -8.9 | 26.9 | 0 | 2019-01-29 | -11.9 | 29.9 | 0 | 2018-01-29 | -8.1 | 26.1 | 0 | 2017-01-29 | -4.2 | 22.2 | 0 | 2016-01-29 | -6.7 | 24.7 | 0 | 26.85 | 0
2025-01-29 | -9.3 | 27.3 | 0 | 2024-01-29 | -2.2 | 20.2 | 0 | 2023-01-29 | -7.2 | 25.2 | 0 | 2022-01-29 | -14.6 | 32.6 | 0 | 2021-01-29 | -12.2 | 30.2 | 0 | 2020-01-29 | -8.3 | 26.3 | 0 | 2019-01-29 | -11.2 | 29.2 | 0 | 2018-01-29 | -7.3 | 25.3 | 0 | 2017-01-29 | -3.9 | 21.9 | 0 | 2016-01-29 | -6.9 | 24.9 | 0 | 26.31 | 0
2025-01-29 | -9.4 | 27.4 | 0 | 2024-01-29 | -1.6 | 19.6 | 0 | 2023-01-29 | -6.8 | 24.8 | 0 | 2022-01-29 | -13.6 | 31.6 | 0 | 2021-01-29 | -11.8 | 29.8 | 0 | 2020-01-29 | -8 | 26 | 0 | 2019-01-29 | -10.2 | 28.2 | 0 | 2018-01-29 | -7 | 25 | 0 | 2017-01-29 | -3.8 | 21.8 | 0 | 2016-01-29 | -7.2 | 25.2 | 0 | 25.94 | 0
2025-01-29 | -9.4 | 27.4 | 0 | 2024-01-29 | -1.3 | 19.3 | 0 | 2023-01-29 | -6.5 | 24.5 | 0 | 2022-01-29 | -13.1 | 31.1 | 0 | 2021-01-29 | -11.8 | 29.8 | 0 | 2020-01-29 | -8 | 26 | 0 | 2019-01-29 | -10 | 28 | 0 | 2018-01-29 | -7 | 25 | 0 | 2017-01-29 | -3.9 | 21.9 | 0 | 2016-01-29 | -7.9 | 25.9 | 0 | 25.89 | 0
2025-01-29 | -9.4 | 27.4 | 0 | 2024-01-29 | -2.3 | 20.3 | 0 | 2023-01-29 | -6.7 | 24.7 | 0 | 2022-01-29 | -14 | 32 | 0 | 2021-01-29 | -12.7 | 30.7 | 0 | 2020-01-29 | -8.9 | 26.9 | 0 | 2019-01-29 | -10.1 | 28.1 | 0 | 2018-01-29 | -7.7 | 25.7 | 0 | 2017-01-29 | -5.7 | 23.7 | 0 | 2016-01-29 | -8.9 | 26.9 | 0 | 26.64 | 0
2025-01-29 | -9.3 | 27.3 | 0 | 2024-01-29 | -3.3 | 21.3 | 0 | 2023-01-29 | -6.7 | 24.7 | 0 | 2022-01-29 | -14 | 32 | 0 | 2021-01-29 | -12.5 | 30.5 | 0 | 2020-01-29 | -10.1 | 28.1 | 0 | 2019-01-29 | -10.2 | 28.2 | 0 | 2018-01-29 | -8.3 | 26.3 | 0 | 2017-01-29 | -6.2 | 24.2 | 0 | 2016-01-29 | -10.3 | 28.3 | 0 | 27.09 | 0
2025-01-29 | -9.9 | 27.9 | 0 | 2024-01-29 | -4.6 | 22.6 | 0 | 2023-01-29 | -5.9 | 23.9 | 0 | 2022-01-29 | -15.8 | 33.8 | 0 | 2021-01-29 | -14.5 | 32.5 | 0 | 2020-01-29 | -10.8 | 28.8 | 0 | 2019-01-29 | -10.2 | 28.2 | 0 | 2018-01-29 | -9 | 27 | 0 | 2017-01-29 | -6.9 | 24.9 | 0 | 2016-01-29 | -10.2 | 28.2 | 0 | 27.78 | 0
2025-01-29 | -10.7 | 28.7 | 0 | 2024-01-29 | -5 | 23 | 0 | 2023-01-29 | -8.7 | 26.7 | 0 | 2022-01-29 | -14.8 | 32.8 | 0 | 2021-01-29 | -14.9 | 32.9 | 0 | 2020-01-29 | -11.6 | 29.6 | 0 | 2019-01-29 | -10.2 | 28.2 | 0 | 2018-01-29 | -9.4 | 27.4 | 0 | 2017-01-29 | -7.8 | 25.8 | 0 | 2016-01-29 | -9.9 | 27.9 | 0 | 28.3 | 0
2025-01-29 | -11.8 | 29.8 | 0 | 2024-01-29 | -5.9 | 23.9 | 0 | 2023-01-29 | -10.7 | 28.7 | 0 | 2022-01-29 | -15.3 | 33.3 | 0 | 2021-01-29 | -16.2 | 34.2 | 0 | 2020-01-29 | -11.2 | 29.2 | 0 | 2019-01-29 | -10.3 | 28.3 | 0 | 2018-01-29 | -10.1 | 28.1 | 0 | 2017-01-29 | -7.9 | 25.9 | 0 | 2016-01-29 | -10.2 | 28.2 | 0 | 28.96 | 0
2025-01-29 | -12.9 | 30.9 | 0 | 2024-01-29 | -6 | 24 | 0 | 2023-01-29 | -10.4 | 28.4 | 0 | 2022-01-29 | -18.7 | 36.7 | 0 | 2021-01-29 | -16.2 | 34.2 | 0 | 2020-01-29 | -12.8 | 30.8 | 0 | 2019-01-29 | -10.4 | 28.4 | 0 | 2018-01-29 | -10.2 | 28.2 | 0 | 2017-01-29 | -8.7 | 26.7 | 0 | 2016-01-29 | -10.9 | 28.9 | 0 | 29.72 | 0
2025-01-29 | -15 | 33 | 0 | 2024-01-29 | -6.5 | 24.5 | 0 | 2023-01-29 | -12.3 | 30.3 | 0 | 2022-01-29 | -16.4 | 34.4 | 0 | 2021-01-29 | -17.5 | 35.5 | 0 | 2020-01-29 | -12.6 | 30.6 | 0 | 2019-01-29 | -10.2 | 28.2 | 0 | 2018-01-29 | -9.8 | 27.8 | 0 | 2017-01-29 | -8.9 | 26.9 | 0 | 2016-01-29 | -12.2 | 30.2 | 0 | 30.14 | 0
2025-01-30 | -16.1 | 34.1 | 0 | 2024-01-30 | -6.2 | 24.2 | 0 | 2023-01-30 | -11.3 | 29.3 | 0 | 2022-01-30 | -16.8 | 34.8 | 0 | 2021-01-30 | -17.8 | 35.8 | 0 | 2020-01-30 | -13 | 31 | 0 | 2019-01-30 | -9.9 | 27.9 | 0 | 2018-01-30 | -9.4 | 27.4 | 0 | 2017-01-30 | -9.4 | 27.4 | 0 | 2016-01-30 | -11.6 | 29.6 | 0 | 30.15 | 0
2025-01-30 | -17.1 | 35.1 | 0 | 2024-01-30 | -7 | 25 | 0 | 2023-01-30 | -11.4 | 29.4 | 0 | 2022-01-30 | -19.7 | 37.7 | 0 | 2021-01-30 | -17.4 | 35.4 | 0 | 2020-01-30 | -13.5 | 31.5 | 0 | 2019-01-30 | -8.7 | 26.7 | 0 | 2018-01-30 | -9.6 | 27.6 | 0 | 2017-01-30 | -11.3 | 29.3 | 0 | 2016-01-30 | -11.3 | 29.3 | 0 | 30.7 | 0
2025-01-30 | -17.2 | 35.2 | 0 | 2024-01-30 | -5 | 23 | 0 | 2023-01-30 | -13.3 | 31.3 | 0 | 2022-01-30 | -20.2 | 38.2 | 0 | 2021-01-30 | -18.1 | 36.1 | 0 | 2020-01-30 | -14.7 | 32.7 | 0 | 2019-01-30 | -9.2 | 27.2 | 0 | 2018-01-30 | -10 | 28 | 0 | 2017-01-30 | -12.8 | 30.8 | 0 | 2016-01-30 | -11.4 | 29.4 | 0 | 31.19 | 0
2025-01-30 | -18.2 | 36.2 | 0 | 2024-01-30 | -4.7 | 22.7 | 0 | 2023-01-30 | -13.4 | 31.4 | 0 | 2022-01-30 | -21.4 | 39.4 | 0 | 2021-01-30 | -17.9 | 35.9 | 0 | 2020-01-30 | -14.2 | 32.2 | 0 | 2019-01-30 | -12.1 | 30.1 | 0 | 2018-01-30 | -10.7 | 28.7 | 0 | 2017-01-30 | -14.1 | 32.1 | 0 | 2016-01-30 | -11.6 | 29.6 | 0 | 31.83 | 0
2025-01-30 | -19.7 | 37.7 | 0 | 2024-01-30 | -4.2 | 22.2 | 0 | 2023-01-30 | -13.9 | 31.9 | 0 | 2022-01-30 | -19.8 | 37.8 | 0 | 2021-01-30 | -18.3 | 36.3 | 0 | 2020-01-30 | -14.5 | 32.5 | 0 | 2019-01-30 | -13.2 | 31.2 | 0 | 2018-01-30 | -10.8 | 28.8 | 0 | 2017-01-30 | -15.1 | 33.1 | 0 | 2016-01-30 | -11.8 | 29.8 | 0 | 32.13 | 0
2025-01-30 | -19.5 | 37.5 | 0 | 2024-01-30 | -4 | 22 | 0 | 2023-01-30 | -14.9 | 32.9 | 0 | 2022-01-30 | -20 | 38 | 0 | 2021-01-30 | -17.8 | 35.8 | 0 | 2020-01-30 | -15.3 | 33.3 | 0 | 2019-01-30 | -14.3 | 32.3 | 0 | 2018-01-30 | -11.2 | 29.2 | 0 | 2017-01-30 | -15.5 | 33.5 | 0 | 2016-01-30 | -11.8 | 29.8 | 0 | 32.43 | 0
2025-01-30 | -21.6 | 39.6 | 0 | 2024-01-30 | -4.1 | 22.1 | 0 | 2023-01-30 | -14.4 | 32.4 | 0 | 2022-01-30 | -20.4 | 38.4 | 0 | 2021-01-30 | -18.2 | 36.2 | 0 | 2020-01-30 | -14.3 | 32.3 | 0 | 2019-01-30 | -15.9 | 33.9 | 0 | 2018-01-30 | -11.5 | 29.5 | 0 | 2017-01-30 | -16.2 | 34.2 | 0 | 2016-01-30 | -11.5 | 29.5 | 0 | 32.81 | 0
2025-01-30 | -21.1 | 39.1 | 0 | 2024-01-30 | -4.8 | 22.8 | 0 | 2023-01-30 | -13.7 | 31.7 | 0 | 2022-01-30 | -21.3 | 39.3 | 0 | 2021-01-30 | -18.1 | 36.1 | 0 | 2020-01-30 | -15.5 | 33.5 | 0 | 2019-01-30 | -16.6 | 34.6 | 0 | 2018-01-30 | -12 | 30 | 0 | 2017-01-30 | -16.8 | 34.8 | 0 | 2016-01-30 | -11.1 | 29.1 | 0 | 33.1 | 0
2025-01-30 | -21.2 | 39.2 | 0 | 2024-01-30 | -5.8 | 23.8 | 0 | 2023-01-30 | -13 | 31 | 0 | 2022-01-30 | -20.6 | 38.6 | 0 | 2021-01-30 | -18.8 | 36.8 | 0 | 2020-01-30 | -14.7 | 32.7 | 0 | 2019-01-30 | -16.7 | 34.7 | 0 | 2018-01-30 | -12.5 | 30.5 | 0 | 2017-01-30 | -16.9 | 34.9 | 0 | 2016-01-30 | -11 | 29 | 0 | 33.12 | 0
2025-01-30 | -20 | 38 | 0 | 2024-01-30 | -7 | 25 | 0 | 2023-01-30 | -12.3 | 30.3 | 0 | 2022-01-30 | -18.7 | 36.7 | 0 | 2021-01-30 | -18.1 | 36.1 | 0 | 2020-01-30 | -13.3 | 31.3 | 0 | 2019-01-30 | -15.3 | 33.3 | 0 | 2018-01-30 | -13 | 31 | 0 | 2017-01-30 | -15.7 | 33.7 | 0 | 2016-01-30 | -10.7 | 28.7 | 0 | 32.41 | 0
2025-01-30 | -17.6 | 35.6 | 0 | 2024-01-30 | -7.5 | 25.5 | 0 | 2023-01-30 | -11.3 | 29.3 | 0 | 2022-01-30 | -17.1 | 35.1 | 0 | 2021-01-30 | -15.8 | 33.8 | 0 | 2020-01-30 | -11.9 | 29.9 | 0 | 2019-01-30 | -14.7 | 32.7 | 0 | 2018-01-30 | -12.7 | 30.7 | 0 | 2017-01-30 | -14.6 | 32.6 | 0 | 2016-01-30 | -9.9 | 27.9 | 0 | 31.31 | 0
2025-01-30 | -16.1 | 34.1 | 0 | 2024-01-30 | -7.2 | 25.2 | 0 | 2023-01-30 | -10.7 | 28.7 | 0 | 2022-01-30 | -15.2 | 33.2 | 0 | 2021-01-30 | -14.6 | 32.6 | 0 | 2020-01-30 | -10.6 | 28.6 | 0 | 2019-01-30 | -13.7 | 31.7 | 0 | 2018-01-30 | -12.4 | 30.4 | 0 | 2017-01-30 | -13.2 | 31.2 | 0 | 2016-01-30 | -8.8 | 26.8 | 0 | 30.25 | 0
2025-01-30 | -15.1 | 33.1 | 0 | 2024-01-30 | -6.6 | 24.6 | 0 | 2023-01-30 | -9.9 | 27.9 | 0 | 2022-01-30 | -13.3 | 31.3 | 0 | 2021-01-30 | -13.7 | 31.7 | 0 | 2020-01-30 | -8.9 | 26.9 | 0 | 2019-01-30 | -13.2 | 31.2 | 0 | 2018-01-30 | -10.9 | 28.9 | 0 | 2017-01-30 | -12.1 | 30.1 | 0 | 2016-01-30 | -7.6 | 25.6 | 0 | 29.13 | 0
2025-01-30 | -13.8 | 31.8 | 0 | 2024-01-30 | -6.1 | 24.1 | 0 | 2023-01-30 | -9.6 | 27.6 | 0 | 2022-01-30 | -11.2 | 29.2 | 0 | 2021-01-30 | -12.9 | 30.9 | 0 | 2020-01-30 | -7.7 | 25.7 | 0 | 2019-01-30 | -12.7 | 30.7 | 0 | 2018-01-30 | -10.2 | 28.2 | 0 | 2017-01-30 | -12.1 | 30.1 | 0 | 2016-01-30 | -7.3 | 25.3 | 0 | 28.36 | 0
2025-01-30 | -12.4 | 30.4 | 0 | 2024-01-30 | -5.8 | 23.8 | 0 | 2023-01-30 | -9.3 | 27.3 | 0 | 2022-01-30 | -10.6 | 28.6 | 0 | 2021-01-30 | -11.9 | 29.9 | 0 | 2020-01-30 | -6.9 | 24.9 | 0 | 2019-01-30 | -12.7 | 30.7 | 0 | 2018-01-30 | -9.7 | 27.7 | 0 | 2017-01-30 | -11.6 | 29.6 | 0 | 2016-01-30 | -6.9 | 24.9 | 0 | 27.78 | 0
2025-01-30 | -12.5 | 30.5 | 0 | 2024-01-30 | -5.7 | 23.7 | 0 | 2023-01-30 | -9.3 | 27.3 | 0 | 2022-01-30 | -10.3 | 28.3 | 0 | 2021-01-30 | -11.6 | 29.6 | 0 | 2020-01-30 | -6.7 | 24.7 | 0 | 2019-01-30 | -12.3 | 30.3 | 0 | 2018-01-30 | -9.2 | 27.2 | 0 | 2017-01-30 | -11.5 | 29.5 | 0 | 2016-01-30 | -6.3 | 24.3 | 0 | 27.54 | 0
2025-01-30 | -11.8 | 29.8 | 0 | 2024-01-30 | -6.2 | 24.2 | 0 | 2023-01-30 | -9.4 | 27.4 | 0 | 2022-01-30 | -10.3 | 28.3 | 0 | 2021-01-30 | -12 | 30 | 0 | 2020-01-30 | -6.8 | 24.8 | 0 | 2019-01-30 | -12.9 | 30.9 | 0 | 2018-01-30 | -9.7 | 27.7 | 0 | 2017-01-30 | -11.3 | 29.3 | 0 | 2016-01-30 | -6.1 | 24.1 | 0 | 27.65 | 0
2025-01-30 | -11.9 | 29.9 | 0 | 2024-01-30 | -6.2 | 24.2 | 0 | 2023-01-30 | -9.7 | 27.7 | 0 | 2022-01-30 | -10.3 | 28.3 | 0 | 2021-01-30 | -13.4 | 31.4 | 0 | 2020-01-30 | -7.3 | 25.3 | 0 | 2019-01-30 | -14 | 32 | 0 | 2018-01-30 | -9.9 | 27.9 | 0 | 2017-01-30 | -12.5 | 30.5 | 0 | 2016-01-30 | -6.5 | 24.5 | 0 | 28.17 | 0
2025-01-30 | -11.8 | 29.8 | 0 | 2024-01-30 | -6.3 | 24.3 | 0 | 2023-01-30 | -9.6 | 27.6 | 0 | 2022-01-30 | -11.4 | 29.4 | 0 | 2021-01-30 | -14.2 | 32.2 | 0 | 2020-01-30 | -8.1 | 26.1 | 0 | 2019-01-30 | -15 | 33 | 0 | 2018-01-30 | -10.7 | 28.7 | 0 | 2017-01-30 | -14 | 32 | 0 | 2016-01-30 | -6.2 | 24.2 | 0 | 28.73 | 0
2025-01-30 | -12 | 30 | 0 | 2024-01-30 | -6.7 | 24.7 | 0 | 2023-01-30 | -9.7 | 27.7 | 0 | 2022-01-30 | -11.7 | 29.7 | 0 | 2021-01-30 | -15.2 | 33.2 | 0 | 2020-01-30 | -8.4 | 26.4 | 0 | 2019-01-30 | -15.8 | 33.8 | 0 | 2018-01-30 | -11.6 | 29.6 | 0 | 2017-01-30 | -14.3 | 32.3 | 0 | 2016-01-30 | -6.1 | 24.1 | 0 | 29.15 | 0
2025-01-30 | -12 | 30 | 0 | 2024-01-30 | -6.7 | 24.7 | 0 | 2023-01-30 | -9.7 | 27.7 | 0 | 2022-01-30 | -12.8 | 30.8 | 0 | 2021-01-30 | -15 | 33 | 0 | 2020-01-30 | -9.2 | 27.2 | 0 | 2019-01-30 | -17.1 | 35.1 | 0 | 2018-01-30 | -12.3 | 30.3 | 0 | 2017-01-30 | -15.6 | 33.6 | 0 | 2016-01-30 | -5.9 | 23.9 | 0 | 29.63 | 0
2025-01-30 | -11.9 | 29.9 | 0 | 2024-01-30 | -7 | 25 | 0 | 2023-01-30 | -9.9 | 27.9 | 0 | 2022-01-30 | -13.3 | 31.3 | 0 | 2021-01-30 | -16.7 | 34.7 | 0 | 2020-01-30 | -9.8 | 27.8 | 0 | 2019-01-30 | -17.7 | 35.7 | 0 | 2018-01-30 | -12.6 | 30.6 | 0 | 2017-01-30 | -15.6 | 33.6 | 0 | 2016-01-30 | -5.5 | 23.5 | 0 | 30 | 0
2025-01-30 | -11.5 | 29.5 | 0 | 2024-01-30 | -7 | 25 | 0 | 2023-01-30 | -9.1 | 27.1 | 0 | 2022-01-30 | -13.9 | 31.9 | 0 | 2021-01-30 | -17.9 | 35.9 | 0 | 2020-01-30 | -10.4 | 28.4 | 0 | 2019-01-30 | -18.4 | 36.4 | 0 | 2018-01-30 | -13.7 | 31.7 | 0 | 2017-01-30 | -17.7 | 35.7 | 0 | 2016-01-30 | -5.3 | 23.3 | 0 | 30.49 | 0
2025-01-30 | -12.2 | 30.2 | 0 | 2024-01-30 | -7.1 | 25.1 | 0 | 2023-01-30 | -9.4 | 27.4 | 0 | 2022-01-30 | -14.6 | 32.6 | 0 | 2021-01-30 | -18.3 | 36.3 | 0 | 2020-01-30 | -11.9 | 29.9 | 0 | 2019-01-30 | -17.6 | 35.6 | 0 | 2018-01-30 | -14.8 | 32.8 | 0 | 2017-01-30 | -16.7 | 34.7 | 0 | 2016-01-30 | -5.5 | 23.5 | 0 | 30.81 | 0
2025-01-31 | -12.3 | 30.3 | 0 | 2024-01-31 | -7.1 | 25.1 | 0 | 2023-01-31 | -9 | 27 | 0 | 2022-01-31 | -15.3 | 33.3 | 0 | 2021-01-31 | -18 | 36 | 0 | 2020-01-31 | -12.2 | 30.2 | 0 | 2019-01-31 | -18 | 36 | 0 | 2018-01-31 | -15.6 | 33.6 | 0 | 2017-01-31 | -17.8 | 35.8 | 0 | 2016-01-31 | -5.6 | 23.6 | 0 | 31.09 | 0
2025-01-31 | -12.1 | 30.1 | 0 | 2024-01-31 | -7.5 | 25.5 | 0 | 2023-01-31 | -8.6 | 26.6 | 0 | 2022-01-31 | -17.4 | 35.4 | 0 | 2021-01-31 | -17 | 35 | 0 | 2020-01-31 | -13 | 31 | 0 | 2019-01-31 | -18.4 | 36.4 | 0 | 2018-01-31 | -16.7 | 34.7 | 0 | 2017-01-31 | -17.6 | 35.6 | 0 | 2016-01-31 | -5.2 | 23.2 | 0 | 31.35 | 0
2025-01-31 | -14 | 32 | 0 | 2024-01-31 | -7.7 | 25.7 | 0 | 2023-01-31 | -9.6 | 27.6 | 0 | 2022-01-31 | -17.2 | 35.2 | 0 | 2021-01-31 | -18.5 | 36.5 | 0 | 2020-01-31 | -13.3 | 31.3 | 0 | 2019-01-31 | -18.4 | 36.4 | 0 | 2018-01-31 | -17.4 | 35.4 | 0 | 2017-01-31 | -17.9 | 35.9 | 0 | 2016-01-31 | -2.6 | 20.6 | 0 | 31.66 | 0
2025-01-31 | -14.6 | 32.6 | 0 | 2024-01-31 | -7.9 | 25.9 | 0 | 2023-01-31 | -10.3 | 28.3 | 0 | 2022-01-31 | -17.5 | 35.5 | 0 | 2021-01-31 | -19.4 | 37.4 | 0 | 2020-01-31 | -15 | 33 | 0 | 2019-01-31 | -18.9 | 36.9 | 0 | 2018-01-31 | -17.9 | 35.9 | 0 | 2017-01-31 | -21 | 39 | 0 | 2016-01-31 | -2.7 | 20.7 | 0 | 32.52 | 0
2025-01-31 | -12.6 | 30.6 | 0 | 2024-01-31 | -7.9 | 25.9 | 0 | 2023-01-31 | -11.1 | 29.1 | 0 | 2022-01-31 | -18.4 | 36.4 | 0 | 2021-01-31 | -18.2 | 36.2 | 0 | 2020-01-31 | -15.1 | 33.1 | 0 | 2019-01-31 | -19.3 | 37.3 | 0 | 2018-01-31 | -18.7 | 36.7 | 0 | 2017-01-31 | -19.8 | 37.8 | 0 | 2016-01-31 | -1.1 | 19.1 | 0 | 32.22 | 0
2025-01-31 | -12.1 | 30.1 | 0 | 2024-01-31 | -7.6 | 25.6 | 0 | 2023-01-31 | -13 | 31 | 0 | 2022-01-31 | -17.2 | 35.2 | 0 | 2021-01-31 | -19.2 | 37.2 | 0 | 2020-01-31 | -13.6 | 31.6 | 0 | 2019-01-31 | -20.1 | 38.1 | 0 | 2018-01-31 | -18.8 | 36.8 | 0 | 2017-01-31 | -19.3 | 37.3 | 0 | 2016-01-31 | -0.4 | 18.4 | 0 | 32.13 | 0
2025-01-31 | -11.6 | 29.6 | 0 | 2024-01-31 | -7.5 | 25.5 | 0 | 2023-01-31 | -16.1 | 34.1 | 0 | 2022-01-31 | -16.7 | 34.7 | 0 | 2021-01-31 | -21.6 | 39.6 | 0 | 2020-01-31 | -13.9 | 31.9 | 0 | 2019-01-31 | -20.5 | 38.5 | 0 | 2018-01-31 | -20.4 | 38.4 | 0 | 2017-01-31 | -18.4 | 36.4 | 0 | 2016-01-31 | 0.3 | 17.7 | 0 | 32.64 | 0
2025-01-31 | -11 | 29 | 0 | 2024-01-31 | -7.2 | 25.2 | 0 | 2023-01-31 | -15.8 | 33.8 | 0 | 2022-01-31 | -16.3 | 34.3 | 0 | 2021-01-31 | -20.1 | 38.1 | 0 | 2020-01-31 | -14.2 | 32.2 | 0 | 2019-01-31 | -19.6 | 37.6 | 0 | 2018-01-31 | -20 | 38 | 0 | 2017-01-31 | -20.2 | 38.2 | 0 | 2016-01-31 | 0.6 | 17.4 | 0 | 32.38 | 0
2025-01-31 | -10.8 | 28.8 | 0 | 2024-01-31 | -7.2 | 25.2 | 0 | 2023-01-31 | -16.5 | 34.5 | 0 | 2022-01-31 | -16.1 | 34.1 | 0 | 2021-01-31 | -20.7 | 38.7 | 0 | 2020-01-31 | -13.7 | 31.7 | 0 | 2019-01-31 | -19.3 | 37.3 | 0 | 2018-01-31 | -19.4 | 37.4 | 0 | 2017-01-31 | -20.6 | 38.6 | 0 | 2016-01-31 | 0.4 | 17.6 | 0 | 32.39 | 0
2025-01-31 | -10.2 | 28.2 | 0 | 2024-01-31 | -6.7 | 24.7 | 0 | 2023-01-31 | -18.6 | 36.6 | 0 | 2022-01-31 | -15.2 | 33.2 | 0 | 2021-01-31 | -19 | 37 | 0 | 2020-01-31 | -13.7 | 31.7 | 0 | 2019-01-31 | -18.6 | 36.6 | 0 | 2018-01-31 | -18.1 | 36.1 | 0 | 2017-01-31 | -18.4 | 36.4 | 0 | 2016-01-31 | -0.3 | 18.3 | 0 | 31.88 | 0
2025-01-31 | -8.1 | 26.1 | 0 | 2024-01-31 | -6 | 24 | 0 | 2023-01-31 | -14 | 32 | 0 | 2022-01-31 | -13.6 | 31.6 | 0 | 2021-01-31 | -16.7 | 34.7 | 0 | 2020-01-31 | -11.2 | 29.2 | 0 | 2019-01-31 | -18.1 | 36.1 | 0 | 2018-01-31 | -16.7 | 34.7 | 0 | 2017-01-31 | -15.6 | 33.6 | 0 | 2016-01-31 | 2.6 | 15.4 | 0 | 29.74 | 0
2025-01-31 | -6.1 | 24.1 | 0 | 2024-01-31 | -5.2 | 23.2 | 0 | 2023-01-31 | -12.6 | 30.6 | 0 | 2022-01-31 | -11.1 | 29.1 | 0 | 2021-01-31 | -15.8 | 33.8 | 0 | 2020-01-31 | -9.5 | 27.5 | 0 | 2019-01-31 | -17.9 | 35.9 | 0 | 2018-01-31 | -14.7 | 32.7 | 0 | 2017-01-31 | -13.3 | 31.3 | 0 | 2016-01-31 | 3.6 | 14.4 | 0 | 28.26 | 0
2025-01-31 | -3.6 | 21.6 | 0 | 2024-01-31 | -4.2 | 22.2 | 0 | 2023-01-31 | -11.4 | 29.4 | 0 | 2022-01-31 | -10 | 28 | 0 | 2021-01-31 | -14.7 | 32.7 | 0 | 2020-01-31 | -8.5 | 26.5 | 0 | 2019-01-31 | -16.6 | 34.6 | 0 | 2018-01-31 | -13.7 | 31.7 | 0 | 2017-01-31 | -11.6 | 29.6 | 0 | 2016-01-31 | 4.3 | 13.7 | 0 | 27 | 0
2025-01-31 | -2.6 | 20.6 | 0 | 2024-01-31 | -3 | 21 | 0 | 2023-01-31 | -10.8 | 28.8 | 0 | 2022-01-31 | -8.2 | 26.2 | 0 | 2021-01-31 | -13.7 | 31.7 | 0 | 2020-01-31 | -7.6 | 25.6 | 0 | 2019-01-31 | -15.8 | 33.8 | 0 | 2018-01-31 | -12.5 | 30.5 | 0 | 2017-01-31 | -9.5 | 27.5 | 0 | 2016-01-31 | 4.9 | 13.1 | 0 | 25.88 | 0
2025-01-31 | -2.2 | 20.2 | 0 | 2024-01-31 | -1.8 | 19.8 | 0 | 2023-01-31 | -9.7 | 27.7 | 0 | 2022-01-31 | -6.5 | 24.5 | 0 | 2021-01-31 | -13.3 | 31.3 | 0 | 2020-01-31 | -7 | 25 | 0 | 2019-01-31 | -15.9 | 33.9 | 0 | 2018-01-31 | -12.6 | 30.6 | 0 | 2017-01-31 | -9.2 | 27.2 | 0 | 2016-01-31 | 5.3 | 12.7 | 0 | 25.29 | 0
2025-01-31 | -2.1 | 20.1 | 0 | 2024-01-31 | -0.8 | 18.8 | 0 | 2023-01-31 | -9.3 | 27.3 | 0 | 2022-01-31 | -6.8 | 24.8 | 0 | 2021-01-31 | -12.9 | 30.9 | 0 | 2020-01-31 | -6.4 | 24.4 | 0 | 2019-01-31 | -15.9 | 33.9 | 0 | 2018-01-31 | -12.1 | 30.1 | 0 | 2017-01-31 | -9.2 | 27.2 | 0 | 2016-01-31 | 5.3 | 12.7 | 0 | 25.02 | 0
2025-01-31 | -2.4 | 20.4 | 0 | 2024-01-31 | 0.1 | 17.9 | 0 | 2023-01-31 | -9.3 | 27.3 | 0 | 2022-01-31 | -7.5 | 25.5 | 0 | 2021-01-31 | -13.1 | 31.1 | 0 | 2020-01-31 | -6.2 | 24.2 | 0 | 2019-01-31 | -16.4 | 34.4 | 0 | 2018-01-31 | -12.2 | 30.2 | 0 | 2017-01-31 | -9.2 | 27.2 | 0 | 2016-01-31 | 5.2 | 12.8 | 0 | 25.1 | 0
2025-01-31 | -2.5 | 20.5 | 0 | 2024-01-31 | 0.1 | 17.9 | 0 | 2023-01-31 | -10.4 | 28.4 | 0 | 2022-01-31 | -9 | 27 | 0 | 2021-01-31 | -15.2 | 33.2 | 0 | 2020-01-31 | -6 | 24 | 0 | 2019-01-31 | -17.1 | 35.1 | 0 | 2018-01-31 | -12.4 | 30.4 | 0 | 2017-01-31 | -10.2 | 28.2 | 0 | 2016-01-31 | 4.4 | 13.6 | 0 | 25.83 | 0
2025-01-31 | -3.4 | 21.4 | 0 | 2024-01-31 | 0.6 | 17.4 | 0 | 2023-01-31 | -11.8 | 29.8 | 0 | 2022-01-31 | -10.8 | 28.8 | 0 | 2021-01-31 | -15.8 | 33.8 | 0 | 2020-01-31 | -6.6 | 24.6 | 0 | 2019-01-31 | -18.4 | 36.4 | 0 | 2018-01-31 | -11.9 | 29.9 | 0 | 2017-01-31 | -10.2 | 28.2 | 0 | 2016-01-31 | 3.6 | 14.4 | 0 | 26.47 | 0
2025-01-31 | -5.1 | 23.1 | 0 | 2024-01-31 | 1.3 | 16.7 | 0 | 2023-01-31 | -14.9 | 32.9 | 0 | 2022-01-31 | -11.4 | 29.4 | 0 | 2021-01-31 | -16.2 | 34.2 | 0 | 2020-01-31 | -6.6 | 24.6 | 0 | 2019-01-31 | -19.1 | 37.1 | 0 | 2018-01-31 | -12.1 | 30.1 | 0 | 2017-01-31 | -10.3 | 28.3 | 0 | 2016-01-31 | 3.2 | 14.8 | 0 | 27.12 | 0
2025-01-31 | -6.7 | 24.7 | 0 | 2024-01-31 | 1.4 | 16.6 | 0 | 2023-01-31 | -19.7 | 37.7 | 0 | 2022-01-31 | -11.7 | 29.7 | 0 | 2021-01-31 | -17.5 | 35.5 | 0 | 2020-01-31 | -6.7 | 24.7 | 0 | 2019-01-31 | -18.1 | 36.1 | 0 | 2018-01-31 | -12.2 | 30.2 | 0 | 2017-01-31 | -10.7 | 28.7 | 0 | 2016-01-31 | 3 | 15 | 0 | 27.89 | 0
2025-01-31 | -7.9 | 25.9 | 0 | 2024-01-31 | 1.6 | 16.4 | 0 | 2023-01-31 | -16.3 | 34.3 | 0 | 2022-01-31 | -12.7 | 30.7 | 0 | 2021-01-31 | -18.1 | 36.1 | 0 | 2020-01-31 | -7 | 25 | 0 | 2019-01-31 | -16.4 | 34.4 | 0 | 2018-01-31 | -12.2 | 30.2 | 0 | 2017-01-31 | -11.1 | 29.1 | 0 | 2016-01-31 | 2.3 | 15.7 | 0 | 27.78 | 0
2025-01-31 | -8.2 | 26.2 | 0 | 2024-01-31 | 1.8 | 16.2 | 0 | 2023-01-31 | -13.9 | 31.9 | 0 | 2022-01-31 | -14.1 | 32.1 | 0 | 2021-01-31 | -18.6 | 36.6 | 0 | 2020-01-31 | -7.5 | 25.5 | 0 | 2019-01-31 | -16.3 | 34.3 | 0 | 2018-01-31 | -11.8 | 29.8 | 0 | 2017-01-31 | -11.3 | 29.3 | 0 | 2016-01-31 | 3.6 | 14.4 | 0 | 27.63 | 0
2025-01-31 | -9.5 | 27.5 | 0 | 2024-01-31 | 1.8 | 16.2 | 0 | 2023-01-31 | -14.2 | 32.2 | 0 | 2022-01-31 | -15.2 | 33.2 | 0 | 2021-01-31 | -18.3 | 36.3 | 0 | 2020-01-31 | -8.3 | 26.3 | 0 | 2019-01-31 | -16.9 | 34.9 | 0 | 2018-01-31 | -11.8 | 29.8 | 0 | 2017-01-31 | -11.6 | 29.6 | 0 | 2016-01-31 | 3.9 | 14.1 | 0 | 28.01 | 0
2025-02-01 | -11.1 | 29.1 | 0 | 2024-02-01 | 1.7 | 16.3 | 0 | 2023-02-01 | -20.1 | 38.1 | 0 | 2022-02-01 | -16.2 | 34.2 | 0 | 2021-02-01 | -17.9 | 35.9 | 0 | 2020-02-01 | -8.5 | 26.5 | 0 | 2019-02-01 | -17.5 | 35.5 | 0 | 2018-02-01 | -11.1 | 29.1 | 0 | 2017-02-01 | -11.7 | 29.7 | 0 | 2016-02-01 | 5 | 13 | 0 | 28.74 | 0
2025-02-01 | -12.6 | 30.6 | 0 | 2024-02-01 | 1.6 | 16.4 | 0 | 2023-02-01 | -19.7 | 37.7 | 0 | 2022-02-01 | -15.9 | 33.9 | 0 | 2021-02-01 | -19.8 | 37.8 | 0 | 2020-02-01 | -9 | 27 | 0 | 2019-02-01 | -18.2 | 36.2 | 0 | 2018-02-01 | -10.7 | 28.7 | 0 | 2017-02-01 | -11.8 | 29.8 | 0 | 2016-02-01 | 5.7 | 12.3 | 0 | 29.04 | 0
2025-02-01 | -13.7 | 31.7 | 0 | 2024-02-01 | 1.9 | 16.1 | 0 | 2023-02-01 | -21 | 39 | 0 | 2022-02-01 | -17.2 | 35.2 | 0 | 2021-02-01 | -18.4 | 36.4 | 0 | 2020-02-01 | -10.3 | 28.3 | 0 | 2019-02-01 | -18.7 | 36.7 | 0 | 2018-02-01 | -10.1 | 28.1 | 0 | 2017-02-01 | -12 | 30 | 0 | 2016-02-01 | 5 | 13 | 0 | 29.45 | 0
2025-02-01 | -14.8 | 32.8 | 0 | 2024-02-01 | 2 | 16 | 0 | 2023-02-01 | -20.1 | 38.1 | 0 | 2022-02-01 | -16.2 | 34.2 | 0 | 2021-02-01 | -19.7 | 37.7 | 0 | 2020-02-01 | -11.2 | 29.2 | 0 | 2019-02-01 | -19 | 37 | 0 | 2018-02-01 | -8.9 | 26.9 | 0 | 2017-02-01 | -12.2 | 30.2 | 0 | 2016-02-01 | 6.3 | 11.7 | 0 | 29.38 | 0
2025-02-01 | -15.6 | 33.6 | 0 | 2024-02-01 | 1.7 | 16.3 | 0 | 2023-02-01 | -21.4 | 39.4 | 0 | 2022-02-01 | -16.4 | 34.4 | 0 | 2021-02-01 | -20.3 | 38.3 | 0 | 2020-02-01 | -11.5 | 29.5 | 0 | 2019-02-01 | -19.5 | 37.5 | 0 | 2018-02-01 | -9 | 27 | 0 | 2017-02-01 | -12 | 30 | 0 | 2016-02-01 | 6.7 | 11.3 | 0 | 29.73 | 0
2025-02-01 | -16.4 | 34.4 | 0 | 2024-02-01 | 1.6 | 16.4 | 0 | 2023-02-01 | -19.5 | 37.5 | 0 | 2022-02-01 | -18.3 | 36.3 | 0 | 2021-02-01 | -20.2 | 38.2 | 0 | 2020-02-01 | -10.6 | 28.6 | 0 | 2019-02-01 | -19.4 | 37.4 | 0 | 2018-02-01 | -8.8 | 26.8 | 0 | 2017-02-01 | -11.9 | 29.9 | 0 | 2016-02-01 | 6.7 | 11.3 | 0 | 29.68 | 0
2025-02-01 | -17.6 | 35.6 | 0 | 2024-02-01 | 1.2 | 16.8 | 0 | 2023-02-01 | -19.2 | 37.2 | 0 | 2022-02-01 | -16.8 | 34.8 | 0 | 2021-02-01 | -19.5 | 37.5 | 0 | 2020-02-01 | -10.5 | 28.5 | 0 | 2019-02-01 | -19.6 | 37.6 | 0 | 2018-02-01 | -8.7 | 26.7 | 0 | 2017-02-01 | -11.7 | 29.7 | 0 | 2016-02-01 | 6.5 | 11.5 | 0 | 29.59 | 0
2025-02-01 | -18.5 | 36.5 | 0 | 2024-02-01 | 0.8 | 17.2 | 0 | 2023-02-01 | -18.7 | 36.7 | 0 | 2022-02-01 | -16.6 | 34.6 | 0 | 2021-02-01 | -19.9 | 37.9 | 0 | 2020-02-01 | -10.6 | 28.6 | 0 | 2019-02-01 | -20 | 38 | 0 | 2018-02-01 | -8.1 | 26.1 | 0 | 2017-02-01 | -11.9 | 29.9 | 0 | 2016-02-01 | 2.8 | 15.2 | 0 | 30.07 | 0
2025-02-01 | -19.3 | 37.3 | 0 | 2024-02-01 | 1 | 17 | 0 | 2023-02-01 | -18.5 | 36.5 | 0 | 2022-02-01 | -16.4 | 34.4 | 0 | 2021-02-01 | -22.1 | 40.1 | 0 | 2020-02-01 | -11.1 | 29.1 | 0 | 2019-02-01 | -19.6 | 37.6 | 0 | 2018-02-01 | -8.1 | 26.1 | 0 | 2017-02-01 | -12.5 | 30.5 | 0 | 2016-02-01 | 2.5 | 15.5 | 0 | 30.41 | 0
2025-02-01 | -19.4 | 37.4 | 0 | 2024-02-01 | 1.3 | 16.7 | 0 | 2023-02-01 | -17.3 | 35.3 | 0 | 2022-02-01 | -14.9 | 32.9 | 0 | 2021-02-01 | -18.1 | 36.1 | 0 | 2020-02-01 | -11 | 29 | 0 | 2019-02-01 | -18.4 | 36.4 | 0 | 2018-02-01 | -4.9 | 22.9 | 0 | 2017-02-01 | -12.1 | 30.1 | 0 | 2016-02-01 | 2.3 | 15.7 | 0 | 29.25 | 0
2025-02-01 | -19.2 | 37.2 | 0 | 2024-02-01 | 1.7 | 16.3 | 0 | 2023-02-01 | -16.4 | 34.4 | 0 | 2022-02-01 | -12.9 | 30.9 | 0 | 2021-02-01 | -15.3 | 33.3 | 0 | 2020-02-01 | -7.9 | 25.9 | 0 | 2019-02-01 | -17 | 35 | 0 | 2018-02-01 | -0.1 | 18.1 | 0 | 2017-02-01 | -10.7 | 28.7 | 0 | 2016-02-01 | 1.8 | 16.2 | 0 | 27.6 | 0
2025-02-01 | -18.5 | 36.5 | 0 | 2024-02-01 | 2.2 | 15.8 | 0 | 2023-02-01 | -12 | 30 | 0 | 2022-02-01 | -10.7 | 28.7 | 0 | 2021-02-01 | -12.6 | 30.6 | 0 | 2020-02-01 | -6.5 | 24.5 | 0 | 2019-02-01 | -15.8 | 33.8 | 0 | 2018-02-01 | 1 | 17 | 0 | 2017-02-01 | -9.2 | 27.2 | 0 | 2016-02-01 | 2.6 | 15.4 | 0 | 25.95 | 0
2025-02-01 | -17.4 | 35.4 | 0 | 2024-02-01 | 2.5 | 15.5 | 0 | 2023-02-01 | -9.5 | 27.5 | 0 | 2022-02-01 | -8.2 | 26.2 | 0 | 2021-02-01 | -10.9 | 28.9 | 0 | 2020-02-01 | -5.5 | 23.5 | 0 | 2019-02-01 | -14.8 | 32.8 | 0 | 2018-02-01 | 3.1 | 14.9 | 0 | 2017-02-01 | -9 | 27 | 0 | 2016-02-01 | 3.1 | 14.9 | 0 | 24.66 | 0
2025-02-01 | -16.3 | 34.3 | 0 | 2024-02-01 | 2.5 | 15.5 | 0 | 2023-02-01 | -7.7 | 25.7 | 0 | 2022-02-01 | -7.9 | 25.9 | 0 | 2021-02-01 | -8.9 | 26.9 | 0 | 2020-02-01 | -4.4 | 22.4 | 0 | 2019-02-01 | -13.6 | 31.6 | 0 | 2018-02-01 | 4 | 14 | 0 | 2017-02-01 | -8.1 | 26.1 | 0 | 2016-02-01 | 3.5 | 14.5 | 0 | 23.69 | 0
2025-02-01 | -15.2 | 33.2 | 0 | 2024-02-01 | 2.6 | 15.4 | 0 | 2023-02-01 | -6.6 | 24.6 | 0 | 2022-02-01 | -6.7 | 24.7 | 0 | 2021-02-01 | -7.2 | 25.2 | 0 | 2020-02-01 | -3.1 | 21.1 | 0 | 2019-02-01 | -12.4 | 30.4 | 0 | 2018-02-01 | 4.6 | 13.4 | 0 | 2017-02-01 | -7.4 | 25.4 | 0 | 2016-02-01 | 3.9 | 14.1 | 0 | 22.75 | 0
2025-02-01 | -14.5 | 32.5 | 0 | 2024-02-01 | 2.4 | 15.6 | 0 | 2023-02-01 | -6.2 | 24.2 | 0 | 2022-02-01 | -6.1 | 24.1 | 0 | 2021-02-01 | -5.9 | 23.9 | 0 | 2020-02-01 | -2.8 | 20.8 | 0 | 2019-02-01 | -11.9 | 29.9 | 0 | 2018-02-01 | 4.7 | 13.3 | 0 | 2017-02-01 | -6.3 | 24.3 | 0 | 2016-02-01 | 3.5 | 14.5 | 0 | 22.31 | 0
2025-02-01 | -14.1 | 32.1 | 0 | 2024-02-01 | 1.6 | 16.4 | 0 | 2023-02-01 | -5.9 | 23.9 | 0 | 2022-02-01 | -6.7 | 24.7 | 0 | 2021-02-01 | -6.1 | 24.1 | 0 | 2020-02-01 | -2.7 | 20.7 | 0 | 2019-02-01 | -13 | 31 | 0 | 2018-02-01 | 4.2 | 13.8 | 0 | 2017-02-01 | -6.9 | 24.9 | 0 | 2016-02-01 | 3.2 | 14.8 | 0 | 22.64 | 0
2025-02-01 | -14.9 | 32.9 | 0 | 2024-02-01 | 1.6 | 16.4 | 0 | 2023-02-01 | -6.4 | 24.4 | 0 | 2022-02-01 | -7.2 | 25.2 | 0 | 2021-02-01 | -7.5 | 25.5 | 0 | 2020-02-01 | -4.1 | 22.1 | 0 | 2019-02-01 | -13.2 | 31.2 | 0 | 2018-02-01 | -0.9 | 18.9 | 0 | 2017-02-01 | -5.9 | 23.9 | 0 | 2016-02-01 | 2.5 | 15.5 | 0 | 23.6 | 0
2025-02-01 | -16.9 | 34.9 | 0 | 2024-02-01 | 1.6 | 16.4 | 0 | 2023-02-01 | -7.2 | 25.2 | 0 | 2022-02-01 | -7.5 | 25.5 | 0 | 2021-02-01 | -9 | 27 | 0 | 2020-02-01 | -4.8 | 22.8 | 0 | 2019-02-01 | -13.5 | 31.5 | 0 | 2018-02-01 | -1.7 | 19.7 | 0 | 2017-02-01 | -5.8 | 23.8 | 0 | 2016-02-01 | 2.3 | 15.7 | 0 | 24.25 | 0
2025-02-01 | -17.5 | 35.5 | 0 | 2024-02-01 | 1.3 | 16.7 | 0 | 2023-02-01 | -6.8 | 24.8 | 0 | 2022-02-01 | -8.2 | 26.2 | 0 | 2021-02-01 | -10 | 28 | 0 | 2020-02-01 | -6.6 | 24.6 | 0 | 2019-02-01 | -14.6 | 32.6 | 0 | 2018-02-01 | -2.4 | 20.4 | 0 | 2017-02-01 | -6.5 | 24.5 | 0 | 2016-02-01 | 2.6 | 15.4 | 0 | 24.87 | 0
2025-02-01 | -18.1 | 36.1 | 0 | 2024-02-01 | 1.2 | 16.8 | 0 | 2023-02-01 | -7.7 | 25.7 | 0 | 2022-02-01 | -9 | 27 | 0 | 2021-02-01 | -11.5 | 29.5 | 0 | 2020-02-01 | -6.5 | 24.5 | 0 | 2019-02-01 | -15 | 33 | 0 | 2018-02-01 | -4.1 | 22.1 | 0 | 2017-02-01 | -9 | 27 | 0 | 2016-02-01 | 2.6 | 15.4 | 0 | 25.71 | 0
2025-02-01 | -17.5 | 35.5 | 0 | 2024-02-01 | 1.3 | 16.7 | 0 | 2023-02-01 | -7.3 | 25.3 | 0 | 2022-02-01 | -9.3 | 27.3 | 0 | 2021-02-01 | -11 | 29 | 0 | 2020-02-01 | -7.2 | 25.2 | 0 | 2019-02-01 | -18 | 36 | 0 | 2018-02-01 | -5.8 | 23.8 | 0 | 2017-02-01 | -7.5 | 25.5 | 0 | 2016-02-01 | 0.5 | 17.5 | 0 | 26.18 | 0
2025-02-01 | -19.4 | 37.4 | 0 | 2024-02-01 | 0.9 | 17.1 | 0 | 2023-02-01 | -7 | 25 | 0 | 2022-02-01 | -7.8 | 25.8 | 0 | 2021-02-01 | -10.2 | 28.2 | 0 | 2020-02-01 | -7.5 | 25.5 | 0 | 2019-02-01 | -16.3 | 34.3 | 0 | 2018-02-01 | -7.5 | 25.5 | 0 | 2017-02-01 | -7.4 | 25.4 | 0 | 2016-02-01 | -0.3 | 18.3 | 0 | 26.25 | 0
2025-02-01 | -20.1 | 38.1 | 0 | 2024-02-01 | 0.8 | 17.2 | 0 | 2023-02-01 | -6.7 | 24.7 | 0 | 2022-02-01 | -7 | 25 | 0 | 2021-02-01 | -11.1 | 29.1 | 0 | 2020-02-01 | -7.7 | 25.7 | 0 | 2019-02-01 | -17 | 35 | 0 | 2018-02-01 | -9.1 | 27.1 | 0 | 2017-02-01 | -6.4 | 24.4 | 0 | 2016-02-01 | -0.7 | 18.7 | 0 | 26.5 | 0
2025-02-02 | -21.1 | 39.1 | 0 | 2024-02-02 | 0.8 | 17.2 | 0 | 2023-02-02 | -6.8 | 24.8 | 0 | 2022-02-02 | -0.9 | 18.9 | 0 | 2021-02-02 | -11 | 29 | 0 | 2020-02-02 | -6.4 | 24.4 | 0 | 2019-02-02 | -17.2 | 35.2 | 0 | 2018-02-02 | -10.2 | 28.2 | 0 | 2017-02-02 | -6.7 | 24.7 | 0 | 2016-02-02 | -0.9 | 18.9 | 0 | 26.04 | 0
2025-02-02 | -21.2 | 39.2 | 0 | 2024-02-02 | 0.8 | 17.2 | 0 | 2023-02-02 | -6.6 | 24.6 | 0 | 2022-02-02 | -0.6 | 18.6 | 0 | 2021-02-02 | -10.6 | 28.6 | 0 | 2020-02-02 | -6.5 | 24.5 | 0 | 2019-02-02 | -16.9 | 34.9 | 0 | 2018-02-02 | -11.7 | 29.7 | 0 | 2017-02-02 | -7.7 | 25.7 | 0 | 2016-02-02 | -1.9 | 19.9 | 0 | 26.29 | 0
2025-02-02 | -22.4 | 40.4 | 0 | 2024-02-02 | 0.7 | 17.3 | 0 | 2023-02-02 | -6.4 | 24.4 | 0 | 2022-02-02 | -1.1 | 19.1 | 0 | 2021-02-02 | -9.9 | 27.9 | 0 | 2020-02-02 | -7.1 | 25.1 | 0 | 2019-02-02 | -16.2 | 34.2 | 0 | 2018-02-02 | -13.2 | 31.2 | 0 | 2017-02-02 | -6.8 | 24.8 | 0 | 2016-02-02 | -2.8 | 20.8 | 0 | 26.52 | 0
2025-02-02 | -21 | 39 | 0 | 2024-02-02 | 1.6 | 16.4 | 0 | 2023-02-02 | -6 | 24 | 0 | 2022-02-02 | -1.2 | 19.2 | 0 | 2021-02-02 | -8.6 | 26.6 | 0 | 2020-02-02 | -7.2 | 25.2 | 0 | 2019-02-02 | -17.1 | 35.1 | 0 | 2018-02-02 | -14.7 | 32.7 | 0 | 2017-02-02 | -7.6 | 25.6 | 0 | 2016-02-02 | -4 | 22 | 0 | 26.58 | 0
2025-02-02 | -21.3 | 39.3 | 0 | 2024-02-02 | 1 | 17 | 0 | 2023-02-02 | -5.9 | 23.9 | 0 | 2022-02-02 | -1.3 | 19.3 | 0 | 2021-02-02 | -8.7 | 26.7 | 0 | 2020-02-02 | -7.2 | 25.2 | 0 | 2019-02-02 | -17 | 35 | 0 | 2018-02-02 | -15.9 | 33.9 | 0 | 2017-02-02 | -10 | 28 | 0 | 2016-02-02 | -5.2 | 23.2 | 0 | 27.15 | 0
2025-02-02 | -21.7 | 39.7 | 0 | 2024-02-02 | 0.6 | 17.4 | 0 | 2023-02-02 | -6.4 | 24.4 | 0 | 2022-02-02 | -1.2 | 19.2 | 0 | 2021-02-02 | -9.7 | 27.7 | 0 | 2020-02-02 | -6.9 | 24.9 | 0 | 2019-02-02 | -16.1 | 34.1 | 0 | 2018-02-02 | -16.6 | 34.6 | 0 | 2017-02-02 | -11.4 | 29.4 | 0 | 2016-02-02 | -6.6 | 24.6 | 0 | 27.6 | 0
2025-02-02 | -21.6 | 39.6 | 0 | 2024-02-02 | 0.4 | 17.6 | 0 | 2023-02-02 | -6.3 | 24.3 | 0 | 2022-02-02 | -0.7 | 18.7 | 0 | 2021-02-02 | -9.7 | 27.7 | 0 | 2020-02-02 | -7.9 | 25.9 | 0 | 2019-02-02 | -15.3 | 33.3 | 0 | 2018-02-02 | -17.4 | 35.4 | 0 | 2017-02-02 | -14.1 | 32.1 | 0 | 2016-02-02 | -7.2 | 25.2 | 0 | 27.98 | 0
2025-02-02 | -21.2 | 39.2 | 0 | 2024-02-02 | 0.1 | 17.9 | 0 | 2023-02-02 | -6.4 | 24.4 | 0 | 2022-02-02 | -0.6 | 18.6 | 0 | 2021-02-02 | -9.6 | 27.6 | 0 | 2020-02-02 | -6.9 | 24.9 | 0 | 2019-02-02 | -14.7 | 32.7 | 0 | 2018-02-02 | -18.3 | 36.3 | 0 | 2017-02-02 | -14.8 | 32.8 | 0 | 2016-02-02 | -7.6 | 25.6 | 0 | 28 | 0
2025-02-02 | -20.9 | 38.9 | 0 | 2024-02-02 | -0.1 | 18.1 | 0 | 2023-02-02 | -6.3 | 24.3 | 0 | 2022-02-02 | -0.5 | 18.5 | 0 | 2021-02-02 | -8.8 | 26.8 | 0 | 2020-02-02 | -6.2 | 24.2 | 0 | 2019-02-02 | -13.9 | 31.9 | 0 | 2018-02-02 | -18.8 | 36.8 | 0 | 2017-02-02 | -15.6 | 33.6 | 0 | 2016-02-02 | -8.1 | 26.1 | 0 | 27.92 | 0
2025-02-02 | -19.3 | 37.3 | 0 | 2024-02-02 | -0.1 | 18.1 | 0 | 2023-02-02 | -5.6 | 23.6 | 0 | 2022-02-02 | 0.2 | 17.8 | 0 | 2021-02-02 | -7.3 | 25.3 | 0 | 2020-02-02 | -5.3 | 23.3 | 0 | 2019-02-02 | -12.6 | 30.6 | 0 | 2018-02-02 | -18.2 | 36.2 | 0 | 2017-02-02 | -14 | 32 | 0 | 2016-02-02 | -7.4 | 25.4 | 0 | 26.96 | 0
2025-02-02 | -17.3 | 35.3 | 0 | 2024-02-02 | 0 | 18 | 0 | 2023-02-02 | -4.5 | 22.5 | 0 | 2022-02-02 | 0.9 | 17.1 | 0 | 2021-02-02 | -6.1 | 24.1 | 0 | 2020-02-02 | -4.6 | 22.6 | 0 | 2019-02-02 | -11.7 | 29.7 | 0 | 2018-02-02 | -17.8 | 35.8 | 0 | 2017-02-02 | -13 | 31 | 0 | 2016-02-02 | -6.1 | 24.1 | 0 | 26.02 | 0
2025-02-02 | -15.9 | 33.9 | 0 | 2024-02-02 | -0.2 | 18.2 | 0 | 2023-02-02 | -3.1 | 21.1 | 0 | 2022-02-02 | 1.7 | 16.3 | 0 | 2021-02-02 | -5.2 | 23.2 | 0 | 2020-02-02 | -4 | 22 | 0 | 2019-02-02 | -10.7 | 28.7 | 0 | 2018-02-02 | -17.1 | 35.1 | 0 | 2017-02-02 | -10.6 | 28.6 | 0 | 2016-02-02 | -5.4 | 23.4 | 0 | 25.05 | 0
2025-02-02 | -14.7 | 32.7 | 0 | 2024-02-02 | 0.1 | 17.9 | 0 | 2023-02-02 | -2.1 | 20.1 | 0 | 2022-02-02 | 2.3 | 15.7 | 0 | 2021-02-02 | -4.7 | 22.7 | 0 | 2020-02-02 | -3.5 | 21.5 | 0 | 2019-02-02 | -9.8 | 27.8 | 0 | 2018-02-02 | -16.7 | 34.7 | 0 | 2017-02-02 | -8.9 | 26.9 | 0 | 2016-02-02 | -4.2 | 22.2 | 0 | 24.22 | 0
2025-02-02 | -14.5 | 32.5 | 0 | 2024-02-02 | -0.1 | 18.1 | 0 | 2023-02-02 | -1.7 | 19.7 | 0 | 2022-02-02 | 2.8 | 15.2 | 0 | 2021-02-02 | -1.4 | 19.4 | 0 | 2020-02-02 | -2.9 | 20.9 | 0 | 2019-02-02 | -8.7 | 26.7 | 0 | 2018-02-02 | -15.9 | 33.9 | 0 | 2017-02-02 | -7.7 | 25.7 | 0 | 2016-02-02 | -3.3 | 21.3 | 0 | 23.34 | 0
2025-02-02 | -14.1 | 32.1 | 0 | 2024-02-02 | -0.8 | 18.8 | 0 | 2023-02-02 | -1.4 | 19.4 | 0 | 2022-02-02 | 3.3 | 14.7 | 0 | 2021-02-02 | -1.5 | 19.5 | 0 | 2020-02-02 | -2.5 | 20.5 | 0 | 2019-02-02 | -7.6 | 25.6 | 0 | 2018-02-02 | -15.9 | 33.9 | 0 | 2017-02-02 | -7 | 25 | 0 | 2016-02-02 | -2.8 | 20.8 | 0 | 23.03 | 0
2025-02-02 | -13.7 | 31.7 | 0 | 2024-02-02 | -1.1 | 19.1 | 0 | 2023-02-02 | -1.2 | 19.2 | 0 | 2022-02-02 | 3.4 | 14.6 | 0 | 2021-02-02 | -2.8 | 20.8 | 0 | 2020-02-02 | -2.1 | 20.1 | 0 | 2019-02-02 | -7.1 | 25.1 | 0 | 2018-02-02 | -15.9 | 33.9 | 0 | 2017-02-02 | -7.5 | 25.5 | 0 | 2016-02-02 | -1.7 | 19.7 | 0 | 22.97 | 0
2025-02-02 | -13.7 | 31.7 | 0 | 2024-02-02 | -1.7 | 19.7 | 0 | 2023-02-02 | -1.3 | 19.3 | 0 | 2022-02-02 | 3.3 | 14.7 | 0 | 2021-02-02 | -1.9 | 19.9 | 0 | 2020-02-02 | -2 | 20 | 0 | 2019-02-02 | -6.4 | 24.4 | 0 | 2018-02-02 | -15.9 | 33.9 | 0 | 2017-02-02 | -7.2 | 25.2 | 0 | 2016-02-02 | -2.1 | 20.1 | 0 | 22.89 | 0
2025-02-02 | -13.5 | 31.5 | 0 | 2024-02-02 | -2.3 | 20.3 | 0 | 2023-02-02 | -1.1 | 19.1 | 0 | 2022-02-02 | 2.8 | 15.2 | 0 | 2021-02-02 | -0.7 | 18.7 | 0 | 2020-02-02 | -2.4 | 20.4 | 0 | 2019-02-02 | -6.3 | 24.3 | 0 | 2018-02-02 | -16.4 | 34.4 | 0 | 2017-02-02 | -8.7 | 26.7 | 0 | 2016-02-02 | -3.7 | 21.7 | 0 | 23.23 | 0
2025-02-02 | -13.5 | 31.5 | 0 | 2024-02-02 | -2.5 | 20.5 | 0 | 2023-02-02 | -1.2 | 19.2 | 0 | 2022-02-02 | 2.7 | 15.3 | 0 | 2021-02-02 | 0 | 18 | 0 | 2020-02-02 | -4.4 | 22.4 | 0 | 2019-02-02 | -6.9 | 24.9 | 0 | 2018-02-02 | -16.9 | 34.9 | 0 | 2017-02-02 | -7.8 | 25.8 | 0 | 2016-02-02 | -4.3 | 22.3 | 0 | 23.48 | 0
2025-02-02 | -13.7 | 31.7 | 0 | 2024-02-02 | -3 | 21 | 0 | 2023-02-02 | -1.5 | 19.5 | 0 | 2022-02-02 | 2.1 | 15.9 | 0 | 2021-02-02 | 0.4 | 17.6 | 0 | 2020-02-02 | -5 | 23 | 0 | 2019-02-02 | -8.5 | 26.5 | 0 | 2018-02-02 | -17 | 35 | 0 | 2017-02-02 | -8.3 | 26.3 | 0 | 2016-02-02 | -5 | 23 | 0 | 23.95 | 0
2025-02-02 | -13.8 | 31.8 | 0 | 2024-02-02 | -3 | 21 | 0 | 2023-02-02 | -3.7 | 21.7 | 0 | 2022-02-02 | 1 | 17 | 0 | 2021-02-02 | 0.5 | 17.5 | 0 | 2020-02-02 | -5.1 | 23.1 | 0 | 2019-02-02 | -9.9 | 27.9 | 0 | 2018-02-02 | -17.6 | 35.6 | 0 | 2017-02-02 | -8.3 | 26.3 | 0 | 2016-02-02 | -4.3 | 22.3 | 0 | 24.42 | 0
2025-02-02 | -13.7 | 31.7 | 0 | 2024-02-02 | -3 | 21 | 0 | 2023-02-02 | -8.3 | 26.3 | 0 | 2022-02-02 | 0.7 | 17.3 | 0 | 2021-02-02 | -1.6 | 19.6 | 0 | 2020-02-02 | -5 | 23 | 0 | 2019-02-02 | -9.1 | 27.1 | 0 | 2018-02-02 | -18.8 | 36.8 | 0 | 2017-02-02 | -8.4 | 26.4 | 0 | 2016-02-02 | -4.3 | 22.3 | 0 | 25.15 | 0
2025-02-02 | -13.7 | 31.7 | 0 | 2024-02-02 | -3.1 | 21.1 | 0 | 2023-02-02 | -10.5 | 28.5 | 0 | 2022-02-02 | 0.7 | 17.3 | 0 | 2021-02-02 | -2.1 | 20.1 | 0 | 2020-02-02 | -4.5 | 22.5 | 0 | 2019-02-02 | -7.9 | 25.9 | 0 | 2018-02-02 | -19 | 37 | 0 | 2017-02-02 | -8.8 | 26.8 | 0 | 2016-02-02 | -4 | 22 | 0 | 25.29 | 0
2025-02-02 | -13.6 | 31.6 | 0 | 2024-02-02 | -3.4 | 21.4 | 0 | 2023-02-02 | -14.7 | 32.7 | 0 | 2022-02-02 | 0.9 | 17.1 | 0 | 2021-02-02 | -2.5 | 20.5 | 0 | 2020-02-02 | -4.9 | 22.9 | 0 | 2019-02-02 | -9.1 | 27.1 | 0 | 2018-02-02 | -19.5 | 37.5 | 0 | 2017-02-02 | -9.2 | 27.2 | 0 | 2016-02-02 | -3.9 | 21.9 | 0 | 25.99 | 0
2025-02-03 | -13.5 | 31.5 | 0 | 2024-02-03 | -3.7 | 21.7 | 0 | 2023-02-03 | -16.1 | 34.1 | 0 | 2022-02-03 | 0.9 | 17.1 | 0 | 2021-02-03 | -3 | 21 | 0 | 2020-02-03 | -4.6 | 22.6 | 0 | 2019-02-03 | -8.7 | 26.7 | 0 | 2018-02-03 | -19.5 | 37.5 | 0 | 2017-02-03 | -9.1 | 27.1 | 0 | 2016-02-03 | -3.9 | 21.9 | 0 | 26.12 | 0
2025-02-03 | -13.2 | 31.2 | 0 | 2024-02-03 | -4.4 | 22.4 | 0 | 2023-02-03 | -17.2 | 35.2 | 0 | 2022-02-03 | 0.3 | 17.7 | 0 | 2021-02-03 | -3 | 21 | 0 | 2020-02-03 | -4.3 | 22.3 | 0 | 2019-02-03 | -7.7 | 25.7 | 0 | 2018-02-03 | -19.4 | 37.4 | 0 | 2017-02-03 | -9.2 | 27.2 | 0 | 2016-02-03 | -4 | 22 | 0 | 26.21 | 0
2025-02-03 | -13 | 31 | 0 | 2024-02-03 | -4.9 | 22.9 | 0 | 2023-02-03 | -18.5 | 36.5 | 0 | 2022-02-03 | 0 | 18 | 0 | 2021-02-03 | -3.3 | 21.3 | 0 | 2020-02-03 | -4.5 | 22.5 | 0 | 2019-02-03 | -9.1 | 27.1 | 0 | 2018-02-03 | -19.2 | 37.2 | 0 | 2017-02-03 | -8.8 | 26.8 | 0 | 2016-02-03 | -3.8 | 21.8 | 0 | 26.51 | 0
2025-02-03 | -12.9 | 30.9 | 0 | 2024-02-03 | -5.5 | 23.5 | 0 | 2023-02-03 | -20.6 | 38.6 | 0 | 2022-02-03 | -0.1 | 18.1 | 0 | 2021-02-03 | -3.7 | 21.7 | 0 | 2020-02-03 | -4.1 | 22.1 | 0 | 2019-02-03 | -9.5 | 27.5 | 0 | 2018-02-03 | -18.4 | 36.4 | 0 | 2017-02-03 | -7.9 | 25.9 | 0 | 2016-02-03 | -3.9 | 21.9 | 0 | 26.66 | 0
2025-02-03 | -12.6 | 30.6 | 0 | 2024-02-03 | -6 | 24 | 0 | 2023-02-03 | -22 | 40 | 0 | 2022-02-03 | -2.5 | 20.5 | 0 | 2021-02-03 | -3.7 | 21.7 | 0 | 2020-02-03 | -4.4 | 22.4 | 0 | 2019-02-03 | -9.9 | 27.9 | 0 | 2018-02-03 | -18.4 | 36.4 | 0 | 2017-02-03 | -7.4 | 25.4 | 0 | 2016-02-03 | -4.8 | 22.8 | 0 | 27.17 | 0
2025-02-03 | -12.8 | 30.8 | 0 | 2024-02-03 | -6.3 | 24.3 | 0 | 2023-02-03 | -23.3 | 41.3 | 0 | 2022-02-03 | -3.8 | 21.8 | 0 | 2021-02-03 | -3.3 | 21.3 | 0 | 2020-02-03 | -4.3 | 22.3 | 0 | 2019-02-03 | -10.6 | 28.6 | 0 | 2018-02-03 | -19.1 | 37.1 | 0 | 2017-02-03 | -7.7 | 25.7 | 0 | 2016-02-03 | -4.3 | 22.3 | 0 | 27.55 | 0
2025-02-03 | -12.6 | 30.6 | 0 | 2024-02-03 | -6.5 | 24.5 | 0 | 2023-02-03 | -24.9 | 42.9 | 0 | 2022-02-03 | -4.9 | 22.9 | 0 | 2021-02-03 | -3.6 | 21.6 | 0 | 2020-02-03 | -3.9 | 21.9 | 0 | 2019-02-03 | -10.4 | 28.4 | 0 | 2018-02-03 | -18.4 | 36.4 | 0 | 2017-02-03 | -8.2 | 26.2 | 0 | 2016-02-03 | -3.6 | 21.6 | 0 | 27.7 | 0
2025-02-03 | -12.3 | 30.3 | 0 | 2024-02-03 | -6.6 | 24.6 | 0 | 2023-02-03 | -26 | 44 | 0 | 2022-02-03 | -5.8 | 23.8 | 0 | 2021-02-03 | -3.9 | 21.9 | 0 | 2020-02-03 | -3.8 | 21.8 | 0 | 2019-02-03 | -10.5 | 28.5 | 0 | 2018-02-03 | -17.4 | 35.4 | 0 | 2017-02-03 | -8.4 | 26.4 | 0 | 2016-02-03 | -2.9 | 20.9 | 0 | 27.76 | 0
2025-02-03 | -11.8 | 29.8 | 0 | 2024-02-03 | -6.5 | 24.5 | 0 | 2023-02-03 | -27 | 45 | 0 | 2022-02-03 | -6.4 | 24.4 | 0 | 2021-02-03 | -4.2 | 22.2 | 0 | 2020-02-03 | -3.3 | 21.3 | 0 | 2019-02-03 | -10.6 | 28.6 | 0 | 2018-02-03 | -16.5 | 34.5 | 0 | 2017-02-03 | -8.6 | 26.6 | 0 | 2016-02-03 | -2.2 | 20.2 | 0 | 27.71 | 0
2025-02-03 | -10.7 | 28.7 | 0 | 2024-02-03 | -5.6 | 23.6 | 0 | 2023-02-03 | -27 | 45 | 0 | 2022-02-03 | -6.9 | 24.9 | 0 | 2021-02-03 | -4.2 | 22.2 | 0 | 2020-02-03 | -1.7 | 19.7 | 0 | 2019-02-03 | -10.4 | 28.4 | 0 | 2018-02-03 | -15.1 | 33.1 | 0 | 2017-02-03 | -8.9 | 26.9 | 0 | 2016-02-03 | -1.3 | 19.3 | 0 | 27.18 | 0
2025-02-03 | -9.3 | 27.3 | 0 | 2024-02-03 | -4.8 | 22.8 | 0 | 2023-02-03 | -27.1 | 45.1 | 0 | 2022-02-03 | -6.9 | 24.9 | 0 | 2021-02-03 | -4.2 | 22.2 | 0 | 2020-02-03 | -0.2 | 18.2 | 0 | 2019-02-03 | -10.4 | 28.4 | 0 | 2018-02-03 | -12.7 | 30.7 | 0 | 2017-02-03 | -8.2 | 26.2 | 0 | 2016-02-03 | -1.1 | 19.1 | 0 | 26.49 | 0
2025-02-03 | -7.8 | 25.8 | 0 | 2024-02-03 | -3.8 | 21.8 | 0 | 2023-02-03 | -27.1 | 45.1 | 0 | 2022-02-03 | -6.9 | 24.9 | 0 | 2021-02-03 | -4.1 | 22.1 | 0 | 2020-02-03 | 1.3 | 16.7 | 0 | 2019-02-03 | -10.8 | 28.8 | 0 | 2018-02-03 | -10.8 | 28.8 | 0 | 2017-02-03 | -8 | 26 | 0 | 2016-02-03 | -0.5 | 18.5 | 0 | 25.85 | 0
2025-02-03 | -6.2 | 24.2 | 0 | 2024-02-03 | -3 | 21 | 0 | 2023-02-03 | -26.9 | 44.9 | 0 | 2022-02-03 | -7.3 | 25.3 | 0 | 2021-02-03 | -4.1 | 22.1 | 0 | 2020-02-03 | 2.3 | 15.7 | 0 | 2019-02-03 | -11.3 | 29.3 | 0 | 2018-02-03 | -9.7 | 27.7 | 0 | 2017-02-03 | -6.9 | 24.9 | 0 | 2016-02-03 | 0 | 18 | 0 | 25.31 | 0
2025-02-03 | -4.4 | 22.4 | 0 | 2024-02-03 | -3 | 21 | 0 | 2023-02-03 | -26.6 | 44.6 | 0 | 2022-02-03 | -7.6 | 25.6 | 0 | 2021-02-03 | -2.3 | 20.3 | 0 | 2020-02-03 | 2.9 | 15.1 | 0 | 2019-02-03 | -11.3 | 29.3 | 0 | 2018-02-03 | -8.4 | 26.4 | 0 | 2017-02-03 | -6.4 | 24.4 | 0 | 2016-02-03 | 0.2 | 17.8 | 0 | 24.69 | 0
2025-02-03 | -3.9 | 21.9 | 0 | 2024-02-03 | -2.5 | 20.5 | 0 | 2023-02-03 | -26.5 | 44.5 | 0 | 2022-02-03 | -8.1 | 26.1 | 0 | 2021-02-03 | -0.2 | 18.2 | 0 | 2020-02-03 | 3.1 | 14.9 | 0 | 2019-02-03 | -12.1 | 30.1 | 0 | 2018-02-03 | -7.9 | 25.9 | 0 | 2017-02-03 | -6.2 | 24.2 | 0 | 2016-02-03 | 0.5 | 17.5 | 0 | 24.38 | 0
2025-02-03 | -2.5 | 20.5 | 0 | 2024-02-03 | -2.4 | 20.4 | 0 | 2023-02-03 | -26.2 | 44.2 | 0 | 2022-02-03 | -8.3 | 26.3 | 0 | 2021-02-03 | 0.8 | 17.2 | 0 | 2020-02-03 | 3.3 | 14.7 | 0 | 2019-02-03 | -12.1 | 30.1 | 0 | 2018-02-03 | -7.5 | 25.5 | 0 | 2017-02-03 | -6.2 | 24.2 | 0 | 2016-02-03 | 0.8 | 17.2 | 0 | 24.03 | 0
2025-02-03 | -1.5 | 19.5 | 0 | 2024-02-03 | -2.4 | 20.4 | 0 | 2023-02-03 | -26.3 | 44.3 | 0 | 2022-02-03 | -8.6 | 26.6 | 0 | 2021-02-03 | 1.2 | 16.8 | 0 | 2020-02-03 | 2.8 | 15.2 | 0 | 2019-02-03 | -12 | 30 | 0 | 2018-02-03 | -7 | 25 | 0 | 2017-02-03 | -6.3 | 24.3 | 0 | 2016-02-03 | 1.4 | 16.6 | 0 | 23.87 | 0
2025-02-03 | -1.2 | 19.2 | 0 | 2024-02-03 | -2.4 | 20.4 | 0 | 2023-02-03 | -26.5 | 44.5 | 0 | 2022-02-03 | -9 | 27 | 0 | 2021-02-03 | -0.3 | 18.3 | 0 | 2020-02-03 | 1.9 | 16.1 | 0 | 2019-02-03 | -12.1 | 30.1 | 0 | 2018-02-03 | -6.9 | 24.9 | 0 | 2017-02-03 | -6.5 | 24.5 | 0 | 2016-02-03 | 1.3 | 16.7 | 0 | 24.17 | 0
2025-02-03 | -0.9 | 18.9 | 0 | 2024-02-03 | -2.6 | 20.6 | 0 | 2023-02-03 | -26.3 | 44.3 | 0 | 2022-02-03 | -9.4 | 27.4 | 0 | 2021-02-03 | -0.3 | 18.3 | 0 | 2020-02-03 | 0.9 | 17.1 | 0 | 2019-02-03 | -12.1 | 30.1 | 0 | 2018-02-03 | -7.1 | 25.1 | 0 | 2017-02-03 | -7.4 | 25.4 | 0 | 2016-02-03 | 0.8 | 17.2 | 0 | 24.44 | 0
2025-02-03 | -0.7 | 18.7 | 0 | 2024-02-03 | -2.9 | 20.9 | 0 | 2023-02-03 | -26.6 | 44.6 | 0 | 2022-02-03 | -9.8 | 27.8 | 0 | 2021-02-03 | -0.7 | 18.7 | 0 | 2020-02-03 | -2.6 | 20.6 | 0 | 2019-02-03 | -12 | 30 | 0 | 2018-02-03 | -7.8 | 25.8 | 0 | 2017-02-03 | -6.4 | 24.4 | 0 | 2016-02-03 | 0.7 | 17.3 | 0 | 24.88 | 0
2025-02-03 | -1.1 | 19.1 | 0 | 2024-02-03 | -2.8 | 20.8 | 0 | 2023-02-03 | -26.9 | 44.9 | 0 | 2022-02-03 | -10.6 | 28.6 | 0 | 2021-02-03 | -1.5 | 19.5 | 0 | 2020-02-03 | -1.1 | 19.1 | 0 | 2019-02-03 | -11.8 | 29.8 | 0 | 2018-02-03 | -8.3 | 26.3 | 0 | 2017-02-03 | -6.5 | 24.5 | 0 | 2016-02-03 | 4.5 | 13.5 | 0 | 24.61 | 0
2025-02-03 | -2 | 20 | 0 | 2024-02-03 | -3.3 | 21.3 | 0 | 2023-02-03 | -27.3 | 45.3 | 0 | 2022-02-03 | -11.3 | 29.3 | 0 | 2021-02-03 | -1.2 | 19.2 | 0 | 2020-02-03 | -2.3 | 20.3 | 0 | 2019-02-03 | -11.7 | 29.7 | 0 | 2018-02-03 | -8 | 26 | 0 | 2017-02-03 | -7.2 | 25.2 | 0 | 2016-02-03 | 7.5 | 10.5 | 0 | 24.68 | 0
2025-02-03 | -2.9 | 20.9 | 0 | 2024-02-03 | -3.6 | 21.6 | 0 | 2023-02-03 | -27.5 | 45.5 | 0 | 2022-02-03 | -11.6 | 29.6 | 0 | 2021-02-03 | -2.4 | 20.4 | 0 | 2020-02-03 | -3 | 21 | 0 | 2019-02-03 | -11.5 | 29.5 | 0 | 2018-02-03 | -7.3 | 25.3 | 0 | 2017-02-03 | -9.2 | 27.2 | 0 | 2016-02-03 | 7.2 | 10.8 | 0 | 25.18 | 0
2025-02-03 | -2.9 | 20.9 | 0 | 2024-02-03 | -4 | 22 | 0 | 2023-02-03 | -27.7 | 45.7 | 0 | 2022-02-03 | -12 | 30 | 0 | 2021-02-03 | -2.3 | 20.3 | 0 | 2020-02-03 | -2.3 | 20.3 | 0 | 2019-02-03 | -11.4 | 29.4 | 0 | 2018-02-03 | -6.8 | 24.8 | 0 | 2017-02-03 | -9.7 | 27.7 | 0 | 2016-02-03 | 6.1 | 11.9 | 0 | 25.3 | 0
2025-02-04 | -4.1 | 22.1 | 0 | 2024-02-04 | -4.3 | 22.3 | 0 | 2023-02-04 | -27.9 | 45.9 | 0 | 2022-02-04 | -12.2 | 30.2 | 0 | 2021-02-04 | -2.6 | 20.6 | 0 | 2020-02-04 | -1.6 | 19.6 | 0 | 2019-02-04 | -11.2 | 29.2 | 0 | 2018-02-04 | -6.7 | 24.7 | 0 | 2017-02-04 | -10.8 | 28.8 | 0 | 2016-02-04 | 4.1 | 13.9 | 0 | 25.73 | 0
2025-02-04 | -5.6 | 23.6 | 0 | 2024-02-04 | -4.2 | 22.2 | 0 | 2023-02-04 | -28.6 | 46.6 | 0 | 2022-02-04 | -12.3 | 30.3 | 0 | 2021-02-04 | -3.8 | 21.8 | 0 | 2020-02-04 | -1.8 | 19.8 | 0 | 2019-02-04 | -10.9 | 28.9 | 0 | 2018-02-04 | -6.9 | 24.9 | 0 | 2017-02-04 | -12.4 | 30.4 | 0 | 2016-02-04 | 3.3 | 14.7 | 0 | 26.32 | 0
2025-02-04 | -7.7 | 25.7 | 0 | 2024-02-04 | -4.5 | 22.5 | 0 | 2023-02-04 | -29.3 | 47.3 | 0 | 2022-02-04 | -12.5 | 30.5 | 0 | 2021-02-04 | -4.3 | 22.3 | 0 | 2020-02-04 | -2.4 | 20.4 | 0 | 2019-02-04 | -10.8 | 28.8 | 0 | 2018-02-04 | -6.3 | 24.3 | 0 | 2017-02-04 | -12.4 | 30.4 | 0 | 2016-02-04 | 3.6 | 14.4 | 0 | 26.66 | 0
2025-02-04 | -7.8 | 25.8 | 0 | 2024-02-04 | -4.7 | 22.7 | 0 | 2023-02-04 | -30.6 | 48.6 | 0 | 2022-02-04 | -12.9 | 30.9 | 0 | 2021-02-04 | -5.6 | 23.6 | 0 | 2020-02-04 | -3.4 | 21.4 | 0 | 2019-02-04 | -10.6 | 28.6 | 0 | 2018-02-04 | -5.5 | 23.5 | 0 | 2017-02-04 | -12.8 | 30.8 | 0 | 2016-02-04 | 2.2 | 15.8 | 0 | 27.17 | 0
2025-02-04 | -7.5 | 25.5 | 0 | 2024-02-04 | -5.5 | 23.5 | 0 | 2023-02-04 | -31.3 | 49.3 | 0 | 2022-02-04 | -13.3 | 31.3 | 0 | 2021-02-04 | -5.8 | 23.8 | 0 | 2020-02-04 | -5.2 | 23.2 | 0 | 2019-02-04 | -10.4 | 28.4 | 0 | 2018-02-04 | -4.3 | 22.3 | 0 | 2017-02-04 | -13.1 | 31.1 | 0 | 2016-02-04 | 2.6 | 15.4 | 0 | 27.38 | 0
2025-02-04 | -7.3 | 25.3 | 0 | 2024-02-04 | -7.7 | 25.7 | 0 | 2023-02-04 | -31 | 49 | 0 | 2022-02-04 | -13.4 | 31.4 | 0 | 2021-02-04 | -6.7 | 24.7 | 0 | 2020-02-04 | -5.6 | 23.6 | 0 | 2019-02-04 | -10.2 | 28.2 | 0 | 2018-02-04 | -4.5 | 22.5 | 0 | 2017-02-04 | -13.3 | 31.3 | 0 | 2016-02-04 | 2.7 | 15.3 | 0 | 27.7 | 0
2025-02-04 | -7.5 | 25.5 | 0 | 2024-02-04 | -7 | 25 | 0 | 2023-02-04 | -32.2 | 50.2 | 0 | 2022-02-04 | -13.6 | 31.6 | 0 | 2021-02-04 | -7 | 25 | 0 | 2020-02-04 | -4.2 | 22.2 | 0 | 2019-02-04 | -10 | 28 | 0 | 2018-02-04 | -3.8 | 21.8 | 0 | 2017-02-04 | -13.7 | 31.7 | 0 | 2016-02-04 | 2.4 | 15.6 | 0 | 27.66 | 0
2025-02-04 | -7.8 | 25.8 | 0 | 2024-02-04 | -6.3 | 24.3 | 0 | 2023-02-04 | -31.8 | 49.8 | 0 | 2022-02-04 | -13.6 | 31.6 | 0 | 2021-02-04 | -7.7 | 25.7 | 0 | 2020-02-04 | -3.7 | 21.7 | 0 | 2019-02-04 | -9.6 | 27.6 | 0 | 2018-02-04 | -3 | 21 | 0 | 2017-02-04 | -14.1 | 32.1 | 0 | 2016-02-04 | 2.5 | 15.5 | 0 | 27.51 | 0
2025-02-04 | -8.7 | 26.7 | 0 | 2024-02-04 | -7 | 25 | 0 | 2023-02-04 | -31.9 | 49.9 | 0 | 2022-02-04 | -13.7 | 31.7 | 0 | 2021-02-04 | -8 | 26 | 0 | 2020-02-04 | -3 | 21 | 0 | 2019-02-04 | -8.7 | 26.7 | 0 | 2018-02-04 | -2.2 | 20.2 | 0 | 2017-02-04 | -13.2 | 31.2 | 0 | 2016-02-04 | 2.6 | 15.4 | 0 | 27.38 | 0
2025-02-04 | -8.7 | 26.7 | 0 | 2024-02-04 | -6.2 | 24.2 | 0 | 2023-02-04 | -30 | 48 | 0 | 2022-02-04 | -13.5 | 31.5 | 0 | 2021-02-04 | -7.6 | 25.6 | 0 | 2020-02-04 | -2.7 | 20.7 | 0 | 2019-02-04 | -8 | 26 | 0 | 2018-02-04 | -2.2 | 20.2 | 0 | 2017-02-04 | -9.8 | 27.8 | 0 | 2016-02-04 | 2.5 | 15.5 | 0 | 26.62 | 0
2025-02-04 | -8.4 | 26.4 | 0 | 2024-02-04 | -5 | 23 | 0 | 2023-02-04 | -27.4 | 45.4 | 0 | 2022-02-04 | -13 | 31 | 0 | 2021-02-04 | -6 | 24 | 0 | 2020-02-04 | -1.3 | 19.3 | 0 | 2019-02-04 | -7.5 | 25.5 | 0 | 2018-02-04 | -1.7 | 19.7 | 0 | 2017-02-04 | -7.9 | 25.9 | 0 | 2016-02-04 | 2.3 | 15.7 | 0 | 25.59 | 0
2025-02-04 | -8.2 | 26.2 | 0 | 2024-02-04 | -3.7 | 21.7 | 0 | 2023-02-04 | -24.8 | 42.8 | 0 | 2022-02-04 | -12.4 | 30.4 | 0 | 2021-02-04 | -4.4 | 22.4 | 0 | 2020-02-04 | -0.3 | 18.3 | 0 | 2019-02-04 | -6.7 | 24.7 | 0 | 2018-02-04 | -1.2 | 19.2 | 0 | 2017-02-04 | -6.4 | 24.4 | 0 | 2016-02-04 | 1.9 | 16.1 | 0 | 24.62 | 0
2025-02-04 | -8.1 | 26.1 | 0 | 2024-02-04 | -2.6 | 20.6 | 0 | 2023-02-04 | -23.4 | 41.4 | 0 | 2022-02-04 | -11.8 | 29.8 | 0 | 2021-02-04 | -2.8 | 20.8 | 0 | 2020-02-04 | 0.3 | 17.7 | 0 | 2019-02-04 | -6.2 | 24.2 | 0 | 2018-02-04 | -0.5 | 18.5 | 0 | 2017-02-04 | -5.1 | 23.1 | 0 | 2016-02-04 | 1.9 | 16.1 | 0 | 23.83 | 0
2025-02-04 | -8.1 | 26.1 | 0 | 2024-02-04 | -2 | 20 | 0 | 2023-02-04 | -22.5 | 40.5 | 0 | 2022-02-04 | -11.9 | 29.9 | 0 | 2021-02-04 | -1.2 | 19.2 | 0 | 2020-02-04 | 0.9 | 17.1 | 0 | 2019-02-04 | -5.3 | 23.3 | 0 | 2018-02-04 | -0.3 | 18.3 | 0 | 2017-02-04 | -4.5 | 22.5 | 0 | 2016-02-04 | 2.5 | 15.5 | 0 | 23.24 | 0
2025-02-04 | -7.7 | 25.7 | 0 | 2024-02-04 | -1.3 | 19.3 | 0 | 2023-02-04 | -21.9 | 39.9 | 0 | 2022-02-04 | -11.1 | 29.1 | 0 | 2021-02-04 | -0.8 | 18.8 | 0 | 2020-02-04 | 1.5 | 16.5 | 0 | 2019-02-04 | -4.6 | 22.6 | 0 | 2018-02-04 | -0.3 | 18.3 | 0 | 2017-02-04 | -3.7 | 21.7 | 0 | 2016-02-04 | 1.9 | 16.1 | 0 | 22.8 | 0
2025-02-04 | -7.3 | 25.3 | 0 | 2024-02-04 | -1.1 | 19.1 | 0 | 2023-02-04 | -20.9 | 38.9 | 0 | 2022-02-04 | -10.9 | 28.9 | 0 | 2021-02-04 | 0 | 18 | 0 | 2020-02-04 | 1.4 | 16.6 | 0 | 2019-02-04 | -4.2 | 22.2 | 0 | 2018-02-04 | 0.5 | 17.5 | 0 | 2017-02-04 | -3.7 | 21.7 | 0 | 2016-02-04 | 1.5 | 16.5 | 0 | 22.47 | 0
2025-02-04 | -8 | 26 | 0 | 2024-02-04 | -1 | 19 | 0 | 2023-02-04 | -20.4 | 38.4 | 0 | 2022-02-04 | -11.2 | 29.2 | 0 | 2021-02-04 | 0.7 | 17.3 | 0 | 2020-02-04 | 1.1 | 16.9 | 0 | 2019-02-04 | -4.1 | 22.1 | 0 | 2018-02-04 | 0.2 | 17.8 | 0 | 2017-02-04 | -3.7 | 21.7 | 0 | 2016-02-04 | 0.9 | 17.1 | 0 | 22.55 | 0
2025-02-04 | -9.1 | 27.1 | 0 | 2024-02-04 | -0.9 | 18.9 | 0 | 2023-02-04 | -20.7 | 38.7 | 0 | 2022-02-04 | -11.8 | 29.8 | 0 | 2021-02-04 | -0.2 | 18.2 | 0 | 2020-02-04 | 1 | 17 | 0 | 2019-02-04 | -4 | 22 | 0 | 2018-02-04 | 0 | 18 | 0 | 2017-02-04 | -3.9 | 21.9 | 0 | 2016-02-04 | 0.3 | 17.7 | 0 | 22.93 | 0
2025-02-04 | -10.3 | 28.3 | 0 | 2024-02-04 | -1.3 | 19.3 | 0 | 2023-02-04 | -20.7 | 38.7 | 0 | 2022-02-04 | -12.1 | 30.1 | 0 | 2021-02-04 | -1.5 | 19.5 | 0 | 2020-02-04 | -0.1 | 18.1 | 0 | 2019-02-04 | -3.8 | 21.8 | 0 | 2018-02-04 | 0 | 18 | 0 | 2017-02-04 | -4.1 | 22.1 | 0 | 2016-02-04 | -0.1 | 18.1 | 0 | 23.4 | 0
2025-02-04 | -11.2 | 29.2 | 0 | 2024-02-04 | -1.5 | 19.5 | 0 | 2023-02-04 | -20.9 | 38.9 | 0 | 2022-02-04 | -13.1 | 31.1 | 0 | 2021-02-04 | -3 | 21 | 0 | 2020-02-04 | -0.8 | 18.8 | 0 | 2019-02-04 | -3.8 | 21.8 | 0 | 2018-02-04 | 0 | 18 | 0 | 2017-02-04 | -4.3 | 22.3 | 0 | 2016-02-04 | -0.4 | 18.4 | 0 | 23.9 | 0
2025-02-04 | -12.6 | 30.6 | 0 | 2024-02-04 | -1.4 | 19.4 | 0 | 2023-02-04 | -20.6 | 38.6 | 0 | 2022-02-04 | -13.3 | 31.3 | 0 | 2021-02-04 | -3.5 | 21.5 | 0 | 2020-02-04 | -1.4 | 19.4 | 0 | 2019-02-04 | -4 | 22 | 0 | 2018-02-04 | 0.2 | 17.8 | 0 | 2017-02-04 | -4.6 | 22.6 | 0 | 2016-02-04 | -1.1 | 19.1 | 0 | 24.23 | 0
2025-02-04 | -13 | 31 | 0 | 2024-02-04 | -1.5 | 19.5 | 0 | 2023-02-04 | -21 | 39 | 0 | 2022-02-04 | -13.9 | 31.9 | 0 | 2021-02-04 | -3.9 | 21.9 | 0 | 2020-02-04 | -2.2 | 20.2 | 0 | 2019-02-04 | -3.8 | 21.8 | 0 | 2018-02-04 | 0.3 | 17.7 | 0 | 2017-02-04 | -5 | 23 | 0 | 2016-02-04 | -1.4 | 19.4 | 0 | 24.54 | 0
2025-02-04 | -15.6 | 33.6 | 0 | 2024-02-04 | -1.4 | 19.4 | 0 | 2023-02-04 | -21.1 | 39.1 | 0 | 2022-02-04 | -13.6 | 31.6 | 0 | 2021-02-04 | -5.2 | 23.2 | 0 | 2020-02-04 | -2.9 | 20.9 | 0 | 2019-02-04 | -3.7 | 21.7 | 0 | 2018-02-04 | -4.5 | 22.5 | 0 | 2017-02-04 | -5.3 | 23.3 | 0 | 2016-02-04 | -1.8 | 19.8 | 0 | 25.51 | 0
2025-02-04 | -15.2 | 33.2 | 0 | 2024-02-04 | -1.3 | 19.3 | 0 | 2023-02-04 | -20.8 | 38.8 | 0 | 2022-02-04 | -14 | 32 | 0 | 2021-02-04 | -6 | 24 | 0 | 2020-02-04 | -2 | 20 | 0 | 2019-02-04 | -2.8 | 20.8 | 0 | 2018-02-04 | -6.7 | 24.7 | 0 | 2017-02-04 | -6 | 24 | 0 | 2016-02-04 | -2.5 | 20.5 | 0 | 25.73 | 0
2025-02-05 | -17.1 | 35.1 | 0 | 2024-02-05 | -1.1 | 19.1 | 0 | 2023-02-05 | -20.6 | 38.6 | 0 | 2022-02-05 | -13.9 | 31.9 | 0 | 2021-02-05 | -6.5 | 24.5 | 0 | 2020-02-05 | -2.2 | 20.2 | 0 | 2019-02-05 | -1.5 | 19.5 | 0 | 2018-02-05 | -7.1 | 25.1 | 0 | 2017-02-05 | -5.5 | 23.5 | 0 | 2016-02-05 | -3.9 | 21.9 | 0 | 25.94 | 0
2025-02-05 | -15.8 | 33.8 | 0 | 2024-02-05 | -1.1 | 19.1 | 0 | 2023-02-05 | -20.1 | 38.1 | 0 | 2022-02-05 | -14.3 | 32.3 | 0 | 2021-02-05 | -8.6 | 26.6 | 0 | 2020-02-05 | -3.5 | 21.5 | 0 | 2019-02-05 | 0.6 | 17.4 | 0 | 2018-02-05 | -7.4 | 25.4 | 0 | 2017-02-05 | -5.9 | 23.9 | 0 | 2016-02-05 | -4.8 | 22.8 | 0 | 26.09 | 0
2025-02-05 | -17.6 | 35.6 | 0 | 2024-02-05 | -1.2 | 19.2 | 0 | 2023-02-05 | -19.5 | 37.5 | 0 | 2022-02-05 | -15.4 | 33.4 | 0 | 2021-02-05 | -9.4 | 27.4 | 0 | 2020-02-05 | -5.1 | 23.1 | 0 | 2019-02-05 | 3.8 | 14.2 | 0 | 2018-02-05 | -8.5 | 26.5 | 0 | 2017-02-05 | -6.4 | 24.4 | 0 | 2016-02-05 | -5.8 | 23.8 | 0 | 26.51 | 0
2025-02-05 | -16.1 | 34.1 | 0 | 2024-02-05 | -1.6 | 19.6 | 0 | 2023-02-05 | -18.8 | 36.8 | 0 | 2022-02-05 | -15.2 | 33.2 | 0 | 2021-02-05 | -8 | 26 | 0 | 2020-02-05 | -5.1 | 23.1 | 0 | 2019-02-05 | 5 | 13 | 0 | 2018-02-05 | -10 | 28 | 0 | 2017-02-05 | -5.1 | 23.1 | 0 | 2016-02-05 | -6.3 | 24.3 | 0 | 26.12 | 0
2025-02-05 | -16.5 | 34.5 | 0 | 2024-02-05 | -2.9 | 20.9 | 0 | 2023-02-05 | -18.1 | 36.1 | 0 | 2022-02-05 | -16.3 | 34.3 | 0 | 2021-02-05 | -7.5 | 25.5 | 0 | 2020-02-05 | -6.7 | 24.7 | 0 | 2019-02-05 | 5.3 | 12.7 | 0 | 2018-02-05 | -10.5 | 28.5 | 0 | 2017-02-05 | -5.3 | 23.3 | 0 | 2016-02-05 | -6.7 | 24.7 | 0 | 26.52 | 0
2025-02-05 | -17.3 | 35.3 | 0 | 2024-02-05 | -3.9 | 21.9 | 0 | 2023-02-05 | -17.6 | 35.6 | 0 | 2022-02-05 | -17.3 | 35.3 | 0 | 2021-02-05 | -7.2 | 25.2 | 0 | 2020-02-05 | -8.3 | 26.3 | 0 | 2019-02-05 | 5.3 | 12.7 | 0 | 2018-02-05 | -11.5 | 29.5 | 0 | 2017-02-05 | -5.6 | 23.6 | 0 | 2016-02-05 | -8.2 | 26.2 | 0 | 27.16 | 0
2025-02-05 | -18.4 | 36.4 | 0 | 2024-02-05 | -4.7 | 22.7 | 0 | 2023-02-05 | -17.1 | 35.1 | 0 | 2022-02-05 | -18.7 | 36.7 | 0 | 2021-02-05 | -6.2 | 24.2 | 0 | 2020-02-05 | -9.1 | 27.1 | 0 | 2019-02-05 | 5.2 | 12.8 | 0 | 2018-02-05 | -13.6 | 31.6 | 0 | 2017-02-05 | -5.8 | 23.8 | 0 | 2016-02-05 | -8.5 | 26.5 | 0 | 27.69 | 0
2025-02-05 | -19.7 | 37.7 | 0 | 2024-02-05 | -4.9 | 22.9 | 0 | 2023-02-05 | -16.8 | 34.8 | 0 | 2022-02-05 | -19.5 | 37.5 | 0 | 2021-02-05 | -5.2 | 23.2 | 0 | 2020-02-05 | -10 | 28 | 0 | 2019-02-05 | 4.9 | 13.1 | 0 | 2018-02-05 | -15.5 | 33.5 | 0 | 2017-02-05 | -5.5 | 23.5 | 0 | 2016-02-05 | -7.5 | 25.5 | 0 | 27.97 | 0
2025-02-05 | -18.7 | 36.7 | 0 | 2024-02-05 | -5.2 | 23.2 | 0 | 2023-02-05 | -16.4 | 34.4 | 0 | 2022-02-05 | -20 | 38 | 0 | 2021-02-05 | -5 | 23 | 0 | 2020-02-05 | -10.4 | 28.4 | 0 | 2019-02-05 | 5.1 | 12.9 | 0 | 2018-02-05 | -16.4 | 34.4 | 0 | 2017-02-05 | -5.3 | 23.3 | 0 | 2016-02-05 | -8.6 | 26.6 | 0 | 28.09 | 0
2025-02-05 | -17.8 | 35.8 | 0 | 2024-02-05 | -4.4 | 22.4 | 0 | 2023-02-05 | -15.4 | 33.4 | 0 | 2022-02-05 | -19.5 | 37.5 | 0 | 2021-02-05 | -3.9 | 21.9 | 0 | 2020-02-05 | -10.5 | 28.5 | 0 | 2019-02-05 | 3 | 15 | 0 | 2018-02-05 | -16.2 | 34.2 | 0 | 2017-02-05 | -4.3 | 22.3 | 0 | 2016-02-05 | -6.7 | 24.7 | 0 | 27.57 | 0
2025-02-05 | -16.3 | 34.3 | 0 | 2024-02-05 | -3.2 | 21.2 | 0 | 2023-02-05 | -13.9 | 31.9 | 0 | 2022-02-05 | -18.3 | 36.3 | 0 | 2021-02-05 | -3.4 | 21.4 | 0 | 2020-02-05 | -10.1 | 28.1 | 0 | 2019-02-05 | 1.1 | 16.9 | 0 | 2018-02-05 | -15.5 | 33.5 | 0 | 2017-02-05 | -4.2 | 22.2 | 0 | 2016-02-05 | -6 | 24 | 0 | 26.98 | 0
2025-02-05 | -15.5 | 33.5 | 0 | 2024-02-05 | -1.8 | 19.8 | 0 | 2023-02-05 | -12.6 | 30.6 | 0 | 2022-02-05 | -17.1 | 35.1 | 0 | 2021-02-05 | -2.3 | 20.3 | 0 | 2020-02-05 | -9.6 | 27.6 | 0 | 2019-02-05 | -1.4 | 19.4 | 0 | 2018-02-05 | -14.4 | 32.4 | 0 | 2017-02-05 | -3 | 21 | 0 | 2016-02-05 | -5.1 | 23.1 | 0 | 26.28 | 0
2025-02-05 | -14.8 | 32.8 | 0 | 2024-02-05 | -0.7 | 18.7 | 0 | 2023-02-05 | -11.3 | 29.3 | 0 | 2022-02-05 | -15.9 | 33.9 | 0 | 2021-02-05 | 1.8 | 16.2 | 0 | 2020-02-05 | -9.2 | 27.2 | 0 | 2019-02-05 | -3.6 | 21.6 | 0 | 2018-02-05 | -13.2 | 31.2 | 0 | 2017-02-05 | -2.1 | 20.1 | 0 | 2016-02-05 | -4.2 | 22.2 | 0 | 25.32 | 0
2025-02-05 | -13.9 | 31.9 | 0 | 2024-02-05 | 0.5 | 17.5 | 0 | 2023-02-05 | -9.8 | 27.8 | 0 | 2022-02-05 | -15.1 | 33.1 | 0 | 2021-02-05 | 1.2 | 16.8 | 0 | 2020-02-05 | -9.2 | 27.2 | 0 | 2019-02-05 | -4.7 | 22.7 | 0 | 2018-02-05 | -11.5 | 29.5 | 0 | 2017-02-05 | -1.9 | 19.9 | 0 | 2016-02-05 | -3.6 | 21.6 | 0 | 24.8 | 0
2025-02-05 | -12.9 | 30.9 | 0 | 2024-02-05 | 0.7 | 17.3 | 0 | 2023-02-05 | -8.9 | 26.9 | 0 | 2022-02-05 | -15.1 | 33.1 | 0 | 2021-02-05 | 0.6 | 17.4 | 0 | 2020-02-05 | -8.6 | 26.6 | 0 | 2019-02-05 | -5.1 | 23.1 | 0 | 2018-02-05 | -9.6 | 27.6 | 0 | 2017-02-05 | -1.2 | 19.2 | 0 | 2016-02-05 | -3 | 21 | 0 | 24.31 | 0
2025-02-05 | -12.4 | 30.4 | 0 | 2024-02-05 | 1 | 17 | 0 | 2023-02-05 | -8.3 | 26.3 | 0 | 2022-02-05 | -14.5 | 32.5 | 0 | 2021-02-05 | -0.3 | 18.3 | 0 | 2020-02-05 | -8.2 | 26.2 | 0 | 2019-02-05 | -6.3 | 24.3 | 0 | 2018-02-05 | -9.4 | 27.4 | 0 | 2017-02-05 | -0.8 | 18.8 | 0 | 2016-02-05 | -2.7 | 20.7 | 0 | 24.19 | 0
2025-02-05 | -12 | 30 | 0 | 2024-02-05 | 1.1 | 16.9 | 0 | 2023-02-05 | -8 | 26 | 0 | 2022-02-05 | -14.2 | 32.2 | 0 | 2021-02-05 | -0.6 | 18.6 | 0 | 2020-02-05 | -8.1 | 26.1 | 0 | 2019-02-05 | -6.8 | 24.8 | 0 | 2018-02-05 | -9.7 | 27.7 | 0 | 2017-02-05 | -1 | 19 | 0 | 2016-02-05 | -3.1 | 21.1 | 0 | 24.24 | 0
2025-02-05 | -12.4 | 30.4 | 0 | 2024-02-05 | 1.4 | 16.6 | 0 | 2023-02-05 | -7.5 | 25.5 | 0 | 2022-02-05 | -15.4 | 33.4 | 0 | 2021-02-05 | -1.7 | 19.7 | 0 | 2020-02-05 | -8.7 | 26.7 | 0 | 2019-02-05 | -7.7 | 25.7 | 0 | 2018-02-05 | -9.4 | 27.4 | 0 | 2017-02-05 | -1 | 19 | 0 | 2016-02-05 | -3.8 | 21.8 | 0 | 24.62 | 0
2025-02-05 | -13.6 | 31.6 | 0 | 2024-02-05 | 0.5 | 17.5 | 0 | 2023-02-05 | -7.5 | 25.5 | 0 | 2022-02-05 | -16.6 | 34.6 | 0 | 2021-02-05 | -2.7 | 20.7 | 0 | 2020-02-05 | -9.1 | 27.1 | 0 | 2019-02-05 | -8.6 | 26.6 | 0 | 2018-02-05 | -9.8 | 27.8 | 0 | 2017-02-05 | -1.1 | 19.1 | 0 | 2016-02-05 | -4.6 | 22.6 | 0 | 25.31 | 0
2025-02-05 | -14.6 | 32.6 | 0 | 2024-02-05 | -0.7 | 18.7 | 0 | 2023-02-05 | -7.2 | 25.2 | 0 | 2022-02-05 | -16.9 | 34.9 | 0 | 2021-02-05 | -3.5 | 21.5 | 0 | 2020-02-05 | -10.1 | 28.1 | 0 | 2019-02-05 | -9.3 | 27.3 | 0 | 2018-02-05 | -9.4 | 27.4 | 0 | 2017-02-05 | -1.9 | 19.9 | 0 | 2016-02-05 | -5.1 | 23.1 | 0 | 25.87 | 0
2025-02-05 | -15.2 | 33.2 | 0 | 2024-02-05 | -1.3 | 19.3 | 0 | 2023-02-05 | -7.1 | 25.1 | 0 | 2022-02-05 | -17.2 | 35.2 | 0 | 2021-02-05 | -4.2 | 22.2 | 0 | 2020-02-05 | -11 | 29 | 0 | 2019-02-05 | -10.4 | 28.4 | 0 | 2018-02-05 | -9 | 27 | 0 | 2017-02-05 | -2.7 | 20.7 | 0 | 2016-02-05 | -5.3 | 23.3 | 0 | 26.34 | 0
2025-02-05 | -15.5 | 33.5 | 0 | 2024-02-05 | -1.9 | 19.9 | 0 | 2023-02-05 | -7 | 25 | 0 | 2022-02-05 | -18.5 | 36.5 | 0 | 2021-02-05 | -4.5 | 22.5 | 0 | 2020-02-05 | -10.7 | 28.7 | 0 | 2019-02-05 | -10.3 | 28.3 | 0 | 2018-02-05 | -9.4 | 27.4 | 0 | 2017-02-05 | -4.4 | 22.4 | 0 | 2016-02-05 | -6.2 | 24.2 | 0 | 26.84 | 0
2025-02-05 | -16.9 | 34.9 | 0 | 2024-02-05 | -2.4 | 20.4 | 0 | 2023-02-05 | -6.8 | 24.8 | 0 | 2022-02-05 | -18.7 | 36.7 | 0 | 2021-02-05 | -5.4 | 23.4 | 0 | 2020-02-05 | -10.2 | 28.2 | 0 | 2019-02-05 | -10.4 | 28.4 | 0 | 2018-02-05 | -10.4 | 28.4 | 0 | 2017-02-05 | -6.8 | 24.8 | 0 | 2016-02-05 | -6.4 | 24.4 | 0 | 27.44 | 0
2025-02-05 | -16.7 | 34.7 | 0 | 2024-02-05 | -3.4 | 21.4 | 0 | 2023-02-05 | -6.7 | 24.7 | 0 | 2022-02-05 | -20.2 | 38.2 | 0 | 2021-02-05 | -6.2 | 24.2 | 0 | 2020-02-05 | -10.2 | 28.2 | 0 | 2019-02-05 | -10.8 | 28.8 | 0 | 2018-02-05 | -10.5 | 28.5 | 0 | 2017-02-05 | -8.8 | 26.8 | 0 | 2016-02-05 | -4.9 | 22.9 | 0 | 27.84 | 0
2025-02-06 | -19.1 | 37.1 | 0 | 2024-02-06 | -4.3 | 22.3 | 0 | 2023-02-06 | -6.6 | 24.6 | 0 | 2022-02-06 | -20.6 | 38.6 | 0 | 2021-02-06 | -7.2 | 25.2 | 0 | 2020-02-06 | -9.9 | 27.9 | 0 | 2019-02-06 | -12 | 30 | 0 | 2018-02-06 | -10.5 | 28.5 | 0 | 2017-02-06 | -9.7 | 27.7 | 0 | 2016-02-06 | -4 | 22 | 0 | 28.39 | 0
2025-02-06 | -19.1 | 37.1 | 0 | 2024-02-06 | -5.1 | 23.1 | 0 | 2023-02-06 | -6.1 | 24.1 | 0 | 2022-02-06 | -19.5 | 37.5 | 0 | 2021-02-06 | -7.9 | 25.9 | 0 | 2020-02-06 | -9.4 | 27.4 | 0 | 2019-02-06 | -12.6 | 30.6 | 0 | 2018-02-06 | -10.2 | 28.2 | 0 | 2017-02-06 | -10.7 | 28.7 | 0 | 2016-02-06 | -3.9 | 21.9 | 0 | 28.45 | 0
2025-02-06 | -19.2 | 37.2 | 0 | 2024-02-06 | -5.4 | 23.4 | 0 | 2023-02-06 | -5.8 | 23.8 | 0 | 2022-02-06 | -18.3 | 36.3 | 0 | 2021-02-06 | -8 | 26 | 0 | 2020-02-06 | -9.8 | 27.8 | 0 | 2019-02-06 | -13.3 | 31.3 | 0 | 2018-02-06 | -10.2 | 28.2 | 0 | 2017-02-06 | -12.2 | 30.2 | 0 | 2016-02-06 | -4.2 | 22.2 | 0 | 28.64 | 0
2025-02-06 | -19.3 | 37.3 | 0 | 2024-02-06 | -5.7 | 23.7 | 0 | 2023-02-06 | -5.6 | 23.6 | 0 | 2022-02-06 | -18.2 | 36.2 | 0 | 2021-02-06 | -9 | 27 | 0 | 2020-02-06 | -9.8 | 27.8 | 0 | 2019-02-06 | -12.8 | 30.8 | 0 | 2018-02-06 | -9.7 | 27.7 | 0 | 2017-02-06 | -14.2 | 32.2 | 0 | 2016-02-06 | -4.2 | 22.2 | 0 | 28.85 | 0
2025-02-06 | -19.6 | 37.6 | 0 | 2024-02-06 | -6.8 | 24.8 | 0 | 2023-02-06 | -6.6 | 24.6 | 0 | 2022-02-06 | -17 | 35 | 0 | 2021-02-06 | -8.7 | 26.7 | 0 | 2020-02-06 | -9.6 | 27.6 | 0 | 2019-02-06 | -12.4 | 30.4 | 0 | 2018-02-06 | -9.7 | 27.7 | 0 | 2017-02-06 | -14 | 32 | 0 | 2016-02-06 | -4.5 | 22.5 | 0 | 28.89 | 0
2025-02-06 | -19.4 | 37.4 | 0 | 2024-02-06 | -7.7 | 25.7 | 0 | 2023-02-06 | -5.8 | 23.8 | 0 | 2022-02-06 | -17.2 | 35.2 | 0 | 2021-02-06 | -8.6 | 26.6 | 0 | 2020-02-06 | -10.1 | 28.1 | 0 | 2019-02-06 | -12.1 | 30.1 | 0 | 2018-02-06 | -9.7 | 27.7 | 0 | 2017-02-06 | -14.1 | 32.1 | 0 | 2016-02-06 | -4.7 | 22.7 | 0 | 28.94 | 0
2025-02-06 | -18.6 | 36.6 | 0 | 2024-02-06 | -8.2 | 26.2 | 0 | 2023-02-06 | -7.9 | 25.9 | 0 | 2022-02-06 | -17.4 | 35.4 | 0 | 2021-02-06 | -8.4 | 26.4 | 0 | 2020-02-06 | -10.5 | 28.5 | 0 | 2019-02-06 | -11.9 | 29.9 | 0 | 2018-02-06 | -9.7 | 27.7 | 0 | 2017-02-06 | -14.5 | 32.5 | 0 | 2016-02-06 | -4.6 | 22.6 | 0 | 29.17 | 0
2025-02-06 | -18 | 36 | 0 | 2024-02-06 | -7.5 | 25.5 | 0 | 2023-02-06 | -8.6 | 26.6 | 0 | 2022-02-06 | -17.3 | 35.3 | 0 | 2021-02-06 | -8.3 | 26.3 | 0 | 2020-02-06 | -10.3 | 28.3 | 0 | 2019-02-06 | -12 | 30 | 0 | 2018-02-06 | -9.7 | 27.7 | 0 | 2017-02-06 | -14.1 | 32.1 | 0 | 2016-02-06 | -4.5 | 22.5 | 0 | 29.03 | 0
2025-02-06 | -16.5 | 34.5 | 0 | 2024-02-06 | -6.6 | 24.6 | 0 | 2023-02-06 | -8.9 | 26.9 | 0 | 2022-02-06 | -17.1 | 35.1 | 0 | 2021-02-06 | -8.6 | 26.6 | 0 | 2020-02-06 | -10.1 | 28.1 | 0 | 2019-02-06 | -11.4 | 29.4 | 0 | 2018-02-06 | -9.4 | 27.4 | 0 | 2017-02-06 | -14.2 | 32.2 | 0 | 2016-02-06 | -4.1 | 22.1 | 0 | 28.69 | 0
2025-02-06 | -15.6 | 33.6 | 0 | 2024-02-06 | -5.4 | 23.4 | 0 | 2023-02-06 | -9 | 27 | 0 | 2022-02-06 | -15.9 | 33.9 | 0 | 2021-02-06 | -8 | 26 | 0 | 2020-02-06 | -9.7 | 27.7 | 0 | 2019-02-06 | -10.9 | 28.9 | 0 | 2018-02-06 | -8.8 | 26.8 | 0 | 2017-02-06 | -13.3 | 31.3 | 0 | 2016-02-06 | -3.5 | 21.5 | 0 | 28.01 | 0
2025-02-06 | -14.8 | 32.8 | 0 | 2024-02-06 | -3.3 | 21.3 | 0 | 2023-02-06 | -8.5 | 26.5 | 0 | 2022-02-06 | -14.2 | 32.2 | 0 | 2021-02-06 | -6.9 | 24.9 | 0 | 2020-02-06 | -8.9 | 26.9 | 0 | 2019-02-06 | -10.8 | 28.8 | 0 | 2018-02-06 | -8.1 | 26.1 | 0 | 2017-02-06 | -12.2 | 30.2 | 0 | 2016-02-06 | -3.3 | 21.3 | 0 | 27.1 | 0
2025-02-06 | -13.7 | 31.7 | 0 | 2024-02-06 | -2.4 | 20.4 | 0 | 2023-02-06 | -7.8 | 25.8 | 0 | 2022-02-06 | -12.8 | 30.8 | 0 | 2021-02-06 | -5.9 | 23.9 | 0 | 2020-02-06 | -8.4 | 26.4 | 0 | 2019-02-06 | -10.7 | 28.7 | 0 | 2018-02-06 | -7.6 | 25.6 | 0 | 2017-02-06 | -11.3 | 29.3 | 0 | 2016-02-06 | -2.6 | 20.6 | 0 | 26.32 | 0
2025-02-06 | -12.5 | 30.5 | 0 | 2024-02-06 | -1.4 | 19.4 | 0 | 2023-02-06 | -7.4 | 25.4 | 0 | 2022-02-06 | -12.1 | 30.1 | 0 | 2021-02-06 | -5.3 | 23.3 | 0 | 2020-02-06 | -7.6 | 25.6 | 0 | 2019-02-06 | -10.4 | 28.4 | 0 | 2018-02-06 | -6.5 | 24.5 | 0 | 2017-02-06 | -10.4 | 28.4 | 0 | 2016-02-06 | -1.3 | 19.3 | 0 | 25.49 | 0
2025-02-06 | -12.3 | 30.3 | 0 | 2024-02-06 | -1 | 19 | 0 | 2023-02-06 | -6.4 | 24.4 | 0 | 2022-02-06 | -11.3 | 29.3 | 0 | 2021-02-06 | -4.8 | 22.8 | 0 | 2020-02-06 | -6.8 | 24.8 | 0 | 2019-02-06 | -10.7 | 28.7 | 0 | 2018-02-06 | -6 | 24 | 0 | 2017-02-06 | -10 | 28 | 0 | 2016-02-06 | -0.3 | 18.3 | 0 | 24.96 | 0
2025-02-06 | -12 | 30 | 0 | 2024-02-06 | -0.3 | 18.3 | 0 | 2023-02-06 | -5.7 | 23.7 | 0 | 2022-02-06 | -10.5 | 28.5 | 0 | 2021-02-06 | -5.2 | 23.2 | 0 | 2020-02-06 | -6.2 | 24.2 | 0 | 2019-02-06 | -10.2 | 28.2 | 0 | 2018-02-06 | -5.9 | 23.9 | 0 | 2017-02-06 | -10 | 28 | 0 | 2016-02-06 | 0.4 | 17.6 | 0 | 24.56 | 0
2025-02-06 | -11.6 | 29.6 | 0 | 2024-02-06 | 0.1 | 17.9 | 0 | 2023-02-06 | -4.9 | 22.9 | 0 | 2022-02-06 | -9.1 | 27.1 | 0 | 2021-02-06 | -5.6 | 23.6 | 0 | 2020-02-06 | -5.7 | 23.7 | 0 | 2019-02-06 | -9.9 | 27.9 | 0 | 2018-02-06 | -6.3 | 24.3 | 0 | 2017-02-06 | -9.9 | 27.9 | 0 | 2016-02-06 | 1.5 | 16.5 | 0 | 24.14 | 0
2025-02-06 | -11.3 | 29.3 | 0 | 2024-02-06 | 0 | 18 | 0 | 2023-02-06 | -5 | 23 | 0 | 2022-02-06 | -9.3 | 27.3 | 0 | 2021-02-06 | -6.3 | 24.3 | 0 | 2020-02-06 | -5.8 | 23.8 | 0 | 2019-02-06 | -10.2 | 28.2 | 0 | 2018-02-06 | -6.7 | 24.7 | 0 | 2017-02-06 | -9.8 | 27.8 | 0 | 2016-02-06 | 1.4 | 16.6 | 0 | 24.3 | 0
2025-02-06 | -11.5 | 29.5 | 0 | 2024-02-06 | -1.2 | 19.2 | 0 | 2023-02-06 | -5.5 | 23.5 | 0 | 2022-02-06 | -9.3 | 27.3 | 0 | 2021-02-06 | -6.9 | 24.9 | 0 | 2020-02-06 | -5.8 | 23.8 | 0 | 2019-02-06 | -10.4 | 28.4 | 0 | 2018-02-06 | -7.9 | 25.9 | 0 | 2017-02-06 | -10.2 | 28.2 | 0 | 2016-02-06 | 1.1 | 16.9 | 0 | 24.76 | 0
2025-02-06 | -11.3 | 29.3 | 0 | 2024-02-06 | -2.4 | 20.4 | 0 | 2023-02-06 | -7.3 | 25.3 | 0 | 2022-02-06 | -9.6 | 27.6 | 0 | 2021-02-06 | -7.5 | 25.5 | 0 | 2020-02-06 | -5.8 | 23.8 | 0 | 2019-02-06 | -10.1 | 28.1 | 0 | 2018-02-06 | -8.5 | 26.5 | 0 | 2017-02-06 | -10 | 28 | 0 | 2016-02-06 | 0.8 | 17.2 | 0 | 25.17 | 0
2025-02-06 | -10.6 | 28.6 | 0 | 2024-02-06 | -2.6 | 20.6 | 0 | 2023-02-06 | -9.1 | 27.1 | 0 | 2022-02-06 | -10 | 28 | 0 | 2021-02-06 | -8.2 | 26.2 | 0 | 2020-02-06 | -5.9 | 23.9 | 0 | 2019-02-06 | -9.9 | 27.9 | 0 | 2018-02-06 | -8.6 | 26.6 | 0 | 2017-02-06 | -10.1 | 28.1 | 0 | 2016-02-06 | 0.5 | 17.5 | 0 | 25.45 | 0
2025-02-06 | -9.7 | 27.7 | 0 | 2024-02-06 | -4.9 | 22.9 | 0 | 2023-02-06 | -11.1 | 29.1 | 0 | 2022-02-06 | -10 | 28 | 0 | 2021-02-06 | -9.1 | 27.1 | 0 | 2020-02-06 | -5.8 | 23.8 | 0 | 2019-02-06 | -9.6 | 27.6 | 0 | 2018-02-06 | -10.2 | 28.2 | 0 | 2017-02-06 | -10.2 | 28.2 | 0 | 2016-02-06 | 0.4 | 17.6 | 0 | 26.02 | 0
2025-02-06 | -6.4 | 24.4 | 0 | 2024-02-06 | -4.6 | 22.6 | 0 | 2023-02-06 | -11.4 | 29.4 | 0 | 2022-02-06 | -10.3 | 28.3 | 0 | 2021-02-06 | -9.3 | 27.3 | 0 | 2020-02-06 | -5.5 | 23.5 | 0 | 2019-02-06 | -8.8 | 26.8 | 0 | 2018-02-06 | -13.6 | 31.6 | 0 | 2017-02-06 | -10.1 | 28.1 | 0 | 2016-02-06 | 0.5 | 17.5 | 0 | 25.95 | 0
2025-02-06 | -3.5 | 21.5 | 0 | 2024-02-06 | -4.6 | 22.6 | 0 | 2023-02-06 | -11.4 | 29.4 | 0 | 2022-02-06 | -10 | 28 | 0 | 2021-02-06 | -9.1 | 27.1 | 0 | 2020-02-06 | -5.6 | 23.6 | 0 | 2019-02-06 | -8.2 | 26.2 | 0 | 2018-02-06 | -13.6 | 31.6 | 0 | 2017-02-06 | -9.9 | 27.9 | 0 | 2016-02-06 | 0.5 | 17.5 | 0 | 25.54 | 0
2025-02-06 | -2.4 | 20.4 | 0 | 2024-02-06 | -4.8 | 22.8 | 0 | 2023-02-06 | -14 | 32 | 0 | 2022-02-06 | -9.5 | 27.5 | 0 | 2021-02-06 | -9.3 | 27.3 | 0 | 2020-02-06 | -5.5 | 23.5 | 0 | 2019-02-06 | -7.9 | 25.9 | 0 | 2018-02-06 | -14.7 | 32.7 | 0 | 2017-02-06 | -10 | 28 | 0 | 2016-02-06 | 0.6 | 17.4 | 0 | 25.75 | 0
2025-02-07 | -2.2 | 20.2 | 0 | 2024-02-07 | -7.4 | 25.4 | 0 | 2023-02-07 | -13.3 | 31.3 | 0 | 2022-02-07 | -9.3 | 27.3 | 0 | 2021-02-07 | -9.9 | 27.9 | 0 | 2020-02-07 | -5.5 | 23.5 | 0 | 2019-02-07 | -7.5 | 25.5 | 0 | 2018-02-07 | -14.8 | 32.8 | 0 | 2017-02-07 | -10.1 | 28.1 | 0 | 2016-02-07 | 0.4 | 17.6 | 0 | 25.96 | 0
2025-02-07 | -2.1 | 20.1 | 0 | 2024-02-07 | -6.5 | 24.5 | 0 | 2023-02-07 | -13.2 | 31.2 | 0 | 2022-02-07 | -9 | 27 | 0 | 2021-02-07 | -10.2 | 28.2 | 0 | 2020-02-07 | -5.5 | 23.5 | 0 | 2019-02-07 | -7.2 | 25.2 | 0 | 2018-02-07 | -15.8 | 33.8 | 0 | 2017-02-07 | -10.3 | 28.3 | 0 | 2016-02-07 | 0.3 | 17.7 | 0 | 25.95 | 0
2025-02-07 | -2.4 | 20.4 | 0 | 2024-02-07 | -5.6 | 23.6 | 0 | 2023-02-07 | -13.2 | 31.2 | 0 | 2022-02-07 | -8.4 | 26.4 | 0 | 2021-02-07 | -10.2 | 28.2 | 0 | 2020-02-07 | -5.5 | 23.5 | 0 | 2019-02-07 | -7.9 | 25.9 | 0 | 2018-02-07 | -16.3 | 34.3 | 0 | 2017-02-07 | -10.5 | 28.5 | 0 | 2016-02-07 | 0.3 | 17.7 | 0 | 25.97 | 0
2025-02-07 | -3.3 | 21.3 | 0 | 2024-02-07 | -7.6 | 25.6 | 0 | 2023-02-07 | -12.1 | 30.1 | 0 | 2022-02-07 | -8.6 | 26.6 | 0 | 2021-02-07 | -10 | 28 | 0 | 2020-02-07 | -5.7 | 23.7 | 0 | 2019-02-07 | -7.5 | 25.5 | 0 | 2018-02-07 | -16.1 | 34.1 | 0 | 2017-02-07 | -10.6 | 28.6 | 0 | 2016-02-07 | 0 | 18 | 0 | 26.15 | 0
2025-02-07 | -3.1 | 21.1 | 0 | 2024-02-07 | -8.1 | 26.1 | 0 | 2023-02-07 | -13.2 | 31.2 | 0 | 2022-02-07 | -9.6 | 27.6 | 0 | 2021-02-07 | -9.3 | 27.3 | 0 | 2020-02-07 | -5.8 | 23.8 | 0 | 2019-02-07 | -7.3 | 25.3 | 0 | 2018-02-07 | -14.6 | 32.6 | 0 | 2017-02-07 | -10.5 | 28.5 | 0 | 2016-02-07 | -0.3 | 18.3 | 0 | 26.18 | 0
2025-02-07 | -5.4 | 23.4 | 0 | 2024-02-07 | -7.5 | 25.5 | 0 | 2023-02-07 | -14.1 | 32.1 | 0 | 2022-02-07 | -8.8 | 26.8 | 0 | 2021-02-07 | -9.1 | 27.1 | 0 | 2020-02-07 | -5.8 | 23.8 | 0 | 2019-02-07 | -7.5 | 25.5 | 0 | 2018-02-07 | -15 | 33 | 0 | 2017-02-07 | -10.5 | 28.5 | 0 | 2016-02-07 | -1.9 | 19.9 | 0 | 26.56 | 0
2025-02-07 | -5.2 | 23.2 | 0 | 2024-02-07 | -7.7 | 25.7 | 0 | 2023-02-07 | -13.2 | 31.2 | 0 | 2022-02-07 | -9.7 | 27.7 | 0 | 2021-02-07 | -9.4 | 27.4 | 0 | 2020-02-07 | -6.2 | 24.2 | 0 | 2019-02-07 | -7.1 | 25.1 | 0 | 2018-02-07 | -14.4 | 32.4 | 0 | 2017-02-07 | -10.5 | 28.5 | 0 | 2016-02-07 | -2.6 | 20.6 | 0 | 26.6 | 0
2025-02-07 | -6.7 | 24.7 | 0 | 2024-02-07 | -6.9 | 24.9 | 0 | 2023-02-07 | -14 | 32 | 0 | 2022-02-07 | -10.7 | 28.7 | 0 | 2021-02-07 | -9.2 | 27.2 | 0 | 2020-02-07 | -6.5 | 24.5 | 0 | 2019-02-07 | -7 | 25 | 0 | 2018-02-07 | -14.2 | 32.2 | 0 | 2017-02-07 | -10.9 | 28.9 | 0 | 2016-02-07 | -3.3 | 21.3 | 0 | 26.94 | 0
2025-02-07 | -7.7 | 25.7 | 0 | 2024-02-07 | -6.7 | 24.7 | 0 | 2023-02-07 | -13.5 | 31.5 | 0 | 2022-02-07 | -11.8 | 29.8 | 0 | 2021-02-07 | -9.6 | 27.6 | 0 | 2020-02-07 | -6.4 | 24.4 | 0 | 2019-02-07 | -6.6 | 24.6 | 0 | 2018-02-07 | -13.9 | 31.9 | 0 | 2017-02-07 | -10.8 | 28.8 | 0 | 2016-02-07 | -3.7 | 21.7 | 0 | 27.07 | 0
2025-02-07 | -7.4 | 25.4 | 0 | 2024-02-07 | -5.6 | 23.6 | 0 | 2023-02-07 | -11.9 | 29.9 | 0 | 2022-02-07 | -10.9 | 28.9 | 0 | 2021-02-07 | -9.1 | 27.1 | 0 | 2020-02-07 | -6.1 | 24.1 | 0 | 2019-02-07 | -6 | 24 | 0 | 2018-02-07 | -13 | 31 | 0 | 2017-02-07 | -10.5 | 28.5 | 0 | 2016-02-07 | -5 | 23 | 0 | 26.55 | 0
2025-02-07 | -7 | 25 | 0 | 2024-02-07 | -4.3 | 22.3 | 0 | 2023-02-07 | -10.3 | 28.3 | 0 | 2022-02-07 | -7.8 | 25.8 | 0 | 2021-02-07 | -8.5 | 26.5 | 0 | 2020-02-07 | -6.2 | 24.2 | 0 | 2019-02-07 | -5.4 | 23.4 | 0 | 2018-02-07 | -12.5 | 30.5 | 0 | 2017-02-07 | -10.7 | 28.7 | 0 | 2016-02-07 | -5.6 | 23.6 | 0 | 25.83 | 0
2025-02-07 | -6.5 | 24.5 | 0 | 2024-02-07 | -2.5 | 20.5 | 0 | 2023-02-07 | -9.1 | 27.1 | 0 | 2022-02-07 | -5.7 | 23.7 | 0 | 2021-02-07 | -8.3 | 26.3 | 0 | 2020-02-07 | -6.8 | 24.8 | 0 | 2019-02-07 | -4.7 | 22.7 | 0 | 2018-02-07 | -11.8 | 29.8 | 0 | 2017-02-07 | -10.7 | 28.7 | 0 | 2016-02-07 | -5.5 | 23.5 | 0 | 25.16 | 0
2025-02-07 | -6.2 | 24.2 | 0 | 2024-02-07 | -1.6 | 19.6 | 0 | 2023-02-07 | -8.7 | 26.7 | 0 | 2022-02-07 | -2.2 | 20.2 | 0 | 2021-02-07 | -7.5 | 25.5 | 0 | 2020-02-07 | -7.2 | 25.2 | 0 | 2019-02-07 | -4.4 | 22.4 | 0 | 2018-02-07 | -11.6 | 29.6 | 0 | 2017-02-07 | -10.3 | 28.3 | 0 | 2016-02-07 | -5.3 | 23.3 | 0 | 24.5 | 0
2025-02-07 | -6.1 | 24.1 | 0 | 2024-02-07 | -1.1 | 19.1 | 0 | 2023-02-07 | -7.2 | 25.2 | 0 | 2022-02-07 | -1.2 | 19.2 | 0 | 2021-02-07 | -6.9 | 24.9 | 0 | 2020-02-07 | -7.7 | 25.7 | 0 | 2019-02-07 | -4.2 | 22.2 | 0 | 2018-02-07 | -11.2 | 29.2 | 0 | 2017-02-07 | -10.1 | 28.1 | 0 | 2016-02-07 | -4.4 | 22.4 | 0 | 24.01 | 0
2025-02-07 | -5.9 | 23.9 | 0 | 2024-02-07 | -1 | 19 | 0 | 2023-02-07 | -6.7 | 24.7 | 0 | 2022-02-07 | -2.1 | 20.1 | 0 | 2021-02-07 | -5.5 | 23.5 | 0 | 2020-02-07 | -8.2 | 26.2 | 0 | 2019-02-07 | -4.1 | 22.1 | 0 | 2018-02-07 | -10.8 | 28.8 | 0 | 2017-02-07 | -9.8 | 27.8 | 0 | 2016-02-07 | -3.9 | 21.9 | 0 | 23.8 | 0
2025-02-07 | -5.4 | 23.4 | 0 | 2024-02-07 | -0.5 | 18.5 | 0 | 2023-02-07 | -7.8 | 25.8 | 0 | 2022-02-07 | -1.4 | 19.4 | 0 | 2021-02-07 | -5.3 | 23.3 | 0 | 2020-02-07 | -8.6 | 26.6 | 0 | 2019-02-07 | -3.9 | 21.9 | 0 | 2018-02-07 | -10.4 | 28.4 | 0 | 2017-02-07 | -9.9 | 27.9 | 0 | 2016-02-07 | -4 | 22 | 0 | 23.72 | 0
2025-02-07 | -5.5 | 23.5 | 0 | 2024-02-07 | -0.5 | 18.5 | 0 | 2023-02-07 | -7.3 | 25.3 | 0 | 2022-02-07 | -3.2 | 21.2 | 0 | 2021-02-07 | -5.3 | 23.3 | 0 | 2020-02-07 | -8.9 | 26.9 | 0 | 2019-02-07 | -3.8 | 21.8 | 0 | 2018-02-07 | -10 | 28 | 0 | 2017-02-07 | -9.9 | 27.9 | 0 | 2016-02-07 | -4.5 | 22.5 | 0 | 23.89 | 0
2025-02-07 | -5.8 | 23.8 | 0 | 2024-02-07 | -1.2 | 19.2 | 0 | 2023-02-07 | -6.8 | 24.8 | 0 | 2022-02-07 | -3.4 | 21.4 | 0 | 2021-02-07 | -5.8 | 23.8 | 0 | 2020-02-07 | -9.3 | 27.3 | 0 | 2019-02-07 | -3.9 | 21.9 | 0 | 2018-02-07 | -9.7 | 27.7 | 0 | 2017-02-07 | -10.1 | 28.1 | 0 | 2016-02-07 | -5.9 | 23.9 | 0 | 24.19 | 0
2025-02-07 | -7.1 | 25.1 | 0 | 2024-02-07 | -2.5 | 20.5 | 0 | 2023-02-07 | -6.5 | 24.5 | 0 | 2022-02-07 | -4.7 | 22.7 | 0 | 2021-02-07 | -6.4 | 24.4 | 0 | 2020-02-07 | -9.9 | 27.9 | 0 | 2019-02-07 | -4.1 | 22.1 | 0 | 2018-02-07 | -9.1 | 27.1 | 0 | 2017-02-07 | -10.6 | 28.6 | 0 | 2016-02-07 | -7.8 | 25.8 | 0 | 24.87 | 0
2025-02-07 | -7.9 | 25.9 | 0 | 2024-02-07 | -3 | 21 | 0 | 2023-02-07 | -5.8 | 23.8 | 0 | 2022-02-07 | -5.3 | 23.3 | 0 | 2021-02-07 | -7.3 | 25.3 | 0 | 2020-02-07 | -10.4 | 28.4 | 0 | 2019-02-07 | -4.1 | 22.1 | 0 | 2018-02-07 | -8.9 | 26.9 | 0 | 2017-02-07 | -10.3 | 28.3 | 0 | 2016-02-07 | -8.3 | 26.3 | 0 | 25.13 | 0
2025-02-07 | -9.8 | 27.8 | 0 | 2024-02-07 | -3.4 | 21.4 | 0 | 2023-02-07 | -4.8 | 22.8 | 0 | 2022-02-07 | -5.9 | 23.9 | 0 | 2021-02-07 | -7.8 | 25.8 | 0 | 2020-02-07 | -11 | 29 | 0 | 2019-02-07 | -4 | 22 | 0 | 2018-02-07 | -9.6 | 27.6 | 0 | 2017-02-07 | -9.7 | 27.7 | 0 | 2016-02-07 | -8.6 | 26.6 | 0 | 25.46 | 0
2025-02-07 | -9.6 | 27.6 | 0 | 2024-02-07 | -4.4 | 22.4 | 0 | 2023-02-07 | -5.2 | 23.2 | 0 | 2022-02-07 | -7.2 | 25.2 | 0 | 2021-02-07 | -9.4 | 27.4 | 0 | 2020-02-07 | -12.6 | 30.6 | 0 | 2019-02-07 | -4 | 22 | 0 | 2018-02-07 | -10.9 | 28.9 | 0 | 2017-02-07 | -8.8 | 26.8 | 0 | 2016-02-07 | -8.7 | 26.7 | 0 | 26.08 | 0
2025-02-07 | -9.6 | 27.6 | 0 | 2024-02-07 | -3.7 | 21.7 | 0 | 2023-02-07 | -3.6 | 21.6 | 0 | 2022-02-07 | -6.3 | 24.3 | 0 | 2021-02-07 | -10 | 28 | 0 | 2020-02-07 | -13.8 | 31.8 | 0 | 2019-02-07 | -3.6 | 21.6 | 0 | 2018-02-07 | -12.3 | 30.3 | 0 | 2017-02-07 | -7.5 | 25.5 | 0 | 2016-02-07 | -9 | 27 | 0 | 25.94 | 0
2025-02-07 | -11.3 | 29.3 | 0 | 2024-02-07 | -3.5 | 21.5 | 0 | 2023-02-07 | -2.5 | 20.5 | 0 | 2022-02-07 | -6.5 | 24.5 | 0 | 2021-02-07 | -11.2 | 29.2 | 0 | 2020-02-07 | -14.1 | 32.1 | 0 | 2019-02-07 | -3.4 | 21.4 | 0 | 2018-02-07 | -13.5 | 31.5 | 0 | 2017-02-07 | -6.1 | 24.1 | 0 | 2016-02-07 | -9.1 | 27.1 | 0 | 26.12 | 0
2025-02-08 | -11.1 | 29.1 | 0 | 2024-02-08 | -3.5 | 21.5 | 0 | 2023-02-08 | -2.2 | 20.2 | 0 | 2022-02-08 | -6.8 | 24.8 | 0 | 2021-02-08 | -12.8 | 30.8 | 0 | 2020-02-08 | -14.5 | 32.5 | 0 | 2019-02-08 | -2.9 | 20.9 | 0 | 2018-02-08 | -13.2 | 31.2 | 0 | 2017-02-08 | -5.5 | 23.5 | 0 | 2016-02-08 | -9 | 27 | 0 | 26.15 | 0
2025-02-08 | -10.4 | 28.4 | 0 | 2024-02-08 | -4.7 | 22.7 | 0 | 2023-02-08 | -1.2 | 19.2 | 0 | 2022-02-08 | -6.8 | 24.8 | 0 | 2021-02-08 | -13.7 | 31.7 | 0 | 2020-02-08 | -15.1 | 33.1 | 0 | 2019-02-08 | -2.1 | 20.1 | 0 | 2018-02-08 | -14.3 | 32.3 | 0 | 2017-02-08 | -4.8 | 22.8 | 0 | 2016-02-08 | -8.9 | 26.9 | 0 | 26.2 | 0
2025-02-08 | -9.8 | 27.8 | 0 | 2024-02-08 | -5.3 | 23.3 | 0 | 2023-02-08 | 0.5 | 17.5 | 0 | 2022-02-08 | -6.8 | 24.8 | 0 | 2021-02-08 | -15.2 | 33.2 | 0 | 2020-02-08 | -15.9 | 33.9 | 0 | 2019-02-08 | -1.2 | 19.2 | 0 | 2018-02-08 | -16.1 | 34.1 | 0 | 2017-02-08 | -3.6 | 21.6 | 0 | 2016-02-08 | -8.5 | 26.5 | 0 | 26.19 | 0
2025-02-08 | -8.8 | 26.8 | 0 | 2024-02-08 | -4.7 | 22.7 | 0 | 2023-02-08 | 1.3 | 16.7 | 0 | 2022-02-08 | -6.8 | 24.8 | 0 | 2021-02-08 | -15.3 | 33.3 | 0 | 2020-02-08 | -16.7 | 34.7 | 0 | 2019-02-08 | 0 | 18 | 0 | 2018-02-08 | -17.1 | 35.1 | 0 | 2017-02-08 | -3.1 | 21.1 | 0 | 2016-02-08 | -8.1 | 26.1 | 0 | 25.93 | 0
2025-02-08 | -8.8 | 26.8 | 0 | 2024-02-08 | -5.5 | 23.5 | 0 | 2023-02-08 | 0.9 | 17.1 | 0 | 2022-02-08 | -6.8 | 24.8 | 0 | 2021-02-08 | -15.8 | 33.8 | 0 | 2020-02-08 | -18.5 | 36.5 | 0 | 2019-02-08 | 1 | 17 | 0 | 2018-02-08 | -16 | 34 | 0 | 2017-02-08 | -0.1 | 18.1 | 0 | 2016-02-08 | -8.1 | 26.1 | 0 | 25.77 | 0
2025-02-08 | -9.8 | 27.8 | 0 | 2024-02-08 | -6 | 24 | 0 | 2023-02-08 | 0.8 | 17.2 | 0 | 2022-02-08 | -7 | 25 | 0 | 2021-02-08 | -16.5 | 34.5 | 0 | 2020-02-08 | -18.7 | 36.7 | 0 | 2019-02-08 | 4 | 14 | 0 | 2018-02-08 | -16.8 | 34.8 | 0 | 2017-02-08 | 1.6 | 16.4 | 0 | 2016-02-08 | -8.2 | 26.2 | 0 | 25.66 | 0
2025-02-08 | -10.2 | 28.2 | 0 | 2024-02-08 | -5.6 | 23.6 | 0 | 2023-02-08 | 1.6 | 16.4 | 0 | 2022-02-08 | -7 | 25 | 0 | 2021-02-08 | -17.1 | 35.1 | 0 | 2020-02-08 | -19.7 | 37.7 | 0 | 2019-02-08 | 6.8 | 11.2 | 0 | 2018-02-08 | -18.9 | 36.9 | 0 | 2017-02-08 | 2.4 | 15.6 | 0 | 2016-02-08 | -8.1 | 26.1 | 0 | 25.58 | 0
2025-02-08 | -11.2 | 29.2 | 0 | 2024-02-08 | -5.3 | 23.3 | 0 | 2023-02-08 | 1.3 | 16.7 | 0 | 2022-02-08 | -7 | 25 | 0 | 2021-02-08 | -18 | 36 | 0 | 2020-02-08 | -20.1 | 38.1 | 0 | 2019-02-08 | 3.7 | 14.3 | 0 | 2018-02-08 | -19.1 | 37.1 | 0 | 2017-02-08 | 2.8 | 15.2 | 0 | 2016-02-08 | -8.3 | 26.3 | 0 | 26.12 | 0
2025-02-08 | -12.7 | 30.7 | 0 | 2024-02-08 | -6.1 | 24.1 | 0 | 2023-02-08 | 0.9 | 17.1 | 0 | 2022-02-08 | -6.5 | 24.5 | 0 | 2021-02-08 | -18.7 | 36.7 | 0 | 2020-02-08 | -20.4 | 38.4 | 0 | 2019-02-08 | 2.1 | 15.9 | 0 | 2018-02-08 | -20.7 | 38.7 | 0 | 2017-02-08 | -1.8 | 19.8 | 0 | 2016-02-08 | -8.1 | 26.1 | 0 | 27.2 | 0
2025-02-08 | -11.6 | 29.6 | 0 | 2024-02-08 | -3.4 | 21.4 | 0 | 2023-02-08 | 1.4 | 16.6 | 0 | 2022-02-08 | -5.9 | 23.9 | 0 | 2021-02-08 | -16.4 | 34.4 | 0 | 2020-02-08 | -20 | 38 | 0 | 2019-02-08 | 2.2 | 15.8 | 0 | 2018-02-08 | -17.4 | 35.4 | 0 | 2017-02-08 | -2.5 | 20.5 | 0 | 2016-02-08 | -7.4 | 25.4 | 0 | 26.1 | 0
2025-02-08 | -8.9 | 26.9 | 0 | 2024-02-08 | -1.3 | 19.3 | 0 | 2023-02-08 | 2.2 | 15.8 | 0 | 2022-02-08 | -5.6 | 23.6 | 0 | 2021-02-08 | -13.1 | 31.1 | 0 | 2020-02-08 | -19.5 | 37.5 | 0 | 2019-02-08 | 1.6 | 16.4 | 0 | 2018-02-08 | -14.7 | 32.7 | 0 | 2017-02-08 | -3.9 | 21.9 | 0 | 2016-02-08 | -6.8 | 24.8 | 0 | 25 | 0
2025-02-08 | -6.6 | 24.6 | 0 | 2024-02-08 | 0.7 | 17.3 | 0 | 2023-02-08 | 2.7 | 15.3 | 0 | 2022-02-08 | -4.6 | 22.6 | 0 | 2021-02-08 | -10.9 | 28.9 | 0 | 2020-02-08 | -18.6 | 36.6 | 0 | 2019-02-08 | 1.7 | 16.3 | 0 | 2018-02-08 | -12 | 30 | 0 | 2017-02-08 | -4.2 | 22.2 | 0 | 2016-02-08 | -6.8 | 24.8 | 0 | 23.86 | 0
2025-02-08 | -6.6 | 24.6 | 0 | 2024-02-08 | 1.9 | 16.1 | 0 | 2023-02-08 | 3.2 | 14.8 | 0 | 2022-02-08 | -4.2 | 22.2 | 0 | 2021-02-08 | -9.2 | 27.2 | 0 | 2020-02-08 | -17.6 | 35.6 | 0 | 2019-02-08 | 0 | 18 | 0 | 2018-02-08 | -10.2 | 28.2 | 0 | 2017-02-08 | -3.7 | 21.7 | 0 | 2016-02-08 | -6.7 | 24.7 | 0 | 23.31 | 0
2025-02-08 | -5.7 | 23.7 | 0 | 2024-02-08 | 3.3 | 14.7 | 0 | 2023-02-08 | 4.1 | 13.9 | 0 | 2022-02-08 | -3.7 | 21.7 | 0 | 2021-02-08 | -8.7 | 26.7 | 0 | 2020-02-08 | -17.2 | 35.2 | 0 | 2019-02-08 | -1 | 19 | 0 | 2018-02-08 | -7 | 25 | 0 | 2017-02-08 | -4 | 22 | 0 | 2016-02-08 | -6.3 | 24.3 | 0 | 22.62 | 0
2025-02-08 | -5 | 23 | 0 | 2024-02-08 | 3.4 | 14.6 | 0 | 2023-02-08 | 4.5 | 13.5 | 0 | 2022-02-08 | -2.5 | 20.5 | 0 | 2021-02-08 | -7.9 | 25.9 | 0 | 2020-02-08 | -16.6 | 34.6 | 0 | 2019-02-08 | -1.7 | 19.7 | 0 | 2018-02-08 | -6.4 | 24.4 | 0 | 2017-02-08 | -3.6 | 21.6 | 0 | 2016-02-08 | -6.2 | 24.2 | 0 | 22.2 | 0
2025-02-08 | -4.5 | 22.5 | 0 | 2024-02-08 | 3.5 | 14.5 | 0 | 2023-02-08 | 5.1 | 12.9 | 0 | 2022-02-08 | -1.8 | 19.8 | 0 | 2021-02-08 | -6.7 | 24.7 | 0 | 2020-02-08 | -15.7 | 33.7 | 0 | 2019-02-08 | -2.1 | 20.1 | 0 | 2018-02-08 | -7.2 | 25.2 | 0 | 2017-02-08 | -3.2 | 21.2 | 0 | 2016-02-08 | -6.1 | 24.1 | 0 | 21.87 | 0
2025-02-08 | -5.6 | 23.6 | 0 | 2024-02-08 | 4 | 14 | 0 | 2023-02-08 | 5.3 | 12.7 | 0 | 2022-02-08 | -1.7 | 19.7 | 0 | 2021-02-08 | -8.2 | 26.2 | 0 | 2020-02-08 | -15.3 | 33.3 | 0 | 2019-02-08 | -3.4 | 21.4 | 0 | 2018-02-08 | -7.5 | 25.5 | 0 | 2017-02-08 | -3.8 | 21.8 | 0 | 2016-02-08 | -6.4 | 24.4 | 0 | 22.26 | 0
2025-02-08 | -6 | 24 | 0 | 2024-02-08 | 2.8 | 15.2 | 0 | 2023-02-08 | 4.6 | 13.4 | 0 | 2022-02-08 | -2.4 | 20.4 | 0 | 2021-02-08 | -8.2 | 26.2 | 0 | 2020-02-08 | -16.4 | 34.4 | 0 | 2019-02-08 | -4.8 | 22.8 | 0 | 2018-02-08 | -8 | 26 | 0 | 2017-02-08 | -4.5 | 22.5 | 0 | 2016-02-08 | -7.1 | 25.1 | 0 | 23 | 0
2025-02-08 | -6.7 | 24.7 | 0 | 2024-02-08 | 2.5 | 15.5 | 0 | 2023-02-08 | 3.1 | 14.9 | 0 | 2022-02-08 | -2.4 | 20.4 | 0 | 2021-02-08 | -9.4 | 27.4 | 0 | 2020-02-08 | -17.2 | 35.2 | 0 | 2019-02-08 | -5.7 | 23.7 | 0 | 2018-02-08 | -7.7 | 25.7 | 0 | 2017-02-08 | -5.6 | 23.6 | 0 | 2016-02-08 | -7.5 | 25.5 | 0 | 23.66 | 0
2025-02-08 | -7.1 | 25.1 | 0 | 2024-02-08 | 1.8 | 16.2 | 0 | 2023-02-08 | 2.4 | 15.6 | 0 | 2022-02-08 | -2.9 | 20.9 | 0 | 2021-02-08 | -11.9 | 29.9 | 0 | 2020-02-08 | -18.1 | 36.1 | 0 | 2019-02-08 | -6.7 | 24.7 | 0 | 2018-02-08 | -8.2 | 26.2 | 0 | 2017-02-08 | -6.6 | 24.6 | 0 | 2016-02-08 | -7.5 | 25.5 | 0 | 24.48 | 0
2025-02-08 | -7.1 | 25.1 | 0 | 2024-02-08 | 1.2 | 16.8 | 0 | 2023-02-08 | 1.2 | 16.8 | 0 | 2022-02-08 | -3.1 | 21.1 | 0 | 2021-02-08 | -12.8 | 30.8 | 0 | 2020-02-08 | -18.2 | 36.2 | 0 | 2019-02-08 | -7.4 | 25.4 | 0 | 2018-02-08 | -9.6 | 27.6 | 0 | 2017-02-08 | -8.2 | 26.2 | 0 | 2016-02-08 | -7.6 | 25.6 | 0 | 25.16 | 0
2025-02-08 | -7.2 | 25.2 | 0 | 2024-02-08 | 0.9 | 17.1 | 0 | 2023-02-08 | 0.5 | 17.5 | 0 | 2022-02-08 | -3.8 | 21.8 | 0 | 2021-02-08 | -12 | 30 | 0 | 2020-02-08 | -19.2 | 37.2 | 0 | 2019-02-08 | -7.9 | 25.9 | 0 | 2018-02-08 | -10.7 | 28.7 | 0 | 2017-02-08 | -9 | 27 | 0 | 2016-02-08 | -7.5 | 25.5 | 0 | 25.59 | 0
2025-02-08 | -7.5 | 25.5 | 0 | 2024-02-08 | 0.8 | 17.2 | 0 | 2023-02-08 | 0 | 18 | 0 | 2022-02-08 | -5.2 | 23.2 | 0 | 2021-02-08 | -12.4 | 30.4 | 0 | 2020-02-08 | -20.3 | 38.3 | 0 | 2019-02-08 | -8.8 | 26.8 | 0 | 2018-02-08 | -11.3 | 29.3 | 0 | 2017-02-08 | -10.3 | 28.3 | 0 | 2016-02-08 | -7.5 | 25.5 | 0 | 26.25 | 0
2025-02-08 | -8.1 | 26.1 | 0 | 2024-02-08 | 0.7 | 17.3 | 0 | 2023-02-08 | -1 | 19 | 0 | 2022-02-08 | -5.9 | 23.9 | 0 | 2021-02-08 | -12.3 | 30.3 | 0 | 2020-02-08 | -20.7 | 38.7 | 0 | 2019-02-08 | -9.4 | 27.4 | 0 | 2018-02-08 | -11.7 | 29.7 | 0 | 2017-02-08 | -11.5 | 29.5 | 0 | 2016-02-08 | -7.4 | 25.4 | 0 | 26.73 | 0
2025-02-09 | -8.1 | 26.1 | 0 | 2024-02-09 | 0.4 | 17.6 | 0 | 2023-02-09 | -2 | 20 | 0 | 2022-02-09 | -6.5 | 24.5 | 0 | 2021-02-09 | -11.7 | 29.7 | 0 | 2020-02-09 | -20.6 | 38.6 | 0 | 2019-02-09 | -10.1 | 28.1 | 0 | 2018-02-09 | -12.6 | 30.6 | 0 | 2017-02-09 | -12.3 | 30.3 | 0 | 2016-02-09 | -8 | 26 | 0 | 27.15 | 0
2025-02-09 | -8.2 | 26.2 | 0 | 2024-02-09 | 0 | 18 | 0 | 2023-02-09 | -4.4 | 22.4 | 0 | 2022-02-09 | -8.1 | 26.1 | 0 | 2021-02-09 | -11.1 | 29.1 | 0 | 2020-02-09 | -22.2 | 40.2 | 0 | 2019-02-09 | -10.5 | 28.5 | 0 | 2018-02-09 | -13.2 | 31.2 | 0 | 2017-02-09 | -13.2 | 31.2 | 0 | 2016-02-09 | -8.3 | 26.3 | 0 | 27.92 | 0
2025-02-09 | -8.4 | 26.4 | 0 | 2024-02-09 | 0.1 | 17.9 | 0 | 2023-02-09 | -4.2 | 22.2 | 0 | 2022-02-09 | -8.2 | 26.2 | 0 | 2021-02-09 | -10.9 | 28.9 | 0 | 2020-02-09 | -21.9 | 39.9 | 0 | 2019-02-09 | -11.1 | 29.1 | 0 | 2018-02-09 | -12.2 | 30.2 | 0 | 2017-02-09 | -14.2 | 32.2 | 0 | 2016-02-09 | -8.4 | 26.4 | 0 | 27.94 | 0
2025-02-09 | -8.4 | 26.4 | 0 | 2024-02-09 | -0.5 | 18.5 | 0 | 2023-02-09 | -5.2 | 23.2 | 0 | 2022-02-09 | -10.1 | 28.1 | 0 | 2021-02-09 | -10.7 | 28.7 | 0 | 2020-02-09 | -22.8 | 40.8 | 0 | 2019-02-09 | -11.1 | 29.1 | 0 | 2018-02-09 | -13.9 | 31.9 | 0 | 2017-02-09 | -14.8 | 32.8 | 0 | 2016-02-09 | -8.5 | 26.5 | 0 | 28.6 | 0
2025-02-09 | -8.4 | 26.4 | 0 | 2024-02-09 | -0.5 | 18.5 | 0 | 2023-02-09 | -7.1 | 25.1 | 0 | 2022-02-09 | -10.7 | 28.7 | 0 | 2021-02-09 | -11.9 | 29.9 | 0 | 2020-02-09 | -22.7 | 40.7 | 0 | 2019-02-09 | -11.4 | 29.4 | 0 | 2018-02-09 | -14.6 | 32.6 | 0 | 2017-02-09 | -15.2 | 33.2 | 0 | 2016-02-09 | -8.7 | 26.7 | 0 | 29.12 | 0
2025-02-09 | -8.6 | 26.6 | 0 | 2024-02-09 | -0.5 | 18.5 | 0 | 2023-02-09 | -7 | 25 | 0 | 2022-02-09 | -9.6 | 27.6 | 0 | 2021-02-09 | -12.1 | 30.1 | 0 | 2020-02-09 | -23.7 | 41.7 | 0 | 2019-02-09 | -11.9 | 29.9 | 0 | 2018-02-09 | -14.9 | 32.9 | 0 | 2017-02-09 | -15.4 | 33.4 | 0 | 2016-02-09 | -8.9 | 26.9 | 0 | 29.26 | 0
2025-02-09 | -10.8 | 28.8 | 0 | 2024-02-09 | -1.2 | 19.2 | 0 | 2023-02-09 | -7.5 | 25.5 | 0 | 2022-02-09 | -13.3 | 31.3 | 0 | 2021-02-09 | -12.2 | 30.2 | 0 | 2020-02-09 | -24.6 | 42.6 | 0 | 2019-02-09 | -12.4 | 30.4 | 0 | 2018-02-09 | -15.9 | 33.9 | 0 | 2017-02-09 | -15.7 | 33.7 | 0 | 2016-02-09 | -8.9 | 26.9 | 0 | 30.25 | 0
2025-02-09 | -11.5 | 29.5 | 0 | 2024-02-09 | -0.6 | 18.6 | 0 | 2023-02-09 | -6.6 | 24.6 | 0 | 2022-02-09 | -10.3 | 28.3 | 0 | 2021-02-09 | -12.1 | 30.1 | 0 | 2020-02-09 | -26.1 | 44.1 | 0 | 2019-02-09 | -12.8 | 30.8 | 0 | 2018-02-09 | -15.6 | 33.6 | 0 | 2017-02-09 | -16.2 | 34.2 | 0 | 2016-02-09 | -9.1 | 27.1 | 0 | 30.09 | 0
2025-02-09 | -9.4 | 27.4 | 0 | 2024-02-09 | -0.3 | 18.3 | 0 | 2023-02-09 | -5.8 | 23.8 | 0 | 2022-02-09 | -11 | 29 | 0 | 2021-02-09 | -12 | 30 | 0 | 2020-02-09 | -23.9 | 41.9 | 0 | 2019-02-09 | -13.2 | 31.2 | 0 | 2018-02-09 | -14.7 | 32.7 | 0 | 2017-02-09 | -16.5 | 34.5 | 0 | 2016-02-09 | -8.9 | 26.9 | 0 | 29.57 | 0
2025-02-09 | -9.2 | 27.2 | 0 | 2024-02-09 | 1 | 17 | 0 | 2023-02-09 | -4.9 | 22.9 | 0 | 2022-02-09 | -9 | 27 | 0 | 2021-02-09 | -11.6 | 29.6 | 0 | 2020-02-09 | -22.2 | 40.2 | 0 | 2019-02-09 | -13 | 31 | 0 | 2018-02-09 | -12.9 | 30.9 | 0 | 2017-02-09 | -16.3 | 34.3 | 0 | 2016-02-09 | -8.5 | 26.5 | 0 | 28.66 | 0
2025-02-09 | -7.7 | 25.7 | 0 | 2024-02-09 | 4.2 | 13.8 | 0 | 2023-02-09 | -3.9 | 21.9 | 0 | 2022-02-09 | -5.4 | 23.4 | 0 | 2021-02-09 | -10.7 | 28.7 | 0 | 2020-02-09 | -19.8 | 37.8 | 0 | 2019-02-09 | -12.5 | 30.5 | 0 | 2018-02-09 | -12 | 30 | 0 | 2017-02-09 | -15.5 | 33.5 | 0 | 2016-02-09 | -7.8 | 25.8 | 0 | 27.11 | 0
2025-02-09 | -6.2 | 24.2 | 0 | 2024-02-09 | 5.8 | 12.2 | 0 | 2023-02-09 | -2.9 | 20.9 | 0 | 2022-02-09 | -3.6 | 21.6 | 0 | 2021-02-09 | -9.8 | 27.8 | 0 | 2020-02-09 | -17.2 | 35.2 | 0 | 2019-02-09 | -12 | 30 | 0 | 2018-02-09 | -10.3 | 28.3 | 0 | 2017-02-09 | -14.9 | 32.9 | 0 | 2016-02-09 | -6.6 | 24.6 | 0 | 25.77 | 0
2025-02-09 | -5.4 | 23.4 | 0 | 2024-02-09 | 7.4 | 10.6 | 0 | 2023-02-09 | -2.2 | 20.2 | 0 | 2022-02-09 | -2.8 | 20.8 | 0 | 2021-02-09 | -7.3 | 25.3 | 0 | 2020-02-09 | -14.8 | 32.8 | 0 | 2019-02-09 | -11.2 | 29.2 | 0 | 2018-02-09 | -8.6 | 26.6 | 0 | 2017-02-09 | -13.5 | 31.5 | 0 | 2016-02-09 | -6.2 | 24.2 | 0 | 24.46 | 0
2025-02-09 | -5 | 23 | 0 | 2024-02-09 | 7.7 | 10.3 | 0 | 2023-02-09 | -1.3 | 19.3 | 0 | 2022-02-09 | -1.9 | 19.9 | 0 | 2021-02-09 | -7.2 | 25.2 | 0 | 2020-02-09 | -12.8 | 30.8 | 0 | 2019-02-09 | -10.1 | 28.1 | 0 | 2018-02-09 | -7.9 | 25.9 | 0 | 2017-02-09 | -13.1 | 31.1 | 0 | 2016-02-09 | -6.5 | 24.5 | 0 | 23.81 | 0
2025-02-09 | -4.9 | 22.9 | 0 | 2024-02-09 | 8.6 | 9.4 | 0 | 2023-02-09 | -0.5 | 18.5 | 0 | 2022-02-09 | -0.9 | 18.9 | 0 | 2021-02-09 | -6.6 | 24.6 | 0 | 2020-02-09 | -11.2 | 29.2 | 0 | 2019-02-09 | -9.4 | 27.4 | 0 | 2018-02-09 | -7.3 | 25.3 | 0 | 2017-02-09 | -12.4 | 30.4 | 0 | 2016-02-09 | -6 | 24 | 0 | 23.06 | 0
2025-02-09 | -4.5 | 22.5 | 0 | 2024-02-09 | 9.4 | 8.6 | 0 | 2023-02-09 | -0.3 | 18.3 | 0 | 2022-02-09 | -0.6 | 18.6 | 0 | 2021-02-09 | -6.6 | 24.6 | 0 | 2020-02-09 | -10.6 | 28.6 | 0 | 2019-02-09 | -8.8 | 26.8 | 0 | 2018-02-09 | -6.8 | 24.8 | 0 | 2017-02-09 | -11.7 | 29.7 | 0 | 2016-02-09 | -5.8 | 23.8 | 0 | 22.63 | 0
2025-02-09 | -4.5 | 22.5 | 0 | 2024-02-09 | 8.9 | 9.1 | 0 | 2023-02-09 | 0 | 18 | 0 | 2022-02-09 | -0.8 | 18.8 | 0 | 2021-02-09 | -7 | 25 | 0 | 2020-02-09 | -10.7 | 28.7 | 0 | 2019-02-09 | -8.5 | 26.5 | 0 | 2018-02-09 | -6.5 | 24.5 | 0 | 2017-02-09 | -11.5 | 29.5 | 0 | 2016-02-09 | -6.6 | 24.6 | 0 | 22.72 | 0
2025-02-09 | -4.7 | 22.7 | 0 | 2024-02-09 | 8.3 | 9.7 | 0 | 2023-02-09 | 0.1 | 17.9 | 0 | 2022-02-09 | -0.6 | 18.6 | 0 | 2021-02-09 | -7 | 25 | 0 | 2020-02-09 | -10.5 | 28.5 | 0 | 2019-02-09 | -9.2 | 27.2 | 0 | 2018-02-09 | -6.9 | 24.9 | 0 | 2017-02-09 | -12.5 | 30.5 | 0 | 2016-02-09 | -6.6 | 24.6 | 0 | 22.96 | 0
2025-02-09 | -4.7 | 22.7 | 0 | 2024-02-09 | 7.9 | 10.1 | 0 | 2023-02-09 | 0.2 | 17.8 | 0 | 2022-02-09 | -0.7 | 18.7 | 0 | 2021-02-09 | -9.3 | 27.3 | 0 | 2020-02-09 | -9.8 | 27.8 | 0 | 2019-02-09 | -10.4 | 28.4 | 0 | 2018-02-09 | -7.4 | 25.4 | 0 | 2017-02-09 | -13.8 | 31.8 | 0 | 2016-02-09 | -6.8 | 24.8 | 0 | 23.48 | 0
2025-02-09 | -4.8 | 22.8 | 0 | 2024-02-09 | 7.5 | 10.5 | 0 | 2023-02-09 | 0.1 | 17.9 | 0 | 2022-02-09 | -1 | 19 | 0 | 2021-02-09 | -9.1 | 27.1 | 0 | 2020-02-09 | -10.7 | 28.7 | 0 | 2019-02-09 | -10.5 | 28.5 | 0 | 2018-02-09 | -7.4 | 25.4 | 0 | 2017-02-09 | -14.2 | 32.2 | 0 | 2016-02-09 | -6.9 | 24.9 | 0 | 23.7 | 0
2025-02-09 | -4.6 | 22.6 | 0 | 2024-02-09 | 7.2 | 10.8 | 0 | 2023-02-09 | 0.2 | 17.8 | 0 | 2022-02-09 | -1.1 | 19.1 | 0 | 2021-02-09 | -9.4 | 27.4 | 0 | 2020-02-09 | -10.8 | 28.8 | 0 | 2019-02-09 | -12 | 30 | 0 | 2018-02-09 | -7.4 | 25.4 | 0 | 2017-02-09 | -14.4 | 32.4 | 0 | 2016-02-09 | -7.3 | 25.3 | 0 | 23.96 | 0
2025-02-09 | -5.5 | 23.5 | 0 | 2024-02-09 | 6.7 | 11.3 | 0 | 2023-02-09 | 0.1 | 17.9 | 0 | 2022-02-09 | -2.6 | 20.6 | 0 | 2021-02-09 | -8.8 | 26.8 | 0 | 2020-02-09 | -10.7 | 28.7 | 0 | 2019-02-09 | -12.4 | 30.4 | 0 | 2018-02-09 | -7.7 | 25.7 | 0 | 2017-02-09 | -15.3 | 33.3 | 0 | 2016-02-09 | -7.5 | 25.5 | 0 | 24.37 | 0
2025-02-09 | -5.6 | 23.6 | 0 | 2024-02-09 | 6.3 | 11.7 | 0 | 2023-02-09 | -0.2 | 18.2 | 0 | 2022-02-09 | -1.9 | 19.9 | 0 | 2021-02-09 | -8.7 | 26.7 | 0 | 2020-02-09 | -10.9 | 28.9 | 0 | 2019-02-09 | -13.4 | 31.4 | 0 | 2018-02-09 | -7.9 | 25.9 | 0 | 2017-02-09 | -15.8 | 33.8 | 0 | 2016-02-09 | -7.7 | 25.7 | 0 | 24.58 | 0
2025-02-09 | -6.4 | 24.4 | 0 | 2024-02-09 | 6.3 | 11.7 | 0 | 2023-02-09 | 0 | 18 | 0 | 2022-02-09 | -1.6 | 19.6 | 0 | 2021-02-09 | -9.6 | 27.6 | 0 | 2020-02-09 | -10.8 | 28.8 | 0 | 2019-02-09 | -15.3 | 33.3 | 0 | 2018-02-09 | -8.7 | 26.7 | 0 | 2017-02-09 | -15.6 | 33.6 | 0 | 2016-02-09 | -7.8 | 25.8 | 0 | 24.95 | 0
2025-02-10 | -6.2 | 24.2 | 0 | 2024-02-10 | 5.6 | 12.4 | 0 | 2023-02-10 | 0.1 | 17.9 | 0 | 2022-02-10 | -1.6 | 19.6 | 0 | 2021-02-10 | -11.1 | 29.1 | 0 | 2020-02-10 | -10.3 | 28.3 | 0 | 2019-02-10 | -15.3 | 33.3 | 0 | 2018-02-10 | -9 | 27 | 0 | 2017-02-10 | -16.1 | 34.1 | 0 | 2016-02-10 | -8 | 26 | 0 | 25.19 | 0
2025-02-10 | -7 | 25 | 0 | 2024-02-10 | 5.5 | 12.5 | 0 | 2023-02-10 | 0.2 | 17.8 | 0 | 2022-02-10 | -2.1 | 20.1 | 0 | 2021-02-10 | -12.4 | 30.4 | 0 | 2020-02-10 | -9.7 | 27.7 | 0 | 2019-02-10 | -13.8 | 31.8 | 0 | 2018-02-10 | -9 | 27 | 0 | 2017-02-10 | -15.8 | 33.8 | 0 | 2016-02-10 | -8 | 26 | 0 | 25.21 | 0
2025-02-10 | -7.6 | 25.6 | 0 | 2024-02-10 | 5.2 | 12.8 | 0 | 2023-02-10 | 1.2 | 16.8 | 0 | 2022-02-10 | -2.2 | 20.2 | 0 | 2021-02-10 | -10.2 | 28.2 | 0 | 2020-02-10 | -8.8 | 26.8 | 0 | 2019-02-10 | -13.9 | 31.9 | 0 | 2018-02-10 | -9 | 27 | 0 | 2017-02-10 | -15.8 | 33.8 | 0 | 2016-02-10 | -8 | 26 | 0 | 24.91 | 0
2025-02-10 | -7.9 | 25.9 | 0 | 2024-02-10 | 5.2 | 12.8 | 0 | 2023-02-10 | 3.3 | 14.7 | 0 | 2022-02-10 | -1.9 | 19.9 | 0 | 2021-02-10 | -12.4 | 30.4 | 0 | 2020-02-10 | -8 | 26 | 0 | 2019-02-10 | -14.8 | 32.8 | 0 | 2018-02-10 | -9 | 27 | 0 | 2017-02-10 | -16 | 34 | 0 | 2016-02-10 | -8 | 26 | 0 | 24.95 | 0
2025-02-10 | -10.5 | 28.5 | 0 | 2024-02-10 | 5.5 | 12.5 | 0 | 2023-02-10 | 4.4 | 13.6 | 0 | 2022-02-10 | -1.8 | 19.8 | 0 | 2021-02-10 | -12.2 | 30.2 | 0 | 2020-02-10 | -7 | 25 | 0 | 2019-02-10 | -14.7 | 32.7 | 0 | 2018-02-10 | -9.1 | 27.1 | 0 | 2017-02-10 | -15.7 | 33.7 | 0 | 2016-02-10 | -8 | 26 | 0 | 24.91 | 0
2025-02-10 | -11.6 | 29.6 | 0 | 2024-02-10 | 4.7 | 13.3 | 0 | 2023-02-10 | 4 | 14 | 0 | 2022-02-10 | 1.7 | 16.3 | 0 | 2021-02-10 | -14 | 32 | 0 | 2020-02-10 | -7 | 25 | 0 | 2019-02-10 | -15.2 | 33.2 | 0 | 2018-02-10 | -9 | 27 | 0 | 2017-02-10 | -16.1 | 34.1 | 0 | 2016-02-10 | -7.8 | 25.8 | 0 | 25.03 | 0
2025-02-10 | -11.8 | 29.8 | 0 | 2024-02-10 | 4.7 | 13.3 | 0 | 2023-02-10 | 3.7 | 14.3 | 0 | 2022-02-10 | 2.4 | 15.6 | 0 | 2021-02-10 | -14.7 | 32.7 | 0 | 2020-02-10 | -7.1 | 25.1 | 0 | 2019-02-10 | -14.3 | 32.3 | 0 | 2018-02-10 | -8.6 | 26.6 | 0 | 2017-02-10 | -16.6 | 34.6 | 0 | 2016-02-10 | -7.8 | 25.8 | 0 | 25.01 | 0
2025-02-10 | -13.4 | 31.4 | 0 | 2024-02-10 | 4.2 | 13.8 | 0 | 2023-02-10 | 3.2 | 14.8 | 0 | 2022-02-10 | 2.1 | 15.9 | 0 | 2021-02-10 | -14.6 | 32.6 | 0 | 2020-02-10 | -7 | 25 | 0 | 2019-02-10 | -15 | 33 | 0 | 2018-02-10 | -8.5 | 26.5 | 0 | 2017-02-10 | -17.4 | 35.4 | 0 | 2016-02-10 | -7.7 | 25.7 | 0 | 25.41 | 0
2025-02-10 | -12.9 | 30.9 | 0 | 2024-02-10 | 3.7 | 14.3 | 0 | 2023-02-10 | 3 | 15 | 0 | 2022-02-10 | 2 | 16 | 0 | 2021-02-10 | -15.3 | 33.3 | 0 | 2020-02-10 | -6.8 | 24.8 | 0 | 2019-02-10 | -14.8 | 32.8 | 0 | 2018-02-10 | -8.2 | 26.2 | 0 | 2017-02-10 | -17.8 | 35.8 | 0 | 2016-02-10 | -7.5 | 25.5 | 0 | 25.46 | 0
2025-02-10 | -12.3 | 30.3 | 0 | 2024-02-10 | 4.2 | 13.8 | 0 | 2023-02-10 | 2.7 | 15.3 | 0 | 2022-02-10 | 1.7 | 16.3 | 0 | 2021-02-10 | -13.5 | 31.5 | 0 | 2020-02-10 | -6.6 | 24.6 | 0 | 2019-02-10 | -13.3 | 31.3 | 0 | 2018-02-10 | -7.8 | 25.8 | 0 | 2017-02-10 | -17.3 | 35.3 | 0 | 2016-02-10 | -7 | 25 | 0 | 24.92 | 0
2025-02-10 | -11.3 | 29.3 | 0 | 2024-02-10 | 4.4 | 13.6 | 0 | 2023-02-10 | 2 | 16 | 0 | 2022-02-10 | 3 | 15 | 0 | 2021-02-10 | -11.5 | 29.5 | 0 | 2020-02-10 | -6 | 24 | 0 | 2019-02-10 | -11.3 | 29.3 | 0 | 2018-02-10 | -7 | 25 | 0 | 2017-02-10 | -16.6 | 34.6 | 0 | 2016-02-10 | -6.5 | 24.5 | 0 | 24.08 | 0
2025-02-10 | -9.8 | 27.8 | 0 | 2024-02-10 | 5.8 | 12.2 | 0 | 2023-02-10 | 1.6 | 16.4 | 0 | 2022-02-10 | 3.1 | 14.9 | 0 | 2021-02-10 | -10.6 | 28.6 | 0 | 2020-02-10 | -4.7 | 22.7 | 0 | 2019-02-10 | -10.2 | 28.2 | 0 | 2018-02-10 | -6.3 | 24.3 | 0 | 2017-02-10 | -16 | 34 | 0 | 2016-02-10 | -5.9 | 23.9 | 0 | 23.3 | 0
2025-02-10 | -9.8 | 27.8 | 0 | 2024-02-10 | 5.3 | 12.7 | 0 | 2023-02-10 | 1.6 | 16.4 | 0 | 2022-02-10 | 3 | 15 | 0 | 2021-02-10 | -9.3 | 27.3 | 0 | 2020-02-10 | -3.7 | 21.7 | 0 | 2019-02-10 | -9.2 | 27.2 | 0 | 2018-02-10 | -5.5 | 23.5 | 0 | 2017-02-10 | -15.1 | 33.1 | 0 | 2016-02-10 | -4.9 | 22.9 | 0 | 22.76 | 0
2025-02-10 | -9.3 | 27.3 | 0 | 2024-02-10 | 5.8 | 12.2 | 0 | 2023-02-10 | 1.3 | 16.7 | 0 | 2022-02-10 | 3.1 | 14.9 | 0 | 2021-02-10 | -7.8 | 25.8 | 0 | 2020-02-10 | -2.3 | 20.3 | 0 | 2019-02-10 | -8.2 | 26.2 | 0 | 2018-02-10 | -5.3 | 23.3 | 0 | 2017-02-10 | -14.4 | 32.4 | 0 | 2016-02-10 | -4.6 | 22.6 | 0 | 22.17 | 0
2025-02-10 | -8.2 | 26.2 | 0 | 2024-02-10 | 5.2 | 12.8 | 0 | 2023-02-10 | 2.2 | 15.8 | 0 | 2022-02-10 | 2.6 | 15.4 | 0 | 2021-02-10 | -7.5 | 25.5 | 0 | 2020-02-10 | -1 | 19 | 0 | 2019-02-10 | -7.7 | 25.7 | 0 | 2018-02-10 | -5.4 | 23.4 | 0 | 2017-02-10 | -13.9 | 31.9 | 0 | 2016-02-10 | -4.6 | 22.6 | 0 | 21.83 | 0
2025-02-10 | -7.4 | 25.4 | 0 | 2024-02-10 | 4.8 | 13.2 | 0 | 2023-02-10 | 1.4 | 16.6 | 0 | 2022-02-10 | 2.7 | 15.3 | 0 | 2021-02-10 | -7.5 | 25.5 | 0 | 2020-02-10 | -0.6 | 18.6 | 0 | 2019-02-10 | -6.8 | 24.8 | 0 | 2018-02-10 | -5.6 | 23.6 | 0 | 2017-02-10 | -13.2 | 31.2 | 0 | 2016-02-10 | -4.4 | 22.4 | 0 | 21.66 | 0
2025-02-10 | -7.5 | 25.5 | 0 | 2024-02-10 | 5 | 13 | 0 | 2023-02-10 | 1.4 | 16.6 | 0 | 2022-02-10 | 2.4 | 15.6 | 0 | 2021-02-10 | -8.2 | 26.2 | 0 | 2020-02-10 | -1.3 | 19.3 | 0 | 2019-02-10 | -7.3 | 25.3 | 0 | 2018-02-10 | -5.4 | 23.4 | 0 | 2017-02-10 | -13.5 | 31.5 | 0 | 2016-02-10 | -5.1 | 23.1 | 0 | 21.95 | 0
2025-02-10 | -8.1 | 26.1 | 0 | 2024-02-10 | 3.7 | 14.3 | 0 | 2023-02-10 | 1.1 | 16.9 | 0 | 2022-02-10 | 2 | 16 | 0 | 2021-02-10 | -9.1 | 27.1 | 0 | 2020-02-10 | -2.3 | 20.3 | 0 | 2019-02-10 | -8.5 | 26.5 | 0 | 2018-02-10 | -5.8 | 23.8 | 0 | 2017-02-10 | -13.5 | 31.5 | 0 | 2016-02-10 | -6.4 | 24.4 | 0 | 22.69 | 0
2025-02-10 | -8.9 | 26.9 | 0 | 2024-02-10 | 3.9 | 14.1 | 0 | 2023-02-10 | 1 | 17 | 0 | 2022-02-10 | 1.9 | 16.1 | 0 | 2021-02-10 | -9.3 | 27.3 | 0 | 2020-02-10 | -3.4 | 21.4 | 0 | 2019-02-10 | -8.2 | 26.2 | 0 | 2018-02-10 | -5.9 | 23.9 | 0 | 2017-02-10 | -13.5 | 31.5 | 0 | 2016-02-10 | -7.4 | 25.4 | 0 | 22.98 | 0
2025-02-10 | -9.6 | 27.6 | 0 | 2024-02-10 | 3.3 | 14.7 | 0 | 2023-02-10 | 0 | 18 | 0 | 2022-02-10 | 1.5 | 16.5 | 0 | 2021-02-10 | -11.1 | 29.1 | 0 | 2020-02-10 | -3.7 | 21.7 | 0 | 2019-02-10 | -10.4 | 28.4 | 0 | 2018-02-10 | -5.9 | 23.9 | 0 | 2017-02-10 | -14 | 32 | 0 | 2016-02-10 | -8.2 | 26.2 | 0 | 23.81 | 0
2025-02-10 | -9.6 | 27.6 | 0 | 2024-02-10 | 3.5 | 14.5 | 0 | 2023-02-10 | -0.6 | 18.6 | 0 | 2022-02-10 | 1.5 | 16.5 | 0 | 2021-02-10 | -10.1 | 28.1 | 0 | 2020-02-10 | -6.1 | 24.1 | 0 | 2019-02-10 | -9.7 | 27.7 | 0 | 2018-02-10 | -6 | 24 | 0 | 2017-02-10 | -14.6 | 32.6 | 0 | 2016-02-10 | -8.4 | 26.4 | 0 | 24.01 | 0
2025-02-10 | -9.8 | 27.8 | 0 | 2024-02-10 | 3.2 | 14.8 | 0 | 2023-02-10 | -0.8 | 18.8 | 0 | 2022-02-10 | 1 | 17 | 0 | 2021-02-10 | -10.8 | 28.8 | 0 | 2020-02-10 | -8.7 | 26.7 | 0 | 2019-02-10 | -11.1 | 29.1 | 0 | 2018-02-10 | -5.8 | 23.8 | 0 | 2017-02-10 | -14.7 | 32.7 | 0 | 2016-02-10 | -8.9 | 26.9 | 0 | 24.64 | 0
2025-02-10 | -10.4 | 28.4 | 0 | 2024-02-10 | 2.9 | 15.1 | 0 | 2023-02-10 | -0.9 | 18.9 | 0 | 2022-02-10 | 0.5 | 17.5 | 0 | 2021-02-10 | -11 | 29 | 0 | 2020-02-10 | -9.4 | 27.4 | 0 | 2019-02-10 | -12.1 | 30.1 | 0 | 2018-02-10 | -5.9 | 23.9 | 0 | 2017-02-10 | -14.9 | 32.9 | 0 | 2016-02-10 | -10.4 | 28.4 | 0 | 25.16 | 0
2025-02-10 | -8.4 | 26.4 | 0 | 2024-02-10 | 2.6 | 15.4 | 0 | 2023-02-10 | -2.5 | 20.5 | 0 | 2022-02-10 | 0.5 | 17.5 | 0 | 2021-02-10 | -11.5 | 29.5 | 0 | 2020-02-10 | -9.1 | 27.1 | 0 | 2019-02-10 | -11.5 | 29.5 | 0 | 2018-02-10 | -6.1 | 24.1 | 0 | 2017-02-10 | -14.7 | 32.7 | 0 | 2016-02-10 | -11.4 | 29.4 | 0 | 25.21 | 0
2025-02-11 | -9.4 | 27.4 | 0 | 2024-02-11 | 2.4 | 15.6 | 0 | 2023-02-11 | -2.9 | 20.9 | 0 | 2022-02-11 | 0.2 | 17.8 | 0 | 2021-02-11 | -12 | 30 | 0 | 2020-02-11 | -11.2 | 29.2 | 0 | 2019-02-11 | -11.8 | 29.8 | 0 | 2018-02-11 | -6.1 | 24.1 | 0 | 2017-02-11 | -14.6 | 32.6 | 0 | 2016-02-11 | -12.2 | 30.2 | 0 | 25.76 | 0
2025-02-11 | -7.5 | 25.5 | 0 | 2024-02-11 | 2.2 | 15.8 | 0 | 2023-02-11 | -3.4 | 21.4 | 0 | 2022-02-11 | 0 | 18 | 0 | 2021-02-11 | -11.9 | 29.9 | 0 | 2020-02-11 | -7.8 | 25.8 | 0 | 2019-02-11 | -10.5 | 28.5 | 0 | 2018-02-11 | -6.8 | 24.8 | 0 | 2017-02-11 | -14.5 | 32.5 | 0 | 2016-02-11 | -12.8 | 30.8 | 0 | 25.3 | 0
2025-02-11 | -6.6 | 24.6 | 0 | 2024-02-11 | 2.2 | 15.8 | 0 | 2023-02-11 | -4.4 | 22.4 | 0 | 2022-02-11 | -0.5 | 18.5 | 0 | 2021-02-11 | -11.6 | 29.6 | 0 | 2020-02-11 | -6.7 | 24.7 | 0 | 2019-02-11 | -12.2 | 30.2 | 0 | 2018-02-11 | -7.6 | 25.6 | 0 | 2017-02-11 | -14.3 | 32.3 | 0 | 2016-02-11 | -13.6 | 31.6 | 0 | 25.53 | 0
2025-02-11 | -7.9 | 25.9 | 0 | 2024-02-11 | 1.8 | 16.2 | 0 | 2023-02-11 | -4.9 | 22.9 | 0 | 2022-02-11 | -0.4 | 18.4 | 0 | 2021-02-11 | -12.9 | 30.9 | 0 | 2020-02-11 | -5.9 | 23.9 | 0 | 2019-02-11 | -11.5 | 29.5 | 0 | 2018-02-11 | -7.8 | 25.8 | 0 | 2017-02-11 | -14.2 | 32.2 | 0 | 2016-02-11 | -14.2 | 32.2 | 0 | 25.79 | 0
2025-02-11 | -9.1 | 27.1 | 0 | 2024-02-11 | 1.5 | 16.5 | 0 | 2023-02-11 | -4.5 | 22.5 | 0 | 2022-02-11 | -0.7 | 18.7 | 0 | 2021-02-11 | -12.3 | 30.3 | 0 | 2020-02-11 | -6.1 | 24.1 | 0 | 2019-02-11 | -11.1 | 29.1 | 0 | 2018-02-11 | -8.8 | 26.8 | 0 | 2017-02-11 | -13.9 | 31.9 | 0 | 2016-02-11 | -15 | 33 | 0 | 26 | 0
2025-02-11 | -9.3 | 27.3 | 0 | 2024-02-11 | 1.6 | 16.4 | 0 | 2023-02-11 | -6.5 | 24.5 | 0 | 2022-02-11 | -0.9 | 18.9 | 0 | 2021-02-11 | -13.9 | 31.9 | 0 | 2020-02-11 | -5.8 | 23.8 | 0 | 2019-02-11 | -12.2 | 30.2 | 0 | 2018-02-11 | -9.1 | 27.1 | 0 | 2017-02-11 | -13.8 | 31.8 | 0 | 2016-02-11 | -15.4 | 33.4 | 0 | 26.53 | 0
2025-02-11 | -9.4 | 27.4 | 0 | 2024-02-11 | 1.2 | 16.8 | 0 | 2023-02-11 | -7.2 | 25.2 | 0 | 2022-02-11 | -1 | 19 | 0 | 2021-02-11 | -15.4 | 33.4 | 0 | 2020-02-11 | -5.9 | 23.9 | 0 | 2019-02-11 | -13.2 | 31.2 | 0 | 2018-02-11 | -10.1 | 28.1 | 0 | 2017-02-11 | -13.9 | 31.9 | 0 | 2016-02-11 | -16.2 | 34.2 | 0 | 27.11 | 0
2025-02-11 | -9.1 | 27.1 | 0 | 2024-02-11 | 0.7 | 17.3 | 0 | 2023-02-11 | -7.9 | 25.9 | 0 | 2022-02-11 | -0.9 | 18.9 | 0 | 2021-02-11 | -16.8 | 34.8 | 0 | 2020-02-11 | -5.8 | 23.8 | 0 | 2019-02-11 | -13.6 | 31.6 | 0 | 2018-02-11 | -9.4 | 27.4 | 0 | 2017-02-11 | -13.8 | 31.8 | 0 | 2016-02-11 | -17 | 35 | 0 | 27.36 | 0
2025-02-11 | -9.3 | 27.3 | 0 | 2024-02-11 | 0.8 | 17.2 | 0 | 2023-02-11 | -8.3 | 26.3 | 0 | 2022-02-11 | -0.8 | 18.8 | 0 | 2021-02-11 | -17.9 | 35.9 | 0 | 2020-02-11 | -5.5 | 23.5 | 0 | 2019-02-11 | -15 | 33 | 0 | 2018-02-11 | -8.7 | 26.7 | 0 | 2017-02-11 | -13.6 | 31.6 | 0 | 2016-02-11 | -17.4 | 35.4 | 0 | 27.57 | 0
2025-02-11 | -7.9 | 25.9 | 0 | 2024-02-11 | 1.1 | 16.9 | 0 | 2023-02-11 | -8 | 26 | 0 | 2022-02-11 | -0.3 | 18.3 | 0 | 2021-02-11 | -14.7 | 32.7 | 0 | 2020-02-11 | -5.7 | 23.7 | 0 | 2019-02-11 | -13 | 31 | 0 | 2018-02-11 | -7.7 | 25.7 | 0 | 2017-02-11 | -13.2 | 31.2 | 0 | 2016-02-11 | -17.8 | 35.8 | 0 | 26.72 | 0
2025-02-11 | -6.9 | 24.9 | 0 | 2024-02-11 | 1.7 | 16.3 | 0 | 2023-02-11 | -7.6 | 25.6 | 0 | 2022-02-11 | 0.1 | 17.9 | 0 | 2021-02-11 | -11.5 | 29.5 | 0 | 2020-02-11 | -5 | 23 | 0 | 2019-02-11 | -11.3 | 29.3 | 0 | 2018-02-11 | -6.7 | 24.7 | 0 | 2017-02-11 | -12.8 | 30.8 | 0 | 2016-02-11 | -17.9 | 35.9 | 0 | 25.79 | 0
2025-02-11 | -6.2 | 24.2 | 0 | 2024-02-11 | 1.7 | 16.3 | 0 | 2023-02-11 | -6.8 | 24.8 | 0 | 2022-02-11 | 1.2 | 16.8 | 0 | 2021-02-11 | -10.4 | 28.4 | 0 | 2020-02-11 | -4.2 | 22.2 | 0 | 2019-02-11 | -10.5 | 28.5 | 0 | 2018-02-11 | -6 | 24 | 0 | 2017-02-11 | -12.3 | 30.3 | 0 | 2016-02-11 | -17.6 | 35.6 | 0 | 25.11 | 0
2025-02-11 | -6 | 24 | 0 | 2024-02-11 | 1.9 | 16.1 | 0 | 2023-02-11 | -5.9 | 23.9 | 0 | 2022-02-11 | 2.1 | 15.9 | 0 | 2021-02-11 | -9.7 | 27.7 | 0 | 2020-02-11 | -3.2 | 21.2 | 0 | 2019-02-11 | -9.8 | 27.8 | 0 | 2018-02-11 | -5.6 | 23.6 | 0 | 2017-02-11 | -12 | 30 | 0 | 2016-02-11 | -17.2 | 35.2 | 0 | 24.54 | 0
2025-02-11 | -6.7 | 24.7 | 0 | 2024-02-11 | 2.1 | 15.9 | 0 | 2023-02-11 | -4.3 | 22.3 | 0 | 2022-02-11 | 2.7 | 15.3 | 0 | 2021-02-11 | -9.4 | 27.4 | 0 | 2020-02-11 | -1.3 | 19.3 | 0 | 2019-02-11 | -9.3 | 27.3 | 0 | 2018-02-11 | -5.7 | 23.7 | 0 | 2017-02-11 | -11.7 | 29.7 | 0 | 2016-02-11 | -17.4 | 35.4 | 0 | 24.1 | 0
2025-02-11 | -6.8 | 24.8 | 0 | 2024-02-11 | 2.1 | 15.9 | 0 | 2023-02-11 | -2.8 | 20.8 | 0 | 2022-02-11 | 3 | 15 | 0 | 2021-02-11 | -9.1 | 27.1 | 0 | 2020-02-11 | -1.2 | 19.2 | 0 | 2019-02-11 | -8.6 | 26.6 | 0 | 2018-02-11 | -5 | 23 | 0 | 2017-02-11 | -11.3 | 29.3 | 0 | 2016-02-11 | -17.8 | 35.8 | 0 | 23.75 | 0
2025-02-11 | -7 | 25 | 0 | 2024-02-11 | 2.4 | 15.6 | 0 | 2023-02-11 | -1 | 19 | 0 | 2022-02-11 | 2 | 16 | 0 | 2021-02-11 | -9.4 | 27.4 | 0 | 2020-02-11 | -0.8 | 18.8 | 0 | 2019-02-11 | -8.1 | 26.1 | 0 | 2018-02-11 | -5 | 23 | 0 | 2017-02-11 | -11.2 | 29.2 | 0 | 2016-02-11 | -17.6 | 35.6 | 0 | 23.57 | 0
2025-02-11 | -6.9 | 24.9 | 0 | 2024-02-11 | 2.2 | 15.8 | 0 | 2023-02-11 | -0.7 | 18.7 | 0 | 2022-02-11 | 2 | 16 | 0 | 2021-02-11 | -9.7 | 27.7 | 0 | 2020-02-11 | -0.6 | 18.6 | 0 | 2019-02-11 | -8.1 | 26.1 | 0 | 2018-02-11 | -5.1 | 23.1 | 0 | 2017-02-11 | -10.8 | 28.8 | 0 | 2016-02-11 | -17.1 | 35.1 | 0 | 23.48 | 0
2025-02-11 | -7.4 | 25.4 | 0 | 2024-02-11 | 1.8 | 16.2 | 0 | 2023-02-11 | -1 | 19 | 0 | 2022-02-11 | 4.1 | 13.9 | 0 | 2021-02-11 | -11.6 | 29.6 | 0 | 2020-02-11 | -1.2 | 19.2 | 0 | 2019-02-11 | -8.8 | 26.8 | 0 | 2018-02-11 | -3.2 | 21.2 | 0 | 2017-02-11 | -10.4 | 28.4 | 0 | 2016-02-11 | -17.2 | 35.2 | 0 | 23.49 | 0
2025-02-11 | -9 | 27 | 0 | 2024-02-11 | 1.7 | 16.3 | 0 | 2023-02-11 | -2 | 20 | 0 | 2022-02-11 | 2.9 | 15.1 | 0 | 2021-02-11 | -12.2 | 30.2 | 0 | 2020-02-11 | -2 | 20 | 0 | 2019-02-11 | -9 | 27 | 0 | 2018-02-11 | -3.1 | 21.1 | 0 | 2017-02-11 | -10.3 | 28.3 | 0 | 2016-02-11 | -17.3 | 35.3 | 0 | 24.03 | 0
2025-02-11 | -9.7 | 27.7 | 0 | 2024-02-11 | 1.5 | 16.5 | 0 | 2023-02-11 | -2 | 20 | 0 | 2022-02-11 | 3 | 15 | 0 | 2021-02-11 | -14.1 | 32.1 | 0 | 2020-02-11 | -2 | 20 | 0 | 2019-02-11 | -10.5 | 28.5 | 0 | 2018-02-11 | -2.9 | 20.9 | 0 | 2017-02-11 | -10.1 | 28.1 | 0 | 2016-02-11 | -17.5 | 35.5 | 0 | 24.43 | 0
2025-02-11 | -10.4 | 28.4 | 0 | 2024-02-11 | 1.4 | 16.6 | 0 | 2023-02-11 | -1.7 | 19.7 | 0 | 2022-02-11 | 2.6 | 15.4 | 0 | 2021-02-11 | -13.4 | 31.4 | 0 | 2020-02-11 | -1.9 | 19.9 | 0 | 2019-02-11 | -10.9 | 28.9 | 0 | 2018-02-11 | -2.6 | 20.6 | 0 | 2017-02-11 | -10.2 | 28.2 | 0 | 2016-02-11 | -18 | 36 | 0 | 24.51 | 0
2025-02-11 | -10.7 | 28.7 | 0 | 2024-02-11 | 0.8 | 17.2 | 0 | 2023-02-11 | -1.6 | 19.6 | 0 | 2022-02-11 | 2.5 | 15.5 | 0 | 2021-02-11 | -14.1 | 32.1 | 0 | 2020-02-11 | -1.2 | 19.2 | 0 | 2019-02-11 | -12.2 | 30.2 | 0 | 2018-02-11 | -2.9 | 20.9 | 0 | 2017-02-11 | -10.3 | 28.3 | 0 | 2016-02-11 | -19.7 | 37.7 | 0 | 24.94 | 0
2025-02-11 | -11.6 | 29.6 | 0 | 2024-02-11 | 0.6 | 17.4 | 0 | 2023-02-11 | -1.8 | 19.8 | 0 | 2022-02-11 | 2.1 | 15.9 | 0 | 2021-02-11 | -15.6 | 33.6 | 0 | 2020-02-11 | -0.8 | 18.8 | 0 | 2019-02-11 | -12.9 | 30.9 | 0 | 2018-02-11 | -4.3 | 22.3 | 0 | 2017-02-11 | -10.3 | 28.3 | 0 | 2016-02-11 | -19.9 | 37.9 | 0 | 25.45 | 0
2025-02-11 | -12.7 | 30.7 | 0 | 2024-02-11 | 0.4 | 17.6 | 0 | 2023-02-11 | -2 | 20 | 0 | 2022-02-11 | 2.1 | 15.9 | 0 | 2021-02-11 | -16.3 | 34.3 | 0 | 2020-02-11 | -0.8 | 18.8 | 0 | 2019-02-11 | -13.7 | 31.7 | 0 | 2018-02-11 | -5.5 | 23.5 | 0 | 2017-02-11 | -10.7 | 28.7 | 0 | 2016-02-11 | -20.4 | 38.4 | 0 | 25.96 | 0
2025-02-12 | -15 | 33 | 0 | 2024-02-12 | 0.1 | 17.9 | 0 | 2023-02-12 | -2.5 | 20.5 | 0 | 2022-02-12 | 2.1 | 15.9 | 0 | 2021-02-12 | -17.2 | 35.2 | 0 | 2020-02-12 | -1.1 | 19.1 | 0 | 2019-02-12 | -14.2 | 32.2 | 0 | 2018-02-12 | -5.8 | 23.8 | 0 | 2017-02-12 | -10.9 | 28.9 | 0 | 2016-02-12 | -20.3 | 38.3 | 0 | 26.48 | 0
2025-02-12 | -17 | 35 | 0 | 2024-02-12 | -0.3 | 18.3 | 0 | 2023-02-12 | -3.4 | 21.4 | 0 | 2022-02-12 | 1.8 | 16.2 | 0 | 2021-02-12 | -18 | 36 | 0 | 2020-02-12 | -1.4 | 19.4 | 0 | 2019-02-12 | -15.9 | 33.9 | 0 | 2018-02-12 | -5.5 | 23.5 | 0 | 2017-02-12 | -11.3 | 29.3 | 0 | 2016-02-12 | -21.3 | 39.3 | 0 | 27.23 | 0
2025-02-12 | -16.3 | 34.3 | 0 | 2024-02-12 | -0.3 | 18.3 | 0 | 2023-02-12 | -3.4 | 21.4 | 0 | 2022-02-12 | 1.8 | 16.2 | 0 | 2021-02-12 | -19.2 | 37.2 | 0 | 2020-02-12 | -1.7 | 19.7 | 0 | 2019-02-12 | -16.2 | 34.2 | 0 | 2018-02-12 | -6.2 | 24.2 | 0 | 2017-02-12 | -11.8 | 29.8 | 0 | 2016-02-12 | -21.1 | 39.1 | 0 | 27.44 | 0
2025-02-12 | -15.9 | 33.9 | 0 | 2024-02-12 | -0.5 | 18.5 | 0 | 2023-02-12 | -4.1 | 22.1 | 0 | 2022-02-12 | 1.6 | 16.4 | 0 | 2021-02-12 | -19.2 | 37.2 | 0 | 2020-02-12 | -2.5 | 20.5 | 0 | 2019-02-12 | -16.7 | 34.7 | 0 | 2018-02-12 | -7.1 | 25.1 | 0 | 2017-02-12 | -12.2 | 30.2 | 0 | 2016-02-12 | -22.1 | 40.1 | 0 | 27.87 | 0
2025-02-12 | -16.6 | 34.6 | 0 | 2024-02-12 | -0.2 | 18.2 | 0 | 2023-02-12 | -4 | 22 | 0 | 2022-02-12 | 1.5 | 16.5 | 0 | 2021-02-12 | -19.3 | 37.3 | 0 | 2020-02-12 | -4.8 | 22.8 | 0 | 2019-02-12 | -17.5 | 35.5 | 0 | 2018-02-12 | -8.2 | 26.2 | 0 | 2017-02-12 | -12.3 | 30.3 | 0 | 2016-02-12 | -21.4 | 39.4 | 0 | 28.28 | 0
2025-02-12 | -16.8 | 34.8 | 0 | 2024-02-12 | -0.3 | 18.3 | 0 | 2023-02-12 | -3.9 | 21.9 | 0 | 2022-02-12 | 1.4 | 16.6 | 0 | 2021-02-12 | -20.9 | 38.9 | 0 | 2020-02-12 | -4.4 | 22.4 | 0 | 2019-02-12 | -17.9 | 35.9 | 0 | 2018-02-12 | -9.3 | 27.3 | 0 | 2017-02-12 | -12.1 | 30.1 | 0 | 2016-02-12 | -20.9 | 38.9 | 0 | 28.51 | 0
2025-02-12 | -18.2 | 36.2 | 0 | 2024-02-12 | -0.6 | 18.6 | 0 | 2023-02-12 | -3.8 | 21.8 | 0 | 2022-02-12 | 1.5 | 16.5 | 0 | 2021-02-12 | -21 | 39 | 0 | 2020-02-12 | -5.3 | 23.3 | 0 | 2019-02-12 | -18 | 36 | 0 | 2018-02-12 | -8.7 | 26.7 | 0 | 2017-02-12 | -12 | 30 | 0 | 2016-02-12 | -21.2 | 39.2 | 0 | 28.73 | 0
2025-02-12 | -18.3 | 36.3 | 0 | 2024-02-12 | -0.6 | 18.6 | 0 | 2023-02-12 | -3.9 | 21.9 | 0 | 2022-02-12 | 1.6 | 16.4 | 0 | 2021-02-12 | -22.9 | 40.9 | 0 | 2020-02-12 | -5.5 | 23.5 | 0 | 2019-02-12 | -17.9 | 35.9 | 0 | 2018-02-12 | -8.6 | 26.6 | 0 | 2017-02-12 | -12.1 | 30.1 | 0 | 2016-02-12 | -21.3 | 39.3 | 0 | 28.95 | 0
2025-02-12 | -19.3 | 37.3 | 0 | 2024-02-12 | -0.6 | 18.6 | 0 | 2023-02-12 | -3.3 | 21.3 | 0 | 2022-02-12 | 1.9 | 16.1 | 0 | 2021-02-12 | -22.3 | 40.3 | 0 | 2020-02-12 | -5.8 | 23.8 | 0 | 2019-02-12 | -17.7 | 35.7 | 0 | 2018-02-12 | -7.8 | 25.8 | 0 | 2017-02-12 | -12.1 | 30.1 | 0 | 2016-02-12 | -20.5 | 38.5 | 0 | 28.75 | 0
2025-02-12 | -16.9 | 34.9 | 0 | 2024-02-12 | -0.4 | 18.4 | 0 | 2023-02-12 | -2.4 | 20.4 | 0 | 2022-02-12 | -0.1 | 18.1 | 0 | 2021-02-12 | -21.2 | 39.2 | 0 | 2020-02-12 | -4.2 | 22.2 | 0 | 2019-02-12 | -17.1 | 35.1 | 0 | 2018-02-12 | -6.8 | 24.8 | 0 | 2017-02-12 | -11.7 | 29.7 | 0 | 2016-02-12 | -18.1 | 36.1 | 0 | 27.89 | 0
2025-02-12 | -15.3 | 33.3 | 0 | 2024-02-12 | -0.3 | 18.3 | 0 | 2023-02-12 | -1.6 | 19.6 | 0 | 2022-02-12 | -6.1 | 24.1 | 0 | 2021-02-12 | -19.6 | 37.6 | 0 | 2020-02-12 | -2.1 | 20.1 | 0 | 2019-02-12 | -17 | 35 | 0 | 2018-02-12 | -5.6 | 23.6 | 0 | 2017-02-12 | -11.4 | 29.4 | 0 | 2016-02-12 | -13.7 | 31.7 | 0 | 27.27 | 0
2025-02-12 | -14.1 | 32.1 | 0 | 2024-02-12 | 0.4 | 17.6 | 0 | 2023-02-12 | -0.6 | 18.6 | 0 | 2022-02-12 | -8.2 | 26.2 | 0 | 2021-02-12 | -18.2 | 36.2 | 0 | 2020-02-12 | -0.8 | 18.8 | 0 | 2019-02-12 | -16.4 | 34.4 | 0 | 2018-02-12 | -5.4 | 23.4 | 0 | 2017-02-12 | -10.8 | 28.8 | 0 | 2016-02-12 | -9.7 | 27.7 | 0 | 26.38 | 0
2025-02-12 | -13 | 31 | 0 | 2024-02-12 | 0.3 | 17.7 | 0 | 2023-02-12 | 0.8 | 17.2 | 0 | 2022-02-12 | -10.6 | 28.6 | 0 | 2021-02-12 | -17.4 | 35.4 | 0 | 2020-02-12 | 0.5 | 17.5 | 0 | 2019-02-12 | -15.5 | 33.5 | 0 | 2018-02-12 | -5 | 23 | 0 | 2017-02-12 | -10.1 | 28.1 | 0 | 2016-02-12 | -7.9 | 25.9 | 0 | 25.79 | 0
2025-02-12 | -12.2 | 30.2 | 0 | 2024-02-12 | 1 | 17 | 0 | 2023-02-12 | 1.9 | 16.1 | 0 | 2022-02-12 | -11.5 | 29.5 | 0 | 2021-02-12 | -16.4 | 34.4 | 0 | 2020-02-12 | 0.8 | 17.2 | 0 | 2019-02-12 | -15.1 | 33.1 | 0 | 2018-02-12 | -5 | 23 | 0 | 2017-02-12 | -10.2 | 28.2 | 0 | 2016-02-12 | -6.5 | 24.5 | 0 | 25.32 | 0
2025-02-12 | -11.6 | 29.6 | 0 | 2024-02-12 | 1.1 | 16.9 | 0 | 2023-02-12 | 3.1 | 14.9 | 0 | 2022-02-12 | -12.4 | 30.4 | 0 | 2021-02-12 | -15.3 | 33.3 | 0 | 2020-02-12 | 1.5 | 16.5 | 0 | 2019-02-12 | -14.8 | 32.8 | 0 | 2018-02-12 | -4.6 | 22.6 | 0 | 2017-02-12 | -10.5 | 28.5 | 0 | 2016-02-12 | -5.8 | 23.8 | 0 | 24.93 | 0
2025-02-12 | -11.2 | 29.2 | 0 | 2024-02-12 | 1.9 | 16.1 | 0 | 2023-02-12 | 3.6 | 14.4 | 0 | 2022-02-12 | -12.6 | 30.6 | 0 | 2021-02-12 | -14.8 | 32.8 | 0 | 2020-02-12 | 1.2 | 16.8 | 0 | 2019-02-12 | -14.1 | 32.1 | 0 | 2018-02-12 | -4.9 | 22.9 | 0 | 2017-02-12 | -10.3 | 28.3 | 0 | 2016-02-12 | -5.1 | 23.1 | 0 | 24.63 | 0
2025-02-12 | -11.2 | 29.2 | 0 | 2024-02-12 | 1.9 | 16.1 | 0 | 2023-02-12 | 2.7 | 15.3 | 0 | 2022-02-12 | -13.2 | 31.2 | 0 | 2021-02-12 | -14.7 | 32.7 | 0 | 2020-02-12 | 0.3 | 17.7 | 0 | 2019-02-12 | -13.9 | 31.9 | 0 | 2018-02-12 | -5.2 | 23.2 | 0 | 2017-02-12 | -9.9 | 27.9 | 0 | 2016-02-12 | -5.2 | 23.2 | 0 | 24.84 | 0
2025-02-12 | -11.7 | 29.7 | 0 | 2024-02-12 | 0.7 | 17.3 | 0 | 2023-02-12 | 2.2 | 15.8 | 0 | 2022-02-12 | -13.7 | 31.7 | 0 | 2021-02-12 | -15.7 | 33.7 | 0 | 2020-02-12 | -0.5 | 18.5 | 0 | 2019-02-12 | -13.8 | 31.8 | 0 | 2018-02-12 | -5.9 | 23.9 | 0 | 2017-02-12 | -9.3 | 27.3 | 0 | 2016-02-12 | -4.9 | 22.9 | 0 | 25.26 | 0
2025-02-12 | -12.4 | 30.4 | 0 | 2024-02-12 | -0.4 | 18.4 | 0 | 2023-02-12 | 1.2 | 16.8 | 0 | 2022-02-12 | -14.2 | 32.2 | 0 | 2021-02-12 | -15.1 | 33.1 | 0 | 2020-02-12 | -1 | 19 | 0 | 2019-02-12 | -13.1 | 31.1 | 0 | 2018-02-12 | -8.4 | 26.4 | 0 | 2017-02-12 | -8.9 | 26.9 | 0 | 2016-02-12 | -7.4 | 25.4 | 0 | 25.97 | 0
2025-02-12 | -12.5 | 30.5 | 0 | 2024-02-12 | -0.9 | 18.9 | 0 | 2023-02-12 | 0.2 | 17.8 | 0 | 2022-02-12 | -14.7 | 32.7 | 0 | 2021-02-12 | -15.8 | 33.8 | 0 | 2020-02-12 | -0.9 | 18.9 | 0 | 2019-02-12 | -11.9 | 29.9 | 0 | 2018-02-12 | -8.9 | 26.9 | 0 | 2017-02-12 | -8.3 | 26.3 | 0 | 2016-02-12 | -9.2 | 27.2 | 0 | 26.29 | 0
2025-02-12 | -12.5 | 30.5 | 0 | 2024-02-12 | -0.9 | 18.9 | 0 | 2023-02-12 | -0.8 | 18.8 | 0 | 2022-02-12 | -14.7 | 32.7 | 0 | 2021-02-12 | -16.5 | 34.5 | 0 | 2020-02-12 | -1 | 19 | 0 | 2019-02-12 | -11.1 | 29.1 | 0 | 2018-02-12 | -9.4 | 27.4 | 0 | 2017-02-12 | -7.8 | 25.8 | 0 | 2016-02-12 | -9.6 | 27.6 | 0 | 26.43 | 0
2025-02-12 | -12.6 | 30.6 | 0 | 2024-02-12 | -2.4 | 20.4 | 0 | 2023-02-12 | -1.8 | 19.8 | 0 | 2022-02-12 | -15.5 | 33.5 | 0 | 2021-02-12 | -16.9 | 34.9 | 0 | 2020-02-12 | -0.8 | 18.8 | 0 | 2019-02-12 | -10.3 | 28.3 | 0 | 2018-02-12 | -12.2 | 30.2 | 0 | 2017-02-12 | -7.1 | 25.1 | 0 | 2016-02-12 | -11.1 | 29.1 | 0 | 27.07 | 0
2025-02-12 | -13.5 | 31.5 | 0 | 2024-02-12 | -2.2 | 20.2 | 0 | 2023-02-12 | -2.3 | 20.3 | 0 | 2022-02-12 | -16.6 | 34.6 | 0 | 2021-02-12 | -17.5 | 35.5 | 0 | 2020-02-12 | -0.6 | 18.6 | 0 | 2019-02-12 | -9.7 | 27.7 | 0 | 2018-02-12 | -10.2 | 28.2 | 0 | 2017-02-12 | -6.9 | 24.9 | 0 | 2016-02-12 | -12.3 | 30.3 | 0 | 27.18 | 0
2025-02-12 | -13.3 | 31.3 | 0 | 2024-02-12 | -3.1 | 21.1 | 0 | 2023-02-12 | -3 | 21 | 0 | 2022-02-12 | -17.4 | 35.4 | 0 | 2021-02-12 | -18.5 | 36.5 | 0 | 2020-02-12 | -0.9 | 18.9 | 0 | 2019-02-12 | -8.8 | 26.8 | 0 | 2018-02-12 | -12.1 | 30.1 | 0 | 2017-02-12 | -7.8 | 25.8 | 0 | 2016-02-12 | -14.2 | 32.2 | 0 | 27.91 | 0
2025-02-13 | -13.3 | 31.3 | 0 | 2024-02-13 | -3.3 | 21.3 | 0 | 2023-02-13 | -4.5 | 22.5 | 0 | 2022-02-13 | -18.3 | 36.3 | 0 | 2021-02-13 | -19.2 | 37.2 | 0 | 2020-02-13 | -0.8 | 18.8 | 0 | 2019-02-13 | -8 | 26 | 0 | 2018-02-13 | -14.2 | 32.2 | 0 | 2017-02-13 | -7.7 | 25.7 | 0 | 2016-02-13 | -15.7 | 33.7 | 0 | 28.5 | 0
2025-02-13 | -12.9 | 30.9 | 0 | 2024-02-13 | -3.9 | 21.9 | 0 | 2023-02-13 | -4.7 | 22.7 | 0 | 2022-02-13 | -18.8 | 36.8 | 0 | 2021-02-13 | -17.9 | 35.9 | 0 | 2020-02-13 | -1.4 | 19.4 | 0 | 2019-02-13 | -7.6 | 25.6 | 0 | 2018-02-13 | -13.3 | 31.3 | 0 | 2017-02-13 | -7.3 | 25.3 | 0 | 2016-02-13 | -17.1 | 35.1 | 0 | 28.49 | 0
2025-02-13 | -12.1 | 30.1 | 0 | 2024-02-13 | -4.2 | 22.2 | 0 | 2023-02-13 | -5.6 | 23.6 | 0 | 2022-02-13 | -19.7 | 37.7 | 0 | 2021-02-13 | -20.5 | 38.5 | 0 | 2020-02-13 | -1.3 | 19.3 | 0 | 2019-02-13 | -7.7 | 25.7 | 0 | 2018-02-13 | -13.4 | 31.4 | 0 | 2017-02-13 | -7.2 | 25.2 | 0 | 2016-02-13 | -19 | 37 | 0 | 29.07 | 0
2025-02-13 | -11.5 | 29.5 | 0 | 2024-02-13 | -5.5 | 23.5 | 0 | 2023-02-13 | -5.3 | 23.3 | 0 | 2022-02-13 | -20.3 | 38.3 | 0 | 2021-02-13 | -20.7 | 38.7 | 0 | 2020-02-13 | -1.5 | 19.5 | 0 | 2019-02-13 | -7.7 | 25.7 | 0 | 2018-02-13 | -14.8 | 32.8 | 0 | 2017-02-13 | -7.2 | 25.2 | 0 | 2016-02-13 | -21.4 | 39.4 | 0 | 29.59 | 0
2025-02-13 | -10.7 | 28.7 | 0 | 2024-02-13 | -6.7 | 24.7 | 0 | 2023-02-13 | -4.7 | 22.7 | 0 | 2022-02-13 | -21 | 39 | 0 | 2021-02-13 | -20.6 | 38.6 | 0 | 2020-02-13 | -1.2 | 19.2 | 0 | 2019-02-13 | -7.5 | 25.5 | 0 | 2018-02-13 | -18.2 | 36.2 | 0 | 2017-02-13 | -7.4 | 25.4 | 0 | 2016-02-13 | -23.9 | 41.9 | 0 | 30.19 | 0
2025-02-13 | -10.5 | 28.5 | 0 | 2024-02-13 | -6.7 | 24.7 | 0 | 2023-02-13 | -5.2 | 23.2 | 0 | 2022-02-13 | -21.7 | 39.7 | 0 | 2021-02-13 | -21.9 | 39.9 | 0 | 2020-02-13 | -2.1 | 20.1 | 0 | 2019-02-13 | -6.7 | 24.7 | 0 | 2018-02-13 | -16.3 | 34.3 | 0 | 2017-02-13 | -7.6 | 25.6 | 0 | 2016-02-13 | -25.7 | 43.7 | 0 | 30.44 | 0
2025-02-13 | -10.2 | 28.2 | 0 | 2024-02-13 | -6.4 | 24.4 | 0 | 2023-02-13 | -6.1 | 24.1 | 0 | 2022-02-13 | -22.1 | 40.1 | 0 | 2021-02-13 | -22.3 | 40.3 | 0 | 2020-02-13 | -2.5 | 20.5 | 0 | 2019-02-13 | -6.2 | 24.2 | 0 | 2018-02-13 | -18.3 | 36.3 | 0 | 2017-02-13 | -7.7 | 25.7 | 0 | 2016-02-13 | -27.3 | 45.3 | 0 | 30.91 | 0
2025-02-13 | -9.7 | 27.7 | 0 | 2024-02-13 | -7.3 | 25.3 | 0 | 2023-02-13 | -5.5 | 23.5 | 0 | 2022-02-13 | -22.6 | 40.6 | 0 | 2021-02-13 | -21.8 | 39.8 | 0 | 2020-02-13 | -2.7 | 20.7 | 0 | 2019-02-13 | -5.9 | 23.9 | 0 | 2018-02-13 | -19.2 | 37.2 | 0 | 2017-02-13 | -7.6 | 25.6 | 0 | 2016-02-13 | -28.5 | 46.5 | 0 | 31.08 | 0
2025-02-13 | -9.2 | 27.2 | 0 | 2024-02-13 | -5.9 | 23.9 | 0 | 2023-02-13 | -4.1 | 22.1 | 0 | 2022-02-13 | -22.7 | 40.7 | 0 | 2021-02-13 | -21.8 | 39.8 | 0 | 2020-02-13 | -2.6 | 20.6 | 0 | 2019-02-13 | -5.7 | 23.7 | 0 | 2018-02-13 | -17.6 | 35.6 | 0 | 2017-02-13 | -7.5 | 25.5 | 0 | 2016-02-13 | -28.8 | 46.8 | 0 | 30.59 | 0
2025-02-13 | -8.1 | 26.1 | 0 | 2024-02-13 | -4 | 22 | 0 | 2023-02-13 | -4.2 | 22.2 | 0 | 2022-02-13 | -21.4 | 39.4 | 0 | 2021-02-13 | -18.6 | 36.6 | 0 | 2020-02-13 | -2.5 | 20.5 | 0 | 2019-02-13 | -2.5 | 20.5 | 0 | 2018-02-13 | -16.1 | 34.1 | 0 | 2017-02-13 | -7.3 | 25.3 | 0 | 2016-02-13 | -28.3 | 46.3 | 0 | 29.3 | 0
2025-02-13 | -7.3 | 25.3 | 0 | 2024-02-13 | -2 | 20 | 0 | 2023-02-13 | -1.6 | 19.6 | 0 | 2022-02-13 | -19.9 | 37.9 | 0 | 2021-02-13 | -17.3 | 35.3 | 0 | 2020-02-13 | -5.6 | 23.6 | 0 | 2019-02-13 | -1.4 | 19.4 | 0 | 2018-02-13 | -12.8 | 30.8 | 0 | 2017-02-13 | -6.1 | 24.1 | 0 | 2016-02-13 | -27.5 | 45.5 | 0 | 28.15 | 0
2025-02-13 | -6.5 | 24.5 | 0 | 2024-02-13 | 0.6 | 17.4 | 0 | 2023-02-13 | -0.1 | 18.1 | 0 | 2022-02-13 | -18.5 | 36.5 | 0 | 2021-02-13 | -16.9 | 34.9 | 0 | 2020-02-13 | -9.3 | 27.3 | 0 | 2019-02-13 | -0.3 | 18.3 | 0 | 2018-02-13 | -10.9 | 28.9 | 0 | 2017-02-13 | -5.3 | 23.3 | 0 | 2016-02-13 | -26.5 | 44.5 | 0 | 27.37 | 0
2025-02-13 | -5.7 | 23.7 | 0 | 2024-02-13 | 1.8 | 16.2 | 0 | 2023-02-13 | 1 | 17 | 0 | 2022-02-13 | -17.3 | 35.3 | 0 | 2021-02-13 | -16 | 34 | 0 | 2020-02-13 | -9.9 | 27.9 | 0 | 2019-02-13 | 0 | 18 | 0 | 2018-02-13 | -9.3 | 27.3 | 0 | 2017-02-13 | -4.7 | 22.7 | 0 | 2016-02-13 | -26.1 | 44.1 | 0 | 26.62 | 0
2025-02-13 | -5 | 23 | 0 | 2024-02-13 | 2 | 16 | 0 | 2023-02-13 | 2.1 | 15.9 | 0 | 2022-02-13 | -16.3 | 34.3 | 0 | 2021-02-13 | -15.3 | 33.3 | 0 | 2020-02-13 | -10.2 | 28.2 | 0 | 2019-02-13 | -0.2 | 18.2 | 0 | 2018-02-13 | -7.7 | 25.7 | 0 | 2017-02-13 | -4.7 | 22.7 | 0 | 2016-02-13 | -25 | 43 | 0 | 26.03 | 0
2025-02-13 | -5.4 | 23.4 | 0 | 2024-02-13 | 2.1 | 15.9 | 0 | 2023-02-13 | 2.8 | 15.2 | 0 | 2022-02-13 | -15.6 | 33.6 | 0 | 2021-02-13 | -14.4 | 32.4 | 0 | 2020-02-13 | -11 | 29 | 0 | 2019-02-13 | -1.3 | 19.3 | 0 | 2018-02-13 | -6.9 | 24.9 | 0 | 2017-02-13 | -4.6 | 22.6 | 0 | 2016-02-13 | -25.1 | 43.1 | 0 | 25.94 | 0
2025-02-13 | -5.4 | 23.4 | 0 | 2024-02-13 | 2 | 16 | 0 | 2023-02-13 | 3.1 | 14.9 | 0 | 2022-02-13 | -15.1 | 33.1 | 0 | 2021-02-13 | -13.5 | 31.5 | 0 | 2020-02-13 | -11.5 | 29.5 | 0 | 2019-02-13 | -1.4 | 19.4 | 0 | 2018-02-13 | -6.8 | 24.8 | 0 | 2017-02-13 | -4.3 | 22.3 | 0 | 2016-02-13 | -24.8 | 42.8 | 0 | 25.77 | 0
2025-02-13 | -6.5 | 24.5 | 0 | 2024-02-13 | 1.5 | 16.5 | 0 | 2023-02-13 | 2.3 | 15.7 | 0 | 2022-02-13 | -15.2 | 33.2 | 0 | 2021-02-13 | -12.8 | 30.8 | 0 | 2020-02-13 | -12.4 | 30.4 | 0 | 2019-02-13 | -2 | 20 | 0 | 2018-02-13 | -6.6 | 24.6 | 0 | 2017-02-13 | -4.6 | 22.6 | 0 | 2016-02-13 | -25.3 | 43.3 | 0 | 26.16 | 0
2025-02-13 | -6.3 | 24.3 | 0 | 2024-02-13 | 0.3 | 17.7 | 0 | 2023-02-13 | 1.5 | 16.5 | 0 | 2022-02-13 | -15.9 | 33.9 | 0 | 2021-02-13 | -12.6 | 30.6 | 0 | 2020-02-13 | -13.3 | 31.3 | 0 | 2019-02-13 | -2.5 | 20.5 | 0 | 2018-02-13 | -6.8 | 24.8 | 0 | 2017-02-13 | -4.8 | 22.8 | 0 | 2016-02-13 | -25.6 | 43.6 | 0 | 26.6 | 0
2025-02-13 | -6.8 | 24.8 | 0 | 2024-02-13 | -1.9 | 19.9 | 0 | 2023-02-13 | 1.6 | 16.4 | 0 | 2022-02-13 | -16.8 | 34.8 | 0 | 2021-02-13 | -13 | 31 | 0 | 2020-02-13 | -13.5 | 31.5 | 0 | 2019-02-13 | -3.2 | 21.2 | 0 | 2018-02-13 | -7.7 | 25.7 | 0 | 2017-02-13 | -6 | 24 | 0 | 2016-02-13 | -25.8 | 43.8 | 0 | 27.31 | 0
2025-02-13 | -7 | 25 | 0 | 2024-02-13 | -2.8 | 20.8 | 0 | 2023-02-13 | 1.5 | 16.5 | 0 | 2022-02-13 | -16.8 | 34.8 | 0 | 2021-02-13 | -13.2 | 31.2 | 0 | 2020-02-13 | -14.3 | 32.3 | 0 | 2019-02-13 | -3.5 | 21.5 | 0 | 2018-02-13 | -8.1 | 26.1 | 0 | 2017-02-13 | -6.7 | 24.7 | 0 | 2016-02-13 | -26 | 44 | 0 | 27.69 | 0
2025-02-13 | -7.4 | 25.4 | 0 | 2024-02-13 | -3.5 | 21.5 | 0 | 2023-02-13 | 1.1 | 16.9 | 0 | 2022-02-13 | -17.4 | 35.4 | 0 | 2021-02-13 | -13.2 | 31.2 | 0 | 2020-02-13 | -14.2 | 32.2 | 0 | 2019-02-13 | -4.3 | 22.3 | 0 | 2018-02-13 | -8.5 | 26.5 | 0 | 2017-02-13 | -7.1 | 25.1 | 0 | 2016-02-13 | -26.3 | 44.3 | 0 | 28.08 | 0
2025-02-13 | -8 | 26 | 0 | 2024-02-13 | -5.1 | 23.1 | 0 | 2023-02-13 | 1.2 | 16.8 | 0 | 2022-02-13 | -17.9 | 35.9 | 0 | 2021-02-13 | -13.2 | 31.2 | 0 | 2020-02-13 | -15.2 | 33.2 | 0 | 2019-02-13 | -5.2 | 23.2 | 0 | 2018-02-13 | -8.6 | 26.6 | 0 | 2017-02-13 | -6.6 | 24.6 | 0 | 2016-02-13 | -26.7 | 44.7 | 0 | 28.53 | 0
2025-02-13 | -9 | 27 | 0 | 2024-02-13 | -6.6 | 24.6 | 0 | 2023-02-13 | 1.4 | 16.6 | 0 | 2022-02-13 | -18.4 | 36.4 | 0 | 2021-02-13 | -13.5 | 31.5 | 0 | 2020-02-13 | -16.5 | 34.5 | 0 | 2019-02-13 | -6.4 | 24.4 | 0 | 2018-02-13 | -8.8 | 26.8 | 0 | 2017-02-13 | -8.1 | 26.1 | 0 | 2016-02-13 | -27 | 45 | 0 | 29.29 | 0
2025-02-13 | -9.9 | 27.9 | 0 | 2024-02-13 | -7.8 | 25.8 | 0 | 2023-02-13 | 1.2 | 16.8 | 0 | 2022-02-13 | -17.2 | 35.2 | 0 | 2021-02-13 | -13.8 | 31.8 | 0 | 2020-02-13 | -18 | 36 | 0 | 2019-02-13 | -6.5 | 24.5 | 0 | 2018-02-13 | -8.8 | 26.8 | 0 | 2017-02-13 | -9 | 27 | 0 | 2016-02-13 | -27.1 | 45.1 | 0 | 29.69 | 0
2025-02-14 | -10.1 | 28.1 | 0 | 2024-02-14 | -9.4 | 27.4 | 0 | 2023-02-14 | 1.3 | 16.7 | 0 | 2022-02-14 | -17.8 | 35.8 | 0 | 2021-02-14 | -14.1 | 32.1 | 0 | 2020-02-14 | -19.4 | 37.4 | 0 | 2019-02-14 | -6.2 | 24.2 | 0 | 2018-02-14 | -9.1 | 27.1 | 0 | 2017-02-14 | -10.7 | 28.7 | 0 | 2016-02-14 | -27.4 | 45.4 | 0 | 30.29 | 0
2025-02-14 | -11 | 29 | 0 | 2024-02-14 | -9.7 | 27.7 | 0 | 2023-02-14 | 1.3 | 16.7 | 0 | 2022-02-14 | -17.9 | 35.9 | 0 | 2021-02-14 | -14 | 32 | 0 | 2020-02-14 | -20.2 | 38.2 | 0 | 2019-02-14 | -6.8 | 24.8 | 0 | 2018-02-14 | -10.2 | 28.2 | 0 | 2017-02-14 | -11.1 | 29.1 | 0 | 2016-02-14 | -28 | 46 | 0 | 30.76 | 0
2025-02-14 | -11.6 | 29.6 | 0 | 2024-02-14 | -9.7 | 27.7 | 0 | 2023-02-14 | 0.9 | 17.1 | 0 | 2022-02-14 | -19.5 | 37.5 | 0 | 2021-02-14 | -13.8 | 31.8 | 0 | 2020-02-14 | -21 | 39 | 0 | 2019-02-14 | -6.8 | 24.8 | 0 | 2018-02-14 | -10.1 | 28.1 | 0 | 2017-02-14 | -11.8 | 29.8 | 0 | 2016-02-14 | -27.8 | 45.8 | 0 | 31.12 | 0
2025-02-14 | -12.5 | 30.5 | 0 | 2024-02-14 | -9.8 | 27.8 | 0 | 2023-02-14 | 0.8 | 17.2 | 0 | 2022-02-14 | -20.4 | 38.4 | 0 | 2021-02-14 | -13.5 | 31.5 | 0 | 2020-02-14 | -21.7 | 39.7 | 0 | 2019-02-14 | -6.8 | 24.8 | 0 | 2018-02-14 | -9.6 | 27.6 | 0 | 2017-02-14 | -10.3 | 28.3 | 0 | 2016-02-14 | -28 | 46 | 0 | 31.18 | 0
2025-02-14 | -14.3 | 32.3 | 0 | 2024-02-14 | -9.9 | 27.9 | 0 | 2023-02-14 | -0.1 | 18.1 | 0 | 2022-02-14 | -20.8 | 38.8 | 0 | 2021-02-14 | -12.8 | 30.8 | 0 | 2020-02-14 | -22.1 | 40.1 | 0 | 2019-02-14 | -7.2 | 25.2 | 0 | 2018-02-14 | -9.1 | 27.1 | 0 | 2017-02-14 | -12 | 30 | 0 | 2016-02-14 | -28.9 | 46.9 | 0 | 31.72 | 0
2025-02-14 | -12.9 | 30.9 | 0 | 2024-02-14 | -10.2 | 28.2 | 0 | 2023-02-14 | -0.6 | 18.6 | 0 | 2022-02-14 | -21.7 | 39.7 | 0 | 2021-02-14 | -12.8 | 30.8 | 0 | 2020-02-14 | -23.1 | 41.1 | 0 | 2019-02-14 | -7.5 | 25.5 | 0 | 2018-02-14 | -6 | 24 | 0 | 2017-02-14 | -13.4 | 31.4 | 0 | 2016-02-14 | -29.6 | 47.6 | 0 | 31.78 | 0
2025-02-14 | -14 | 32 | 0 | 2024-02-14 | -9.9 | 27.9 | 0 | 2023-02-14 | -2.3 | 20.3 | 0 | 2022-02-14 | -22.3 | 40.3 | 0 | 2021-02-14 | -12.6 | 30.6 | 0 | 2020-02-14 | -24.8 | 42.8 | 0 | 2019-02-14 | -8.8 | 26.8 | 0 | 2018-02-14 | -8.5 | 26.5 | 0 | 2017-02-14 | -13.9 | 31.9 | 0 | 2016-02-14 | -29 | 47 | 0 | 32.61 | 0
2025-02-14 | -15.9 | 33.9 | 0 | 2024-02-14 | -10.4 | 28.4 | 0 | 2023-02-14 | -2.3 | 20.3 | 0 | 2022-02-14 | -23 | 41 | 0 | 2021-02-14 | -12.6 | 30.6 | 0 | 2020-02-14 | -24.9 | 42.9 | 0 | 2019-02-14 | -10.1 | 28.1 | 0 | 2018-02-14 | -9.8 | 27.8 | 0 | 2017-02-14 | -10.7 | 28.7 | 0 | 2016-02-14 | -29.3 | 47.3 | 0 | 32.9 | 0
2025-02-14 | -14.7 | 32.7 | 0 | 2024-02-14 | -10.3 | 28.3 | 0 | 2023-02-14 | -2.7 | 20.7 | 0 | 2022-02-14 | -23.3 | 41.3 | 0 | 2021-02-14 | -12.5 | 30.5 | 0 | 2020-02-14 | -25 | 43 | 0 | 2019-02-14 | -10.3 | 28.3 | 0 | 2018-02-14 | -4.5 | 22.5 | 0 | 2017-02-14 | -9.3 | 27.3 | 0 | 2016-02-14 | -28.6 | 46.6 | 0 | 32.12 | 0
2025-02-14 | -12.9 | 30.9 | 0 | 2024-02-14 | -10.5 | 28.5 | 0 | 2023-02-14 | -0.9 | 18.9 | 0 | 2022-02-14 | -22 | 40 | 0 | 2021-02-14 | -13.2 | 31.2 | 0 | 2020-02-14 | -23.1 | 41.1 | 0 | 2019-02-14 | -9.6 | 27.6 | 0 | 2018-02-14 | -1.1 | 19.1 | 0 | 2017-02-14 | -8.4 | 26.4 | 0 | 2016-02-14 | -27.5 | 45.5 | 0 | 30.92 | 0
2025-02-14 | -10.5 | 28.5 | 0 | 2024-02-14 | -10.1 | 28.1 | 0 | 2023-02-14 | 0.8 | 17.2 | 0 | 2022-02-14 | -19.9 | 37.9 | 0 | 2021-02-14 | -11.9 | 29.9 | 0 | 2020-02-14 | -22.1 | 40.1 | 0 | 2019-02-14 | -9.1 | 27.1 | 0 | 2018-02-14 | 1.7 | 16.3 | 0 | 2017-02-14 | -7.4 | 25.4 | 0 | 2016-02-14 | -25.5 | 43.5 | 0 | 29.4 | 0
2025-02-14 | -9.8 | 27.8 | 0 | 2024-02-14 | -9.2 | 27.2 | 0 | 2023-02-14 | 2.3 | 15.7 | 0 | 2022-02-14 | -18.3 | 36.3 | 0 | 2021-02-14 | -10.8 | 28.8 | 0 | 2020-02-14 | -20.8 | 38.8 | 0 | 2019-02-14 | -8.3 | 26.3 | 0 | 2018-02-14 | 2.6 | 15.4 | 0 | 2017-02-14 | -6 | 24 | 0 | 2016-02-14 | -23.9 | 41.9 | 0 | 28.22 | 0
2025-02-14 | -8.8 | 26.8 | 0 | 2024-02-14 | -8.1 | 26.1 | 0 | 2023-02-14 | 3.3 | 14.7 | 0 | 2022-02-14 | -16.9 | 34.9 | 0 | 2021-02-14 | -9.4 | 27.4 | 0 | 2020-02-14 | -19.7 | 37.7 | 0 | 2019-02-14 | -7.6 | 25.6 | 0 | 2018-02-14 | 3 | 15 | 0 | 2017-02-14 | -4.7 | 22.7 | 0 | 2016-02-14 | -22.5 | 40.5 | 0 | 27.14 | 0
2025-02-14 | -8.3 | 26.3 | 0 | 2024-02-14 | -7.5 | 25.5 | 0 | 2023-02-14 | 4 | 14 | 0 | 2022-02-14 | -16 | 34 | 0 | 2021-02-14 | -8.6 | 26.6 | 0 | 2020-02-14 | -18.8 | 36.8 | 0 | 2019-02-14 | -6.4 | 24.4 | 0 | 2018-02-14 | 3.7 | 14.3 | 0 | 2017-02-14 | -4.7 | 22.7 | 0 | 2016-02-14 | -21.3 | 39.3 | 0 | 26.39 | 0
2025-02-14 | -8 | 26 | 0 | 2024-02-14 | -6.6 | 24.6 | 0 | 2023-02-14 | 4.7 | 13.3 | 0 | 2022-02-14 | -15.3 | 33.3 | 0 | 2021-02-14 | -7.8 | 25.8 | 0 | 2020-02-14 | -17.7 | 35.7 | 0 | 2019-02-14 | -5.6 | 23.6 | 0 | 2018-02-14 | 4.5 | 13.5 | 0 | 2017-02-14 | -4.1 | 22.1 | 0 | 2016-02-14 | -20.1 | 38.1 | 0 | 25.6 | 0
2025-02-14 | -7.3 | 25.3 | 0 | 2024-02-14 | -5.7 | 23.7 | 0 | 2023-02-14 | 5.1 | 12.9 | 0 | 2022-02-14 | -14.9 | 32.9 | 0 | 2021-02-14 | -7.5 | 25.5 | 0 | 2020-02-14 | -16.8 | 34.8 | 0 | 2019-02-14 | -5.5 | 23.5 | 0 | 2018-02-14 | 5 | 13 | 0 | 2017-02-14 | -4 | 22 | 0 | 2016-02-14 | -19.2 | 37.2 | 0 | 25.08 | 0
2025-02-14 | -7.6 | 25.6 | 0 | 2024-02-14 | -5.3 | 23.3 | 0 | 2023-02-14 | 5.6 | 12.4 | 0 | 2022-02-14 | -14.9 | 32.9 | 0 | 2021-02-14 | -7.9 | 25.9 | 0 | 2020-02-14 | -16.5 | 34.5 | 0 | 2019-02-14 | -5.5 | 23.5 | 0 | 2018-02-14 | 4.6 | 13.4 | 0 | 2017-02-14 | -3.8 | 21.8 | 0 | 2016-02-14 | -18.7 | 36.7 | 0 | 25 | 0
2025-02-14 | -8.2 | 26.2 | 0 | 2024-02-14 | -5.5 | 23.5 | 0 | 2023-02-14 | 4.8 | 13.2 | 0 | 2022-02-14 | -15.4 | 33.4 | 0 | 2021-02-14 | -7.6 | 25.6 | 0 | 2020-02-14 | -16.7 | 34.7 | 0 | 2019-02-14 | -6.6 | 24.6 | 0 | 2018-02-14 | 3.8 | 14.2 | 0 | 2017-02-14 | -3.6 | 21.6 | 0 | 2016-02-14 | -18.5 | 36.5 | 0 | 25.35 | 0
2025-02-14 | -9.7 | 27.7 | 0 | 2024-02-14 | -5.8 | 23.8 | 0 | 2023-02-14 | 3.7 | 14.3 | 0 | 2022-02-14 | -15.6 | 33.6 | 0 | 2021-02-14 | -9.3 | 27.3 | 0 | 2020-02-14 | -17.3 | 35.3 | 0 | 2019-02-14 | -8.1 | 26.1 | 0 | 2018-02-14 | 2.7 | 15.3 | 0 | 2017-02-14 | -3.8 | 21.8 | 0 | 2016-02-14 | -19.6 | 37.6 | 0 | 26.28 | 0
2025-02-14 | -12.8 | 30.8 | 0 | 2024-02-14 | -6 | 24 | 0 | 2023-02-14 | 2.8 | 15.2 | 0 | 2022-02-14 | -16.2 | 34.2 | 0 | 2021-02-14 | -9.3 | 27.3 | 0 | 2020-02-14 | -18.5 | 36.5 | 0 | 2019-02-14 | -10 | 28 | 0 | 2018-02-14 | 1.9 | 16.1 | 0 | 2017-02-14 | -4.8 | 22.8 | 0 | 2016-02-14 | -20.5 | 38.5 | 0 | 27.34 | 0
2025-02-14 | -13.1 | 31.1 | 0 | 2024-02-14 | -6.3 | 24.3 | 0 | 2023-02-14 | 1.5 | 16.5 | 0 | 2022-02-14 | -17.1 | 35.1 | 0 | 2021-02-14 | -9.4 | 27.4 | 0 | 2020-02-14 | -18.7 | 36.7 | 0 | 2019-02-14 | -8.2 | 26.2 | 0 | 2018-02-14 | 1.2 | 16.8 | 0 | 2017-02-14 | -5.1 | 23.1 | 0 | 2016-02-14 | -21.4 | 39.4 | 0 | 27.66 | 0
2025-02-14 | -12 | 30 | 0 | 2024-02-14 | -6.8 | 24.8 | 0 | 2023-02-14 | 0.4 | 17.6 | 0 | 2022-02-14 | -17.9 | 35.9 | 0 | 2021-02-14 | -10.8 | 28.8 | 0 | 2020-02-14 | -19.3 | 37.3 | 0 | 2019-02-14 | -8.1 | 26.1 | 0 | 2018-02-14 | 0.3 | 17.7 | 0 | 2017-02-14 | -5.3 | 23.3 | 0 | 2016-02-14 | -21.8 | 39.8 | 0 | 28.13 | 0
2025-02-14 | -12 | 30 | 0 | 2024-02-14 | -7.2 | 25.2 | 0 | 2023-02-14 | 0.3 | 17.7 | 0 | 2022-02-14 | -18.2 | 36.2 | 0 | 2021-02-14 | -12.7 | 30.7 | 0 | 2020-02-14 | -19.4 | 37.4 | 0 | 2019-02-14 | -7.2 | 25.2 | 0 | 2018-02-14 | -0.1 | 18.1 | 0 | 2017-02-14 | -5.2 | 23.2 | 0 | 2016-02-14 | -22.2 | 40.2 | 0 | 28.39 | 0
2025-02-14 | -12.3 | 30.3 | 0 | 2024-02-14 | -8.2 | 26.2 | 0 | 2023-02-14 | -0.3 | 18.3 | 0 | 2022-02-14 | -18.4 | 36.4 | 0 | 2021-02-14 | -11.5 | 29.5 | 0 | 2020-02-14 | -18.9 | 36.9 | 0 | 2019-02-14 | -6.6 | 24.6 | 0 | 2018-02-14 | -0.6 | 18.6 | 0 | 2017-02-14 | -5.2 | 23.2 | 0 | 2016-02-14 | -22.7 | 40.7 | 0 | 28.47 | 0
2025-02-15 | -13.5 | 31.5 | 0 | 2024-02-15 | -8.7 | 26.7 | 0 | 2023-02-15 | -0.4 | 18.4 | 0 | 2022-02-15 | -18.1 | 36.1 | 0 | 2021-02-15 | -10.6 | 28.6 | 0 | 2020-02-15 | -18.3 | 36.3 | 0 | 2019-02-15 | -6.2 | 24.2 | 0 | 2018-02-15 | -0.8 | 18.8 | 0 | 2017-02-15 | -5 | 23 | 0 | 2016-02-15 | -22.8 | 40.8 | 0 | 28.44 | 0
2025-02-15 | -14 | 32 | 0 | 2024-02-15 | -9.7 | 27.7 | 0 | 2023-02-15 | -0.7 | 18.7 | 0 | 2022-02-15 | -17.7 | 35.7 | 0 | 2021-02-15 | -11.4 | 29.4 | 0 | 2020-02-15 | -17 | 35 | 0 | 2019-02-15 | -5.9 | 23.9 | 0 | 2018-02-15 | -1.8 | 19.8 | 0 | 2017-02-15 | -5.2 | 23.2 | 0 | 2016-02-15 | -23.1 | 41.1 | 0 | 28.65 | 0
2025-02-15 | -13.2 | 31.2 | 0 | 2024-02-15 | -10.6 | 28.6 | 0 | 2023-02-15 | -0.7 | 18.7 | 0 | 2022-02-15 | -18.4 | 36.4 | 0 | 2021-02-15 | -10.8 | 28.8 | 0 | 2020-02-15 | -15.7 | 33.7 | 0 | 2019-02-15 | -6 | 24 | 0 | 2018-02-15 | -3.4 | 21.4 | 0 | 2017-02-15 | -5.7 | 23.7 | 0 | 2016-02-15 | -24 | 42 | 0 | 28.85 | 0
2025-02-15 | -13.5 | 31.5 | 0 | 2024-02-15 | -10.9 | 28.9 | 0 | 2023-02-15 | -0.7 | 18.7 | 0 | 2022-02-15 | -18.2 | 36.2 | 0 | 2021-02-15 | -10.9 | 28.9 | 0 | 2020-02-15 | -15.2 | 33.2 | 0 | 2019-02-15 | -5.9 | 23.9 | 0 | 2018-02-15 | -4.5 | 22.5 | 0 | 2017-02-15 | -5.9 | 23.9 | 0 | 2016-02-15 | -24.1 | 42.1 | 0 | 28.98 | 0
2025-02-15 | -12.8 | 30.8 | 0 | 2024-02-15 | -11.9 | 29.9 | 0 | 2023-02-15 | -0.5 | 18.5 | 0 | 2022-02-15 | -17.4 | 35.4 | 0 | 2021-02-15 | -11.2 | 29.2 | 0 | 2020-02-15 | -15.3 | 33.3 | 0 | 2019-02-15 | -6.4 | 24.4 | 0 | 2018-02-15 | -2.1 | 20.1 | 0 | 2017-02-15 | -6 | 24 | 0 | 2016-02-15 | -26.1 | 44.1 | 0 | 28.97 | 0
2025-02-15 | -13 | 31 | 0 | 2024-02-15 | -11.8 | 29.8 | 0 | 2023-02-15 | -0.3 | 18.3 | 0 | 2022-02-15 | -17.2 | 35.2 | 0 | 2021-02-15 | -10.8 | 28.8 | 0 | 2020-02-15 | -15 | 33 | 0 | 2019-02-15 | -6.3 | 24.3 | 0 | 2018-02-15 | -2.1 | 20.1 | 0 | 2017-02-15 | -5.8 | 23.8 | 0 | 2016-02-15 | -24.8 | 42.8 | 0 | 28.71 | 0
2025-02-15 | -13.6 | 31.6 | 0 | 2024-02-15 | -12.8 | 30.8 | 0 | 2023-02-15 | 0.1 | 17.9 | 0 | 2022-02-15 | -16.2 | 34.2 | 0 | 2021-02-15 | -11.2 | 29.2 | 0 | 2020-02-15 | -14.6 | 32.6 | 0 | 2019-02-15 | -5.7 | 23.7 | 0 | 2018-02-15 | -0.6 | 18.6 | 0 | 2017-02-15 | -5.6 | 23.6 | 0 | 2016-02-15 | -25.4 | 43.4 | 0 | 28.56 | 0
2025-02-15 | -14.7 | 32.7 | 0 | 2024-02-15 | -13 | 31 | 0 | 2023-02-15 | -0.4 | 18.4 | 0 | 2022-02-15 | -16.3 | 34.3 | 0 | 2021-02-15 | -11 | 29 | 0 | 2020-02-15 | -14.5 | 32.5 | 0 | 2019-02-15 | -5.1 | 23.1 | 0 | 2018-02-15 | 0.3 | 17.7 | 0 | 2017-02-15 | -5.4 | 23.4 | 0 | 2016-02-15 | -25.3 | 43.3 | 0 | 28.54 | 0
2025-02-15 | -14.5 | 32.5 | 0 | 2024-02-15 | -11.6 | 29.6 | 0 | 2023-02-15 | 1 | 17 | 0 | 2022-02-15 | -15.7 | 33.7 | 0 | 2021-02-15 | -10.5 | 28.5 | 0 | 2020-02-15 | -13.9 | 31.9 | 0 | 2019-02-15 | -4.8 | 22.8 | 0 | 2018-02-15 | 0.9 | 17.1 | 0 | 2017-02-15 | -5.4 | 23.4 | 0 | 2016-02-15 | -24.3 | 42.3 | 0 | 27.88 | 0
2025-02-15 | -13 | 31 | 0 | 2024-02-15 | -9.3 | 27.3 | 0 | 2023-02-15 | 2.3 | 15.7 | 0 | 2022-02-15 | -14.9 | 32.9 | 0 | 2021-02-15 | -9.7 | 27.7 | 0 | 2020-02-15 | -12.8 | 30.8 | 0 | 2019-02-15 | -4.4 | 22.4 | 0 | 2018-02-15 | 0.9 | 17.1 | 0 | 2017-02-15 | -5.5 | 23.5 | 0 | 2016-02-15 | -21.4 | 39.4 | 0 | 26.78 | 0
2025-02-15 | -11.4 | 29.4 | 0 | 2024-02-15 | -7.4 | 25.4 | 0 | 2023-02-15 | 2.4 | 15.6 | 0 | 2022-02-15 | -13.4 | 31.4 | 0 | 2021-02-15 | -8.5 | 26.5 | 0 | 2020-02-15 | -11.2 | 29.2 | 0 | 2019-02-15 | -2.4 | 20.4 | 0 | 2018-02-15 | 1.4 | 16.6 | 0 | 2017-02-15 | -4.6 | 22.6 | 0 | 2016-02-15 | -19.1 | 37.1 | 0 | 25.42 | 0
2025-02-15 | -9.4 | 27.4 | 0 | 2024-02-15 | -6.8 | 24.8 | 0 | 2023-02-15 | 2.2 | 15.8 | 0 | 2022-02-15 | -12.5 | 30.5 | 0 | 2021-02-15 | -7.3 | 25.3 | 0 | 2020-02-15 | -8.3 | 26.3 | 0 | 2019-02-15 | -0.8 | 18.8 | 0 | 2018-02-15 | 0.7 | 17.3 | 0 | 2017-02-15 | -3.7 | 21.7 | 0 | 2016-02-15 | -16.6 | 34.6 | 0 | 24.25 | 0
2025-02-15 | -8.3 | 26.3 | 0 | 2024-02-15 | -5.8 | 23.8 | 0 | 2023-02-15 | 4 | 14 | 0 | 2022-02-15 | -11.3 | 29.3 | 0 | 2021-02-15 | -6.9 | 24.9 | 0 | 2020-02-15 | -6.9 | 24.9 | 0 | 2019-02-15 | 2.6 | 15.4 | 0 | 2018-02-15 | 3.1 | 14.9 | 0 | 2017-02-15 | -2.6 | 20.6 | 0 | 2016-02-15 | -13.5 | 31.5 | 0 | 22.56 | 0
2025-02-15 | -8.3 | 26.3 | 0 | 2024-02-15 | -5.4 | 23.4 | 0 | 2023-02-15 | 3.5 | 14.5 | 0 | 2022-02-15 | -10.1 | 28.1 | 0 | 2021-02-15 | -6.4 | 24.4 | 0 | 2020-02-15 | -6.8 | 24.8 | 0 | 2019-02-15 | 4.1 | 13.9 | 0 | 2018-02-15 | 4.9 | 13.1 | 0 | 2017-02-15 | -2.5 | 20.5 | 0 | 2016-02-15 | -11.8 | 29.8 | 0 | 21.88 | 0
2025-02-15 | -8.2 | 26.2 | 0 | 2024-02-15 | -4.6 | 22.6 | 0 | 2023-02-15 | 2.4 | 15.6 | 0 | 2022-02-15 | -9.8 | 27.8 | 0 | 2021-02-15 | -6 | 24 | 0 | 2020-02-15 | -6.6 | 24.6 | 0 | 2019-02-15 | 4.3 | 13.7 | 0 | 2018-02-15 | 5.3 | 12.7 | 0 | 2017-02-15 | -1.7 | 19.7 | 0 | 2016-02-15 | -10.3 | 28.3 | 0 | 21.52 | 0
2025-02-15 | -8.4 | 26.4 | 0 | 2024-02-15 | -4.4 | 22.4 | 0 | 2023-02-15 | 6.6 | 11.4 | 0 | 2022-02-15 | -9.5 | 27.5 | 0 | 2021-02-15 | -5.6 | 23.6 | 0 | 2020-02-15 | -6.1 | 24.1 | 0 | 2019-02-15 | 3.9 | 14.1 | 0 | 2018-02-15 | 5.3 | 12.7 | 0 | 2017-02-15 | -1.7 | 19.7 | 0 | 2016-02-15 | -9.9 | 27.9 | 0 | 20.98 | 0
2025-02-15 | -9.5 | 27.5 | 0 | 2024-02-15 | -4.8 | 22.8 | 0 | 2023-02-15 | 7.7 | 10.3 | 0 | 2022-02-15 | -9.6 | 27.6 | 0 | 2021-02-15 | -5.9 | 23.9 | 0 | 2020-02-15 | -6.4 | 24.4 | 0 | 2019-02-15 | 3.4 | 14.6 | 0 | 2018-02-15 | 5.5 | 12.5 | 0 | 2017-02-15 | -1.8 | 19.8 | 0 | 2016-02-15 | -10.1 | 28.1 | 0 | 21.15 | 0
2025-02-15 | -10.2 | 28.2 | 0 | 2024-02-15 | -5.1 | 23.1 | 0 | 2023-02-15 | 7.9 | 10.1 | 0 | 2022-02-15 | -11.2 | 29.2 | 0 | 2021-02-15 | -5.9 | 23.9 | 0 | 2020-02-15 | -6.4 | 24.4 | 0 | 2019-02-15 | 2.2 | 15.8 | 0 | 2018-02-15 | 5.2 | 12.8 | 0 | 2017-02-15 | -2.5 | 20.5 | 0 | 2016-02-15 | -10.7 | 28.7 | 0 | 21.67 | 0
2025-02-15 | -10.4 | 28.4 | 0 | 2024-02-15 | -5 | 23 | 0 | 2023-02-15 | 8.3 | 9.7 | 0 | 2022-02-15 | -11.2 | 29.2 | 0 | 2021-02-15 | -7.5 | 25.5 | 0 | 2020-02-15 | -6.2 | 24.2 | 0 | 2019-02-15 | 0.8 | 17.2 | 0 | 2018-02-15 | 4.2 | 13.8 | 0 | 2017-02-15 | -2.9 | 20.9 | 0 | 2016-02-15 | -10.9 | 28.9 | 0 | 22.08 | 0
2025-02-15 | -10.8 | 28.8 | 0 | 2024-02-15 | -6.5 | 24.5 | 0 | 2023-02-15 | 8.9 | 9.1 | 0 | 2022-02-15 | -12.2 | 30.2 | 0 | 2021-02-15 | -6.9 | 24.9 | 0 | 2020-02-15 | -6 | 24 | 0 | 2019-02-15 | 0.4 | 17.6 | 0 | 2018-02-15 | 4.5 | 13.5 | 0 | 2017-02-15 | -3.1 | 21.1 | 0 | 2016-02-15 | -10.9 | 28.9 | 0 | 22.26 | 0
2025-02-15 | -10.9 | 28.9 | 0 | 2024-02-15 | -7 | 25 | 0 | 2023-02-15 | 8.7 | 9.3 | 0 | 2022-02-15 | -18.1 | 36.1 | 0 | 2021-02-15 | -7.1 | 25.1 | 0 | 2020-02-15 | -5.7 | 23.7 | 0 | 2019-02-15 | -0.8 | 18.8 | 0 | 2018-02-15 | 3.4 | 14.6 | 0 | 2017-02-15 | -2 | 20 | 0 | 2016-02-15 | -10.9 | 28.9 | 0 | 23.04 | 0
2025-02-15 | -11.1 | 29.1 | 0 | 2024-02-15 | -7.1 | 25.1 | 0 | 2023-02-15 | 7.8 | 10.2 | 0 | 2022-02-15 | -14.4 | 32.4 | 0 | 2021-02-15 | -7 | 25 | 0 | 2020-02-15 | -4.6 | 22.6 | 0 | 2019-02-15 | -1.6 | 19.6 | 0 | 2018-02-15 | 4.5 | 13.5 | 0 | 2017-02-15 | -3.3 | 21.3 | 0 | 2016-02-15 | -11.7 | 29.7 | 0 | 22.85 | 0
2025-02-15 | -11 | 29 | 0 | 2024-02-15 | -7.1 | 25.1 | 0 | 2023-02-15 | 6.1 | 11.9 | 0 | 2022-02-15 | -14.6 | 32.6 | 0 | 2021-02-15 | -7 | 25 | 0 | 2020-02-15 | -3.9 | 21.9 | 0 | 2019-02-15 | -2.8 | 20.8 | 0 | 2018-02-15 | 4 | 14 | 0 | 2017-02-15 | -3.7 | 21.7 | 0 | 2016-02-15 | -11.5 | 29.5 | 0 | 23.15 | 0
2025-02-15 | -10.8 | 28.8 | 0 | 2024-02-15 | -7 | 25 | 0 | 2023-02-15 | 6.1 | 11.9 | 0 | 2022-02-15 | -15.2 | 33.2 | 0 | 2021-02-15 | -7.6 | 25.6 | 0 | 2020-02-15 | -3.2 | 21.2 | 0 | 2019-02-15 | -3.5 | 21.5 | 0 | 2018-02-15 | 3.6 | 14.4 | 0 | 2017-02-15 | -4.2 | 22.2 | 0 | 2016-02-15 | -11.1 | 29.1 | 0 | 23.29 | 0
2025-02-16 | -10.9 | 28.9 | 0 | 2024-02-16 | -6.8 | 24.8 | 0 | 2023-02-16 | 5.7 | 12.3 | 0 | 2022-02-16 | -15.4 | 33.4 | 0 | 2021-02-16 | -8 | 26 | 0 | 2020-02-16 | -3.5 | 21.5 | 0 | 2019-02-16 | -3.2 | 21.2 | 0 | 2018-02-16 | 3.1 | 14.9 | 0 | 2017-02-16 | -4.6 | 22.6 | 0 | 2016-02-16 | -10.9 | 28.9 | 0 | 23.45 | 0
2025-02-16 | -10.9 | 28.9 | 0 | 2024-02-16 | -6.9 | 24.9 | 0 | 2023-02-16 | 5.6 | 12.4 | 0 | 2022-02-16 | -14.6 | 32.6 | 0 | 2021-02-16 | -8.1 | 26.1 | 0 | 2020-02-16 | -3 | 21 | 0 | 2019-02-16 | -3.1 | 21.1 | 0 | 2018-02-16 | 3 | 15 | 0 | 2017-02-16 | -5.2 | 23.2 | 0 | 2016-02-16 | -10.4 | 28.4 | 0 | 23.36 | 0
2025-02-16 | -10.4 | 28.4 | 0 | 2024-02-16 | -6.9 | 24.9 | 0 | 2023-02-16 | 5.1 | 12.9 | 0 | 2022-02-16 | -14.8 | 32.8 | 0 | 2021-02-16 | -8.2 | 26.2 | 0 | 2020-02-16 | -2.6 | 20.6 | 0 | 2019-02-16 | -3.4 | 21.4 | 0 | 2018-02-16 | 2.9 | 15.1 | 0 | 2017-02-16 | -5.8 | 23.8 | 0 | 2016-02-16 | -10 | 28 | 0 | 23.41 | 0
2025-02-16 | -10.1 | 28.1 | 0 | 2024-02-16 | -6.9 | 24.9 | 0 | 2023-02-16 | 4.7 | 13.3 | 0 | 2022-02-16 | -14.7 | 32.7 | 0 | 2021-02-16 | -8.2 | 26.2 | 0 | 2020-02-16 | -1 | 19 | 0 | 2019-02-16 | -3.6 | 21.6 | 0 | 2018-02-16 | 2.6 | 15.4 | 0 | 2017-02-16 | -6.4 | 24.4 | 0 | 2016-02-16 | -9.7 | 27.7 | 0 | 23.33 | 0
2025-02-16 | -9.6 | 27.6 | 0 | 2024-02-16 | -7 | 25 | 0 | 2023-02-16 | 4 | 14 | 0 | 2022-02-16 | -14.2 | 32.2 | 0 | 2021-02-16 | -8.5 | 26.5 | 0 | 2020-02-16 | -0.7 | 18.7 | 0 | 2019-02-16 | -4 | 22 | 0 | 2018-02-16 | 1.8 | 16.2 | 0 | 2017-02-16 | -6.7 | 24.7 | 0 | 2016-02-16 | -9.3 | 27.3 | 0 | 23.42 | 0
2025-02-16 | -9.5 | 27.5 | 0 | 2024-02-16 | -7.4 | 25.4 | 0 | 2023-02-16 | 3.2 | 14.8 | 0 | 2022-02-16 | -13.1 | 31.1 | 0 | 2021-02-16 | -8.4 | 26.4 | 0 | 2020-02-16 | -0.6 | 18.6 | 0 | 2019-02-16 | -4.4 | 22.4 | 0 | 2018-02-16 | 2 | 16 | 0 | 2017-02-16 | -7.7 | 25.7 | 0 | 2016-02-16 | -8.8 | 26.8 | 0 | 23.47 | 0
2025-02-16 | -9.5 | 27.5 | 0 | 2024-02-16 | -7 | 25 | 0 | 2023-02-16 | 2.6 | 15.4 | 0 | 2022-02-16 | -12.1 | 30.1 | 0 | 2021-02-16 | -8.3 | 26.3 | 0 | 2020-02-16 | -0.6 | 18.6 | 0 | 2019-02-16 | -6.5 | 24.5 | 0 | 2018-02-16 | 2.1 | 15.9 | 0 | 2017-02-16 | -8.4 | 26.4 | 0 | 2016-02-16 | -8.4 | 26.4 | 0 | 23.61 | 0
2025-02-16 | -9.6 | 27.6 | 0 | 2024-02-16 | -7.6 | 25.6 | 0 | 2023-02-16 | 2.1 | 15.9 | 0 | 2022-02-16 | -11.1 | 29.1 | 0 | 2021-02-16 | -8.1 | 26.1 | 0 | 2020-02-16 | -0.5 | 18.5 | 0 | 2019-02-16 | -7.6 | 25.6 | 0 | 2018-02-16 | 1.4 | 16.6 | 0 | 2017-02-16 | -9 | 27 | 0 | 2016-02-16 | -7.9 | 25.9 | 0 | 23.79 | 0
2025-02-16 | -9.5 | 27.5 | 0 | 2024-02-16 | -8.1 | 26.1 | 0 | 2023-02-16 | 1.5 | 16.5 | 0 | 2022-02-16 | -9.8 | 27.8 | 0 | 2021-02-16 | -8.1 | 26.1 | 0 | 2020-02-16 | -0.4 | 18.4 | 0 | 2019-02-16 | -7.9 | 25.9 | 0 | 2018-02-16 | 0.3 | 17.7 | 0 | 2017-02-16 | -9 | 27 | 0 | 2016-02-16 | -7.3 | 25.3 | 0 | 23.83 | 0
2025-02-16 | -9.4 | 27.4 | 0 | 2024-02-16 | -6.5 | 24.5 | 0 | 2023-02-16 | 1.3 | 16.7 | 0 | 2022-02-16 | -8.2 | 26.2 | 0 | 2021-02-16 | -8.1 | 26.1 | 0 | 2020-02-16 | -0.1 | 18.1 | 0 | 2019-02-16 | -8 | 26 | 0 | 2018-02-16 | -1.6 | 19.6 | 0 | 2017-02-16 | -9 | 27 | 0 | 2016-02-16 | -6.5 | 24.5 | 0 | 23.61 | 0
2025-02-16 | -9.1 | 27.1 | 0 | 2024-02-16 | -5.8 | 23.8 | 0 | 2023-02-16 | 1.4 | 16.6 | 0 | 2022-02-16 | -6.2 | 24.2 | 0 | 2021-02-16 | -8.5 | 26.5 | 0 | 2020-02-16 | 0.6 | 17.4 | 0 | 2019-02-16 | -7.3 | 25.3 | 0 | 2018-02-16 | -2.7 | 20.7 | 0 | 2017-02-16 | -8.4 | 26.4 | 0 | 2016-02-16 | -5.8 | 23.8 | 0 | 23.18 | 0
2025-02-16 | -8.9 | 26.9 | 0 | 2024-02-16 | -4.4 | 22.4 | 0 | 2023-02-16 | 0.6 | 17.4 | 0 | 2022-02-16 | -4.2 | 22.2 | 0 | 2021-02-16 | -9.2 | 27.2 | 0 | 2020-02-16 | 1.8 | 16.2 | 0 | 2019-02-16 | -6.6 | 24.6 | 0 | 2018-02-16 | -4.2 | 22.2 | 0 | 2017-02-16 | -7.7 | 25.7 | 0 | 2016-02-16 | -5.6 | 23.6 | 0 | 22.84 | 0
2025-02-16 | -8.3 | 26.3 | 0 | 2024-02-16 | -3.5 | 21.5 | 0 | 2023-02-16 | 0.7 | 17.3 | 0 | 2022-02-16 | 1.8 | 16.2 | 0 | 2021-02-16 | -10.2 | 28.2 | 0 | 2020-02-16 | 2.6 | 15.4 | 0 | 2019-02-16 | -6.1 | 24.1 | 0 | 2018-02-16 | -3.7 | 21.7 | 0 | 2017-02-16 | -6.6 | 24.6 | 0 | 2016-02-16 | -5 | 23 | 0 | 21.83 | 0
2025-02-16 | -8.4 | 26.4 | 0 | 2024-02-16 | -2.5 | 20.5 | 0 | 2023-02-16 | 0.6 | 17.4 | 0 | 2022-02-16 | 3.7 | 14.3 | 0 | 2021-02-16 | -10.9 | 28.9 | 0 | 2020-02-16 | 3.4 | 14.6 | 0 | 2019-02-16 | -5.5 | 23.5 | 0 | 2018-02-16 | -3 | 21 | 0 | 2017-02-16 | -5.5 | 23.5 | 0 | 2016-02-16 | -4.3 | 22.3 | 0 | 21.24 | 0
2025-02-16 | -8.6 | 26.6 | 0 | 2024-02-16 | -2.8 | 20.8 | 0 | 2023-02-16 | 0.3 | 17.7 | 0 | 2022-02-16 | 5.7 | 12.3 | 0 | 2021-02-16 | -11 | 29 | 0 | 2020-02-16 | 3 | 15 | 0 | 2019-02-16 | -5.2 | 23.2 | 0 | 2018-02-16 | -2.7 | 20.7 | 0 | 2017-02-16 | -4.6 | 22.6 | 0 | 2016-02-16 | -4.3 | 22.3 | 0 | 21.02 | 0
2025-02-16 | -8.9 | 26.9 | 0 | 2024-02-16 | -3.4 | 21.4 | 0 | 2023-02-16 | 0.2 | 17.8 | 0 | 2022-02-16 | 6.3 | 11.7 | 0 | 2021-02-16 | -10.9 | 28.9 | 0 | 2020-02-16 | 2.8 | 15.2 | 0 | 2019-02-16 | -5.3 | 23.3 | 0 | 2018-02-16 | -2.2 | 20.2 | 0 | 2017-02-16 | -4.8 | 22.8 | 0 | 2016-02-16 | -4.5 | 22.5 | 0 | 21.07 | 0
2025-02-16 | -8.9 | 26.9 | 0 | 2024-02-16 | -4.1 | 22.1 | 0 | 2023-02-16 | 0.3 | 17.7 | 0 | 2022-02-16 | 6 | 12 | 0 | 2021-02-16 | -11.2 | 29.2 | 0 | 2020-02-16 | 2.5 | 15.5 | 0 | 2019-02-16 | -5.7 | 23.7 | 0 | 2018-02-16 | -2.4 | 20.4 | 0 | 2017-02-16 | -4.8 | 22.8 | 0 | 2016-02-16 | -4.3 | 22.3 | 0 | 21.26 | 0
2025-02-16 | -8.9 | 26.9 | 0 | 2024-02-16 | -4.3 | 22.3 | 0 | 2023-02-16 | 0.6 | 17.4 | 0 | 2022-02-16 | 5.5 | 12.5 | 0 | 2021-02-16 | -11.2 | 29.2 | 0 | 2020-02-16 | 1.9 | 16.1 | 0 | 2019-02-16 | -6.2 | 24.2 | 0 | 2018-02-16 | -3.6 | 21.6 | 0 | 2017-02-16 | -4.5 | 22.5 | 0 | 2016-02-16 | -4.3 | 22.3 | 0 | 21.5 | 0
2025-02-16 | -8.7 | 26.7 | 0 | 2024-02-16 | -5.3 | 23.3 | 0 | 2023-02-16 | 0.4 | 17.6 | 0 | 2022-02-16 | 5.7 | 12.3 | 0 | 2021-02-16 | -11 | 29 | 0 | 2020-02-16 | 1.4 | 16.6 | 0 | 2019-02-16 | -7.4 | 25.4 | 0 | 2018-02-16 | -4.8 | 22.8 | 0 | 2017-02-16 | -4.6 | 22.6 | 0 | 2016-02-16 | -4.2 | 22.2 | 0 | 21.85 | 0
2025-02-16 | -9.8 | 27.8 | 0 | 2024-02-16 | -6.5 | 24.5 | 0 | 2023-02-16 | 0.1 | 17.9 | 0 | 2022-02-16 | 5.7 | 12.3 | 0 | 2021-02-16 | -10.8 | 28.8 | 0 | 2020-02-16 | 1.4 | 16.6 | 0 | 2019-02-16 | -8.2 | 26.2 | 0 | 2018-02-16 | -5.8 | 23.8 | 0 | 2017-02-16 | -5.1 | 23.1 | 0 | 2016-02-16 | -4.2 | 22.2 | 0 | 22.32 | 0
2025-02-16 | -11.3 | 29.3 | 0 | 2024-02-16 | -9 | 27 | 0 | 2023-02-16 | -0.5 | 18.5 | 0 | 2022-02-16 | 5.8 | 12.2 | 0 | 2021-02-16 | -11.2 | 29.2 | 0 | 2020-02-16 | 0.1 | 17.9 | 0 | 2019-02-16 | -9.4 | 27.4 | 0 | 2018-02-16 | -7 | 25 | 0 | 2017-02-16 | -5.2 | 23.2 | 0 | 2016-02-16 | -4.3 | 22.3 | 0 | 23.2 | 0
2025-02-16 | -11.4 | 29.4 | 0 | 2024-02-16 | -7.6 | 25.6 | 0 | 2023-02-16 | -0.7 | 18.7 | 0 | 2022-02-16 | 5.8 | 12.2 | 0 | 2021-02-16 | -11.7 | 29.7 | 0 | 2020-02-16 | -0.4 | 18.4 | 0 | 2019-02-16 | -11.3 | 29.3 | 0 | 2018-02-16 | -7.1 | 25.1 | 0 | 2017-02-16 | -5.3 | 23.3 | 0 | 2016-02-16 | -4.2 | 22.2 | 0 | 23.39 | 0
2025-02-16 | -11.6 | 29.6 | 0 | 2024-02-16 | -7.9 | 25.9 | 0 | 2023-02-16 | -1.2 | 19.2 | 0 | 2022-02-16 | 5.8 | 12.2 | 0 | 2021-02-16 | -12 | 30 | 0 | 2020-02-16 | -1.9 | 19.9 | 0 | 2019-02-16 | -9.8 | 27.8 | 0 | 2018-02-16 | -7.9 | 25.9 | 0 | 2017-02-16 | -5.3 | 23.3 | 0 | 2016-02-16 | -4 | 22 | 0 | 23.58 | 0
2025-02-16 | -11.7 | 29.7 | 0 | 2024-02-16 | -9.1 | 27.1 | 0 | 2023-02-16 | -2 | 20 | 0 | 2022-02-16 | 5.6 | 12.4 | 0 | 2021-02-16 | -13.2 | 31.2 | 0 | 2020-02-16 | -3.2 | 21.2 | 0 | 2019-02-16 | -10.6 | 28.6 | 0 | 2018-02-16 | -9.9 | 27.9 | 0 | 2017-02-16 | -6.3 | 24.3 | 0 | 2016-02-16 | -4.1 | 22.1 | 0 | 24.45 | 0
2025-02-17 | -11.8 | 29.8 | 0 | 2024-02-17 | -9.7 | 27.7 | 0 | 2023-02-17 | -2.9 | 20.9 | 0 | 2022-02-17 | 5.6 | 12.4 | 0 | 2021-02-17 | -14.2 | 32.2 | 0 | 2020-02-17 | -4.7 | 22.7 | 0 | 2019-02-17 | -11.9 | 29.9 | 0 | 2018-02-17 | -10.3 | 28.3 | 0 | 2017-02-17 | -6.9 | 24.9 | 0 | 2016-02-17 | -5.3 | 23.3 | 0 | 25.21 | 0
2025-02-17 | -12.7 | 30.7 | 0 | 2024-02-17 | -10 | 28 | 0 | 2023-02-17 | -3.3 | 21.3 | 0 | 2022-02-17 | 5.7 | 12.3 | 0 | 2021-02-17 | -15 | 33 | 0 | 2020-02-17 | -5.4 | 23.4 | 0 | 2019-02-17 | -14.4 | 32.4 | 0 | 2018-02-17 | -11.2 | 29.2 | 0 | 2017-02-17 | -8 | 26 | 0 | 2016-02-17 | -5.7 | 23.7 | 0 | 26 | 0
2025-02-17 | -13.2 | 31.2 | 0 | 2024-02-17 | -10.6 | 28.6 | 0 | 2023-02-17 | -3.7 | 21.7 | 0 | 2022-02-17 | 5.5 | 12.5 | 0 | 2021-02-17 | -15.7 | 33.7 | 0 | 2020-02-17 | -6.5 | 24.5 | 0 | 2019-02-17 | -16 | 34 | 0 | 2018-02-17 | -11.4 | 29.4 | 0 | 2017-02-17 | -8.5 | 26.5 | 0 | 2016-02-17 | -5.2 | 23.2 | 0 | 26.53 | 0
2025-02-17 | -13.5 | 31.5 | 0 | 2024-02-17 | -10.6 | 28.6 | 0 | 2023-02-17 | -3.8 | 21.8 | 0 | 2022-02-17 | 5.5 | 12.5 | 0 | 2021-02-17 | -15.9 | 33.9 | 0 | 2020-02-17 | -7.2 | 25.2 | 0 | 2019-02-17 | -15.5 | 33.5 | 0 | 2018-02-17 | -12.5 | 30.5 | 0 | 2017-02-17 | -8.8 | 26.8 | 0 | 2016-02-17 | -7.2 | 25.2 | 0 | 26.95 | 0
2025-02-17 | -14.5 | 32.5 | 0 | 2024-02-17 | -11.2 | 29.2 | 0 | 2023-02-17 | -4 | 22 | 0 | 2022-02-17 | 4.7 | 13.3 | 0 | 2021-02-17 | -17.3 | 35.3 | 0 | 2020-02-17 | -8.4 | 26.4 | 0 | 2019-02-17 | -15.3 | 33.3 | 0 | 2018-02-17 | -12 | 30 | 0 | 2017-02-17 | -8.8 | 26.8 | 0 | 2016-02-17 | -6.6 | 24.6 | 0 | 27.34 | 0
2025-02-17 | -15.1 | 33.1 | 0 | 2024-02-17 | -11.8 | 29.8 | 0 | 2023-02-17 | -4.7 | 22.7 | 0 | 2022-02-17 | 4.4 | 13.6 | 0 | 2021-02-17 | -18.5 | 36.5 | 0 | 2020-02-17 | -9.2 | 27.2 | 0 | 2019-02-17 | -16.2 | 34.2 | 0 | 2018-02-17 | -12.7 | 30.7 | 0 | 2017-02-17 | -9.2 | 27.2 | 0 | 2016-02-17 | -6.9 | 24.9 | 0 | 27.99 | 0
2025-02-17 | -15.5 | 33.5 | 0 | 2024-02-17 | -12.4 | 30.4 | 0 | 2023-02-17 | -6 | 24 | 0 | 2022-02-17 | 4.8 | 13.2 | 0 | 2021-02-17 | -19.8 | 37.8 | 0 | 2020-02-17 | -10.3 | 28.3 | 0 | 2019-02-17 | -16.9 | 34.9 | 0 | 2018-02-17 | -13.1 | 31.1 | 0 | 2017-02-17 | -11.4 | 29.4 | 0 | 2016-02-17 | -8.2 | 26.2 | 0 | 28.88 | 0
2025-02-17 | -16 | 34 | 0 | 2024-02-17 | -14 | 32 | 0 | 2023-02-17 | -6.8 | 24.8 | 0 | 2022-02-17 | 4.3 | 13.7 | 0 | 2021-02-17 | -20.3 | 38.3 | 0 | 2020-02-17 | -11 | 29 | 0 | 2019-02-17 | -18.4 | 36.4 | 0 | 2018-02-17 | -14.2 | 32.2 | 0 | 2017-02-17 | -12.8 | 30.8 | 0 | 2016-02-17 | -8.1 | 26.1 | 0 | 29.73 | 0
2025-02-17 | -16.1 | 34.1 | 0 | 2024-02-17 | -14 | 32 | 0 | 2023-02-17 | -7.5 | 25.5 | 0 | 2022-02-17 | 4.1 | 13.9 | 0 | 2021-02-17 | -19.5 | 37.5 | 0 | 2020-02-17 | -11.3 | 29.3 | 0 | 2019-02-17 | -18.8 | 36.8 | 0 | 2018-02-17 | -12.8 | 30.8 | 0 | 2017-02-17 | -12.7 | 30.7 | 0 | 2016-02-17 | -9.5 | 27.5 | 0 | 29.81 | 0
2025-02-17 | -15.8 | 33.8 | 0 | 2024-02-17 | -13 | 31 | 0 | 2023-02-17 | -7.6 | 25.6 | 0 | 2022-02-17 | 4.1 | 13.9 | 0 | 2021-02-17 | -17.2 | 35.2 | 0 | 2020-02-17 | -10.4 | 28.4 | 0 | 2019-02-17 | -15.5 | 33.5 | 0 | 2018-02-17 | -9.8 | 27.8 | 0 | 2017-02-17 | -10.8 | 28.8 | 0 | 2016-02-17 | -7.2 | 25.2 | 0 | 28.32 | 0
2025-02-17 | -15.2 | 33.2 | 0 | 2024-02-17 | -11.3 | 29.3 | 0 | 2023-02-17 | -8.3 | 26.3 | 0 | 2022-02-17 | 4.4 | 13.6 | 0 | 2021-02-17 | -15.3 | 33.3 | 0 | 2020-02-17 | -9.6 | 27.6 | 0 | 2019-02-17 | -13.4 | 31.4 | 0 | 2018-02-17 | -6.6 | 24.6 | 0 | 2017-02-17 | -9.2 | 27.2 | 0 | 2016-02-17 | -4.7 | 22.7 | 0 | 26.92 | 0
2025-02-17 | -14.6 | 32.6 | 0 | 2024-02-17 | -10.9 | 28.9 | 0 | 2023-02-17 | -9.4 | 27.4 | 0 | 2022-02-17 | 4.9 | 13.1 | 0 | 2021-02-17 | -12.7 | 30.7 | 0 | 2020-02-17 | -9.1 | 27.1 | 0 | 2019-02-17 | -11.7 | 29.7 | 0 | 2018-02-17 | -4.5 | 22.5 | 0 | 2017-02-17 | -7.7 | 25.7 | 0 | 2016-02-17 | -2.9 | 20.9 | 0 | 25.86 | 0
2025-02-17 | -13 | 31 | 0 | 2024-02-17 | -10.1 | 28.1 | 0 | 2023-02-17 | -9.3 | 27.3 | 0 | 2022-02-17 | 4.8 | 13.2 | 0 | 2021-02-17 | -10.8 | 28.8 | 0 | 2020-02-17 | -8.4 | 26.4 | 0 | 2019-02-17 | -11 | 29 | 0 | 2018-02-17 | -3.4 | 21.4 | 0 | 2017-02-17 | -6.5 | 24.5 | 0 | 2016-02-17 | -1 | 19 | 0 | 24.87 | 0
2025-02-17 | -11.4 | 29.4 | 0 | 2024-02-17 | -9.1 | 27.1 | 0 | 2023-02-17 | -8.7 | 26.7 | 0 | 2022-02-17 | 4.8 | 13.2 | 0 | 2021-02-17 | -9.1 | 27.1 | 0 | 2020-02-17 | -7.7 | 25.7 | 0 | 2019-02-17 | -9.9 | 27.9 | 0 | 2018-02-17 | -2.4 | 20.4 | 0 | 2017-02-17 | -4.9 | 22.9 | 0 | 2016-02-17 | 0.1 | 17.9 | 0 | 23.83 | 0
2025-02-17 | -10.4 | 28.4 | 0 | 2024-02-17 | -9.1 | 27.1 | 0 | 2023-02-17 | -7.2 | 25.2 | 0 | 2022-02-17 | 4.1 | 13.9 | 0 | 2021-02-17 | -8.2 | 26.2 | 0 | 2020-02-17 | -7.3 | 25.3 | 0 | 2019-02-17 | -9.7 | 27.7 | 0 | 2018-02-17 | -2.5 | 20.5 | 0 | 2017-02-17 | -4.5 | 22.5 | 0 | 2016-02-17 | 0 | 18 | 0 | 23.48 | 0
2025-02-17 | -9.7 | 27.7 | 0 | 2024-02-17 | -8.9 | 26.9 | 0 | 2023-02-17 | -7.3 | 25.3 | 0 | 2022-02-17 | 3.5 | 14.5 | 0 | 2021-02-17 | -7.3 | 25.3 | 0 | 2020-02-17 | -6.9 | 24.9 | 0 | 2019-02-17 | -9.4 | 27.4 | 0 | 2018-02-17 | -2.3 | 20.3 | 0 | 2017-02-17 | -3.9 | 21.9 | 0 | 2016-02-17 | -1.8 | 19.8 | 0 | 23.4 | 0
2025-02-17 | -9.7 | 27.7 | 0 | 2024-02-17 | -9 | 27 | 0 | 2023-02-17 | -7.3 | 25.3 | 0 | 2022-02-17 | 2.8 | 15.2 | 0 | 2021-02-17 | -7.4 | 25.4 | 0 | 2020-02-17 | -7 | 25 | 0 | 2019-02-17 | -9.4 | 27.4 | 0 | 2018-02-17 | -2.4 | 20.4 | 0 | 2017-02-17 | -3.2 | 21.2 | 0 | 2016-02-17 | -1.1 | 19.1 | 0 | 23.37 | 0
2025-02-17 | -10.1 | 28.1 | 0 | 2024-02-17 | -9.4 | 27.4 | 0 | 2023-02-17 | -7.9 | 25.9 | 0 | 2022-02-17 | 0.9 | 17.1 | 0 | 2021-02-17 | -7.6 | 25.6 | 0 | 2020-02-17 | -7.7 | 25.7 | 0 | 2019-02-17 | -9.5 | 27.5 | 0 | 2018-02-17 | -2.6 | 20.6 | 0 | 2017-02-17 | -3.8 | 21.8 | 0 | 2016-02-17 | -5.7 | 23.7 | 0 | 24.34 | 0
2025-02-17 | -10.8 | 28.8 | 0 | 2024-02-17 | -10.6 | 28.6 | 0 | 2023-02-17 | -8.4 | 26.4 | 0 | 2022-02-17 | -0.2 | 18.2 | 0 | 2021-02-17 | -8.9 | 26.9 | 0 | 2020-02-17 | -8.6 | 26.6 | 0 | 2019-02-17 | -10.9 | 28.9 | 0 | 2018-02-17 | -2.8 | 20.8 | 0 | 2017-02-17 | -4.1 | 22.1 | 0 | 2016-02-17 | -6.7 | 24.7 | 0 | 25.2 | 0
2025-02-17 | -11.7 | 29.7 | 0 | 2024-02-17 | -11.8 | 29.8 | 0 | 2023-02-17 | -8.8 | 26.8 | 0 | 2022-02-17 | -2 | 20 | 0 | 2021-02-17 | -10.1 | 28.1 | 0 | 2020-02-17 | -9.8 | 27.8 | 0 | 2019-02-17 | -10.8 | 28.8 | 0 | 2018-02-17 | -3.3 | 21.3 | 0 | 2017-02-17 | -5.1 | 23.1 | 0 | 2016-02-17 | -9 | 27 | 0 | 26.24 | 0
2025-02-17 | -11.4 | 29.4 | 0 | 2024-02-17 | -13.3 | 31.3 | 0 | 2023-02-17 | -9.3 | 27.3 | 0 | 2022-02-17 | -2.8 | 20.8 | 0 | 2021-02-17 | -10.4 | 28.4 | 0 | 2020-02-17 | -12.1 | 30.1 | 0 | 2019-02-17 | -12.1 | 30.1 | 0 | 2018-02-17 | -3.4 | 21.4 | 0 | 2017-02-17 | -4.3 | 22.3 | 0 | 2016-02-17 | -10.5 | 28.5 | 0 | 26.96 | 0
2025-02-17 | -12.4 | 30.4 | 0 | 2024-02-17 | -13.2 | 31.2 | 0 | 2023-02-17 | -10.2 | 28.2 | 0 | 2022-02-17 | -3.2 | 21.2 | 0 | 2021-02-17 | -10.6 | 28.6 | 0 | 2020-02-17 | -11.3 | 29.3 | 0 | 2019-02-17 | -12.6 | 30.6 | 0 | 2018-02-17 | -3.6 | 21.6 | 0 | 2017-02-17 | -4.1 | 22.1 | 0 | 2016-02-17 | -10.7 | 28.7 | 0 | 27.19 | 0
2025-02-17 | -12.9 | 30.9 | 0 | 2024-02-17 | -15 | 33 | 0 | 2023-02-17 | -10.7 | 28.7 | 0 | 2022-02-17 | -3.9 | 21.9 | 0 | 2021-02-17 | -14.6 | 32.6 | 0 | 2020-02-17 | -11.3 | 29.3 | 0 | 2019-02-17 | -13.3 | 31.3 | 0 | 2018-02-17 | -5 | 23 | 0 | 2017-02-17 | -3.8 | 21.8 | 0 | 2016-02-17 | -11.6 | 29.6 | 0 | 28.21 | 0
2025-02-17 | -13.5 | 31.5 | 0 | 2024-02-17 | -15.7 | 33.7 | 0 | 2023-02-17 | -12.8 | 30.8 | 0 | 2022-02-17 | -4.5 | 22.5 | 0 | 2021-02-17 | -11.9 | 29.9 | 0 | 2020-02-17 | -13.7 | 31.7 | 0 | 2019-02-17 | -13.4 | 31.4 | 0 | 2018-02-17 | -4.5 | 22.5 | 0 | 2017-02-17 | -4.3 | 22.3 | 0 | 2016-02-17 | -12.7 | 30.7 | 0 | 28.7 | 0
2025-02-18 | -14.1 | 32.1 | 0 | 2024-02-18 | -14.7 | 32.7 | 0 | 2023-02-18 | -15.8 | 33.8 | 0 | 2022-02-18 | -5.4 | 23.4 | 0 | 2021-02-18 | -13.3 | 31.3 | 0 | 2020-02-18 | -13.2 | 31.2 | 0 | 2019-02-18 | -13.4 | 31.4 | 0 | 2018-02-18 | -4.3 | 22.3 | 0 | 2017-02-18 | -4.7 | 22.7 | 0 | 2016-02-18 | -14 | 32 | 0 | 29.29 | 0
2025-02-18 | -14.9 | 32.9 | 0 | 2024-02-18 | -14.3 | 32.3 | 0 | 2023-02-18 | -14.6 | 32.6 | 0 | 2022-02-18 | -6.7 | 24.7 | 0 | 2021-02-18 | -14 | 32 | 0 | 2020-02-18 | -13.1 | 31.1 | 0 | 2019-02-18 | -13.2 | 31.2 | 0 | 2018-02-18 | -4.8 | 22.8 | 0 | 2017-02-18 | -4.8 | 22.8 | 0 | 2016-02-18 | -14.6 | 32.6 | 0 | 29.5 | 0
2025-02-18 | -15.7 | 33.7 | 0 | 2024-02-18 | -13.9 | 31.9 | 0 | 2023-02-18 | -16.4 | 34.4 | 0 | 2022-02-18 | -8.1 | 26.1 | 0 | 2021-02-18 | -14 | 32 | 0 | 2020-02-18 | -13.5 | 31.5 | 0 | 2019-02-18 | -12.6 | 30.6 | 0 | 2018-02-18 | -5.1 | 23.1 | 0 | 2017-02-18 | -5.6 | 23.6 | 0 | 2016-02-18 | -15.6 | 33.6 | 0 | 30.05 | 0
2025-02-18 | -16.4 | 34.4 | 0 | 2024-02-18 | -13.2 | 31.2 | 0 | 2023-02-18 | -15.6 | 33.6 | 0 | 2022-02-18 | -9.3 | 27.3 | 0 | 2021-02-18 | -14.2 | 32.2 | 0 | 2020-02-18 | -12.8 | 30.8 | 0 | 2019-02-18 | -12.5 | 30.5 | 0 | 2018-02-18 | -5 | 23 | 0 | 2017-02-18 | -6.2 | 24.2 | 0 | 2016-02-18 | -16.5 | 34.5 | 0 | 30.17 | 0
2025-02-18 | -16.8 | 34.8 | 0 | 2024-02-18 | -11.4 | 29.4 | 0 | 2023-02-18 | -16.1 | 34.1 | 0 | 2022-02-18 | -10.1 | 28.1 | 0 | 2021-02-18 | -14.1 | 32.1 | 0 | 2020-02-18 | -12.5 | 30.5 | 0 | 2019-02-18 | -11.9 | 29.9 | 0 | 2018-02-18 | -5.5 | 23.5 | 0 | 2017-02-18 | -5.4 | 23.4 | 0 | 2016-02-18 | -17.8 | 35.8 | 0 | 30.16 | 0
2025-02-18 | -16.8 | 34.8 | 0 | 2024-02-18 | -10.2 | 28.2 | 0 | 2023-02-18 | -15.8 | 33.8 | 0 | 2022-02-18 | -11.4 | 29.4 | 0 | 2021-02-18 | -14.9 | 32.9 | 0 | 2020-02-18 | -11.9 | 29.9 | 0 | 2019-02-18 | -11.9 | 29.9 | 0 | 2018-02-18 | -6 | 24 | 0 | 2017-02-18 | -5.8 | 23.8 | 0 | 2016-02-18 | -19.8 | 37.8 | 0 | 30.45 | 0
2025-02-18 | -17 | 35 | 0 | 2024-02-18 | -9.5 | 27.5 | 0 | 2023-02-18 | -15.9 | 33.9 | 0 | 2022-02-18 | -11.9 | 29.9 | 0 | 2021-02-18 | -15.9 | 33.9 | 0 | 2020-02-18 | -11.4 | 29.4 | 0 | 2019-02-18 | -11.9 | 29.9 | 0 | 2018-02-18 | -6.3 | 24.3 | 0 | 2017-02-18 | -7.5 | 25.5 | 0 | 2016-02-18 | -18.8 | 36.8 | 0 | 30.61 | 0
2025-02-18 | -17.7 | 35.7 | 0 | 2024-02-18 | -8.4 | 26.4 | 0 | 2023-02-18 | -14.2 | 32.2 | 0 | 2022-02-18 | -12.4 | 30.4 | 0 | 2021-02-18 | -17.1 | 35.1 | 0 | 2020-02-18 | -11.5 | 29.5 | 0 | 2019-02-18 | -11.9 | 29.9 | 0 | 2018-02-18 | -6.6 | 24.6 | 0 | 2017-02-18 | -8.2 | 26.2 | 0 | 2016-02-18 | -19.6 | 37.6 | 0 | 30.76 | 0
2025-02-18 | -17.4 | 35.4 | 0 | 2024-02-18 | -8.2 | 26.2 | 0 | 2023-02-18 | -12.1 | 30.1 | 0 | 2022-02-18 | -13.2 | 31.2 | 0 | 2021-02-18 | -16.9 | 34.9 | 0 | 2020-02-18 | -11.3 | 29.3 | 0 | 2019-02-18 | -11.8 | 29.8 | 0 | 2018-02-18 | -6.1 | 24.1 | 0 | 2017-02-18 | -7.1 | 25.1 | 0 | 2016-02-18 | -19.6 | 37.6 | 0 | 30.37 | 0
2025-02-18 | -16.6 | 34.6 | 0 | 2024-02-18 | -7 | 25 | 0 | 2023-02-18 | -9.5 | 27.5 | 0 | 2022-02-18 | -13.9 | 31.9 | 0 | 2021-02-18 | -14.5 | 32.5 | 0 | 2020-02-18 | -11.2 | 29.2 | 0 | 2019-02-18 | -11.1 | 29.1 | 0 | 2018-02-18 | -4.2 | 22.2 | 0 | 2017-02-18 | -5.1 | 23.1 | 0 | 2016-02-18 | -17.5 | 35.5 | 0 | 29.06 | 0
2025-02-18 | -16.1 | 34.1 | 0 | 2024-02-18 | -5 | 23 | 0 | 2023-02-18 | -7 | 25 | 0 | 2022-02-18 | -13.8 | 31.8 | 0 | 2021-02-18 | -10.9 | 28.9 | 0 | 2020-02-18 | -10.4 | 28.4 | 0 | 2019-02-18 | -10.3 | 28.3 | 0 | 2018-02-18 | -2.2 | 20.2 | 0 | 2017-02-18 | -2.3 | 20.3 | 0 | 2016-02-18 | -15.6 | 33.6 | 0 | 27.36 | 0
2025-02-18 | -15.3 | 33.3 | 0 | 2024-02-18 | -3.5 | 21.5 | 0 | 2023-02-18 | -4.1 | 22.1 | 0 | 2022-02-18 | -13.7 | 31.7 | 0 | 2021-02-18 | -7.8 | 25.8 | 0 | 2020-02-18 | -9.5 | 27.5 | 0 | 2019-02-18 | -10 | 28 | 0 | 2018-02-18 | -0.1 | 18.1 | 0 | 2017-02-18 | 0.3 | 17.7 | 0 | 2016-02-18 | -13.9 | 31.9 | 0 | 25.76 | 0
2025-02-18 | -14.8 | 32.8 | 0 | 2024-02-18 | -3.9 | 21.9 | 0 | 2023-02-18 | -3.2 | 21.2 | 0 | 2022-02-18 | -13.5 | 31.5 | 0 | 2021-02-18 | -6.2 | 24.2 | 0 | 2020-02-18 | -8.2 | 26.2 | 0 | 2019-02-18 | -9.4 | 27.4 | 0 | 2018-02-18 | 0.9 | 17.1 | 0 | 2017-02-18 | 4 | 14 | 0 | 2016-02-18 | -11.8 | 29.8 | 0 | 24.61 | 0
2025-02-18 | -14.3 | 32.3 | 0 | 2024-02-18 | -3.4 | 21.4 | 0 | 2023-02-18 | -2.2 | 20.2 | 0 | 2022-02-18 | -12.7 | 30.7 | 0 | 2021-02-18 | -4.7 | 22.7 | 0 | 2020-02-18 | -6.8 | 24.8 | 0 | 2019-02-18 | -8 | 26 | 0 | 2018-02-18 | 1.5 | 16.5 | 0 | 2017-02-18 | 6.3 | 11.7 | 0 | 2016-02-18 | -10.8 | 28.8 | 0 | 23.51 | 0
2025-02-18 | -14.1 | 32.1 | 0 | 2024-02-18 | -2.8 | 20.8 | 0 | 2023-02-18 | -1.8 | 19.8 | 0 | 2022-02-18 | -12.8 | 30.8 | 0 | 2021-02-18 | -5 | 23 | 0 | 2020-02-18 | -5 | 23 | 0 | 2019-02-18 | -7.8 | 25.8 | 0 | 2018-02-18 | 1.9 | 16.1 | 0 | 2017-02-18 | 7.7 | 10.3 | 0 | 2016-02-18 | -9.8 | 27.8 | 0 | 22.95 | 0
2025-02-18 | -14.1 | 32.1 | 0 | 2024-02-18 | -2.5 | 20.5 | 0 | 2023-02-18 | -1 | 19 | 0 | 2022-02-18 | -12.5 | 30.5 | 0 | 2021-02-18 | -5 | 23 | 0 | 2020-02-18 | -2.7 | 20.7 | 0 | 2019-02-18 | -7.6 | 25.6 | 0 | 2018-02-18 | 1.9 | 16.1 | 0 | 2017-02-18 | 8.3 | 9.7 | 0 | 2016-02-18 | -9.4 | 27.4 | 0 | 22.46 | 0
2025-02-18 | -13.9 | 31.9 | 0 | 2024-02-18 | -1.9 | 19.9 | 0 | 2023-02-18 | -1.2 | 19.2 | 0 | 2022-02-18 | -12.7 | 30.7 | 0 | 2021-02-18 | -5.6 | 23.6 | 0 | 2020-02-18 | 2.9 | 15.1 | 0 | 2019-02-18 | -7.6 | 25.6 | 0 | 2018-02-18 | 2.4 | 15.6 | 0 | 2017-02-18 | 9.1 | 8.9 | 0 | 2016-02-18 | -8.8 | 26.8 | 0 | 21.73 | 0
2025-02-18 | -14.5 | 32.5 | 0 | 2024-02-18 | -2.1 | 20.1 | 0 | 2023-02-18 | -1.4 | 19.4 | 0 | 2022-02-18 | -12.5 | 30.5 | 0 | 2021-02-18 | -5.6 | 23.6 | 0 | 2020-02-18 | 3.8 | 14.2 | 0 | 2019-02-18 | -7.9 | 25.9 | 0 | 2018-02-18 | 1.8 | 16.2 | 0 | 2017-02-18 | 8.5 | 9.5 | 0 | 2016-02-18 | -8.8 | 26.8 | 0 | 21.87 | 0
2025-02-18 | -14.7 | 32.7 | 0 | 2024-02-18 | -2 | 20 | 0 | 2023-02-18 | -1.4 | 19.4 | 0 | 2022-02-18 | -13.8 | 31.8 | 0 | 2021-02-18 | -6.6 | 24.6 | 0 | 2020-02-18 | 3.6 | 14.4 | 0 | 2019-02-18 | -9.5 | 27.5 | 0 | 2018-02-18 | 1 | 17 | 0 | 2017-02-18 | 7.2 | 10.8 | 0 | 2016-02-18 | -10.3 | 28.3 | 0 | 22.65 | 0
2025-02-18 | -15 | 33 | 0 | 2024-02-18 | -3.2 | 21.2 | 0 | 2023-02-18 | -1.4 | 19.4 | 0 | 2022-02-18 | -16.1 | 34.1 | 0 | 2021-02-18 | -7.3 | 25.3 | 0 | 2020-02-18 | 4.1 | 13.9 | 0 | 2019-02-18 | -9.7 | 27.7 | 0 | 2018-02-18 | 0.1 | 17.9 | 0 | 2017-02-18 | 6.7 | 11.3 | 0 | 2016-02-18 | -11.7 | 29.7 | 0 | 23.35 | 0
2025-02-18 | -15.2 | 33.2 | 0 | 2024-02-18 | -3.3 | 21.3 | 0 | 2023-02-18 | -1 | 19 | 0 | 2022-02-18 | -17.1 | 35.1 | 0 | 2021-02-18 | -8.4 | 26.4 | 0 | 2020-02-18 | 3.5 | 14.5 | 0 | 2019-02-18 | -11.2 | 29.2 | 0 | 2018-02-18 | -0.6 | 18.6 | 0 | 2017-02-18 | 5.7 | 12.3 | 0 | 2016-02-18 | -12.6 | 30.6 | 0 | 24.02 | 0
2025-02-18 | -15.2 | 33.2 | 0 | 2024-02-18 | -5.7 | 23.7 | 0 | 2023-02-18 | -0.7 | 18.7 | 0 | 2022-02-18 | -16.9 | 34.9 | 0 | 2021-02-18 | -8.1 | 26.1 | 0 | 2020-02-18 | 2.7 | 15.3 | 0 | 2019-02-18 | -11.4 | 29.4 | 0 | 2018-02-18 | -1 | 19 | 0 | 2017-02-18 | 5.5 | 12.5 | 0 | 2016-02-18 | -13.1 | 31.1 | 0 | 24.39 | 0
2025-02-18 | -15.4 | 33.4 | 0 | 2024-02-18 | -5.3 | 23.3 | 0 | 2023-02-18 | -0.8 | 18.8 | 0 | 2022-02-18 | -16.8 | 34.8 | 0 | 2021-02-18 | -7.3 | 25.3 | 0 | 2020-02-18 | 1.6 | 16.4 | 0 | 2019-02-18 | -12.5 | 30.5 | 0 | 2018-02-18 | -1.8 | 19.8 | 0 | 2017-02-18 | 4.9 | 13.1 | 0 | 2016-02-18 | -13.7 | 31.7 | 0 | 24.71 | 0
2025-02-18 | -15.5 | 33.5 | 0 | 2024-02-18 | -7.1 | 25.1 | 0 | 2023-02-18 | -0.8 | 18.8 | 0 | 2022-02-18 | -15.8 | 33.8 | 0 | 2021-02-18 | -8.1 | 26.1 | 0 | 2020-02-18 | 1.4 | 16.6 | 0 | 2019-02-18 | -14.7 | 32.7 | 0 | 2018-02-18 | -2.8 | 20.8 | 0 | 2017-02-18 | 4.3 | 13.7 | 0 | 2016-02-18 | -14.6 | 32.6 | 0 | 25.37 | 0
2025-02-19 | -16.2 | 34.2 | 0 | 2024-02-19 | -8.5 | 26.5 | 0 | 2023-02-19 | -0.8 | 18.8 | 0 | 2022-02-19 | -14.3 | 32.3 | 0 | 2021-02-19 | -9.2 | 27.2 | 0 | 2020-02-19 | 1.1 | 16.9 | 0 | 2019-02-19 | -14.5 | 32.5 | 0 | 2018-02-19 | -3 | 21 | 0 | 2017-02-19 | 3.6 | 14.4 | 0 | 2016-02-19 | -15.4 | 33.4 | 0 | 25.72 | 0
2025-02-19 | -17.9 | 35.9 | 0 | 2024-02-19 | -9.8 | 27.8 | 0 | 2023-02-19 | -0.8 | 18.8 | 0 | 2022-02-19 | -13.7 | 31.7 | 0 | 2021-02-19 | -9.8 | 27.8 | 0 | 2020-02-19 | 0.9 | 17.1 | 0 | 2019-02-19 | -16 | 34 | 0 | 2018-02-19 | -2.5 | 20.5 | 0 | 2017-02-19 | 2.7 | 15.3 | 0 | 2016-02-19 | -15.3 | 33.3 | 0 | 26.22 | 0
2025-02-19 | -18.7 | 36.7 | 0 | 2024-02-19 | -10.9 | 28.9 | 0 | 2023-02-19 | -1.1 | 19.1 | 0 | 2022-02-19 | -14 | 32 | 0 | 2021-02-19 | -9.4 | 27.4 | 0 | 2020-02-19 | -0.5 | 18.5 | 0 | 2019-02-19 | -16.6 | 34.6 | 0 | 2018-02-19 | -2.1 | 20.1 | 0 | 2017-02-19 | 1.5 | 16.5 | 0 | 2016-02-19 | -16.3 | 34.3 | 0 | 26.81 | 0
2025-02-19 | -18.8 | 36.8 | 0 | 2024-02-19 | -11.7 | 29.7 | 0 | 2023-02-19 | -1.2 | 19.2 | 0 | 2022-02-19 | -11.7 | 29.7 | 0 | 2021-02-19 | -9.2 | 27.2 | 0 | 2020-02-19 | -1.1 | 19.1 | 0 | 2019-02-19 | -16.6 | 34.6 | 0 | 2018-02-19 | -2.6 | 20.6 | 0 | 2017-02-19 | 1.9 | 16.1 | 0 | 2016-02-19 | -19.5 | 37.5 | 0 | 27.05 | 0
2025-02-19 | -18 | 36 | 0 | 2024-02-19 | -12.6 | 30.6 | 0 | 2023-02-19 | -1.2 | 19.2 | 0 | 2022-02-19 | -10.8 | 28.8 | 0 | 2021-02-19 | -9.2 | 27.2 | 0 | 2020-02-19 | -1.3 | 19.3 | 0 | 2019-02-19 | -17.5 | 35.5 | 0 | 2018-02-19 | -3.1 | 21.1 | 0 | 2017-02-19 | 1.6 | 16.4 | 0 | 2016-02-19 | -20.9 | 38.9 | 0 | 27.3 | 0
2025-02-19 | -18.1 | 36.1 | 0 | 2024-02-19 | -13.1 | 31.1 | 0 | 2023-02-19 | -1.8 | 19.8 | 0 | 2022-02-19 | -10.2 | 28.2 | 0 | 2021-02-19 | -9.6 | 27.6 | 0 | 2020-02-19 | -2.4 | 20.4 | 0 | 2019-02-19 | -20 | 38 | 0 | 2018-02-19 | -3.5 | 21.5 | 0 | 2017-02-19 | 1.3 | 16.7 | 0 | 2016-02-19 | -21.1 | 39.1 | 0 | 27.85 | 0
2025-02-19 | -18.6 | 36.6 | 0 | 2024-02-19 | -13.8 | 31.8 | 0 | 2023-02-19 | -1.7 | 19.7 | 0 | 2022-02-19 | -9.9 | 27.9 | 0 | 2021-02-19 | -9.6 | 27.6 | 0 | 2020-02-19 | -2.7 | 20.7 | 0 | 2019-02-19 | -20.6 | 38.6 | 0 | 2018-02-19 | -3.7 | 21.7 | 0 | 2017-02-19 | 1.7 | 16.3 | 0 | 2016-02-19 | -19.1 | 37.1 | 0 | 27.8 | 0
2025-02-19 | -17 | 35 | 0 | 2024-02-19 | -14.9 | 32.9 | 0 | 2023-02-19 | -1.7 | 19.7 | 0 | 2022-02-19 | -9.1 | 27.1 | 0 | 2021-02-19 | -9.5 | 27.5 | 0 | 2020-02-19 | -3.7 | 21.7 | 0 | 2019-02-19 | -21.1 | 39.1 | 0 | 2018-02-19 | -4.4 | 22.4 | 0 | 2017-02-19 | 0.6 | 17.4 | 0 | 2016-02-19 | -18.2 | 36.2 | 0 | 27.9 | 0
2025-02-19 | -16.9 | 34.9 | 0 | 2024-02-19 | -14.9 | 32.9 | 0 | 2023-02-19 | -1.3 | 19.3 | 0 | 2022-02-19 | -5.3 | 23.3 | 0 | 2021-02-19 | -9.2 | 27.2 | 0 | 2020-02-19 | -5.8 | 23.8 | 0 | 2019-02-19 | -19.9 | 37.9 | 0 | 2018-02-19 | -3.9 | 21.9 | 0 | 2017-02-19 | 1.7 | 16.3 | 0 | 2016-02-19 | -17.6 | 35.6 | 0 | 27.31 | 0
2025-02-19 | -15.5 | 33.5 | 0 | 2024-02-19 | -13.8 | 31.8 | 0 | 2023-02-19 | -0.8 | 18.8 | 0 | 2022-02-19 | -4.2 | 22.2 | 0 | 2021-02-19 | -9 | 27 | 0 | 2020-02-19 | -6.4 | 24.4 | 0 | 2019-02-19 | -17.3 | 35.3 | 0 | 2018-02-19 | -2.4 | 20.4 | 0 | 2017-02-19 | 4.1 | 13.9 | 0 | 2016-02-19 | -16.1 | 34.1 | 0 | 26.14 | 0
2025-02-19 | -14.9 | 32.9 | 0 | 2024-02-19 | -12.8 | 30.8 | 0 | 2023-02-19 | 0.4 | 17.6 | 0 | 2022-02-19 | -2.6 | 20.6 | 0 | 2021-02-19 | -8.3 | 26.3 | 0 | 2020-02-19 | -7.2 | 25.2 | 0 | 2019-02-19 | -14.7 | 32.7 | 0 | 2018-02-19 | 1 | 17 | 0 | 2017-02-19 | 5.2 | 12.8 | 0 | 2016-02-19 | -14.2 | 32.2 | 0 | 24.81 | 0
2025-02-19 | -13.8 | 31.8 | 0 | 2024-02-19 | -12.1 | 30.1 | 0 | 2023-02-19 | 1.1 | 16.9 | 0 | 2022-02-19 | -3.6 | 21.6 | 0 | 2021-02-19 | -7.5 | 25.5 | 0 | 2020-02-19 | -7.6 | 25.6 | 0 | 2019-02-19 | -13.2 | 31.2 | 0 | 2018-02-19 | 3.9 | 14.1 | 0 | 2017-02-19 | 5.7 | 12.3 | 0 | 2016-02-19 | -11.9 | 29.9 | 0 | 23.9 | 0
2025-02-19 | -13.1 | 31.1 | 0 | 2024-02-19 | -11.5 | 29.5 | 0 | 2023-02-19 | 2.2 | 15.8 | 0 | 2022-02-19 | -3.6 | 21.6 | 0 | 2021-02-19 | -6.8 | 24.8 | 0 | 2020-02-19 | -8 | 26 | 0 | 2019-02-19 | -12.1 | 30.1 | 0 | 2018-02-19 | 5.3 | 12.7 | 0 | 2017-02-19 | 5.8 | 12.2 | 0 | 2016-02-19 | -9.2 | 27.2 | 0 | 23.1 | 0
2025-02-19 | -12.6 | 30.6 | 0 | 2024-02-19 | -10.7 | 28.7 | 0 | 2023-02-19 | 2.8 | 15.2 | 0 | 2022-02-19 | -5 | 23 | 0 | 2021-02-19 | -6.7 | 24.7 | 0 | 2020-02-19 | -8.2 | 26.2 | 0 | 2019-02-19 | -10.9 | 28.9 | 0 | 2018-02-19 | 6.3 | 11.7 | 0 | 2017-02-19 | 6.4 | 11.6 | 0 | 2016-02-19 | -7.3 | 25.3 | 0 | 22.59 | 0
2025-02-19 | -11.3 | 29.3 | 0 | 2024-02-19 | -10.6 | 28.6 | 0 | 2023-02-19 | 3.8 | 14.2 | 0 | 2022-02-19 | -6.7 | 24.7 | 0 | 2021-02-19 | -6.7 | 24.7 | 0 | 2020-02-19 | -7.8 | 25.8 | 0 | 2019-02-19 | -9.6 | 27.6 | 0 | 2018-02-19 | 5.8 | 12.2 | 0 | 2017-02-19 | 6.7 | 11.3 | 0 | 2016-02-19 | -6.3 | 24.3 | 0 | 22.27 | 0
2025-02-19 | -10.3 | 28.3 | 0 | 2024-02-19 | -10 | 28 | 0 | 2023-02-19 | 4.9 | 13.1 | 0 | 2022-02-19 | -7.8 | 25.8 | 0 | 2021-02-19 | -6.8 | 24.8 | 0 | 2020-02-19 | -7.9 | 25.9 | 0 | 2019-02-19 | -8.9 | 26.9 | 0 | 2018-02-19 | 5 | 13 | 0 | 2017-02-19 | 6.6 | 11.4 | 0 | 2016-02-19 | -5.7 | 23.7 | 0 | 22.09 | 0
2025-02-19 | -10.2 | 28.2 | 0 | 2024-02-19 | -9.8 | 27.8 | 0 | 2023-02-19 | 4.9 | 13.1 | 0 | 2022-02-19 | -9.5 | 27.5 | 0 | 2021-02-19 | -7.1 | 25.1 | 0 | 2020-02-19 | -8.2 | 26.2 | 0 | 2019-02-19 | -9.1 | 27.1 | 0 | 2018-02-19 | 3.3 | 14.7 | 0 | 2017-02-19 | 5.8 | 12.2 | 0 | 2016-02-19 | -6.4 | 24.4 | 0 | 22.63 | 0
2025-02-19 | -10.5 | 28.5 | 0 | 2024-02-19 | -9.9 | 27.9 | 0 | 2023-02-19 | 5 | 13 | 0 | 2022-02-19 | -10.9 | 28.9 | 0 | 2021-02-19 | -7.2 | 25.2 | 0 | 2020-02-19 | -8.6 | 26.6 | 0 | 2019-02-19 | -9.5 | 27.5 | 0 | 2018-02-19 | 2.5 | 15.5 | 0 | 2017-02-19 | 5.7 | 12.3 | 0 | 2016-02-19 | -5.8 | 23.8 | 0 | 22.92 | 0
2025-02-19 | -10.8 | 28.8 | 0 | 2024-02-19 | -10.6 | 28.6 | 0 | 2023-02-19 | 4.7 | 13.3 | 0 | 2022-02-19 | -11.9 | 29.9 | 0 | 2021-02-19 | -7.6 | 25.6 | 0 | 2020-02-19 | -9.9 | 27.9 | 0 | 2019-02-19 | -11.3 | 29.3 | 0 | 2018-02-19 | 2.5 | 15.5 | 0 | 2017-02-19 | 5.1 | 12.9 | 0 | 2016-02-19 | -5.1 | 23.1 | 0 | 23.49 | 0
2025-02-19 | -11 | 29 | 0 | 2024-02-19 | -10.8 | 28.8 | 0 | 2023-02-19 | 4.9 | 13.1 | 0 | 2022-02-19 | -12.3 | 30.3 | 0 | 2021-02-19 | -8.1 | 26.1 | 0 | 2020-02-19 | -10.4 | 28.4 | 0 | 2019-02-19 | -12.8 | 30.8 | 0 | 2018-02-19 | 2.2 | 15.8 | 0 | 2017-02-19 | 4.1 | 13.9 | 0 | 2016-02-19 | -5.2 | 23.2 | 0 | 23.94 | 0
2025-02-19 | -12.3 | 30.3 | 0 | 2024-02-19 | -11.2 | 29.2 | 0 | 2023-02-19 | 5.6 | 12.4 | 0 | 2022-02-19 | -12.5 | 30.5 | 0 | 2021-02-19 | -9.8 | 27.8 | 0 | 2020-02-19 | -11.4 | 29.4 | 0 | 2019-02-19 | -12.1 | 30.1 | 0 | 2018-02-19 | 1.8 | 16.2 | 0 | 2017-02-19 | 3 | 15 | 0 | 2016-02-19 | -5.2 | 23.2 | 0 | 24.41 | 0
2025-02-19 | -12.6 | 30.6 | 0 | 2024-02-19 | -13.1 | 31.1 | 0 | 2023-02-19 | 5.6 | 12.4 | 0 | 2022-02-19 | -13 | 31 | 0 | 2021-02-19 | -8.6 | 26.6 | 0 | 2020-02-19 | -11.5 | 29.5 | 0 | 2019-02-19 | -11.7 | 29.7 | 0 | 2018-02-19 | 1.7 | 16.3 | 0 | 2017-02-19 | 2.1 | 15.9 | 0 | 2016-02-19 | -4.1 | 22.1 | 0 | 24.52 | 0
2025-02-19 | -13.2 | 31.2 | 0 | 2024-02-19 | -12.4 | 30.4 | 0 | 2023-02-19 | 5 | 13 | 0 | 2022-02-19 | -13.6 | 31.6 | 0 | 2021-02-19 | -8.6 | 26.6 | 0 | 2020-02-19 | -11.7 | 29.7 | 0 | 2019-02-19 | -12.6 | 30.6 | 0 | 2018-02-19 | 1.6 | 16.4 | 0 | 2017-02-19 | 1 | 17 | 0 | 2016-02-19 | -4.1 | 22.1 | 0 | 24.86 | 0
2025-02-19 | -13.2 | 31.2 | 0 | 2024-02-19 | -12.4 | 30.4 | 0 | 2023-02-19 | 4.4 | 13.6 | 0 | 2022-02-19 | -14.2 | 32.2 | 0 | 2021-02-19 | -8.4 | 26.4 | 0 | 2020-02-19 | -12.4 | 30.4 | 0 | 2019-02-19 | -13.2 | 31.2 | 0 | 2018-02-19 | 1.6 | 16.4 | 0 | 2017-02-19 | -0.2 | 18.2 | 0 | 2016-02-19 | -3.1 | 21.1 | 0 | 25.11 | 0
2025-02-20 | -12.8 | 30.8 | 0 | 2024-02-20 | -12.8 | 30.8 | 0 | 2023-02-20 | 4.1 | 13.9 | 0 | 2022-02-20 | -16 | 34 | 0 | 2021-02-20 | -9.6 | 27.6 | 0 | 2020-02-20 | -12.6 | 30.6 | 0 | 2019-02-20 | -15.2 | 33.2 | 0 | 2018-02-20 | 1.1 | 16.9 | 0 | 2017-02-20 | -1.1 | 19.1 | 0 | 2016-02-20 | -2.7 | 20.7 | 0 | 25.76 | 0
2025-02-20 | -12.5 | 30.5 | 0 | 2024-02-20 | -11.1 | 29.1 | 0 | 2023-02-20 | 4.1 | 13.9 | 0 | 2022-02-20 | -16.4 | 34.4 | 0 | 2021-02-20 | -11.6 | 29.6 | 0 | 2020-02-20 | -13.3 | 31.3 | 0 | 2019-02-20 | -17.5 | 35.5 | 0 | 2018-02-20 | 1 | 17 | 0 | 2017-02-20 | -3.1 | 21.1 | 0 | 2016-02-20 | 0.5 | 17.5 | 0 | 25.99 | 0
2025-02-20 | -14 | 32 | 0 | 2024-02-20 | -11.1 | 29.1 | 0 | 2023-02-20 | 4.4 | 13.6 | 0 | 2022-02-20 | -17.6 | 35.6 | 0 | 2021-02-20 | -13.2 | 31.2 | 0 | 2020-02-20 | -13.1 | 31.1 | 0 | 2019-02-20 | -16.4 | 34.4 | 0 | 2018-02-20 | 0.9 | 17.1 | 0 | 2017-02-20 | -2.6 | 20.6 | 0 | 2016-02-20 | -0.5 | 18.5 | 0 | 26.32 | 0
2025-02-20 | -15.6 | 33.6 | 0 | 2024-02-20 | -11.3 | 29.3 | 0 | 2023-02-20 | 4.2 | 13.8 | 0 | 2022-02-20 | -18.7 | 36.7 | 0 | 2021-02-20 | -11.6 | 29.6 | 0 | 2020-02-20 | -12 | 30 | 0 | 2019-02-20 | -15.4 | 33.4 | 0 | 2018-02-20 | 0.7 | 17.3 | 0 | 2017-02-20 | -2.9 | 20.9 | 0 | 2016-02-20 | 0.1 | 17.9 | 0 | 26.25 | 0
2025-02-20 | -16.1 | 34.1 | 0 | 2024-02-20 | -11.5 | 29.5 | 0 | 2023-02-20 | 4 | 14 | 0 | 2022-02-20 | -17.7 | 35.7 | 0 | 2021-02-20 | -12.1 | 30.1 | 0 | 2020-02-20 | -13.1 | 31.1 | 0 | 2019-02-20 | -16.7 | 34.7 | 0 | 2018-02-20 | 0.8 | 17.2 | 0 | 2017-02-20 | -3.5 | 21.5 | 0 | 2016-02-20 | 0.4 | 17.6 | 0 | 26.55 | 0
2025-02-20 | -16.5 | 34.5 | 0 | 2024-02-20 | -11.9 | 29.9 | 0 | 2023-02-20 | 3.5 | 14.5 | 0 | 2022-02-20 | -17.3 | 35.3 | 0 | 2021-02-20 | -12.4 | 30.4 | 0 | 2020-02-20 | -13.8 | 31.8 | 0 | 2019-02-20 | -18.1 | 36.1 | 0 | 2018-02-20 | 0.9 | 17.1 | 0 | 2017-02-20 | -4.5 | 22.5 | 0 | 2016-02-20 | 1.4 | 16.6 | 0 | 26.87 | 0
2025-02-20 | -17.2 | 35.2 | 0 | 2024-02-20 | -12.1 | 30.1 | 0 | 2023-02-20 | 3.4 | 14.6 | 0 | 2022-02-20 | -17.1 | 35.1 | 0 | 2021-02-20 | -12.7 | 30.7 | 0 | 2020-02-20 | -14.1 | 32.1 | 0 | 2019-02-20 | -17.2 | 35.2 | 0 | 2018-02-20 | 0.8 | 17.2 | 0 | 2017-02-20 | -6.1 | 24.1 | 0 | 2016-02-20 | 1.4 | 16.6 | 0 | 27.09 | 0
2025-02-20 | -17.7 | 35.7 | 0 | 2024-02-20 | -12 | 30 | 0 | 2023-02-20 | 3.3 | 14.7 | 0 | 2022-02-20 | -17.5 | 35.5 | 0 | 2021-02-20 | -12.9 | 30.9 | 0 | 2020-02-20 | -15.2 | 33.2 | 0 | 2019-02-20 | -17.7 | 35.7 | 0 | 2018-02-20 | 0.9 | 17.1 | 0 | 2017-02-20 | -6 | 24 | 0 | 2016-02-20 | 2.3 | 15.7 | 0 | 27.25 | 0
2025-02-20 | -17.1 | 35.1 | 0 | 2024-02-20 | -11.9 | 29.9 | 0 | 2023-02-20 | 3 | 15 | 0 | 2022-02-20 | -16.2 | 34.2 | 0 | 2021-02-20 | -14.1 | 32.1 | 0 | 2020-02-20 | -15.5 | 33.5 | 0 | 2019-02-20 | -18 | 36 | 0 | 2018-02-20 | 1.1 | 16.9 | 0 | 2017-02-20 | -5.7 | 23.7 | 0 | 2016-02-20 | 3.2 | 14.8 | 0 | 27.12 | 0
2025-02-20 | -15.8 | 33.8 | 0 | 2024-02-20 | -11.4 | 29.4 | 0 | 2023-02-20 | 2.7 | 15.3 | 0 | 2022-02-20 | -14.1 | 32.1 | 0 | 2021-02-20 | -12.2 | 30.2 | 0 | 2020-02-20 | -15.3 | 33.3 | 0 | 2019-02-20 | -15.9 | 33.9 | 0 | 2018-02-20 | 1.2 | 16.8 | 0 | 2017-02-20 | -4.8 | 22.8 | 0 | 2016-02-20 | 3.7 | 14.3 | 0 | 26.19 | 0
2025-02-20 | -13.8 | 31.8 | 0 | 2024-02-20 | -10.5 | 28.5 | 0 | 2023-02-20 | 3.5 | 14.5 | 0 | 2022-02-20 | -12 | 30 | 0 | 2021-02-20 | -11.1 | 29.1 | 0 | 2020-02-20 | -14.2 | 32.2 | 0 | 2019-02-20 | -12.9 | 30.9 | 0 | 2018-02-20 | 1.4 | 16.6 | 0 | 2017-02-20 | -4 | 22 | 0 | 2016-02-20 | 4.1 | 13.9 | 0 | 24.95 | 0
2025-02-20 | -11.9 | 29.9 | 0 | 2024-02-20 | -9.6 | 27.6 | 0 | 2023-02-20 | 3.7 | 14.3 | 0 | 2022-02-20 | -10.5 | 28.5 | 0 | 2021-02-20 | -9.1 | 27.1 | 0 | 2020-02-20 | -13.6 | 31.6 | 0 | 2019-02-20 | -11.4 | 29.4 | 0 | 2018-02-20 | 1.7 | 16.3 | 0 | 2017-02-20 | -3 | 21 | 0 | 2016-02-20 | 4.1 | 13.9 | 0 | 23.96 | 0
2025-02-20 | -10 | 28 | 0 | 2024-02-20 | -9.3 | 27.3 | 0 | 2023-02-20 | 0.5 | 17.5 | 0 | 2022-02-20 | -8.5 | 26.5 | 0 | 2021-02-20 | -7.4 | 25.4 | 0 | 2020-02-20 | -12.8 | 30.8 | 0 | 2019-02-20 | -9.4 | 27.4 | 0 | 2018-02-20 | 1.9 | 16.1 | 0 | 2017-02-20 | -2 | 20 | 0 | 2016-02-20 | 3.8 | 14.2 | 0 | 23.32 | 0
2025-02-20 | -9.3 | 27.3 | 0 | 2024-02-20 | -8.8 | 26.8 | 0 | 2023-02-20 | 0.7 | 17.3 | 0 | 2022-02-20 | -5.3 | 23.3 | 0 | 2021-02-20 | -5.5 | 23.5 | 0 | 2020-02-20 | -12.5 | 30.5 | 0 | 2019-02-20 | -8.2 | 26.2 | 0 | 2018-02-20 | 1.8 | 16.2 | 0 | 2017-02-20 | -0.8 | 18.8 | 0 | 2016-02-20 | 4 | 14 | 0 | 22.39 | 0
2025-02-20 | -8.9 | 26.9 | 0 | 2024-02-20 | -8 | 26 | 0 | 2023-02-20 | 0.9 | 17.1 | 0 | 2022-02-20 | -4.7 | 22.7 | 0 | 2021-02-20 | -4.8 | 22.8 | 0 | 2020-02-20 | -12.2 | 30.2 | 0 | 2019-02-20 | -6.8 | 24.8 | 0 | 2018-02-20 | 2 | 16 | 0 | 2017-02-20 | 0.3 | 17.7 | 0 | 2016-02-20 | 3.8 | 14.2 | 0 | 21.84 | 0
2025-02-20 | -8.4 | 26.4 | 0 | 2024-02-20 | -7.3 | 25.3 | 0 | 2023-02-20 | 0.4 | 17.6 | 0 | 2022-02-20 | -3.2 | 21.2 | 0 | 2021-02-20 | -4.6 | 22.6 | 0 | 2020-02-20 | -12.1 | 30.1 | 0 | 2019-02-20 | -7.2 | 25.2 | 0 | 2018-02-20 | 2 | 16 | 0 | 2017-02-20 | 0.8 | 17.2 | 0 | 2016-02-20 | 4.5 | 13.5 | 0 | 21.51 | 0
2025-02-20 | -8.3 | 26.3 | 0 | 2024-02-20 | -7.2 | 25.2 | 0 | 2023-02-20 | -0.4 | 18.4 | 0 | 2022-02-20 | -2 | 20 | 0 | 2021-02-20 | -4.3 | 22.3 | 0 | 2020-02-20 | -12 | 30 | 0 | 2019-02-20 | -7.2 | 25.2 | 0 | 2018-02-20 | 1.8 | 16.2 | 0 | 2017-02-20 | 0.3 | 17.7 | 0 | 2016-02-20 | 4.4 | 13.6 | 0 | 21.49 | 0
2025-02-20 | -7.8 | 25.8 | 0 | 2024-02-20 | -7.5 | 25.5 | 0 | 2023-02-20 | -1.6 | 19.6 | 0 | 2022-02-20 | -0.7 | 18.7 | 0 | 2021-02-20 | -4.1 | 22.1 | 0 | 2020-02-20 | -12.3 | 30.3 | 0 | 2019-02-20 | -7.3 | 25.3 | 0 | 2018-02-20 | 1.9 | 16.1 | 0 | 2017-02-20 | -0.2 | 18.2 | 0 | 2016-02-20 | 4.1 | 13.9 | 0 | 21.55 | 0
2025-02-20 | -8.6 | 26.6 | 0 | 2024-02-20 | -8.3 | 26.3 | 0 | 2023-02-20 | -3.1 | 21.1 | 0 | 2022-02-20 | 0 | 18 | 0 | 2021-02-20 | -4.9 | 22.9 | 0 | 2020-02-20 | -13 | 31 | 0 | 2019-02-20 | -8.6 | 26.6 | 0 | 2018-02-20 | 1.7 | 16.3 | 0 | 2017-02-20 | -0.5 | 18.5 | 0 | 2016-02-20 | 3.8 | 14.2 | 0 | 22.15 | 0
2025-02-20 | -9 | 27 | 0 | 2024-02-20 | -9.1 | 27.1 | 0 | 2023-02-20 | -3.4 | 21.4 | 0 | 2022-02-20 | 1 | 17 | 0 | 2021-02-20 | -5.3 | 23.3 | 0 | 2020-02-20 | -13.4 | 31.4 | 0 | 2019-02-20 | -8.9 | 26.9 | 0 | 2018-02-20 | 1.8 | 16.2 | 0 | 2017-02-20 | -1.6 | 19.6 | 0 | 2016-02-20 | 3.3 | 14.7 | 0 | 22.46 | 0
2025-02-20 | -8.8 | 26.8 | 0 | 2024-02-20 | -9.7 | 27.7 | 0 | 2023-02-20 | -4.2 | 22.2 | 0 | 2022-02-20 | 1.7 | 16.3 | 0 | 2021-02-20 | -4.6 | 22.6 | 0 | 2020-02-20 | -14.4 | 32.4 | 0 | 2019-02-20 | -8.6 | 26.6 | 0 | 2018-02-20 | 1.4 | 16.6 | 0 | 2017-02-20 | -2.4 | 20.4 | 0 | 2016-02-20 | 3.4 | 14.6 | 0 | 22.62 | 0
2025-02-20 | -9.3 | 27.3 | 0 | 2024-02-20 | -10 | 28 | 0 | 2023-02-20 | -5.6 | 23.6 | 0 | 2022-02-20 | 2.2 | 15.8 | 0 | 2021-02-20 | -5.5 | 23.5 | 0 | 2020-02-20 | -15.6 | 33.6 | 0 | 2019-02-20 | -7.8 | 25.8 | 0 | 2018-02-20 | 1.4 | 16.6 | 0 | 2017-02-20 | -4.6 | 22.6 | 0 | 2016-02-20 | 3 | 15 | 0 | 23.18 | 0
2025-02-20 | -9.8 | 27.8 | 0 | 2024-02-20 | -10.8 | 28.8 | 0 | 2023-02-20 | -7.7 | 25.7 | 0 | 2022-02-20 | 2.7 | 15.3 | 0 | 2021-02-20 | -8 | 26 | 0 | 2020-02-20 | -16.1 | 34.1 | 0 | 2019-02-20 | -8.4 | 26.4 | 0 | 2018-02-20 | 1.2 | 16.8 | 0 | 2017-02-20 | -4.4 | 22.4 | 0 | 2016-02-20 | 2.2 | 15.8 | 0 | 23.91 | 0
2025-02-20 | -10.5 | 28.5 | 0 | 2024-02-20 | -12.1 | 30.1 | 0 | 2023-02-20 | -8.8 | 26.8 | 0 | 2022-02-20 | 3.4 | 14.6 | 0 | 2021-02-20 | -11.1 | 29.1 | 0 | 2020-02-20 | -16.9 | 34.9 | 0 | 2019-02-20 | -8 | 26 | 0 | 2018-02-20 | 1.4 | 16.6 | 0 | 2017-02-20 | -5.8 | 23.8 | 0 | 2016-02-20 | 2.6 | 15.4 | 0 | 24.58 | 0
2025-02-21 | -10.8 | 28.8 | 0 | 2024-02-21 | -12.6 | 30.6 | 0 | 2023-02-21 | -9.9 | 27.9 | 0 | 2022-02-21 | 3.4 | 14.6 | 0 | 2021-02-21 | -11.5 | 29.5 | 0 | 2020-02-21 | -17.5 | 35.5 | 0 | 2019-02-21 | -7.8 | 25.8 | 0 | 2018-02-21 | 1.5 | 16.5 | 0 | 2017-02-21 | -8.3 | 26.3 | 0 | 2016-02-21 | 2.4 | 15.6 | 0 | 25.11 | 0
2025-02-21 | -11.9 | 29.9 | 0 | 2024-02-21 | -12.7 | 30.7 | 0 | 2023-02-21 | -11.1 | 29.1 | 0 | 2022-02-21 | 3.5 | 14.5 | 0 | 2021-02-21 | -13.4 | 31.4 | 0 | 2020-02-21 | -17.7 | 35.7 | 0 | 2019-02-21 | -7.8 | 25.8 | 0 | 2018-02-21 | 1.5 | 16.5 | 0 | 2017-02-21 | -8 | 26 | 0 | 2016-02-21 | 1.5 | 16.5 | 0 | 25.61 | 0
2025-02-21 | -12.1 | 30.1 | 0 | 2024-02-21 | -13.5 | 31.5 | 0 | 2023-02-21 | -11.2 | 29.2 | 0 | 2022-02-21 | 3.3 | 14.7 | 0 | 2021-02-21 | -11.8 | 29.8 | 0 | 2020-02-21 | -17.9 | 35.9 | 0 | 2019-02-21 | -7.7 | 25.7 | 0 | 2018-02-21 | 1.3 | 16.7 | 0 | 2017-02-21 | -8.4 | 26.4 | 0 | 2016-02-21 | 1.8 | 16.2 | 0 | 25.62 | 0
2025-02-21 | -12.1 | 30.1 | 0 | 2024-02-21 | -12.4 | 30.4 | 0 | 2023-02-21 | -11.8 | 29.8 | 0 | 2022-02-21 | 3.6 | 14.4 | 0 | 2021-02-21 | -13.2 | 31.2 | 0 | 2020-02-21 | -18.9 | 36.9 | 0 | 2019-02-21 | -7.3 | 25.3 | 0 | 2018-02-21 | 1.7 | 16.3 | 0 | 2017-02-21 | -6.4 | 24.4 | 0 | 2016-02-21 | 1.6 | 16.4 | 0 | 25.52 | 0
2025-02-21 | -12.2 | 30.2 | 0 | 2024-02-21 | -12.5 | 30.5 | 0 | 2023-02-21 | -12.1 | 30.1 | 0 | 2022-02-21 | 3.5 | 14.5 | 0 | 2021-02-21 | -15.8 | 33.8 | 0 | 2020-02-21 | -18.4 | 36.4 | 0 | 2019-02-21 | -7.2 | 25.2 | 0 | 2018-02-21 | 1.5 | 16.5 | 0 | 2017-02-21 | -9.1 | 27.1 | 0 | 2016-02-21 | 1.5 | 16.5 | 0 | 26.08 | 0
2025-02-21 | -12.3 | 30.3 | 0 | 2024-02-21 | -13.1 | 31.1 | 0 | 2023-02-21 | -12.5 | 30.5 | 0 | 2022-02-21 | 2 | 16 | 0 | 2021-02-21 | -13.6 | 31.6 | 0 | 2020-02-21 | -17.6 | 35.6 | 0 | 2019-02-21 | -6.9 | 24.9 | 0 | 2018-02-21 | 8.7 | 9.3 | 0 | 2017-02-21 | -9.2 | 27.2 | 0 | 2016-02-21 | 1 | 17 | 0 | 25.35 | 0
2025-02-21 | -12.4 | 30.4 | 0 | 2024-02-21 | -13.3 | 31.3 | 0 | 2023-02-21 | -12.6 | 30.6 | 0 | 2022-02-21 | 1.7 | 16.3 | 0 | 2021-02-21 | -14.5 | 32.5 | 0 | 2020-02-21 | -15.7 | 33.7 | 0 | 2019-02-21 | -7.1 | 25.1 | 0 | 2018-02-21 | 8.9 | 9.1 | 0 | 2017-02-21 | -7.9 | 25.9 | 0 | 2016-02-21 | 0.5 | 17.5 | 0 | 25.24 | 0
2025-02-21 | -12.4 | 30.4 | 0 | 2024-02-21 | -14.1 | 32.1 | 0 | 2023-02-21 | -13.2 | 31.2 | 0 | 2022-02-21 | 1 | 17 | 0 | 2021-02-21 | -15 | 33 | 0 | 2020-02-21 | -15.3 | 33.3 | 0 | 2019-02-21 | -7.3 | 25.3 | 0 | 2018-02-21 | 5.7 | 12.3 | 0 | 2017-02-21 | -7.3 | 25.3 | 0 | 2016-02-21 | 0.2 | 17.8 | 0 | 25.77 | 0
2025-02-21 | -12.3 | 30.3 | 0 | 2024-02-21 | -12.7 | 30.7 | 0 | 2023-02-21 | -13.3 | 31.3 | 0 | 2022-02-21 | 1 | 17 | 0 | 2021-02-21 | -13.9 | 31.9 | 0 | 2020-02-21 | -15 | 33 | 0 | 2019-02-21 | -6.7 | 24.7 | 0 | 2018-02-21 | 8.5 | 9.5 | 0 | 2017-02-21 | -6.2 | 24.2 | 0 | 2016-02-21 | 0.1 | 17.9 | 0 | 25.05 | 0
2025-02-21 | -11.9 | 29.9 | 0 | 2024-02-21 | -10.4 | 28.4 | 0 | 2023-02-21 | -12.6 | 30.6 | 0 | 2022-02-21 | 0.8 | 17.2 | 0 | 2021-02-21 | -12.8 | 30.8 | 0 | 2020-02-21 | -13.6 | 31.6 | 0 | 2019-02-21 | -3.4 | 21.4 | 0 | 2018-02-21 | 8.4 | 9.6 | 0 | 2017-02-21 | -5.2 | 23.2 | 0 | 2016-02-21 | 0 | 18 | 0 | 24.07 | 0
2025-02-21 | -11.6 | 29.6 | 0 | 2024-02-21 | -8 | 26 | 0 | 2023-02-21 | -11.7 | 29.7 | 0 | 2022-02-21 | -0.2 | 18.2 | 0 | 2021-02-21 | -9.7 | 27.7 | 0 | 2020-02-21 | -10.2 | 28.2 | 0 | 2019-02-21 | 0.4 | 17.6 | 0 | 2018-02-21 | 8.3 | 9.7 | 0 | 2017-02-21 | -3.4 | 21.4 | 0 | 2016-02-21 | 0.8 | 17.2 | 0 | 22.53 | 0
2025-02-21 | -11.2 | 29.2 | 0 | 2024-02-21 | -5.1 | 23.1 | 0 | 2023-02-21 | -10.8 | 28.8 | 0 | 2022-02-21 | -2.4 | 20.4 | 0 | 2021-02-21 | -5.3 | 23.3 | 0 | 2020-02-21 | -6.5 | 24.5 | 0 | 2019-02-21 | 1.4 | 16.6 | 0 | 2018-02-21 | 7.3 | 10.7 | 0 | 2017-02-21 | -2.5 | 20.5 | 0 | 2016-02-21 | 1.6 | 16.4 | 0 | 21.35 | 0
2025-02-21 | -10.1 | 28.1 | 0 | 2024-02-21 | -2.9 | 20.9 | 0 | 2023-02-21 | -9.4 | 27.4 | 0 | 2022-02-21 | -2.9 | 20.9 | 0 | 2021-02-21 | -3.7 | 21.7 | 0 | 2020-02-21 | -3.9 | 21.9 | 0 | 2019-02-21 | 1.7 | 16.3 | 0 | 2018-02-21 | 6.6 | 11.4 | 0 | 2017-02-21 | -1 | 19 | 0 | 2016-02-21 | -1.2 | 19.2 | 0 | 20.68 | 0
2025-02-21 | -9.4 | 27.4 | 0 | 2024-02-21 | -1 | 19 | 0 | 2023-02-21 | -8.9 | 26.9 | 0 | 2022-02-21 | -2.6 | 20.6 | 0 | 2021-02-21 | -2.5 | 20.5 | 0 | 2020-02-21 | -2.4 | 20.4 | 0 | 2019-02-21 | 2 | 16 | 0 | 2018-02-21 | 5.3 | 12.7 | 0 | 2017-02-21 | 0.6 | 17.4 | 0 | 2016-02-21 | -1 | 19 | 0 | 19.99 | 0
2025-02-21 | -9.5 | 27.5 | 0 | 2024-02-21 | 0.8 | 17.2 | 0 | 2023-02-21 | -9 | 27 | 0 | 2022-02-21 | -2.6 | 20.6 | 0 | 2021-02-21 | -1.9 | 19.9 | 0 | 2020-02-21 | -1.4 | 19.4 | 0 | 2019-02-21 | 2.5 | 15.5 | 0 | 2018-02-21 | 3.8 | 14.2 | 0 | 2017-02-21 | 1.1 | 16.9 | 0 | 2016-02-21 | -1.2 | 19.2 | 0 | 19.74 | 0
2025-02-21 | -9 | 27 | 0 | 2024-02-21 | 2.7 | 15.3 | 0 | 2023-02-21 | -9.4 | 27.4 | 0 | 2022-02-21 | -2.9 | 20.9 | 0 | 2021-02-21 | -1.5 | 19.5 | 0 | 2020-02-21 | -0.7 | 18.7 | 0 | 2019-02-21 | 2.6 | 15.4 | 0 | 2018-02-21 | 3.2 | 14.8 | 0 | 2017-02-21 | 0.9 | 17.1 | 0 | 2016-02-21 | -1.7 | 19.7 | 0 | 19.58 | 0
2025-02-21 | -9 | 27 | 0 | 2024-02-21 | 4.5 | 13.5 | 0 | 2023-02-21 | -9.1 | 27.1 | 0 | 2022-02-21 | -3.2 | 21.2 | 0 | 2021-02-21 | -1.5 | 19.5 | 0 | 2020-02-21 | -0.9 | 18.9 | 0 | 2019-02-21 | 2.3 | 15.7 | 0 | 2018-02-21 | 3.3 | 14.7 | 0 | 2017-02-21 | 0.7 | 17.3 | 0 | 2016-02-21 | -2.6 | 20.6 | 0 | 19.55 | 0
2025-02-21 | -8.9 | 26.9 | 0 | 2024-02-21 | 1.3 | 16.7 | 0 | 2023-02-21 | -9.3 | 27.3 | 0 | 2022-02-21 | -3.6 | 21.6 | 0 | 2021-02-21 | -2.4 | 20.4 | 0 | 2020-02-21 | -1.7 | 19.7 | 0 | 2019-02-21 | 2 | 16 | 0 | 2018-02-21 | 3 | 15 | 0 | 2017-02-21 | 0.4 | 17.6 | 0 | 2016-02-21 | -3.6 | 21.6 | 0 | 20.28 | 0
2025-02-21 | -9.6 | 27.6 | 0 | 2024-02-21 | 0 | 18 | 0 | 2023-02-21 | -9.8 | 27.8 | 0 | 2022-02-21 | -4.2 | 22.2 | 0 | 2021-02-21 | -3 | 21 | 0 | 2020-02-21 | -2.9 | 20.9 | 0 | 2019-02-21 | 1.6 | 16.4 | 0 | 2018-02-21 | 2.5 | 15.5 | 0 | 2017-02-21 | -0.3 | 18.3 | 0 | 2016-02-21 | -4.8 | 22.8 | 0 | 21.05 | 0
2025-02-21 | -9 | 27 | 0 | 2024-02-21 | -0.7 | 18.7 | 0 | 2023-02-21 | -11.9 | 29.9 | 0 | 2022-02-21 | -4.9 | 22.9 | 0 | 2021-02-21 | -4.7 | 22.7 | 0 | 2020-02-21 | -3.3 | 21.3 | 0 | 2019-02-21 | 0.7 | 17.3 | 0 | 2018-02-21 | 1.5 | 16.5 | 0 | 2017-02-21 | 0 | 18 | 0 | 2016-02-21 | -5.5 | 23.5 | 0 | 21.78 | 0
2025-02-21 | -12.4 | 30.4 | 0 | 2024-02-21 | 2.2 | 15.8 | 0 | 2023-02-21 | -10 | 28 | 0 | 2022-02-21 | -4.8 | 22.8 | 0 | 2021-02-21 | -5.4 | 23.4 | 0 | 2020-02-21 | -3.7 | 21.7 | 0 | 2019-02-21 | -0.4 | 18.4 | 0 | 2018-02-21 | 0.6 | 17.4 | 0 | 2017-02-21 | -0.4 | 18.4 | 0 | 2016-02-21 | -6.3 | 24.3 | 0 | 22.06 | 0
2025-02-21 | -12.3 | 30.3 | 0 | 2024-02-21 | 3.6 | 14.4 | 0 | 2023-02-21 | -8.1 | 26.1 | 0 | 2022-02-21 | -4.7 | 22.7 | 0 | 2021-02-21 | -6.3 | 24.3 | 0 | 2020-02-21 | -3.6 | 21.6 | 0 | 2019-02-21 | -0.9 | 18.9 | 0 | 2018-02-21 | -0.4 | 18.4 | 0 | 2017-02-21 | -0.6 | 18.6 | 0 | 2016-02-21 | -7.1 | 25.1 | 0 | 22.04 | 0
2025-02-21 | -12.7 | 30.7 | 0 | 2024-02-21 | 3.7 | 14.3 | 0 | 2023-02-21 | -6.8 | 24.8 | 0 | 2022-02-21 | -5 | 23 | 0 | 2021-02-21 | -6.9 | 24.9 | 0 | 2020-02-21 | -3.3 | 21.3 | 0 | 2019-02-21 | -1.3 | 19.3 | 0 | 2018-02-21 | -0.8 | 18.8 | 0 | 2017-02-21 | -0.7 | 18.7 | 0 | 2016-02-21 | -8.2 | 26.2 | 0 | 22.2 | 0
2025-02-21 | -15.5 | 33.5 | 0 | 2024-02-21 | 3.5 | 14.5 | 0 | 2023-02-21 | -6.6 | 24.6 | 0 | 2022-02-21 | -5.7 | 23.7 | 0 | 2021-02-21 | -9.5 | 27.5 | 0 | 2020-02-21 | -3.8 | 21.8 | 0 | 2019-02-21 | -2.2 | 20.2 | 0 | 2018-02-21 | -1.2 | 19.2 | 0 | 2017-02-21 | -0.7 | 18.7 | 0 | 2016-02-21 | -9 | 27 | 0 | 23.07 | 0
2025-02-22 | -14.8 | 32.8 | 0 | 2024-02-22 | 2.8 | 15.2 | 0 | 2023-02-22 | -8 | 26 | 0 | 2022-02-22 | -6.2 | 24.2 | 0 | 2021-02-22 | -7.6 | 25.6 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -3.1 | 21.1 | 0 | 2018-02-22 | -2.2 | 20.2 | 0 | 2017-02-22 | -0.5 | 18.5 | 0 | 2016-02-22 | -9.9 | 27.9 | 0 | 23.34 | 0
2025-02-22 | -15 | 33 | 0 | 2024-02-22 | 2.3 | 15.7 | 0 | 2023-02-22 | -9.6 | 27.6 | 0 | 2022-02-22 | -7 | 25 | 0 | 2021-02-22 | -8.1 | 26.1 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -4.4 | 22.4 | 0 | 2018-02-22 | -2.7 | 20.7 | 0 | 2017-02-22 | -0.2 | 18.2 | 0 | 2016-02-22 | -10.5 | 28.5 | 0 | 23.91 | 0
2025-02-22 | -14.6 | 32.6 | 0 | 2024-02-22 | 1.9 | 16.1 | 0 | 2023-02-22 | -10.7 | 28.7 | 0 | 2022-02-22 | -7.5 | 25.5 | 0 | 2021-02-22 | -7.7 | 25.7 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -4.8 | 22.8 | 0 | 2018-02-22 | -3.2 | 21.2 | 0 | 2017-02-22 | -0.2 | 18.2 | 0 | 2016-02-22 | -11.1 | 29.1 | 0 | 24.18 | 0
2025-02-22 | -15.2 | 33.2 | 0 | 2024-02-22 | 1.8 | 16.2 | 0 | 2023-02-22 | -11.4 | 29.4 | 0 | 2022-02-22 | -8.1 | 26.1 | 0 | 2021-02-22 | -8 | 26 | 0 | 2020-02-22 | -4.1 | 22.1 | 0 | 2019-02-22 | -5.6 | 23.6 | 0 | 2018-02-22 | -3.8 | 21.8 | 0 | 2017-02-22 | -0.1 | 18.1 | 0 | 2016-02-22 | -11.4 | 29.4 | 0 | 24.59 | 0
2025-02-22 | -15.9 | 33.9 | 0 | 2024-02-22 | 2 | 16 | 0 | 2023-02-22 | -11.8 | 29.8 | 0 | 2022-02-22 | -8.4 | 26.4 | 0 | 2021-02-22 | -8.3 | 26.3 | 0 | 2020-02-22 | -4 | 22 | 0 | 2019-02-22 | -6.6 | 24.6 | 0 | 2018-02-22 | -4.7 | 22.7 | 0 | 2017-02-22 | 0 | 18 | 0 | 2016-02-22 | -12.5 | 30.5 | 0 | 25.02 | 0
2025-02-22 | -16.4 | 34.4 | 0 | 2024-02-22 | 1.8 | 16.2 | 0 | 2023-02-22 | -12.7 | 30.7 | 0 | 2022-02-22 | -8.6 | 26.6 | 0 | 2021-02-22 | -7.9 | 25.9 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -9.4 | 27.4 | 0 | 2018-02-22 | -5.3 | 23.3 | 0 | 2017-02-22 | 0.2 | 17.8 | 0 | 2016-02-22 | -15.3 | 33.3 | 0 | 25.75 | 0
2025-02-22 | -16.5 | 34.5 | 0 | 2024-02-22 | 2 | 16 | 0 | 2023-02-22 | -13.1 | 31.1 | 0 | 2022-02-22 | -8.9 | 26.9 | 0 | 2021-02-22 | -7.3 | 25.3 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -8.6 | 26.6 | 0 | 2018-02-22 | -5.9 | 23.9 | 0 | 2017-02-22 | 0.2 | 17.8 | 0 | 2016-02-22 | -16.1 | 34.1 | 0 | 25.81 | 0
2025-02-22 | -17.6 | 35.6 | 0 | 2024-02-22 | 0.4 | 17.6 | 0 | 2023-02-22 | -13 | 31 | 0 | 2022-02-22 | -9.2 | 27.2 | 0 | 2021-02-22 | -7 | 25 | 0 | 2020-02-22 | -3.9 | 21.9 | 0 | 2019-02-22 | -8.9 | 26.9 | 0 | 2018-02-22 | -6.1 | 24.1 | 0 | 2017-02-22 | 0.3 | 17.7 | 0 | 2016-02-22 | -15 | 33 | 0 | 26 | 0
2025-02-22 | -16.5 | 34.5 | 0 | 2024-02-22 | 1.4 | 16.6 | 0 | 2023-02-22 | -12.8 | 30.8 | 0 | 2022-02-22 | -9.2 | 27.2 | 0 | 2021-02-22 | -6.3 | 24.3 | 0 | 2020-02-22 | -4 | 22 | 0 | 2019-02-22 | -8.2 | 26.2 | 0 | 2018-02-22 | -6.1 | 24.1 | 0 | 2017-02-22 | 0.4 | 17.6 | 0 | 2016-02-22 | -15.6 | 33.6 | 0 | 25.69 | 0
2025-02-22 | -14 | 32 | 0 | 2024-02-22 | 1.4 | 16.6 | 0 | 2023-02-22 | -12.1 | 30.1 | 0 | 2022-02-22 | -8.9 | 26.9 | 0 | 2021-02-22 | -4.6 | 22.6 | 0 | 2020-02-22 | -2.9 | 20.9 | 0 | 2019-02-22 | -7 | 25 | 0 | 2018-02-22 | -6 | 24 | 0 | 2017-02-22 | 0.8 | 17.2 | 0 | 2016-02-22 | -12.9 | 30.9 | 0 | 24.62 | 0
2025-02-22 | -12.4 | 30.4 | 0 | 2024-02-22 | 2 | 16 | 0 | 2023-02-22 | -11.1 | 29.1 | 0 | 2022-02-22 | -8.2 | 26.2 | 0 | 2021-02-22 | -4 | 22 | 0 | 2020-02-22 | -1.7 | 19.7 | 0 | 2019-02-22 | -4.8 | 22.8 | 0 | 2018-02-22 | -5.6 | 23.6 | 0 | 2017-02-22 | 2.8 | 15.2 | 0 | 2016-02-22 | -11.5 | 29.5 | 0 | 23.45 | 0
2025-02-22 | -10.7 | 28.7 | 0 | 2024-02-22 | 2.5 | 15.5 | 0 | 2023-02-22 | -10.6 | 28.6 | 0 | 2022-02-22 | -7.8 | 25.8 | 0 | 2021-02-22 | -3.8 | 21.8 | 0 | 2020-02-22 | -0.6 | 18.6 | 0 | 2019-02-22 | -3.7 | 21.7 | 0 | 2018-02-22 | -4.8 | 22.8 | 0 | 2017-02-22 | 3.2 | 14.8 | 0 | 2016-02-22 | -10.8 | 28.8 | 0 | 22.71 | 0
2025-02-22 | -8.9 | 26.9 | 0 | 2024-02-22 | 4.5 | 13.5 | 0 | 2023-02-22 | -10 | 28 | 0 | 2022-02-22 | -7.3 | 25.3 | 0 | 2021-02-22 | -3.7 | 21.7 | 0 | 2020-02-22 | 0.8 | 17.2 | 0 | 2019-02-22 | -2.4 | 20.4 | 0 | 2018-02-22 | -4.3 | 22.3 | 0 | 2017-02-22 | 3.1 | 14.9 | 0 | 2016-02-22 | -10.3 | 28.3 | 0 | 21.85 | 0
2025-02-22 | -7.2 | 25.2 | 0 | 2024-02-22 | 6 | 12 | 0 | 2023-02-22 | -9.2 | 27.2 | 0 | 2022-02-22 | -6.7 | 24.7 | 0 | 2021-02-22 | -3.2 | 21.2 | 0 | 2020-02-22 | 1.7 | 16.3 | 0 | 2019-02-22 | -2.3 | 20.3 | 0 | 2018-02-22 | -3.9 | 21.9 | 0 | 2017-02-22 | 3.1 | 14.9 | 0 | 2016-02-22 | -9.5 | 27.5 | 0 | 21.12 | 0
2025-02-22 | -6.2 | 24.2 | 0 | 2024-02-22 | 7.3 | 10.7 | 0 | 2023-02-22 | -8.9 | 26.9 | 0 | 2022-02-22 | -6.7 | 24.7 | 0 | 2021-02-22 | -2.6 | 20.6 | 0 | 2020-02-22 | 2.5 | 15.5 | 0 | 2019-02-22 | -1.7 | 19.7 | 0 | 2018-02-22 | -4 | 22 | 0 | 2017-02-22 | 4.1 | 13.9 | 0 | 2016-02-22 | -8.9 | 26.9 | 0 | 20.51 | 0
2025-02-22 | -6.3 | 24.3 | 0 | 2024-02-22 | 7.2 | 10.8 | 0 | 2023-02-22 | -8.9 | 26.9 | 0 | 2022-02-22 | -6 | 24 | 0 | 2021-02-22 | -1.6 | 19.6 | 0 | 2020-02-22 | 2.9 | 15.1 | 0 | 2019-02-22 | -1.1 | 19.1 | 0 | 2018-02-22 | -3.4 | 21.4 | 0 | 2017-02-22 | 4.1 | 13.9 | 0 | 2016-02-22 | -8.6 | 26.6 | 0 | 20.17 | 0
2025-02-22 | -2.5 | 20.5 | 0 | 2024-02-22 | 6 | 12 | 0 | 2023-02-22 | -8.3 | 26.3 | 0 | 2022-02-22 | -6.1 | 24.1 | 0 | 2021-02-22 | -1.9 | 19.9 | 0 | 2020-02-22 | 3.3 | 14.7 | 0 | 2019-02-22 | -1.3 | 19.3 | 0 | 2018-02-22 | -3.2 | 21.2 | 0 | 2017-02-22 | 3.5 | 14.5 | 0 | 2016-02-22 | -8.5 | 26.5 | 0 | 19.9 | 0
2025-02-22 | -2.5 | 20.5 | 0 | 2024-02-22 | 5.1 | 12.9 | 0 | 2023-02-22 | -8 | 26 | 0 | 2022-02-22 | -5.4 | 23.4 | 0 | 2021-02-22 | -1.6 | 19.6 | 0 | 2020-02-22 | 2.9 | 15.1 | 0 | 2019-02-22 | -2.1 | 20.1 | 0 | 2018-02-22 | -2.6 | 20.6 | 0 | 2017-02-22 | 4.1 | 13.9 | 0 | 2016-02-22 | -9.1 | 27.1 | 0 | 19.92 | 0
2025-02-22 | -2.7 | 20.7 | 0 | 2024-02-22 | 3.5 | 14.5 | 0 | 2023-02-22 | -8 | 26 | 0 | 2022-02-22 | -5.3 | 23.3 | 0 | 2021-02-22 | -1.6 | 19.6 | 0 | 2020-02-22 | 1.6 | 16.4 | 0 | 2019-02-22 | -3.2 | 21.2 | 0 | 2018-02-22 | -3.9 | 21.9 | 0 | 2017-02-22 | 3.1 | 14.9 | 0 | 2016-02-22 | -10.2 | 28.2 | 0 | 20.67 | 0
2025-02-22 | -2.7 | 20.7 | 0 | 2024-02-22 | 3.2 | 14.8 | 0 | 2023-02-22 | -8.2 | 26.2 | 0 | 2022-02-22 | -4.1 | 22.1 | 0 | 2021-02-22 | -1.5 | 19.5 | 0 | 2020-02-22 | 0.4 | 17.6 | 0 | 2019-02-22 | -3.7 | 21.7 | 0 | 2018-02-22 | -5.3 | 23.3 | 0 | 2017-02-22 | 3 | 15 | 0 | 2016-02-22 | -11.6 | 29.6 | 0 | 21.05 | 0
2025-02-22 | -2.9 | 20.9 | 0 | 2024-02-22 | 2.9 | 15.1 | 0 | 2023-02-22 | -8.5 | 26.5 | 0 | 2022-02-22 | -2.5 | 20.5 | 0 | 2021-02-22 | -1.2 | 19.2 | 0 | 2020-02-22 | -0.6 | 18.6 | 0 | 2019-02-22 | -4.5 | 22.5 | 0 | 2018-02-22 | -4.9 | 22.9 | 0 | 2017-02-22 | 2.7 | 15.3 | 0 | 2016-02-22 | -12.4 | 30.4 | 0 | 21.19 | 0
2025-02-22 | -3.6 | 21.6 | 0 | 2024-02-22 | 2.6 | 15.4 | 0 | 2023-02-22 | -8.4 | 26.4 | 0 | 2022-02-22 | -2.4 | 20.4 | 0 | 2021-02-22 | -0.7 | 18.7 | 0 | 2020-02-22 | -1.3 | 19.3 | 0 | 2019-02-22 | -5.8 | 23.8 | 0 | 2018-02-22 | -6 | 24 | 0 | 2017-02-22 | 2.7 | 15.3 | 0 | 2016-02-22 | -13.8 | 31.8 | 0 | 21.67 | 0
2025-02-22 | -3.9 | 21.9 | 0 | 2024-02-22 | 2.2 | 15.8 | 0 | 2023-02-22 | -8.4 | 26.4 | 0 | 2022-02-22 | -2 | 20 | 0 | 2021-02-22 | 0 | 18 | 0 | 2020-02-22 | -1.8 | 19.8 | 0 | 2019-02-22 | -6.5 | 24.5 | 0 | 2018-02-22 | -5.7 | 23.7 | 0 | 2017-02-22 | 2.2 | 15.8 | 0 | 2016-02-22 | -15.7 | 33.7 | 0 | 21.96 | 0
2025-02-22 | -4 | 22 | 0 | 2024-02-22 | 2.3 | 15.7 | 0 | 2023-02-22 | -8.9 | 26.9 | 0 | 2022-02-22 | -1.7 | 19.7 | 0 | 2021-02-22 | 0.6 | 17.4 | 0 | 2020-02-22 | -2.1 | 20.1 | 0 | 2019-02-22 | -6.6 | 24.6 | 0 | 2018-02-22 | -6 | 24 | 0 | 2017-02-22 | 2.5 | 15.5 | 0 | 2016-02-22 | -15.7 | 33.7 | 0 | 21.96 | 0
2025-02-23 | -4 | 22 | 0 | 2024-02-23 | 2.2 | 15.8 | 0 | 2023-02-23 | -9.7 | 27.7 | 0 | 2022-02-23 | -1.2 | 19.2 | 0 | 2021-02-23 | 1 | 17 | 0 | 2020-02-23 | -2.5 | 20.5 | 0 | 2019-02-23 | -8.7 | 26.7 | 0 | 2018-02-23 | -5.6 | 23.6 | 0 | 2017-02-23 | 2.5 | 15.5 | 0 | 2016-02-23 | -15.6 | 33.6 | 0 | 22.16 | 0
2025-02-23 | -4.2 | 22.2 | 0 | 2024-02-23 | 2.1 | 15.9 | 0 | 2023-02-23 | -9.9 | 27.9 | 0 | 2022-02-23 | -0.2 | 18.2 | 0 | 2021-02-23 | 0.6 | 17.4 | 0 | 2020-02-23 | -2.8 | 20.8 | 0 | 2019-02-23 | -9.2 | 27.2 | 0 | 2018-02-23 | -6.1 | 24.1 | 0 | 2017-02-23 | 1.9 | 16.1 | 0 | 2016-02-23 | -15.3 | 33.3 | 0 | 22.31 | 0
2025-02-23 | -4.4 | 22.4 | 0 | 2024-02-23 | 2 | 16 | 0 | 2023-02-23 | -10.3 | 28.3 | 0 | 2022-02-23 | 0.8 | 17.2 | 0 | 2021-02-23 | 0.3 | 17.7 | 0 | 2020-02-23 | -2.9 | 20.9 | 0 | 2019-02-23 | -9.3 | 27.3 | 0 | 2018-02-23 | -6.2 | 24.2 | 0 | 2017-02-23 | 2.3 | 15.7 | 0 | 2016-02-23 | -16.1 | 34.1 | 0 | 22.38 | 0
2025-02-23 | -4.6 | 22.6 | 0 | 2024-02-23 | 1.8 | 16.2 | 0 | 2023-02-23 | -11.3 | 29.3 | 0 | 2022-02-23 | -0.1 | 18.1 | 0 | 2021-02-23 | -0.1 | 18.1 | 0 | 2020-02-23 | -3.5 | 21.5 | 0 | 2019-02-23 | -10.3 | 28.3 | 0 | 2018-02-23 | -6.3 | 24.3 | 0 | 2017-02-23 | 2 | 16 | 0 | 2016-02-23 | -16.4 | 34.4 | 0 | 22.88 | 0
2025-02-23 | -4.5 | 22.5 | 0 | 2024-02-23 | 1.6 | 16.4 | 0 | 2023-02-23 | -12.1 | 30.1 | 0 | 2022-02-23 | -1.4 | 19.4 | 0 | 2021-02-23 | -0.3 | 18.3 | 0 | 2020-02-23 | -3.6 | 21.6 | 0 | 2019-02-23 | -10.9 | 28.9 | 0 | 2018-02-23 | -6.5 | 24.5 | 0 | 2017-02-23 | 1.9 | 16.1 | 0 | 2016-02-23 | -17.4 | 35.4 | 0 | 23.32 | 0
2025-02-23 | -4.5 | 22.5 | 0 | 2024-02-23 | 1.2 | 16.8 | 0 | 2023-02-23 | -12.2 | 30.2 | 0 | 2022-02-23 | -2.2 | 20.2 | 0 | 2021-02-23 | -0.3 | 18.3 | 0 | 2020-02-23 | -3.9 | 21.9 | 0 | 2019-02-23 | -9.1 | 27.1 | 0 | 2018-02-23 | -6.8 | 24.8 | 0 | 2017-02-23 | 2.9 | 15.1 | 0 | 2016-02-23 | -17.4 | 35.4 | 0 | 23.23 | 0
2025-02-23 | -4.5 | 22.5 | 0 | 2024-02-23 | 1.1 | 16.9 | 0 | 2023-02-23 | -11.8 | 29.8 | 0 | 2022-02-23 | -3.9 | 21.9 | 0 | 2021-02-23 | -0.1 | 18.1 | 0 | 2020-02-23 | -4.7 | 22.7 | 0 | 2019-02-23 | -8.4 | 26.4 | 0 | 2018-02-23 | -7 | 25 | 0 | 2017-02-23 | 4.6 | 13.4 | 0 | 2016-02-23 | -17.8 | 35.8 | 0 | 23.25 | 0
2025-02-23 | -4.5 | 22.5 | 0 | 2024-02-23 | 1 | 17 | 0 | 2023-02-23 | -11.9 | 29.9 | 0 | 2022-02-23 | -6.3 | 24.3 | 0 | 2021-02-23 | 0.1 | 17.9 | 0 | 2020-02-23 | -4.6 | 22.6 | 0 | 2019-02-23 | -8.3 | 26.3 | 0 | 2018-02-23 | -6.9 | 24.9 | 0 | 2017-02-23 | 5.6 | 12.4 | 0 | 2016-02-23 | -16.2 | 34.2 | 0 | 23.2 | 0
2025-02-23 | -4.1 | 22.1 | 0 | 2024-02-23 | 1 | 17 | 0 | 2023-02-23 | -12 | 30 | 0 | 2022-02-23 | -8 | 26 | 0 | 2021-02-23 | -0.2 | 18.2 | 0 | 2020-02-23 | -4.2 | 22.2 | 0 | 2019-02-23 | -7.2 | 25.2 | 0 | 2018-02-23 | -6.5 | 24.5 | 0 | 2017-02-23 | 7 | 11 | 0 | 2016-02-23 | -15.4 | 33.4 | 0 | 22.96 | 0
2025-02-23 | -3.7 | 21.7 | 0 | 2024-02-23 | 1.4 | 16.6 | 0 | 2023-02-23 | -11.8 | 29.8 | 0 | 2022-02-23 | -9.3 | 27.3 | 0 | 2021-02-23 | 0 | 18 | 0 | 2020-02-23 | -1.4 | 19.4 | 0 | 2019-02-23 | -5.1 | 23.1 | 0 | 2018-02-23 | -5.8 | 23.8 | 0 | 2017-02-23 | 8.2 | 9.8 | 0 | 2016-02-23 | -13.9 | 31.9 | 0 | 22.14 | 0
2025-02-23 | -3.5 | 21.5 | 0 | 2024-02-23 | 2 | 16 | 0 | 2023-02-23 | -11.3 | 29.3 | 0 | 2022-02-23 | -9.8 | 27.8 | 0 | 2021-02-23 | 0.5 | 17.5 | 0 | 2020-02-23 | 1.1 | 16.9 | 0 | 2019-02-23 | -4.4 | 22.4 | 0 | 2018-02-23 | -4.6 | 22.6 | 0 | 2017-02-23 | 7.3 | 10.7 | 0 | 2016-02-23 | -12.1 | 30.1 | 0 | 21.48 | 0
2025-02-23 | -2.8 | 20.8 | 0 | 2024-02-23 | 2.3 | 15.7 | 0 | 2023-02-23 | -10.9 | 28.9 | 0 | 2022-02-23 | -9.9 | 27.9 | 0 | 2021-02-23 | 0.9 | 17.1 | 0 | 2020-02-23 | 3 | 15 | 0 | 2019-02-23 | -2.4 | 20.4 | 0 | 2018-02-23 | -4 | 22 | 0 | 2017-02-23 | 8.6 | 9.4 | 0 | 2016-02-23 | -10.5 | 28.5 | 0 | 20.57 | 0
2025-02-23 | -2.7 | 20.7 | 0 | 2024-02-23 | 2.6 | 15.4 | 0 | 2023-02-23 | -10.7 | 28.7 | 0 | 2022-02-23 | -9.5 | 27.5 | 0 | 2021-02-23 | 0.9 | 17.1 | 0 | 2020-02-23 | 3.9 | 14.1 | 0 | 2019-02-23 | -0.6 | 18.6 | 0 | 2018-02-23 | -3.6 | 21.6 | 0 | 2017-02-23 | 9.6 | 8.4 | 0 | 2016-02-23 | -9 | 27 | 0 | 19.91 | 0
2025-02-23 | -2.1 | 20.1 | 0 | 2024-02-23 | 3.4 | 14.6 | 0 | 2023-02-23 | -10.4 | 28.4 | 0 | 2022-02-23 | -9.2 | 27.2 | 0 | 2021-02-23 | 0.8 | 17.2 | 0 | 2020-02-23 | 4.6 | 13.4 | 0 | 2019-02-23 | 0 | 18 | 0 | 2018-02-23 | -3.5 | 21.5 | 0 | 2017-02-23 | 9.5 | 8.5 | 0 | 2016-02-23 | -7.8 | 25.8 | 0 | 19.47 | 0
2025-02-23 | -1.8 | 19.8 | 0 | 2024-02-23 | 3.5 | 14.5 | 0 | 2023-02-23 | -9.6 | 27.6 | 0 | 2022-02-23 | -8.9 | 26.9 | 0 | 2021-02-23 | 1.1 | 16.9 | 0 | 2020-02-23 | 5.9 | 12.1 | 0 | 2019-02-23 | 0.2 | 17.8 | 0 | 2018-02-23 | -3.5 | 21.5 | 0 | 2017-02-23 | 10.7 | 7.3 | 0 | 2016-02-23 | -7.1 | 25.1 | 0 | 18.95 | 0
2025-02-23 | -1.6 | 19.6 | 0 | 2024-02-23 | 3.2 | 14.8 | 0 | 2023-02-23 | -9.8 | 27.8 | 0 | 2022-02-23 | -9.7 | 27.7 | 0 | 2021-02-23 | 0.8 | 17.2 | 0 | 2020-02-23 | 5.3 | 12.7 | 0 | 2019-02-23 | 0.1 | 17.9 | 0 | 2018-02-23 | -3 | 21 | 0 | 2017-02-23 | 11.2 | 6.8 | 0 | 2016-02-23 | -6.8 | 24.8 | 0 | 19.03 | 0
2025-02-23 | -1.5 | 19.5 | 0 | 2024-02-23 | -0.4 | 18.4 | 0 | 2023-02-23 | -10.7 | 28.7 | 0 | 2022-02-23 | -10.2 | 28.2 | 0 | 2021-02-23 | 1 | 17 | 0 | 2020-02-23 | 5.6 | 12.4 | 0 | 2019-02-23 | -0.1 | 18.1 | 0 | 2018-02-23 | -2.7 | 20.7 | 0 | 2017-02-23 | 11.2 | 6.8 | 0 | 2016-02-23 | -7.1 | 25.1 | 0 | 19.49 | 0
2025-02-23 | -1.6 | 19.6 | 0 | 2024-02-23 | -2.7 | 20.7 | 0 | 2023-02-23 | -11.5 | 29.5 | 0 | 2022-02-23 | -10.9 | 28.9 | 0 | 2021-02-23 | 1 | 17 | 0 | 2020-02-23 | 4.7 | 13.3 | 0 | 2019-02-23 | -0.5 | 18.5 | 0 | 2018-02-23 | -2.3 | 20.3 | 0 | 2017-02-23 | 10.2 | 7.8 | 0 | 2016-02-23 | -7.2 | 25.2 | 0 | 20.08 | 0
2025-02-23 | -2.1 | 20.1 | 0 | 2024-02-23 | -4.7 | 22.7 | 0 | 2023-02-23 | -11.7 | 29.7 | 0 | 2022-02-23 | -11.6 | 29.6 | 0 | 2021-02-23 | 1.1 | 16.9 | 0 | 2020-02-23 | 3.7 | 14.3 | 0 | 2019-02-23 | -1.6 | 19.6 | 0 | 2018-02-23 | -1.4 | 19.4 | 0 | 2017-02-23 | 9.8 | 8.2 | 0 | 2016-02-23 | -7.7 | 25.7 | 0 | 20.62 | 0
2025-02-23 | -2.1 | 20.1 | 0 | 2024-02-23 | -6.6 | 24.6 | 0 | 2023-02-23 | -11.7 | 29.7 | 0 | 2022-02-23 | -12 | 30 | 0 | 2021-02-23 | 1.4 | 16.6 | 0 | 2020-02-23 | 2.8 | 15.2 | 0 | 2019-02-23 | -2 | 20 | 0 | 2018-02-23 | -0.9 | 18.9 | 0 | 2017-02-23 | 7.4 | 10.6 | 0 | 2016-02-23 | -7.7 | 25.7 | 0 | 21.14 | 0
2025-02-23 | -2.9 | 20.9 | 0 | 2024-02-23 | -8.2 | 26.2 | 0 | 2023-02-23 | -11.9 | 29.9 | 0 | 2022-02-23 | -12.5 | 30.5 | 0 | 2021-02-23 | 1.7 | 16.3 | 0 | 2020-02-23 | 2.5 | 15.5 | 0 | 2019-02-23 | -2.3 | 20.3 | 0 | 2018-02-23 | -0.7 | 18.7 | 0 | 2017-02-23 | 6 | 12 | 0 | 2016-02-23 | -7.6 | 25.6 | 0 | 21.59 | 0
2025-02-23 | -3.6 | 21.6 | 0 | 2024-02-23 | -9.1 | 27.1 | 0 | 2023-02-23 | -11.8 | 29.8 | 0 | 2022-02-23 | -12.7 | 30.7 | 0 | 2021-02-23 | 2.1 | 15.9 | 0 | 2020-02-23 | 2.8 | 15.2 | 0 | 2019-02-23 | -2.5 | 20.5 | 0 | 2018-02-23 | 0.3 | 17.7 | 0 | 2017-02-23 | 4.8 | 13.2 | 0 | 2016-02-23 | -7.3 | 25.3 | 0 | 21.7 | 0
2025-02-23 | -3.7 | 21.7 | 0 | 2024-02-23 | -9.9 | 27.9 | 0 | 2023-02-23 | -11.7 | 29.7 | 0 | 2022-02-23 | -13.3 | 31.3 | 0 | 2021-02-23 | 1.8 | 16.2 | 0 | 2020-02-23 | 2.6 | 15.4 | 0 | 2019-02-23 | -3 | 21 | 0 | 2018-02-23 | 1.1 | 16.9 | 0 | 2017-02-23 | 4.1 | 13.9 | 0 | 2016-02-23 | -7 | 25 | 0 | 21.9 | 0
2025-02-23 | -3.6 | 21.6 | 0 | 2024-02-23 | -10.9 | 28.9 | 0 | 2023-02-23 | -11.6 | 29.6 | 0 | 2022-02-23 | -13.8 | 31.8 | 0 | 2021-02-23 | 2 | 16 | 0 | 2020-02-23 | 2.9 | 15.1 | 0 | 2019-02-23 | -3.5 | 21.5 | 0 | 2018-02-23 | 1.8 | 16.2 | 0 | 2017-02-23 | 3.6 | 14.4 | 0 | 2016-02-23 | -6.8 | 24.8 | 0 | 21.99 | 0
2025-02-24 | -3.4 | 21.4 | 0 | 2024-02-24 | -11.8 | 29.8 | 0 | 2023-02-24 | -11.7 | 29.7 | 0 | 2022-02-24 | -14.3 | 32.3 | 0 | 2021-02-24 | 1.6 | 16.4 | 0 | 2020-02-24 | 2.4 | 15.6 | 0 | 2019-02-24 | -2.9 | 20.9 | 0 | 2018-02-24 | 2.6 | 15.4 | 0 | 2017-02-24 | 2.9 | 15.1 | 0 | 2016-02-24 | -6.7 | 24.7 | 0 | 22.13 | 0
2025-02-24 | -3.8 | 21.8 | 0 | 2024-02-24 | -12.9 | 30.9 | 0 | 2023-02-24 | -11.5 | 29.5 | 0 | 2022-02-24 | -15 | 33 | 0 | 2021-02-24 | 1.4 | 16.6 | 0 | 2020-02-24 | 2.7 | 15.3 | 0 | 2019-02-24 | -2.5 | 20.5 | 0 | 2018-02-24 | 2.1 | 15.9 | 0 | 2017-02-24 | 1.8 | 16.2 | 0 | 2016-02-24 | -6.4 | 24.4 | 0 | 22.41 | 0
2025-02-24 | -3.4 | 21.4 | 0 | 2024-02-24 | -14 | 32 | 0 | 2023-02-24 | -11.7 | 29.7 | 0 | 2022-02-24 | -15.5 | 33.5 | 0 | 2021-02-24 | 0.9 | 17.1 | 0 | 2020-02-24 | 2.1 | 15.9 | 0 | 2019-02-24 | -2.9 | 20.9 | 0 | 2018-02-24 | 2.5 | 15.5 | 0 | 2017-02-24 | 1.2 | 16.8 | 0 | 2016-02-24 | -6.3 | 24.3 | 0 | 22.71 | 0
2025-02-24 | -3.2 | 21.2 | 0 | 2024-02-24 | -14.8 | 32.8 | 0 | 2023-02-24 | -11.6 | 29.6 | 0 | 2022-02-24 | -15.8 | 33.8 | 0 | 2021-02-24 | 0.2 | 17.8 | 0 | 2020-02-24 | 1.4 | 16.6 | 0 | 2019-02-24 | -2.9 | 20.9 | 0 | 2018-02-24 | 2.4 | 15.6 | 0 | 2017-02-24 | 1.3 | 16.7 | 0 | 2016-02-24 | -6.1 | 24.1 | 0 | 22.91 | 0
2025-02-24 | -3 | 21 | 0 | 2024-02-24 | -15.5 | 33.5 | 0 | 2023-02-24 | -13.5 | 31.5 | 0 | 2022-02-24 | -16.9 | 34.9 | 0 | 2021-02-24 | -1.3 | 19.3 | 0 | 2020-02-24 | 0.4 | 17.6 | 0 | 2019-02-24 | -3.7 | 21.7 | 0 | 2018-02-24 | 2.5 | 15.5 | 0 | 2017-02-24 | -0.5 | 18.5 | 0 | 2016-02-24 | -6 | 24 | 0 | 23.75 | 0
2025-02-24 | -2.6 | 20.6 | 0 | 2024-02-24 | -15.9 | 33.9 | 0 | 2023-02-24 | -13.6 | 31.6 | 0 | 2022-02-24 | -17.1 | 35.1 | 0 | 2021-02-24 | -1.5 | 19.5 | 0 | 2020-02-24 | 0.7 | 17.3 | 0 | 2019-02-24 | -3.6 | 21.6 | 0 | 2018-02-24 | 2.1 | 15.9 | 0 | 2017-02-24 | 0.8 | 17.2 | 0 | 2016-02-24 | -6.2 | 24.2 | 0 | 23.69 | 0
2025-02-24 | -1.9 | 19.9 | 0 | 2024-02-24 | -16.6 | 34.6 | 0 | 2023-02-24 | -15.1 | 33.1 | 0 | 2022-02-24 | -17.2 | 35.2 | 0 | 2021-02-24 | -2.3 | 20.3 | 0 | 2020-02-24 | 0.6 | 17.4 | 0 | 2019-02-24 | -3.5 | 21.5 | 0 | 2018-02-24 | 1.9 | 16.1 | 0 | 2017-02-24 | 0.5 | 17.5 | 0 | 2016-02-24 | -6.4 | 24.4 | 0 | 24 | 0
2025-02-24 | -1.8 | 19.8 | 0 | 2024-02-24 | -16.8 | 34.8 | 0 | 2023-02-24 | -15.5 | 33.5 | 0 | 2022-02-24 | -17.5 | 35.5 | 0 | 2021-02-24 | -2.8 | 20.8 | 0 | 2020-02-24 | 0.2 | 17.8 | 0 | 2019-02-24 | -2.7 | 20.7 | 0 | 2018-02-24 | 1.8 | 16.2 | 0 | 2017-02-24 | 0.3 | 17.7 | 0 | 2016-02-24 | -6.3 | 24.3 | 0 | 24.11 | 0
2025-02-24 | -1.4 | 19.4 | 0 | 2024-02-24 | -16 | 34 | 0 | 2023-02-24 | -15.6 | 33.6 | 0 | 2022-02-24 | -17.2 | 35.2 | 0 | 2021-02-24 | -2.1 | 20.1 | 0 | 2020-02-24 | 0.5 | 17.5 | 0 | 2019-02-24 | -1.6 | 19.6 | 0 | 2018-02-24 | 1 | 17 | 0 | 2017-02-24 | 0.6 | 17.4 | 0 | 2016-02-24 | -5.7 | 23.7 | 0 | 23.75 | 0
2025-02-24 | -0.8 | 18.8 | 0 | 2024-02-24 | -15.6 | 33.6 | 0 | 2023-02-24 | -15.4 | 33.4 | 0 | 2022-02-24 | -16.4 | 34.4 | 0 | 2021-02-24 | -0.9 | 18.9 | 0 | 2020-02-24 | 2.6 | 15.4 | 0 | 2019-02-24 | -0.3 | 18.3 | 0 | 2018-02-24 | 0.8 | 17.2 | 0 | 2017-02-24 | 1.5 | 16.5 | 0 | 2016-02-24 | -4.8 | 22.8 | 0 | 22.93 | 0
2025-02-24 | 0.6 | 17.4 | 0 | 2024-02-24 | -14.3 | 32.3 | 0 | 2023-02-24 | -14.9 | 32.9 | 0 | 2022-02-24 | -15.4 | 33.4 | 0 | 2021-02-24 | -0.1 | 18.1 | 0 | 2020-02-24 | 4.1 | 13.9 | 0 | 2019-02-24 | 0 | 18 | 0 | 2018-02-24 | 0.8 | 17.2 | 0 | 2017-02-24 | 1.6 | 16.4 | 0 | 2016-02-24 | -3.8 | 21.8 | 0 | 22.14 | 0
2025-02-24 | 1.6 | 16.4 | 0 | 2024-02-24 | -13.3 | 31.3 | 0 | 2023-02-24 | -14.6 | 32.6 | 0 | 2022-02-24 | -14.1 | 32.1 | 0 | 2021-02-24 | 1.4 | 16.6 | 0 | 2020-02-24 | 5.2 | 12.8 | 0 | 2019-02-24 | 0.3 | 17.7 | 0 | 2018-02-24 | 0.4 | 17.6 | 0 | 2017-02-24 | 2 | 16 | 0 | 2016-02-24 | -2.4 | 20.4 | 0 | 21.35 | 0
2025-02-24 | 2.6 | 15.4 | 0 | 2024-02-24 | -11.9 | 29.9 | 0 | 2023-02-24 | -13.9 | 31.9 | 0 | 2022-02-24 | -12.8 | 30.8 | 0 | 2021-02-24 | 0.8 | 17.2 | 0 | 2020-02-24 | 6.8 | 11.2 | 0 | 2019-02-24 | 0.3 | 17.7 | 0 | 2018-02-24 | 0.4 | 17.6 | 0 | 2017-02-24 | 2.2 | 15.8 | 0 | 2016-02-24 | -1.4 | 19.4 | 0 | 20.69 | 0
2025-02-24 | 2.9 | 15.1 | 0 | 2024-02-24 | -11.4 | 29.4 | 0 | 2023-02-24 | -13.1 | 31.1 | 0 | 2022-02-24 | -12.1 | 30.1 | 0 | 2021-02-24 | 0.2 | 17.8 | 0 | 2020-02-24 | 7.2 | 10.8 | 0 | 2019-02-24 | 0.8 | 17.2 | 0 | 2018-02-24 | 0.6 | 17.4 | 0 | 2017-02-24 | 2 | 16 | 0 | 2016-02-24 | -0.6 | 18.6 | 0 | 20.35 | 0
2025-02-24 | 4 | 14 | 0 | 2024-02-24 | -11 | 29 | 0 | 2023-02-24 | -13.5 | 31.5 | 0 | 2022-02-24 | -11 | 29 | 0 | 2021-02-24 | 0.2 | 17.8 | 0 | 2020-02-24 | 7.2 | 10.8 | 0 | 2019-02-24 | 1.6 | 16.4 | 0 | 2018-02-24 | 0.7 | 17.3 | 0 | 2017-02-24 | 1.9 | 16.1 | 0 | 2016-02-24 | -0.6 | 18.6 | 0 | 20.05 | 0
2025-02-24 | 4.5 | 13.5 | 0 | 2024-02-24 | -10.2 | 28.2 | 0 | 2023-02-24 | -13.2 | 31.2 | 0 | 2022-02-24 | -10.7 | 28.7 | 0 | 2021-02-24 | 0.1 | 17.9 | 0 | 2020-02-24 | 8.1 | 9.9 | 0 | 2019-02-24 | 1.6 | 16.4 | 0 | 2018-02-24 | 1 | 17 | 0 | 2017-02-24 | 1.9 | 16.1 | 0 | 2016-02-24 | -0.5 | 18.5 | 0 | 19.74 | 0
2025-02-24 | 4.9 | 13.1 | 0 | 2024-02-24 | -10 | 28 | 0 | 2023-02-24 | -13 | 31 | 0 | 2022-02-24 | -10.3 | 28.3 | 0 | 2021-02-24 | 0 | 18 | 0 | 2020-02-24 | 8.2 | 9.8 | 0 | 2019-02-24 | 2.3 | 15.7 | 0 | 2018-02-24 | 0.8 | 17.2 | 0 | 2017-02-24 | 1.7 | 16.3 | 0 | 2016-02-24 | -0.3 | 18.3 | 0 | 19.57 | 0
2025-02-24 | 5.3 | 12.7 | 0 | 2024-02-24 | -10.5 | 28.5 | 0 | 2023-02-24 | -13.1 | 31.1 | 0 | 2022-02-24 | -10.1 | 28.1 | 0 | 2021-02-24 | 0 | 18 | 0 | 2020-02-24 | 6.8 | 11.2 | 0 | 2019-02-24 | 4.2 | 13.8 | 0 | 2018-02-24 | 0.6 | 17.4 | 0 | 2017-02-24 | 1.8 | 16.2 | 0 | 2016-02-24 | -0.1 | 18.1 | 0 | 19.51 | 0
2025-02-24 | 5.6 | 12.4 | 0 | 2024-02-24 | -11.4 | 29.4 | 0 | 2023-02-24 | -14.2 | 32.2 | 0 | 2022-02-24 | -10.5 | 28.5 | 0 | 2021-02-24 | 0 | 18 | 0 | 2020-02-24 | 4.8 | 13.2 | 0 | 2019-02-24 | 2.7 | 15.3 | 0 | 2018-02-24 | -0.3 | 18.3 | 0 | 2017-02-24 | 1.6 | 16.4 | 0 | 2016-02-24 | 0.1 | 17.9 | 0 | 20.16 | 0
2025-02-24 | 5.6 | 12.4 | 0 | 2024-02-24 | -12.1 | 30.1 | 0 | 2023-02-24 | -14.6 | 32.6 | 0 | 2022-02-24 | -11 | 29 | 0 | 2021-02-24 | 0 | 18 | 0 | 2020-02-24 | 4 | 14 | 0 | 2019-02-24 | 2 | 16 | 0 | 2018-02-24 | -1 | 19 | 0 | 2017-02-24 | 1.4 | 16.6 | 0 | 2016-02-24 | 0.2 | 17.8 | 0 | 20.55 | 0
2025-02-24 | 5.4 | 12.6 | 0 | 2024-02-24 | -12.8 | 30.8 | 0 | 2023-02-24 | -15.3 | 33.3 | 0 | 2022-02-24 | -11.7 | 29.7 | 0 | 2021-02-24 | 0 | 18 | 0 | 2020-02-24 | 3.4 | 14.6 | 0 | 2019-02-24 | 1.4 | 16.6 | 0 | 2018-02-24 | -1.9 | 19.9 | 0 | 2017-02-24 | 1.1 | 16.9 | 0 | 2016-02-24 | 0.1 | 17.9 | 0 | 21.03 | 0
2025-02-24 | 5 | 13 | 0 | 2024-02-24 | -12.6 | 30.6 | 0 | 2023-02-24 | -17 | 35 | 0 | 2022-02-24 | -12.5 | 30.5 | 0 | 2021-02-24 | 0.1 | 17.9 | 0 | 2020-02-24 | 2.8 | 15.2 | 0 | 2019-02-24 | 1.5 | 16.5 | 0 | 2018-02-24 | -1.9 | 19.9 | 0 | 2017-02-24 | 1.2 | 16.8 | 0 | 2016-02-24 | 0.1 | 17.9 | 0 | 21.33 | 0
2025-02-24 | 4.4 | 13.6 | 0 | 2024-02-24 | -13.1 | 31.1 | 0 | 2023-02-24 | -19.2 | 37.2 | 0 | 2022-02-24 | -13.2 | 31.2 | 0 | 2021-02-24 | 0.1 | 17.9 | 0 | 2020-02-24 | 1.9 | 16.1 | 0 | 2019-02-24 | 1.1 | 16.9 | 0 | 2018-02-24 | -2.6 | 20.6 | 0 | 2017-02-24 | 1 | 17 | 0 | 2016-02-24 | 0.1 | 17.9 | 0 | 21.95 | 0
2025-02-24 | 4.1 | 13.9 | 0 | 2024-02-24 | -13.4 | 31.4 | 0 | 2023-02-24 | -17.7 | 35.7 | 0 | 2022-02-24 | -13.6 | 31.6 | 0 | 2021-02-24 | -0.5 | 18.5 | 0 | 2020-02-24 | 1.9 | 16.1 | 0 | 2019-02-24 | 1.3 | 16.7 | 0 | 2018-02-24 | -2.9 | 20.9 | 0 | 2017-02-24 | 1.4 | 16.6 | 0 | 2016-02-24 | 0.3 | 17.7 | 0 | 21.91 | 0
2025-02-25 | 3.7 | 14.3 | 0 | 2024-02-25 | -14 | 32 | 0 | 2023-02-25 | -19 | 37 | 0 | 2022-02-25 | -13.2 | 31.2 | 0 | 2021-02-25 | -1.3 | 19.3 | 0 | 2020-02-25 | 2 | 16 | 0 | 2019-02-25 | 1.1 | 16.9 | 0 | 2018-02-25 | -2.9 | 20.9 | 0 | 2017-02-25 | 0.9 | 17.1 | 0 | 2016-02-25 | 0.2 | 17.8 | 0 | 22.25 | 0
2025-02-25 | 3.4 | 14.6 | 0 | 2024-02-25 | -13.9 | 31.9 | 0 | 2023-02-25 | -20.1 | 38.1 | 0 | 2022-02-25 | -13.3 | 31.3 | 0 | 2021-02-25 | -2.4 | 20.4 | 0 | 2020-02-25 | 2.1 | 15.9 | 0 | 2019-02-25 | 0.1 | 17.9 | 0 | 2018-02-25 | -2.6 | 20.6 | 0 | 2017-02-25 | 1 | 17 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 22.54 | 0
2025-02-25 | 3 | 15 | 0 | 2024-02-25 | -14 | 32 | 0 | 2023-02-25 | -21.1 | 39.1 | 0 | 2022-02-25 | -13.3 | 31.3 | 0 | 2021-02-25 | -3.7 | 21.7 | 0 | 2020-02-25 | 2 | 16 | 0 | 2019-02-25 | -0.4 | 18.4 | 0 | 2018-02-25 | -2.7 | 20.7 | 0 | 2017-02-25 | 1 | 17 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 22.89 | 0
2025-02-25 | 2 | 16 | 0 | 2024-02-25 | -13.9 | 31.9 | 0 | 2023-02-25 | -20.6 | 38.6 | 0 | 2022-02-25 | -13.2 | 31.2 | 0 | 2021-02-25 | -4.3 | 22.3 | 0 | 2020-02-25 | 1.6 | 16.4 | 0 | 2019-02-25 | -1.3 | 19.3 | 0 | 2018-02-25 | -2.5 | 20.5 | 0 | 2017-02-25 | 0.7 | 17.3 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 23.12 | 0
2025-02-25 | 0.9 | 17.1 | 0 | 2024-02-25 | -13.9 | 31.9 | 0 | 2023-02-25 | -22.6 | 40.6 | 0 | 2022-02-25 | -13.1 | 31.1 | 0 | 2021-02-25 | -4.8 | 22.8 | 0 | 2020-02-25 | 1 | 17 | 0 | 2019-02-25 | -1.7 | 19.7 | 0 | 2018-02-25 | -2.6 | 20.6 | 0 | 2017-02-25 | 0.6 | 17.4 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 23.59 | 0
2025-02-25 | -0.2 | 18.2 | 0 | 2024-02-25 | -14.2 | 32.2 | 0 | 2023-02-25 | -22.2 | 40.2 | 0 | 2022-02-25 | -13 | 31 | 0 | 2021-02-25 | -5.3 | 23.3 | 0 | 2020-02-25 | 1.4 | 16.6 | 0 | 2019-02-25 | -2.3 | 20.3 | 0 | 2018-02-25 | -2.7 | 20.7 | 0 | 2017-02-25 | 0.4 | 17.6 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 23.78 | 0
2025-02-25 | -0.7 | 18.7 | 0 | 2024-02-25 | -13.8 | 31.8 | 0 | 2023-02-25 | -22.5 | 40.5 | 0 | 2022-02-25 | -12.9 | 30.9 | 0 | 2021-02-25 | -5.9 | 23.9 | 0 | 2020-02-25 | 1.1 | 16.9 | 0 | 2019-02-25 | -2.6 | 20.6 | 0 | 2018-02-25 | -2.9 | 20.9 | 0 | 2017-02-25 | 0.4 | 17.6 | 0 | 2016-02-25 | 0.3 | 17.7 | 0 | 23.95 | 0
2025-02-25 | -1 | 19 | 0 | 2024-02-25 | -14.1 | 32.1 | 0 | 2023-02-25 | -20.7 | 38.7 | 0 | 2022-02-25 | -13.2 | 31.2 | 0 | 2021-02-25 | -7.3 | 25.3 | 0 | 2020-02-25 | 0.6 | 17.4 | 0 | 2019-02-25 | -3.5 | 21.5 | 0 | 2018-02-25 | -3.2 | 21.2 | 0 | 2017-02-25 | 0.5 | 17.5 | 0 | 2016-02-25 | 0.6 | 17.4 | 0 | 24.13 | 0
2025-02-25 | -0.3 | 18.3 | 0 | 2024-02-25 | -11.9 | 29.9 | 0 | 2023-02-25 | -19.6 | 37.6 | 0 | 2022-02-25 | -13.6 | 31.6 | 0 | 2021-02-25 | -5.7 | 23.7 | 0 | 2020-02-25 | 1 | 17 | 0 | 2019-02-25 | -4.8 | 22.8 | 0 | 2018-02-25 | -3.5 | 21.5 | 0 | 2017-02-25 | 0.4 | 17.6 | 0 | 2016-02-25 | 0.6 | 17.4 | 0 | 23.74 | 0
2025-02-25 | 1.1 | 16.9 | 0 | 2024-02-25 | -7.8 | 25.8 | 0 | 2023-02-25 | -17.1 | 35.1 | 0 | 2022-02-25 | -13.3 | 31.3 | 0 | 2021-02-25 | -5.3 | 23.3 | 0 | 2020-02-25 | 1.4 | 16.6 | 0 | 2019-02-25 | -5.4 | 23.4 | 0 | 2018-02-25 | -3.2 | 21.2 | 0 | 2017-02-25 | 0.6 | 17.4 | 0 | 2016-02-25 | 0.8 | 17.2 | 0 | 22.82 | 0
2025-02-25 | 2.9 | 15.1 | 0 | 2024-02-25 | -4.7 | 22.7 | 0 | 2023-02-25 | -15.2 | 33.2 | 0 | 2022-02-25 | -12.7 | 30.7 | 0 | 2021-02-25 | -6.6 | 24.6 | 0 | 2020-02-25 | 2 | 16 | 0 | 2019-02-25 | -6 | 24 | 0 | 2018-02-25 | -2.2 | 20.2 | 0 | 2017-02-25 | 1.1 | 16.9 | 0 | 2016-02-25 | 1.1 | 16.9 | 0 | 22.03 | 0
2025-02-25 | 4 | 14 | 0 | 2024-02-25 | -2.3 | 20.3 | 0 | 2023-02-25 | -13.9 | 31.9 | 0 | 2022-02-25 | -12.8 | 30.8 | 0 | 2021-02-25 | -7.5 | 25.5 | 0 | 2020-02-25 | 2.1 | 15.9 | 0 | 2019-02-25 | -6.1 | 24.1 | 0 | 2018-02-25 | -0.8 | 18.8 | 0 | 2017-02-25 | 1.3 | 16.7 | 0 | 2016-02-25 | 1.1 | 16.9 | 0 | 21.49 | 0
2025-02-25 | 4.3 | 13.7 | 0 | 2024-02-25 | -1 | 19 | 0 | 2023-02-25 | -13.9 | 31.9 | 0 | 2022-02-25 | -12.6 | 30.6 | 0 | 2021-02-25 | -7.6 | 25.6 | 0 | 2020-02-25 | 2.6 | 15.4 | 0 | 2019-02-25 | -6.6 | 24.6 | 0 | 2018-02-25 | 0.2 | 17.8 | 0 | 2017-02-25 | 1.7 | 16.3 | 0 | 2016-02-25 | 0.5 | 17.5 | 0 | 21.24 | 0
2025-02-25 | 3.8 | 14.2 | 0 | 2024-02-25 | -0.9 | 18.9 | 0 | 2023-02-25 | -14 | 32 | 0 | 2022-02-25 | -12.1 | 30.1 | 0 | 2021-02-25 | -7.5 | 25.5 | 0 | 2020-02-25 | 3.3 | 14.7 | 0 | 2019-02-25 | -7.3 | 25.3 | 0 | 2018-02-25 | 0.7 | 17.3 | 0 | 2017-02-25 | 1.6 | 16.4 | 0 | 2016-02-25 | 0.1 | 17.9 | 0 | 21.23 | 0
2025-02-25 | 3.1 | 14.9 | 0 | 2024-02-25 | 0 | 18 | 0 | 2023-02-25 | -13.6 | 31.6 | 0 | 2022-02-25 | -11.2 | 29.2 | 0 | 2021-02-25 | -7.5 | 25.5 | 0 | 2020-02-25 | 4 | 14 | 0 | 2019-02-25 | -7.6 | 25.6 | 0 | 2018-02-25 | 1.5 | 16.5 | 0 | 2017-02-25 | 1.5 | 16.5 | 0 | 2016-02-25 | -0.4 | 18.4 | 0 | 21.02 | 0
2025-02-25 | 2.5 | 15.5 | 0 | 2024-02-25 | 0.6 | 17.4 | 0 | 2023-02-25 | -13.6 | 31.6 | 0 | 2022-02-25 | -10.5 | 28.5 | 0 | 2021-02-25 | -7.7 | 25.7 | 0 | 2020-02-25 | 4.2 | 13.8 | 0 | 2019-02-25 | -6.6 | 24.6 | 0 | 2018-02-25 | 2.8 | 15.2 | 0 | 2017-02-25 | 2.1 | 15.9 | 0 | 2016-02-25 | -0.6 | 18.6 | 0 | 20.68 | 0
2025-02-25 | 2.1 | 15.9 | 0 | 2024-02-25 | 0.8 | 17.2 | 0 | 2023-02-25 | -13.6 | 31.6 | 0 | 2022-02-25 | -10.7 | 28.7 | 0 | 2021-02-25 | -7.8 | 25.8 | 0 | 2020-02-25 | 4.2 | 13.8 | 0 | 2019-02-25 | -6.7 | 24.7 | 0 | 2018-02-25 | 7.5 | 10.5 | 0 | 2017-02-25 | 3.5 | 14.5 | 0 | 2016-02-25 | -1.4 | 19.4 | 0 | 20.21 | 0
2025-02-25 | 2.2 | 15.8 | 0 | 2024-02-25 | 0.7 | 17.3 | 0 | 2023-02-25 | -14.3 | 32.3 | 0 | 2022-02-25 | -11.6 | 29.6 | 0 | 2021-02-25 | -8.5 | 26.5 | 0 | 2020-02-25 | 3.9 | 14.1 | 0 | 2019-02-25 | -7.5 | 25.5 | 0 | 2018-02-25 | 7.2 | 10.8 | 0 | 2017-02-25 | 3 | 15 | 0 | 2016-02-25 | -1.4 | 19.4 | 0 | 20.63 | 0
2025-02-25 | 1.9 | 16.1 | 0 | 2024-02-25 | 0.6 | 17.4 | 0 | 2023-02-25 | -14.9 | 32.9 | 0 | 2022-02-25 | -13.8 | 31.8 | 0 | 2021-02-25 | -10.8 | 28.8 | 0 | 2020-02-25 | 3.5 | 14.5 | 0 | 2019-02-25 | -8.4 | 26.4 | 0 | 2018-02-25 | 6.1 | 11.9 | 0 | 2017-02-25 | 2.8 | 15.2 | 0 | 2016-02-25 | -2.1 | 20.1 | 0 | 21.51 | 0
2025-02-25 | 1.9 | 16.1 | 0 | 2024-02-25 | 0.9 | 17.1 | 0 | 2023-02-25 | -16.1 | 34.1 | 0 | 2022-02-25 | -14.2 | 32.2 | 0 | 2021-02-25 | -10.3 | 28.3 | 0 | 2020-02-25 | 3.2 | 14.8 | 0 | 2019-02-25 | -9.1 | 27.1 | 0 | 2018-02-25 | 5.1 | 12.9 | 0 | 2017-02-25 | 2.7 | 15.3 | 0 | 2016-02-25 | -2.5 | 20.5 | 0 | 21.84 | 0
2025-02-25 | 1.6 | 16.4 | 0 | 2024-02-25 | 0.6 | 17.4 | 0 | 2023-02-25 | -17.5 | 35.5 | 0 | 2022-02-25 | -14.5 | 32.5 | 0 | 2021-02-25 | -11.5 | 29.5 | 0 | 2020-02-25 | 2.5 | 15.5 | 0 | 2019-02-25 | -9.7 | 27.7 | 0 | 2018-02-25 | 4.1 | 13.9 | 0 | 2017-02-25 | 2.4 | 15.6 | 0 | 2016-02-25 | -2.6 | 20.6 | 0 | 22.46 | 0
2025-02-25 | 1.6 | 16.4 | 0 | 2024-02-25 | 0 | 18 | 0 | 2023-02-25 | -17.2 | 35.2 | 0 | 2022-02-25 | -17.9 | 35.9 | 0 | 2021-02-25 | -10.9 | 28.9 | 0 | 2020-02-25 | 2.2 | 15.8 | 0 | 2019-02-25 | -10.2 | 28.2 | 0 | 2018-02-25 | 3.4 | 14.6 | 0 | 2017-02-25 | 1.9 | 16.1 | 0 | 2016-02-25 | -4.1 | 22.1 | 0 | 23.12 | 0
2025-02-25 | 1.5 | 16.5 | 0 | 2024-02-25 | -0.6 | 18.6 | 0 | 2023-02-25 | -17.1 | 35.1 | 0 | 2022-02-25 | -18.2 | 36.2 | 0 | 2021-02-25 | -10.6 | 28.6 | 0 | 2020-02-25 | 1.6 | 16.4 | 0 | 2019-02-25 | -10.7 | 28.7 | 0 | 2018-02-25 | 2.6 | 15.4 | 0 | 2017-02-25 | 1.9 | 16.1 | 0 | 2016-02-25 | -5.1 | 23.1 | 0 | 23.47 | 0
2025-02-25 | 1.5 | 16.5 | 0 | 2024-02-25 | -0.9 | 18.9 | 0 | 2023-02-25 | -16.7 | 34.7 | 0 | 2022-02-25 | -19.1 | 37.1 | 0 | 2021-02-25 | -10.2 | 28.2 | 0 | 2020-02-25 | 1 | 17 | 0 | 2019-02-25 | -11.2 | 29.2 | 0 | 2018-02-25 | 2.1 | 15.9 | 0 | 2017-02-25 | 0.9 | 17.1 | 0 | 2016-02-25 | -6.4 | 24.4 | 0 | 23.9 | 0
2025-02-26 | 1.7 | 16.3 | 0 | 2024-02-26 | -1.2 | 19.2 | 0 | 2023-02-26 | -16.7 | 34.7 | 0 | 2022-02-26 | -17.4 | 35.4 | 0 | 2021-02-26 | -10.1 | 28.1 | 0 | 2020-02-26 | 0.5 | 17.5 | 0 | 2019-02-26 | -11.6 | 29.6 | 0 | 2018-02-26 | 1.8 | 16.2 | 0 | 2017-02-26 | -0.1 | 18.1 | 0 | 2016-02-26 | -7.7 | 25.7 | 0 | 24.08 | 0
2025-02-26 | 0.8 | 17.2 | 0 | 2024-02-26 | -0.8 | 18.8 | 0 | 2023-02-26 | -16.3 | 34.3 | 0 | 2022-02-26 | -19 | 37 | 0 | 2021-02-26 | -11.4 | 29.4 | 0 | 2020-02-26 | 0.2 | 17.8 | 0 | 2019-02-26 | -13.5 | 31.5 | 0 | 2018-02-26 | 1.7 | 16.3 | 0 | 2017-02-26 | -1.1 | 19.1 | 0 | 2016-02-26 | -9.3 | 27.3 | 0 | 24.87 | 0
2025-02-26 | 0.9 | 17.1 | 0 | 2024-02-26 | 0.6 | 17.4 | 0 | 2023-02-26 | -16.2 | 34.2 | 0 | 2022-02-26 | -20.3 | 38.3 | 0 | 2021-02-26 | -10.7 | 28.7 | 0 | 2020-02-26 | -0.2 | 18.2 | 0 | 2019-02-26 | -14.2 | 32.2 | 0 | 2018-02-26 | 1.4 | 16.6 | 0 | 2017-02-26 | -1.6 | 19.6 | 0 | 2016-02-26 | -10.8 | 28.8 | 0 | 25.11 | 0
2025-02-26 | 0.4 | 17.6 | 0 | 2024-02-26 | 1.4 | 16.6 | 0 | 2023-02-26 | -15.8 | 33.8 | 0 | 2022-02-26 | -19.2 | 37.2 | 0 | 2021-02-26 | -10.7 | 28.7 | 0 | 2020-02-26 | -0.6 | 18.6 | 0 | 2019-02-26 | -15.4 | 33.4 | 0 | 2018-02-26 | 0.8 | 17.2 | 0 | 2017-02-26 | -2.5 | 20.5 | 0 | 2016-02-26 | -12 | 30 | 0 | 25.36 | 0
2025-02-26 | 0.1 | 17.9 | 0 | 2024-02-26 | 1.4 | 16.6 | 0 | 2023-02-26 | -15.5 | 33.5 | 0 | 2022-02-26 | -20.1 | 38.1 | 0 | 2021-02-26 | -10.7 | 28.7 | 0 | 2020-02-26 | -0.9 | 18.9 | 0 | 2019-02-26 | -16 | 34 | 0 | 2018-02-26 | 0.4 | 17.6 | 0 | 2017-02-26 | -3.7 | 21.7 | 0 | 2016-02-26 | -12.9 | 30.9 | 0 | 25.79 | 0
2025-02-26 | 0 | 18 | 0 | 2024-02-26 | 0.7 | 17.3 | 0 | 2023-02-26 | -15.2 | 33.2 | 0 | 2022-02-26 | -22.5 | 40.5 | 0 | 2021-02-26 | -11.5 | 29.5 | 0 | 2020-02-26 | -1.2 | 19.2 | 0 | 2019-02-26 | -16.2 | 34.2 | 0 | 2018-02-26 | 0 | 18 | 0 | 2017-02-26 | -4.6 | 22.6 | 0 | 2016-02-26 | -13.7 | 31.7 | 0 | 26.42 | 0
2025-02-26 | -0.4 | 18.4 | 0 | 2024-02-26 | 0.8 | 17.2 | 0 | 2023-02-26 | -14.3 | 32.3 | 0 | 2022-02-26 | -21.1 | 39.1 | 0 | 2021-02-26 | -13.4 | 31.4 | 0 | 2020-02-26 | -1.4 | 19.4 | 0 | 2019-02-26 | -16.7 | 34.7 | 0 | 2018-02-26 | -0.1 | 18.1 | 0 | 2017-02-26 | -5.9 | 23.9 | 0 | 2016-02-26 | -14.3 | 32.3 | 0 | 26.68 | 0
2025-02-26 | -1.2 | 19.2 | 0 | 2024-02-26 | -0.3 | 18.3 | 0 | 2023-02-26 | -13.7 | 31.7 | 0 | 2022-02-26 | -21.1 | 39.1 | 0 | 2021-02-26 | -12.6 | 30.6 | 0 | 2020-02-26 | -1.7 | 19.7 | 0 | 2019-02-26 | -17.2 | 35.2 | 0 | 2018-02-26 | -0.1 | 18.1 | 0 | 2017-02-26 | -6.7 | 24.7 | 0 | 2016-02-26 | -14.9 | 32.9 | 0 | 26.95 | 0
2025-02-26 | -2.4 | 20.4 | 0 | 2024-02-26 | -1.6 | 19.6 | 0 | 2023-02-26 | -12.7 | 30.7 | 0 | 2022-02-26 | -19.7 | 37.7 | 0 | 2021-02-26 | -12.3 | 30.3 | 0 | 2020-02-26 | -1.7 | 19.7 | 0 | 2019-02-26 | -16.8 | 34.8 | 0 | 2018-02-26 | 0.8 | 17.2 | 0 | 2017-02-26 | -7.1 | 25.1 | 0 | 2016-02-26 | -14.7 | 32.7 | 0 | 26.82 | 0
2025-02-26 | -2.8 | 20.8 | 0 | 2024-02-26 | -0.4 | 18.4 | 0 | 2023-02-26 | -12 | 30 | 0 | 2022-02-26 | -17 | 35 | 0 | 2021-02-26 | -10 | 28 | 0 | 2020-02-26 | -1.5 | 19.5 | 0 | 2019-02-26 | -16.3 | 34.3 | 0 | 2018-02-26 | 1.9 | 16.1 | 0 | 2017-02-26 | -7.1 | 25.1 | 0 | 2016-02-26 | -14.2 | 32.2 | 0 | 25.94 | 0
2025-02-26 | -2 | 20 | 0 | 2024-02-26 | 1.8 | 16.2 | 0 | 2023-02-26 | -11.2 | 29.2 | 0 | 2022-02-26 | -13.8 | 31.8 | 0 | 2021-02-26 | -6.2 | 24.2 | 0 | 2020-02-26 | -1.2 | 19.2 | 0 | 2019-02-26 | -15.7 | 33.7 | 0 | 2018-02-26 | 2.3 | 15.7 | 0 | 2017-02-26 | -6 | 24 | 0 | 2016-02-26 | -13.4 | 31.4 | 0 | 24.54 | 0
2025-02-26 | -1.6 | 19.6 | 0 | 2024-02-26 | 2.4 | 15.6 | 0 | 2023-02-26 | -9.8 | 27.8 | 0 | 2022-02-26 | -10.1 | 28.1 | 0 | 2021-02-26 | -4.6 | 22.6 | 0 | 2020-02-26 | -1.3 | 19.3 | 0 | 2019-02-26 | -15 | 33 | 0 | 2018-02-26 | 2.8 | 15.2 | 0 | 2017-02-26 | -5.7 | 23.7 | 0 | 2016-02-26 | -12.3 | 30.3 | 0 | 23.52 | 0
2025-02-26 | -0.8 | 18.8 | 0 | 2024-02-26 | 2.4 | 15.6 | 0 | 2023-02-26 | -8.7 | 26.7 | 0 | 2022-02-26 | -6.5 | 24.5 | 0 | 2021-02-26 | -3.1 | 21.1 | 0 | 2020-02-26 | -1 | 19 | 0 | 2019-02-26 | -14.2 | 32.2 | 0 | 2018-02-26 | 3 | 15 | 0 | 2017-02-26 | -4.3 | 22.3 | 0 | 2016-02-26 | -11.2 | 29.2 | 0 | 22.44 | 0
2025-02-26 | 0 | 18 | 0 | 2024-02-26 | 2.9 | 15.1 | 0 | 2023-02-26 | -7.5 | 25.5 | 0 | 2022-02-26 | -5 | 23 | 0 | 2021-02-26 | -1.8 | 19.8 | 0 | 2020-02-26 | -0.6 | 18.6 | 0 | 2019-02-26 | -13.5 | 31.5 | 0 | 2018-02-26 | 3.6 | 14.4 | 0 | 2017-02-26 | -3 | 21 | 0 | 2016-02-26 | -10.3 | 28.3 | 0 | 21.52 | 0
2025-02-26 | 0.5 | 17.5 | 0 | 2024-02-26 | 3.3 | 14.7 | 0 | 2023-02-26 | -6.7 | 24.7 | 0 | 2022-02-26 | -4.7 | 22.7 | 0 | 2021-02-26 | -0.8 | 18.8 | 0 | 2020-02-26 | -0.6 | 18.6 | 0 | 2019-02-26 | -12.9 | 30.9 | 0 | 2018-02-26 | 3.9 | 14.1 | 0 | 2017-02-26 | -1.6 | 19.6 | 0 | 2016-02-26 | -10 | 28 | 0 | 20.96 | 0
2025-02-26 | 0.8 | 17.2 | 0 | 2024-02-26 | 3.6 | 14.4 | 0 | 2023-02-26 | -5 | 23 | 0 | 2022-02-26 | -3.9 | 21.9 | 0 | 2021-02-26 | 0.3 | 17.7 | 0 | 2020-02-26 | -1.3 | 19.3 | 0 | 2019-02-26 | -12.3 | 30.3 | 0 | 2018-02-26 | 4 | 14 | 0 | 2017-02-26 | -0.8 | 18.8 | 0 | 2016-02-26 | -9.6 | 27.6 | 0 | 20.42 | 0
2025-02-26 | 0.8 | 17.2 | 0 | 2024-02-26 | 3.7 | 14.3 | 0 | 2023-02-26 | -3.5 | 21.5 | 0 | 2022-02-26 | -4.2 | 22.2 | 0 | 2021-02-26 | 0.6 | 17.4 | 0 | 2020-02-26 | -1.8 | 19.8 | 0 | 2019-02-26 | -12.1 | 30.1 | 0 | 2018-02-26 | 4.2 | 13.8 | 0 | 2017-02-26 | 0 | 18 | 0 | 2016-02-26 | -9.3 | 27.3 | 0 | 20.16 | 0
2025-02-26 | 1 | 17 | 0 | 2024-02-26 | 3.1 | 14.9 | 0 | 2023-02-26 | -3.5 | 21.5 | 0 | 2022-02-26 | -4.4 | 22.4 | 0 | 2021-02-26 | 0.2 | 17.8 | 0 | 2020-02-26 | -1.8 | 19.8 | 0 | 2019-02-26 | -12.5 | 30.5 | 0 | 2018-02-26 | 3.7 | 14.3 | 0 | 2017-02-26 | -0.4 | 18.4 | 0 | 2016-02-26 | -9.4 | 27.4 | 0 | 20.4 | 0
2025-02-26 | 0.1 | 17.9 | 0 | 2024-02-26 | 0.9 | 17.1 | 0 | 2023-02-26 | -4.3 | 22.3 | 0 | 2022-02-26 | -4.6 | 22.6 | 0 | 2021-02-26 | -2.3 | 20.3 | 0 | 2020-02-26 | -1.8 | 19.8 | 0 | 2019-02-26 | -13.4 | 31.4 | 0 | 2018-02-26 | 1.8 | 16.2 | 0 | 2017-02-26 | -0.6 | 18.6 | 0 | 2016-02-26 | -9.9 | 27.9 | 0 | 21.41 | 0
2025-02-26 | -1.6 | 19.6 | 0 | 2024-02-26 | -0.1 | 18.1 | 0 | 2023-02-26 | -5.1 | 23.1 | 0 | 2022-02-26 | -4.8 | 22.8 | 0 | 2021-02-26 | -3.3 | 21.3 | 0 | 2020-02-26 | -1.9 | 19.9 | 0 | 2019-02-26 | -14.7 | 32.7 | 0 | 2018-02-26 | 1.3 | 16.7 | 0 | 2017-02-26 | -1.3 | 19.3 | 0 | 2016-02-26 | -10.7 | 28.7 | 0 | 22.22 | 0
2025-02-26 | -2.4 | 20.4 | 0 | 2024-02-26 | -1.5 | 19.5 | 0 | 2023-02-26 | -6.7 | 24.7 | 0 | 2022-02-26 | -4.9 | 22.9 | 0 | 2021-02-26 | -4.1 | 22.1 | 0 | 2020-02-26 | -1.6 | 19.6 | 0 | 2019-02-26 | -15.6 | 33.6 | 0 | 2018-02-26 | 0 | 18 | 0 | 2017-02-26 | -1.7 | 19.7 | 0 | 2016-02-26 | -11.6 | 29.6 | 0 | 23.01 | 0
2025-02-26 | -2.5 | 20.5 | 0 | 2024-02-26 | -0.8 | 18.8 | 0 | 2023-02-26 | -5.2 | 23.2 | 0 | 2022-02-26 | -5.5 | 23.5 | 0 | 2021-02-26 | -5 | 23 | 0 | 2020-02-26 | -1.1 | 19.1 | 0 | 2019-02-26 | -15.1 | 33.1 | 0 | 2018-02-26 | 0.5 | 17.5 | 0 | 2017-02-26 | -2.1 | 20.1 | 0 | 2016-02-26 | -12.4 | 30.4 | 0 | 22.92 | 0
2025-02-26 | -2.5 | 20.5 | 0 | 2024-02-26 | -0.6 | 18.6 | 0 | 2023-02-26 | -4.8 | 22.8 | 0 | 2022-02-26 | -6.1 | 24.1 | 0 | 2021-02-26 | -4.9 | 22.9 | 0 | 2020-02-26 | -0.4 | 18.4 | 0 | 2019-02-26 | -15.5 | 33.5 | 0 | 2018-02-26 | 0 | 18 | 0 | 2017-02-26 | -1.5 | 19.5 | 0 | 2016-02-26 | -12.1 | 30.1 | 0 | 22.84 | 0
2025-02-26 | -2.5 | 20.5 | 0 | 2024-02-26 | -0.6 | 18.6 | 0 | 2023-02-26 | -6.7 | 24.7 | 0 | 2022-02-26 | -6.3 | 24.3 | 0 | 2021-02-26 | -9.7 | 27.7 | 0 | 2020-02-26 | 0 | 18 | 0 | 2019-02-26 | -16.6 | 34.6 | 0 | 2018-02-26 | -0.8 | 18.8 | 0 | 2017-02-26 | -1.4 | 19.4 | 0 | 2016-02-26 | -13.3 | 31.3 | 0 | 23.79 | 0
2025-02-27 | -2.4 | 20.4 | 0 | 2024-02-27 | 0.2 | 17.8 | 0 | 2023-02-27 | -8.4 | 26.4 | 0 | 2022-02-27 | -6.2 | 24.2 | 0 | 2021-02-27 | -10.6 | 28.6 | 0 | 2020-02-27 | 0.1 | 17.9 | 0 | 2019-02-27 | -17.1 | 35.1 | 0 | 2018-02-27 | -0.8 | 18.8 | 0 | 2017-02-27 | -1.3 | 19.3 | 0 | 2016-02-27 | -14.5 | 32.5 | 0 | 24.1 | 0
2025-02-27 | -3 | 21 | 0 | 2024-02-27 | -0.2 | 18.2 | 0 | 2023-02-27 | -9.1 | 27.1 | 0 | 2022-02-27 | -5.9 | 23.9 | 0 | 2021-02-27 | -9.9 | 27.9 | 0 | 2020-02-27 | 0.1 | 17.9 | 0 | 2019-02-27 | -17 | 35 | 0 | 2018-02-27 | -1.2 | 19.2 | 0 | 2017-02-27 | -0.6 | 18.6 | 0 | 2016-02-27 | -14.5 | 32.5 | 0 | 24.13 | 0
2025-02-27 | -3.9 | 21.9 | 0 | 2024-02-27 | -0.5 | 18.5 | 0 | 2023-02-27 | -10 | 28 | 0 | 2022-02-27 | -5.7 | 23.7 | 0 | 2021-02-27 | -10.9 | 28.9 | 0 | 2020-02-27 | 0.1 | 17.9 | 0 | 2019-02-27 | -19.6 | 37.6 | 0 | 2018-02-27 | -1.9 | 19.9 | 0 | 2017-02-27 | 0 | 18 | 0 | 2016-02-27 | -15.1 | 33.1 | 0 | 24.75 | 0
2025-02-27 | -5.6 | 23.6 | 0 | 2024-02-27 | -0.8 | 18.8 | 0 | 2023-02-27 | -12 | 30 | 0 | 2022-02-27 | -5.7 | 23.7 | 0 | 2021-02-27 | -12.2 | 30.2 | 0 | 2020-02-27 | 0.2 | 17.8 | 0 | 2019-02-27 | -22.1 | 40.1 | 0 | 2018-02-27 | -2.5 | 20.5 | 0 | 2017-02-27 | 0.7 | 17.3 | 0 | 2016-02-27 | -14.8 | 32.8 | 0 | 25.48 | 0
2025-02-27 | -6.7 | 24.7 | 0 | 2024-02-27 | -0.9 | 18.9 | 0 | 2023-02-27 | -11.8 | 29.8 | 0 | 2022-02-27 | -5.2 | 23.2 | 0 | 2021-02-27 | -11 | 29 | 0 | 2020-02-27 | 0.4 | 17.6 | 0 | 2019-02-27 | -20.8 | 38.8 | 0 | 2018-02-27 | -2.6 | 20.6 | 0 | 2017-02-27 | 0.5 | 17.5 | 0 | 2016-02-27 | -14.9 | 32.9 | 0 | 25.3 | 0
2025-02-27 | -5.7 | 23.7 | 0 | 2024-02-27 | -0.9 | 18.9 | 0 | 2023-02-27 | -13.5 | 31.5 | 0 | 2022-02-27 | -5 | 23 | 0 | 2021-02-27 | -10.3 | 28.3 | 0 | 2020-02-27 | 0.3 | 17.7 | 0 | 2019-02-27 | -21.1 | 39.1 | 0 | 2018-02-27 | -3 | 21 | 0 | 2017-02-27 | 0 | 18 | 0 | 2016-02-27 | -13.2 | 31.2 | 0 | 25.24 | 0
2025-02-27 | -6.3 | 24.3 | 0 | 2024-02-27 | -2 | 20 | 0 | 2023-02-27 | -13.9 | 31.9 | 0 | 2022-02-27 | -4.3 | 22.3 | 0 | 2021-02-27 | -10.2 | 28.2 | 0 | 2020-02-27 | 0.2 | 17.8 | 0 | 2019-02-27 | -22.9 | 40.9 | 0 | 2018-02-27 | -3.2 | 21.2 | 0 | 2017-02-27 | 0.3 | 17.7 | 0 | 2016-02-27 | -12.7 | 30.7 | 0 | 25.5 | 0
2025-02-27 | -5.7 | 23.7 | 0 | 2024-02-27 | -2.2 | 20.2 | 0 | 2023-02-27 | -12.7 | 30.7 | 0 | 2022-02-27 | -4.1 | 22.1 | 0 | 2021-02-27 | -9.5 | 27.5 | 0 | 2020-02-27 | 0.2 | 17.8 | 0 | 2019-02-27 | -22.1 | 40.1 | 0 | 2018-02-27 | -3.2 | 21.2 | 0 | 2017-02-27 | 1 | 17 | 0 | 2016-02-27 | -11.7 | 29.7 | 0 | 25 | 0
2025-02-27 | -5.3 | 23.3 | 0 | 2024-02-27 | -0.7 | 18.7 | 0 | 2023-02-27 | -12.2 | 30.2 | 0 | 2022-02-27 | -3.7 | 21.7 | 0 | 2021-02-27 | -8.2 | 26.2 | 0 | 2020-02-27 | 0.3 | 17.7 | 0 | 2019-02-27 | -22.2 | 40.2 | 0 | 2018-02-27 | -2.1 | 20.1 | 0 | 2017-02-27 | 1 | 17 | 0 | 2016-02-27 | -8.9 | 26.9 | 0 | 24.2 | 0
2025-02-27 | -4.8 | 22.8 | 0 | 2024-02-27 | 1.4 | 16.6 | 0 | 2023-02-27 | -9.5 | 27.5 | 0 | 2022-02-27 | -3.3 | 21.3 | 0 | 2021-02-27 | -7.3 | 25.3 | 0 | 2020-02-27 | 0.2 | 17.8 | 0 | 2019-02-27 | -20.1 | 38.1 | 0 | 2018-02-27 | -0.1 | 18.1 | 0 | 2017-02-27 | 2.1 | 15.9 | 0 | 2016-02-27 | -7 | 25 | 0 | 22.84 | 0
2025-02-27 | -4.2 | 22.2 | 0 | 2024-02-27 | 3.6 | 14.4 | 0 | 2023-02-27 | -8 | 26 | 0 | 2022-02-27 | -2.8 | 20.8 | 0 | 2021-02-27 | -6.3 | 24.3 | 0 | 2020-02-27 | 0 | 18 | 0 | 2019-02-27 | -16.8 | 34.8 | 0 | 2018-02-27 | 1.6 | 16.4 | 0 | 2017-02-27 | 2.9 | 15.1 | 0 | 2016-02-27 | -4.6 | 22.6 | 0 | 21.46 | 0
2025-02-27 | -3.8 | 21.8 | 0 | 2024-02-27 | 6.1 | 11.9 | 0 | 2023-02-27 | -6.9 | 24.9 | 0 | 2022-02-27 | -1.7 | 19.7 | 0 | 2021-02-27 | -5.2 | 23.2 | 0 | 2020-02-27 | -0.4 | 18.4 | 0 | 2019-02-27 | -15.5 | 33.5 | 0 | 2018-02-27 | 3.6 | 14.4 | 0 | 2017-02-27 | 3 | 15 | 0 | 2016-02-27 | -2 | 20 | 0 | 20.28 | 0
2025-02-27 | -3 | 21 | 0 | 2024-02-27 | 8.1 | 9.9 | 0 | 2023-02-27 | -6 | 24 | 0 | 2022-02-27 | -4 | 22 | 0 | 2021-02-27 | -4.1 | 22.1 | 0 | 2020-02-27 | -1.7 | 19.7 | 0 | 2019-02-27 | -15.2 | 33.2 | 0 | 2018-02-27 | 6.6 | 11.4 | 0 | 2017-02-27 | 3.6 | 14.4 | 0 | 2016-02-27 | -0.8 | 18.8 | 0 | 19.65 | 0
2025-02-27 | -2.3 | 20.3 | 0 | 2024-02-27 | 9.7 | 8.3 | 0 | 2023-02-27 | -6.1 | 24.1 | 0 | 2022-02-27 | -3.8 | 21.8 | 0 | 2021-02-27 | -1.7 | 19.7 | 0 | 2020-02-27 | -2.9 | 20.9 | 0 | 2019-02-27 | -14.6 | 32.6 | 0 | 2018-02-27 | 7.7 | 10.3 | 0 | 2017-02-27 | 3.1 | 14.9 | 0 | 2016-02-27 | -0.4 | 18.4 | 0 | 19.13 | 0
2025-02-27 | -1.2 | 19.2 | 0 | 2024-02-27 | 11.5 | 6.5 | 0 | 2023-02-27 | -5.8 | 23.8 | 0 | 2022-02-27 | -4.6 | 22.6 | 0 | 2021-02-27 | 0.9 | 17.1 | 0 | 2020-02-27 | -4.6 | 22.6 | 0 | 2019-02-27 | -14.5 | 32.5 | 0 | 2018-02-27 | 8 | 10 | 0 | 2017-02-27 | 3 | 15 | 0 | 2016-02-27 | 0.4 | 17.6 | 0 | 18.69 | 0
2025-02-27 | -0.5 | 18.5 | 0 | 2024-02-27 | 10.6 | 7.4 | 0 | 2023-02-27 | -6 | 24 | 0 | 2022-02-27 | -4.7 | 22.7 | 0 | 2021-02-27 | 3.1 | 14.9 | 0 | 2020-02-27 | -5.4 | 23.4 | 0 | 2019-02-27 | -14.4 | 32.4 | 0 | 2018-02-27 | 8.3 | 9.7 | 0 | 2017-02-27 | 3.5 | 14.5 | 0 | 2016-02-27 | 0.9 | 17.1 | 0 | 18.46 | 0
2025-02-27 | -0.3 | 18.3 | 0 | 2024-02-27 | 10.3 | 7.7 | 0 | 2023-02-27 | -5.7 | 23.7 | 0 | 2022-02-27 | -4.7 | 22.7 | 0 | 2021-02-27 | 2.8 | 15.2 | 0 | 2020-02-27 | -5.8 | 23.8 | 0 | 2019-02-27 | -14.4 | 32.4 | 0 | 2018-02-27 | 8.5 | 9.5 | 0 | 2017-02-27 | 3.1 | 14.9 | 0 | 2016-02-27 | 0.8 | 17.2 | 0 | 18.54 | 0
2025-02-27 | -0.1 | 18.1 | 0 | 2024-02-27 | 8 | 10 | 0 | 2023-02-27 | -6 | 24 | 0 | 2022-02-27 | -6.1 | 24.1 | 0 | 2021-02-27 | 1.3 | 16.7 | 0 | 2020-02-27 | -6 | 24 | 0 | 2019-02-27 | -14.9 | 32.9 | 0 | 2018-02-27 | 7.1 | 10.9 | 0 | 2017-02-27 | 2.8 | 15.2 | 0 | 2016-02-27 | 0.8 | 17.2 | 0 | 19.31 | 0
2025-02-27 | -0.1 | 18.1 | 0 | 2024-02-27 | 6.6 | 11.4 | 0 | 2023-02-27 | -6.6 | 24.6 | 0 | 2022-02-27 | -7 | 25 | 0 | 2021-02-27 | 0 | 18 | 0 | 2020-02-27 | -6.1 | 24.1 | 0 | 2019-02-27 | -15.4 | 33.4 | 0 | 2018-02-27 | 5.9 | 12.1 | 0 | 2017-02-27 | 2 | 16 | 0 | 2016-02-27 | 0.8 | 17.2 | 0 | 19.99 | 0
2025-02-27 | -0.3 | 18.3 | 0 | 2024-02-27 | 5.7 | 12.3 | 0 | 2023-02-27 | -6.6 | 24.6 | 0 | 2022-02-27 | -7.7 | 25.7 | 0 | 2021-02-27 | -1.5 | 19.5 | 0 | 2020-02-27 | -6.6 | 24.6 | 0 | 2019-02-27 | -15.9 | 33.9 | 0 | 2018-02-27 | 5 | 13 | 0 | 2017-02-27 | 1.9 | 16.1 | 0 | 2016-02-27 | 1.2 | 16.8 | 0 | 20.48 | 0
2025-02-27 | 0.2 | 17.8 | 0 | 2024-02-27 | 6.8 | 11.2 | 0 | 2023-02-27 | -6.8 | 24.8 | 0 | 2022-02-27 | -8.7 | 26.7 | 0 | 2021-02-27 | -1.3 | 19.3 | 0 | 2020-02-27 | -7.2 | 25.2 | 0 | 2019-02-27 | -16.4 | 34.4 | 0 | 2018-02-27 | 4.6 | 13.4 | 0 | 2017-02-27 | 0.2 | 17.8 | 0 | 2016-02-27 | 1.7 | 16.3 | 0 | 20.69 | 0
2025-02-27 | 1.2 | 16.8 | 0 | 2024-02-27 | 8.6 | 9.4 | 0 | 2023-02-27 | -6.8 | 24.8 | 0 | 2022-02-27 | -9.8 | 27.8 | 0 | 2021-02-27 | -0.2 | 18.2 | 0 | 2020-02-27 | -8.2 | 26.2 | 0 | 2019-02-27 | -17.1 | 35.1 | 0 | 2018-02-27 | 4.7 | 13.3 | 0 | 2017-02-27 | -0.4 | 18.4 | 0 | 2016-02-27 | 1.9 | 16.1 | 0 | 20.61 | 0
2025-02-27 | 1.5 | 16.5 | 0 | 2024-02-27 | 10.8 | 7.2 | 0 | 2023-02-27 | -7.1 | 25.1 | 0 | 2022-02-27 | -11.1 | 29.1 | 0 | 2021-02-27 | 0.4 | 17.6 | 0 | 2020-02-27 | -8.8 | 26.8 | 0 | 2019-02-27 | -16.5 | 34.5 | 0 | 2018-02-27 | 4.3 | 13.7 | 0 | 2017-02-27 | -1.4 | 19.4 | 0 | 2016-02-27 | 1.9 | 16.1 | 0 | 20.6 | 0
2025-02-27 | 1.4 | 16.6 | 0 | 2024-02-27 | 9.5 | 8.5 | 0 | 2023-02-27 | -7.2 | 25.2 | 0 | 2022-02-27 | -12.3 | 30.3 | 0 | 2021-02-27 | -0.3 | 18.3 | 0 | 2020-02-27 | -9.3 | 27.3 | 0 | 2019-02-27 | -15.7 | 33.7 | 0 | 2018-02-27 | 4.8 | 13.2 | 0 | 2017-02-27 | -1.3 | 19.3 | 0 | 2016-02-27 | 2 | 16 | 0 | 20.84 | 0
2025-02-28 | 1.1 | 16.9 | 0 | 2024-02-28 | 7.8 | 10.2 | 0 | 2023-02-28 | -7.4 | 25.4 | 0 | 2022-02-28 | -13.4 | 31.4 | 0 | 2021-02-28 | -1.1 | 19.1 | 0 | 2020-02-28 | -9.4 | 27.4 | 0 | 2019-02-28 | -15.7 | 33.7 | 0 | 2018-02-28 | 4.7 | 13.3 | 0 | 2017-02-28 | -1.8 | 19.8 | 0 | 2016-02-28 | 2.1 | 15.9 | 0 | 21.31 | 0
2025-02-28 | -0.7 | 18.7 | 0 | 2024-02-28 | 6.9 | 11.1 | 0 | 2023-02-28 | -7.2 | 25.2 | 0 | 2022-02-28 | -14.3 | 32.3 | 0 | 2021-02-28 | -1.1 | 19.1 | 0 | 2020-02-28 | -10 | 28 | 0 | 2019-02-28 | -15.8 | 33.8 | 0 | 2018-02-28 | 4.2 | 13.8 | 0 | 2017-02-28 | -3.3 | 21.3 | 0 | 2016-02-28 | 2.1 | 15.9 | 0 | 21.92 | 0
2025-02-28 | -4.4 | 22.4 | 0 | 2024-02-28 | 6.5 | 11.5 | 0 | 2023-02-28 | -7.3 | 25.3 | 0 | 2022-02-28 | -15.3 | 33.3 | 0 | 2021-02-28 | -1.1 | 19.1 | 0 | 2020-02-28 | -10.6 | 28.6 | 0 | 2019-02-28 | -15.8 | 33.8 | 0 | 2018-02-28 | 4.3 | 13.7 | 0 | 2017-02-28 | -3.6 | 21.6 | 0 | 2016-02-28 | 2.1 | 15.9 | 0 | 22.52 | 0
2025-02-28 | -7 | 25 | 0 | 2024-02-28 | 7 | 11 | 0 | 2023-02-28 | -7 | 25 | 0 | 2022-02-28 | -16 | 34 | 0 | 2021-02-28 | -1.7 | 19.7 | 0 | 2020-02-28 | -11.5 | 29.5 | 0 | 2019-02-28 | -18 | 36 | 0 | 2018-02-28 | 4 | 14 | 0 | 2017-02-28 | -5.2 | 23.2 | 0 | 2016-02-28 | -1.6 | 19.6 | 0 | 23.7 | 0
2025-02-28 | -9.1 | 27.1 | 0 | 2024-02-28 | 6.7 | 11.3 | 0 | 2023-02-28 | -7.4 | 25.4 | 0 | 2022-02-28 | -16.9 | 34.9 | 0 | 2021-02-28 | -1.9 | 19.9 | 0 | 2020-02-28 | -12.1 | 30.1 | 0 | 2019-02-28 | -18.9 | 36.9 | 0 | 2018-02-28 | 3.7 | 14.3 | 0 | 2017-02-28 | -3.9 | 21.9 | 0 | 2016-02-28 | -3.2 | 21.2 | 0 | 24.3 | 0
2025-02-28 | -11 | 29 | 0 | 2024-02-28 | 7.8 | 10.2 | 0 | 2023-02-28 | -7.3 | 25.3 | 0 | 2022-02-28 | -17.7 | 35.7 | 0 | 2021-02-28 | -5.6 | 23.6 | 0 | 2020-02-28 | -12.2 | 30.2 | 0 | 2019-02-28 | -19.2 | 37.2 | 0 | 2018-02-28 | 3.3 | 14.7 | 0 | 2017-02-28 | -3.4 | 21.4 | 0 | 2016-02-28 | -4.5 | 22.5 | 0 | 24.98 | 0
2025-02-28 | -11.7 | 29.7 | 0 | 2024-02-28 | 6.1 | 11.9 | 0 | 2023-02-28 | -7 | 25 | 0 | 2022-02-28 | -17.5 | 35.5 | 0 | 2021-02-28 | -4.8 | 22.8 | 0 | 2020-02-28 | -12.3 | 30.3 | 0 | 2019-02-28 | -19.1 | 37.1 | 0 | 2018-02-28 | 2.7 | 15.3 | 0 | 2017-02-28 | -3.2 | 21.2 | 0 | 2016-02-28 | -5 | 23 | 0 | 25.18 | 0
2025-02-28 | -13 | 31 | 0 | 2024-02-28 | 6.4 | 11.6 | 0 | 2023-02-28 | -6.7 | 24.7 | 0 | 2022-02-28 | -18.8 | 36.8 | 0 | 2021-02-28 | -7.5 | 25.5 | 0 | 2020-02-28 | -12.3 | 30.3 | 0 | 2019-02-28 | -19.1 | 37.1 | 0 | 2018-02-28 | 2.2 | 15.8 | 0 | 2017-02-28 | -4.1 | 22.1 | 0 | 2016-02-28 | -6 | 24 | 0 | 25.89 | 0
2025-02-28 | -12.8 | 30.8 | 0 | 2024-02-28 | 7.2 | 10.8 | 0 | 2023-02-28 | -6 | 24 | 0 | 2022-02-28 | -18.1 | 36.1 | 0 | 2021-02-28 | -6.9 | 24.9 | 0 | 2020-02-28 | -12.1 | 30.1 | 0 | 2019-02-28 | -18.8 | 36.8 | 0 | 2018-02-28 | 2.4 | 15.6 | 0 | 2017-02-28 | -3.7 | 21.7 | 0 | 2016-02-28 | -6.8 | 24.8 | 0 | 25.56 | 0
2025-02-28 | -12.5 | 30.5 | 0 | 2024-02-28 | 7.3 | 10.7 | 0 | 2023-02-28 | -5.4 | 23.4 | 0 | 2022-02-28 | -17 | 35 | 0 | 2021-02-28 | -6.3 | 24.3 | 0 | 2020-02-28 | -11.8 | 29.8 | 0 | 2019-02-28 | -16.2 | 34.2 | 0 | 2018-02-28 | 4.7 | 13.3 | 0 | 2017-02-28 | -0.7 | 18.7 | 0 | 2016-02-28 | -8.2 | 26.2 | 0 | 24.61 | 0
2025-02-28 | -12.4 | 30.4 | 0 | 2024-02-28 | 8.8 | 9.2 | 0 | 2023-02-28 | -5 | 23 | 0 | 2022-02-28 | -16.2 | 34.2 | 0 | 2021-02-28 | -1.1 | 19.1 | 0 | 2020-02-28 | -11.1 | 29.1 | 0 | 2019-02-28 | -14.1 | 32.1 | 0 | 2018-02-28 | 5.7 | 12.3 | 0 | 2017-02-28 | 1.4 | 16.6 | 0 | 2016-02-28 | -8.3 | 26.3 | 0 | 23.23 | 0
2025-02-28 | -11.5 | 29.5 | 0 | 2024-02-28 | 11.1 | 6.9 | 0 | 2023-02-28 | -4.4 | 22.4 | 0 | 2022-02-28 | -15.4 | 33.4 | 0 | 2021-02-28 | 0.9 | 17.1 | 0 | 2020-02-28 | -10.4 | 28.4 | 0 | 2019-02-28 | -11.9 | 29.9 | 0 | 2018-02-28 | 7.3 | 10.7 | 0 | 2017-02-28 | 2.8 | 15.2 | 0 | 2016-02-28 | -8.2 | 26.2 | 0 | 21.97 | 0
2025-02-28 | -10.6 | 28.6 | 0 | 2024-02-28 | 12.8 | 5.2 | 0 | 2023-02-28 | -3.7 | 21.7 | 0 | 2022-02-28 | -14.4 | 32.4 | 0 | 2021-02-28 | 0.9 | 17.1 | 0 | 2020-02-28 | -9.3 | 27.3 | 0 | 2019-02-28 | -9.9 | 27.9 | 0 | 2018-02-28 | 8.6 | 9.4 | 0 | 2017-02-28 | 3.4 | 14.6 | 0 | 2016-02-28 | -8.1 | 26.1 | 0 | 21.03 | 0
2025-02-28 | -10 | 28 | 0 | 2024-02-28 | 13 | 5 | 0 | 2023-02-28 | -3.1 | 21.1 | 0 | 2022-02-28 | -13.4 | 31.4 | 0 | 2021-02-28 | 2.8 | 15.2 | 0 | 2020-02-28 | -9 | 27 | 0 | 2019-02-28 | -9.2 | 27.2 | 0 | 2018-02-28 | 9.6 | 8.4 | 0 | 2017-02-28 | 3.4 | 14.6 | 0 | 2016-02-28 | -7.7 | 25.7 | 0 | 20.36 | 0
2025-02-28 | -9.3 | 27.3 | 0 | 2024-02-28 | 14.9 | 3.1 | 0 | 2023-02-28 | -2.6 | 20.6 | 0 | 2022-02-28 | -12.6 | 30.6 | 0 | 2021-02-28 | 3.3 | 14.7 | 0 | 2020-02-28 | -9.3 | 27.3 | 0 | 2019-02-28 | -8.6 | 26.6 | 0 | 2018-02-28 | 8.8 | 9.2 | 0 | 2017-02-28 | 4.3 | 13.7 | 0 | 2016-02-28 | -7.5 | 25.5 | 0 | 19.86 | 0
2025-02-28 | -8.8 | 26.8 | 0 | 2024-02-28 | 15.6 | 2.4 | 0 | 2023-02-28 | -2.2 | 20.2 | 0 | 2022-02-28 | -11.5 | 29.5 | 0 | 2021-02-28 | 3.3 | 14.7 | 0 | 2020-02-28 | -9 | 27 | 0 | 2019-02-28 | -8 | 26 | 0 | 2018-02-28 | 5.5 | 12.5 | 0 | 2017-02-28 | 4.1 | 13.9 | 0 | 2016-02-28 | -6.7 | 24.7 | 0 | 19.77 | 0
2025-02-28 | -8.4 | 26.4 | 0 | 2024-02-28 | 14.3 | 3.7 | 0 | 2023-02-28 | -2.1 | 20.1 | 0 | 2022-02-28 | -10.8 | 28.8 | 0 | 2021-02-28 | 3.7 | 14.3 | 0 | 2020-02-28 | -8.5 | 26.5 | 0 | 2019-02-28 | -7.7 | 25.7 | 0 | 2018-02-28 | 5 | 13 | 0 | 2017-02-28 | 3.3 | 14.7 | 0 | 2016-02-28 | -6.5 | 24.5 | 0 | 19.77 | 0
2025-02-28 | -8.6 | 26.6 | 0 | 2024-02-28 | 7.3 | 10.7 | 0 | 2023-02-28 | -1.9 | 19.9 | 0 | 2022-02-28 | -11.3 | 29.3 | 0 | 2021-02-28 | 2.8 | 15.2 | 0 | 2020-02-28 | -9.3 | 27.3 | 0 | 2019-02-28 | -7.9 | 25.9 | 0 | 2018-02-28 | 4.7 | 13.3 | 0 | 2017-02-28 | 2.8 | 15.2 | 0 | 2016-02-28 | -7.6 | 25.6 | 0 | 20.9 | 0
2025-02-28 | -10.2 | 28.2 | 0 | 2024-02-28 | 2.8 | 15.2 | 0 | 2023-02-28 | -1 | 19 | 0 | 2022-02-28 | -13 | 31 | 0 | 2021-02-28 | 1.4 | 16.6 | 0 | 2020-02-28 | -9.9 | 27.9 | 0 | 2019-02-28 | -8.8 | 26.8 | 0 | 2018-02-28 | 3.2 | 14.8 | 0 | 2017-02-28 | 2.2 | 15.8 | 0 | 2016-02-28 | -7.9 | 25.9 | 0 | 22.12 | 0
2025-02-28 | -10.3 | 28.3 | 0 | 2024-02-28 | 1.1 | 16.9 | 0 | 2023-02-28 | -0.8 | 18.8 | 0 | 2022-02-28 | -12.9 | 30.9 | 0 | 2021-02-28 | 1.4 | 16.6 | 0 | 2020-02-28 | -9.7 | 27.7 | 0 | 2019-02-28 | -11.6 | 29.6 | 0 | 2018-02-28 | 3.1 | 14.9 | 0 | 2017-02-28 | 2.1 | 15.9 | 0 | 2016-02-28 | -8 | 26 | 0 | 22.56 | 0
2025-02-28 | -10.5 | 28.5 | 0 | 2024-02-28 | -1 | 19 | 0 | 2023-02-28 | -0.8 | 18.8 | 0 | 2022-02-28 | -14.4 | 32.4 | 0 | 2021-02-28 | 1.4 | 16.6 | 0 | 2020-02-28 | -10.2 | 28.2 | 0 | 2019-02-28 | -11.8 | 29.8 | 0 | 2018-02-28 | 2.7 | 15.3 | 0 | 2017-02-28 | 2.4 | 15.6 | 0 | 2016-02-28 | -8.2 | 26.2 | 0 | 23.04 | 0
2025-02-28 | -10.2 | 28.2 | 0 | 2024-02-28 | -7.1 | 25.1 | 0 | 2023-02-28 | -1.2 | 19.2 | 0 | 2022-02-28 | -13.7 | 31.7 | 0 | 2021-02-28 | 1.3 | 16.7 | 0 | 2020-02-28 | -11 | 29 | 0 | 2019-02-28 | -11.8 | 29.8 | 0 | 2018-02-28 | 2.5 | 15.5 | 0 | 2017-02-28 | 2.2 | 15.8 | 0 | 2016-02-28 | -8.4 | 26.4 | 0 | 23.74 | 0
2025-02-28 | -10.1 | 28.1 | 0 | 2024-02-28 | -10.9 | 28.9 | 0 | 2023-02-28 | -1.1 | 19.1 | 0 | 2022-02-28 | -14.3 | 32.3 | 0 | 2021-02-28 | 2.2 | 15.8 | 0 | 2020-02-28 | -11.8 | 29.8 | 0 | 2019-02-28 | -12.7 | 30.7 | 0 | 2018-02-28 | 2.2 | 15.8 | 0 | 2017-02-28 | 2.4 | 15.6 | 0 | 2016-02-28 | -8.7 | 26.7 | 0 | 24.28 | 0
2025-02-28 | -9.5 | 27.5 | 0 | 2024-02-28 | -12.7 | 30.7 | 0 | 2023-02-28 | -2.1 | 20.1 | 0 | 2022-02-28 | -15.1 | 33.1 | 0 | 2021-02-28 | 3.5 | 14.5 | 0 | 2020-02-28 | -11.9 | 29.9 | 0 | 2019-02-28 | -12.9 | 30.9 | 0 | 2018-02-28 | 1.4 | 16.6 | 0 | 2017-02-28 | 2.2 | 15.8 | 0 | 2016-02-28 | -8.7 | 26.7 | 0 | 24.58 | 0
2025-03-01 | -9.1 | 27.1 | 0 | 2024-03-01 | -13.2 | 31.2 | 0 | 2023-03-01 | -2.5 | 20.5 | 0 | 2022-03-01 | -15.4 | 33.4 | 0 | 2021-03-01 | 4.3 | 13.7 | 0 | 2020-03-01 | -13.1 | 31.1 | 0 | 2019-03-01 | -13.8 | 31.8 | 0 | 2018-03-01 | 1.1 | 16.9 | 0 | 2017-03-01 | 1.5 | 16.5 | 0 | 2016-03-01 | -12.6 | 30.6 | 0 | 25.28 | 0
2025-03-01 | -8.9 | 26.9 | 0 | 2024-03-01 | -12.4 | 30.4 | 0 | 2023-03-01 | -3.6 | 21.6 | 0 | 2022-03-01 | -16.2 | 34.2 | 0 | 2021-03-01 | 4 | 14 | 0 | 2020-03-01 | -15.9 | 33.9 | 0 | 2019-03-01 | -15.5 | 33.5 | 0 | 2018-03-01 | 1 | 17 | 0 | 2017-03-01 | 1 | 17 | 0 | 2016-03-01 | -13.6 | 31.6 | 0 | 26.01 | 0
2025-03-01 | -8.8 | 26.8 | 0 | 2024-03-01 | -11.3 | 29.3 | 0 | 2023-03-01 | -4.1 | 22.1 | 0 | 2022-03-01 | -15.6 | 33.6 | 0 | 2021-03-01 | 3.2 | 14.8 | 0 | 2020-03-01 | -14 | 32 | 0 | 2019-03-01 | -14.4 | 32.4 | 0 | 2018-03-01 | 0.9 | 17.1 | 0 | 2017-03-01 | 1.1 | 16.9 | 0 | 2016-03-01 | -14.3 | 32.3 | 0 | 25.73 | 0
2025-03-01 | -8.8 | 26.8 | 0 | 2024-03-01 | -10 | 28 | 0 | 2023-03-01 | -3.9 | 21.9 | 0 | 2022-03-01 | -16 | 34 | 0 | 2021-03-01 | 2.7 | 15.3 | 0 | 2020-03-01 | -13.6 | 31.6 | 0 | 2019-03-01 | -15.1 | 33.1 | 0 | 2018-03-01 | 1 | 17 | 0 | 2017-03-01 | 1.1 | 16.9 | 0 | 2016-03-01 | -15 | 33 | 0 | 25.76 | 0
2025-03-01 | -8.5 | 26.5 | 0 | 2024-03-01 | -9.3 | 27.3 | 0 | 2023-03-01 | -4.6 | 22.6 | 0 | 2022-03-01 | -15.9 | 33.9 | 0 | 2021-03-01 | 3.7 | 14.3 | 0 | 2020-03-01 | -13.9 | 31.9 | 0 | 2019-03-01 | -16.1 | 34.1 | 0 | 2018-03-01 | 0.6 | 17.4 | 0 | 2017-03-01 | 1.2 | 16.8 | 0 | 2016-03-01 | -15.6 | 33.6 | 0 | 25.84 | 0
2025-03-01 | -8.3 | 26.3 | 0 | 2024-03-01 | -8.9 | 26.9 | 0 | 2023-03-01 | -5.3 | 23.3 | 0 | 2022-03-01 | -15.6 | 33.6 | 0 | 2021-03-01 | 3.2 | 14.8 | 0 | 2020-03-01 | -13.7 | 31.7 | 0 | 2019-03-01 | -15.5 | 33.5 | 0 | 2018-03-01 | 0.1 | 17.9 | 0 | 2017-03-01 | 1 | 17 | 0 | 2016-03-01 | -16.4 | 34.4 | 0 | 25.94 | 0
2025-03-01 | -8 | 26 | 0 | 2024-03-01 | -9 | 27 | 0 | 2023-03-01 | -9.1 | 27.1 | 0 | 2022-03-01 | -15.2 | 33.2 | 0 | 2021-03-01 | 3.2 | 14.8 | 0 | 2020-03-01 | -14.4 | 32.4 | 0 | 2019-03-01 | -19.4 | 37.4 | 0 | 2018-03-01 | -0.9 | 18.9 | 0 | 2017-03-01 | 1.6 | 16.4 | 0 | 2016-03-01 | -17.5 | 35.5 | 0 | 26.87 | 0
2025-03-01 | -7.3 | 25.3 | 0 | 2024-03-01 | -8.3 | 26.3 | 0 | 2023-03-01 | -9.6 | 27.6 | 0 | 2022-03-01 | -14.8 | 32.8 | 0 | 2021-03-01 | 2.8 | 15.2 | 0 | 2020-03-01 | -16.7 | 34.7 | 0 | 2019-03-01 | -16.7 | 34.7 | 0 | 2018-03-01 | -0.9 | 18.9 | 0 | 2017-03-01 | 1.6 | 16.4 | 0 | 2016-03-01 | -17.4 | 35.4 | 0 | 26.73 | 0
2025-03-01 | -6.9 | 24.9 | 0 | 2024-03-01 | -7.3 | 25.3 | 0 | 2023-03-01 | -6.6 | 24.6 | 0 | 2022-03-01 | -14.4 | 32.4 | 0 | 2021-03-01 | 2.9 | 15.1 | 0 | 2020-03-01 | -15.1 | 33.1 | 0 | 2019-03-01 | -15.9 | 33.9 | 0 | 2018-03-01 | 0 | 18 | 0 | 2017-03-01 | 1.7 | 16.3 | 0 | 2016-03-01 | -15.9 | 33.9 | 0 | 25.75 | 0
2025-03-01 | -6.3 | 24.3 | 0 | 2024-03-01 | -6.2 | 24.2 | 0 | 2023-03-01 | -4.7 | 22.7 | 0 | 2022-03-01 | -14.1 | 32.1 | 0 | 2021-03-01 | 2.8 | 15.2 | 0 | 2020-03-01 | -12.8 | 30.8 | 0 | 2019-03-01 | -14 | 32 | 0 | 2018-03-01 | 1.1 | 16.9 | 0 | 2017-03-01 | 2.5 | 15.5 | 0 | 2016-03-01 | -15.2 | 33.2 | 0 | 24.69 | 0
2025-03-01 | -7 | 25 | 0 | 2024-03-01 | -4.8 | 22.8 | 0 | 2023-03-01 | -3.6 | 21.6 | 0 | 2022-03-01 | -13.2 | 31.2 | 0 | 2021-03-01 | 2.7 | 15.3 | 0 | 2020-03-01 | -10 | 28 | 0 | 2019-03-01 | -10.8 | 28.8 | 0 | 2018-03-01 | 2.1 | 15.9 | 0 | 2017-03-01 | 2.6 | 15.4 | 0 | 2016-03-01 | -13.9 | 31.9 | 0 | 23.59 | 0
2025-03-01 | -7.6 | 25.6 | 0 | 2024-03-01 | -3 | 21 | 0 | 2023-03-01 | -1.8 | 19.8 | 0 | 2022-03-01 | -12.8 | 30.8 | 0 | 2021-03-01 | 0.6 | 17.4 | 0 | 2020-03-01 | -8.4 | 26.4 | 0 | 2019-03-01 | -7.8 | 25.8 | 0 | 2018-03-01 | 3.2 | 14.8 | 0 | 2017-03-01 | 2.7 | 15.3 | 0 | 2016-03-01 | -12.6 | 30.6 | 0 | 22.75 | 0
2025-03-01 | -8.9 | 26.9 | 0 | 2024-03-01 | -1.9 | 19.9 | 0 | 2023-03-01 | 0.3 | 17.7 | 0 | 2022-03-01 | -12.5 | 30.5 | 0 | 2021-03-01 | -1.2 | 19.2 | 0 | 2020-03-01 | -7.2 | 25.2 | 0 | 2019-03-01 | -6 | 24 | 0 | 2018-03-01 | 4.3 | 13.7 | 0 | 2017-03-01 | 2.7 | 15.3 | 0 | 2016-03-01 | -11.9 | 29.9 | 0 | 22.23 | 0
2025-03-01 | -10.2 | 28.2 | 0 | 2024-03-01 | -0.2 | 18.2 | 0 | 2023-03-01 | 0.9 | 17.1 | 0 | 2022-03-01 | -11.9 | 29.9 | 0 | 2021-03-01 | -2.3 | 20.3 | 0 | 2020-03-01 | -6.2 | 24.2 | 0 | 2019-03-01 | -4.6 | 22.6 | 0 | 2018-03-01 | 4.8 | 13.2 | 0 | 2017-03-01 | 3.5 | 14.5 | 0 | 2016-03-01 | -11.3 | 29.3 | 0 | 21.75 | 0
2025-03-01 | -10.1 | 28.1 | 0 | 2024-03-01 | 2 | 16 | 0 | 2023-03-01 | 0.9 | 17.1 | 0 | 2022-03-01 | -11.4 | 29.4 | 0 | 2021-03-01 | -3.3 | 21.3 | 0 | 2020-03-01 | -5.7 | 23.7 | 0 | 2019-03-01 | -3.6 | 21.6 | 0 | 2018-03-01 | 5.1 | 12.9 | 0 | 2017-03-01 | 4.1 | 13.9 | 0 | 2016-03-01 | -11.2 | 29.2 | 0 | 21.32 | 0
2025-03-01 | -9.6 | 27.6 | 0 | 2024-03-01 | 4 | 14 | 0 | 2023-03-01 | 0.9 | 17.1 | 0 | 2022-03-01 | -11.1 | 29.1 | 0 | 2021-03-01 | -4.4 | 22.4 | 0 | 2020-03-01 | -5.2 | 23.2 | 0 | 2019-03-01 | -3.9 | 21.9 | 0 | 2018-03-01 | 5.3 | 12.7 | 0 | 2017-03-01 | 4 | 14 | 0 | 2016-03-01 | -11.1 | 29.1 | 0 | 21.11 | 0
2025-03-01 | -10.2 | 28.2 | 0 | 2024-03-01 | 5.8 | 12.2 | 0 | 2023-03-01 | 1.1 | 16.9 | 0 | 2022-03-01 | -10.5 | 28.5 | 0 | 2021-03-01 | -5.5 | 23.5 | 0 | 2020-03-01 | -4.8 | 22.8 | 0 | 2019-03-01 | -4.2 | 22.2 | 0 | 2018-03-01 | 3.7 | 14.3 | 0 | 2017-03-01 | 4 | 14 | 0 | 2016-03-01 | -11 | 29 | 0 | 21.16 | 0
2025-03-01 | -10.6 | 28.6 | 0 | 2024-03-01 | 5.2 | 12.8 | 0 | 2023-03-01 | 1.2 | 16.8 | 0 | 2022-03-01 | -10.2 | 28.2 | 0 | 2021-03-01 | -6.4 | 24.4 | 0 | 2020-03-01 | -5.2 | 23.2 | 0 | 2019-03-01 | -4.8 | 22.8 | 0 | 2018-03-01 | 1.3 | 16.7 | 0 | 2017-03-01 | 3.1 | 14.9 | 0 | 2016-03-01 | -11.4 | 29.4 | 0 | 21.78 | 0
2025-03-01 | -11.7 | 29.7 | 0 | 2024-03-01 | 3.3 | 14.7 | 0 | 2023-03-01 | 0.6 | 17.4 | 0 | 2022-03-01 | -10.2 | 28.2 | 0 | 2021-03-01 | -8 | 26 | 0 | 2020-03-01 | -6.1 | 24.1 | 0 | 2019-03-01 | -5.9 | 23.9 | 0 | 2018-03-01 | 0.4 | 17.6 | 0 | 2017-03-01 | 2.6 | 15.4 | 0 | 2016-03-01 | -12.2 | 30.2 | 0 | 22.72 | 0
2025-03-01 | -12.1 | 30.1 | 0 | 2024-03-01 | 2.3 | 15.7 | 0 | 2023-03-01 | 0.3 | 17.7 | 0 | 2022-03-01 | -9.9 | 27.9 | 0 | 2021-03-01 | -9.7 | 27.7 | 0 | 2020-03-01 | -8.2 | 26.2 | 0 | 2019-03-01 | -6.7 | 24.7 | 0 | 2018-03-01 | 0.6 | 17.4 | 0 | 2017-03-01 | 2.4 | 15.6 | 0 | 2016-03-01 | -12.3 | 30.3 | 0 | 23.33 | 0
2025-03-01 | -12.8 | 30.8 | 0 | 2024-03-01 | 1.9 | 16.1 | 0 | 2023-03-01 | -0.1 | 18.1 | 0 | 2022-03-01 | -9.7 | 27.7 | 0 | 2021-03-01 | -11.7 | 29.7 | 0 | 2020-03-01 | -7.6 | 25.6 | 0 | 2019-03-01 | -7.1 | 25.1 | 0 | 2018-03-01 | 0.7 | 17.3 | 0 | 2017-03-01 | 2.1 | 15.9 | 0 | 2016-03-01 | -12.5 | 30.5 | 0 | 23.68 | 0
2025-03-01 | -13.4 | 31.4 | 0 | 2024-03-01 | 1 | 17 | 0 | 2023-03-01 | -0.5 | 18.5 | 0 | 2022-03-01 | -9.7 | 27.7 | 0 | 2021-03-01 | -13.2 | 31.2 | 0 | 2020-03-01 | -7.9 | 25.9 | 0 | 2019-03-01 | -8.6 | 26.6 | 0 | 2018-03-01 | 0.4 | 17.6 | 0 | 2017-03-01 | 1.6 | 16.4 | 0 | 2016-03-01 | -12.2 | 30.2 | 0 | 24.25 | 0
2025-03-01 | -14.1 | 32.1 | 0 | 2024-03-01 | -0.4 | 18.4 | 0 | 2023-03-01 | -1.3 | 19.3 | 0 | 2022-03-01 | -9.8 | 27.8 | 0 | 2021-03-01 | -14.7 | 32.7 | 0 | 2020-03-01 | -6.4 | 24.4 | 0 | 2019-03-01 | -9 | 27 | 0 | 2018-03-01 | -0.2 | 18.2 | 0 | 2017-03-01 | 1 | 17 | 0 | 2016-03-01 | -11.7 | 29.7 | 0 | 24.66 | 0
2025-03-01 | -15.1 | 33.1 | 0 | 2024-03-01 | 0 | 18 | 0 | 2023-03-01 | -1.2 | 19.2 | 0 | 2022-03-01 | -9.6 | 27.6 | 0 | 2021-03-01 | -15.6 | 33.6 | 0 | 2020-03-01 | -6.4 | 24.4 | 0 | 2019-03-01 | -10.1 | 28.1 | 0 | 2018-03-01 | -0.4 | 18.4 | 0 | 2017-03-01 | 0.6 | 17.4 | 0 | 2016-03-01 | -11.1 | 29.1 | 0 | 24.89 | 0
2025-03-02 | -15.9 | 33.9 | 0 | 2024-03-02 | 0.6 | 17.4 | 0 | 2023-03-02 | -1 | 19 | 0 | 2022-03-02 | -9.3 | 27.3 | 0 | 2021-03-02 | -16.7 | 34.7 | 0 | 2020-03-02 | -7.3 | 25.3 | 0 | 2019-03-02 | -9.9 | 27.9 | 0 | 2018-03-02 | -0.4 | 18.4 | 0 | 2017-03-02 | -1.1 | 19.1 | 0 | 2016-03-02 | -10.8 | 28.8 | 0 | 25.18 | 0
2025-03-02 | -17 | 35 | 0 | 2024-03-02 | 1.3 | 16.7 | 0 | 2023-03-02 | -1 | 19 | 0 | 2022-03-02 | -10.9 | 28.9 | 0 | 2021-03-02 | -17.3 | 35.3 | 0 | 2020-03-02 | -7.2 | 25.2 | 0 | 2019-03-02 | -10.3 | 28.3 | 0 | 2018-03-02 | -0.4 | 18.4 | 0 | 2017-03-02 | -2.6 | 20.6 | 0 | 2016-03-02 | -10.3 | 28.3 | 0 | 25.57 | 0
2025-03-02 | -18.1 | 36.1 | 0 | 2024-03-02 | 0.9 | 17.1 | 0 | 2023-03-02 | -0.9 | 18.9 | 0 | 2022-03-02 | -12.2 | 30.2 | 0 | 2021-03-02 | -17.5 | 35.5 | 0 | 2020-03-02 | -6.6 | 24.6 | 0 | 2019-03-02 | -11 | 29 | 0 | 2018-03-02 | -0.6 | 18.6 | 0 | 2017-03-02 | -3.6 | 21.6 | 0 | 2016-03-02 | -10.2 | 28.2 | 0 | 25.98 | 0
2025-03-02 | -19.1 | 37.1 | 0 | 2024-03-02 | 0.4 | 17.6 | 0 | 2023-03-02 | -0.9 | 18.9 | 0 | 2022-03-02 | -11.8 | 29.8 | 0 | 2021-03-02 | -17.7 | 35.7 | 0 | 2020-03-02 | -6 | 24 | 0 | 2019-03-02 | -11.1 | 29.1 | 0 | 2018-03-02 | -0.9 | 18.9 | 0 | 2017-03-02 | -4.9 | 22.9 | 0 | 2016-03-02 | -9.8 | 27.8 | 0 | 26.18 | 0
2025-03-02 | -19.6 | 37.6 | 0 | 2024-03-02 | -0.6 | 18.6 | 0 | 2023-03-02 | -1.1 | 19.1 | 0 | 2022-03-02 | -12.2 | 30.2 | 0 | 2021-03-02 | -17.8 | 35.8 | 0 | 2020-03-02 | -6 | 24 | 0 | 2019-03-02 | -11.1 | 29.1 | 0 | 2018-03-02 | -0.9 | 18.9 | 0 | 2017-03-02 | -7.2 | 25.2 | 0 | 2016-03-02 | -9.5 | 27.5 | 0 | 26.6 | 0
2025-03-02 | -20.8 | 38.8 | 0 | 2024-03-02 | -3.7 | 21.7 | 0 | 2023-03-02 | -1.3 | 19.3 | 0 | 2022-03-02 | -13 | 31 | 0 | 2021-03-02 | -18.1 | 36.1 | 0 | 2020-03-02 | -5.7 | 23.7 | 0 | 2019-03-02 | -11.5 | 29.5 | 0 | 2018-03-02 | -0.8 | 18.8 | 0 | 2017-03-02 | -8.4 | 26.4 | 0 | 2016-03-02 | -10.2 | 28.2 | 0 | 27.35 | 0
2025-03-02 | -21 | 39 | 0 | 2024-03-02 | -4.1 | 22.1 | 0 | 2023-03-02 | -1.2 | 19.2 | 0 | 2022-03-02 | -12.4 | 30.4 | 0 | 2021-03-02 | -18.4 | 36.4 | 0 | 2020-03-02 | -5.4 | 23.4 | 0 | 2019-03-02 | -10.7 | 28.7 | 0 | 2018-03-02 | -0.8 | 18.8 | 0 | 2017-03-02 | -9.7 | 27.7 | 0 | 2016-03-02 | -11.2 | 29.2 | 0 | 27.49 | 0
2025-03-02 | -21.2 | 39.2 | 0 | 2024-03-02 | -2 | 20 | 0 | 2023-03-02 | -1.2 | 19.2 | 0 | 2022-03-02 | -12.4 | 30.4 | 0 | 2021-03-02 | -18.5 | 36.5 | 0 | 2020-03-02 | -6 | 24 | 0 | 2019-03-02 | -10.3 | 28.3 | 0 | 2018-03-02 | -1.2 | 19.2 | 0 | 2017-03-02 | -11.2 | 29.2 | 0 | 2016-03-02 | -11.4 | 29.4 | 0 | 27.54 | 0
2025-03-02 | -20.6 | 38.6 | 0 | 2024-03-02 | -0.2 | 18.2 | 0 | 2023-03-02 | -1.1 | 19.1 | 0 | 2022-03-02 | -12 | 30 | 0 | 2021-03-02 | -17.9 | 35.9 | 0 | 2020-03-02 | -5.7 | 23.7 | 0 | 2019-03-02 | -8.8 | 26.8 | 0 | 2018-03-02 | -1.2 | 19.2 | 0 | 2017-03-02 | -12.1 | 30.1 | 0 | 2016-03-02 | -11.8 | 29.8 | 0 | 27.14 | 0
2025-03-02 | -19.5 | 37.5 | 0 | 2024-03-02 | 2 | 16 | 0 | 2023-03-02 | -0.8 | 18.8 | 0 | 2022-03-02 | -10.9 | 28.9 | 0 | 2021-03-02 | -16.7 | 34.7 | 0 | 2020-03-02 | -5 | 23 | 0 | 2019-03-02 | -8.1 | 26.1 | 0 | 2018-03-02 | -1.3 | 19.3 | 0 | 2017-03-02 | -12.5 | 30.5 | 0 | 2016-03-02 | -12 | 30 | 0 | 26.48 | 0
2025-03-02 | -18.3 | 36.3 | 0 | 2024-03-02 | 5.2 | 12.8 | 0 | 2023-03-02 | -0.7 | 18.7 | 0 | 2022-03-02 | -8.2 | 26.2 | 0 | 2021-03-02 | -15.5 | 33.5 | 0 | 2020-03-02 | -3.4 | 21.4 | 0 | 2019-03-02 | -7 | 25 | 0 | 2018-03-02 | -1.2 | 19.2 | 0 | 2017-03-02 | -12 | 30 | 0 | 2016-03-02 | -11.5 | 29.5 | 0 | 25.26 | 0
2025-03-02 | -17.1 | 35.1 | 0 | 2024-03-02 | 5.8 | 12.2 | 0 | 2023-03-02 | -0.3 | 18.3 | 0 | 2022-03-02 | -6.6 | 24.6 | 0 | 2021-03-02 | -14.3 | 32.3 | 0 | 2020-03-02 | -2 | 20 | 0 | 2019-03-02 | -5.6 | 23.6 | 0 | 2018-03-02 | -1 | 19 | 0 | 2017-03-02 | -11.4 | 29.4 | 0 | 2016-03-02 | -11.4 | 29.4 | 0 | 24.39 | 0
2025-03-02 | -15.9 | 33.9 | 0 | 2024-03-02 | 5 | 13 | 0 | 2023-03-02 | -0.2 | 18.2 | 0 | 2022-03-02 | -5 | 23 | 0 | 2021-03-02 | -13.1 | 31.1 | 0 | 2020-03-02 | -1.4 | 19.4 | 0 | 2019-03-02 | -4.9 | 22.9 | 0 | 2018-03-02 | -0.8 | 18.8 | 0 | 2017-03-02 | -11.1 | 29.1 | 0 | 2016-03-02 | -10.5 | 28.5 | 0 | 23.79 | 0
2025-03-02 | -14.9 | 32.9 | 0 | 2024-03-02 | 5.1 | 12.9 | 0 | 2023-03-02 | -0.1 | 18.1 | 0 | 2022-03-02 | -4.2 | 22.2 | 0 | 2021-03-02 | -11.5 | 29.5 | 0 | 2020-03-02 | 0.1 | 17.9 | 0 | 2019-03-02 | -4.6 | 22.6 | 0 | 2018-03-02 | -0.3 | 18.3 | 0 | 2017-03-02 | -10.2 | 28.2 | 0 | 2016-03-02 | -9.6 | 27.6 | 0 | 23.02 | 0
2025-03-02 | -13.6 | 31.6 | 0 | 2024-03-02 | 5.1 | 12.9 | 0 | 2023-03-02 | 1 | 17 | 0 | 2022-03-02 | -3.8 | 21.8 | 0 | 2021-03-02 | -10 | 28 | 0 | 2020-03-02 | 0.5 | 17.5 | 0 | 2019-03-02 | -4.2 | 22.2 | 0 | 2018-03-02 | 0 | 18 | 0 | 2017-03-02 | -10.1 | 28.1 | 0 | 2016-03-02 | -8.7 | 26.7 | 0 | 22.38 | 0
2025-03-02 | -13 | 31 | 0 | 2024-03-02 | 5 | 13 | 0 | 2023-03-02 | 2.5 | 15.5 | 0 | 2022-03-02 | -3.1 | 21.1 | 0 | 2021-03-02 | -8.9 | 26.9 | 0 | 2020-03-02 | 2.2 | 15.8 | 0 | 2019-03-02 | -3.4 | 21.4 | 0 | 2018-03-02 | 0.2 | 17.8 | 0 | 2017-03-02 | -9.2 | 27.2 | 0 | 2016-03-02 | -8.1 | 26.1 | 0 | 21.58 | 0
2025-03-02 | -12.4 | 30.4 | 0 | 2024-03-02 | 4.7 | 13.3 | 0 | 2023-03-02 | 2.4 | 15.6 | 0 | 2022-03-02 | -3.1 | 21.1 | 0 | 2021-03-02 | -8.1 | 26.1 | 0 | 2020-03-02 | 3.6 | 14.4 | 0 | 2019-03-02 | -3.1 | 21.1 | 0 | 2018-03-02 | 0.6 | 17.4 | 0 | 2017-03-02 | -9.1 | 27.1 | 0 | 2016-03-02 | -7.9 | 25.9 | 0 | 21.24 | 0
2025-03-02 | -12.5 | 30.5 | 0 | 2024-03-02 | 4.1 | 13.9 | 0 | 2023-03-02 | 1.7 | 16.3 | 0 | 2022-03-02 | -3.9 | 21.9 | 0 | 2021-03-02 | -7.9 | 25.9 | 0 | 2020-03-02 | 3.8 | 14.2 | 0 | 2019-03-02 | -4.1 | 22.1 | 0 | 2018-03-02 | 0.4 | 17.6 | 0 | 2017-03-02 | -9.2 | 27.2 | 0 | 2016-03-02 | -8 | 26 | 0 | 21.56 | 0
2025-03-02 | -13 | 31 | 0 | 2024-03-02 | 3.6 | 14.4 | 0 | 2023-03-02 | 0.3 | 17.7 | 0 | 2022-03-02 | -4 | 22 | 0 | 2021-03-02 | -8.8 | 26.8 | 0 | 2020-03-02 | 3.8 | 14.2 | 0 | 2019-03-02 | -4.8 | 22.8 | 0 | 2018-03-02 | 0.2 | 17.8 | 0 | 2017-03-02 | -9.6 | 27.6 | 0 | 2016-03-02 | -9.5 | 27.5 | 0 | 22.18 | 0
2025-03-02 | -14 | 32 | 0 | 2024-03-02 | 3.4 | 14.6 | 0 | 2023-03-02 | 0.6 | 17.4 | 0 | 2022-03-02 | -3.8 | 21.8 | 0 | 2021-03-02 | -8.5 | 26.5 | 0 | 2020-03-02 | 3.6 | 14.4 | 0 | 2019-03-02 | -5.1 | 23.1 | 0 | 2018-03-02 | -0.5 | 18.5 | 0 | 2017-03-02 | -9.3 | 27.3 | 0 | 2016-03-02 | -10.3 | 28.3 | 0 | 22.39 | 0
2025-03-02 | -15.6 | 33.6 | 0 | 2024-03-02 | 3.5 | 14.5 | 0 | 2023-03-02 | -0.5 | 18.5 | 0 | 2022-03-02 | -3.8 | 21.8 | 0 | 2021-03-02 | -8.3 | 26.3 | 0 | 2020-03-02 | 3.6 | 14.4 | 0 | 2019-03-02 | -5.4 | 23.4 | 0 | 2018-03-02 | -1.1 | 19.1 | 0 | 2017-03-02 | -9.3 | 27.3 | 0 | 2016-03-02 | -10.4 | 28.4 | 0 | 22.73 | 0
2025-03-02 | -16 | 34 | 0 | 2024-03-02 | 3 | 15 | 0 | 2023-03-02 | -2.2 | 20.2 | 0 | 2022-03-02 | -4 | 22 | 0 | 2021-03-02 | -8.9 | 26.9 | 0 | 2020-03-02 | 3.5 | 14.5 | 0 | 2019-03-02 | -5.4 | 23.4 | 0 | 2018-03-02 | -0.7 | 18.7 | 0 | 2017-03-02 | -9.8 | 27.8 | 0 | 2016-03-02 | -10.7 | 28.7 | 0 | 23.12 | 0
2025-03-02 | -19.8 | 37.8 | 0 | 2024-03-02 | 2 | 16 | 0 | 2023-03-02 | -3.3 | 21.3 | 0 | 2022-03-02 | -4.4 | 22.4 | 0 | 2021-03-02 | -8.8 | 26.8 | 0 | 2020-03-02 | 3.2 | 14.8 | 0 | 2019-03-02 | -7.1 | 25.1 | 0 | 2018-03-02 | -0.5 | 18.5 | 0 | 2017-03-02 | -10.2 | 28.2 | 0 | 2016-03-02 | -11.9 | 29.9 | 0 | 24.08 | 0
2025-03-02 | -18.9 | 36.9 | 0 | 2024-03-02 | 1.6 | 16.4 | 0 | 2023-03-02 | -5 | 23 | 0 | 2022-03-02 | -4.9 | 22.9 | 0 | 2021-03-02 | -8.6 | 26.6 | 0 | 2020-03-02 | 1.9 | 16.1 | 0 | 2019-03-02 | -7.7 | 25.7 | 0 | 2018-03-02 | -1 | 19 | 0 | 2017-03-02 | -10.7 | 28.7 | 0 | 2016-03-02 | -13.4 | 31.4 | 0 | 24.67 | 0
2025-03-03 | -18.6 | 36.6 | 0 | 2024-03-03 | 1.5 | 16.5 | 0 | 2023-03-03 | -6.5 | 24.5 | 0 | 2022-03-03 | -8.2 | 26.2 | 0 | 2021-03-03 | -8 | 26 | 0 | 2020-03-03 | 1 | 17 | 0 | 2019-03-03 | -9.9 | 27.9 | 0 | 2018-03-03 | -1 | 19 | 0 | 2017-03-03 | -11.7 | 29.7 | 0 | 2016-03-03 | -14.9 | 32.9 | 0 | 25.63 | 0
2025-03-03 | -19.9 | 37.9 | 0 | 2024-03-03 | 1.3 | 16.7 | 0 | 2023-03-03 | -7.3 | 25.3 | 0 | 2022-03-03 | -10 | 28 | 0 | 2021-03-03 | -7.3 | 25.3 | 0 | 2020-03-03 | 0.1 | 17.9 | 0 | 2019-03-03 | -9 | 27 | 0 | 2018-03-03 | -1.1 | 19.1 | 0 | 2017-03-03 | -12.2 | 30.2 | 0 | 2016-03-03 | -15.9 | 33.9 | 0 | 26.13 | 0
2025-03-03 | -20.9 | 38.9 | 0 | 2024-03-03 | 1.4 | 16.6 | 0 | 2023-03-03 | -8.3 | 26.3 | 0 | 2022-03-03 | -6.9 | 24.9 | 0 | 2021-03-03 | -6.2 | 24.2 | 0 | 2020-03-03 | -1.4 | 19.4 | 0 | 2019-03-03 | -9.4 | 27.4 | 0 | 2018-03-03 | -1.5 | 19.5 | 0 | 2017-03-03 | -12.9 | 30.9 | 0 | 2016-03-03 | -17.1 | 35.1 | 0 | 26.32 | 0
2025-03-03 | -22.1 | 40.1 | 0 | 2024-03-03 | 1.6 | 16.4 | 0 | 2023-03-03 | -9.3 | 27.3 | 0 | 2022-03-03 | -9.5 | 27.5 | 0 | 2021-03-03 | -5.6 | 23.6 | 0 | 2020-03-03 | -1.5 | 19.5 | 0 | 2019-03-03 | -8.9 | 26.9 | 0 | 2018-03-03 | -1.5 | 19.5 | 0 | 2017-03-03 | -13.5 | 31.5 | 0 | 2016-03-03 | -17.6 | 35.6 | 0 | 26.79 | 0
2025-03-03 | -20.1 | 38.1 | 0 | 2024-03-03 | 1.7 | 16.3 | 0 | 2023-03-03 | -10.5 | 28.5 | 0 | 2022-03-03 | -10.5 | 28.5 | 0 | 2021-03-03 | -5.3 | 23.3 | 0 | 2020-03-03 | -2.2 | 20.2 | 0 | 2019-03-03 | -8.7 | 26.7 | 0 | 2018-03-03 | -1.6 | 19.6 | 0 | 2017-03-03 | -13.9 | 31.9 | 0 | 2016-03-03 | -19.1 | 37.1 | 0 | 27.02 | 0
2025-03-03 | -21.3 | 39.3 | 0 | 2024-03-03 | 2.3 | 15.7 | 0 | 2023-03-03 | -10.4 | 28.4 | 0 | 2022-03-03 | -11 | 29 | 0 | 2021-03-03 | -5.3 | 23.3 | 0 | 2020-03-03 | -2.6 | 20.6 | 0 | 2019-03-03 | -8.2 | 26.2 | 0 | 2018-03-03 | -1.3 | 19.3 | 0 | 2017-03-03 | -13.9 | 31.9 | 0 | 2016-03-03 | -19.1 | 37.1 | 0 | 27.08 | 0
2025-03-03 | -22.7 | 40.7 | 0 | 2024-03-03 | 2 | 16 | 0 | 2023-03-03 | -11.6 | 29.6 | 0 | 2022-03-03 | -12 | 30 | 0 | 2021-03-03 | -5 | 23 | 0 | 2020-03-03 | -3.5 | 21.5 | 0 | 2019-03-03 | -7.3 | 25.3 | 0 | 2018-03-03 | -1 | 19 | 0 | 2017-03-03 | -14.2 | 32.2 | 0 | 2016-03-03 | -20.8 | 38.8 | 0 | 27.61 | 0
2025-03-03 | -22.6 | 40.6 | 0 | 2024-03-03 | 2.4 | 15.6 | 0 | 2023-03-03 | -12 | 30 | 0 | 2022-03-03 | -12.7 | 30.7 | 0 | 2021-03-03 | -4.6 | 22.6 | 0 | 2020-03-03 | -3.4 | 21.4 | 0 | 2019-03-03 | -6.8 | 24.8 | 0 | 2018-03-03 | -0.9 | 18.9 | 0 | 2017-03-03 | -15.9 | 33.9 | 0 | 2016-03-03 | -21.5 | 39.5 | 0 | 27.8 | 0
2025-03-03 | -20.1 | 38.1 | 0 | 2024-03-03 | 2.8 | 15.2 | 0 | 2023-03-03 | -10.3 | 28.3 | 0 | 2022-03-03 | -12.5 | 30.5 | 0 | 2021-03-03 | -4.1 | 22.1 | 0 | 2020-03-03 | -3.5 | 21.5 | 0 | 2019-03-03 | -6.1 | 24.1 | 0 | 2018-03-03 | -0.6 | 18.6 | 0 | 2017-03-03 | -15.1 | 33.1 | 0 | 2016-03-03 | -20.9 | 38.9 | 0 | 27.04 | 0
2025-03-03 | -16 | 34 | 0 | 2024-03-03 | 3.4 | 14.6 | 0 | 2023-03-03 | -9.2 | 27.2 | 0 | 2022-03-03 | -12.5 | 30.5 | 0 | 2021-03-03 | -3.2 | 21.2 | 0 | 2020-03-03 | -2.4 | 20.4 | 0 | 2019-03-03 | -6.6 | 24.6 | 0 | 2018-03-03 | -0.2 | 18.2 | 0 | 2017-03-03 | -13.5 | 31.5 | 0 | 2016-03-03 | -18.4 | 36.4 | 0 | 25.86 | 0
2025-03-03 | -11 | 29 | 0 | 2024-03-03 | 4.2 | 13.8 | 0 | 2023-03-03 | -7.8 | 25.8 | 0 | 2022-03-03 | -12.4 | 30.4 | 0 | 2021-03-03 | -2.8 | 20.8 | 0 | 2020-03-03 | 0.7 | 17.3 | 0 | 2019-03-03 | -5.3 | 23.3 | 0 | 2018-03-03 | 0.5 | 17.5 | 0 | 2017-03-03 | -12.4 | 30.4 | 0 | 2016-03-03 | -16.6 | 34.6 | 0 | 24.29 | 0
2025-03-03 | -8.5 | 26.5 | 0 | 2024-03-03 | 5 | 13 | 0 | 2023-03-03 | -6.5 | 24.5 | 0 | 2022-03-03 | -11.7 | 29.7 | 0 | 2021-03-03 | -1.8 | 19.8 | 0 | 2020-03-03 | 2.6 | 15.4 | 0 | 2019-03-03 | -4 | 22 | 0 | 2018-03-03 | 1.3 | 16.7 | 0 | 2017-03-03 | -12.2 | 30.2 | 0 | 2016-03-03 | -15.1 | 33.1 | 0 | 23.09 | 0
2025-03-03 | -6.7 | 24.7 | 0 | 2024-03-03 | 5.7 | 12.3 | 0 | 2023-03-03 | -5 | 23 | 0 | 2022-03-03 | -11.3 | 29.3 | 0 | 2021-03-03 | -1.5 | 19.5 | 0 | 2020-03-03 | 3 | 15 | 0 | 2019-03-03 | -3.4 | 21.4 | 0 | 2018-03-03 | 2.1 | 15.9 | 0 | 2017-03-03 | -12.3 | 30.3 | 0 | 2016-03-03 | -14.2 | 32.2 | 0 | 22.36 | 0
2025-03-03 | -5.3 | 23.3 | 0 | 2024-03-03 | 6.6 | 11.4 | 0 | 2023-03-03 | -4.5 | 22.5 | 0 | 2022-03-03 | -10.9 | 28.9 | 0 | 2021-03-03 | -0.8 | 18.8 | 0 | 2020-03-03 | 2.9 | 15.1 | 0 | 2019-03-03 | -2.7 | 20.7 | 0 | 2018-03-03 | 2.5 | 15.5 | 0 | 2017-03-03 | -11.5 | 29.5 | 0 | 2016-03-03 | -12.8 | 30.8 | 0 | 21.65 | 0
2025-03-03 | -4.2 | 22.2 | 0 | 2024-03-03 | 7 | 11 | 0 | 2023-03-03 | -3.6 | 21.6 | 0 | 2022-03-03 | -10.6 | 28.6 | 0 | 2021-03-03 | -0.7 | 18.7 | 0 | 2020-03-03 | 2.7 | 15.3 | 0 | 2019-03-03 | -1.9 | 19.9 | 0 | 2018-03-03 | 2.4 | 15.6 | 0 | 2017-03-03 | -10.4 | 28.4 | 0 | 2016-03-03 | -12.4 | 30.4 | 0 | 21.17 | 0
2025-03-03 | -3.8 | 21.8 | 0 | 2024-03-03 | 7.1 | 10.9 | 0 | 2023-03-03 | -3.3 | 21.3 | 0 | 2022-03-03 | -10.6 | 28.6 | 0 | 2021-03-03 | -0.6 | 18.6 | 0 | 2020-03-03 | 2.6 | 15.4 | 0 | 2019-03-03 | -2 | 20 | 0 | 2018-03-03 | 1.6 | 16.4 | 0 | 2017-03-03 | -10.4 | 28.4 | 0 | 2016-03-03 | -11.9 | 29.9 | 0 | 21.13 | 0
2025-03-03 | -3.6 | 21.6 | 0 | 2024-03-03 | 7.3 | 10.7 | 0 | 2023-03-03 | -3.5 | 21.5 | 0 | 2022-03-03 | -10.6 | 28.6 | 0 | 2021-03-03 | -0.8 | 18.8 | 0 | 2020-03-03 | 2 | 16 | 0 | 2019-03-03 | -1.9 | 19.9 | 0 | 2018-03-03 | 1.5 | 16.5 | 0 | 2017-03-03 | -10.1 | 28.1 | 0 | 2016-03-03 | -11.2 | 29.2 | 0 | 21.09 | 0
2025-03-03 | -3.6 | 21.6 | 0 | 2024-03-03 | 7 | 11 | 0 | 2023-03-03 | -4.6 | 22.6 | 0 | 2022-03-03 | -10.8 | 28.8 | 0 | 2021-03-03 | -0.8 | 18.8 | 0 | 2020-03-03 | 0.8 | 17.2 | 0 | 2019-03-03 | -2.4 | 20.4 | 0 | 2018-03-03 | 1.3 | 16.7 | 0 | 2017-03-03 | -11.6 | 29.6 | 0 | 2016-03-03 | -11.5 | 29.5 | 0 | 21.62 | 0
2025-03-03 | -4.8 | 22.8 | 0 | 2024-03-03 | 4.9 | 13.1 | 0 | 2023-03-03 | -5.1 | 23.1 | 0 | 2022-03-03 | -11.7 | 29.7 | 0 | 2021-03-03 | -1.3 | 19.3 | 0 | 2020-03-03 | 0.6 | 17.4 | 0 | 2019-03-03 | -3 | 21 | 0 | 2018-03-03 | 1 | 17 | 0 | 2017-03-03 | -12.2 | 30.2 | 0 | 2016-03-03 | -12.1 | 30.1 | 0 | 22.37 | 0
2025-03-03 | -5.4 | 23.4 | 0 | 2024-03-03 | 2.4 | 15.6 | 0 | 2023-03-03 | -5.2 | 23.2 | 0 | 2022-03-03 | -13.2 | 31.2 | 0 | 2021-03-03 | -1.3 | 19.3 | 0 | 2020-03-03 | 1.1 | 16.9 | 0 | 2019-03-03 | -3.6 | 21.6 | 0 | 2018-03-03 | 1 | 17 | 0 | 2017-03-03 | -13.2 | 31.2 | 0 | 2016-03-03 | -13.8 | 31.8 | 0 | 23.12 | 0
2025-03-03 | -5.4 | 23.4 | 0 | 2024-03-03 | 2.3 | 15.7 | 0 | 2023-03-03 | -5.6 | 23.6 | 0 | 2022-03-03 | -13.4 | 31.4 | 0 | 2021-03-03 | -2 | 20 | 0 | 2020-03-03 | 1.6 | 16.4 | 0 | 2019-03-03 | -3.9 | 21.9 | 0 | 2018-03-03 | 1.2 | 16.8 | 0 | 2017-03-03 | -13.7 | 31.7 | 0 | 2016-03-03 | -15.4 | 33.4 | 0 | 23.43 | 0
2025-03-03 | -4.6 | 22.6 | 0 | 2024-03-03 | 1.9 | 16.1 | 0 | 2023-03-03 | -5.4 | 23.4 | 0 | 2022-03-03 | -15.2 | 33.2 | 0 | 2021-03-03 | -2 | 20 | 0 | 2020-03-03 | 1.6 | 16.4 | 0 | 2019-03-03 | -3.9 | 21.9 | 0 | 2018-03-03 | 1.3 | 16.7 | 0 | 2017-03-03 | -14 | 32 | 0 | 2016-03-03 | -15.9 | 33.9 | 0 | 23.62 | 0
2025-03-03 | -4.2 | 22.2 | 0 | 2024-03-03 | 3.5 | 14.5 | 0 | 2023-03-03 | -5.3 | 23.3 | 0 | 2022-03-03 | -15.4 | 33.4 | 0 | 2021-03-03 | -1.9 | 19.9 | 0 | 2020-03-03 | 1.1 | 16.9 | 0 | 2019-03-03 | -4.4 | 22.4 | 0 | 2018-03-03 | 0.6 | 17.4 | 0 | 2017-03-03 | -15.5 | 33.5 | 0 | 2016-03-03 | -15.9 | 33.9 | 0 | 23.74 | 0
2025-03-03 | -4 | 22 | 0 | 2024-03-03 | 3.4 | 14.6 | 0 | 2023-03-03 | -5.4 | 23.4 | 0 | 2022-03-03 | -19.9 | 37.9 | 0 | 2021-03-03 | -2.7 | 20.7 | 0 | 2020-03-03 | 0.3 | 17.7 | 0 | 2019-03-03 | -4.7 | 22.7 | 0 | 2018-03-03 | -0.2 | 18.2 | 0 | 2017-03-03 | -16.3 | 34.3 | 0 | 2016-03-03 | -18.4 | 36.4 | 0 | 24.79 | 0
2025-03-04 | -3.8 | 21.8 | 0 | 2024-03-04 | 2.5 | 15.5 | 0 | 2023-03-04 | -6.2 | 24.2 | 0 | 2022-03-04 | -17 | 35 | 0 | 2021-03-04 | -3.6 | 21.6 | 0 | 2020-03-04 | 0.7 | 17.3 | 0 | 2019-03-04 | -5.2 | 23.2 | 0 | 2018-03-04 | -1.1 | 19.1 | 0 | 2017-03-04 | -16.4 | 34.4 | 0 | 2016-03-04 | -18.1 | 36.1 | 0 | 24.82 | 0
2025-03-04 | -3.8 | 21.8 | 0 | 2024-03-04 | 3 | 15 | 0 | 2023-03-04 | -7.2 | 25.2 | 0 | 2022-03-04 | -17.4 | 35.4 | 0 | 2021-03-04 | -4.2 | 22.2 | 0 | 2020-03-04 | 0.7 | 17.3 | 0 | 2019-03-04 | -6.1 | 24.1 | 0 | 2018-03-04 | -1.9 | 19.9 | 0 | 2017-03-04 | -16.9 | 34.9 | 0 | 2016-03-04 | -18.7 | 36.7 | 0 | 25.25 | 0
2025-03-04 | -3.8 | 21.8 | 0 | 2024-03-04 | 2 | 16 | 0 | 2023-03-04 | -7 | 25 | 0 | 2022-03-04 | -18 | 36 | 0 | 2021-03-04 | -5.4 | 23.4 | 0 | 2020-03-04 | 0.8 | 17.2 | 0 | 2019-03-04 | -6.3 | 24.3 | 0 | 2018-03-04 | -2.2 | 20.2 | 0 | 2017-03-04 | -16.6 | 34.6 | 0 | 2016-03-04 | -19 | 37 | 0 | 25.55 | 0
2025-03-04 | -3.2 | 21.2 | 0 | 2024-03-04 | 2.5 | 15.5 | 0 | 2023-03-04 | -6.7 | 24.7 | 0 | 2022-03-04 | -18.8 | 36.8 | 0 | 2021-03-04 | -6.6 | 24.6 | 0 | 2020-03-04 | 0.9 | 17.1 | 0 | 2019-03-04 | -5.8 | 23.8 | 0 | 2018-03-04 | -2.4 | 20.4 | 0 | 2017-03-04 | -16.6 | 34.6 | 0 | 2016-03-04 | -19.2 | 37.2 | 0 | 25.59 | 0
2025-03-04 | -3.2 | 21.2 | 0 | 2024-03-04 | 2.2 | 15.8 | 0 | 2023-03-04 | -5.5 | 23.5 | 0 | 2022-03-04 | -19.3 | 37.3 | 0 | 2021-03-04 | -7.9 | 25.9 | 0 | 2020-03-04 | 1 | 17 | 0 | 2019-03-04 | -6.3 | 24.3 | 0 | 2018-03-04 | -2.6 | 20.6 | 0 | 2017-03-04 | -16.6 | 34.6 | 0 | 2016-03-04 | -20.2 | 38.2 | 0 | 25.84 | 0
2025-03-04 | -3.4 | 21.4 | 0 | 2024-03-04 | 1.5 | 16.5 | 0 | 2023-03-04 | -4.3 | 22.3 | 0 | 2022-03-04 | -19.9 | 37.9 | 0 | 2021-03-04 | -8.2 | 26.2 | 0 | 2020-03-04 | 1.1 | 16.9 | 0 | 2019-03-04 | -6.9 | 24.9 | 0 | 2018-03-04 | -2.8 | 20.8 | 0 | 2017-03-04 | -17.2 | 35.2 | 0 | 2016-03-04 | -20.6 | 38.6 | 0 | 26.07 | 0
2025-03-04 | -3 | 21 | 0 | 2024-03-04 | 1.8 | 16.2 | 0 | 2023-03-04 | -3.8 | 21.8 | 0 | 2022-03-04 | -20 | 38 | 0 | 2021-03-04 | -10 | 28 | 0 | 2020-03-04 | 1 | 17 | 0 | 2019-03-04 | -7.8 | 25.8 | 0 | 2018-03-04 | -3 | 21 | 0 | 2017-03-04 | -18.4 | 36.4 | 0 | 2016-03-04 | -20.9 | 38.9 | 0 | 26.41 | 0
2025-03-04 | -2.9 | 20.9 | 0 | 2024-03-04 | 2.1 | 15.9 | 0 | 2023-03-04 | -3.5 | 21.5 | 0 | 2022-03-04 | -20 | 38 | 0 | 2021-03-04 | -10.5 | 28.5 | 0 | 2020-03-04 | 1 | 17 | 0 | 2019-03-04 | -10.3 | 28.3 | 0 | 2018-03-04 | -3.2 | 21.2 | 0 | 2017-03-04 | -19.5 | 37.5 | 0 | 2016-03-04 | -20.8 | 38.8 | 0 | 26.76 | 0
2025-03-04 | -1.7 | 19.7 | 0 | 2024-03-04 | 2.5 | 15.5 | 0 | 2023-03-04 | -3.1 | 21.1 | 0 | 2022-03-04 | -17 | 35 | 0 | 2021-03-04 | -11.5 | 29.5 | 0 | 2020-03-04 | 0.7 | 17.3 | 0 | 2019-03-04 | -11.2 | 29.2 | 0 | 2018-03-04 | -3.2 | 21.2 | 0 | 2017-03-04 | -20 | 38 | 0 | 2016-03-04 | -19 | 37 | 0 | 26.35 | 0
2025-03-04 | -0.8 | 18.8 | 0 | 2024-03-04 | 3.1 | 14.9 | 0 | 2023-03-04 | -2.3 | 20.3 | 0 | 2022-03-04 | -12.8 | 30.8 | 0 | 2021-03-04 | -11.9 | 29.9 | 0 | 2020-03-04 | 1.1 | 16.9 | 0 | 2019-03-04 | -10.6 | 28.6 | 0 | 2018-03-04 | -3.1 | 21.1 | 0 | 2017-03-04 | -20.2 | 38.2 | 0 | 2016-03-04 | -15.4 | 33.4 | 0 | 25.29 | 0
2025-03-04 | 0.2 | 17.8 | 0 | 2024-03-04 | 4 | 14 | 0 | 2023-03-04 | -1.5 | 19.5 | 0 | 2022-03-04 | -10.2 | 28.2 | 0 | 2021-03-04 | -12.1 | 30.1 | 0 | 2020-03-04 | 1.5 | 16.5 | 0 | 2019-03-04 | -9.8 | 27.8 | 0 | 2018-03-04 | -2.2 | 20.2 | 0 | 2017-03-04 | -19.5 | 37.5 | 0 | 2016-03-04 | -11.8 | 29.8 | 0 | 24.14 | 0
2025-03-04 | -0.8 | 18.8 | 0 | 2024-03-04 | 6 | 12 | 0 | 2023-03-04 | -1.3 | 19.3 | 0 | 2022-03-04 | -8.6 | 26.6 | 0 | 2021-03-04 | -11.5 | 29.5 | 0 | 2020-03-04 | 1.9 | 16.1 | 0 | 2019-03-04 | -8.8 | 26.8 | 0 | 2018-03-04 | -1.2 | 19.2 | 0 | 2017-03-04 | -18.5 | 36.5 | 0 | 2016-03-04 | -8.7 | 26.7 | 0 | 23.15 | 0
2025-03-04 | -0.2 | 18.2 | 0 | 2024-03-04 | 8 | 10 | 0 | 2023-03-04 | -1 | 19 | 0 | 2022-03-04 | -6.4 | 24.4 | 0 | 2021-03-04 | -10.5 | 28.5 | 0 | 2020-03-04 | 1.8 | 16.2 | 0 | 2019-03-04 | -8.2 | 26.2 | 0 | 2018-03-04 | -0.6 | 18.6 | 0 | 2017-03-04 | -17.5 | 35.5 | 0 | 2016-03-04 | -6.8 | 24.8 | 0 | 22.14 | 0
2025-03-04 | 0.6 | 17.4 | 0 | 2024-03-04 | 9.3 | 8.7 | 0 | 2023-03-04 | -0.8 | 18.8 | 0 | 2022-03-04 | -5.7 | 23.7 | 0 | 2021-03-04 | -10 | 28 | 0 | 2020-03-04 | 2.6 | 15.4 | 0 | 2019-03-04 | -7.6 | 25.6 | 0 | 2018-03-04 | -0.3 | 18.3 | 0 | 2017-03-04 | -16.2 | 34.2 | 0 | 2016-03-04 | -5.7 | 23.7 | 0 | 21.38 | 0
2025-03-04 | 0 | 18 | 0 | 2024-03-04 | 10.2 | 7.8 | 0 | 2023-03-04 | -0.6 | 18.6 | 0 | 2022-03-04 | -4.4 | 22.4 | 0 | 2021-03-04 | -9.2 | 27.2 | 0 | 2020-03-04 | 3.4 | 14.6 | 0 | 2019-03-04 | -6.9 | 24.9 | 0 | 2018-03-04 | 0.3 | 17.7 | 0 | 2017-03-04 | -15.3 | 33.3 | 0 | 2016-03-04 | -4.9 | 22.9 | 0 | 20.74 | 0
2025-03-04 | 0.1 | 17.9 | 0 | 2024-03-04 | 11.6 | 6.4 | 0 | 2023-03-04 | -0.6 | 18.6 | 0 | 2022-03-04 | -3.4 | 21.4 | 0 | 2021-03-04 | -8.9 | 26.9 | 0 | 2020-03-04 | 3.6 | 14.4 | 0 | 2019-03-04 | -7 | 25 | 0 | 2018-03-04 | 0.8 | 17.2 | 0 | 2017-03-04 | -14.6 | 32.6 | 0 | 2016-03-04 | -4.5 | 22.5 | 0 | 20.29 | 0
2025-03-04 | 0.2 | 17.8 | 0 | 2024-03-04 | 10.9 | 7.1 | 0 | 2023-03-04 | -0.4 | 18.4 | 0 | 2022-03-04 | -3.1 | 21.1 | 0 | 2021-03-04 | -8.2 | 26.2 | 0 | 2020-03-04 | 3.2 | 14.8 | 0 | 2019-03-04 | -6.9 | 24.9 | 0 | 2018-03-04 | 0.5 | 17.5 | 0 | 2017-03-04 | -14.3 | 32.3 | 0 | 2016-03-04 | -4.9 | 22.9 | 0 | 20.3 | 0
2025-03-04 | 0.2 | 17.8 | 0 | 2024-03-04 | 8.6 | 9.4 | 0 | 2023-03-04 | -0.5 | 18.5 | 0 | 2022-03-04 | -4.6 | 22.6 | 0 | 2021-03-04 | -8.8 | 26.8 | 0 | 2020-03-04 | 2.8 | 15.2 | 0 | 2019-03-04 | -7.4 | 25.4 | 0 | 2018-03-04 | -0.1 | 18.1 | 0 | 2017-03-04 | -14.5 | 32.5 | 0 | 2016-03-04 | -5.1 | 23.1 | 0 | 20.94 | 0
2025-03-04 | 0.1 | 17.9 | 0 | 2024-03-04 | 6.5 | 11.5 | 0 | 2023-03-04 | -0.4 | 18.4 | 0 | 2022-03-04 | -4.2 | 22.2 | 0 | 2021-03-04 | -8.7 | 26.7 | 0 | 2020-03-04 | 1.8 | 16.2 | 0 | 2019-03-04 | -8.5 | 26.5 | 0 | 2018-03-04 | -1 | 19 | 0 | 2017-03-04 | -14.9 | 32.9 | 0 | 2016-03-04 | -6.7 | 24.7 | 0 | 21.6 | 0
2025-03-04 | 0.1 | 17.9 | 0 | 2024-03-04 | 4.2 | 13.8 | 0 | 2023-03-04 | -0.9 | 18.9 | 0 | 2022-03-04 | -6 | 24 | 0 | 2021-03-04 | -8.8 | 26.8 | 0 | 2020-03-04 | 1.8 | 16.2 | 0 | 2019-03-04 | -8 | 26 | 0 | 2018-03-04 | -1.2 | 19.2 | 0 | 2017-03-04 | -15.2 | 33.2 | 0 | 2016-03-04 | -8.4 | 26.4 | 0 | 22.24 | 0
2025-03-04 | 0.4 | 17.6 | 0 | 2024-03-04 | 4.2 | 13.8 | 0 | 2023-03-04 | -1.6 | 19.6 | 0 | 2022-03-04 | -6.4 | 24.4 | 0 | 2021-03-04 | -9.1 | 27.1 | 0 | 2020-03-04 | 1.7 | 16.3 | 0 | 2019-03-04 | -9.1 | 27.1 | 0 | 2018-03-04 | -1.4 | 19.4 | 0 | 2017-03-04 | -15.2 | 33.2 | 0 | 2016-03-04 | -8.9 | 26.9 | 0 | 22.54 | 0
2025-03-04 | 0.2 | 17.8 | 0 | 2024-03-04 | 3.9 | 14.1 | 0 | 2023-03-04 | -1.1 | 19.1 | 0 | 2022-03-04 | -5 | 23 | 0 | 2021-03-04 | -9.7 | 27.7 | 0 | 2020-03-04 | 1.5 | 16.5 | 0 | 2019-03-04 | -9.6 | 27.6 | 0 | 2018-03-04 | -1.5 | 19.5 | 0 | 2017-03-04 | -15.2 | 33.2 | 0 | 2016-03-04 | -9.3 | 27.3 | 0 | 22.58 | 0
2025-03-04 | 0.1 | 17.9 | 0 | 2024-03-04 | 3.3 | 14.7 | 0 | 2023-03-04 | -1.3 | 19.3 | 0 | 2022-03-04 | -7.3 | 25.3 | 0 | 2021-03-04 | -10.3 | 28.3 | 0 | 2020-03-04 | 0.5 | 17.5 | 0 | 2019-03-04 | -10.5 | 28.5 | 0 | 2018-03-04 | -2.1 | 20.1 | 0 | 2017-03-04 | -15.2 | 33.2 | 0 | 2016-03-04 | -10.1 | 28.1 | 0 | 23.29 | 0
2025-03-04 | 0.2 | 17.8 | 0 | 2024-03-04 | 2.2 | 15.8 | 0 | 2023-03-04 | -1.4 | 19.4 | 0 | 2022-03-04 | -9.7 | 27.7 | 0 | 2021-03-04 | -11.2 | 29.2 | 0 | 2020-03-04 | -0.2 | 18.2 | 0 | 2019-03-04 | -11.7 | 29.7 | 0 | 2018-03-04 | -2.5 | 20.5 | 0 | 2017-03-04 | -15.7 | 33.7 | 0 | 2016-03-04 | -10.4 | 28.4 | 0 | 24.04 | 0
2025-03-05 | 0.2 | 17.8 | 0 | 2024-03-05 | 1.8 | 16.2 | 0 | 2023-03-05 | -1.8 | 19.8 | 0 | 2022-03-05 | -9.2 | 27.2 | 0 | 2021-03-05 | -12.2 | 30.2 | 0 | 2020-03-05 | -0.2 | 18.2 | 0 | 2019-03-05 | -13.2 | 31.2 | 0 | 2018-03-05 | -3 | 21 | 0 | 2017-03-05 | -16.3 | 34.3 | 0 | 2016-03-05 | -11.1 | 29.1 | 0 | 24.5 | 0
2025-03-05 | 0.1 | 17.9 | 0 | 2024-03-05 | 1.1 | 16.9 | 0 | 2023-03-05 | -1.4 | 19.4 | 0 | 2022-03-05 | -9.5 | 27.5 | 0 | 2021-03-05 | -12.7 | 30.7 | 0 | 2020-03-05 | -0.6 | 18.6 | 0 | 2019-03-05 | -14.4 | 32.4 | 0 | 2018-03-05 | -3.4 | 21.4 | 0 | 2017-03-05 | -16.7 | 34.7 | 0 | 2016-03-05 | -13.2 | 31.2 | 0 | 25.07 | 0
2025-03-05 | 0.1 | 17.9 | 0 | 2024-03-05 | 1.1 | 16.9 | 0 | 2023-03-05 | -1.6 | 19.6 | 0 | 2022-03-05 | -11.9 | 29.9 | 0 | 2021-03-05 | -13 | 31 | 0 | 2020-03-05 | -0.6 | 18.6 | 0 | 2019-03-05 | -15.8 | 33.8 | 0 | 2018-03-05 | -3.7 | 21.7 | 0 | 2017-03-05 | -17.5 | 35.5 | 0 | 2016-03-05 | -14 | 32 | 0 | 25.69 | 0
2025-03-05 | 0 | 18 | 0 | 2024-03-05 | 0.6 | 17.4 | 0 | 2023-03-05 | -1.6 | 19.6 | 0 | 2022-03-05 | -12.9 | 30.9 | 0 | 2021-03-05 | -13.5 | 31.5 | 0 | 2020-03-05 | -0.7 | 18.7 | 0 | 2019-03-05 | -16.2 | 34.2 | 0 | 2018-03-05 | -3.9 | 21.9 | 0 | 2017-03-05 | -17 | 35 | 0 | 2016-03-05 | -14.2 | 32.2 | 0 | 25.94 | 0
2025-03-05 | 0.1 | 17.9 | 0 | 2024-03-05 | 0.9 | 17.1 | 0 | 2023-03-05 | -1.8 | 19.8 | 0 | 2022-03-05 | -11 | 29 | 0 | 2021-03-05 | -13.9 | 31.9 | 0 | 2020-03-05 | -0.8 | 18.8 | 0 | 2019-03-05 | -16.4 | 34.4 | 0 | 2018-03-05 | -4.1 | 22.1 | 0 | 2017-03-05 | -17.6 | 35.6 | 0 | 2016-03-05 | -14.2 | 32.2 | 0 | 25.88 | 0
2025-03-05 | 0.3 | 17.7 | 0 | 2024-03-05 | 1.3 | 16.7 | 0 | 2023-03-05 | -1.9 | 19.9 | 0 | 2022-03-05 | -13.2 | 31.2 | 0 | 2021-03-05 | -14.4 | 32.4 | 0 | 2020-03-05 | -1.6 | 19.6 | 0 | 2019-03-05 | -17 | 35 | 0 | 2018-03-05 | -4.1 | 22.1 | 0 | 2017-03-05 | -17.9 | 35.9 | 0 | 2016-03-05 | -15.1 | 33.1 | 0 | 26.36 | 0
2025-03-05 | 0.3 | 17.7 | 0 | 2024-03-05 | -0.2 | 18.2 | 0 | 2023-03-05 | -3.2 | 21.2 | 0 | 2022-03-05 | -12.6 | 30.6 | 0 | 2021-03-05 | -15 | 33 | 0 | 2020-03-05 | -2.2 | 20.2 | 0 | 2019-03-05 | -18.1 | 36.1 | 0 | 2018-03-05 | -4.3 | 22.3 | 0 | 2017-03-05 | -20.2 | 38.2 | 0 | 2016-03-05 | -16.9 | 34.9 | 0 | 27.24 | 0
2025-03-05 | 0.4 | 17.6 | 0 | 2024-03-05 | 0 | 18 | 0 | 2023-03-05 | -2.4 | 20.4 | 0 | 2022-03-05 | -13.8 | 31.8 | 0 | 2021-03-05 | -15.4 | 33.4 | 0 | 2020-03-05 | -2.7 | 20.7 | 0 | 2019-03-05 | -18.5 | 36.5 | 0 | 2018-03-05 | -4.2 | 22.2 | 0 | 2017-03-05 | -20.3 | 38.3 | 0 | 2016-03-05 | -16.2 | 34.2 | 0 | 27.31 | 0
2025-03-05 | 0.6 | 17.4 | 0 | 2024-03-05 | 4.5 | 13.5 | 0 | 2023-03-05 | -2.7 | 20.7 | 0 | 2022-03-05 | -12.3 | 30.3 | 0 | 2021-03-05 | -15 | 33 | 0 | 2020-03-05 | -1.1 | 19.1 | 0 | 2019-03-05 | -16.4 | 34.4 | 0 | 2018-03-05 | -4.4 | 22.4 | 0 | 2017-03-05 | -18.6 | 36.6 | 0 | 2016-03-05 | -14.2 | 32.2 | 0 | 25.96 | 0
2025-03-05 | 0.9 | 17.1 | 0 | 2024-03-05 | 7.8 | 10.2 | 0 | 2023-03-05 | -1.6 | 19.6 | 0 | 2022-03-05 | -10.5 | 28.5 | 0 | 2021-03-05 | -14 | 32 | 0 | 2020-03-05 | 0 | 18 | 0 | 2019-03-05 | -14.9 | 32.9 | 0 | 2018-03-05 | -4 | 22 | 0 | 2017-03-05 | -16.4 | 34.4 | 0 | 2016-03-05 | -11.3 | 29.3 | 0 | 24.4 | 0
2025-03-05 | 1.3 | 16.7 | 0 | 2024-03-05 | 12.5 | 5.5 | 0 | 2023-03-05 | 0.2 | 17.8 | 0 | 2022-03-05 | -8.2 | 26.2 | 0 | 2021-03-05 | -12.3 | 30.3 | 0 | 2020-03-05 | 1 | 17 | 0 | 2019-03-05 | -13.6 | 31.6 | 0 | 2018-03-05 | -2.2 | 20.2 | 0 | 2017-03-05 | -15.4 | 33.4 | 0 | 2016-03-05 | -8.7 | 26.7 | 0 | 22.54 | 0
2025-03-05 | 1.7 | 16.3 | 0 | 2024-03-05 | 13.9 | 4.1 | 0 | 2023-03-05 | 1.4 | 16.6 | 0 | 2022-03-05 | -4.9 | 22.9 | 0 | 2021-03-05 | -11 | 29 | 0 | 2020-03-05 | 1.6 | 16.4 | 0 | 2019-03-05 | -12.7 | 30.7 | 0 | 2018-03-05 | -0.3 | 18.3 | 0 | 2017-03-05 | -13.7 | 31.7 | 0 | 2016-03-05 | -6.2 | 24.2 | 0 | 21.02 | 0
2025-03-05 | 2.2 | 15.8 | 0 | 2024-03-05 | 14.8 | 3.2 | 0 | 2023-03-05 | 2.5 | 15.5 | 0 | 2022-03-05 | -3.2 | 21.2 | 0 | 2021-03-05 | -8.5 | 26.5 | 0 | 2020-03-05 | 1.4 | 16.6 | 0 | 2019-03-05 | -11 | 29 | 0 | 2018-03-05 | 1.1 | 16.9 | 0 | 2017-03-05 | -11.9 | 29.9 | 0 | 2016-03-05 | -4.3 | 22.3 | 0 | 19.69 | 0
2025-03-05 | 2.5 | 15.5 | 0 | 2024-03-05 | 16.1 | 1.9 | 0 | 2023-03-05 | 3.5 | 14.5 | 0 | 2022-03-05 | -2.3 | 20.3 | 0 | 2021-03-05 | -7.2 | 25.2 | 0 | 2020-03-05 | 1.5 | 16.5 | 0 | 2019-03-05 | -9.7 | 27.7 | 0 | 2018-03-05 | 1.3 | 16.7 | 0 | 2017-03-05 | -10.5 | 28.5 | 0 | 2016-03-05 | -2.8 | 20.8 | 0 | 18.76 | 0
2025-03-05 | 2 | 16 | 0 | 2024-03-05 | 16.5 | 1.5 | 0 | 2023-03-05 | 4.1 | 13.9 | 0 | 2022-03-05 | -1.4 | 19.4 | 0 | 2021-03-05 | -6.6 | 24.6 | 0 | 2020-03-05 | 1.6 | 16.4 | 0 | 2019-03-05 | -8.5 | 26.5 | 0 | 2018-03-05 | 0.6 | 17.4 | 0 | 2017-03-05 | -9.4 | 27.4 | 0 | 2016-03-05 | -1.6 | 19.6 | 0 | 18.27 | 0
2025-03-05 | 1.8 | 16.2 | 0 | 2024-03-05 | 16.6 | 1.4 | 0 | 2023-03-05 | 4.5 | 13.5 | 0 | 2022-03-05 | -0.8 | 18.8 | 0 | 2021-03-05 | -6.8 | 24.8 | 0 | 2020-03-05 | 1.9 | 16.1 | 0 | 2019-03-05 | -8.3 | 26.3 | 0 | 2018-03-05 | 0.8 | 17.2 | 0 | 2017-03-05 | -8.6 | 26.6 | 0 | 2016-03-05 | -1.1 | 19.1 | 0 | 18 | 0
2025-03-05 | 1.6 | 16.4 | 0 | 2024-03-05 | 16.9 | 1.1 | 0 | 2023-03-05 | 4.3 | 13.7 | 0 | 2022-03-05 | -1.2 | 19.2 | 0 | 2021-03-05 | -6 | 24 | 0 | 2020-03-05 | 2.3 | 15.7 | 0 | 2019-03-05 | -9 | 27 | 0 | 2018-03-05 | 1.1 | 16.9 | 0 | 2017-03-05 | -8 | 26 | 0 | 2016-03-05 | -0.9 | 18.9 | 0 | 17.89 | 0
2025-03-05 | 1.7 | 16.3 | 0 | 2024-03-05 | 15.9 | 2.1 | 0 | 2023-03-05 | 4.3 | 13.7 | 0 | 2022-03-05 | -1.6 | 19.6 | 0 | 2021-03-05 | -6.7 | 24.7 | 0 | 2020-03-05 | 2 | 16 | 0 | 2019-03-05 | -8.8 | 26.8 | 0 | 2018-03-05 | 0.8 | 17.2 | 0 | 2017-03-05 | -7.6 | 25.6 | 0 | 2016-03-05 | -1.5 | 19.5 | 0 | 18.15 | 0
2025-03-05 | 1.6 | 16.4 | 0 | 2024-03-05 | 13.8 | 4.2 | 0 | 2023-03-05 | 3.4 | 14.6 | 0 | 2022-03-05 | -2 | 20 | 0 | 2021-03-05 | -8 | 26 | 0 | 2020-03-05 | 1.7 | 16.3 | 0 | 2019-03-05 | -9.2 | 27.2 | 0 | 2018-03-05 | 0.3 | 17.7 | 0 | 2017-03-05 | -8.4 | 26.4 | 0 | 2016-03-05 | -2.4 | 20.4 | 0 | 18.92 | 0
2025-03-05 | 1.6 | 16.4 | 0 | 2024-03-05 | 13.2 | 4.8 | 0 | 2023-03-05 | 2.3 | 15.7 | 0 | 2022-03-05 | -1.7 | 19.7 | 0 | 2021-03-05 | -9.6 | 27.6 | 0 | 2020-03-05 | 1.1 | 16.9 | 0 | 2019-03-05 | -10 | 28 | 0 | 2018-03-05 | -0.1 | 18.1 | 0 | 2017-03-05 | -8.8 | 26.8 | 0 | 2016-03-05 | -3.5 | 21.5 | 0 | 19.55 | 0
2025-03-05 | 1.7 | 16.3 | 0 | 2024-03-05 | 10 | 8 | 0 | 2023-03-05 | 1.6 | 16.4 | 0 | 2022-03-05 | -2.4 | 20.4 | 0 | 2021-03-05 | -10.5 | 28.5 | 0 | 2020-03-05 | 0.1 | 17.9 | 0 | 2019-03-05 | -11.2 | 29.2 | 0 | 2018-03-05 | -0.1 | 18.1 | 0 | 2017-03-05 | -9.4 | 27.4 | 0 | 2016-03-05 | -3.9 | 21.9 | 0 | 20.41 | 0
2025-03-05 | 2.3 | 15.7 | 0 | 2024-03-05 | 9.2 | 8.8 | 0 | 2023-03-05 | 0.8 | 17.2 | 0 | 2022-03-05 | -2.7 | 20.7 | 0 | 2021-03-05 | -9.8 | 27.8 | 0 | 2020-03-05 | 0 | 18 | 0 | 2019-03-05 | -12.5 | 30.5 | 0 | 2018-03-05 | -0.7 | 18.7 | 0 | 2017-03-05 | -10 | 28 | 0 | 2016-03-05 | -4.1 | 22.1 | 0 | 20.75 | 0
2025-03-05 | 2.4 | 15.6 | 0 | 2024-03-05 | 8.4 | 9.6 | 0 | 2023-03-05 | 1.7 | 16.3 | 0 | 2022-03-05 | -2.8 | 20.8 | 0 | 2021-03-05 | -10.1 | 28.1 | 0 | 2020-03-05 | 0 | 18 | 0 | 2019-03-05 | -14.4 | 32.4 | 0 | 2018-03-05 | -0.9 | 18.9 | 0 | 2017-03-05 | -10.6 | 28.6 | 0 | 2016-03-05 | -4.4 | 22.4 | 0 | 21.07 | 0
2025-03-05 | 1.8 | 16.2 | 0 | 2024-03-05 | 7.6 | 10.4 | 0 | 2023-03-05 | 0.4 | 17.6 | 0 | 2022-03-05 | -2.6 | 20.6 | 0 | 2021-03-05 | -10.5 | 28.5 | 0 | 2020-03-05 | -0.2 | 18.2 | 0 | 2019-03-05 | -12.9 | 30.9 | 0 | 2018-03-05 | -1 | 19 | 0 | 2017-03-05 | -10.5 | 28.5 | 0 | 2016-03-05 | -4.9 | 22.9 | 0 | 21.28 | 0
2025-03-06 | 2.6 | 15.4 | 0 | 2024-03-06 | 6.5 | 11.5 | 0 | 2023-03-06 | -1.6 | 19.6 | 0 | 2022-03-06 | -2.3 | 20.3 | 0 | 2021-03-06 | -10.5 | 28.5 | 0 | 2020-03-06 | -0.5 | 18.5 | 0 | 2019-03-06 | -14.7 | 32.7 | 0 | 2018-03-06 | -1.1 | 19.1 | 0 | 2017-03-06 | -10.9 | 28.9 | 0 | 2016-03-06 | -5.8 | 23.8 | 0 | 21.83 | 0
2025-03-06 | 2.5 | 15.5 | 0 | 2024-03-06 | 5.7 | 12.3 | 0 | 2023-03-06 | -3 | 21 | 0 | 2022-03-06 | -2 | 20 | 0 | 2021-03-06 | -10.4 | 28.4 | 0 | 2020-03-06 | -1.1 | 19.1 | 0 | 2019-03-06 | -15.2 | 33.2 | 0 | 2018-03-06 | -1.2 | 19.2 | 0 | 2017-03-06 | -10.9 | 28.9 | 0 | 2016-03-06 | -6.3 | 24.3 | 0 | 22.19 | 0
2025-03-06 | 3.4 | 14.6 | 0 | 2024-03-06 | 4.9 | 13.1 | 0 | 2023-03-06 | -1.6 | 19.6 | 0 | 2022-03-06 | -1.7 | 19.7 | 0 | 2021-03-06 | -10.5 | 28.5 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -14.8 | 32.8 | 0 | 2018-03-06 | -1.3 | 19.3 | 0 | 2017-03-06 | -10.6 | 28.6 | 0 | 2016-03-06 | -7.7 | 25.7 | 0 | 22.11 | 0
2025-03-06 | 4.2 | 13.8 | 0 | 2024-03-06 | 4.2 | 13.8 | 0 | 2023-03-06 | -2.2 | 20.2 | 0 | 2022-03-06 | -2.6 | 20.6 | 0 | 2021-03-06 | -10.6 | 28.6 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -15.9 | 33.9 | 0 | 2018-03-06 | -1.4 | 19.4 | 0 | 2017-03-06 | -10.8 | 28.8 | 0 | 2016-03-06 | -8.4 | 26.4 | 0 | 22.47 | 0
2025-03-06 | 3.9 | 14.1 | 0 | 2024-03-06 | 4 | 14 | 0 | 2023-03-06 | -1.8 | 19.8 | 0 | 2022-03-06 | -2.4 | 20.4 | 0 | 2021-03-06 | -10.6 | 28.6 | 0 | 2020-03-06 | -1.4 | 19.4 | 0 | 2019-03-06 | -17.3 | 35.3 | 0 | 2018-03-06 | -1.5 | 19.5 | 0 | 2017-03-06 | -10.7 | 28.7 | 0 | 2016-03-06 | -10.8 | 28.8 | 0 | 22.86 | 0
2025-03-06 | 4.8 | 13.2 | 0 | 2024-03-06 | 4.1 | 13.9 | 0 | 2023-03-06 | -3 | 21 | 0 | 2022-03-06 | -2.8 | 20.8 | 0 | 2021-03-06 | -10.5 | 28.5 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -16.8 | 34.8 | 0 | 2018-03-06 | -1.4 | 19.4 | 0 | 2017-03-06 | -11.5 | 29.5 | 0 | 2016-03-06 | -10 | 28 | 0 | 22.83 | 0
2025-03-06 | 3.2 | 14.8 | 0 | 2024-03-06 | 4 | 14 | 0 | 2023-03-06 | -3.6 | 21.6 | 0 | 2022-03-06 | -2.5 | 20.5 | 0 | 2021-03-06 | -10.4 | 28.4 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -19.1 | 37.1 | 0 | 2018-03-06 | -1.4 | 19.4 | 0 | 2017-03-06 | -11.2 | 29.2 | 0 | 2016-03-06 | -9.8 | 27.8 | 0 | 23.2 | 0
2025-03-06 | 2.3 | 15.7 | 0 | 2024-03-06 | 3.9 | 14.1 | 0 | 2023-03-06 | -4.3 | 22.3 | 0 | 2022-03-06 | -2.4 | 20.4 | 0 | 2021-03-06 | -10.8 | 28.8 | 0 | 2020-03-06 | -1.3 | 19.3 | 0 | 2019-03-06 | -18.8 | 36.8 | 0 | 2018-03-06 | -1.6 | 19.6 | 0 | 2017-03-06 | -10.3 | 28.3 | 0 | 2016-03-06 | -11.4 | 29.4 | 0 | 23.47 | 0
2025-03-06 | 2.3 | 15.7 | 0 | 2024-03-06 | 4.1 | 13.9 | 0 | 2023-03-06 | -3.8 | 21.8 | 0 | 2022-03-06 | -1.8 | 19.8 | 0 | 2021-03-06 | -11.1 | 29.1 | 0 | 2020-03-06 | -1.3 | 19.3 | 0 | 2019-03-06 | -18.9 | 36.9 | 0 | 2018-03-06 | -1.2 | 19.2 | 0 | 2017-03-06 | -9.4 | 27.4 | 0 | 2016-03-06 | -9.1 | 27.1 | 0 | 23.02 | 0
2025-03-06 | 2.8 | 15.2 | 0 | 2024-03-06 | 4.4 | 13.6 | 0 | 2023-03-06 | -2.4 | 20.4 | 0 | 2022-03-06 | -0.7 | 18.7 | 0 | 2021-03-06 | -10.6 | 28.6 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -15.2 | 33.2 | 0 | 2018-03-06 | -0.9 | 18.9 | 0 | 2017-03-06 | -7.8 | 25.8 | 0 | 2016-03-06 | -6.1 | 24.1 | 0 | 21.77 | 0
2025-03-06 | 2.9 | 15.1 | 0 | 2024-03-06 | 4.6 | 13.4 | 0 | 2023-03-06 | -1.3 | 19.3 | 0 | 2022-03-06 | 1.3 | 16.7 | 0 | 2021-03-06 | -9.4 | 27.4 | 0 | 2020-03-06 | -1 | 19 | 0 | 2019-03-06 | -14.6 | 32.6 | 0 | 2018-03-06 | -0.6 | 18.6 | 0 | 2017-03-06 | -6.5 | 24.5 | 0 | 2016-03-06 | -3.2 | 21.2 | 0 | 20.78 | 0
2025-03-06 | 3 | 15 | 0 | 2024-03-06 | 5.1 | 12.9 | 0 | 2023-03-06 | 0.1 | 17.9 | 0 | 2022-03-06 | 6 | 12 | 0 | 2021-03-06 | -8.6 | 26.6 | 0 | 2020-03-06 | -0.6 | 18.6 | 0 | 2019-03-06 | -12.7 | 30.7 | 0 | 2018-03-06 | -0.1 | 18.1 | 0 | 2017-03-06 | -5.4 | 23.4 | 0 | 2016-03-06 | -1.7 | 19.7 | 0 | 19.49 | 0
2025-03-06 | 2.6 | 15.4 | 0 | 2024-03-06 | 5.4 | 12.6 | 0 | 2023-03-06 | 1 | 17 | 0 | 2022-03-06 | 9.2 | 8.8 | 0 | 2021-03-06 | -8 | 26 | 0 | 2020-03-06 | -0.4 | 18.4 | 0 | 2019-03-06 | -11.4 | 29.4 | 0 | 2018-03-06 | 0.5 | 17.5 | 0 | 2017-03-06 | -4.6 | 22.6 | 0 | 2016-03-06 | 0.2 | 17.8 | 0 | 18.55 | 0
2025-03-06 | 2.8 | 15.2 | 0 | 2024-03-06 | 5.6 | 12.4 | 0 | 2023-03-06 | 1.4 | 16.6 | 0 | 2022-03-06 | 12.5 | 5.5 | 0 | 2021-03-06 | -7.9 | 25.9 | 0 | 2020-03-06 | -0.4 | 18.4 | 0 | 2019-03-06 | -10.8 | 28.8 | 0 | 2018-03-06 | -0.3 | 18.3 | 0 | 2017-03-06 | -3.2 | 21.2 | 0 | 2016-03-06 | 1.6 | 16.4 | 0 | 17.87 | 0
2025-03-06 | 2.7 | 15.3 | 0 | 2024-03-06 | 5.7 | 12.3 | 0 | 2023-03-06 | 2.3 | 15.7 | 0 | 2022-03-06 | 12.9 | 5.1 | 0 | 2021-03-06 | -7.5 | 25.5 | 0 | 2020-03-06 | -0.3 | 18.3 | 0 | 2019-03-06 | -10.5 | 28.5 | 0 | 2018-03-06 | -0.4 | 18.4 | 0 | 2017-03-06 | -3.2 | 21.2 | 0 | 2016-03-06 | 2.4 | 15.6 | 0 | 17.59 | 0
2025-03-06 | 2.1 | 15.9 | 0 | 2024-03-06 | 5.4 | 12.6 | 0 | 2023-03-06 | 2.9 | 15.1 | 0 | 2022-03-06 | 12.4 | 5.6 | 0 | 2021-03-06 | -7.4 | 25.4 | 0 | 2020-03-06 | -0.3 | 18.3 | 0 | 2019-03-06 | -10.5 | 28.5 | 0 | 2018-03-06 | 0 | 18 | 0 | 2017-03-06 | -2.6 | 20.6 | 0 | 2016-03-06 | 2.8 | 15.2 | 0 | 17.52 | 0
2025-03-06 | 0 | 18 | 0 | 2024-03-06 | 5.3 | 12.7 | 0 | 2023-03-06 | 3.5 | 14.5 | 0 | 2022-03-06 | 11.4 | 6.6 | 0 | 2021-03-06 | -7.5 | 25.5 | 0 | 2020-03-06 | -0.7 | 18.7 | 0 | 2019-03-06 | -10.3 | 28.3 | 0 | 2018-03-06 | 0.2 | 17.8 | 0 | 2017-03-06 | -2.2 | 20.2 | 0 | 2016-03-06 | 2.9 | 15.1 | 0 | 17.74 | 0
2025-03-06 | -1.8 | 19.8 | 0 | 2024-03-06 | 5.2 | 12.8 | 0 | 2023-03-06 | 3.8 | 14.2 | 0 | 2022-03-06 | 10.6 | 7.4 | 0 | 2021-03-06 | -7.7 | 25.7 | 0 | 2020-03-06 | -1.2 | 19.2 | 0 | 2019-03-06 | -10.7 | 28.7 | 0 | 2018-03-06 | -0.6 | 18.6 | 0 | 2017-03-06 | -2.5 | 20.5 | 0 | 2016-03-06 | 1.9 | 16.1 | 0 | 18.3 | 0
2025-03-06 | -2.5 | 20.5 | 0 | 2024-03-06 | 4.8 | 13.2 | 0 | 2023-03-06 | 2.4 | 15.6 | 0 | 2022-03-06 | 8.7 | 9.3 | 0 | 2021-03-06 | -8.5 | 26.5 | 0 | 2020-03-06 | -1.4 | 19.4 | 0 | 2019-03-06 | -11.8 | 29.8 | 0 | 2018-03-06 | -1.3 | 19.3 | 0 | 2017-03-06 | -2.8 | 20.8 | 0 | 2016-03-06 | 0.5 | 17.5 | 0 | 19.19 | 0
2025-03-06 | -3.9 | 21.9 | 0 | 2024-03-06 | 4.4 | 13.6 | 0 | 2023-03-06 | -0.5 | 18.5 | 0 | 2022-03-06 | 6.3 | 11.7 | 0 | 2021-03-06 | -11.4 | 29.4 | 0 | 2020-03-06 | -1.6 | 19.6 | 0 | 2019-03-06 | -12.4 | 30.4 | 0 | 2018-03-06 | -1.4 | 19.4 | 0 | 2017-03-06 | -3.3 | 21.3 | 0 | 2016-03-06 | -0.3 | 18.3 | 0 | 20.41 | 0
2025-03-06 | -6.4 | 24.4 | 0 | 2024-03-06 | 4.3 | 13.7 | 0 | 2023-03-06 | -0.5 | 18.5 | 0 | 2022-03-06 | 5.3 | 12.7 | 0 | 2021-03-06 | -10.6 | 28.6 | 0 | 2020-03-06 | -2.1 | 20.1 | 0 | 2019-03-06 | -14.1 | 32.1 | 0 | 2018-03-06 | -1.2 | 19.2 | 0 | 2017-03-06 | -3.4 | 21.4 | 0 | 2016-03-06 | -0.9 | 18.9 | 0 | 20.96 | 0
2025-03-06 | -7.3 | 25.3 | 0 | 2024-03-06 | 4.3 | 13.7 | 0 | 2023-03-06 | -0.6 | 18.6 | 0 | 2022-03-06 | 4.7 | 13.3 | 0 | 2021-03-06 | -9.8 | 27.8 | 0 | 2020-03-06 | -2.9 | 20.9 | 0 | 2019-03-06 | -14.5 | 32.5 | 0 | 2018-03-06 | -1.4 | 19.4 | 0 | 2017-03-06 | -3.3 | 21.3 | 0 | 2016-03-06 | -1.1 | 19.1 | 0 | 21.19 | 0
2025-03-06 | -7.9 | 25.9 | 0 | 2024-03-06 | 4.4 | 13.6 | 0 | 2023-03-06 | -1 | 19 | 0 | 2022-03-06 | 4.1 | 13.9 | 0 | 2021-03-06 | -9.7 | 27.7 | 0 | 2020-03-06 | -3.8 | 21.8 | 0 | 2019-03-06 | -14.9 | 32.9 | 0 | 2018-03-06 | -1 | 19 | 0 | 2017-03-06 | -2.7 | 20.7 | 0 | 2016-03-06 | -1.2 | 19.2 | 0 | 21.37 | 0
2025-03-06 | -8.3 | 26.3 | 0 | 2024-03-06 | 4.3 | 13.7 | 0 | 2023-03-06 | -1.7 | 19.7 | 0 | 2022-03-06 | 3.9 | 14.1 | 0 | 2021-03-06 | -9.5 | 27.5 | 0 | 2020-03-06 | -4.8 | 22.8 | 0 | 2019-03-06 | -15.3 | 33.3 | 0 | 2018-03-06 | -1 | 19 | 0 | 2017-03-06 | -2.6 | 20.6 | 0 | 2016-03-06 | -2.2 | 20.2 | 0 | 21.72 | 0
2025-03-07 | -8.4 | 26.4 | 0 | 2024-03-07 | 4 | 14 | 0 | 2023-03-07 | -2.2 | 20.2 | 0 | 2022-03-07 | 3.5 | 14.5 | 0 | 2021-03-07 | -9.7 | 27.7 | 0 | 2020-03-07 | -5.5 | 23.5 | 0 | 2019-03-07 | -15.4 | 33.4 | 0 | 2018-03-07 | -1.1 | 19.1 | 0 | 2017-03-07 | -2.5 | 20.5 | 0 | 2016-03-07 | -2 | 20 | 0 | 21.93 | 0
2025-03-07 | -8.4 | 26.4 | 0 | 2024-03-07 | 3.5 | 14.5 | 0 | 2023-03-07 | -2.4 | 20.4 | 0 | 2022-03-07 | 3.1 | 14.9 | 0 | 2021-03-07 | -10 | 28 | 0 | 2020-03-07 | -6.2 | 24.2 | 0 | 2019-03-07 | -17.1 | 35.1 | 0 | 2018-03-07 | -1.3 | 19.3 | 0 | 2017-03-07 | -2.5 | 20.5 | 0 | 2016-03-07 | -1.8 | 19.8 | 0 | 22.31 | 0
2025-03-07 | -8.2 | 26.2 | 0 | 2024-03-07 | 3.4 | 14.6 | 0 | 2023-03-07 | -3.6 | 21.6 | 0 | 2022-03-07 | 3 | 15 | 0 | 2021-03-07 | -10.5 | 28.5 | 0 | 2020-03-07 | -6.5 | 24.5 | 0 | 2019-03-07 | -17.1 | 35.1 | 0 | 2018-03-07 | -1.2 | 19.2 | 0 | 2017-03-07 | -2.4 | 20.4 | 0 | 2016-03-07 | -1.9 | 19.9 | 0 | 22.5 | 0
2025-03-07 | -7.9 | 25.9 | 0 | 2024-03-07 | 2.9 | 15.1 | 0 | 2023-03-07 | -4.3 | 22.3 | 0 | 2022-03-07 | 1.4 | 16.6 | 0 | 2021-03-07 | -11.7 | 29.7 | 0 | 2020-03-07 | -7.3 | 25.3 | 0 | 2019-03-07 | -19.2 | 37.2 | 0 | 2018-03-07 | -1.6 | 19.6 | 0 | 2017-03-07 | -2.5 | 20.5 | 0 | 2016-03-07 | -1.3 | 19.3 | 0 | 23.15 | 0
2025-03-07 | -7.8 | 25.8 | 0 | 2024-03-07 | 2.4 | 15.6 | 0 | 2023-03-07 | -5 | 23 | 0 | 2022-03-07 | 1.4 | 16.6 | 0 | 2021-03-07 | -13.7 | 31.7 | 0 | 2020-03-07 | -8.1 | 26.1 | 0 | 2019-03-07 | -18.8 | 36.8 | 0 | 2018-03-07 | -1.5 | 19.5 | 0 | 2017-03-07 | -2.6 | 20.6 | 0 | 2016-03-07 | -1.6 | 19.6 | 0 | 23.53 | 0
2025-03-07 | -8.1 | 26.1 | 0 | 2024-03-07 | 1.7 | 16.3 | 0 | 2023-03-07 | -5.7 | 23.7 | 0 | 2022-03-07 | 1.1 | 16.9 | 0 | 2021-03-07 | -13.8 | 31.8 | 0 | 2020-03-07 | -8.8 | 26.8 | 0 | 2019-03-07 | -18.7 | 36.7 | 0 | 2018-03-07 | -2.1 | 20.1 | 0 | 2017-03-07 | -2 | 20 | 0 | 2016-03-07 | 1 | 17 | 0 | 23.54 | 0
2025-03-07 | -8.4 | 26.4 | 0 | 2024-03-07 | 1.3 | 16.7 | 0 | 2023-03-07 | -6.4 | 24.4 | 0 | 2022-03-07 | 0.7 | 17.3 | 0 | 2021-03-07 | -16.3 | 34.3 | 0 | 2020-03-07 | -9.4 | 27.4 | 0 | 2019-03-07 | -21.1 | 39.1 | 0 | 2018-03-07 | -2.3 | 20.3 | 0 | 2017-03-07 | -1.8 | 19.8 | 0 | 2016-03-07 | 1.1 | 16.9 | 0 | 24.26 | 0
2025-03-07 | -7.2 | 25.2 | 0 | 2024-03-07 | 0.8 | 17.2 | 0 | 2023-03-07 | -6.8 | 24.8 | 0 | 2022-03-07 | 0.6 | 17.4 | 0 | 2021-03-07 | -16.4 | 34.4 | 0 | 2020-03-07 | -11.7 | 29.7 | 0 | 2019-03-07 | -21 | 39 | 0 | 2018-03-07 | -2.1 | 20.1 | 0 | 2017-03-07 | -1.4 | 19.4 | 0 | 2016-03-07 | 0.9 | 17.1 | 0 | 24.43 | 0
2025-03-07 | -5.9 | 23.9 | 0 | 2024-03-07 | 1.8 | 16.2 | 0 | 2023-03-07 | -6.2 | 24.2 | 0 | 2022-03-07 | 0.6 | 17.4 | 0 | 2021-03-07 | -13.7 | 31.7 | 0 | 2020-03-07 | -9 | 27 | 0 | 2019-03-07 | -18.8 | 36.8 | 0 | 2018-03-07 | -2 | 20 | 0 | 2017-03-07 | -1 | 19 | 0 | 2016-03-07 | 1 | 17 | 0 | 23.32 | 0
2025-03-07 | -4.5 | 22.5 | 0 | 2024-03-07 | 3.5 | 14.5 | 0 | 2023-03-07 | -5.8 | 23.8 | 0 | 2022-03-07 | 0.6 | 17.4 | 0 | 2021-03-07 | -11.7 | 29.7 | 0 | 2020-03-07 | -8.2 | 26.2 | 0 | 2019-03-07 | -15.8 | 33.8 | 0 | 2018-03-07 | -2 | 20 | 0 | 2017-03-07 | -0.6 | 18.6 | 0 | 2016-03-07 | 1.2 | 16.8 | 0 | 22.33 | 0
2025-03-07 | -3.8 | 21.8 | 0 | 2024-03-07 | 5.1 | 12.9 | 0 | 2023-03-07 | -5.7 | 23.7 | 0 | 2022-03-07 | -0.4 | 18.4 | 0 | 2021-03-07 | -10.8 | 28.8 | 0 | 2020-03-07 | -6.5 | 24.5 | 0 | 2019-03-07 | -13.7 | 31.7 | 0 | 2018-03-07 | -1.9 | 19.9 | 0 | 2017-03-07 | -0.3 | 18.3 | 0 | 2016-03-07 | 1.8 | 16.2 | 0 | 21.62 | 0
2025-03-07 | -2.8 | 20.8 | 0 | 2024-03-07 | 6.8 | 11.2 | 0 | 2023-03-07 | -5.5 | 23.5 | 0 | 2022-03-07 | -0.4 | 18.4 | 0 | 2021-03-07 | -9.4 | 27.4 | 0 | 2020-03-07 | -5.8 | 23.8 | 0 | 2019-03-07 | -11.8 | 29.8 | 0 | 2018-03-07 | -1.2 | 19.2 | 0 | 2017-03-07 | 0.2 | 17.8 | 0 | 2016-03-07 | 2.4 | 15.6 | 0 | 20.75 | 0
2025-03-07 | -1.9 | 19.9 | 0 | 2024-03-07 | 8.2 | 9.8 | 0 | 2023-03-07 | -4.8 | 22.8 | 0 | 2022-03-07 | -0.2 | 18.2 | 0 | 2021-03-07 | -8.3 | 26.3 | 0 | 2020-03-07 | -4.6 | 22.6 | 0 | 2019-03-07 | -10.6 | 28.6 | 0 | 2018-03-07 | -1 | 19 | 0 | 2017-03-07 | 0.4 | 17.6 | 0 | 2016-03-07 | 3.4 | 14.6 | 0 | 19.94 | 0
2025-03-07 | -1.3 | 19.3 | 0 | 2024-03-07 | 9.4 | 8.6 | 0 | 2023-03-07 | -4.4 | 22.4 | 0 | 2022-03-07 | -0.1 | 18.1 | 0 | 2021-03-07 | -7.4 | 25.4 | 0 | 2020-03-07 | -4.2 | 22.2 | 0 | 2019-03-07 | -9.4 | 27.4 | 0 | 2018-03-07 | -0.6 | 18.6 | 0 | 2017-03-07 | 0.9 | 17.1 | 0 | 2016-03-07 | 3.9 | 14.1 | 0 | 19.32 | 0
2025-03-07 | -1.2 | 19.2 | 0 | 2024-03-07 | 10.3 | 7.7 | 0 | 2023-03-07 | -4 | 22 | 0 | 2022-03-07 | -0.1 | 18.1 | 0 | 2021-03-07 | -7.2 | 25.2 | 0 | 2020-03-07 | -3.3 | 21.3 | 0 | 2019-03-07 | -8.8 | 26.8 | 0 | 2018-03-07 | -0.2 | 18.2 | 0 | 2017-03-07 | 1.2 | 16.8 | 0 | 2016-03-07 | 4.5 | 13.5 | 0 | 18.88 | 0
2025-03-07 | -1.3 | 19.3 | 0 | 2024-03-07 | 10.6 | 7.4 | 0 | 2023-03-07 | -3.8 | 21.8 | 0 | 2022-03-07 | -0.3 | 18.3 | 0 | 2021-03-07 | -6.6 | 24.6 | 0 | 2020-03-07 | -2.5 | 20.5 | 0 | 2019-03-07 | -8.3 | 26.3 | 0 | 2018-03-07 | -0.4 | 18.4 | 0 | 2017-03-07 | 1.7 | 16.3 | 0 | 2016-03-07 | 4.7 | 13.3 | 0 | 18.62 | 0
2025-03-07 | -1.7 | 19.7 | 0 | 2024-03-07 | 10.3 | 7.7 | 0 | 2023-03-07 | -3.8 | 21.8 | 0 | 2022-03-07 | -0.2 | 18.2 | 0 | 2021-03-07 | -6.6 | 24.6 | 0 | 2020-03-07 | -1.7 | 19.7 | 0 | 2019-03-07 | -8.2 | 26.2 | 0 | 2018-03-07 | -0.8 | 18.8 | 0 | 2017-03-07 | 1.9 | 16.1 | 0 | 2016-03-07 | 4.8 | 13.2 | 0 | 18.6 | 0
2025-03-07 | -2.4 | 20.4 | 0 | 2024-03-07 | 9.2 | 8.8 | 0 | 2023-03-07 | -3.6 | 21.6 | 0 | 2022-03-07 | -0.4 | 18.4 | 0 | 2021-03-07 | -6.5 | 24.5 | 0 | 2020-03-07 | -1.9 | 19.9 | 0 | 2019-03-07 | -8.5 | 26.5 | 0 | 2018-03-07 | -1.4 | 19.4 | 0 | 2017-03-07 | 2.1 | 15.9 | 0 | 2016-03-07 | 4.9 | 13.1 | 0 | 18.85 | 0
2025-03-07 | -2.6 | 20.6 | 0 | 2024-03-07 | 6.8 | 11.2 | 0 | 2023-03-07 | -3.3 | 21.3 | 0 | 2022-03-07 | -0.4 | 18.4 | 0 | 2021-03-07 | -9.4 | 27.4 | 0 | 2020-03-07 | -2.6 | 20.6 | 0 | 2019-03-07 | -10.2 | 28.2 | 0 | 2018-03-07 | -1.6 | 19.6 | 0 | 2017-03-07 | 2 | 16 | 0 | 2016-03-07 | 4.4 | 13.6 | 0 | 19.69 | 0
2025-03-07 | -3 | 21 | 0 | 2024-03-07 | 6 | 12 | 0 | 2023-03-07 | -3.4 | 21.4 | 0 | 2022-03-07 | -0.2 | 18.2 | 0 | 2021-03-07 | -8.6 | 26.6 | 0 | 2020-03-07 | -2.5 | 20.5 | 0 | 2019-03-07 | -9.8 | 27.8 | 0 | 2018-03-07 | -2 | 20 | 0 | 2017-03-07 | 6.4 | 11.6 | 0 | 2016-03-07 | 4.5 | 13.5 | 0 | 19.26 | 0
2025-03-07 | -3.4 | 21.4 | 0 | 2024-03-07 | 4.8 | 13.2 | 0 | 2023-03-07 | -3.6 | 21.6 | 0 | 2022-03-07 | -0.5 | 18.5 | 0 | 2021-03-07 | -9.7 | 27.7 | 0 | 2020-03-07 | -2.4 | 20.4 | 0 | 2019-03-07 | -11.3 | 29.3 | 0 | 2018-03-07 | -2 | 20 | 0 | 2017-03-07 | 6.8 | 11.2 | 0 | 2016-03-07 | 3.5 | 14.5 | 0 | 19.78 | 0
2025-03-07 | -4.1 | 22.1 | 0 | 2024-03-07 | 3.4 | 14.6 | 0 | 2023-03-07 | -3.9 | 21.9 | 0 | 2022-03-07 | -0.8 | 18.8 | 0 | 2021-03-07 | -10.5 | 28.5 | 0 | 2020-03-07 | -1.8 | 19.8 | 0 | 2019-03-07 | -12.4 | 30.4 | 0 | 2018-03-07 | -2.1 | 20.1 | 0 | 2017-03-07 | 7 | 11 | 0 | 2016-03-07 | 2.6 | 15.4 | 0 | 20.26 | 0
2025-03-07 | -3.4 | 21.4 | 0 | 2024-03-07 | 1.5 | 16.5 | 0 | 2023-03-07 | -4.2 | 22.2 | 0 | 2022-03-07 | -1.4 | 19.4 | 0 | 2021-03-07 | -11.3 | 29.3 | 0 | 2020-03-07 | -1.6 | 19.6 | 0 | 2019-03-07 | -12.2 | 30.2 | 0 | 2018-03-07 | -2.2 | 20.2 | 0 | 2017-03-07 | 6.4 | 11.6 | 0 | 2016-03-07 | 3.2 | 14.8 | 0 | 20.52 | 0
2025-03-07 | -3.7 | 21.7 | 0 | 2024-03-07 | -0.5 | 18.5 | 0 | 2023-03-07 | -4.6 | 22.6 | 0 | 2022-03-07 | -2.9 | 20.9 | 0 | 2021-03-07 | -12.2 | 30.2 | 0 | 2020-03-07 | -1.2 | 19.2 | 0 | 2019-03-07 | -12.4 | 30.4 | 0 | 2018-03-07 | -2.2 | 20.2 | 0 | 2017-03-07 | 6.5 | 11.5 | 0 | 2016-03-07 | 2.9 | 15.1 | 0 | 21.03 | 0
2025-03-08 | -4.2 | 22.2 | 0 | 2024-03-08 | -0.2 | 18.2 | 0 | 2023-03-08 | -4.8 | 22.8 | 0 | 2022-03-08 | -3.4 | 21.4 | 0 | 2021-03-08 | -12.8 | 30.8 | 0 | 2020-03-08 | -1.2 | 19.2 | 0 | 2019-03-08 | -13.6 | 31.6 | 0 | 2018-03-08 | -2.4 | 20.4 | 0 | 2017-03-08 | 5.3 | 12.7 | 0 | 2016-03-08 | 2.2 | 15.8 | 0 | 21.51 | 0
2025-03-08 | -5.4 | 23.4 | 0 | 2024-03-08 | -0.2 | 18.2 | 0 | 2023-03-08 | -5 | 23 | 0 | 2022-03-08 | -4.2 | 22.2 | 0 | 2021-03-08 | -14 | 32 | 0 | 2020-03-08 | -1.1 | 19.1 | 0 | 2019-03-08 | -14.7 | 32.7 | 0 | 2018-03-08 | -2.5 | 20.5 | 0 | 2017-03-08 | 4.4 | 13.6 | 0 | 2016-03-08 | 2.9 | 15.1 | 0 | 21.98 | 0
2025-03-08 | -6.2 | 24.2 | 0 | 2024-03-08 | 0 | 18 | 0 | 2023-03-08 | -5.2 | 23.2 | 0 | 2022-03-08 | -4.7 | 22.7 | 0 | 2021-03-08 | -13.7 | 31.7 | 0 | 2020-03-08 | -0.9 | 18.9 | 0 | 2019-03-08 | -14.7 | 32.7 | 0 | 2018-03-08 | -2.2 | 20.2 | 0 | 2017-03-08 | 3.8 | 14.2 | 0 | 2016-03-08 | 1.8 | 16.2 | 0 | 22.2 | 0
2025-03-08 | -7 | 25 | 0 | 2024-03-08 | -0.9 | 18.9 | 0 | 2023-03-08 | -5.4 | 23.4 | 0 | 2022-03-08 | -5.8 | 23.8 | 0 | 2021-03-08 | -15.1 | 33.1 | 0 | 2020-03-08 | -0.5 | 18.5 | 0 | 2019-03-08 | -15.4 | 33.4 | 0 | 2018-03-08 | -2.3 | 20.3 | 0 | 2017-03-08 | 4 | 14 | 0 | 2016-03-08 | 1.1 | 16.9 | 0 | 22.73 | 0
2025-03-08 | -7.8 | 25.8 | 0 | 2024-03-08 | -1.7 | 19.7 | 0 | 2023-03-08 | -5.7 | 23.7 | 0 | 2022-03-08 | -5.5 | 23.5 | 0 | 2021-03-08 | -16 | 34 | 0 | 2020-03-08 | -0.6 | 18.6 | 0 | 2019-03-08 | -15 | 33 | 0 | 2018-03-08 | -2.5 | 20.5 | 0 | 2017-03-08 | 2.9 | 15.1 | 0 | 2016-03-08 | 1.6 | 16.4 | 0 | 23.03 | 0
2025-03-08 | -7.9 | 25.9 | 0 | 2024-03-08 | -2.6 | 20.6 | 0 | 2023-03-08 | -5.8 | 23.8 | 0 | 2022-03-08 | -5.8 | 23.8 | 0 | 2021-03-08 | -16 | 34 | 0 | 2020-03-08 | -0.9 | 18.9 | 0 | 2019-03-08 | -14.9 | 32.9 | 0 | 2018-03-08 | -2.7 | 20.7 | 0 | 2017-03-08 | 2.2 | 15.8 | 0 | 2016-03-08 | 1.8 | 16.2 | 0 | 23.26 | 0
2025-03-08 | -8.3 | 26.3 | 0 | 2024-03-08 | -2.9 | 20.9 | 0 | 2023-03-08 | -6.2 | 24.2 | 0 | 2022-03-08 | -6.2 | 24.2 | 0 | 2021-03-08 | -17.1 | 35.1 | 0 | 2020-03-08 | -1.1 | 19.1 | 0 | 2019-03-08 | -15.3 | 33.3 | 0 | 2018-03-08 | -2.6 | 20.6 | 0 | 2017-03-08 | 2.1 | 15.9 | 0 | 2016-03-08 | 1.6 | 16.4 | 0 | 23.6 | 0
2025-03-08 | -8.4 | 26.4 | 0 | 2024-03-08 | -2.1 | 20.1 | 0 | 2023-03-08 | -6.9 | 24.9 | 0 | 2022-03-08 | -6.5 | 24.5 | 0 | 2021-03-08 | -18.5 | 36.5 | 0 | 2020-03-08 | -1.8 | 19.8 | 0 | 2019-03-08 | -15.2 | 33.2 | 0 | 2018-03-08 | -2.6 | 20.6 | 0 | 2017-03-08 | 1.9 | 16.1 | 0 | 2016-03-08 | 1.5 | 16.5 | 0 | 23.86 | 0
2025-03-08 | -8.3 | 26.3 | 0 | 2024-03-08 | -0.7 | 18.7 | 0 | 2023-03-08 | -6.3 | 24.3 | 0 | 2022-03-08 | -5.7 | 23.7 | 0 | 2021-03-08 | -17.5 | 35.5 | 0 | 2020-03-08 | -0.9 | 18.9 | 0 | 2019-03-08 | -13.3 | 31.3 | 0 | 2018-03-08 | -2.4 | 20.4 | 0 | 2017-03-08 | 2.9 | 15.1 | 0 | 2016-03-08 | 1.7 | 16.3 | 0 | 23.05 | 0
2025-03-08 | -8 | 26 | 0 | 2024-03-08 | 0.5 | 17.5 | 0 | 2023-03-08 | -6 | 24 | 0 | 2022-03-08 | -5.7 | 23.7 | 0 | 2021-03-08 | -13.7 | 31.7 | 0 | 2020-03-08 | 0.4 | 17.6 | 0 | 2019-03-08 | -11.2 | 29.2 | 0 | 2018-03-08 | -1.9 | 19.9 | 0 | 2017-03-08 | 3.8 | 14.2 | 0 | 2016-03-08 | 3.3 | 14.7 | 0 | 21.85 | 0
2025-03-08 | -7.5 | 25.5 | 0 | 2024-03-08 | 2 | 16 | 0 | 2023-03-08 | -5.3 | 23.3 | 0 | 2022-03-08 | -5.3 | 23.3 | 0 | 2021-03-08 | -9.6 | 27.6 | 0 | 2020-03-08 | 2 | 16 | 0 | 2019-03-08 | -9.1 | 27.1 | 0 | 2018-03-08 | -1.6 | 19.6 | 0 | 2017-03-08 | 5.1 | 12.9 | 0 | 2016-03-08 | 3.9 | 14.1 | 0 | 20.54 | 0
2025-03-08 | -6.8 | 24.8 | 0 | 2024-03-08 | 3.5 | 14.5 | 0 | 2023-03-08 | -3.5 | 21.5 | 0 | 2022-03-08 | -4.9 | 22.9 | 0 | 2021-03-08 | -6.1 | 24.1 | 0 | 2020-03-08 | 3 | 15 | 0 | 2019-03-08 | -7.1 | 25.1 | 0 | 2018-03-08 | -1.5 | 19.5 | 0 | 2017-03-08 | 5.9 | 12.1 | 0 | 2016-03-08 | 4.3 | 13.7 | 0 | 19.32 | 0
2025-03-08 | -5.6 | 23.6 | 0 | 2024-03-08 | 5.1 | 12.9 | 0 | 2023-03-08 | -2 | 20 | 0 | 2022-03-08 | -4.1 | 22.1 | 0 | 2021-03-08 | -4.3 | 22.3 | 0 | 2020-03-08 | 3.6 | 14.4 | 0 | 2019-03-08 | -4.9 | 22.9 | 0 | 2018-03-08 | -1.5 | 19.5 | 0 | 2017-03-08 | 6.7 | 11.3 | 0 | 2016-03-08 | 4.8 | 13.2 | 0 | 18.22 | 0
2025-03-08 | -4.5 | 22.5 | 0 | 2024-03-08 | 6.8 | 11.2 | 0 | 2023-03-08 | -0.6 | 18.6 | 0 | 2022-03-08 | -3.8 | 21.8 | 0 | 2021-03-08 | -3.6 | 21.6 | 0 | 2020-03-08 | 4.7 | 13.3 | 0 | 2019-03-08 | -3.6 | 21.6 | 0 | 2018-03-08 | -1.7 | 19.7 | 0 | 2017-03-08 | 6.7 | 11.3 | 0 | 2016-03-08 | 4.7 | 13.3 | 0 | 17.49 | 0
2025-03-08 | -3.4 | 21.4 | 0 | 2024-03-08 | 7.7 | 10.3 | 0 | 2023-03-08 | -0.2 | 18.2 | 0 | 2022-03-08 | -3.3 | 21.3 | 0 | 2021-03-08 | -3.3 | 21.3 | 0 | 2020-03-08 | 5.3 | 12.7 | 0 | 2019-03-08 | -2.3 | 20.3 | 0 | 2018-03-08 | -1.9 | 19.9 | 0 | 2017-03-08 | 7.4 | 10.6 | 0 | 2016-03-08 | 5.1 | 12.9 | 0 | 16.89 | 0
2025-03-08 | -2.2 | 20.2 | 0 | 2024-03-08 | 8.2 | 9.8 | 0 | 2023-03-08 | 0.5 | 17.5 | 0 | 2022-03-08 | -2.8 | 20.8 | 0 | 2021-03-08 | -3.5 | 21.5 | 0 | 2020-03-08 | 5.5 | 12.5 | 0 | 2019-03-08 | -1.5 | 19.5 | 0 | 2018-03-08 | -1.9 | 19.9 | 0 | 2017-03-08 | 7.3 | 10.7 | 0 | 2016-03-08 | 5.3 | 12.7 | 0 | 16.51 | 0
2025-03-08 | -1.4 | 19.4 | 0 | 2024-03-08 | 7.5 | 10.5 | 0 | 2023-03-08 | 0.1 | 17.9 | 0 | 2022-03-08 | -2.5 | 20.5 | 0 | 2021-03-08 | -2.3 | 20.3 | 0 | 2020-03-08 | 6 | 12 | 0 | 2019-03-08 | -1.8 | 19.8 | 0 | 2018-03-08 | -2.1 | 20.1 | 0 | 2017-03-08 | 6.3 | 11.7 | 0 | 2016-03-08 | 5 | 13 | 0 | 16.52 | 0
2025-03-08 | -1.2 | 19.2 | 0 | 2024-03-08 | 6.2 | 11.8 | 0 | 2023-03-08 | -0.2 | 18.2 | 0 | 2022-03-08 | -3.2 | 21.2 | 0 | 2021-03-08 | -2.2 | 20.2 | 0 | 2020-03-08 | 6.2 | 11.8 | 0 | 2019-03-08 | -2.5 | 20.5 | 0 | 2018-03-08 | -2.3 | 20.3 | 0 | 2017-03-08 | 4.5 | 13.5 | 0 | 2016-03-08 | 4.3 | 13.7 | 0 | 17.04 | 0
2025-03-08 | -2 | 20 | 0 | 2024-03-08 | 3.9 | 14.1 | 0 | 2023-03-08 | -1.5 | 19.5 | 0 | 2022-03-08 | -4.1 | 22.1 | 0 | 2021-03-08 | -2.5 | 20.5 | 0 | 2020-03-08 | 5.3 | 12.7 | 0 | 2019-03-08 | -3.8 | 21.8 | 0 | 2018-03-08 | -2.5 | 20.5 | 0 | 2017-03-08 | 3.6 | 14.4 | 0 | 2016-03-08 | 3.8 | 14.2 | 0 | 17.98 | 0
2025-03-08 | -2.7 | 20.7 | 0 | 2024-03-08 | 2.9 | 15.1 | 0 | 2023-03-08 | -1.7 | 19.7 | 0 | 2022-03-08 | -3.6 | 21.6 | 0 | 2021-03-08 | -2.4 | 20.4 | 0 | 2020-03-08 | 4.5 | 13.5 | 0 | 2019-03-08 | -4.8 | 22.8 | 0 | 2018-03-08 | -2.4 | 20.4 | 0 | 2017-03-08 | 2.5 | 15.5 | 0 | 2016-03-08 | 3.2 | 14.8 | 0 | 18.45 | 0
2025-03-08 | -3.2 | 21.2 | 0 | 2024-03-08 | 2 | 16 | 0 | 2023-03-08 | -0.7 | 18.7 | 0 | 2022-03-08 | -3.4 | 21.4 | 0 | 2021-03-08 | -2.4 | 20.4 | 0 | 2020-03-08 | 4.9 | 13.1 | 0 | 2019-03-08 | -6 | 24 | 0 | 2018-03-08 | -2.7 | 20.7 | 0 | 2017-03-08 | 2.2 | 15.8 | 0 | 2016-03-08 | 2.5 | 15.5 | 0 | 18.68 | 0
2025-03-08 | -3.6 | 21.6 | 0 | 2024-03-08 | 0.9 | 17.1 | 0 | 2023-03-08 | -2 | 20 | 0 | 2022-03-08 | -3.3 | 21.3 | 0 | 2021-03-08 | -2.8 | 20.8 | 0 | 2020-03-08 | 4.6 | 13.4 | 0 | 2019-03-08 | -6.4 | 24.4 | 0 | 2018-03-08 | -2.3 | 20.3 | 0 | 2017-03-08 | 2 | 16 | 0 | 2016-03-08 | 1.9 | 16.1 | 0 | 19.1 | 0
2025-03-08 | -5 | 23 | 0 | 2024-03-08 | 1.1 | 16.9 | 0 | 2023-03-08 | -2.4 | 20.4 | 0 | 2022-03-08 | -2.5 | 20.5 | 0 | 2021-03-08 | -3.1 | 21.1 | 0 | 2020-03-08 | 4.3 | 13.7 | 0 | 2019-03-08 | -7.5 | 25.5 | 0 | 2018-03-08 | -2.5 | 20.5 | 0 | 2017-03-08 | 1.5 | 16.5 | 0 | 2016-03-08 | 1.6 | 16.4 | 0 | 19.45 | 0
2025-03-08 | -5.9 | 23.9 | 0 | 2024-03-08 | 1.2 | 16.8 | 0 | 2023-03-08 | -3 | 21 | 0 | 2022-03-08 | -2.3 | 20.3 | 0 | 2021-03-08 | -3.3 | 21.3 | 0 | 2020-03-08 | 4.3 | 13.7 | 0 | 2019-03-08 | -7.8 | 25.8 | 0 | 2018-03-08 | -2.6 | 20.6 | 0 | 2017-03-08 | 1.9 | 16.1 | 0 | 2016-03-08 | 1.5 | 16.5 | 0 | 19.6 | 0
2025-03-09 | -5.5 | 23.5 | 0 | 2024-03-09 | 1.3 | 16.7 | 0 | 2023-03-09 | -3.8 | 21.8 | 0 | 2022-03-09 | -1.7 | 19.7 | 0 | 2021-03-09 | -3.1 | 21.1 | 0 | 2020-03-09 | 4.1 | 13.9 | 0 | 2019-03-09 | -8.7 | 26.7 | 0 | 2018-03-09 | -3 | 21 | 0 | 2017-03-09 | -0.2 | 18.2 | 0 | 2016-03-09 | 1.4 | 16.6 | 0 | 19.92 | 0
2025-03-09 | -5.6 | 23.6 | 0 | 2024-03-09 | 1.1 | 16.9 | 0 | 2023-03-09 | -4 | 22 | 0 | 2022-03-09 | -2 | 20 | 0 | 2021-03-09 | -3.5 | 21.5 | 0 | 2020-03-09 | 5 | 13 | 0 | 2019-03-09 | -9.3 | 27.3 | 0 | 2018-03-09 | -3.1 | 21.1 | 0 | 2017-03-09 | -1.4 | 19.4 | 0 | 2016-03-09 | 1.1 | 16.9 | 0 | 20.17 | 0
2025-03-09 | -5.8 | 23.8 | 0 | 2024-03-09 | 1 | 17 | 0 | 2023-03-09 | -4.4 | 22.4 | 0 | 2022-03-09 | -3.1 | 21.1 | 0 | 2021-03-09 | -6.4 | 24.4 | 0 | 2020-03-09 | 4.9 | 13.1 | 0 | 2019-03-09 | -10 | 28 | 0 | 2018-03-09 | -3.1 | 21.1 | 0 | 2017-03-09 | -1 | 19 | 0 | 2016-03-09 | 1.4 | 16.6 | 0 | 20.65 | 0
2025-03-09 | -6.2 | 24.2 | 0 | 2024-03-09 | 1 | 17 | 0 | 2023-03-09 | -4.4 | 22.4 | 0 | 2022-03-09 | -3.6 | 21.6 | 0 | 2021-03-09 | -5.7 | 23.7 | 0 | 2020-03-09 | 4.7 | 13.3 | 0 | 2019-03-09 | -10.5 | 28.5 | 0 | 2018-03-09 | -3.4 | 21.4 | 0 | 2017-03-09 | -1.7 | 19.7 | 0 | 2016-03-09 | 1 | 17 | 0 | 20.88 | 0
2025-03-09 | -5.4 | 23.4 | 0 | 2024-03-09 | 0.8 | 17.2 | 0 | 2023-03-09 | -4.4 | 22.4 | 0 | 2022-03-09 | -2.8 | 20.8 | 0 | 2021-03-09 | -5.8 | 23.8 | 0 | 2020-03-09 | 4.5 | 13.5 | 0 | 2019-03-09 | -11.4 | 29.4 | 0 | 2018-03-09 | -3.8 | 21.8 | 0 | 2017-03-09 | -2.1 | 20.1 | 0 | 2016-03-09 | 1 | 17 | 0 | 20.94 | 0
2025-03-09 | -5 | 23 | 0 | 2024-03-09 | 0.7 | 17.3 | 0 | 2023-03-09 | -4.6 | 22.6 | 0 | 2022-03-09 | -2.9 | 20.9 | 0 | 2021-03-09 | -7.3 | 25.3 | 0 | 2020-03-09 | 4.5 | 13.5 | 0 | 2019-03-09 | -13.2 | 31.2 | 0 | 2018-03-09 | -3.9 | 21.9 | 0 | 2017-03-09 | -3.4 | 21.4 | 0 | 2016-03-09 | 1.4 | 16.6 | 0 | 21.37 | 0
2025-03-09 | -4.3 | 22.3 | 0 | 2024-03-09 | 0.3 | 17.7 | 0 | 2023-03-09 | -4.6 | 22.6 | 0 | 2022-03-09 | -4 | 22 | 0 | 2021-03-09 | -9 | 27 | 0 | 2020-03-09 | 4 | 14 | 0 | 2019-03-09 | -12.9 | 30.9 | 0 | 2018-03-09 | -4.6 | 22.6 | 0 | 2017-03-09 | -3.9 | 21.9 | 0 | 2016-03-09 | 2.5 | 15.5 | 0 | 21.65 | 0
2025-03-09 | -4 | 22 | 0 | 2024-03-09 | 0.4 | 17.6 | 0 | 2023-03-09 | -4.9 | 22.9 | 0 | 2022-03-09 | -4.7 | 22.7 | 0 | 2021-03-09 | -7.3 | 25.3 | 0 | 2020-03-09 | 3.8 | 14.2 | 0 | 2019-03-09 | -12.1 | 30.1 | 0 | 2018-03-09 | -4 | 22 | 0 | 2017-03-09 | -4.2 | 22.2 | 0 | 2016-03-09 | 1.3 | 16.7 | 0 | 21.57 | 0
2025-03-09 | -3.2 | 21.2 | 0 | 2024-03-09 | 1.1 | 16.9 | 0 | 2023-03-09 | -5.2 | 23.2 | 0 | 2022-03-09 | -3.6 | 21.6 | 0 | 2021-03-09 | -4.6 | 22.6 | 0 | 2020-03-09 | 4.9 | 13.1 | 0 | 2019-03-09 | -11.4 | 29.4 | 0 | 2018-03-09 | -3.4 | 21.4 | 0 | 2017-03-09 | -4.4 | 22.4 | 0 | 2016-03-09 | 5.9 | 12.1 | 0 | 20.39 | 0
2025-03-09 | -2.4 | 20.4 | 0 | 2024-03-09 | 3 | 15 | 0 | 2023-03-09 | -5 | 23 | 0 | 2022-03-09 | -1.8 | 19.8 | 0 | 2021-03-09 | -0.7 | 18.7 | 0 | 2020-03-09 | 6.5 | 11.5 | 0 | 2019-03-09 | -8.5 | 26.5 | 0 | 2018-03-09 | -2.5 | 20.5 | 0 | 2017-03-09 | -3.9 | 21.9 | 0 | 2016-03-09 | 8.4 | 9.6 | 0 | 18.69 | 0
2025-03-09 | -1.1 | 19.1 | 0 | 2024-03-09 | 6.4 | 11.6 | 0 | 2023-03-09 | -3.9 | 21.9 | 0 | 2022-03-09 | -0.7 | 18.7 | 0 | 2021-03-09 | 2.5 | 15.5 | 0 | 2020-03-09 | 8.6 | 9.4 | 0 | 2019-03-09 | -5.6 | 23.6 | 0 | 2018-03-09 | -1.9 | 19.9 | 0 | 2017-03-09 | -3.5 | 21.5 | 0 | 2016-03-09 | 10 | 8 | 0 | 16.92 | 0
2025-03-09 | -0.5 | 18.5 | 0 | 2024-03-09 | 7 | 11 | 0 | 2023-03-09 | -3 | 21 | 0 | 2022-03-09 | 0.1 | 17.9 | 0 | 2021-03-09 | 3.7 | 14.3 | 0 | 2020-03-09 | 10 | 8 | 0 | 2019-03-09 | -2.8 | 20.8 | 0 | 2018-03-09 | -1.3 | 19.3 | 0 | 2017-03-09 | -3.4 | 21.4 | 0 | 2016-03-09 | 9.8 | 8.2 | 0 | 16.04 | 0
2025-03-09 | -0.1 | 18.1 | 0 | 2024-03-09 | 5.9 | 12.1 | 0 | 2023-03-09 | -1.9 | 19.9 | 0 | 2022-03-09 | 0.8 | 17.2 | 0 | 2021-03-09 | 4.1 | 13.9 | 0 | 2020-03-09 | 11.6 | 6.4 | 0 | 2019-03-09 | -2.2 | 20.2 | 0 | 2018-03-09 | -0.2 | 18.2 | 0 | 2017-03-09 | -3.1 | 21.1 | 0 | 2016-03-09 | 9.9 | 8.1 | 0 | 15.52 | 0
2025-03-09 | 1.4 | 16.6 | 0 | 2024-03-09 | 5.2 | 12.8 | 0 | 2023-03-09 | -0.8 | 18.8 | 0 | 2022-03-09 | 1.3 | 16.7 | 0 | 2021-03-09 | 4.8 | 13.2 | 0 | 2020-03-09 | 12.4 | 5.6 | 0 | 2019-03-09 | -1.2 | 19.2 | 0 | 2018-03-09 | -0.6 | 18.6 | 0 | 2017-03-09 | -1.9 | 19.9 | 0 | 2016-03-09 | 9.2 | 8.8 | 0 | 15.02 | 0
2025-03-09 | 1.3 | 16.7 | 0 | 2024-03-09 | 5.2 | 12.8 | 0 | 2023-03-09 | 0.4 | 17.6 | 0 | 2022-03-09 | 1.8 | 16.2 | 0 | 2021-03-09 | 5 | 13 | 0 | 2020-03-09 | 12.2 | 5.8 | 0 | 2019-03-09 | -0.7 | 18.7 | 0 | 2018-03-09 | 0.1 | 17.9 | 0 | 2017-03-09 | -1.4 | 19.4 | 0 | 2016-03-09 | 8.3 | 9.7 | 0 | 14.78 | 0
2025-03-09 | 1.6 | 16.4 | 0 | 2024-03-09 | 5.3 | 12.7 | 0 | 2023-03-09 | 1.1 | 16.9 | 0 | 2022-03-09 | 2.1 | 15.9 | 0 | 2021-03-09 | 5.2 | 12.8 | 0 | 2020-03-09 | 11.9 | 6.1 | 0 | 2019-03-09 | -0.6 | 18.6 | 0 | 2018-03-09 | 0.2 | 17.8 | 0 | 2017-03-09 | -0.8 | 18.8 | 0 | 2016-03-09 | 8.5 | 9.5 | 0 | 14.55 | 0
2025-03-09 | 0.8 | 17.2 | 0 | 2024-03-09 | 5.6 | 12.4 | 0 | 2023-03-09 | 1.8 | 16.2 | 0 | 2022-03-09 | 2.4 | 15.6 | 0 | 2021-03-09 | 5.4 | 12.6 | 0 | 2020-03-09 | 11.6 | 6.4 | 0 | 2019-03-09 | -1 | 19 | 0 | 2018-03-09 | 0.1 | 17.9 | 0 | 2017-03-09 | -0.7 | 18.7 | 0 | 2016-03-09 | 9.3 | 8.7 | 0 | 14.47 | 0
2025-03-09 | 1.2 | 16.8 | 0 | 2024-03-09 | 5.5 | 12.5 | 0 | 2023-03-09 | 1.6 | 16.4 | 0 | 2022-03-09 | 2.4 | 15.6 | 0 | 2021-03-09 | 5.2 | 12.8 | 0 | 2020-03-09 | 10 | 8 | 0 | 2019-03-09 | -1.9 | 19.9 | 0 | 2018-03-09 | -0.5 | 18.5 | 0 | 2017-03-09 | -0.9 | 18.9 | 0 | 2016-03-09 | 11 | 7 | 0 | 14.64 | 0
2025-03-09 | 1.2 | 16.8 | 0 | 2024-03-09 | 5.2 | 12.8 | 0 | 2023-03-09 | 1.1 | 16.9 | 0 | 2022-03-09 | 1 | 17 | 0 | 2021-03-09 | 4.9 | 13.1 | 0 | 2020-03-09 | 9.1 | 8.9 | 0 | 2019-03-09 | -2.9 | 20.9 | 0 | 2018-03-09 | -0.7 | 18.7 | 0 | 2017-03-09 | -1.6 | 19.6 | 0 | 2016-03-09 | 10.8 | 7.2 | 0 | 15.19 | 0
2025-03-09 | 1.2 | 16.8 | 0 | 2024-03-09 | 5.2 | 12.8 | 0 | 2023-03-09 | 0.7 | 17.3 | 0 | 2022-03-09 | 0.6 | 17.4 | 0 | 2021-03-09 | 4.3 | 13.7 | 0 | 2020-03-09 | 8.5 | 9.5 | 0 | 2019-03-09 | -4.1 | 22.1 | 0 | 2018-03-09 | -1.3 | 19.3 | 0 | 2017-03-09 | -2.2 | 20.2 | 0 | 2016-03-09 | 10.5 | 7.5 | 0 | 15.66 | 0
2025-03-09 | 0.6 | 17.4 | 0 | 2024-03-09 | 5.1 | 12.9 | 0 | 2023-03-09 | 0.7 | 17.3 | 0 | 2022-03-09 | 0 | 18 | 0 | 2021-03-09 | 0.7 | 17.3 | 0 | 2020-03-09 | 7.7 | 10.3 | 0 | 2019-03-09 | -4.9 | 22.9 | 0 | 2018-03-09 | -1.5 | 19.5 | 0 | 2017-03-09 | -3 | 21 | 0 | 2016-03-09 | 10.4 | 7.6 | 0 | 16.42 | 0
2025-03-09 | -1.1 | 19.1 | 0 | 2024-03-09 | 5.2 | 12.8 | 0 | 2023-03-09 | 0.1 | 17.9 | 0 | 2022-03-09 | -0.4 | 18.4 | 0 | 2021-03-09 | 1.3 | 16.7 | 0 | 2020-03-09 | 5.7 | 12.3 | 0 | 2019-03-09 | -5.4 | 23.4 | 0 | 2018-03-09 | -1.7 | 19.7 | 0 | 2017-03-09 | -3.7 | 21.7 | 0 | 2016-03-09 | 8.7 | 9.3 | 0 | 17.13 | 0
2025-03-09 | -1 | 19 | 0 | 2024-03-09 | 5 | 13 | 0 | 2023-03-09 | 0.2 | 17.8 | 0 | 2022-03-09 | -1.2 | 19.2 | 0 | 2021-03-09 | 0.7 | 17.3 | 0 | 2020-03-09 | 6 | 12 | 0 | 2019-03-09 | -6.6 | 24.6 | 0 | 2018-03-09 | -2.3 | 20.3 | 0 | 2017-03-09 | -4.1 | 22.1 | 0 | 2016-03-09 | 9.1 | 8.9 | 0 | 17.42 | 0
2025-03-09 | -0.9 | 18.9 | 0 | 2024-03-09 | 4.8 | 13.2 | 0 | 2023-03-09 | -0.1 | 18.1 | 0 | 2022-03-09 | -1 | 19 | 0 | 2021-03-09 | -0.2 | 18.2 | 0 | 2020-03-09 | 5.6 | 12.4 | 0 | 2019-03-09 | -6.5 | 24.5 | 0 | 2018-03-09 | -3.5 | 21.5 | 0 | 2017-03-09 | -4 | 22 | 0 | 2016-03-09 | 8 | 10 | 0 | 17.78 | 0
2025-03-10 | -1 | 19 | 0 | 2024-03-10 | 4.8 | 13.2 | 0 | 2023-03-10 | -0.4 | 18.4 | 0 | 2022-03-10 | 0.2 | 17.8 | 0 | 2021-03-10 | -1.1 | 19.1 | 0 | 2020-03-10 | 4 | 14 | 0 | 2019-03-10 | -6.7 | 24.7 | 0 | 2018-03-10 | -3.7 | 21.7 | 0 | 2017-03-10 | -4.3 | 22.3 | 0 | 2016-03-10 | 7.4 | 10.6 | 0 | 18.08 | 0
2025-03-10 | -0.8 | 18.8 | 0 | 2024-03-10 | 4.5 | 13.5 | 0 | 2023-03-10 | -0.8 | 18.8 | 0 | 2022-03-10 | -0.3 | 18.3 | 0 | 2021-03-10 | -1.9 | 19.9 | 0 | 2020-03-10 | 3.3 | 14.7 | 0 | 2019-03-10 | -6.6 | 24.6 | 0 | 2018-03-10 | -4 | 22 | 0 | 2017-03-10 | -4.2 | 22.2 | 0 | 2016-03-10 | 6.9 | 11.1 | 0 | 18.39 | 0
2025-03-10 | -1 | 19 | 0 | 2024-03-10 | 4.3 | 13.7 | 0 | 2023-03-10 | -2.4 | 20.4 | 0 | 2022-03-10 | -1 | 19 | 0 | 2021-03-10 | -2.9 | 20.9 | 0 | 2020-03-10 | 3.1 | 14.9 | 0 | 2019-03-10 | -6.8 | 24.8 | 0 | 2018-03-10 | -4.4 | 22.4 | 0 | 2017-03-10 | -4 | 22 | 0 | 2016-03-10 | 7.2 | 10.8 | 0 | 18.79 | 0
2025-03-10 | -1 | 19 | 0 | 2024-03-10 | 4.2 | 13.8 | 0 | 2023-03-10 | -3.2 | 21.2 | 0 | 2022-03-10 | -1.2 | 19.2 | 0 | 2021-03-10 | -4.4 | 22.4 | 0 | 2020-03-10 | 2.6 | 15.4 | 0 | 2019-03-10 | -6.6 | 24.6 | 0 | 2018-03-10 | -4.4 | 22.4 | 0 | 2017-03-10 | -4.7 | 22.7 | 0 | 2016-03-10 | 7.3 | 10.7 | 0 | 19.14 | 0
2025-03-10 | -1.2 | 19.2 | 0 | 2024-03-10 | 2.9 | 15.1 | 0 | 2023-03-10 | -4.1 | 22.1 | 0 | 2022-03-10 | -1.8 | 19.8 | 0 | 2021-03-10 | -4.7 | 22.7 | 0 | 2020-03-10 | 2.6 | 15.4 | 0 | 2019-03-10 | -6.7 | 24.7 | 0 | 2018-03-10 | -4.4 | 22.4 | 0 | 2017-03-10 | -6.2 | 24.2 | 0 | 2016-03-10 | 6.9 | 11.1 | 0 | 19.67 | 0
2025-03-10 | -1.3 | 19.3 | 0 | 2024-03-10 | 2.5 | 15.5 | 0 | 2023-03-10 | -5.9 | 23.9 | 0 | 2022-03-10 | -1.8 | 19.8 | 0 | 2021-03-10 | -4.4 | 22.4 | 0 | 2020-03-10 | 5.5 | 12.5 | 0 | 2019-03-10 | -6.4 | 24.4 | 0 | 2018-03-10 | -5 | 23 | 0 | 2017-03-10 | -6.2 | 24.2 | 0 | 2016-03-10 | 6.5 | 11.5 | 0 | 19.65 | 0
2025-03-10 | -1.9 | 19.9 | 0 | 2024-03-10 | 2.3 | 15.7 | 0 | 2023-03-10 | -4.4 | 22.4 | 0 | 2022-03-10 | -3.4 | 21.4 | 0 | 2021-03-10 | -6.3 | 24.3 | 0 | 2020-03-10 | 5.5 | 12.5 | 0 | 2019-03-10 | -6.9 | 24.9 | 0 | 2018-03-10 | -5.2 | 23.2 | 0 | 2017-03-10 | -6.7 | 24.7 | 0 | 2016-03-10 | 4.4 | 13.6 | 0 | 20.26 | 0
2025-03-10 | -2 | 20 | 0 | 2024-03-10 | 2.2 | 15.8 | 0 | 2023-03-10 | -4.4 | 22.4 | 0 | 2022-03-10 | -3.5 | 21.5 | 0 | 2021-03-10 | -5.7 | 23.7 | 0 | 2020-03-10 | 4.8 | 13.2 | 0 | 2019-03-10 | -7.3 | 25.3 | 0 | 2018-03-10 | -5 | 23 | 0 | 2017-03-10 | -8.2 | 26.2 | 0 | 2016-03-10 | 5 | 13 | 0 | 20.41 | 0
2025-03-10 | -2.3 | 20.3 | 0 | 2024-03-10 | 1.9 | 16.1 | 0 | 2023-03-10 | -4.5 | 22.5 | 0 | 2022-03-10 | -2.6 | 20.6 | 0 | 2021-03-10 | -3.7 | 21.7 | 0 | 2020-03-10 | 2.6 | 15.4 | 0 | 2019-03-10 | -6.4 | 24.4 | 0 | 2018-03-10 | -4.2 | 22.2 | 0 | 2017-03-10 | -7.9 | 25.9 | 0 | 2016-03-10 | 4.5 | 13.5 | 0 | 20.26 | 0
2025-03-10 | -0.6 | 18.6 | 0 | 2024-03-10 | 1.2 | 16.8 | 0 | 2023-03-10 | -4.2 | 22.2 | 0 | 2022-03-10 | -2 | 20 | 0 | 2021-03-10 | -0.6 | 18.6 | 0 | 2020-03-10 | 6 | 12 | 0 | 2019-03-10 | -5.2 | 23.2 | 0 | 2018-03-10 | -2.7 | 20.7 | 0 | 2017-03-10 | -7.7 | 25.7 | 0 | 2016-03-10 | 4.5 | 13.5 | 0 | 19.13 | 0
2025-03-10 | 0.9 | 17.1 | 0 | 2024-03-10 | 0.8 | 17.2 | 0 | 2023-03-10 | -4.3 | 22.3 | 0 | 2022-03-10 | -1.5 | 19.5 | 0 | 2021-03-10 | 2 | 16 | 0 | 2020-03-10 | 7.2 | 10.8 | 0 | 2019-03-10 | -4.5 | 22.5 | 0 | 2018-03-10 | -1.6 | 19.6 | 0 | 2017-03-10 | -8.1 | 26.1 | 0 | 2016-03-10 | 4.7 | 13.3 | 0 | 18.44 | 0
2025-03-10 | 1.5 | 16.5 | 0 | 2024-03-10 | 0.3 | 17.7 | 0 | 2023-03-10 | -4.1 | 22.1 | 0 | 2022-03-10 | -0.7 | 18.7 | 0 | 2021-03-10 | 3.4 | 14.6 | 0 | 2020-03-10 | 7.1 | 10.9 | 0 | 2019-03-10 | -3.3 | 21.3 | 0 | 2018-03-10 | -1.3 | 19.3 | 0 | 2017-03-10 | -7.9 | 25.9 | 0 | 2016-03-10 | 4.3 | 13.7 | 0 | 18.07 | 0
2025-03-10 | 2.4 | 15.6 | 0 | 2024-03-10 | -0.8 | 18.8 | 0 | 2023-03-10 | -4.3 | 22.3 | 0 | 2022-03-10 | 0.1 | 17.9 | 0 | 2021-03-10 | 4.1 | 13.9 | 0 | 2020-03-10 | 7 | 11 | 0 | 2019-03-10 | -1.5 | 19.5 | 0 | 2018-03-10 | -0.3 | 18.3 | 0 | 2017-03-10 | -7.2 | 25.2 | 0 | 2016-03-10 | 3.8 | 14.2 | 0 | 17.67 | 0
2025-03-10 | 3.6 | 14.4 | 0 | 2024-03-10 | -1.7 | 19.7 | 0 | 2023-03-10 | -3.7 | 21.7 | 0 | 2022-03-10 | 0.9 | 17.1 | 0 | 2021-03-10 | 5.4 | 12.6 | 0 | 2020-03-10 | 6.9 | 11.1 | 0 | 2019-03-10 | -0.2 | 18.2 | 0 | 2018-03-10 | 0.2 | 17.8 | 0 | 2017-03-10 | -6.3 | 24.3 | 0 | 2016-03-10 | 4.3 | 13.7 | 0 | 17.06 | 0
2025-03-10 | 4.1 | 13.9 | 0 | 2024-03-10 | -1.6 | 19.6 | 0 | 2023-03-10 | -2.9 | 20.9 | 0 | 2022-03-10 | 1.7 | 16.3 | 0 | 2021-03-10 | 6.2 | 11.8 | 0 | 2020-03-10 | 6.1 | 11.9 | 0 | 2019-03-10 | 0.3 | 17.7 | 0 | 2018-03-10 | 0.2 | 17.8 | 0 | 2017-03-10 | -7.6 | 25.6 | 0 | 2016-03-10 | 4.4 | 13.6 | 0 | 16.91 | 0
2025-03-10 | 4.3 | 13.7 | 0 | 2024-03-10 | -2.1 | 20.1 | 0 | 2023-03-10 | -2.1 | 20.1 | 0 | 2022-03-10 | 1.8 | 16.2 | 0 | 2021-03-10 | 7.8 | 10.2 | 0 | 2020-03-10 | 5.7 | 12.3 | 0 | 2019-03-10 | 1.3 | 16.7 | 0 | 2018-03-10 | 0.4 | 17.6 | 0 | 2017-03-10 | -7.7 | 25.7 | 0 | 2016-03-10 | 4.3 | 13.7 | 0 | 16.63 | 0
2025-03-10 | 4.4 | 13.6 | 0 | 2024-03-10 | -2.4 | 20.4 | 0 | 2023-03-10 | -2.2 | 20.2 | 0 | 2022-03-10 | 2.1 | 15.9 | 0 | 2021-03-10 | 8 | 10 | 0 | 2020-03-10 | 3.5 | 14.5 | 0 | 2019-03-10 | 2.7 | 15.3 | 0 | 2018-03-10 | 0.4 | 17.6 | 0 | 2017-03-10 | -7.1 | 25.1 | 0 | 2016-03-10 | 3.1 | 14.9 | 0 | 16.75 | 0
2025-03-10 | 4.2 | 13.8 | 0 | 2024-03-10 | -3.2 | 21.2 | 0 | 2023-03-10 | -2.4 | 20.4 | 0 | 2022-03-10 | 2.3 | 15.7 | 0 | 2021-03-10 | 4.8 | 13.2 | 0 | 2020-03-10 | 2.2 | 15.8 | 0 | 2019-03-10 | 2.5 | 15.5 | 0 | 2018-03-10 | 0.5 | 17.5 | 0 | 2017-03-10 | -9.3 | 27.3 | 0 | 2016-03-10 | 2.4 | 15.6 | 0 | 17.6 | 0
2025-03-10 | 3.3 | 14.7 | 0 | 2024-03-10 | -3.6 | 21.6 | 0 | 2023-03-10 | -3.5 | 21.5 | 0 | 2022-03-10 | 1.1 | 16.9 | 0 | 2021-03-10 | 4.4 | 13.6 | 0 | 2020-03-10 | 1.4 | 16.6 | 0 | 2019-03-10 | 2.4 | 15.6 | 0 | 2018-03-10 | -0.2 | 18.2 | 0 | 2017-03-10 | -11.1 | 29.1 | 0 | 2016-03-10 | 2 | 16 | 0 | 18.38 | 0
2025-03-10 | 2.2 | 15.8 | 0 | 2024-03-10 | -3.5 | 21.5 | 0 | 2023-03-10 | -4.1 | 22.1 | 0 | 2022-03-10 | 0.1 | 17.9 | 0 | 2021-03-10 | 5.3 | 12.7 | 0 | 2020-03-10 | 0.8 | 17.2 | 0 | 2019-03-10 | 1.9 | 16.1 | 0 | 2018-03-10 | -0.8 | 18.8 | 0 | 2017-03-10 | -12.7 | 30.7 | 0 | 2016-03-10 | 1.8 | 16.2 | 0 | 18.9 | 0
2025-03-10 | 2.1 | 15.9 | 0 | 2024-03-10 | -4 | 22 | 0 | 2023-03-10 | -4.4 | 22.4 | 0 | 2022-03-10 | -0.6 | 18.6 | 0 | 2021-03-10 | 6.2 | 11.8 | 0 | 2020-03-10 | -0.1 | 18.1 | 0 | 2019-03-10 | 1.8 | 16.2 | 0 | 2018-03-10 | -1.3 | 19.3 | 0 | 2017-03-10 | -13.8 | 31.8 | 0 | 2016-03-10 | 2 | 16 | 0 | 19.21 | 0
2025-03-10 | 1 | 17 | 0 | 2024-03-10 | -4.5 | 22.5 | 0 | 2023-03-10 | -4.3 | 22.3 | 0 | 2022-03-10 | -1.3 | 19.3 | 0 | 2021-03-10 | 8.7 | 9.3 | 0 | 2020-03-10 | -1 | 19 | 0 | 2019-03-10 | 1.8 | 16.2 | 0 | 2018-03-10 | -1.7 | 19.7 | 0 | 2017-03-10 | -14.8 | 32.8 | 0 | 2016-03-10 | 1.3 | 16.7 | 0 | 19.48 | 0
2025-03-10 | 1.4 | 16.6 | 0 | 2024-03-10 | -4.9 | 22.9 | 0 | 2023-03-10 | -4.9 | 22.9 | 0 | 2022-03-10 | -0.8 | 18.8 | 0 | 2021-03-10 | 8.3 | 9.7 | 0 | 2020-03-10 | -2.1 | 20.1 | 0 | 2019-03-10 | 1.5 | 16.5 | 0 | 2018-03-10 | -1.8 | 19.8 | 0 | 2017-03-10 | -16.2 | 34.2 | 0 | 2016-03-10 | 1 | 17 | 0 | 19.85 | 0
2025-03-10 | 1.3 | 16.7 | 0 | 2024-03-10 | -4.7 | 22.7 | 0 | 2023-03-10 | -4.5 | 22.5 | 0 | 2022-03-10 | -1.2 | 19.2 | 0 | 2021-03-10 | 8 | 10 | 0 | 2020-03-10 | -3 | 21 | 0 | 2019-03-10 | 1.2 | 16.8 | 0 | 2018-03-10 | -2.1 | 20.1 | 0 | 2017-03-10 | -17.1 | 35.1 | 0 | 2016-03-10 | 1 | 17 | 0 | 20.11 | 0
2025-03-11 | 0.4 | 17.6 | 0 | 2024-03-11 | -4.4 | 22.4 | 0 | 2023-03-11 | -4.2 | 22.2 | 0 | 2022-03-11 | -1.6 | 19.6 | 0 | 2021-03-11 | 7.5 | 10.5 | 0 | 2020-03-11 | -3.4 | 21.4 | 0 | 2019-03-11 | 1.6 | 16.4 | 0 | 2018-03-11 | -2.5 | 20.5 | 0 | 2017-03-11 | -17.9 | 35.9 | 0 | 2016-03-11 | 0.8 | 17.2 | 0 | 20.37 | 0
2025-03-11 | 0 | 18 | 0 | 2024-03-11 | -4 | 22 | 0 | 2023-03-11 | -4.3 | 22.3 | 0 | 2022-03-11 | -1.5 | 19.5 | 0 | 2021-03-11 | 7.3 | 10.7 | 0 | 2020-03-11 | -4.1 | 22.1 | 0 | 2019-03-11 | 1.7 | 16.3 | 0 | 2018-03-11 | -2.8 | 20.8 | 0 | 2017-03-11 | -18.4 | 36.4 | 0 | 2016-03-11 | 0.7 | 17.3 | 0 | 20.54 | 0
2025-03-11 | -0.4 | 18.4 | 0 | 2024-03-11 | -3.5 | 21.5 | 0 | 2023-03-11 | -4.9 | 22.9 | 0 | 2022-03-11 | -1.8 | 19.8 | 0 | 2021-03-11 | 7.1 | 10.9 | 0 | 2020-03-11 | -4.9 | 22.9 | 0 | 2019-03-11 | 1.8 | 16.2 | 0 | 2018-03-11 | -3 | 21 | 0 | 2017-03-11 | -18.8 | 36.8 | 0 | 2016-03-11 | 1 | 17 | 0 | 20.74 | 0
2025-03-11 | -1.2 | 19.2 | 0 | 2024-03-11 | -3.1 | 21.1 | 0 | 2023-03-11 | -4.9 | 22.9 | 0 | 2022-03-11 | -2.4 | 20.4 | 0 | 2021-03-11 | 7.4 | 10.6 | 0 | 2020-03-11 | -5.2 | 23.2 | 0 | 2019-03-11 | 1.7 | 16.3 | 0 | 2018-03-11 | -3.2 | 21.2 | 0 | 2017-03-11 | -19 | 37 | 0 | 2016-03-11 | 0.8 | 17.2 | 0 | 20.91 | 0
2025-03-11 | -1.3 | 19.3 | 0 | 2024-03-11 | -2.4 | 20.4 | 0 | 2023-03-11 | -5 | 23 | 0 | 2022-03-11 | -2.7 | 20.7 | 0 | 2021-03-11 | 8 | 10 | 0 | 2020-03-11 | -5.8 | 23.8 | 0 | 2019-03-11 | 1.5 | 16.5 | 0 | 2018-03-11 | -3.5 | 21.5 | 0 | 2017-03-11 | -19.4 | 37.4 | 0 | 2016-03-11 | -0.2 | 18.2 | 0 | 21.08 | 0
2025-03-11 | -1.8 | 19.8 | 0 | 2024-03-11 | -2.4 | 20.4 | 0 | 2023-03-11 | -4.9 | 22.9 | 0 | 2022-03-11 | -2.9 | 20.9 | 0 | 2021-03-11 | 7.8 | 10.2 | 0 | 2020-03-11 | -6 | 24 | 0 | 2019-03-11 | 1.6 | 16.4 | 0 | 2018-03-11 | -3.9 | 21.9 | 0 | 2017-03-11 | -19.5 | 37.5 | 0 | 2016-03-11 | -0.5 | 18.5 | 0 | 21.25 | 0
2025-03-11 | -1.7 | 19.7 | 0 | 2024-03-11 | -2.6 | 20.6 | 0 | 2023-03-11 | -4.9 | 22.9 | 0 | 2022-03-11 | -3.8 | 21.8 | 0 | 2021-03-11 | 7.8 | 10.2 | 0 | 2020-03-11 | -6.8 | 24.8 | 0 | 2019-03-11 | 1.7 | 16.3 | 0 | 2018-03-11 | -4 | 22 | 0 | 2017-03-11 | -19.6 | 37.6 | 0 | 2016-03-11 | -1.2 | 19.2 | 0 | 21.51 | 0
2025-03-11 | 0.3 | 17.7 | 0 | 2024-03-11 | -2.9 | 20.9 | 0 | 2023-03-11 | -5 | 23 | 0 | 2022-03-11 | -4.3 | 22.3 | 0 | 2021-03-11 | 7.4 | 10.6 | 0 | 2020-03-11 | -6.1 | 24.1 | 0 | 2019-03-11 | 1.8 | 16.2 | 0 | 2018-03-11 | -4.1 | 22.1 | 0 | 2017-03-11 | -19.1 | 37.1 | 0 | 2016-03-11 | -1.3 | 19.3 | 0 | 21.33 | 0
2025-03-11 | 5.9 | 12.1 | 0 | 2024-03-11 | -3 | 21 | 0 | 2023-03-11 | -4.2 | 22.2 | 0 | 2022-03-11 | -4.1 | 22.1 | 0 | 2021-03-11 | 7.9 | 10.1 | 0 | 2020-03-11 | -5.6 | 23.6 | 0 | 2019-03-11 | 2.1 | 15.9 | 0 | 2018-03-11 | -3.9 | 21.9 | 0 | 2017-03-11 | -18.7 | 36.7 | 0 | 2016-03-11 | -0.3 | 18.3 | 0 | 20.39 | 0
2025-03-11 | 8.3 | 9.7 | 0 | 2024-03-11 | -2 | 20 | 0 | 2023-03-11 | -2.6 | 20.6 | 0 | 2022-03-11 | -3.8 | 21.8 | 0 | 2021-03-11 | 9.5 | 8.5 | 0 | 2020-03-11 | -5.1 | 23.1 | 0 | 2019-03-11 | 2.5 | 15.5 | 0 | 2018-03-11 | -3.1 | 21.1 | 0 | 2017-03-11 | -18.4 | 36.4 | 0 | 2016-03-11 | 0.4 | 17.6 | 0 | 19.43 | 0
2025-03-11 | 9.2 | 8.8 | 0 | 2024-03-11 | -1.4 | 19.4 | 0 | 2023-03-11 | -2 | 20 | 0 | 2022-03-11 | -3 | 21 | 0 | 2021-03-11 | 11 | 7 | 0 | 2020-03-11 | -4.6 | 22.6 | 0 | 2019-03-11 | 2.3 | 15.7 | 0 | 2018-03-11 | -1.9 | 19.9 | 0 | 2017-03-11 | -18.2 | 36.2 | 0 | 2016-03-11 | 0.7 | 17.3 | 0 | 18.79 | 0
2025-03-11 | 10.1 | 7.9 | 0 | 2024-03-11 | 0 | 18 | 0 | 2023-03-11 | -1 | 19 | 0 | 2022-03-11 | -2.6 | 20.6 | 0 | 2021-03-11 | 11.3 | 6.7 | 0 | 2020-03-11 | -3.8 | 21.8 | 0 | 2019-03-11 | 2.3 | 15.7 | 0 | 2018-03-11 | -1.3 | 19.3 | 0 | 2017-03-11 | -17.7 | 35.7 | 0 | 2016-03-11 | 1.2 | 16.8 | 0 | 18.15 | 0
2025-03-11 | 10.4 | 7.6 | 0 | 2024-03-11 | 2 | 16 | 0 | 2023-03-11 | 0.7 | 17.3 | 0 | 2022-03-11 | -1.3 | 19.3 | 0 | 2021-03-11 | 12.9 | 5.1 | 0 | 2020-03-11 | -3.4 | 21.4 | 0 | 2019-03-11 | 1.2 | 16.8 | 0 | 2018-03-11 | -1.3 | 19.3 | 0 | 2017-03-11 | -17.3 | 35.3 | 0 | 2016-03-11 | 2.2 | 15.8 | 0 | 17.39 | 0
2025-03-11 | 11 | 7 | 0 | 2024-03-11 | 3.4 | 14.6 | 0 | 2023-03-11 | 1.2 | 16.8 | 0 | 2022-03-11 | -1.1 | 19.1 | 0 | 2021-03-11 | 13.7 | 4.3 | 0 | 2020-03-11 | -3 | 21 | 0 | 2019-03-11 | 1.6 | 16.4 | 0 | 2018-03-11 | -0.5 | 18.5 | 0 | 2017-03-11 | -16.2 | 34.2 | 0 | 2016-03-11 | 3.1 | 14.9 | 0 | 16.68 | 0
2025-03-11 | 9.8 | 8.2 | 0 | 2024-03-11 | 4 | 14 | 0 | 2023-03-11 | 1.9 | 16.1 | 0 | 2022-03-11 | -1.2 | 19.2 | 0 | 2021-03-11 | 13.7 | 4.3 | 0 | 2020-03-11 | -2.5 | 20.5 | 0 | 2019-03-11 | 0.8 | 17.2 | 0 | 2018-03-11 | -0.3 | 18.3 | 0 | 2017-03-11 | -15.2 | 33.2 | 0 | 2016-03-11 | 3.2 | 14.8 | 0 | 16.58 | 0
2025-03-11 | 5.4 | 12.6 | 0 | 2024-03-11 | 4.4 | 13.6 | 0 | 2023-03-11 | 2 | 16 | 0 | 2022-03-11 | -2.2 | 20.2 | 0 | 2021-03-11 | 14.7 | 3.3 | 0 | 2020-03-11 | -1.9 | 19.9 | 0 | 2019-03-11 | 1.1 | 16.9 | 0 | 2018-03-11 | -0.6 | 18.6 | 0 | 2017-03-11 | -14.8 | 32.8 | 0 | 2016-03-11 | 3.1 | 14.9 | 0 | 16.88 | 0
2025-03-11 | 7.8 | 10.2 | 0 | 2024-03-11 | 4.9 | 13.1 | 0 | 2023-03-11 | 1.9 | 16.1 | 0 | 2022-03-11 | -2.2 | 20.2 | 0 | 2021-03-11 | 13.4 | 4.6 | 0 | 2020-03-11 | -1.7 | 19.7 | 0 | 2019-03-11 | 0.8 | 17.2 | 0 | 2018-03-11 | -0.1 | 18.1 | 0 | 2017-03-11 | -14.8 | 32.8 | 0 | 2016-03-11 | 2.6 | 15.4 | 0 | 16.74 | 0
2025-03-11 | 6.1 | 11.9 | 0 | 2024-03-11 | 4.5 | 13.5 | 0 | 2023-03-11 | 1.7 | 16.3 | 0 | 2022-03-11 | -2.3 | 20.3 | 0 | 2021-03-11 | 13.2 | 4.8 | 0 | 2020-03-11 | -1.7 | 19.7 | 0 | 2019-03-11 | 0.6 | 17.4 | 0 | 2018-03-11 | -0.4 | 18.4 | 0 | 2017-03-11 | -14.8 | 32.8 | 0 | 2016-03-11 | 2.3 | 15.7 | 0 | 17.08 | 0
2025-03-11 | 4.5 | 13.5 | 0 | 2024-03-11 | 3.4 | 14.6 | 0 | 2023-03-11 | -0.3 | 18.3 | 0 | 2022-03-11 | -2.3 | 20.3 | 0 | 2021-03-11 | 12.1 | 5.9 | 0 | 2020-03-11 | -2.3 | 20.3 | 0 | 2019-03-11 | -0.3 | 18.3 | 0 | 2018-03-11 | -0.6 | 18.6 | 0 | 2017-03-11 | -15.2 | 33.2 | 0 | 2016-03-11 | 1.1 | 16.9 | 0 | 17.99 | 0
2025-03-11 | 1.9 | 16.1 | 0 | 2024-03-11 | 2.8 | 15.2 | 0 | 2023-03-11 | -1.2 | 19.2 | 0 | 2022-03-11 | -2.2 | 20.2 | 0 | 2021-03-11 | 12.7 | 5.3 | 0 | 2020-03-11 | -2.6 | 20.6 | 0 | 2019-03-11 | -1.1 | 19.1 | 0 | 2018-03-11 | -1.8 | 19.8 | 0 | 2017-03-11 | -15.3 | 33.3 | 0 | 2016-03-11 | 0.9 | 17.1 | 0 | 18.59 | 0
2025-03-11 | 0.2 | 17.8 | 0 | 2024-03-11 | 0.2 | 17.8 | 0 | 2023-03-11 | -2.3 | 20.3 | 0 | 2022-03-11 | -2.4 | 20.4 | 0 | 2021-03-11 | 10.9 | 7.1 | 0 | 2020-03-11 | -2.8 | 20.8 | 0 | 2019-03-11 | -1.4 | 19.4 | 0 | 2018-03-11 | -2.7 | 20.7 | 0 | 2017-03-11 | -15.2 | 33.2 | 0 | 2016-03-11 | 0.3 | 17.7 | 0 | 19.52 | 0
2025-03-11 | -1.8 | 19.8 | 0 | 2024-03-11 | 0.6 | 17.4 | 0 | 2023-03-11 | -3.1 | 21.1 | 0 | 2022-03-11 | -2.3 | 20.3 | 0 | 2021-03-11 | 9.9 | 8.1 | 0 | 2020-03-11 | -2.8 | 20.8 | 0 | 2019-03-11 | -1.6 | 19.6 | 0 | 2018-03-11 | -2.2 | 20.2 | 0 | 2017-03-11 | -15.4 | 33.4 | 0 | 2016-03-11 | 0 | 18 | 0 | 19.87 | 0
2025-03-11 | -2.7 | 20.7 | 0 | 2024-03-11 | 0.6 | 17.4 | 0 | 2023-03-11 | -4.1 | 22.1 | 0 | 2022-03-11 | -2.4 | 20.4 | 0 | 2021-03-11 | 8.7 | 9.3 | 0 | 2020-03-11 | -3 | 21 | 0 | 2019-03-11 | -2.1 | 20.1 | 0 | 2018-03-11 | -1.1 | 19.1 | 0 | 2017-03-11 | -15.8 | 33.8 | 0 | 2016-03-11 | -1.6 | 19.6 | 0 | 20.35 | 0
2025-03-11 | -3.5 | 21.5 | 0 | 2024-03-11 | 1.5 | 16.5 | 0 | 2023-03-11 | -4.7 | 22.7 | 0 | 2022-03-11 | -2.3 | 20.3 | 0 | 2021-03-11 | 6.8 | 11.2 | 0 | 2020-03-11 | -2.7 | 20.7 | 0 | 2019-03-11 | -2 | 20 | 0 | 2018-03-11 | -1.8 | 19.8 | 0 | 2017-03-11 | -16 | 34 | 0 | 2016-03-11 | -1.7 | 19.7 | 0 | 20.64 | 0
2025-03-12 | -3.9 | 21.9 | 0 | 2024-03-12 | 1.7 | 16.3 | 0 | 2023-03-12 | -4.4 | 22.4 | 0 | 2022-03-12 | -2.4 | 20.4 | 0 | 2021-03-12 | 5.5 | 12.5 | 0 | 2020-03-12 | -2.9 | 20.9 | 0 | 2019-03-12 | -2.3 | 20.3 | 0 | 2018-03-12 | -2.4 | 20.4 | 0 | 2017-03-12 | -16.2 | 34.2 | 0 | 2016-03-12 | -2.3 | 20.3 | 0 | 20.96 | 0
2025-03-12 | -4.8 | 22.8 | 0 | 2024-03-12 | 1.4 | 16.6 | 0 | 2023-03-12 | -6.3 | 24.3 | 0 | 2022-03-12 | -2.5 | 20.5 | 0 | 2021-03-12 | 5 | 13 | 0 | 2020-03-12 | -3 | 21 | 0 | 2019-03-12 | -2.4 | 20.4 | 0 | 2018-03-12 | -2.6 | 20.6 | 0 | 2017-03-12 | -16.6 | 34.6 | 0 | 2016-03-12 | -2.1 | 20.1 | 0 | 21.39 | 0
2025-03-12 | -5.7 | 23.7 | 0 | 2024-03-12 | 0.9 | 17.1 | 0 | 2023-03-12 | -6.8 | 24.8 | 0 | 2022-03-12 | -2.5 | 20.5 | 0 | 2021-03-12 | 3.5 | 14.5 | 0 | 2020-03-12 | -3.1 | 21.1 | 0 | 2019-03-12 | -2.5 | 20.5 | 0 | 2018-03-12 | -3.3 | 21.3 | 0 | 2017-03-12 | -16.8 | 34.8 | 0 | 2016-03-12 | -2.8 | 20.8 | 0 | 21.91 | 0
2025-03-12 | -6.6 | 24.6 | 0 | 2024-03-12 | -1 | 19 | 0 | 2023-03-12 | -6.7 | 24.7 | 0 | 2022-03-12 | -2.4 | 20.4 | 0 | 2021-03-12 | 2.8 | 15.2 | 0 | 2020-03-12 | -3.1 | 21.1 | 0 | 2019-03-12 | -3.2 | 21.2 | 0 | 2018-03-12 | -3.4 | 21.4 | 0 | 2017-03-12 | -17.1 | 35.1 | 0 | 2016-03-12 | -2.4 | 20.4 | 0 | 22.31 | 0
2025-03-12 | -7 | 25 | 0 | 2024-03-12 | -1.2 | 19.2 | 0 | 2023-03-12 | -8 | 26 | 0 | 2022-03-12 | -2.2 | 20.2 | 0 | 2021-03-12 | 2.2 | 15.8 | 0 | 2020-03-12 | -3.2 | 21.2 | 0 | 2019-03-12 | -4.3 | 22.3 | 0 | 2018-03-12 | -3.8 | 21.8 | 0 | 2017-03-12 | -17.4 | 35.4 | 0 | 2016-03-12 | -2.7 | 20.7 | 0 | 22.76 | 0
2025-03-12 | -7.7 | 25.7 | 0 | 2024-03-12 | -2.8 | 20.8 | 0 | 2023-03-12 | -9 | 27 | 0 | 2022-03-12 | -3.7 | 21.7 | 0 | 2021-03-12 | 1.7 | 16.3 | 0 | 2020-03-12 | -3.3 | 21.3 | 0 | 2019-03-12 | -5.5 | 23.5 | 0 | 2018-03-12 | -4.8 | 22.8 | 0 | 2017-03-12 | -17.8 | 35.8 | 0 | 2016-03-12 | -2.6 | 20.6 | 0 | 23.55 | 0
2025-03-12 | -8 | 26 | 0 | 2024-03-12 | -1.8 | 19.8 | 0 | 2023-03-12 | -9.4 | 27.4 | 0 | 2022-03-12 | -4.3 | 22.3 | 0 | 2021-03-12 | 0.8 | 17.2 | 0 | 2020-03-12 | -3.3 | 21.3 | 0 | 2019-03-12 | -6.9 | 24.9 | 0 | 2018-03-12 | -6.2 | 24.2 | 0 | 2017-03-12 | -18 | 36 | 0 | 2016-03-12 | -2 | 20 | 0 | 23.91 | 0
2025-03-12 | -8.2 | 26.2 | 0 | 2024-03-12 | -2.4 | 20.4 | 0 | 2023-03-12 | -8.7 | 26.7 | 0 | 2022-03-12 | -4.1 | 22.1 | 0 | 2021-03-12 | 1.1 | 16.9 | 0 | 2020-03-12 | -3.3 | 21.3 | 0 | 2019-03-12 | -7 | 25 | 0 | 2018-03-12 | -5.6 | 23.6 | 0 | 2017-03-12 | -18.1 | 36.1 | 0 | 2016-03-12 | -1.2 | 19.2 | 0 | 23.75 | 0
2025-03-12 | -7.7 | 25.7 | 0 | 2024-03-12 | 0.9 | 17.1 | 0 | 2023-03-12 | -7 | 25 | 0 | 2022-03-12 | -4 | 22 | 0 | 2021-03-12 | 1.9 | 16.1 | 0 | 2020-03-12 | -3.2 | 21.2 | 0 | 2019-03-12 | -7.6 | 25.6 | 0 | 2018-03-12 | -5.6 | 23.6 | 0 | 2017-03-12 | -17.4 | 35.4 | 0 | 2016-03-12 | 0.2 | 17.8 | 0 | 22.95 | 0
2025-03-12 | -7 | 25 | 0 | 2024-03-12 | 2.8 | 15.2 | 0 | 2023-03-12 | -3.8 | 21.8 | 0 | 2022-03-12 | -4.3 | 22.3 | 0 | 2021-03-12 | 2.4 | 15.6 | 0 | 2020-03-12 | -2.7 | 20.7 | 0 | 2019-03-12 | -6.8 | 24.8 | 0 | 2018-03-12 | -2.8 | 20.8 | 0 | 2017-03-12 | -16.8 | 34.8 | 0 | 2016-03-12 | 1.3 | 16.7 | 0 | 21.77 | 0
2025-03-12 | -6.5 | 24.5 | 0 | 2024-03-12 | 4.7 | 13.3 | 0 | 2023-03-12 | -1.5 | 19.5 | 0 | 2022-03-12 | -5.1 | 23.1 | 0 | 2021-03-12 | 2.8 | 15.2 | 0 | 2020-03-12 | -1.7 | 19.7 | 0 | 2019-03-12 | -6 | 24 | 0 | 2018-03-12 | -1.2 | 19.2 | 0 | 2017-03-12 | -15.9 | 33.9 | 0 | 2016-03-12 | 3 | 15 | 0 | 20.74 | 0
2025-03-12 | -5.8 | 23.8 | 0 | 2024-03-12 | 5.6 | 12.4 | 0 | 2023-03-12 | -0.1 | 18.1 | 0 | 2022-03-12 | -6 | 24 | 0 | 2021-03-12 | 3.8 | 14.2 | 0 | 2020-03-12 | -1.4 | 19.4 | 0 | 2019-03-12 | -5 | 23 | 0 | 2018-03-12 | -0.7 | 18.7 | 0 | 2017-03-12 | -15 | 33 | 0 | 2016-03-12 | 4.6 | 13.4 | 0 | 20 | 0
2025-03-12 | -5 | 23 | 0 | 2024-03-12 | 7.2 | 10.8 | 0 | 2023-03-12 | 0.9 | 17.1 | 0 | 2022-03-12 | -6.2 | 24.2 | 0 | 2021-03-12 | 5.1 | 12.9 | 0 | 2020-03-12 | -0.4 | 18.4 | 0 | 2019-03-12 | -4 | 22 | 0 | 2018-03-12 | -0.4 | 18.4 | 0 | 2017-03-12 | -14 | 32 | 0 | 2016-03-12 | 6.8 | 11.2 | 0 | 19 | 0
2025-03-12 | -4.2 | 22.2 | 0 | 2024-03-12 | 9 | 9 | 0 | 2023-03-12 | 1.7 | 16.3 | 0 | 2022-03-12 | -6 | 24 | 0 | 2021-03-12 | 5.8 | 12.2 | 0 | 2020-03-12 | 0.4 | 17.6 | 0 | 2019-03-12 | -3 | 21 | 0 | 2018-03-12 | 0.7 | 17.3 | 0 | 2017-03-12 | -13.1 | 31.1 | 0 | 2016-03-12 | 8.2 | 9.8 | 0 | 18.05 | 0
2025-03-12 | -3.7 | 21.7 | 0 | 2024-03-12 | 9.7 | 8.3 | 0 | 2023-03-12 | 1.9 | 16.1 | 0 | 2022-03-12 | -6 | 24 | 0 | 2021-03-12 | 6.4 | 11.6 | 0 | 2020-03-12 | 1.1 | 16.9 | 0 | 2019-03-12 | -2.2 | 20.2 | 0 | 2018-03-12 | 1 | 17 | 0 | 2017-03-12 | -12.2 | 30.2 | 0 | 2016-03-12 | 9.5 | 8.5 | 0 | 17.45 | 0
2025-03-12 | -3.5 | 21.5 | 0 | 2024-03-12 | 10.4 | 7.6 | 0 | 2023-03-12 | 2.1 | 15.9 | 0 | 2022-03-12 | -5.3 | 23.3 | 0 | 2021-03-12 | 5.2 | 12.8 | 0 | 2020-03-12 | 1.4 | 16.6 | 0 | 2019-03-12 | -1.3 | 19.3 | 0 | 2018-03-12 | 1 | 17 | 0 | 2017-03-12 | -11.1 | 29.1 | 0 | 2016-03-12 | 9.9 | 8.1 | 0 | 17.12 | 0
2025-03-12 | -3.2 | 21.2 | 0 | 2024-03-12 | 11.3 | 6.7 | 0 | 2023-03-12 | 1.8 | 16.2 | 0 | 2022-03-12 | -5.1 | 23.1 | 0 | 2021-03-12 | 5.3 | 12.7 | 0 | 2020-03-12 | 1.6 | 16.4 | 0 | 2019-03-12 | -1 | 19 | 0 | 2018-03-12 | 0.9 | 17.1 | 0 | 2017-03-12 | -11.5 | 29.5 | 0 | 2016-03-12 | 10.1 | 7.9 | 0 | 16.98 | 0
2025-03-12 | -2.9 | 20.9 | 0 | 2024-03-12 | 10.4 | 7.6 | 0 | 2023-03-12 | 1.9 | 16.1 | 0 | 2022-03-12 | -5.3 | 23.3 | 0 | 2021-03-12 | 2.8 | 15.2 | 0 | 2020-03-12 | 1.7 | 16.3 | 0 | 2019-03-12 | -1.2 | 19.2 | 0 | 2018-03-12 | 0.6 | 17.4 | 0 | 2017-03-12 | -11.6 | 29.6 | 0 | 2016-03-12 | 9.8 | 8.2 | 0 | 17.38 | 0
2025-03-12 | -3.7 | 21.7 | 0 | 2024-03-12 | 7.8 | 10.2 | 0 | 2023-03-12 | 1.5 | 16.5 | 0 | 2022-03-12 | -6.6 | 24.6 | 0 | 2021-03-12 | 3.6 | 14.4 | 0 | 2020-03-12 | 1.1 | 16.9 | 0 | 2019-03-12 | -1.8 | 19.8 | 0 | 2018-03-12 | 0.4 | 17.6 | 0 | 2017-03-12 | -11.6 | 29.6 | 0 | 2016-03-12 | 7.8 | 10.2 | 0 | 18.15 | 0
2025-03-12 | -4.2 | 22.2 | 0 | 2024-03-12 | 6 | 12 | 0 | 2023-03-12 | 1.1 | 16.9 | 0 | 2022-03-12 | -7.4 | 25.4 | 0 | 2021-03-12 | -0.6 | 18.6 | 0 | 2020-03-12 | 0.6 | 17.4 | 0 | 2019-03-12 | -3.1 | 21.1 | 0 | 2018-03-12 | 0 | 18 | 0 | 2017-03-12 | -11.9 | 29.9 | 0 | 2016-03-12 | 6.8 | 11.2 | 0 | 19.27 | 0
2025-03-12 | -5 | 23 | 0 | 2024-03-12 | 5.8 | 12.2 | 0 | 2023-03-12 | 0.3 | 17.7 | 0 | 2022-03-12 | -7.7 | 25.7 | 0 | 2021-03-12 | -1.6 | 19.6 | 0 | 2020-03-12 | 0.3 | 17.7 | 0 | 2019-03-12 | -4.4 | 22.4 | 0 | 2018-03-12 | -0.3 | 18.3 | 0 | 2017-03-12 | -12.6 | 30.6 | 0 | 2016-03-12 | 5.9 | 12.1 | 0 | 19.93 | 0
2025-03-12 | -4.8 | 22.8 | 0 | 2024-03-12 | 2.6 | 15.4 | 0 | 2023-03-12 | 0.1 | 17.9 | 0 | 2022-03-12 | -8.1 | 26.1 | 0 | 2021-03-12 | -2.9 | 20.9 | 0 | 2020-03-12 | 0 | 18 | 0 | 2019-03-12 | -4.8 | 22.8 | 0 | 2018-03-12 | -0.4 | 18.4 | 0 | 2017-03-12 | -12.4 | 30.4 | 0 | 2016-03-12 | 4.8 | 13.2 | 0 | 20.59 | 0
2025-03-12 | -6.1 | 24.1 | 0 | 2024-03-12 | 0.7 | 17.3 | 0 | 2023-03-12 | 0.1 | 17.9 | 0 | 2022-03-12 | -8.7 | 26.7 | 0 | 2021-03-12 | -4.1 | 22.1 | 0 | 2020-03-12 | -0.3 | 18.3 | 0 | 2019-03-12 | -4.3 | 22.3 | 0 | 2018-03-12 | -0.6 | 18.6 | 0 | 2017-03-12 | -12.9 | 30.9 | 0 | 2016-03-12 | 4 | 14 | 0 | 21.22 | 0
2025-03-12 | -6.4 | 24.4 | 0 | 2024-03-12 | 2.3 | 15.7 | 0 | 2023-03-12 | -0.2 | 18.2 | 0 | 2022-03-12 | -9.2 | 27.2 | 0 | 2021-03-12 | -4.9 | 22.9 | 0 | 2020-03-12 | -0.3 | 18.3 | 0 | 2019-03-12 | -4.2 | 22.2 | 0 | 2018-03-12 | -1.1 | 19.1 | 0 | 2017-03-12 | -13.4 | 31.4 | 0 | 2016-03-12 | 4.4 | 13.6 | 0 | 21.3 | 0
2025-03-13 | -6.7 | 24.7 | 0 | 2024-03-13 | 2 | 16 | 0 | 2023-03-13 | -0.6 | 18.6 | 0 | 2022-03-13 | -9.6 | 27.6 | 0 | 2021-03-13 | -6 | 24 | 0 | 2020-03-13 | -0.1 | 18.1 | 0 | 2019-03-13 | -4.7 | 22.7 | 0 | 2018-03-13 | -1.3 | 19.3 | 0 | 2017-03-13 | -13.5 | 31.5 | 0 | 2016-03-13 | 6.1 | 11.9 | 0 | 21.44 | 0
2025-03-13 | -7.5 | 25.5 | 0 | 2024-03-13 | 2.1 | 15.9 | 0 | 2023-03-13 | -1 | 19 | 0 | 2022-03-13 | -9.9 | 27.9 | 0 | 2021-03-13 | -6.7 | 24.7 | 0 | 2020-03-13 | 0.1 | 17.9 | 0 | 2019-03-13 | -5.3 | 23.3 | 0 | 2018-03-13 | -1.2 | 19.2 | 0 | 2017-03-13 | -14 | 32 | 0 | 2016-03-13 | 4.7 | 13.3 | 0 | 21.87 | 0
2025-03-13 | -8.1 | 26.1 | 0 | 2024-03-13 | 0.8 | 17.2 | 0 | 2023-03-13 | -1 | 19 | 0 | 2022-03-13 | -10.3 | 28.3 | 0 | 2021-03-13 | -7.3 | 25.3 | 0 | 2020-03-13 | 0.6 | 17.4 | 0 | 2019-03-13 | -6 | 24 | 0 | 2018-03-13 | -1.2 | 19.2 | 0 | 2017-03-13 | -14.5 | 32.5 | 0 | 2016-03-13 | 3.4 | 14.6 | 0 | 22.36 | 0
2025-03-13 | -8.5 | 26.5 | 0 | 2024-03-13 | 0.5 | 17.5 | 0 | 2023-03-13 | -1.3 | 19.3 | 0 | 2022-03-13 | -10.9 | 28.9 | 0 | 2021-03-13 | -8.2 | 26.2 | 0 | 2020-03-13 | 0.7 | 17.3 | 0 | 2019-03-13 | -5.5 | 23.5 | 0 | 2018-03-13 | -1.2 | 19.2 | 0 | 2017-03-13 | -15.1 | 33.1 | 0 | 2016-03-13 | 3.6 | 14.4 | 0 | 22.59 | 0
2025-03-13 | -8.9 | 26.9 | 0 | 2024-03-13 | -0.5 | 18.5 | 0 | 2023-03-13 | -1.5 | 19.5 | 0 | 2022-03-13 | -11.4 | 29.4 | 0 | 2021-03-13 | -8.6 | 26.6 | 0 | 2020-03-13 | 0.6 | 17.4 | 0 | 2019-03-13 | -6 | 24 | 0 | 2018-03-13 | -1.1 | 19.1 | 0 | 2017-03-13 | -16.2 | 34.2 | 0 | 2016-03-13 | 3.4 | 14.6 | 0 | 23.02 | 0
2025-03-13 | -9 | 27 | 0 | 2024-03-13 | 0.4 | 17.6 | 0 | 2023-03-13 | -1.8 | 19.8 | 0 | 2022-03-13 | -12 | 30 | 0 | 2021-03-13 | -8.9 | 26.9 | 0 | 2020-03-13 | 1.2 | 16.8 | 0 | 2019-03-13 | -6.4 | 24.4 | 0 | 2018-03-13 | -0.9 | 18.9 | 0 | 2017-03-13 | -16 | 34 | 0 | 2016-03-13 | 2.3 | 15.7 | 0 | 23.11 | 0
2025-03-13 | -8.8 | 26.8 | 0 | 2024-03-13 | 0.3 | 17.7 | 0 | 2023-03-13 | -1.9 | 19.9 | 0 | 2022-03-13 | -12.5 | 30.5 | 0 | 2021-03-13 | -9.2 | 27.2 | 0 | 2020-03-13 | 1.3 | 16.7 | 0 | 2019-03-13 | -6.1 | 24.1 | 0 | 2018-03-13 | -0.9 | 18.9 | 0 | 2017-03-13 | -16.9 | 34.9 | 0 | 2016-03-13 | 1.1 | 16.9 | 0 | 23.36 | 0
2025-03-13 | -8.6 | 26.6 | 0 | 2024-03-13 | 0.6 | 17.4 | 0 | 2023-03-13 | -2.1 | 20.1 | 0 | 2022-03-13 | -12.7 | 30.7 | 0 | 2021-03-13 | -9.2 | 27.2 | 0 | 2020-03-13 | 2.3 | 15.7 | 0 | 2019-03-13 | -5.6 | 23.6 | 0 | 2018-03-13 | -1 | 19 | 0 | 2017-03-13 | -15.9 | 33.9 | 0 | 2016-03-13 | 1.2 | 16.8 | 0 | 23.1 | 0
2025-03-13 | -7.6 | 25.6 | 0 | 2024-03-13 | 1.2 | 16.8 | 0 | 2023-03-13 | -1.8 | 19.8 | 0 | 2022-03-13 | -11.7 | 29.7 | 0 | 2021-03-13 | -8.7 | 26.7 | 0 | 2020-03-13 | 3.5 | 14.5 | 0 | 2019-03-13 | -4 | 22 | 0 | 2018-03-13 | -0.8 | 18.8 | 0 | 2017-03-13 | -14.9 | 32.9 | 0 | 2016-03-13 | 2.7 | 15.3 | 0 | 22.21 | 0
2025-03-13 | -5.6 | 23.6 | 0 | 2024-03-13 | 1.6 | 16.4 | 0 | 2023-03-13 | -1.5 | 19.5 | 0 | 2022-03-13 | -10.3 | 28.3 | 0 | 2021-03-13 | -8.4 | 26.4 | 0 | 2020-03-13 | 6.4 | 11.6 | 0 | 2019-03-13 | -2.6 | 20.6 | 0 | 2018-03-13 | -0.5 | 18.5 | 0 | 2017-03-13 | -14 | 32 | 0 | 2016-03-13 | 3.5 | 14.5 | 0 | 21.14 | 0
2025-03-13 | -3.8 | 21.8 | 0 | 2024-03-13 | 3 | 15 | 0 | 2023-03-13 | -1 | 19 | 0 | 2022-03-13 | -8.9 | 26.9 | 0 | 2021-03-13 | -7.6 | 25.6 | 0 | 2020-03-13 | 6.8 | 11.2 | 0 | 2019-03-13 | -1.1 | 19.1 | 0 | 2018-03-13 | -0.4 | 18.4 | 0 | 2017-03-13 | -13 | 31 | 0 | 2016-03-13 | 4.4 | 13.6 | 0 | 20.16 | 0
2025-03-13 | -2 | 20 | 0 | 2024-03-13 | 5.1 | 12.9 | 0 | 2023-03-13 | -0.3 | 18.3 | 0 | 2022-03-13 | -8.1 | 26.1 | 0 | 2021-03-13 | -6.8 | 24.8 | 0 | 2020-03-13 | 6.8 | 11.2 | 0 | 2019-03-13 | -0.2 | 18.2 | 0 | 2018-03-13 | -0.5 | 18.5 | 0 | 2017-03-13 | -12.3 | 30.3 | 0 | 2016-03-13 | 5.4 | 12.6 | 0 | 19.29 | 0
2025-03-13 | -1 | 19 | 0 | 2024-03-13 | 6 | 12 | 0 | 2023-03-13 | 0.8 | 17.2 | 0 | 2022-03-13 | -6.7 | 24.7 | 0 | 2021-03-13 | -5 | 23 | 0 | 2020-03-13 | 6.3 | 11.7 | 0 | 2019-03-13 | 0.5 | 17.5 | 0 | 2018-03-13 | -0.6 | 18.6 | 0 | 2017-03-13 | -11.6 | 29.6 | 0 | 2016-03-13 | 6.7 | 11.3 | 0 | 18.46 | 0
2025-03-13 | 0.4 | 17.6 | 0 | 2024-03-13 | 7.6 | 10.4 | 0 | 2023-03-13 | 1.1 | 16.9 | 0 | 2022-03-13 | -5.3 | 23.3 | 0 | 2021-03-13 | -3.2 | 21.2 | 0 | 2020-03-13 | 6.4 | 11.6 | 0 | 2019-03-13 | 0.6 | 17.4 | 0 | 2018-03-13 | -0.8 | 18.8 | 0 | 2017-03-13 | -11.1 | 29.1 | 0 | 2016-03-13 | 7.1 | 10.9 | 0 | 17.72 | 0
2025-03-13 | 1.5 | 16.5 | 0 | 2024-03-13 | 8.2 | 9.8 | 0 | 2023-03-13 | 1.1 | 16.9 | 0 | 2022-03-13 | -4.3 | 22.3 | 0 | 2021-03-13 | -2.5 | 20.5 | 0 | 2020-03-13 | 6.3 | 11.7 | 0 | 2019-03-13 | 0.8 | 17.2 | 0 | 2018-03-13 | -1.2 | 19.2 | 0 | 2017-03-13 | -10.7 | 28.7 | 0 | 2016-03-13 | 7.6 | 10.4 | 0 | 17.32 | 0
2025-03-13 | 2.8 | 15.2 | 0 | 2024-03-13 | 9.3 | 8.7 | 0 | 2023-03-13 | 1.1 | 16.9 | 0 | 2022-03-13 | -3.8 | 21.8 | 0 | 2021-03-13 | -2.1 | 20.1 | 0 | 2020-03-13 | 4.8 | 13.2 | 0 | 2019-03-13 | 0.9 | 17.1 | 0 | 2018-03-13 | -1 | 19 | 0 | 2017-03-13 | -10.2 | 28.2 | 0 | 2016-03-13 | 8.1 | 9.9 | 0 | 17.01 | 0
2025-03-13 | 3.7 | 14.3 | 0 | 2024-03-13 | 10.2 | 7.8 | 0 | 2023-03-13 | 0.8 | 17.2 | 0 | 2022-03-13 | -3.5 | 21.5 | 0 | 2021-03-13 | -1.6 | 19.6 | 0 | 2020-03-13 | 4.2 | 13.8 | 0 | 2019-03-13 | -1.2 | 19.2 | 0 | 2018-03-13 | -1.7 | 19.7 | 0 | 2017-03-13 | -10.2 | 28.2 | 0 | 2016-03-13 | 7.4 | 10.6 | 0 | 17.19 | 0
2025-03-13 | 3.1 | 14.9 | 0 | 2024-03-13 | 8.2 | 9.8 | 0 | 2023-03-13 | 0.8 | 17.2 | 0 | 2022-03-13 | -3.8 | 21.8 | 0 | 2021-03-13 | -1.4 | 19.4 | 0 | 2020-03-13 | 3.9 | 14.1 | 0 | 2019-03-13 | -1.4 | 19.4 | 0 | 2018-03-13 | -1.7 | 19.7 | 0 | 2017-03-13 | -9.9 | 27.9 | 0 | 2016-03-13 | 5.1 | 12.9 | 0 | 17.71 | 0
2025-03-13 | 1 | 17 | 0 | 2024-03-13 | 6 | 12 | 0 | 2023-03-13 | 0.5 | 17.5 | 0 | 2022-03-13 | -4.9 | 22.9 | 0 | 2021-03-13 | -0.9 | 18.9 | 0 | 2020-03-13 | 3.5 | 14.5 | 0 | 2019-03-13 | -1.5 | 19.5 | 0 | 2018-03-13 | -1.6 | 19.6 | 0 | 2017-03-13 | -9.9 | 27.9 | 0 | 2016-03-13 | 4.7 | 13.3 | 0 | 18.31 | 0
2025-03-13 | 0.8 | 17.2 | 0 | 2024-03-13 | 4.7 | 13.3 | 0 | 2023-03-13 | 0.3 | 17.7 | 0 | 2022-03-13 | -4.9 | 22.9 | 0 | 2021-03-13 | -0.9 | 18.9 | 0 | 2020-03-13 | 3.1 | 14.9 | 0 | 2019-03-13 | -1.6 | 19.6 | 0 | 2018-03-13 | -1.5 | 19.5 | 0 | 2017-03-13 | -10.1 | 28.1 | 0 | 2016-03-13 | 3.8 | 14.2 | 0 | 18.63 | 0
2025-03-13 | 0.2 | 17.8 | 0 | 2024-03-13 | 4.2 | 13.8 | 0 | 2023-03-13 | 0.2 | 17.8 | 0 | 2022-03-13 | -4.7 | 22.7 | 0 | 2021-03-13 | -0.9 | 18.9 | 0 | 2020-03-13 | 3 | 15 | 0 | 2019-03-13 | -1.2 | 19.2 | 0 | 2018-03-13 | -1.4 | 19.4 | 0 | 2017-03-13 | -10.2 | 28.2 | 0 | 2016-03-13 | 3.4 | 14.6 | 0 | 18.74 | 0
2025-03-13 | -1.3 | 19.3 | 0 | 2024-03-13 | 2.5 | 15.5 | 0 | 2023-03-13 | 0.1 | 17.9 | 0 | 2022-03-13 | -4.8 | 22.8 | 0 | 2021-03-13 | -0.9 | 18.9 | 0 | 2020-03-13 | 2.8 | 15.2 | 0 | 2019-03-13 | -1 | 19 | 0 | 2018-03-13 | -1.4 | 19.4 | 0 | 2017-03-13 | -10.1 | 28.1 | 0 | 2016-03-13 | 2.9 | 15.1 | 0 | 19.12 | 0
2025-03-13 | -1.4 | 19.4 | 0 | 2024-03-13 | 2.1 | 15.9 | 0 | 2023-03-13 | -0.1 | 18.1 | 0 | 2022-03-13 | -5 | 23 | 0 | 2021-03-13 | -0.7 | 18.7 | 0 | 2020-03-13 | 2.6 | 15.4 | 0 | 2019-03-13 | -1.2 | 19.2 | 0 | 2018-03-13 | -1.4 | 19.4 | 0 | 2017-03-13 | -10.2 | 28.2 | 0 | 2016-03-13 | 2.3 | 15.7 | 0 | 19.3 | 0
2025-03-13 | -2.6 | 20.6 | 0 | 2024-03-13 | 1.9 | 16.1 | 0 | 2023-03-13 | -0.1 | 18.1 | 0 | 2022-03-13 | -5 | 23 | 0 | 2021-03-13 | -0.1 | 18.1 | 0 | 2020-03-13 | 2.3 | 15.7 | 0 | 2019-03-13 | -1.1 | 19.1 | 0 | 2018-03-13 | -1.3 | 19.3 | 0 | 2017-03-13 | -10.4 | 28.4 | 0 | 2016-03-13 | 1.7 | 16.3 | 0 | 19.47 | 0
2025-03-14 | -3.4 | 21.4 | 0 | 2024-03-14 | 1.9 | 16.1 | 0 | 2023-03-14 | 0 | 18 | 0 | 2022-03-14 | -4.7 | 22.7 | 0 | 2021-03-14 | -1.4 | 19.4 | 0 | 2020-03-14 | 2.2 | 15.8 | 0 | 2019-03-14 | -1.1 | 19.1 | 0 | 2018-03-14 | -1.3 | 19.3 | 0 | 2017-03-14 | -10.7 | 28.7 | 0 | 2016-03-14 | 1.6 | 16.4 | 0 | 19.69 | 0
2025-03-14 | -4.1 | 22.1 | 0 | 2024-03-14 | -0.8 | 18.8 | 0 | 2023-03-14 | 0 | 18 | 0 | 2022-03-14 | -4.1 | 22.1 | 0 | 2021-03-14 | -1.2 | 19.2 | 0 | 2020-03-14 | 2.2 | 15.8 | 0 | 2019-03-14 | -1 | 19 | 0 | 2018-03-14 | -1.3 | 19.3 | 0 | 2017-03-14 | -10.6 | 28.6 | 0 | 2016-03-14 | 1.5 | 16.5 | 0 | 19.94 | 0
2025-03-14 | -3.6 | 21.6 | 0 | 2024-03-14 | -0.3 | 18.3 | 0 | 2023-03-14 | 0 | 18 | 0 | 2022-03-14 | -3.4 | 21.4 | 0 | 2021-03-14 | -1.5 | 19.5 | 0 | 2020-03-14 | 1.6 | 16.4 | 0 | 2019-03-14 | -0.9 | 18.9 | 0 | 2018-03-14 | -1.5 | 19.5 | 0 | 2017-03-14 | -10.7 | 28.7 | 0 | 2016-03-14 | 1.2 | 16.8 | 0 | 19.91 | 0
2025-03-14 | -3.9 | 21.9 | 0 | 2024-03-14 | -1.6 | 19.6 | 0 | 2023-03-14 | 0.2 | 17.8 | 0 | 2022-03-14 | -3 | 21 | 0 | 2021-03-14 | -3.1 | 21.1 | 0 | 2020-03-14 | 1.1 | 16.9 | 0 | 2019-03-14 | -0.8 | 18.8 | 0 | 2018-03-14 | -1.6 | 19.6 | 0 | 2017-03-14 | -10.9 | 28.9 | 0 | 2016-03-14 | 0.8 | 17.2 | 0 | 20.28 | 0
2025-03-14 | -4.7 | 22.7 | 0 | 2024-03-14 | -0.2 | 18.2 | 0 | 2023-03-14 | 0.4 | 17.6 | 0 | 2022-03-14 | -2.9 | 20.9 | 0 | 2021-03-14 | -2.4 | 20.4 | 0 | 2020-03-14 | 1.1 | 16.9 | 0 | 2019-03-14 | -0.7 | 18.7 | 0 | 2018-03-14 | -1.7 | 19.7 | 0 | 2017-03-14 | -10.8 | 28.8 | 0 | 2016-03-14 | 0.6 | 17.4 | 0 | 20.13 | 0
2025-03-14 | -4.4 | 22.4 | 0 | 2024-03-14 | -0.8 | 18.8 | 0 | 2023-03-14 | 0.4 | 17.6 | 0 | 2022-03-14 | -2.4 | 20.4 | 0 | 2021-03-14 | -2.4 | 20.4 | 0 | 2020-03-14 | 1 | 17 | 0 | 2019-03-14 | -0.6 | 18.6 | 0 | 2018-03-14 | -1.7 | 19.7 | 0 | 2017-03-14 | -10.9 | 28.9 | 0 | 2016-03-14 | 0.4 | 17.6 | 0 | 20.14 | 0
2025-03-14 | -5.1 | 23.1 | 0 | 2024-03-14 | -1.8 | 19.8 | 0 | 2023-03-14 | 0.3 | 17.7 | 0 | 2022-03-14 | -2.2 | 20.2 | 0 | 2021-03-14 | -3 | 21 | 0 | 2020-03-14 | 1.1 | 16.9 | 0 | 2019-03-14 | -0.6 | 18.6 | 0 | 2018-03-14 | -1.6 | 19.6 | 0 | 2017-03-14 | -11.1 | 29.1 | 0 | 2016-03-14 | 0.1 | 17.9 | 0 | 20.39 | 0
2025-03-14 | -4.5 | 22.5 | 0 | 2024-03-14 | -2.2 | 20.2 | 0 | 2023-03-14 | 0.3 | 17.7 | 0 | 2022-03-14 | -2.4 | 20.4 | 0 | 2021-03-14 | -3.6 | 21.6 | 0 | 2020-03-14 | 1.1 | 16.9 | 0 | 2019-03-14 | -0.4 | 18.4 | 0 | 2018-03-14 | -1.5 | 19.5 | 0 | 2017-03-14 | -11.3 | 29.3 | 0 | 2016-03-14 | -0.1 | 18.1 | 0 | 20.46 | 0
2025-03-14 | -2.7 | 20.7 | 0 | 2024-03-14 | 1.9 | 16.1 | 0 | 2023-03-14 | 0.4 | 17.6 | 0 | 2022-03-14 | -2.5 | 20.5 | 0 | 2021-03-14 | -3 | 21 | 0 | 2020-03-14 | 1.2 | 16.8 | 0 | 2019-03-14 | 0.1 | 17.9 | 0 | 2018-03-14 | -1.3 | 19.3 | 0 | 2017-03-14 | -10.9 | 28.9 | 0 | 2016-03-14 | -0.2 | 18.2 | 0 | 19.7 | 0
2025-03-14 | 0.4 | 17.6 | 0 | 2024-03-14 | 5.3 | 12.7 | 0 | 2023-03-14 | 0.6 | 17.4 | 0 | 2022-03-14 | -1.2 | 19.2 | 0 | 2021-03-14 | -4.2 | 22.2 | 0 | 2020-03-14 | 1.5 | 16.5 | 0 | 2019-03-14 | 0.7 | 17.3 | 0 | 2018-03-14 | -0.9 | 18.9 | 0 | 2017-03-14 | -10.6 | 28.6 | 0 | 2016-03-14 | -0.2 | 18.2 | 0 | 18.86 | 0
2025-03-14 | 2.5 | 15.5 | 0 | 2024-03-14 | 7.8 | 10.2 | 0 | 2023-03-14 | 1 | 17 | 0 | 2022-03-14 | 0.2 | 17.8 | 0 | 2021-03-14 | -4.5 | 22.5 | 0 | 2020-03-14 | 1.9 | 16.1 | 0 | 2019-03-14 | 1.2 | 16.8 | 0 | 2018-03-14 | -0.4 | 18.4 | 0 | 2017-03-14 | -10.4 | 28.4 | 0 | 2016-03-14 | -0.5 | 18.5 | 0 | 18.12 | 0
2025-03-14 | 5.8 | 12.2 | 0 | 2024-03-14 | 9.2 | 8.8 | 0 | 2023-03-14 | 1.3 | 16.7 | 0 | 2022-03-14 | 0.8 | 17.2 | 0 | 2021-03-14 | -4.5 | 22.5 | 0 | 2020-03-14 | 2.3 | 15.7 | 0 | 2019-03-14 | 2.2 | 15.8 | 0 | 2018-03-14 | -0.1 | 18.1 | 0 | 2017-03-14 | -10.1 | 28.1 | 0 | 2016-03-14 | -0.1 | 18.1 | 0 | 17.32 | 0
2025-03-14 | 7.3 | 10.7 | 0 | 2024-03-14 | 11.1 | 6.9 | 0 | 2023-03-14 | 1.7 | 16.3 | 0 | 2022-03-14 | 2.8 | 15.2 | 0 | 2021-03-14 | -5 | 23 | 0 | 2020-03-14 | 2.9 | 15.1 | 0 | 2019-03-14 | 2.8 | 15.2 | 0 | 2018-03-14 | 0.1 | 17.9 | 0 | 2017-03-14 | -9.4 | 27.4 | 0 | 2016-03-14 | 0.1 | 17.9 | 0 | 16.56 | 0
2025-03-14 | 8.8 | 9.2 | 0 | 2024-03-14 | 11.9 | 6.1 | 0 | 2023-03-14 | 1.4 | 16.6 | 0 | 2022-03-14 | 3.8 | 14.2 | 0 | 2021-03-14 | -5.2 | 23.2 | 0 | 2020-03-14 | 3.1 | 14.9 | 0 | 2019-03-14 | 3.2 | 14.8 | 0 | 2018-03-14 | 0.5 | 17.5 | 0 | 2017-03-14 | -9.1 | 27.1 | 0 | 2016-03-14 | 0.5 | 17.5 | 0 | 16.11 | 0
2025-03-14 | 8.9 | 9.1 | 0 | 2024-03-14 | 12.4 | 5.6 | 0 | 2023-03-14 | 1.8 | 16.2 | 0 | 2022-03-14 | 4.9 | 13.1 | 0 | 2021-03-14 | -4 | 22 | 0 | 2020-03-14 | 3.8 | 14.2 | 0 | 2019-03-14 | 3.8 | 14.2 | 0 | 2018-03-14 | 0.9 | 17.1 | 0 | 2017-03-14 | -8.8 | 26.8 | 0 | 2016-03-14 | 1 | 17 | 0 | 15.53 | 0
2025-03-14 | 8.5 | 9.5 | 0 | 2024-03-14 | 12.6 | 5.4 | 0 | 2023-03-14 | 0.8 | 17.2 | 0 | 2022-03-14 | 4.6 | 13.4 | 0 | 2021-03-14 | -4.4 | 22.4 | 0 | 2020-03-14 | 3.9 | 14.1 | 0 | 2019-03-14 | 2.3 | 15.7 | 0 | 2018-03-14 | 0.5 | 17.5 | 0 | 2017-03-14 | -8.7 | 26.7 | 0 | 2016-03-14 | 0.8 | 17.2 | 0 | 15.91 | 0
2025-03-14 | 7.9 | 10.1 | 0 | 2024-03-14 | 12.3 | 5.7 | 0 | 2023-03-14 | 1.1 | 16.9 | 0 | 2022-03-14 | 4.3 | 13.7 | 0 | 2021-03-14 | -4.2 | 22.2 | 0 | 2020-03-14 | 4.2 | 13.8 | 0 | 2019-03-14 | 2.6 | 15.4 | 0 | 2018-03-14 | 0.4 | 17.6 | 0 | 2017-03-14 | -8.8 | 26.8 | 0 | 2016-03-14 | 1.3 | 16.7 | 0 | 15.89 | 0
2025-03-14 | 8.4 | 9.6 | 0 | 2024-03-14 | 11.6 | 6.4 | 0 | 2023-03-14 | 0.9 | 17.1 | 0 | 2022-03-14 | 4 | 14 | 0 | 2021-03-14 | -5.2 | 23.2 | 0 | 2020-03-14 | 3.6 | 14.4 | 0 | 2019-03-14 | 2.5 | 15.5 | 0 | 2018-03-14 | -0.2 | 18.2 | 0 | 2017-03-14 | -9.2 | 27.2 | 0 | 2016-03-14 | 1.6 | 16.4 | 0 | 16.2 | 0
2025-03-14 | 6.4 | 11.6 | 0 | 2024-03-14 | 10.3 | 7.7 | 0 | 2023-03-14 | 0.8 | 17.2 | 0 | 2022-03-14 | 3.9 | 14.1 | 0 | 2021-03-14 | -6.5 | 24.5 | 0 | 2020-03-14 | 3.1 | 14.9 | 0 | 2019-03-14 | 2.6 | 15.4 | 0 | 2018-03-14 | -0.8 | 18.8 | 0 | 2017-03-14 | -9.9 | 27.9 | 0 | 2016-03-14 | 1.9 | 16.1 | 0 | 16.82 | 0
2025-03-14 | 5.6 | 12.4 | 0 | 2024-03-14 | 9.8 | 8.2 | 0 | 2023-03-14 | 0.5 | 17.5 | 0 | 2022-03-14 | 2.4 | 15.6 | 0 | 2021-03-14 | -7.3 | 25.3 | 0 | 2020-03-14 | 2.2 | 15.8 | 0 | 2019-03-14 | 1.9 | 16.1 | 0 | 2018-03-14 | -1 | 19 | 0 | 2017-03-14 | -10.2 | 28.2 | 0 | 2016-03-14 | 2 | 16 | 0 | 17.41 | 0
2025-03-14 | 4.9 | 13.1 | 0 | 2024-03-14 | 9.1 | 8.9 | 0 | 2023-03-14 | 0 | 18 | 0 | 2022-03-14 | 1.9 | 16.1 | 0 | 2021-03-14 | -8.4 | 26.4 | 0 | 2020-03-14 | 2 | 16 | 0 | 2019-03-14 | 2.4 | 15.6 | 0 | 2018-03-14 | -1.4 | 19.4 | 0 | 2017-03-14 | -10.1 | 28.1 | 0 | 2016-03-14 | 1.9 | 16.1 | 0 | 17.77 | 0
2025-03-14 | 4.3 | 13.7 | 0 | 2024-03-14 | 8.7 | 9.3 | 0 | 2023-03-14 | -0.2 | 18.2 | 0 | 2022-03-14 | 1.4 | 16.6 | 0 | 2021-03-14 | -9.5 | 27.5 | 0 | 2020-03-14 | 1 | 17 | 0 | 2019-03-14 | 2.1 | 15.9 | 0 | 2018-03-14 | -1.9 | 19.9 | 0 | 2017-03-14 | -10 | 28 | 0 | 2016-03-14 | 1.9 | 16.1 | 0 | 18.22 | 0
2025-03-14 | 3.8 | 14.2 | 0 | 2024-03-14 | 7.8 | 10.2 | 0 | 2023-03-14 | -0.2 | 18.2 | 0 | 2022-03-14 | 1.4 | 16.6 | 0 | 2021-03-14 | -10 | 28 | 0 | 2020-03-14 | 0.1 | 17.9 | 0 | 2019-03-14 | 2.1 | 15.9 | 0 | 2018-03-14 | -2.2 | 20.2 | 0 | 2017-03-14 | -10.3 | 28.3 | 0 | 2016-03-14 | 1.8 | 16.2 | 0 | 18.57 | 0
2025-03-14 | 3.2 | 14.8 | 0 | 2024-03-14 | 7 | 11 | 0 | 2023-03-14 | -0.7 | 18.7 | 0 | 2022-03-14 | 1 | 17 | 0 | 2021-03-14 | -10.8 | 28.8 | 0 | 2020-03-14 | -1.4 | 19.4 | 0 | 2019-03-14 | 2.1 | 15.9 | 0 | 2018-03-14 | -2.4 | 20.4 | 0 | 2017-03-14 | -10.5 | 28.5 | 0 | 2016-03-14 | 1.7 | 16.3 | 0 | 19.08 | 0
2025-03-15 | 2.9 | 15.1 | 0 | 2024-03-15 | 6.1 | 11.9 | 0 | 2023-03-15 | -1.3 | 19.3 | 0 | 2022-03-15 | 0.8 | 17.2 | 0 | 2021-03-15 | -11.6 | 29.6 | 0 | 2020-03-15 | -2.2 | 20.2 | 0 | 2019-03-15 | 2.5 | 15.5 | 0 | 2018-03-15 | -2.5 | 20.5 | 0 | 2017-03-15 | -10.4 | 28.4 | 0 | 2016-03-15 | 1.7 | 16.3 | 0 | 19.4 | 0
2025-03-15 | 2.6 | 15.4 | 0 | 2024-03-15 | 5.7 | 12.3 | 0 | 2023-03-15 | -2 | 20 | 0 | 2022-03-15 | 0.4 | 17.6 | 0 | 2021-03-15 | -12.2 | 30.2 | 0 | 2020-03-15 | -3.2 | 21.2 | 0 | 2019-03-15 | 5.8 | 12.2 | 0 | 2018-03-15 | -2.4 | 20.4 | 0 | 2017-03-15 | -10.2 | 28.2 | 0 | 2016-03-15 | 1.9 | 16.1 | 0 | 19.36 | 0
2025-03-15 | 1.9 | 16.1 | 0 | 2024-03-15 | 5.6 | 12.4 | 0 | 2023-03-15 | -2.8 | 20.8 | 0 | 2022-03-15 | 0.2 | 17.8 | 0 | 2021-03-15 | -12.8 | 30.8 | 0 | 2020-03-15 | -4.3 | 22.3 | 0 | 2019-03-15 | 5.1 | 12.9 | 0 | 2018-03-15 | -2.4 | 20.4 | 0 | 2017-03-15 | -10.2 | 28.2 | 0 | 2016-03-15 | 1.9 | 16.1 | 0 | 19.78 | 0
2025-03-15 | 1.6 | 16.4 | 0 | 2024-03-15 | 5.4 | 12.6 | 0 | 2023-03-15 | -3.8 | 21.8 | 0 | 2022-03-15 | -0.6 | 18.6 | 0 | 2021-03-15 | -13.3 | 31.3 | 0 | 2020-03-15 | -5.3 | 23.3 | 0 | 2019-03-15 | 3.1 | 14.9 | 0 | 2018-03-15 | -2.4 | 20.4 | 0 | 2017-03-15 | -9.9 | 27.9 | 0 | 2016-03-15 | 1.8 | 16.2 | 0 | 20.34 | 0
2025-03-15 | 1.6 | 16.4 | 0 | 2024-03-15 | 4.9 | 13.1 | 0 | 2023-03-15 | -4.6 | 22.6 | 0 | 2022-03-15 | -1.2 | 19.2 | 0 | 2021-03-15 | -13.6 | 31.6 | 0 | 2020-03-15 | -6.2 | 24.2 | 0 | 2019-03-15 | 2.1 | 15.9 | 0 | 2018-03-15 | -2.3 | 20.3 | 0 | 2017-03-15 | -9.9 | 27.9 | 0 | 2016-03-15 | 1.7 | 16.3 | 0 | 20.75 | 0
2025-03-15 | 1.3 | 16.7 | 0 | 2024-03-15 | 4.4 | 13.6 | 0 | 2023-03-15 | -5.3 | 23.3 | 0 | 2022-03-15 | -2.1 | 20.1 | 0 | 2021-03-15 | -14 | 32 | 0 | 2020-03-15 | -7.3 | 25.3 | 0 | 2019-03-15 | 2.5 | 15.5 | 0 | 2018-03-15 | -2.5 | 20.5 | 0 | 2017-03-15 | -10.1 | 28.1 | 0 | 2016-03-15 | 1.8 | 16.2 | 0 | 21.13 | 0
2025-03-15 | 1 | 17 | 0 | 2024-03-15 | 4 | 14 | 0 | 2023-03-15 | -6.1 | 24.1 | 0 | 2022-03-15 | -2.7 | 20.7 | 0 | 2021-03-15 | -14.4 | 32.4 | 0 | 2020-03-15 | -8.2 | 26.2 | 0 | 2019-03-15 | 2.3 | 15.7 | 0 | 2018-03-15 | -2.6 | 20.6 | 0 | 2017-03-15 | -10.4 | 28.4 | 0 | 2016-03-15 | 1.4 | 16.6 | 0 | 21.57 | 0
2025-03-15 | 1.5 | 16.5 | 0 | 2024-03-15 | 4.4 | 13.6 | 0 | 2023-03-15 | -6.7 | 24.7 | 0 | 2022-03-15 | -3 | 21 | 0 | 2021-03-15 | -14.4 | 32.4 | 0 | 2020-03-15 | -8.6 | 26.6 | 0 | 2019-03-15 | 7.8 | 10.2 | 0 | 2018-03-15 | -2.8 | 20.8 | 0 | 2017-03-15 | -10.5 | 28.5 | 0 | 2016-03-15 | 1.6 | 16.4 | 0 | 21.07 | 0
2025-03-15 | 2.8 | 15.2 | 0 | 2024-03-15 | 5.2 | 12.8 | 0 | 2023-03-15 | -5.7 | 23.7 | 0 | 2022-03-15 | -1.5 | 19.5 | 0 | 2021-03-15 | -13.8 | 31.8 | 0 | 2020-03-15 | -8.4 | 26.4 | 0 | 2019-03-15 | 7.3 | 10.7 | 0 | 2018-03-15 | -2.5 | 20.5 | 0 | 2017-03-15 | -10.4 | 28.4 | 0 | 2016-03-15 | 2.3 | 15.7 | 0 | 20.47 | 0
2025-03-15 | 5.3 | 12.7 | 0 | 2024-03-15 | 7.1 | 10.9 | 0 | 2023-03-15 | -3.8 | 21.8 | 0 | 2022-03-15 | 0.2 | 17.8 | 0 | 2021-03-15 | -13.2 | 31.2 | 0 | 2020-03-15 | -7.5 | 25.5 | 0 | 2019-03-15 | 6.5 | 11.5 | 0 | 2018-03-15 | -1.6 | 19.6 | 0 | 2017-03-15 | -10 | 28 | 0 | 2016-03-15 | 2.5 | 15.5 | 0 | 19.45 | 0
2025-03-15 | 7.3 | 10.7 | 0 | 2024-03-15 | 8.4 | 9.6 | 0 | 2023-03-15 | -2.6 | 20.6 | 0 | 2022-03-15 | 1.4 | 16.6 | 0 | 2021-03-15 | -12.2 | 30.2 | 0 | 2020-03-15 | -6.7 | 24.7 | 0 | 2019-03-15 | 5.8 | 12.2 | 0 | 2018-03-15 | -0.3 | 18.3 | 0 | 2017-03-15 | -9.3 | 27.3 | 0 | 2016-03-15 | 3.3 | 14.7 | 0 | 18.49 | 0
2025-03-15 | 10.7 | 7.3 | 0 | 2024-03-15 | 9.2 | 8.8 | 0 | 2023-03-15 | -1 | 19 | 0 | 2022-03-15 | 2 | 16 | 0 | 2021-03-15 | -11.6 | 29.6 | 0 | 2020-03-15 | -5.7 | 23.7 | 0 | 2019-03-15 | 6.7 | 11.3 | 0 | 2018-03-15 | 0.9 | 17.1 | 0 | 2017-03-15 | -8.9 | 26.9 | 0 | 2016-03-15 | 3.5 | 14.5 | 0 | 17.42 | 0
2025-03-15 | 12.2 | 5.8 | 0 | 2024-03-15 | 9.1 | 8.9 | 0 | 2023-03-15 | 0.4 | 17.6 | 0 | 2022-03-15 | 2.2 | 15.8 | 0 | 2021-03-15 | -10.2 | 28.2 | 0 | 2020-03-15 | -4.8 | 22.8 | 0 | 2019-03-15 | 6.5 | 11.5 | 0 | 2018-03-15 | 1.4 | 16.6 | 0 | 2017-03-15 | -8.6 | 26.6 | 0 | 2016-03-15 | 3.9 | 14.1 | 0 | 16.79 | 0
2025-03-15 | 13.6 | 4.4 | 0 | 2024-03-15 | 10.7 | 7.3 | 0 | 2023-03-15 | 1.7 | 16.3 | 0 | 2022-03-15 | 2.5 | 15.5 | 0 | 2021-03-15 | -9 | 27 | 0 | 2020-03-15 | -3.4 | 21.4 | 0 | 2019-03-15 | 6.4 | 11.6 | 0 | 2018-03-15 | 1 | 17 | 0 | 2017-03-15 | -8.4 | 26.4 | 0 | 2016-03-15 | 3.6 | 14.4 | 0 | 16.13 | 0
2025-03-15 | 14.8 | 3.2 | 0 | 2024-03-15 | 10.8 | 7.2 | 0 | 2023-03-15 | 1.7 | 16.3 | 0 | 2022-03-15 | 2.7 | 15.3 | 0 | 2021-03-15 | -7.6 | 25.6 | 0 | 2020-03-15 | -2.7 | 20.7 | 0 | 2019-03-15 | 6 | 12 | 0 | 2018-03-15 | 0.8 | 17.2 | 0 | 2017-03-15 | -7.8 | 25.8 | 0 | 2016-03-15 | 3.6 | 14.4 | 0 | 15.77 | 0
2025-03-15 | 14.5 | 3.5 | 0 | 2024-03-15 | 10.5 | 7.5 | 0 | 2023-03-15 | 1.4 | 16.6 | 0 | 2022-03-15 | 2.7 | 15.3 | 0 | 2021-03-15 | -6.3 | 24.3 | 0 | 2020-03-15 | -2.5 | 20.5 | 0 | 2019-03-15 | 6.3 | 11.7 | 0 | 2018-03-15 | 0.4 | 17.6 | 0 | 2017-03-15 | -7.3 | 25.3 | 0 | 2016-03-15 | 3.7 | 14.3 | 0 | 15.66 | 0
2025-03-15 | 13.1 | 4.9 | 0 | 2024-03-15 | 10.5 | 7.5 | 0 | 2023-03-15 | 2.3 | 15.7 | 0 | 2022-03-15 | 2.7 | 15.3 | 0 | 2021-03-15 | -5.9 | 23.9 | 0 | 2020-03-15 | -2.1 | 20.1 | 0 | 2019-03-15 | 6.3 | 11.7 | 0 | 2018-03-15 | 0.5 | 17.5 | 0 | 2017-03-15 | -6.9 | 24.9 | 0 | 2016-03-15 | 3.8 | 14.2 | 0 | 15.57 | 0
2025-03-15 | 13.7 | 4.3 | 0 | 2024-03-15 | 9.4 | 8.6 | 0 | 2023-03-15 | 2.7 | 15.3 | 0 | 2022-03-15 | 2.4 | 15.6 | 0 | 2021-03-15 | -5.8 | 23.8 | 0 | 2020-03-15 | -2 | 20 | 0 | 2019-03-15 | 5.6 | 12.4 | 0 | 2018-03-15 | 0.2 | 17.8 | 0 | 2017-03-15 | -6.5 | 24.5 | 0 | 2016-03-15 | 3.9 | 14.1 | 0 | 15.64 | 0
2025-03-15 | 10.1 | 7.9 | 0 | 2024-03-15 | 7.9 | 10.1 | 0 | 2023-03-15 | 1.4 | 16.6 | 0 | 2022-03-15 | 1.8 | 16.2 | 0 | 2021-03-15 | -6.1 | 24.1 | 0 | 2020-03-15 | -2.5 | 20.5 | 0 | 2019-03-15 | 4.8 | 13.2 | 0 | 2018-03-15 | -0.3 | 18.3 | 0 | 2017-03-15 | -6.6 | 24.6 | 0 | 2016-03-15 | 3.5 | 14.5 | 0 | 16.6 | 0
2025-03-15 | 10.6 | 7.4 | 0 | 2024-03-15 | 7 | 11 | 0 | 2023-03-15 | 0.6 | 17.4 | 0 | 2022-03-15 | 0.3 | 17.7 | 0 | 2021-03-15 | -6.9 | 24.9 | 0 | 2020-03-15 | -3.2 | 21.2 | 0 | 2019-03-15 | 4 | 14 | 0 | 2018-03-15 | -0.8 | 18.8 | 0 | 2017-03-15 | -6.2 | 24.2 | 0 | 2016-03-15 | 3.5 | 14.5 | 0 | 17.11 | 0
2025-03-15 | 10.9 | 7.1 | 0 | 2024-03-15 | 7 | 11 | 0 | 2023-03-15 | -0.2 | 18.2 | 0 | 2022-03-15 | -0.8 | 18.8 | 0 | 2021-03-15 | -7.5 | 25.5 | 0 | 2020-03-15 | -3.8 | 21.8 | 0 | 2019-03-15 | 3.7 | 14.3 | 0 | 2018-03-15 | -1.4 | 19.4 | 0 | 2017-03-15 | -6.6 | 24.6 | 0 | 2016-03-15 | 3.4 | 14.6 | 0 | 17.53 | 0
2025-03-15 | 10.5 | 7.5 | 0 | 2024-03-15 | 5.2 | 12.8 | 0 | 2023-03-15 | 0 | 18 | 0 | 2022-03-15 | -2.3 | 20.3 | 0 | 2021-03-15 | -7.6 | 25.6 | 0 | 2020-03-15 | -4.1 | 22.1 | 0 | 2019-03-15 | 3.2 | 14.8 | 0 | 2018-03-15 | -2.2 | 20.2 | 0 | 2017-03-15 | -7.1 | 25.1 | 0 | 2016-03-15 | 3.5 | 14.5 | 0 | 18.09 | 0
2025-03-15 | 5.5 | 12.5 | 0 | 2024-03-15 | 3.9 | 14.1 | 0 | 2023-03-15 | -0.2 | 18.2 | 0 | 2022-03-15 | -1.4 | 19.4 | 0 | 2021-03-15 | -9.1 | 27.1 | 0 | 2020-03-15 | -5.2 | 23.2 | 0 | 2019-03-15 | 3 | 15 | 0 | 2018-03-15 | -2.7 | 20.7 | 0 | 2017-03-15 | -7.6 | 25.6 | 0 | 2016-03-15 | 3.2 | 14.8 | 0 | 19.06 | 0
2025-03-15 | 9 | 9 | 0 | 2024-03-15 | 2.7 | 15.3 | 0 | 2023-03-15 | -0.4 | 18.4 | 0 | 2022-03-15 | -1.5 | 19.5 | 0 | 2021-03-15 | -10.3 | 28.3 | 0 | 2020-03-15 | -5.5 | 23.5 | 0 | 2019-03-15 | 3 | 15 | 0 | 2018-03-15 | -3.5 | 21.5 | 0 | 2017-03-15 | -8.3 | 26.3 | 0 | 2016-03-15 | 3.5 | 14.5 | 0 | 19.13 | 0
2025-03-16 | 10.2 | 7.8 | 0 | 2024-03-16 | 0.9 | 17.1 | 0 | 2023-03-16 | 0.1 | 17.9 | 0 | 2022-03-16 | -1.9 | 19.9 | 0 | 2021-03-16 | -9.1 | 27.1 | 0 | 2020-03-16 | -6.3 | 24.3 | 0 | 2019-03-16 | 1.9 | 16.1 | 0 | 2018-03-16 | -4.1 | 22.1 | 0 | 2017-03-16 | -8.7 | 26.7 | 0 | 2016-03-16 | 3.4 | 14.6 | 0 | 19.36 | 0
2025-03-16 | 9.2 | 8.8 | 0 | 2024-03-16 | 0.7 | 17.3 | 0 | 2023-03-16 | -0.4 | 18.4 | 0 | 2022-03-16 | -1.7 | 19.7 | 0 | 2021-03-16 | -9.3 | 27.3 | 0 | 2020-03-16 | -7.7 | 25.7 | 0 | 2019-03-16 | 2 | 16 | 0 | 2018-03-16 | -5.4 | 23.4 | 0 | 2017-03-16 | -8.9 | 26.9 | 0 | 2016-03-16 | 3.8 | 14.2 | 0 | 19.77 | 0
2025-03-16 | 8.8 | 9.2 | 0 | 2024-03-16 | 0.5 | 17.5 | 0 | 2023-03-16 | 0.5 | 17.5 | 0 | 2022-03-16 | -2.2 | 20.2 | 0 | 2021-03-16 | -9.8 | 27.8 | 0 | 2020-03-16 | -8.1 | 26.1 | 0 | 2019-03-16 | 1.3 | 16.7 | 0 | 2018-03-16 | -6.3 | 24.3 | 0 | 2017-03-16 | -9.8 | 27.8 | 0 | 2016-03-16 | 3.7 | 14.3 | 0 | 20.14 | 0
2025-03-16 | 8.4 | 9.6 | 0 | 2024-03-16 | -0.8 | 18.8 | 0 | 2023-03-16 | -0.3 | 18.3 | 0 | 2022-03-16 | -2.5 | 20.5 | 0 | 2021-03-16 | -9.7 | 27.7 | 0 | 2020-03-16 | -8.7 | 26.7 | 0 | 2019-03-16 | 1.1 | 16.9 | 0 | 2018-03-16 | -7 | 25 | 0 | 2017-03-16 | -9.9 | 27.9 | 0 | 2016-03-16 | 3.7 | 14.3 | 0 | 20.57 | 0
2025-03-16 | 8.7 | 9.3 | 0 | 2024-03-16 | -2.2 | 20.2 | 0 | 2023-03-16 | -0.5 | 18.5 | 0 | 2022-03-16 | -2.2 | 20.2 | 0 | 2021-03-16 | -9.8 | 27.8 | 0 | 2020-03-16 | -9.1 | 27.1 | 0 | 2019-03-16 | 0.7 | 17.3 | 0 | 2018-03-16 | -8.1 | 26.1 | 0 | 2017-03-16 | -10.2 | 28.2 | 0 | 2016-03-16 | 3.7 | 14.3 | 0 | 20.9 | 0
2025-03-16 | 8.2 | 9.8 | 0 | 2024-03-16 | -2.5 | 20.5 | 0 | 2023-03-16 | -0.4 | 18.4 | 0 | 2022-03-16 | -2.3 | 20.3 | 0 | 2021-03-16 | -10.2 | 28.2 | 0 | 2020-03-16 | -9.4 | 27.4 | 0 | 2019-03-16 | 0.1 | 17.9 | 0 | 2018-03-16 | -9 | 27 | 0 | 2017-03-16 | -10.4 | 28.4 | 0 | 2016-03-16 | 3.3 | 14.7 | 0 | 21.26 | 0
2025-03-16 | 8.5 | 9.5 | 0 | 2024-03-16 | -2.2 | 20.2 | 0 | 2023-03-16 | -0.5 | 18.5 | 0 | 2022-03-16 | -2.5 | 20.5 | 0 | 2021-03-16 | -10.1 | 28.1 | 0 | 2020-03-16 | -9.9 | 27.9 | 0 | 2019-03-16 | -1.9 | 19.9 | 0 | 2018-03-16 | -9.1 | 27.1 | 0 | 2017-03-16 | -11.3 | 29.3 | 0 | 2016-03-16 | 3.3 | 14.7 | 0 | 21.57 | 0
2025-03-16 | 7.8 | 10.2 | 0 | 2024-03-16 | -2.2 | 20.2 | 0 | 2023-03-16 | -0.5 | 18.5 | 0 | 2022-03-16 | -1.8 | 19.8 | 0 | 2021-03-16 | -10 | 28 | 0 | 2020-03-16 | -9.7 | 27.7 | 0 | 2019-03-16 | -3.6 | 21.6 | 0 | 2018-03-16 | -9.4 | 27.4 | 0 | 2017-03-16 | -11.8 | 29.8 | 0 | 2016-03-16 | 3.5 | 14.5 | 0 | 21.77 | 0
2025-03-16 | 8.2 | 9.8 | 0 | 2024-03-16 | 0 | 18 | 0 | 2023-03-16 | 0.4 | 17.6 | 0 | 2022-03-16 | 0.8 | 17.2 | 0 | 2021-03-16 | -7.2 | 25.2 | 0 | 2020-03-16 | -8.5 | 26.5 | 0 | 2019-03-16 | -3.9 | 21.9 | 0 | 2018-03-16 | -9.6 | 27.6 | 0 | 2017-03-16 | -11.1 | 29.1 | 0 | 2016-03-16 | 4.2 | 13.8 | 0 | 20.67 | 0
2025-03-16 | 9.2 | 8.8 | 0 | 2024-03-16 | 1.4 | 16.6 | 0 | 2023-03-16 | 1.1 | 16.9 | 0 | 2022-03-16 | 2.1 | 15.9 | 0 | 2021-03-16 | -5 | 23 | 0 | 2020-03-16 | -7.2 | 25.2 | 0 | 2019-03-16 | -3.9 | 21.9 | 0 | 2018-03-16 | -9.7 | 27.7 | 0 | 2017-03-16 | -10.3 | 28.3 | 0 | 2016-03-16 | 5 | 13 | 0 | 19.73 | 0
2025-03-16 | 10.5 | 7.5 | 0 | 2024-03-16 | 3 | 15 | 0 | 2023-03-16 | 1.3 | 16.7 | 0 | 2022-03-16 | 2.8 | 15.2 | 0 | 2021-03-16 | -3.5 | 21.5 | 0 | 2020-03-16 | -6.5 | 24.5 | 0 | 2019-03-16 | -4 | 22 | 0 | 2018-03-16 | -8.8 | 26.8 | 0 | 2017-03-16 | -9.1 | 27.1 | 0 | 2016-03-16 | 5.7 | 12.3 | 0 | 18.86 | 0
2025-03-16 | 12.1 | 5.9 | 0 | 2024-03-16 | 4 | 14 | 0 | 2023-03-16 | -0.6 | 18.6 | 0 | 2022-03-16 | 3.7 | 14.3 | 0 | 2021-03-16 | -2.2 | 20.2 | 0 | 2020-03-16 | -5.2 | 23.2 | 0 | 2019-03-16 | -3.1 | 21.1 | 0 | 2018-03-16 | -7.7 | 25.7 | 0 | 2017-03-16 | -7.8 | 25.8 | 0 | 2016-03-16 | 6.3 | 11.7 | 0 | 18.05 | 0
2025-03-16 | 12.2 | 5.8 | 0 | 2024-03-16 | 5.6 | 12.4 | 0 | 2023-03-16 | -0.4 | 18.4 | 0 | 2022-03-16 | 4.1 | 13.9 | 0 | 2021-03-16 | -1.4 | 19.4 | 0 | 2020-03-16 | -3.8 | 21.8 | 0 | 2019-03-16 | -3 | 21 | 0 | 2018-03-16 | -6.8 | 24.8 | 0 | 2017-03-16 | -6.5 | 24.5 | 0 | 2016-03-16 | 6.8 | 11.2 | 0 | 17.32 | 0
2025-03-16 | 12.3 | 5.7 | 0 | 2024-03-16 | 5.9 | 12.1 | 0 | 2023-03-16 | -0.1 | 18.1 | 0 | 2022-03-16 | 4.3 | 13.7 | 0 | 2021-03-16 | 0.1 | 17.9 | 0 | 2020-03-16 | -3 | 21 | 0 | 2019-03-16 | -2.6 | 20.6 | 0 | 2018-03-16 | -6.4 | 24.4 | 0 | 2017-03-16 | -5.4 | 23.4 | 0 | 2016-03-16 | 7.5 | 10.5 | 0 | 16.74 | 0
2025-03-16 | 14.5 | 3.5 | 0 | 2024-03-16 | 6.3 | 11.7 | 0 | 2023-03-16 | 0.6 | 17.4 | 0 | 2022-03-16 | 5.2 | 12.8 | 0 | 2021-03-16 | 0.7 | 17.3 | 0 | 2020-03-16 | -1.9 | 19.9 | 0 | 2019-03-16 | -1.3 | 19.3 | 0 | 2018-03-16 | -5.8 | 23.8 | 0 | 2017-03-16 | -4.4 | 22.4 | 0 | 2016-03-16 | 7 | 11 | 0 | 15.91 | 0
2025-03-16 | 16.1 | 1.9 | 0 | 2024-03-16 | 5.6 | 12.4 | 0 | 2023-03-16 | 1.4 | 16.6 | 0 | 2022-03-16 | 5.1 | 12.9 | 0 | 2021-03-16 | 1.7 | 16.3 | 0 | 2020-03-16 | -1.3 | 19.3 | 0 | 2019-03-16 | -1.1 | 19.1 | 0 | 2018-03-16 | -5.6 | 23.6 | 0 | 2017-03-16 | -3.4 | 21.4 | 0 | 2016-03-16 | 6.8 | 11.2 | 0 | 15.47 | 0
2025-03-16 | 14.6 | 3.4 | 0 | 2024-03-16 | 4.8 | 13.2 | 0 | 2023-03-16 | 2 | 16 | 0 | 2022-03-16 | 5 | 13 | 0 | 2021-03-16 | 2.4 | 15.6 | 0 | 2020-03-16 | -1.5 | 19.5 | 0 | 2019-03-16 | -1.1 | 19.1 | 0 | 2018-03-16 | -4.9 | 22.9 | 0 | 2017-03-16 | -2.7 | 20.7 | 0 | 2016-03-16 | 5.5 | 12.5 | 0 | 15.59 | 0
2025-03-16 | 13.4 | 4.6 | 0 | 2024-03-16 | 4.1 | 13.9 | 0 | 2023-03-16 | 1.9 | 16.1 | 0 | 2022-03-16 | 4.2 | 13.8 | 0 | 2021-03-16 | 2.9 | 15.1 | 0 | 2020-03-16 | -1.4 | 19.4 | 0 | 2019-03-16 | -1.8 | 19.8 | 0 | 2018-03-16 | -4.6 | 22.6 | 0 | 2017-03-16 | -2.2 | 20.2 | 0 | 2016-03-16 | 4.6 | 13.4 | 0 | 15.89 | 0
2025-03-16 | 11.9 | 6.1 | 0 | 2024-03-16 | 2.5 | 15.5 | 0 | 2023-03-16 | 1.7 | 16.3 | 0 | 2022-03-16 | 3.3 | 14.7 | 0 | 2021-03-16 | 1.5 | 16.5 | 0 | 2020-03-16 | -2 | 20 | 0 | 2019-03-16 | -2.4 | 20.4 | 0 | 2018-03-16 | -4.8 | 22.8 | 0 | 2017-03-16 | -2.8 | 20.8 | 0 | 2016-03-16 | 4.1 | 13.9 | 0 | 16.7 | 0
2025-03-16 | 11.1 | 6.9 | 0 | 2024-03-16 | 1.1 | 16.9 | 0 | 2023-03-16 | 1.4 | 16.6 | 0 | 2022-03-16 | 2.8 | 15.2 | 0 | 2021-03-16 | 0.7 | 17.3 | 0 | 2020-03-16 | -2.2 | 20.2 | 0 | 2019-03-16 | -3.2 | 21.2 | 0 | 2018-03-16 | -4.9 | 22.9 | 0 | 2017-03-16 | -3.5 | 21.5 | 0 | 2016-03-16 | 3.7 | 14.3 | 0 | 17.3 | 0
2025-03-16 | 10.4 | 7.6 | 0 | 2024-03-16 | 1.3 | 16.7 | 0 | 2023-03-16 | 1.3 | 16.7 | 0 | 2022-03-16 | 2.3 | 15.7 | 0 | 2021-03-16 | -2 | 20 | 0 | 2020-03-16 | -2.4 | 20.4 | 0 | 2019-03-16 | -3.8 | 21.8 | 0 | 2018-03-16 | -5.7 | 23.7 | 0 | 2017-03-16 | -4.4 | 22.4 | 0 | 2016-03-16 | 3.4 | 14.6 | 0 | 17.96 | 0
2025-03-16 | 9.4 | 8.6 | 0 | 2024-03-16 | 2.5 | 15.5 | 0 | 2023-03-16 | 1 | 17 | 0 | 2022-03-16 | 2.2 | 15.8 | 0 | 2021-03-16 | -2.3 | 20.3 | 0 | 2020-03-16 | -2.6 | 20.6 | 0 | 2019-03-16 | -4.6 | 22.6 | 0 | 2018-03-16 | -7.2 | 25.2 | 0 | 2017-03-16 | -5.5 | 23.5 | 0 | 2016-03-16 | 3.2 | 14.8 | 0 | 18.39 | 0
2025-03-16 | 8.6 | 9.4 | 0 | 2024-03-16 | 3.4 | 14.6 | 0 | 2023-03-16 | 0.8 | 17.2 | 0 | 2022-03-16 | 1.9 | 16.1 | 0 | 2021-03-16 | -1.7 | 19.7 | 0 | 2020-03-16 | -3.2 | 21.2 | 0 | 2019-03-16 | -5.3 | 23.3 | 0 | 2018-03-16 | -8.1 | 26.1 | 0 | 2017-03-16 | -6.9 | 24.9 | 0 | 2016-03-16 | 3.1 | 14.9 | 0 | 18.74 | 0
2025-03-16 | 7.5 | 10.5 | 0 | 2024-03-16 | 3.4 | 14.6 | 0 | 2023-03-16 | 0.7 | 17.3 | 0 | 2022-03-16 | 1 | 17 | 0 | 2021-03-16 | -2 | 20 | 0 | 2020-03-16 | -3.6 | 21.6 | 0 | 2019-03-16 | -5.5 | 23.5 | 0 | 2018-03-16 | -8.8 | 26.8 | 0 | 2017-03-16 | -6.4 | 24.4 | 0 | 2016-03-16 | 2.8 | 15.2 | 0 | 19.09 | 0
2025-03-17 | 5.3 | 12.7 | 0 | 2024-03-17 | 3.1 | 14.9 | 0 | 2023-03-17 | 0.3 | 17.7 | 0 | 2022-03-17 | 0.2 | 17.8 | 0 | 2021-03-17 | -3.1 | 21.1 | 0 | 2020-03-17 | -3.2 | 21.2 | 0 | 2019-03-17 | -6.6 | 24.6 | 0 | 2018-03-17 | -9.4 | 27.4 | 0 | 2017-03-17 | -5.7 | 23.7 | 0 | 2016-03-17 | 2.7 | 15.3 | 0 | 19.64 | 0
2025-03-17 | 4.4 | 13.6 | 0 | 2024-03-17 | 2.7 | 15.3 | 0 | 2023-03-17 | 0.4 | 17.6 | 0 | 2022-03-17 | 0 | 18 | 0 | 2021-03-17 | -3.2 | 21.2 | 0 | 2020-03-17 | -3 | 21 | 0 | 2019-03-17 | -6.7 | 24.7 | 0 | 2018-03-17 | -9.2 | 27.2 | 0 | 2017-03-17 | -5.8 | 23.8 | 0 | 2016-03-17 | 2.8 | 15.2 | 0 | 19.76 | 0
2025-03-17 | 2.8 | 15.2 | 0 | 2024-03-17 | 2.3 | 15.7 | 0 | 2023-03-17 | 0.4 | 17.6 | 0 | 2022-03-17 | 0 | 18 | 0 | 2021-03-17 | -4 | 22 | 0 | 2020-03-17 | -2.3 | 20.3 | 0 | 2019-03-17 | -6.5 | 24.5 | 0 | 2018-03-17 | -9.2 | 27.2 | 0 | 2017-03-17 | -7.4 | 25.4 | 0 | 2016-03-17 | 3.7 | 14.3 | 0 | 20.02 | 0
2025-03-17 | 2.7 | 15.3 | 0 | 2024-03-17 | 2.8 | 15.2 | 0 | 2023-03-17 | 0 | 18 | 0 | 2022-03-17 | 0.4 | 17.6 | 0 | 2021-03-17 | -4.8 | 22.8 | 0 | 2020-03-17 | -0.2 | 18.2 | 0 | 2019-03-17 | -6.7 | 24.7 | 0 | 2018-03-17 | -9.5 | 27.5 | 0 | 2017-03-17 | -8.2 | 26.2 | 0 | 2016-03-17 | 2.7 | 15.3 | 0 | 20.08 | 0
2025-03-17 | 1.7 | 16.3 | 0 | 2024-03-17 | 2.9 | 15.1 | 0 | 2023-03-17 | -0.1 | 18.1 | 0 | 2022-03-17 | 1.1 | 16.9 | 0 | 2021-03-17 | -6 | 24 | 0 | 2020-03-17 | -2 | 20 | 0 | 2019-03-17 | -7.6 | 25.6 | 0 | 2018-03-17 | -10.1 | 28.1 | 0 | 2017-03-17 | -10.2 | 28.2 | 0 | 2016-03-17 | 2.3 | 15.7 | 0 | 20.8 | 0
2025-03-17 | 1.6 | 16.4 | 0 | 2024-03-17 | 2.9 | 15.1 | 0 | 2023-03-17 | 0.1 | 17.9 | 0 | 2022-03-17 | 1.3 | 16.7 | 0 | 2021-03-17 | -4 | 22 | 0 | 2020-03-17 | -1 | 19 | 0 | 2019-03-17 | -8.1 | 26.1 | 0 | 2018-03-17 | -8.3 | 26.3 | 0 | 2017-03-17 | -11.2 | 29.2 | 0 | 2016-03-17 | 1.8 | 16.2 | 0 | 20.49 | 0
2025-03-17 | -0.1 | 18.1 | 0 | 2024-03-17 | 2 | 16 | 0 | 2023-03-17 | 0.1 | 17.9 | 0 | 2022-03-17 | 1.1 | 16.9 | 0 | 2021-03-17 | -3.4 | 21.4 | 0 | 2020-03-17 | 0.4 | 17.6 | 0 | 2019-03-17 | -9.1 | 27.1 | 0 | 2018-03-17 | -9.1 | 27.1 | 0 | 2017-03-17 | -11.1 | 29.1 | 0 | 2016-03-17 | 1.9 | 16.1 | 0 | 20.73 | 0
2025-03-17 | -1.6 | 19.6 | 0 | 2024-03-17 | 2 | 16 | 0 | 2023-03-17 | 0.5 | 17.5 | 0 | 2022-03-17 | 1.1 | 16.9 | 0 | 2021-03-17 | -3.6 | 21.6 | 0 | 2020-03-17 | 1.2 | 16.8 | 0 | 2019-03-17 | -8.5 | 26.5 | 0 | 2018-03-17 | -8.5 | 26.5 | 0 | 2017-03-17 | -10.9 | 28.9 | 0 | 2016-03-17 | 2.2 | 15.8 | 0 | 20.61 | 0
2025-03-17 | -2 | 20 | 0 | 2024-03-17 | 2.8 | 15.2 | 0 | 2023-03-17 | 0.8 | 17.2 | 0 | 2022-03-17 | 2.8 | 15.2 | 0 | 2021-03-17 | -1.3 | 19.3 | 0 | 2020-03-17 | 1.8 | 16.2 | 0 | 2019-03-17 | -6.8 | 24.8 | 0 | 2018-03-17 | -8 | 26 | 0 | 2017-03-17 | -10 | 28 | 0 | 2016-03-17 | 3.8 | 14.2 | 0 | 19.61 | 0
2025-03-17 | -2.4 | 20.4 | 0 | 2024-03-17 | 4 | 14 | 0 | 2023-03-17 | 1.4 | 16.6 | 0 | 2022-03-17 | 5.5 | 12.5 | 0 | 2021-03-17 | 1 | 17 | 0 | 2020-03-17 | 1.4 | 16.6 | 0 | 2019-03-17 | -6.2 | 24.2 | 0 | 2018-03-17 | -8.9 | 26.9 | 0 | 2017-03-17 | -8.4 | 26.4 | 0 | 2016-03-17 | 6.6 | 11.4 | 0 | 18.6 | 0
2025-03-17 | -2.6 | 20.6 | 0 | 2024-03-17 | 4.6 | 13.4 | 0 | 2023-03-17 | 1.4 | 16.6 | 0 | 2022-03-17 | 8.1 | 9.9 | 0 | 2021-03-17 | 2.8 | 15.2 | 0 | 2020-03-17 | 1.9 | 16.1 | 0 | 2019-03-17 | -5.8 | 23.8 | 0 | 2018-03-17 | -9.2 | 27.2 | 0 | 2017-03-17 | -6.7 | 24.7 | 0 | 2016-03-17 | 8.6 | 9.4 | 0 | 17.69 | 0
2025-03-17 | -2.3 | 20.3 | 0 | 2024-03-17 | 4.7 | 13.3 | 0 | 2023-03-17 | 1.3 | 16.7 | 0 | 2022-03-17 | 10.8 | 7.2 | 0 | 2021-03-17 | 3.9 | 14.1 | 0 | 2020-03-17 | 2.5 | 15.5 | 0 | 2019-03-17 | -5.3 | 23.3 | 0 | 2018-03-17 | -9.5 | 27.5 | 0 | 2017-03-17 | -5.5 | 23.5 | 0 | 2016-03-17 | 10.3 | 7.7 | 0 | 16.91 | 0
2025-03-17 | -2.5 | 20.5 | 0 | 2024-03-17 | 5.6 | 12.4 | 0 | 2023-03-17 | 1.6 | 16.4 | 0 | 2022-03-17 | 12.7 | 5.3 | 0 | 2021-03-17 | 4.9 | 13.1 | 0 | 2020-03-17 | 3.5 | 14.5 | 0 | 2019-03-17 | -4.9 | 22.9 | 0 | 2018-03-17 | -9 | 27 | 0 | 2017-03-17 | -4.3 | 22.3 | 0 | 2016-03-17 | 6.9 | 11.1 | 0 | 16.55 | 0
2025-03-17 | -1.2 | 19.2 | 0 | 2024-03-17 | 4.5 | 13.5 | 0 | 2023-03-17 | 1.6 | 16.4 | 0 | 2022-03-17 | 14 | 4 | 0 | 2021-03-17 | 6.4 | 11.6 | 0 | 2020-03-17 | 4.1 | 13.9 | 0 | 2019-03-17 | -3.3 | 21.3 | 0 | 2018-03-17 | -9.2 | 27.2 | 0 | 2017-03-17 | -3.2 | 21.2 | 0 | 2016-03-17 | 8.1 | 9.9 | 0 | 15.82 | 0
2025-03-17 | 0.5 | 17.5 | 0 | 2024-03-17 | 4.5 | 13.5 | 0 | 2023-03-17 | 1.6 | 16.4 | 0 | 2022-03-17 | 15 | 3 | 0 | 2021-03-17 | 7.3 | 10.7 | 0 | 2020-03-17 | 4.9 | 13.1 | 0 | 2019-03-17 | -3.1 | 21.1 | 0 | 2018-03-17 | -8.5 | 26.5 | 0 | 2017-03-17 | -2.2 | 20.2 | 0 | 2016-03-17 | 7.5 | 10.5 | 0 | 15.25 | 0
2025-03-17 | 2.1 | 15.9 | 0 | 2024-03-17 | 5.1 | 12.9 | 0 | 2023-03-17 | 2.1 | 15.9 | 0 | 2022-03-17 | 15.4 | 2.6 | 0 | 2021-03-17 | 8 | 10 | 0 | 2020-03-17 | 5.5 | 12.5 | 0 | 2019-03-17 | -2.7 | 20.7 | 0 | 2018-03-17 | -8.1 | 26.1 | 0 | 2017-03-17 | -1.6 | 19.6 | 0 | 2016-03-17 | 4.6 | 13.4 | 0 | 14.96 | 0
2025-03-17 | 2.4 | 15.6 | 0 | 2024-03-17 | 5.4 | 12.6 | 0 | 2023-03-17 | 2.4 | 15.6 | 0 | 2022-03-17 | 14.7 | 3.3 | 0 | 2021-03-17 | 7.3 | 10.7 | 0 | 2020-03-17 | 5.4 | 12.6 | 0 | 2019-03-17 | -2.5 | 20.5 | 0 | 2018-03-17 | -7.8 | 25.8 | 0 | 2017-03-17 | -1.1 | 19.1 | 0 | 2016-03-17 | 8.4 | 9.6 | 0 | 14.54 | 0
2025-03-17 | 2.1 | 15.9 | 0 | 2024-03-17 | 5 | 13 | 0 | 2023-03-17 | 4.7 | 13.3 | 0 | 2022-03-17 | 13.9 | 4.1 | 0 | 2021-03-17 | 5.7 | 12.3 | 0 | 2020-03-17 | 4.4 | 13.6 | 0 | 2019-03-17 | -2.8 | 20.8 | 0 | 2018-03-17 | -7.8 | 25.8 | 0 | 2017-03-17 | -1.3 | 19.3 | 0 | 2016-03-17 | 6.3 | 11.7 | 0 | 14.98 | 0
2025-03-17 | 1.1 | 16.9 | 0 | 2024-03-17 | 4.6 | 13.4 | 0 | 2023-03-17 | 4.8 | 13.2 | 0 | 2022-03-17 | 12.3 | 5.7 | 0 | 2021-03-17 | 4.8 | 13.2 | 0 | 2020-03-17 | 3.8 | 14.2 | 0 | 2019-03-17 | -3.4 | 21.4 | 0 | 2018-03-17 | -8.2 | 26.2 | 0 | 2017-03-17 | -1.8 | 19.8 | 0 | 2016-03-17 | 5.2 | 12.8 | 0 | 15.68 | 0
2025-03-17 | -1.3 | 19.3 | 0 | 2024-03-17 | 3.7 | 14.3 | 0 | 2023-03-17 | 4.8 | 13.2 | 0 | 2022-03-17 | 11.4 | 6.6 | 0 | 2021-03-17 | 4.5 | 13.5 | 0 | 2020-03-17 | 2.8 | 15.2 | 0 | 2019-03-17 | -4.6 | 22.6 | 0 | 2018-03-17 | -9.1 | 27.1 | 0 | 2017-03-17 | -2.6 | 20.6 | 0 | 2016-03-17 | 3.3 | 14.7 | 0 | 16.71 | 0
2025-03-17 | -1.5 | 19.5 | 0 | 2024-03-17 | 3.2 | 14.8 | 0 | 2023-03-17 | 4.7 | 13.3 | 0 | 2022-03-17 | 11.1 | 6.9 | 0 | 2021-03-17 | 3.9 | 14.1 | 0 | 2020-03-17 | 2 | 16 | 0 | 2019-03-17 | -4.3 | 22.3 | 0 | 2018-03-17 | -9.9 | 27.9 | 0 | 2017-03-17 | -5.2 | 23.2 | 0 | 2016-03-17 | 2.7 | 15.3 | 0 | 17.33 | 0
2025-03-17 | -1.9 | 19.9 | 0 | 2024-03-17 | 2 | 16 | 0 | 2023-03-17 | 3.7 | 14.3 | 0 | 2022-03-17 | 10 | 8 | 0 | 2021-03-17 | 3.4 | 14.6 | 0 | 2020-03-17 | 2.4 | 15.6 | 0 | 2019-03-17 | -5.3 | 23.3 | 0 | 2018-03-17 | -10.4 | 28.4 | 0 | 2017-03-17 | -4.9 | 22.9 | 0 | 2016-03-17 | 2.5 | 15.5 | 0 | 17.85 | 0
2025-03-17 | -3.8 | 21.8 | 0 | 2024-03-17 | 0.9 | 17.1 | 0 | 2023-03-17 | 3.1 | 14.9 | 0 | 2022-03-17 | 8.5 | 9.5 | 0 | 2021-03-17 | 3 | 15 | 0 | 2020-03-17 | 1.7 | 16.3 | 0 | 2019-03-17 | -6.5 | 24.5 | 0 | 2018-03-17 | -10.7 | 28.7 | 0 | 2017-03-17 | -6.5 | 24.5 | 0 | 2016-03-17 | 2.3 | 15.7 | 0 | 18.8 | 0
2025-03-17 | -3.7 | 21.7 | 0 | 2024-03-17 | 0.9 | 17.1 | 0 | 2023-03-17 | 2.2 | 15.8 | 0 | 2022-03-17 | 8 | 10 | 0 | 2021-03-17 | 2.5 | 15.5 | 0 | 2020-03-17 | 0.3 | 17.7 | 0 | 2019-03-17 | -7.9 | 25.9 | 0 | 2018-03-17 | -11.1 | 29.1 | 0 | 2017-03-17 | -7.5 | 25.5 | 0 | 2016-03-17 | 2.8 | 15.2 | 0 | 19.35 | 0
2025-03-18 | -3.8 | 21.8 | 0 | 2024-03-18 | 0.7 | 17.3 | 0 | 2023-03-18 | 1.4 | 16.6 | 0 | 2022-03-18 | 7.8 | 10.2 | 0 | 2021-03-18 | 2 | 16 | 0 | 2020-03-18 | 0 | 18 | 0 | 2019-03-18 | -8.1 | 26.1 | 0 | 2018-03-18 | -12.6 | 30.6 | 0 | 2017-03-18 | -6.5 | 24.5 | 0 | 2016-03-18 | 2.7 | 15.3 | 0 | 19.64 | 0
2025-03-18 | -5 | 23 | 0 | 2024-03-18 | 0.6 | 17.4 | 0 | 2023-03-18 | 1.1 | 16.9 | 0 | 2022-03-18 | 5 | 13 | 0 | 2021-03-18 | 1.7 | 16.3 | 0 | 2020-03-18 | -0.6 | 18.6 | 0 | 2019-03-18 | -9.2 | 27.2 | 0 | 2018-03-18 | -14 | 32 | 0 | 2017-03-18 | -8.4 | 26.4 | 0 | 2016-03-18 | 2.2 | 15.8 | 0 | 20.66 | 0
2025-03-18 | -5.6 | 23.6 | 0 | 2024-03-18 | 0.3 | 17.7 | 0 | 2023-03-18 | 0.4 | 17.6 | 0 | 2022-03-18 | 4.6 | 13.4 | 0 | 2021-03-18 | 1.4 | 16.6 | 0 | 2020-03-18 | -1.5 | 19.5 | 0 | 2019-03-18 | -10.3 | 28.3 | 0 | 2018-03-18 | -13.4 | 31.4 | 0 | 2017-03-18 | -12.2 | 30.2 | 0 | 2016-03-18 | 2 | 16 | 0 | 21.43 | 0
2025-03-18 | -5.2 | 23.2 | 0 | 2024-03-18 | -0.1 | 18.1 | 0 | 2023-03-18 | 0.1 | 17.9 | 0 | 2022-03-18 | 4.8 | 13.2 | 0 | 2021-03-18 | 1.7 | 16.3 | 0 | 2020-03-18 | -2.2 | 20.2 | 0 | 2019-03-18 | -11.4 | 29.4 | 0 | 2018-03-18 | -14.7 | 32.7 | 0 | 2017-03-18 | -12.5 | 30.5 | 0 | 2016-03-18 | 1.1 | 16.9 | 0 | 21.84 | 0
2025-03-18 | -6.5 | 24.5 | 0 | 2024-03-18 | -0.6 | 18.6 | 0 | 2023-03-18 | 0.2 | 17.8 | 0 | 2022-03-18 | 2.5 | 15.5 | 0 | 2021-03-18 | 1.8 | 16.2 | 0 | 2020-03-18 | -2.7 | 20.7 | 0 | 2019-03-18 | -11.6 | 29.6 | 0 | 2018-03-18 | -15.1 | 33.1 | 0 | 2017-03-18 | -14.2 | 32.2 | 0 | 2016-03-18 | 0.8 | 17.2 | 0 | 22.54 | 0
2025-03-18 | -6.7 | 24.7 | 0 | 2024-03-18 | -1.2 | 19.2 | 0 | 2023-03-18 | -0.2 | 18.2 | 0 | 2022-03-18 | 3.5 | 14.5 | 0 | 2021-03-18 | 1.9 | 16.1 | 0 | 2020-03-18 | -2.7 | 20.7 | 0 | 2019-03-18 | -10.6 | 28.6 | 0 | 2018-03-18 | -15.9 | 33.9 | 0 | 2017-03-18 | -14.1 | 32.1 | 0 | 2016-03-18 | 0 | 18 | 0 | 22.6 | 0
2025-03-18 | -6.3 | 24.3 | 0 | 2024-03-18 | -1.3 | 19.3 | 0 | 2023-03-18 | -0.5 | 18.5 | 0 | 2022-03-18 | 3.1 | 14.9 | 0 | 2021-03-18 | 1.3 | 16.7 | 0 | 2020-03-18 | -3.5 | 21.5 | 0 | 2019-03-18 | -11.9 | 29.9 | 0 | 2018-03-18 | -15.4 | 33.4 | 0 | 2017-03-18 | -11.9 | 29.9 | 0 | 2016-03-18 | -1.1 | 19.1 | 0 | 22.75 | 0
2025-03-18 | -4.4 | 22.4 | 0 | 2024-03-18 | -1 | 19 | 0 | 2023-03-18 | -0.3 | 18.3 | 0 | 2022-03-18 | 2.6 | 15.4 | 0 | 2021-03-18 | 1.3 | 16.7 | 0 | 2020-03-18 | -2.6 | 20.6 | 0 | 2019-03-18 | -10.5 | 28.5 | 0 | 2018-03-18 | -15.6 | 33.6 | 0 | 2017-03-18 | -11.1 | 29.1 | 0 | 2016-03-18 | -1.3 | 19.3 | 0 | 22.29 | 0
2025-03-18 | -1.3 | 19.3 | 0 | 2024-03-18 | -0.5 | 18.5 | 0 | 2023-03-18 | 0 | 18 | 0 | 2022-03-18 | 4 | 14 | 0 | 2021-03-18 | 1.7 | 16.3 | 0 | 2020-03-18 | -1.6 | 19.6 | 0 | 2019-03-18 | -9.4 | 27.4 | 0 | 2018-03-18 | -14.2 | 32.2 | 0 | 2017-03-18 | -9.2 | 27.2 | 0 | 2016-03-18 | -0.5 | 18.5 | 0 | 21.1 | 0
2025-03-18 | 0.8 | 17.2 | 0 | 2024-03-18 | 0.2 | 17.8 | 0 | 2023-03-18 | 0.6 | 17.4 | 0 | 2022-03-18 | 4.3 | 13.7 | 0 | 2021-03-18 | 2.6 | 15.4 | 0 | 2020-03-18 | -0.9 | 18.9 | 0 | 2019-03-18 | -6.7 | 24.7 | 0 | 2018-03-18 | -12.5 | 30.5 | 0 | 2017-03-18 | -6.1 | 24.1 | 0 | 2016-03-18 | -0.2 | 18.2 | 0 | 19.79 | 0
2025-03-18 | 2.8 | 15.2 | 0 | 2024-03-18 | 0.7 | 17.3 | 0 | 2023-03-18 | 0.7 | 17.3 | 0 | 2022-03-18 | 5.2 | 12.8 | 0 | 2021-03-18 | 3.7 | 14.3 | 0 | 2020-03-18 | 0 | 18 | 0 | 2019-03-18 | -5.3 | 23.3 | 0 | 2018-03-18 | -10.7 | 28.7 | 0 | 2017-03-18 | -3 | 21 | 0 | 2016-03-18 | 0.3 | 17.7 | 0 | 18.56 | 0
2025-03-18 | 3.8 | 14.2 | 0 | 2024-03-18 | 0.4 | 17.6 | 0 | 2023-03-18 | 1.8 | 16.2 | 0 | 2022-03-18 | 5.7 | 12.3 | 0 | 2021-03-18 | 4.6 | 13.4 | 0 | 2020-03-18 | 0.7 | 17.3 | 0 | 2019-03-18 | -4.1 | 22.1 | 0 | 2018-03-18 | -9.8 | 27.8 | 0 | 2017-03-18 | -1.6 | 19.6 | 0 | 2016-03-18 | 0.4 | 17.6 | 0 | 17.81 | 0
2025-03-18 | 4.7 | 13.3 | 0 | 2024-03-18 | 0.9 | 17.1 | 0 | 2023-03-18 | 2.5 | 15.5 | 0 | 2022-03-18 | 6.5 | 11.5 | 0 | 2021-03-18 | 4.3 | 13.7 | 0 | 2020-03-18 | 1.5 | 16.5 | 0 | 2019-03-18 | -3.3 | 21.3 | 0 | 2018-03-18 | -8.5 | 26.5 | 0 | 2017-03-18 | -0.7 | 18.7 | 0 | 2016-03-18 | 0.6 | 17.4 | 0 | 17.15 | 0
2025-03-18 | 6.1 | 11.9 | 0 | 2024-03-18 | -0.6 | 18.6 | 0 | 2023-03-18 | 2.5 | 15.5 | 0 | 2022-03-18 | 8.2 | 9.8 | 0 | 2021-03-18 | 4.9 | 13.1 | 0 | 2020-03-18 | 2.5 | 15.5 | 0 | 2019-03-18 | -2.7 | 20.7 | 0 | 2018-03-18 | -7.1 | 25.1 | 0 | 2017-03-18 | -0.1 | 18.1 | 0 | 2016-03-18 | 1 | 17 | 0 | 16.53 | 0
2025-03-18 | 6.7 | 11.3 | 0 | 2024-03-18 | 0.5 | 17.5 | 0 | 2023-03-18 | 3 | 15 | 0 | 2022-03-18 | 8.9 | 9.1 | 0 | 2021-03-18 | 4.8 | 13.2 | 0 | 2020-03-18 | 2.8 | 15.2 | 0 | 2019-03-18 | -2.4 | 20.4 | 0 | 2018-03-18 | -6.3 | 24.3 | 0 | 2017-03-18 | 0 | 18 | 0 | 2016-03-18 | 1 | 17 | 0 | 16.1 | 0
2025-03-18 | 7.5 | 10.5 | 0 | 2024-03-18 | 0.3 | 17.7 | 0 | 2023-03-18 | 0.9 | 17.1 | 0 | 2022-03-18 | 9.9 | 8.1 | 0 | 2021-03-18 | 4.1 | 13.9 | 0 | 2020-03-18 | 2.8 | 15.2 | 0 | 2019-03-18 | -2.2 | 20.2 | 0 | 2018-03-18 | -5.5 | 23.5 | 0 | 2017-03-18 | -0.1 | 18.1 | 0 | 2016-03-18 | 1.2 | 16.8 | 0 | 16.11 | 0
2025-03-18 | 7.3 | 10.7 | 0 | 2024-03-18 | -0.6 | 18.6 | 0 | 2023-03-18 | -0.5 | 18.5 | 0 | 2022-03-18 | 9.8 | 8.2 | 0 | 2021-03-18 | 2.8 | 15.2 | 0 | 2020-03-18 | 2.5 | 15.5 | 0 | 2019-03-18 | -1.7 | 19.7 | 0 | 2018-03-18 | -5 | 23 | 0 | 2017-03-18 | -0.2 | 18.2 | 0 | 2016-03-18 | 1 | 17 | 0 | 16.46 | 0
2025-03-18 | 6.5 | 11.5 | 0 | 2024-03-18 | -0.6 | 18.6 | 0 | 2023-03-18 | 0.4 | 17.6 | 0 | 2022-03-18 | 7.7 | 10.3 | 0 | 2021-03-18 | 1.7 | 16.3 | 0 | 2020-03-18 | 2 | 16 | 0 | 2019-03-18 | -1.8 | 19.8 | 0 | 2018-03-18 | -5.1 | 23.1 | 0 | 2017-03-18 | -0.9 | 18.9 | 0 | 2016-03-18 | 0.3 | 17.7 | 0 | 16.98 | 0
2025-03-18 | 4.3 | 13.7 | 0 | 2024-03-18 | -1.1 | 19.1 | 0 | 2023-03-18 | -0.3 | 18.3 | 0 | 2022-03-18 | 5.9 | 12.1 | 0 | 2021-03-18 | 0.2 | 17.8 | 0 | 2020-03-18 | 1.3 | 16.7 | 0 | 2019-03-18 | -2.4 | 20.4 | 0 | 2018-03-18 | -5.3 | 23.3 | 0 | 2017-03-18 | -1.8 | 19.8 | 0 | 2016-03-18 | -0.9 | 18.9 | 0 | 18.01 | 0
2025-03-18 | 2.1 | 15.9 | 0 | 2024-03-18 | -1.4 | 19.4 | 0 | 2023-03-18 | -1.3 | 19.3 | 0 | 2022-03-18 | 5.3 | 12.7 | 0 | 2021-03-18 | -0.6 | 18.6 | 0 | 2020-03-18 | 0.7 | 17.3 | 0 | 2019-03-18 | -3.1 | 21.1 | 0 | 2018-03-18 | -6.5 | 24.5 | 0 | 2017-03-18 | -2.8 | 20.8 | 0 | 2016-03-18 | -1.8 | 19.8 | 0 | 18.94 | 0
2025-03-18 | 1.8 | 16.2 | 0 | 2024-03-18 | -1.8 | 19.8 | 0 | 2023-03-18 | -2.4 | 20.4 | 0 | 2022-03-18 | 4.8 | 13.2 | 0 | 2021-03-18 | -1.4 | 19.4 | 0 | 2020-03-18 | 0.4 | 17.6 | 0 | 2019-03-18 | -4 | 22 | 0 | 2018-03-18 | -8.7 | 26.7 | 0 | 2017-03-18 | -3.5 | 21.5 | 0 | 2016-03-18 | -2.5 | 20.5 | 0 | 19.73 | 0
2025-03-18 | 2.2 | 15.8 | 0 | 2024-03-18 | -2 | 20 | 0 | 2023-03-18 | -2.4 | 20.4 | 0 | 2022-03-18 | 4.9 | 13.1 | 0 | 2021-03-18 | -2.4 | 20.4 | 0 | 2020-03-18 | 0.1 | 17.9 | 0 | 2019-03-18 | -4.8 | 22.8 | 0 | 2018-03-18 | -7.8 | 25.8 | 0 | 2017-03-18 | -4 | 22 | 0 | 2016-03-18 | -3 | 21 | 0 | 19.92 | 0
2025-03-18 | 1.2 | 16.8 | 0 | 2024-03-18 | -2.6 | 20.6 | 0 | 2023-03-18 | -4.2 | 22.2 | 0 | 2022-03-18 | 4.7 | 13.3 | 0 | 2021-03-18 | -3.4 | 21.4 | 0 | 2020-03-18 | -0.6 | 18.6 | 0 | 2019-03-18 | -7.2 | 25.2 | 0 | 2018-03-18 | -8.3 | 26.3 | 0 | 2017-03-18 | -4.3 | 22.3 | 0 | 2016-03-18 | -3.7 | 21.7 | 0 | 20.84 | 0
2025-03-18 | 1.3 | 16.7 | 0 | 2024-03-18 | -3.3 | 21.3 | 0 | 2023-03-18 | -5.2 | 23.2 | 0 | 2022-03-18 | 4.5 | 13.5 | 0 | 2021-03-18 | -4.4 | 22.4 | 0 | 2020-03-18 | -0.6 | 18.6 | 0 | 2019-03-18 | -7.7 | 25.7 | 0 | 2018-03-18 | -8 | 26 | 0 | 2017-03-18 | -4.7 | 22.7 | 0 | 2016-03-18 | -4.5 | 22.5 | 0 | 21.26 | 0
2025-03-19 | 1.1 | 16.9 | 0 | 2024-03-19 | -4.3 | 22.3 | 0 | 2023-03-19 | -5.9 | 23.9 | 0 | 2022-03-19 | 4.9 | 13.1 | 0 | 2021-03-19 | -5.5 | 23.5 | 0 | 2020-03-19 | -0.5 | 18.5 | 0 | 2019-03-19 | -7.6 | 25.6 | 0 | 2018-03-19 | -10.1 | 28.1 | 0 | 2017-03-19 | -7 | 25 | 0 | 2016-03-19 | -5.2 | 23.2 | 0 | 22.01 | 0
2025-03-19 | 1.1 | 16.9 | 0 | 2024-03-19 | -5.2 | 23.2 | 0 | 2023-03-19 | -6.6 | 24.6 | 0 | 2022-03-19 | 4.2 | 13.8 | 0 | 2021-03-19 | -6.3 | 24.3 | 0 | 2020-03-19 | -0.6 | 18.6 | 0 | 2019-03-19 | -8.4 | 26.4 | 0 | 2018-03-19 | -10.9 | 28.9 | 0 | 2017-03-19 | -6.9 | 24.9 | 0 | 2016-03-19 | -5.8 | 23.8 | 0 | 22.54 | 0
2025-03-19 | 0.3 | 17.7 | 0 | 2024-03-19 | -5.1 | 23.1 | 0 | 2023-03-19 | -6.7 | 24.7 | 0 | 2022-03-19 | 3.9 | 14.1 | 0 | 2021-03-19 | -6.9 | 24.9 | 0 | 2020-03-19 | -0.4 | 18.4 | 0 | 2019-03-19 | -8.2 | 26.2 | 0 | 2018-03-19 | -12.1 | 30.1 | 0 | 2017-03-19 | -6.7 | 24.7 | 0 | 2016-03-19 | -6.9 | 24.9 | 0 | 22.88 | 0
2025-03-19 | -1 | 19 | 0 | 2024-03-19 | -5.9 | 23.9 | 0 | 2023-03-19 | -7 | 25 | 0 | 2022-03-19 | 4 | 14 | 0 | 2021-03-19 | -7.5 | 25.5 | 0 | 2020-03-19 | -0.4 | 18.4 | 0 | 2019-03-19 | -10.9 | 28.9 | 0 | 2018-03-19 | -11.6 | 29.6 | 0 | 2017-03-19 | -9.7 | 27.7 | 0 | 2016-03-19 | -7.8 | 25.8 | 0 | 23.78 | 0
2025-03-19 | -0.1 | 18.1 | 0 | 2024-03-19 | -6.4 | 24.4 | 0 | 2023-03-19 | -6.9 | 24.9 | 0 | 2022-03-19 | 3.8 | 14.2 | 0 | 2021-03-19 | -8 | 26 | 0 | 2020-03-19 | -0.4 | 18.4 | 0 | 2019-03-19 | -11.5 | 29.5 | 0 | 2018-03-19 | -13.7 | 31.7 | 0 | 2017-03-19 | -6 | 24 | 0 | 2016-03-19 | -8.7 | 26.7 | 0 | 23.79 | 0
2025-03-19 | -0.5 | 18.5 | 0 | 2024-03-19 | -7.6 | 25.6 | 0 | 2023-03-19 | -6.6 | 24.6 | 0 | 2022-03-19 | 3.4 | 14.6 | 0 | 2021-03-19 | -8.5 | 26.5 | 0 | 2020-03-19 | -0.4 | 18.4 | 0 | 2019-03-19 | -10.6 | 28.6 | 0 | 2018-03-19 | -12.5 | 30.5 | 0 | 2017-03-19 | -8.1 | 26.1 | 0 | 2016-03-19 | -9.4 | 27.4 | 0 | 24.08 | 0
2025-03-19 | -0.3 | 18.3 | 0 | 2024-03-19 | -6.8 | 24.8 | 0 | 2023-03-19 | -7 | 25 | 0 | 2022-03-19 | 2.7 | 15.3 | 0 | 2021-03-19 | -9 | 27 | 0 | 2020-03-19 | -0.5 | 18.5 | 0 | 2019-03-19 | -11.8 | 29.8 | 0 | 2018-03-19 | -12.9 | 30.9 | 0 | 2017-03-19 | -8 | 26 | 0 | 2016-03-19 | -9.9 | 27.9 | 0 | 24.35 | 0
2025-03-19 | 0.7 | 17.3 | 0 | 2024-03-19 | -6 | 24 | 0 | 2023-03-19 | -7.1 | 25.1 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | -8.5 | 26.5 | 0 | 2020-03-19 | -0.2 | 18.2 | 0 | 2019-03-19 | -11.4 | 29.4 | 0 | 2018-03-19 | -12.8 | 30.8 | 0 | 2017-03-19 | -6.7 | 24.7 | 0 | 2016-03-19 | -9.4 | 27.4 | 0 | 23.9 | 0
2025-03-19 | 1.6 | 16.4 | 0 | 2024-03-19 | -5.4 | 23.4 | 0 | 2023-03-19 | -8.5 | 26.5 | 0 | 2022-03-19 | 2.1 | 15.9 | 0 | 2021-03-19 | -7.7 | 25.7 | 0 | 2020-03-19 | 0.3 | 17.7 | 0 | 2019-03-19 | -9.3 | 27.3 | 0 | 2018-03-19 | -11.9 | 29.9 | 0 | 2017-03-19 | -5.6 | 23.6 | 0 | 2016-03-19 | -8.7 | 26.7 | 0 | 23.31 | 0
2025-03-19 | 3.3 | 14.7 | 0 | 2024-03-19 | -4.3 | 22.3 | 0 | 2023-03-19 | -8.7 | 26.7 | 0 | 2022-03-19 | 2.2 | 15.8 | 0 | 2021-03-19 | -6.7 | 24.7 | 0 | 2020-03-19 | 0.8 | 17.2 | 0 | 2019-03-19 | -6.3 | 24.3 | 0 | 2018-03-19 | -11.2 | 29.2 | 0 | 2017-03-19 | -2.1 | 20.1 | 0 | 2016-03-19 | -7.5 | 25.5 | 0 | 22.05 | 0
2025-03-19 | 5.9 | 12.1 | 0 | 2024-03-19 | -3.9 | 21.9 | 0 | 2023-03-19 | -8.3 | 26.3 | 0 | 2022-03-19 | 2.3 | 15.7 | 0 | 2021-03-19 | -5.6 | 23.6 | 0 | 2020-03-19 | 1.6 | 16.4 | 0 | 2019-03-19 | -3.6 | 21.6 | 0 | 2018-03-19 | -9.9 | 27.9 | 0 | 2017-03-19 | -0.8 | 18.8 | 0 | 2016-03-19 | -5.7 | 23.7 | 0 | 20.8 | 0
2025-03-19 | 8 | 10 | 0 | 2024-03-19 | -2.5 | 20.5 | 0 | 2023-03-19 | -7.7 | 25.7 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | -3.7 | 21.7 | 0 | 2020-03-19 | 2 | 16 | 0 | 2019-03-19 | -2.3 | 20.3 | 0 | 2018-03-19 | -9 | 27 | 0 | 2017-03-19 | 1 | 17 | 0 | 2016-03-19 | -5.1 | 23.1 | 0 | 19.69 | 0
2025-03-19 | 10.2 | 7.8 | 0 | 2024-03-19 | -2 | 20 | 0 | 2023-03-19 | -7.4 | 25.4 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | -2.4 | 20.4 | 0 | 2020-03-19 | 2.7 | 15.3 | 0 | 2019-03-19 | -1.5 | 19.5 | 0 | 2018-03-19 | -7.6 | 25.6 | 0 | 2017-03-19 | 1.1 | 16.9 | 0 | 2016-03-19 | -3 | 21 | 0 | 18.75 | 0
2025-03-19 | 11.4 | 6.6 | 0 | 2024-03-19 | -0.8 | 18.8 | 0 | 2023-03-19 | -7.3 | 25.3 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | -2.2 | 20.2 | 0 | 2020-03-19 | 3.1 | 14.9 | 0 | 2019-03-19 | -0.3 | 18.3 | 0 | 2018-03-19 | -6.7 | 24.7 | 0 | 2017-03-19 | 2.7 | 15.3 | 0 | 2016-03-19 | -2.1 | 20.1 | 0 | 17.98 | 0
2025-03-19 | 12.5 | 5.5 | 0 | 2024-03-19 | -1.2 | 19.2 | 0 | 2023-03-19 | -6.2 | 24.2 | 0 | 2022-03-19 | 2.5 | 15.5 | 0 | 2021-03-19 | -0.7 | 18.7 | 0 | 2020-03-19 | 3.6 | 14.4 | 0 | 2019-03-19 | 0.7 | 17.3 | 0 | 2018-03-19 | -5 | 23 | 0 | 2017-03-19 | 3.2 | 14.8 | 0 | 2016-03-19 | -1.2 | 19.2 | 0 | 17.18 | 0
2025-03-19 | 13.6 | 4.4 | 0 | 2024-03-19 | -0.9 | 18.9 | 0 | 2023-03-19 | -5 | 23 | 0 | 2022-03-19 | 2.5 | 15.5 | 0 | 2021-03-19 | 0 | 18 | 0 | 2020-03-19 | 3.6 | 14.4 | 0 | 2019-03-19 | 1.4 | 16.6 | 0 | 2018-03-19 | -4.4 | 22.4 | 0 | 2017-03-19 | 3.9 | 14.1 | 0 | 2016-03-19 | -0.8 | 18.8 | 0 | 16.61 | 0
2025-03-19 | 13.7 | 4.3 | 0 | 2024-03-19 | -0.3 | 18.3 | 0 | 2023-03-19 | -4.2 | 22.2 | 0 | 2022-03-19 | 2.5 | 15.5 | 0 | 2021-03-19 | 0.5 | 17.5 | 0 | 2020-03-19 | 3.8 | 14.2 | 0 | 2019-03-19 | 1.6 | 16.4 | 0 | 2018-03-19 | -4.4 | 22.4 | 0 | 2017-03-19 | 3.6 | 14.4 | 0 | 2016-03-19 | -0.3 | 18.3 | 0 | 16.35 | 0
2025-03-19 | 12.9 | 5.1 | 0 | 2024-03-19 | -0.8 | 18.8 | 0 | 2023-03-19 | -3.8 | 21.8 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | 0.8 | 17.2 | 0 | 2020-03-19 | 3.7 | 14.3 | 0 | 2019-03-19 | 1.7 | 16.3 | 0 | 2018-03-19 | -5.1 | 23.1 | 0 | 2017-03-19 | 4 | 14 | 0 | 2016-03-19 | -0.4 | 18.4 | 0 | 16.46 | 0
2025-03-19 | 9.9 | 8.1 | 0 | 2024-03-19 | -0.8 | 18.8 | 0 | 2023-03-19 | -4.5 | 22.5 | 0 | 2022-03-19 | 2.4 | 15.6 | 0 | 2021-03-19 | 0 | 18 | 0 | 2020-03-19 | 3.4 | 14.6 | 0 | 2019-03-19 | 0.2 | 17.8 | 0 | 2018-03-19 | -5.9 | 23.9 | 0 | 2017-03-19 | 2.8 | 15.2 | 0 | 2016-03-19 | -1.3 | 19.3 | 0 | 17.38 | 0
2025-03-19 | 7.3 | 10.7 | 0 | 2024-03-19 | -0.8 | 18.8 | 0 | 2023-03-19 | -4.7 | 22.7 | 0 | 2022-03-19 | 2.2 | 15.8 | 0 | 2021-03-19 | -0.5 | 18.5 | 0 | 2020-03-19 | 3.2 | 14.8 | 0 | 2019-03-19 | -0.5 | 18.5 | 0 | 2018-03-19 | -6.4 | 24.4 | 0 | 2017-03-19 | 1.6 | 16.4 | 0 | 2016-03-19 | -3.1 | 21.1 | 0 | 18.17 | 0
2025-03-19 | 5 | 13 | 0 | 2024-03-19 | -0.6 | 18.6 | 0 | 2023-03-19 | -5.4 | 23.4 | 0 | 2022-03-19 | 2.1 | 15.9 | 0 | 2021-03-19 | -1.1 | 19.1 | 0 | 2020-03-19 | 3 | 15 | 0 | 2019-03-19 | -1.2 | 19.2 | 0 | 2018-03-19 | -6.6 | 24.6 | 0 | 2017-03-19 | 0.8 | 17.2 | 0 | 2016-03-19 | -4.4 | 22.4 | 0 | 18.84 | 0
2025-03-19 | 5.1 | 12.9 | 0 | 2024-03-19 | -0.7 | 18.7 | 0 | 2023-03-19 | -4.3 | 22.3 | 0 | 2022-03-19 | 1.7 | 16.3 | 0 | 2021-03-19 | -1.2 | 19.2 | 0 | 2020-03-19 | 2.8 | 15.2 | 0 | 2019-03-19 | -1.8 | 19.8 | 0 | 2018-03-19 | -7 | 25 | 0 | 2017-03-19 | -0.9 | 18.9 | 0 | 2016-03-19 | -3.9 | 21.9 | 0 | 19.02 | 0
2025-03-19 | 3.6 | 14.4 | 0 | 2024-03-19 | -0.5 | 18.5 | 0 | 2023-03-19 | -4.2 | 22.2 | 0 | 2022-03-19 | 1.5 | 16.5 | 0 | 2021-03-19 | -1.9 | 19.9 | 0 | 2020-03-19 | 2.7 | 15.3 | 0 | 2019-03-19 | -2.5 | 20.5 | 0 | 2018-03-19 | -7.5 | 25.5 | 0 | 2017-03-19 | -0.5 | 18.5 | 0 | 2016-03-19 | -4.5 | 22.5 | 0 | 19.38 | 0
2025-03-19 | 3 | 15 | 0 | 2024-03-19 | -0.6 | 18.6 | 0 | 2023-03-19 | -4 | 22 | 0 | 2022-03-19 | 1.4 | 16.6 | 0 | 2021-03-19 | -2.1 | 20.1 | 0 | 2020-03-19 | 2.5 | 15.5 | 0 | 2019-03-19 | -3.5 | 21.5 | 0 | 2018-03-19 | -8.9 | 26.9 | 0 | 2017-03-19 | -1.5 | 19.5 | 0 | 2016-03-19 | -4.7 | 22.7 | 0 | 19.84 | 0
2025-03-20 | 2.5 | 15.5 | 0 | 2024-03-20 | -0.6 | 18.6 | 0 | 2023-03-20 | -3.8 | 21.8 | 0 | 2022-03-20 | 1.4 | 16.6 | 0 | 2021-03-20 | -2.5 | 20.5 | 0 | 2020-03-20 | 2.4 | 15.6 | 0 | 2019-03-20 | -4 | 22 | 0 | 2018-03-20 | -8.7 | 26.7 | 0 | 2017-03-20 | -2.5 | 20.5 | 0 | 2016-03-20 | -5.5 | 23.5 | 0 | 20.13 | 0
2025-03-20 | 10.3 | 7.7 | 0 | 2024-03-20 | -0.9 | 18.9 | 0 | 2023-03-20 | -2.7 | 20.7 | 0 | 2022-03-20 | 1.6 | 16.4 | 0 | 2021-03-20 | -2.9 | 20.9 | 0 | 2020-03-20 | 2.1 | 15.9 | 0 | 2019-03-20 | -4.2 | 22.2 | 0 | 2018-03-20 | -7.6 | 25.6 | 0 | 2017-03-20 | -3.9 | 21.9 | 0 | 2016-03-20 | -6.7 | 24.7 | 0 | 19.49 | 0
2025-03-20 | 11 | 7 | 0 | 2024-03-20 | -1.2 | 19.2 | 0 | 2023-03-20 | -2.9 | 20.9 | 0 | 2022-03-20 | 1.5 | 16.5 | 0 | 2021-03-20 | -3.1 | 21.1 | 0 | 2020-03-20 | 2 | 16 | 0 | 2019-03-20 | -4.8 | 22.8 | 0 | 2018-03-20 | -8.2 | 26.2 | 0 | 2017-03-20 | -5.2 | 23.2 | 0 | 2016-03-20 | -7.4 | 25.4 | 0 | 19.83 | 0
2025-03-20 | 10.9 | 7.1 | 0 | 2024-03-20 | -1.1 | 19.1 | 0 | 2023-03-20 | -3.2 | 21.2 | 0 | 2022-03-20 | 3 | 15 | 0 | 2021-03-20 | -3.5 | 21.5 | 0 | 2020-03-20 | 2.3 | 15.7 | 0 | 2019-03-20 | -5.2 | 23.2 | 0 | 2018-03-20 | -11.2 | 29.2 | 0 | 2017-03-20 | -6 | 24 | 0 | 2016-03-20 | -8.8 | 26.8 | 0 | 20.28 | 0
2025-03-20 | 10.4 | 7.6 | 0 | 2024-03-20 | -1.1 | 19.1 | 0 | 2023-03-20 | -3.7 | 21.7 | 0 | 2022-03-20 | 4.8 | 13.2 | 0 | 2021-03-20 | -4 | 22 | 0 | 2020-03-20 | 2.6 | 15.4 | 0 | 2019-03-20 | -5.4 | 23.4 | 0 | 2018-03-20 | -11.6 | 29.6 | 0 | 2017-03-20 | -6.6 | 24.6 | 0 | 2016-03-20 | -10.3 | 28.3 | 0 | 20.49 | 0
2025-03-20 | 8.4 | 9.6 | 0 | 2024-03-20 | -0.9 | 18.9 | 0 | 2023-03-20 | -3.3 | 21.3 | 0 | 2022-03-20 | 4.8 | 13.2 | 0 | 2021-03-20 | -4.3 | 22.3 | 0 | 2020-03-20 | 3.5 | 14.5 | 0 | 2019-03-20 | -5.5 | 23.5 | 0 | 2018-03-20 | -11.2 | 29.2 | 0 | 2017-03-20 | -7.9 | 25.9 | 0 | 2016-03-20 | -9.4 | 27.4 | 0 | 20.58 | 0
2025-03-20 | 8.8 | 9.2 | 0 | 2024-03-20 | -1.5 | 19.5 | 0 | 2023-03-20 | -3.4 | 21.4 | 0 | 2022-03-20 | 4.5 | 13.5 | 0 | 2021-03-20 | -4.7 | 22.7 | 0 | 2020-03-20 | 2.9 | 15.1 | 0 | 2019-03-20 | -6.8 | 24.8 | 0 | 2018-03-20 | -10.5 | 28.5 | 0 | 2017-03-20 | -7.1 | 25.1 | 0 | 2016-03-20 | -10.4 | 28.4 | 0 | 20.82 | 0
2025-03-20 | 10.9 | 7.1 | 0 | 2024-03-20 | -0.9 | 18.9 | 0 | 2023-03-20 | -2.6 | 20.6 | 0 | 2022-03-20 | 4 | 14 | 0 | 2021-03-20 | -2.9 | 20.9 | 0 | 2020-03-20 | 2.7 | 15.3 | 0 | 2019-03-20 | -4.4 | 22.4 | 0 | 2018-03-20 | -10.6 | 28.6 | 0 | 2017-03-20 | -6.1 | 24.1 | 0 | 2016-03-20 | -8.4 | 26.4 | 0 | 19.83 | 0
2025-03-20 | 13 | 5 | 0 | 2024-03-20 | -0.2 | 18.2 | 0 | 2023-03-20 | -1.3 | 19.3 | 0 | 2022-03-20 | 3.5 | 14.5 | 0 | 2021-03-20 | -0.4 | 18.4 | 0 | 2020-03-20 | 3 | 15 | 0 | 2019-03-20 | -2.2 | 20.2 | 0 | 2018-03-20 | -10.1 | 28.1 | 0 | 2017-03-20 | -4.7 | 22.7 | 0 | 2016-03-20 | -6 | 24 | 0 | 18.54 | 0
2025-03-20 | 14.5 | 3.5 | 0 | 2024-03-20 | 1.3 | 16.7 | 0 | 2023-03-20 | -0.2 | 18.2 | 0 | 2022-03-20 | 3.5 | 14.5 | 0 | 2021-03-20 | 2.3 | 15.7 | 0 | 2020-03-20 | 3.8 | 14.2 | 0 | 2019-03-20 | -0.1 | 18.1 | 0 | 2018-03-20 | -9.1 | 27.1 | 0 | 2017-03-20 | -2 | 20 | 0 | 2016-03-20 | -4.8 | 22.8 | 0 | 17.08 | 0
2025-03-20 | 15.7 | 2.3 | 0 | 2024-03-20 | 1.8 | 16.2 | 0 | 2023-03-20 | 1 | 17 | 0 | 2022-03-20 | 3.9 | 14.1 | 0 | 2021-03-20 | 5.1 | 12.9 | 0 | 2020-03-20 | 11.4 | 6.6 | 0 | 2019-03-20 | 2.4 | 15.6 | 0 | 2018-03-20 | -7.5 | 25.5 | 0 | 2017-03-20 | 0.3 | 17.7 | 0 | 2016-03-20 | -3.1 | 21.1 | 0 | 14.9 | 0
2025-03-20 | 16.5 | 1.5 | 0 | 2024-03-20 | 2 | 16 | 0 | 2023-03-20 | 2.1 | 15.9 | 0 | 2022-03-20 | 4.2 | 13.8 | 0 | 2021-03-20 | 6.6 | 11.4 | 0 | 2020-03-20 | 12.4 | 5.6 | 0 | 2019-03-20 | 3.6 | 14.4 | 0 | 2018-03-20 | -5.9 | 23.9 | 0 | 2017-03-20 | 1.7 | 16.3 | 0 | 2016-03-20 | -2.6 | 20.6 | 0 | 13.94 | 0
2025-03-20 | 14.4 | 3.6 | 0 | 2024-03-20 | 2.8 | 15.2 | 0 | 2023-03-20 | 3.2 | 14.8 | 0 | 2022-03-20 | 3.8 | 14.2 | 0 | 2021-03-20 | 8.7 | 9.3 | 0 | 2020-03-20 | 13.5 | 4.5 | 0 | 2019-03-20 | 4.8 | 13.2 | 0 | 2018-03-20 | -4.6 | 22.6 | 0 | 2017-03-20 | 2.2 | 15.8 | 0 | 2016-03-20 | -1.1 | 19.1 | 0 | 13.23 | 0
2025-03-20 | 13.4 | 4.6 | 0 | 2024-03-20 | 0.8 | 17.2 | 0 | 2023-03-20 | 3.4 | 14.6 | 0 | 2022-03-20 | 3.8 | 14.2 | 0 | 2021-03-20 | 10.7 | 7.3 | 0 | 2020-03-20 | 13.7 | 4.3 | 0 | 2019-03-20 | 5.9 | 12.1 | 0 | 2018-03-20 | -3.1 | 21.1 | 0 | 2017-03-20 | 2.6 | 15.4 | 0 | 2016-03-20 | 0 | 18 | 0 | 12.88 | 0
2025-03-20 | 12.4 | 5.6 | 0 | 2024-03-20 | -0.2 | 18.2 | 0 | 2023-03-20 | 4 | 14 | 0 | 2022-03-20 | 4.2 | 13.8 | 0 | 2021-03-20 | 12.3 | 5.7 | 0 | 2020-03-20 | 13.5 | 4.5 | 0 | 2019-03-20 | 6.5 | 11.5 | 0 | 2018-03-20 | -2.2 | 20.2 | 0 | 2017-03-20 | 3.2 | 14.8 | 0 | 2016-03-20 | 1 | 17 | 0 | 12.53 | 0
2025-03-20 | 9.2 | 8.8 | 0 | 2024-03-20 | 1.1 | 16.9 | 0 | 2023-03-20 | 4.1 | 13.9 | 0 | 2022-03-20 | 4.5 | 13.5 | 0 | 2021-03-20 | 12.5 | 5.5 | 0 | 2020-03-20 | 8 | 10 | 0 | 2019-03-20 | 6.5 | 11.5 | 0 | 2018-03-20 | -0.8 | 18.8 | 0 | 2017-03-20 | 4 | 14 | 0 | 2016-03-20 | 1.4 | 16.6 | 0 | 12.95 | 0
2025-03-20 | 9.1 | 8.9 | 0 | 2024-03-20 | -0.7 | 18.7 | 0 | 2023-03-20 | 4.6 | 13.4 | 0 | 2022-03-20 | 5.5 | 12.5 | 0 | 2021-03-20 | 13 | 5 | 0 | 2020-03-20 | 6.4 | 11.6 | 0 | 2019-03-20 | 6 | 12 | 0 | 2018-03-20 | -0.7 | 18.7 | 0 | 2017-03-20 | 4.3 | 13.7 | 0 | 2016-03-20 | 1.8 | 16.2 | 0 | 13.07 | 0
2025-03-20 | 8.9 | 9.1 | 0 | 2024-03-20 | -0.4 | 18.4 | 0 | 2023-03-20 | 3.5 | 14.5 | 0 | 2022-03-20 | 6.8 | 11.2 | 0 | 2021-03-20 | 12.9 | 5.1 | 0 | 2020-03-20 | 5.1 | 12.9 | 0 | 2019-03-20 | 6.4 | 11.6 | 0 | 2018-03-20 | -0.8 | 18.8 | 0 | 2017-03-20 | 4 | 14 | 0 | 2016-03-20 | 0.9 | 17.1 | 0 | 13.27 | 0
2025-03-20 | 7.7 | 10.3 | 0 | 2024-03-20 | -1.5 | 19.5 | 0 | 2023-03-20 | 3.2 | 14.8 | 0 | 2022-03-20 | 6 | 12 | 0 | 2021-03-20 | 10.6 | 7.4 | 0 | 2020-03-20 | 3.4 | 14.6 | 0 | 2019-03-20 | 5.1 | 12.9 | 0 | 2018-03-20 | -1.2 | 19.2 | 0 | 2017-03-20 | 3.2 | 14.8 | 0 | 2016-03-20 | -0.3 | 18.3 | 0 | 14.38 | 0
2025-03-20 | 6.5 | 11.5 | 0 | 2024-03-20 | -3.2 | 21.2 | 0 | 2023-03-20 | 2.5 | 15.5 | 0 | 2022-03-20 | 4.7 | 13.3 | 0 | 2021-03-20 | 6.8 | 11.2 | 0 | 2020-03-20 | 1.3 | 16.7 | 0 | 2019-03-20 | 4.2 | 13.8 | 0 | 2018-03-20 | -2.5 | 20.5 | 0 | 2017-03-20 | 2.9 | 15.1 | 0 | 2016-03-20 | -2.2 | 20.2 | 0 | 15.9 | 0
2025-03-20 | 5.8 | 12.2 | 0 | 2024-03-20 | -4.7 | 22.7 | 0 | 2023-03-20 | 2.2 | 15.8 | 0 | 2022-03-20 | 4.1 | 13.9 | 0 | 2021-03-20 | 5.4 | 12.6 | 0 | 2020-03-20 | 0.2 | 17.8 | 0 | 2019-03-20 | 3.2 | 14.8 | 0 | 2018-03-20 | -2.7 | 20.7 | 0 | 2017-03-20 | 2.4 | 15.6 | 0 | 2016-03-20 | -2.9 | 20.9 | 0 | 16.7 | 0
2025-03-20 | 5.5 | 12.5 | 0 | 2024-03-20 | -5.5 | 23.5 | 0 | 2023-03-20 | 1.8 | 16.2 | 0 | 2022-03-20 | 2.3 | 15.7 | 0 | 2021-03-20 | 3.5 | 14.5 | 0 | 2020-03-20 | -1 | 19 | 0 | 2019-03-20 | 3.2 | 14.8 | 0 | 2018-03-20 | -3.8 | 21.8 | 0 | 2017-03-20 | 2 | 16 | 0 | 2016-03-20 | -4.1 | 22.1 | 0 | 17.61 | 0
2025-03-20 | 2.4 | 15.6 | 0 | 2024-03-20 | -5.9 | 23.9 | 0 | 2023-03-20 | 1.7 | 16.3 | 0 | 2022-03-20 | 1.2 | 16.8 | 0 | 2021-03-20 | 1.8 | 16.2 | 0 | 2020-03-20 | -1.9 | 19.9 | 0 | 2019-03-20 | 3.2 | 14.8 | 0 | 2018-03-20 | -4.2 | 22.2 | 0 | 2017-03-20 | 1.6 | 16.4 | 0 | 2016-03-20 | -4.4 | 22.4 | 0 | 18.45 | 0
2025-03-20 | 0.5 | 17.5 | 0 | 2024-03-20 | -6.3 | 24.3 | 0 | 2023-03-20 | 1.6 | 16.4 | 0 | 2022-03-20 | 1.4 | 16.6 | 0 | 2021-03-20 | 1.8 | 16.2 | 0 | 2020-03-20 | -3.3 | 21.3 | 0 | 2019-03-20 | 1.6 | 16.4 | 0 | 2018-03-20 | -5 | 23 | 0 | 2017-03-20 | 1.8 | 16.2 | 0 | 2016-03-20 | -4.6 | 22.6 | 0 | 19.05 | 0
2025-03-21 | -0.2 | 18.2 | 0 | 2024-03-21 | -7.2 | 25.2 | 0 | 2023-03-21 | 1.6 | 16.4 | 0 | 2022-03-21 | 0.7 | 17.3 | 0 | 2021-03-21 | -1.7 | 19.7 | 0 | 2020-03-21 | -4.5 | 22.5 | 0 | 2019-03-21 | 1.1 | 16.9 | 0 | 2018-03-21 | -5.3 | 23.3 | 0 | 2017-03-21 | 1.5 | 16.5 | 0 | 2016-03-21 | -6.2 | 24.2 | 0 | 20.02 | 0
2025-03-21 | -1 | 19 | 0 | 2024-03-21 | -7.9 | 25.9 | 0 | 2023-03-21 | 1.6 | 16.4 | 0 | 2022-03-21 | 0.7 | 17.3 | 0 | 2021-03-21 | -2 | 20 | 0 | 2020-03-21 | -6.1 | 24.1 | 0 | 2019-03-21 | 1.4 | 16.6 | 0 | 2018-03-21 | -6 | 24 | 0 | 2017-03-21 | 1.3 | 16.7 | 0 | 2016-03-21 | -6.9 | 24.9 | 0 | 20.49 | 0
2025-03-21 | -2 | 20 | 0 | 2024-03-21 | -8.6 | 26.6 | 0 | 2023-03-21 | 1.2 | 16.8 | 0 | 2022-03-21 | -0.9 | 18.9 | 0 | 2021-03-21 | -2.3 | 20.3 | 0 | 2020-03-21 | -7.3 | 25.3 | 0 | 2019-03-21 | 2.1 | 15.9 | 0 | 2018-03-21 | -6.2 | 24.2 | 0 | 2017-03-21 | 1.5 | 16.5 | 0 | 2016-03-21 | -6.7 | 24.7 | 0 | 20.92 | 0
2025-03-21 | -2.3 | 20.3 | 0 | 2024-03-21 | -8.9 | 26.9 | 0 | 2023-03-21 | 0.7 | 17.3 | 0 | 2022-03-21 | -0.6 | 18.6 | 0 | 2021-03-21 | -2 | 20 | 0 | 2020-03-21 | -8.3 | 26.3 | 0 | 2019-03-21 | 1 | 17 | 0 | 2018-03-21 | -6.9 | 24.9 | 0 | 2017-03-21 | 1.4 | 16.6 | 0 | 2016-03-21 | -8.7 | 26.7 | 0 | 21.46 | 0
2025-03-21 | -3.5 | 21.5 | 0 | 2024-03-21 | -9.5 | 27.5 | 0 | 2023-03-21 | 0.1 | 17.9 | 0 | 2022-03-21 | -1.3 | 19.3 | 0 | 2021-03-21 | -0.9 | 18.9 | 0 | 2020-03-21 | -9.1 | 27.1 | 0 | 2019-03-21 | 0.1 | 17.9 | 0 | 2018-03-21 | -7.2 | 25.2 | 0 | 2017-03-21 | 1.1 | 16.9 | 0 | 2016-03-21 | -8.2 | 26.2 | 0 | 21.84 | 0
2025-03-21 | -4.7 | 22.7 | 0 | 2024-03-21 | -9.5 | 27.5 | 0 | 2023-03-21 | -1 | 19 | 0 | 2022-03-21 | -2.8 | 20.8 | 0 | 2021-03-21 | -0.8 | 18.8 | 0 | 2020-03-21 | -10.2 | 28.2 | 0 | 2019-03-21 | -0.1 | 18.1 | 0 | 2018-03-21 | -7.9 | 25.9 | 0 | 2017-03-21 | 0.8 | 17.2 | 0 | 2016-03-21 | -8.6 | 26.6 | 0 | 22.48 | 0
2025-03-21 | -5.3 | 23.3 | 0 | 2024-03-21 | -10 | 28 | 0 | 2023-03-21 | 0 | 18 | 0 | 2022-03-21 | -1.5 | 19.5 | 0 | 2021-03-21 | -1 | 19 | 0 | 2020-03-21 | -10.9 | 28.9 | 0 | 2019-03-21 | 1.1 | 16.9 | 0 | 2018-03-21 | -8.6 | 26.6 | 0 | 2017-03-21 | 1 | 17 | 0 | 2016-03-21 | -9.1 | 27.1 | 0 | 22.43 | 0
2025-03-21 | -5 | 23 | 0 | 2024-03-21 | -10.4 | 28.4 | 0 | 2023-03-21 | 0.1 | 17.9 | 0 | 2022-03-21 | -1 | 19 | 0 | 2021-03-21 | -0.6 | 18.6 | 0 | 2020-03-21 | -10.8 | 28.8 | 0 | 2019-03-21 | 2.8 | 15.2 | 0 | 2018-03-21 | -7.9 | 25.9 | 0 | 2017-03-21 | 0.5 | 17.5 | 0 | 2016-03-21 | -5.6 | 23.6 | 0 | 21.79 | 0
2025-03-21 | -4.2 | 22.2 | 0 | 2024-03-21 | -10 | 28 | 0 | 2023-03-21 | 1 | 17 | 0 | 2022-03-21 | 1.2 | 16.8 | 0 | 2021-03-21 | 1.8 | 16.2 | 0 | 2020-03-21 | -10.3 | 28.3 | 0 | 2019-03-21 | 3.9 | 14.1 | 0 | 2018-03-21 | -6.9 | 24.9 | 0 | 2017-03-21 | 0.9 | 17.1 | 0 | 2016-03-21 | -4.2 | 22.2 | 0 | 20.68 | 0
2025-03-21 | -2.8 | 20.8 | 0 | 2024-03-21 | -9.7 | 27.7 | 0 | 2023-03-21 | 0.8 | 17.2 | 0 | 2022-03-21 | 2.3 | 15.7 | 0 | 2021-03-21 | 5.5 | 12.5 | 0 | 2020-03-21 | -9.4 | 27.4 | 0 | 2019-03-21 | 4.2 | 13.8 | 0 | 2018-03-21 | -5 | 23 | 0 | 2017-03-21 | 1.6 | 16.4 | 0 | 2016-03-21 | -2.5 | 20.5 | 0 | 19.5 | 0
2025-03-21 | -1.9 | 19.9 | 0 | 2024-03-21 | -8.7 | 26.7 | 0 | 2023-03-21 | 1.1 | 16.9 | 0 | 2022-03-21 | 3.3 | 14.7 | 0 | 2021-03-21 | 8.8 | 9.2 | 0 | 2020-03-21 | -8.3 | 26.3 | 0 | 2019-03-21 | 4.7 | 13.3 | 0 | 2018-03-21 | -3.2 | 21.2 | 0 | 2017-03-21 | 3 | 15 | 0 | 2016-03-21 | -0.8 | 18.8 | 0 | 18.2 | 0
2025-03-21 | -0.3 | 18.3 | 0 | 2024-03-21 | -7.8 | 25.8 | 0 | 2023-03-21 | 0.5 | 17.5 | 0 | 2022-03-21 | 4 | 14 | 0 | 2021-03-21 | 11.2 | 6.8 | 0 | 2020-03-21 | -6.9 | 24.9 | 0 | 2019-03-21 | 5.7 | 12.3 | 0 | 2018-03-21 | -2.1 | 20.1 | 0 | 2017-03-21 | 3.1 | 14.9 | 0 | 2016-03-21 | 0.8 | 17.2 | 0 | 17.18 | 0
2025-03-21 | 1.7 | 16.3 | 0 | 2024-03-21 | -6.3 | 24.3 | 0 | 2023-03-21 | 1.2 | 16.8 | 0 | 2022-03-21 | 4.7 | 13.3 | 0 | 2021-03-21 | 13.2 | 4.8 | 0 | 2020-03-21 | -6.4 | 24.4 | 0 | 2019-03-21 | 5.6 | 12.4 | 0 | 2018-03-21 | -1.2 | 19.2 | 0 | 2017-03-21 | 3.1 | 14.9 | 0 | 2016-03-21 | 2.3 | 15.7 | 0 | 16.21 | 0
2025-03-21 | 2.9 | 15.1 | 0 | 2024-03-21 | -5.5 | 23.5 | 0 | 2023-03-21 | 1.4 | 16.6 | 0 | 2022-03-21 | 5.4 | 12.6 | 0 | 2021-03-21 | 14.3 | 3.7 | 0 | 2020-03-21 | -5.7 | 23.7 | 0 | 2019-03-21 | 5.8 | 12.2 | 0 | 2018-03-21 | -0.3 | 18.3 | 0 | 2017-03-21 | 3.9 | 14.1 | 0 | 2016-03-21 | 3.6 | 14.4 | 0 | 15.42 | 0
2025-03-21 | 4.5 | 13.5 | 0 | 2024-03-21 | -5.1 | 23.1 | 0 | 2023-03-21 | 2.2 | 15.8 | 0 | 2022-03-21 | 5.5 | 12.5 | 0 | 2021-03-21 | 14.9 | 3.1 | 0 | 2020-03-21 | -5.3 | 23.3 | 0 | 2019-03-21 | 5.5 | 12.5 | 0 | 2018-03-21 | 1 | 17 | 0 | 2017-03-21 | 4.5 | 13.5 | 0 | 2016-03-21 | 4.3 | 13.7 | 0 | 14.8 | 0
2025-03-21 | 5 | 13 | 0 | 2024-03-21 | -4.2 | 22.2 | 0 | 2023-03-21 | 2.7 | 15.3 | 0 | 2022-03-21 | 5.3 | 12.7 | 0 | 2021-03-21 | 15.4 | 2.6 | 0 | 2020-03-21 | -4 | 22 | 0 | 2019-03-21 | 4.8 | 13.2 | 0 | 2018-03-21 | 2.2 | 15.8 | 0 | 2017-03-21 | 5.5 | 12.5 | 0 | 2016-03-21 | 4.6 | 13.4 | 0 | 14.27 | 0
2025-03-21 | 5.8 | 12.2 | 0 | 2024-03-21 | -4.2 | 22.2 | 0 | 2023-03-21 | 2.7 | 15.3 | 0 | 2022-03-21 | 5.2 | 12.8 | 0 | 2021-03-21 | 15.1 | 2.9 | 0 | 2020-03-21 | -3.8 | 21.8 | 0 | 2019-03-21 | 4.8 | 13.2 | 0 | 2018-03-21 | 2.6 | 15.4 | 0 | 2017-03-21 | 4.9 | 13.1 | 0 | 2016-03-21 | 3.4 | 14.6 | 0 | 14.35 | 0
2025-03-21 | 6.1 | 11.9 | 0 | 2024-03-21 | -4.6 | 22.6 | 0 | 2023-03-21 | 1.9 | 16.1 | 0 | 2022-03-21 | 4.7 | 13.3 | 0 | 2021-03-21 | 14.3 | 3.7 | 0 | 2020-03-21 | -4.1 | 22.1 | 0 | 2019-03-21 | 4.5 | 13.5 | 0 | 2018-03-21 | 2.8 | 15.2 | 0 | 2017-03-21 | 3.5 | 14.5 | 0 | 2016-03-21 | 1.7 | 16.3 | 0 | 14.92 | 0
2025-03-21 | 4.2 | 13.8 | 0 | 2024-03-21 | -5.6 | 23.6 | 0 | 2023-03-21 | 1 | 17 | 0 | 2022-03-21 | 2.6 | 15.4 | 0 | 2021-03-21 | 12 | 6 | 0 | 2020-03-21 | -4.6 | 22.6 | 0 | 2019-03-21 | 3.2 | 14.8 | 0 | 2018-03-21 | 2.1 | 15.9 | 0 | 2017-03-21 | 2.8 | 15.2 | 0 | 2016-03-21 | 0.8 | 17.2 | 0 | 16.15 | 0
2025-03-21 | 3.3 | 14.7 | 0 | 2024-03-21 | -6.3 | 24.3 | 0 | 2023-03-21 | -0.4 | 18.4 | 0 | 2022-03-21 | 1.6 | 16.4 | 0 | 2021-03-21 | 9.6 | 8.4 | 0 | 2020-03-21 | -5.2 | 23.2 | 0 | 2019-03-21 | 2.9 | 15.1 | 0 | 2018-03-21 | 1.3 | 16.7 | 0 | 2017-03-21 | 3.5 | 14.5 | 0 | 2016-03-21 | -0.8 | 18.8 | 0 | 17.05 | 0
2025-03-21 | 2.3 | 15.7 | 0 | 2024-03-21 | -6.8 | 24.8 | 0 | 2023-03-21 | 0.2 | 17.8 | 0 | 2022-03-21 | 0.6 | 17.4 | 0 | 2021-03-21 | 8.6 | 9.4 | 0 | 2020-03-21 | -5.6 | 23.6 | 0 | 2019-03-21 | 3 | 15 | 0 | 2018-03-21 | -0.2 | 18.2 | 0 | 2017-03-21 | 3.6 | 14.4 | 0 | 2016-03-21 | -2.1 | 20.1 | 0 | 17.64 | 0
2025-03-21 | 2.2 | 15.8 | 0 | 2024-03-21 | -7.6 | 25.6 | 0 | 2023-03-21 | -1.4 | 19.4 | 0 | 2022-03-21 | -0.2 | 18.2 | 0 | 2021-03-21 | 8.3 | 9.7 | 0 | 2020-03-21 | -6.3 | 24.3 | 0 | 2019-03-21 | 2.5 | 15.5 | 0 | 2018-03-21 | -0.7 | 18.7 | 0 | 2017-03-21 | 0.7 | 17.3 | 0 | 2016-03-21 | -2.1 | 20.1 | 0 | 18.46 | 0
2025-03-21 | 0.8 | 17.2 | 0 | 2024-03-21 | -8.4 | 26.4 | 0 | 2023-03-21 | -0.9 | 18.9 | 0 | 2022-03-21 | -1.3 | 19.3 | 0 | 2021-03-21 | 7 | 11 | 0 | 2020-03-21 | -5.7 | 23.7 | 0 | 2019-03-21 | 1.8 | 16.2 | 0 | 2018-03-21 | -1.2 | 19.2 | 0 | 2017-03-21 | -1.8 | 19.8 | 0 | 2016-03-21 | -3.6 | 21.6 | 0 | 19.33 | 0
2025-03-21 | 0.1 | 17.9 | 0 | 2024-03-21 | -9.3 | 27.3 | 0 | 2023-03-21 | -1.3 | 19.3 | 0 | 2022-03-21 | -1.6 | 19.6 | 0 | 2021-03-21 | 6.3 | 11.7 | 0 | 2020-03-21 | -6.4 | 24.4 | 0 | 2019-03-21 | 2.7 | 15.3 | 0 | 2018-03-21 | -3.2 | 21.2 | 0 | 2017-03-21 | -3.9 | 21.9 | 0 | 2016-03-21 | -4 | 22 | 0 | 20.06 | 0
2025-03-22 | -0.6 | 18.6 | 0 | 2024-03-22 | -9.6 | 27.6 | 0 | 2023-03-22 | -1.6 | 19.6 | 0 | 2022-03-22 | -1.6 | 19.6 | 0 | 2021-03-22 | 2.3 | 15.7 | 0 | 2020-03-22 | -6.7 | 24.7 | 0 | 2019-03-22 | 2.8 | 15.2 | 0 | 2018-03-22 | -2.8 | 20.8 | 0 | 2017-03-22 | -7.1 | 25.1 | 0 | 2016-03-22 | -3.6 | 21.6 | 0 | 20.85 | 0
2025-03-22 | -1.2 | 19.2 | 0 | 2024-03-22 | -10.6 | 28.6 | 0 | 2023-03-22 | -2.1 | 20.1 | 0 | 2022-03-22 | -2 | 20 | 0 | 2021-03-22 | -1.9 | 19.9 | 0 | 2020-03-22 | -7.3 | 25.3 | 0 | 2019-03-22 | 2.6 | 15.4 | 0 | 2018-03-22 | -2.5 | 20.5 | 0 | 2017-03-22 | -8 | 26 | 0 | 2016-03-22 | -3.8 | 21.8 | 0 | 21.68 | 0
2025-03-22 | -0.4 | 18.4 | 0 | 2024-03-22 | -10.8 | 28.8 | 0 | 2023-03-22 | -3.3 | 21.3 | 0 | 2022-03-22 | -2.1 | 20.1 | 0 | 2021-03-22 | -1 | 19 | 0 | 2020-03-22 | -8.1 | 26.1 | 0 | 2019-03-22 | 2.4 | 15.6 | 0 | 2018-03-22 | -2.8 | 20.8 | 0 | 2017-03-22 | -9.8 | 27.8 | 0 | 2016-03-22 | -4.5 | 22.5 | 0 | 22.04 | 0
2025-03-22 | -0.4 | 18.4 | 0 | 2024-03-22 | -11.1 | 29.1 | 0 | 2023-03-22 | -4.1 | 22.1 | 0 | 2022-03-22 | -2.9 | 20.9 | 0 | 2021-03-22 | -1.4 | 19.4 | 0 | 2020-03-22 | -8.5 | 26.5 | 0 | 2019-03-22 | 2 | 16 | 0 | 2018-03-22 | -3.2 | 21.2 | 0 | 2017-03-22 | -11.4 | 29.4 | 0 | 2016-03-22 | -4.9 | 22.9 | 0 | 22.59 | 0
2025-03-22 | -0.9 | 18.9 | 0 | 2024-03-22 | -11.7 | 29.7 | 0 | 2023-03-22 | -4.8 | 22.8 | 0 | 2022-03-22 | -3.1 | 21.1 | 0 | 2021-03-22 | -2 | 20 | 0 | 2020-03-22 | -8.9 | 26.9 | 0 | 2019-03-22 | 1.9 | 16.1 | 0 | 2018-03-22 | -3.6 | 21.6 | 0 | 2017-03-22 | -13 | 31 | 0 | 2016-03-22 | -5.6 | 23.6 | 0 | 23.17 | 0
2025-03-22 | -2.3 | 20.3 | 0 | 2024-03-22 | -12.5 | 30.5 | 0 | 2023-03-22 | -4.6 | 22.6 | 0 | 2022-03-22 | -3.9 | 21.9 | 0 | 2021-03-22 | -2.5 | 20.5 | 0 | 2020-03-22 | -9.4 | 27.4 | 0 | 2019-03-22 | 2.1 | 15.9 | 0 | 2018-03-22 | -4.1 | 22.1 | 0 | 2017-03-22 | -13.6 | 31.6 | 0 | 2016-03-22 | -6.4 | 24.4 | 0 | 23.72 | 0
2025-03-22 | -1.2 | 19.2 | 0 | 2024-03-22 | -13.8 | 31.8 | 0 | 2023-03-22 | -4.7 | 22.7 | 0 | 2022-03-22 | -5.2 | 23.2 | 0 | 2021-03-22 | -3.6 | 21.6 | 0 | 2020-03-22 | -9.6 | 27.6 | 0 | 2019-03-22 | 1.5 | 16.5 | 0 | 2018-03-22 | -4.4 | 22.4 | 0 | 2017-03-22 | -14.5 | 32.5 | 0 | 2016-03-22 | -6.6 | 24.6 | 0 | 24.21 | 0
2025-03-22 | -0.1 | 18.1 | 0 | 2024-03-22 | -11.4 | 29.4 | 0 | 2023-03-22 | -4.5 | 22.5 | 0 | 2022-03-22 | -3.8 | 21.8 | 0 | 2021-03-22 | 0.7 | 17.3 | 0 | 2020-03-22 | -7.9 | 25.9 | 0 | 2019-03-22 | 1.9 | 16.1 | 0 | 2018-03-22 | -4.2 | 22.2 | 0 | 2017-03-22 | -14.5 | 32.5 | 0 | 2016-03-22 | -5.4 | 23.4 | 0 | 22.92 | 0
2025-03-22 | 2 | 16 | 0 | 2024-03-22 | -10.2 | 28.2 | 0 | 2023-03-22 | -3.8 | 21.8 | 0 | 2022-03-22 | -3 | 21 | 0 | 2021-03-22 | 4.4 | 13.6 | 0 | 2020-03-22 | -6.3 | 24.3 | 0 | 2019-03-22 | 1.6 | 16.4 | 0 | 2018-03-22 | -3.5 | 21.5 | 0 | 2017-03-22 | -14.3 | 32.3 | 0 | 2016-03-22 | -3 | 21 | 0 | 21.61 | 0
2025-03-22 | 4.9 | 13.1 | 0 | 2024-03-22 | -9.4 | 27.4 | 0 | 2023-03-22 | -3.3 | 21.3 | 0 | 2022-03-22 | -1.6 | 19.6 | 0 | 2021-03-22 | 8.9 | 9.1 | 0 | 2020-03-22 | -4.8 | 22.8 | 0 | 2019-03-22 | 1.6 | 16.4 | 0 | 2018-03-22 | -2.1 | 20.1 | 0 | 2017-03-22 | -13.3 | 31.3 | 0 | 2016-03-22 | -0.3 | 18.3 | 0 | 19.94 | 0
2025-03-22 | 6.3 | 11.7 | 0 | 2024-03-22 | -9 | 27 | 0 | 2023-03-22 | -2.6 | 20.6 | 0 | 2022-03-22 | -0.4 | 18.4 | 0 | 2021-03-22 | 12 | 6 | 0 | 2020-03-22 | -3.6 | 21.6 | 0 | 2019-03-22 | 1.6 | 16.4 | 0 | 2018-03-22 | -0.8 | 18.8 | 0 | 2017-03-22 | -12.6 | 30.6 | 0 | 2016-03-22 | 1.6 | 16.4 | 0 | 18.75 | 0
2025-03-22 | 6.4 | 11.6 | 0 | 2024-03-22 | -7.7 | 25.7 | 0 | 2023-03-22 | -1.8 | 19.8 | 0 | 2022-03-22 | 0.1 | 17.9 | 0 | 2021-03-22 | 14.5 | 3.5 | 0 | 2020-03-22 | -3.7 | 21.7 | 0 | 2019-03-22 | 1.9 | 16.1 | 0 | 2018-03-22 | 0.2 | 17.8 | 0 | 2017-03-22 | -11.6 | 29.6 | 0 | 2016-03-22 | 2.8 | 15.2 | 0 | 17.89 | 0
2025-03-22 | 5.1 | 12.9 | 0 | 2024-03-22 | -7.2 | 25.2 | 0 | 2023-03-22 | -0.9 | 18.9 | 0 | 2022-03-22 | 1.6 | 16.4 | 0 | 2021-03-22 | 16.2 | 1.8 | 0 | 2020-03-22 | -2.5 | 20.5 | 0 | 2019-03-22 | 2.5 | 15.5 | 0 | 2018-03-22 | 1.7 | 16.3 | 0 | 2017-03-22 | -10.6 | 28.6 | 0 | 2016-03-22 | 4.4 | 13.6 | 0 | 16.97 | 0
2025-03-22 | 4.5 | 13.5 | 0 | 2024-03-22 | -5.3 | 23.3 | 0 | 2023-03-22 | -0.3 | 18.3 | 0 | 2022-03-22 | 2.9 | 15.1 | 0 | 2021-03-22 | 17 | 1 | 0 | 2020-03-22 | -1.7 | 19.7 | 0 | 2019-03-22 | 2.4 | 15.6 | 0 | 2018-03-22 | 2.7 | 15.3 | 0 | 2017-03-22 | -10.1 | 28.1 | 0 | 2016-03-22 | 4.7 | 13.3 | 0 | 16.32 | 0
2025-03-22 | -0.5 | 18.5 | 0 | 2024-03-22 | -5.2 | 23.2 | 0 | 2023-03-22 | 0.2 | 17.8 | 0 | 2022-03-22 | 3.9 | 14.1 | 0 | 2021-03-22 | 17.4 | 0.6 | 0 | 2020-03-22 | -1.2 | 19.2 | 0 | 2019-03-22 | 2.6 | 15.4 | 0 | 2018-03-22 | 3.2 | 14.8 | 0 | 2017-03-22 | -8.8 | 26.8 | 0 | 2016-03-22 | 4.7 | 13.3 | 0 | 16.37 | 0
2025-03-22 | -2.2 | 20.2 | 0 | 2024-03-22 | -4.7 | 22.7 | 0 | 2023-03-22 | 0.2 | 17.8 | 0 | 2022-03-22 | 4.2 | 13.8 | 0 | 2021-03-22 | 18 | 0 | 0 | 2020-03-22 | -0.9 | 18.9 | 0 | 2019-03-22 | 1.5 | 16.5 | 0 | 2018-03-22 | 3.6 | 14.4 | 0 | 2017-03-22 | -7.8 | 25.8 | 0 | 2016-03-22 | 4.5 | 13.5 | 0 | 16.36 | 0
2025-03-22 | -3.3 | 21.3 | 0 | 2024-03-22 | -4.6 | 22.6 | 0 | 2023-03-22 | -0.1 | 18.1 | 0 | 2022-03-22 | 4.7 | 13.3 | 0 | 2021-03-22 | 17.8 | 0.2 | 0 | 2020-03-22 | -0.8 | 18.8 | 0 | 2019-03-22 | 0.7 | 17.3 | 0 | 2018-03-22 | 4.3 | 13.7 | 0 | 2017-03-22 | -7.2 | 25.2 | 0 | 2016-03-22 | 5 | 13 | 0 | 16.35 | 0
2025-03-22 | -4 | 22 | 0 | 2024-03-22 | -4.5 | 22.5 | 0 | 2023-03-22 | -0.4 | 18.4 | 0 | 2022-03-22 | 4.9 | 13.1 | 0 | 2021-03-22 | 16.8 | 1.2 | 0 | 2020-03-22 | -1.2 | 19.2 | 0 | 2019-03-22 | 0 | 18 | 0 | 2018-03-22 | 3.8 | 14.2 | 0 | 2017-03-22 | -6.9 | 24.9 | 0 | 2016-03-22 | 4.3 | 13.7 | 0 | 16.72 | 0
2025-03-22 | -4.6 | 22.6 | 0 | 2024-03-22 | -4.8 | 22.8 | 0 | 2023-03-22 | -0.8 | 18.8 | 0 | 2022-03-22 | 3 | 15 | 0 | 2021-03-22 | 13.1 | 4.9 | 0 | 2020-03-22 | -2.3 | 20.3 | 0 | 2019-03-22 | -1 | 19 | 0 | 2018-03-22 | 4.3 | 13.7 | 0 | 2017-03-22 | -6.8 | 24.8 | 0 | 2016-03-22 | 2.2 | 15.8 | 0 | 17.77 | 0
2025-03-22 | -5.2 | 23.2 | 0 | 2024-03-22 | -5 | 23 | 0 | 2023-03-22 | -0.8 | 18.8 | 0 | 2022-03-22 | 3.1 | 14.9 | 0 | 2021-03-22 | 12.2 | 5.8 | 0 | 2020-03-22 | -3.3 | 21.3 | 0 | 2019-03-22 | -1.6 | 19.6 | 0 | 2018-03-22 | 1.5 | 16.5 | 0 | 2017-03-22 | -7.1 | 25.1 | 0 | 2016-03-22 | 0.6 | 17.4 | 0 | 18.56 | 0
2025-03-22 | -5.8 | 23.8 | 0 | 2024-03-22 | -5.3 | 23.3 | 0 | 2023-03-22 | -0.7 | 18.7 | 0 | 2022-03-22 | 0.8 | 17.2 | 0 | 2021-03-22 | 10.7 | 7.3 | 0 | 2020-03-22 | -4 | 22 | 0 | 2019-03-22 | -1.9 | 19.9 | 0 | 2018-03-22 | 1.6 | 16.4 | 0 | 2017-03-22 | -7.4 | 25.4 | 0 | 2016-03-22 | 0.2 | 17.8 | 0 | 19.18 | 0
2025-03-22 | -6.3 | 24.3 | 0 | 2024-03-22 | -5.8 | 23.8 | 0 | 2023-03-22 | -1.1 | 19.1 | 0 | 2022-03-22 | 1.2 | 16.8 | 0 | 2021-03-22 | 10.3 | 7.7 | 0 | 2020-03-22 | -4.2 | 22.2 | 0 | 2019-03-22 | -2.2 | 20.2 | 0 | 2018-03-22 | 0.9 | 17.1 | 0 | 2017-03-22 | -7.8 | 25.8 | 0 | 2016-03-22 | 0 | 18 | 0 | 19.5 | 0
2025-03-22 | -7 | 25 | 0 | 2024-03-22 | -6.3 | 24.3 | 0 | 2023-03-22 | -1.4 | 19.4 | 0 | 2022-03-22 | 0.2 | 17.8 | 0 | 2021-03-22 | 8 | 10 | 0 | 2020-03-22 | -4.5 | 22.5 | 0 | 2019-03-22 | -2.7 | 20.7 | 0 | 2018-03-22 | 1.7 | 16.3 | 0 | 2017-03-22 | -8.2 | 26.2 | 0 | 2016-03-22 | 0.1 | 17.9 | 0 | 20.01 | 0
2025-03-22 | -8 | 26 | 0 | 2024-03-22 | -6 | 24 | 0 | 2023-03-22 | -1.5 | 19.5 | 0 | 2022-03-22 | 0.6 | 17.4 | 0 | 2021-03-22 | 7.1 | 10.9 | 0 | 2020-03-22 | -4.7 | 22.7 | 0 | 2019-03-22 | -3 | 21 | 0 | 2018-03-22 | 0.8 | 17.2 | 0 | 2017-03-22 | -8.2 | 26.2 | 0 | 2016-03-22 | 0 | 18 | 0 | 20.29 | 0
2025-03-23 | -8.5 | 26.5 | 0 | 2024-03-23 | -5.9 | 23.9 | 0 | 2023-03-23 | -1.5 | 19.5 | 0 | 2022-03-23 | -0.3 | 18.3 | 0 | 2021-03-23 | 7 | 11 | 0 | 2020-03-23 | -4.9 | 22.9 | 0 | 2019-03-23 | -3.5 | 21.5 | 0 | 2018-03-23 | 0.4 | 17.6 | 0 | 2017-03-23 | -10.3 | 28.3 | 0 | 2016-03-23 | -0.1 | 18.1 | 0 | 20.76 | 0
2025-03-23 | -9.4 | 27.4 | 0 | 2024-03-23 | -5.7 | 23.7 | 0 | 2023-03-23 | -1.5 | 19.5 | 0 | 2022-03-23 | -2 | 20 | 0 | 2021-03-23 | 6.8 | 11.2 | 0 | 2020-03-23 | -5 | 23 | 0 | 2019-03-23 | -4.7 | 22.7 | 0 | 2018-03-23 | 0.2 | 17.8 | 0 | 2017-03-23 | -11.5 | 29.5 | 0 | 2016-03-23 | 0.2 | 17.8 | 0 | 21.26 | 0
2025-03-23 | -9.6 | 27.6 | 0 | 2024-03-23 | -6.3 | 24.3 | 0 | 2023-03-23 | -1.4 | 19.4 | 0 | 2022-03-23 | -2.8 | 20.8 | 0 | 2021-03-23 | 6.8 | 11.2 | 0 | 2020-03-23 | -5 | 23 | 0 | 2019-03-23 | -5.8 | 23.8 | 0 | 2018-03-23 | -0.6 | 18.6 | 0 | 2017-03-23 | -12.9 | 30.9 | 0 | 2016-03-23 | 0 | 18 | 0 | 21.76 | 0
2025-03-23 | -10 | 28 | 0 | 2024-03-23 | -6.9 | 24.9 | 0 | 2023-03-23 | -1.4 | 19.4 | 0 | 2022-03-23 | -3.9 | 21.9 | 0 | 2021-03-23 | 6 | 12 | 0 | 2020-03-23 | -5.2 | 23.2 | 0 | 2019-03-23 | -6.5 | 24.5 | 0 | 2018-03-23 | -1 | 19 | 0 | 2017-03-23 | -12.7 | 30.7 | 0 | 2016-03-23 | -0.3 | 18.3 | 0 | 22.19 | 0
2025-03-23 | -10.4 | 28.4 | 0 | 2024-03-23 | -7.1 | 25.1 | 0 | 2023-03-23 | -1.3 | 19.3 | 0 | 2022-03-23 | -4.3 | 22.3 | 0 | 2021-03-23 | 5.1 | 12.9 | 0 | 2020-03-23 | -5.5 | 23.5 | 0 | 2019-03-23 | -7.3 | 25.3 | 0 | 2018-03-23 | -3 | 21 | 0 | 2017-03-23 | -12.1 | 30.1 | 0 | 2016-03-23 | -0.2 | 18.2 | 0 | 22.61 | 0
2025-03-23 | -10.9 | 28.9 | 0 | 2024-03-23 | -7.2 | 25.2 | 0 | 2023-03-23 | -1.3 | 19.3 | 0 | 2022-03-23 | -4.5 | 22.5 | 0 | 2021-03-23 | 3 | 15 | 0 | 2020-03-23 | -5.5 | 23.5 | 0 | 2019-03-23 | -8.2 | 26.2 | 0 | 2018-03-23 | -3.3 | 21.3 | 0 | 2017-03-23 | -12.2 | 30.2 | 0 | 2016-03-23 | -0.5 | 18.5 | 0 | 23.06 | 0
2025-03-23 | -11.2 | 29.2 | 0 | 2024-03-23 | -7.1 | 25.1 | 0 | 2023-03-23 | -1.3 | 19.3 | 0 | 2022-03-23 | -5.5 | 23.5 | 0 | 2021-03-23 | -0.1 | 18.1 | 0 | 2020-03-23 | -5.1 | 23.1 | 0 | 2019-03-23 | -8.8 | 26.8 | 0 | 2018-03-23 | -4.4 | 22.4 | 0 | 2017-03-23 | -12.9 | 30.9 | 0 | 2016-03-23 | -0.4 | 18.4 | 0 | 23.68 | 0
2025-03-23 | -10.6 | 28.6 | 0 | 2024-03-23 | -7 | 25 | 0 | 2023-03-23 | -1.2 | 19.2 | 0 | 2022-03-23 | -2.9 | 20.9 | 0 | 2021-03-23 | 3.1 | 14.9 | 0 | 2020-03-23 | -4.7 | 22.7 | 0 | 2019-03-23 | -8.9 | 26.9 | 0 | 2018-03-23 | -3.8 | 21.8 | 0 | 2017-03-23 | -11.4 | 29.4 | 0 | 2016-03-23 | -0.3 | 18.3 | 0 | 22.77 | 0
2025-03-23 | -9.5 | 27.5 | 0 | 2024-03-23 | -6.7 | 24.7 | 0 | 2023-03-23 | -0.9 | 18.9 | 0 | 2022-03-23 | -1.9 | 19.9 | 0 | 2021-03-23 | 7.5 | 10.5 | 0 | 2020-03-23 | -4.6 | 22.6 | 0 | 2019-03-23 | -8.3 | 26.3 | 0 | 2018-03-23 | -2.8 | 20.8 | 0 | 2017-03-23 | -8.1 | 26.1 | 0 | 2016-03-23 | -0.4 | 18.4 | 0 | 21.57 | 0
2025-03-23 | -8.9 | 26.9 | 0 | 2024-03-23 | -6 | 24 | 0 | 2023-03-23 | -0.8 | 18.8 | 0 | 2022-03-23 | -0.4 | 18.4 | 0 | 2021-03-23 | 10 | 8 | 0 | 2020-03-23 | -3.6 | 21.6 | 0 | 2019-03-23 | -7.2 | 25.2 | 0 | 2018-03-23 | -2 | 20 | 0 | 2017-03-23 | -6.8 | 24.8 | 0 | 2016-03-23 | -1.1 | 19.1 | 0 | 20.68 | 0
2025-03-23 | -7.8 | 25.8 | 0 | 2024-03-23 | -5.8 | 23.8 | 0 | 2023-03-23 | 0 | 18 | 0 | 2022-03-23 | 0.6 | 17.4 | 0 | 2021-03-23 | 13.1 | 4.9 | 0 | 2020-03-23 | -2.5 | 20.5 | 0 | 2019-03-23 | -7.1 | 25.1 | 0 | 2018-03-23 | -0.4 | 18.4 | 0 | 2017-03-23 | -4.8 | 22.8 | 0 | 2016-03-23 | -0.2 | 18.2 | 0 | 19.49 | 0
2025-03-23 | -6.3 | 24.3 | 0 | 2024-03-23 | -4.9 | 22.9 | 0 | 2023-03-23 | 0.2 | 17.8 | 0 | 2022-03-23 | 1.4 | 16.6 | 0 | 2021-03-23 | 15.5 | 2.5 | 0 | 2020-03-23 | -1.3 | 19.3 | 0 | 2019-03-23 | -6 | 24 | 0 | 2018-03-23 | 0.6 | 17.4 | 0 | 2017-03-23 | -3.3 | 21.3 | 0 | 2016-03-23 | -0.2 | 18.2 | 0 | 18.43 | 0
2025-03-23 | -5.3 | 23.3 | 0 | 2024-03-23 | -4.3 | 22.3 | 0 | 2023-03-23 | 0.2 | 17.8 | 0 | 2022-03-23 | 2.7 | 15.3 | 0 | 2021-03-23 | 17.7 | 0.3 | 0 | 2020-03-23 | -0.8 | 18.8 | 0 | 2019-03-23 | -4.7 | 22.7 | 0 | 2018-03-23 | 2.2 | 15.8 | 0 | 2017-03-23 | -1.1 | 19.1 | 0 | 2016-03-23 | 0.6 | 17.4 | 0 | 17.28 | 0
2025-03-23 | -3.5 | 21.5 | 0 | 2024-03-23 | -3.3 | 21.3 | 0 | 2023-03-23 | 0.5 | 17.5 | 0 | 2022-03-23 | 3.6 | 14.4 | 0 | 2021-03-23 | 18.8 | 0 | 0.8 | 2020-03-23 | -1 | 19 | 0 | 2019-03-23 | -4 | 22 | 0 | 2018-03-23 | 3.4 | 14.6 | 0 | 2017-03-23 | -0.7 | 18.7 | 0 | 2016-03-23 | 1.2 | 16.8 | 0 | 16.58 | 0.08
2025-03-23 | -2 | 20 | 0 | 2024-03-23 | -2 | 20 | 0 | 2023-03-23 | 1.3 | 16.7 | 0 | 2022-03-23 | 3.2 | 14.8 | 0 | 2021-03-23 | 19.8 | 0 | 1.8 | 2020-03-23 | -0.8 | 18.8 | 0 | 2019-03-23 | -2.6 | 20.6 | 0 | 2018-03-23 | 3.8 | 14.2 | 0 | 2017-03-23 | 0.2 | 17.8 | 0 | 2016-03-23 | 2.5 | 15.5 | 0 | 15.84 | 0.18
2025-03-23 | -1.8 | 19.8 | 0 | 2024-03-23 | -1.5 | 19.5 | 0 | 2023-03-23 | 1.9 | 16.1 | 0 | 2022-03-23 | 3.8 | 14.2 | 0 | 2021-03-23 | 19.5 | 0 | 1.5 | 2020-03-23 | -0.2 | 18.2 | 0 | 2019-03-23 | -1.1 | 19.1 | 0 | 2018-03-23 | 4 | 14 | 0 | 2017-03-23 | 0.6 | 17.4 | 0 | 2016-03-23 | 2.8 | 15.2 | 0 | 15.35 | 0.15
2025-03-23 | -1.5 | 19.5 | 0 | 2024-03-23 | -2.1 | 20.1 | 0 | 2023-03-23 | 2.6 | 15.4 | 0 | 2022-03-23 | 3.2 | 14.8 | 0 | 2021-03-23 | 18.4 | 0 | 0.4 | 2020-03-23 | 0 | 18 | 0 | 2019-03-23 | -0.1 | 18.1 | 0 | 2018-03-23 | 4.3 | 13.7 | 0 | 2017-03-23 | 1.1 | 16.9 | 0 | 2016-03-23 | 3.1 | 14.9 | 0 | 15.14 | 0.04
2025-03-23 | -1.1 | 19.1 | 0 | 2024-03-23 | -2.1 | 20.1 | 0 | 2023-03-23 | 2.9 | 15.1 | 0 | 2022-03-23 | 3 | 15 | 0 | 2021-03-23 | 17.6 | 0.4 | 0 | 2020-03-23 | -0.2 | 18.2 | 0 | 2019-03-23 | 0.4 | 17.6 | 0 | 2018-03-23 | 4 | 14 | 0 | 2017-03-23 | 1.5 | 16.5 | 0 | 2016-03-23 | 1.9 | 16.1 | 0 | 15.21 | 0
2025-03-23 | -2.8 | 20.8 | 0 | 2024-03-23 | -3.6 | 21.6 | 0 | 2023-03-23 | 2.9 | 15.1 | 0 | 2022-03-23 | 2.4 | 15.6 | 0 | 2021-03-23 | 13.9 | 4.1 | 0 | 2020-03-23 | -0.4 | 18.4 | 0 | 2019-03-23 | 0.1 | 17.9 | 0 | 2018-03-23 | 3.5 | 14.5 | 0 | 2017-03-23 | -0.1 | 18.1 | 0 | 2016-03-23 | 1 | 17 | 0 | 16.31 | 0
2025-03-23 | -4.2 | 22.2 | 0 | 2024-03-23 | -5.9 | 23.9 | 0 | 2023-03-23 | 2.3 | 15.7 | 0 | 2022-03-23 | 1.9 | 16.1 | 0 | 2021-03-23 | 12.6 | 5.4 | 0 | 2020-03-23 | -0.8 | 18.8 | 0 | 2019-03-23 | -1.6 | 19.6 | 0 | 2018-03-23 | 2.3 | 15.7 | 0 | 2017-03-23 | 0.1 | 17.9 | 0 | 2016-03-23 | -0.1 | 18.1 | 0 | 17.34 | 0
2025-03-23 | -6 | 24 | 0 | 2024-03-23 | -6.4 | 24.4 | 0 | 2023-03-23 | 2.8 | 15.2 | 0 | 2022-03-23 | 1.9 | 16.1 | 0 | 2021-03-23 | 10.6 | 7.4 | 0 | 2020-03-23 | -1 | 19 | 0 | 2019-03-23 | -1.5 | 19.5 | 0 | 2018-03-23 | 1.8 | 16.2 | 0 | 2017-03-23 | -1 | 19 | 0 | 2016-03-23 | -0.4 | 18.4 | 0 | 17.92 | 0
2025-03-23 | -5.4 | 23.4 | 0 | 2024-03-23 | -6.8 | 24.8 | 0 | 2023-03-23 | 2.8 | 15.2 | 0 | 2022-03-23 | 1.4 | 16.6 | 0 | 2021-03-23 | 9 | 9 | 0 | 2020-03-23 | -1 | 19 | 0 | 2019-03-23 | -1.7 | 19.7 | 0 | 2018-03-23 | 1 | 17 | 0 | 2017-03-23 | -1.4 | 19.4 | 0 | 2016-03-23 | -0.5 | 18.5 | 0 | 18.26 | 0
2025-03-23 | -5.3 | 23.3 | 0 | 2024-03-23 | -7.2 | 25.2 | 0 | 2023-03-23 | 2 | 16 | 0 | 2022-03-23 | 0.7 | 17.3 | 0 | 2021-03-23 | 6.2 | 11.8 | 0 | 2020-03-23 | -1 | 19 | 0 | 2019-03-23 | -1.3 | 19.3 | 0 | 2018-03-23 | 0.1 | 17.9 | 0 | 2017-03-23 | -1.7 | 19.7 | 0 | 2016-03-23 | -1 | 19 | 0 | 18.85 | 0
2025-03-23 | -5.5 | 23.5 | 0 | 2024-03-23 | -7.7 | 25.7 | 0 | 2023-03-23 | 1.1 | 16.9 | 0 | 2022-03-23 | 0.6 | 17.4 | 0 | 2021-03-23 | 5.6 | 12.4 | 0 | 2020-03-23 | -1.3 | 19.3 | 0 | 2019-03-23 | -2.4 | 20.4 | 0 | 2018-03-23 | -0.8 | 18.8 | 0 | 2017-03-23 | -1.8 | 19.8 | 0 | 2016-03-23 | -1.6 | 19.6 | 0 | 19.38 | 0
2025-03-24 | -4.6 | 22.6 | 0 | 2024-03-24 | -8.3 | 26.3 | 0 | 2023-03-24 | 1.6 | 16.4 | 0 | 2022-03-24 | 0.2 | 17.8 | 0 | 2021-03-24 | 5.6 | 12.4 | 0 | 2020-03-24 | -1.5 | 19.5 | 0 | 2019-03-24 | -2.7 | 20.7 | 0 | 2018-03-24 | -1.3 | 19.3 | 0 | 2017-03-24 | -2 | 20 | 0 | 2016-03-24 | -1.9 | 19.9 | 0 | 19.49 | 0
2025-03-24 | -4.3 | 22.3 | 0 | 2024-03-24 | -8.2 | 26.2 | 0 | 2023-03-24 | 1.1 | 16.9 | 0 | 2022-03-24 | 0.3 | 17.7 | 0 | 2021-03-24 | 7.6 | 10.4 | 0 | 2020-03-24 | -1.4 | 19.4 | 0 | 2019-03-24 | -2.9 | 20.9 | 0 | 2018-03-24 | -1.9 | 19.9 | 0 | 2017-03-24 | -1.9 | 19.9 | 0 | 2016-03-24 | -2 | 20 | 0 | 19.36 | 0
2025-03-24 | -4.3 | 22.3 | 0 | 2024-03-24 | -8 | 26 | 0 | 2023-03-24 | 1.3 | 16.7 | 0 | 2022-03-24 | 0.5 | 17.5 | 0 | 2021-03-24 | 7.5 | 10.5 | 0 | 2020-03-24 | -1.3 | 19.3 | 0 | 2019-03-24 | -3.6 | 21.6 | 0 | 2018-03-24 | -3 | 21 | 0 | 2017-03-24 | -2.3 | 20.3 | 0 | 2016-03-24 | -2.2 | 20.2 | 0 | 19.54 | 0
2025-03-24 | -3.9 | 21.9 | 0 | 2024-03-24 | -6 | 24 | 0 | 2023-03-24 | 0.8 | 17.2 | 0 | 2022-03-24 | 1 | 17 | 0 | 2021-03-24 | 7.4 | 10.6 | 0 | 2020-03-24 | -1.3 | 19.3 | 0 | 2019-03-24 | -3.9 | 21.9 | 0 | 2018-03-24 | -3.7 | 21.7 | 0 | 2017-03-24 | -2.5 | 20.5 | 0 | 2016-03-24 | -2.5 | 20.5 | 0 | 19.46 | 0
2025-03-24 | -3.5 | 21.5 | 0 | 2024-03-24 | -6.9 | 24.9 | 0 | 2023-03-24 | 0.6 | 17.4 | 0 | 2022-03-24 | 1.2 | 16.8 | 0 | 2021-03-24 | 4 | 14 | 0 | 2020-03-24 | -1.7 | 19.7 | 0 | 2019-03-24 | -3.6 | 21.6 | 0 | 2018-03-24 | -4.8 | 22.8 | 0 | 2017-03-24 | -2.3 | 20.3 | 0 | 2016-03-24 | -2.7 | 20.7 | 0 | 19.97 | 0
2025-03-24 | -3.6 | 21.6 | 0 | 2024-03-24 | -8 | 26 | 0 | 2023-03-24 | 0.2 | 17.8 | 0 | 2022-03-24 | 1.5 | 16.5 | 0 | 2021-03-24 | 3.5 | 14.5 | 0 | 2020-03-24 | -1.8 | 19.8 | 0 | 2019-03-24 | -3.8 | 21.8 | 0 | 2018-03-24 | -5.8 | 23.8 | 0 | 2017-03-24 | -3.9 | 21.9 | 0 | 2016-03-24 | -2.8 | 20.8 | 0 | 20.45 | 0
2025-03-24 | -4.6 | 22.6 | 0 | 2024-03-24 | -8.7 | 26.7 | 0 | 2023-03-24 | -0.4 | 18.4 | 0 | 2022-03-24 | 1.5 | 16.5 | 0 | 2021-03-24 | 4.1 | 13.9 | 0 | 2020-03-24 | -1.9 | 19.9 | 0 | 2019-03-24 | -4.3 | 22.3 | 0 | 2018-03-24 | -6.6 | 24.6 | 0 | 2017-03-24 | -4.3 | 22.3 | 0 | 2016-03-24 | -3.8 | 21.8 | 0 | 20.9 | 0
2025-03-24 | -4.9 | 22.9 | 0 | 2024-03-24 | -8.2 | 26.2 | 0 | 2023-03-24 | -0.1 | 18.1 | 0 | 2022-03-24 | 1.7 | 16.3 | 0 | 2021-03-24 | 4.8 | 13.2 | 0 | 2020-03-24 | -1.7 | 19.7 | 0 | 2019-03-24 | -3.4 | 21.4 | 0 | 2018-03-24 | -6.7 | 24.7 | 0 | 2017-03-24 | -4 | 22 | 0 | 2016-03-24 | -4.8 | 22.8 | 0 | 20.73 | 0
2025-03-24 | -4.6 | 22.6 | 0 | 2024-03-24 | -7.2 | 25.2 | 0 | 2023-03-24 | -0.6 | 18.6 | 0 | 2022-03-24 | 2.1 | 15.9 | 0 | 2021-03-24 | 6.9 | 11.1 | 0 | 2020-03-24 | -1.3 | 19.3 | 0 | 2019-03-24 | -1.6 | 19.6 | 0 | 2018-03-24 | -6.5 | 24.5 | 0 | 2017-03-24 | -3.7 | 21.7 | 0 | 2016-03-24 | -5.8 | 23.8 | 0 | 20.23 | 0
2025-03-24 | -4 | 22 | 0 | 2024-03-24 | -6.1 | 24.1 | 0 | 2023-03-24 | -0.4 | 18.4 | 0 | 2022-03-24 | 2.5 | 15.5 | 0 | 2021-03-24 | 8.8 | 9.2 | 0 | 2020-03-24 | -0.8 | 18.8 | 0 | 2019-03-24 | 0.4 | 17.6 | 0 | 2018-03-24 | -6.1 | 24.1 | 0 | 2017-03-24 | -2.8 | 20.8 | 0 | 2016-03-24 | -6.8 | 24.8 | 0 | 19.53 | 0
2025-03-24 | -2.1 | 20.1 | 0 | 2024-03-24 | -5 | 23 | 0 | 2023-03-24 | 0.2 | 17.8 | 0 | 2022-03-24 | 2.9 | 15.1 | 0 | 2021-03-24 | 10.4 | 7.6 | 0 | 2020-03-24 | -0.2 | 18.2 | 0 | 2019-03-24 | 2 | 16 | 0 | 2018-03-24 | -5.5 | 23.5 | 0 | 2017-03-24 | -1.9 | 19.9 | 0 | 2016-03-24 | -6.8 | 24.8 | 0 | 18.6 | 0
2025-03-24 | -0.3 | 18.3 | 0 | 2024-03-24 | -3.2 | 21.2 | 0 | 2023-03-24 | 0.5 | 17.5 | 0 | 2022-03-24 | 3.7 | 14.3 | 0 | 2021-03-24 | 9.9 | 8.1 | 0 | 2020-03-24 | 0.3 | 17.7 | 0 | 2019-03-24 | 2.6 | 15.4 | 0 | 2018-03-24 | -4.7 | 22.7 | 0 | 2017-03-24 | -1.3 | 19.3 | 0 | 2016-03-24 | -6.7 | 24.7 | 0 | 17.92 | 0
2025-03-24 | 3 | 15 | 0 | 2024-03-24 | -2 | 20 | 0 | 2023-03-24 | 1.1 | 16.9 | 0 | 2022-03-24 | 4.8 | 13.2 | 0 | 2021-03-24 | 9.7 | 8.3 | 0 | 2020-03-24 | 1 | 17 | 0 | 2019-03-24 | 3.2 | 14.8 | 0 | 2018-03-24 | -3.9 | 21.9 | 0 | 2017-03-24 | -1 | 19 | 0 | 2016-03-24 | -6.9 | 24.9 | 0 | 17.1 | 0
2025-03-24 | 4.9 | 13.1 | 0 | 2024-03-24 | -0.7 | 18.7 | 0 | 2023-03-24 | 1.7 | 16.3 | 0 | 2022-03-24 | 7 | 11 | 0 | 2021-03-24 | 10.3 | 7.7 | 0 | 2020-03-24 | 1.7 | 16.3 | 0 | 2019-03-24 | 3.1 | 14.9 | 0 | 2018-03-24 | -3.3 | 21.3 | 0 | 2017-03-24 | -0.6 | 18.6 | 0 | 2016-03-24 | -6.7 | 24.7 | 0 | 16.26 | 0
2025-03-24 | 4.4 | 13.6 | 0 | 2024-03-24 | 0.1 | 17.9 | 0 | 2023-03-24 | 2.1 | 15.9 | 0 | 2022-03-24 | 8.1 | 9.9 | 0 | 2021-03-24 | 10.2 | 7.8 | 0 | 2020-03-24 | 2.4 | 15.6 | 0 | 2019-03-24 | 2.9 | 15.1 | 0 | 2018-03-24 | -2.2 | 20.2 | 0 | 2017-03-24 | 0.1 | 17.9 | 0 | 2016-03-24 | -6.2 | 24.2 | 0 | 15.81 | 0
2025-03-24 | 4.8 | 13.2 | 0 | 2024-03-24 | 0.6 | 17.4 | 0 | 2023-03-24 | 2.1 | 15.9 | 0 | 2022-03-24 | 8.8 | 9.2 | 0 | 2021-03-24 | 10.1 | 7.9 | 0 | 2020-03-24 | 3.1 | 14.9 | 0 | 2019-03-24 | 1.2 | 16.8 | 0 | 2018-03-24 | -1.5 | 19.5 | 0 | 2017-03-24 | 0.2 | 17.8 | 0 | 2016-03-24 | -6.1 | 24.1 | 0 | 15.67 | 0
2025-03-24 | 5.2 | 12.8 | 0 | 2024-03-24 | 1.1 | 16.9 | 0 | 2023-03-24 | 2 | 16 | 0 | 2022-03-24 | 9.4 | 8.6 | 0 | 2021-03-24 | 10.4 | 7.6 | 0 | 2020-03-24 | 3.9 | 14.1 | 0 | 2019-03-24 | 0 | 18 | 0 | 2018-03-24 | -1.5 | 19.5 | 0 | 2017-03-24 | 0.2 | 17.8 | 0 | 2016-03-24 | -5.8 | 23.8 | 0 | 15.51 | 0
2025-03-24 | 5.5 | 12.5 | 0 | 2024-03-24 | 0.7 | 17.3 | 0 | 2023-03-24 | 1.8 | 16.2 | 0 | 2022-03-24 | 10.1 | 7.9 | 0 | 2021-03-24 | 9.9 | 8.1 | 0 | 2020-03-24 | 4.3 | 13.7 | 0 | 2019-03-24 | -1.2 | 19.2 | 0 | 2018-03-24 | -2 | 20 | 0 | 2017-03-24 | 0.2 | 17.8 | 0 | 2016-03-24 | -5.6 | 23.6 | 0 | 15.63 | 0
2025-03-24 | 7 | 11 | 0 | 2024-03-24 | -1.6 | 19.6 | 0 | 2023-03-24 | 1 | 17 | 0 | 2022-03-24 | 8.1 | 9.9 | 0 | 2021-03-24 | 9.6 | 8.4 | 0 | 2020-03-24 | 3.3 | 14.7 | 0 | 2019-03-24 | -1.9 | 19.9 | 0 | 2018-03-24 | -2.6 | 20.6 | 0 | 2017-03-24 | 0 | 18 | 0 | 2016-03-24 | -5.6 | 23.6 | 0 | 16.27 | 0
2025-03-24 | 5.7 | 12.3 | 0 | 2024-03-24 | -1.8 | 19.8 | 0 | 2023-03-24 | -0.2 | 18.2 | 0 | 2022-03-24 | 7.1 | 10.9 | 0 | 2021-03-24 | 9.2 | 8.8 | 0 | 2020-03-24 | 3 | 15 | 0 | 2019-03-24 | -2.4 | 20.4 | 0 | 2018-03-24 | -3.3 | 21.3 | 0 | 2017-03-24 | 0 | 18 | 0 | 2016-03-24 | -5.1 | 23.1 | 0 | 16.78 | 0
2025-03-24 | 3.5 | 14.5 | 0 | 2024-03-24 | -2.1 | 20.1 | 0 | 2023-03-24 | 0.1 | 17.9 | 0 | 2022-03-24 | 6 | 12 | 0 | 2021-03-24 | 8.7 | 9.3 | 0 | 2020-03-24 | 1.6 | 16.4 | 0 | 2019-03-24 | -2.6 | 20.6 | 0 | 2018-03-24 | -3 | 21 | 0 | 2017-03-24 | 0 | 18 | 0 | 2016-03-24 | -4.5 | 22.5 | 0 | 17.23 | 0
2025-03-24 | 2.7 | 15.3 | 0 | 2024-03-24 | -2.9 | 20.9 | 0 | 2023-03-24 | -0.4 | 18.4 | 0 | 2022-03-24 | 5.8 | 12.2 | 0 | 2021-03-24 | 8.9 | 9.1 | 0 | 2020-03-24 | -0.3 | 18.3 | 0 | 2019-03-24 | -3.4 | 21.4 | 0 | 2018-03-24 | -3.6 | 21.6 | 0 | 2017-03-24 | -0.1 | 18.1 | 0 | 2016-03-24 | -4 | 22 | 0 | 17.73 | 0
2025-03-24 | 1.8 | 16.2 | 0 | 2024-03-24 | -4.9 | 22.9 | 0 | 2023-03-24 | -1 | 19 | 0 | 2022-03-24 | 5.1 | 12.9 | 0 | 2021-03-24 | 9.3 | 8.7 | 0 | 2020-03-24 | 0.1 | 17.9 | 0 | 2019-03-24 | -4.2 | 22.2 | 0 | 2018-03-24 | -3.8 | 21.8 | 0 | 2017-03-24 | -0.3 | 18.3 | 0 | 2016-03-24 | -3.6 | 21.6 | 0 | 18.15 | 0
2025-03-24 | 1.4 | 16.6 | 0 | 2024-03-24 | -4.8 | 22.8 | 0 | 2023-03-24 | -1.6 | 19.6 | 0 | 2022-03-24 | 5.1 | 12.9 | 0 | 2021-03-24 | 10.8 | 7.2 | 0 | 2020-03-24 | -1.7 | 19.7 | 0 | 2019-03-24 | -4.7 | 22.7 | 0 | 2018-03-24 | -4.2 | 22.2 | 0 | 2017-03-24 | -0.4 | 18.4 | 0 | 2016-03-24 | -3.4 | 21.4 | 0 | 18.35 | 0
2025-03-25 | 0.8 | 17.2 | 0 | 2024-03-25 | -6 | 24 | 0 | 2023-03-25 | -1.9 | 19.9 | 0 | 2022-03-25 | 4.3 | 13.7 | 0 | 2021-03-25 | 10.2 | 7.8 | 0 | 2020-03-25 | -1.4 | 19.4 | 0 | 2019-03-25 | -5.6 | 23.6 | 0 | 2018-03-25 | -4.8 | 22.8 | 0 | 2017-03-25 | -0.3 | 18.3 | 0 | 2016-03-25 | -3 | 21 | 0 | 18.77 | 0
2025-03-25 | 0.4 | 17.6 | 0 | 2024-03-25 | -5.1 | 23.1 | 0 | 2023-03-25 | -2.5 | 20.5 | 0 | 2022-03-25 | 3.8 | 14.2 | 0 | 2021-03-25 | 9.4 | 8.6 | 0 | 2020-03-25 | -2.3 | 20.3 | 0 | 2019-03-25 | -6.8 | 24.8 | 0 | 2018-03-25 | -5.6 | 23.6 | 0 | 2017-03-25 | -0.8 | 18.8 | 0 | 2016-03-25 | -2.4 | 20.4 | 0 | 19.19 | 0
2025-03-25 | 0.2 | 17.8 | 0 | 2024-03-25 | -5.2 | 23.2 | 0 | 2023-03-25 | -2.7 | 20.7 | 0 | 2022-03-25 | 3 | 15 | 0 | 2021-03-25 | 8 | 10 | 0 | 2020-03-25 | -2.5 | 20.5 | 0 | 2019-03-25 | -7.6 | 25.6 | 0 | 2018-03-25 | -5.9 | 23.9 | 0 | 2017-03-25 | -0.7 | 18.7 | 0 | 2016-03-25 | -2.4 | 20.4 | 0 | 19.58 | 0
2025-03-25 | 0.4 | 17.6 | 0 | 2024-03-25 | -6 | 24 | 0 | 2023-03-25 | -2.7 | 20.7 | 0 | 2022-03-25 | 2.6 | 15.4 | 0 | 2021-03-25 | 7.8 | 10.2 | 0 | 2020-03-25 | -3.4 | 21.4 | 0 | 2019-03-25 | -7.4 | 25.4 | 0 | 2018-03-25 | -5.7 | 23.7 | 0 | 2017-03-25 | 0 | 18 | 0 | 2016-03-25 | -2 | 20 | 0 | 19.64 | 0
2025-03-25 | 0.7 | 17.3 | 0 | 2024-03-25 | -6.4 | 24.4 | 0 | 2023-03-25 | -3.7 | 21.7 | 0 | 2022-03-25 | 2.3 | 15.7 | 0 | 2021-03-25 | 8 | 10 | 0 | 2020-03-25 | -3.5 | 21.5 | 0 | 2019-03-25 | -7 | 25 | 0 | 2018-03-25 | -5.3 | 23.3 | 0 | 2017-03-25 | -1.3 | 19.3 | 0 | 2016-03-25 | -1.7 | 19.7 | 0 | 19.79 | 0
2025-03-25 | 0.6 | 17.4 | 0 | 2024-03-25 | -6.1 | 24.1 | 0 | 2023-03-25 | -3.6 | 21.6 | 0 | 2022-03-25 | 2.1 | 15.9 | 0 | 2021-03-25 | 9.3 | 8.7 | 0 | 2020-03-25 | -3.6 | 21.6 | 0 | 2019-03-25 | -8.6 | 26.6 | 0 | 2018-03-25 | -5.3 | 23.3 | 0 | 2017-03-25 | -2.9 | 20.9 | 0 | 2016-03-25 | -1.4 | 19.4 | 0 | 19.95 | 0
2025-03-25 | 0.4 | 17.6 | 0 | 2024-03-25 | -5.8 | 23.8 | 0 | 2023-03-25 | -3.7 | 21.7 | 0 | 2022-03-25 | 1.3 | 16.7 | 0 | 2021-03-25 | 9.9 | 8.1 | 0 | 2020-03-25 | -2.5 | 20.5 | 0 | 2019-03-25 | -9.8 | 27.8 | 0 | 2018-03-25 | -5 | 23 | 0 | 2017-03-25 | -3 | 21 | 0 | 2016-03-25 | -1.3 | 19.3 | 0 | 19.95 | 0
2025-03-25 | 0.7 | 17.3 | 0 | 2024-03-25 | -4 | 22 | 0 | 2023-03-25 | -3.2 | 21.2 | 0 | 2022-03-25 | 3.1 | 14.9 | 0 | 2021-03-25 | 10.2 | 7.8 | 0 | 2020-03-25 | -2 | 20 | 0 | 2019-03-25 | -10.1 | 28.1 | 0 | 2018-03-25 | -5.1 | 23.1 | 0 | 2017-03-25 | -1.1 | 19.1 | 0 | 2016-03-25 | -1 | 19 | 0 | 19.25 | 0
2025-03-25 | 1.6 | 16.4 | 0 | 2024-03-25 | -1.3 | 19.3 | 0 | 2023-03-25 | -2.5 | 20.5 | 0 | 2022-03-25 | 5.8 | 12.2 | 0 | 2021-03-25 | 11.1 | 6.9 | 0 | 2020-03-25 | -1.1 | 19.1 | 0 | 2019-03-25 | -7.8 | 25.8 | 0 | 2018-03-25 | -4.4 | 22.4 | 0 | 2017-03-25 | -0.4 | 18.4 | 0 | 2016-03-25 | -0.8 | 18.8 | 0 | 17.98 | 0
2025-03-25 | 2 | 16 | 0 | 2024-03-25 | 1.2 | 16.8 | 0 | 2023-03-25 | -1.7 | 19.7 | 0 | 2022-03-25 | 6.6 | 11.4 | 0 | 2021-03-25 | 12.3 | 5.7 | 0 | 2020-03-25 | 1.2 | 16.8 | 0 | 2019-03-25 | -6 | 24 | 0 | 2018-03-25 | -2.5 | 20.5 | 0 | 2017-03-25 | -0.2 | 18.2 | 0 | 2016-03-25 | -0.8 | 18.8 | 0 | 16.79 | 0
2025-03-25 | 2.2 | 15.8 | 0 | 2024-03-25 | 2.9 | 15.1 | 0 | 2023-03-25 | -0.7 | 18.7 | 0 | 2022-03-25 | 8.1 | 9.9 | 0 | 2021-03-25 | 14.5 | 3.5 | 0 | 2020-03-25 | 3.1 | 14.9 | 0 | 2019-03-25 | -5.1 | 23.1 | 0 | 2018-03-25 | -0.8 | 18.8 | 0 | 2017-03-25 | -0.2 | 18.2 | 0 | 2016-03-25 | -1.1 | 19.1 | 0 | 15.71 | 0
2025-03-25 | 2.8 | 15.2 | 0 | 2024-03-25 | 4.4 | 13.6 | 0 | 2023-03-25 | -0.6 | 18.6 | 0 | 2022-03-25 | 8.1 | 9.9 | 0 | 2021-03-25 | 16.8 | 1.2 | 0 | 2020-03-25 | 4 | 14 | 0 | 2019-03-25 | -4 | 22 | 0 | 2018-03-25 | 0.9 | 17.1 | 0 | 2017-03-25 | 0 | 18 | 0 | 2016-03-25 | -1.4 | 19.4 | 0 | 14.9 | 0
2025-03-25 | 3.7 | 14.3 | 0 | 2024-03-25 | 6.1 | 11.9 | 0 | 2023-03-25 | -0.4 | 18.4 | 0 | 2022-03-25 | 9.6 | 8.4 | 0 | 2021-03-25 | 18.6 | 0 | 0.6 | 2020-03-25 | 4.7 | 13.3 | 0 | 2019-03-25 | -3.4 | 21.4 | 0 | 2018-03-25 | 1.6 | 16.4 | 0 | 2017-03-25 | 0.1 | 17.9 | 0 | 2016-03-25 | -1.7 | 19.7 | 0 | 14.17 | 0.06
2025-03-25 | 3.1 | 14.9 | 0 | 2024-03-25 | 7.8 | 10.2 | 0 | 2023-03-25 | -0.3 | 18.3 | 0 | 2022-03-25 | 8.6 | 9.4 | 0 | 2021-03-25 | 18.9 | 0 | 0.9 | 2020-03-25 | 5.2 | 12.8 | 0 | 2019-03-25 | -2 | 20 | 0 | 2018-03-25 | 2.5 | 15.5 | 0 | 2017-03-25 | 1.2 | 16.8 | 0 | 2016-03-25 | -2 | 20 | 0 | 13.79 | 0.09
2025-03-25 | 2.5 | 15.5 | 0 | 2024-03-25 | 8.5 | 9.5 | 0 | 2023-03-25 | -0.5 | 18.5 | 0 | 2022-03-25 | 8.1 | 9.9 | 0 | 2021-03-25 | 18.9 | 0 | 0.9 | 2020-03-25 | 4.6 | 13.4 | 0 | 2019-03-25 | -1.3 | 19.3 | 0 | 2018-03-25 | 3.6 | 14.4 | 0 | 2017-03-25 | 1.8 | 16.2 | 0 | 2016-03-25 | -1.8 | 19.8 | 0 | 13.65 | 0.09
2025-03-25 | 3.2 | 14.8 | 0 | 2024-03-25 | 9.5 | 8.5 | 0 | 2023-03-25 | -0.8 | 18.8 | 0 | 2022-03-25 | 6.5 | 11.5 | 0 | 2021-03-25 | 18.6 | 0 | 0.6 | 2020-03-25 | 4.4 | 13.6 | 0 | 2019-03-25 | -0.4 | 18.4 | 0 | 2018-03-25 | 3.6 | 14.4 | 0 | 2017-03-25 | 2.3 | 15.7 | 0 | 2016-03-25 | -1.6 | 19.6 | 0 | 13.53 | 0.06
2025-03-25 | 3.2 | 14.8 | 0 | 2024-03-25 | 8.8 | 9.2 | 0 | 2023-03-25 | -0.4 | 18.4 | 0 | 2022-03-25 | 5.2 | 12.8 | 0 | 2021-03-25 | 18.5 | 0 | 0.5 | 2020-03-25 | 4.2 | 13.8 | 0 | 2019-03-25 | 0.2 | 17.8 | 0 | 2018-03-25 | 4.2 | 13.8 | 0 | 2017-03-25 | 2.8 | 15.2 | 0 | 2016-03-25 | -1.3 | 19.3 | 0 | 13.51 | 0.05
2025-03-25 | 2.3 | 15.7 | 0 | 2024-03-25 | 7.5 | 10.5 | 0 | 2023-03-25 | 0 | 18 | 0 | 2022-03-25 | 4.8 | 13.2 | 0 | 2021-03-25 | 17.2 | 0.8 | 0 | 2020-03-25 | 3.8 | 14.2 | 0 | 2019-03-25 | -0.1 | 18.1 | 0 | 2018-03-25 | 3.7 | 14.3 | 0 | 2017-03-25 | 2.9 | 15.1 | 0 | 2016-03-25 | -1 | 19 | 0 | 13.89 | 0
2025-03-25 | 1.3 | 16.7 | 0 | 2024-03-25 | 5.9 | 12.1 | 0 | 2023-03-25 | 0.2 | 17.8 | 0 | 2022-03-25 | 4.2 | 13.8 | 0 | 2021-03-25 | 15.6 | 2.4 | 0 | 2020-03-25 | 3.4 | 14.6 | 0 | 2019-03-25 | -0.1 | 18.1 | 0 | 2018-03-25 | 2 | 16 | 0 | 2017-03-25 | 1.7 | 16.3 | 0 | 2016-03-25 | -0.7 | 18.7 | 0 | 14.65 | 0
2025-03-25 | 0.8 | 17.2 | 0 | 2024-03-25 | 4.2 | 13.8 | 0 | 2023-03-25 | 0.2 | 17.8 | 0 | 2022-03-25 | 3.6 | 14.4 | 0 | 2021-03-25 | 13.7 | 4.3 | 0 | 2020-03-25 | 3 | 15 | 0 | 2019-03-25 | -1.8 | 19.8 | 0 | 2018-03-25 | -0.3 | 18.3 | 0 | 2017-03-25 | -0.2 | 18.2 | 0 | 2016-03-25 | -2.9 | 20.9 | 0 | 15.97 | 0
2025-03-25 | 0.6 | 17.4 | 0 | 2024-03-25 | 3.3 | 14.7 | 0 | 2023-03-25 | 0.4 | 17.6 | 0 | 2022-03-25 | 3.1 | 14.9 | 0 | 2021-03-25 | 10.7 | 7.3 | 0 | 2020-03-25 | 2.8 | 15.2 | 0 | 2019-03-25 | -2.7 | 20.7 | 0 | 2018-03-25 | 0 | 18 | 0 | 2017-03-25 | -1.7 | 19.7 | 0 | 2016-03-25 | -3.8 | 21.8 | 0 | 16.73 | 0
2025-03-25 | 0.1 | 17.9 | 0 | 2024-03-25 | 2.7 | 15.3 | 0 | 2023-03-25 | 0.4 | 17.6 | 0 | 2022-03-25 | 2.9 | 15.1 | 0 | 2021-03-25 | 9.6 | 8.4 | 0 | 2020-03-25 | 2.8 | 15.2 | 0 | 2019-03-25 | -4.7 | 22.7 | 0 | 2018-03-25 | -1.7 | 19.7 | 0 | 2017-03-25 | -5 | 23 | 0 | 2016-03-25 | -5 | 23 | 0 | 17.79 | 0
2025-03-25 | -0.4 | 18.4 | 0 | 2024-03-25 | 2 | 16 | 0 | 2023-03-25 | 0.5 | 17.5 | 0 | 2022-03-25 | 2.4 | 15.6 | 0 | 2021-03-25 | 10.7 | 7.3 | 0 | 2020-03-25 | 2.3 | 15.7 | 0 | 2019-03-25 | -5.1 | 23.1 | 0 | 2018-03-25 | -0.9 | 18.9 | 0 | 2017-03-25 | -2.7 | 20.7 | 0 | 2016-03-25 | -3.8 | 21.8 | 0 | 17.5 | 0
2025-03-25 | -0.8 | 18.8 | 0 | 2024-03-25 | 1.1 | 16.9 | 0 | 2023-03-25 | 0.8 | 17.2 | 0 | 2022-03-25 | 1.8 | 16.2 | 0 | 2021-03-25 | 11 | 7 | 0 | 2020-03-25 | 1.7 | 16.3 | 0 | 2019-03-25 | -4.6 | 22.6 | 0 | 2018-03-25 | -2.5 | 20.5 | 0 | 2017-03-25 | -3.2 | 21.2 | 0 | 2016-03-25 | -4.2 | 22.2 | 0 | 17.89 | 0
2025-03-26 | -1.4 | 19.4 | 0 | 2024-03-26 | 1.2 | 16.8 | 0 | 2023-03-26 | 2.7 | 15.3 | 0 | 2022-03-26 | 1.6 | 16.4 | 0 | 2021-03-26 | 10.2 | 7.8 | 0 | 2020-03-26 | 2 | 16 | 0 | 2019-03-26 | -4.3 | 22.3 | 0 | 2018-03-26 | -3.2 | 21.2 | 0 | 2017-03-26 | -4.6 | 22.6 | 0 | 2016-03-26 | -5.7 | 23.7 | 0 | 18.15 | 0
2025-03-26 | -2.2 | 20.2 | 0 | 2024-03-26 | 0.2 | 17.8 | 0 | 2023-03-26 | 2.6 | 15.4 | 0 | 2022-03-26 | 1.6 | 16.4 | 0 | 2021-03-26 | 9.2 | 8.8 | 0 | 2020-03-26 | 2.4 | 15.6 | 0 | 2019-03-26 | -4.2 | 22.2 | 0 | 2018-03-26 | -3.4 | 21.4 | 0 | 2017-03-26 | -5.9 | 23.9 | 0 | 2016-03-26 | -5.3 | 23.3 | 0 | 18.5 | 0
2025-03-26 | -2.5 | 20.5 | 0 | 2024-03-26 | -0.6 | 18.6 | 0 | 2023-03-26 | 2.3 | 15.7 | 0 | 2022-03-26 | 1.4 | 16.6 | 0 | 2021-03-26 | 8.1 | 9.9 | 0 | 2020-03-26 | 2.6 | 15.4 | 0 | 2019-03-26 | -6 | 24 | 0 | 2018-03-26 | -3.9 | 21.9 | 0 | 2017-03-26 | -5.3 | 23.3 | 0 | 2016-03-26 | -6.9 | 24.9 | 0 | 19.08 | 0
2025-03-26 | -2.5 | 20.5 | 0 | 2024-03-26 | -1.1 | 19.1 | 0 | 2023-03-26 | 2.4 | 15.6 | 0 | 2022-03-26 | 1.2 | 16.8 | 0 | 2021-03-26 | 7 | 11 | 0 | 2020-03-26 | 2.1 | 15.9 | 0 | 2019-03-26 | -5.3 | 23.3 | 0 | 2018-03-26 | -4.5 | 22.5 | 0 | 2017-03-26 | -5.8 | 23.8 | 0 | 2016-03-26 | -8.5 | 26.5 | 0 | 19.5 | 0
2025-03-26 | -2.4 | 20.4 | 0 | 2024-03-26 | -0.5 | 18.5 | 0 | 2023-03-26 | 1.9 | 16.1 | 0 | 2022-03-26 | 0.7 | 17.3 | 0 | 2021-03-26 | 6.6 | 11.4 | 0 | 2020-03-26 | 2 | 16 | 0 | 2019-03-26 | -6 | 24 | 0 | 2018-03-26 | -3.9 | 21.9 | 0 | 2017-03-26 | -6 | 24 | 0 | 2016-03-26 | -7.7 | 25.7 | 0 | 19.53 | 0
2025-03-26 | -3 | 21 | 0 | 2024-03-26 | -1 | 19 | 0 | 2023-03-26 | 2.1 | 15.9 | 0 | 2022-03-26 | 0.8 | 17.2 | 0 | 2021-03-26 | 6.4 | 11.6 | 0 | 2020-03-26 | 1.9 | 16.1 | 0 | 2019-03-26 | -6.8 | 24.8 | 0 | 2018-03-26 | -4 | 22 | 0 | 2017-03-26 | -6.5 | 24.5 | 0 | 2016-03-26 | -7.6 | 25.6 | 0 | 19.77 | 0
2025-03-26 | -2.9 | 20.9 | 0 | 2024-03-26 | -0.2 | 18.2 | 0 | 2023-03-26 | 0.8 | 17.2 | 0 | 2022-03-26 | 0.9 | 17.1 | 0 | 2021-03-26 | 6 | 12 | 0 | 2020-03-26 | 2.2 | 15.8 | 0 | 2019-03-26 | -8 | 26 | 0 | 2018-03-26 | -4.7 | 22.7 | 0 | 2017-03-26 | -6.7 | 24.7 | 0 | 2016-03-26 | -8.3 | 26.3 | 0 | 20.09 | 0
2025-03-26 | -2.1 | 20.1 | 0 | 2024-03-26 | 0.4 | 17.6 | 0 | 2023-03-26 | 0.8 | 17.2 | 0 | 2022-03-26 | 1 | 17 | 0 | 2021-03-26 | 6.1 | 11.9 | 0 | 2020-03-26 | 2.8 | 15.2 | 0 | 2019-03-26 | -6.9 | 24.9 | 0 | 2018-03-26 | -3.6 | 21.6 | 0 | 2017-03-26 | -6.5 | 24.5 | 0 | 2016-03-26 | -6.7 | 24.7 | 0 | 19.47 | 0
2025-03-26 | -1.7 | 19.7 | 0 | 2024-03-26 | 2 | 16 | 0 | 2023-03-26 | 1.2 | 16.8 | 0 | 2022-03-26 | 1.6 | 16.4 | 0 | 2021-03-26 | 6 | 12 | 0 | 2020-03-26 | 3 | 15 | 0 | 2019-03-26 | -6.2 | 24.2 | 0 | 2018-03-26 | -1.6 | 19.6 | 0 | 2017-03-26 | -5 | 23 | 0 | 2016-03-26 | -3.8 | 21.8 | 0 | 18.45 | 0
2025-03-26 | -1.1 | 19.1 | 0 | 2024-03-26 | 3.2 | 14.8 | 0 | 2023-03-26 | 1.9 | 16.1 | 0 | 2022-03-26 | 2.9 | 15.1 | 0 | 2021-03-26 | 5.7 | 12.3 | 0 | 2020-03-26 | 3.8 | 14.2 | 0 | 2019-03-26 | -5.1 | 23.1 | 0 | 2018-03-26 | 0 | 18 | 0 | 2017-03-26 | -3.7 | 21.7 | 0 | 2016-03-26 | -1.5 | 19.5 | 0 | 17.39 | 0
2025-03-26 | -0.3 | 18.3 | 0 | 2024-03-26 | 5.4 | 12.6 | 0 | 2023-03-26 | 2.2 | 15.8 | 0 | 2022-03-26 | 4.4 | 13.6 | 0 | 2021-03-26 | 5.7 | 12.3 | 0 | 2020-03-26 | 5.1 | 12.9 | 0 | 2019-03-26 | -4.3 | 22.3 | 0 | 2018-03-26 | 1.5 | 16.5 | 0 | 2017-03-26 | -2.2 | 20.2 | 0 | 2016-03-26 | -0.2 | 18.2 | 0 | 16.27 | 0
2025-03-26 | 0.2 | 17.8 | 0 | 2024-03-26 | 7.3 | 10.7 | 0 | 2023-03-26 | 2.8 | 15.2 | 0 | 2022-03-26 | 5.7 | 12.3 | 0 | 2021-03-26 | 6.1 | 11.9 | 0 | 2020-03-26 | 6.9 | 11.1 | 0 | 2019-03-26 | -3.8 | 21.8 | 0 | 2018-03-26 | 3.6 | 14.4 | 0 | 2017-03-26 | -1.7 | 19.7 | 0 | 2016-03-26 | 0.9 | 17.1 | 0 | 15.2 | 0
2025-03-26 | 1.6 | 16.4 | 0 | 2024-03-26 | 8.4 | 9.6 | 0 | 2023-03-26 | 3 | 15 | 0 | 2022-03-26 | 7.8 | 10.2 | 0 | 2021-03-26 | 6.8 | 11.2 | 0 | 2020-03-26 | 8.2 | 9.8 | 0 | 2019-03-26 | -2.8 | 20.8 | 0 | 2018-03-26 | 4 | 14 | 0 | 2017-03-26 | -1.3 | 19.3 | 0 | 2016-03-26 | 2.1 | 15.9 | 0 | 14.22 | 0
2025-03-26 | 1.4 | 16.6 | 0 | 2024-03-26 | 9.6 | 8.4 | 0 | 2023-03-26 | 3.1 | 14.9 | 0 | 2022-03-26 | 6.7 | 11.3 | 0 | 2021-03-26 | 6.1 | 11.9 | 0 | 2020-03-26 | 9.9 | 8.1 | 0 | 2019-03-26 | -1.9 | 19.9 | 0 | 2018-03-26 | 5.2 | 12.8 | 0 | 2017-03-26 | -1.2 | 19.2 | 0 | 2016-03-26 | 3.3 | 14.7 | 0 | 13.78 | 0
2025-03-26 | 2.4 | 15.6 | 0 | 2024-03-26 | 10.6 | 7.4 | 0 | 2023-03-26 | 4 | 14 | 0 | 2022-03-26 | 6.4 | 11.6 | 0 | 2021-03-26 | 5 | 13 | 0 | 2020-03-26 | 10.9 | 7.1 | 0 | 2019-03-26 | -1.5 | 19.5 | 0 | 2018-03-26 | 5.3 | 12.7 | 0 | 2017-03-26 | -0.8 | 18.8 | 0 | 2016-03-26 | 4.5 | 13.5 | 0 | 13.32 | 0
2025-03-26 | 2.2 | 15.8 | 0 | 2024-03-26 | 10 | 8 | 0 | 2023-03-26 | 4 | 14 | 0 | 2022-03-26 | 7.2 | 10.8 | 0 | 2021-03-26 | 4.4 | 13.6 | 0 | 2020-03-26 | 8.1 | 9.9 | 0 | 2019-03-26 | -0.6 | 18.6 | 0 | 2018-03-26 | 5.5 | 12.5 | 0 | 2017-03-26 | -1.1 | 19.1 | 0 | 2016-03-26 | 4.7 | 13.3 | 0 | 13.56 | 0
2025-03-26 | 0.9 | 17.1 | 0 | 2024-03-26 | 9.4 | 8.6 | 0 | 2023-03-26 | 4.4 | 13.6 | 0 | 2022-03-26 | 7 | 11 | 0 | 2021-03-26 | 3.3 | 14.7 | 0 | 2020-03-26 | 8 | 10 | 0 | 2019-03-26 | 0 | 18 | 0 | 2018-03-26 | 5.6 | 12.4 | 0 | 2017-03-26 | -1.2 | 19.2 | 0 | 2016-03-26 | 5.1 | 12.9 | 0 | 13.75 | 0
2025-03-26 | 0.4 | 17.6 | 0 | 2024-03-26 | 9 | 9 | 0 | 2023-03-26 | 4 | 14 | 0 | 2022-03-26 | 6.5 | 11.5 | 0 | 2021-03-26 | 3.1 | 14.9 | 0 | 2020-03-26 | 8 | 10 | 0 | 2019-03-26 | 0.2 | 17.8 | 0 | 2018-03-26 | 5.1 | 12.9 | 0 | 2017-03-26 | -1.4 | 19.4 | 0 | 2016-03-26 | 4.9 | 13.1 | 0 | 14.02 | 0
2025-03-26 | -0.2 | 18.2 | 0 | 2024-03-26 | 8.6 | 9.4 | 0 | 2023-03-26 | 3.7 | 14.3 | 0 | 2022-03-26 | 4 | 14 | 0 | 2021-03-26 | 1.8 | 16.2 | 0 | 2020-03-26 | 5 | 13 | 0 | 2019-03-26 | -0.1 | 18.1 | 0 | 2018-03-26 | 3.9 | 14.1 | 0 | 2017-03-26 | -1.2 | 19.2 | 0 | 2016-03-26 | 2.6 | 15.4 | 0 | 15.19 | 0
2025-03-26 | -1.1 | 19.1 | 0 | 2024-03-26 | 8.6 | 9.4 | 0 | 2023-03-26 | 2.7 | 15.3 | 0 | 2022-03-26 | 3.6 | 14.4 | 0 | 2021-03-26 | 1.8 | 16.2 | 0 | 2020-03-26 | 3.9 | 14.1 | 0 | 2019-03-26 | -1.4 | 19.4 | 0 | 2018-03-26 | 2 | 16 | 0 | 2017-03-26 | -1.2 | 19.2 | 0 | 2016-03-26 | 1.8 | 16.2 | 0 | 15.93 | 0
2025-03-26 | -0.9 | 18.9 | 0 | 2024-03-26 | 8.5 | 9.5 | 0 | 2023-03-26 | 2 | 16 | 0 | 2022-03-26 | 3.6 | 14.4 | 0 | 2021-03-26 | 1.3 | 16.7 | 0 | 2020-03-26 | 3 | 15 | 0 | 2019-03-26 | -1.7 | 19.7 | 0 | 2018-03-26 | 1 | 17 | 0 | 2017-03-26 | -1.4 | 19.4 | 0 | 2016-03-26 | -0.2 | 18.2 | 0 | 16.48 | 0
2025-03-26 | -1.3 | 19.3 | 0 | 2024-03-26 | 8.4 | 9.6 | 0 | 2023-03-26 | 2.3 | 15.7 | 0 | 2022-03-26 | 2.9 | 15.1 | 0 | 2021-03-26 | 0.9 | 17.1 | 0 | 2020-03-26 | 2.7 | 15.3 | 0 | 2019-03-26 | -3 | 21 | 0 | 2018-03-26 | 0.1 | 17.9 | 0 | 2017-03-26 | -1.2 | 19.2 | 0 | 2016-03-26 | -0.3 | 18.3 | 0 | 16.85 | 0
2025-03-26 | -1.9 | 19.9 | 0 | 2024-03-26 | 7.7 | 10.3 | 0 | 2023-03-26 | 1.5 | 16.5 | 0 | 2022-03-26 | 2.5 | 15.5 | 0 | 2021-03-26 | 0.6 | 17.4 | 0 | 2020-03-26 | 2.8 | 15.2 | 0 | 2019-03-26 | -3.8 | 21.8 | 0 | 2018-03-26 | -0.1 | 18.1 | 0 | 2017-03-26 | -0.9 | 18.9 | 0 | 2016-03-26 | -1 | 19 | 0 | 17.26 | 0
2025-03-26 | -3 | 21 | 0 | 2024-03-26 | 6.9 | 11.1 | 0 | 2023-03-26 | 0.9 | 17.1 | 0 | 2022-03-26 | 2.4 | 15.6 | 0 | 2021-03-26 | 0.4 | 17.6 | 0 | 2020-03-26 | 1.7 | 16.3 | 0 | 2019-03-26 | -4.2 | 22.2 | 0 | 2018-03-26 | -1 | 19 | 0 | 2017-03-26 | -0.7 | 18.7 | 0 | 2016-03-26 | -1.9 | 19.9 | 0 | 17.85 | 0
2025-03-27 | -3.3 | 21.3 | 0 | 2024-03-27 | 6.9 | 11.1 | 0 | 2023-03-27 | 0.4 | 17.6 | 0 | 2022-03-27 | 1.8 | 16.2 | 0 | 2021-03-27 | 0.3 | 17.7 | 0 | 2020-03-27 | 1.1 | 16.9 | 0 | 2019-03-27 | -4.7 | 22.7 | 0 | 2018-03-27 | -2 | 20 | 0 | 2017-03-27 | -1 | 19 | 0 | 2016-03-27 | -1.7 | 19.7 | 0 | 18.22 | 0
2025-03-27 | -3.5 | 21.5 | 0 | 2024-03-27 | 6.5 | 11.5 | 0 | 2023-03-27 | -0.5 | 18.5 | 0 | 2022-03-27 | 1 | 17 | 0 | 2021-03-27 | -0.2 | 18.2 | 0 | 2020-03-27 | 0.8 | 17.2 | 0 | 2019-03-27 | -5.7 | 23.7 | 0 | 2018-03-27 | -2.6 | 20.6 | 0 | 2017-03-27 | -0.8 | 18.8 | 0 | 2016-03-27 | -3.1 | 21.1 | 0 | 18.81 | 0
2025-03-27 | -3.4 | 21.4 | 0 | 2024-03-27 | 5.9 | 12.1 | 0 | 2023-03-27 | -1.7 | 19.7 | 0 | 2022-03-27 | -0.2 | 18.2 | 0 | 2021-03-27 | -0.5 | 18.5 | 0 | 2020-03-27 | 0.7 | 17.3 | 0 | 2019-03-27 | -6.1 | 24.1 | 0 | 2018-03-27 | -2.3 | 20.3 | 0 | 2017-03-27 | -0.6 | 18.6 | 0 | 2016-03-27 | -3.6 | 21.6 | 0 | 19.18 | 0
2025-03-27 | -4.1 | 22.1 | 0 | 2024-03-27 | 5.3 | 12.7 | 0 | 2023-03-27 | -1.6 | 19.6 | 0 | 2022-03-27 | -1.3 | 19.3 | 0 | 2021-03-27 | -0.8 | 18.8 | 0 | 2020-03-27 | 0.5 | 17.5 | 0 | 2019-03-27 | -6.6 | 24.6 | 0 | 2018-03-27 | -3.2 | 21.2 | 0 | 2017-03-27 | -0.6 | 18.6 | 0 | 2016-03-27 | -4.1 | 22.1 | 0 | 19.65 | 0
2025-03-27 | -4.4 | 22.4 | 0 | 2024-03-27 | 5.1 | 12.9 | 0 | 2023-03-27 | -1.9 | 19.9 | 0 | 2022-03-27 | -2.6 | 20.6 | 0 | 2021-03-27 | -0.9 | 18.9 | 0 | 2020-03-27 | 0.4 | 17.6 | 0 | 2019-03-27 | -7.6 | 25.6 | 0 | 2018-03-27 | -3.2 | 21.2 | 0 | 2017-03-27 | -0.6 | 18.6 | 0 | 2016-03-27 | -4 | 22 | 0 | 19.97 | 0
2025-03-27 | -5.3 | 23.3 | 0 | 2024-03-27 | 4.9 | 13.1 | 0 | 2023-03-27 | -2.6 | 20.6 | 0 | 2022-03-27 | -3 | 21 | 0 | 2021-03-27 | -1 | 19 | 0 | 2020-03-27 | -0.1 | 18.1 | 0 | 2019-03-27 | -8.5 | 26.5 | 0 | 2018-03-27 | -3.2 | 21.2 | 0 | 2017-03-27 | -0.3 | 18.3 | 0 | 2016-03-27 | -3.4 | 21.4 | 0 | 20.25 | 0
2025-03-27 | -6 | 24 | 0 | 2024-03-27 | 4.5 | 13.5 | 0 | 2023-03-27 | -2.6 | 20.6 | 0 | 2022-03-27 | -3.8 | 21.8 | 0 | 2021-03-27 | -0.8 | 18.8 | 0 | 2020-03-27 | -0.5 | 18.5 | 0 | 2019-03-27 | -9.2 | 27.2 | 0 | 2018-03-27 | -3.4 | 21.4 | 0 | 2017-03-27 | -0.1 | 18.1 | 0 | 2016-03-27 | -4.1 | 22.1 | 0 | 20.6 | 0
2025-03-27 | -4.2 | 22.2 | 0 | 2024-03-27 | 4.9 | 13.1 | 0 | 2023-03-27 | -0.5 | 18.5 | 0 | 2022-03-27 | -4.8 | 22.8 | 0 | 2021-03-27 | -0.4 | 18.4 | 0 | 2020-03-27 | -0.2 | 18.2 | 0 | 2019-03-27 | -7.8 | 25.8 | 0 | 2018-03-27 | -1.3 | 19.3 | 0 | 2017-03-27 | 0.1 | 17.9 | 0 | 2016-03-27 | -2.2 | 20.2 | 0 | 19.64 | 0
2025-03-27 | -1.6 | 19.6 | 0 | 2024-03-27 | 7 | 11 | 0 | 2023-03-27 | 0 | 18 | 0 | 2022-03-27 | -5.5 | 23.5 | 0 | 2021-03-27 | 0 | 18 | 0 | 2020-03-27 | 0.6 | 17.4 | 0 | 2019-03-27 | -5 | 23 | 0 | 2018-03-27 | 2.4 | 15.6 | 0 | 2017-03-27 | 0.2 | 17.8 | 0 | 2016-03-27 | -1.3 | 19.3 | 0 | 18.32 | 0
2025-03-27 | -0.1 | 18.1 | 0 | 2024-03-27 | 9.4 | 8.6 | 0 | 2023-03-27 | 1.4 | 16.6 | 0 | 2022-03-27 | -5.6 | 23.6 | 0 | 2021-03-27 | 0.7 | 17.3 | 0 | 2020-03-27 | 1.7 | 16.3 | 0 | 2019-03-27 | -2.2 | 20.2 | 0 | 2018-03-27 | 3.9 | 14.1 | 0 | 2017-03-27 | 0.4 | 17.6 | 0 | 2016-03-27 | 0.4 | 17.6 | 0 | 17 | 0
2025-03-27 | 2.1 | 15.9 | 0 | 2024-03-27 | 11.3 | 6.7 | 0 | 2023-03-27 | 3 | 15 | 0 | 2022-03-27 | -5.4 | 23.4 | 0 | 2021-03-27 | 1.4 | 16.6 | 0 | 2020-03-27 | 2.9 | 15.1 | 0 | 2019-03-27 | 0.5 | 17.5 | 0 | 2018-03-27 | 4.5 | 13.5 | 0 | 2017-03-27 | 0.7 | 17.3 | 0 | 2016-03-27 | 2.8 | 15.2 | 0 | 15.62 | 0
2025-03-27 | 3.6 | 14.4 | 0 | 2024-03-27 | 13.4 | 4.6 | 0 | 2023-03-27 | 4.9 | 13.1 | 0 | 2022-03-27 | -4.8 | 22.8 | 0 | 2021-03-27 | 2.6 | 15.4 | 0 | 2020-03-27 | 4.5 | 13.5 | 0 | 2019-03-27 | 2.5 | 15.5 | 0 | 2018-03-27 | 5.3 | 12.7 | 0 | 2017-03-27 | 1 | 17 | 0 | 2016-03-27 | 5.6 | 12.4 | 0 | 14.14 | 0
2025-03-27 | 5.7 | 12.3 | 0 | 2024-03-27 | 13.9 | 4.1 | 0 | 2023-03-27 | 5.1 | 12.9 | 0 | 2022-03-27 | -4.8 | 22.8 | 0 | 2021-03-27 | 3.1 | 14.9 | 0 | 2020-03-27 | 5.1 | 12.9 | 0 | 2019-03-27 | 3.2 | 14.8 | 0 | 2018-03-27 | 5.9 | 12.1 | 0 | 2017-03-27 | 1.4 | 16.6 | 0 | 2016-03-27 | 7.6 | 10.4 | 0 | 13.38 | 0
2025-03-27 | 6.5 | 11.5 | 0 | 2024-03-27 | 14.8 | 3.2 | 0 | 2023-03-27 | 6.1 | 11.9 | 0 | 2022-03-27 | -5.2 | 23.2 | 0 | 2021-03-27 | 2.8 | 15.2 | 0 | 2020-03-27 | 6.5 | 11.5 | 0 | 2019-03-27 | 4 | 14 | 0 | 2018-03-27 | 6.2 | 11.8 | 0 | 2017-03-27 | 1.5 | 16.5 | 0 | 2016-03-27 | 10 | 8 | 0 | 12.68 | 0
2025-03-27 | 7.9 | 10.1 | 0 | 2024-03-27 | 15 | 3 | 0 | 2023-03-27 | 5.8 | 12.2 | 0 | 2022-03-27 | -4.5 | 22.5 | 0 | 2021-03-27 | 3 | 15 | 0 | 2020-03-27 | 7.3 | 10.7 | 0 | 2019-03-27 | 4.9 | 13.1 | 0 | 2018-03-27 | 5.5 | 12.5 | 0 | 2017-03-27 | 1.9 | 16.1 | 0 | 2016-03-27 | 11.1 | 6.9 | 0 | 12.21 | 0
2025-03-27 | 8 | 10 | 0 | 2024-03-27 | 12.8 | 5.2 | 0 | 2023-03-27 | 5.3 | 12.7 | 0 | 2022-03-27 | -5.4 | 23.4 | 0 | 2021-03-27 | 3.1 | 14.9 | 0 | 2020-03-27 | 7.8 | 10.2 | 0 | 2019-03-27 | 5.1 | 12.9 | 0 | 2018-03-27 | 5.7 | 12.3 | 0 | 2017-03-27 | 2 | 16 | 0 | 2016-03-27 | 12.2 | 5.8 | 0 | 12.34 | 0
2025-03-27 | 7.9 | 10.1 | 0 | 2024-03-27 | 13.1 | 4.9 | 0 | 2023-03-27 | 5 | 13 | 0 | 2022-03-27 | -6.2 | 24.2 | 0 | 2021-03-27 | 3.9 | 14.1 | 0 | 2020-03-27 | 7.7 | 10.3 | 0 | 2019-03-27 | 5.2 | 12.8 | 0 | 2018-03-27 | 5.4 | 12.6 | 0 | 2017-03-27 | 2.2 | 15.8 | 0 | 2016-03-27 | 12.4 | 5.6 | 0 | 12.34 | 0
2025-03-27 | 6.3 | 11.7 | 0 | 2024-03-27 | 11.8 | 6.2 | 0 | 2023-03-27 | 4.9 | 13.1 | 0 | 2022-03-27 | -7 | 25 | 0 | 2021-03-27 | 4 | 14 | 0 | 2020-03-27 | 7.3 | 10.7 | 0 | 2019-03-27 | 4.7 | 13.3 | 0 | 2018-03-27 | 4.6 | 13.4 | 0 | 2017-03-27 | 2.1 | 15.9 | 0 | 2016-03-27 | 11.7 | 6.3 | 0 | 12.96 | 0
2025-03-27 | 5.6 | 12.4 | 0 | 2024-03-27 | 11.1 | 6.9 | 0 | 2023-03-27 | 5.4 | 12.6 | 0 | 2022-03-27 | -8.3 | 26.3 | 0 | 2021-03-27 | 3.4 | 14.6 | 0 | 2020-03-27 | 5.4 | 12.6 | 0 | 2019-03-27 | 3.3 | 14.7 | 0 | 2018-03-27 | 2.4 | 15.6 | 0 | 2017-03-27 | 2.1 | 15.9 | 0 | 2016-03-27 | 9.7 | 8.3 | 0 | 13.99 | 0
2025-03-27 | 4.7 | 13.3 | 0 | 2024-03-27 | 10.4 | 7.6 | 0 | 2023-03-27 | 5.2 | 12.8 | 0 | 2022-03-27 | -9.1 | 27.1 | 0 | 2021-03-27 | 2.9 | 15.1 | 0 | 2020-03-27 | 2.2 | 15.8 | 0 | 2019-03-27 | 1.8 | 16.2 | 0 | 2018-03-27 | 0.3 | 17.7 | 0 | 2017-03-27 | 1.6 | 16.4 | 0 | 2016-03-27 | 7 | 11 | 0 | 15.3 | 0
2025-03-27 | 3.6 | 14.4 | 0 | 2024-03-27 | 9.7 | 8.3 | 0 | 2023-03-27 | 3.9 | 14.1 | 0 | 2022-03-27 | -9.7 | 27.7 | 0 | 2021-03-27 | 2.9 | 15.1 | 0 | 2020-03-27 | 2.5 | 15.5 | 0 | 2019-03-27 | 0.6 | 17.4 | 0 | 2018-03-27 | 0.4 | 17.6 | 0 | 2017-03-27 | 1.2 | 16.8 | 0 | 2016-03-27 | 6.1 | 11.9 | 0 | 15.88 | 0
2025-03-27 | 3.1 | 14.9 | 0 | 2024-03-27 | 8.9 | 9.1 | 0 | 2023-03-27 | 2.8 | 15.2 | 0 | 2022-03-27 | -10.3 | 28.3 | 0 | 2021-03-27 | 2.4 | 15.6 | 0 | 2020-03-27 | -0.5 | 18.5 | 0 | 2019-03-27 | -0.6 | 18.6 | 0 | 2018-03-27 | 0.9 | 17.1 | 0 | 2017-03-27 | 1.1 | 16.9 | 0 | 2016-03-27 | 4.7 | 13.3 | 0 | 16.75 | 0
2025-03-27 | 2.4 | 15.6 | 0 | 2024-03-27 | 8.2 | 9.8 | 0 | 2023-03-27 | 1.4 | 16.6 | 0 | 2022-03-27 | -10.8 | 28.8 | 0 | 2021-03-27 | 2.3 | 15.7 | 0 | 2020-03-27 | 1.5 | 16.5 | 0 | 2019-03-27 | -0.5 | 18.5 | 0 | 2018-03-27 | 1.3 | 16.7 | 0 | 2017-03-27 | 1.1 | 16.9 | 0 | 2016-03-27 | 4.4 | 13.6 | 0 | 16.87 | 0
2025-03-27 | 1.7 | 16.3 | 0 | 2024-03-27 | 7.4 | 10.6 | 0 | 2023-03-27 | 0 | 18 | 0 | 2022-03-27 | -11.3 | 29.3 | 0 | 2021-03-27 | 1.2 | 16.8 | 0 | 2020-03-27 | -1 | 19 | 0 | 2019-03-27 | -1 | 19 | 0 | 2018-03-27 | 1.2 | 16.8 | 0 | 2017-03-27 | 0.9 | 17.1 | 0 | 2016-03-27 | 3.5 | 14.5 | 0 | 17.74 | 0
2025-03-28 | 1.1 | 16.9 | 0 | 2024-03-28 | 6.1 | 11.9 | 0 | 2023-03-28 | -0.9 | 18.9 | 0 | 2022-03-28 | -11.6 | 29.6 | 0 | 2021-03-28 | 1.7 | 16.3 | 0 | 2020-03-28 | -0.8 | 18.8 | 0 | 2019-03-28 | -0.6 | 18.6 | 0 | 2018-03-28 | 1.4 | 16.6 | 0 | 2017-03-28 | 1.1 | 16.9 | 0 | 2016-03-28 | 3 | 15 | 0 | 17.95 | 0
2025-03-28 | -0.5 | 18.5 | 0 | 2024-03-28 | 5.4 | 12.6 | 0 | 2023-03-28 | -2.6 | 20.6 | 0 | 2022-03-28 | -11.9 | 29.9 | 0 | 2021-03-28 | 1.8 | 16.2 | 0 | 2020-03-28 | -1.5 | 19.5 | 0 | 2019-03-28 | -1.4 | 19.4 | 0 | 2018-03-28 | 1.3 | 16.7 | 0 | 2017-03-28 | 0.8 | 17.2 | 0 | 2016-03-28 | 1.9 | 16.1 | 0 | 18.67 | 0
2025-03-28 | -2.6 | 20.6 | 0 | 2024-03-28 | 4.7 | 13.3 | 0 | 2023-03-28 | -2.5 | 20.5 | 0 | 2022-03-28 | -12.1 | 30.1 | 0 | 2021-03-28 | 2 | 16 | 0 | 2020-03-28 | -2.9 | 20.9 | 0 | 2019-03-28 | -1.1 | 19.1 | 0 | 2018-03-28 | 1.3 | 16.7 | 0 | 2017-03-28 | 0.9 | 17.1 | 0 | 2016-03-28 | 3.4 | 14.6 | 0 | 18.89 | 0
2025-03-28 | -4.5 | 22.5 | 0 | 2024-03-28 | 4.4 | 13.6 | 0 | 2023-03-28 | -3.7 | 21.7 | 0 | 2022-03-28 | -12.5 | 30.5 | 0 | 2021-03-28 | 1.6 | 16.4 | 0 | 2020-03-28 | -2 | 20 | 0 | 2019-03-28 | -0.2 | 18.2 | 0 | 2018-03-28 | 1.5 | 16.5 | 0 | 2017-03-28 | 0.7 | 17.3 | 0 | 2016-03-28 | 4.2 | 13.8 | 0 | 19.05 | 0
2025-03-28 | -5.5 | 23.5 | 0 | 2024-03-28 | 4 | 14 | 0 | 2023-03-28 | -4.2 | 22.2 | 0 | 2022-03-28 | -12.6 | 30.6 | 0 | 2021-03-28 | 1.3 | 16.7 | 0 | 2020-03-28 | -4.5 | 22.5 | 0 | 2019-03-28 | 0.6 | 17.4 | 0 | 2018-03-28 | 1.3 | 16.7 | 0 | 2017-03-28 | 1.1 | 16.9 | 0 | 2016-03-28 | 4.2 | 13.8 | 0 | 19.43 | 0
2025-03-28 | -6.2 | 24.2 | 0 | 2024-03-28 | 3.3 | 14.7 | 0 | 2023-03-28 | -4.2 | 22.2 | 0 | 2022-03-28 | -12.8 | 30.8 | 0 | 2021-03-28 | 1.6 | 16.4 | 0 | 2020-03-28 | -4.2 | 22.2 | 0 | 2019-03-28 | 1.3 | 16.7 | 0 | 2018-03-28 | 1.4 | 16.6 | 0 | 2017-03-28 | 1.1 | 16.9 | 0 | 2016-03-28 | 4.3 | 13.7 | 0 | 19.44 | 0
2025-03-28 | -6.7 | 24.7 | 0 | 2024-03-28 | 2.3 | 15.7 | 0 | 2023-03-28 | -5.1 | 23.1 | 0 | 2022-03-28 | -13.2 | 31.2 | 0 | 2021-03-28 | 1.6 | 16.4 | 0 | 2020-03-28 | -4.6 | 22.6 | 0 | 2019-03-28 | 2.8 | 15.2 | 0 | 2018-03-28 | 1.6 | 16.4 | 0 | 2017-03-28 | 1.5 | 16.5 | 0 | 2016-03-28 | 4.3 | 13.7 | 0 | 19.55 | 0
2025-03-28 | -6 | 24 | 0 | 2024-03-28 | 3 | 15 | 0 | 2023-03-28 | -4.2 | 22.2 | 0 | 2022-03-28 | -12.8 | 30.8 | 0 | 2021-03-28 | 1.5 | 16.5 | 0 | 2020-03-28 | -1.9 | 19.9 | 0 | 2019-03-28 | 3.8 | 14.2 | 0 | 2018-03-28 | 2 | 16 | 0 | 2017-03-28 | 1.3 | 16.7 | 0 | 2016-03-28 | 3.3 | 14.7 | 0 | 19 | 0
2025-03-28 | -5.2 | 23.2 | 0 | 2024-03-28 | 3.8 | 14.2 | 0 | 2023-03-28 | -2.1 | 20.1 | 0 | 2022-03-28 | -12.9 | 30.9 | 0 | 2021-03-28 | 1.8 | 16.2 | 0 | 2020-03-28 | -0.5 | 18.5 | 0 | 2019-03-28 | 3.2 | 14.8 | 0 | 2018-03-28 | 2.5 | 15.5 | 0 | 2017-03-28 | 1.5 | 16.5 | 0 | 2016-03-28 | 3.5 | 14.5 | 0 | 18.44 | 0
2025-03-28 | -4.4 | 22.4 | 0 | 2024-03-28 | 5.5 | 12.5 | 0 | 2023-03-28 | -0.6 | 18.6 | 0 | 2022-03-28 | -12.5 | 30.5 | 0 | 2021-03-28 | 3 | 15 | 0 | 2020-03-28 | 0.8 | 17.2 | 0 | 2019-03-28 | 4.2 | 13.8 | 0 | 2018-03-28 | 3.9 | 14.1 | 0 | 2017-03-28 | 1.9 | 16.1 | 0 | 2016-03-28 | 3.7 | 14.3 | 0 | 17.45 | 0
2025-03-28 | -3.6 | 21.6 | 0 | 2024-03-28 | 4.9 | 13.1 | 0 | 2023-03-28 | 0.1 | 17.9 | 0 | 2022-03-28 | -11.8 | 29.8 | 0 | 2021-03-28 | 4.3 | 13.7 | 0 | 2020-03-28 | 2.8 | 15.2 | 0 | 2019-03-28 | 5.1 | 12.9 | 0 | 2018-03-28 | 4.5 | 13.5 | 0 | 2017-03-28 | 2.4 | 15.6 | 0 | 2016-03-28 | 4 | 14 | 0 | 16.73 | 0
2025-03-28 | -2.1 | 20.1 | 0 | 2024-03-28 | 5.2 | 12.8 | 0 | 2023-03-28 | 1.1 | 16.9 | 0 | 2022-03-28 | -12.2 | 30.2 | 0 | 2021-03-28 | 3.6 | 14.4 | 0 | 2020-03-28 | 4.2 | 13.8 | 0 | 2019-03-28 | 6.4 | 11.6 | 0 | 2018-03-28 | 5.4 | 12.6 | 0 | 2017-03-28 | 2.8 | 15.2 | 0 | 2016-03-28 | 4.6 | 13.4 | 0 | 16.1 | 0
2025-03-28 | -0.2 | 18.2 | 0 | 2024-03-28 | 6.3 | 11.7 | 0 | 2023-03-28 | 1.3 | 16.7 | 0 | 2022-03-28 | -10.8 | 28.8 | 0 | 2021-03-28 | 4.1 | 13.9 | 0 | 2020-03-28 | 5.6 | 12.4 | 0 | 2019-03-28 | 6.5 | 11.5 | 0 | 2018-03-28 | 5.3 | 12.7 | 0 | 2017-03-28 | 4 | 14 | 0 | 2016-03-28 | 5.3 | 12.7 | 0 | 15.26 | 0
2025-03-28 | 0.8 | 17.2 | 0 | 2024-03-28 | 7.7 | 10.3 | 0 | 2023-03-28 | 1.9 | 16.1 | 0 | 2022-03-28 | -10.9 | 28.9 | 0 | 2021-03-28 | 6.1 | 11.9 | 0 | 2020-03-28 | 5.4 | 12.6 | 0 | 2019-03-28 | 6.2 | 11.8 | 0 | 2018-03-28 | 5.5 | 12.5 | 0 | 2017-03-28 | 4.4 | 13.6 | 0 | 2016-03-28 | 5.5 | 12.5 | 0 | 14.74 | 0
2025-03-28 | 0.8 | 17.2 | 0 | 2024-03-28 | 9.2 | 8.8 | 0 | 2023-03-28 | 2.2 | 15.8 | 0 | 2022-03-28 | -10.1 | 28.1 | 0 | 2021-03-28 | 7.6 | 10.4 | 0 | 2020-03-28 | 5.5 | 12.5 | 0 | 2019-03-28 | 6.2 | 11.8 | 0 | 2018-03-28 | 5.4 | 12.6 | 0 | 2017-03-28 | 5.4 | 12.6 | 0 | 2016-03-28 | 5.4 | 12.6 | 0 | 14.24 | 0
2025-03-28 | 1.2 | 16.8 | 0 | 2024-03-28 | 9.1 | 8.9 | 0 | 2023-03-28 | 2 | 16 | 0 | 2022-03-28 | -9.4 | 27.4 | 0 | 2021-03-28 | 9 | 9 | 0 | 2020-03-28 | 7 | 11 | 0 | 2019-03-28 | 6.5 | 11.5 | 0 | 2018-03-28 | 5 | 13 | 0 | 2017-03-28 | 5.2 | 12.8 | 0 | 2016-03-28 | 4.8 | 13.2 | 0 | 13.96 | 0
2025-03-28 | 1.3 | 16.7 | 0 | 2024-03-28 | 9 | 9 | 0 | 2023-03-28 | 2.3 | 15.7 | 0 | 2022-03-28 | -7.7 | 25.7 | 0 | 2021-03-28 | 7.9 | 10.1 | 0 | 2020-03-28 | 6.1 | 11.9 | 0 | 2019-03-28 | 6.6 | 11.4 | 0 | 2018-03-28 | 5.1 | 12.9 | 0 | 2017-03-28 | 4.9 | 13.1 | 0 | 2016-03-28 | 5.2 | 12.8 | 0 | 13.93 | 0
2025-03-28 | 1.2 | 16.8 | 0 | 2024-03-28 | 9 | 9 | 0 | 2023-03-28 | 2.4 | 15.6 | 0 | 2022-03-28 | -8.5 | 26.5 | 0 | 2021-03-28 | 10.2 | 7.8 | 0 | 2020-03-28 | 5 | 13 | 0 | 2019-03-28 | 6.5 | 11.5 | 0 | 2018-03-28 | 4.4 | 13.6 | 0 | 2017-03-28 | 5.4 | 12.6 | 0 | 2016-03-28 | 5.1 | 12.9 | 0 | 13.93 | 0
2025-03-28 | 0.2 | 17.8 | 0 | 2024-03-28 | 7.5 | 10.5 | 0 | 2023-03-28 | 1.7 | 16.3 | 0 | 2022-03-28 | -7.8 | 25.8 | 0 | 2021-03-28 | 10.4 | 7.6 | 0 | 2020-03-28 | 4.5 | 13.5 | 0 | 2019-03-28 | 6.4 | 11.6 | 0 | 2018-03-28 | 4.5 | 13.5 | 0 | 2017-03-28 | 5.1 | 12.9 | 0 | 2016-03-28 | 3 | 15 | 0 | 14.45 | 0
2025-03-28 | -0.4 | 18.4 | 0 | 2024-03-28 | 5 | 13 | 0 | 2023-03-28 | 1 | 17 | 0 | 2022-03-28 | -7.7 | 25.7 | 0 | 2021-03-28 | 9.2 | 8.8 | 0 | 2020-03-28 | 4.4 | 13.6 | 0 | 2019-03-28 | 6.1 | 11.9 | 0 | 2018-03-28 | 3.2 | 14.8 | 0 | 2017-03-28 | 5.1 | 12.9 | 0 | 2016-03-28 | 2.6 | 15.4 | 0 | 15.15 | 0
2025-03-28 | -1.8 | 19.8 | 0 | 2024-03-28 | 3.8 | 14.2 | 0 | 2023-03-28 | -1.4 | 19.4 | 0 | 2022-03-28 | -7.7 | 25.7 | 0 | 2021-03-28 | 6.6 | 11.4 | 0 | 2020-03-28 | 4.2 | 13.8 | 0 | 2019-03-28 | 5.8 | 12.2 | 0 | 2018-03-28 | 3.6 | 14.4 | 0 | 2017-03-28 | 4.8 | 13.2 | 0 | 2016-03-28 | 2.7 | 15.3 | 0 | 15.94 | 0
2025-03-28 | -2.5 | 20.5 | 0 | 2024-03-28 | 2.5 | 15.5 | 0 | 2023-03-28 | -2.2 | 20.2 | 0 | 2022-03-28 | -8.3 | 26.3 | 0 | 2021-03-28 | 5.3 | 12.7 | 0 | 2020-03-28 | 4 | 14 | 0 | 2019-03-28 | 5.8 | 12.2 | 0 | 2018-03-28 | 2.9 | 15.1 | 0 | 2017-03-28 | 4.1 | 13.9 | 0 | 2016-03-28 | 2.5 | 15.5 | 0 | 16.59 | 0
2025-03-28 | -3 | 21 | 0 | 2024-03-28 | 1.8 | 16.2 | 0 | 2023-03-28 | -2.6 | 20.6 | 0 | 2022-03-28 | -8 | 26 | 0 | 2021-03-28 | 4.3 | 13.7 | 0 | 2020-03-28 | 3.9 | 14.1 | 0 | 2019-03-28 | 5.8 | 12.2 | 0 | 2018-03-28 | 3.5 | 14.5 | 0 | 2017-03-28 | 4 | 14 | 0 | 2016-03-28 | 2.5 | 15.5 | 0 | 16.78 | 0
2025-03-28 | -3 | 21 | 0 | 2024-03-28 | 0.7 | 17.3 | 0 | 2023-03-28 | -1.6 | 19.6 | 0 | 2022-03-28 | -8.1 | 26.1 | 0 | 2021-03-28 | 2.8 | 15.2 | 0 | 2020-03-28 | 3.5 | 14.5 | 0 | 2019-03-28 | 5.6 | 12.4 | 0 | 2018-03-28 | 2.4 | 15.6 | 0 | 2017-03-28 | 3.8 | 14.2 | 0 | 2016-03-28 | 2.2 | 15.8 | 0 | 17.17 | 0
2025-03-29 | -3.3 | 21.3 | 0 | 2024-03-29 | 2.5 | 15.5 | 0 | 2023-03-29 | -2.9 | 20.9 | 0 | 2022-03-29 | -8.2 | 26.2 | 0 | 2021-03-29 | 2 | 16 | 0 | 2020-03-29 | 3.6 | 14.4 | 0 | 2019-03-29 | 5.3 | 12.7 | 0 | 2018-03-29 | 3 | 15 | 0 | 2017-03-29 | 2.8 | 15.2 | 0 | 2016-03-29 | 1.9 | 16.1 | 0 | 17.33 | 0
2025-03-29 | -3.6 | 21.6 | 0 | 2024-03-29 | 1.1 | 16.9 | 0 | 2023-03-29 | -4.2 | 22.2 | 0 | 2022-03-29 | -8.2 | 26.2 | 0 | 2021-03-29 | 0.9 | 17.1 | 0 | 2020-03-29 | 3.3 | 14.7 | 0 | 2019-03-29 | 4.7 | 13.3 | 0 | 2018-03-29 | 3.1 | 14.9 | 0 | 2017-03-29 | 1.9 | 16.1 | 0 | 2016-03-29 | 1.2 | 16.8 | 0 | 17.98 | 0
2025-03-29 | -3.7 | 21.7 | 0 | 2024-03-29 | -0.4 | 18.4 | 0 | 2023-03-29 | -4.3 | 22.3 | 0 | 2022-03-29 | -9.4 | 27.4 | 0 | 2021-03-29 | 0.3 | 17.7 | 0 | 2020-03-29 | 3.3 | 14.7 | 0 | 2019-03-29 | 4.1 | 13.9 | 0 | 2018-03-29 | 2.1 | 15.9 | 0 | 2017-03-29 | 1.9 | 16.1 | 0 | 2016-03-29 | 0.7 | 17.3 | 0 | 18.54 | 0
2025-03-29 | -3.7 | 21.7 | 0 | 2024-03-29 | -2.2 | 20.2 | 0 | 2023-03-29 | -4 | 22 | 0 | 2022-03-29 | -9.5 | 27.5 | 0 | 2021-03-29 | -0.7 | 18.7 | 0 | 2020-03-29 | 3.5 | 14.5 | 0 | 2019-03-29 | 4 | 14 | 0 | 2018-03-29 | 2.2 | 15.8 | 0 | 2017-03-29 | 1.6 | 16.4 | 0 | 2016-03-29 | -0.2 | 18.2 | 0 | 18.9 | 0
2025-03-29 | -3.7 | 21.7 | 0 | 2024-03-29 | -2 | 20 | 0 | 2023-03-29 | -3.8 | 21.8 | 0 | 2022-03-29 | -10 | 28 | 0 | 2021-03-29 | -1.2 | 19.2 | 0 | 2020-03-29 | 3.8 | 14.2 | 0 | 2019-03-29 | 4.2 | 13.8 | 0 | 2018-03-29 | 2 | 16 | 0 | 2017-03-29 | 0.3 | 17.7 | 0 | 2016-03-29 | -1.2 | 19.2 | 0 | 19.16 | 0
2025-03-29 | -3.7 | 21.7 | 0 | 2024-03-29 | -1.6 | 19.6 | 0 | 2023-03-29 | -4.2 | 22.2 | 0 | 2022-03-29 | -10.3 | 28.3 | 0 | 2021-03-29 | -2.4 | 20.4 | 0 | 2020-03-29 | 4.2 | 13.8 | 0 | 2019-03-29 | 3.4 | 14.6 | 0 | 2018-03-29 | 1.8 | 16.2 | 0 | 2017-03-29 | 0 | 18 | 0 | 2016-03-29 | -2.3 | 20.3 | 0 | 19.51 | 0
2025-03-29 | -4.6 | 22.6 | 0 | 2024-03-29 | -2.4 | 20.4 | 0 | 2023-03-29 | -4.5 | 22.5 | 0 | 2022-03-29 | -10.3 | 28.3 | 0 | 2021-03-29 | -3.8 | 21.8 | 0 | 2020-03-29 | 4.8 | 13.2 | 0 | 2019-03-29 | 2.3 | 15.7 | 0 | 2018-03-29 | 2 | 16 | 0 | 2017-03-29 | -0.4 | 18.4 | 0 | 2016-03-29 | -3 | 21 | 0 | 19.99 | 0
2025-03-29 | -4.7 | 22.7 | 0 | 2024-03-29 | -1 | 19 | 0 | 2023-03-29 | -4.1 | 22.1 | 0 | 2022-03-29 | -9.4 | 27.4 | 0 | 2021-03-29 | -4 | 22 | 0 | 2020-03-29 | 3.9 | 14.1 | 0 | 2019-03-29 | 2.2 | 15.8 | 0 | 2018-03-29 | 2.9 | 15.1 | 0 | 2017-03-29 | 0 | 18 | 0 | 2016-03-29 | -2.7 | 20.7 | 0 | 19.69 | 0
2025-03-29 | -4.6 | 22.6 | 0 | 2024-03-29 | 1.5 | 16.5 | 0 | 2023-03-29 | -2.3 | 20.3 | 0 | 2022-03-29 | -8.1 | 26.1 | 0 | 2021-03-29 | -3.6 | 21.6 | 0 | 2020-03-29 | 2.8 | 15.2 | 0 | 2019-03-29 | 2.4 | 15.6 | 0 | 2018-03-29 | 4.3 | 13.7 | 0 | 2017-03-29 | 0.5 | 17.5 | 0 | 2016-03-29 | -1.5 | 19.5 | 0 | 18.86 | 0
2025-03-29 | -4.6 | 22.6 | 0 | 2024-03-29 | 1.7 | 16.3 | 0 | 2023-03-29 | 0.8 | 17.2 | 0 | 2022-03-29 | -6.9 | 24.9 | 0 | 2021-03-29 | -3.3 | 21.3 | 0 | 2020-03-29 | 3.1 | 14.9 | 0 | 2019-03-29 | 2.8 | 15.2 | 0 | 2018-03-29 | 5.7 | 12.3 | 0 | 2017-03-29 | 2.8 | 15.2 | 0 | 2016-03-29 | -0.4 | 18.4 | 0 | 17.83 | 0
2025-03-29 | -4.4 | 22.4 | 0 | 2024-03-29 | 3.4 | 14.6 | 0 | 2023-03-29 | 3 | 15 | 0 | 2022-03-29 | -6.3 | 24.3 | 0 | 2021-03-29 | -1.8 | 19.8 | 0 | 2020-03-29 | 3.5 | 14.5 | 0 | 2019-03-29 | 3.2 | 14.8 | 0 | 2018-03-29 | 6.8 | 11.2 | 0 | 2017-03-29 | 3.7 | 14.3 | 0 | 2016-03-29 | 0.7 | 17.3 | 0 | 16.82 | 0
2025-03-29 | -4.3 | 22.3 | 0 | 2024-03-29 | 5 | 13 | 0 | 2023-03-29 | 5.2 | 12.8 | 0 | 2022-03-29 | -4.7 | 22.7 | 0 | 2021-03-29 | -0.7 | 18.7 | 0 | 2020-03-29 | 3.3 | 14.7 | 0 | 2019-03-29 | 3.7 | 14.3 | 0 | 2018-03-29 | 6.8 | 11.2 | 0 | 2017-03-29 | 3.8 | 14.2 | 0 | 2016-03-29 | 2.4 | 15.6 | 0 | 15.95 | 0
2025-03-29 | -3.8 | 21.8 | 0 | 2024-03-29 | 4.4 | 13.6 | 0 | 2023-03-29 | 5.6 | 12.4 | 0 | 2022-03-29 | -2.6 | 20.6 | 0 | 2021-03-29 | -0.1 | 18.1 | 0 | 2020-03-29 | 3.7 | 14.3 | 0 | 2019-03-29 | 4.1 | 13.9 | 0 | 2018-03-29 | 7.2 | 10.8 | 0 | 2017-03-29 | 3.5 | 14.5 | 0 | 2016-03-29 | 3.7 | 14.3 | 0 | 15.43 | 0
2025-03-29 | -3 | 21 | 0 | 2024-03-29 | 4.9 | 13.1 | 0 | 2023-03-29 | 6.6 | 11.4 | 0 | 2022-03-29 | -2.7 | 20.7 | 0 | 2021-03-29 | 0.8 | 17.2 | 0 | 2020-03-29 | 4.1 | 13.9 | 0 | 2019-03-29 | 4.1 | 13.9 | 0 | 2018-03-29 | 6.7 | 11.3 | 0 | 2017-03-29 | 4.1 | 13.9 | 0 | 2016-03-29 | 4.2 | 13.8 | 0 | 15.02 | 0
2025-03-29 | -1.9 | 19.9 | 0 | 2024-03-29 | 5.8 | 12.2 | 0 | 2023-03-29 | 7.1 | 10.9 | 0 | 2022-03-29 | -1.9 | 19.9 | 0 | 2021-03-29 | 2 | 16 | 0 | 2020-03-29 | 4.4 | 13.6 | 0 | 2019-03-29 | 4 | 14 | 0 | 2018-03-29 | 5.8 | 12.2 | 0 | 2017-03-29 | 4.7 | 13.3 | 0 | 2016-03-29 | 6.2 | 11.8 | 0 | 14.38 | 0
2025-03-29 | -0.9 | 18.9 | 0 | 2024-03-29 | 6 | 12 | 0 | 2023-03-29 | 6.7 | 11.3 | 0 | 2022-03-29 | -0.8 | 18.8 | 0 | 2021-03-29 | 3 | 15 | 0 | 2020-03-29 | 4.7 | 13.3 | 0 | 2019-03-29 | 4.5 | 13.5 | 0 | 2018-03-29 | 4.9 | 13.1 | 0 | 2017-03-29 | 5.1 | 12.9 | 0 | 2016-03-29 | 5.9 | 12.1 | 0 | 14.09 | 0
2025-03-29 | -0.7 | 18.7 | 0 | 2024-03-29 | 6.8 | 11.2 | 0 | 2023-03-29 | 6.4 | 11.6 | 0 | 2022-03-29 | -0.6 | 18.6 | 0 | 2021-03-29 | 3.7 | 14.3 | 0 | 2020-03-29 | 5 | 13 | 0 | 2019-03-29 | 4.2 | 13.8 | 0 | 2018-03-29 | 4.5 | 13.5 | 0 | 2017-03-29 | 5.5 | 12.5 | 0 | 2016-03-29 | 6 | 12 | 0 | 13.92 | 0
2025-03-29 | -1.9 | 19.9 | 0 | 2024-03-29 | 5.5 | 12.5 | 0 | 2023-03-29 | 2.1 | 15.9 | 0 | 2022-03-29 | -0.8 | 18.8 | 0 | 2021-03-29 | 3.5 | 14.5 | 0 | 2020-03-29 | 4.9 | 13.1 | 0 | 2019-03-29 | 4.1 | 13.9 | 0 | 2018-03-29 | 4.3 | 13.7 | 0 | 2017-03-29 | 4.5 | 13.5 | 0 | 2016-03-29 | 5.6 | 12.4 | 0 | 14.82 | 0
2025-03-29 | -2.2 | 20.2 | 0 | 2024-03-29 | 3.9 | 14.1 | 0 | 2023-03-29 | -0.5 | 18.5 | 0 | 2022-03-29 | -1.2 | 19.2 | 0 | 2021-03-29 | 2.2 | 15.8 | 0 | 2020-03-29 | 4.8 | 13.2 | 0 | 2019-03-29 | 3.4 | 14.6 | 0 | 2018-03-29 | 4.3 | 13.7 | 0 | 2017-03-29 | 3.9 | 14.1 | 0 | 2016-03-29 | 4.6 | 13.4 | 0 | 15.68 | 0
2025-03-29 | -2.4 | 20.4 | 0 | 2024-03-29 | 2.5 | 15.5 | 0 | 2023-03-29 | -1 | 19 | 0 | 2022-03-29 | -1.8 | 19.8 | 0 | 2021-03-29 | 0.4 | 17.6 | 0 | 2020-03-29 | 4.5 | 13.5 | 0 | 2019-03-29 | 3.1 | 14.9 | 0 | 2018-03-29 | 4 | 14 | 0 | 2017-03-29 | 3.2 | 14.8 | 0 | 2016-03-29 | 1.6 | 16.4 | 0 | 16.59 | 0
2025-03-29 | -3.1 | 21.1 | 0 | 2024-03-29 | 2.4 | 15.6 | 0 | 2023-03-29 | -1.4 | 19.4 | 0 | 2022-03-29 | -2.2 | 20.2 | 0 | 2021-03-29 | 0.2 | 17.8 | 0 | 2020-03-29 | 4.4 | 13.6 | 0 | 2019-03-29 | 1.4 | 16.6 | 0 | 2018-03-29 | 3.8 | 14.2 | 0 | 2017-03-29 | 3.2 | 14.8 | 0 | 2016-03-29 | 0.8 | 17.2 | 0 | 17.05 | 0
2025-03-29 | -3.3 | 21.3 | 0 | 2024-03-29 | 2.2 | 15.8 | 0 | 2023-03-29 | -2.3 | 20.3 | 0 | 2022-03-29 | -3.1 | 21.1 | 0 | 2021-03-29 | -2.8 | 20.8 | 0 | 2020-03-29 | 4.2 | 13.8 | 0 | 2019-03-29 | 0.8 | 17.2 | 0 | 2018-03-29 | 3.6 | 14.4 | 0 | 2017-03-29 | 2.4 | 15.6 | 0 | 2016-03-29 | 0.9 | 17.1 | 0 | 17.74 | 0
2025-03-29 | -2.9 | 20.9 | 0 | 2024-03-29 | 1.9 | 16.1 | 0 | 2023-03-29 | -3.2 | 21.2 | 0 | 2022-03-29 | -4.1 | 22.1 | 0 | 2021-03-29 | -3.9 | 21.9 | 0 | 2020-03-29 | 4.5 | 13.5 | 0 | 2019-03-29 | -0.6 | 18.6 | 0 | 2018-03-29 | 3.7 | 14.3 | 0 | 2017-03-29 | 1.4 | 16.6 | 0 | 2016-03-29 | -2.6 | 20.6 | 0 | 18.58 | 0
2025-03-29 | -2.9 | 20.9 | 0 | 2024-03-29 | 1.5 | 16.5 | 0 | 2023-03-29 | -4.4 | 22.4 | 0 | 2022-03-29 | -4.8 | 22.8 | 0 | 2021-03-29 | -2.3 | 20.3 | 0 | 2020-03-29 | 6.1 | 11.9 | 0 | 2019-03-29 | -0.2 | 18.2 | 0 | 2018-03-29 | 3.7 | 14.3 | 0 | 2017-03-29 | 0.7 | 17.3 | 0 | 2016-03-29 | -1.7 | 19.7 | 0 | 18.43 | 0
2025-03-30 | -2.5 | 20.5 | 0 | 2024-03-30 | 1.4 | 16.6 | 0 | 2023-03-30 | -5.8 | 23.8 | 0 | 2022-03-30 | -5.5 | 23.5 | 0 | 2021-03-30 | -2.5 | 20.5 | 0 | 2020-03-30 | 8.1 | 9.9 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 4.2 | 13.8 | 0 | 2017-03-30 | -1.2 | 19.2 | 0 | 2016-03-30 | -1.2 | 19.2 | 0 | 18.52 | 0
2025-03-30 | -2.5 | 20.5 | 0 | 2024-03-30 | 1 | 17 | 0 | 2023-03-30 | -7 | 25 | 0 | 2022-03-30 | -6.4 | 24.4 | 0 | 2021-03-30 | -1.5 | 19.5 | 0 | 2020-03-30 | 7.2 | 10.8 | 0 | 2019-03-30 | 0.1 | 17.9 | 0 | 2018-03-30 | 3.8 | 14.2 | 0 | 2017-03-30 | -1.1 | 19.1 | 0 | 2016-03-30 | -1.8 | 19.8 | 0 | 18.82 | 0
2025-03-30 | -2.2 | 20.2 | 0 | 2024-03-30 | 0.7 | 17.3 | 0 | 2023-03-30 | -7.7 | 25.7 | 0 | 2022-03-30 | -7.4 | 25.4 | 0 | 2021-03-30 | -2 | 20 | 0 | 2020-03-30 | 6.2 | 11.8 | 0 | 2019-03-30 | -0.1 | 18.1 | 0 | 2018-03-30 | 3.6 | 14.4 | 0 | 2017-03-30 | -2.1 | 20.1 | 0 | 2016-03-30 | -3.2 | 21.2 | 0 | 19.42 | 0
2025-03-30 | -1.9 | 19.9 | 0 | 2024-03-30 | 0.6 | 17.4 | 0 | 2023-03-30 | -7.8 | 25.8 | 0 | 2022-03-30 | -7.4 | 25.4 | 0 | 2021-03-30 | -1.1 | 19.1 | 0 | 2020-03-30 | 6.2 | 11.8 | 0 | 2019-03-30 | 0.1 | 17.9 | 0 | 2018-03-30 | 3.3 | 14.7 | 0 | 2017-03-30 | -2.7 | 20.7 | 0 | 2016-03-30 | -2.2 | 20.2 | 0 | 19.29 | 0
2025-03-30 | -2 | 20 | 0 | 2024-03-30 | -1 | 19 | 0 | 2023-03-30 | -8 | 26 | 0 | 2022-03-30 | -8.3 | 26.3 | 0 | 2021-03-30 | -1.2 | 19.2 | 0 | 2020-03-30 | 5.7 | 12.3 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 2.5 | 15.5 | 0 | 2017-03-30 | -3 | 21 | 0 | 2016-03-30 | -4.3 | 22.3 | 0 | 19.98 | 0
2025-03-30 | -2.1 | 20.1 | 0 | 2024-03-30 | -1.5 | 19.5 | 0 | 2023-03-30 | -9.1 | 27.1 | 0 | 2022-03-30 | -8.3 | 26.3 | 0 | 2021-03-30 | -0.9 | 18.9 | 0 | 2020-03-30 | 5.1 | 12.9 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 2.5 | 15.5 | 0 | 2017-03-30 | -2.2 | 20.2 | 0 | 2016-03-30 | -3.8 | 21.8 | 0 | 20.05 | 0
2025-03-30 | -2.1 | 20.1 | 0 | 2024-03-30 | -1.2 | 19.2 | 0 | 2023-03-30 | -9.7 | 27.7 | 0 | 2022-03-30 | -8.6 | 26.6 | 0 | 2021-03-30 | -0.7 | 18.7 | 0 | 2020-03-30 | 5.3 | 12.7 | 0 | 2019-03-30 | -0.6 | 18.6 | 0 | 2018-03-30 | 2.3 | 15.7 | 0 | 2017-03-30 | -2.3 | 20.3 | 0 | 2016-03-30 | -3.8 | 21.8 | 0 | 20.14 | 0
2025-03-30 | -2.2 | 20.2 | 0 | 2024-03-30 | -1.1 | 19.1 | 0 | 2023-03-30 | -8.4 | 26.4 | 0 | 2022-03-30 | -6.3 | 24.3 | 0 | 2021-03-30 | 1.1 | 16.9 | 0 | 2020-03-30 | 5.4 | 12.6 | 0 | 2019-03-30 | -0.6 | 18.6 | 0 | 2018-03-30 | 2.4 | 15.6 | 0 | 2017-03-30 | -0.9 | 18.9 | 0 | 2016-03-30 | -1.8 | 19.8 | 0 | 19.24 | 0
2025-03-30 | -2.1 | 20.1 | 0 | 2024-03-30 | 0 | 18 | 0 | 2023-03-30 | -7.1 | 25.1 | 0 | 2022-03-30 | -2.9 | 20.9 | 0 | 2021-03-30 | 3.3 | 14.7 | 0 | 2020-03-30 | 6 | 12 | 0 | 2019-03-30 | -0.9 | 18.9 | 0 | 2018-03-30 | 2.6 | 15.4 | 0 | 2017-03-30 | 0.9 | 17.1 | 0 | 2016-03-30 | 1 | 17 | 0 | 17.92 | 0
2025-03-30 | -2.2 | 20.2 | 0 | 2024-03-30 | -0.3 | 18.3 | 0 | 2023-03-30 | -5.6 | 23.6 | 0 | 2022-03-30 | -1 | 19 | 0 | 2021-03-30 | 6 | 12 | 0 | 2020-03-30 | 6.8 | 11.2 | 0 | 2019-03-30 | -1.3 | 19.3 | 0 | 2018-03-30 | 3.3 | 14.7 | 0 | 2017-03-30 | 1.7 | 16.3 | 0 | 2016-03-30 | 4 | 14 | 0 | 16.86 | 0
2025-03-30 | -1.9 | 19.9 | 0 | 2024-03-30 | 1.5 | 16.5 | 0 | 2023-03-30 | -4.4 | 22.4 | 0 | 2022-03-30 | 0.1 | 17.9 | 0 | 2021-03-30 | 9.7 | 8.3 | 0 | 2020-03-30 | 7.5 | 10.5 | 0 | 2019-03-30 | -1.3 | 19.3 | 0 | 2018-03-30 | 4.6 | 13.4 | 0 | 2017-03-30 | 2.2 | 15.8 | 0 | 2016-03-30 | 6.1 | 11.9 | 0 | 15.59 | 0
2025-03-30 | -1.7 | 19.7 | 0 | 2024-03-30 | 2.5 | 15.5 | 0 | 2023-03-30 | -3.3 | 21.3 | 0 | 2022-03-30 | 2 | 16 | 0 | 2021-03-30 | 12.2 | 5.8 | 0 | 2020-03-30 | 7.9 | 10.1 | 0 | 2019-03-30 | -0.5 | 18.5 | 0 | 2018-03-30 | 4.5 | 13.5 | 0 | 2017-03-30 | 2.8 | 15.2 | 0 | 2016-03-30 | 7.6 | 10.4 | 0 | 14.6 | 0
2025-03-30 | -1.2 | 19.2 | 0 | 2024-03-30 | 3.2 | 14.8 | 0 | 2023-03-30 | -2.7 | 20.7 | 0 | 2022-03-30 | 2.4 | 15.6 | 0 | 2021-03-30 | 13.6 | 4.4 | 0 | 2020-03-30 | 8.3 | 9.7 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 4.7 | 13.3 | 0 | 2017-03-30 | 3.4 | 14.6 | 0 | 2016-03-30 | 8.8 | 9.2 | 0 | 13.97 | 0
2025-03-30 | -0.9 | 18.9 | 0 | 2024-03-30 | 4.7 | 13.3 | 0 | 2023-03-30 | -1.4 | 19.4 | 0 | 2022-03-30 | 2.3 | 15.7 | 0 | 2021-03-30 | 15.1 | 2.9 | 0 | 2020-03-30 | 8.5 | 9.5 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 5.3 | 12.7 | 0 | 2017-03-30 | 4.3 | 13.7 | 0 | 2016-03-30 | 11.1 | 6.9 | 0 | 13.12 | 0
2025-03-30 | -0.6 | 18.6 | 0 | 2024-03-30 | 5.2 | 12.8 | 0 | 2023-03-30 | -0.2 | 18.2 | 0 | 2022-03-30 | 3.2 | 14.8 | 0 | 2021-03-30 | 16.1 | 1.9 | 0 | 2020-03-30 | 8.2 | 9.8 | 0 | 2019-03-30 | -0.2 | 18.2 | 0 | 2018-03-30 | 5.4 | 12.6 | 0 | 2017-03-30 | 4.3 | 13.7 | 0 | 2016-03-30 | 10.3 | 7.7 | 0 | 12.83 | 0
2025-03-30 | -0.3 | 18.3 | 0 | 2024-03-30 | 5.9 | 12.1 | 0 | 2023-03-30 | 0.1 | 17.9 | 0 | 2022-03-30 | 2 | 16 | 0 | 2021-03-30 | 16.6 | 1.4 | 0 | 2020-03-30 | 6.3 | 11.7 | 0 | 2019-03-30 | -0.1 | 18.1 | 0 | 2018-03-30 | 5.8 | 12.2 | 0 | 2017-03-30 | 4.2 | 13.8 | 0 | 2016-03-30 | 9.1 | 8.9 | 0 | 13.04 | 0
2025-03-30 | -0.2 | 18.2 | 0 | 2024-03-30 | 6.9 | 11.1 | 0 | 2023-03-30 | 0.1 | 17.9 | 0 | 2022-03-30 | 1.8 | 16.2 | 0 | 2021-03-30 | 17 | 1 | 0 | 2020-03-30 | 5.7 | 12.3 | 0 | 2019-03-30 | 0 | 18 | 0 | 2018-03-30 | 5 | 13 | 0 | 2017-03-30 | 4.3 | 13.7 | 0 | 2016-03-30 | 9.6 | 8.4 | 0 | 12.98 | 0
2025-03-30 | -0.1 | 18.1 | 0 | 2024-03-30 | 6.2 | 11.8 | 0 | 2023-03-30 | 0.3 | 17.7 | 0 | 2022-03-30 | -1.6 | 19.6 | 0 | 2021-03-30 | 16.9 | 1.1 | 0 | 2020-03-30 | 5.1 | 12.9 | 0 | 2019-03-30 | 0.5 | 17.5 | 0 | 2018-03-30 | 3.8 | 14.2 | 0 | 2017-03-30 | 3.3 | 14.7 | 0 | 2016-03-30 | 8.6 | 9.4 | 0 | 13.7 | 0
2025-03-30 | -0.2 | 18.2 | 0 | 2024-03-30 | 5.1 | 12.9 | 0 | 2023-03-30 | 0.3 | 17.7 | 0 | 2022-03-30 | -1.4 | 19.4 | 0 | 2021-03-30 | 15.3 | 2.7 | 0 | 2020-03-30 | 4.6 | 13.4 | 0 | 2019-03-30 | 0.9 | 17.1 | 0 | 2018-03-30 | 3.3 | 14.7 | 0 | 2017-03-30 | 2.7 | 15.3 | 0 | 2016-03-30 | 7.5 | 10.5 | 0 | 14.19 | 0
2025-03-30 | -0.2 | 18.2 | 0 | 2024-03-30 | 2.3 | 15.7 | 0 | 2023-03-30 | -1.5 | 19.5 | 0 | 2022-03-30 | -1.3 | 19.3 | 0 | 2021-03-30 | 14.4 | 3.6 | 0 | 2020-03-30 | 3.5 | 14.5 | 0 | 2019-03-30 | 0.7 | 17.3 | 0 | 2018-03-30 | 2.4 | 15.6 | 0 | 2017-03-30 | 2.5 | 15.5 | 0 | 2016-03-30 | 7.5 | 10.5 | 0 | 14.97 | 0
2025-03-30 | -0.1 | 18.1 | 0 | 2024-03-30 | 1.5 | 16.5 | 0 | 2023-03-30 | -1.8 | 19.8 | 0 | 2022-03-30 | -1.1 | 19.1 | 0 | 2021-03-30 | 14.1 | 3.9 | 0 | 2020-03-30 | 3 | 15 | 0 | 2019-03-30 | 0.8 | 17.2 | 0 | 2018-03-30 | 1.8 | 16.2 | 0 | 2017-03-30 | 2.3 | 15.7 | 0 | 2016-03-30 | 6.1 | 11.9 | 0 | 15.34 | 0
2025-03-30 | -0.1 | 18.1 | 0 | 2024-03-30 | 1.1 | 16.9 | 0 | 2023-03-30 | -1.8 | 19.8 | 0 | 2022-03-30 | -1.5 | 19.5 | 0 | 2021-03-30 | 13.7 | 4.3 | 0 | 2020-03-30 | 2.7 | 15.3 | 0 | 2019-03-30 | 0.6 | 17.4 | 0 | 2018-03-30 | 1.2 | 16.8 | 0 | 2017-03-30 | 1.8 | 16.2 | 0 | 2016-03-30 | 7 | 11 | 0 | 15.53 | 0
2025-03-30 | -0.1 | 18.1 | 0 | 2024-03-30 | 0.8 | 17.2 | 0 | 2023-03-30 | -1.8 | 19.8 | 0 | 2022-03-30 | -1.3 | 19.3 | 0 | 2021-03-30 | 14 | 4 | 0 | 2020-03-30 | 2.2 | 15.8 | 0 | 2019-03-30 | 0.7 | 17.3 | 0 | 2018-03-30 | -0.1 | 18.1 | 0 | 2017-03-30 | 1.4 | 16.6 | 0 | 2016-03-30 | 7.2 | 10.8 | 0 | 15.7 | 0
2025-03-30 | 0 | 18 | 0 | 2024-03-30 | 1.1 | 16.9 | 0 | 2023-03-30 | -1.9 | 19.9 | 0 | 2022-03-30 | -1.1 | 19.1 | 0 | 2021-03-30 | 13.4 | 4.6 | 0 | 2020-03-30 | 1.8 | 16.2 | 0 | 2019-03-30 | 0.6 | 17.4 | 0 | 2018-03-30 | -0.5 | 18.5 | 0 | 2017-03-30 | 1 | 17 | 0 | 2016-03-30 | 7.8 | 10.2 | 0 | 15.78 | 0
2025-03-31 | 0 | 18 | 0 | 2024-03-31 | 2.1 | 15.9 | 0 | 2023-03-31 | -2.9 | 20.9 | 0 | 2022-03-31 | -1 | 19 | 0 | 2021-03-31 | 13.6 | 4.4 | 0 | 2020-03-31 | 1.4 | 16.6 | 0 | 2019-03-31 | 0.5 | 17.5 | 0 | 2018-03-31 | -1.6 | 19.6 | 0 | 2017-03-31 | 1.4 | 16.6 | 0 | 2016-03-31 | 6.5 | 11.5 | 0 | 16 | 0
2025-03-31 | 0.1 | 17.9 | 0 | 2024-03-31 | 2.5 | 15.5 | 0 | 2023-03-31 | -3.9 | 21.9 | 0 | 2022-03-31 | -0.9 | 18.9 | 0 | 2021-03-31 | 14.4 | 3.6 | 0 | 2020-03-31 | 1.2 | 16.8 | 0 | 2019-03-31 | 0.4 | 17.6 | 0 | 2018-03-31 | -2.4 | 20.4 | 0 | 2017-03-31 | 1.4 | 16.6 | 0 | 2016-03-31 | 4.8 | 13.2 | 0 | 16.24 | 0
2025-03-31 | 0.1 | 17.9 | 0 | 2024-03-31 | 2.4 | 15.6 | 0 | 2023-03-31 | -5.2 | 23.2 | 0 | 2022-03-31 | -0.8 | 18.8 | 0 | 2021-03-31 | 12.7 | 5.3 | 0 | 2020-03-31 | 0.9 | 17.1 | 0 | 2019-03-31 | 0.3 | 17.7 | 0 | 2018-03-31 | -2.7 | 20.7 | 0 | 2017-03-31 | 1.1 | 16.9 | 0 | 2016-03-31 | 5 | 13 | 0 | 16.62 | 0
2025-03-31 | 0.1 | 17.9 | 0 | 2024-03-31 | 2.5 | 15.5 | 0 | 2023-03-31 | -4.5 | 22.5 | 0 | 2022-03-31 | -1 | 19 | 0 | 2021-03-31 | 12 | 6 | 0 | 2020-03-31 | 1 | 17 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | -3 | 21 | 0 | 2017-03-31 | 0.7 | 17.3 | 0 | 2016-03-31 | 4.6 | 13.4 | 0 | 16.76 | 0
2025-03-31 | 0.3 | 17.7 | 0 | 2024-03-31 | 2.4 | 15.6 | 0 | 2023-03-31 | -4.8 | 22.8 | 0 | 2022-03-31 | -0.7 | 18.7 | 0 | 2021-03-31 | 11.9 | 6.1 | 0 | 2020-03-31 | 0.8 | 17.2 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | -3.5 | 21.5 | 0 | 2017-03-31 | 0.9 | 17.1 | 0 | 2016-03-31 | 4.8 | 13.2 | 0 | 16.79 | 0
2025-03-31 | 0.5 | 17.5 | 0 | 2024-03-31 | 2 | 16 | 0 | 2023-03-31 | -5.3 | 23.3 | 0 | 2022-03-31 | -0.6 | 18.6 | 0 | 2021-03-31 | 10.4 | 7.6 | 0 | 2020-03-31 | 0.4 | 17.6 | 0 | 2019-03-31 | -0.2 | 18.2 | 0 | 2018-03-31 | -3.8 | 21.8 | 0 | 2017-03-31 | 0.4 | 17.6 | 0 | 2016-03-31 | 5 | 13 | 0 | 17.12 | 0
2025-03-31 | 0.3 | 17.7 | 0 | 2024-03-31 | 0.2 | 17.8 | 0 | 2023-03-31 | -5.3 | 23.3 | 0 | 2022-03-31 | -0.4 | 18.4 | 0 | 2021-03-31 | 10.7 | 7.3 | 0 | 2020-03-31 | 0.3 | 17.7 | 0 | 2019-03-31 | -0.5 | 18.5 | 0 | 2018-03-31 | -3.2 | 21.2 | 0 | 2017-03-31 | 0.3 | 17.7 | 0 | 2016-03-31 | 6.3 | 11.7 | 0 | 17.13 | 0
2025-03-31 | 0.6 | 17.4 | 0 | 2024-03-31 | 1.9 | 16.1 | 0 | 2023-03-31 | -5.2 | 23.2 | 0 | 2022-03-31 | 0.1 | 17.9 | 0 | 2021-03-31 | 11.2 | 6.8 | 0 | 2020-03-31 | 0.8 | 17.2 | 0 | 2019-03-31 | -1.3 | 19.3 | 0 | 2018-03-31 | -1.6 | 19.6 | 0 | 2017-03-31 | 0.5 | 17.5 | 0 | 2016-03-31 | 6.1 | 11.9 | 0 | 16.69 | 0
2025-03-31 | 3.1 | 14.9 | 0 | 2024-03-31 | 2.2 | 15.8 | 0 | 2023-03-31 | -2.4 | 20.4 | 0 | 2022-03-31 | 0.6 | 17.4 | 0 | 2021-03-31 | 11.7 | 6.3 | 0 | 2020-03-31 | 1.3 | 16.7 | 0 | 2019-03-31 | -1.3 | 19.3 | 0 | 2018-03-31 | -0.1 | 18.1 | 0 | 2017-03-31 | 0.7 | 17.3 | 0 | 2016-03-31 | 7.6 | 10.4 | 0 | 15.66 | 0
2025-03-31 | 6.3 | 11.7 | 0 | 2024-03-31 | 4.4 | 13.6 | 0 | 2023-03-31 | -1.2 | 19.2 | 0 | 2022-03-31 | 0.7 | 17.3 | 0 | 2021-03-31 | 12.5 | 5.5 | 0 | 2020-03-31 | 1.5 | 16.5 | 0 | 2019-03-31 | -1.1 | 19.1 | 0 | 2018-03-31 | 2 | 16 | 0 | 2017-03-31 | 1.1 | 16.9 | 0 | 2016-03-31 | 8 | 10 | 0 | 14.58 | 0
2025-03-31 | 7.8 | 10.2 | 0 | 2024-03-31 | 5.4 | 12.6 | 0 | 2023-03-31 | 0.5 | 17.5 | 0 | 2022-03-31 | 1.7 | 16.3 | 0 | 2021-03-31 | 12.4 | 5.6 | 0 | 2020-03-31 | 2.6 | 15.4 | 0 | 2019-03-31 | -0.8 | 18.8 | 0 | 2018-03-31 | 2.5 | 15.5 | 0 | 2017-03-31 | 1.6 | 16.4 | 0 | 2016-03-31 | 8.6 | 9.4 | 0 | 13.77 | 0
2025-03-31 | 4.4 | 13.6 | 0 | 2024-03-31 | 6.7 | 11.3 | 0 | 2023-03-31 | 1.5 | 16.5 | 0 | 2022-03-31 | 2.7 | 15.3 | 0 | 2021-03-31 | 12.6 | 5.4 | 0 | 2020-03-31 | 3.7 | 14.3 | 0 | 2019-03-31 | -0.1 | 18.1 | 0 | 2018-03-31 | 5.2 | 12.8 | 0 | 2017-03-31 | 1.8 | 16.2 | 0 | 2016-03-31 | 9.7 | 8.3 | 0 | 13.18 | 0
2025-03-31 | 7.3 | 10.7 | 0 | 2024-03-31 | 6.4 | 11.6 | 0 | 2023-03-31 | 1.6 | 16.4 | 0 | 2022-03-31 | 3.8 | 14.2 | 0 | 2021-03-31 | 12.6 | 5.4 | 0 | 2020-03-31 | 6.3 | 11.7 | 0 | 2019-03-31 | 0.4 | 17.6 | 0 | 2018-03-31 | 6.2 | 11.8 | 0 | 2017-03-31 | 1.2 | 16.8 | 0 | 2016-03-31 | 9.9 | 8.1 | 0 | 12.43 | 0
2025-03-31 | 7.8 | 10.2 | 0 | 2024-03-31 | 8.5 | 9.5 | 0 | 2023-03-31 | 1.8 | 16.2 | 0 | 2022-03-31 | 3.4 | 14.6 | 0 | 2021-03-31 | 6.8 | 11.2 | 0 | 2020-03-31 | 7.3 | 10.7 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | 7.6 | 10.4 | 0 | 2017-03-31 | 0.6 | 17.4 | 0 | 2016-03-31 | 10.2 | 7.8 | 0 | 12.6 | 0
2025-03-31 | 8.5 | 9.5 | 0 | 2024-03-31 | 9.1 | 8.9 | 0 | 2023-03-31 | -0.1 | 18.1 | 0 | 2022-03-31 | 7.4 | 10.6 | 0 | 2021-03-31 | 6.1 | 11.9 | 0 | 2020-03-31 | 8 | 10 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | 7.5 | 10.5 | 0 | 2017-03-31 | 0.4 | 17.6 | 0 | 2016-03-31 | 10.1 | 7.9 | 0 | 12.3 | 0
2025-03-31 | 6.5 | 11.5 | 0 | 2024-03-31 | 10.1 | 7.9 | 0 | 2023-03-31 | -0.4 | 18.4 | 0 | 2022-03-31 | 9.7 | 8.3 | 0 | 2021-03-31 | 4.9 | 13.1 | 0 | 2020-03-31 | 8.4 | 9.6 | 0 | 2019-03-31 | -0.1 | 18.1 | 0 | 2018-03-31 | 7.1 | 10.9 | 0 | 2017-03-31 | 0 | 18 | 0 | 2016-03-31 | 10.7 | 7.3 | 0 | 12.31 | 0
2025-03-31 | 3.7 | 14.3 | 0 | 2024-03-31 | 10.3 | 7.7 | 0 | 2023-03-31 | -0.2 | 18.2 | 0 | 2022-03-31 | 10.8 | 7.2 | 0 | 2021-03-31 | 4.7 | 13.3 | 0 | 2020-03-31 | 8.2 | 9.8 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | 6.6 | 11.4 | 0 | 2017-03-31 | 0 | 18 | 0 | 2016-03-31 | 11.7 | 6.3 | 0 | 12.42 | 0
2025-03-31 | 2.8 | 15.2 | 0 | 2024-03-31 | 9.9 | 8.1 | 0 | 2023-03-31 | -0.3 | 18.3 | 0 | 2022-03-31 | 8.9 | 9.1 | 0 | 2021-03-31 | 5 | 13 | 0 | 2020-03-31 | 6.6 | 11.4 | 0 | 2019-03-31 | 0.4 | 17.6 | 0 | 2018-03-31 | 6.2 | 11.8 | 0 | 2017-03-31 | 0.2 | 17.8 | 0 | 2016-03-31 | 12.2 | 5.8 | 0 | 12.81 | 0
2025-03-31 | 3.1 | 14.9 | 0 | 2024-03-31 | 8.7 | 9.3 | 0 | 2023-03-31 | -0.5 | 18.5 | 0 | 2022-03-31 | 13.3 | 4.7 | 0 | 2021-03-31 | 5 | 13 | 0 | 2020-03-31 | 5 | 13 | 0 | 2019-03-31 | 0.2 | 17.8 | 0 | 2018-03-31 | 5.2 | 12.8 | 0 | 2017-03-31 | 0 | 18 | 0 | 2016-03-31 | 11.6 | 6.4 | 0 | 12.84 | 0
2025-03-31 | 1.5 | 16.5 | 0 | 2024-03-31 | 7.9 | 10.1 | 0 | 2023-03-31 | -0.5 | 18.5 | 0 | 2022-03-31 | 12.2 | 5.8 | 0 | 2021-03-31 | 3.5 | 14.5 | 0 | 2020-03-31 | 2.6 | 15.4 | 0 | 2019-03-31 | 0 | 18 | 0 | 2018-03-31 | 5.3 | 12.7 | 0 | 2017-03-31 | 0.1 | 17.9 | 0 | 2016-03-31 | 11.8 | 6.2 | 0 | 13.56 | 0
2025-03-31 | 0.7 | 17.3 | 0 | 2024-03-31 | 4.8 | 13.2 | 0 | 2023-03-31 | -0.5 | 18.5 | 0 | 2022-03-31 | 10.2 | 7.8 | 0 | 2021-03-31 | 2.1 | 15.9 | 0 | 2020-03-31 | 1.5 | 16.5 | 0 | 2019-03-31 | -0.2 | 18.2 | 0 | 2018-03-31 | 6 | 12 | 0 | 2017-03-31 | 0.1 | 17.9 | 0 | 2016-03-31 | 12.1 | 5.9 | 0 | 14.32 | 0
2025-03-31 | 0.1 | 17.9 | 0 | 2024-03-31 | 3 | 15 | 0 | 2023-03-31 | -0.4 | 18.4 | 0 | 2022-03-31 | 8.9 | 9.1 | 0 | 2021-03-31 | 2.3 | 15.7 | 0 | 2020-03-31 | 1.6 | 16.4 | 0 | 2019-03-31 | -0.6 | 18.6 | 0 | 2018-03-31 | 7.2 | 10.8 | 0 | 2017-03-31 | 0.1 | 17.9 | 0 | 2016-03-31 | 12.2 | 5.8 | 0 | 14.56 | 0
2025-03-31 | -0.4 | 18.4 | 0 | 2024-03-31 | 2.1 | 15.9 | 0 | 2023-03-31 | -0.3 | 18.3 | 0 | 2022-03-31 | 8.1 | 9.9 | 0 | 2021-03-31 | 1.7 | 16.3 | 0 | 2020-03-31 | 0.2 | 17.8 | 0 | 2019-03-31 | -1.7 | 19.7 | 0 | 2018-03-31 | 4.8 | 13.2 | 0 | 2017-03-31 | 0.2 | 17.8 | 0 | 2016-03-31 | 12.3 | 5.7 | 0 | 15.3 | 0
2025-03-31 | -0.6 | 18.6 | 0 | 2024-03-31 | 1.6 | 16.4 | 0 | 2023-03-31 | -0.1 | 18.1 | 0 | 2022-03-31 | 7.9 | 10.1 | 0 | 2021-03-31 | 2.5 | 15.5 | 0 | 2020-03-31 | -0.6 | 18.6 | 0 | 2019-03-31 | -2.5 | 20.5 | 0 | 2018-03-31 | 3.8 | 14.2 | 0 | 2017-03-31 | 0.2 | 17.8 | 0 | 2016-03-31 | 12.3 | 5.7 | 0 | 15.55 | 0
2025-04-01 | -0.8 | 18.8 | 0 | 2024-04-01 | 0.3 | 17.7 | 0 | 2023-04-01 | 0 | 18 | 0 | 2022-04-01 | 7.2 | 10.8 | 0 | 2021-04-01 | 3.2 | 14.8 | 0 | 2020-04-01 | 0.8 | 17.2 | 0 | 2019-04-01 | -3.2 | 21.2 | 0 | 2018-04-01 | 4.4 | 13.6 | 0 | 2017-04-01 | 0.2 | 17.8 | 0 | 2016-04-01 | 12 | 6 | 0 | 15.59 | 0
2025-04-01 | -1.2 | 19.2 | 0 | 2024-04-01 | 0.6 | 17.4 | 0 | 2023-04-01 | 0 | 18 | 0 | 2022-04-01 | 6.3 | 11.7 | 0 | 2021-04-01 | 2.9 | 15.1 | 0 | 2020-04-01 | -1.4 | 19.4 | 0 | 2019-04-01 | -4.1 | 22.1 | 0 | 2018-04-01 | 5.2 | 12.8 | 0 | 2017-04-01 | 0.2 | 17.8 | 0 | 2016-04-01 | 14 | 4 | 0 | 15.75 | 0
2025-04-01 | -1.2 | 19.2 | 0 | 2024-04-01 | 0.3 | 17.7 | 0 | 2023-04-01 | -0.1 | 18.1 | 0 | 2022-04-01 | 5.4 | 12.6 | 0 | 2021-04-01 | 2.7 | 15.3 | 0 | 2020-04-01 | -1.2 | 19.2 | 0 | 2019-04-01 | -5.1 | 23.1 | 0 | 2018-04-01 | 5.2 | 12.8 | 0 | 2017-04-01 | 0.2 | 17.8 | 0 | 2016-04-01 | 13.4 | 4.6 | 0 | 16.04 | 0
2025-04-01 | -1.4 | 19.4 | 0 | 2024-04-01 | -0.4 | 18.4 | 0 | 2023-04-01 | 0 | 18 | 0 | 2022-04-01 | 5 | 13 | 0 | 2021-04-01 | 2.2 | 15.8 | 0 | 2020-04-01 | -1.9 | 19.9 | 0 | 2019-04-01 | -5.8 | 23.8 | 0 | 2018-04-01 | 3.9 | 14.1 | 0 | 2017-04-01 | 0.1 | 17.9 | 0 | 2016-04-01 | 13.1 | 4.9 | 0 | 16.52 | 0
2025-04-01 | -2.3 | 20.3 | 0 | 2024-04-01 | 0.5 | 17.5 | 0 | 2023-04-01 | 0 | 18 | 0 | 2022-04-01 | 4 | 14 | 0 | 2021-04-01 | 1 | 17 | 0 | 2020-04-01 | -2 | 20 | 0 | 2019-04-01 | -6.3 | 24.3 | 0 | 2018-04-01 | 1.7 | 16.3 | 0 | 2017-04-01 | 0 | 18 | 0 | 2016-04-01 | 13.1 | 4.9 | 0 | 17.03 | 0
2025-04-01 | -2.5 | 20.5 | 0 | 2024-04-01 | -2.3 | 20.3 | 0 | 2023-04-01 | 0.1 | 17.9 | 0 | 2022-04-01 | 3.3 | 14.7 | 0 | 2021-04-01 | 0.7 | 17.3 | 0 | 2020-04-01 | -1.7 | 19.7 | 0 | 2019-04-01 | -6.9 | 24.9 | 0 | 2018-04-01 | 0.7 | 17.3 | 0 | 2017-04-01 | 0 | 18 | 0 | 2016-04-01 | 12.5 | 5.5 | 0 | 17.61 | 0
2025-04-01 | -3.7 | 21.7 | 0 | 2024-04-01 | -0.8 | 18.8 | 0 | 2023-04-01 | 0.2 | 17.8 | 0 | 2022-04-01 | 2.9 | 15.1 | 0 | 2021-04-01 | 0.1 | 17.9 | 0 | 2020-04-01 | -2.2 | 20.2 | 0 | 2019-04-01 | -7.6 | 25.6 | 0 | 2018-04-01 | -0.6 | 18.6 | 0 | 2017-04-01 | 0 | 18 | 0 | 2016-04-01 | 11.6 | 6.4 | 0 | 18.01 | 0
2025-04-01 | -3.5 | 21.5 | 0 | 2024-04-01 | 0.1 | 17.9 | 0 | 2023-04-01 | 0.3 | 17.7 | 0 | 2022-04-01 | 2.7 | 15.3 | 0 | 2021-04-01 | -0.9 | 18.9 | 0 | 2020-04-01 | 0.2 | 17.8 | 0 | 2019-04-01 | -7 | 25 | 0 | 2018-04-01 | -2 | 20 | 0 | 2017-04-01 | 0.1 | 17.9 | 0 | 2016-04-01 | 11.4 | 6.6 | 0 | 17.86 | 0
2025-04-01 | -4.1 | 22.1 | 0 | 2024-04-01 | 1.7 | 16.3 | 0 | 2023-04-01 | 0.5 | 17.5 | 0 | 2022-04-01 | 3 | 15 | 0 | 2021-04-01 | -1.3 | 19.3 | 0 | 2020-04-01 | 2.1 | 15.9 | 0 | 2019-04-01 | -6 | 24 | 0 | 2018-04-01 | -1.8 | 19.8 | 0 | 2017-04-01 | 0.3 | 17.7 | 0 | 2016-04-01 | 11.6 | 6.4 | 0 | 17.4 | 0
2025-04-01 | -3.7 | 21.7 | 0 | 2024-04-01 | 4 | 14 | 0 | 2023-04-01 | 0.8 | 17.2 | 0 | 2022-04-01 | 2.1 | 15.9 | 0 | 2021-04-01 | -1.3 | 19.3 | 0 | 2020-04-01 | 3 | 15 | 0 | 2019-04-01 | -4.9 | 22.9 | 0 | 2018-04-01 | -1.2 | 19.2 | 0 | 2017-04-01 | 0.6 | 17.4 | 0 | 2016-04-01 | 11.9 | 6.1 | 0 | 16.87 | 0
2025-04-01 | -2.8 | 20.8 | 0 | 2024-04-01 | 6.6 | 11.4 | 0 | 2023-04-01 | 1.2 | 16.8 | 0 | 2022-04-01 | 2.2 | 15.8 | 0 | 2021-04-01 | -1 | 19 | 0 | 2020-04-01 | 3.8 | 14.2 | 0 | 2019-04-01 | -3.7 | 21.7 | 0 | 2018-04-01 | -0.6 | 18.6 | 0 | 2017-04-01 | 0.9 | 17.1 | 0 | 2016-04-01 | 11.9 | 6.1 | 0 | 16.15 | 0
2025-04-01 | -2.1 | 20.1 | 0 | 2024-04-01 | 9 | 9 | 0 | 2023-04-01 | 2.2 | 15.8 | 0 | 2022-04-01 | 2.7 | 15.3 | 0 | 2021-04-01 | -1.4 | 19.4 | 0 | 2020-04-01 | 4.5 | 13.5 | 0 | 2019-04-01 | -2.4 | 20.4 | 0 | 2018-04-01 | -0.8 | 18.8 | 0 | 2017-04-01 | 1.3 | 16.7 | 0 | 2016-04-01 | 10.1 | 7.9 | 0 | 15.69 | 0
2025-04-01 | -1 | 19 | 0 | 2024-04-01 | 8.6 | 9.4 | 0 | 2023-04-01 | 4.9 | 13.1 | 0 | 2022-04-01 | 4.6 | 13.4 | 0 | 2021-04-01 | 0.2 | 17.8 | 0 | 2020-04-01 | 4.8 | 13.2 | 0 | 2019-04-01 | -1.9 | 19.9 | 0 | 2018-04-01 | 0 | 18 | 0 | 2017-04-01 | 1.8 | 16.2 | 0 | 2016-04-01 | 9.8 | 8.2 | 0 | 14.82 | 0
2025-04-01 | -0.4 | 18.4 | 0 | 2024-04-01 | 9.4 | 8.6 | 0 | 2023-04-01 | 8.5 | 9.5 | 0 | 2022-04-01 | 3.9 | 14.1 | 0 | 2021-04-01 | -0.1 | 18.1 | 0 | 2020-04-01 | 6.3 | 11.7 | 0 | 2019-04-01 | -0.4 | 18.4 | 0 | 2018-04-01 | 1.2 | 16.8 | 0 | 2017-04-01 | 2.6 | 15.4 | 0 | 2016-04-01 | 8.8 | 9.2 | 0 | 14.02 | 0
2025-04-01 | 0.2 | 17.8 | 0 | 2024-04-01 | 10.3 | 7.7 | 0 | 2023-04-01 | 9 | 9 | 0 | 2022-04-01 | 3 | 15 | 0 | 2021-04-01 | -0.3 | 18.3 | 0 | 2020-04-01 | 6.2 | 11.8 | 0 | 2019-04-01 | 0.7 | 17.3 | 0 | 2018-04-01 | 1.8 | 16.2 | 0 | 2017-04-01 | 3.9 | 14.1 | 0 | 2016-04-01 | 9.7 | 8.3 | 0 | 13.55 | 0
2025-04-01 | 0.5 | 17.5 | 0 | 2024-04-01 | 11.2 | 6.8 | 0 | 2023-04-01 | 8.4 | 9.6 | 0 | 2022-04-01 | 2 | 16 | 0 | 2021-04-01 | -1.8 | 19.8 | 0 | 2020-04-01 | 6.7 | 11.3 | 0 | 2019-04-01 | 1.3 | 16.7 | 0 | 2018-04-01 | 2.6 | 15.4 | 0 | 2017-04-01 | 3.7 | 14.3 | 0 | 2016-04-01 | 9.4 | 8.6 | 0 | 13.6 | 0
2025-04-01 | 0.2 | 17.8 | 0 | 2024-04-01 | 10.1 | 7.9 | 0 | 2023-04-01 | 6.9 | 11.1 | 0 | 2022-04-01 | 0.9 | 17.1 | 0 | 2021-04-01 | -3 | 21 | 0 | 2020-04-01 | 6.5 | 11.5 | 0 | 2019-04-01 | 1.7 | 16.3 | 0 | 2018-04-01 | 1.4 | 16.6 | 0 | 2017-04-01 | 3.6 | 14.4 | 0 | 2016-04-01 | 8.1 | 9.9 | 0 | 14.36 | 0
2025-04-01 | 0.1 | 17.9 | 0 | 2024-04-01 | 9.1 | 8.9 | 0 | 2023-04-01 | 6.7 | 11.3 | 0 | 2022-04-01 | 0.9 | 17.1 | 0 | 2021-04-01 | -3.7 | 21.7 | 0 | 2020-04-01 | 6.3 | 11.7 | 0 | 2019-04-01 | 2.1 | 15.9 | 0 | 2018-04-01 | 1.2 | 16.8 | 0 | 2017-04-01 | 3.9 | 14.1 | 0 | 2016-04-01 | 7.1 | 10.9 | 0 | 14.63 | 0
2025-04-01 | -0.9 | 18.9 | 0 | 2024-04-01 | 8 | 10 | 0 | 2023-04-01 | 4.2 | 13.8 | 0 | 2022-04-01 | 1.1 | 16.9 | 0 | 2021-04-01 | -4.7 | 22.7 | 0 | 2020-04-01 | 5.5 | 12.5 | 0 | 2019-04-01 | 1.7 | 16.3 | 0 | 2018-04-01 | -0.1 | 18.1 | 0 | 2017-04-01 | 3.5 | 14.5 | 0 | 2016-04-01 | 5.7 | 12.3 | 0 | 15.6 | 0
2025-04-01 | -2.2 | 20.2 | 0 | 2024-04-01 | 6 | 12 | 0 | 2023-04-01 | 2.6 | 15.4 | 0 | 2022-04-01 | 1 | 17 | 0 | 2021-04-01 | -4.8 | 22.8 | 0 | 2020-04-01 | 4.7 | 13.3 | 0 | 2019-04-01 | 0.8 | 17.2 | 0 | 2018-04-01 | -0.9 | 18.9 | 0 | 2017-04-01 | 2 | 16 | 0 | 2016-04-01 | 4.2 | 13.8 | 0 | 16.66 | 0
2025-04-01 | -3 | 21 | 0 | 2024-04-01 | 4.4 | 13.6 | 0 | 2023-04-01 | 1.9 | 16.1 | 0 | 2022-04-01 | 0.8 | 17.2 | 0 | 2021-04-01 | -4.5 | 22.5 | 0 | 2020-04-01 | 4.5 | 13.5 | 0 | 2019-04-01 | 0.1 | 17.9 | 0 | 2018-04-01 | -1.2 | 19.2 | 0 | 2017-04-01 | 1.2 | 16.8 | 0 | 2016-04-01 | 3.6 | 14.4 | 0 | 17.22 | 0
2025-04-01 | -3.6 | 21.6 | 0 | 2024-04-01 | 3.5 | 14.5 | 0 | 2023-04-01 | 1.4 | 16.6 | 0 | 2022-04-01 | 0.5 | 17.5 | 0 | 2021-04-01 | -4.6 | 22.6 | 0 | 2020-04-01 | 4.5 | 13.5 | 0 | 2019-04-01 | -0.8 | 18.8 | 0 | 2018-04-01 | -1.8 | 19.8 | 0 | 2017-04-01 | 0.9 | 17.1 | 0 | 2016-04-01 | 3 | 15 | 0 | 17.7 | 0
2025-04-01 | -4.5 | 22.5 | 0 | 2024-04-01 | 2.5 | 15.5 | 0 | 2023-04-01 | 0.8 | 17.2 | 0 | 2022-04-01 | 0.2 | 17.8 | 0 | 2021-04-01 | -4.7 | 22.7 | 0 | 2020-04-01 | 4.5 | 13.5 | 0 | 2019-04-01 | -1.1 | 19.1 | 0 | 2018-04-01 | -2.6 | 20.6 | 0 | 2017-04-01 | 0.4 | 17.6 | 0 | 2016-04-01 | 2.6 | 15.4 | 0 | 18.19 | 0
2025-04-01 | -5.4 | 23.4 | 0 | 2024-04-01 | 1.5 | 16.5 | 0 | 2023-04-01 | -1 | 19 | 0 | 2022-04-01 | -0.6 | 18.6 | 0 | 2021-04-01 | -5.5 | 23.5 | 0 | 2020-04-01 | 3.8 | 14.2 | 0 | 2019-04-01 | -1.7 | 19.7 | 0 | 2018-04-01 | -3 | 21 | 0 | 2017-04-01 | 0.3 | 17.7 | 0 | 2016-04-01 | 2.4 | 15.6 | 0 | 18.92 | 0
2025-04-02 | -5.7 | 23.7 | 0 | 2024-04-02 | 0.4 | 17.6 | 0 | 2023-04-02 | -3.1 | 21.1 | 0 | 2022-04-02 | -1.3 | 19.3 | 0 | 2021-04-02 | -4.9 | 22.9 | 0 | 2020-04-02 | 1 | 17 | 0 | 2019-04-02 | -2.3 | 20.3 | 0 | 2018-04-02 | -3.9 | 21.9 | 0 | 2017-04-02 | -0.4 | 18.4 | 0 | 2016-04-02 | 2.2 | 15.8 | 0 | 19.8 | 0
2025-04-02 | -6.5 | 24.5 | 0 | 2024-04-02 | -1.6 | 19.6 | 0 | 2023-04-02 | -4.7 | 22.7 | 0 | 2022-04-02 | -1.6 | 19.6 | 0 | 2021-04-02 | -5.3 | 23.3 | 0 | 2020-04-02 | 1.2 | 16.8 | 0 | 2019-04-02 | -3 | 21 | 0 | 2018-04-02 | -3.6 | 21.6 | 0 | 2017-04-02 | 0 | 18 | 0 | 2016-04-02 | 1.4 | 16.6 | 0 | 20.37 | 0
2025-04-02 | -7.5 | 25.5 | 0 | 2024-04-02 | -1.6 | 19.6 | 0 | 2023-04-02 | -5.8 | 23.8 | 0 | 2022-04-02 | -1.8 | 19.8 | 0 | 2021-04-02 | -5.5 | 23.5 | 0 | 2020-04-02 | -0.2 | 18.2 | 0 | 2019-04-02 | -2.7 | 20.7 | 0 | 2018-04-02 | -4.1 | 22.1 | 0 | 2017-04-02 | -0.6 | 18.6 | 0 | 2016-04-02 | 1.1 | 16.9 | 0 | 20.87 | 0
2025-04-02 | -8.3 | 26.3 | 0 | 2024-04-02 | -3.1 | 21.1 | 0 | 2023-04-02 | -7 | 25 | 0 | 2022-04-02 | -2.4 | 20.4 | 0 | 2021-04-02 | -5.9 | 23.9 | 0 | 2020-04-02 | -1 | 19 | 0 | 2019-04-02 | -2.3 | 20.3 | 0 | 2018-04-02 | -5.1 | 23.1 | 0 | 2017-04-02 | -1.3 | 19.3 | 0 | 2016-04-02 | 0.8 | 17.2 | 0 | 21.56 | 0
2025-04-02 | -8.9 | 26.9 | 0 | 2024-04-02 | -2.8 | 20.8 | 0 | 2023-04-02 | -8.4 | 26.4 | 0 | 2022-04-02 | -2.8 | 20.8 | 0 | 2021-04-02 | -6.3 | 24.3 | 0 | 2020-04-02 | -1.1 | 19.1 | 0 | 2019-04-02 | -2.3 | 20.3 | 0 | 2018-04-02 | -8.2 | 26.2 | 0 | 2017-04-02 | -1.4 | 19.4 | 0 | 2016-04-02 | -0.1 | 18.1 | 0 | 22.23 | 0
2025-04-02 | -8.6 | 26.6 | 0 | 2024-04-02 | -3.3 | 21.3 | 0 | 2023-04-02 | -9.1 | 27.1 | 0 | 2022-04-02 | -3.2 | 21.2 | 0 | 2021-04-02 | -6.8 | 24.8 | 0 | 2020-04-02 | 0.9 | 17.1 | 0 | 2019-04-02 | -2 | 20 | 0 | 2018-04-02 | -5.8 | 23.8 | 0 | 2017-04-02 | -1.8 | 19.8 | 0 | 2016-04-02 | -2.1 | 20.1 | 0 | 22.18 | 0
2025-04-02 | -8.5 | 26.5 | 0 | 2024-04-02 | -2.2 | 20.2 | 0 | 2023-04-02 | -9.3 | 27.3 | 0 | 2022-04-02 | -3.3 | 21.3 | 0 | 2021-04-02 | -7.2 | 25.2 | 0 | 2020-04-02 | 0.4 | 17.6 | 0 | 2019-04-02 | -1.7 | 19.7 | 0 | 2018-04-02 | -5.6 | 23.6 | 0 | 2017-04-02 | -2.2 | 20.2 | 0 | 2016-04-02 | -2 | 20 | 0 | 22.16 | 0
2025-04-02 | -6.7 | 24.7 | 0 | 2024-04-02 | -0.4 | 18.4 | 0 | 2023-04-02 | -9 | 27 | 0 | 2022-04-02 | -1.9 | 19.9 | 0 | 2021-04-02 | -6.3 | 24.3 | 0 | 2020-04-02 | 2.4 | 15.6 | 0 | 2019-04-02 | -1.1 | 19.1 | 0 | 2018-04-02 | -4.2 | 22.2 | 0 | 2017-04-02 | -1.9 | 19.9 | 0 | 2016-04-02 | 0.6 | 17.4 | 0 | 20.85 | 0
2025-04-02 | -4.9 | 22.9 | 0 | 2024-04-02 | 2 | 16 | 0 | 2023-04-02 | -8.2 | 26.2 | 0 | 2022-04-02 | -0.9 | 18.9 | 0 | 2021-04-02 | -5.3 | 23.3 | 0 | 2020-04-02 | 4 | 14 | 0 | 2019-04-02 | -0.3 | 18.3 | 0 | 2018-04-02 | -1.3 | 19.3 | 0 | 2017-04-02 | -0.3 | 18.3 | 0 | 2016-04-02 | 2 | 16 | 0 | 19.32 | 0
2025-04-02 | -2.9 | 20.9 | 0 | 2024-04-02 | 4 | 14 | 0 | 2023-04-02 | -8 | 26 | 0 | 2022-04-02 | 0.8 | 17.2 | 0 | 2021-04-02 | -3.9 | 21.9 | 0 | 2020-04-02 | 4.6 | 13.4 | 0 | 2019-04-02 | 0.8 | 17.2 | 0 | 2018-04-02 | -0.4 | 18.4 | 0 | 2017-04-02 | 2.9 | 15.1 | 0 | 2016-04-02 | 3.6 | 14.4 | 0 | 17.85 | 0
2025-04-02 | -2.1 | 20.1 | 0 | 2024-04-02 | 6.6 | 11.4 | 0 | 2023-04-02 | -6.6 | 24.6 | 0 | 2022-04-02 | 1.8 | 16.2 | 0 | 2021-04-02 | -2.1 | 20.1 | 0 | 2020-04-02 | 6.3 | 11.7 | 0 | 2019-04-02 | 2.1 | 15.9 | 0 | 2018-04-02 | 0 | 18 | 0 | 2017-04-02 | 5.2 | 12.8 | 0 | 2016-04-02 | 4.2 | 13.8 | 0 | 16.46 | 0
2025-04-02 | -1 | 19 | 0 | 2024-04-02 | 8.3 | 9.7 | 0 | 2023-04-02 | -5.4 | 23.4 | 0 | 2022-04-02 | 3.1 | 14.9 | 0 | 2021-04-02 | -1 | 19 | 0 | 2020-04-02 | 8.1 | 9.9 | 0 | 2019-04-02 | 4.3 | 13.7 | 0 | 2018-04-02 | 1.3 | 16.7 | 0 | 2017-04-02 | 6.8 | 11.2 | 0 | 2016-04-02 | 3.7 | 14.3 | 0 | 15.18 | 0
2025-04-02 | -1.1 | 19.1 | 0 | 2024-04-02 | 9.6 | 8.4 | 0 | 2023-04-02 | -4 | 22 | 0 | 2022-04-02 | 3.7 | 14.3 | 0 | 2021-04-02 | 0.3 | 17.7 | 0 | 2020-04-02 | 7.5 | 10.5 | 0 | 2019-04-02 | 5.2 | 12.8 | 0 | 2018-04-02 | 1.8 | 16.2 | 0 | 2017-04-02 | 7.4 | 10.6 | 0 | 2016-04-02 | 5.6 | 12.4 | 0 | 14.4 | 0
2025-04-02 | -0.1 | 18.1 | 0 | 2024-04-02 | 9.8 | 8.2 | 0 | 2023-04-02 | -2.9 | 20.9 | 0 | 2022-04-02 | 4.8 | 13.2 | 0 | 2021-04-02 | 1.7 | 16.3 | 0 | 2020-04-02 | 8.5 | 9.5 | 0 | 2019-04-02 | 5.9 | 12.1 | 0 | 2018-04-02 | 3.2 | 14.8 | 0 | 2017-04-02 | 8.2 | 9.8 | 0 | 2016-04-02 | 4.9 | 13.1 | 0 | 13.6 | 0
2025-04-02 | -0.5 | 18.5 | 0 | 2024-04-02 | 10.7 | 7.3 | 0 | 2023-04-02 | -2.2 | 20.2 | 0 | 2022-04-02 | 5.3 | 12.7 | 0 | 2021-04-02 | 2.5 | 15.5 | 0 | 2020-04-02 | 9.5 | 8.5 | 0 | 2019-04-02 | 6.2 | 11.8 | 0 | 2018-04-02 | 4.5 | 13.5 | 0 | 2017-04-02 | 9 | 9 | 0 | 2016-04-02 | 5.4 | 12.6 | 0 | 12.96 | 0
2025-04-02 | -0.2 | 18.2 | 0 | 2024-04-02 | 11.2 | 6.8 | 0 | 2023-04-02 | -1.4 | 19.4 | 0 | 2022-04-02 | 6 | 12 | 0 | 2021-04-02 | 3.3 | 14.7 | 0 | 2020-04-02 | 10.2 | 7.8 | 0 | 2019-04-02 | 6.9 | 11.1 | 0 | 2018-04-02 | 4.5 | 13.5 | 0 | 2017-04-02 | 9.4 | 8.6 | 0 | 2016-04-02 | 6 | 12 | 0 | 12.41 | 0
2025-04-02 | -0.7 | 18.7 | 0 | 2024-04-02 | 11.1 | 6.9 | 0 | 2023-04-02 | -0.3 | 18.3 | 0 | 2022-04-02 | 6.5 | 11.5 | 0 | 2021-04-02 | 2.9 | 15.1 | 0 | 2020-04-02 | 10.4 | 7.6 | 0 | 2019-04-02 | 6.6 | 11.4 | 0 | 2018-04-02 | 4.8 | 13.2 | 0 | 2017-04-02 | 9.6 | 8.4 | 0 | 2016-04-02 | 5 | 13 | 0 | 12.41 | 0
2025-04-02 | -0.9 | 18.9 | 0 | 2024-04-02 | 9.8 | 8.2 | 0 | 2023-04-02 | 0.4 | 17.6 | 0 | 2022-04-02 | 5.9 | 12.1 | 0 | 2021-04-02 | 2.6 | 15.4 | 0 | 2020-04-02 | 9.7 | 8.3 | 0 | 2019-04-02 | 6.5 | 11.5 | 0 | 2018-04-02 | 4.3 | 13.7 | 0 | 2017-04-02 | 9.5 | 8.5 | 0 | 2016-04-02 | 4.3 | 13.7 | 0 | 12.79 | 0
2025-04-02 | -3.1 | 21.1 | 0 | 2024-04-02 | 8.8 | 9.2 | 0 | 2023-04-02 | -0.4 | 18.4 | 0 | 2022-04-02 | 4.8 | 13.2 | 0 | 2021-04-02 | 1.6 | 16.4 | 0 | 2020-04-02 | 8.2 | 9.8 | 0 | 2019-04-02 | 5.8 | 12.2 | 0 | 2018-04-02 | 3.4 | 14.6 | 0 | 2017-04-02 | 8.4 | 9.6 | 0 | 2016-04-02 | 2.2 | 15.8 | 0 | 14.03 | 0
2025-04-02 | -3.2 | 21.2 | 0 | 2024-04-02 | 7.9 | 10.1 | 0 | 2023-04-02 | -1.9 | 19.9 | 0 | 2022-04-02 | 3.8 | 14.2 | 0 | 2021-04-02 | 0.3 | 17.7 | 0 | 2020-04-02 | 7.7 | 10.3 | 0 | 2019-04-02 | 4.8 | 13.2 | 0 | 2018-04-02 | 1.2 | 16.8 | 0 | 2017-04-02 | 6 | 12 | 0 | 2016-04-02 | 0.8 | 17.2 | 0 | 15.26 | 0
2025-04-02 | -2.8 | 20.8 | 0 | 2024-04-02 | 7.2 | 10.8 | 0 | 2023-04-02 | -1.5 | 19.5 | 0 | 2022-04-02 | 1.7 | 16.3 | 0 | 2021-04-02 | -0.5 | 18.5 | 0 | 2020-04-02 | 6.8 | 11.2 | 0 | 2019-04-02 | 4.3 | 13.7 | 0 | 2018-04-02 | 1 | 17 | 0 | 2017-04-02 | 6.3 | 11.7 | 0 | 2016-04-02 | -0.5 | 18.5 | 0 | 15.8 | 0
2025-04-02 | -2.5 | 20.5 | 0 | 2024-04-02 | 6.7 | 11.3 | 0 | 2023-04-02 | -1.1 | 19.1 | 0 | 2022-04-02 | 2.4 | 15.6 | 0 | 2021-04-02 | -2.7 | 20.7 | 0 | 2020-04-02 | 5.4 | 12.6 | 0 | 2019-04-02 | 4 | 14 | 0 | 2018-04-02 | 0.6 | 17.4 | 0 | 2017-04-02 | 3.8 | 14.2 | 0 | 2016-04-02 | -1.9 | 19.9 | 0 | 16.53 | 0
2025-04-02 | -1.9 | 19.9 | 0 | 2024-04-02 | 6.2 | 11.8 | 0 | 2023-04-02 | -1.6 | 19.6 | 0 | 2022-04-02 | 1.8 | 16.2 | 0 | 2021-04-02 | -3.2 | 21.2 | 0 | 2020-04-02 | 4.7 | 13.3 | 0 | 2019-04-02 | 5.2 | 12.8 | 0 | 2018-04-02 | 0.2 | 17.8 | 0 | 2017-04-02 | 4.7 | 13.3 | 0 | 2016-04-02 | -2.7 | 20.7 | 0 | 16.66 | 0
2025-04-02 | -1.6 | 19.6 | 0 | 2024-04-02 | 5.9 | 12.1 | 0 | 2023-04-02 | -1.9 | 19.9 | 0 | 2022-04-02 | 1.4 | 16.6 | 0 | 2021-04-02 | -3.5 | 21.5 | 0 | 2020-04-02 | 4.2 | 13.8 | 0 | 2019-04-02 | 4.9 | 13.1 | 0 | 2018-04-02 | 0 | 18 | 0 | 2017-04-02 | 1.1 | 16.9 | 0 | 2016-04-02 | -3.8 | 21.8 | 0 | 17.33 | 0
2025-04-03 | -1 | 19 | 0 | 2024-04-03 | 5.7 | 12.3 | 0 | 2023-04-03 | -1.9 | 19.9 | 0 | 2022-04-03 | -1.9 | 19.9 | 0 | 2021-04-03 | -5 | 23 | 0 | 2020-04-03 | 4.2 | 13.8 | 0 | 2019-04-03 | 4.7 | 13.3 | 0 | 2018-04-03 | -0.1 | 18.1 | 0 | 2017-04-03 | 2.1 | 15.9 | 0 | 2016-04-03 | -4.2 | 22.2 | 0 | 17.74 | 0
2025-04-03 | -0.4 | 18.4 | 0 | 2024-04-03 | 5.3 | 12.7 | 0 | 2023-04-03 | -2.1 | 20.1 | 0 | 2022-04-03 | -0.5 | 18.5 | 0 | 2021-04-03 | -4.1 | 22.1 | 0 | 2020-04-03 | 4.1 | 13.9 | 0 | 2019-04-03 | 4.5 | 13.5 | 0 | 2018-04-03 | -0.2 | 18.2 | 0 | 2017-04-03 | -0.2 | 18.2 | 0 | 2016-04-03 | -4.8 | 22.8 | 0 | 17.84 | 0
2025-04-03 | -0.2 | 18.2 | 0 | 2024-04-03 | 4.4 | 13.6 | 0 | 2023-04-03 | -2.5 | 20.5 | 0 | 2022-04-03 | -1.2 | 19.2 | 0 | 2021-04-03 | -6.3 | 24.3 | 0 | 2020-04-03 | 3.8 | 14.2 | 0 | 2019-04-03 | 4.1 | 13.9 | 0 | 2018-04-03 | -0.7 | 18.7 | 0 | 2017-04-03 | -0.4 | 18.4 | 0 | 2016-04-03 | -5.6 | 23.6 | 0 | 18.46 | 0
2025-04-03 | 0.1 | 17.9 | 0 | 2024-04-03 | 4.3 | 13.7 | 0 | 2023-04-03 | -2.6 | 20.6 | 0 | 2022-04-03 | -0.9 | 18.9 | 0 | 2021-04-03 | -6.9 | 24.9 | 0 | 2020-04-03 | 3.8 | 14.2 | 0 | 2019-04-03 | 3.8 | 14.2 | 0 | 2018-04-03 | -0.1 | 18.1 | 0 | 2017-04-03 | 0 | 18 | 0 | 2016-04-03 | -6.3 | 24.3 | 0 | 18.48 | 0
2025-04-03 | 0.4 | 17.6 | 0 | 2024-04-03 | 4.1 | 13.9 | 0 | 2023-04-03 | -2.7 | 20.7 | 0 | 2022-04-03 | -0.7 | 18.7 | 0 | 2021-04-03 | -6.8 | 24.8 | 0 | 2020-04-03 | 4 | 14 | 0 | 2019-04-03 | 3.5 | 14.5 | 0 | 2018-04-03 | -0.5 | 18.5 | 0 | 2017-04-03 | -0.9 | 18.9 | 0 | 2016-04-03 | -7.5 | 25.5 | 0 | 18.71 | 0
2025-04-03 | 0.9 | 17.1 | 0 | 2024-04-03 | 4.2 | 13.8 | 0 | 2023-04-03 | -2.6 | 20.6 | 0 | 2022-04-03 | -1.3 | 19.3 | 0 | 2021-04-03 | -7.5 | 25.5 | 0 | 2020-04-03 | 4.5 | 13.5 | 0 | 2019-04-03 | 3.5 | 14.5 | 0 | 2018-04-03 | -1.9 | 19.9 | 0 | 2017-04-03 | -1 | 19 | 0 | 2016-04-03 | -8.6 | 26.6 | 0 | 18.98 | 0
2025-04-03 | 4.2 | 13.8 | 0 | 2024-04-03 | 4 | 14 | 0 | 2023-04-03 | -3 | 21 | 0 | 2022-04-03 | -1.1 | 19.1 | 0 | 2021-04-03 | -6.7 | 24.7 | 0 | 2020-04-03 | 4.6 | 13.4 | 0 | 2019-04-03 | 3.1 | 14.9 | 0 | 2018-04-03 | -1.5 | 19.5 | 0 | 2017-04-03 | -1 | 19 | 0 | 2016-04-03 | -9.2 | 27.2 | 0 | 18.66 | 0
2025-04-03 | 5.2 | 12.8 | 0 | 2024-04-03 | 4.3 | 13.7 | 0 | 2023-04-03 | -3 | 21 | 0 | 2022-04-03 | 0.4 | 17.6 | 0 | 2021-04-03 | -3.8 | 21.8 | 0 | 2020-04-03 | 4.8 | 13.2 | 0 | 2019-04-03 | 4 | 14 | 0 | 2018-04-03 | 0.3 | 17.7 | 0 | 2017-04-03 | 0.3 | 17.7 | 0 | 2016-04-03 | -9.5 | 27.5 | 0 | 17.7 | 0
2025-04-03 | 6.6 | 11.4 | 0 | 2024-04-03 | 4.8 | 13.2 | 0 | 2023-04-03 | 0 | 18 | 0 | 2022-04-03 | 2.4 | 15.6 | 0 | 2021-04-03 | -0.5 | 18.5 | 0 | 2020-04-03 | 5.5 | 12.5 | 0 | 2019-04-03 | 4.8 | 13.2 | 0 | 2018-04-03 | 1.5 | 16.5 | 0 | 2017-04-03 | 1.3 | 16.7 | 0 | 2016-04-03 | -9.1 | 27.1 | 0 | 16.27 | 0
2025-04-03 | 8.2 | 9.8 | 0 | 2024-04-03 | 5 | 13 | 0 | 2023-04-03 | 1 | 17 | 0 | 2022-04-03 | 3.5 | 14.5 | 0 | 2021-04-03 | 1.7 | 16.3 | 0 | 2020-04-03 | 6.3 | 11.7 | 0 | 2019-04-03 | 6.1 | 11.9 | 0 | 2018-04-03 | 2.1 | 15.9 | 0 | 2017-04-03 | 2.7 | 15.3 | 0 | 2016-04-03 | -8.5 | 26.5 | 0 | 15.19 | 0
2025-04-03 | 9 | 9 | 0 | 2024-04-03 | 5.8 | 12.2 | 0 | 2023-04-03 | 3 | 15 | 0 | 2022-04-03 | 4.8 | 13.2 | 0 | 2021-04-03 | 4.5 | 13.5 | 0 | 2020-04-03 | 7 | 11 | 0 | 2019-04-03 | 5.9 | 12.1 | 0 | 2018-04-03 | 2.9 | 15.1 | 0 | 2017-04-03 | 3.3 | 14.7 | 0 | 2016-04-03 | -7.6 | 25.6 | 0 | 14.14 | 0
2025-04-03 | 11.3 | 6.7 | 0 | 2024-04-03 | 5.2 | 12.8 | 0 | 2023-04-03 | 4.3 | 13.7 | 0 | 2022-04-03 | 6.2 | 11.8 | 0 | 2021-04-03 | 5.8 | 12.2 | 0 | 2020-04-03 | 7.8 | 10.2 | 0 | 2019-04-03 | 4.7 | 13.3 | 0 | 2018-04-03 | 4.6 | 13.4 | 0 | 2017-04-03 | 5.3 | 12.7 | 0 | 2016-04-03 | -7.1 | 25.1 | 0 | 13.19 | 0
2025-04-03 | 15.4 | 2.6 | 0 | 2024-04-03 | 4.2 | 13.8 | 0 | 2023-04-03 | 4.9 | 13.1 | 0 | 2022-04-03 | 7.5 | 10.5 | 0 | 2021-04-03 | 7.8 | 10.2 | 0 | 2020-04-03 | 8 | 10 | 0 | 2019-04-03 | 6.5 | 11.5 | 0 | 2018-04-03 | 5.8 | 12.2 | 0 | 2017-04-03 | 5.8 | 12.2 | 0 | 2016-04-03 | -6.3 | 24.3 | 0 | 12.04 | 0
2025-04-03 | 17.1 | 0.9 | 0 | 2024-04-03 | 4.2 | 13.8 | 0 | 2023-04-03 | 6.7 | 11.3 | 0 | 2022-04-03 | 7 | 11 | 0 | 2021-04-03 | 8.9 | 9.1 | 0 | 2020-04-03 | 9.2 | 8.8 | 0 | 2019-04-03 | 6.1 | 11.9 | 0 | 2018-04-03 | 6.7 | 11.3 | 0 | 2017-04-03 | 6.8 | 11.2 | 0 | 2016-04-03 | -6.7 | 24.7 | 0 | 11.4 | 0
2025-04-03 | 18.9 | 0 | 0.9 | 2024-04-03 | 3.9 | 14.1 | 0 | 2023-04-03 | 7.1 | 10.9 | 0 | 2022-04-03 | 5.7 | 12.3 | 0 | 2021-04-03 | 9.5 | 8.5 | 0 | 2020-04-03 | 9.3 | 8.7 | 0 | 2019-04-03 | 5.2 | 12.8 | 0 | 2018-04-03 | 5.5 | 12.5 | 0 | 2017-04-03 | 7.7 | 10.3 | 0 | 2016-04-03 | -5.6 | 23.6 | 0 | 11.37 | 0.09
2025-04-03 | 18.4 | 0 | 0.4 | 2024-04-03 | 3 | 15 | 0 | 2023-04-03 | 7.3 | 10.7 | 0 | 2022-04-03 | 5 | 13 | 0 | 2021-04-03 | 9.6 | 8.4 | 0 | 2020-04-03 | 9.4 | 8.6 | 0 | 2019-04-03 | 5.1 | 12.9 | 0 | 2018-04-03 | 5.2 | 12.8 | 0 | 2017-04-03 | 8.2 | 9.8 | 0 | 2016-04-03 | -6.3 | 24.3 | 0 | 11.55 | 0.04
2025-04-03 | 18.5 | 0 | 0.5 | 2024-04-03 | 2.6 | 15.4 | 0 | 2023-04-03 | 7.6 | 10.4 | 0 | 2022-04-03 | 4.9 | 13.1 | 0 | 2021-04-03 | 9.9 | 8.1 | 0 | 2020-04-03 | 9.8 | 8.2 | 0 | 2019-04-03 | 4.5 | 13.5 | 0 | 2018-04-03 | 4.9 | 13.1 | 0 | 2017-04-03 | 8.4 | 9.6 | 0 | 2016-04-03 | -5 | 23 | 0 | 11.44 | 0.05
2025-04-03 | 16.4 | 1.6 | 0 | 2024-04-03 | 1.6 | 16.4 | 0 | 2023-04-03 | 8.2 | 9.8 | 0 | 2022-04-03 | 3.1 | 14.9 | 0 | 2021-04-03 | 8.8 | 9.2 | 0 | 2020-04-03 | 9.6 | 8.4 | 0 | 2019-04-03 | 4.1 | 13.9 | 0 | 2018-04-03 | 4.3 | 13.7 | 0 | 2017-04-03 | 7.1 | 10.9 | 0 | 2016-04-03 | -5.6 | 23.6 | 0 | 12.24 | 0
2025-04-03 | 11.8 | 6.2 | 0 | 2024-04-03 | 0.4 | 17.6 | 0 | 2023-04-03 | 7.5 | 10.5 | 0 | 2022-04-03 | 2.9 | 15.1 | 0 | 2021-04-03 | 6.7 | 11.3 | 0 | 2020-04-03 | 8.7 | 9.3 | 0 | 2019-04-03 | 3 | 15 | 0 | 2018-04-03 | 3.7 | 14.3 | 0 | 2017-04-03 | 5.3 | 12.7 | 0 | 2016-04-03 | -6.5 | 24.5 | 0 | 13.65 | 0
2025-04-03 | 10.4 | 7.6 | 0 | 2024-04-03 | 0.4 | 17.6 | 0 | 2023-04-03 | 6.7 | 11.3 | 0 | 2022-04-03 | 2.5 | 15.5 | 0 | 2021-04-03 | 4.8 | 13.2 | 0 | 2020-04-03 | 8.1 | 9.9 | 0 | 2019-04-03 | 1.9 | 16.1 | 0 | 2018-04-03 | 3.2 | 14.8 | 0 | 2017-04-03 | 4.7 | 13.3 | 0 | 2016-04-03 | -7 | 25 | 0 | 14.43 | 0
2025-04-03 | 9.2 | 8.8 | 0 | 2024-04-03 | 0.3 | 17.7 | 0 | 2023-04-03 | 6.1 | 11.9 | 0 | 2022-04-03 | 2.3 | 15.7 | 0 | 2021-04-03 | 4.8 | 13.2 | 0 | 2020-04-03 | 7.9 | 10.1 | 0 | 2019-04-03 | 1 | 17 | 0 | 2018-04-03 | 3.2 | 14.8 | 0 | 2017-04-03 | 5 | 13 | 0 | 2016-04-03 | -7.3 | 25.3 | 0 | 14.75 | 0
2025-04-03 | 8 | 10 | 0 | 2024-04-03 | 0.4 | 17.6 | 0 | 2023-04-03 | 4.9 | 13.1 | 0 | 2022-04-03 | 2 | 16 | 0 | 2021-04-03 | 4.5 | 13.5 | 0 | 2020-04-03 | 8.1 | 9.9 | 0 | 2019-04-03 | 0.2 | 17.8 | 0 | 2018-04-03 | 2.6 | 15.4 | 0 | 2017-04-03 | 4.7 | 13.3 | 0 | 2016-04-03 | -7.7 | 25.7 | 0 | 15.23 | 0
2025-04-03 | 6.8 | 11.2 | 0 | 2024-04-03 | 0.5 | 17.5 | 0 | 2023-04-03 | 4.5 | 13.5 | 0 | 2022-04-03 | 2.5 | 15.5 | 0 | 2021-04-03 | 4.2 | 13.8 | 0 | 2020-04-03 | 7.8 | 10.2 | 0 | 2019-04-03 | -0.4 | 18.4 | 0 | 2018-04-03 | 0.7 | 17.3 | 0 | 2017-04-03 | 4.4 | 13.6 | 0 | 2016-04-03 | -8 | 26 | 0 | 15.7 | 0
2025-04-03 | 4.3 | 13.7 | 0 | 2024-04-03 | 0.4 | 17.6 | 0 | 2023-04-03 | 4.3 | 13.7 | 0 | 2022-04-03 | 1.2 | 16.8 | 0 | 2021-04-03 | 3.7 | 14.3 | 0 | 2020-04-03 | 7.5 | 10.5 | 0 | 2019-04-03 | -0.7 | 18.7 | 0 | 2018-04-03 | -0.1 | 18.1 | 0 | 2017-04-03 | 3.5 | 14.5 | 0 | 2016-04-03 | -8.6 | 26.6 | 0 | 16.45 | 0
2025-04-04 | 4.3 | 13.7 | 0 | 2024-04-04 | 0.2 | 17.8 | 0 | 2023-04-04 | 4.3 | 13.7 | 0 | 2022-04-04 | 0.6 | 17.4 | 0 | 2021-04-04 | 3 | 15 | 0 | 2020-04-04 | 5.9 | 12.1 | 0 | 2019-04-04 | -1.1 | 19.1 | 0 | 2018-04-04 | -0.7 | 18.7 | 0 | 2017-04-04 | 3 | 15 | 0 | 2016-04-04 | -8.7 | 26.7 | 0 | 16.92 | 0
2025-04-04 | 3.5 | 14.5 | 0 | 2024-04-04 | 0.4 | 17.6 | 0 | 2023-04-04 | 2.7 | 15.3 | 0 | 2022-04-04 | 0.6 | 17.4 | 0 | 2021-04-04 | 3 | 15 | 0 | 2020-04-04 | 3.9 | 14.1 | 0 | 2019-04-04 | -1.6 | 19.6 | 0 | 2018-04-04 | -0.7 | 18.7 | 0 | 2017-04-04 | 1.5 | 16.5 | 0 | 2016-04-04 | -8.6 | 26.6 | 0 | 17.53 | 0
2025-04-04 | 3.4 | 14.6 | 0 | 2024-04-04 | 0.3 | 17.7 | 0 | 2023-04-04 | 3 | 15 | 0 | 2022-04-04 | 0.5 | 17.5 | 0 | 2021-04-04 | 2.4 | 15.6 | 0 | 2020-04-04 | 4.3 | 13.7 | 0 | 2019-04-04 | -2 | 20 | 0 | 2018-04-04 | -0.5 | 18.5 | 0 | 2017-04-04 | 1.4 | 16.6 | 0 | 2016-04-04 | -8.6 | 26.6 | 0 | 17.58 | 0
2025-04-04 | 1 | 17 | 0 | 2024-04-04 | 0.1 | 17.9 | 0 | 2023-04-04 | 2.3 | 15.7 | 0 | 2022-04-04 | 0.8 | 17.2 | 0 | 2021-04-04 | 1.6 | 16.4 | 0 | 2020-04-04 | 4.4 | 13.6 | 0 | 2019-04-04 | -2.3 | 20.3 | 0 | 2018-04-04 | -0.1 | 18.1 | 0 | 2017-04-04 | 1.1 | 16.9 | 0 | 2016-04-04 | -8.6 | 26.6 | 0 | 17.97 | 0
2025-04-04 | 2.2 | 15.8 | 0 | 2024-04-04 | 0 | 18 | 0 | 2023-04-04 | 0.6 | 17.4 | 0 | 2022-04-04 | 0.4 | 17.6 | 0 | 2021-04-04 | 1 | 17 | 0 | 2020-04-04 | 3.2 | 14.8 | 0 | 2019-04-04 | -3 | 21 | 0 | 2018-04-04 | 0 | 18 | 0 | 2017-04-04 | 0.6 | 17.4 | 0 | 2016-04-04 | -8.7 | 26.7 | 0 | 18.37 | 0
2025-04-04 | 1.1 | 16.9 | 0 | 2024-04-04 | -0.5 | 18.5 | 0 | 2023-04-04 | -0.1 | 18.1 | 0 | 2022-04-04 | 0.1 | 17.9 | 0 | 2021-04-04 | 0.2 | 17.8 | 0 | 2020-04-04 | 3.1 | 14.9 | 0 | 2019-04-04 | -3.1 | 21.1 | 0 | 2018-04-04 | 0.1 | 17.9 | 0 | 2017-04-04 | 0.5 | 17.5 | 0 | 2016-04-04 | -8.9 | 26.9 | 0 | 18.75 | 0
2025-04-04 | 1.4 | 16.6 | 0 | 2024-04-04 | -1.1 | 19.1 | 0 | 2023-04-04 | 0.6 | 17.4 | 0 | 2022-04-04 | -0.1 | 18.1 | 0 | 2021-04-04 | 0.2 | 17.8 | 0 | 2020-04-04 | 3.6 | 14.4 | 0 | 2019-04-04 | -3.2 | 21.2 | 0 | 2018-04-04 | 0.1 | 17.9 | 0 | 2017-04-04 | 0.6 | 17.4 | 0 | 2016-04-04 | -9 | 27 | 0 | 18.69 | 0
2025-04-04 | 2.6 | 15.4 | 0 | 2024-04-04 | -1.3 | 19.3 | 0 | 2023-04-04 | 1.2 | 16.8 | 0 | 2022-04-04 | 0.4 | 17.6 | 0 | 2021-04-04 | 2.8 | 15.2 | 0 | 2020-04-04 | 5.4 | 12.6 | 0 | 2019-04-04 | -2.9 | 20.9 | 0 | 2018-04-04 | 0.1 | 17.9 | 0 | 2017-04-04 | 0.9 | 17.1 | 0 | 2016-04-04 | -8.7 | 26.7 | 0 | 17.95 | 0
2025-04-04 | 3.2 | 14.8 | 0 | 2024-04-04 | -1.3 | 19.3 | 0 | 2023-04-04 | 2.7 | 15.3 | 0 | 2022-04-04 | 2.8 | 15.2 | 0 | 2021-04-04 | 5.5 | 12.5 | 0 | 2020-04-04 | 6.7 | 11.3 | 0 | 2019-04-04 | -2.6 | 20.6 | 0 | 2018-04-04 | 0.1 | 17.9 | 0 | 2017-04-04 | 1.9 | 16.1 | 0 | 2016-04-04 | -7.2 | 25.2 | 0 | 16.82 | 0
2025-04-04 | 4.3 | 13.7 | 0 | 2024-04-04 | -1.2 | 19.2 | 0 | 2023-04-04 | 3.7 | 14.3 | 0 | 2022-04-04 | 5.3 | 12.7 | 0 | 2021-04-04 | 6.8 | 11.2 | 0 | 2020-04-04 | 8.3 | 9.7 | 0 | 2019-04-04 | -1.8 | 19.8 | 0 | 2018-04-04 | 0.1 | 17.9 | 0 | 2017-04-04 | 3.2 | 14.8 | 0 | 2016-04-04 | -6.3 | 24.3 | 0 | 15.76 | 0
2025-04-04 | 5.4 | 12.6 | 0 | 2024-04-04 | -1.2 | 19.2 | 0 | 2023-04-04 | 4.5 | 13.5 | 0 | 2022-04-04 | 7.9 | 10.1 | 0 | 2021-04-04 | 9.1 | 8.9 | 0 | 2020-04-04 | 9.4 | 8.6 | 0 | 2019-04-04 | -1.6 | 19.6 | 0 | 2018-04-04 | 0.4 | 17.6 | 0 | 2017-04-04 | 3.3 | 14.7 | 0 | 2016-04-04 | -5.9 | 23.9 | 0 | 14.87 | 0
2025-04-04 | 7 | 11 | 0 | 2024-04-04 | -1.4 | 19.4 | 0 | 2023-04-04 | 5.8 | 12.2 | 0 | 2022-04-04 | 8.9 | 9.1 | 0 | 2021-04-04 | 10.2 | 7.8 | 0 | 2020-04-04 | 11.1 | 6.9 | 0 | 2019-04-04 | -1.6 | 19.6 | 0 | 2018-04-04 | 1.8 | 16.2 | 0 | 2017-04-04 | 3.2 | 14.8 | 0 | 2016-04-04 | -5.6 | 23.6 | 0 | 14.06 | 0
2025-04-04 | 8.2 | 9.8 | 0 | 2024-04-04 | -0.9 | 18.9 | 0 | 2023-04-04 | 7 | 11 | 0 | 2022-04-04 | 8.7 | 9.3 | 0 | 2021-04-04 | 10.9 | 7.1 | 0 | 2020-04-04 | 11.7 | 6.3 | 0 | 2019-04-04 | -1.3 | 19.3 | 0 | 2018-04-04 | 5.2 | 12.8 | 0 | 2017-04-04 | 3.2 | 14.8 | 0 | 2016-04-04 | -4.4 | 22.4 | 0 | 13.17 | 0
2025-04-04 | 8.7 | 9.3 | 0 | 2024-04-04 | -0.2 | 18.2 | 0 | 2023-04-04 | 7.1 | 10.9 | 0 | 2022-04-04 | 8.8 | 9.2 | 0 | 2021-04-04 | 10.7 | 7.3 | 0 | 2020-04-04 | 13.3 | 4.7 | 0 | 2019-04-04 | -0.1 | 18.1 | 0 | 2018-04-04 | 5.7 | 12.3 | 0 | 2017-04-04 | 3.4 | 14.6 | 0 | 2016-04-04 | -2.9 | 20.9 | 0 | 12.55 | 0
2025-04-04 | 9.9 | 8.1 | 0 | 2024-04-04 | -0.2 | 18.2 | 0 | 2023-04-04 | 7.5 | 10.5 | 0 | 2022-04-04 | 9.3 | 8.7 | 0 | 2021-04-04 | 12.5 | 5.5 | 0 | 2020-04-04 | 13.9 | 4.1 | 0 | 2019-04-04 | 0.7 | 17.3 | 0 | 2018-04-04 | 5.2 | 12.8 | 0 | 2017-04-04 | 3.6 | 14.4 | 0 | 2016-04-04 | -2.1 | 20.1 | 0 | 11.97 | 0
2025-04-04 | 10.4 | 7.6 | 0 | 2024-04-04 | 0 | 18 | 0 | 2023-04-04 | 7.6 | 10.4 | 0 | 2022-04-04 | 9.3 | 8.7 | 0 | 2021-04-04 | 13 | 5 | 0 | 2020-04-04 | 13.6 | 4.4 | 0 | 2019-04-04 | 1.1 | 16.9 | 0 | 2018-04-04 | 2.8 | 15.2 | 0 | 2017-04-04 | 3.5 | 14.5 | 0 | 2016-04-04 | -2.3 | 20.3 | 0 | 12.1 | 0
2025-04-04 | 10.7 | 7.3 | 0 | 2024-04-04 | 0.2 | 17.8 | 0 | 2023-04-04 | 8.1 | 9.9 | 0 | 2022-04-04 | 9.4 | 8.6 | 0 | 2021-04-04 | 13.3 | 4.7 | 0 | 2020-04-04 | 13.8 | 4.2 | 0 | 2019-04-04 | 1.6 | 16.4 | 0 | 2018-04-04 | 2.3 | 15.7 | 0 | 2017-04-04 | 3.5 | 14.5 | 0 | 2016-04-04 | -2 | 20 | 0 | 11.91 | 0
2025-04-04 | 10 | 8 | 0 | 2024-04-04 | 0 | 18 | 0 | 2023-04-04 | 7.5 | 10.5 | 0 | 2022-04-04 | 9.2 | 8.8 | 0 | 2021-04-04 | 13.1 | 4.9 | 0 | 2020-04-04 | 13.3 | 4.7 | 0 | 2019-04-04 | 1.4 | 16.6 | 0 | 2018-04-04 | 0 | 18 | 0 | 2017-04-04 | 3.5 | 14.5 | 0 | 2016-04-04 | -2.5 | 20.5 | 0 | 12.45 | 0
2025-04-04 | 8.6 | 9.4 | 0 | 2024-04-04 | 0.5 | 17.5 | 0 | 2023-04-04 | 6.2 | 11.8 | 0 | 2022-04-04 | 8.1 | 9.9 | 0 | 2021-04-04 | 12.1 | 5.9 | 0 | 2020-04-04 | 12.8 | 5.2 | 0 | 2019-04-04 | 1.1 | 16.9 | 0 | 2018-04-04 | -1.6 | 19.6 | 0 | 2017-04-04 | 3.5 | 14.5 | 0 | 2016-04-04 | -3.1 | 21.1 | 0 | 13.18 | 0
2025-04-04 | 7 | 11 | 0 | 2024-04-04 | 0.4 | 17.6 | 0 | 2023-04-04 | 3 | 15 | 0 | 2022-04-04 | 6.3 | 11.7 | 0 | 2021-04-04 | 10.4 | 7.6 | 0 | 2020-04-04 | 10 | 8 | 0 | 2019-04-04 | 0.1 | 17.9 | 0 | 2018-04-04 | -4.7 | 22.7 | 0 | 2017-04-04 | 3.2 | 14.8 | 0 | 2016-04-04 | -4.4 | 22.4 | 0 | 14.87 | 0
2025-04-04 | 6.6 | 11.4 | 0 | 2024-04-04 | 0.4 | 17.6 | 0 | 2023-04-04 | 3 | 15 | 0 | 2022-04-04 | 6.2 | 11.8 | 0 | 2021-04-04 | 8.5 | 9.5 | 0 | 2020-04-04 | 9.8 | 8.2 | 0 | 2019-04-04 | -1.3 | 19.3 | 0 | 2018-04-04 | -5.8 | 23.8 | 0 | 2017-04-04 | 3.1 | 14.9 | 0 | 2016-04-04 | -5.3 | 23.3 | 0 | 15.48 | 0
2025-04-04 | 5.5 | 12.5 | 0 | 2024-04-04 | 0.2 | 17.8 | 0 | 2023-04-04 | 2.5 | 15.5 | 0 | 2022-04-04 | 4.5 | 13.5 | 0 | 2021-04-04 | 9.4 | 8.6 | 0 | 2020-04-04 | 9.6 | 8.4 | 0 | 2019-04-04 | -1.2 | 19.2 | 0 | 2018-04-04 | -7.2 | 25.2 | 0 | 2017-04-04 | 2.9 | 15.1 | 0 | 2016-04-04 | -4.9 | 22.9 | 0 | 15.87 | 0
2025-04-04 | 3.6 | 14.4 | 0 | 2024-04-04 | -0.1 | 18.1 | 0 | 2023-04-04 | 1.8 | 16.2 | 0 | 2022-04-04 | 5 | 13 | 0 | 2021-04-04 | 8.6 | 9.4 | 0 | 2020-04-04 | 9.7 | 8.3 | 0 | 2019-04-04 | -2.1 | 20.1 | 0 | 2018-04-04 | -7.8 | 25.8 | 0 | 2017-04-04 | 3.7 | 14.3 | 0 | 2016-04-04 | -5.3 | 23.3 | 0 | 16.29 | 0
2025-04-04 | 2.9 | 15.1 | 0 | 2024-04-04 | 0 | 18 | 0 | 2023-04-04 | 0.9 | 17.1 | 0 | 2022-04-04 | 3.6 | 14.4 | 0 | 2021-04-04 | 7.3 | 10.7 | 0 | 2020-04-04 | 9.3 | 8.7 | 0 | 2019-04-04 | -4.1 | 22.1 | 0 | 2018-04-04 | -8.2 | 26.2 | 0 | 2017-04-04 | 4.8 | 13.2 | 0 | 2016-04-04 | -6.1 | 24.1 | 0 | 16.96 | 0
2025-04-05 | 3.8 | 14.2 | 0 | 2024-04-05 | 0.1 | 17.9 | 0 | 2023-04-05 | 0.6 | 17.4 | 0 | 2022-04-05 | 3.3 | 14.7 | 0 | 2021-04-05 | 6.5 | 11.5 | 0 | 2020-04-05 | 9.3 | 8.7 | 0 | 2019-04-05 | -4.4 | 22.4 | 0 | 2018-04-05 | -8.9 | 26.9 | 0 | 2017-04-05 | 5 | 13 | 0 | 2016-04-05 | -6.5 | 24.5 | 0 | 17.12 | 0
2025-04-05 | 3 | 15 | 0 | 2024-04-05 | 0 | 18 | 0 | 2023-04-05 | 0.7 | 17.3 | 0 | 2022-04-05 | 3.1 | 14.9 | 0 | 2021-04-05 | 5.3 | 12.7 | 0 | 2020-04-05 | 9 | 9 | 0 | 2019-04-05 | -5.4 | 23.4 | 0 | 2018-04-05 | -9.3 | 27.3 | 0 | 2017-04-05 | 2.9 | 15.1 | 0 | 2016-04-05 | -7.5 | 25.5 | 0 | 17.82 | 0
2025-04-05 | 3.4 | 14.6 | 0 | 2024-04-05 | 0 | 18 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 2.5 | 15.5 | 0 | 2021-04-05 | 4.2 | 13.8 | 0 | 2020-04-05 | 8.6 | 9.4 | 0 | 2019-04-05 | -6.3 | 24.3 | 0 | 2018-04-05 | -9.5 | 27.5 | 0 | 2017-04-05 | 2.8 | 15.2 | 0 | 2016-04-05 | -8 | 26 | 0 | 18.23 | 0
2025-04-05 | 3.2 | 14.8 | 0 | 2024-04-05 | 0 | 18 | 0 | 2023-04-05 | -0.6 | 18.6 | 0 | 2022-04-05 | 2.4 | 15.6 | 0 | 2021-04-05 | 3.4 | 14.6 | 0 | 2020-04-05 | 8 | 10 | 0 | 2019-04-05 | -5.5 | 23.5 | 0 | 2018-04-05 | -10.1 | 28.1 | 0 | 2017-04-05 | 2.9 | 15.1 | 0 | 2016-04-05 | -8.5 | 26.5 | 0 | 18.48 | 0
2025-04-05 | 3.3 | 14.7 | 0 | 2024-04-05 | 0.1 | 17.9 | 0 | 2023-04-05 | -1.6 | 19.6 | 0 | 2022-04-05 | 2.4 | 15.6 | 0 | 2021-04-05 | 2.9 | 15.1 | 0 | 2020-04-05 | 7.4 | 10.6 | 0 | 2019-04-05 | -6.5 | 24.5 | 0 | 2018-04-05 | -10.6 | 28.6 | 0 | 2017-04-05 | 2.7 | 15.3 | 0 | 2016-04-05 | -9.5 | 27.5 | 0 | 18.94 | 0
2025-04-05 | 2.8 | 15.2 | 0 | 2024-04-05 | 0.1 | 17.9 | 0 | 2023-04-05 | -2.1 | 20.1 | 0 | 2022-04-05 | 0.5 | 17.5 | 0 | 2021-04-05 | 1.9 | 16.1 | 0 | 2020-04-05 | 7.4 | 10.6 | 0 | 2019-04-05 | -6.2 | 24.2 | 0 | 2018-04-05 | -11.1 | 29.1 | 0 | 2017-04-05 | 2.7 | 15.3 | 0 | 2016-04-05 | -10.5 | 28.5 | 0 | 19.45 | 0
2025-04-05 | 2.3 | 15.7 | 0 | 2024-04-05 | 0.2 | 17.8 | 0 | 2023-04-05 | -2.2 | 20.2 | 0 | 2022-04-05 | 0.6 | 17.4 | 0 | 2021-04-05 | 2.1 | 15.9 | 0 | 2020-04-05 | 7.1 | 10.9 | 0 | 2019-04-05 | -6.4 | 24.4 | 0 | 2018-04-05 | -11.5 | 29.5 | 0 | 2017-04-05 | 2.5 | 15.5 | 0 | 2016-04-05 | -9.7 | 27.7 | 0 | 19.5 | 0
2025-04-05 | 2.2 | 15.8 | 0 | 2024-04-05 | 0.6 | 17.4 | 0 | 2023-04-05 | -2.5 | 20.5 | 0 | 2022-04-05 | 1.5 | 16.5 | 0 | 2021-04-05 | 3.7 | 14.3 | 0 | 2020-04-05 | 6.9 | 11.1 | 0 | 2019-04-05 | -4 | 22 | 0 | 2018-04-05 | -11 | 29 | 0 | 2017-04-05 | 2.5 | 15.5 | 0 | 2016-04-05 | -7.8 | 25.8 | 0 | 18.79 | 0
2025-04-05 | 2.3 | 15.7 | 0 | 2024-04-05 | 1.1 | 16.9 | 0 | 2023-04-05 | -2.6 | 20.6 | 0 | 2022-04-05 | 4.5 | 13.5 | 0 | 2021-04-05 | 6 | 12 | 0 | 2020-04-05 | 7.5 | 10.5 | 0 | 2019-04-05 | -1.8 | 19.8 | 0 | 2018-04-05 | -10.2 | 28.2 | 0 | 2017-04-05 | 2.9 | 15.1 | 0 | 2016-04-05 | -6.2 | 24.2 | 0 | 17.65 | 0
2025-04-05 | 2 | 16 | 0 | 2024-04-05 | 2.1 | 15.9 | 0 | 2023-04-05 | -2.8 | 20.8 | 0 | 2022-04-05 | 7.5 | 10.5 | 0 | 2021-04-05 | 7.8 | 10.2 | 0 | 2020-04-05 | 7.9 | 10.1 | 0 | 2019-04-05 | -0.6 | 18.6 | 0 | 2018-04-05 | -9.3 | 27.3 | 0 | 2017-04-05 | 4.2 | 13.8 | 0 | 2016-04-05 | -5.5 | 23.5 | 0 | 16.67 | 0
2025-04-05 | 1.6 | 16.4 | 0 | 2024-04-05 | 2.5 | 15.5 | 0 | 2023-04-05 | -2.4 | 20.4 | 0 | 2022-04-05 | 8.9 | 9.1 | 0 | 2021-04-05 | 8.9 | 9.1 | 0 | 2020-04-05 | 7.8 | 10.2 | 0 | 2019-04-05 | 0.1 | 17.9 | 0 | 2018-04-05 | -8.3 | 26.3 | 0 | 2017-04-05 | 4.9 | 13.1 | 0 | 2016-04-05 | -4.4 | 22.4 | 0 | 16.04 | 0
2025-04-05 | 1.4 | 16.6 | 0 | 2024-04-05 | 2.9 | 15.1 | 0 | 2023-04-05 | -2.1 | 20.1 | 0 | 2022-04-05 | 10.3 | 7.7 | 0 | 2021-04-05 | 9.9 | 8.1 | 0 | 2020-04-05 | 7.9 | 10.1 | 0 | 2019-04-05 | 0.9 | 17.1 | 0 | 2018-04-05 | -6.7 | 24.7 | 0 | 2017-04-05 | 5.4 | 12.6 | 0 | 2016-04-05 | -3.2 | 21.2 | 0 | 15.33 | 0
2025-04-05 | 2 | 16 | 0 | 2024-04-05 | 3.3 | 14.7 | 0 | 2023-04-05 | -1.4 | 19.4 | 0 | 2022-04-05 | 10.5 | 7.5 | 0 | 2021-04-05 | 10.8 | 7.2 | 0 | 2020-04-05 | 7.8 | 10.2 | 0 | 2019-04-05 | 1.5 | 16.5 | 0 | 2018-04-05 | -5.8 | 23.8 | 0 | 2017-04-05 | 5.9 | 12.1 | 0 | 2016-04-05 | -2.8 | 20.8 | 0 | 14.82 | 0
2025-04-05 | 2.5 | 15.5 | 0 | 2024-04-05 | 4.2 | 13.8 | 0 | 2023-04-05 | -0.7 | 18.7 | 0 | 2022-04-05 | 11.6 | 6.4 | 0 | 2021-04-05 | 12.1 | 5.9 | 0 | 2020-04-05 | 8.3 | 9.7 | 0 | 2019-04-05 | 2.3 | 15.7 | 0 | 2018-04-05 | -4.6 | 22.6 | 0 | 2017-04-05 | 7.4 | 10.6 | 0 | 2016-04-05 | -1 | 19 | 0 | 13.79 | 0
2025-04-05 | 3.7 | 14.3 | 0 | 2024-04-05 | 5.2 | 12.8 | 0 | 2023-04-05 | -0.5 | 18.5 | 0 | 2022-04-05 | 12.3 | 5.7 | 0 | 2021-04-05 | 12.4 | 5.6 | 0 | 2020-04-05 | 9.9 | 8.1 | 0 | 2019-04-05 | 2.3 | 15.7 | 0 | 2018-04-05 | -3.5 | 21.5 | 0 | 2017-04-05 | 7.3 | 10.7 | 0 | 2016-04-05 | -0.8 | 18.8 | 0 | 13.17 | 0
2025-04-05 | 3.4 | 14.6 | 0 | 2024-04-05 | 3.7 | 14.3 | 0 | 2023-04-05 | -0.1 | 18.1 | 0 | 2022-04-05 | 12 | 6 | 0 | 2021-04-05 | 13.4 | 4.6 | 0 | 2020-04-05 | 9.6 | 8.4 | 0 | 2019-04-05 | 2.5 | 15.5 | 0 | 2018-04-05 | -3.2 | 21.2 | 0 | 2017-04-05 | 7.7 | 10.3 | 0 | 2016-04-05 | -0.5 | 18.5 | 0 | 13.15 | 0
2025-04-05 | 3.6 | 14.4 | 0 | 2024-04-05 | 4.5 | 13.5 | 0 | 2023-04-05 | -0.1 | 18.1 | 0 | 2022-04-05 | 12.7 | 5.3 | 0 | 2021-04-05 | 13.4 | 4.6 | 0 | 2020-04-05 | 9.2 | 8.8 | 0 | 2019-04-05 | 2.9 | 15.1 | 0 | 2018-04-05 | -1.9 | 19.9 | 0 | 2017-04-05 | 8 | 10 | 0 | 2016-04-05 | -0.5 | 18.5 | 0 | 12.82 | 0
2025-04-05 | 4.3 | 13.7 | 0 | 2024-04-05 | 4.9 | 13.1 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 11.9 | 6.1 | 0 | 2021-04-05 | 13.2 | 4.8 | 0 | 2020-04-05 | 9.4 | 8.6 | 0 | 2019-04-05 | 2.5 | 15.5 | 0 | 2018-04-05 | -1.9 | 19.9 | 0 | 2017-04-05 | 7.4 | 10.6 | 0 | 2016-04-05 | -0.5 | 18.5 | 0 | 12.88 | 0
2025-04-05 | 4.3 | 13.7 | 0 | 2024-04-05 | 5.1 | 12.9 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 11 | 7 | 0 | 2021-04-05 | 12 | 6 | 0 | 2020-04-05 | 8.1 | 9.9 | 0 | 2019-04-05 | 1 | 17 | 0 | 2018-04-05 | -2.8 | 20.8 | 0 | 2017-04-05 | 6.7 | 11.3 | 0 | 2016-04-05 | -1.3 | 19.3 | 0 | 13.59 | 0
2025-04-05 | 3.7 | 14.3 | 0 | 2024-04-05 | 4.6 | 13.4 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 8.3 | 9.7 | 0 | 2021-04-05 | 10.1 | 7.9 | 0 | 2020-04-05 | 6.4 | 11.6 | 0 | 2019-04-05 | 0 | 18 | 0 | 2018-04-05 | -3 | 21 | 0 | 2017-04-05 | 4.8 | 13.2 | 0 | 2016-04-05 | -3.2 | 21.2 | 0 | 14.83 | 0
2025-04-05 | 3.5 | 14.5 | 0 | 2024-04-05 | 4.3 | 13.7 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 7.7 | 10.3 | 0 | 2021-04-05 | 9 | 9 | 0 | 2020-04-05 | 4.8 | 13.2 | 0 | 2019-04-05 | 0.1 | 17.9 | 0 | 2018-04-05 | -4.2 | 22.2 | 0 | 2017-04-05 | 4.4 | 13.6 | 0 | 2016-04-05 | -6 | 24 | 0 | 15.64 | 0
2025-04-05 | 3.8 | 14.2 | 0 | 2024-04-05 | 4.5 | 13.5 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 7.8 | 10.2 | 0 | 2021-04-05 | 6.5 | 11.5 | 0 | 2020-04-05 | 4.1 | 13.9 | 0 | 2019-04-05 | 0 | 18 | 0 | 2018-04-05 | -4.4 | 22.4 | 0 | 2017-04-05 | 3.4 | 14.6 | 0 | 2016-04-05 | -4.9 | 22.9 | 0 | 15.92 | 0
2025-04-05 | 3.8 | 14.2 | 0 | 2024-04-05 | 4.2 | 13.8 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 6.8 | 11.2 | 0 | 2021-04-05 | 4.3 | 13.7 | 0 | 2020-04-05 | 3.7 | 14.3 | 0 | 2019-04-05 | 0.1 | 17.9 | 0 | 2018-04-05 | -4.8 | 22.8 | 0 | 2017-04-05 | 3.4 | 14.6 | 0 | 2016-04-05 | -5.3 | 23.3 | 0 | 16.38 | 0
2025-04-05 | 3.2 | 14.8 | 0 | 2024-04-05 | 4.1 | 13.9 | 0 | 2023-04-05 | 0 | 18 | 0 | 2022-04-05 | 5.8 | 12.2 | 0 | 2021-04-05 | 4.6 | 13.4 | 0 | 2020-04-05 | 1.7 | 16.3 | 0 | 2019-04-05 | 0.2 | 17.8 | 0 | 2018-04-05 | -4.9 | 22.9 | 0 | 2017-04-05 | 3.6 | 14.4 | 0 | 2016-04-05 | -5.1 | 23.1 | 0 | 16.68 | 0
2025-04-06 | 2.4 | 15.6 | 0 | 2024-04-06 | 3.7 | 14.3 | 0 | 2023-04-06 | 0 | 18 | 0 | 2022-04-06 | 3.9 | 14.1 | 0 | 2021-04-06 | 6.3 | 11.7 | 0 | 2020-04-06 | 1.1 | 16.9 | 0 | 2019-04-06 | 0.4 | 17.6 | 0 | 2018-04-06 | -5.5 | 23.5 | 0 | 2017-04-06 | 3.3 | 14.7 | 0 | 2016-04-06 | -5.2 | 23.2 | 0 | 16.96 | 0
2025-04-06 | 2.6 | 15.4 | 0 | 2024-04-06 | 4 | 14 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 3.1 | 14.9 | 0 | 2021-04-06 | 5 | 13 | 0 | 2020-04-06 | -0.2 | 18.2 | 0 | 2019-04-06 | 0.2 | 17.8 | 0 | 2018-04-06 | -5.6 | 23.6 | 0 | 2017-04-06 | 3.3 | 14.7 | 0 | 2016-04-06 | -5.7 | 23.7 | 0 | 17.32 | 0
2025-04-06 | 2.7 | 15.3 | 0 | 2024-04-06 | 3.8 | 14.2 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 3.4 | 14.6 | 0 | 2021-04-06 | 2.6 | 15.4 | 0 | 2020-04-06 | 0.1 | 17.9 | 0 | 2019-04-06 | 0.2 | 17.8 | 0 | 2018-04-06 | -6 | 24 | 0 | 2017-04-06 | 3.1 | 14.9 | 0 | 2016-04-06 | -4.9 | 22.9 | 0 | 17.49 | 0
2025-04-06 | 2.7 | 15.3 | 0 | 2024-04-06 | 3.1 | 14.9 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 4.2 | 13.8 | 0 | 2021-04-06 | -0.1 | 18.1 | 0 | 2020-04-06 | -0.5 | 18.5 | 0 | 2019-04-06 | 0.4 | 17.6 | 0 | 2018-04-06 | -6.5 | 24.5 | 0 | 2017-04-06 | 3.2 | 14.8 | 0 | 2016-04-06 | -4.4 | 22.4 | 0 | 17.78 | 0
2025-04-06 | 2.6 | 15.4 | 0 | 2024-04-06 | 3.6 | 14.4 | 0 | 2023-04-06 | 0.2 | 17.8 | 0 | 2022-04-06 | 3.3 | 14.7 | 0 | 2021-04-06 | -0.3 | 18.3 | 0 | 2020-04-06 | -0.4 | 18.4 | 0 | 2019-04-06 | 0.7 | 17.3 | 0 | 2018-04-06 | -5.7 | 23.7 | 0 | 2017-04-06 | 2.9 | 15.1 | 0 | 2016-04-06 | -4 | 22 | 0 | 17.71 | 0
2025-04-06 | 3.2 | 14.8 | 0 | 2024-04-06 | 2.7 | 15.3 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 3.3 | 14.7 | 0 | 2021-04-06 | 1.5 | 16.5 | 0 | 2020-04-06 | -1.4 | 19.4 | 0 | 2019-04-06 | 0.7 | 17.3 | 0 | 2018-04-06 | -4.4 | 22.4 | 0 | 2017-04-06 | 2.8 | 15.2 | 0 | 2016-04-06 | -4.2 | 22.2 | 0 | 17.57 | 0
2025-04-06 | 3.6 | 14.4 | 0 | 2024-04-06 | 3 | 15 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 2.8 | 15.2 | 0 | 2021-04-06 | -0.8 | 18.8 | 0 | 2020-04-06 | -2 | 20 | 0 | 2019-04-06 | 1 | 17 | 0 | 2018-04-06 | -4.1 | 22.1 | 0 | 2017-04-06 | 2.5 | 15.5 | 0 | 2016-04-06 | -4.1 | 22.1 | 0 | 17.8 | 0
2025-04-06 | 3.6 | 14.4 | 0 | 2024-04-06 | 3.6 | 14.4 | 0 | 2023-04-06 | 0.1 | 17.9 | 0 | 2022-04-06 | 4.4 | 13.6 | 0 | 2021-04-06 | 3.2 | 14.8 | 0 | 2020-04-06 | 0.6 | 17.4 | 0 | 2019-04-06 | 1.4 | 16.6 | 0 | 2018-04-06 | -2.7 | 20.7 | 0 | 2017-04-06 | 2.4 | 15.6 | 0 | 2016-04-06 | -2.8 | 20.8 | 0 | 16.62 | 0
2025-04-06 | 3.8 | 14.2 | 0 | 2024-04-06 | 5.2 | 12.8 | 0 | 2023-04-06 | 0.2 | 17.8 | 0 | 2022-04-06 | 7.2 | 10.8 | 0 | 2021-04-06 | 5.1 | 12.9 | 0 | 2020-04-06 | 4.3 | 13.7 | 0 | 2019-04-06 | 1.6 | 16.4 | 0 | 2018-04-06 | -1 | 19 | 0 | 2017-04-06 | 2.3 | 15.7 | 0 | 2016-04-06 | -0.9 | 18.9 | 0 | 15.22 | 0
2025-04-06 | 4.4 | 13.6 | 0 | 2024-04-06 | 6.2 | 11.8 | 0 | 2023-04-06 | 0.2 | 17.8 | 0 | 2022-04-06 | 9.8 | 8.2 | 0 | 2021-04-06 | 7.1 | 10.9 | 0 | 2020-04-06 | 6.7 | 11.3 | 0 | 2019-04-06 | 2.2 | 15.8 | 0 | 2018-04-06 | 0.4 | 17.6 | 0 | 2017-04-06 | 2.4 | 15.6 | 0 | 2016-04-06 | -0.5 | 18.5 | 0 | 14.11 | 0
2025-04-06 | 4.9 | 13.1 | 0 | 2024-04-06 | 8 | 10 | 0 | 2023-04-06 | 1 | 17 | 0 | 2022-04-06 | 12.4 | 5.6 | 0 | 2021-04-06 | 8.3 | 9.7 | 0 | 2020-04-06 | 9.5 | 8.5 | 0 | 2019-04-06 | 3 | 15 | 0 | 2018-04-06 | 2.1 | 15.9 | 0 | 2017-04-06 | 2.7 | 15.3 | 0 | 2016-04-06 | 1.2 | 16.8 | 0 | 12.69 | 0
2025-04-06 | 6.3 | 11.7 | 0 | 2024-04-06 | 7.8 | 10.2 | 0 | 2023-04-06 | 2.3 | 15.7 | 0 | 2022-04-06 | 13.3 | 4.7 | 0 | 2021-04-06 | 10.3 | 7.7 | 0 | 2020-04-06 | 11.2 | 6.8 | 0 | 2019-04-06 | 3.5 | 14.5 | 0 | 2018-04-06 | 2.9 | 15.1 | 0 | 2017-04-06 | 2.7 | 15.3 | 0 | 2016-04-06 | 1.1 | 16.9 | 0 | 11.86 | 0
2025-04-06 | 6.2 | 11.8 | 0 | 2024-04-06 | 10.3 | 7.7 | 0 | 2023-04-06 | 5.5 | 12.5 | 0 | 2022-04-06 | 14.1 | 3.9 | 0 | 2021-04-06 | 11.7 | 6.3 | 0 | 2020-04-06 | 12.3 | 5.7 | 0 | 2019-04-06 | 5 | 13 | 0 | 2018-04-06 | 2.5 | 15.5 | 0 | 2017-04-06 | 2.9 | 15.1 | 0 | 2016-04-06 | 0.2 | 17.8 | 0 | 10.93 | 0
2025-04-06 | 5.9 | 12.1 | 0 | 2024-04-06 | 10 | 8 | 0 | 2023-04-06 | 7.2 | 10.8 | 0 | 2022-04-06 | 14.9 | 3.1 | 0 | 2021-04-06 | 13.3 | 4.7 | 0 | 2020-04-06 | 13.3 | 4.7 | 0 | 2019-04-06 | 6.8 | 11.2 | 0 | 2018-04-06 | 2.2 | 15.8 | 0 | 2017-04-06 | 3 | 15 | 0 | 2016-04-06 | -1.8 | 19.8 | 0 | 10.52 | 0
2025-04-06 | 6.9 | 11.1 | 0 | 2024-04-06 | 10.4 | 7.6 | 0 | 2023-04-06 | 8.1 | 9.9 | 0 | 2022-04-06 | 15.2 | 2.8 | 0 | 2021-04-06 | 14.2 | 3.8 | 0 | 2020-04-06 | 14 | 4 | 0 | 2019-04-06 | 7.9 | 10.1 | 0 | 2018-04-06 | 2.3 | 15.7 | 0 | 2017-04-06 | 3.1 | 14.9 | 0 | 2016-04-06 | -2.9 | 20.9 | 0 | 10.08 | 0
2025-04-06 | 6.5 | 11.5 | 0 | 2024-04-06 | 11.5 | 6.5 | 0 | 2023-04-06 | 9.2 | 8.8 | 0 | 2022-04-06 | 15.2 | 2.8 | 0 | 2021-04-06 | 14.9 | 3.1 | 0 | 2020-04-06 | 14.2 | 3.8 | 0 | 2019-04-06 | 8.8 | 9.2 | 0 | 2018-04-06 | 1.2 | 16.8 | 0 | 2017-04-06 | 3.1 | 14.9 | 0 | 2016-04-06 | -2.9 | 20.9 | 0 | 9.83 | 0
2025-04-06 | 6.1 | 11.9 | 0 | 2024-04-06 | 10.8 | 7.2 | 0 | 2023-04-06 | 9.2 | 8.8 | 0 | 2022-04-06 | 13.5 | 4.5 | 0 | 2021-04-06 | 15.8 | 2.2 | 0 | 2020-04-06 | 13.9 | 4.1 | 0 | 2019-04-06 | 9.4 | 8.6 | 0 | 2018-04-06 | 1.1 | 16.9 | 0 | 2017-04-06 | 3 | 15 | 0 | 2016-04-06 | -2.5 | 20.5 | 0 | 9.97 | 0
2025-04-06 | 5.3 | 12.7 | 0 | 2024-04-06 | 8.8 | 9.2 | 0 | 2023-04-06 | 8.8 | 9.2 | 0 | 2022-04-06 | 12.5 | 5.5 | 0 | 2021-04-06 | 14.8 | 3.2 | 0 | 2020-04-06 | 12.7 | 5.3 | 0 | 2019-04-06 | 10.3 | 7.7 | 0 | 2018-04-06 | 1.2 | 16.8 | 0 | 2017-04-06 | 3 | 15 | 0 | 2016-04-06 | -2.4 | 20.4 | 0 | 10.5 | 0
2025-04-06 | 4.1 | 13.9 | 0 | 2024-04-06 | 7.3 | 10.7 | 0 | 2023-04-06 | 7.9 | 10.1 | 0 | 2022-04-06 | 11.2 | 6.8 | 0 | 2021-04-06 | 11.9 | 6.1 | 0 | 2020-04-06 | 10.9 | 7.1 | 0 | 2019-04-06 | 8.2 | 9.8 | 0 | 2018-04-06 | 0.2 | 17.8 | 0 | 2017-04-06 | 3 | 15 | 0 | 2016-04-06 | -2.1 | 20.1 | 0 | 11.74 | 0
2025-04-06 | 2.4 | 15.6 | 0 | 2024-04-06 | 6.7 | 11.3 | 0 | 2023-04-06 | 7.3 | 10.7 | 0 | 2022-04-06 | 10 | 8 | 0 | 2021-04-06 | 10.9 | 7.1 | 0 | 2020-04-06 | 8.8 | 9.2 | 0 | 2019-04-06 | 7.5 | 10.5 | 0 | 2018-04-06 | -0.3 | 18.3 | 0 | 2017-04-06 | 3.2 | 14.8 | 0 | 2016-04-06 | -2 | 20 | 0 | 12.55 | 0
2025-04-06 | 2 | 16 | 0 | 2024-04-06 | 6.3 | 11.7 | 0 | 2023-04-06 | 6.1 | 11.9 | 0 | 2022-04-06 | 8.5 | 9.5 | 0 | 2021-04-06 | 7.3 | 10.7 | 0 | 2020-04-06 | 8 | 10 | 0 | 2019-04-06 | 6.7 | 11.3 | 0 | 2018-04-06 | -0.4 | 18.4 | 0 | 2017-04-06 | 3.4 | 14.6 | 0 | 2016-04-06 | -1.6 | 19.6 | 0 | 13.37 | 0
2025-04-06 | 2.3 | 15.7 | 0 | 2024-04-06 | 5.1 | 12.9 | 0 | 2023-04-06 | 4.4 | 13.6 | 0 | 2022-04-06 | 8 | 10 | 0 | 2021-04-06 | 8.4 | 9.6 | 0 | 2020-04-06 | 5.9 | 12.1 | 0 | 2019-04-06 | 5 | 13 | 0 | 2018-04-06 | -0.3 | 18.3 | 0 | 2017-04-06 | 3.3 | 14.7 | 0 | 2016-04-06 | -1.3 | 19.3 | 0 | 13.92 | 0
2025-04-06 | 1.4 | 16.6 | 0 | 2024-04-06 | 5.2 | 12.8 | 0 | 2023-04-06 | 4.1 | 13.9 | 0 | 2022-04-06 | 7.5 | 10.5 | 0 | 2021-04-06 | 7.6 | 10.4 | 0 | 2020-04-06 | 2.5 | 15.5 | 0 | 2019-04-06 | 5.2 | 12.8 | 0 | 2018-04-06 | -0.1 | 18.1 | 0 | 2017-04-06 | 3 | 15 | 0 | 2016-04-06 | -0.8 | 18.8 | 0 | 14.44 | 0
2025-04-06 | -0.3 | 18.3 | 0 | 2024-04-06 | 5.2 | 12.8 | 0 | 2023-04-06 | 3.9 | 14.1 | 0 | 2022-04-06 | 7.6 | 10.4 | 0 | 2021-04-06 | 4.3 | 13.7 | 0 | 2020-04-06 | 3.9 | 14.1 | 0 | 2019-04-06 | 4.2 | 13.8 | 0 | 2018-04-06 | 0.1 | 17.9 | 0 | 2017-04-06 | 2.4 | 15.6 | 0 | 2016-04-06 | -1 | 19 | 0 | 14.97 | 0
2025-04-07 | -0.6 | 18.6 | 0 | 2024-04-07 | 4.6 | 13.4 | 0 | 2023-04-07 | 3.8 | 14.2 | 0 | 2022-04-07 | 7.2 | 10.8 | 0 | 2021-04-07 | 5.3 | 12.7 | 0 | 2020-04-07 | 2.1 | 15.9 | 0 | 2019-04-07 | 2 | 16 | 0 | 2018-04-07 | -0.8 | 18.8 | 0 | 2017-04-07 | 2.5 | 15.5 | 0 | 2016-04-07 | -0.6 | 18.6 | 0 | 15.45 | 0
2025-04-07 | -2 | 20 | 0 | 2024-04-07 | 4.5 | 13.5 | 0 | 2023-04-07 | 3.7 | 14.3 | 0 | 2022-04-07 | 5.2 | 12.8 | 0 | 2021-04-07 | 6.4 | 11.6 | 0 | 2020-04-07 | 4.4 | 13.6 | 0 | 2019-04-07 | 0.4 | 17.6 | 0 | 2018-04-07 | -1.5 | 19.5 | 0 | 2017-04-07 | 2 | 16 | 0 | 2016-04-07 | -0.1 | 18.1 | 0 | 15.7 | 0
2025-04-07 | -2.3 | 20.3 | 0 | 2024-04-07 | 2.5 | 15.5 | 0 | 2023-04-07 | 2.3 | 15.7 | 0 | 2022-04-07 | 4.4 | 13.6 | 0 | 2021-04-07 | 6.8 | 11.2 | 0 | 2020-04-07 | 2 | 16 | 0 | 2019-04-07 | 0.3 | 17.7 | 0 | 2018-04-07 | -1.5 | 19.5 | 0 | 2017-04-07 | 2 | 16 | 0 | 2016-04-07 | 0.3 | 17.7 | 0 | 16.32 | 0
2025-04-07 | -2.7 | 20.7 | 0 | 2024-04-07 | -0.2 | 18.2 | 0 | 2023-04-07 | 1.4 | 16.6 | 0 | 2022-04-07 | 3.8 | 14.2 | 0 | 2021-04-07 | 5.7 | 12.3 | 0 | 2020-04-07 | 0.7 | 17.3 | 0 | 2019-04-07 | 1.2 | 16.8 | 0 | 2018-04-07 | -1.9 | 19.9 | 0 | 2017-04-07 | 1.8 | 16.2 | 0 | 2016-04-07 | 0.6 | 17.4 | 0 | 16.96 | 0
2025-04-07 | -4.9 | 22.9 | 0 | 2024-04-07 | -0.2 | 18.2 | 0 | 2023-04-07 | 1.3 | 16.7 | 0 | 2022-04-07 | 3.3 | 14.7 | 0 | 2021-04-07 | 4.8 | 13.2 | 0 | 2020-04-07 | -0.4 | 18.4 | 0 | 2019-04-07 | 0.8 | 17.2 | 0 | 2018-04-07 | -2.3 | 20.3 | 0 | 2017-04-07 | 1.7 | 16.3 | 0 | 2016-04-07 | 0.4 | 17.6 | 0 | 17.55 | 0
2025-04-07 | -2.9 | 20.9 | 0 | 2024-04-07 | -0.2 | 18.2 | 0 | 2023-04-07 | 0.8 | 17.2 | 0 | 2022-04-07 | 3.3 | 14.7 | 0 | 2021-04-07 | 2.7 | 15.3 | 0 | 2020-04-07 | 0.4 | 17.6 | 0 | 2019-04-07 | 1.5 | 16.5 | 0 | 2018-04-07 | -2.8 | 20.8 | 0 | 2017-04-07 | 1.9 | 16.1 | 0 | 2016-04-07 | 0.4 | 17.6 | 0 | 17.49 | 0
2025-04-07 | -4 | 22 | 0 | 2024-04-07 | -1.2 | 19.2 | 0 | 2023-04-07 | -0.4 | 18.4 | 0 | 2022-04-07 | 3.5 | 14.5 | 0 | 2021-04-07 | 2.2 | 15.8 | 0 | 2020-04-07 | 0.2 | 17.8 | 0 | 2019-04-07 | 1.8 | 16.2 | 0 | 2018-04-07 | -2.4 | 20.4 | 0 | 2017-04-07 | 2.3 | 15.7 | 0 | 2016-04-07 | 0.5 | 17.5 | 0 | 17.75 | 0
2025-04-07 | -0.7 | 18.7 | 0 | 2024-04-07 | 2.4 | 15.6 | 0 | 2023-04-07 | -0.7 | 18.7 | 0 | 2022-04-07 | 3.6 | 14.4 | 0 | 2021-04-07 | 6.1 | 11.9 | 0 | 2020-04-07 | 2.6 | 15.4 | 0 | 2019-04-07 | 2.6 | 15.4 | 0 | 2018-04-07 | -2.1 | 20.1 | 0 | 2017-04-07 | 2.2 | 15.8 | 0 | 2016-04-07 | 0.8 | 17.2 | 0 | 16.32 | 0
2025-04-07 | 2.3 | 15.7 | 0 | 2024-04-07 | 5.6 | 12.4 | 0 | 2023-04-07 | -0.5 | 18.5 | 0 | 2022-04-07 | 4 | 14 | 0 | 2021-04-07 | 9.2 | 8.8 | 0 | 2020-04-07 | 5.4 | 12.6 | 0 | 2019-04-07 | 4.2 | 13.8 | 0 | 2018-04-07 | -1.6 | 19.6 | 0 | 2017-04-07 | 2.4 | 15.6 | 0 | 2016-04-07 | 1.1 | 16.9 | 0 | 14.79 | 0
2025-04-07 | 4.4 | 13.6 | 0 | 2024-04-07 | 8.7 | 9.3 | 0 | 2023-04-07 | -0.2 | 18.2 | 0 | 2022-04-07 | 4.5 | 13.5 | 0 | 2021-04-07 | 12.1 | 5.9 | 0 | 2020-04-07 | 7.9 | 10.1 | 0 | 2019-04-07 | 5.2 | 12.8 | 0 | 2018-04-07 | -1.1 | 19.1 | 0 | 2017-04-07 | 3 | 15 | 0 | 2016-04-07 | 1.4 | 16.6 | 0 | 13.41 | 0
2025-04-07 | 5.1 | 12.9 | 0 | 2024-04-07 | 9.8 | 8.2 | 0 | 2023-04-07 | 0 | 18 | 0 | 2022-04-07 | 5.4 | 12.6 | 0 | 2021-04-07 | 14.4 | 3.6 | 0 | 2020-04-07 | 9.9 | 8.1 | 0 | 2019-04-07 | 6.7 | 11.3 | 0 | 2018-04-07 | -0.8 | 18.8 | 0 | 2017-04-07 | 2.8 | 15.2 | 0 | 2016-04-07 | 2.7 | 15.3 | 0 | 12.4 | 0
2025-04-07 | 6.3 | 11.7 | 0 | 2024-04-07 | 12 | 6 | 0 | 2023-04-07 | 0.7 | 17.3 | 0 | 2022-04-07 | 6.6 | 11.4 | 0 | 2021-04-07 | 15.4 | 2.6 | 0 | 2020-04-07 | 11.2 | 6.8 | 0 | 2019-04-07 | 7.4 | 10.6 | 0 | 2018-04-07 | -0.4 | 18.4 | 0 | 2017-04-07 | 2.5 | 15.5 | 0 | 2016-04-07 | 4 | 14 | 0 | 11.43 | 0
2025-04-07 | 6.5 | 11.5 | 0 | 2024-04-07 | 13.1 | 4.9 | 0 | 2023-04-07 | 1.3 | 16.7 | 0 | 2022-04-07 | 7 | 11 | 0 | 2021-04-07 | 16.7 | 1.3 | 0 | 2020-04-07 | 12.2 | 5.8 | 0 | 2019-04-07 | 8 | 10 | 0 | 2018-04-07 | 0 | 18 | 0 | 2017-04-07 | 2.3 | 15.7 | 0 | 2016-04-07 | 5.2 | 12.8 | 0 | 10.77 | 0
2025-04-07 | 7.5 | 10.5 | 0 | 2024-04-07 | 13.8 | 4.2 | 0 | 2023-04-07 | 2 | 16 | 0 | 2022-04-07 | 7.3 | 10.7 | 0 | 2021-04-07 | 17.2 | 0.8 | 0 | 2020-04-07 | 11.9 | 6.1 | 0 | 2019-04-07 | 8.7 | 9.3 | 0 | 2018-04-07 | 0.6 | 17.4 | 0 | 2017-04-07 | 2.8 | 15.2 | 0 | 2016-04-07 | 5.8 | 12.2 | 0 | 10.24 | 0
2025-04-07 | 9 | 9 | 0 | 2024-04-07 | 14.9 | 3.1 | 0 | 2023-04-07 | 2.4 | 15.6 | 0 | 2022-04-07 | 7.2 | 10.8 | 0 | 2021-04-07 | 18.2 | 0 | 0.2 | 2020-04-07 | 12.4 | 5.6 | 0 | 2019-04-07 | 9.3 | 8.7 | 0 | 2018-04-07 | 1.1 | 16.9 | 0 | 2017-04-07 | 2.7 | 15.3 | 0 | 2016-04-07 | 5.5 | 12.5 | 0 | 9.75 | 0.02
2025-04-07 | 7.8 | 10.2 | 0 | 2024-04-07 | 15.7 | 2.3 | 0 | 2023-04-07 | 2.2 | 15.8 | 0 | 2022-04-07 | 7.3 | 10.7 | 0 | 2021-04-07 | 17.8 | 0.2 | 0 | 2020-04-07 | 12 | 6 | 0 | 2019-04-07 | 9.4 | 8.6 | 0 | 2018-04-07 | 1.3 | 16.7 | 0 | 2017-04-07 | 3 | 15 | 0 | 2016-04-07 | 6.6 | 11.4 | 0 | 9.69 | 0
2025-04-07 | 8.1 | 9.9 | 0 | 2024-04-07 | 16.2 | 1.8 | 0 | 2023-04-07 | 2.8 | 15.2 | 0 | 2022-04-07 | 7.3 | 10.7 | 0 | 2021-04-07 | 17.9 | 0.1 | 0 | 2020-04-07 | 12.5 | 5.5 | 0 | 2019-04-07 | 9 | 9 | 0 | 2018-04-07 | 0.9 | 17.1 | 0 | 2017-04-07 | 3 | 15 | 0 | 2016-04-07 | 4.4 | 13.6 | 0 | 9.79 | 0
2025-04-07 | 7.5 | 10.5 | 0 | 2024-04-07 | 15.9 | 2.1 | 0 | 2023-04-07 | 2.4 | 15.6 | 0 | 2022-04-07 | 7.2 | 10.8 | 0 | 2021-04-07 | 17.4 | 0.6 | 0 | 2020-04-07 | 11.7 | 6.3 | 0 | 2019-04-07 | 8.2 | 9.8 | 0 | 2018-04-07 | 0.9 | 17.1 | 0 | 2017-04-07 | 3 | 15 | 0 | 2016-04-07 | 3.2 | 14.8 | 0 | 10.26 | 0
2025-04-07 | 6.2 | 11.8 | 0 | 2024-04-07 | 14.3 | 3.7 | 0 | 2023-04-07 | 2 | 16 | 0 | 2022-04-07 | 6.7 | 11.3 | 0 | 2021-04-07 | 15 | 3 | 0 | 2020-04-07 | 10.1 | 7.9 | 0 | 2019-04-07 | 7 | 11 | 0 | 2018-04-07 | -0.4 | 18.4 | 0 | 2017-04-07 | 2.3 | 15.7 | 0 | 2016-04-07 | 2.8 | 15.2 | 0 | 11.4 | 0
2025-04-07 | 5.2 | 12.8 | 0 | 2024-04-07 | 12 | 6 | 0 | 2023-04-07 | 0.8 | 17.2 | 0 | 2022-04-07 | 6.1 | 11.9 | 0 | 2021-04-07 | 13.2 | 4.8 | 0 | 2020-04-07 | 9.7 | 8.3 | 0 | 2019-04-07 | 5.6 | 12.4 | 0 | 2018-04-07 | -2 | 20 | 0 | 2017-04-07 | 1.9 | 16.1 | 0 | 2016-04-07 | 2.8 | 15.2 | 0 | 12.47 | 0
2025-04-07 | 2.9 | 15.1 | 0 | 2024-04-07 | 8.8 | 9.2 | 0 | 2023-04-07 | 0 | 18 | 0 | 2022-04-07 | 5.6 | 12.4 | 0 | 2021-04-07 | 12.8 | 5.2 | 0 | 2020-04-07 | 7.2 | 10.8 | 0 | 2019-04-07 | 5 | 13 | 0 | 2018-04-07 | -2.2 | 20.2 | 0 | 2017-04-07 | 1.5 | 16.5 | 0 | 2016-04-07 | 2.8 | 15.2 | 0 | 13.56 | 0
2025-04-07 | 2.7 | 15.3 | 0 | 2024-04-07 | 10.3 | 7.7 | 0 | 2023-04-07 | -1.3 | 19.3 | 0 | 2022-04-07 | 5.2 | 12.8 | 0 | 2021-04-07 | 11.5 | 6.5 | 0 | 2020-04-07 | 6 | 12 | 0 | 2019-04-07 | 4.6 | 13.4 | 0 | 2018-04-07 | -3.8 | 21.8 | 0 | 2017-04-07 | 1.1 | 16.9 | 0 | 2016-04-07 | 2.5 | 15.5 | 0 | 14.12 | 0
2025-04-07 | 1.2 | 16.8 | 0 | 2024-04-07 | 8.3 | 9.7 | 0 | 2023-04-07 | -2.7 | 20.7 | 0 | 2022-04-07 | 4.7 | 13.3 | 0 | 2021-04-07 | 10.6 | 7.4 | 0 | 2020-04-07 | 6.5 | 11.5 | 0 | 2019-04-07 | 4 | 14 | 0 | 2018-04-07 | -4.6 | 22.6 | 0 | 2017-04-07 | 0.8 | 17.2 | 0 | 2016-04-07 | 2.6 | 15.4 | 0 | 14.86 | 0
2025-04-07 | 0.3 | 17.7 | 0 | 2024-04-07 | 6.2 | 11.8 | 0 | 2023-04-07 | -3.3 | 21.3 | 0 | 2022-04-07 | 4.1 | 13.9 | 0 | 2021-04-07 | 9.8 | 8.2 | 0 | 2020-04-07 | 5.2 | 12.8 | 0 | 2019-04-07 | 3.8 | 14.2 | 0 | 2018-04-07 | -3.6 | 21.6 | 0 | 2017-04-07 | 0.4 | 17.6 | 0 | 2016-04-07 | 2.6 | 15.4 | 0 | 15.45 | 0
2025-04-08 | 0 | 18 | 0 | 2024-04-08 | 4.8 | 13.2 | 0 | 2023-04-08 | -3.6 | 21.6 | 0 | 2022-04-08 | 3.4 | 14.6 | 0 | 2021-04-08 | 9 | 9 | 0 | 2020-04-08 | 5.2 | 12.8 | 0 | 2019-04-08 | 3.6 | 14.4 | 0 | 2018-04-08 | -3.6 | 21.6 | 0 | 2017-04-08 | 0.1 | 17.9 | 0 | 2016-04-08 | 3 | 15 | 0 | 15.81 | 0
2025-04-08 | -0.1 | 18.1 | 0 | 2024-04-08 | 5.4 | 12.6 | 0 | 2023-04-08 | -3.7 | 21.7 | 0 | 2022-04-08 | 2.6 | 15.4 | 0 | 2021-04-08 | 8.1 | 9.9 | 0 | 2020-04-08 | 2 | 16 | 0 | 2019-04-08 | 3.6 | 14.4 | 0 | 2018-04-08 | -3.9 | 21.9 | 0 | 2017-04-08 | -0.2 | 18.2 | 0 | 2016-04-08 | 2.2 | 15.8 | 0 | 16.4 | 0
2025-04-08 | -0.3 | 18.3 | 0 | 2024-04-08 | 1.8 | 16.2 | 0 | 2023-04-08 | -5.1 | 23.1 | 0 | 2022-04-08 | 1.5 | 16.5 | 0 | 2021-04-08 | 7.5 | 10.5 | 0 | 2020-04-08 | 2.1 | 15.9 | 0 | 2019-04-08 | 0.7 | 17.3 | 0 | 2018-04-08 | -3.4 | 21.4 | 0 | 2017-04-08 | -0.4 | 18.4 | 0 | 2016-04-08 | 1.6 | 16.4 | 0 | 17.4 | 0
2025-04-08 | -0.6 | 18.6 | 0 | 2024-04-08 | 2.8 | 15.2 | 0 | 2023-04-08 | -5.7 | 23.7 | 0 | 2022-04-08 | 0.6 | 17.4 | 0 | 2021-04-08 | 7.4 | 10.6 | 0 | 2020-04-08 | 1.8 | 16.2 | 0 | 2019-04-08 | -0.2 | 18.2 | 0 | 2018-04-08 | -3.2 | 21.2 | 0 | 2017-04-08 | -0.5 | 18.5 | 0 | 2016-04-08 | 0.9 | 17.1 | 0 | 17.67 | 0
2025-04-08 | -0.8 | 18.8 | 0 | 2024-04-08 | 2.5 | 15.5 | 0 | 2023-04-08 | -6.1 | 24.1 | 0 | 2022-04-08 | 0.3 | 17.7 | 0 | 2021-04-08 | 6.8 | 11.2 | 0 | 2020-04-08 | 1.1 | 16.9 | 0 | 2019-04-08 | 0 | 18 | 0 | 2018-04-08 | -3.3 | 21.3 | 0 | 2017-04-08 | -0.4 | 18.4 | 0 | 2016-04-08 | 1 | 17 | 0 | 17.89 | 0
2025-04-08 | -2.1 | 20.1 | 0 | 2024-04-08 | 1.8 | 16.2 | 0 | 2023-04-08 | -6.4 | 24.4 | 0 | 2022-04-08 | 0.1 | 17.9 | 0 | 2021-04-08 | 6.1 | 11.9 | 0 | 2020-04-08 | 1.2 | 16.8 | 0 | 2019-04-08 | 0.1 | 17.9 | 0 | 2018-04-08 | -2.8 | 20.8 | 0 | 2017-04-08 | -0.5 | 18.5 | 0 | 2016-04-08 | 0 | 18 | 0 | 18.25 | 0
2025-04-08 | -2.7 | 20.7 | 0 | 2024-04-08 | 1.2 | 16.8 | 0 | 2023-04-08 | -6.4 | 24.4 | 0 | 2022-04-08 | 0.1 | 17.9 | 0 | 2021-04-08 | 6.3 | 11.7 | 0 | 2020-04-08 | 1.1 | 16.9 | 0 | 2019-04-08 | 0 | 18 | 0 | 2018-04-08 | -3.1 | 21.1 | 0 | 2017-04-08 | -0.5 | 18.5 | 0 | 2016-04-08 | -0.9 | 18.9 | 0 | 18.49 | 0
2025-04-08 | -3.2 | 21.2 | 0 | 2024-04-08 | 4.2 | 13.8 | 0 | 2023-04-08 | -2.9 | 20.9 | 0 | 2022-04-08 | 0.1 | 17.9 | 0 | 2021-04-08 | 8.1 | 9.9 | 0 | 2020-04-08 | 1.2 | 16.8 | 0 | 2019-04-08 | -0.5 | 18.5 | 0 | 2018-04-08 | -2.7 | 20.7 | 0 | 2017-04-08 | -0.2 | 18.2 | 0 | 2016-04-08 | -2.2 | 20.2 | 0 | 17.81 | 0
2025-04-08 | -5.6 | 23.6 | 0 | 2024-04-08 | 7.3 | 10.7 | 0 | 2023-04-08 | -0.8 | 18.8 | 0 | 2022-04-08 | 0.6 | 17.4 | 0 | 2021-04-08 | 10.4 | 7.6 | 0 | 2020-04-08 | 2 | 16 | 0 | 2019-04-08 | -0.6 | 18.6 | 0 | 2018-04-08 | -2.7 | 20.7 | 0 | 2017-04-08 | 0.9 | 17.1 | 0 | 2016-04-08 | -2.7 | 20.7 | 0 | 17.12 | 0
2025-04-08 | -6.9 | 24.9 | 0 | 2024-04-08 | 10.3 | 7.7 | 0 | 2023-04-08 | 0.6 | 17.4 | 0 | 2022-04-08 | 1.2 | 16.8 | 0 | 2021-04-08 | 13.1 | 4.9 | 0 | 2020-04-08 | 2.8 | 15.2 | 0 | 2019-04-08 | -0.8 | 18.8 | 0 | 2018-04-08 | -2.3 | 20.3 | 0 | 2017-04-08 | 2.6 | 15.4 | 0 | 2016-04-08 | -3.2 | 21.2 | 0 | 16.26 | 0
2025-04-08 | -7.3 | 25.3 | 0 | 2024-04-08 | 12.7 | 5.3 | 0 | 2023-04-08 | 1.9 | 16.1 | 0 | 2022-04-08 | 2.2 | 15.8 | 0 | 2021-04-08 | 15.8 | 2.2 | 0 | 2020-04-08 | 3.4 | 14.6 | 0 | 2019-04-08 | -0.6 | 18.6 | 0 | 2018-04-08 | -2.3 | 20.3 | 0 | 2017-04-08 | 3.6 | 14.4 | 0 | 2016-04-08 | -3.6 | 21.6 | 0 | 15.42 | 0
2025-04-08 | -7.6 | 25.6 | 0 | 2024-04-08 | 15.3 | 2.7 | 0 | 2023-04-08 | 2.6 | 15.4 | 0 | 2022-04-08 | 2.9 | 15.1 | 0 | 2021-04-08 | 17.4 | 0.6 | 0 | 2020-04-08 | 4.3 | 13.7 | 0 | 2019-04-08 | -0.3 | 18.3 | 0 | 2018-04-08 | -1.2 | 19.2 | 0 | 2017-04-08 | 5.4 | 12.6 | 0 | 2016-04-08 | -4 | 22 | 0 | 14.52 | 0
2025-04-08 | -7.5 | 25.5 | 0 | 2024-04-08 | 16.4 | 1.6 | 0 | 2023-04-08 | 3.8 | 14.2 | 0 | 2022-04-08 | 3.4 | 14.6 | 0 | 2021-04-08 | 18.9 | 0 | 0.9 | 2020-04-08 | 5.5 | 12.5 | 0 | 2019-04-08 | -0.2 | 18.2 | 0 | 2018-04-08 | -0.4 | 18.4 | 0 | 2017-04-08 | 6.4 | 11.6 | 0 | 2016-04-08 | -3.5 | 21.5 | 0 | 13.81 | 0.09
2025-04-08 | -6.6 | 24.6 | 0 | 2024-04-08 | 17.5 | 0.5 | 0 | 2023-04-08 | 4.8 | 13.2 | 0 | 2022-04-08 | 4.4 | 13.6 | 0 | 2021-04-08 | 20.2 | 0 | 2.2 | 2020-04-08 | 7.1 | 10.9 | 0 | 2019-04-08 | -0.1 | 18.1 | 0 | 2018-04-08 | 0.3 | 17.7 | 0 | 2017-04-08 | 7.4 | 10.6 | 0 | 2016-04-08 | -3.3 | 21.3 | 0 | 13.05 | 0.22
2025-04-08 | -6.2 | 24.2 | 0 | 2024-04-08 | 17.1 | 0.9 | 0 | 2023-04-08 | 5.1 | 12.9 | 0 | 2022-04-08 | 6.6 | 11.4 | 0 | 2021-04-08 | 21.1 | 0 | 3.1 | 2020-04-08 | 7.2 | 10.8 | 0 | 2019-04-08 | 0.1 | 17.9 | 0 | 2018-04-08 | -0.6 | 18.6 | 0 | 2017-04-08 | 9.1 | 8.9 | 0 | 2016-04-08 | -3 | 21 | 0 | 12.66 | 0.31
2025-04-08 | -5.9 | 23.9 | 0 | 2024-04-08 | 15.3 | 2.7 | 0 | 2023-04-08 | 5.4 | 12.6 | 0 | 2022-04-08 | 7.9 | 10.1 | 0 | 2021-04-08 | 21.6 | 0 | 3.6 | 2020-04-08 | 7.7 | 10.3 | 0 | 2019-04-08 | 0.3 | 17.7 | 0 | 2018-04-08 | 0.5 | 17.5 | 0 | 2017-04-08 | 9.3 | 8.7 | 0 | 2016-04-08 | -3.2 | 21.2 | 0 | 12.47 | 0.36
2025-04-08 | -4.2 | 22.2 | 0 | 2024-04-08 | 16.5 | 1.5 | 0 | 2023-04-08 | 5.6 | 12.4 | 0 | 2022-04-08 | 9.1 | 8.9 | 0 | 2021-04-08 | 21.9 | 0 | 3.9 | 2020-04-08 | 7.7 | 10.3 | 0 | 2019-04-08 | 0.6 | 17.4 | 0 | 2018-04-08 | -0.2 | 18.2 | 0 | 2017-04-08 | 9.3 | 8.7 | 0 | 2016-04-08 | -3.5 | 21.5 | 0 | 12.11 | 0.39
2025-04-08 | -3.8 | 21.8 | 0 | 2024-04-08 | 17.1 | 0.9 | 0 | 2023-04-08 | 5.7 | 12.3 | 0 | 2022-04-08 | 8 | 10 | 0 | 2021-04-08 | 21.1 | 0 | 3.1 | 2020-04-08 | 7.6 | 10.4 | 0 | 2019-04-08 | 0.9 | 17.1 | 0 | 2018-04-08 | -0.4 | 18.4 | 0 | 2017-04-08 | 9.1 | 8.9 | 0 | 2016-04-08 | -3.1 | 21.1 | 0 | 12.09 | 0.31
2025-04-08 | -3.9 | 21.9 | 0 | 2024-04-08 | 15.6 | 2.4 | 0 | 2023-04-08 | 4.9 | 13.1 | 0 | 2022-04-08 | 6.4 | 11.6 | 0 | 2021-04-08 | 19.5 | 0 | 1.5 | 2020-04-08 | 7.1 | 10.9 | 0 | 2019-04-08 | 0.8 | 17.2 | 0 | 2018-04-08 | -1.6 | 19.6 | 0 | 2017-04-08 | 7.8 | 10.2 | 0 | 2016-04-08 | -3 | 21 | 0 | 12.79 | 0.15
2025-04-08 | -3.9 | 21.9 | 0 | 2024-04-08 | 13.3 | 4.7 | 0 | 2023-04-08 | 3.9 | 14.1 | 0 | 2022-04-08 | 4.3 | 13.7 | 0 | 2021-04-08 | 17.2 | 0.8 | 0 | 2020-04-08 | 6.4 | 11.6 | 0 | 2019-04-08 | 0.5 | 17.5 | 0 | 2018-04-08 | -2.8 | 20.8 | 0 | 2017-04-08 | 4.6 | 13.4 | 0 | 2016-04-08 | -3.1 | 21.1 | 0 | 13.96 | 0
2025-04-08 | -4.5 | 22.5 | 0 | 2024-04-08 | 11.4 | 6.6 | 0 | 2023-04-08 | 3.3 | 14.7 | 0 | 2022-04-08 | 3.8 | 14.2 | 0 | 2021-04-08 | 14.9 | 3.1 | 0 | 2020-04-08 | 6.2 | 11.8 | 0 | 2019-04-08 | 0.8 | 17.2 | 0 | 2018-04-08 | -3.6 | 21.6 | 0 | 2017-04-08 | 4.2 | 13.8 | 0 | 2016-04-08 | -3.5 | 21.5 | 0 | 14.7 | 0
2025-04-08 | -5.8 | 23.8 | 0 | 2024-04-08 | 10.7 | 7.3 | 0 | 2023-04-08 | 1.5 | 16.5 | 0 | 2022-04-08 | 4.4 | 13.6 | 0 | 2021-04-08 | 14.4 | 3.6 | 0 | 2020-04-08 | 5.8 | 12.2 | 0 | 2019-04-08 | 0.4 | 17.6 | 0 | 2018-04-08 | -4.1 | 22.1 | 0 | 2017-04-08 | 4 | 14 | 0 | 2016-04-08 | -4.5 | 22.5 | 0 | 15.32 | 0
2025-04-08 | -7.3 | 25.3 | 0 | 2024-04-08 | 10.4 | 7.6 | 0 | 2023-04-08 | 0.8 | 17.2 | 0 | 2022-04-08 | 3.8 | 14.2 | 0 | 2021-04-08 | 13.5 | 4.5 | 0 | 2020-04-08 | 5.5 | 12.5 | 0 | 2019-04-08 | 0.2 | 17.8 | 0 | 2018-04-08 | -4.5 | 22.5 | 0 | 2017-04-08 | 3.2 | 14.8 | 0 | 2016-04-08 | -4.8 | 22.8 | 0 | 15.92 | 0
2025-04-08 | -7.9 | 25.9 | 0 | 2024-04-08 | 9.3 | 8.7 | 0 | 2023-04-08 | 0 | 18 | 0 | 2022-04-08 | 3.7 | 14.3 | 0 | 2021-04-08 | 13.3 | 4.7 | 0 | 2020-04-08 | 5.5 | 12.5 | 0 | 2019-04-08 | -1.9 | 19.9 | 0 | 2018-04-08 | -6.1 | 24.1 | 0 | 2017-04-08 | 2.7 | 15.3 | 0 | 2016-04-08 | -5 | 23 | 0 | 16.64 | 0
2025-04-09 | -6.5 | 24.5 | 0 | 2024-04-09 | 8.5 | 9.5 | 0 | 2023-04-09 | -1.3 | 19.3 | 0 | 2022-04-09 | 2.8 | 15.2 | 0 | 2021-04-09 | 12.2 | 5.8 | 0 | 2020-04-09 | 5.3 | 12.7 | 0 | 2019-04-09 | -0.1 | 18.1 | 0 | 2018-04-09 | -4.9 | 22.9 | 0 | 2017-04-09 | 1.3 | 16.7 | 0 | 2016-04-09 | -5.5 | 23.5 | 0 | 16.82 | 0
2025-04-09 | -7.2 | 25.2 | 0 | 2024-04-09 | 7.3 | 10.7 | 0 | 2023-04-09 | -2.6 | 20.6 | 0 | 2022-04-09 | 1.9 | 16.1 | 0 | 2021-04-09 | 11.2 | 6.8 | 0 | 2020-04-09 | 5.2 | 12.8 | 0 | 2019-04-09 | -0.6 | 18.6 | 0 | 2018-04-09 | -5 | 23 | 0 | 2017-04-09 | 1 | 17 | 0 | 2016-04-09 | -6 | 24 | 0 | 17.48 | 0
2025-04-09 | -8.8 | 26.8 | 0 | 2024-04-09 | 6.1 | 11.9 | 0 | 2023-04-09 | -2.2 | 20.2 | 0 | 2022-04-09 | 1 | 17 | 0 | 2021-04-09 | 10.7 | 7.3 | 0 | 2020-04-09 | 4.8 | 13.2 | 0 | 2019-04-09 | -0.5 | 18.5 | 0 | 2018-04-09 | -5 | 23 | 0 | 2017-04-09 | 1.8 | 16.2 | 0 | 2016-04-09 | -6.3 | 24.3 | 0 | 17.84 | 0
2025-04-09 | -11 | 29 | 0 | 2024-04-09 | 6.7 | 11.3 | 0 | 2023-04-09 | -3.9 | 21.9 | 0 | 2022-04-09 | -0.1 | 18.1 | 0 | 2021-04-09 | 9.6 | 8.4 | 0 | 2020-04-09 | 4.5 | 13.5 | 0 | 2019-04-09 | -0.5 | 18.5 | 0 | 2018-04-09 | -5.3 | 23.3 | 0 | 2017-04-09 | 0.4 | 17.6 | 0 | 2016-04-09 | -6.8 | 24.8 | 0 | 18.64 | 0
2025-04-09 | -11.6 | 29.6 | 0 | 2024-04-09 | 6.5 | 11.5 | 0 | 2023-04-09 | -4.8 | 22.8 | 0 | 2022-04-09 | -1.9 | 19.9 | 0 | 2021-04-09 | 7.5 | 10.5 | 0 | 2020-04-09 | 4.6 | 13.4 | 0 | 2019-04-09 | -1.7 | 19.7 | 0 | 2018-04-09 | -6 | 24 | 0 | 2017-04-09 | 0.7 | 17.3 | 0 | 2016-04-09 | -7.3 | 25.3 | 0 | 19.4 | 0
2025-04-09 | -13.4 | 31.4 | 0 | 2024-04-09 | 5.9 | 12.1 | 0 | 2023-04-09 | -2.9 | 20.9 | 0 | 2022-04-09 | -0.9 | 18.9 | 0 | 2021-04-09 | 7.7 | 10.3 | 0 | 2020-04-09 | 4.8 | 13.2 | 0 | 2019-04-09 | -2.3 | 20.3 | 0 | 2018-04-09 | -7.3 | 25.3 | 0 | 2017-04-09 | -0.9 | 18.9 | 0 | 2016-04-09 | -8.2 | 26.2 | 0 | 19.75 | 0
2025-04-09 | -11.5 | 29.5 | 0 | 2024-04-09 | 3.8 | 14.2 | 0 | 2023-04-09 | -3.8 | 21.8 | 0 | 2022-04-09 | -1.5 | 19.5 | 0 | 2021-04-09 | 8 | 10 | 0 | 2020-04-09 | 4.1 | 13.9 | 0 | 2019-04-09 | -2.6 | 20.6 | 0 | 2018-04-09 | -7.2 | 25.2 | 0 | 2017-04-09 | 0.4 | 17.6 | 0 | 2016-04-09 | -8.8 | 26.8 | 0 | 19.91 | 0
2025-04-09 | -10.9 | 28.9 | 0 | 2024-04-09 | 8 | 10 | 0 | 2023-04-09 | -1.2 | 19.2 | 0 | 2022-04-09 | 1.8 | 16.2 | 0 | 2021-04-09 | 10.1 | 7.9 | 0 | 2020-04-09 | 4.2 | 13.8 | 0 | 2019-04-09 | -2.5 | 20.5 | 0 | 2018-04-09 | -4.8 | 22.8 | 0 | 2017-04-09 | 2.8 | 15.2 | 0 | 2016-04-09 | -8.4 | 26.4 | 0 | 18.09 | 0
2025-04-09 | -8.1 | 26.1 | 0 | 2024-04-09 | 10.3 | 7.7 | 0 | 2023-04-09 | 1.3 | 16.7 | 0 | 2022-04-09 | 4 | 14 | 0 | 2021-04-09 | 14.5 | 3.5 | 0 | 2020-04-09 | 4.3 | 13.7 | 0 | 2019-04-09 | -2.8 | 20.8 | 0 | 2018-04-09 | -4 | 22 | 0 | 2017-04-09 | 5.1 | 12.9 | 0 | 2016-04-09 | -7.9 | 25.9 | 0 | 16.33 | 0
2025-04-09 | -5.8 | 23.8 | 0 | 2024-04-09 | 12.8 | 5.2 | 0 | 2023-04-09 | 3.6 | 14.4 | 0 | 2022-04-09 | 6.9 | 11.1 | 0 | 2021-04-09 | 17.7 | 0.3 | 0 | 2020-04-09 | 3 | 15 | 0 | 2019-04-09 | -2.7 | 20.7 | 0 | 2018-04-09 | -2.6 | 20.6 | 0 | 2017-04-09 | 8.3 | 9.7 | 0 | 2016-04-09 | -7 | 25 | 0 | 14.58 | 0
2025-04-09 | -4.5 | 22.5 | 0 | 2024-04-09 | 14.6 | 3.4 | 0 | 2023-04-09 | 5.5 | 12.5 | 0 | 2022-04-09 | 8.5 | 9.5 | 0 | 2021-04-09 | 19.5 | 0 | 1.5 | 2020-04-09 | 2.5 | 15.5 | 0 | 2019-04-09 | -2.5 | 20.5 | 0 | 2018-04-09 | -2.3 | 20.3 | 0 | 2017-04-09 | 10.9 | 7.1 | 0 | 2016-04-09 | -5.8 | 23.8 | 0 | 13.51 | 0.15
2025-04-09 | -3.5 | 21.5 | 0 | 2024-04-09 | 16.5 | 1.5 | 0 | 2023-04-09 | 7.2 | 10.8 | 0 | 2022-04-09 | 9.1 | 8.9 | 0 | 2021-04-09 | 20.9 | 0 | 2.9 | 2020-04-09 | 1.1 | 16.9 | 0 | 2019-04-09 | -2.7 | 20.7 | 0 | 2018-04-09 | -1.5 | 19.5 | 0 | 2017-04-09 | 13.2 | 4.8 | 0 | 2016-04-09 | -5.2 | 23.2 | 0 | 12.78 | 0.29
2025-04-09 | -2.4 | 20.4 | 0 | 2024-04-09 | 17.6 | 0.4 | 0 | 2023-04-09 | 8.3 | 9.7 | 0 | 2022-04-09 | 9.5 | 8.5 | 0 | 2021-04-09 | 21.5 | 0 | 3.5 | 2020-04-09 | 1.2 | 16.8 | 0 | 2019-04-09 | -2.5 | 20.5 | 0 | 2018-04-09 | 0.2 | 17.8 | 0 | 2017-04-09 | 15.4 | 2.6 | 0 | 2016-04-09 | -4.4 | 22.4 | 0 | 11.91 | 0.35
2025-04-09 | -1.1 | 19.1 | 0 | 2024-04-09 | 18.6 | 0 | 0.6 | 2023-04-09 | 9.2 | 8.8 | 0 | 2022-04-09 | 9.6 | 8.4 | 0 | 2021-04-09 | 22.7 | 0 | 4.7 | 2020-04-09 | 3.1 | 14.9 | 0 | 2019-04-09 | -2.1 | 20.1 | 0 | 2018-04-09 | 1.2 | 16.8 | 0 | 2017-04-09 | 15.7 | 2.3 | 0 | 2016-04-09 | -2.3 | 20.3 | 0 | 11.07 | 0.53
2025-04-09 | -0.2 | 18.2 | 0 | 2024-04-09 | 20 | 0 | 2 | 2023-04-09 | 9.3 | 8.7 | 0 | 2022-04-09 | 8 | 10 | 0 | 2021-04-09 | 22.7 | 0 | 4.7 | 2020-04-09 | 4.2 | 13.8 | 0 | 2019-04-09 | -1.8 | 19.8 | 0 | 2018-04-09 | 1 | 17 | 0 | 2017-04-09 | 15.9 | 2.1 | 0 | 2016-04-09 | -1.7 | 19.7 | 0 | 10.93 | 0.67
2025-04-09 | 0.5 | 17.5 | 0 | 2024-04-09 | 20.9 | 0 | 2.9 | 2023-04-09 | 10 | 8 | 0 | 2022-04-09 | 9.3 | 8.7 | 0 | 2021-04-09 | 19.8 | 0 | 1.8 | 2020-04-09 | 5.2 | 12.8 | 0 | 2019-04-09 | -1.1 | 19.1 | 0 | 2018-04-09 | 1.4 | 16.6 | 0 | 2017-04-09 | 15.4 | 2.6 | 0 | 2016-04-09 | -0.8 | 18.8 | 0 | 10.41 | 0.47
2025-04-09 | 0.5 | 17.5 | 0 | 2024-04-09 | 20.6 | 0 | 2.6 | 2023-04-09 | 10.4 | 7.6 | 0 | 2022-04-09 | 9.4 | 8.6 | 0 | 2021-04-09 | 20.5 | 0 | 2.5 | 2020-04-09 | 6 | 12 | 0 | 2019-04-09 | -0.6 | 18.6 | 0 | 2018-04-09 | 2.1 | 15.9 | 0 | 2017-04-09 | 14.5 | 3.5 | 0 | 2016-04-09 | -0.4 | 18.4 | 0 | 10.21 | 0.51
2025-04-09 | 1.1 | 16.9 | 0 | 2024-04-09 | 19.2 | 0 | 1.2 | 2023-04-09 | 10.4 | 7.6 | 0 | 2022-04-09 | 9.5 | 8.5 | 0 | 2021-04-09 | 18.6 | 0 | 0.6 | 2020-04-09 | 6.2 | 11.8 | 0 | 2019-04-09 | -0.3 | 18.3 | 0 | 2018-04-09 | 1.8 | 16.2 | 0 | 2017-04-09 | 14.6 | 3.4 | 0 | 2016-04-09 | -0.6 | 18.6 | 0 | 10.13 | 0.18
2025-04-09 | 0.9 | 17.1 | 0 | 2024-04-09 | 17.6 | 0.4 | 0 | 2023-04-09 | 8.8 | 9.2 | 0 | 2022-04-09 | 8.8 | 9.2 | 0 | 2021-04-09 | 17.6 | 0.4 | 0 | 2020-04-09 | 5.3 | 12.7 | 0 | 2019-04-09 | -0.5 | 18.5 | 0 | 2018-04-09 | 1.3 | 16.7 | 0 | 2017-04-09 | 14 | 4 | 0 | 2016-04-09 | -1.5 | 19.5 | 0 | 10.77 | 0
2025-04-09 | -0.3 | 18.3 | 0 | 2024-04-09 | 15.6 | 2.4 | 0 | 2023-04-09 | 7.6 | 10.4 | 0 | 2022-04-09 | 7.5 | 10.5 | 0 | 2021-04-09 | 15.5 | 2.5 | 0 | 2020-04-09 | 3.2 | 14.8 | 0 | 2019-04-09 | -0.7 | 18.7 | 0 | 2018-04-09 | 0.2 | 17.8 | 0 | 2017-04-09 | 13.5 | 4.5 | 0 | 2016-04-09 | -2.5 | 20.5 | 0 | 12.04 | 0
2025-04-09 | -3 | 21 | 0 | 2024-04-09 | 14.3 | 3.7 | 0 | 2023-04-09 | 5.9 | 12.1 | 0 | 2022-04-09 | 6.3 | 11.7 | 0 | 2021-04-09 | 15.6 | 2.4 | 0 | 2020-04-09 | 3.3 | 14.7 | 0 | 2019-04-09 | -0.6 | 18.6 | 0 | 2018-04-09 | -1.2 | 19.2 | 0 | 2017-04-09 | 12.6 | 5.4 | 0 | 2016-04-09 | -3.1 | 21.1 | 0 | 12.99 | 0
2025-04-09 | -2.3 | 20.3 | 0 | 2024-04-09 | 13.8 | 4.2 | 0 | 2023-04-09 | 4.7 | 13.3 | 0 | 2022-04-09 | 4.2 | 13.8 | 0 | 2021-04-09 | 14.5 | 3.5 | 0 | 2020-04-09 | 1.7 | 16.3 | 0 | 2019-04-09 | -0.8 | 18.8 | 0 | 2018-04-09 | -1.6 | 19.6 | 0 | 2017-04-09 | 10.8 | 7.2 | 0 | 2016-04-09 | -3.9 | 21.9 | 0 | 13.89 | 0
2025-04-09 | -2.5 | 20.5 | 0 | 2024-04-09 | 13.2 | 4.8 | 0 | 2023-04-09 | 3.7 | 14.3 | 0 | 2022-04-09 | 5.7 | 12.3 | 0 | 2021-04-09 | 13.4 | 4.6 | 0 | 2020-04-09 | 1.2 | 16.8 | 0 | 2019-04-09 | -1.8 | 19.8 | 0 | 2018-04-09 | -2.4 | 20.4 | 0 | 2017-04-09 | 11.6 | 6.4 | 0 | 2016-04-09 | -4.8 | 22.8 | 0 | 14.27 | 0
2025-04-09 | -3 | 21 | 0 | 2024-04-09 | 11.8 | 6.2 | 0 | 2023-04-09 | 2.9 | 15.1 | 0 | 2022-04-09 | 3.1 | 14.9 | 0 | 2021-04-09 | 12.5 | 5.5 | 0 | 2020-04-09 | 0.9 | 17.1 | 0 | 2019-04-09 | -1.2 | 19.2 | 0 | 2018-04-09 | -3.3 | 21.3 | 0 | 2017-04-09 | 11.6 | 6.4 | 0 | 2016-04-09 | -5.5 | 23.5 | 0 | 15.02 | 0
2025-04-10 | -3.9 | 21.9 | 0 | 2024-04-10 | 10.3 | 7.7 | 0 | 2023-04-10 | 2.3 | 15.7 | 0 | 2022-04-10 | 2.6 | 15.4 | 0 | 2021-04-10 | 11 | 7 | 0 | 2020-04-10 | 1.2 | 16.8 | 0 | 2019-04-10 | -3.1 | 21.1 | 0 | 2018-04-10 | -2.9 | 20.9 | 0 | 2017-04-10 | 10.7 | 7.3 | 0 | 2016-04-10 | -5.9 | 23.9 | 0 | 15.77 | 0
2025-04-10 | -3.6 | 21.6 | 0 | 2024-04-10 | 9.2 | 8.8 | 0 | 2023-04-10 | 1.9 | 16.1 | 0 | 2022-04-10 | 1.9 | 16.1 | 0 | 2021-04-10 | 11 | 7 | 0 | 2020-04-10 | 1.1 | 16.9 | 0 | 2019-04-10 | -3.7 | 21.7 | 0 | 2018-04-10 | -2.7 | 20.7 | 0 | 2017-04-10 | 10 | 8 | 0 | 2016-04-10 | -7 | 25 | 0 | 16.19 | 0
2025-04-10 | -6.5 | 24.5 | 0 | 2024-04-10 | 8.8 | 9.2 | 0 | 2023-04-10 | 1.1 | 16.9 | 0 | 2022-04-10 | 0.6 | 17.4 | 0 | 2021-04-10 | 10 | 8 | 0 | 2020-04-10 | 0.9 | 17.1 | 0 | 2019-04-10 | -5 | 23 | 0 | 2018-04-10 | -3.5 | 21.5 | 0 | 2017-04-10 | 10.6 | 7.4 | 0 | 2016-04-10 | -8.2 | 26.2 | 0 | 17.12 | 0
2025-04-10 | -6.1 | 24.1 | 0 | 2024-04-10 | 8.3 | 9.7 | 0 | 2023-04-10 | 0.5 | 17.5 | 0 | 2022-04-10 | -0.2 | 18.2 | 0 | 2021-04-10 | 8.5 | 9.5 | 0 | 2020-04-10 | 0.9 | 17.1 | 0 | 2019-04-10 | -5.9 | 23.9 | 0 | 2018-04-10 | -2.4 | 20.4 | 0 | 2017-04-10 | 10.8 | 7.2 | 0 | 2016-04-10 | -7.7 | 25.7 | 0 | 17.33 | 0
2025-04-10 | -8.6 | 26.6 | 0 | 2024-04-10 | 7.5 | 10.5 | 0 | 2023-04-10 | 0.3 | 17.7 | 0 | 2022-04-10 | 1 | 17 | 0 | 2021-04-10 | 9 | 9 | 0 | 2020-04-10 | 0.2 | 17.8 | 0 | 2019-04-10 | -6 | 24 | 0 | 2018-04-10 | -2.6 | 20.6 | 0 | 2017-04-10 | 11.1 | 6.9 | 0 | 2016-04-10 | -8.5 | 26.5 | 0 | 17.66 | 0
2025-04-10 | -8.7 | 26.7 | 0 | 2024-04-10 | 6.9 | 11.1 | 0 | 2023-04-10 | -0.9 | 18.9 | 0 | 2022-04-10 | 1.1 | 16.9 | 0 | 2021-04-10 | 8.2 | 9.8 | 0 | 2020-04-10 | 0.3 | 17.7 | 0 | 2019-04-10 | -3.1 | 21.1 | 0 | 2018-04-10 | -2.9 | 20.9 | 0 | 2017-04-10 | 11.6 | 6.4 | 0 | 2016-04-10 | -9.9 | 27.9 | 0 | 17.74 | 0
2025-04-10 | -7.7 | 25.7 | 0 | 2024-04-10 | 5.8 | 12.2 | 0 | 2023-04-10 | -0.3 | 18.3 | 0 | 2022-04-10 | 0.7 | 17.3 | 0 | 2021-04-10 | 9 | 9 | 0 | 2020-04-10 | 0.6 | 17.4 | 0 | 2019-04-10 | -2.9 | 20.9 | 0 | 2018-04-10 | -2.9 | 20.9 | 0 | 2017-04-10 | 11.1 | 6.9 | 0 | 2016-04-10 | -9.2 | 27.2 | 0 | 17.58 | 0
2025-04-10 | -5.3 | 23.3 | 0 | 2024-04-10 | 7 | 11 | 0 | 2023-04-10 | 1.8 | 16.2 | 0 | 2022-04-10 | 1.5 | 16.5 | 0 | 2021-04-10 | 10.9 | 7.1 | 0 | 2020-04-10 | 0.8 | 17.2 | 0 | 2019-04-10 | -3 | 21 | 0 | 2018-04-10 | -1.8 | 19.8 | 0 | 2017-04-10 | 12.1 | 5.9 | 0 | 2016-04-10 | -6.5 | 24.5 | 0 | 16.25 | 0
2025-04-10 | -2.1 | 20.1 | 0 | 2024-04-10 | 8.3 | 9.7 | 0 | 2023-04-10 | 5.1 | 12.9 | 0 | 2022-04-10 | 2.3 | 15.7 | 0 | 2021-04-10 | 14.4 | 3.6 | 0 | 2020-04-10 | 1.8 | 16.2 | 0 | 2019-04-10 | -2.1 | 20.1 | 0 | 2018-04-10 | -0.9 | 18.9 | 0 | 2017-04-10 | 15.3 | 2.7 | 0 | 2016-04-10 | -5 | 23 | 0 | 14.29 | 0
2025-04-10 | 0.2 | 17.8 | 0 | 2024-04-10 | 10.2 | 7.8 | 0 | 2023-04-10 | 8.2 | 9.8 | 0 | 2022-04-10 | 3.5 | 14.5 | 0 | 2021-04-10 | 16.1 | 1.9 | 0 | 2020-04-10 | 2.5 | 15.5 | 0 | 2019-04-10 | -0.7 | 18.7 | 0 | 2018-04-10 | -0.7 | 18.7 | 0 | 2017-04-10 | 18.6 | 0 | 0.6 | 2016-04-10 | -4 | 22 | 0 | 12.67 | 0.06
2025-04-10 | 1.8 | 16.2 | 0 | 2024-04-10 | 12.2 | 5.8 | 0 | 2023-04-10 | 11.1 | 6.9 | 0 | 2022-04-10 | 3.2 | 14.8 | 0 | 2021-04-10 | 18.1 | 0 | 0.1 | 2020-04-10 | 3.3 | 14.7 | 0 | 2019-04-10 | 0.3 | 17.7 | 0 | 2018-04-10 | 0.4 | 17.6 | 0 | 2017-04-10 | 20 | 0 | 2 | 2016-04-10 | -2.8 | 20.8 | 0 | 11.45 | 0.21
2025-04-10 | 2.3 | 15.7 | 0 | 2024-04-10 | 13.6 | 4.4 | 0 | 2023-04-10 | 13.3 | 4.7 | 0 | 2022-04-10 | 4.6 | 13.4 | 0 | 2021-04-10 | 19.3 | 0 | 1.3 | 2020-04-10 | 4.2 | 13.8 | 0 | 2019-04-10 | 1.5 | 16.5 | 0 | 2018-04-10 | 2.2 | 15.8 | 0 | 2017-04-10 | 22.6 | 0 | 4.6 | 2016-04-10 | -1.8 | 19.8 | 0 | 10.41 | 0.59
2025-04-10 | 2.8 | 15.2 | 0 | 2024-04-10 | 16.7 | 1.3 | 0 | 2023-04-10 | 15.2 | 2.8 | 0 | 2022-04-10 | 6.2 | 11.8 | 0 | 2021-04-10 | 20.9 | 0 | 2.9 | 2020-04-10 | 4 | 14 | 0 | 2019-04-10 | 2.4 | 15.6 | 0 | 2018-04-10 | 3.1 | 14.9 | 0 | 2017-04-10 | 23.2 | 0 | 5.2 | 2016-04-10 | -0.2 | 18.2 | 0 | 9.38 | 0.81
2025-04-10 | 3.7 | 14.3 | 0 | 2024-04-10 | 20.6 | 0 | 2.6 | 2023-04-10 | 16.4 | 1.6 | 0 | 2022-04-10 | 5.7 | 12.3 | 0 | 2021-04-10 | 22 | 0 | 4 | 2020-04-10 | 4.5 | 13.5 | 0 | 2019-04-10 | 3.3 | 14.7 | 0 | 2018-04-10 | 4.1 | 13.9 | 0 | 2017-04-10 | 23.4 | 0 | 5.4 | 2016-04-10 | 0.8 | 17.2 | 0 | 8.75 | 1.2
2025-04-10 | 3.5 | 14.5 | 0 | 2024-04-10 | 21.4 | 0 | 3.4 | 2023-04-10 | 18.2 | 0 | 0.2 | 2022-04-10 | 7.4 | 10.6 | 0 | 2021-04-10 | 23.3 | 0 | 5.3 | 2020-04-10 | 4.4 | 13.6 | 0 | 2019-04-10 | 2.7 | 15.3 | 0 | 2018-04-10 | 2.3 | 15.7 | 0 | 2017-04-10 | 24 | 0 | 6 | 2016-04-10 | 1.2 | 16.8 | 0 | 8.65 | 1.49
2025-04-10 | 4.2 | 13.8 | 0 | 2024-04-10 | 21 | 0 | 3 | 2023-04-10 | 18.5 | 0 | 0.5 | 2022-04-10 | 5.8 | 12.2 | 0 | 2021-04-10 | 24.3 | 0 | 6.3 | 2020-04-10 | 4.2 | 13.8 | 0 | 2019-04-10 | 2.7 | 15.3 | 0 | 2018-04-10 | 4 | 14 | 0 | 2017-04-10 | 23.5 | 0 | 5.5 | 2016-04-10 | 2.3 | 15.7 | 0 | 8.48 | 1.53
2025-04-10 | 4.1 | 13.9 | 0 | 2024-04-10 | 20.9 | 0 | 2.9 | 2023-04-10 | 17.8 | 0.2 | 0 | 2022-04-10 | 5.5 | 12.5 | 0 | 2021-04-10 | 24.4 | 0 | 6.4 | 2020-04-10 | 3.6 | 14.4 | 0 | 2019-04-10 | 3.5 | 14.5 | 0 | 2018-04-10 | 5 | 13 | 0 | 2017-04-10 | 22.9 | 0 | 4.9 | 2016-04-10 | 2.3 | 15.7 | 0 | 8.42 | 1.42
2025-04-10 | 3.8 | 14.2 | 0 | 2024-04-10 | 19.9 | 0 | 1.9 | 2023-04-10 | 15.9 | 2.1 | 0 | 2022-04-10 | 5.2 | 12.8 | 0 | 2021-04-10 | 24 | 0 | 6 | 2020-04-10 | 4.1 | 13.9 | 0 | 2019-04-10 | 2.8 | 15.2 | 0 | 2018-04-10 | 4.2 | 13.8 | 0 | 2017-04-10 | 17.1 | 0.9 | 0 | 2016-04-10 | 2.2 | 15.8 | 0 | 8.87 | 0.79
2025-04-10 | 3.3 | 14.7 | 0 | 2024-04-10 | 18.2 | 0 | 0.2 | 2023-04-10 | 13.8 | 4.2 | 0 | 2022-04-10 | 4.9 | 13.1 | 0 | 2021-04-10 | 22.1 | 0 | 4.1 | 2020-04-10 | 4 | 14 | 0 | 2019-04-10 | 2.4 | 15.6 | 0 | 2018-04-10 | 3.7 | 14.3 | 0 | 2017-04-10 | 15.2 | 2.8 | 0 | 2016-04-10 | 0.8 | 17.2 | 0 | 9.59 | 0.43
2025-04-10 | 3.1 | 14.9 | 0 | 2024-04-10 | 16.4 | 1.6 | 0 | 2023-04-10 | 12 | 6 | 0 | 2022-04-10 | 4.4 | 13.6 | 0 | 2021-04-10 | 18.3 | 0 | 0.3 | 2020-04-10 | 3.8 | 14.2 | 0 | 2019-04-10 | 1.5 | 16.5 | 0 | 2018-04-10 | 2.4 | 15.6 | 0 | 2017-04-10 | 14.5 | 3.5 | 0 | 2016-04-10 | 0.1 | 17.9 | 0 | 10.38 | 0.03
2025-04-10 | 2.3 | 15.7 | 0 | 2024-04-10 | 14.5 | 3.5 | 0 | 2023-04-10 | 11.3 | 6.7 | 0 | 2022-04-10 | 4.2 | 13.8 | 0 | 2021-04-10 | 17.2 | 0.8 | 0 | 2020-04-10 | 3.5 | 14.5 | 0 | 2019-04-10 | -0.5 | 18.5 | 0 | 2018-04-10 | 1.6 | 16.4 | 0 | 2017-04-10 | 14.4 | 3.6 | 0 | 2016-04-10 | -0.4 | 18.4 | 0 | 11.19 | 0
2025-04-10 | 2.3 | 15.7 | 0 | 2024-04-10 | 13.4 | 4.6 | 0 | 2023-04-10 | 10.7 | 7.3 | 0 | 2022-04-10 | 3.8 | 14.2 | 0 | 2021-04-10 | 15.8 | 2.2 | 0 | 2020-04-10 | 2.4 | 15.6 | 0 | 2019-04-10 | -1.7 | 19.7 | 0 | 2018-04-10 | 1.1 | 16.9 | 0 | 2017-04-10 | 13.6 | 4.4 | 0 | 2016-04-10 | -2.6 | 20.6 | 0 | 12.12 | 0
2025-04-10 | 2.4 | 15.6 | 0 | 2024-04-10 | 11.4 | 6.6 | 0 | 2023-04-10 | 9.6 | 8.4 | 0 | 2022-04-10 | 3.3 | 14.7 | 0 | 2021-04-10 | 15.8 | 2.2 | 0 | 2020-04-10 | 0.9 | 17.1 | 0 | 2019-04-10 | -1 | 19 | 0 | 2018-04-10 | 0.1 | 17.9 | 0 | 2017-04-10 | 12.7 | 5.3 | 0 | 2016-04-10 | -2.8 | 20.8 | 0 | 12.76 | 0
2025-04-10 | 1 | 17 | 0 | 2024-04-10 | 6.8 | 11.2 | 0 | 2023-04-10 | 8.7 | 9.3 | 0 | 2022-04-10 | 2.3 | 15.7 | 0 | 2021-04-10 | 15.1 | 2.9 | 0 | 2020-04-10 | 0.1 | 17.9 | 0 | 2019-04-10 | -2.2 | 20.2 | 0 | 2018-04-10 | -1 | 19 | 0 | 2017-04-10 | 12.8 | 5.2 | 0 | 2016-04-10 | -2.5 | 20.5 | 0 | 13.89 | 0
2025-04-11 | 0.2 | 17.8 | 0 | 2024-04-11 | 8.4 | 9.6 | 0 | 2023-04-11 | 9.5 | 8.5 | 0 | 2022-04-11 | 2.2 | 15.8 | 0 | 2021-04-11 | 13.2 | 4.8 | 0 | 2020-04-11 | 0.5 | 17.5 | 0 | 2019-04-11 | -2.8 | 20.8 | 0 | 2018-04-11 | -0.8 | 18.8 | 0 | 2017-04-11 | 12.3 | 5.7 | 0 | 2016-04-11 | -2.3 | 20.3 | 0 | 13.96 | 0
2025-04-11 | 0.2 | 17.8 | 0 | 2024-04-11 | 8.1 | 9.9 | 0 | 2023-04-11 | 9.4 | 8.6 | 0 | 2022-04-11 | 0.6 | 17.4 | 0 | 2021-04-11 | 13.3 | 4.7 | 0 | 2020-04-11 | -0.1 | 18.1 | 0 | 2019-04-11 | -3.8 | 21.8 | 0 | 2018-04-11 | -1.7 | 19.7 | 0 | 2017-04-11 | 11 | 7 | 0 | 2016-04-11 | -2.2 | 20.2 | 0 | 14.52 | 0
2025-04-11 | 0.1 | 17.9 | 0 | 2024-04-11 | 6 | 12 | 0 | 2023-04-11 | 8.8 | 9.2 | 0 | 2022-04-11 | -0.9 | 18.9 | 0 | 2021-04-11 | 12.1 | 5.9 | 0 | 2020-04-11 | -0.7 | 18.7 | 0 | 2019-04-11 | -4.1 | 22.1 | 0 | 2018-04-11 | -2 | 20 | 0 | 2017-04-11 | 8 | 10 | 0 | 2016-04-11 | -1.9 | 19.9 | 0 | 15.46 | 0
2025-04-11 | 0 | 18 | 0 | 2024-04-11 | 5.9 | 12.1 | 0 | 2023-04-11 | 8.9 | 9.1 | 0 | 2022-04-11 | -1.3 | 19.3 | 0 | 2021-04-11 | 10.5 | 7.5 | 0 | 2020-04-11 | -1 | 19 | 0 | 2019-04-11 | -5 | 23 | 0 | 2018-04-11 | -2.6 | 20.6 | 0 | 2017-04-11 | 6.2 | 11.8 | 0 | 2016-04-11 | -1.8 | 19.8 | 0 | 16.02 | 0
2025-04-11 | 0.1 | 17.9 | 0 | 2024-04-11 | 5.5 | 12.5 | 0 | 2023-04-11 | 9.1 | 8.9 | 0 | 2022-04-11 | -1.8 | 19.8 | 0 | 2021-04-11 | 8.9 | 9.1 | 0 | 2020-04-11 | -1.9 | 19.9 | 0 | 2019-04-11 | -4.3 | 22.3 | 0 | 2018-04-11 | -2.9 | 20.9 | 0 | 2017-04-11 | 5.6 | 12.4 | 0 | 2016-04-11 | -1.7 | 19.7 | 0 | 16.34 | 0
2025-04-11 | 0.1 | 17.9 | 0 | 2024-04-11 | 4.7 | 13.3 | 0 | 2023-04-11 | 8.9 | 9.1 | 0 | 2022-04-11 | -2.8 | 20.8 | 0 | 2021-04-11 | 8.1 | 9.9 | 0 | 2020-04-11 | -1.8 | 19.8 | 0 | 2019-04-11 | -3.1 | 21.1 | 0 | 2018-04-11 | -4 | 22 | 0 | 2017-04-11 | 5.4 | 12.6 | 0 | 2016-04-11 | -1.6 | 19.6 | 0 | 16.61 | 0
2025-04-11 | 0.2 | 17.8 | 0 | 2024-04-11 | 5.2 | 12.8 | 0 | 2023-04-11 | 8.8 | 9.2 | 0 | 2022-04-11 | -2.8 | 20.8 | 0 | 2021-04-11 | 7.5 | 10.5 | 0 | 2020-04-11 | -1.7 | 19.7 | 0 | 2019-04-11 | -3.3 | 21.3 | 0 | 2018-04-11 | -2.3 | 20.3 | 0 | 2017-04-11 | 5 | 13 | 0 | 2016-04-11 | -0.7 | 18.7 | 0 | 16.41 | 0
2025-04-11 | 0.4 | 17.6 | 0 | 2024-04-11 | 6.6 | 11.4 | 0 | 2023-04-11 | 9.5 | 8.5 | 0 | 2022-04-11 | 0.7 | 17.3 | 0 | 2021-04-11 | 8.7 | 9.3 | 0 | 2020-04-11 | -0.8 | 18.8 | 0 | 2019-04-11 | -2.4 | 20.4 | 0 | 2018-04-11 | -1.4 | 19.4 | 0 | 2017-04-11 | 5.6 | 12.4 | 0 | 2016-04-11 | -0.1 | 18.1 | 0 | 15.32 | 0
2025-04-11 | 0.8 | 17.2 | 0 | 2024-04-11 | 7.9 | 10.1 | 0 | 2023-04-11 | 9.7 | 8.3 | 0 | 2022-04-11 | 4 | 14 | 0 | 2021-04-11 | 10.5 | 7.5 | 0 | 2020-04-11 | 0.3 | 17.7 | 0 | 2019-04-11 | -1.6 | 19.6 | 0 | 2018-04-11 | -0.1 | 18.1 | 0 | 2017-04-11 | 5.4 | 12.6 | 0 | 2016-04-11 | 0.4 | 17.6 | 0 | 14.27 | 0
2025-04-11 | 1.2 | 16.8 | 0 | 2024-04-11 | 8.2 | 9.8 | 0 | 2023-04-11 | 12.1 | 5.9 | 0 | 2022-04-11 | 5.2 | 12.8 | 0 | 2021-04-11 | 12.8 | 5.2 | 0 | 2020-04-11 | 2.2 | 15.8 | 0 | 2019-04-11 | -0.5 | 18.5 | 0 | 2018-04-11 | 3.4 | 14.6 | 0 | 2017-04-11 | 4.8 | 13.2 | 0 | 2016-04-11 | 0.8 | 17.2 | 0 | 12.98 | 0
2025-04-11 | 1.6 | 16.4 | 0 | 2024-04-11 | 8.9 | 9.1 | 0 | 2023-04-11 | 13.1 | 4.9 | 0 | 2022-04-11 | 5.8 | 12.2 | 0 | 2021-04-11 | 14.4 | 3.6 | 0 | 2020-04-11 | 3.1 | 14.9 | 0 | 2019-04-11 | 1 | 17 | 0 | 2018-04-11 | 5.5 | 12.5 | 0 | 2017-04-11 | 5.4 | 12.6 | 0 | 2016-04-11 | 0.9 | 17.1 | 0 | 12.03 | 0
2025-04-11 | 2 | 16 | 0 | 2024-04-11 | 9.6 | 8.4 | 0 | 2023-04-11 | 14.8 | 3.2 | 0 | 2022-04-11 | 7.7 | 10.3 | 0 | 2021-04-11 | 15.7 | 2.3 | 0 | 2020-04-11 | 3.5 | 14.5 | 0 | 2019-04-11 | 1.7 | 16.3 | 0 | 2018-04-11 | 6.6 | 11.4 | 0 | 2017-04-11 | 5.9 | 12.1 | 0 | 2016-04-11 | 1.5 | 16.5 | 0 | 11.1 | 0
2025-04-11 | 2.4 | 15.6 | 0 | 2024-04-11 | 10.1 | 7.9 | 0 | 2023-04-11 | 16.1 | 1.9 | 0 | 2022-04-11 | 9.3 | 8.7 | 0 | 2021-04-11 | 17.1 | 0.9 | 0 | 2020-04-11 | 4.5 | 13.5 | 0 | 2019-04-11 | 2.9 | 15.1 | 0 | 2018-04-11 | 6.3 | 11.7 | 0 | 2017-04-11 | 6.5 | 11.5 | 0 | 2016-04-11 | 2.1 | 15.9 | 0 | 10.27 | 0
2025-04-11 | 2.8 | 15.2 | 0 | 2024-04-11 | 10.2 | 7.8 | 0 | 2023-04-11 | 16.7 | 1.3 | 0 | 2022-04-11 | 10.5 | 7.5 | 0 | 2021-04-11 | 18.4 | 0 | 0.4 | 2020-04-11 | 6.1 | 11.9 | 0 | 2019-04-11 | 3.9 | 14.1 | 0 | 2018-04-11 | 5.9 | 12.1 | 0 | 2017-04-11 | 7.5 | 10.5 | 0 | 2016-04-11 | 4.8 | 13.2 | 0 | 9.36 | 0.04
2025-04-11 | 3.4 | 14.6 | 0 | 2024-04-11 | 10.3 | 7.7 | 0 | 2023-04-11 | 17.2 | 0.8 | 0 | 2022-04-11 | 10.6 | 7.4 | 0 | 2021-04-11 | 19.7 | 0 | 1.7 | 2020-04-11 | 6.7 | 11.3 | 0 | 2019-04-11 | 4.2 | 13.8 | 0 | 2018-04-11 | 6.5 | 11.5 | 0 | 2017-04-11 | 8.2 | 9.8 | 0 | 2016-04-11 | 5.4 | 12.6 | 0 | 8.95 | 0.17
2025-04-11 | 3.7 | 14.3 | 0 | 2024-04-11 | 11 | 7 | 0 | 2023-04-11 | 17.8 | 0.2 | 0 | 2022-04-11 | 11.6 | 6.4 | 0 | 2021-04-11 | 18.6 | 0 | 0.6 | 2020-04-11 | 6.7 | 11.3 | 0 | 2019-04-11 | 4.9 | 13.1 | 0 | 2018-04-11 | 6.1 | 11.9 | 0 | 2017-04-11 | 8.8 | 9.2 | 0 | 2016-04-11 | 6.3 | 11.7 | 0 | 8.51 | 0.06
2025-04-11 | 4.2 | 13.8 | 0 | 2024-04-11 | 11.8 | 6.2 | 0 | 2023-04-11 | 18 | 0 | 0 | 2022-04-11 | 12 | 6 | 0 | 2021-04-11 | 17.1 | 0.9 | 0 | 2020-04-11 | 7.7 | 10.3 | 0 | 2019-04-11 | 5.1 | 12.9 | 0 | 2018-04-11 | 6.4 | 11.6 | 0 | 2017-04-11 | 8.8 | 9.2 | 0 | 2016-04-11 | 6.8 | 11.2 | 0 | 8.21 | 0
2025-04-11 | 4.2 | 13.8 | 0 | 2024-04-11 | 11.9 | 6.1 | 0 | 2023-04-11 | 20.1 | 0 | 2.1 | 2022-04-11 | 11.9 | 6.1 | 0 | 2021-04-11 | 16.4 | 1.6 | 0 | 2020-04-11 | 7 | 11 | 0 | 2019-04-11 | 4.8 | 13.2 | 0 | 2018-04-11 | 2.6 | 15.4 | 0 | 2017-04-11 | 8.2 | 9.8 | 0 | 2016-04-11 | 7.2 | 10.8 | 0 | 8.78 | 0.21
2025-04-11 | 3.9 | 14.1 | 0 | 2024-04-11 | 11.9 | 6.1 | 0 | 2023-04-11 | 18.1 | 0 | 0.1 | 2022-04-11 | 11.2 | 6.8 | 0 | 2021-04-11 | 15.3 | 2.7 | 0 | 2020-04-11 | 6.4 | 11.6 | 0 | 2019-04-11 | 3.9 | 14.1 | 0 | 2018-04-11 | 1.8 | 16.2 | 0 | 2017-04-11 | 7.7 | 10.3 | 0 | 2016-04-11 | 7.4 | 10.6 | 0 | 9.25 | 0.01
2025-04-11 | 3.2 | 14.8 | 0 | 2024-04-11 | 12 | 6 | 0 | 2023-04-11 | 16.4 | 1.6 | 0 | 2022-04-11 | 10.1 | 7.9 | 0 | 2021-04-11 | 14.6 | 3.4 | 0 | 2020-04-11 | 3.8 | 14.2 | 0 | 2019-04-11 | 2.7 | 15.3 | 0 | 2018-04-11 | 1.3 | 16.7 | 0 | 2017-04-11 | 6.9 | 11.1 | 0 | 2016-04-11 | 7.6 | 10.4 | 0 | 10.14 | 0
2025-04-11 | 3.1 | 14.9 | 0 | 2024-04-11 | 12.6 | 5.4 | 0 | 2023-04-11 | 14.1 | 3.9 | 0 | 2022-04-11 | 9.6 | 8.4 | 0 | 2021-04-11 | 13.8 | 4.2 | 0 | 2020-04-11 | 3.2 | 14.8 | 0 | 2019-04-11 | 1.8 | 16.2 | 0 | 2018-04-11 | 1.3 | 16.7 | 0 | 2017-04-11 | 6.8 | 11.2 | 0 | 2016-04-11 | 7.6 | 10.4 | 0 | 10.61 | 0
2025-04-11 | 2.9 | 15.1 | 0 | 2024-04-11 | 12.8 | 5.2 | 0 | 2023-04-11 | 12.6 | 5.4 | 0 | 2022-04-11 | 9.7 | 8.3 | 0 | 2021-04-11 | 12.7 | 5.3 | 0 | 2020-04-11 | 2.8 | 15.2 | 0 | 2019-04-11 | 2.2 | 15.8 | 0 | 2018-04-11 | 1.1 | 16.9 | 0 | 2017-04-11 | 6.6 | 11.4 | 0 | 2016-04-11 | 7.7 | 10.3 | 0 | 10.89 | 0
2025-04-11 | 3.5 | 14.5 | 0 | 2024-04-11 | 11.9 | 6.1 | 0 | 2023-04-11 | 11.9 | 6.1 | 0 | 2022-04-11 | 8.5 | 9.5 | 0 | 2021-04-11 | 12.3 | 5.7 | 0 | 2020-04-11 | 1.7 | 16.3 | 0 | 2019-04-11 | 2.2 | 15.8 | 0 | 2018-04-11 | 1 | 17 | 0 | 2017-04-11 | 6.4 | 11.6 | 0 | 2016-04-11 | 7.7 | 10.3 | 0 | 11.29 | 0
2025-04-11 | 3.5 | 14.5 | 0 | 2024-04-11 | 11.7 | 6.3 | 0 | 2023-04-11 | 10.6 | 7.4 | 0 | 2022-04-11 | 8.8 | 9.2 | 0 | 2021-04-11 | 12 | 6 | 0 | 2020-04-11 | 0.9 | 17.1 | 0 | 2019-04-11 | 2 | 16 | 0 | 2018-04-11 | 0.4 | 17.6 | 0 | 2017-04-11 | 6 | 12 | 0 | 2016-04-11 | 7.5 | 10.5 | 0 | 11.66 | 0
2025-04-12 | 3.3 | 14.7 | 0 | 2024-04-12 | 11.4 | 6.6 | 0 | 2023-04-12 | 10.4 | 7.6 | 0 | 2022-04-12 | 8.1 | 9.9 | 0 | 2021-04-12 | 11.3 | 6.7 | 0 | 2020-04-12 | 0.5 | 17.5 | 0 | 2019-04-12 | 2.2 | 15.8 | 0 | 2018-04-12 | 0.8 | 17.2 | 0 | 2017-04-12 | 5.8 | 12.2 | 0 | 2016-04-12 | 4.2 | 13.8 | 0 | 12.2 | 0
2025-04-12 | 2.8 | 15.2 | 0 | 2024-04-12 | 11.4 | 6.6 | 0 | 2023-04-12 | 9.8 | 8.2 | 0 | 2022-04-12 | 6.8 | 11.2 | 0 | 2021-04-12 | 10.6 | 7.4 | 0 | 2020-04-12 | -0.1 | 18.1 | 0 | 2019-04-12 | 2 | 16 | 0 | 2018-04-12 | 0.7 | 17.3 | 0 | 2017-04-12 | 5.7 | 12.3 | 0 | 2016-04-12 | 3.4 | 14.6 | 0 | 12.69 | 0
2025-04-12 | 3.5 | 14.5 | 0 | 2024-04-12 | 11.2 | 6.8 | 0 | 2023-04-12 | 8.8 | 9.2 | 0 | 2022-04-12 | 6.8 | 11.2 | 0 | 2021-04-12 | 10.3 | 7.7 | 0 | 2020-04-12 | -0.5 | 18.5 | 0 | 2019-04-12 | 1.8 | 16.2 | 0 | 2018-04-12 | -0.4 | 18.4 | 0 | 2017-04-12 | 5.5 | 12.5 | 0 | 2016-04-12 | 3 | 15 | 0 | 13 | 0
2025-04-12 | 3.4 | 14.6 | 0 | 2024-04-12 | 11.1 | 6.9 | 0 | 2023-04-12 | 8.7 | 9.3 | 0 | 2022-04-12 | 6.7 | 11.3 | 0 | 2021-04-12 | 9 | 9 | 0 | 2020-04-12 | -0.8 | 18.8 | 0 | 2019-04-12 | 1.7 | 16.3 | 0 | 2018-04-12 | 0.5 | 17.5 | 0 | 2017-04-12 | 5.3 | 12.7 | 0 | 2016-04-12 | 2.5 | 15.5 | 0 | 13.19 | 0
2025-04-12 | 3.3 | 14.7 | 0 | 2024-04-12 | 11.7 | 6.3 | 0 | 2023-04-12 | 8.1 | 9.9 | 0 | 2022-04-12 | 6.7 | 11.3 | 0 | 2021-04-12 | 9.2 | 8.8 | 0 | 2020-04-12 | -0.8 | 18.8 | 0 | 2019-04-12 | 1.9 | 16.1 | 0 | 2018-04-12 | 0.2 | 17.8 | 0 | 2017-04-12 | 5.2 | 12.8 | 0 | 2016-04-12 | 1.4 | 16.6 | 0 | 13.31 | 0
2025-04-12 | 3.4 | 14.6 | 0 | 2024-04-12 | 12.4 | 5.6 | 0 | 2023-04-12 | 7.8 | 10.2 | 0 | 2022-04-12 | 6 | 12 | 0 | 2021-04-12 | 8.6 | 9.4 | 0 | 2020-04-12 | -1.9 | 19.9 | 0 | 2019-04-12 | 1.6 | 16.4 | 0 | 2018-04-12 | -0.8 | 18.8 | 0 | 2017-04-12 | 5.7 | 12.3 | 0 | 2016-04-12 | 0 | 18 | 0 | 13.72 | 0
2025-04-12 | 3.3 | 14.7 | 0 | 2024-04-12 | 12.5 | 5.5 | 0 | 2023-04-12 | 7.7 | 10.3 | 0 | 2022-04-12 | 7.1 | 10.9 | 0 | 2021-04-12 | 9.1 | 8.9 | 0 | 2020-04-12 | 0.4 | 17.6 | 0 | 2019-04-12 | 1.7 | 16.3 | 0 | 2018-04-12 | 0 | 18 | 0 | 2017-04-12 | 6.5 | 11.5 | 0 | 2016-04-12 | -0.2 | 18.2 | 0 | 13.19 | 0
2025-04-12 | 3.7 | 14.3 | 0 | 2024-04-12 | 13.3 | 4.7 | 0 | 2023-04-12 | 8 | 10 | 0 | 2022-04-12 | 7.2 | 10.8 | 0 | 2021-04-12 | 9.9 | 8.1 | 0 | 2020-04-12 | 2.5 | 15.5 | 0 | 2019-04-12 | 2.5 | 15.5 | 0 | 2018-04-12 | 0.3 | 17.7 | 0 | 2017-04-12 | 6.7 | 11.3 | 0 | 2016-04-12 | 1.2 | 16.8 | 0 | 12.47 | 0
2025-04-12 | 4.3 | 13.7 | 0 | 2024-04-12 | 13.3 | 4.7 | 0 | 2023-04-12 | 9.3 | 8.7 | 0 | 2022-04-12 | 9.5 | 8.5 | 0 | 2021-04-12 | 12 | 6 | 0 | 2020-04-12 | 5.2 | 12.8 | 0 | 2019-04-12 | 3.8 | 14.2 | 0 | 2018-04-12 | 1.5 | 16.5 | 0 | 2017-04-12 | 6.8 | 11.2 | 0 | 2016-04-12 | 2.2 | 15.8 | 0 | 11.21 | 0
2025-04-12 | 5.4 | 12.6 | 0 | 2024-04-12 | 14.7 | 3.3 | 0 | 2023-04-12 | 11 | 7 | 0 | 2022-04-12 | 10.8 | 7.2 | 0 | 2021-04-12 | 13.7 | 4.3 | 0 | 2020-04-12 | 8.7 | 9.3 | 0 | 2019-04-12 | 4.6 | 13.4 | 0 | 2018-04-12 | 3.4 | 14.6 | 0 | 2017-04-12 | 7.4 | 10.6 | 0 | 2016-04-12 | 3.9 | 14.1 | 0 | 9.64 | 0
2025-04-12 | 6.5 | 11.5 | 0 | 2024-04-12 | 15.5 | 2.5 | 0 | 2023-04-12 | 12.2 | 5.8 | 0 | 2022-04-12 | 13.3 | 4.7 | 0 | 2021-04-12 | 15.1 | 2.9 | 0 | 2020-04-12 | 8.4 | 9.6 | 0 | 2019-04-12 | 7.2 | 10.8 | 0 | 2018-04-12 | 5 | 13 | 0 | 2017-04-12 | 7.3 | 10.7 | 0 | 2016-04-12 | 4.6 | 13.4 | 0 | 8.49 | 0
2025-04-12 | 7.8 | 10.2 | 0 | 2024-04-12 | 15 | 3 | 0 | 2023-04-12 | 14.3 | 3.7 | 0 | 2022-04-12 | 13.4 | 4.6 | 0 | 2021-04-12 | 16.2 | 1.8 | 0 | 2020-04-12 | 8.2 | 9.8 | 0 | 2019-04-12 | 9.2 | 8.8 | 0 | 2018-04-12 | 6 | 12 | 0 | 2017-04-12 | 8.7 | 9.3 | 0 | 2016-04-12 | 5.2 | 12.8 | 0 | 7.6 | 0
2025-04-12 | 8.6 | 9.4 | 0 | 2024-04-12 | 12.6 | 5.4 | 0 | 2023-04-12 | 14.3 | 3.7 | 0 | 2022-04-12 | 14.5 | 3.5 | 0 | 2021-04-12 | 16.8 | 1.2 | 0 | 2020-04-12 | 9.4 | 8.6 | 0 | 2019-04-12 | 10.7 | 7.3 | 0 | 2018-04-12 | 7.2 | 10.8 | 0 | 2017-04-12 | 8.9 | 9.1 | 0 | 2016-04-12 | 4.2 | 13.8 | 0 | 7.28 | 0
2025-04-12 | 9.1 | 8.9 | 0 | 2024-04-12 | 11.4 | 6.6 | 0 | 2023-04-12 | 16.2 | 1.8 | 0 | 2022-04-12 | 15.5 | 2.5 | 0 | 2021-04-12 | 16.1 | 1.9 | 0 | 2020-04-12 | 9.8 | 8.2 | 0 | 2019-04-12 | 11.3 | 6.7 | 0 | 2018-04-12 | 6.6 | 11.4 | 0 | 2017-04-12 | 7.4 | 10.6 | 0 | 2016-04-12 | 6 | 12 | 0 | 7.06 | 0
2025-04-12 | 9.3 | 8.7 | 0 | 2024-04-12 | 11.2 | 6.8 | 0 | 2023-04-12 | 16.6 | 1.4 | 0 | 2022-04-12 | 16.2 | 1.8 | 0 | 2021-04-12 | 17.6 | 0.4 | 0 | 2020-04-12 | 10.7 | 7.3 | 0 | 2019-04-12 | 11.2 | 6.8 | 0 | 2018-04-12 | 5.5 | 12.5 | 0 | 2017-04-12 | 8.1 | 9.9 | 0 | 2016-04-12 | 6.5 | 11.5 | 0 | 6.71 | 0
2025-04-12 | 9.3 | 8.7 | 0 | 2024-04-12 | 11 | 7 | 0 | 2023-04-12 | 18.3 | 0 | 0.3 | 2022-04-12 | 17.1 | 0.9 | 0 | 2021-04-12 | 17.1 | 0.9 | 0 | 2020-04-12 | 11.8 | 6.2 | 0 | 2019-04-12 | 8.8 | 9.2 | 0 | 2018-04-12 | 5.1 | 12.9 | 0 | 2017-04-12 | 7.2 | 10.8 | 0 | 2016-04-12 | 5.2 | 12.8 | 0 | 6.94 | 0.03
2025-04-12 | 10.1 | 7.9 | 0 | 2024-04-12 | 10.8 | 7.2 | 0 | 2023-04-12 | 18.6 | 0 | 0.6 | 2022-04-12 | 16.7 | 1.3 | 0 | 2021-04-12 | 17.6 | 0.4 | 0 | 2020-04-12 | 11.9 | 6.1 | 0 | 2019-04-12 | 7.2 | 10.8 | 0 | 2018-04-12 | 5 | 13 | 0 | 2017-04-12 | 8.2 | 9.8 | 0 | 2016-04-12 | 5.3 | 12.7 | 0 | 6.92 | 0.06
2025-04-12 | 10.9 | 7.1 | 0 | 2024-04-12 | 10.8 | 7.2 | 0 | 2023-04-12 | 18.9 | 0 | 0.9 | 2022-04-12 | 17.2 | 0.8 | 0 | 2021-04-12 | 17 | 1 | 0 | 2020-04-12 | 11.7 | 6.3 | 0 | 2019-04-12 | 6.8 | 11.2 | 0 | 2018-04-12 | 4.9 | 13.1 | 0 | 2017-04-12 | 7.1 | 10.9 | 0 | 2016-04-12 | 5.5 | 12.5 | 0 | 7.01 | 0.09
2025-04-12 | 10.2 | 7.8 | 0 | 2024-04-12 | 10 | 8 | 0 | 2023-04-12 | 18.2 | 0 | 0.2 | 2022-04-12 | 15.6 | 2.4 | 0 | 2021-04-12 | 15.4 | 2.6 | 0 | 2020-04-12 | 10.9 | 7.1 | 0 | 2019-04-12 | 7.1 | 10.9 | 0 | 2018-04-12 | 4.6 | 13.4 | 0 | 2017-04-12 | 6.4 | 11.6 | 0 | 2016-04-12 | 4 | 14 | 0 | 7.78 | 0.02
2025-04-12 | 8.4 | 9.6 | 0 | 2024-04-12 | 9.4 | 8.6 | 0 | 2023-04-12 | 14.6 | 3.4 | 0 | 2022-04-12 | 14.2 | 3.8 | 0 | 2021-04-12 | 14.2 | 3.8 | 0 | 2020-04-12 | 9.9 | 8.1 | 0 | 2019-04-12 | 6.9 | 11.1 | 0 | 2018-04-12 | 4.3 | 13.7 | 0 | 2017-04-12 | 6.1 | 11.9 | 0 | 2016-04-12 | 2.5 | 15.5 | 0 | 8.95 | 0
2025-04-12 | 5.8 | 12.2 | 0 | 2024-04-12 | 9.1 | 8.9 | 0 | 2023-04-12 | 12.8 | 5.2 | 0 | 2022-04-12 | 12.4 | 5.6 | 0 | 2021-04-12 | 13.5 | 4.5 | 0 | 2020-04-12 | 9.7 | 8.3 | 0 | 2019-04-12 | 7 | 11 | 0 | 2018-04-12 | 4.2 | 13.8 | 0 | 2017-04-12 | 4.8 | 13.2 | 0 | 2016-04-12 | 1.4 | 16.6 | 0 | 9.93 | 0
2025-04-12 | 4.4 | 13.6 | 0 | 2024-04-12 | 8.6 | 9.4 | 0 | 2023-04-12 | 12.8 | 5.2 | 0 | 2022-04-12 | 11.5 | 6.5 | 0 | 2021-04-12 | 12.8 | 5.2 | 0 | 2020-04-12 | 9.6 | 8.4 | 0 | 2019-04-12 | 6.4 | 11.6 | 0 | 2018-04-12 | 3.9 | 14.1 | 0 | 2017-04-12 | 4 | 14 | 0 | 2016-04-12 | 0.2 | 17.8 | 0 | 10.58 | 0
2025-04-12 | 4.6 | 13.4 | 0 | 2024-04-12 | 8.1 | 9.9 | 0 | 2023-04-12 | 12.2 | 5.8 | 0 | 2022-04-12 | 10.9 | 7.1 | 0 | 2021-04-12 | 12 | 6 | 0 | 2020-04-12 | 9.2 | 8.8 | 0 | 2019-04-12 | 5.1 | 12.9 | 0 | 2018-04-12 | 3.4 | 14.6 | 0 | 2017-04-12 | 3.8 | 14.2 | 0 | 2016-04-12 | -1.8 | 19.8 | 0 | 11.25 | 0
2025-04-12 | 2 | 16 | 0 | 2024-04-12 | 7.2 | 10.8 | 0 | 2023-04-12 | 10.8 | 7.2 | 0 | 2022-04-12 | 8.3 | 9.7 | 0 | 2021-04-12 | 11.4 | 6.6 | 0 | 2020-04-12 | 9 | 9 | 0 | 2019-04-12 | 4.7 | 13.3 | 0 | 2018-04-12 | 2.9 | 15.1 | 0 | 2017-04-12 | 3.8 | 14.2 | 0 | 2016-04-12 | -1.2 | 19.2 | 0 | 12.11 | 0
2025-04-13 | 0.7 | 17.3 | 0 | 2024-04-13 | 6.8 | 11.2 | 0 | 2023-04-13 | 8.9 | 9.1 | 0 | 2022-04-13 | 8.5 | 9.5 | 0 | 2021-04-13 | 11.1 | 6.9 | 0 | 2020-04-13 | 8.7 | 9.3 | 0 | 2019-04-13 | 10.8 | 7.2 | 0 | 2018-04-13 | 2.9 | 15.1 | 0 | 2017-04-13 | 3.7 | 14.3 | 0 | 2016-04-13 | -2.7 | 20.7 | 0 | 12.06 | 0
2025-04-13 | 1.2 | 16.8 | 0 | 2024-04-13 | 6.3 | 11.7 | 0 | 2023-04-13 | 9 | 9 | 0 | 2022-04-13 | 8.1 | 9.9 | 0 | 2021-04-13 | 10.8 | 7.2 | 0 | 2020-04-13 | 8.9 | 9.1 | 0 | 2019-04-13 | 5.4 | 12.6 | 0 | 2018-04-13 | 2.3 | 15.7 | 0 | 2017-04-13 | 3.6 | 14.4 | 0 | 2016-04-13 | -2.9 | 20.9 | 0 | 12.73 | 0
2025-04-13 | 1.7 | 16.3 | 0 | 2024-04-13 | 5.7 | 12.3 | 0 | 2023-04-13 | 7.3 | 10.7 | 0 | 2022-04-13 | 7.4 | 10.6 | 0 | 2021-04-13 | 10.6 | 7.4 | 0 | 2020-04-13 | 8.9 | 9.1 | 0 | 2019-04-13 | 7.4 | 10.6 | 0 | 2018-04-13 | 2 | 16 | 0 | 2017-04-13 | 3 | 15 | 0 | 2016-04-13 | -2.7 | 20.7 | 0 | 12.87 | 0
2025-04-13 | -0.8 | 18.8 | 0 | 2024-04-13 | 5.4 | 12.6 | 0 | 2023-04-13 | 7.7 | 10.3 | 0 | 2022-04-13 | 7.7 | 10.3 | 0 | 2021-04-13 | 10 | 8 | 0 | 2020-04-13 | 7.9 | 10.1 | 0 | 2019-04-13 | 7.9 | 10.1 | 0 | 2018-04-13 | 1.9 | 16.1 | 0 | 2017-04-13 | 2.1 | 15.9 | 0 | 2016-04-13 | -4.2 | 22.2 | 0 | 13.44 | 0
2025-04-13 | 0.9 | 17.1 | 0 | 2024-04-13 | 4.5 | 13.5 | 0 | 2023-04-13 | 7.6 | 10.4 | 0 | 2022-04-13 | 6.9 | 11.1 | 0 | 2021-04-13 | 9.5 | 8.5 | 0 | 2020-04-13 | 7.3 | 10.7 | 0 | 2019-04-13 | 7.7 | 10.3 | 0 | 2018-04-13 | 1.8 | 16.2 | 0 | 2017-04-13 | 1.7 | 16.3 | 0 | 2016-04-13 | -4.3 | 22.3 | 0 | 13.64 | 0
2025-04-13 | 1.3 | 16.7 | 0 | 2024-04-13 | 4.2 | 13.8 | 0 | 2023-04-13 | 4 | 14 | 0 | 2022-04-13 | 6.7 | 11.3 | 0 | 2021-04-13 | 8.9 | 9.1 | 0 | 2020-04-13 | 6.4 | 11.6 | 0 | 2019-04-13 | 7.6 | 10.4 | 0 | 2018-04-13 | 1.4 | 16.6 | 0 | 2017-04-13 | 1.3 | 16.7 | 0 | 2016-04-13 | -3.8 | 21.8 | 0 | 14.2 | 0
2025-04-13 | 0 | 18 | 0 | 2024-04-13 | 3.9 | 14.1 | 0 | 2023-04-13 | 6.1 | 11.9 | 0 | 2022-04-13 | 6.8 | 11.2 | 0 | 2021-04-13 | 8.6 | 9.4 | 0 | 2020-04-13 | 6.9 | 11.1 | 0 | 2019-04-13 | 5.8 | 12.2 | 0 | 2018-04-13 | 1.5 | 16.5 | 0 | 2017-04-13 | 1.3 | 16.7 | 0 | 2016-04-13 | -3.3 | 21.3 | 0 | 14.24 | 0
2025-04-13 | 3.4 | 14.6 | 0 | 2024-04-13 | 3.3 | 14.7 | 0 | 2023-04-13 | 9.4 | 8.6 | 0 | 2022-04-13 | 7.8 | 10.2 | 0 | 2021-04-13 | 8.7 | 9.3 | 0 | 2020-04-13 | 8.1 | 9.9 | 0 | 2019-04-13 | 8.6 | 9.4 | 0 | 2018-04-13 | 2.5 | 15.5 | 0 | 2017-04-13 | 2.6 | 15.4 | 0 | 2016-04-13 | -1.3 | 19.3 | 0 | 12.69 | 0
2025-04-13 | 6.3 | 11.7 | 0 | 2024-04-13 | 3.1 | 14.9 | 0 | 2023-04-13 | 13.5 | 4.5 | 0 | 2022-04-13 | 8.6 | 9.4 | 0 | 2021-04-13 | 10.2 | 7.8 | 0 | 2020-04-13 | 8.9 | 9.1 | 0 | 2019-04-13 | 9.8 | 8.2 | 0 | 2018-04-13 | 3.3 | 14.7 | 0 | 2017-04-13 | 4 | 14 | 0 | 2016-04-13 | -0.3 | 18.3 | 0 | 11.26 | 0
2025-04-13 | 8.8 | 9.2 | 0 | 2024-04-13 | 3.8 | 14.2 | 0 | 2023-04-13 | 17.4 | 0.6 | 0 | 2022-04-13 | 9.8 | 8.2 | 0 | 2021-04-13 | 11 | 7 | 0 | 2020-04-13 | 9.9 | 8.1 | 0 | 2019-04-13 | 11.3 | 6.7 | 0 | 2018-04-13 | 5 | 13 | 0 | 2017-04-13 | 5.9 | 12.1 | 0 | 2016-04-13 | 1.1 | 16.9 | 0 | 9.6 | 0
2025-04-13 | 9.7 | 8.3 | 0 | 2024-04-13 | 4 | 14 | 0 | 2023-04-13 | 21 | 0 | 3 | 2022-04-13 | 10.2 | 7.8 | 0 | 2021-04-13 | 13.3 | 4.7 | 0 | 2020-04-13 | 11.1 | 6.9 | 0 | 2019-04-13 | 12.2 | 5.8 | 0 | 2018-04-13 | 5.6 | 12.4 | 0 | 2017-04-13 | 7.7 | 10.3 | 0 | 2016-04-13 | 1.7 | 16.3 | 0 | 8.65 | 0.3
2025-04-13 | 11.9 | 6.1 | 0 | 2024-04-13 | 3.9 | 14.1 | 0 | 2023-04-13 | 24 | 0 | 6 | 2022-04-13 | 8.3 | 9.7 | 0 | 2021-04-13 | 14.6 | 3.4 | 0 | 2020-04-13 | 12.5 | 5.5 | 0 | 2019-04-13 | 13.4 | 4.6 | 0 | 2018-04-13 | 6.2 | 11.8 | 0 | 2017-04-13 | 9 | 9 | 0 | 2016-04-13 | 2.3 | 15.7 | 0 | 7.99 | 0.6
2025-04-13 | 13 | 5 | 0 | 2024-04-13 | 5.1 | 12.9 | 0 | 2023-04-13 | 26.8 | 0 | 8.8 | 2022-04-13 | 8.3 | 9.7 | 0 | 2021-04-13 | 16.4 | 1.6 | 0 | 2020-04-13 | 14.3 | 3.7 | 0 | 2019-04-13 | 14 | 4 | 0 | 2018-04-13 | 7.4 | 10.6 | 0 | 2017-04-13 | 10.4 | 7.6 | 0 | 2016-04-13 | 4.5 | 13.5 | 0 | 6.86 | 0.88
2025-04-13 | 13.9 | 4.1 | 0 | 2024-04-13 | 5.1 | 12.9 | 0 | 2023-04-13 | 27.2 | 0 | 9.2 | 2022-04-13 | 8.6 | 9.4 | 0 | 2021-04-13 | 16.5 | 1.5 | 0 | 2020-04-13 | 15 | 3 | 0 | 2019-04-13 | 15.1 | 2.9 | 0 | 2018-04-13 | 8.3 | 9.7 | 0 | 2017-04-13 | 11.4 | 6.6 | 0 | 2016-04-13 | 5.2 | 12.8 | 0 | 6.29 | 0.92
2025-04-13 | 14.9 | 3.1 | 0 | 2024-04-13 | 5.1 | 12.9 | 0 | 2023-04-13 | 28.2 | 0 | 10.2 | 2022-04-13 | 8.8 | 9.2 | 0 | 2021-04-13 | 16.9 | 1.1 | 0 | 2020-04-13 | 14.9 | 3.1 | 0 | 2019-04-13 | 15.3 | 2.7 | 0 | 2018-04-13 | 8.7 | 9.3 | 0 | 2017-04-13 | 12.7 | 5.3 | 0 | 2016-04-13 | 6.4 | 11.6 | 0 | 5.83 | 1.02
2025-04-13 | 15.8 | 2.2 | 0 | 2024-04-13 | 4.5 | 13.5 | 0 | 2023-04-13 | 29.6 | 0 | 11.6 | 2022-04-13 | 9.2 | 8.8 | 0 | 2021-04-13 | 17.3 | 0.7 | 0 | 2020-04-13 | 15.1 | 2.9 | 0 | 2019-04-13 | 14.9 | 3.1 | 0 | 2018-04-13 | 8.8 | 9.2 | 0 | 2017-04-13 | 12.7 | 5.3 | 0 | 2016-04-13 | 5.9 | 12.1 | 0 | 5.78 | 1.16
2025-04-13 | 15.9 | 2.1 | 0 | 2024-04-13 | 4.2 | 13.8 | 0 | 2023-04-13 | 29.5 | 0 | 11.5 | 2022-04-13 | 8.6 | 9.4 | 0 | 2021-04-13 | 17.5 | 0.5 | 0 | 2020-04-13 | 15.3 | 2.7 | 0 | 2019-04-13 | 14.8 | 3.2 | 0 | 2018-04-13 | 8.1 | 9.9 | 0 | 2017-04-13 | 13.4 | 4.6 | 0 | 2016-04-13 | 6.2 | 11.8 | 0 | 5.8 | 1.15
2025-04-13 | 16.1 | 1.9 | 0 | 2024-04-13 | 4 | 14 | 0 | 2023-04-13 | 29.4 | 0 | 11.4 | 2022-04-13 | 8.3 | 9.7 | 0 | 2021-04-13 | 17.2 | 0.8 | 0 | 2020-04-13 | 14.8 | 3.2 | 0 | 2019-04-13 | 14.4 | 3.6 | 0 | 2018-04-13 | 7.8 | 10.2 | 0 | 2017-04-13 | 12.8 | 5.2 | 0 | 2016-04-13 | 6 | 12 | 0 | 6.06 | 1.14
2025-04-13 | 14.8 | 3.2 | 0 | 2024-04-13 | 4.1 | 13.9 | 0 | 2023-04-13 | 26.1 | 0 | 8.1 | 2022-04-13 | 7.5 | 10.5 | 0 | 2021-04-13 | 16.3 | 1.7 | 0 | 2020-04-13 | 14.3 | 3.7 | 0 | 2019-04-13 | 9.8 | 8.2 | 0 | 2018-04-13 | 7.4 | 10.6 | 0 | 2017-04-13 | 11.5 | 6.5 | 0 | 2016-04-13 | 5.8 | 12.2 | 0 | 7.05 | 0.81
2025-04-13 | 10.9 | 7.1 | 0 | 2024-04-13 | 4.4 | 13.6 | 0 | 2023-04-13 | 23.5 | 0 | 5.5 | 2022-04-13 | 6.5 | 11.5 | 0 | 2021-04-13 | 15 | 3 | 0 | 2020-04-13 | 9 | 9 | 0 | 2019-04-13 | 7.6 | 10.4 | 0 | 2018-04-13 | 6.3 | 11.7 | 0 | 2017-04-13 | 8.8 | 9.2 | 0 | 2016-04-13 | 4.4 | 13.6 | 0 | 8.91 | 0.55
2025-04-13 | 10.6 | 7.4 | 0 | 2024-04-13 | 5 | 13 | 0 | 2023-04-13 | 22.1 | 0 | 4.1 | 2022-04-13 | 6.5 | 11.5 | 0 | 2021-04-13 | 13.9 | 4.1 | 0 | 2020-04-13 | 5.6 | 12.4 | 0 | 2019-04-13 | 6.1 | 11.9 | 0 | 2018-04-13 | 5.5 | 12.5 | 0 | 2017-04-13 | 7.6 | 10.4 | 0 | 2016-04-13 | 3 | 15 | 0 | 9.82 | 0.41
2025-04-13 | 7.6 | 10.4 | 0 | 2024-04-13 | 4.8 | 13.2 | 0 | 2023-04-13 | 20.1 | 0 | 2.1 | 2022-04-13 | 6.5 | 11.5 | 0 | 2021-04-13 | 12.8 | 5.2 | 0 | 2020-04-13 | 4.3 | 13.7 | 0 | 2019-04-13 | 4.7 | 13.3 | 0 | 2018-04-13 | 5.6 | 12.4 | 0 | 2017-04-13 | 6.9 | 11.1 | 0 | 2016-04-13 | 2.5 | 15.5 | 0 | 10.63 | 0.21
2025-04-13 | 7.9 | 10.1 | 0 | 2024-04-13 | 3.3 | 14.7 | 0 | 2023-04-13 | 16.8 | 1.2 | 0 | 2022-04-13 | 6.5 | 11.5 | 0 | 2021-04-13 | 12.2 | 5.8 | 0 | 2020-04-13 | 3.6 | 14.4 | 0 | 2019-04-13 | 3.5 | 14.5 | 0 | 2018-04-13 | 4.9 | 13.1 | 0 | 2017-04-13 | 7.4 | 10.6 | 0 | 2016-04-13 | 2.6 | 15.4 | 0 | 11.13 | 0
2025-04-13 | 4.3 | 13.7 | 0 | 2024-04-13 | 2.4 | 15.6 | 0 | 2023-04-13 | 16.2 | 1.8 | 0 | 2022-04-13 | 6.4 | 11.6 | 0 | 2021-04-13 | 10.6 | 7.4 | 0 | 2020-04-13 | 2.8 | 15.2 | 0 | 2019-04-13 | 1.3 | 16.7 | 0 | 2018-04-13 | 4 | 14 | 0 | 2017-04-13 | 5.3 | 12.7 | 0 | 2016-04-13 | 0.2 | 17.8 | 0 | 12.65 | 0
2025-04-14 | 4.7 | 13.3 | 0 | 2024-04-14 | 1.9 | 16.1 | 0 | 2023-04-14 | 15.9 | 2.1 | 0 | 2022-04-14 | 6.2 | 11.8 | 0 | 2021-04-14 | 10.6 | 7.4 | 0 | 2020-04-14 | 2.6 | 15.4 | 0 | 2019-04-14 | 1.8 | 16.2 | 0 | 2018-04-14 | 3.9 | 14.1 | 0 | 2017-04-14 | 4.3 | 13.7 | 0 | 2016-04-14 | 0.4 | 17.6 | 0 | 12.77 | 0
2025-04-14 | 3.4 | 14.6 | 0 | 2024-04-14 | 1.4 | 16.6 | 0 | 2023-04-14 | 15 | 3 | 0 | 2022-04-14 | 6.2 | 11.8 | 0 | 2021-04-14 | 10.8 | 7.2 | 0 | 2020-04-14 | 2.5 | 15.5 | 0 | 2019-04-14 | 1 | 17 | 0 | 2018-04-14 | 3.5 | 14.5 | 0 | 2017-04-14 | 3.9 | 14.1 | 0 | 2016-04-14 | -1.1 | 19.1 | 0 | 13.34 | 0
2025-04-14 | 1.5 | 16.5 | 0 | 2024-04-14 | 1.2 | 16.8 | 0 | 2023-04-14 | 14.3 | 3.7 | 0 | 2022-04-14 | 6.2 | 11.8 | 0 | 2021-04-14 | 10.7 | 7.3 | 0 | 2020-04-14 | 2.1 | 15.9 | 0 | 2019-04-14 | 0.4 | 17.6 | 0 | 2018-04-14 | 3.2 | 14.8 | 0 | 2017-04-14 | 3 | 15 | 0 | 2016-04-14 | -2.5 | 20.5 | 0 | 13.99 | 0
2025-04-14 | 1.6 | 16.4 | 0 | 2024-04-14 | 0.9 | 17.1 | 0 | 2023-04-14 | 14.2 | 3.8 | 0 | 2022-04-14 | 6.1 | 11.9 | 0 | 2021-04-14 | 10.9 | 7.1 | 0 | 2020-04-14 | 1.5 | 16.5 | 0 | 2019-04-14 | 1.8 | 16.2 | 0 | 2018-04-14 | 2.7 | 15.3 | 0 | 2017-04-14 | 1.6 | 16.4 | 0 | 2016-04-14 | -3 | 21 | 0 | 14.17 | 0
2025-04-14 | 1.7 | 16.3 | 0 | 2024-04-14 | 1.1 | 16.9 | 0 | 2023-04-14 | 12.6 | 5.4 | 0 | 2022-04-14 | 6.3 | 11.7 | 0 | 2021-04-14 | 10.6 | 7.4 | 0 | 2020-04-14 | 0.9 | 17.1 | 0 | 2019-04-14 | 0 | 18 | 0 | 2018-04-14 | 2.1 | 15.9 | 0 | 2017-04-14 | 1.8 | 16.2 | 0 | 2016-04-14 | -3.1 | 21.1 | 0 | 14.6 | 0
2025-04-14 | 0.4 | 17.6 | 0 | 2024-04-14 | 0.8 | 17.2 | 0 | 2023-04-14 | 11.4 | 6.6 | 0 | 2022-04-14 | 6.3 | 11.7 | 0 | 2021-04-14 | 9.6 | 8.4 | 0 | 2020-04-14 | 0.9 | 17.1 | 0 | 2019-04-14 | -1.1 | 19.1 | 0 | 2018-04-14 | 1.5 | 16.5 | 0 | 2017-04-14 | -0.4 | 18.4 | 0 | 2016-04-14 | -4.5 | 22.5 | 0 | 15.51 | 0
2025-04-14 | 0 | 18 | 0 | 2024-04-14 | 1 | 17 | 0 | 2023-04-14 | 11.2 | 6.8 | 0 | 2022-04-14 | 6.4 | 11.6 | 0 | 2021-04-14 | 8.5 | 9.5 | 0 | 2020-04-14 | 1 | 17 | 0 | 2019-04-14 | 0 | 18 | 0 | 2018-04-14 | 0.1 | 17.9 | 0 | 2017-04-14 | 1.8 | 16.2 | 0 | 2016-04-14 | -2.5 | 20.5 | 0 | 15.25 | 0
2025-04-14 | 4.4 | 13.6 | 0 | 2024-04-14 | 3.2 | 14.8 | 0 | 2023-04-14 | 12.8 | 5.2 | 0 | 2022-04-14 | 6.6 | 11.4 | 0 | 2021-04-14 | 9.7 | 8.3 | 0 | 2020-04-14 | 2.2 | 15.8 | 0 | 2019-04-14 | 2.5 | 15.5 | 0 | 2018-04-14 | -1.2 | 19.2 | 0 | 2017-04-14 | 4.5 | 13.5 | 0 | 2016-04-14 | 1 | 17 | 0 | 13.43 | 0
2025-04-14 | 7.1 | 10.9 | 0 | 2024-04-14 | 5.4 | 12.6 | 0 | 2023-04-14 | 14.2 | 3.8 | 0 | 2022-04-14 | 6.6 | 11.4 | 0 | 2021-04-14 | 11.6 | 6.4 | 0 | 2020-04-14 | 3.6 | 14.4 | 0 | 2019-04-14 | 4.1 | 13.9 | 0 | 2018-04-14 | -1.9 | 19.9 | 0 | 2017-04-14 | 7.4 | 10.6 | 0 | 2016-04-14 | 3 | 15 | 0 | 11.89 | 0
2025-04-14 | 10.7 | 7.3 | 0 | 2024-04-14 | 7.1 | 10.9 | 0 | 2023-04-14 | 15.7 | 2.3 | 0 | 2022-04-14 | 7.2 | 10.8 | 0 | 2021-04-14 | 12.2 | 5.8 | 0 | 2020-04-14 | 3 | 15 | 0 | 2019-04-14 | 5.1 | 12.9 | 0 | 2018-04-14 | -2.4 | 20.4 | 0 | 2017-04-14 | 9.4 | 8.6 | 0 | 2016-04-14 | 4.8 | 13.2 | 0 | 10.72 | 0
2025-04-14 | 13.1 | 4.9 | 0 | 2024-04-14 | 8.1 | 9.9 | 0 | 2023-04-14 | 17.7 | 0.3 | 0 | 2022-04-14 | 7.6 | 10.4 | 0 | 2021-04-14 | 13.9 | 4.1 | 0 | 2020-04-14 | 3.3 | 14.7 | 0 | 2019-04-14 | 5.4 | 12.6 | 0 | 2018-04-14 | -2.2 | 20.2 | 0 | 2017-04-14 | 11.4 | 6.6 | 0 | 2016-04-14 | 6.3 | 11.7 | 0 | 9.54 | 0
2025-04-14 | 14 | 4 | 0 | 2024-04-14 | 8.1 | 9.9 | 0 | 2023-04-14 | 19.4 | 0 | 1.4 | 2022-04-14 | 9.2 | 8.8 | 0 | 2021-04-14 | 13.9 | 4.1 | 0 | 2020-04-14 | 4.1 | 13.9 | 0 | 2019-04-14 | 6.9 | 11.1 | 0 | 2018-04-14 | -3.8 | 21.8 | 0 | 2017-04-14 | 11.9 | 6.1 | 0 | 2016-04-14 | 7.9 | 10.1 | 0 | 8.98 | 0.14
2025-04-14 | 14.9 | 3.1 | 0 | 2024-04-14 | 8 | 10 | 0 | 2023-04-14 | 20.7 | 0 | 2.7 | 2022-04-14 | 10 | 8 | 0 | 2021-04-14 | 15.5 | 2.5 | 0 | 2020-04-14 | 6.2 | 11.8 | 0 | 2019-04-14 | 7 | 11 | 0 | 2018-04-14 | -3.3 | 21.3 | 0 | 2017-04-14 | 13.1 | 4.9 | 0 | 2016-04-14 | 8.9 | 9.1 | 0 | 8.17 | 0.27
2025-04-14 | 15.6 | 2.4 | 0 | 2024-04-14 | 7.8 | 10.2 | 0 | 2023-04-14 | 20.6 | 0 | 2.6 | 2022-04-14 | 12.7 | 5.3 | 0 | 2021-04-14 | 10.9 | 7.1 | 0 | 2020-04-14 | 5.5 | 12.5 | 0 | 2019-04-14 | 6.3 | 11.7 | 0 | 2018-04-14 | -2.5 | 20.5 | 0 | 2017-04-14 | 13.9 | 4.1 | 0 | 2016-04-14 | 10 | 8 | 0 | 8.18 | 0.26
2025-04-14 | 17.1 | 0.9 | 0 | 2024-04-14 | 7.6 | 10.4 | 0 | 2023-04-14 | 21.3 | 0 | 3.3 | 2022-04-14 | 13.2 | 4.8 | 0 | 2021-04-14 | 11.8 | 6.2 | 0 | 2020-04-14 | 6.3 | 11.7 | 0 | 2019-04-14 | 5.3 | 12.7 | 0 | 2018-04-14 | -1.8 | 19.8 | 0 | 2017-04-14 | 14 | 4 | 0 | 2016-04-14 | 10.3 | 7.7 | 0 | 7.82 | 0.33
2025-04-14 | 16.2 | 1.8 | 0 | 2024-04-14 | 7.4 | 10.6 | 0 | 2023-04-14 | 21.9 | 0 | 3.9 | 2022-04-14 | 15.2 | 2.8 | 0 | 2021-04-14 | 15.1 | 2.9 | 0 | 2020-04-14 | 6 | 12 | 0 | 2019-04-14 | 3.4 | 14.6 | 0 | 2018-04-14 | -2.5 | 20.5 | 0 | 2017-04-14 | 14.9 | 3.1 | 0 | 2016-04-14 | 10.3 | 7.7 | 0 | 7.6 | 0.39
2025-04-14 | 15.7 | 2.3 | 0 | 2024-04-14 | 7.7 | 10.3 | 0 | 2023-04-14 | 21.3 | 0 | 3.3 | 2022-04-14 | 12.3 | 5.7 | 0 | 2021-04-14 | 14.3 | 3.7 | 0 | 2020-04-14 | 6.4 | 11.6 | 0 | 2019-04-14 | 2.5 | 15.5 | 0 | 2018-04-14 | -2.8 | 20.8 | 0 | 2017-04-14 | 15.4 | 2.6 | 0 | 2016-04-14 | 10.3 | 7.7 | 0 | 8.02 | 0.33
2025-04-14 | 15.2 | 2.8 | 0 | 2024-04-14 | 7.2 | 10.8 | 0 | 2023-04-14 | 21.4 | 0 | 3.4 | 2022-04-14 | 13.4 | 4.6 | 0 | 2021-04-14 | 14.6 | 3.4 | 0 | 2020-04-14 | 6 | 12 | 0 | 2019-04-14 | 2.2 | 15.8 | 0 | 2018-04-14 | -3.3 | 21.3 | 0 | 2017-04-14 | 14.5 | 3.5 | 0 | 2016-04-14 | 10.2 | 7.8 | 0 | 8.2 | 0.34
2025-04-14 | 14.3 | 3.7 | 0 | 2024-04-14 | 7.7 | 10.3 | 0 | 2023-04-14 | 19.2 | 0 | 1.2 | 2022-04-14 | 11.8 | 6.2 | 0 | 2021-04-14 | 14.4 | 3.6 | 0 | 2020-04-14 | 5.2 | 12.8 | 0 | 2019-04-14 | 1.5 | 16.5 | 0 | 2018-04-14 | -2.8 | 20.8 | 0 | 2017-04-14 | 13.7 | 4.3 | 0 | 2016-04-14 | 9.2 | 8.8 | 0 | 8.7 | 0.12
2025-04-14 | 12.6 | 5.4 | 0 | 2024-04-14 | 6.6 | 11.4 | 0 | 2023-04-14 | 15.4 | 2.6 | 0 | 2022-04-14 | 9.6 | 8.4 | 0 | 2021-04-14 | 11.9 | 6.1 | 0 | 2020-04-14 | 3.9 | 14.1 | 0 | 2019-04-14 | 1.3 | 16.7 | 0 | 2018-04-14 | -3.8 | 21.8 | 0 | 2017-04-14 | 10.4 | 7.6 | 0 | 2016-04-14 | 6.8 | 11.2 | 0 | 10.53 | 0
2025-04-14 | 10.3 | 7.7 | 0 | 2024-04-14 | 7.2 | 10.8 | 0 | 2023-04-14 | 15.1 | 2.9 | 0 | 2022-04-14 | 8.2 | 9.8 | 0 | 2021-04-14 | 11.7 | 6.3 | 0 | 2020-04-14 | 2.8 | 15.2 | 0 | 2019-04-14 | 1.6 | 16.4 | 0 | 2018-04-14 | -4.2 | 22.2 | 0 | 2017-04-14 | 7.2 | 10.8 | 0 | 2016-04-14 | 6.2 | 11.8 | 0 | 11.39 | 0
2025-04-14 | 9.6 | 8.4 | 0 | 2024-04-14 | 6.3 | 11.7 | 0 | 2023-04-14 | 14.6 | 3.4 | 0 | 2022-04-14 | 6.5 | 11.5 | 0 | 2021-04-14 | 10 | 8 | 0 | 2020-04-14 | 2.8 | 15.2 | 0 | 2019-04-14 | 1.8 | 16.2 | 0 | 2018-04-14 | -4.3 | 22.3 | 0 | 2017-04-14 | 9.3 | 8.7 | 0 | 2016-04-14 | 5.1 | 12.9 | 0 | 11.83 | 0
2025-04-14 | 8.7 | 9.3 | 0 | 2024-04-14 | 5.9 | 12.1 | 0 | 2023-04-14 | 13.1 | 4.9 | 0 | 2022-04-14 | 6.8 | 11.2 | 0 | 2021-04-14 | 8.9 | 9.1 | 0 | 2020-04-14 | 3.1 | 14.9 | 0 | 2019-04-14 | 1.8 | 16.2 | 0 | 2018-04-14 | -4.6 | 22.6 | 0 | 2017-04-14 | 6.4 | 11.6 | 0 | 2016-04-14 | 3.9 | 14.1 | 0 | 12.6 | 0
2025-04-14 | 6.4 | 11.6 | 0 | 2024-04-14 | 6.1 | 11.9 | 0 | 2023-04-14 | 11.9 | 6.1 | 0 | 2022-04-14 | 5.3 | 12.7 | 0 | 2021-04-14 | 8.7 | 9.3 | 0 | 2020-04-14 | 0.3 | 17.7 | 0 | 2019-04-14 | 1.9 | 16.1 | 0 | 2018-04-14 | -5 | 23 | 0 | 2017-04-14 | 7.8 | 10.2 | 0 | 2016-04-14 | 2.4 | 15.6 | 0 | 13.42 | 0
2025-04-15 | 5.9 | 12.1 | 0 | 2024-04-15 | 6.1 | 11.9 | 0 | 2023-04-15 | 10.9 | 7.1 | 0 | 2022-04-15 | 4.3 | 13.7 | 0 | 2021-04-15 | 9.2 | 8.8 | 0 | 2020-04-15 | -0.8 | 18.8 | 0 | 2019-04-15 | 2.3 | 15.7 | 0 | 2018-04-15 | -5 | 23 | 0 | 2017-04-15 | 7.5 | 10.5 | 0 | 2016-04-15 | 0.9 | 17.1 | 0 | 13.87 | 0
2025-04-15 | 6.3 | 11.7 | 0 | 2024-04-15 | 6.3 | 11.7 | 0 | 2023-04-15 | 10.4 | 7.6 | 0 | 2022-04-15 | 4.3 | 13.7 | 0 | 2021-04-15 | 9.5 | 8.5 | 0 | 2020-04-15 | -0.4 | 18.4 | 0 | 2019-04-15 | 2.7 | 15.3 | 0 | 2018-04-15 | -5 | 23 | 0 | 2017-04-15 | 7.2 | 10.8 | 0 | 2016-04-15 | -0.3 | 18.3 | 0 | 13.9 | 0
2025-04-15 | 5.9 | 12.1 | 0 | 2024-04-15 | 6 | 12 | 0 | 2023-04-15 | 10.5 | 7.5 | 0 | 2022-04-15 | 2.6 | 15.4 | 0 | 2021-04-15 | 10.5 | 7.5 | 0 | 2020-04-15 | -1.5 | 19.5 | 0 | 2019-04-15 | 3.1 | 14.9 | 0 | 2018-04-15 | -5 | 23 | 0 | 2017-04-15 | 3.5 | 14.5 | 0 | 2016-04-15 | 0.2 | 17.8 | 0 | 14.42 | 0
2025-04-15 | 4.4 | 13.6 | 0 | 2024-04-15 | 5.8 | 12.2 | 0 | 2023-04-15 | 8 | 10 | 0 | 2022-04-15 | 2.8 | 15.2 | 0 | 2021-04-15 | 9 | 9 | 0 | 2020-04-15 | -2.3 | 20.3 | 0 | 2019-04-15 | 2.9 | 15.1 | 0 | 2018-04-15 | -5.2 | 23.2 | 0 | 2017-04-15 | 4.8 | 13.2 | 0 | 2016-04-15 | -0.6 | 18.6 | 0 | 15.04 | 0
2025-04-15 | 4.1 | 13.9 | 0 | 2024-04-15 | 5.8 | 12.2 | 0 | 2023-04-15 | 6.8 | 11.2 | 0 | 2022-04-15 | 2.6 | 15.4 | 0 | 2021-04-15 | 8.4 | 9.6 | 0 | 2020-04-15 | -2.7 | 20.7 | 0 | 2019-04-15 | 3.4 | 14.6 | 0 | 2018-04-15 | -4.7 | 22.7 | 0 | 2017-04-15 | 1.3 | 16.7 | 0 | 2016-04-15 | 0.2 | 17.8 | 0 | 15.48 | 0
2025-04-15 | 1.8 | 16.2 | 0 | 2024-04-15 | 5.3 | 12.7 | 0 | 2023-04-15 | 6.4 | 11.6 | 0 | 2022-04-15 | 1.2 | 16.8 | 0 | 2021-04-15 | 8.2 | 9.8 | 0 | 2020-04-15 | -3 | 21 | 0 | 2019-04-15 | 3.1 | 14.9 | 0 | 2018-04-15 | -4.4 | 22.4 | 0 | 2017-04-15 | 1.1 | 16.9 | 0 | 2016-04-15 | 0 | 18 | 0 | 16.03 | 0
2025-04-15 | 3.1 | 14.9 | 0 | 2024-04-15 | 4.5 | 13.5 | 0 | 2023-04-15 | 7.8 | 10.2 | 0 | 2022-04-15 | 1.8 | 16.2 | 0 | 2021-04-15 | 8.2 | 9.8 | 0 | 2020-04-15 | -2.7 | 20.7 | 0 | 2019-04-15 | 3.1 | 14.9 | 0 | 2018-04-15 | -4.2 | 22.2 | 0 | 2017-04-15 | 0.4 | 17.6 | 0 | 2016-04-15 | 0.6 | 17.4 | 0 | 15.74 | 0
2025-04-15 | 6.3 | 11.7 | 0 | 2024-04-15 | 6 | 12 | 0 | 2023-04-15 | 11.7 | 6.3 | 0 | 2022-04-15 | 5.4 | 12.6 | 0 | 2021-04-15 | 8.4 | 9.6 | 0 | 2020-04-15 | -1.8 | 19.8 | 0 | 2019-04-15 | 3.2 | 14.8 | 0 | 2018-04-15 | -4.4 | 22.4 | 0 | 2017-04-15 | 5.5 | 12.5 | 0 | 2016-04-15 | 2.9 | 15.1 | 0 | 13.68 | 0
2025-04-15 | 8.4 | 9.6 | 0 | 2024-04-15 | 7.1 | 10.9 | 0 | 2023-04-15 | 13.6 | 4.4 | 0 | 2022-04-15 | 8.4 | 9.6 | 0 | 2021-04-15 | 9.2 | 8.8 | 0 | 2020-04-15 | -0.8 | 18.8 | 0 | 2019-04-15 | 2.8 | 15.2 | 0 | 2018-04-15 | -4.3 | 22.3 | 0 | 2017-04-15 | 9.3 | 8.7 | 0 | 2016-04-15 | 5.5 | 12.5 | 0 | 12.08 | 0
2025-04-15 | 8.1 | 9.9 | 0 | 2024-04-15 | 8.4 | 9.6 | 0 | 2023-04-15 | 15.9 | 2.1 | 0 | 2022-04-15 | 10.6 | 7.4 | 0 | 2021-04-15 | 9 | 9 | 0 | 2020-04-15 | 0.6 | 17.4 | 0 | 2019-04-15 | 2.7 | 15.3 | 0 | 2018-04-15 | -4.2 | 22.2 | 0 | 2017-04-15 | 12.1 | 5.9 | 0 | 2016-04-15 | 7.7 | 10.3 | 0 | 10.91 | 0
2025-04-15 | 8.9 | 9.1 | 0 | 2024-04-15 | 9.5 | 8.5 | 0 | 2023-04-15 | 17.4 | 0.6 | 0 | 2022-04-15 | 10.9 | 7.1 | 0 | 2021-04-15 | 8.7 | 9.3 | 0 | 2020-04-15 | 1.9 | 16.1 | 0 | 2019-04-15 | 3.7 | 14.3 | 0 | 2018-04-15 | -3.5 | 21.5 | 0 | 2017-04-15 | 15 | 3 | 0 | 2016-04-15 | 10.5 | 7.5 | 0 | 9.7 | 0
2025-04-15 | 10.1 | 7.9 | 0 | 2024-04-15 | 11 | 7 | 0 | 2023-04-15 | 19.4 | 0 | 1.4 | 2022-04-15 | 12.7 | 5.3 | 0 | 2021-04-15 | 9 | 9 | 0 | 2020-04-15 | 2.6 | 15.4 | 0 | 2019-04-15 | 3.2 | 14.8 | 0 | 2018-04-15 | -3.3 | 21.3 | 0 | 2017-04-15 | 16.1 | 1.9 | 0 | 2016-04-15 | 11.5 | 6.5 | 0 | 8.91 | 0.14
2025-04-15 | 9.8 | 8.2 | 0 | 2024-04-15 | 12.8 | 5.2 | 0 | 2023-04-15 | 21.6 | 0 | 3.6 | 2022-04-15 | 11.7 | 6.3 | 0 | 2021-04-15 | 9.2 | 8.8 | 0 | 2020-04-15 | 4.4 | 13.6 | 0 | 2019-04-15 | 3 | 15 | 0 | 2018-04-15 | -3.8 | 21.8 | 0 | 2017-04-15 | 17 | 1 | 0 | 2016-04-15 | 12.3 | 5.7 | 0 | 8.56 | 0.36
2025-04-15 | 8.6 | 9.4 | 0 | 2024-04-15 | 14.1 | 3.9 | 0 | 2023-04-15 | 22.4 | 0 | 4.4 | 2022-04-15 | 10.1 | 7.9 | 0 | 2021-04-15 | 9.3 | 8.7 | 0 | 2020-04-15 | 2.2 | 15.8 | 0 | 2019-04-15 | 3.4 | 14.6 | 0 | 2018-04-15 | -3.9 | 21.9 | 0 | 2017-04-15 | 17.4 | 0.6 | 0 | 2016-04-15 | 13 | 5 | 0 | 8.78 | 0.44
2025-04-15 | 4.8 | 13.2 | 0 | 2024-04-15 | 12.9 | 5.1 | 0 | 2023-04-15 | 23.6 | 0 | 5.6 | 2022-04-15 | 11.7 | 6.3 | 0 | 2021-04-15 | 9.2 | 8.8 | 0 | 2020-04-15 | 1.6 | 16.4 | 0 | 2019-04-15 | 3.5 | 14.5 | 0 | 2018-04-15 | -3.8 | 21.8 | 0 | 2017-04-15 | 13.2 | 4.8 | 0 | 2016-04-15 | 13.9 | 4.1 | 0 | 9.5 | 0.56
2025-04-15 | 8.4 | 9.6 | 0 | 2024-04-15 | 12.8 | 5.2 | 0 | 2023-04-15 | 24.1 | 0 | 6.1 | 2022-04-15 | 13.3 | 4.7 | 0 | 2021-04-15 | 9.2 | 8.8 | 0 | 2020-04-15 | 0.7 | 17.3 | 0 | 2019-04-15 | 3.4 | 14.6 | 0 | 2018-04-15 | -4.2 | 22.2 | 0 | 2017-04-15 | 9.9 | 8.1 | 0 | 2016-04-15 | 14 | 4 | 0 | 9.45 | 0.61
2025-04-15 | 6 | 12 | 0 | 2024-04-15 | 9.8 | 8.2 | 0 | 2023-04-15 | 24.6 | 0 | 6.6 | 2022-04-15 | 12.4 | 5.6 | 0 | 2021-04-15 | 8.9 | 9.1 | 0 | 2020-04-15 | 0.1 | 17.9 | 0 | 2019-04-15 | 3.7 | 14.3 | 0 | 2018-04-15 | -4.1 | 22.1 | 0 | 2017-04-15 | 9.8 | 8.2 | 0 | 2016-04-15 | 14 | 4 | 0 | 10.14 | 0.66
2025-04-15 | 6.4 | 11.6 | 0 | 2024-04-15 | 8.7 | 9.3 | 0 | 2023-04-15 | 24.1 | 0 | 6.1 | 2022-04-15 | 11.4 | 6.6 | 0 | 2021-04-15 | 8.2 | 9.8 | 0 | 2020-04-15 | 1.6 | 16.4 | 0 | 2019-04-15 | 2.6 | 15.4 | 0 | 2018-04-15 | -3.7 | 21.7 | 0 | 2017-04-15 | 9.9 | 8.1 | 0 | 2016-04-15 | 13.5 | 4.5 | 0 | 10.34 | 0.61
2025-04-15 | 6.3 | 11.7 | 0 | 2024-04-15 | 8.8 | 9.2 | 0 | 2023-04-15 | 22.7 | 0 | 4.7 | 2022-04-15 | 10 | 8 | 0 | 2021-04-15 | 8.2 | 9.8 | 0 | 2020-04-15 | 1.3 | 16.7 | 0 | 2019-04-15 | 2.6 | 15.4 | 0 | 2018-04-15 | -3.5 | 21.5 | 0 | 2017-04-15 | 10 | 8 | 0 | 2016-04-15 | 12.2 | 5.8 | 0 | 10.61 | 0.47
2025-04-15 | 3.9 | 14.1 | 0 | 2024-04-15 | 7.3 | 10.7 | 0 | 2023-04-15 | 18.9 | 0 | 0.9 | 2022-04-15 | 9.6 | 8.4 | 0 | 2021-04-15 | 7.5 | 10.5 | 0 | 2020-04-15 | -0.1 | 18.1 | 0 | 2019-04-15 | 2.6 | 15.4 | 0 | 2018-04-15 | -3.2 | 21.2 | 0 | 2017-04-15 | 10.1 | 7.9 | 0 | 2016-04-15 | 9.5 | 8.5 | 0 | 11.48 | 0.09
2025-04-15 | 3.5 | 14.5 | 0 | 2024-04-15 | 6.9 | 11.1 | 0 | 2023-04-15 | 17.9 | 0.1 | 0 | 2022-04-15 | 6.8 | 11.2 | 0 | 2021-04-15 | 7.1 | 10.9 | 0 | 2020-04-15 | -0.5 | 18.5 | 0 | 2019-04-15 | 2.6 | 15.4 | 0 | 2018-04-15 | -2.8 | 20.8 | 0 | 2017-04-15 | 10.2 | 7.8 | 0 | 2016-04-15 | 8.2 | 9.8 | 0 | 12.01 | 0
2025-04-15 | 2.9 | 15.1 | 0 | 2024-04-15 | 6.4 | 11.6 | 0 | 2023-04-15 | 16.2 | 1.8 | 0 | 2022-04-15 | 6.4 | 11.6 | 0 | 2021-04-15 | 6.6 | 11.4 | 0 | 2020-04-15 | -2 | 20 | 0 | 2019-04-15 | 2.3 | 15.7 | 0 | 2018-04-15 | -2.5 | 20.5 | 0 | 2017-04-15 | 10.3 | 7.7 | 0 | 2016-04-15 | 8.4 | 9.6 | 0 | 12.5 | 0
2025-04-15 | 2.7 | 15.3 | 0 | 2024-04-15 | 5 | 13 | 0 | 2023-04-15 | 16.5 | 1.5 | 0 | 2022-04-15 | 6 | 12 | 0 | 2021-04-15 | 6.3 | 11.7 | 0 | 2020-04-15 | -2.8 | 20.8 | 0 | 2019-04-15 | 1.5 | 16.5 | 0 | 2018-04-15 | -2.2 | 20.2 | 0 | 2017-04-15 | 10.1 | 7.9 | 0 | 2016-04-15 | 8 | 10 | 0 | 12.89 | 0
2025-04-15 | 1.7 | 16.3 | 0 | 2024-04-15 | 5.1 | 12.9 | 0 | 2023-04-15 | 15.1 | 2.9 | 0 | 2022-04-15 | 5.8 | 12.2 | 0 | 2021-04-15 | 6.3 | 11.7 | 0 | 2020-04-15 | -3.2 | 21.2 | 0 | 2019-04-15 | 1.2 | 16.8 | 0 | 2018-04-15 | -2.5 | 20.5 | 0 | 2017-04-15 | 10.6 | 7.4 | 0 | 2016-04-15 | 7.1 | 10.9 | 0 | 13.28 | 0
2025-04-16 | 0.7 | 17.3 | 0 | 2024-04-16 | 5 | 13 | 0 | 2023-04-16 | 13.9 | 4.1 | 0 | 2022-04-16 | 4.4 | 13.6 | 0 | 2021-04-16 | 5.6 | 12.4 | 0 | 2020-04-16 | -3.1 | 21.1 | 0 | 2019-04-16 | 1.1 | 16.9 | 0 | 2018-04-16 | -2 | 20 | 0 | 2017-04-16 | 10.3 | 7.7 | 0 | 2016-04-16 | 7.4 | 10.6 | 0 | 13.67 | 0
2025-04-16 | 0.4 | 17.6 | 0 | 2024-04-16 | 4.7 | 13.3 | 0 | 2023-04-16 | 12.2 | 5.8 | 0 | 2022-04-16 | 3 | 15 | 0 | 2021-04-16 | 5.3 | 12.7 | 0 | 2020-04-16 | -3.8 | 21.8 | 0 | 2019-04-16 | 1.3 | 16.7 | 0 | 2018-04-16 | -1.9 | 19.9 | 0 | 2017-04-16 | 10.9 | 7.1 | 0 | 2016-04-16 | 5.2 | 12.8 | 0 | 14.27 | 0
2025-04-16 | 0.2 | 17.8 | 0 | 2024-04-16 | 2.9 | 15.1 | 0 | 2023-04-16 | 9.8 | 8.2 | 0 | 2022-04-16 | 2.6 | 15.4 | 0 | 2021-04-16 | 5.1 | 12.9 | 0 | 2020-04-16 | -5.2 | 23.2 | 0 | 2019-04-16 | 1.1 | 16.9 | 0 | 2018-04-16 | -1.6 | 19.6 | 0 | 2017-04-16 | 11.6 | 6.4 | 0 | 2016-04-16 | 3.7 | 14.3 | 0 | 14.98 | 0
2025-04-16 | -0.2 | 18.2 | 0 | 2024-04-16 | 1.5 | 16.5 | 0 | 2023-04-16 | 10.7 | 7.3 | 0 | 2022-04-16 | 1.6 | 16.4 | 0 | 2021-04-16 | 4.5 | 13.5 | 0 | 2020-04-16 | -4.6 | 22.6 | 0 | 2019-04-16 | 1.3 | 16.7 | 0 | 2018-04-16 | -1.7 | 19.7 | 0 | 2017-04-16 | 11.9 | 6.1 | 0 | 2016-04-16 | 3.2 | 14.8 | 0 | 15.18 | 0
2025-04-16 | -0.2 | 18.2 | 0 | 2024-04-16 | 1.7 | 16.3 | 0 | 2023-04-16 | 10.8 | 7.2 | 0 | 2022-04-16 | 1.8 | 16.2 | 0 | 2021-04-16 | 4 | 14 | 0 | 2020-04-16 | -5.3 | 23.3 | 0 | 2019-04-16 | 1.1 | 16.9 | 0 | 2018-04-16 | -1.6 | 19.6 | 0 | 2017-04-16 | 12.5 | 5.5 | 0 | 2016-04-16 | 3.1 | 14.9 | 0 | 15.21 | 0
2025-04-16 | -0.6 | 18.6 | 0 | 2024-04-16 | 1.2 | 16.8 | 0 | 2023-04-16 | 10.1 | 7.9 | 0 | 2022-04-16 | 1.2 | 16.8 | 0 | 2021-04-16 | 3 | 15 | 0 | 2020-04-16 | -4.6 | 22.6 | 0 | 2019-04-16 | 1.1 | 16.9 | 0 | 2018-04-16 | -1.2 | 19.2 | 0 | 2017-04-16 | 12.7 | 5.3 | 0 | 2016-04-16 | 2.8 | 15.2 | 0 | 15.43 | 0
2025-04-16 | -0.7 | 18.7 | 0 | 2024-04-16 | 2.9 | 15.1 | 0 | 2023-04-16 | 9.9 | 8.1 | 0 | 2022-04-16 | 0.6 | 17.4 | 0 | 2021-04-16 | 2.5 | 15.5 | 0 | 2020-04-16 | -4.4 | 22.4 | 0 | 2019-04-16 | 1.6 | 16.4 | 0 | 2018-04-16 | -1 | 19 | 0 | 2017-04-16 | 13.3 | 4.7 | 0 | 2016-04-16 | 3.2 | 14.8 | 0 | 15.21 | 0
2025-04-16 | -0.4 | 18.4 | 0 | 2024-04-16 | 4.8 | 13.2 | 0 | 2023-04-16 | 11.4 | 6.6 | 0 | 2022-04-16 | 1.8 | 16.2 | 0 | 2021-04-16 | 3.1 | 14.9 | 0 | 2020-04-16 | -2 | 20 | 0 | 2019-04-16 | 2.5 | 15.5 | 0 | 2018-04-16 | -0.4 | 18.4 | 0 | 2017-04-16 | 13.6 | 4.4 | 0 | 2016-04-16 | 5.5 | 12.5 | 0 | 14.01 | 0
2025-04-16 | 0.1 | 17.9 | 0 | 2024-04-16 | 6.2 | 11.8 | 0 | 2023-04-16 | 13.3 | 4.7 | 0 | 2022-04-16 | 2.2 | 15.8 | 0 | 2021-04-16 | 3.8 | 14.2 | 0 | 2020-04-16 | -0.2 | 18.2 | 0 | 2019-04-16 | 3.5 | 14.5 | 0 | 2018-04-16 | -0.2 | 18.2 | 0 | 2017-04-16 | 13.9 | 4.1 | 0 | 2016-04-16 | 8.2 | 9.8 | 0 | 12.92 | 0
2025-04-16 | 0.6 | 17.4 | 0 | 2024-04-16 | 7.3 | 10.7 | 0 | 2023-04-16 | 15.5 | 2.5 | 0 | 2022-04-16 | 2.7 | 15.3 | 0 | 2021-04-16 | 4.7 | 13.3 | 0 | 2020-04-16 | 1.6 | 16.4 | 0 | 2019-04-16 | 4.8 | 13.2 | 0 | 2018-04-16 | 0.2 | 17.8 | 0 | 2017-04-16 | 14 | 4 | 0 | 2016-04-16 | 10.1 | 7.9 | 0 | 11.85 | 0
2025-04-16 | 1.1 | 16.9 | 0 | 2024-04-16 | 8.7 | 9.3 | 0 | 2023-04-16 | 17.6 | 0.4 | 0 | 2022-04-16 | 3.6 | 14.4 | 0 | 2021-04-16 | 5.9 | 12.1 | 0 | 2020-04-16 | 1.7 | 16.3 | 0 | 2019-04-16 | 7.1 | 10.9 | 0 | 2018-04-16 | 0.3 | 17.7 | 0 | 2017-04-16 | 14 | 4 | 0 | 2016-04-16 | 12.4 | 5.6 | 0 | 10.76 | 0
2025-04-16 | 2.1 | 15.9 | 0 | 2024-04-16 | 9.5 | 8.5 | 0 | 2023-04-16 | 19.1 | 0 | 1.1 | 2022-04-16 | 4.5 | 13.5 | 0 | 2021-04-16 | 5.8 | 12.2 | 0 | 2020-04-16 | 2.6 | 15.4 | 0 | 2019-04-16 | 8.5 | 9.5 | 0 | 2018-04-16 | 0.4 | 17.6 | 0 | 2017-04-16 | 14.9 | 3.1 | 0 | 2016-04-16 | 14.1 | 3.9 | 0 | 9.96 | 0.11
2025-04-16 | 3.4 | 14.6 | 0 | 2024-04-16 | 10.5 | 7.5 | 0 | 2023-04-16 | 21.1 | 0 | 3.1 | 2022-04-16 | 5.1 | 12.9 | 0 | 2021-04-16 | 7.9 | 10.1 | 0 | 2020-04-16 | 3.4 | 14.6 | 0 | 2019-04-16 | 8.6 | 9.4 | 0 | 2018-04-16 | 0.4 | 17.6 | 0 | 2017-04-16 | 14.7 | 3.3 | 0 | 2016-04-16 | 14.8 | 3.2 | 0 | 9.32 | 0.31
2025-04-16 | 3.1 | 14.9 | 0 | 2024-04-16 | 11.4 | 6.6 | 0 | 2023-04-16 | 22.4 | 0 | 4.4 | 2022-04-16 | 5.9 | 12.1 | 0 | 2021-04-16 | 8.3 | 9.7 | 0 | 2020-04-16 | 3.8 | 14.2 | 0 | 2019-04-16 | 9.3 | 8.7 | 0 | 2018-04-16 | 0.5 | 17.5 | 0 | 2017-04-16 | 14.9 | 3.1 | 0 | 2016-04-16 | 16.3 | 1.7 | 0 | 8.85 | 0.44
2025-04-16 | 4.1 | 13.9 | 0 | 2024-04-16 | 12.4 | 5.6 | 0 | 2023-04-16 | 23.9 | 0 | 5.9 | 2022-04-16 | 6 | 12 | 0 | 2021-04-16 | 7 | 11 | 0 | 2020-04-16 | 3.9 | 14.1 | 0 | 2019-04-16 | 10.1 | 7.9 | 0 | 2018-04-16 | 0.6 | 17.4 | 0 | 2017-04-16 | 15.2 | 2.8 | 0 | 2016-04-16 | 15.8 | 2.2 | 0 | 8.69 | 0.59
2025-04-16 | 4.1 | 13.9 | 0 | 2024-04-16 | 13.5 | 4.5 | 0 | 2023-04-16 | 25.2 | 0 | 7.2 | 2022-04-16 | 6.1 | 11.9 | 0 | 2021-04-16 | 7.5 | 10.5 | 0 | 2020-04-16 | 4.1 | 13.9 | 0 | 2019-04-16 | 10.4 | 7.6 | 0 | 2018-04-16 | 0.9 | 17.1 | 0 | 2017-04-16 | 15.3 | 2.7 | 0 | 2016-04-16 | 16.4 | 1.6 | 0 | 8.37 | 0.72
2025-04-16 | 5 | 13 | 0 | 2024-04-16 | 13.8 | 4.2 | 0 | 2023-04-16 | 24.9 | 0 | 6.9 | 2022-04-16 | 7 | 11 | 0 | 2021-04-16 | 7.5 | 10.5 | 0 | 2020-04-16 | 4.1 | 13.9 | 0 | 2019-04-16 | 10.4 | 7.6 | 0 | 2018-04-16 | 1 | 17 | 0 | 2017-04-16 | 12.1 | 5.9 | 0 | 2016-04-16 | 16.5 | 1.5 | 0 | 8.46 | 0.69
2025-04-16 | 5.1 | 12.9 | 0 | 2024-04-16 | 12.9 | 5.1 | 0 | 2023-04-16 | 24.9 | 0 | 6.9 | 2022-04-16 | 5.3 | 12.7 | 0 | 2021-04-16 | 7.4 | 10.6 | 0 | 2020-04-16 | 4.3 | 13.7 | 0 | 2019-04-16 | 10 | 8 | 0 | 2018-04-16 | 1.1 | 16.9 | 0 | 2017-04-16 | 11.5 | 6.5 | 0 | 2016-04-16 | 15.7 | 2.3 | 0 | 8.87 | 0.69
2025-04-16 | 3.4 | 14.6 | 0 | 2024-04-16 | 11.9 | 6.1 | 0 | 2023-04-16 | 22.8 | 0 | 4.8 | 2022-04-16 | 4.3 | 13.7 | 0 | 2021-04-16 | 7.4 | 10.6 | 0 | 2020-04-16 | 3 | 15 | 0 | 2019-04-16 | 9.1 | 8.9 | 0 | 2018-04-16 | 1.1 | 16.9 | 0 | 2017-04-16 | 11.1 | 6.9 | 0 | 2016-04-16 | 14.5 | 3.5 | 0 | 9.62 | 0.48
2025-04-16 | 2.7 | 15.3 | 0 | 2024-04-16 | 11.1 | 6.9 | 0 | 2023-04-16 | 20.4 | 0 | 2.4 | 2022-04-16 | 3.5 | 14.5 | 0 | 2021-04-16 | 6.6 | 11.4 | 0 | 2020-04-16 | 1.3 | 16.7 | 0 | 2019-04-16 | 6.9 | 11.1 | 0 | 2018-04-16 | 1.2 | 16.8 | 0 | 2017-04-16 | 10.1 | 7.9 | 0 | 2016-04-16 | 12.6 | 5.4 | 0 | 10.6 | 0.24
2025-04-16 | 1.8 | 16.2 | 0 | 2024-04-16 | 9.3 | 8.7 | 0 | 2023-04-16 | 19.6 | 0 | 1.6 | 2022-04-16 | 3.2 | 14.8 | 0 | 2021-04-16 | 6.2 | 11.8 | 0 | 2020-04-16 | 0 | 18 | 0 | 2019-04-16 | 7 | 11 | 0 | 2018-04-16 | 1.1 | 16.9 | 0 | 2017-04-16 | 9.6 | 8.4 | 0 | 2016-04-16 | 9.6 | 8.4 | 0 | 11.42 | 0.16
2025-04-16 | 1.5 | 16.5 | 0 | 2024-04-16 | 7.2 | 10.8 | 0 | 2023-04-16 | 18.2 | 0 | 0.2 | 2022-04-16 | 2.8 | 15.2 | 0 | 2021-04-16 | 5.4 | 12.6 | 0 | 2020-04-16 | -0.4 | 18.4 | 0 | 2019-04-16 | 5.5 | 12.5 | 0 | 2018-04-16 | 1.1 | 16.9 | 0 | 2017-04-16 | 8.9 | 9.1 | 0 | 2016-04-16 | 9.3 | 8.7 | 0 | 12.07 | 0.02
2025-04-16 | 1.3 | 16.7 | 0 | 2024-04-16 | 5.8 | 12.2 | 0 | 2023-04-16 | 17.3 | 0.7 | 0 | 2022-04-16 | 2.3 | 15.7 | 0 | 2021-04-16 | 4.5 | 13.5 | 0 | 2020-04-16 | -1.4 | 19.4 | 0 | 2019-04-16 | 3.7 | 14.3 | 0 | 2018-04-16 | 1.1 | 16.9 | 0 | 2017-04-16 | 8.6 | 9.4 | 0 | 2016-04-16 | 9.8 | 8.2 | 0 | 12.7 | 0
2025-04-16 | 1.5 | 16.5 | 0 | 2024-04-16 | 3.9 | 14.1 | 0 | 2023-04-16 | 16.3 | 1.7 | 0 | 2022-04-16 | 2.4 | 15.6 | 0 | 2021-04-16 | 4.2 | 13.8 | 0 | 2020-04-16 | -1.5 | 19.5 | 0 | 2019-04-16 | 3.8 | 14.2 | 0 | 2018-04-16 | 0.8 | 17.2 | 0 | 2017-04-16 | 8.1 | 9.9 | 0 | 2016-04-16 | 7.4 | 10.6 | 0 | 13.31 | 0
2025-04-17 | 0.7 | 17.3 | 0 | 2024-04-17 | 1.7 | 16.3 | 0 | 2023-04-17 | 14.9 | 3.1 | 0 | 2022-04-17 | 0.5 | 17.5 | 0 | 2021-04-17 | 4 | 14 | 0 | 2020-04-17 | -2.1 | 20.1 | 0 | 2019-04-17 | 2.1 | 15.9 | 0 | 2018-04-17 | 0.3 | 17.7 | 0 | 2017-04-17 | 7.7 | 10.3 | 0 | 2016-04-17 | 7.1 | 10.9 | 0 | 14.31 | 0
2025-04-17 | 0.7 | 17.3 | 0 | 2024-04-17 | 2.6 | 15.4 | 0 | 2023-04-17 | 14.4 | 3.6 | 0 | 2022-04-17 | -0.7 | 18.7 | 0 | 2021-04-17 | 3.9 | 14.1 | 0 | 2020-04-17 | -1.9 | 19.9 | 0 | 2019-04-17 | 0 | 18 | 0 | 2018-04-17 | 0.2 | 17.8 | 0 | 2017-04-17 | 7 | 11 | 0 | 2016-04-17 | 4.8 | 13.2 | 0 | 14.9 | 0
2025-04-17 | -0.1 | 18.1 | 0 | 2024-04-17 | 1.5 | 16.5 | 0 | 2023-04-17 | 14.3 | 3.7 | 0 | 2022-04-17 | -0.6 | 18.6 | 0 | 2021-04-17 | 3.8 | 14.2 | 0 | 2020-04-17 | -2.2 | 20.2 | 0 | 2019-04-17 | -0.5 | 18.5 | 0 | 2018-04-17 | 0.2 | 17.8 | 0 | 2017-04-17 | 6.1 | 11.9 | 0 | 2016-04-17 | 5.7 | 12.3 | 0 | 15.18 | 0
2025-04-17 | 0 | 18 | 0 | 2024-04-17 | 0.5 | 17.5 | 0 | 2023-04-17 | 13.4 | 4.6 | 0 | 2022-04-17 | -0.4 | 18.4 | 0 | 2021-04-17 | 4.2 | 13.8 | 0 | 2020-04-17 | -2.4 | 20.4 | 0 | 2019-04-17 | -0.6 | 18.6 | 0 | 2018-04-17 | 0.3 | 17.7 | 0 | 2017-04-17 | 6.1 | 11.9 | 0 | 2016-04-17 | 3.3 | 14.7 | 0 | 15.56 | 0
2025-04-17 | -1.2 | 19.2 | 0 | 2024-04-17 | -1 | 19 | 0 | 2023-04-17 | 15 | 3 | 0 | 2022-04-17 | -1.5 | 19.5 | 0 | 2021-04-17 | 4.1 | 13.9 | 0 | 2020-04-17 | -2.1 | 20.1 | 0 | 2019-04-17 | -0.9 | 18.9 | 0 | 2018-04-17 | 0.3 | 17.7 | 0 | 2017-04-17 | 5.8 | 12.2 | 0 | 2016-04-17 | 3.1 | 14.9 | 0 | 15.84 | 0
2025-04-17 | -1.3 | 19.3 | 0 | 2024-04-17 | -1 | 19 | 0 | 2023-04-17 | 13.1 | 4.9 | 0 | 2022-04-17 | -1.6 | 19.6 | 0 | 2021-04-17 | 3.8 | 14.2 | 0 | 2020-04-17 | -3 | 21 | 0 | 2019-04-17 | 1.6 | 16.4 | 0 | 2018-04-17 | 0.5 | 17.5 | 0 | 2017-04-17 | 5 | 13 | 0 | 2016-04-17 | 2.9 | 15.1 | 0 | 16 | 0
2025-04-17 | -0.8 | 18.8 | 0 | 2024-04-17 | 0.5 | 17.5 | 0 | 2023-04-17 | 11.9 | 6.1 | 0 | 2022-04-17 | -0.9 | 18.9 | 0 | 2021-04-17 | 3.9 | 14.1 | 0 | 2020-04-17 | -2.4 | 20.4 | 0 | 2019-04-17 | -0.3 | 18.3 | 0 | 2018-04-17 | 0.7 | 17.3 | 0 | 2017-04-17 | 4.7 | 13.3 | 0 | 2016-04-17 | 4.7 | 13.3 | 0 | 15.8 | 0
2025-04-17 | 0.4 | 17.6 | 0 | 2024-04-17 | 2 | 16 | 0 | 2023-04-17 | 10.1 | 7.9 | 0 | 2022-04-17 | 0.1 | 17.9 | 0 | 2021-04-17 | 5.7 | 12.3 | 0 | 2020-04-17 | -0.2 | 18.2 | 0 | 2019-04-17 | 2.8 | 15.2 | 0 | 2018-04-17 | 0.9 | 17.1 | 0 | 2017-04-17 | 5 | 13 | 0 | 2016-04-17 | 8.6 | 9.4 | 0 | 14.46 | 0
2025-04-17 | 1.1 | 16.9 | 0 | 2024-04-17 | 3.9 | 14.1 | 0 | 2023-04-17 | 8.9 | 9.1 | 0 | 2022-04-17 | 1.2 | 16.8 | 0 | 2021-04-17 | 6.7 | 11.3 | 0 | 2020-04-17 | 1.2 | 16.8 | 0 | 2019-04-17 | 6.8 | 11.2 | 0 | 2018-04-17 | 1.1 | 16.9 | 0 | 2017-04-17 | 5 | 13 | 0 | 2016-04-17 | 11.4 | 6.6 | 0 | 13.27 | 0
2025-04-17 | 2.2 | 15.8 | 0 | 2024-04-17 | 4.4 | 13.6 | 0 | 2023-04-17 | 7.9 | 10.1 | 0 | 2022-04-17 | 3.2 | 14.8 | 0 | 2021-04-17 | 7.3 | 10.7 | 0 | 2020-04-17 | 1.4 | 16.6 | 0 | 2019-04-17 | 9.3 | 8.7 | 0 | 2018-04-17 | 1.1 | 16.9 | 0 | 2017-04-17 | 6.6 | 11.4 | 0 | 2016-04-17 | 13.8 | 4.2 | 0 | 12.28 | 0
2025-04-17 | 3.2 | 14.8 | 0 | 2024-04-17 | 5.8 | 12.2 | 0 | 2023-04-17 | 8.3 | 9.7 | 0 | 2022-04-17 | 4.4 | 13.6 | 0 | 2021-04-17 | 8.1 | 9.9 | 0 | 2020-04-17 | 2.9 | 15.1 | 0 | 2019-04-17 | 11.1 | 6.9 | 0 | 2018-04-17 | 1.2 | 16.8 | 0 | 2017-04-17 | 6.5 | 11.5 | 0 | 2016-04-17 | 17.1 | 0.9 | 0 | 11.14 | 0
2025-04-17 | 4 | 14 | 0 | 2024-04-17 | 7.3 | 10.7 | 0 | 2023-04-17 | 8.1 | 9.9 | 0 | 2022-04-17 | 4.9 | 13.1 | 0 | 2021-04-17 | 8.5 | 9.5 | 0 | 2020-04-17 | 2.9 | 15.1 | 0 | 2019-04-17 | 11.8 | 6.2 | 0 | 2018-04-17 | 1.3 | 16.7 | 0 | 2017-04-17 | 7 | 11 | 0 | 2016-04-17 | 18 | 0 | 0 | 10.62 | 0
2025-04-17 | 5.8 | 12.2 | 0 | 2024-04-17 | 9.4 | 8.6 | 0 | 2023-04-17 | 8.6 | 9.4 | 0 | 2022-04-17 | 5.6 | 12.4 | 0 | 2021-04-17 | 9.5 | 8.5 | 0 | 2020-04-17 | 3.4 | 14.6 | 0 | 2019-04-17 | 13.1 | 4.9 | 0 | 2018-04-17 | 1 | 17 | 0 | 2017-04-17 | 6.4 | 11.6 | 0 | 2016-04-17 | 20.5 | 0 | 2.5 | 9.92 | 0.25
2025-04-17 | 6.9 | 11.1 | 0 | 2024-04-17 | 9 | 9 | 0 | 2023-04-17 | 8.1 | 9.9 | 0 | 2022-04-17 | 6.5 | 11.5 | 0 | 2021-04-17 | 10.8 | 7.2 | 0 | 2020-04-17 | 3.8 | 14.2 | 0 | 2019-04-17 | 13.3 | 4.7 | 0 | 2018-04-17 | 0.8 | 17.2 | 0 | 2017-04-17 | 7 | 11 | 0 | 2016-04-17 | 21.3 | 0 | 3.3 | 9.58 | 0.33
2025-04-17 | 7.9 | 10.1 | 0 | 2024-04-17 | 10.9 | 7.1 | 0 | 2023-04-17 | 8.8 | 9.2 | 0 | 2022-04-17 | 8.1 | 9.9 | 0 | 2021-04-17 | 11.6 | 6.4 | 0 | 2020-04-17 | 5.6 | 12.4 | 0 | 2019-04-17 | 13.3 | 4.7 | 0 | 2018-04-17 | 1 | 17 | 0 | 2017-04-17 | 5.9 | 12.1 | 0 | 2016-04-17 | 21.7 | 0 | 3.7 | 8.89 | 0.37
2025-04-17 | 9.4 | 8.6 | 0 | 2024-04-17 | 10.3 | 7.7 | 0 | 2023-04-17 | 9.6 | 8.4 | 0 | 2022-04-17 | 7.5 | 10.5 | 0 | 2021-04-17 | 11.9 | 6.1 | 0 | 2020-04-17 | 6.1 | 11.9 | 0 | 2019-04-17 | 14 | 4 | 0 | 2018-04-17 | 1.3 | 16.7 | 0 | 2017-04-17 | 5.5 | 12.5 | 0 | 2016-04-17 | 22.5 | 0 | 4.5 | 8.64 | 0.45
2025-04-17 | 9.7 | 8.3 | 0 | 2024-04-17 | 9.7 | 8.3 | 0 | 2023-04-17 | 9.7 | 8.3 | 0 | 2022-04-17 | 8.7 | 9.3 | 0 | 2021-04-17 | 11.8 | 6.2 | 0 | 2020-04-17 | 6.1 | 11.9 | 0 | 2019-04-17 | 13.5 | 4.5 | 0 | 2018-04-17 | 0.7 | 17.3 | 0 | 2017-04-17 | 4.6 | 13.4 | 0 | 2016-04-17 | 22.7 | 0 | 4.7 | 8.75 | 0.47
2025-04-17 | 10.1 | 7.9 | 0 | 2024-04-17 | 9.6 | 8.4 | 0 | 2023-04-17 | 10.9 | 7.1 | 0 | 2022-04-17 | 8.1 | 9.9 | 0 | 2021-04-17 | 12.1 | 5.9 | 0 | 2020-04-17 | 5.6 | 12.4 | 0 | 2019-04-17 | 13.8 | 4.2 | 0 | 2018-04-17 | 0.4 | 17.6 | 0 | 2017-04-17 | 4.4 | 13.6 | 0 | 2016-04-17 | 22.1 | 0 | 4.1 | 8.7 | 0.41
2025-04-17 | 9.2 | 8.8 | 0 | 2024-04-17 | 8.5 | 9.5 | 0 | 2023-04-17 | 10.6 | 7.4 | 0 | 2022-04-17 | 7.5 | 10.5 | 0 | 2021-04-17 | 11.2 | 6.8 | 0 | 2020-04-17 | 5.1 | 12.9 | 0 | 2019-04-17 | 12.2 | 5.8 | 0 | 2018-04-17 | 0 | 18 | 0 | 2017-04-17 | 3.9 | 14.1 | 0 | 2016-04-17 | 20.9 | 0 | 2.9 | 9.38 | 0.29
2025-04-17 | 5.8 | 12.2 | 0 | 2024-04-17 | 7.6 | 10.4 | 0 | 2023-04-17 | 9.8 | 8.2 | 0 | 2022-04-17 | 6.1 | 11.9 | 0 | 2021-04-17 | 9.7 | 8.3 | 0 | 2020-04-17 | 3.8 | 14.2 | 0 | 2019-04-17 | 8.8 | 9.2 | 0 | 2018-04-17 | -0.2 | 18.2 | 0 | 2017-04-17 | 3.1 | 14.9 | 0 | 2016-04-17 | 17.7 | 0.3 | 0 | 10.78 | 0
2025-04-17 | 6.2 | 11.8 | 0 | 2024-04-17 | 7 | 11 | 0 | 2023-04-17 | 9.6 | 8.4 | 0 | 2022-04-17 | 3.8 | 14.2 | 0 | 2021-04-17 | 8.4 | 9.6 | 0 | 2020-04-17 | 3 | 15 | 0 | 2019-04-17 | 7.5 | 10.5 | 0 | 2018-04-17 | -0.3 | 18.3 | 0 | 2017-04-17 | 2.6 | 15.4 | 0 | 2016-04-17 | 16.4 | 1.6 | 0 | 11.58 | 0
2025-04-17 | 4 | 14 | 0 | 2024-04-17 | 6.9 | 11.1 | 0 | 2023-04-17 | 8.6 | 9.4 | 0 | 2022-04-17 | 2.9 | 15.1 | 0 | 2021-04-17 | 8.2 | 9.8 | 0 | 2020-04-17 | 2.7 | 15.3 | 0 | 2019-04-17 | 7.5 | 10.5 | 0 | 2018-04-17 | -0.6 | 18.6 | 0 | 2017-04-17 | 2 | 16 | 0 | 2016-04-17 | 15 | 3 | 0 | 12.28 | 0
2025-04-17 | 2.9 | 15.1 | 0 | 2024-04-17 | 7 | 11 | 0 | 2023-04-17 | 5.2 | 12.8 | 0 | 2022-04-17 | 2.1 | 15.9 | 0 | 2021-04-17 | 7.5 | 10.5 | 0 | 2020-04-17 | 1.6 | 16.4 | 0 | 2019-04-17 | 7 | 11 | 0 | 2018-04-17 | -0.6 | 18.6 | 0 | 2017-04-17 | 0.7 | 17.3 | 0 | 2016-04-17 | 14.8 | 3.2 | 0 | 13.18 | 0
2025-04-17 | 3.3 | 14.7 | 0 | 2024-04-17 | 7 | 11 | 0 | 2023-04-17 | 4.8 | 13.2 | 0 | 2022-04-17 | 2.7 | 15.3 | 0 | 2021-04-17 | 6.8 | 11.2 | 0 | 2020-04-17 | 1.1 | 16.9 | 0 | 2019-04-17 | 7 | 11 | 0 | 2018-04-17 | -0.5 | 18.5 | 0 | 2017-04-17 | -1.3 | 19.3 | 0 | 2016-04-17 | 13.2 | 4.8 | 0 | 13.59 | 0
2025-04-18 | 1.7 | 16.3 | 0 | 2024-04-18 | 7 | 11 | 0 | 2023-04-18 | 4 | 14 | 0 | 2022-04-18 | 0.1 | 17.9 | 0 | 2021-04-18 | 6.4 | 11.6 | 0 | 2020-04-18 | -0.4 | 18.4 | 0 | 2019-04-18 | 6.8 | 11.2 | 0 | 2018-04-18 | -0.5 | 18.5 | 0 | 2017-04-18 | -0.7 | 18.7 | 0 | 2016-04-18 | 8.3 | 9.7 | 0 | 14.73 | 0
2025-04-18 | 0.9 | 17.1 | 0 | 2024-04-18 | 6.8 | 11.2 | 0 | 2023-04-18 | 4 | 14 | 0 | 2022-04-18 | -1.3 | 19.3 | 0 | 2021-04-18 | 5.9 | 12.1 | 0 | 2020-04-18 | -2.8 | 20.8 | 0 | 2019-04-18 | 5.9 | 12.1 | 0 | 2018-04-18 | -0.5 | 18.5 | 0 | 2017-04-18 | -1.9 | 19.9 | 0 | 2016-04-18 | 11.3 | 6.7 | 0 | 15.17 | 0
2025-04-18 | 1 | 17 | 0 | 2024-04-18 | 6.6 | 11.4 | 0 | 2023-04-18 | 3.8 | 14.2 | 0 | 2022-04-18 | -0.1 | 18.1 | 0 | 2021-04-18 | 5 | 13 | 0 | 2020-04-18 | -1.8 | 19.8 | 0 | 2019-04-18 | 6.2 | 11.8 | 0 | 2018-04-18 | -0.4 | 18.4 | 0 | 2017-04-18 | -1.7 | 19.7 | 0 | 2016-04-18 | 10.3 | 7.7 | 0 | 15.11 | 0
2025-04-18 | -1 | 19 | 0 | 2024-04-18 | 6.3 | 11.7 | 0 | 2023-04-18 | 3.2 | 14.8 | 0 | 2022-04-18 | -0.6 | 18.6 | 0 | 2021-04-18 | 5.1 | 12.9 | 0 | 2020-04-18 | -2.8 | 20.8 | 0 | 2019-04-18 | 6.2 | 11.8 | 0 | 2018-04-18 | -0.3 | 18.3 | 0 | 2017-04-18 | -2.4 | 20.4 | 0 | 2016-04-18 | 8.7 | 9.3 | 0 | 15.76 | 0
2025-04-18 | -0.4 | 18.4 | 0 | 2024-04-18 | 6.3 | 11.7 | 0 | 2023-04-18 | 3 | 15 | 0 | 2022-04-18 | -1.7 | 19.7 | 0 | 2021-04-18 | 5.1 | 12.9 | 0 | 2020-04-18 | -3.2 | 21.2 | 0 | 2019-04-18 | 4.7 | 13.3 | 0 | 2018-04-18 | -0.3 | 18.3 | 0 | 2017-04-18 | -3 | 21 | 0 | 2016-04-18 | 8.5 | 9.5 | 0 | 16.1 | 0
2025-04-18 | -0.5 | 18.5 | 0 | 2024-04-18 | 4.5 | 13.5 | 0 | 2023-04-18 | 3.3 | 14.7 | 0 | 2022-04-18 | -3.7 | 21.7 | 0 | 2021-04-18 | 4 | 14 | 0 | 2020-04-18 | -3 | 21 | 0 | 2019-04-18 | 3.7 | 14.3 | 0 | 2018-04-18 | -0.1 | 18.1 | 0 | 2017-04-18 | -2.9 | 20.9 | 0 | 2016-04-18 | 7.2 | 10.8 | 0 | 16.75 | 0
2025-04-18 | -0.1 | 18.1 | 0 | 2024-04-18 | 4.1 | 13.9 | 0 | 2023-04-18 | 3.5 | 14.5 | 0 | 2022-04-18 | -1.9 | 19.9 | 0 | 2021-04-18 | 5.2 | 12.8 | 0 | 2020-04-18 | -2.7 | 20.7 | 0 | 2019-04-18 | 4.2 | 13.8 | 0 | 2018-04-18 | 0.6 | 17.4 | 0 | 2017-04-18 | -2.2 | 20.2 | 0 | 2016-04-18 | 7.5 | 10.5 | 0 | 16.18 | 0
2025-04-18 | 2.4 | 15.6 | 0 | 2024-04-18 | 3.5 | 14.5 | 0 | 2023-04-18 | 4.2 | 13.8 | 0 | 2022-04-18 | 1.1 | 16.9 | 0 | 2021-04-18 | 5.5 | 12.5 | 0 | 2020-04-18 | 0.1 | 17.9 | 0 | 2019-04-18 | 4.7 | 13.3 | 0 | 2018-04-18 | 1.4 | 16.6 | 0 | 2017-04-18 | 0.8 | 17.2 | 0 | 2016-04-18 | 10.6 | 7.4 | 0 | 14.57 | 0
2025-04-18 | 5 | 13 | 0 | 2024-04-18 | 3.7 | 14.3 | 0 | 2023-04-18 | 5.3 | 12.7 | 0 | 2022-04-18 | 2.5 | 15.5 | 0 | 2021-04-18 | 6.2 | 11.8 | 0 | 2020-04-18 | 3.2 | 14.8 | 0 | 2019-04-18 | 6.8 | 11.2 | 0 | 2018-04-18 | 1.9 | 16.1 | 0 | 2017-04-18 | 3.1 | 14.9 | 0 | 2016-04-18 | 12.1 | 5.9 | 0 | 13.02 | 0
2025-04-18 | 7.7 | 10.3 | 0 | 2024-04-18 | 4.1 | 13.9 | 0 | 2023-04-18 | 5.1 | 12.9 | 0 | 2022-04-18 | 4 | 14 | 0 | 2021-04-18 | 6.8 | 11.2 | 0 | 2020-04-18 | 5 | 13 | 0 | 2019-04-18 | 8.4 | 9.6 | 0 | 2018-04-18 | 2.7 | 15.3 | 0 | 2017-04-18 | 4.4 | 13.6 | 0 | 2016-04-18 | 13.7 | 4.3 | 0 | 11.81 | 0
2025-04-18 | 10.8 | 7.2 | 0 | 2024-04-18 | 5 | 13 | 0 | 2023-04-18 | 6 | 12 | 0 | 2022-04-18 | 5.4 | 12.6 | 0 | 2021-04-18 | 8.1 | 9.9 | 0 | 2020-04-18 | 6.3 | 11.7 | 0 | 2019-04-18 | 10.3 | 7.7 | 0 | 2018-04-18 | 3.5 | 14.5 | 0 | 2017-04-18 | 5.5 | 12.5 | 0 | 2016-04-18 | 14.2 | 3.8 | 0 | 10.49 | 0
2025-04-18 | 11.1 | 6.9 | 0 | 2024-04-18 | 5.9 | 12.1 | 0 | 2023-04-18 | 6.2 | 11.8 | 0 | 2022-04-18 | 7.9 | 10.1 | 0 | 2021-04-18 | 9.8 | 8.2 | 0 | 2020-04-18 | 6.4 | 11.6 | 0 | 2019-04-18 | 14 | 4 | 0 | 2018-04-18 | 4.2 | 13.8 | 0 | 2017-04-18 | 7.5 | 10.5 | 0 | 2016-04-18 | 14.2 | 3.8 | 0 | 9.28 | 0
2025-04-18 | 12.8 | 5.2 | 0 | 2024-04-18 | 6.8 | 11.2 | 0 | 2023-04-18 | 6.9 | 11.1 | 0 | 2022-04-18 | 8.2 | 9.8 | 0 | 2021-04-18 | 11.9 | 6.1 | 0 | 2020-04-18 | 7.1 | 10.9 | 0 | 2019-04-18 | 15.9 | 2.1 | 0 | 2018-04-18 | 5.6 | 12.4 | 0 | 2017-04-18 | 7.7 | 10.3 | 0 | 2016-04-18 | 13 | 5 | 0 | 8.41 | 0
2025-04-18 | 12.9 | 5.1 | 0 | 2024-04-18 | 7.6 | 10.4 | 0 | 2023-04-18 | 6.9 | 11.1 | 0 | 2022-04-18 | 10.1 | 7.9 | 0 | 2021-04-18 | 13.2 | 4.8 | 0 | 2020-04-18 | 8 | 10 | 0 | 2019-04-18 | 17.7 | 0.3 | 0 | 2018-04-18 | 6.1 | 11.9 | 0 | 2017-04-18 | 9 | 9 | 0 | 2016-04-18 | 13.8 | 4.2 | 0 | 7.47 | 0
2025-04-18 | 11.6 | 6.4 | 0 | 2024-04-18 | 8.1 | 9.9 | 0 | 2023-04-18 | 6.2 | 11.8 | 0 | 2022-04-18 | 11.2 | 6.8 | 0 | 2021-04-18 | 15.6 | 2.4 | 0 | 2020-04-18 | 9.2 | 8.8 | 0 | 2019-04-18 | 17.6 | 0.4 | 0 | 2018-04-18 | 6.4 | 11.6 | 0 | 2017-04-18 | 9.6 | 8.4 | 0 | 2016-04-18 | 14.3 | 3.7 | 0 | 7.02 | 0
2025-04-18 | 13.1 | 4.9 | 0 | 2024-04-18 | 8.6 | 9.4 | 0 | 2023-04-18 | 6.4 | 11.6 | 0 | 2022-04-18 | 10.9 | 7.1 | 0 | 2021-04-18 | 13.4 | 4.6 | 0 | 2020-04-18 | 10.3 | 7.7 | 0 | 2019-04-18 | 17.3 | 0.7 | 0 | 2018-04-18 | 6.4 | 11.6 | 0 | 2017-04-18 | 10.5 | 7.5 | 0 | 2016-04-18 | 14.1 | 3.9 | 0 | 6.9 | 0
2025-04-18 | 13 | 5 | 0 | 2024-04-18 | 8.6 | 9.4 | 0 | 2023-04-18 | 7 | 11 | 0 | 2022-04-18 | 10.5 | 7.5 | 0 | 2021-04-18 | 13.8 | 4.2 | 0 | 2020-04-18 | 10.9 | 7.1 | 0 | 2019-04-18 | 15.3 | 2.7 | 0 | 2018-04-18 | 6.1 | 11.9 | 0 | 2017-04-18 | 10 | 8 | 0 | 2016-04-18 | 13.1 | 4.9 | 0 | 7.17 | 0
2025-04-18 | 15.3 | 2.7 | 0 | 2024-04-18 | 8.4 | 9.6 | 0 | 2023-04-18 | 5.9 | 12.1 | 0 | 2022-04-18 | 9.5 | 8.5 | 0 | 2021-04-18 | 11.4 | 6.6 | 0 | 2020-04-18 | 10.3 | 7.7 | 0 | 2019-04-18 | 16 | 2 | 0 | 2018-04-18 | 5 | 13 | 0 | 2017-04-18 | 10 | 8 | 0 | 2016-04-18 | 11 | 7 | 0 | 7.72 | 0
2025-04-18 | 14.9 | 3.1 | 0 | 2024-04-18 | 8.2 | 9.8 | 0 | 2023-04-18 | 5.5 | 12.5 | 0 | 2022-04-18 | 9 | 9 | 0 | 2021-04-18 | 11.1 | 6.9 | 0 | 2020-04-18 | 9.3 | 8.7 | 0 | 2019-04-18 | 16 | 2 | 0 | 2018-04-18 | 4.8 | 13.2 | 0 | 2017-04-18 | 9.3 | 8.7 | 0 | 2016-04-18 | 9.3 | 8.7 | 0 | 8.26 | 0
2025-04-18 | 13.7 | 4.3 | 0 | 2024-04-18 | 8 | 10 | 0 | 2023-04-18 | 4.8 | 13.2 | 0 | 2022-04-18 | 8.3 | 9.7 | 0 | 2021-04-18 | 9.6 | 8.4 | 0 | 2020-04-18 | 7.2 | 10.8 | 0 | 2019-04-18 | 16.5 | 1.5 | 0 | 2018-04-18 | 3.9 | 14.1 | 0 | 2017-04-18 | 6.7 | 11.3 | 0 | 2016-04-18 | 6.3 | 11.7 | 0 | 9.5 | 0
2025-04-18 | 13.4 | 4.6 | 0 | 2024-04-18 | 8 | 10 | 0 | 2023-04-18 | 3.2 | 14.8 | 0 | 2022-04-18 | 7.9 | 10.1 | 0 | 2021-04-18 | 9.2 | 8.8 | 0 | 2020-04-18 | 5.5 | 12.5 | 0 | 2019-04-18 | 16.1 | 1.9 | 0 | 2018-04-18 | 2.9 | 15.1 | 0 | 2017-04-18 | 5 | 13 | 0 | 2016-04-18 | 5.7 | 12.3 | 0 | 10.31 | 0
2025-04-18 | 12.8 | 5.2 | 0 | 2024-04-18 | 7.8 | 10.2 | 0 | 2023-04-18 | 1.7 | 16.3 | 0 | 2022-04-18 | 7.1 | 10.9 | 0 | 2021-04-18 | 8.8 | 9.2 | 0 | 2020-04-18 | 4.7 | 13.3 | 0 | 2019-04-18 | 15.7 | 2.3 | 0 | 2018-04-18 | 2.2 | 15.8 | 0 | 2017-04-18 | 5.1 | 12.9 | 0 | 2016-04-18 | 5.5 | 12.5 | 0 | 10.86 | 0
2025-04-18 | 11.2 | 6.8 | 0 | 2024-04-18 | 8 | 10 | 0 | 2023-04-18 | 1.1 | 16.9 | 0 | 2022-04-18 | 4.6 | 13.4 | 0 | 2021-04-18 | 8.4 | 9.6 | 0 | 2020-04-18 | 4.5 | 13.5 | 0 | 2019-04-18 | 14.8 | 3.2 | 0 | 2018-04-18 | 1.4 | 16.6 | 0 | 2017-04-18 | 5 | 13 | 0 | 2016-04-18 | 5.4 | 12.6 | 0 | 11.56 | 0
2025-04-18 | 10.8 | 7.2 | 0 | 2024-04-18 | 8.3 | 9.7 | 0 | 2023-04-18 | 1.1 | 16.9 | 0 | 2022-04-18 | 4.2 | 13.8 | 0 | 2021-04-18 | 8.3 | 9.7 | 0 | 2020-04-18 | 4.1 | 13.9 | 0 | 2019-04-18 | 15.8 | 2.2 | 0 | 2018-04-18 | 0.9 | 17.1 | 0 | 2017-04-18 | 4.9 | 13.1 | 0 | 2016-04-18 | 5.3 | 12.7 | 0 | 11.63 | 0
2025-04-19 | 10.8 | 7.2 | 0 | 2024-04-19 | 8.3 | 9.7 | 0 | 2023-04-19 | 1.1 | 16.9 | 0 | 2022-04-19 | 4 | 14 | 0 | 2021-04-19 | 7.9 | 10.1 | 0 | 2020-04-19 | 3.1 | 14.9 | 0 | 2019-04-19 | 16 | 2 | 0 | 2018-04-19 | 0.4 | 17.6 | 0 | 2017-04-19 | 4.7 | 13.3 | 0 | 2016-04-19 | 5 | 13 | 0 | 11.87 | 0
2025-04-19 | 10.5 | 7.5 | 0 | 2024-04-19 | 8.1 | 9.9 | 0 | 2023-04-19 | 1.4 | 16.6 | 0 | 2022-04-19 | 3.6 | 14.4 | 0 | 2021-04-19 | 6.9 | 11.1 | 0 | 2020-04-19 | 2.1 | 15.9 | 0 | 2019-04-19 | 13.5 | 4.5 | 0 | 2018-04-19 | 0.1 | 17.9 | 0 | 2017-04-19 | 4.2 | 13.8 | 0 | 2016-04-19 | 4.5 | 13.5 | 0 | 12.51 | 0
2025-04-19 | 10.3 | 7.7 | 0 | 2024-04-19 | 7.8 | 10.2 | 0 | 2023-04-19 | 1.2 | 16.8 | 0 | 2022-04-19 | 2.9 | 15.1 | 0 | 2021-04-19 | 6.5 | 11.5 | 0 | 2020-04-19 | 1.8 | 16.2 | 0 | 2019-04-19 | 12.3 | 5.7 | 0 | 2018-04-19 | -0.1 | 18.1 | 0 | 2017-04-19 | 3.6 | 14.4 | 0 | 2016-04-19 | 3.9 | 14.1 | 0 | 12.98 | 0
2025-04-19 | 9 | 9 | 0 | 2024-04-19 | 7.7 | 10.3 | 0 | 2023-04-19 | 0.9 | 17.1 | 0 | 2022-04-19 | 2.1 | 15.9 | 0 | 2021-04-19 | 6 | 12 | 0 | 2020-04-19 | 2.4 | 15.6 | 0 | 2019-04-19 | 12.2 | 5.8 | 0 | 2018-04-19 | -0.1 | 18.1 | 0 | 2017-04-19 | 3 | 15 | 0 | 2016-04-19 | 2.5 | 15.5 | 0 | 13.43 | 0
2025-04-19 | 9.2 | 8.8 | 0 | 2024-04-19 | 7.7 | 10.3 | 0 | 2023-04-19 | 0.6 | 17.4 | 0 | 2022-04-19 | 1.9 | 16.1 | 0 | 2021-04-19 | 5.6 | 12.4 | 0 | 2020-04-19 | 3.1 | 14.9 | 0 | 2019-04-19 | 11.6 | 6.4 | 0 | 2018-04-19 | -0.1 | 18.1 | 0 | 2017-04-19 | 3.2 | 14.8 | 0 | 2016-04-19 | 2 | 16 | 0 | 13.52 | 0
2025-04-19 | 10.1 | 7.9 | 0 | 2024-04-19 | 7.3 | 10.7 | 0 | 2023-04-19 | 0.5 | 17.5 | 0 | 2022-04-19 | 1.4 | 16.6 | 0 | 2021-04-19 | 3.2 | 14.8 | 0 | 2020-04-19 | 3.8 | 14.2 | 0 | 2019-04-19 | 10.6 | 7.4 | 0 | 2018-04-19 | -0.2 | 18.2 | 0 | 2017-04-19 | 3.2 | 14.8 | 0 | 2016-04-19 | 2.3 | 15.7 | 0 | 13.78 | 0
2025-04-19 | 11.4 | 6.6 | 0 | 2024-04-19 | 7.3 | 10.7 | 0 | 2023-04-19 | 0.9 | 17.1 | 0 | 2022-04-19 | 1.1 | 16.9 | 0 | 2021-04-19 | 4.8 | 13.2 | 0 | 2020-04-19 | 4.5 | 13.5 | 0 | 2019-04-19 | 9.7 | 8.3 | 0 | 2018-04-19 | -0.1 | 18.1 | 0 | 2017-04-19 | 3.6 | 14.4 | 0 | 2016-04-19 | 1.8 | 16.2 | 0 | 13.5 | 0
2025-04-19 | 11.9 | 6.1 | 0 | 2024-04-19 | 7.8 | 10.2 | 0 | 2023-04-19 | 1 | 17 | 0 | 2022-04-19 | 0.8 | 17.2 | 0 | 2021-04-19 | 7.5 | 10.5 | 0 | 2020-04-19 | 5.5 | 12.5 | 0 | 2019-04-19 | 8.8 | 9.2 | 0 | 2018-04-19 | -0.1 | 18.1 | 0 | 2017-04-19 | 4.8 | 13.2 | 0 | 2016-04-19 | 3.9 | 14.1 | 0 | 12.81 | 0
2025-04-19 | 12.5 | 5.5 | 0 | 2024-04-19 | 8.4 | 9.6 | 0 | 2023-04-19 | 2 | 16 | 0 | 2022-04-19 | 0.7 | 17.3 | 0 | 2021-04-19 | 9 | 9 | 0 | 2020-04-19 | 6.7 | 11.3 | 0 | 2019-04-19 | 7.3 | 10.7 | 0 | 2018-04-19 | 1.6 | 16.4 | 0 | 2017-04-19 | 7.2 | 10.8 | 0 | 2016-04-19 | 5.7 | 12.3 | 0 | 11.89 | 0
2025-04-19 | 13.2 | 4.8 | 0 | 2024-04-19 | 9 | 9 | 0 | 2023-04-19 | 2.2 | 15.8 | 0 | 2022-04-19 | 0.6 | 17.4 | 0 | 2021-04-19 | 10.9 | 7.1 | 0 | 2020-04-19 | 7 | 11 | 0 | 2019-04-19 | 6.1 | 11.9 | 0 | 2018-04-19 | 1.5 | 16.5 | 0 | 2017-04-19 | 7.8 | 10.2 | 0 | 2016-04-19 | 7.2 | 10.8 | 0 | 11.45 | 0
2025-04-19 | 15.4 | 2.6 | 0 | 2024-04-19 | 9.7 | 8.3 | 0 | 2023-04-19 | 3.3 | 14.7 | 0 | 2022-04-19 | 1.8 | 16.2 | 0 | 2021-04-19 | 12.3 | 5.7 | 0 | 2020-04-19 | 6.3 | 11.7 | 0 | 2019-04-19 | 5.9 | 12.1 | 0 | 2018-04-19 | 1.4 | 16.6 | 0 | 2017-04-19 | 8.2 | 9.8 | 0 | 2016-04-19 | 9.5 | 8.5 | 0 | 10.62 | 0
2025-04-19 | 17.2 | 0.8 | 0 | 2024-04-19 | 11.2 | 6.8 | 0 | 2023-04-19 | 3.5 | 14.5 | 0 | 2022-04-19 | 2.2 | 15.8 | 0 | 2021-04-19 | 13.7 | 4.3 | 0 | 2020-04-19 | 5.8 | 12.2 | 0 | 2019-04-19 | 5.9 | 12.1 | 0 | 2018-04-19 | 1.6 | 16.4 | 0 | 2017-04-19 | 8.1 | 9.9 | 0 | 2016-04-19 | 10.8 | 7.2 | 0 | 10 | 0
2025-04-19 | 18.7 | 0 | 0.7 | 2024-04-19 | 11.6 | 6.4 | 0 | 2023-04-19 | 2.9 | 15.1 | 0 | 2022-04-19 | 2.8 | 15.2 | 0 | 2021-04-19 | 15 | 3 | 0 | 2020-04-19 | 5.8 | 12.2 | 0 | 2019-04-19 | 5.8 | 12.2 | 0 | 2018-04-19 | 1.9 | 16.1 | 0 | 2017-04-19 | 7.5 | 10.5 | 0 | 2016-04-19 | 12.5 | 5.5 | 0 | 9.62 | 0.07
2025-04-19 | 19.9 | 0 | 1.9 | 2024-04-19 | 11.2 | 6.8 | 0 | 2023-04-19 | 3.8 | 14.2 | 0 | 2022-04-19 | 2.6 | 15.4 | 0 | 2021-04-19 | 15.2 | 2.8 | 0 | 2020-04-19 | 5.5 | 12.5 | 0 | 2019-04-19 | 5.5 | 12.5 | 0 | 2018-04-19 | 2.3 | 15.7 | 0 | 2017-04-19 | 7.7 | 10.3 | 0 | 2016-04-19 | 13.4 | 4.6 | 0 | 9.48 | 0.19
2025-04-19 | 19.6 | 0 | 1.6 | 2024-04-19 | 11.6 | 6.4 | 0 | 2023-04-19 | 3.3 | 14.7 | 0 | 2022-04-19 | 2.9 | 15.1 | 0 | 2021-04-19 | 17.6 | 0.4 | 0 | 2020-04-19 | 6 | 12 | 0 | 2019-04-19 | 5.4 | 12.6 | 0 | 2018-04-19 | 3 | 15 | 0 | 2017-04-19 | 8.2 | 9.8 | 0 | 2016-04-19 | 13.7 | 4.3 | 0 | 9.03 | 0.16
2025-04-19 | 19.4 | 0 | 1.4 | 2024-04-19 | 10.7 | 7.3 | 0 | 2023-04-19 | 3.6 | 14.4 | 0 | 2022-04-19 | 2.8 | 15.2 | 0 | 2021-04-19 | 17.8 | 0.2 | 0 | 2020-04-19 | 7.1 | 10.9 | 0 | 2019-04-19 | 5.3 | 12.7 | 0 | 2018-04-19 | 3 | 15 | 0 | 2017-04-19 | 8.9 | 9.1 | 0 | 2016-04-19 | 14 | 4 | 0 | 8.88 | 0.14
2025-04-19 | 17.6 | 0.4 | 0 | 2024-04-19 | 9.9 | 8.1 | 0 | 2023-04-19 | 3.4 | 14.6 | 0 | 2022-04-19 | 3.6 | 14.4 | 0 | 2021-04-19 | 16.1 | 1.9 | 0 | 2020-04-19 | 7.3 | 10.7 | 0 | 2019-04-19 | 5.2 | 12.8 | 0 | 2018-04-19 | 2.5 | 15.5 | 0 | 2017-04-19 | 9.3 | 8.7 | 0 | 2016-04-19 | 13.9 | 4.1 | 0 | 9.12 | 0
2025-04-19 | 16.3 | 1.7 | 0 | 2024-04-19 | 10.5 | 7.5 | 0 | 2023-04-19 | 3.2 | 14.8 | 0 | 2022-04-19 | 3.8 | 14.2 | 0 | 2021-04-19 | 16.4 | 1.6 | 0 | 2020-04-19 | 7.3 | 10.7 | 0 | 2019-04-19 | 5.1 | 12.9 | 0 | 2018-04-19 | 1.9 | 16.1 | 0 | 2017-04-19 | 9.8 | 8.2 | 0 | 2016-04-19 | 14.1 | 3.9 | 0 | 9.16 | 0
2025-04-19 | 14.9 | 3.1 | 0 | 2024-04-19 | 11 | 7 | 0 | 2023-04-19 | 2.6 | 15.4 | 0 | 2022-04-19 | 3.2 | 14.8 | 0 | 2021-04-19 | 15.3 | 2.7 | 0 | 2020-04-19 | 4.7 | 13.3 | 0 | 2019-04-19 | 4.9 | 13.1 | 0 | 2018-04-19 | 1.6 | 16.4 | 0 | 2017-04-19 | 9.8 | 8.2 | 0 | 2016-04-19 | 13.3 | 4.7 | 0 | 9.87 | 0
2025-04-19 | 13.7 | 4.3 | 0 | 2024-04-19 | 10.2 | 7.8 | 0 | 2023-04-19 | 2 | 16 | 0 | 2022-04-19 | 2.9 | 15.1 | 0 | 2021-04-19 | 13 | 5 | 0 | 2020-04-19 | 3.6 | 14.4 | 0 | 2019-04-19 | 4.5 | 13.5 | 0 | 2018-04-19 | 1.2 | 16.8 | 0 | 2017-04-19 | 9.7 | 8.3 | 0 | 2016-04-19 | 11.9 | 6.1 | 0 | 10.73 | 0
2025-04-19 | 12.1 | 5.9 | 0 | 2024-04-19 | 10 | 8 | 0 | 2023-04-19 | 2.1 | 15.9 | 0 | 2022-04-19 | 3.1 | 14.9 | 0 | 2021-04-19 | 11.9 | 6.1 | 0 | 2020-04-19 | 2.5 | 15.5 | 0 | 2019-04-19 | 4.3 | 13.7 | 0 | 2018-04-19 | 0.9 | 17.1 | 0 | 2017-04-19 | 9.4 | 8.6 | 0 | 2016-04-19 | 11 | 7 | 0 | 11.27 | 0
2025-04-19 | 9.2 | 8.8 | 0 | 2024-04-19 | 7.9 | 10.1 | 0 | 2023-04-19 | 2.1 | 15.9 | 0 | 2022-04-19 | 3.3 | 14.7 | 0 | 2021-04-19 | 10.8 | 7.2 | 0 | 2020-04-19 | 1.4 | 16.6 | 0 | 2019-04-19 | 4.2 | 13.8 | 0 | 2018-04-19 | 0.2 | 17.8 | 0 | 2017-04-19 | 9.2 | 8.8 | 0 | 2016-04-19 | 9.8 | 8.2 | 0 | 12.19 | 0
2025-04-19 | 7.6 | 10.4 | 0 | 2024-04-19 | 7.2 | 10.8 | 0 | 2023-04-19 | 1.9 | 16.1 | 0 | 2022-04-19 | 3.1 | 14.9 | 0 | 2021-04-19 | 10.7 | 7.3 | 0 | 2020-04-19 | 0.6 | 17.4 | 0 | 2019-04-19 | 4.1 | 13.9 | 0 | 2018-04-19 | 0.1 | 17.9 | 0 | 2017-04-19 | 8.7 | 9.3 | 0 | 2016-04-19 | 7.5 | 10.5 | 0 | 12.85 | 0
2025-04-19 | 6 | 12 | 0 | 2024-04-19 | 5.5 | 12.5 | 0 | 2023-04-19 | 2 | 16 | 0 | 2022-04-19 | 2.2 | 15.8 | 0 | 2021-04-19 | 11 | 7 | 0 | 2020-04-19 | -0.7 | 18.7 | 0 | 2019-04-19 | 4.1 | 13.9 | 0 | 2018-04-19 | 0 | 18 | 0 | 2017-04-19 | 7.2 | 10.8 | 0 | 2016-04-19 | 6.1 | 11.9 | 0 | 13.66 | 0
2025-04-20 | 4.3 | 13.7 | 0 | 2024-04-20 | 5.7 | 12.3 | 0 | 2023-04-20 | 1.6 | 16.4 | 0 | 2022-04-20 | 1.6 | 16.4 | 0 | 2021-04-20 | 11.2 | 6.8 | 0 | 2020-04-20 | -1.6 | 19.6 | 0 | 2019-04-20 | 4.1 | 13.9 | 0 | 2018-04-20 | -0.1 | 18.1 | 0 | 2017-04-20 | 6.5 | 11.5 | 0 | 2016-04-20 | 5.4 | 12.6 | 0 | 14.13 | 0
2025-04-20 | 3.2 | 14.8 | 0 | 2024-04-20 | 5.4 | 12.6 | 0 | 2023-04-20 | 1.7 | 16.3 | 0 | 2022-04-20 | 1.3 | 16.7 | 0 | 2021-04-20 | 11.2 | 6.8 | 0 | 2020-04-20 | -1.7 | 19.7 | 0 | 2019-04-20 | 4.1 | 13.9 | 0 | 2018-04-20 | 0 | 18 | 0 | 2017-04-20 | 6 | 12 | 0 | 2016-04-20 | 5.6 | 12.4 | 0 | 14.32 | 0
2025-04-20 | 2.6 | 15.4 | 0 | 2024-04-20 | 5 | 13 | 0 | 2023-04-20 | 1.6 | 16.4 | 0 | 2022-04-20 | 1.2 | 16.8 | 0 | 2021-04-20 | 9.3 | 8.7 | 0 | 2020-04-20 | -2.4 | 20.4 | 0 | 2019-04-20 | 4.1 | 13.9 | 0 | 2018-04-20 | -0.4 | 18.4 | 0 | 2017-04-20 | 5.8 | 12.2 | 0 | 2016-04-20 | 4.2 | 13.8 | 0 | 14.9 | 0
2025-04-20 | 2.5 | 15.5 | 0 | 2024-04-20 | 4.7 | 13.3 | 0 | 2023-04-20 | 1.8 | 16.2 | 0 | 2022-04-20 | 1.1 | 16.9 | 0 | 2021-04-20 | 7.8 | 10.2 | 0 | 2020-04-20 | -3.4 | 21.4 | 0 | 2019-04-20 | 4.2 | 13.8 | 0 | 2018-04-20 | -1.2 | 19.2 | 0 | 2017-04-20 | 5.6 | 12.4 | 0 | 2016-04-20 | 3.1 | 14.9 | 0 | 15.38 | 0
2025-04-20 | 1.6 | 16.4 | 0 | 2024-04-20 | 3.9 | 14.1 | 0 | 2023-04-20 | 1.8 | 16.2 | 0 | 2022-04-20 | 0.9 | 17.1 | 0 | 2021-04-20 | 5.7 | 12.3 | 0 | 2020-04-20 | -4.6 | 22.6 | 0 | 2019-04-20 | 4.1 | 13.9 | 0 | 2018-04-20 | -1.6 | 19.6 | 0 | 2017-04-20 | 5.1 | 12.9 | 0 | 2016-04-20 | 2.7 | 15.3 | 0 | 16.04 | 0
2025-04-20 | 1.6 | 16.4 | 0 | 2024-04-20 | 2.4 | 15.6 | 0 | 2023-04-20 | 0.6 | 17.4 | 0 | 2022-04-20 | 0.9 | 17.1 | 0 | 2021-04-20 | 5.4 | 12.6 | 0 | 2020-04-20 | -5.5 | 23.5 | 0 | 2019-04-20 | 4.1 | 13.9 | 0 | 2018-04-20 | -1.4 | 19.4 | 0 | 2017-04-20 | 4.5 | 13.5 | 0 | 2016-04-20 | 2.3 | 15.7 | 0 | 16.51 | 0
2025-04-20 | 1.5 | 16.5 | 0 | 2024-04-20 | 2.6 | 15.4 | 0 | 2023-04-20 | 0.6 | 17.4 | 0 | 2022-04-20 | 0.5 | 17.5 | 0 | 2021-04-20 | 4.9 | 13.1 | 0 | 2020-04-20 | -3.7 | 21.7 | 0 | 2019-04-20 | 4.4 | 13.6 | 0 | 2018-04-20 | -0.8 | 18.8 | 0 | 2017-04-20 | 3.8 | 14.2 | 0 | 2016-04-20 | 3.2 | 14.8 | 0 | 16.3 | 0
2025-04-20 | 2.3 | 15.7 | 0 | 2024-04-20 | 4.2 | 13.8 | 0 | 2023-04-20 | 1.5 | 16.5 | 0 | 2022-04-20 | 1 | 17 | 0 | 2021-04-20 | 4.4 | 13.6 | 0 | 2020-04-20 | -3.2 | 21.2 | 0 | 2019-04-20 | 4.9 | 13.1 | 0 | 2018-04-20 | -0.1 | 18.1 | 0 | 2017-04-20 | 4.4 | 13.6 | 0 | 2016-04-20 | 4.7 | 13.3 | 0 | 15.59 | 0
2025-04-20 | 3.1 | 14.9 | 0 | 2024-04-20 | 5.2 | 12.8 | 0 | 2023-04-20 | 2.8 | 15.2 | 0 | 2022-04-20 | 1.2 | 16.8 | 0 | 2021-04-20 | 5.6 | 12.4 | 0 | 2020-04-20 | -2.2 | 20.2 | 0 | 2019-04-20 | 6 | 12 | 0 | 2018-04-20 | 1 | 17 | 0 | 2017-04-20 | 5 | 13 | 0 | 2016-04-20 | 5.8 | 12.2 | 0 | 14.65 | 0
2025-04-20 | 4.1 | 13.9 | 0 | 2024-04-20 | 5.6 | 12.4 | 0 | 2023-04-20 | 3.3 | 14.7 | 0 | 2022-04-20 | 2.1 | 15.9 | 0 | 2021-04-20 | 5.7 | 12.3 | 0 | 2020-04-20 | -0.9 | 18.9 | 0 | 2019-04-20 | 6.1 | 11.9 | 0 | 2018-04-20 | 2.1 | 15.9 | 0 | 2017-04-20 | 5.8 | 12.2 | 0 | 2016-04-20 | 7.2 | 10.8 | 0 | 13.89 | 0
2025-04-20 | 5.2 | 12.8 | 0 | 2024-04-20 | 4.1 | 13.9 | 0 | 2023-04-20 | 3.9 | 14.1 | 0 | 2022-04-20 | 2.8 | 15.2 | 0 | 2021-04-20 | 5.9 | 12.1 | 0 | 2020-04-20 | -0.1 | 18.1 | 0 | 2019-04-20 | 6.9 | 11.1 | 0 | 2018-04-20 | 3.5 | 14.5 | 0 | 2017-04-20 | 6.6 | 11.4 | 0 | 2016-04-20 | 8.6 | 9.4 | 0 | 13.26 | 0
2025-04-20 | 6.1 | 11.9 | 0 | 2024-04-20 | 4 | 14 | 0 | 2023-04-20 | 4.9 | 13.1 | 0 | 2022-04-20 | 4.4 | 13.6 | 0 | 2021-04-20 | 7.3 | 10.7 | 0 | 2020-04-20 | 0.2 | 17.8 | 0 | 2019-04-20 | 7.4 | 10.6 | 0 | 2018-04-20 | 5.3 | 12.7 | 0 | 2017-04-20 | 7.6 | 10.4 | 0 | 2016-04-20 | 10.4 | 7.6 | 0 | 12.24 | 0
2025-04-20 | 7.7 | 10.3 | 0 | 2024-04-20 | 4.1 | 13.9 | 0 | 2023-04-20 | 6.6 | 11.4 | 0 | 2022-04-20 | 5.9 | 12.1 | 0 | 2021-04-20 | 6 | 12 | 0 | 2020-04-20 | 3.1 | 14.9 | 0 | 2019-04-20 | 7.5 | 10.5 | 0 | 2018-04-20 | 7 | 11 | 0 | 2017-04-20 | 8.8 | 9.2 | 0 | 2016-04-20 | 11.2 | 6.8 | 0 | 11.21 | 0
2025-04-20 | 8.9 | 9.1 | 0 | 2024-04-20 | 4.6 | 13.4 | 0 | 2023-04-20 | 7 | 11 | 0 | 2022-04-20 | 6.5 | 11.5 | 0 | 2021-04-20 | 6.5 | 11.5 | 0 | 2020-04-20 | 3.5 | 14.5 | 0 | 2019-04-20 | 6.3 | 11.7 | 0 | 2018-04-20 | 8 | 10 | 0 | 2017-04-20 | 8.9 | 9.1 | 0 | 2016-04-20 | 12.6 | 5.4 | 0 | 10.72 | 0
2025-04-20 | 9.7 | 8.3 | 0 | 2024-04-20 | 6.5 | 11.5 | 0 | 2023-04-20 | 8.5 | 9.5 | 0 | 2022-04-20 | 7.4 | 10.6 | 0 | 2021-04-20 | 6.8 | 11.2 | 0 | 2020-04-20 | 4.1 | 13.9 | 0 | 2019-04-20 | 6.4 | 11.6 | 0 | 2018-04-20 | 7.9 | 10.1 | 0 | 2017-04-20 | 9.6 | 8.4 | 0 | 2016-04-20 | 14.1 | 3.9 | 0 | 9.9 | 0
2025-04-20 | 10.2 | 7.8 | 0 | 2024-04-20 | 7.8 | 10.2 | 0 | 2023-04-20 | 9.2 | 8.8 | 0 | 2022-04-20 | 8.2 | 9.8 | 0 | 2021-04-20 | 6 | 12 | 0 | 2020-04-20 | 4.7 | 13.3 | 0 | 2019-04-20 | 6.7 | 11.3 | 0 | 2018-04-20 | 9.9 | 8.1 | 0 | 2017-04-20 | 10.2 | 7.8 | 0 | 2016-04-20 | 14.6 | 3.4 | 0 | 9.25 | 0
2025-04-20 | 9.9 | 8.1 | 0 | 2024-04-20 | 3.9 | 14.1 | 0 | 2023-04-20 | 9.4 | 8.6 | 0 | 2022-04-20 | 8 | 10 | 0 | 2021-04-20 | 5.8 | 12.2 | 0 | 2020-04-20 | 5.2 | 12.8 | 0 | 2019-04-20 | 6.3 | 11.7 | 0 | 2018-04-20 | 9.8 | 8.2 | 0 | 2017-04-20 | 10.1 | 7.9 | 0 | 2016-04-20 | 15.6 | 2.4 | 0 | 9.6 | 0
2025-04-20 | 10.5 | 7.5 | 0 | 2024-04-20 | 6.8 | 11.2 | 0 | 2023-04-20 | 9.7 | 8.3 | 0 | 2022-04-20 | 8.3 | 9.7 | 0 | 2021-04-20 | 5 | 13 | 0 | 2020-04-20 | 6 | 12 | 0 | 2019-04-20 | 6.3 | 11.7 | 0 | 2018-04-20 | 9.8 | 8.2 | 0 | 2017-04-20 | 9.6 | 8.4 | 0 | 2016-04-20 | 15.3 | 2.7 | 0 | 9.27 | 0
2025-04-20 | 10.1 | 7.9 | 0 | 2024-04-20 | 6.6 | 11.4 | 0 | 2023-04-20 | 9 | 9 | 0 | 2022-04-20 | 7.8 | 10.2 | 0 | 2021-04-20 | 4.3 | 13.7 | 0 | 2020-04-20 | 5 | 13 | 0 | 2019-04-20 | 6.1 | 11.9 | 0 | 2018-04-20 | 8.8 | 9.2 | 0 | 2017-04-20 | 9.2 | 8.8 | 0 | 2016-04-20 | 14.6 | 3.4 | 0 | 9.85 | 0
2025-04-20 | 8.2 | 9.8 | 0 | 2024-04-20 | 6.4 | 11.6 | 0 | 2023-04-20 | 8.3 | 9.7 | 0 | 2022-04-20 | 6.9 | 11.1 | 0 | 2021-04-20 | 3.7 | 14.3 | 0 | 2020-04-20 | 2.2 | 15.8 | 0 | 2019-04-20 | 5.8 | 12.2 | 0 | 2018-04-20 | 7.6 | 10.4 | 0 | 2017-04-20 | 8.1 | 9.9 | 0 | 2016-04-20 | 11.2 | 6.8 | 0 | 11.16 | 0
2025-04-20 | 5 | 13 | 0 | 2024-04-20 | 5.1 | 12.9 | 0 | 2023-04-20 | 7.8 | 10.2 | 0 | 2022-04-20 | 3.6 | 14.4 | 0 | 2021-04-20 | 3.5 | 14.5 | 0 | 2020-04-20 | 0.4 | 17.6 | 0 | 2019-04-20 | 5.7 | 12.3 | 0 | 2018-04-20 | 5.8 | 12.2 | 0 | 2017-04-20 | 7.6 | 10.4 | 0 | 2016-04-20 | 10.7 | 7.3 | 0 | 12.48 | 0
2025-04-20 | 3.4 | 14.6 | 0 | 2024-04-20 | 5.4 | 12.6 | 0 | 2023-04-20 | 7.5 | 10.5 | 0 | 2022-04-20 | 2.8 | 15.2 | 0 | 2021-04-20 | 3 | 15 | 0 | 2020-04-20 | -0.1 | 18.1 | 0 | 2019-04-20 | 5.7 | 12.3 | 0 | 2018-04-20 | 4.9 | 13.1 | 0 | 2017-04-20 | 7.2 | 10.8 | 0 | 2016-04-20 | 9.5 | 8.5 | 0 | 13.07 | 0
2025-04-20 | 4.1 | 13.9 | 0 | 2024-04-20 | 3.6 | 14.4 | 0 | 2023-04-20 | 6.9 | 11.1 | 0 | 2022-04-20 | 2.8 | 15.2 | 0 | 2021-04-20 | 2.5 | 15.5 | 0 | 2020-04-20 | 0.3 | 17.7 | 0 | 2019-04-20 | 5.7 | 12.3 | 0 | 2018-04-20 | 2.5 | 15.5 | 0 | 2017-04-20 | 7.3 | 10.7 | 0 | 2016-04-20 | 7.2 | 10.8 | 0 | 13.71 | 0
2025-04-20 | 2.7 | 15.3 | 0 | 2024-04-20 | 2.5 | 15.5 | 0 | 2023-04-20 | 6.8 | 11.2 | 0 | 2022-04-20 | 1.2 | 16.8 | 0 | 2021-04-20 | 2.1 | 15.9 | 0 | 2020-04-20 | -0.9 | 18.9 | 0 | 2019-04-20 | 5.7 | 12.3 | 0 | 2018-04-20 | 2.2 | 15.8 | 0 | 2017-04-20 | 7 | 11 | 0 | 2016-04-20 | 7.3 | 10.7 | 0 | 14.34 | 0
2025-04-21 | 3.5 | 14.5 | 0 | 2024-04-21 | 2 | 16 | 0 | 2023-04-21 | 6.3 | 11.7 | 0 | 2022-04-21 | 0.6 | 17.4 | 0 | 2021-04-21 | 1.9 | 16.1 | 0 | 2020-04-21 | -1.3 | 19.3 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | 1.9 | 16.1 | 0 | 2017-04-21 | 6.5 | 11.5 | 0 | 2016-04-21 | 6.5 | 11.5 | 0 | 14.64 | 0
2025-04-21 | 2 | 16 | 0 | 2024-04-21 | 0.7 | 17.3 | 0 | 2023-04-21 | 6 | 12 | 0 | 2022-04-21 | 0.1 | 17.9 | 0 | 2021-04-21 | 1.6 | 16.4 | 0 | 2020-04-21 | -0.1 | 18.1 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | 0.3 | 17.7 | 0 | 2017-04-21 | 6.5 | 11.5 | 0 | 2016-04-21 | 5.7 | 12.3 | 0 | 15.15 | 0
2025-04-21 | 1 | 17 | 0 | 2024-04-21 | 0.6 | 17.4 | 0 | 2023-04-21 | 5.8 | 12.2 | 0 | 2022-04-21 | 0.8 | 17.2 | 0 | 2021-04-21 | 0.5 | 17.5 | 0 | 2020-04-21 | -1.5 | 19.5 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | 0.4 | 17.6 | 0 | 2017-04-21 | 6.4 | 11.6 | 0 | 2016-04-21 | 3.6 | 14.4 | 0 | 15.67 | 0
2025-04-21 | 0.8 | 17.2 | 0 | 2024-04-21 | 0 | 18 | 0 | 2023-04-21 | 5.3 | 12.7 | 0 | 2022-04-21 | 0.7 | 17.3 | 0 | 2021-04-21 | -1.3 | 19.3 | 0 | 2020-04-21 | -2.6 | 20.6 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | -0.8 | 18.8 | 0 | 2017-04-21 | 6 | 12 | 0 | 2016-04-21 | 3.2 | 14.8 | 0 | 16.3 | 0
2025-04-21 | -0.6 | 18.6 | 0 | 2024-04-21 | 0.8 | 17.2 | 0 | 2023-04-21 | 4.7 | 13.3 | 0 | 2022-04-21 | 1.8 | 16.2 | 0 | 2021-04-21 | -1.1 | 19.1 | 0 | 2020-04-21 | -1.9 | 19.9 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | -1.3 | 19.3 | 0 | 2017-04-21 | 5.9 | 12.1 | 0 | 2016-04-21 | 1.2 | 16.8 | 0 | 16.48 | 0
2025-04-21 | -0.6 | 18.6 | 0 | 2024-04-21 | 1.4 | 16.6 | 0 | 2023-04-21 | 3.5 | 14.5 | 0 | 2022-04-21 | 1.9 | 16.1 | 0 | 2021-04-21 | -2.4 | 20.4 | 0 | 2020-04-21 | -0.6 | 18.6 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | -2.3 | 20.3 | 0 | 2017-04-21 | 6.2 | 11.8 | 0 | 2016-04-21 | 2.8 | 15.2 | 0 | 16.44 | 0
2025-04-21 | 1.6 | 16.4 | 0 | 2024-04-21 | 1.6 | 16.4 | 0 | 2023-04-21 | 3.2 | 14.8 | 0 | 2022-04-21 | 3 | 15 | 0 | 2021-04-21 | -3 | 21 | 0 | 2020-04-21 | 0.2 | 17.8 | 0 | 2019-04-21 | 5.8 | 12.2 | 0 | 2018-04-21 | -0.6 | 18.6 | 0 | 2017-04-21 | 6.8 | 11.2 | 0 | 2016-04-21 | 2.8 | 15.2 | 0 | 15.86 | 0
2025-04-21 | 3.6 | 14.4 | 0 | 2024-04-21 | 2.1 | 15.9 | 0 | 2023-04-21 | 4.2 | 13.8 | 0 | 2022-04-21 | 3.4 | 14.6 | 0 | 2021-04-21 | -2.6 | 20.6 | 0 | 2020-04-21 | 1.7 | 16.3 | 0 | 2019-04-21 | 6.6 | 11.4 | 0 | 2018-04-21 | 2 | 16 | 0 | 2017-04-21 | 7.5 | 10.5 | 0 | 2016-04-21 | 7.1 | 10.9 | 0 | 14.44 | 0
2025-04-21 | 5.8 | 12.2 | 0 | 2024-04-21 | 3.3 | 14.7 | 0 | 2023-04-21 | 5.6 | 12.4 | 0 | 2022-04-21 | 6.5 | 11.5 | 0 | 2021-04-21 | -3.1 | 21.1 | 0 | 2020-04-21 | 0.9 | 17.1 | 0 | 2019-04-21 | 7.3 | 10.7 | 0 | 2018-04-21 | 3.8 | 14.2 | 0 | 2017-04-21 | 8.2 | 9.8 | 0 | 2016-04-21 | 10.6 | 7.4 | 0 | 13.11 | 0
2025-04-21 | 6.5 | 11.5 | 0 | 2024-04-21 | 4.5 | 13.5 | 0 | 2023-04-21 | 8 | 10 | 0 | 2022-04-21 | 10.1 | 7.9 | 0 | 2021-04-21 | -2.9 | 20.9 | 0 | 2020-04-21 | 3.4 | 14.6 | 0 | 2019-04-21 | 8.1 | 9.9 | 0 | 2018-04-21 | 5.3 | 12.7 | 0 | 2017-04-21 | 8.9 | 9.1 | 0 | 2016-04-21 | 12.9 | 5.1 | 0 | 11.52 | 0
2025-04-21 | 8.6 | 9.4 | 0 | 2024-04-21 | 4.6 | 13.4 | 0 | 2023-04-21 | 9.6 | 8.4 | 0 | 2022-04-21 | 11.8 | 6.2 | 0 | 2021-04-21 | -2.6 | 20.6 | 0 | 2020-04-21 | 4.4 | 13.6 | 0 | 2019-04-21 | 8.7 | 9.3 | 0 | 2018-04-21 | 7 | 11 | 0 | 2017-04-21 | 10.3 | 7.7 | 0 | 2016-04-21 | 15.6 | 2.4 | 0 | 10.2 | 0
2025-04-21 | 9.6 | 8.4 | 0 | 2024-04-21 | 5.4 | 12.6 | 0 | 2023-04-21 | 10.5 | 7.5 | 0 | 2022-04-21 | 12.4 | 5.6 | 0 | 2021-04-21 | -2.1 | 20.1 | 0 | 2020-04-21 | 4.3 | 13.7 | 0 | 2019-04-21 | 9.5 | 8.5 | 0 | 2018-04-21 | 9 | 9 | 0 | 2017-04-21 | 11.2 | 6.8 | 0 | 2016-04-21 | 18.2 | 0 | 0.2 | 9.22 | 0.02
2025-04-21 | 11.2 | 6.8 | 0 | 2024-04-21 | 6.4 | 11.6 | 0 | 2023-04-21 | 12 | 6 | 0 | 2022-04-21 | 9.5 | 8.5 | 0 | 2021-04-21 | -2.5 | 20.5 | 0 | 2020-04-21 | 2.3 | 15.7 | 0 | 2019-04-21 | 10.6 | 7.4 | 0 | 2018-04-21 | 9.4 | 8.6 | 0 | 2017-04-21 | 13.4 | 4.6 | 0 | 2016-04-21 | 19.9 | 0 | 1.9 | 8.97 | 0.19
2025-04-21 | 10.9 | 7.1 | 0 | 2024-04-21 | 7 | 11 | 0 | 2023-04-21 | 13.6 | 4.4 | 0 | 2022-04-21 | 8.7 | 9.3 | 0 | 2021-04-21 | -0.3 | 18.3 | 0 | 2020-04-21 | 6.1 | 11.9 | 0 | 2019-04-21 | 12.2 | 5.8 | 0 | 2018-04-21 | 11 | 7 | 0 | 2017-04-21 | 15 | 3 | 0 | 2016-04-21 | 20 | 0 | 2 | 7.78 | 0.2
2025-04-21 | 10.3 | 7.7 | 0 | 2024-04-21 | 8 | 10 | 0 | 2023-04-21 | 14.5 | 3.5 | 0 | 2022-04-21 | 8.8 | 9.2 | 0 | 2021-04-21 | 0.6 | 17.4 | 0 | 2020-04-21 | 6.7 | 11.3 | 0 | 2019-04-21 | 12.7 | 5.3 | 0 | 2018-04-21 | 11.3 | 6.7 | 0 | 2017-04-21 | 14.2 | 3.8 | 0 | 2016-04-21 | 22.2 | 0 | 4.2 | 7.49 | 0.42
2025-04-21 | 8.1 | 9.9 | 0 | 2024-04-21 | 9 | 9 | 0 | 2023-04-21 | 15.3 | 2.7 | 0 | 2022-04-21 | 8.9 | 9.1 | 0 | 2021-04-21 | 1.5 | 16.5 | 0 | 2020-04-21 | 4.6 | 13.4 | 0 | 2019-04-21 | 12.8 | 5.2 | 0 | 2018-04-21 | 12 | 6 | 0 | 2017-04-21 | 13.1 | 4.9 | 0 | 2016-04-21 | 21.9 | 0 | 3.9 | 7.67 | 0.39
2025-04-21 | 7.9 | 10.1 | 0 | 2024-04-21 | 8.8 | 9.2 | 0 | 2023-04-21 | 15.1 | 2.9 | 0 | 2022-04-21 | 9 | 9 | 0 | 2021-04-21 | 2 | 16 | 0 | 2020-04-21 | 4.3 | 13.7 | 0 | 2019-04-21 | 12.5 | 5.5 | 0 | 2018-04-21 | 12.1 | 5.9 | 0 | 2017-04-21 | 12 | 6 | 0 | 2016-04-21 | 21.7 | 0 | 3.7 | 7.83 | 0.37
2025-04-21 | 6.8 | 11.2 | 0 | 2024-04-21 | 7.7 | 10.3 | 0 | 2023-04-21 | 15 | 3 | 0 | 2022-04-21 | 9.6 | 8.4 | 0 | 2021-04-21 | 1.5 | 16.5 | 0 | 2020-04-21 | 2.6 | 15.4 | 0 | 2019-04-21 | 12.3 | 5.7 | 0 | 2018-04-21 | 12 | 6 | 0 | 2017-04-21 | 12.8 | 5.2 | 0 | 2016-04-21 | 21 | 0 | 3 | 8.17 | 0.3
2025-04-21 | 6.3 | 11.7 | 0 | 2024-04-21 | 8.4 | 9.6 | 0 | 2023-04-21 | 13.1 | 4.9 | 0 | 2022-04-21 | 9.9 | 8.1 | 0 | 2021-04-21 | 0.6 | 17.4 | 0 | 2020-04-21 | 1.6 | 16.4 | 0 | 2019-04-21 | 11.8 | 6.2 | 0 | 2018-04-21 | 11.1 | 6.9 | 0 | 2017-04-21 | 11.3 | 6.7 | 0 | 2016-04-21 | 19.9 | 0 | 1.9 | 8.79 | 0.19
2025-04-21 | 5.6 | 12.4 | 0 | 2024-04-21 | 6.8 | 11.2 | 0 | 2023-04-21 | 11.8 | 6.2 | 0 | 2022-04-21 | 9.2 | 8.8 | 0 | 2021-04-21 | 0.3 | 17.7 | 0 | 2020-04-21 | 0.2 | 17.8 | 0 | 2019-04-21 | 11 | 7 | 0 | 2018-04-21 | 9.1 | 8.9 | 0 | 2017-04-21 | 8.9 | 9.1 | 0 | 2016-04-21 | 17.5 | 0.5 | 0 | 9.96 | 0
2025-04-21 | 5.8 | 12.2 | 0 | 2024-04-21 | 3.9 | 14.1 | 0 | 2023-04-21 | 11.5 | 6.5 | 0 | 2022-04-21 | 9 | 9 | 0 | 2021-04-21 | 0.3 | 17.7 | 0 | 2020-04-21 | -1.4 | 19.4 | 0 | 2019-04-21 | 10.7 | 7.3 | 0 | 2018-04-21 | 8.3 | 9.7 | 0 | 2017-04-21 | 8.6 | 9.4 | 0 | 2016-04-21 | 17.6 | 0.4 | 0 | 10.57 | 0
2025-04-21 | 6.3 | 11.7 | 0 | 2024-04-21 | 1.2 | 16.8 | 0 | 2023-04-21 | 10.7 | 7.3 | 0 | 2022-04-21 | 7.2 | 10.8 | 0 | 2021-04-21 | -0.2 | 18.2 | 0 | 2020-04-21 | -1.9 | 19.9 | 0 | 2019-04-21 | 9.8 | 8.2 | 0 | 2018-04-21 | 5.6 | 12.4 | 0 | 2017-04-21 | 8.2 | 9.8 | 0 | 2016-04-21 | 16.9 | 1.1 | 0 | 11.62 | 0
2025-04-21 | 6.4 | 11.6 | 0 | 2024-04-21 | 0.4 | 17.6 | 0 | 2023-04-21 | 10.9 | 7.1 | 0 | 2022-04-21 | 7.6 | 10.4 | 0 | 2021-04-21 | -1.3 | 19.3 | 0 | 2020-04-21 | -2.3 | 20.3 | 0 | 2019-04-21 | 8.8 | 9.2 | 0 | 2018-04-21 | 3.6 | 14.4 | 0 | 2017-04-21 | 7.9 | 10.1 | 0 | 2016-04-21 | 14.7 | 3.3 | 0 | 12.33 | 0
2025-04-21 | 7.1 | 10.9 | 0 | 2024-04-21 | -0.4 | 18.4 | 0 | 2023-04-21 | 8.8 | 9.2 | 0 | 2022-04-21 | 6.6 | 11.4 | 0 | 2021-04-21 | -2.2 | 20.2 | 0 | 2020-04-21 | -3 | 21 | 0 | 2019-04-21 | 5.7 | 12.3 | 0 | 2018-04-21 | 1.6 | 16.4 | 0 | 2017-04-21 | 7.5 | 10.5 | 0 | 2016-04-21 | 14.1 | 3.9 | 0 | 13.42 | 0
2025-04-22 | 7.3 | 10.7 | 0 | 2024-04-22 | -1.2 | 19.2 | 0 | 2023-04-22 | 9.8 | 8.2 | 0 | 2022-04-22 | 5.5 | 12.5 | 0 | 2021-04-22 | -2.2 | 20.2 | 0 | 2020-04-22 | -3.8 | 21.8 | 0 | 2019-04-22 | 6.8 | 11.2 | 0 | 2018-04-22 | 4.4 | 13.6 | 0 | 2017-04-22 | 7.1 | 10.9 | 0 | 2016-04-22 | 14.2 | 3.8 | 0 | 13.21 | 0
2025-04-22 | 7.8 | 10.2 | 0 | 2024-04-22 | -1.8 | 19.8 | 0 | 2023-04-22 | 10.2 | 7.8 | 0 | 2022-04-22 | 5.9 | 12.1 | 0 | 2021-04-22 | -2.3 | 20.3 | 0 | 2020-04-22 | -4.8 | 22.8 | 0 | 2019-04-22 | 6.6 | 11.4 | 0 | 2018-04-22 | 1.1 | 16.9 | 0 | 2017-04-22 | 6.9 | 11.1 | 0 | 2016-04-22 | 14.1 | 3.9 | 0 | 13.63 | 0
2025-04-22 | 8 | 10 | 0 | 2024-04-22 | -2 | 20 | 0 | 2023-04-22 | 10 | 8 | 0 | 2022-04-22 | 5.7 | 12.3 | 0 | 2021-04-22 | -3.1 | 21.1 | 0 | 2020-04-22 | -4.8 | 22.8 | 0 | 2019-04-22 | 5.8 | 12.2 | 0 | 2018-04-22 | 2.8 | 15.2 | 0 | 2017-04-22 | 6.7 | 11.3 | 0 | 2016-04-22 | 12 | 6 | 0 | 13.89 | 0
2025-04-22 | 7.8 | 10.2 | 0 | 2024-04-22 | -3.3 | 21.3 | 0 | 2023-04-22 | 9.3 | 8.7 | 0 | 2022-04-22 | 6.1 | 11.9 | 0 | 2021-04-22 | -2.5 | 20.5 | 0 | 2020-04-22 | -5.4 | 23.4 | 0 | 2019-04-22 | 5.1 | 12.9 | 0 | 2018-04-22 | -0.8 | 18.8 | 0 | 2017-04-22 | 6.3 | 11.7 | 0 | 2016-04-22 | 11.2 | 6.8 | 0 | 14.62 | 0
2025-04-22 | 7.9 | 10.1 | 0 | 2024-04-22 | -3 | 21 | 0 | 2023-04-22 | 9 | 9 | 0 | 2022-04-22 | 5.8 | 12.2 | 0 | 2021-04-22 | -3 | 21 | 0 | 2020-04-22 | -5.5 | 23.5 | 0 | 2019-04-22 | 4.8 | 13.2 | 0 | 2018-04-22 | -0.9 | 18.9 | 0 | 2017-04-22 | 6.1 | 11.9 | 0 | 2016-04-22 | 11 | 7 | 0 | 14.78 | 0
2025-04-22 | 8.4 | 9.6 | 0 | 2024-04-22 | -3.8 | 21.8 | 0 | 2023-04-22 | 8 | 10 | 0 | 2022-04-22 | 5.2 | 12.8 | 0 | 2021-04-22 | -3.1 | 21.1 | 0 | 2020-04-22 | -6 | 24 | 0 | 2019-04-22 | 3.7 | 14.3 | 0 | 2018-04-22 | -0.7 | 18.7 | 0 | 2017-04-22 | 5.7 | 12.3 | 0 | 2016-04-22 | 11.2 | 6.8 | 0 | 15.14 | 0
2025-04-22 | 8 | 10 | 0 | 2024-04-22 | -2 | 20 | 0 | 2023-04-22 | 8.6 | 9.4 | 0 | 2022-04-22 | 5.3 | 12.7 | 0 | 2021-04-22 | -3.2 | 21.2 | 0 | 2020-04-22 | -5.8 | 23.8 | 0 | 2019-04-22 | 5.9 | 12.1 | 0 | 2018-04-22 | 0 | 18 | 0 | 2017-04-22 | 5 | 13 | 0 | 2016-04-22 | 11.7 | 6.3 | 0 | 14.65 | 0
2025-04-22 | 8.2 | 9.8 | 0 | 2024-04-22 | -0.6 | 18.6 | 0 | 2023-04-22 | 8.7 | 9.3 | 0 | 2022-04-22 | 6.1 | 11.9 | 0 | 2021-04-22 | -2.2 | 20.2 | 0 | 2020-04-22 | -5.7 | 23.7 | 0 | 2019-04-22 | 5.9 | 12.1 | 0 | 2018-04-22 | 3.6 | 14.4 | 0 | 2017-04-22 | 4.9 | 13.1 | 0 | 2016-04-22 | 12.2 | 5.8 | 0 | 13.89 | 0
2025-04-22 | 8.3 | 9.7 | 0 | 2024-04-22 | 0.2 | 17.8 | 0 | 2023-04-22 | 10.1 | 7.9 | 0 | 2022-04-22 | 6.6 | 11.4 | 0 | 2021-04-22 | -1.9 | 19.9 | 0 | 2020-04-22 | -4.8 | 22.8 | 0 | 2019-04-22 | 9.6 | 8.4 | 0 | 2018-04-22 | 7.4 | 10.6 | 0 | 2017-04-22 | 4.7 | 13.3 | 0 | 2016-04-22 | 12.1 | 5.9 | 0 | 12.77 | 0
2025-04-22 | 9.3 | 8.7 | 0 | 2024-04-22 | 1.3 | 16.7 | 0 | 2023-04-22 | 13.2 | 4.8 | 0 | 2022-04-22 | 7.9 | 10.1 | 0 | 2021-04-22 | -0.9 | 18.9 | 0 | 2020-04-22 | -3.6 | 21.6 | 0 | 2019-04-22 | 12.2 | 5.8 | 0 | 2018-04-22 | 9.3 | 8.7 | 0 | 2017-04-22 | 4.9 | 13.1 | 0 | 2016-04-22 | 12.5 | 5.5 | 0 | 11.39 | 0
2025-04-22 | 9.6 | 8.4 | 0 | 2024-04-22 | 2.7 | 15.3 | 0 | 2023-04-22 | 16.6 | 1.4 | 0 | 2022-04-22 | 9.7 | 8.3 | 0 | 2021-04-22 | 1.1 | 16.9 | 0 | 2020-04-22 | -2.6 | 20.6 | 0 | 2019-04-22 | 15.1 | 2.9 | 0 | 2018-04-22 | 10.4 | 7.6 | 0 | 2017-04-22 | 5.5 | 12.5 | 0 | 2016-04-22 | 13 | 5 | 0 | 9.89 | 0
2025-04-22 | 9.4 | 8.6 | 0 | 2024-04-22 | 4.1 | 13.9 | 0 | 2023-04-22 | 19.2 | 0 | 1.2 | 2022-04-22 | 9.4 | 8.6 | 0 | 2021-04-22 | 2.2 | 15.8 | 0 | 2020-04-22 | -0.8 | 18.8 | 0 | 2019-04-22 | 16.8 | 1.2 | 0 | 2018-04-22 | 11.5 | 6.5 | 0 | 2017-04-22 | 6 | 12 | 0 | 2016-04-22 | 14.6 | 3.4 | 0 | 8.88 | 0.12
2025-04-22 | 10.4 | 7.6 | 0 | 2024-04-22 | 6.5 | 11.5 | 0 | 2023-04-22 | 19.2 | 0 | 1.2 | 2022-04-22 | 10.5 | 7.5 | 0 | 2021-04-22 | 3.2 | 14.8 | 0 | 2020-04-22 | 0.4 | 17.6 | 0 | 2019-04-22 | 17.4 | 0.6 | 0 | 2018-04-22 | 12.3 | 5.7 | 0 | 2017-04-22 | 7.2 | 10.8 | 0 | 2016-04-22 | 13.6 | 4.4 | 0 | 8.05 | 0.12
2025-04-22 | 10 | 8 | 0 | 2024-04-22 | 7.3 | 10.7 | 0 | 2023-04-22 | 21.5 | 0 | 3.5 | 2022-04-22 | 11.8 | 6.2 | 0 | 2021-04-22 | 4.3 | 13.7 | 0 | 2020-04-22 | 1.8 | 16.2 | 0 | 2019-04-22 | 18.1 | 0 | 0.1 | 2018-04-22 | 13.6 | 4.4 | 0 | 2017-04-22 | 8.9 | 9.1 | 0 | 2016-04-22 | 12.6 | 5.4 | 0 | 7.37 | 0.36
2025-04-22 | 10.7 | 7.3 | 0 | 2024-04-22 | 9 | 9 | 0 | 2023-04-22 | 25.9 | 0 | 7.9 | 2022-04-22 | 12.3 | 5.7 | 0 | 2021-04-22 | 4.9 | 13.1 | 0 | 2020-04-22 | 1.7 | 16.3 | 0 | 2019-04-22 | 19.6 | 0 | 1.6 | 2018-04-22 | 14.4 | 3.6 | 0 | 2017-04-22 | 9.8 | 8.2 | 0 | 2016-04-22 | 12.2 | 5.8 | 0 | 6.9 | 0.95
2025-04-22 | 11 | 7 | 0 | 2024-04-22 | 10 | 8 | 0 | 2023-04-22 | 24 | 0 | 6 | 2022-04-22 | 11.8 | 6.2 | 0 | 2021-04-22 | 5.4 | 12.6 | 0 | 2020-04-22 | 2.7 | 15.3 | 0 | 2019-04-22 | 18.9 | 0 | 0.9 | 2018-04-22 | 14.1 | 3.9 | 0 | 2017-04-22 | 10.5 | 7.5 | 0 | 2016-04-22 | 11.8 | 6.2 | 0 | 6.67 | 0.69
2025-04-22 | 10.6 | 7.4 | 0 | 2024-04-22 | 11 | 7 | 0 | 2023-04-22 | 23.5 | 0 | 5.5 | 2022-04-22 | 11.8 | 6.2 | 0 | 2021-04-22 | 5.4 | 12.6 | 0 | 2020-04-22 | 2.7 | 15.3 | 0 | 2019-04-22 | 19 | 0 | 1 | 2018-04-22 | 14.7 | 3.3 | 0 | 2017-04-22 | 10.8 | 7.2 | 0 | 2016-04-22 | 12.1 | 5.9 | 0 | 6.49 | 0.65
2025-04-22 | 9.9 | 8.1 | 0 | 2024-04-22 | 9.6 | 8.4 | 0 | 2023-04-22 | 21.8 | 0 | 3.8 | 2022-04-22 | 11.2 | 6.8 | 0 | 2021-04-22 | 6 | 12 | 0 | 2020-04-22 | 2.5 | 15.5 | 0 | 2019-04-22 | 19.2 | 0 | 1.2 | 2018-04-22 | 14.2 | 3.8 | 0 | 2017-04-22 | 11.1 | 6.9 | 0 | 2016-04-22 | 11.1 | 6.9 | 0 | 6.84 | 0.5
2025-04-22 | 9.2 | 8.8 | 0 | 2024-04-22 | 9.2 | 8.8 | 0 | 2023-04-22 | 21.1 | 0 | 3.1 | 2022-04-22 | 10.6 | 7.4 | 0 | 2021-04-22 | 5.9 | 12.1 | 0 | 2020-04-22 | 1.5 | 16.5 | 0 | 2019-04-22 | 17.4 | 0.6 | 0 | 2018-04-22 | 13.5 | 4.5 | 0 | 2017-04-22 | 10.5 | 7.5 | 0 | 2016-04-22 | 9.3 | 8.7 | 0 | 7.49 | 0.31
2025-04-22 | 8.3 | 9.7 | 0 | 2024-04-22 | 7.3 | 10.7 | 0 | 2023-04-22 | 15.6 | 2.4 | 0 | 2022-04-22 | 9.3 | 8.7 | 0 | 2021-04-22 | 5.3 | 12.7 | 0 | 2020-04-22 | 0.5 | 17.5 | 0 | 2019-04-22 | 15.9 | 2.1 | 0 | 2018-04-22 | 11.8 | 6.2 | 0 | 2017-04-22 | 9.1 | 8.9 | 0 | 2016-04-22 | 7.8 | 10.2 | 0 | 8.91 | 0
2025-04-22 | 7.6 | 10.4 | 0 | 2024-04-22 | 6.4 | 11.6 | 0 | 2023-04-22 | 12.6 | 5.4 | 0 | 2022-04-22 | 7.5 | 10.5 | 0 | 2021-04-22 | 3.8 | 14.2 | 0 | 2020-04-22 | -0.1 | 18.1 | 0 | 2019-04-22 | 14.7 | 3.3 | 0 | 2018-04-22 | 8 | 10 | 0 | 2017-04-22 | 6.2 | 11.8 | 0 | 2016-04-22 | 7.1 | 10.9 | 0 | 10.62 | 0
2025-04-22 | 7.2 | 10.8 | 0 | 2024-04-22 | 5.5 | 12.5 | 0 | 2023-04-22 | 11.4 | 6.6 | 0 | 2022-04-22 | 5.5 | 12.5 | 0 | 2021-04-22 | 2.6 | 15.4 | 0 | 2020-04-22 | -0.3 | 18.3 | 0 | 2019-04-22 | 13.8 | 4.2 | 0 | 2018-04-22 | 8.2 | 9.8 | 0 | 2017-04-22 | 5.8 | 12.2 | 0 | 2016-04-22 | 6.5 | 11.5 | 0 | 11.38 | 0
2025-04-22 | 6.7 | 11.3 | 0 | 2024-04-22 | 4.9 | 13.1 | 0 | 2023-04-22 | 10.9 | 7.1 | 0 | 2022-04-22 | 4.5 | 13.5 | 0 | 2021-04-22 | 1.9 | 16.1 | 0 | 2020-04-22 | -1.1 | 19.1 | 0 | 2019-04-22 | 13.1 | 4.9 | 0 | 2018-04-22 | 10 | 8 | 0 | 2017-04-22 | 7.3 | 10.7 | 0 | 2016-04-22 | 5.9 | 12.1 | 0 | 11.59 | 0
2025-04-22 | 4 | 14 | 0 | 2024-04-22 | 3.8 | 14.2 | 0 | 2023-04-22 | 10.3 | 7.7 | 0 | 2022-04-22 | 2.1 | 15.9 | 0 | 2021-04-22 | 0.2 | 17.8 | 0 | 2020-04-22 | -1.7 | 19.7 | 0 | 2019-04-22 | 12.1 | 5.9 | 0 | 2018-04-22 | 4.6 | 13.4 | 0 | 2017-04-22 | 4.7 | 13.3 | 0 | 2016-04-22 | 5.4 | 12.6 | 0 | 13.45 | 0
2025-04-23 | 4 | 14 | 0 | 2024-04-23 | 3.3 | 14.7 | 0 | 2023-04-23 | 9.8 | 8.2 | 0 | 2022-04-23 | 2.1 | 15.9 | 0 | 2021-04-23 | 0.2 | 17.8 | 0 | 2020-04-23 | -4.5 | 22.5 | 0 | 2019-04-23 | 11.3 | 6.7 | 0 | 2018-04-23 | 7.2 | 10.8 | 0 | 2017-04-23 | 3 | 15 | 0 | 2016-04-23 | 5 | 13 | 0 | 13.86 | 0
2025-04-23 | 4.2 | 13.8 | 0 | 2024-04-23 | 2.3 | 15.7 | 0 | 2023-04-23 | 9 | 9 | 0 | 2022-04-23 | 0.7 | 17.3 | 0 | 2021-04-23 | 0.6 | 17.4 | 0 | 2020-04-23 | -3.9 | 21.9 | 0 | 2019-04-23 | 12 | 6 | 0 | 2018-04-23 | 1.6 | 16.4 | 0 | 2017-04-23 | 1.1 | 16.9 | 0 | 2016-04-23 | 4.5 | 13.5 | 0 | 14.79 | 0
2025-04-23 | 3.5 | 14.5 | 0 | 2024-04-23 | 1.9 | 16.1 | 0 | 2023-04-23 | 8.5 | 9.5 | 0 | 2022-04-23 | 1.2 | 16.8 | 0 | 2021-04-23 | 0.5 | 17.5 | 0 | 2020-04-23 | -6.4 | 24.4 | 0 | 2019-04-23 | 11 | 7 | 0 | 2018-04-23 | 0.7 | 17.3 | 0 | 2017-04-23 | 0.6 | 17.4 | 0 | 2016-04-23 | 3.5 | 14.5 | 0 | 15.5 | 0
2025-04-23 | 2.1 | 15.9 | 0 | 2024-04-23 | 2 | 16 | 0 | 2023-04-23 | 8.1 | 9.9 | 0 | 2022-04-23 | 0.4 | 17.6 | 0 | 2021-04-23 | 0.6 | 17.4 | 0 | 2020-04-23 | -5.9 | 23.9 | 0 | 2019-04-23 | 9.3 | 8.7 | 0 | 2018-04-23 | 1.4 | 16.6 | 0 | 2017-04-23 | -0.3 | 18.3 | 0 | 2016-04-23 | 1.6 | 16.4 | 0 | 16.07 | 0
2025-04-23 | 1.7 | 16.3 | 0 | 2024-04-23 | 3.8 | 14.2 | 0 | 2023-04-23 | 7.9 | 10.1 | 0 | 2022-04-23 | 0.8 | 17.2 | 0 | 2021-04-23 | 1.1 | 16.9 | 0 | 2020-04-23 | -4.8 | 22.8 | 0 | 2019-04-23 | 8.2 | 9.8 | 0 | 2018-04-23 | -0.4 | 18.4 | 0 | 2017-04-23 | -0.7 | 18.7 | 0 | 2016-04-23 | 1 | 17 | 0 | 16.14 | 0
2025-04-23 | 0.9 | 17.1 | 0 | 2024-04-23 | 4.1 | 13.9 | 0 | 2023-04-23 | 7.6 | 10.4 | 0 | 2022-04-23 | -0.1 | 18.1 | 0 | 2021-04-23 | 1.2 | 16.8 | 0 | 2020-04-23 | -6.5 | 24.5 | 0 | 2019-04-23 | 7.7 | 10.3 | 0 | 2018-04-23 | -0.7 | 18.7 | 0 | 2017-04-23 | 0.3 | 17.7 | 0 | 2016-04-23 | 0.4 | 17.6 | 0 | 16.51 | 0
2025-04-23 | 3.3 | 14.7 | 0 | 2024-04-23 | 5.5 | 12.5 | 0 | 2023-04-23 | 7.3 | 10.7 | 0 | 2022-04-23 | 1.8 | 16.2 | 0 | 2021-04-23 | 1.6 | 16.4 | 0 | 2020-04-23 | -3.9 | 21.9 | 0 | 2019-04-23 | 8.6 | 9.4 | 0 | 2018-04-23 | 2.1 | 15.9 | 0 | 2017-04-23 | 1.7 | 16.3 | 0 | 2016-04-23 | 1.1 | 16.9 | 0 | 15.09 | 0
2025-04-23 | 4.6 | 13.4 | 0 | 2024-04-23 | 8.3 | 9.7 | 0 | 2023-04-23 | 7.6 | 10.4 | 0 | 2022-04-23 | 2.9 | 15.1 | 0 | 2021-04-23 | 5 | 13 | 0 | 2020-04-23 | -2.8 | 20.8 | 0 | 2019-04-23 | 8.8 | 9.2 | 0 | 2018-04-23 | 4.9 | 13.1 | 0 | 2017-04-23 | 4.7 | 13.3 | 0 | 2016-04-23 | 2 | 16 | 0 | 13.4 | 0
2025-04-23 | 6 | 12 | 0 | 2024-04-23 | 11.6 | 6.4 | 0 | 2023-04-23 | 8.3 | 9.7 | 0 | 2022-04-23 | 3.9 | 14.1 | 0 | 2021-04-23 | 6.1 | 11.9 | 0 | 2020-04-23 | -1.8 | 19.8 | 0 | 2019-04-23 | 9.2 | 8.8 | 0 | 2018-04-23 | 8.8 | 9.2 | 0 | 2017-04-23 | 8.6 | 9.4 | 0 | 2016-04-23 | 3.3 | 14.7 | 0 | 11.6 | 0
2025-04-23 | 7.4 | 10.6 | 0 | 2024-04-23 | 13.1 | 4.9 | 0 | 2023-04-23 | 8.9 | 9.1 | 0 | 2022-04-23 | 5.1 | 12.9 | 0 | 2021-04-23 | 7.9 | 10.1 | 0 | 2020-04-23 | -0.6 | 18.6 | 0 | 2019-04-23 | 11.7 | 6.3 | 0 | 2018-04-23 | 11.8 | 6.2 | 0 | 2017-04-23 | 11.6 | 6.4 | 0 | 2016-04-23 | 4.3 | 13.7 | 0 | 9.88 | 0
2025-04-23 | 8.9 | 9.1 | 0 | 2024-04-23 | 14.3 | 3.7 | 0 | 2023-04-23 | 9.4 | 8.6 | 0 | 2022-04-23 | 6 | 12 | 0 | 2021-04-23 | 9.5 | 8.5 | 0 | 2020-04-23 | 0.4 | 17.6 | 0 | 2019-04-23 | 12.6 | 5.4 | 0 | 2018-04-23 | 13.7 | 4.3 | 0 | 2017-04-23 | 14.4 | 3.6 | 0 | 2016-04-23 | 5.9 | 12.1 | 0 | 8.49 | 0
2025-04-23 | 10.2 | 7.8 | 0 | 2024-04-23 | 16.8 | 1.2 | 0 | 2023-04-23 | 10.3 | 7.7 | 0 | 2022-04-23 | 6.9 | 11.1 | 0 | 2021-04-23 | 11.3 | 6.7 | 0 | 2020-04-23 | 2.5 | 15.5 | 0 | 2019-04-23 | 12.7 | 5.3 | 0 | 2018-04-23 | 16.2 | 1.8 | 0 | 2017-04-23 | 16 | 2 | 0 | 2016-04-23 | 7.2 | 10.8 | 0 | 6.99 | 0
2025-04-23 | 11.2 | 6.8 | 0 | 2024-04-23 | 15.8 | 2.2 | 0 | 2023-04-23 | 11 | 7 | 0 | 2022-04-23 | 8.1 | 9.9 | 0 | 2021-04-23 | 12.8 | 5.2 | 0 | 2020-04-23 | 3.6 | 14.4 | 0 | 2019-04-23 | 14.3 | 3.7 | 0 | 2018-04-23 | 17.5 | 0.5 | 0 | 2017-04-23 | 17.1 | 0.9 | 0 | 2016-04-23 | 8.6 | 9.4 | 0 | 6 | 0
2025-04-23 | 12.2 | 5.8 | 0 | 2024-04-23 | 16.5 | 1.5 | 0 | 2023-04-23 | 11.5 | 6.5 | 0 | 2022-04-23 | 9.5 | 8.5 | 0 | 2021-04-23 | 13.8 | 4.2 | 0 | 2020-04-23 | 5.2 | 12.8 | 0 | 2019-04-23 | 16.4 | 1.6 | 0 | 2018-04-23 | 17.6 | 0.4 | 0 | 2017-04-23 | 17.9 | 0.1 | 0 | 2016-04-23 | 9.6 | 8.4 | 0 | 4.98 | 0
2025-04-23 | 13.1 | 4.9 | 0 | 2024-04-23 | 16.1 | 1.9 | 0 | 2023-04-23 | 11.6 | 6.4 | 0 | 2022-04-23 | 9.2 | 8.8 | 0 | 2021-04-23 | 14.9 | 3.1 | 0 | 2020-04-23 | 6.3 | 11.7 | 0 | 2019-04-23 | 17.6 | 0.4 | 0 | 2018-04-23 | 19.2 | 0 | 1.2 | 2017-04-23 | 18.4 | 0 | 0.4 | 2016-04-23 | 10 | 8 | 0 | 4.52 | 0.16
2025-04-23 | 14.1 | 3.9 | 0 | 2024-04-23 | 16.1 | 1.9 | 0 | 2023-04-23 | 11.3 | 6.7 | 0 | 2022-04-23 | 9.6 | 8.4 | 0 | 2021-04-23 | 15.3 | 2.7 | 0 | 2020-04-23 | 6.4 | 11.6 | 0 | 2019-04-23 | 16.5 | 1.5 | 0 | 2018-04-23 | 18.9 | 0 | 0.9 | 2017-04-23 | 18.9 | 0 | 0.9 | 2016-04-23 | 9.9 | 8.1 | 0 | 4.48 | 0.18
2025-04-23 | 14.2 | 3.8 | 0 | 2024-04-23 | 15.6 | 2.4 | 0 | 2023-04-23 | 10.7 | 7.3 | 0 | 2022-04-23 | 9.5 | 8.5 | 0 | 2021-04-23 | 15.8 | 2.2 | 0 | 2020-04-23 | 7.1 | 10.9 | 0 | 2019-04-23 | 15.4 | 2.6 | 0 | 2018-04-23 | 18.9 | 0 | 0.9 | 2017-04-23 | 17.8 | 0.2 | 0 | 2016-04-23 | 10 | 8 | 0 | 4.59 | 0.09
2025-04-23 | 14.1 | 3.9 | 0 | 2024-04-23 | 14.8 | 3.2 | 0 | 2023-04-23 | 10.1 | 7.9 | 0 | 2022-04-23 | 9.3 | 8.7 | 0 | 2021-04-23 | 15.7 | 2.3 | 0 | 2020-04-23 | 7.2 | 10.8 | 0 | 2019-04-23 | 13.2 | 4.8 | 0 | 2018-04-23 | 18.7 | 0 | 0.7 | 2017-04-23 | 16.5 | 1.5 | 0 | 2016-04-23 | 9.6 | 8.4 | 0 | 5.15 | 0.07
2025-04-23 | 13.2 | 4.8 | 0 | 2024-04-23 | 14.4 | 3.6 | 0 | 2023-04-23 | 9.2 | 8.8 | 0 | 2022-04-23 | 8.7 | 9.3 | 0 | 2021-04-23 | 15.1 | 2.9 | 0 | 2020-04-23 | 6.5 | 11.5 | 0 | 2019-04-23 | 11.2 | 6.8 | 0 | 2018-04-23 | 17.1 | 0.9 | 0 | 2017-04-23 | 13.9 | 4.1 | 0 | 2016-04-23 | 8.7 | 9.3 | 0 | 6.2 | 0
2025-04-23 | 11.2 | 6.8 | 0 | 2024-04-23 | 14.3 | 3.7 | 0 | 2023-04-23 | 9 | 9 | 0 | 2022-04-23 | 8 | 10 | 0 | 2021-04-23 | 12.9 | 5.1 | 0 | 2020-04-23 | 5 | 13 | 0 | 2019-04-23 | 10.6 | 7.4 | 0 | 2018-04-23 | 14.1 | 3.9 | 0 | 2017-04-23 | 11.2 | 6.8 | 0 | 2016-04-23 | 7.1 | 10.9 | 0 | 7.66 | 0
2025-04-23 | 9.8 | 8.2 | 0 | 2024-04-23 | 11.5 | 6.5 | 0 | 2023-04-23 | 8.7 | 9.3 | 0 | 2022-04-23 | 6.8 | 11.2 | 0 | 2021-04-23 | 11.9 | 6.1 | 0 | 2020-04-23 | 2.7 | 15.3 | 0 | 2019-04-23 | 10.7 | 7.3 | 0 | 2018-04-23 | 12 | 6 | 0 | 2017-04-23 | 9.8 | 8.2 | 0 | 2016-04-23 | 5.7 | 12.3 | 0 | 9.04 | 0
2025-04-23 | 9.2 | 8.8 | 0 | 2024-04-23 | 9.6 | 8.4 | 0 | 2023-04-23 | 7.8 | 10.2 | 0 | 2022-04-23 | 7 | 11 | 0 | 2021-04-23 | 10.1 | 7.9 | 0 | 2020-04-23 | 1.7 | 16.3 | 0 | 2019-04-23 | 11.4 | 6.6 | 0 | 2018-04-23 | 10.4 | 7.6 | 0 | 2017-04-23 | 7.6 | 10.4 | 0 | 2016-04-23 | 4.9 | 13.1 | 0 | 10.03 | 0
2025-04-23 | 7.6 | 10.4 | 0 | 2024-04-23 | 9.4 | 8.6 | 0 | 2023-04-23 | 6.6 | 11.4 | 0 | 2022-04-23 | 6.7 | 11.3 | 0 | 2021-04-23 | 9.7 | 8.3 | 0 | 2020-04-23 | 0 | 18 | 0 | 2019-04-23 | 12 | 6 | 0 | 2018-04-23 | 10.9 | 7.1 | 0 | 2017-04-23 | 6.5 | 11.5 | 0 | 2016-04-23 | 4.2 | 13.8 | 0 | 10.64 | 0
2025-04-23 | 5.2 | 12.8 | 0 | 2024-04-23 | 9.4 | 8.6 | 0 | 2023-04-23 | 6.8 | 11.2 | 0 | 2022-04-23 | 6.8 | 11.2 | 0 | 2021-04-23 | 9.1 | 8.9 | 0 | 2020-04-23 | -2.2 | 20.2 | 0 | 2019-04-23 | 11.9 | 6.1 | 0 | 2018-04-23 | 9.9 | 8.1 | 0 | 2017-04-23 | 5.4 | 12.6 | 0 | 2016-04-23 | 3.3 | 14.7 | 0 | 11.44 | 0
2025-04-24 | 5.6 | 12.4 | 0 | 2024-04-24 | 8.9 | 9.1 | 0 | 2023-04-24 | 6.7 | 11.3 | 0 | 2022-04-24 | 6.6 | 11.4 | 0 | 2021-04-24 | 8.8 | 9.2 | 0 | 2020-04-24 | -2 | 20 | 0 | 2019-04-24 | 8.6 | 9.4 | 0 | 2018-04-24 | 8.8 | 9.2 | 0 | 2017-04-24 | 3.5 | 14.5 | 0 | 2016-04-24 | 2.2 | 15.8 | 0 | 12.23 | 0
2025-04-24 | 4.7 | 13.3 | 0 | 2024-04-24 | 8.6 | 9.4 | 0 | 2023-04-24 | 6.6 | 11.4 | 0 | 2022-04-24 | 6.7 | 11.3 | 0 | 2021-04-24 | 8 | 10 | 0 | 2020-04-24 | -1.6 | 19.6 | 0 | 2019-04-24 | 7.6 | 10.4 | 0 | 2018-04-24 | 6.3 | 11.7 | 0 | 2017-04-24 | 2.4 | 15.6 | 0 | 2016-04-24 | 1.1 | 16.9 | 0 | 12.96 | 0
2025-04-24 | 4.6 | 13.4 | 0 | 2024-04-24 | 8.5 | 9.5 | 0 | 2023-04-24 | 6.3 | 11.7 | 0 | 2022-04-24 | 6.7 | 11.3 | 0 | 2021-04-24 | 6.3 | 11.7 | 0 | 2020-04-24 | -3 | 21 | 0 | 2019-04-24 | 6.8 | 11.2 | 0 | 2018-04-24 | 5.3 | 12.7 | 0 | 2017-04-24 | 1.5 | 16.5 | 0 | 2016-04-24 | 0.2 | 17.8 | 0 | 13.68 | 0
2025-04-24 | 4.2 | 13.8 | 0 | 2024-04-24 | 8.5 | 9.5 | 0 | 2023-04-24 | 6.7 | 11.3 | 0 | 2022-04-24 | 6.6 | 11.4 | 0 | 2021-04-24 | 6.1 | 11.9 | 0 | 2020-04-24 | -3.2 | 21.2 | 0 | 2019-04-24 | 6.3 | 11.7 | 0 | 2018-04-24 | 5.1 | 12.9 | 0 | 2017-04-24 | 1.1 | 16.9 | 0 | 2016-04-24 | -0.7 | 18.7 | 0 | 13.93 | 0
2025-04-24 | 3.3 | 14.7 | 0 | 2024-04-24 | 8.4 | 9.6 | 0 | 2023-04-24 | 6.3 | 11.7 | 0 | 2022-04-24 | 6 | 12 | 0 | 2021-04-24 | 5.5 | 12.5 | 0 | 2020-04-24 | -3 | 21 | 0 | 2019-04-24 | 5.1 | 12.9 | 0 | 2018-04-24 | 4.2 | 13.8 | 0 | 2017-04-24 | 0.8 | 17.2 | 0 | 2016-04-24 | -0.8 | 18.8 | 0 | 14.42 | 0
2025-04-24 | 3.6 | 14.4 | 0 | 2024-04-24 | 6.6 | 11.4 | 0 | 2023-04-24 | 5.8 | 12.2 | 0 | 2022-04-24 | 5.3 | 12.7 | 0 | 2021-04-24 | 4.5 | 13.5 | 0 | 2020-04-24 | -2.7 | 20.7 | 0 | 2019-04-24 | 4.7 | 13.3 | 0 | 2018-04-24 | 7.5 | 10.5 | 0 | 2017-04-24 | 0.4 | 17.6 | 0 | 2016-04-24 | -0.5 | 18.5 | 0 | 14.48 | 0
2025-04-24 | 5 | 13 | 0 | 2024-04-24 | 3.7 | 14.3 | 0 | 2023-04-24 | 5.1 | 12.9 | 0 | 2022-04-24 | 4.7 | 13.3 | 0 | 2021-04-24 | 6.1 | 11.9 | 0 | 2020-04-24 | -0.8 | 18.8 | 0 | 2019-04-24 | 4.2 | 13.8 | 0 | 2018-04-24 | 7 | 11 | 0 | 2017-04-24 | 0.4 | 17.6 | 0 | 2016-04-24 | 0.6 | 17.4 | 0 | 14.4 | 0
2025-04-24 | 6.8 | 11.2 | 0 | 2024-04-24 | 2 | 16 | 0 | 2023-04-24 | 5.2 | 12.8 | 0 | 2022-04-24 | 4.7 | 13.3 | 0 | 2021-04-24 | 8.3 | 9.7 | 0 | 2020-04-24 | 1.8 | 16.2 | 0 | 2019-04-24 | 4.2 | 13.8 | 0 | 2018-04-24 | 8.9 | 9.1 | 0 | 2017-04-24 | 1.1 | 16.9 | 0 | 2016-04-24 | 2.2 | 15.8 | 0 | 13.48 | 0
2025-04-24 | 8.2 | 9.8 | 0 | 2024-04-24 | 1.2 | 16.8 | 0 | 2023-04-24 | 5.1 | 12.9 | 0 | 2022-04-24 | 4.2 | 13.8 | 0 | 2021-04-24 | 11.9 | 6.1 | 0 | 2020-04-24 | 3.3 | 14.7 | 0 | 2019-04-24 | 4.8 | 13.2 | 0 | 2018-04-24 | 12.7 | 5.3 | 0 | 2017-04-24 | 2.4 | 15.6 | 0 | 2016-04-24 | 3.6 | 14.4 | 0 | 12.26 | 0
2025-04-24 | 8.5 | 9.5 | 0 | 2024-04-24 | 0.9 | 17.1 | 0 | 2023-04-24 | 5.3 | 12.7 | 0 | 2022-04-24 | 7.2 | 10.8 | 0 | 2021-04-24 | 13.6 | 4.4 | 0 | 2020-04-24 | 4.5 | 13.5 | 0 | 2019-04-24 | 4.8 | 13.2 | 0 | 2018-04-24 | 15.9 | 2.1 | 0 | 2017-04-24 | 4.1 | 13.9 | 0 | 2016-04-24 | 4.4 | 13.6 | 0 | 11.08 | 0
2025-04-24 | 8 | 10 | 0 | 2024-04-24 | 1.9 | 16.1 | 0 | 2023-04-24 | 5.8 | 12.2 | 0 | 2022-04-24 | 7.7 | 10.3 | 0 | 2021-04-24 | 16.5 | 1.5 | 0 | 2020-04-24 | 5.6 | 12.4 | 0 | 2019-04-24 | 5.6 | 12.4 | 0 | 2018-04-24 | 17.8 | 0.2 | 0 | 2017-04-24 | 5 | 13 | 0 | 2016-04-24 | 5.7 | 12.3 | 0 | 10.04 | 0
2025-04-24 | 10.8 | 7.2 | 0 | 2024-04-24 | 2.8 | 15.2 | 0 | 2023-04-24 | 6.2 | 11.8 | 0 | 2022-04-24 | 9.6 | 8.4 | 0 | 2021-04-24 | 18.4 | 0 | 0.4 | 2020-04-24 | 5.8 | 12.2 | 0 | 2019-04-24 | 5.3 | 12.7 | 0 | 2018-04-24 | 19 | 0 | 1 | 2017-04-24 | 6.2 | 11.8 | 0 | 2016-04-24 | 7.5 | 10.5 | 0 | 8.98 | 0.14
2025-04-24 | 14.1 | 3.9 | 0 | 2024-04-24 | 4.1 | 13.9 | 0 | 2023-04-24 | 6.9 | 11.1 | 0 | 2022-04-24 | 11.7 | 6.3 | 0 | 2021-04-24 | 18.8 | 0 | 0.8 | 2020-04-24 | 6.8 | 11.2 | 0 | 2019-04-24 | 5.8 | 12.2 | 0 | 2018-04-24 | 19 | 0 | 1 | 2017-04-24 | 8 | 10 | 0 | 2016-04-24 | 9.1 | 8.9 | 0 | 7.75 | 0.18
2025-04-24 | 17.1 | 0.9 | 0 | 2024-04-24 | 4.3 | 13.7 | 0 | 2023-04-24 | 7.7 | 10.3 | 0 | 2022-04-24 | 12.3 | 5.7 | 0 | 2021-04-24 | 18.3 | 0 | 0.3 | 2020-04-24 | 7 | 11 | 0 | 2019-04-24 | 6.4 | 11.6 | 0 | 2018-04-24 | 18.7 | 0 | 0.7 | 2017-04-24 | 8.9 | 9.1 | 0 | 2016-04-24 | 9.8 | 8.2 | 0 | 7.05 | 0.1
2025-04-24 | 18.2 | 0 | 0.2 | 2024-04-24 | 5.2 | 12.8 | 0 | 2023-04-24 | 8.9 | 9.1 | 0 | 2022-04-24 | 13.6 | 4.4 | 0 | 2021-04-24 | 18.4 | 0 | 0.4 | 2020-04-24 | 8.2 | 9.8 | 0 | 2019-04-24 | 8.7 | 9.3 | 0 | 2018-04-24 | 19.9 | 0 | 1.9 | 2017-04-24 | 9.7 | 8.3 | 0 | 2016-04-24 | 10.5 | 7.5 | 0 | 6.12 | 0.25
2025-04-24 | 17.6 | 0.4 | 0 | 2024-04-24 | 5 | 13 | 0 | 2023-04-24 | 8.9 | 9.1 | 0 | 2022-04-24 | 13.5 | 4.5 | 0 | 2021-04-24 | 17.9 | 0.1 | 0 | 2020-04-24 | 8.9 | 9.1 | 0 | 2019-04-24 | 8.1 | 9.9 | 0 | 2018-04-24 | 18.9 | 0 | 0.9 | 2017-04-24 | 10.5 | 7.5 | 0 | 2016-04-24 | 11.7 | 6.3 | 0 | 5.99 | 0.09
2025-04-24 | 16.9 | 1.1 | 0 | 2024-04-24 | 4.7 | 13.3 | 0 | 2023-04-24 | 8.8 | 9.2 | 0 | 2022-04-24 | 13.6 | 4.4 | 0 | 2021-04-24 | 17.6 | 0.4 | 0 | 2020-04-24 | 9.3 | 8.7 | 0 | 2019-04-24 | 7.8 | 10.2 | 0 | 2018-04-24 | 17.8 | 0.2 | 0 | 2017-04-24 | 10.7 | 7.3 | 0 | 2016-04-24 | 11.7 | 6.3 | 0 | 6.11 | 0
2025-04-24 | 17.5 | 0.5 | 0 | 2024-04-24 | 4.5 | 13.5 | 0 | 2023-04-24 | 8.1 | 9.9 | 0 | 2022-04-24 | 13.6 | 4.4 | 0 | 2021-04-24 | 17.7 | 0.3 | 0 | 2020-04-24 | 8.9 | 9.1 | 0 | 2019-04-24 | 7.6 | 10.4 | 0 | 2018-04-24 | 16.7 | 1.3 | 0 | 2017-04-24 | 10.7 | 7.3 | 0 | 2016-04-24 | 11.5 | 6.5 | 0 | 6.32 | 0
2025-04-24 | 16.5 | 1.5 | 0 | 2024-04-24 | 3.9 | 14.1 | 0 | 2023-04-24 | 8.1 | 9.9 | 0 | 2022-04-24 | 12.4 | 5.6 | 0 | 2021-04-24 | 16.4 | 1.6 | 0 | 2020-04-24 | 8.4 | 9.6 | 0 | 2019-04-24 | 7 | 11 | 0 | 2018-04-24 | 15.5 | 2.5 | 0 | 2017-04-24 | 9.5 | 8.5 | 0 | 2016-04-24 | 10.9 | 7.1 | 0 | 7.14 | 0
2025-04-24 | 14.7 | 3.3 | 0 | 2024-04-24 | 2.4 | 15.6 | 0 | 2023-04-24 | 6.6 | 11.4 | 0 | 2022-04-24 | 10.8 | 7.2 | 0 | 2021-04-24 | 14.8 | 3.2 | 0 | 2020-04-24 | 6.3 | 11.7 | 0 | 2019-04-24 | 6.7 | 11.3 | 0 | 2018-04-24 | 14.2 | 3.8 | 0 | 2017-04-24 | 8 | 10 | 0 | 2016-04-24 | 9.2 | 8.8 | 0 | 8.63 | 0
2025-04-24 | 13.4 | 4.6 | 0 | 2024-04-24 | 1.8 | 16.2 | 0 | 2023-04-24 | 5.8 | 12.2 | 0 | 2022-04-24 | 9.4 | 8.6 | 0 | 2021-04-24 | 12.6 | 5.4 | 0 | 2020-04-24 | 5.1 | 12.9 | 0 | 2019-04-24 | 6.6 | 11.4 | 0 | 2018-04-24 | 13.7 | 4.3 | 0 | 2017-04-24 | 6.8 | 11.2 | 0 | 2016-04-24 | 7.2 | 10.8 | 0 | 9.76 | 0
2025-04-24 | 12.5 | 5.5 | 0 | 2024-04-24 | 0.7 | 17.3 | 0 | 2023-04-24 | 5.1 | 12.9 | 0 | 2022-04-24 | 8.7 | 9.3 | 0 | 2021-04-24 | 11.2 | 6.8 | 0 | 2020-04-24 | 4.2 | 13.8 | 0 | 2019-04-24 | 5.8 | 12.2 | 0 | 2018-04-24 | 13.2 | 4.8 | 0 | 2017-04-24 | 6.5 | 11.5 | 0 | 2016-04-24 | 6.2 | 11.8 | 0 | 10.59 | 0
2025-04-24 | 13.5 | 4.5 | 0 | 2024-04-24 | -0.2 | 18.2 | 0 | 2023-04-24 | 5.3 | 12.7 | 0 | 2022-04-24 | 8.5 | 9.5 | 0 | 2021-04-24 | 9.7 | 8.3 | 0 | 2020-04-24 | 1.9 | 16.1 | 0 | 2019-04-24 | 5.6 | 12.4 | 0 | 2018-04-24 | 12.7 | 5.3 | 0 | 2017-04-24 | 5.6 | 12.4 | 0 | 2016-04-24 | 4.8 | 13.2 | 0 | 11.26 | 0
2025-04-24 | 13.4 | 4.6 | 0 | 2024-04-24 | -1.1 | 19.1 | 0 | 2023-04-24 | 5.2 | 12.8 | 0 | 2022-04-24 | 7.9 | 10.1 | 0 | 2021-04-24 | 9.3 | 8.7 | 0 | 2020-04-24 | 2 | 16 | 0 | 2019-04-24 | 5 | 13 | 0 | 2018-04-24 | 10.8 | 7.2 | 0 | 2017-04-24 | 4.9 | 13.1 | 0 | 2016-04-24 | 5.9 | 12.1 | 0 | 11.67 | 0
2025-04-25 | 12.4 | 5.6 | 0 | 2024-04-25 | -2.4 | 20.4 | 0 | 2023-04-25 | 4.4 | 13.6 | 0 | 2022-04-25 | 7.5 | 10.5 | 0 | 2021-04-25 | 8.7 | 9.3 | 0 | 2020-04-25 | 0.3 | 17.7 | 0 | 2019-04-25 | 4.8 | 13.2 | 0 | 2018-04-25 | 11.5 | 6.5 | 0 | 2017-04-25 | 4.4 | 13.6 | 0 | 2016-04-25 | 4.7 | 13.3 | 0 | 12.37 | 0
2025-04-25 | 11.6 | 6.4 | 0 | 2024-04-25 | -1.9 | 19.9 | 0 | 2023-04-25 | 4 | 14 | 0 | 2022-04-25 | 7.4 | 10.6 | 0 | 2021-04-25 | 8.4 | 9.6 | 0 | 2020-04-25 | 0.7 | 17.3 | 0 | 2019-04-25 | 4.3 | 13.7 | 0 | 2018-04-25 | 10.9 | 7.1 | 0 | 2017-04-25 | 4.2 | 13.8 | 0 | 2016-04-25 | 3.4 | 14.6 | 0 | 12.7 | 0
2025-04-25 | 10.6 | 7.4 | 0 | 2024-04-25 | -2 | 20 | 0 | 2023-04-25 | 3.1 | 14.9 | 0 | 2022-04-25 | 7.5 | 10.5 | 0 | 2021-04-25 | 6.2 | 11.8 | 0 | 2020-04-25 | 0.1 | 17.9 | 0 | 2019-04-25 | 4 | 14 | 0 | 2018-04-25 | 10.6 | 7.4 | 0 | 2017-04-25 | 4.1 | 13.9 | 0 | 2016-04-25 | 2.7 | 15.3 | 0 | 13.31 | 0
2025-04-25 | 8.3 | 9.7 | 0 | 2024-04-25 | -2.8 | 20.8 | 0 | 2023-04-25 | 2.3 | 15.7 | 0 | 2022-04-25 | 7.6 | 10.4 | 0 | 2021-04-25 | 5.4 | 12.6 | 0 | 2020-04-25 | -1.5 | 19.5 | 0 | 2019-04-25 | 3.9 | 14.1 | 0 | 2018-04-25 | 10.8 | 7.2 | 0 | 2017-04-25 | 4 | 14 | 0 | 2016-04-25 | 1.6 | 16.4 | 0 | 14.04 | 0
2025-04-25 | 8.7 | 9.3 | 0 | 2024-04-25 | -3.4 | 21.4 | 0 | 2023-04-25 | 0.8 | 17.2 | 0 | 2022-04-25 | 7.5 | 10.5 | 0 | 2021-04-25 | 4.9 | 13.1 | 0 | 2020-04-25 | -3.1 | 21.1 | 0 | 2019-04-25 | 3.8 | 14.2 | 0 | 2018-04-25 | 9.8 | 8.2 | 0 | 2017-04-25 | 3.7 | 14.3 | 0 | 2016-04-25 | 0.2 | 17.8 | 0 | 14.71 | 0
2025-04-25 | 6.2 | 11.8 | 0 | 2024-04-25 | -3.9 | 21.9 | 0 | 2023-04-25 | 1.4 | 16.6 | 0 | 2022-04-25 | 7.3 | 10.7 | 0 | 2021-04-25 | 5.4 | 12.6 | 0 | 2020-04-25 | -0.4 | 18.4 | 0 | 2019-04-25 | 3.8 | 14.2 | 0 | 2018-04-25 | 9.2 | 8.8 | 0 | 2017-04-25 | 2.9 | 15.1 | 0 | 2016-04-25 | -0.2 | 18.2 | 0 | 14.83 | 0
2025-04-25 | 8.6 | 9.4 | 0 | 2024-04-25 | -2.4 | 20.4 | 0 | 2023-04-25 | 2.5 | 15.5 | 0 | 2022-04-25 | 7.1 | 10.9 | 0 | 2021-04-25 | 5.8 | 12.2 | 0 | 2020-04-25 | 1.8 | 16.2 | 0 | 2019-04-25 | 4.1 | 13.9 | 0 | 2018-04-25 | 8.9 | 9.1 | 0 | 2017-04-25 | 3.6 | 14.4 | 0 | 2016-04-25 | 0.2 | 17.8 | 0 | 13.98 | 0
2025-04-25 | 9.2 | 8.8 | 0 | 2024-04-25 | -1.2 | 19.2 | 0 | 2023-04-25 | 3.7 | 14.3 | 0 | 2022-04-25 | 7.8 | 10.2 | 0 | 2021-04-25 | 8.6 | 9.4 | 0 | 2020-04-25 | 4.4 | 13.6 | 0 | 2019-04-25 | 4.8 | 13.2 | 0 | 2018-04-25 | 10.4 | 7.6 | 0 | 2017-04-25 | 5.6 | 12.4 | 0 | 2016-04-25 | 1.8 | 16.2 | 0 | 12.49 | 0
2025-04-25 | 9.6 | 8.4 | 0 | 2024-04-25 | -0.2 | 18.2 | 0 | 2023-04-25 | 4.5 | 13.5 | 0 | 2022-04-25 | 8 | 10 | 0 | 2021-04-25 | 11.7 | 6.3 | 0 | 2020-04-25 | 6.5 | 11.5 | 0 | 2019-04-25 | 5.7 | 12.3 | 0 | 2018-04-25 | 11 | 7 | 0 | 2017-04-25 | 7.7 | 10.3 | 0 | 2016-04-25 | 2.7 | 15.3 | 0 | 11.28 | 0
2025-04-25 | 10.5 | 7.5 | 0 | 2024-04-25 | 0.5 | 17.5 | 0 | 2023-04-25 | 5.9 | 12.1 | 0 | 2022-04-25 | 9.6 | 8.4 | 0 | 2021-04-25 | 12.9 | 5.1 | 0 | 2020-04-25 | 8.5 | 9.5 | 0 | 2019-04-25 | 6.4 | 11.6 | 0 | 2018-04-25 | 11.6 | 6.4 | 0 | 2017-04-25 | 9.3 | 8.7 | 0 | 2016-04-25 | 2.9 | 15.1 | 0 | 10.19 | 0
2025-04-25 | 11.6 | 6.4 | 0 | 2024-04-25 | 1.8 | 16.2 | 0 | 2023-04-25 | 8.2 | 9.8 | 0 | 2022-04-25 | 13 | 5 | 0 | 2021-04-25 | 12.9 | 5.1 | 0 | 2020-04-25 | 9.4 | 8.6 | 0 | 2019-04-25 | 7.5 | 10.5 | 0 | 2018-04-25 | 11.7 | 6.3 | 0 | 2017-04-25 | 10.7 | 7.3 | 0 | 2016-04-25 | 4.3 | 13.7 | 0 | 8.89 | 0
2025-04-25 | 12.7 | 5.3 | 0 | 2024-04-25 | 3.1 | 14.9 | 0 | 2023-04-25 | 9.8 | 8.2 | 0 | 2022-04-25 | 16.5 | 1.5 | 0 | 2021-04-25 | 12.1 | 5.9 | 0 | 2020-04-25 | 11.4 | 6.6 | 0 | 2019-04-25 | 8.6 | 9.4 | 0 | 2018-04-25 | 11.2 | 6.8 | 0 | 2017-04-25 | 12 | 6 | 0 | 2016-04-25 | 5 | 13 | 0 | 7.76 | 0
2025-04-25 | 13 | 5 | 0 | 2024-04-25 | 4.1 | 13.9 | 0 | 2023-04-25 | 9 | 9 | 0 | 2022-04-25 | 18.8 | 0 | 0.8 | 2021-04-25 | 12.3 | 5.7 | 0 | 2020-04-25 | 12.4 | 5.6 | 0 | 2019-04-25 | 9.5 | 8.5 | 0 | 2018-04-25 | 11.2 | 6.8 | 0 | 2017-04-25 | 13.6 | 4.4 | 0 | 2016-04-25 | 6.5 | 11.5 | 0 | 7.04 | 0.08
2025-04-25 | 15.1 | 2.9 | 0 | 2024-04-25 | 5.9 | 12.1 | 0 | 2023-04-25 | 9 | 9 | 0 | 2022-04-25 | 19.9 | 0 | 1.9 | 2021-04-25 | 11.5 | 6.5 | 0 | 2020-04-25 | 12.8 | 5.2 | 0 | 2019-04-25 | 11 | 7 | 0 | 2018-04-25 | 11.3 | 6.7 | 0 | 2017-04-25 | 13.7 | 4.3 | 0 | 2016-04-25 | 7.2 | 10.8 | 0 | 6.45 | 0.19
2025-04-25 | 15.8 | 2.2 | 0 | 2024-04-25 | 7.2 | 10.8 | 0 | 2023-04-25 | 9.2 | 8.8 | 0 | 2022-04-25 | 17.7 | 0.3 | 0 | 2021-04-25 | 13.2 | 4.8 | 0 | 2020-04-25 | 13.7 | 4.3 | 0 | 2019-04-25 | 12.3 | 5.7 | 0 | 2018-04-25 | 11.5 | 6.5 | 0 | 2017-04-25 | 11.2 | 6.8 | 0 | 2016-04-25 | 8.3 | 9.7 | 0 | 5.99 | 0
2025-04-25 | 16.1 | 1.9 | 0 | 2024-04-25 | 7.3 | 10.7 | 0 | 2023-04-25 | 9.3 | 8.7 | 0 | 2022-04-25 | 17.2 | 0.8 | 0 | 2021-04-25 | 7.9 | 10.1 | 0 | 2020-04-25 | 13.9 | 4.1 | 0 | 2019-04-25 | 12.7 | 5.3 | 0 | 2018-04-25 | 11 | 7 | 0 | 2017-04-25 | 10.4 | 7.6 | 0 | 2016-04-25 | 8.2 | 9.8 | 0 | 6.6 | 0
2025-04-25 | 16.5 | 1.5 | 0 | 2024-04-25 | 7.8 | 10.2 | 0 | 2023-04-25 | 10.1 | 7.9 | 0 | 2022-04-25 | 16.8 | 1.2 | 0 | 2021-04-25 | 12.1 | 5.9 | 0 | 2020-04-25 | 14.7 | 3.3 | 0 | 2019-04-25 | 13.9 | 4.1 | 0 | 2018-04-25 | 11.2 | 6.8 | 0 | 2017-04-25 | 9.8 | 8.2 | 0 | 2016-04-25 | 8.2 | 9.8 | 0 | 5.89 | 0
2025-04-25 | 16 | 2 | 0 | 2024-04-25 | 8.3 | 9.7 | 0 | 2023-04-25 | 8.6 | 9.4 | 0 | 2022-04-25 | 17.4 | 0.6 | 0 | 2021-04-25 | 10 | 8 | 0 | 2020-04-25 | 14.3 | 3.7 | 0 | 2019-04-25 | 14.3 | 3.7 | 0 | 2018-04-25 | 11.3 | 6.7 | 0 | 2017-04-25 | 9.7 | 8.3 | 0 | 2016-04-25 | 7.8 | 10.2 | 0 | 6.23 | 0
2025-04-25 | 14.7 | 3.3 | 0 | 2024-04-25 | 7.5 | 10.5 | 0 | 2023-04-25 | 8.1 | 9.9 | 0 | 2022-04-25 | 16 | 2 | 0 | 2021-04-25 | 7.2 | 10.8 | 0 | 2020-04-25 | 14.1 | 3.9 | 0 | 2019-04-25 | 13.9 | 4.1 | 0 | 2018-04-25 | 11.1 | 6.9 | 0 | 2017-04-25 | 9.8 | 8.2 | 0 | 2016-04-25 | 7.2 | 10.8 | 0 | 7.04 | 0
2025-04-25 | 13.5 | 4.5 | 0 | 2024-04-25 | 5.3 | 12.7 | 0 | 2023-04-25 | 5.5 | 12.5 | 0 | 2022-04-25 | 14.2 | 3.8 | 0 | 2021-04-25 | 3.7 | 14.3 | 0 | 2020-04-25 | 11 | 7 | 0 | 2019-04-25 | 10.7 | 7.3 | 0 | 2018-04-25 | 10.9 | 7.1 | 0 | 2017-04-25 | 9.5 | 8.5 | 0 | 2016-04-25 | 6.7 | 11.3 | 0 | 8.9 | 0
2025-04-25 | 13.1 | 4.9 | 0 | 2024-04-25 | 4.5 | 13.5 | 0 | 2023-04-25 | 4.9 | 13.1 | 0 | 2022-04-25 | 13.8 | 4.2 | 0 | 2021-04-25 | 2.7 | 15.3 | 0 | 2020-04-25 | 10.1 | 7.9 | 0 | 2019-04-25 | 8.8 | 9.2 | 0 | 2018-04-25 | 10.5 | 7.5 | 0 | 2017-04-25 | 9.3 | 8.7 | 0 | 2016-04-25 | 5.9 | 12.1 | 0 | 9.64 | 0
2025-04-25 | 12.5 | 5.5 | 0 | 2024-04-25 | 4.4 | 13.6 | 0 | 2023-04-25 | 4.9 | 13.1 | 0 | 2022-04-25 | 12 | 6 | 0 | 2021-04-25 | 1.6 | 16.4 | 0 | 2020-04-25 | 7.8 | 10.2 | 0 | 2019-04-25 | 8.3 | 9.7 | 0 | 2018-04-25 | 10.1 | 7.9 | 0 | 2017-04-25 | 9 | 9 | 0 | 2016-04-25 | 5.2 | 12.8 | 0 | 10.42 | 0
2025-04-25 | 11.7 | 6.3 | 0 | 2024-04-25 | 2.3 | 15.7 | 0 | 2023-04-25 | 5.2 | 12.8 | 0 | 2022-04-25 | 11.6 | 6.4 | 0 | 2021-04-25 | 0.9 | 17.1 | 0 | 2020-04-25 | 7.6 | 10.4 | 0 | 2019-04-25 | 8.4 | 9.6 | 0 | 2018-04-25 | 9.7 | 8.3 | 0 | 2017-04-25 | 8.8 | 9.2 | 0 | 2016-04-25 | 4.7 | 13.3 | 0 | 10.91 | 0
2025-04-25 | 11.3 | 6.7 | 0 | 2024-04-25 | 1.3 | 16.7 | 0 | 2023-04-25 | 3.8 | 14.2 | 0 | 2022-04-25 | 11.2 | 6.8 | 0 | 2021-04-25 | 0.7 | 17.3 | 0 | 2020-04-25 | 6.9 | 11.1 | 0 | 2019-04-25 | 7.3 | 10.7 | 0 | 2018-04-25 | 9.4 | 8.6 | 0 | 2017-04-25 | 8.6 | 9.4 | 0 | 2016-04-25 | 4.5 | 13.5 | 0 | 11.5 | 0
2025-04-26 | 11 | 7 | 0 | 2024-04-26 | 1.6 | 16.4 | 0 | 2023-04-26 | 3.6 | 14.4 | 0 | 2022-04-26 | 10.7 | 7.3 | 0 | 2021-04-26 | 0.2 | 17.8 | 0 | 2020-04-26 | 5.1 | 12.9 | 0 | 2019-04-26 | 6.8 | 11.2 | 0 | 2018-04-26 | 9.2 | 8.8 | 0 | 2017-04-26 | 8.4 | 9.6 | 0 | 2016-04-26 | 4 | 14 | 0 | 11.94 | 0
2025-04-26 | 10.6 | 7.4 | 0 | 2024-04-26 | 0.3 | 17.7 | 0 | 2023-04-26 | 3 | 15 | 0 | 2022-04-26 | 10.2 | 7.8 | 0 | 2021-04-26 | -0.4 | 18.4 | 0 | 2020-04-26 | 4.6 | 13.4 | 0 | 2019-04-26 | 6.3 | 11.7 | 0 | 2018-04-26 | 8.9 | 9.1 | 0 | 2017-04-26 | 8.6 | 9.4 | 0 | 2016-04-26 | 3.7 | 14.3 | 0 | 12.42 | 0
2025-04-26 | 10.2 | 7.8 | 0 | 2024-04-26 | -2.8 | 20.8 | 0 | 2023-04-26 | 2 | 16 | 0 | 2022-04-26 | 10 | 8 | 0 | 2021-04-26 | -0.6 | 18.6 | 0 | 2020-04-26 | 4.4 | 13.6 | 0 | 2019-04-26 | 6.2 | 11.8 | 0 | 2018-04-26 | 8.7 | 9.3 | 0 | 2017-04-26 | 8.9 | 9.1 | 0 | 2016-04-26 | 3.4 | 14.6 | 0 | 12.96 | 0
2025-04-26 | 9.5 | 8.5 | 0 | 2024-04-26 | -0.8 | 18.8 | 0 | 2023-04-26 | 0.9 | 17.1 | 0 | 2022-04-26 | 9.7 | 8.3 | 0 | 2021-04-26 | -0.8 | 18.8 | 0 | 2020-04-26 | 4.9 | 13.1 | 0 | 2019-04-26 | 6.1 | 11.9 | 0 | 2018-04-26 | 8.4 | 9.6 | 0 | 2017-04-26 | 9 | 9 | 0 | 2016-04-26 | 2.8 | 15.2 | 0 | 13.03 | 0
2025-04-26 | 9.2 | 8.8 | 0 | 2024-04-26 | -1 | 19 | 0 | 2023-04-26 | 0.6 | 17.4 | 0 | 2022-04-26 | 9.4 | 8.6 | 0 | 2021-04-26 | -1 | 19 | 0 | 2020-04-26 | 6.2 | 11.8 | 0 | 2019-04-26 | 6 | 12 | 0 | 2018-04-26 | 8.2 | 9.8 | 0 | 2017-04-26 | 9.1 | 8.9 | 0 | 2016-04-26 | 2.2 | 15.8 | 0 | 13.11 | 0
2025-04-26 | 8.7 | 9.3 | 0 | 2024-04-26 | -1.3 | 19.3 | 0 | 2023-04-26 | 0.4 | 17.6 | 0 | 2022-04-26 | 8.3 | 9.7 | 0 | 2021-04-26 | -1.2 | 19.2 | 0 | 2020-04-26 | 5.9 | 12.1 | 0 | 2019-04-26 | 6.3 | 11.7 | 0 | 2018-04-26 | 7.9 | 10.1 | 0 | 2017-04-26 | 9.1 | 8.9 | 0 | 2016-04-26 | 1.6 | 16.4 | 0 | 13.43 | 0
2025-04-26 | 7.3 | 10.7 | 0 | 2024-04-26 | 0.1 | 17.9 | 0 | 2023-04-26 | 1.7 | 16.3 | 0 | 2022-04-26 | 8.6 | 9.4 | 0 | 2021-04-26 | -1.4 | 19.4 | 0 | 2020-04-26 | 5.8 | 12.2 | 0 | 2019-04-26 | 6.8 | 11.2 | 0 | 2018-04-26 | 8 | 10 | 0 | 2017-04-26 | 9.3 | 8.7 | 0 | 2016-04-26 | 1.1 | 16.9 | 0 | 13.27 | 0
2025-04-26 | 7.3 | 10.7 | 0 | 2024-04-26 | 3.6 | 14.4 | 0 | 2023-04-26 | 3.2 | 14.8 | 0 | 2022-04-26 | 9.4 | 8.6 | 0 | 2021-04-26 | -1 | 19 | 0 | 2020-04-26 | 6.2 | 11.8 | 0 | 2019-04-26 | 7.7 | 10.3 | 0 | 2018-04-26 | 8 | 10 | 0 | 2017-04-26 | 9.6 | 8.4 | 0 | 2016-04-26 | 1 | 17 | 0 | 12.5 | 0
2025-04-26 | 7.6 | 10.4 | 0 | 2024-04-26 | 7.4 | 10.6 | 0 | 2023-04-26 | 4.1 | 13.9 | 0 | 2022-04-26 | 10.2 | 7.8 | 0 | 2021-04-26 | 0.6 | 17.4 | 0 | 2020-04-26 | 7.2 | 10.8 | 0 | 2019-04-26 | 7.5 | 10.5 | 0 | 2018-04-26 | 7.5 | 10.5 | 0 | 2017-04-26 | 10.5 | 7.5 | 0 | 2016-04-26 | 1.5 | 16.5 | 0 | 11.59 | 0
2025-04-26 | 8.2 | 9.8 | 0 | 2024-04-26 | 8.9 | 9.1 | 0 | 2023-04-26 | 4.3 | 13.7 | 0 | 2022-04-26 | 11.7 | 6.3 | 0 | 2021-04-26 | 1.9 | 16.1 | 0 | 2020-04-26 | 8.3 | 9.7 | 0 | 2019-04-26 | 6.6 | 11.4 | 0 | 2018-04-26 | 7.2 | 10.8 | 0 | 2017-04-26 | 11.6 | 6.4 | 0 | 2016-04-26 | 2.7 | 15.3 | 0 | 10.86 | 0
2025-04-26 | 8.6 | 9.4 | 0 | 2024-04-26 | 10.3 | 7.7 | 0 | 2023-04-26 | 4.2 | 13.8 | 0 | 2022-04-26 | 13 | 5 | 0 | 2021-04-26 | 3.1 | 14.9 | 0 | 2020-04-26 | 9.2 | 8.8 | 0 | 2019-04-26 | 6.8 | 11.2 | 0 | 2018-04-26 | 6.9 | 11.1 | 0 | 2017-04-26 | 13.1 | 4.9 | 0 | 2016-04-26 | 3.3 | 14.7 | 0 | 10.15 | 0
2025-04-26 | 8.7 | 9.3 | 0 | 2024-04-26 | 10.8 | 7.2 | 0 | 2023-04-26 | 4.9 | 13.1 | 0 | 2022-04-26 | 13.8 | 4.2 | 0 | 2021-04-26 | 5.4 | 12.6 | 0 | 2020-04-26 | 11.2 | 6.8 | 0 | 2019-04-26 | 7.7 | 10.3 | 0 | 2018-04-26 | 7.3 | 10.7 | 0 | 2017-04-26 | 14.1 | 3.9 | 0 | 2016-04-26 | 4.5 | 13.5 | 0 | 9.16 | 0
2025-04-26 | 8.1 | 9.9 | 0 | 2024-04-26 | 11.6 | 6.4 | 0 | 2023-04-26 | 5.6 | 12.4 | 0 | 2022-04-26 | 13.6 | 4.4 | 0 | 2021-04-26 | 6.8 | 11.2 | 0 | 2020-04-26 | 12.1 | 5.9 | 0 | 2019-04-26 | 8.6 | 9.4 | 0 | 2018-04-26 | 7 | 11 | 0 | 2017-04-26 | 15.2 | 2.8 | 0 | 2016-04-26 | 6.6 | 11.4 | 0 | 8.48 | 0
2025-04-26 | 8.3 | 9.7 | 0 | 2024-04-26 | 12.9 | 5.1 | 0 | 2023-04-26 | 6 | 12 | 0 | 2022-04-26 | 13.5 | 4.5 | 0 | 2021-04-26 | 8.5 | 9.5 | 0 | 2020-04-26 | 12.5 | 5.5 | 0 | 2019-04-26 | 9.2 | 8.8 | 0 | 2018-04-26 | 7.9 | 10.1 | 0 | 2017-04-26 | 17 | 1 | 0 | 2016-04-26 | 7.5 | 10.5 | 0 | 7.67 | 0
2025-04-26 | 8 | 10 | 0 | 2024-04-26 | 13.4 | 4.6 | 0 | 2023-04-26 | 6 | 12 | 0 | 2022-04-26 | 12.7 | 5.3 | 0 | 2021-04-26 | 9.5 | 8.5 | 0 | 2020-04-26 | 12 | 6 | 0 | 2019-04-26 | 10.3 | 7.7 | 0 | 2018-04-26 | 9.4 | 8.6 | 0 | 2017-04-26 | 17.2 | 0.8 | 0 | 2016-04-26 | 8.9 | 9.1 | 0 | 7.26 | 0
2025-04-26 | 8 | 10 | 0 | 2024-04-26 | 13.8 | 4.2 | 0 | 2023-04-26 | 6.7 | 11.3 | 0 | 2022-04-26 | 11.6 | 6.4 | 0 | 2021-04-26 | 10.3 | 7.7 | 0 | 2020-04-26 | 12.5 | 5.5 | 0 | 2019-04-26 | 11 | 7 | 0 | 2018-04-26 | 11 | 7 | 0 | 2017-04-26 | 17.1 | 0.9 | 0 | 2016-04-26 | 9.8 | 8.2 | 0 | 6.82 | 0
2025-04-26 | 7.7 | 10.3 | 0 | 2024-04-26 | 14 | 4 | 0 | 2023-04-26 | 8 | 10 | 0 | 2022-04-26 | 11.1 | 6.9 | 0 | 2021-04-26 | 11.1 | 6.9 | 0 | 2020-04-26 | 12.4 | 5.6 | 0 | 2019-04-26 | 11.6 | 6.4 | 0 | 2018-04-26 | 12.3 | 5.7 | 0 | 2017-04-26 | 17.9 | 0.1 | 0 | 2016-04-26 | 10.3 | 7.7 | 0 | 6.36 | 0
2025-04-26 | 7.4 | 10.6 | 0 | 2024-04-26 | 13.9 | 4.1 | 0 | 2023-04-26 | 8.2 | 9.8 | 0 | 2022-04-26 | 10.3 | 7.7 | 0 | 2021-04-26 | 10.7 | 7.3 | 0 | 2020-04-26 | 12.5 | 5.5 | 0 | 2019-04-26 | 11.9 | 6.1 | 0 | 2018-04-26 | 12 | 6 | 0 | 2017-04-26 | 17.7 | 0.3 | 0 | 2016-04-26 | 10.4 | 7.6 | 0 | 6.5 | 0
2025-04-26 | 6.7 | 11.3 | 0 | 2024-04-26 | 12.9 | 5.1 | 0 | 2023-04-26 | 7.5 | 10.5 | 0 | 2022-04-26 | 9.7 | 8.3 | 0 | 2021-04-26 | 9.7 | 8.3 | 0 | 2020-04-26 | 11.5 | 6.5 | 0 | 2019-04-26 | 11.9 | 6.1 | 0 | 2018-04-26 | 12.5 | 5.5 | 0 | 2017-04-26 | 16.3 | 1.7 | 0 | 2016-04-26 | 9.5 | 8.5 | 0 | 7.18 | 0
2025-04-26 | 6.1 | 11.9 | 0 | 2024-04-26 | 10.2 | 7.8 | 0 | 2023-04-26 | 7.1 | 10.9 | 0 | 2022-04-26 | 9.4 | 8.6 | 0 | 2021-04-26 | 7.5 | 10.5 | 0 | 2020-04-26 | 9.4 | 8.6 | 0 | 2019-04-26 | 11.8 | 6.2 | 0 | 2018-04-26 | 10.9 | 7.1 | 0 | 2017-04-26 | 14.5 | 3.5 | 0 | 2016-04-26 | 8.3 | 9.7 | 0 | 8.48 | 0
2025-04-26 | 5.4 | 12.6 | 0 | 2024-04-26 | 9.1 | 8.9 | 0 | 2023-04-26 | 6.6 | 11.4 | 0 | 2022-04-26 | 8.9 | 9.1 | 0 | 2021-04-26 | 6.4 | 11.6 | 0 | 2020-04-26 | 9.2 | 8.8 | 0 | 2019-04-26 | 11.9 | 6.1 | 0 | 2018-04-26 | 9 | 9 | 0 | 2017-04-26 | 13.2 | 4.8 | 0 | 2016-04-26 | 7.1 | 10.9 | 0 | 9.32 | 0
2025-04-26 | 4.6 | 13.4 | 0 | 2024-04-26 | 9.1 | 8.9 | 0 | 2023-04-26 | 6.2 | 11.8 | 0 | 2022-04-26 | 8.2 | 9.8 | 0 | 2021-04-26 | 5 | 13 | 0 | 2020-04-26 | 9.7 | 8.3 | 0 | 2019-04-26 | 10.4 | 7.6 | 0 | 2018-04-26 | 8.6 | 9.4 | 0 | 2017-04-26 | 13.2 | 4.8 | 0 | 2016-04-26 | 5.8 | 12.2 | 0 | 9.92 | 0
2025-04-26 | 3.8 | 14.2 | 0 | 2024-04-26 | 6.5 | 11.5 | 0 | 2023-04-26 | 5.4 | 12.6 | 0 | 2022-04-26 | 8 | 10 | 0 | 2021-04-26 | 3.1 | 14.9 | 0 | 2020-04-26 | 9.5 | 8.5 | 0 | 2019-04-26 | 8.1 | 9.9 | 0 | 2018-04-26 | 7 | 11 | 0 | 2017-04-26 | 13 | 5 | 0 | 2016-04-26 | 4.9 | 13.1 | 0 | 11.07 | 0
2025-04-26 | 3.4 | 14.6 | 0 | 2024-04-26 | 6.2 | 11.8 | 0 | 2023-04-26 | 5.2 | 12.8 | 0 | 2022-04-26 | 7.6 | 10.4 | 0 | 2021-04-26 | 2.6 | 15.4 | 0 | 2020-04-26 | 8.1 | 9.9 | 0 | 2019-04-26 | 7.5 | 10.5 | 0 | 2018-04-26 | 6.6 | 11.4 | 0 | 2017-04-26 | 12.5 | 5.5 | 0 | 2016-04-26 | 3.8 | 14.2 | 0 | 11.65 | 0
2025-04-27 | 3 | 15 | 0 | 2024-04-27 | 6.3 | 11.7 | 0 | 2023-04-27 | 4.5 | 13.5 | 0 | 2022-04-27 | 6.6 | 11.4 | 0 | 2021-04-27 | 1.7 | 16.3 | 0 | 2020-04-27 | 7.6 | 10.4 | 0 | 2019-04-27 | 7.2 | 10.8 | 0 | 2018-04-27 | 6.2 | 11.8 | 0 | 2017-04-27 | 12.1 | 5.9 | 0 | 2016-04-27 | 2.5 | 15.5 | 0 | 12.23 | 0
2025-04-27 | 3 | 15 | 0 | 2024-04-27 | 5.5 | 12.5 | 0 | 2023-04-27 | 5.4 | 12.6 | 0 | 2022-04-27 | 6 | 12 | 0 | 2021-04-27 | 3.4 | 14.6 | 0 | 2020-04-27 | 6.6 | 11.4 | 0 | 2019-04-27 | 7.2 | 10.8 | 0 | 2018-04-27 | 5.1 | 12.9 | 0 | 2017-04-27 | 12.3 | 5.7 | 0 | 2016-04-27 | 0.4 | 17.6 | 0 | 12.51 | 0
2025-04-27 | 2.7 | 15.3 | 0 | 2024-04-27 | 4.5 | 13.5 | 0 | 2023-04-27 | 4.3 | 13.7 | 0 | 2022-04-27 | 5.3 | 12.7 | 0 | 2021-04-27 | 1.7 | 16.3 | 0 | 2020-04-27 | 5.9 | 12.1 | 0 | 2019-04-27 | 6.8 | 11.2 | 0 | 2018-04-27 | 4.2 | 13.8 | 0 | 2017-04-27 | 12.4 | 5.6 | 0 | 2016-04-27 | -0.2 | 18.2 | 0 | 13.24 | 0
2025-04-27 | 2.9 | 15.1 | 0 | 2024-04-27 | 2.4 | 15.6 | 0 | 2023-04-27 | 3.5 | 14.5 | 0 | 2022-04-27 | 4.1 | 13.9 | 0 | 2021-04-27 | 1.8 | 16.2 | 0 | 2020-04-27 | 5.5 | 12.5 | 0 | 2019-04-27 | 6.6 | 11.4 | 0 | 2018-04-27 | 4 | 14 | 0 | 2017-04-27 | 12.3 | 5.7 | 0 | 2016-04-27 | -1.6 | 19.6 | 0 | 13.85 | 0
2025-04-27 | 3.3 | 14.7 | 0 | 2024-04-27 | 3.3 | 14.7 | 0 | 2023-04-27 | 3.1 | 14.9 | 0 | 2022-04-27 | 2.6 | 15.4 | 0 | 2021-04-27 | 2.8 | 15.2 | 0 | 2020-04-27 | 5.3 | 12.7 | 0 | 2019-04-27 | 5.7 | 12.3 | 0 | 2018-04-27 | 3.3 | 14.7 | 0 | 2017-04-27 | 12.2 | 5.8 | 0 | 2016-04-27 | -2.5 | 20.5 | 0 | 14.09 | 0
2025-04-27 | 3.9 | 14.1 | 0 | 2024-04-27 | 3 | 15 | 0 | 2023-04-27 | 2.8 | 15.2 | 0 | 2022-04-27 | 1.8 | 16.2 | 0 | 2021-04-27 | 2.8 | 15.2 | 0 | 2020-04-27 | 5 | 13 | 0 | 2019-04-27 | 4.4 | 13.6 | 0 | 2018-04-27 | 2.5 | 15.5 | 0 | 2017-04-27 | 12 | 6 | 0 | 2016-04-27 | -2.6 | 20.6 | 0 | 14.44 | 0
2025-04-27 | 4.3 | 13.7 | 0 | 2024-04-27 | 4.4 | 13.6 | 0 | 2023-04-27 | 3.2 | 14.8 | 0 | 2022-04-27 | 1.2 | 16.8 | 0 | 2021-04-27 | 3.8 | 14.2 | 0 | 2020-04-27 | 5.2 | 12.8 | 0 | 2019-04-27 | 3.8 | 14.2 | 0 | 2018-04-27 | 2.4 | 15.6 | 0 | 2017-04-27 | 12 | 6 | 0 | 2016-04-27 | -1.9 | 19.9 | 0 | 14.16 | 0
2025-04-27 | 5 | 13 | 0 | 2024-04-27 | 7.4 | 10.6 | 0 | 2023-04-27 | 4 | 14 | 0 | 2022-04-27 | 0.7 | 17.3 | 0 | 2021-04-27 | 5.8 | 12.2 | 0 | 2020-04-27 | 6.1 | 11.9 | 0 | 2019-04-27 | 3.9 | 14.1 | 0 | 2018-04-27 | 4.2 | 13.8 | 0 | 2017-04-27 | 12.2 | 5.8 | 0 | 2016-04-27 | -1.2 | 19.2 | 0 | 13.19 | 0
2025-04-27 | 5.2 | 12.8 | 0 | 2024-04-27 | 11.3 | 6.7 | 0 | 2023-04-27 | 5.4 | 12.6 | 0 | 2022-04-27 | 0.5 | 17.5 | 0 | 2021-04-27 | 6.8 | 11.2 | 0 | 2020-04-27 | 8.6 | 9.4 | 0 | 2019-04-27 | 4.2 | 13.8 | 0 | 2018-04-27 | 5.1 | 12.9 | 0 | 2017-04-27 | 12.2 | 5.8 | 0 | 2016-04-27 | 0 | 18 | 0 | 12.07 | 0
2025-04-27 | 6.8 | 11.2 | 0 | 2024-04-27 | 13.3 | 4.7 | 0 | 2023-04-27 | 6.8 | 11.2 | 0 | 2022-04-27 | 0.6 | 17.4 | 0 | 2021-04-27 | 7.8 | 10.2 | 0 | 2020-04-27 | 9.4 | 8.6 | 0 | 2019-04-27 | 4.9 | 13.1 | 0 | 2018-04-27 | 7.4 | 10.6 | 0 | 2017-04-27 | 12.8 | 5.2 | 0 | 2016-04-27 | 1 | 17 | 0 | 10.92 | 0
2025-04-27 | 10.4 | 7.6 | 0 | 2024-04-27 | 16 | 2 | 0 | 2023-04-27 | 9.1 | 8.9 | 0 | 2022-04-27 | 0.8 | 17.2 | 0 | 2021-04-27 | 8.9 | 9.1 | 0 | 2020-04-27 | 11.2 | 6.8 | 0 | 2019-04-27 | 4.7 | 13.3 | 0 | 2018-04-27 | 9.3 | 8.7 | 0 | 2017-04-27 | 14.6 | 3.4 | 0 | 2016-04-27 | 2.2 | 15.8 | 0 | 9.28 | 0
2025-04-27 | 13.9 | 4.1 | 0 | 2024-04-27 | 18.3 | 0 | 0.3 | 2023-04-27 | 11 | 7 | 0 | 2022-04-27 | 1.6 | 16.4 | 0 | 2021-04-27 | 10.1 | 7.9 | 0 | 2020-04-27 | 10.7 | 7.3 | 0 | 2019-04-27 | 3.8 | 14.2 | 0 | 2018-04-27 | 11.5 | 6.5 | 0 | 2017-04-27 | 18.8 | 0 | 0.8 | 2016-04-27 | 3.3 | 14.7 | 0 | 7.81 | 0.11
2025-04-27 | 15.6 | 2.4 | 0 | 2024-04-27 | 19.4 | 0 | 1.4 | 2023-04-27 | 11.3 | 6.7 | 0 | 2022-04-27 | 2.9 | 15.1 | 0 | 2021-04-27 | 11.1 | 6.9 | 0 | 2020-04-27 | 11.9 | 6.1 | 0 | 2019-04-27 | 3.6 | 14.4 | 0 | 2018-04-27 | 12.8 | 5.2 | 0 | 2017-04-27 | 22.1 | 0 | 4.1 | 2016-04-27 | 4.7 | 13.3 | 0 | 7.01 | 0.55
2025-04-27 | 16.7 | 1.3 | 0 | 2024-04-27 | 19 | 0 | 1 | 2023-04-27 | 11 | 7 | 0 | 2022-04-27 | 2.9 | 15.1 | 0 | 2021-04-27 | 12.1 | 5.9 | 0 | 2020-04-27 | 12.5 | 5.5 | 0 | 2019-04-27 | 3.1 | 14.9 | 0 | 2018-04-27 | 14.9 | 3.1 | 0 | 2017-04-27 | 23.6 | 0 | 5.6 | 2016-04-27 | 5.1 | 12.9 | 0 | 6.57 | 0.66
2025-04-27 | 17.6 | 0.4 | 0 | 2024-04-27 | 14.8 | 3.2 | 0 | 2023-04-27 | 12.6 | 5.4 | 0 | 2022-04-27 | 2.8 | 15.2 | 0 | 2021-04-27 | 12.7 | 5.3 | 0 | 2020-04-27 | 12.6 | 5.4 | 0 | 2019-04-27 | 3.1 | 14.9 | 0 | 2018-04-27 | 14.6 | 3.4 | 0 | 2017-04-27 | 25.6 | 0 | 7.6 | 2016-04-27 | 6.8 | 11.2 | 0 | 6.44 | 0.76
2025-04-27 | 18.5 | 0 | 0.5 | 2024-04-27 | 13 | 5 | 0 | 2023-04-27 | 11.7 | 6.3 | 0 | 2022-04-27 | 2.4 | 15.6 | 0 | 2021-04-27 | 14 | 4 | 0 | 2020-04-27 | 12.1 | 5.9 | 0 | 2019-04-27 | 1.2 | 16.8 | 0 | 2018-04-27 | 15.7 | 2.3 | 0 | 2017-04-27 | 26.3 | 0 | 8.3 | 2016-04-27 | 7.9 | 10.1 | 0 | 6.6 | 0.88
2025-04-27 | 18.7 | 0 | 0.7 | 2024-04-27 | 11.7 | 6.3 | 0 | 2023-04-27 | 12.4 | 5.6 | 0 | 2022-04-27 | 2.1 | 15.9 | 0 | 2021-04-27 | 14.3 | 3.7 | 0 | 2020-04-27 | 11.9 | 6.1 | 0 | 2019-04-27 | 1.6 | 16.4 | 0 | 2018-04-27 | 15.2 | 2.8 | 0 | 2017-04-27 | 25.8 | 0 | 7.8 | 2016-04-27 | 7.5 | 10.5 | 0 | 6.73 | 0.85
2025-04-27 | 18.1 | 0 | 0.1 | 2024-04-27 | 10.8 | 7.2 | 0 | 2023-04-27 | 11.9 | 6.1 | 0 | 2022-04-27 | 2.9 | 15.1 | 0 | 2021-04-27 | 14.5 | 3.5 | 0 | 2020-04-27 | 11.8 | 6.2 | 0 | 2019-04-27 | 2.5 | 15.5 | 0 | 2018-04-27 | 14.8 | 3.2 | 0 | 2017-04-27 | 26.1 | 0 | 8.1 | 2016-04-27 | 8.4 | 9.6 | 0 | 6.64 | 0.82
2025-04-27 | 17.2 | 0.8 | 0 | 2024-04-27 | 11 | 7 | 0 | 2023-04-27 | 10.8 | 7.2 | 0 | 2022-04-27 | 2.9 | 15.1 | 0 | 2021-04-27 | 13.2 | 4.8 | 0 | 2020-04-27 | 10.2 | 7.8 | 0 | 2019-04-27 | 3.3 | 14.7 | 0 | 2018-04-27 | 14 | 4 | 0 | 2017-04-27 | 23.5 | 0 | 5.5 | 2016-04-27 | 7.8 | 10.2 | 0 | 7.16 | 0.55
2025-04-27 | 15.1 | 2.9 | 0 | 2024-04-27 | 10.7 | 7.3 | 0 | 2023-04-27 | 9.1 | 8.9 | 0 | 2022-04-27 | 3 | 15 | 0 | 2021-04-27 | 13.3 | 4.7 | 0 | 2020-04-27 | 7.9 | 10.1 | 0 | 2019-04-27 | 3.4 | 14.6 | 0 | 2018-04-27 | 12.4 | 5.6 | 0 | 2017-04-27 | 22.3 | 0 | 4.3 | 2016-04-27 | 6.2 | 11.8 | 0 | 8.09 | 0.43
2025-04-27 | 12.5 | 5.5 | 0 | 2024-04-27 | 10.4 | 7.6 | 0 | 2023-04-27 | 8.6 | 9.4 | 0 | 2022-04-27 | 1.8 | 16.2 | 0 | 2021-04-27 | 12.7 | 5.3 | 0 | 2020-04-27 | 6.4 | 11.6 | 0 | 2019-04-27 | 3.2 | 14.8 | 0 | 2018-04-27 | 10.9 | 7.1 | 0 | 2017-04-27 | 21.1 | 0 | 3.1 | 2016-04-27 | 4.8 | 13.2 | 0 | 9.07 | 0.31
2025-04-27 | 13 | 5 | 0 | 2024-04-27 | 10.3 | 7.7 | 0 | 2023-04-27 | 7.4 | 10.6 | 0 | 2022-04-27 | 1.9 | 16.1 | 0 | 2021-04-27 | 11.7 | 6.3 | 0 | 2020-04-27 | 5 | 13 | 0 | 2019-04-27 | 3.1 | 14.9 | 0 | 2018-04-27 | 10.3 | 7.7 | 0 | 2017-04-27 | 20.1 | 0 | 2.1 | 2016-04-27 | 2.9 | 15.1 | 0 | 9.64 | 0.21
2025-04-27 | 8.9 | 9.1 | 0 | 2024-04-27 | 10.3 | 7.7 | 0 | 2023-04-27 | 7.7 | 10.3 | 0 | 2022-04-27 | 1.6 | 16.4 | 0 | 2021-04-27 | 11.8 | 6.2 | 0 | 2020-04-27 | 4.5 | 13.5 | 0 | 2019-04-27 | 2.3 | 15.7 | 0 | 2018-04-27 | 8.9 | 9.1 | 0 | 2017-04-27 | 20.6 | 0 | 2.6 | 2016-04-27 | 1.7 | 16.3 | 0 | 10.43 | 0.26
2025-04-27 | 9.8 | 8.2 | 0 | 2024-04-27 | 10.3 | 7.7 | 0 | 2023-04-27 | 6.2 | 11.8 | 0 | 2022-04-27 | 0.1 | 17.9 | 0 | 2021-04-27 | 10.2 | 7.8 | 0 | 2020-04-27 | 3.2 | 14.8 | 0 | 2019-04-27 | 2 | 16 | 0 | 2018-04-27 | 7.4 | 10.6 | 0 | 2017-04-27 | 22 | 0 | 4 | 2016-04-27 | 1.1 | 16.9 | 0 | 11.17 | 0.4
2025-04-28 | 8 | 10 | 0 | 2024-04-28 | 9.5 | 8.5 | 0 | 2023-04-28 | 6.1 | 11.9 | 0 | 2022-04-28 | 0.4 | 17.6 | 0 | 2021-04-28 | 10.4 | 7.6 | 0 | 2020-04-28 | 2.5 | 15.5 | 0 | 2019-04-28 | 2 | 16 | 0 | 2018-04-28 | 7.5 | 10.5 | 0 | 2017-04-28 | 17.4 | 0.6 | 0 | 2016-04-28 | -0.1 | 18.1 | 0 | 11.63 | 0
2025-04-28 | 7.1 | 10.9 | 0 | 2024-04-28 | 9.6 | 8.4 | 0 | 2023-04-28 | 6.5 | 11.5 | 0 | 2022-04-28 | -0.5 | 18.5 | 0 | 2021-04-28 | 9.8 | 8.2 | 0 | 2020-04-28 | 2.9 | 15.1 | 0 | 2019-04-28 | 1.3 | 16.7 | 0 | 2018-04-28 | 6.3 | 11.7 | 0 | 2017-04-28 | 16.2 | 1.8 | 0 | 2016-04-28 | 0.1 | 17.9 | 0 | 12.07 | 0
2025-04-28 | 7 | 11 | 0 | 2024-04-28 | 9.9 | 8.1 | 0 | 2023-04-28 | 6.3 | 11.7 | 0 | 2022-04-28 | -0.3 | 18.3 | 0 | 2021-04-28 | 8.7 | 9.3 | 0 | 2020-04-28 | 1.1 | 16.9 | 0 | 2019-04-28 | 0.8 | 17.2 | 0 | 2018-04-28 | 5.5 | 12.5 | 0 | 2017-04-28 | 15.9 | 2.1 | 0 | 2016-04-28 | 0.5 | 17.5 | 0 | 12.46 | 0
2025-04-28 | 5.6 | 12.4 | 0 | 2024-04-28 | 9.2 | 8.8 | 0 | 2023-04-28 | 5.4 | 12.6 | 0 | 2022-04-28 | -0.3 | 18.3 | 0 | 2021-04-28 | 8.4 | 9.6 | 0 | 2020-04-28 | 0.6 | 17.4 | 0 | 2019-04-28 | 0.7 | 17.3 | 0 | 2018-04-28 | 5.5 | 12.5 | 0 | 2017-04-28 | 16.1 | 1.9 | 0 | 2016-04-28 | -0.1 | 18.1 | 0 | 12.89 | 0
2025-04-28 | 4.9 | 13.1 | 0 | 2024-04-28 | 8.9 | 9.1 | 0 | 2023-04-28 | 4.3 | 13.7 | 0 | 2022-04-28 | -0.7 | 18.7 | 0 | 2021-04-28 | 7.6 | 10.4 | 0 | 2020-04-28 | -0.9 | 18.9 | 0 | 2019-04-28 | 0.5 | 17.5 | 0 | 2018-04-28 | 6.6 | 11.4 | 0 | 2017-04-28 | 15.8 | 2.2 | 0 | 2016-04-28 | -1.3 | 19.3 | 0 | 13.43 | 0
2025-04-28 | 3.2 | 14.8 | 0 | 2024-04-28 | 9.2 | 8.8 | 0 | 2023-04-28 | 2.9 | 15.1 | 0 | 2022-04-28 | -1 | 19 | 0 | 2021-04-28 | 7.3 | 10.7 | 0 | 2020-04-28 | 0.6 | 17.4 | 0 | 2019-04-28 | -0.8 | 18.8 | 0 | 2018-04-28 | 6.9 | 11.1 | 0 | 2017-04-28 | 13.9 | 4.1 | 0 | 2016-04-28 | -1.3 | 19.3 | 0 | 13.91 | 0
2025-04-28 | 6.7 | 11.3 | 0 | 2024-04-28 | 10.3 | 7.7 | 0 | 2023-04-28 | 5 | 13 | 0 | 2022-04-28 | -0.5 | 18.5 | 0 | 2021-04-28 | 8.8 | 9.2 | 0 | 2020-04-28 | 2.3 | 15.7 | 0 | 2019-04-28 | 0.3 | 17.7 | 0 | 2018-04-28 | 7.1 | 10.9 | 0 | 2017-04-28 | 12.5 | 5.5 | 0 | 2016-04-28 | -0.1 | 18.1 | 0 | 12.76 | 0
2025-04-28 | 9.6 | 8.4 | 0 | 2024-04-28 | 11.4 | 6.6 | 0 | 2023-04-28 | 7.9 | 10.1 | 0 | 2022-04-28 | 0.7 | 17.3 | 0 | 2021-04-28 | 11.3 | 6.7 | 0 | 2020-04-28 | 5.7 | 12.3 | 0 | 2019-04-28 | 0.6 | 17.4 | 0 | 2018-04-28 | 7.2 | 10.8 | 0 | 2017-04-28 | 12.1 | 5.9 | 0 | 2016-04-28 | 0.7 | 17.3 | 0 | 11.28 | 0
2025-04-28 | 12.7 | 5.3 | 0 | 2024-04-28 | 13 | 5 | 0 | 2023-04-28 | 10.6 | 7.4 | 0 | 2022-04-28 | 1.8 | 16.2 | 0 | 2021-04-28 | 13.3 | 4.7 | 0 | 2020-04-28 | 8 | 10 | 0 | 2019-04-28 | 2 | 16 | 0 | 2018-04-28 | 7.4 | 10.6 | 0 | 2017-04-28 | 13.8 | 4.2 | 0 | 2016-04-28 | 1.3 | 16.7 | 0 | 9.61 | 0
2025-04-28 | 15.3 | 2.7 | 0 | 2024-04-28 | 15.1 | 2.9 | 0 | 2023-04-28 | 12.6 | 5.4 | 0 | 2022-04-28 | 3.2 | 14.8 | 0 | 2021-04-28 | 15.1 | 2.9 | 0 | 2020-04-28 | 9.3 | 8.7 | 0 | 2019-04-28 | 3.3 | 14.7 | 0 | 2018-04-28 | 8.2 | 9.8 | 0 | 2017-04-28 | 14.4 | 3.6 | 0 | 2016-04-28 | 2.3 | 15.7 | 0 | 8.12 | 0
2025-04-28 | 18.4 | 0 | 0.4 | 2024-04-28 | 17.3 | 0.7 | 0 | 2023-04-28 | 14.5 | 3.5 | 0 | 2022-04-28 | 5 | 13 | 0 | 2021-04-28 | 15.2 | 2.8 | 0 | 2020-04-28 | 10.1 | 7.9 | 0 | 2019-04-28 | 3.2 | 14.8 | 0 | 2018-04-28 | 9.1 | 8.9 | 0 | 2017-04-28 | 15.2 | 2.8 | 0 | 2016-04-28 | 3.7 | 14.3 | 0 | 6.87 | 0.04
2025-04-28 | 19.6 | 0 | 1.6 | 2024-04-28 | 18.6 | 0 | 0.6 | 2023-04-28 | 15.8 | 2.2 | 0 | 2022-04-28 | 6.4 | 11.6 | 0 | 2021-04-28 | 15.1 | 2.9 | 0 | 2020-04-28 | 12.3 | 5.7 | 0 | 2019-04-28 | 4.9 | 13.1 | 0 | 2018-04-28 | 9.1 | 8.9 | 0 | 2017-04-28 | 15.7 | 2.3 | 0 | 2016-04-28 | 4 | 14 | 0 | 6.07 | 0.22
2025-04-28 | 20.3 | 0 | 2.3 | 2024-04-28 | 19 | 0 | 1 | 2023-04-28 | 17.2 | 0.8 | 0 | 2022-04-28 | 7.4 | 10.6 | 0 | 2021-04-28 | 14 | 4 | 0 | 2020-04-28 | 13 | 5 | 0 | 2019-04-28 | 6.3 | 11.7 | 0 | 2018-04-28 | 8.9 | 9.1 | 0 | 2017-04-28 | 16.8 | 1.2 | 0 | 2016-04-28 | 5.1 | 12.9 | 0 | 5.53 | 0.33
2025-04-28 | 21.2 | 0 | 3.2 | 2024-04-28 | 20.1 | 0 | 2.1 | 2023-04-28 | 17.8 | 0.2 | 0 | 2022-04-28 | 8.9 | 9.1 | 0 | 2021-04-28 | 11.6 | 6.4 | 0 | 2020-04-28 | 13.5 | 4.5 | 0 | 2019-04-28 | 7.4 | 10.6 | 0 | 2018-04-28 | 9 | 9 | 0 | 2017-04-28 | 17.2 | 0.8 | 0 | 2016-04-28 | 7.2 | 10.8 | 0 | 5.14 | 0.53
2025-04-28 | 21.4 | 0 | 3.4 | 2024-04-28 | 20.7 | 0 | 2.7 | 2023-04-28 | 18.3 | 0 | 0.3 | 2022-04-28 | 9.3 | 8.7 | 0 | 2021-04-28 | 10.8 | 7.2 | 0 | 2020-04-28 | 14.6 | 3.4 | 0 | 2019-04-28 | 8.7 | 9.3 | 0 | 2018-04-28 | 10.1 | 7.9 | 0 | 2017-04-28 | 17.7 | 0.3 | 0 | 2016-04-28 | 7.9 | 10.1 | 0 | 4.69 | 0.64
2025-04-28 | 21.6 | 0 | 3.6 | 2024-04-28 | 19.5 | 0 | 1.5 | 2023-04-28 | 18.4 | 0 | 0.4 | 2022-04-28 | 9.7 | 8.3 | 0 | 2021-04-28 | 9.8 | 8.2 | 0 | 2020-04-28 | 15.1 | 2.9 | 0 | 2019-04-28 | 9.3 | 8.7 | 0 | 2018-04-28 | 9.7 | 8.3 | 0 | 2017-04-28 | 19.1 | 0 | 1.1 | 2016-04-28 | 8 | 10 | 0 | 4.64 | 0.66
2025-04-28 | 21.4 | 0 | 3.4 | 2024-04-28 | 19.9 | 0 | 1.9 | 2023-04-28 | 18.3 | 0 | 0.3 | 2022-04-28 | 9.8 | 8.2 | 0 | 2021-04-28 | 9.5 | 8.5 | 0 | 2020-04-28 | 14.9 | 3.1 | 0 | 2019-04-28 | 9.7 | 8.3 | 0 | 2018-04-28 | 10 | 8 | 0 | 2017-04-28 | 18.9 | 0 | 0.9 | 2016-04-28 | 9.5 | 8.5 | 0 | 4.46 | 0.65
2025-04-28 | 20.5 | 0 | 2.5 | 2024-04-28 | 20.1 | 0 | 2.1 | 2023-04-28 | 17.7 | 0.3 | 0 | 2022-04-28 | 9.3 | 8.7 | 0 | 2021-04-28 | 8.9 | 9.1 | 0 | 2020-04-28 | 14.1 | 3.9 | 0 | 2019-04-28 | 9.4 | 8.6 | 0 | 2018-04-28 | 8.4 | 9.6 | 0 | 2017-04-28 | 18 | 0 | 0 | 2016-04-28 | 8.7 | 9.3 | 0 | 4.95 | 0.46
2025-04-28 | 19 | 0 | 1 | 2024-04-28 | 18.8 | 0 | 0.8 | 2023-04-28 | 16.8 | 1.2 | 0 | 2022-04-28 | 8.4 | 9.6 | 0 | 2021-04-28 | 8.2 | 9.8 | 0 | 2020-04-28 | 14.2 | 3.8 | 0 | 2019-04-28 | 8.5 | 9.5 | 0 | 2018-04-28 | 7.4 | 10.6 | 0 | 2017-04-28 | 17 | 1 | 0 | 2016-04-28 | 7.9 | 10.1 | 0 | 5.56 | 0.18
2025-04-28 | 16.6 | 1.4 | 0 | 2024-04-28 | 16.4 | 1.6 | 0 | 2023-04-28 | 14.9 | 3.1 | 0 | 2022-04-28 | 7.2 | 10.8 | 0 | 2021-04-28 | 8.6 | 9.4 | 0 | 2020-04-28 | 10 | 8 | 0 | 2019-04-28 | 7.1 | 10.9 | 0 | 2018-04-28 | 6.9 | 11.1 | 0 | 2017-04-28 | 15.8 | 2.2 | 0 | 2016-04-28 | 6.8 | 11.2 | 0 | 6.97 | 0
2025-04-28 | 13.9 | 4.1 | 0 | 2024-04-28 | 14.6 | 3.4 | 0 | 2023-04-28 | 13.6 | 4.4 | 0 | 2022-04-28 | 6.2 | 11.8 | 0 | 2021-04-28 | 8.7 | 9.3 | 0 | 2020-04-28 | 9.1 | 8.9 | 0 | 2019-04-28 | 5.4 | 12.6 | 0 | 2018-04-28 | 6.6 | 11.4 | 0 | 2017-04-28 | 14.5 | 3.5 | 0 | 2016-04-28 | 5.1 | 12.9 | 0 | 8.23 | 0
2025-04-28 | 12.7 | 5.3 | 0 | 2024-04-28 | 12.6 | 5.4 | 0 | 2023-04-28 | 13.2 | 4.8 | 0 | 2022-04-28 | 4.3 | 13.7 | 0 | 2021-04-28 | 8.8 | 9.2 | 0 | 2020-04-28 | 6.5 | 11.5 | 0 | 2019-04-28 | 3.6 | 14.4 | 0 | 2018-04-28 | 6.1 | 11.9 | 0 | 2017-04-28 | 13.1 | 4.9 | 0 | 2016-04-28 | 3.1 | 14.9 | 0 | 9.6 | 0
2025-04-28 | 11 | 7 | 0 | 2024-04-28 | 10.9 | 7.1 | 0 | 2023-04-28 | 12.8 | 5.2 | 0 | 2022-04-28 | 2 | 16 | 0 | 2021-04-28 | 8.8 | 9.2 | 0 | 2020-04-28 | 7.2 | 10.8 | 0 | 2019-04-28 | 4.3 | 13.7 | 0 | 2018-04-28 | 5.6 | 12.4 | 0 | 2017-04-28 | 13.1 | 4.9 | 0 | 2016-04-28 | 3 | 15 | 0 | 10.13 | 0
2025-04-28 | 10 | 8 | 0 | 2024-04-28 | 9.2 | 8.8 | 0 | 2023-04-28 | 12.4 | 5.6 | 0 | 2022-04-28 | 1.5 | 16.5 | 0 | 2021-04-28 | 8.7 | 9.3 | 0 | 2020-04-28 | 5.4 | 12.6 | 0 | 2019-04-28 | 3.1 | 14.9 | 0 | 2018-04-28 | 5.3 | 12.7 | 0 | 2017-04-28 | 13 | 5 | 0 | 2016-04-28 | 2.2 | 15.8 | 0 | 10.92 | 0
2025-04-29 | 11.3 | 6.7 | 0 | 2024-04-29 | 8.2 | 9.8 | 0 | 2023-04-29 | 11.6 | 6.4 | 0 | 2022-04-29 | 1 | 17 | 0 | 2021-04-29 | 8.8 | 9.2 | 0 | 2020-04-29 | 5.1 | 12.9 | 0 | 2019-04-29 | 1.8 | 16.2 | 0 | 2018-04-29 | 5.2 | 12.8 | 0 | 2017-04-29 | 12.8 | 5.2 | 0 | 2016-04-29 | 0.7 | 17.3 | 0 | 11.35 | 0
2025-04-29 | 9.6 | 8.4 | 0 | 2024-04-29 | 7.4 | 10.6 | 0 | 2023-04-29 | 10.9 | 7.1 | 0 | 2022-04-29 | -0.8 | 18.8 | 0 | 2021-04-29 | 8.3 | 9.7 | 0 | 2020-04-29 | 4.2 | 13.8 | 0 | 2019-04-29 | 1.7 | 16.3 | 0 | 2018-04-29 | 4.8 | 13.2 | 0 | 2017-04-29 | 12.3 | 5.7 | 0 | 2016-04-29 | 0 | 18 | 0 | 12.16 | 0
2025-04-29 | 10.7 | 7.3 | 0 | 2024-04-29 | 6.6 | 11.4 | 0 | 2023-04-29 | 11.1 | 6.9 | 0 | 2022-04-29 | -0.4 | 18.4 | 0 | 2021-04-29 | 7.9 | 10.1 | 0 | 2020-04-29 | 3.4 | 14.6 | 0 | 2019-04-29 | 0.6 | 17.4 | 0 | 2018-04-29 | 4.7 | 13.3 | 0 | 2017-04-29 | 12.5 | 5.5 | 0 | 2016-04-29 | -0.2 | 18.2 | 0 | 12.31 | 0
2025-04-29 | 11.6 | 6.4 | 0 | 2024-04-29 | 6.1 | 11.9 | 0 | 2023-04-29 | 11.1 | 6.9 | 0 | 2022-04-29 | 0.7 | 17.3 | 0 | 2021-04-29 | 7.9 | 10.1 | 0 | 2020-04-29 | 3 | 15 | 0 | 2019-04-29 | -1.2 | 19.2 | 0 | 2018-04-29 | 4.6 | 13.4 | 0 | 2017-04-29 | 12.2 | 5.8 | 0 | 2016-04-29 | -0.7 | 18.7 | 0 | 12.47 | 0
2025-04-29 | 12.6 | 5.4 | 0 | 2024-04-29 | 5.6 | 12.4 | 0 | 2023-04-29 | 10.5 | 7.5 | 0 | 2022-04-29 | -0.1 | 18.1 | 0 | 2021-04-29 | 8.3 | 9.7 | 0 | 2020-04-29 | 3.1 | 14.9 | 0 | 2019-04-29 | -1.9 | 19.9 | 0 | 2018-04-29 | 3.8 | 14.2 | 0 | 2017-04-29 | 12.1 | 5.9 | 0 | 2016-04-29 | -2.2 | 20.2 | 0 | 12.82 | 0
2025-04-29 | 13.6 | 4.4 | 0 | 2024-04-29 | 5 | 13 | 0 | 2023-04-29 | 10.2 | 7.8 | 0 | 2022-04-29 | -2 | 20 | 0 | 2021-04-29 | 8.2 | 9.8 | 0 | 2020-04-29 | 3.1 | 14.9 | 0 | 2019-04-29 | -2.8 | 20.8 | 0 | 2018-04-29 | 3.5 | 14.5 | 0 | 2017-04-29 | 11.8 | 6.2 | 0 | 2016-04-29 | -2.5 | 20.5 | 0 | 13.19 | 0
2025-04-29 | 14.7 | 3.3 | 0 | 2024-04-29 | 5 | 13 | 0 | 2023-04-29 | 10.3 | 7.7 | 0 | 2022-04-29 | 1.1 | 16.9 | 0 | 2021-04-29 | 8.6 | 9.4 | 0 | 2020-04-29 | 3.6 | 14.4 | 0 | 2019-04-29 | -1.1 | 19.1 | 0 | 2018-04-29 | 3.7 | 14.3 | 0 | 2017-04-29 | 12.1 | 5.9 | 0 | 2016-04-29 | -0.5 | 18.5 | 0 | 12.25 | 0
2025-04-29 | 17.2 | 0.8 | 0 | 2024-04-29 | 5.2 | 12.8 | 0 | 2023-04-29 | 11 | 7 | 0 | 2022-04-29 | 2.8 | 15.2 | 0 | 2021-04-29 | 9.6 | 8.4 | 0 | 2020-04-29 | 5.9 | 12.1 | 0 | 2019-04-29 | 2.7 | 15.3 | 0 | 2018-04-29 | 3.8 | 14.2 | 0 | 2017-04-29 | 12.5 | 5.5 | 0 | 2016-04-29 | 1.9 | 16.1 | 0 | 10.74 | 0
2025-04-29 | 18.8 | 0 | 0.8 | 2024-04-29 | 5.8 | 12.2 | 0 | 2023-04-29 | 12.5 | 5.5 | 0 | 2022-04-29 | 4.5 | 13.5 | 0 | 2021-04-29 | 10.9 | 7.1 | 0 | 2020-04-29 | 8.8 | 9.2 | 0 | 2019-04-29 | 4.4 | 13.6 | 0 | 2018-04-29 | 4.9 | 13.1 | 0 | 2017-04-29 | 13.1 | 4.9 | 0 | 2016-04-29 | 4.4 | 13.6 | 0 | 9.27 | 0.08
2025-04-29 | 21.8 | 0 | 3.8 | 2024-04-29 | 5.8 | 12.2 | 0 | 2023-04-29 | 11.6 | 6.4 | 0 | 2022-04-29 | 6 | 12 | 0 | 2021-04-29 | 12.7 | 5.3 | 0 | 2020-04-29 | 10.9 | 7.1 | 0 | 2019-04-29 | 5.6 | 12.4 | 0 | 2018-04-29 | 5.5 | 12.5 | 0 | 2017-04-29 | 14 | 4 | 0 | 2016-04-29 | 6.1 | 11.9 | 0 | 8.38 | 0.38
2025-04-29 | 21.4 | 0 | 3.4 | 2024-04-29 | 7.4 | 10.6 | 0 | 2023-04-29 | 8.7 | 9.3 | 0 | 2022-04-29 | 7.2 | 10.8 | 0 | 2021-04-29 | 13.8 | 4.2 | 0 | 2020-04-29 | 13.7 | 4.3 | 0 | 2019-04-29 | 7.3 | 10.7 | 0 | 2018-04-29 | 4.9 | 13.1 | 0 | 2017-04-29 | 14.1 | 3.9 | 0 | 2016-04-29 | 8 | 10 | 0 | 7.69 | 0.34
2025-04-29 | 21.3 | 0 | 3.3 | 2024-04-29 | 8.1 | 9.9 | 0 | 2023-04-29 | 8 | 10 | 0 | 2022-04-29 | 9 | 9 | 0 | 2021-04-29 | 14.5 | 3.5 | 0 | 2020-04-29 | 14.7 | 3.3 | 0 | 2019-04-29 | 8.2 | 9.8 | 0 | 2018-04-29 | 5.5 | 12.5 | 0 | 2017-04-29 | 15.9 | 2.1 | 0 | 2016-04-29 | 9 | 9 | 0 | 6.91 | 0.33
2025-04-29 | 23.2 | 0 | 5.2 | 2024-04-29 | 8.8 | 9.2 | 0 | 2023-04-29 | 8.3 | 9.7 | 0 | 2022-04-29 | 10.9 | 7.1 | 0 | 2021-04-29 | 15.5 | 2.5 | 0 | 2020-04-29 | 16.1 | 1.9 | 0 | 2019-04-29 | 8.3 | 9.7 | 0 | 2018-04-29 | 4.9 | 13.1 | 0 | 2017-04-29 | 16.5 | 1.5 | 0 | 2016-04-29 | 10.2 | 7.8 | 0 | 6.25 | 0.52
2025-04-29 | 19.8 | 0 | 1.8 | 2024-04-29 | 9.2 | 8.8 | 0 | 2023-04-29 | 8.4 | 9.6 | 0 | 2022-04-29 | 10.8 | 7.2 | 0 | 2021-04-29 | 16.3 | 1.7 | 0 | 2020-04-29 | 15.8 | 2.2 | 0 | 2019-04-29 | 8.7 | 9.3 | 0 | 2018-04-29 | 6 | 12 | 0 | 2017-04-29 | 15.9 | 2.1 | 0 | 2016-04-29 | 11 | 7 | 0 | 5.99 | 0.18
2025-04-29 | 20.1 | 0 | 2.1 | 2024-04-29 | 11.1 | 6.9 | 0 | 2023-04-29 | 8.3 | 9.7 | 0 | 2022-04-29 | 12.6 | 5.4 | 0 | 2021-04-29 | 15.9 | 2.1 | 0 | 2020-04-29 | 15.8 | 2.2 | 0 | 2019-04-29 | 9.1 | 8.9 | 0 | 2018-04-29 | 5.5 | 12.5 | 0 | 2017-04-29 | 15.6 | 2.4 | 0 | 2016-04-29 | 12.3 | 5.7 | 0 | 5.58 | 0.21
2025-04-29 | 23.3 | 0 | 5.3 | 2024-04-29 | 11.1 | 6.9 | 0 | 2023-04-29 | 8.4 | 9.6 | 0 | 2022-04-29 | 12.5 | 5.5 | 0 | 2021-04-29 | 15.5 | 2.5 | 0 | 2020-04-29 | 15.6 | 2.4 | 0 | 2019-04-29 | 8.9 | 9.1 | 0 | 2018-04-29 | 5.5 | 12.5 | 0 | 2017-04-29 | 15 | 3 | 0 | 2016-04-29 | 12.5 | 5.5 | 0 | 5.7 | 0.53
2025-04-29 | 24 | 0 | 6 | 2024-04-29 | 11.3 | 6.7 | 0 | 2023-04-29 | 8.7 | 9.3 | 0 | 2022-04-29 | 13.2 | 4.8 | 0 | 2021-04-29 | 15.7 | 2.3 | 0 | 2020-04-29 | 16.2 | 1.8 | 0 | 2019-04-29 | 8.6 | 9.4 | 0 | 2018-04-29 | 4.4 | 13.6 | 0 | 2017-04-29 | 14.1 | 3.9 | 0 | 2016-04-29 | 12.3 | 5.7 | 0 | 5.75 | 0.6
2025-04-29 | 24.2 | 0 | 6.2 | 2024-04-29 | 11.3 | 6.7 | 0 | 2023-04-29 | 8.7 | 9.3 | 0 | 2022-04-29 | 12.9 | 5.1 | 0 | 2021-04-29 | 15.4 | 2.6 | 0 | 2020-04-29 | 15.5 | 2.5 | 0 | 2019-04-29 | 8.1 | 9.9 | 0 | 2018-04-29 | 4.5 | 13.5 | 0 | 2017-04-29 | 13.8 | 4.2 | 0 | 2016-04-29 | 12.3 | 5.7 | 0 | 5.95 | 0.62
2025-04-29 | 17.1 | 0.9 | 0 | 2024-04-29 | 11.4 | 6.6 | 0 | 2023-04-29 | 8.5 | 9.5 | 0 | 2022-04-29 | 11.8 | 6.2 | 0 | 2021-04-29 | 14.7 | 3.3 | 0 | 2020-04-29 | 14.9 | 3.1 | 0 | 2019-04-29 | 7.4 | 10.6 | 0 | 2018-04-29 | 4.5 | 13.5 | 0 | 2017-04-29 | 10.7 | 7.3 | 0 | 2016-04-29 | 11.4 | 6.6 | 0 | 6.76 | 0
2025-04-29 | 18.4 | 0 | 0.4 | 2024-04-29 | 11.1 | 6.9 | 0 | 2023-04-29 | 8.3 | 9.7 | 0 | 2022-04-29 | 10.4 | 7.6 | 0 | 2021-04-29 | 12.9 | 5.1 | 0 | 2020-04-29 | 13.8 | 4.2 | 0 | 2019-04-29 | 6.5 | 11.5 | 0 | 2018-04-29 | 4.8 | 13.2 | 0 | 2017-04-29 | 7.7 | 10.3 | 0 | 2016-04-29 | 10.6 | 7.4 | 0 | 7.59 | 0.04
2025-04-29 | 18.9 | 0 | 0.9 | 2024-04-29 | 10.6 | 7.4 | 0 | 2023-04-29 | 7.9 | 10.1 | 0 | 2022-04-29 | 9.8 | 8.2 | 0 | 2021-04-29 | 13.2 | 4.8 | 0 | 2020-04-29 | 13.5 | 4.5 | 0 | 2019-04-29 | 6.9 | 11.1 | 0 | 2018-04-29 | 5.7 | 12.3 | 0 | 2017-04-29 | 6.4 | 11.6 | 0 | 2016-04-29 | 8 | 10 | 0 | 8 | 0.09
2025-04-29 | 17.8 | 0.2 | 0 | 2024-04-29 | 10.6 | 7.4 | 0 | 2023-04-29 | 8.1 | 9.9 | 0 | 2022-04-29 | 8.1 | 9.9 | 0 | 2021-04-29 | 12.6 | 5.4 | 0 | 2020-04-29 | 12.8 | 5.2 | 0 | 2019-04-29 | 6.2 | 11.8 | 0 | 2018-04-29 | 7.4 | 10.6 | 0 | 2017-04-29 | 5.8 | 12.2 | 0 | 2016-04-29 | 7.4 | 10.6 | 0 | 8.32 | 0
2025-04-29 | 15.6 | 2.4 | 0 | 2024-04-29 | 10.7 | 7.3 | 0 | 2023-04-29 | 8 | 10 | 0 | 2022-04-29 | 7.1 | 10.9 | 0 | 2021-04-29 | 12.2 | 5.8 | 0 | 2020-04-29 | 12.5 | 5.5 | 0 | 2019-04-29 | 5.7 | 12.3 | 0 | 2018-04-29 | 7.6 | 10.4 | 0 | 2017-04-29 | 5.1 | 12.9 | 0 | 2016-04-29 | 7.3 | 10.7 | 0 | 8.82 | 0
2025-04-29 | 8.9 | 9.1 | 0 | 2024-04-29 | 8.3 | 9.7 | 0 | 2023-04-29 | 7.8 | 10.2 | 0 | 2022-04-29 | 4.9 | 13.1 | 0 | 2021-04-29 | 11.1 | 6.9 | 0 | 2020-04-29 | 12.2 | 5.8 | 0 | 2019-04-29 | 4.8 | 13.2 | 0 | 2018-04-29 | 7.8 | 10.2 | 0 | 2017-04-29 | 4.7 | 13.3 | 0 | 2016-04-29 | 3.3 | 14.7 | 0 | 10.62 | 0
2025-04-30 | 5 | 13 | 0 | 2024-04-30 | 8.2 | 9.8 | 0 | 2023-04-30 | 7.6 | 10.4 | 0 | 2022-04-30 | 4.3 | 13.7 | 0 | 2021-04-30 | 10.7 | 7.3 | 0 | 2020-04-30 | 12 | 6 | 0 | 2019-04-30 | 5.1 | 12.9 | 0 | 2018-04-30 | 7.3 | 10.7 | 0 | 2017-04-30 | 4.1 | 13.9 | 0 | 2016-04-30 | 3.3 | 14.7 | 0 | 11.24 | 0
2025-04-30 | 3 | 15 | 0 | 2024-04-30 | 6.9 | 11.1 | 0 | 2023-04-30 | 7.5 | 10.5 | 0 | 2022-04-30 | 2 | 16 | 0 | 2021-04-30 | 10.1 | 7.9 | 0 | 2020-04-30 | 12.2 | 5.8 | 0 | 2019-04-30 | 5.1 | 12.9 | 0 | 2018-04-30 | 6 | 12 | 0 | 2017-04-30 | 3.6 | 14.4 | 0 | 2016-04-30 | 2.1 | 15.9 | 0 | 12.15 | 0
2025-04-30 | 1.2 | 16.8 | 0 | 2024-04-30 | 6.9 | 11.1 | 0 | 2023-04-30 | 7.3 | 10.7 | 0 | 2022-04-30 | 1.5 | 16.5 | 0 | 2021-04-30 | 9.8 | 8.2 | 0 | 2020-04-30 | 12.1 | 5.9 | 0 | 2019-04-30 | 5 | 13 | 0 | 2018-04-30 | 5.4 | 12.6 | 0 | 2017-04-30 | 3.5 | 14.5 | 0 | 2016-04-30 | 0.6 | 17.4 | 0 | 12.67 | 0
2025-04-30 | 0.2 | 17.8 | 0 | 2024-04-30 | 6.6 | 11.4 | 0 | 2023-04-30 | 7.4 | 10.6 | 0 | 2022-04-30 | 1.5 | 16.5 | 0 | 2021-04-30 | 10 | 8 | 0 | 2020-04-30 | 12.1 | 5.9 | 0 | 2019-04-30 | 5 | 13 | 0 | 2018-04-30 | 5.4 | 12.6 | 0 | 2017-04-30 | 3.1 | 14.9 | 0 | 2016-04-30 | 0.3 | 17.7 | 0 | 12.84 | 0
2025-04-30 | 0 | 18 | 0 | 2024-04-30 | 6.5 | 11.5 | 0 | 2023-04-30 | 7.1 | 10.9 | 0 | 2022-04-30 | 0.3 | 17.7 | 0 | 2021-04-30 | 9.8 | 8.2 | 0 | 2020-04-30 | 11.7 | 6.3 | 0 | 2019-04-30 | 4.3 | 13.7 | 0 | 2018-04-30 | 5.4 | 12.6 | 0 | 2017-04-30 | 2.9 | 15.1 | 0 | 2016-04-30 | 0.4 | 17.6 | 0 | 13.16 | 0
2025-04-30 | 0 | 18 | 0 | 2024-04-30 | 6.6 | 11.4 | 0 | 2023-04-30 | 7.2 | 10.8 | 0 | 2022-04-30 | 2 | 16 | 0 | 2021-04-30 | 9.6 | 8.4 | 0 | 2020-04-30 | 10 | 8 | 0 | 2019-04-30 | 4.5 | 13.5 | 0 | 2018-04-30 | 5.4 | 12.6 | 0 | 2017-04-30 | 2.8 | 15.2 | 0 | 2016-04-30 | 0.2 | 17.8 | 0 | 13.17 | 0
2025-04-30 | -0.6 | 18.6 | 0 | 2024-04-30 | 6.4 | 11.6 | 0 | 2023-04-30 | 7.1 | 10.9 | 0 | 2022-04-30 | 3.4 | 14.6 | 0 | 2021-04-30 | 9.7 | 8.3 | 0 | 2020-04-30 | 9.6 | 8.4 | 0 | 2019-04-30 | 4.7 | 13.3 | 0 | 2018-04-30 | 6.3 | 11.7 | 0 | 2017-04-30 | 2.7 | 15.3 | 0 | 2016-04-30 | 3.2 | 14.8 | 0 | 12.75 | 0
2025-04-30 | 0 | 18 | 0 | 2024-04-30 | 6.7 | 11.3 | 0 | 2023-04-30 | 7.7 | 10.3 | 0 | 2022-04-30 | 5.4 | 12.6 | 0 | 2021-04-30 | 9.9 | 8.1 | 0 | 2020-04-30 | 9.8 | 8.2 | 0 | 2019-04-30 | 5.3 | 12.7 | 0 | 2018-04-30 | 7.3 | 10.7 | 0 | 2017-04-30 | 3.1 | 14.9 | 0 | 2016-04-30 | 5.3 | 12.7 | 0 | 11.95 | 0
2025-04-30 | 0.9 | 17.1 | 0 | 2024-04-30 | 7 | 11 | 0 | 2023-04-30 | 9.3 | 8.7 | 0 | 2022-04-30 | 7.1 | 10.9 | 0 | 2021-04-30 | 10.1 | 7.9 | 0 | 2020-04-30 | 10.6 | 7.4 | 0 | 2019-04-30 | 6.1 | 11.9 | 0 | 2018-04-30 | 9.5 | 8.5 | 0 | 2017-04-30 | 2.8 | 15.2 | 0 | 2016-04-30 | 7.5 | 10.5 | 0 | 10.91 | 0
2025-04-30 | 1.8 | 16.2 | 0 | 2024-04-30 | 7.7 | 10.3 | 0 | 2023-04-30 | 9.9 | 8.1 | 0 | 2022-04-30 | 9.3 | 8.7 | 0 | 2021-04-30 | 10.3 | 7.7 | 0 | 2020-04-30 | 10.7 | 7.3 | 0 | 2019-04-30 | 7.8 | 10.2 | 0 | 2018-04-30 | 11.9 | 6.1 | 0 | 2017-04-30 | 2.8 | 15.2 | 0 | 2016-04-30 | 9.5 | 8.5 | 0 | 9.83 | 0
2025-04-30 | 2.9 | 15.1 | 0 | 2024-04-30 | 7.5 | 10.5 | 0 | 2023-04-30 | 10.9 | 7.1 | 0 | 2022-04-30 | 11.1 | 6.9 | 0 | 2021-04-30 | 10.4 | 7.6 | 0 | 2020-04-30 | 11.5 | 6.5 | 0 | 2019-04-30 | 9.1 | 8.9 | 0 | 2018-04-30 | 13.6 | 4.4 | 0 | 2017-04-30 | 3.2 | 14.8 | 0 | 2016-04-30 | 10.8 | 7.2 | 0 | 8.9 | 0
2025-04-30 | 3.1 | 14.9 | 0 | 2024-04-30 | 6.5 | 11.5 | 0 | 2023-04-30 | 11.3 | 6.7 | 0 | 2022-04-30 | 11.8 | 6.2 | 0 | 2021-04-30 | 10.1 | 7.9 | 0 | 2020-04-30 | 11.8 | 6.2 | 0 | 2019-04-30 | 9.6 | 8.4 | 0 | 2018-04-30 | 16.2 | 1.8 | 0 | 2017-04-30 | 3.1 | 14.9 | 0 | 2016-04-30 | 12.6 | 5.4 | 0 | 8.39 | 0
2025-04-30 | 4.8 | 13.2 | 0 | 2024-04-30 | 6.5 | 11.5 | 0 | 2023-04-30 | 11.7 | 6.3 | 0 | 2022-04-30 | 13.4 | 4.6 | 0 | 2021-04-30 | 9.7 | 8.3 | 0 | 2020-04-30 | 12.4 | 5.6 | 0 | 2019-04-30 | 11.5 | 6.5 | 0 | 2018-04-30 | 17.9 | 0.1 | 0 | 2017-04-30 | 3 | 15 | 0 | 2016-04-30 | 13.2 | 4.8 | 0 | 7.59 | 0
2025-04-30 | 6.3 | 11.7 | 0 | 2024-04-30 | 7.2 | 10.8 | 0 | 2023-04-30 | 12.2 | 5.8 | 0 | 2022-04-30 | 13.8 | 4.2 | 0 | 2021-04-30 | 6.7 | 11.3 | 0 | 2020-04-30 | 12.7 | 5.3 | 0 | 2019-04-30 | 12.3 | 5.7 | 0 | 2018-04-30 | 17.6 | 0.4 | 0 | 2017-04-30 | 3.1 | 14.9 | 0 | 2016-04-30 | 14.4 | 3.6 | 0 | 7.37 | 0
2025-04-30 | 8 | 10 | 0 | 2024-04-30 | 7.5 | 10.5 | 0 | 2023-04-30 | 12.1 | 5.9 | 0 | 2022-04-30 | 14.4 | 3.6 | 0 | 2021-04-30 | 2.9 | 15.1 | 0 | 2020-04-30 | 12.3 | 5.7 | 0 | 2019-04-30 | 12.5 | 5.5 | 0 | 2018-04-30 | 12.6 | 5.4 | 0 | 2017-04-30 | 2.8 | 15.2 | 0 | 2016-04-30 | 15 | 3 | 0 | 7.99 | 0
2025-04-30 | 8.8 | 9.2 | 0 | 2024-04-30 | 7.2 | 10.8 | 0 | 2023-04-30 | 11 | 7 | 0 | 2022-04-30 | 15.6 | 2.4 | 0 | 2021-04-30 | 1.8 | 16.2 | 0 | 2020-04-30 | 12.6 | 5.4 | 0 | 2019-04-30 | 13.4 | 4.6 | 0 | 2018-04-30 | 12.8 | 5.2 | 0 | 2017-04-30 | 3.1 | 14.9 | 0 | 2016-04-30 | 15.4 | 2.6 | 0 | 7.83 | 0
2025-04-30 | 9.4 | 8.6 | 0 | 2024-04-30 | 7 | 11 | 0 | 2023-04-30 | 10.6 | 7.4 | 0 | 2022-04-30 | 16 | 2 | 0 | 2021-04-30 | 0.9 | 17.1 | 0 | 2020-04-30 | 12.3 | 5.7 | 0 | 2019-04-30 | 13.4 | 4.6 | 0 | 2018-04-30 | 12.1 | 5.9 | 0 | 2017-04-30 | 3.3 | 14.7 | 0 | 2016-04-30 | 15.8 | 2.2 | 0 | 7.92 | 0
2025-04-30 | 9.2 | 8.8 | 0 | 2024-04-30 | 7 | 11 | 0 | 2023-04-30 | 10.5 | 7.5 | 0 | 2022-04-30 | 15.7 | 2.3 | 0 | 2021-04-30 | 0.4 | 17.6 | 0 | 2020-04-30 | 11.7 | 6.3 | 0 | 2019-04-30 | 12.9 | 5.1 | 0 | 2018-04-30 | 10.5 | 7.5 | 0 | 2017-04-30 | 3.5 | 14.5 | 0 | 2016-04-30 | 15.8 | 2.2 | 0 | 8.28 | 0
2025-04-30 | 8.8 | 9.2 | 0 | 2024-04-30 | 6.4 | 11.6 | 0 | 2023-04-30 | 10.2 | 7.8 | 0 | 2022-04-30 | 14.9 | 3.1 | 0 | 2021-04-30 | 0.4 | 17.6 | 0 | 2020-04-30 | 10.9 | 7.1 | 0 | 2019-04-30 | 12.2 | 5.8 | 0 | 2018-04-30 | 10 | 8 | 0 | 2017-04-30 | 3.4 | 14.6 | 0 | 2016-04-30 | 14.6 | 3.4 | 0 | 8.82 | 0
2025-04-30 | 7.5 | 10.5 | 0 | 2024-04-30 | 5.8 | 12.2 | 0 | 2023-04-30 | 10.3 | 7.7 | 0 | 2022-04-30 | 13.3 | 4.7 | 0 | 2021-04-30 | 1 | 17 | 0 | 2020-04-30 | 9.8 | 8.2 | 0 | 2019-04-30 | 11 | 7 | 0 | 2018-04-30 | 9.1 | 8.9 | 0 | 2017-04-30 | 3.8 | 14.2 | 0 | 2016-04-30 | 12.3 | 5.7 | 0 | 9.61 | 0
2025-04-30 | 6.9 | 11.1 | 0 | 2024-04-30 | 5.7 | 12.3 | 0 | 2023-04-30 | 9.6 | 8.4 | 0 | 2022-04-30 | 11.9 | 6.1 | 0 | 2021-04-30 | 1.7 | 16.3 | 0 | 2020-04-30 | 9.6 | 8.4 | 0 | 2019-04-30 | 9.8 | 8.2 | 0 | 2018-04-30 | 7.5 | 10.5 | 0 | 2017-04-30 | 3.5 | 14.5 | 0 | 2016-04-30 | 10.8 | 7.2 | 0 | 10.3 | 0
2025-04-30 | 5.4 | 12.6 | 0 | 2024-04-30 | 5.6 | 12.4 | 0 | 2023-04-30 | 9 | 9 | 0 | 2022-04-30 | 9.2 | 8.8 | 0 | 2021-04-30 | 2.7 | 15.3 | 0 | 2020-04-30 | 10 | 8 | 0 | 2019-04-30 | 8.9 | 9.1 | 0 | 2018-04-30 | 6.4 | 11.6 | 0 | 2017-04-30 | 3.6 | 14.4 | 0 | 2016-04-30 | 9.6 | 8.4 | 0 | 10.96 | 0
2025-04-30 | 3.8 | 14.2 | 0 | 2024-04-30 | 5.7 | 12.3 | 0 | 2023-04-30 | 8.7 | 9.3 | 0 | 2022-04-30 | 6.4 | 11.6 | 0 | 2021-04-30 | 2.5 | 15.5 | 0 | 2020-04-30 | 10 | 8 | 0 | 2019-04-30 | 8.7 | 9.3 | 0 | 2018-04-30 | 5.5 | 12.5 | 0 | 2017-04-30 | 3.5 | 14.5 | 0 | 2016-04-30 | 8.2 | 9.8 | 0 | 11.7 | 0
2025-04-30 | 3.8 | 14.2 | 0 | 2024-04-30 | 5.8 | 12.2 | 0 | 2023-04-30 | 8.4 | 9.6 | 0 | 2022-04-30 | 7.8 | 10.2 | 0 | 2021-04-30 | 2.5 | 15.5 | 0 | 2020-04-30 | 10 | 8 | 0 | 2019-04-30 | 8.1 | 9.9 | 0 | 2018-04-30 | 6 | 12 | 0 | 2017-04-30 | 3.6 | 14.4 | 0 | 2016-04-30 | 8.2 | 9.8 | 0 | 11.58 | 0
2025-05-01 | 1.6 | 16.4 | 0 | 2024-05-01 | 5.7 | 12.3 | 0 | 2023-05-01 | 8.3 | 9.7 | 0 | 2022-05-01 | 7 | 11 | 0 | 2021-05-01 | 2.2 | 15.8 | 0 | 2020-05-01 | 10.1 | 7.9 | 0 | 2019-05-01 | 7.6 | 10.4 | 0 | 2018-05-01 | 3.4 | 14.6 | 0 | 2017-05-01 | 3.7 | 14.3 | 0 | 2016-05-01 | 6.3 | 11.7 | 0 | 12.41 | 0
2025-05-01 | 1.5 | 16.5 | 0 | 2024-05-01 | 5.6 | 12.4 | 0 | 2023-05-01 | 8.4 | 9.6 | 0 | 2022-05-01 | 5.8 | 12.2 | 0 | 2021-05-01 | 1.8 | 16.2 | 0 | 2020-05-01 | 10.3 | 7.7 | 0 | 2019-05-01 | 7.1 | 10.9 | 0 | 2018-05-01 | 6 | 12 | 0 | 2017-05-01 | 3.8 | 14.2 | 0 | 2016-05-01 | 5.9 | 12.1 | 0 | 12.38 | 0
2025-05-01 | 0.9 | 17.1 | 0 | 2024-05-01 | 5.5 | 12.5 | 0 | 2023-05-01 | 8.2 | 9.8 | 0 | 2022-05-01 | 4.7 | 13.3 | 0 | 2021-05-01 | 0.9 | 17.1 | 0 | 2020-05-01 | 10.3 | 7.7 | 0 | 2019-05-01 | 5.7 | 12.3 | 0 | 2018-05-01 | 4.3 | 13.7 | 0 | 2017-05-01 | 4 | 14 | 0 | 2016-05-01 | 6.5 | 11.5 | 0 | 12.9 | 0
2025-05-01 | 1.1 | 16.9 | 0 | 2024-05-01 | 5.6 | 12.4 | 0 | 2023-05-01 | 8.2 | 9.8 | 0 | 2022-05-01 | 2.8 | 15.2 | 0 | 2021-05-01 | 0.2 | 17.8 | 0 | 2020-05-01 | 10.6 | 7.4 | 0 | 2019-05-01 | 4.8 | 13.2 | 0 | 2018-05-01 | 2.8 | 15.2 | 0 | 2017-05-01 | 4.2 | 13.8 | 0 | 2016-05-01 | 7.3 | 10.7 | 0 | 13.24 | 0
2025-05-01 | -0.5 | 18.5 | 0 | 2024-05-01 | 5.6 | 12.4 | 0 | 2023-05-01 | 8.2 | 9.8 | 0 | 2022-05-01 | 2.3 | 15.7 | 0 | 2021-05-01 | -0.5 | 18.5 | 0 | 2020-05-01 | 10.3 | 7.7 | 0 | 2019-05-01 | 4.5 | 13.5 | 0 | 2018-05-01 | 3.1 | 14.9 | 0 | 2017-05-01 | 4.5 | 13.5 | 0 | 2016-05-01 | 7.3 | 10.7 | 0 | 13.52 | 0
2025-05-01 | -0.8 | 18.8 | 0 | 2024-05-01 | 5.7 | 12.3 | 0 | 2023-05-01 | 8.4 | 9.6 | 0 | 2022-05-01 | 2.2 | 15.8 | 0 | 2021-05-01 | -0.8 | 18.8 | 0 | 2020-05-01 | 9.9 | 8.1 | 0 | 2019-05-01 | 3.7 | 14.3 | 0 | 2018-05-01 | 1.3 | 16.7 | 0 | 2017-05-01 | 4.7 | 13.3 | 0 | 2016-05-01 | 7.2 | 10.8 | 0 | 13.85 | 0
2025-05-01 | 1.6 | 16.4 | 0 | 2024-05-01 | 5.8 | 12.2 | 0 | 2023-05-01 | 8.4 | 9.6 | 0 | 2022-05-01 | 5.2 | 12.8 | 0 | 2021-05-01 | -0.6 | 18.6 | 0 | 2020-05-01 | 9.8 | 8.2 | 0 | 2019-05-01 | 4 | 14 | 0 | 2018-05-01 | 4.3 | 13.7 | 0 | 2017-05-01 | 4.9 | 13.1 | 0 | 2016-05-01 | 7.3 | 10.7 | 0 | 12.93 | 0
2025-05-01 | 5.1 | 12.9 | 0 | 2024-05-01 | 6.5 | 11.5 | 0 | 2023-05-01 | 8.5 | 9.5 | 0 | 2022-05-01 | 8.5 | 9.5 | 0 | 2021-05-01 | 0.3 | 17.7 | 0 | 2020-05-01 | 10.4 | 7.6 | 0 | 2019-05-01 | 4.3 | 13.7 | 0 | 2018-05-01 | 6.7 | 11.3 | 0 | 2017-05-01 | 5.3 | 12.7 | 0 | 2016-05-01 | 7.9 | 10.1 | 0 | 11.65 | 0
2025-05-01 | 8 | 10 | 0 | 2024-05-01 | 7.1 | 10.9 | 0 | 2023-05-01 | 9 | 9 | 0 | 2022-05-01 | 10.9 | 7.1 | 0 | 2021-05-01 | 1.4 | 16.6 | 0 | 2020-05-01 | 10.8 | 7.2 | 0 | 2019-05-01 | 4.3 | 13.7 | 0 | 2018-05-01 | 7.5 | 10.5 | 0 | 2017-05-01 | 5.6 | 12.4 | 0 | 2016-05-01 | 8.6 | 9.4 | 0 | 10.68 | 0
2025-05-01 | 10.2 | 7.8 | 0 | 2024-05-01 | 7.6 | 10.4 | 0 | 2023-05-01 | 8 | 10 | 0 | 2022-05-01 | 13.5 | 4.5 | 0 | 2021-05-01 | 2.5 | 15.5 | 0 | 2020-05-01 | 12.9 | 5.1 | 0 | 2019-05-01 | 5 | 13 | 0 | 2018-05-01 | 9.4 | 8.6 | 0 | 2017-05-01 | 6.2 | 11.8 | 0 | 2016-05-01 | 9.5 | 8.5 | 0 | 9.52 | 0
2025-05-01 | 12.3 | 5.7 | 0 | 2024-05-01 | 8.3 | 9.7 | 0 | 2023-05-01 | 7.2 | 10.8 | 0 | 2022-05-01 | 15.3 | 2.7 | 0 | 2021-05-01 | 3.3 | 14.7 | 0 | 2020-05-01 | 12.8 | 5.2 | 0 | 2019-05-01 | 5.3 | 12.7 | 0 | 2018-05-01 | 13.4 | 4.6 | 0 | 2017-05-01 | 6.5 | 11.5 | 0 | 2016-05-01 | 6.4 | 11.6 | 0 | 8.92 | 0
2025-05-01 | 13.7 | 4.3 | 0 | 2024-05-01 | 9.6 | 8.4 | 0 | 2023-05-01 | 6.6 | 11.4 | 0 | 2022-05-01 | 15.9 | 2.1 | 0 | 2021-05-01 | 4.8 | 13.2 | 0 | 2020-05-01 | 10.9 | 7.1 | 0 | 2019-05-01 | 5.2 | 12.8 | 0 | 2018-05-01 | 15.1 | 2.9 | 0 | 2017-05-01 | 7 | 11 | 0 | 2016-05-01 | 6.2 | 11.8 | 0 | 8.5 | 0
2025-05-01 | 15.9 | 2.1 | 0 | 2024-05-01 | 11.1 | 6.9 | 0 | 2023-05-01 | 6.3 | 11.7 | 0 | 2022-05-01 | 17.2 | 0.8 | 0 | 2021-05-01 | 6.1 | 11.9 | 0 | 2020-05-01 | 11.6 | 6.4 | 0 | 2019-05-01 | 3.3 | 14.7 | 0 | 2018-05-01 | 16.1 | 1.9 | 0 | 2017-05-01 | 7.3 | 10.7 | 0 | 2016-05-01 | 7 | 11 | 0 | 7.81 | 0
2025-05-01 | 15.6 | 2.4 | 0 | 2024-05-01 | 12.9 | 5.1 | 0 | 2023-05-01 | 6.3 | 11.7 | 0 | 2022-05-01 | 17.8 | 0.2 | 0 | 2021-05-01 | 7.9 | 10.1 | 0 | 2020-05-01 | 11.1 | 6.9 | 0 | 2019-05-01 | 2.5 | 15.5 | 0 | 2018-05-01 | 17 | 1 | 0 | 2017-05-01 | 7.6 | 10.4 | 0 | 2016-05-01 | 7.6 | 10.4 | 0 | 7.37 | 0
2025-05-01 | 15.2 | 2.8 | 0 | 2024-05-01 | 13.7 | 4.3 | 0 | 2023-05-01 | 8.1 | 9.9 | 0 | 2022-05-01 | 18.6 | 0 | 0.6 | 2021-05-01 | 8.7 | 9.3 | 0 | 2020-05-01 | 11.2 | 6.8 | 0 | 2019-05-01 | 2.8 | 15.2 | 0 | 2018-05-01 | 18.6 | 0 | 0.6 | 2017-05-01 | 7.8 | 10.2 | 0 | 2016-05-01 | 6.7 | 11.3 | 0 | 6.98 | 0.12
2025-05-01 | 15.2 | 2.8 | 0 | 2024-05-01 | 14.8 | 3.2 | 0 | 2023-05-01 | 8.4 | 9.6 | 0 | 2022-05-01 | 18.8 | 0 | 0.8 | 2021-05-01 | 10.2 | 7.8 | 0 | 2020-05-01 | 12.7 | 5.3 | 0 | 2019-05-01 | 3.7 | 14.3 | 0 | 2018-05-01 | 18.5 | 0 | 0.5 | 2017-05-01 | 7.9 | 10.1 | 0 | 2016-05-01 | 6.4 | 11.6 | 0 | 6.47 | 0.13
2025-05-01 | 14.8 | 3.2 | 0 | 2024-05-01 | 14.4 | 3.6 | 0 | 2023-05-01 | 11.4 | 6.6 | 0 | 2022-05-01 | 19.2 | 0 | 1.2 | 2021-05-01 | 11.2 | 6.8 | 0 | 2020-05-01 | 13.8 | 4.2 | 0 | 2019-05-01 | 4.5 | 13.5 | 0 | 2018-05-01 | 18.9 | 0 | 0.9 | 2017-05-01 | 8.1 | 9.9 | 0 | 2016-05-01 | 6.4 | 11.6 | 0 | 5.94 | 0.21
2025-05-01 | 13 | 5 | 0 | 2024-05-01 | 14.7 | 3.3 | 0 | 2023-05-01 | 10.3 | 7.7 | 0 | 2022-05-01 | 18.6 | 0 | 0.6 | 2021-05-01 | 10 | 8 | 0 | 2020-05-01 | 14.2 | 3.8 | 0 | 2019-05-01 | 4.6 | 13.4 | 0 | 2018-05-01 | 18.3 | 0 | 0.3 | 2017-05-01 | 8.2 | 9.8 | 0 | 2016-05-01 | 6.2 | 11.8 | 0 | 6.28 | 0.09
2025-05-01 | 13.3 | 4.7 | 0 | 2024-05-01 | 14.5 | 3.5 | 0 | 2023-05-01 | 9.2 | 8.8 | 0 | 2022-05-01 | 17.5 | 0.5 | 0 | 2021-05-01 | 7.3 | 10.7 | 0 | 2020-05-01 | 13.4 | 4.6 | 0 | 2019-05-01 | 2.3 | 15.7 | 0 | 2018-05-01 | 18.2 | 0 | 0.2 | 2017-05-01 | 8.2 | 9.8 | 0 | 2016-05-01 | 6 | 12 | 0 | 7.03 | 0.02
2025-05-01 | 11.5 | 6.5 | 0 | 2024-05-01 | 13.5 | 4.5 | 0 | 2023-05-01 | 8.3 | 9.7 | 0 | 2022-05-01 | 15.8 | 2.2 | 0 | 2021-05-01 | 6.7 | 11.3 | 0 | 2020-05-01 | 12.1 | 5.9 | 0 | 2019-05-01 | 1.5 | 16.5 | 0 | 2018-05-01 | 16.6 | 1.4 | 0 | 2017-05-01 | 7.9 | 10.1 | 0 | 2016-05-01 | 6.2 | 11.8 | 0 | 7.99 | 0
2025-05-01 | 9.6 | 8.4 | 0 | 2024-05-01 | 12.8 | 5.2 | 0 | 2023-05-01 | 6.7 | 11.3 | 0 | 2022-05-01 | 14.6 | 3.4 | 0 | 2021-05-01 | 4.8 | 13.2 | 0 | 2020-05-01 | 10.7 | 7.3 | 0 | 2019-05-01 | 1.1 | 16.9 | 0 | 2018-05-01 | 16.6 | 1.4 | 0 | 2017-05-01 | 8.1 | 9.9 | 0 | 2016-05-01 | 6 | 12 | 0 | 8.9 | 0
2025-05-01 | 8.7 | 9.3 | 0 | 2024-05-01 | 11.7 | 6.3 | 0 | 2023-05-01 | 6.3 | 11.7 | 0 | 2022-05-01 | 13.6 | 4.4 | 0 | 2021-05-01 | 4.7 | 13.3 | 0 | 2020-05-01 | 9.8 | 8.2 | 0 | 2019-05-01 | 1.1 | 16.9 | 0 | 2018-05-01 | 15.8 | 2.2 | 0 | 2017-05-01 | 9 | 9 | 0 | 2016-05-01 | 5.9 | 12.1 | 0 | 9.34 | 0
2025-05-01 | 8.2 | 9.8 | 0 | 2024-05-01 | 11 | 7 | 0 | 2023-05-01 | 5.9 | 12.1 | 0 | 2022-05-01 | 12.8 | 5.2 | 0 | 2021-05-01 | 4.3 | 13.7 | 0 | 2020-05-01 | 7 | 11 | 0 | 2019-05-01 | 1.2 | 16.8 | 0 | 2018-05-01 | 14.6 | 3.4 | 0 | 2017-05-01 | 9.6 | 8.4 | 0 | 2016-05-01 | 5.9 | 12.1 | 0 | 9.95 | 0
2025-05-01 | 8.4 | 9.6 | 0 | 2024-05-01 | 11.3 | 6.7 | 0 | 2023-05-01 | 5.5 | 12.5 | 0 | 2022-05-01 | 11.8 | 6.2 | 0 | 2021-05-01 | 3.7 | 14.3 | 0 | 2020-05-01 | 5.7 | 12.3 | 0 | 2019-05-01 | 1.4 | 16.6 | 0 | 2018-05-01 | 14 | 4 | 0 | 2017-05-01 | 10.1 | 7.9 | 0 | 2016-05-01 | 5.9 | 12.1 | 0 | 10.22 | 0
2025-05-02 | 8.3 | 9.7 | 0 | 2024-05-02 | 11 | 7 | 0 | 2023-05-02 | 4.3 | 13.7 | 0 | 2022-05-02 | 11.7 | 6.3 | 0 | 2021-05-02 | 3.6 | 14.4 | 0 | 2020-05-02 | 5.4 | 12.6 | 0 | 2019-05-02 | 1.7 | 16.3 | 0 | 2018-05-02 | 12.3 | 5.7 | 0 | 2017-05-02 | 9.9 | 8.1 | 0 | 2016-05-02 | 6.1 | 11.9 | 0 | 10.57 | 0
2025-05-02 | 8.1 | 9.9 | 0 | 2024-05-02 | 11.1 | 6.9 | 0 | 2023-05-02 | 3.5 | 14.5 | 0 | 2022-05-02 | 11.3 | 6.7 | 0 | 2021-05-02 | 3.7 | 14.3 | 0 | 2020-05-02 | 4.3 | 13.7 | 0 | 2019-05-02 | 1.8 | 16.2 | 0 | 2018-05-02 | 14.2 | 3.8 | 0 | 2017-05-02 | 10.4 | 7.6 | 0 | 2016-05-02 | 6.1 | 11.9 | 0 | 10.55 | 0
2025-05-02 | 8.3 | 9.7 | 0 | 2024-05-02 | 10.8 | 7.2 | 0 | 2023-05-02 | 4.6 | 13.4 | 0 | 2022-05-02 | 10.1 | 7.9 | 0 | 2021-05-02 | 4 | 14 | 0 | 2020-05-02 | 5.4 | 12.6 | 0 | 2019-05-02 | 1.9 | 16.1 | 0 | 2018-05-02 | 13.7 | 4.3 | 0 | 2017-05-02 | 11.9 | 6.1 | 0 | 2016-05-02 | 6.1 | 11.9 | 0 | 10.32 | 0
2025-05-02 | 8 | 10 | 0 | 2024-05-02 | 9.2 | 8.8 | 0 | 2023-05-02 | 5 | 13 | 0 | 2022-05-02 | 9.4 | 8.6 | 0 | 2021-05-02 | 3.9 | 14.1 | 0 | 2020-05-02 | 4.9 | 13.1 | 0 | 2019-05-02 | 2.1 | 15.9 | 0 | 2018-05-02 | 13 | 5 | 0 | 2017-05-02 | 12.4 | 5.6 | 0 | 2016-05-02 | 6.1 | 11.9 | 0 | 10.6 | 0
2025-05-02 | 8.3 | 9.7 | 0 | 2024-05-02 | 7.9 | 10.1 | 0 | 2023-05-02 | 5.2 | 12.8 | 0 | 2022-05-02 | 8.9 | 9.1 | 0 | 2021-05-02 | 2.7 | 15.3 | 0 | 2020-05-02 | 4.6 | 13.4 | 0 | 2019-05-02 | 2.4 | 15.6 | 0 | 2018-05-02 | 13.8 | 4.2 | 0 | 2017-05-02 | 11.4 | 6.6 | 0 | 2016-05-02 | 6.3 | 11.7 | 0 | 10.85 | 0
2025-05-02 | 8.6 | 9.4 | 0 | 2024-05-02 | 7.5 | 10.5 | 0 | 2023-05-02 | 4.7 | 13.3 | 0 | 2022-05-02 | 8.4 | 9.6 | 0 | 2021-05-02 | 1.9 | 16.1 | 0 | 2020-05-02 | 3.2 | 14.8 | 0 | 2019-05-02 | 2.5 | 15.5 | 0 | 2018-05-02 | 13.7 | 4.3 | 0 | 2017-05-02 | 10.4 | 7.6 | 0 | 2016-05-02 | 6.5 | 11.5 | 0 | 11.26 | 0
2025-05-02 | 9.5 | 8.5 | 0 | 2024-05-02 | 8.2 | 9.8 | 0 | 2023-05-02 | 5.6 | 12.4 | 0 | 2022-05-02 | 7.7 | 10.3 | 0 | 2021-05-02 | 2.5 | 15.5 | 0 | 2020-05-02 | 5.2 | 12.8 | 0 | 2019-05-02 | 2.9 | 15.1 | 0 | 2018-05-02 | 14.1 | 3.9 | 0 | 2017-05-02 | 10.7 | 7.3 | 0 | 2016-05-02 | 6.6 | 11.4 | 0 | 10.7 | 0
2025-05-02 | 11.3 | 6.7 | 0 | 2024-05-02 | 10.3 | 7.7 | 0 | 2023-05-02 | 6.4 | 11.6 | 0 | 2022-05-02 | 7.2 | 10.8 | 0 | 2021-05-02 | 4.6 | 13.4 | 0 | 2020-05-02 | 8.7 | 9.3 | 0 | 2019-05-02 | 3.2 | 14.8 | 0 | 2018-05-02 | 15.9 | 2.1 | 0 | 2017-05-02 | 11.5 | 6.5 | 0 | 2016-05-02 | 6.8 | 11.2 | 0 | 9.41 | 0
2025-05-02 | 14 | 4 | 0 | 2024-05-02 | 12.8 | 5.2 | 0 | 2023-05-02 | 6.6 | 11.4 | 0 | 2022-05-02 | 7.6 | 10.4 | 0 | 2021-05-02 | 6 | 12 | 0 | 2020-05-02 | 12.1 | 5.9 | 0 | 2019-05-02 | 3.8 | 14.2 | 0 | 2018-05-02 | 18.1 | 0 | 0.1 | 2017-05-02 | 12.4 | 5.6 | 0 | 2016-05-02 | 7.1 | 10.9 | 0 | 7.96 | 0.01
2025-05-02 | 15.7 | 2.3 | 0 | 2024-05-02 | 11.9 | 6.1 | 0 | 2023-05-02 | 7.8 | 10.2 | 0 | 2022-05-02 | 8.9 | 9.1 | 0 | 2021-05-02 | 7.6 | 10.4 | 0 | 2020-05-02 | 13.5 | 4.5 | 0 | 2019-05-02 | 4.3 | 13.7 | 0 | 2018-05-02 | 21.6 | 0 | 3.6 | 2017-05-02 | 13.3 | 4.7 | 0 | 2016-05-02 | 8 | 10 | 0 | 7.1 | 0.36
2025-05-02 | 16.3 | 1.7 | 0 | 2024-05-02 | 13.2 | 4.8 | 0 | 2023-05-02 | 8.3 | 9.7 | 0 | 2022-05-02 | 11.6 | 6.4 | 0 | 2021-05-02 | 8.6 | 9.4 | 0 | 2020-05-02 | 14.8 | 3.2 | 0 | 2019-05-02 | 4.5 | 13.5 | 0 | 2018-05-02 | 25 | 0 | 7 | 2017-05-02 | 14.1 | 3.9 | 0 | 2016-05-02 | 8.6 | 9.4 | 0 | 6.2 | 0.7
2025-05-02 | 16.9 | 1.1 | 0 | 2024-05-02 | 13.1 | 4.9 | 0 | 2023-05-02 | 9.4 | 8.6 | 0 | 2022-05-02 | 12.5 | 5.5 | 0 | 2021-05-02 | 9.3 | 8.7 | 0 | 2020-05-02 | 16.2 | 1.8 | 0 | 2019-05-02 | 5 | 13 | 0 | 2018-05-02 | 27 | 0 | 9 | 2017-05-02 | 14.9 | 3.1 | 0 | 2016-05-02 | 8 | 10 | 0 | 5.67 | 0.9
2025-05-02 | 18.2 | 0 | 0.2 | 2024-05-02 | 14.6 | 3.4 | 0 | 2023-05-02 | 9.1 | 8.9 | 0 | 2022-05-02 | 14.3 | 3.7 | 0 | 2021-05-02 | 10.9 | 7.1 | 0 | 2020-05-02 | 17 | 1 | 0 | 2019-05-02 | 6.2 | 11.8 | 0 | 2018-05-02 | 25.6 | 0 | 7.6 | 2017-05-02 | 13.9 | 4.1 | 0 | 2016-05-02 | 8.7 | 9.3 | 0 | 4.93 | 0.78
2025-05-02 | 19.4 | 0 | 1.4 | 2024-05-02 | 15 | 3 | 0 | 2023-05-02 | 11.7 | 6.3 | 0 | 2022-05-02 | 14.9 | 3.1 | 0 | 2021-05-02 | 13 | 5 | 0 | 2020-05-02 | 18.3 | 0 | 0.3 | 2019-05-02 | 6.8 | 11.2 | 0 | 2018-05-02 | 25 | 0 | 7 | 2017-05-02 | 11.9 | 6.1 | 0 | 2016-05-02 | 8.9 | 9.1 | 0 | 4.38 | 0.87
2025-05-02 | 20.2 | 0 | 2.2 | 2024-05-02 | 16.1 | 1.9 | 0 | 2023-05-02 | 7.6 | 10.4 | 0 | 2022-05-02 | 14.6 | 3.4 | 0 | 2021-05-02 | 13.5 | 4.5 | 0 | 2020-05-02 | 19.2 | 0 | 1.2 | 2019-05-02 | 7.4 | 10.6 | 0 | 2018-05-02 | 23.8 | 0 | 5.8 | 2017-05-02 | 14 | 4 | 0 | 2016-05-02 | 9 | 9 | 0 | 4.38 | 0.92
2025-05-02 | 20.6 | 0 | 2.6 | 2024-05-02 | 17.6 | 0.4 | 0 | 2023-05-02 | 9.3 | 8.7 | 0 | 2022-05-02 | 14.6 | 3.4 | 0 | 2021-05-02 | 13.9 | 4.1 | 0 | 2020-05-02 | 20.3 | 0 | 2.3 | 2019-05-02 | 8.2 | 9.8 | 0 | 2018-05-02 | 23.8 | 0 | 5.8 | 2017-05-02 | 13 | 5 | 0 | 2016-05-02 | 8.7 | 9.3 | 0 | 4.07 | 1.07
2025-05-02 | 21 | 0 | 3 | 2024-05-02 | 17.5 | 0.5 | 0 | 2023-05-02 | 9.7 | 8.3 | 0 | 2022-05-02 | 12.5 | 5.5 | 0 | 2021-05-02 | 13.7 | 4.3 | 0 | 2020-05-02 | 17.7 | 0.3 | 0 | 2019-05-02 | 9 | 9 | 0 | 2018-05-02 | 22.1 | 0 | 4.1 | 2017-05-02 | 11.8 | 6.2 | 0 | 2016-05-02 | 8.7 | 9.3 | 0 | 4.34 | 0.71
2025-05-02 | 19.6 | 0 | 1.6 | 2024-05-02 | 18.7 | 0 | 0.7 | 2023-05-02 | 10.8 | 7.2 | 0 | 2022-05-02 | 12.5 | 5.5 | 0 | 2021-05-02 | 14.2 | 3.8 | 0 | 2020-05-02 | 15.8 | 2.2 | 0 | 2019-05-02 | 9.2 | 8.8 | 0 | 2018-05-02 | 23.2 | 0 | 5.2 | 2017-05-02 | 11.3 | 6.7 | 0 | 2016-05-02 | 8.4 | 9.6 | 0 | 4.38 | 0.75
2025-05-02 | 18.7 | 0 | 0.7 | 2024-05-02 | 17.8 | 0.2 | 0 | 2023-05-02 | 8.9 | 9.1 | 0 | 2022-05-02 | 12.1 | 5.9 | 0 | 2021-05-02 | 12.8 | 5.2 | 0 | 2020-05-02 | 15.1 | 2.9 | 0 | 2019-05-02 | 8.8 | 9.2 | 0 | 2018-05-02 | 22.1 | 0 | 4.1 | 2017-05-02 | 9.5 | 8.5 | 0 | 2016-05-02 | 7.8 | 10.2 | 0 | 5.12 | 0.48
2025-05-02 | 16.2 | 1.8 | 0 | 2024-05-02 | 15.9 | 2.1 | 0 | 2023-05-02 | 8.4 | 9.6 | 0 | 2022-05-02 | 11.8 | 6.2 | 0 | 2021-05-02 | 11.6 | 6.4 | 0 | 2020-05-02 | 14.5 | 3.5 | 0 | 2019-05-02 | 8.1 | 9.9 | 0 | 2018-05-02 | 17.1 | 0.9 | 0 | 2017-05-02 | 8.5 | 9.5 | 0 | 2016-05-02 | 7.1 | 10.9 | 0 | 6.08 | 0
2025-05-02 | 13.1 | 4.9 | 0 | 2024-05-02 | 14.3 | 3.7 | 0 | 2023-05-02 | 8 | 10 | 0 | 2022-05-02 | 10.8 | 7.2 | 0 | 2021-05-02 | 11.6 | 6.4 | 0 | 2020-05-02 | 11.9 | 6.1 | 0 | 2019-05-02 | 7.6 | 10.4 | 0 | 2018-05-02 | 16.1 | 1.9 | 0 | 2017-05-02 | 8.5 | 9.5 | 0 | 2016-05-02 | 6.7 | 11.3 | 0 | 7.14 | 0
2025-05-02 | 11.8 | 6.2 | 0 | 2024-05-02 | 12.5 | 5.5 | 0 | 2023-05-02 | 7.7 | 10.3 | 0 | 2022-05-02 | 10.7 | 7.3 | 0 | 2021-05-02 | 11.1 | 6.9 | 0 | 2020-05-02 | 10.8 | 7.2 | 0 | 2019-05-02 | 6.7 | 11.3 | 0 | 2018-05-02 | 15.4 | 2.6 | 0 | 2017-05-02 | 8.2 | 9.8 | 0 | 2016-05-02 | 6.6 | 11.4 | 0 | 7.85 | 0
2025-05-02 | 10.5 | 7.5 | 0 | 2024-05-02 | 11 | 7 | 0 | 2023-05-02 | 7 | 11 | 0 | 2022-05-02 | 10.7 | 7.3 | 0 | 2021-05-02 | 11.2 | 6.8 | 0 | 2020-05-02 | 10.2 | 7.8 | 0 | 2019-05-02 | 6.8 | 11.2 | 0 | 2018-05-02 | 12.6 | 5.4 | 0 | 2017-05-02 | 8 | 10 | 0 | 2016-05-02 | 6.4 | 11.6 | 0 | 8.56 | 0
2025-05-02 | 9.7 | 8.3 | 0 | 2024-05-02 | 10.2 | 7.8 | 0 | 2023-05-02 | 7.9 | 10.1 | 0 | 2022-05-02 | 10.6 | 7.4 | 0 | 2021-05-02 | 10.8 | 7.2 | 0 | 2020-05-02 | 10.5 | 7.5 | 0 | 2019-05-02 | 5.7 | 12.3 | 0 | 2018-05-02 | 12 | 6 | 0 | 2017-05-02 | 7.6 | 10.4 | 0 | 2016-05-02 | 6.3 | 11.7 | 0 | 8.87 | 0
2025-05-03 | 8.9 | 9.1 | 0 | 2024-05-03 | 9.4 | 8.6 | 0 | 2023-05-03 | 7.6 | 10.4 | 0 | 2022-05-03 | 10.7 | 7.3 | 0 | 2021-05-03 | 10.4 | 7.6 | 0 | 2020-05-03 | 10.1 | 7.9 | 0 | 2019-05-03 | 5.4 | 12.6 | 0 | 2018-05-03 | 12.1 | 5.9 | 0 | 2017-05-03 | 7.1 | 10.9 | 0 | 2016-05-03 | 4.8 | 13.2 | 0 | 9.35 | 0
2025-05-03 | 8.4 | 9.6 | 0 | 2024-05-03 | 7.7 | 10.3 | 0 | 2023-05-03 | 7.3 | 10.7 | 0 | 2022-05-03 | 10.5 | 7.5 | 0 | 2021-05-03 | 8.8 | 9.2 | 0 | 2020-05-03 | 9.6 | 8.4 | 0 | 2019-05-03 | 5.4 | 12.6 | 0 | 2018-05-03 | 12.4 | 5.6 | 0 | 2017-05-03 | 7.1 | 10.9 | 0 | 2016-05-03 | 2.8 | 15.2 | 0 | 10 | 0
2025-05-03 | 7.7 | 10.3 | 0 | 2024-05-03 | 9.3 | 8.7 | 0 | 2023-05-03 | 7.1 | 10.9 | 0 | 2022-05-03 | 10.4 | 7.6 | 0 | 2021-05-03 | 8.3 | 9.7 | 0 | 2020-05-03 | 9.4 | 8.6 | 0 | 2019-05-03 | 5.4 | 12.6 | 0 | 2018-05-03 | 13 | 5 | 0 | 2017-05-03 | 7.2 | 10.8 | 0 | 2016-05-03 | 3.3 | 14.7 | 0 | 9.89 | 0
2025-05-03 | 6.7 | 11.3 | 0 | 2024-05-03 | 8.9 | 9.1 | 0 | 2023-05-03 | 7 | 11 | 0 | 2022-05-03 | 9.8 | 8.2 | 0 | 2021-05-03 | 7.7 | 10.3 | 0 | 2020-05-03 | 9 | 9 | 0 | 2019-05-03 | 5.6 | 12.4 | 0 | 2018-05-03 | 13.2 | 4.8 | 0 | 2017-05-03 | 6.5 | 11.5 | 0 | 2016-05-03 | -0.4 | 18.4 | 0 | 10.6 | 0
2025-05-03 | 7 | 11 | 0 | 2024-05-03 | 8.2 | 9.8 | 0 | 2023-05-03 | 7 | 11 | 0 | 2022-05-03 | 9.8 | 8.2 | 0 | 2021-05-03 | 6.9 | 11.1 | 0 | 2020-05-03 | 8.9 | 9.1 | 0 | 2019-05-03 | 5.4 | 12.6 | 0 | 2018-05-03 | 11.9 | 6.1 | 0 | 2017-05-03 | 5.3 | 12.7 | 0 | 2016-05-03 | 0.3 | 17.7 | 0 | 10.93 | 0
2025-05-03 | 6.8 | 11.2 | 0 | 2024-05-03 | 7.2 | 10.8 | 0 | 2023-05-03 | 7.2 | 10.8 | 0 | 2022-05-03 | 9.9 | 8.1 | 0 | 2021-05-03 | 6.9 | 11.1 | 0 | 2020-05-03 | 7.5 | 10.5 | 0 | 2019-05-03 | 5.8 | 12.2 | 0 | 2018-05-03 | 12.5 | 5.5 | 0 | 2017-05-03 | 4.2 | 13.8 | 0 | 2016-05-03 | 0.4 | 17.6 | 0 | 11.16 | 0
2025-05-03 | 7.4 | 10.6 | 0 | 2024-05-03 | 7.8 | 10.2 | 0 | 2023-05-03 | 7.6 | 10.4 | 0 | 2022-05-03 | 9.9 | 8.1 | 0 | 2021-05-03 | 7 | 11 | 0 | 2020-05-03 | 8.5 | 9.5 | 0 | 2019-05-03 | 6 | 12 | 0 | 2018-05-03 | 13.7 | 4.3 | 0 | 2017-05-03 | 3.7 | 14.3 | 0 | 2016-05-03 | 1.2 | 16.8 | 0 | 10.72 | 0
2025-05-03 | 7.8 | 10.2 | 0 | 2024-05-03 | 10.1 | 7.9 | 0 | 2023-05-03 | 7.7 | 10.3 | 0 | 2022-05-03 | 10.1 | 7.9 | 0 | 2021-05-03 | 7.5 | 10.5 | 0 | 2020-05-03 | 10.3 | 7.7 | 0 | 2019-05-03 | 6.3 | 11.7 | 0 | 2018-05-03 | 13.7 | 4.3 | 0 | 2017-05-03 | 4.3 | 13.7 | 0 | 2016-05-03 | 5.5 | 12.5 | 0 | 9.67 | 0
2025-05-03 | 8.1 | 9.9 | 0 | 2024-05-03 | 10.6 | 7.4 | 0 | 2023-05-03 | 7.7 | 10.3 | 0 | 2022-05-03 | 9.8 | 8.2 | 0 | 2021-05-03 | 7.5 | 10.5 | 0 | 2020-05-03 | 12.2 | 5.8 | 0 | 2019-05-03 | 6.7 | 11.3 | 0 | 2018-05-03 | 14.7 | 3.3 | 0 | 2017-05-03 | 4.3 | 13.7 | 0 | 2016-05-03 | 7.8 | 10.2 | 0 | 9.06 | 0
2025-05-03 | 8.5 | 9.5 | 0 | 2024-05-03 | 11.3 | 6.7 | 0 | 2023-05-03 | 7.5 | 10.5 | 0 | 2022-05-03 | 11.5 | 6.5 | 0 | 2021-05-03 | 7.3 | 10.7 | 0 | 2020-05-03 | 14.9 | 3.1 | 0 | 2019-05-03 | 7.2 | 10.8 | 0 | 2018-05-03 | 16.4 | 1.6 | 0 | 2017-05-03 | 5.3 | 12.7 | 0 | 2016-05-03 | 10.1 | 7.9 | 0 | 8 | 0
2025-05-03 | 9.2 | 8.8 | 0 | 2024-05-03 | 12.7 | 5.3 | 0 | 2023-05-03 | 7.2 | 10.8 | 0 | 2022-05-03 | 11.8 | 6.2 | 0 | 2021-05-03 | 7 | 11 | 0 | 2020-05-03 | 16.4 | 1.6 | 0 | 2019-05-03 | 7.8 | 10.2 | 0 | 2018-05-03 | 16.3 | 1.7 | 0 | 2017-05-03 | 6.7 | 11.3 | 0 | 2016-05-03 | 11.3 | 6.7 | 0 | 7.36 | 0
2025-05-03 | 10.1 | 7.9 | 0 | 2024-05-03 | 15.1 | 2.9 | 0 | 2023-05-03 | 7.5 | 10.5 | 0 | 2022-05-03 | 12.7 | 5.3 | 0 | 2021-05-03 | 6.7 | 11.3 | 0 | 2020-05-03 | 18.6 | 0 | 0.6 | 2019-05-03 | 8.3 | 9.7 | 0 | 2018-05-03 | 16.9 | 1.1 | 0 | 2017-05-03 | 8 | 10 | 0 | 2016-05-03 | 12.8 | 5.2 | 0 | 6.39 | 0.06
2025-05-03 | 12.1 | 5.9 | 0 | 2024-05-03 | 16.2 | 1.8 | 0 | 2023-05-03 | 8.8 | 9.2 | 0 | 2022-05-03 | 13.3 | 4.7 | 0 | 2021-05-03 | 6.5 | 11.5 | 0 | 2020-05-03 | 18.7 | 0 | 0.7 | 2019-05-03 | 8.3 | 9.7 | 0 | 2018-05-03 | 16.9 | 1.1 | 0 | 2017-05-03 | 9.6 | 8.4 | 0 | 2016-05-03 | 13.8 | 4.2 | 0 | 5.65 | 0.07
2025-05-03 | 12.7 | 5.3 | 0 | 2024-05-03 | 17.4 | 0.6 | 0 | 2023-05-03 | 9.1 | 8.9 | 0 | 2022-05-03 | 13.1 | 4.9 | 0 | 2021-05-03 | 6.2 | 11.8 | 0 | 2020-05-03 | 19.4 | 0 | 1.4 | 2019-05-03 | 9.2 | 8.8 | 0 | 2018-05-03 | 16.3 | 1.7 | 0 | 2017-05-03 | 11.7 | 6.3 | 0 | 2016-05-03 | 13.4 | 4.6 | 0 | 5.29 | 0.14
2025-05-03 | 13.5 | 4.5 | 0 | 2024-05-03 | 17.9 | 0.1 | 0 | 2023-05-03 | 8.5 | 9.5 | 0 | 2022-05-03 | 13.7 | 4.3 | 0 | 2021-05-03 | 6.4 | 11.6 | 0 | 2020-05-03 | 19.6 | 0 | 1.6 | 2019-05-03 | 9.2 | 8.8 | 0 | 2018-05-03 | 16.6 | 1.4 | 0 | 2017-05-03 | 12.7 | 5.3 | 0 | 2016-05-03 | 14.8 | 3.2 | 0 | 4.87 | 0.16
2025-05-03 | 14.1 | 3.9 | 0 | 2024-05-03 | 17.9 | 0.1 | 0 | 2023-05-03 | 8.1 | 9.9 | 0 | 2022-05-03 | 14.1 | 3.9 | 0 | 2021-05-03 | 6.3 | 11.7 | 0 | 2020-05-03 | 21.2 | 0 | 3.2 | 2019-05-03 | 9.3 | 8.7 | 0 | 2018-05-03 | 15.6 | 2.4 | 0 | 2017-05-03 | 13 | 5 | 0 | 2016-05-03 | 15.6 | 2.4 | 0 | 4.8 | 0.32
2025-05-03 | 14.7 | 3.3 | 0 | 2024-05-03 | 17.8 | 0.2 | 0 | 2023-05-03 | 7.9 | 10.1 | 0 | 2022-05-03 | 13.9 | 4.1 | 0 | 2021-05-03 | 5.9 | 12.1 | 0 | 2020-05-03 | 21.8 | 0 | 3.8 | 2019-05-03 | 9.6 | 8.4 | 0 | 2018-05-03 | 15.4 | 2.6 | 0 | 2017-05-03 | 13.5 | 4.5 | 0 | 2016-05-03 | 15 | 3 | 0 | 4.83 | 0.38
2025-05-03 | 14.9 | 3.1 | 0 | 2024-05-03 | 17.2 | 0.8 | 0 | 2023-05-03 | 7.6 | 10.4 | 0 | 2022-05-03 | 13.9 | 4.1 | 0 | 2021-05-03 | 6 | 12 | 0 | 2020-05-03 | 21.1 | 0 | 3.1 | 2019-05-03 | 9.9 | 8.1 | 0 | 2018-05-03 | 15.3 | 2.7 | 0 | 2017-05-03 | 13.4 | 4.6 | 0 | 2016-05-03 | 15 | 3 | 0 | 4.88 | 0.31
2025-05-03 | 14.2 | 3.8 | 0 | 2024-05-03 | 16.4 | 1.6 | 0 | 2023-05-03 | 6.9 | 11.1 | 0 | 2022-05-03 | 13.2 | 4.8 | 0 | 2021-05-03 | 5.8 | 12.2 | 0 | 2020-05-03 | 18.4 | 0 | 0.4 | 2019-05-03 | 10 | 8 | 0 | 2018-05-03 | 15.2 | 2.8 | 0 | 2017-05-03 | 12.8 | 5.2 | 0 | 2016-05-03 | 14 | 4 | 0 | 5.35 | 0.04
2025-05-03 | 12.4 | 5.6 | 0 | 2024-05-03 | 15.3 | 2.7 | 0 | 2023-05-03 | 6.6 | 11.4 | 0 | 2022-05-03 | 12.6 | 5.4 | 0 | 2021-05-03 | 5.6 | 12.4 | 0 | 2020-05-03 | 15.6 | 2.4 | 0 | 2019-05-03 | 9.7 | 8.3 | 0 | 2018-05-03 | 14.8 | 3.2 | 0 | 2017-05-03 | 10.4 | 7.6 | 0 | 2016-05-03 | 10.7 | 7.3 | 0 | 6.63 | 0
2025-05-03 | 11.8 | 6.2 | 0 | 2024-05-03 | 14.9 | 3.1 | 0 | 2023-05-03 | 6.5 | 11.5 | 0 | 2022-05-03 | 11.6 | 6.4 | 0 | 2021-05-03 | 5.7 | 12.3 | 0 | 2020-05-03 | 13 | 5 | 0 | 2019-05-03 | 9.4 | 8.6 | 0 | 2018-05-03 | 14.3 | 3.7 | 0 | 2017-05-03 | 9.8 | 8.2 | 0 | 2016-05-03 | 8.8 | 9.2 | 0 | 7.42 | 0
2025-05-03 | 10.5 | 7.5 | 0 | 2024-05-03 | 15.6 | 2.4 | 0 | 2023-05-03 | 6.3 | 11.7 | 0 | 2022-05-03 | 10.6 | 7.4 | 0 | 2021-05-03 | 6.1 | 11.9 | 0 | 2020-05-03 | 11.2 | 6.8 | 0 | 2019-05-03 | 9.3 | 8.7 | 0 | 2018-05-03 | 13.8 | 4.2 | 0 | 2017-05-03 | 7.8 | 10.2 | 0 | 2016-05-03 | 8 | 10 | 0 | 8.08 | 0
2025-05-03 | 10.2 | 7.8 | 0 | 2024-05-03 | 14.9 | 3.1 | 0 | 2023-05-03 | 6.1 | 11.9 | 0 | 2022-05-03 | 10.2 | 7.8 | 0 | 2021-05-03 | 6.5 | 11.5 | 0 | 2020-05-03 | 10.2 | 7.8 | 0 | 2019-05-03 | 9.1 | 8.9 | 0 | 2018-05-03 | 12.9 | 5.1 | 0 | 2017-05-03 | 4.4 | 13.6 | 0 | 2016-05-03 | 7.5 | 10.5 | 0 | 8.8 | 0
2025-05-03 | 9.2 | 8.8 | 0 | 2024-05-03 | 14.4 | 3.6 | 0 | 2023-05-03 | 5.9 | 12.1 | 0 | 2022-05-03 | 10.2 | 7.8 | 0 | 2021-05-03 | 6.8 | 11.2 | 0 | 2020-05-03 | 9.3 | 8.7 | 0 | 2019-05-03 | 8.9 | 9.1 | 0 | 2018-05-03 | 11.9 | 6.1 | 0 | 2017-05-03 | 5.3 | 12.7 | 0 | 2016-05-03 | 6 | 12 | 0 | 9.21 | 0
2025-05-04 | 9 | 9 | 0 | 2024-05-04 | 14.3 | 3.7 | 0 | 2023-05-04 | 5.8 | 12.2 | 0 | 2022-05-04 | 10 | 8 | 0 | 2021-05-04 | 7 | 11 | 0 | 2020-05-04 | 6.8 | 11.2 | 0 | 2019-05-04 | 8.6 | 9.4 | 0 | 2018-05-04 | 10.7 | 7.3 | 0 | 2017-05-04 | 5.2 | 12.8 | 0 | 2016-05-04 | 5.2 | 12.8 | 0 | 9.74 | 0
2025-05-04 | 8.1 | 9.9 | 0 | 2024-05-04 | 14.3 | 3.7 | 0 | 2023-05-04 | 5.9 | 12.1 | 0 | 2022-05-04 | 10 | 8 | 0 | 2021-05-04 | 7.4 | 10.6 | 0 | 2020-05-04 | 8.1 | 9.9 | 0 | 2019-05-04 | 8.5 | 9.5 | 0 | 2018-05-04 | 10.1 | 7.9 | 0 | 2017-05-04 | 3.7 | 14.3 | 0 | 2016-05-04 | 3.9 | 14.1 | 0 | 10 | 0
2025-05-04 | 7.4 | 10.6 | 0 | 2024-05-04 | 14.2 | 3.8 | 0 | 2023-05-04 | 5.7 | 12.3 | 0 | 2022-05-04 | 10.1 | 7.9 | 0 | 2021-05-04 | 7.8 | 10.2 | 0 | 2020-05-04 | 7.8 | 10.2 | 0 | 2019-05-04 | 8.4 | 9.6 | 0 | 2018-05-04 | 8.8 | 9.2 | 0 | 2017-05-04 | 2.9 | 15.1 | 0 | 2016-05-04 | 4.2 | 13.8 | 0 | 10.27 | 0
2025-05-04 | 6.3 | 11.7 | 0 | 2024-05-04 | 13.5 | 4.5 | 0 | 2023-05-04 | 5.5 | 12.5 | 0 | 2022-05-04 | 10 | 8 | 0 | 2021-05-04 | 7.8 | 10.2 | 0 | 2020-05-04 | 7.4 | 10.6 | 0 | 2019-05-04 | 8 | 10 | 0 | 2018-05-04 | 6.2 | 11.8 | 0 | 2017-05-04 | 0.7 | 17.3 | 0 | 2016-05-04 | 4.9 | 13.1 | 0 | 10.97 | 0
2025-05-04 | 6.3 | 11.7 | 0 | 2024-05-04 | 12.7 | 5.3 | 0 | 2023-05-04 | 5.8 | 12.2 | 0 | 2022-05-04 | 9.9 | 8.1 | 0 | 2021-05-04 | 8.1 | 9.9 | 0 | 2020-05-04 | 6.7 | 11.3 | 0 | 2019-05-04 | 7.9 | 10.1 | 0 | 2018-05-04 | 7.3 | 10.7 | 0 | 2017-05-04 | 1.9 | 16.1 | 0 | 2016-05-04 | 3.4 | 14.6 | 0 | 11 | 0
2025-05-04 | 7 | 11 | 0 | 2024-05-04 | 12.1 | 5.9 | 0 | 2023-05-04 | 5.6 | 12.4 | 0 | 2022-05-04 | 9.9 | 8.1 | 0 | 2021-05-04 | 8.3 | 9.7 | 0 | 2020-05-04 | 6.1 | 11.9 | 0 | 2019-05-04 | 7.7 | 10.3 | 0 | 2018-05-04 | 7.6 | 10.4 | 0 | 2017-05-04 | 0.9 | 17.1 | 0 | 2016-05-04 | 3.9 | 14.1 | 0 | 11.09 | 0
2025-05-04 | 7.7 | 10.3 | 0 | 2024-05-04 | 11.8 | 6.2 | 0 | 2023-05-04 | 5.6 | 12.4 | 0 | 2022-05-04 | 10.2 | 7.8 | 0 | 2021-05-04 | 8.7 | 9.3 | 0 | 2020-05-04 | 5.8 | 12.2 | 0 | 2019-05-04 | 8.3 | 9.7 | 0 | 2018-05-04 | 7.7 | 10.3 | 0 | 2017-05-04 | 2.6 | 15.4 | 0 | 2016-05-04 | 4.8 | 13.2 | 0 | 10.68 | 0
2025-05-04 | 10.1 | 7.9 | 0 | 2024-05-04 | 12 | 6 | 0 | 2023-05-04 | 5.8 | 12.2 | 0 | 2022-05-04 | 10.7 | 7.3 | 0 | 2021-05-04 | 9.6 | 8.4 | 0 | 2020-05-04 | 5.8 | 12.2 | 0 | 2019-05-04 | 8.4 | 9.6 | 0 | 2018-05-04 | 8 | 10 | 0 | 2017-05-04 | 5.1 | 12.9 | 0 | 2016-05-04 | 6.1 | 11.9 | 0 | 9.84 | 0
2025-05-04 | 11.9 | 6.1 | 0 | 2024-05-04 | 13.2 | 4.8 | 0 | 2023-05-04 | 6 | 12 | 0 | 2022-05-04 | 11.3 | 6.7 | 0 | 2021-05-04 | 10.8 | 7.2 | 0 | 2020-05-04 | 5.5 | 12.5 | 0 | 2019-05-04 | 10.6 | 7.4 | 0 | 2018-05-04 | 8.4 | 9.6 | 0 | 2017-05-04 | 7.4 | 10.6 | 0 | 2016-05-04 | 7.2 | 10.8 | 0 | 8.77 | 0
2025-05-04 | 13.5 | 4.5 | 0 | 2024-05-04 | 14.4 | 3.6 | 0 | 2023-05-04 | 6.5 | 11.5 | 0 | 2022-05-04 | 11.8 | 6.2 | 0 | 2021-05-04 | 11.3 | 6.7 | 0 | 2020-05-04 | 5.4 | 12.6 | 0 | 2019-05-04 | 11.7 | 6.3 | 0 | 2018-05-04 | 9.4 | 8.6 | 0 | 2017-05-04 | 10.3 | 7.7 | 0 | 2016-05-04 | 9.1 | 8.9 | 0 | 7.66 | 0
2025-05-04 | 14 | 4 | 0 | 2024-05-04 | 16.6 | 1.4 | 0 | 2023-05-04 | 7.5 | 10.5 | 0 | 2022-05-04 | 12.2 | 5.8 | 0 | 2021-05-04 | 12.8 | 5.2 | 0 | 2020-05-04 | 5.2 | 12.8 | 0 | 2019-05-04 | 12.8 | 5.2 | 0 | 2018-05-04 | 10 | 8 | 0 | 2017-05-04 | 12.5 | 5.5 | 0 | 2016-05-04 | 11.2 | 6.8 | 0 | 6.52 | 0
2025-05-04 | 14.8 | 3.2 | 0 | 2024-05-04 | 18.6 | 0 | 0.6 | 2023-05-04 | 8.3 | 9.7 | 0 | 2022-05-04 | 14.1 | 3.9 | 0 | 2021-05-04 | 12.9 | 5.1 | 0 | 2020-05-04 | 6.1 | 11.9 | 0 | 2019-05-04 | 12.7 | 5.3 | 0 | 2018-05-04 | 9.4 | 8.6 | 0 | 2017-05-04 | 13.8 | 4.2 | 0 | 2016-05-04 | 13 | 5 | 0 | 5.69 | 0.06
2025-05-04 | 16.6 | 1.4 | 0 | 2024-05-04 | 19.6 | 0 | 1.6 | 2023-05-04 | 8.8 | 9.2 | 0 | 2022-05-04 | 15.7 | 2.3 | 0 | 2021-05-04 | 13 | 5 | 0 | 2020-05-04 | 8 | 10 | 0 | 2019-05-04 | 14.8 | 3.2 | 0 | 2018-05-04 | 9.7 | 8.3 | 0 | 2017-05-04 | 14.4 | 3.6 | 0 | 2016-05-04 | 13.6 | 4.4 | 0 | 4.74 | 0.16
2025-05-04 | 17.6 | 0.4 | 0 | 2024-05-04 | 20.9 | 0 | 2.9 | 2023-05-04 | 9.9 | 8.1 | 0 | 2022-05-04 | 15.6 | 2.4 | 0 | 2021-05-04 | 13.1 | 4.9 | 0 | 2020-05-04 | 9.6 | 8.4 | 0 | 2019-05-04 | 15.2 | 2.8 | 0 | 2018-05-04 | 10.1 | 7.9 | 0 | 2017-05-04 | 15.1 | 2.9 | 0 | 2016-05-04 | 13.5 | 4.5 | 0 | 4.23 | 0.29
2025-05-04 | 19 | 0 | 1 | 2024-05-04 | 21.7 | 0 | 3.7 | 2023-05-04 | 9.8 | 8.2 | 0 | 2022-05-04 | 17.3 | 0.7 | 0 | 2021-05-04 | 13.2 | 4.8 | 0 | 2020-05-04 | 10.1 | 7.9 | 0 | 2019-05-04 | 15.8 | 2.2 | 0 | 2018-05-04 | 10.2 | 7.8 | 0 | 2017-05-04 | 15.1 | 2.9 | 0 | 2016-05-04 | 14.9 | 3.1 | 0 | 3.76 | 0.47
2025-05-04 | 19.9 | 0 | 1.9 | 2024-05-04 | 22.4 | 0 | 4.4 | 2023-05-04 | 9.3 | 8.7 | 0 | 2022-05-04 | 17.1 | 0.9 | 0 | 2021-05-04 | 13 | 5 | 0 | 2020-05-04 | 10 | 8 | 0 | 2019-05-04 | 15.6 | 2.4 | 0 | 2018-05-04 | 11.7 | 6.3 | 0 | 2017-05-04 | 15.5 | 2.5 | 0 | 2016-05-04 | 13.5 | 4.5 | 0 | 3.83 | 0.63
2025-05-04 | 19.6 | 0 | 1.6 | 2024-05-04 | 22.1 | 0 | 4.1 | 2023-05-04 | 9.9 | 8.1 | 0 | 2022-05-04 | 17.2 | 0.8 | 0 | 2021-05-04 | 12.2 | 5.8 | 0 | 2020-05-04 | 10.2 | 7.8 | 0 | 2019-05-04 | 16.5 | 1.5 | 0 | 2018-05-04 | 14.6 | 3.4 | 0 | 2017-05-04 | 15.3 | 2.7 | 0 | 2016-05-04 | 13.4 | 4.6 | 0 | 3.47 | 0.57
2025-05-04 | 20 | 0 | 2 | 2024-05-04 | 21.8 | 0 | 3.8 | 2023-05-04 | 9.2 | 8.8 | 0 | 2022-05-04 | 16.8 | 1.2 | 0 | 2021-05-04 | 12 | 6 | 0 | 2020-05-04 | 10.1 | 7.9 | 0 | 2019-05-04 | 15.8 | 2.2 | 0 | 2018-05-04 | 17.3 | 0.7 | 0 | 2017-05-04 | 14.2 | 3.8 | 0 | 2016-05-04 | 12.4 | 5.6 | 0 | 3.62 | 0.58
2025-05-04 | 18.2 | 0 | 0.2 | 2024-05-04 | 20.5 | 0 | 2.5 | 2023-05-04 | 8.8 | 9.2 | 0 | 2022-05-04 | 16.1 | 1.9 | 0 | 2021-05-04 | 11.4 | 6.6 | 0 | 2020-05-04 | 7.5 | 10.5 | 0 | 2019-05-04 | 15.8 | 2.2 | 0 | 2018-05-04 | 22.2 | 0 | 4.2 | 2017-05-04 | 14 | 4 | 0 | 2016-05-04 | 12.1 | 5.9 | 0 | 4.03 | 0.69
2025-05-04 | 18.3 | 0 | 0.3 | 2024-05-04 | 19.1 | 0 | 1.1 | 2023-05-04 | 8.2 | 9.8 | 0 | 2022-05-04 | 14 | 4 | 0 | 2021-05-04 | 10.2 | 7.8 | 0 | 2020-05-04 | 6.1 | 11.9 | 0 | 2019-05-04 | 12.9 | 5.1 | 0 | 2018-05-04 | 21.3 | 0 | 3.3 | 2017-05-04 | 11.4 | 6.6 | 0 | 2016-05-04 | 11.6 | 6.4 | 0 | 5.16 | 0.47
2025-05-04 | 16.3 | 1.7 | 0 | 2024-05-04 | 17.1 | 0.9 | 0 | 2023-05-04 | 7.9 | 10.1 | 0 | 2022-05-04 | 12.6 | 5.4 | 0 | 2021-05-04 | 9.9 | 8.1 | 0 | 2020-05-04 | 4.8 | 13.2 | 0 | 2019-05-04 | 12.5 | 5.5 | 0 | 2018-05-04 | 18.9 | 0 | 0.9 | 2017-05-04 | 9.1 | 8.9 | 0 | 2016-05-04 | 10.6 | 7.4 | 0 | 6.12 | 0.09
2025-05-04 | 14.5 | 3.5 | 0 | 2024-05-04 | 16 | 2 | 0 | 2023-05-04 | 7.9 | 10.1 | 0 | 2022-05-04 | 11.8 | 6.2 | 0 | 2021-05-04 | 9.3 | 8.7 | 0 | 2020-05-04 | 4 | 14 | 0 | 2019-05-04 | 11.8 | 6.2 | 0 | 2018-05-04 | 11 | 7 | 0 | 2017-05-04 | 7.6 | 10.4 | 0 | 2016-05-04 | 9.4 | 8.6 | 0 | 7.67 | 0
2025-05-04 | 13.9 | 4.1 | 0 | 2024-05-04 | 15.4 | 2.6 | 0 | 2023-05-04 | 7.3 | 10.7 | 0 | 2022-05-04 | 10.3 | 7.7 | 0 | 2021-05-04 | 9.1 | 8.9 | 0 | 2020-05-04 | 2.8 | 15.2 | 0 | 2019-05-04 | 10.9 | 7.1 | 0 | 2018-05-04 | 7.6 | 10.4 | 0 | 2017-05-04 | 7.2 | 10.8 | 0 | 2016-05-04 | 9.3 | 8.7 | 0 | 8.62 | 0
2025-05-04 | 11.6 | 6.4 | 0 | 2024-05-04 | 14.2 | 3.8 | 0 | 2023-05-04 | 5.1 | 12.9 | 0 | 2022-05-04 | 9.2 | 8.8 | 0 | 2021-05-04 | 8.6 | 9.4 | 0 | 2020-05-04 | 1.7 | 16.3 | 0 | 2019-05-04 | 7.3 | 10.7 | 0 | 2018-05-04 | 7.4 | 10.6 | 0 | 2017-05-04 | 7.2 | 10.8 | 0 | 2016-05-04 | 9.4 | 8.6 | 0 | 9.83 | 0
2025-05-05 | 11.9 | 6.1 | 0 | 2024-05-05 | 15 | 3 | 0 | 2023-05-05 | 6.2 | 11.8 | 0 | 2022-05-05 | 8.4 | 9.6 | 0 | 2021-05-05 | 8.1 | 9.9 | 0 | 2020-05-05 | 0.8 | 17.2 | 0 | 2019-05-05 | 8 | 10 | 0 | 2018-05-05 | 7.3 | 10.7 | 0 | 2017-05-05 | 7.1 | 10.9 | 0 | 2016-05-05 | 9.4 | 8.6 | 0 | 9.78 | 0
2025-05-05 | 11.9 | 6.1 | 0 | 2024-05-05 | 14.6 | 3.4 | 0 | 2023-05-05 | 5.9 | 12.1 | 0 | 2022-05-05 | 6.7 | 11.3 | 0 | 2021-05-05 | 7.8 | 10.2 | 0 | 2020-05-05 | 0.3 | 17.7 | 0 | 2019-05-05 | 5.8 | 12.2 | 0 | 2018-05-05 | 7 | 11 | 0 | 2017-05-05 | 7.1 | 10.9 | 0 | 2016-05-05 | 9.5 | 8.5 | 0 | 10.34 | 0
2025-05-05 | 11.4 | 6.6 | 0 | 2024-05-05 | 15.4 | 2.6 | 0 | 2023-05-05 | 6.5 | 11.5 | 0 | 2022-05-05 | 5.2 | 12.8 | 0 | 2021-05-05 | 7.9 | 10.1 | 0 | 2020-05-05 | -0.4 | 18.4 | 0 | 2019-05-05 | 5 | 13 | 0 | 2018-05-05 | 6.5 | 11.5 | 0 | 2017-05-05 | 7.1 | 10.9 | 0 | 2016-05-05 | 9.4 | 8.6 | 0 | 10.6 | 0
2025-05-05 | 11 | 7 | 0 | 2024-05-05 | 15.8 | 2.2 | 0 | 2023-05-05 | 6.5 | 11.5 | 0 | 2022-05-05 | 5.9 | 12.1 | 0 | 2021-05-05 | 8 | 10 | 0 | 2020-05-05 | -0.7 | 18.7 | 0 | 2019-05-05 | 5.2 | 12.8 | 0 | 2018-05-05 | 6 | 12 | 0 | 2017-05-05 | 7.1 | 10.9 | 0 | 2016-05-05 | 9.4 | 8.6 | 0 | 10.58 | 0
2025-05-05 | 10.4 | 7.6 | 0 | 2024-05-05 | 15.8 | 2.2 | 0 | 2023-05-05 | 6.4 | 11.6 | 0 | 2022-05-05 | 4.5 | 13.5 | 0 | 2021-05-05 | 8.1 | 9.9 | 0 | 2020-05-05 | -0.9 | 18.9 | 0 | 2019-05-05 | 6.3 | 11.7 | 0 | 2018-05-05 | 6.5 | 11.5 | 0 | 2017-05-05 | 7 | 11 | 0 | 2016-05-05 | 9.1 | 8.9 | 0 | 10.68 | 0
2025-05-05 | 10.2 | 7.8 | 0 | 2024-05-05 | 12.8 | 5.2 | 0 | 2023-05-05 | 5.8 | 12.2 | 0 | 2022-05-05 | 4.9 | 13.1 | 0 | 2021-05-05 | 8.2 | 9.8 | 0 | 2020-05-05 | -1.6 | 19.6 | 0 | 2019-05-05 | 4.6 | 13.4 | 0 | 2018-05-05 | 6.6 | 11.4 | 0 | 2017-05-05 | 7 | 11 | 0 | 2016-05-05 | 9 | 9 | 0 | 11.25 | 0
2025-05-05 | 10.1 | 7.9 | 0 | 2024-05-05 | 11.6 | 6.4 | 0 | 2023-05-05 | 7.9 | 10.1 | 0 | 2022-05-05 | 5.7 | 12.3 | 0 | 2021-05-05 | 8.2 | 9.8 | 0 | 2020-05-05 | -0.3 | 18.3 | 0 | 2019-05-05 | 5.7 | 12.3 | 0 | 2018-05-05 | 7.6 | 10.4 | 0 | 2017-05-05 | 7.1 | 10.9 | 0 | 2016-05-05 | 9 | 9 | 0 | 10.74 | 0
2025-05-05 | 11.3 | 6.7 | 0 | 2024-05-05 | 11.7 | 6.3 | 0 | 2023-05-05 | 9.2 | 8.8 | 0 | 2022-05-05 | 7.4 | 10.6 | 0 | 2021-05-05 | 8.5 | 9.5 | 0 | 2020-05-05 | 0.4 | 17.6 | 0 | 2019-05-05 | 9.9 | 8.1 | 0 | 2018-05-05 | 9.8 | 8.2 | 0 | 2017-05-05 | 7.3 | 10.7 | 0 | 2016-05-05 | 10.8 | 7.2 | 0 | 9.37 | 0
2025-05-05 | 13.5 | 4.5 | 0 | 2024-05-05 | 11.6 | 6.4 | 0 | 2023-05-05 | 10.3 | 7.7 | 0 | 2022-05-05 | 8.4 | 9.6 | 0 | 2021-05-05 | 8.9 | 9.1 | 0 | 2020-05-05 | 1.7 | 16.3 | 0 | 2019-05-05 | 12.3 | 5.7 | 0 | 2018-05-05 | 12.2 | 5.8 | 0 | 2017-05-05 | 7.5 | 10.5 | 0 | 2016-05-05 | 11.5 | 6.5 | 0 | 8.21 | 0
2025-05-05 | 14.4 | 3.6 | 0 | 2024-05-05 | 11.3 | 6.7 | 0 | 2023-05-05 | 11.1 | 6.9 | 0 | 2022-05-05 | 9.5 | 8.5 | 0 | 2021-05-05 | 9.2 | 8.8 | 0 | 2020-05-05 | 2.7 | 15.3 | 0 | 2019-05-05 | 14.6 | 3.4 | 0 | 2018-05-05 | 14.5 | 3.5 | 0 | 2017-05-05 | 7.7 | 10.3 | 0 | 2016-05-05 | 12.8 | 5.2 | 0 | 7.22 | 0
2025-05-05 | 17 | 1 | 0 | 2024-05-05 | 11.3 | 6.7 | 0 | 2023-05-05 | 12 | 6 | 0 | 2022-05-05 | 10.5 | 7.5 | 0 | 2021-05-05 | 9.8 | 8.2 | 0 | 2020-05-05 | 4.5 | 13.5 | 0 | 2019-05-05 | 15.9 | 2.1 | 0 | 2018-05-05 | 17 | 1 | 0 | 2017-05-05 | 8 | 10 | 0 | 2016-05-05 | 15.5 | 2.5 | 0 | 5.85 | 0
2025-05-05 | 18.1 | 0 | 0.1 | 2024-05-05 | 11.1 | 6.9 | 0 | 2023-05-05 | 13.2 | 4.8 | 0 | 2022-05-05 | 12.1 | 5.9 | 0 | 2021-05-05 | 10.2 | 7.8 | 0 | 2020-05-05 | 6.1 | 11.9 | 0 | 2019-05-05 | 17.3 | 0.7 | 0 | 2018-05-05 | 19.3 | 0 | 1.3 | 2017-05-05 | 8.1 | 9.9 | 0 | 2016-05-05 | 15.3 | 2.7 | 0 | 5.06 | 0.14
2025-05-05 | 18.6 | 0 | 0.6 | 2024-05-05 | 11.5 | 6.5 | 0 | 2023-05-05 | 14.4 | 3.6 | 0 | 2022-05-05 | 13.8 | 4.2 | 0 | 2021-05-05 | 10.2 | 7.8 | 0 | 2020-05-05 | 7.2 | 10.8 | 0 | 2019-05-05 | 18.1 | 0 | 0.1 | 2018-05-05 | 19.9 | 0 | 1.9 | 2017-05-05 | 7.6 | 10.4 | 0 | 2016-05-05 | 16.6 | 1.4 | 0 | 4.47 | 0.26
2025-05-05 | 19.2 | 0 | 1.2 | 2024-05-05 | 12 | 6 | 0 | 2023-05-05 | 15.6 | 2.4 | 0 | 2022-05-05 | 14.5 | 3.5 | 0 | 2021-05-05 | 10.4 | 7.6 | 0 | 2020-05-05 | 9.1 | 8.9 | 0 | 2019-05-05 | 18.6 | 0 | 0.6 | 2018-05-05 | 21.5 | 0 | 3.5 | 2017-05-05 | 7.8 | 10.2 | 0 | 2016-05-05 | 17.6 | 0.4 | 0 | 3.9 | 0.53
2025-05-05 | 19.5 | 0 | 1.5 | 2024-05-05 | 12.7 | 5.3 | 0 | 2023-05-05 | 15.8 | 2.2 | 0 | 2022-05-05 | 15.9 | 2.1 | 0 | 2021-05-05 | 10.3 | 7.7 | 0 | 2020-05-05 | 9.9 | 8.1 | 0 | 2019-05-05 | 19.8 | 0 | 1.8 | 2018-05-05 | 22.8 | 0 | 4.8 | 2017-05-05 | 7.5 | 10.5 | 0 | 2016-05-05 | 17.7 | 0.3 | 0 | 3.62 | 0.81
2025-05-05 | 19.5 | 0 | 1.5 | 2024-05-05 | 12.7 | 5.3 | 0 | 2023-05-05 | 17.4 | 0.6 | 0 | 2022-05-05 | 16.7 | 1.3 | 0 | 2021-05-05 | 10.3 | 7.7 | 0 | 2020-05-05 | 10.5 | 7.5 | 0 | 2019-05-05 | 20.4 | 0 | 2.4 | 2018-05-05 | 22.5 | 0 | 4.5 | 2017-05-05 | 7.8 | 10.2 | 0 | 2016-05-05 | 18.6 | 0 | 0.6 | 3.26 | 0.9
2025-05-05 | 18.9 | 0 | 0.9 | 2024-05-05 | 12.9 | 5.1 | 0 | 2023-05-05 | 17.5 | 0.5 | 0 | 2022-05-05 | 17.3 | 0.7 | 0 | 2021-05-05 | 10.4 | 7.6 | 0 | 2020-05-05 | 11 | 7 | 0 | 2019-05-05 | 19.8 | 0 | 1.8 | 2018-05-05 | 22.3 | 0 | 4.3 | 2017-05-05 | 8 | 10 | 0 | 2016-05-05 | 18.7 | 0 | 0.7 | 3.09 | 0.77
2025-05-05 | 18.7 | 0 | 0.7 | 2024-05-05 | 13 | 5 | 0 | 2023-05-05 | 17 | 1 | 0 | 2022-05-05 | 16.8 | 1.2 | 0 | 2021-05-05 | 10 | 8 | 0 | 2020-05-05 | 10.3 | 7.7 | 0 | 2019-05-05 | 19.7 | 0 | 1.7 | 2018-05-05 | 21.1 | 0 | 3.1 | 2017-05-05 | 8.3 | 9.7 | 0 | 2016-05-05 | 18.1 | 0 | 0.1 | 3.26 | 0.56
2025-05-05 | 15.3 | 2.7 | 0 | 2024-05-05 | 13 | 5 | 0 | 2023-05-05 | 16.5 | 1.5 | 0 | 2022-05-05 | 16 | 2 | 0 | 2021-05-05 | 10.3 | 7.7 | 0 | 2020-05-05 | 10 | 8 | 0 | 2019-05-05 | 18.8 | 0 | 0.8 | 2018-05-05 | 21.1 | 0 | 3.1 | 2017-05-05 | 8.3 | 9.7 | 0 | 2016-05-05 | 16.8 | 1.2 | 0 | 3.78 | 0.39
2025-05-05 | 15 | 3 | 0 | 2024-05-05 | 13 | 5 | 0 | 2023-05-05 | 14.4 | 3.6 | 0 | 2022-05-05 | 15.2 | 2.8 | 0 | 2021-05-05 | 10.2 | 7.8 | 0 | 2020-05-05 | 8.6 | 9.4 | 0 | 2019-05-05 | 17.1 | 0.9 | 0 | 2018-05-05 | 18.9 | 0 | 0.9 | 2017-05-05 | 8.2 | 9.8 | 0 | 2016-05-05 | 14.5 | 3.5 | 0 | 4.58 | 0.09
2025-05-05 | 14.7 | 3.3 | 0 | 2024-05-05 | 13 | 5 | 0 | 2023-05-05 | 13.3 | 4.7 | 0 | 2022-05-05 | 13.9 | 4.1 | 0 | 2021-05-05 | 8.1 | 9.9 | 0 | 2020-05-05 | 6.3 | 11.7 | 0 | 2019-05-05 | 12.9 | 5.1 | 0 | 2018-05-05 | 17.3 | 0.7 | 0 | 2017-05-05 | 8.1 | 9.9 | 0 | 2016-05-05 | 11.9 | 6.1 | 0 | 6.05 | 0
2025-05-05 | 14.4 | 3.6 | 0 | 2024-05-05 | 12.9 | 5.1 | 0 | 2023-05-05 | 12.2 | 5.8 | 0 | 2022-05-05 | 12.5 | 5.5 | 0 | 2021-05-05 | 8.6 | 9.4 | 0 | 2020-05-05 | 6.5 | 11.5 | 0 | 2019-05-05 | 12.9 | 5.1 | 0 | 2018-05-05 | 16.2 | 1.8 | 0 | 2017-05-05 | 8.1 | 9.9 | 0 | 2016-05-05 | 10.5 | 7.5 | 0 | 6.52 | 0
2025-05-05 | 14.3 | 3.7 | 0 | 2024-05-05 | 12.9 | 5.1 | 0 | 2023-05-05 | 11.2 | 6.8 | 0 | 2022-05-05 | 12 | 6 | 0 | 2021-05-05 | 8.2 | 9.8 | 0 | 2020-05-05 | 5.6 | 12.4 | 0 | 2019-05-05 | 12.9 | 5.1 | 0 | 2018-05-05 | 14.2 | 3.8 | 0 | 2017-05-05 | 8.1 | 9.9 | 0 | 2016-05-05 | 11.6 | 6.4 | 0 | 6.9 | 0
2025-05-05 | 14.2 | 3.8 | 0 | 2024-05-05 | 12.9 | 5.1 | 0 | 2023-05-05 | 8.3 | 9.7 | 0 | 2022-05-05 | 10.2 | 7.8 | 0 | 2021-05-05 | 7.8 | 10.2 | 0 | 2020-05-05 | 5.9 | 12.1 | 0 | 2019-05-05 | 11.9 | 6.1 | 0 | 2018-05-05 | 13.1 | 4.9 | 0 | 2017-05-05 | 8.2 | 9.8 | 0 | 2016-05-05 | 10.9 | 7.1 | 0 | 7.66 | 0
2025-05-06 | 13.8 | 4.2 | 0 | 2024-05-06 | 12.9 | 5.1 | 0 | 2023-05-06 | 9.2 | 8.8 | 0 | 2022-05-06 | 9.6 | 8.4 | 0 | 2021-05-06 | 7.5 | 10.5 | 0 | 2020-05-06 | 4.8 | 13.2 | 0 | 2019-05-06 | 9.9 | 8.1 | 0 | 2018-05-06 | 13.5 | 4.5 | 0 | 2017-05-06 | 7.8 | 10.2 | 0 | 2016-05-06 | 9.6 | 8.4 | 0 | 8.14 | 0
2025-05-06 | 13.4 | 4.6 | 0 | 2024-05-06 | 12.8 | 5.2 | 0 | 2023-05-06 | 7.4 | 10.6 | 0 | 2022-05-06 | 8.2 | 9.8 | 0 | 2021-05-06 | 7 | 11 | 0 | 2020-05-06 | 4.2 | 13.8 | 0 | 2019-05-06 | 10.7 | 7.3 | 0 | 2018-05-06 | 11.3 | 6.7 | 0 | 2017-05-06 | 7.3 | 10.7 | 0 | 2016-05-06 | 8 | 10 | 0 | 8.97 | 0
2025-05-06 | 13.2 | 4.8 | 0 | 2024-05-06 | 12.4 | 5.6 | 0 | 2023-05-06 | 5.4 | 12.6 | 0 | 2022-05-06 | 7.5 | 10.5 | 0 | 2021-05-06 | 6.6 | 11.4 | 0 | 2020-05-06 | 3.8 | 14.2 | 0 | 2019-05-06 | 8.9 | 9.1 | 0 | 2018-05-06 | 12.2 | 5.8 | 0 | 2017-05-06 | 7.2 | 10.8 | 0 | 2016-05-06 | 7.8 | 10.2 | 0 | 9.5 | 0
2025-05-06 | 13.1 | 4.9 | 0 | 2024-05-06 | 11 | 7 | 0 | 2023-05-06 | 6.2 | 11.8 | 0 | 2022-05-06 | 7 | 11 | 0 | 2021-05-06 | 5.4 | 12.6 | 0 | 2020-05-06 | 3.4 | 14.6 | 0 | 2019-05-06 | 8.3 | 9.7 | 0 | 2018-05-06 | 10.8 | 7.2 | 0 | 2017-05-06 | 7.3 | 10.7 | 0 | 2016-05-06 | 7 | 11 | 0 | 10.05 | 0
2025-05-06 | 13 | 5 | 0 | 2024-05-06 | 10.2 | 7.8 | 0 | 2023-05-06 | 5.5 | 12.5 | 0 | 2022-05-06 | 8.1 | 9.9 | 0 | 2021-05-06 | 4.1 | 13.9 | 0 | 2020-05-06 | 2.7 | 15.3 | 0 | 2019-05-06 | 7.7 | 10.3 | 0 | 2018-05-06 | 10.2 | 7.8 | 0 | 2017-05-06 | 7.4 | 10.6 | 0 | 2016-05-06 | 6.7 | 11.3 | 0 | 10.44 | 0
2025-05-06 | 12.9 | 5.1 | 0 | 2024-05-06 | 7.9 | 10.1 | 0 | 2023-05-06 | 6.6 | 11.4 | 0 | 2022-05-06 | 7.1 | 10.9 | 0 | 2021-05-06 | 3.4 | 14.6 | 0 | 2020-05-06 | 2.4 | 15.6 | 0 | 2019-05-06 | 6 | 12 | 0 | 2018-05-06 | 9.3 | 8.7 | 0 | 2017-05-06 | 7.2 | 10.8 | 0 | 2016-05-06 | 6.8 | 11.2 | 0 | 11.04 | 0
2025-05-06 | 13.2 | 4.8 | 0 | 2024-05-06 | 10.6 | 7.4 | 0 | 2023-05-06 | 8.3 | 9.7 | 0 | 2022-05-06 | 8.1 | 9.9 | 0 | 2021-05-06 | 4.3 | 13.7 | 0 | 2020-05-06 | 3.7 | 14.3 | 0 | 2019-05-06 | 8.7 | 9.3 | 0 | 2018-05-06 | 9.6 | 8.4 | 0 | 2017-05-06 | 7.3 | 10.7 | 0 | 2016-05-06 | 8.5 | 9.5 | 0 | 9.77 | 0
2025-05-06 | 13.7 | 4.3 | 0 | 2024-05-06 | 11.7 | 6.3 | 0 | 2023-05-06 | 10.7 | 7.3 | 0 | 2022-05-06 | 10.5 | 7.5 | 0 | 2021-05-06 | 5.5 | 12.5 | 0 | 2020-05-06 | 5.6 | 12.4 | 0 | 2019-05-06 | 11.9 | 6.1 | 0 | 2018-05-06 | 10.9 | 7.1 | 0 | 2017-05-06 | 7.7 | 10.3 | 0 | 2016-05-06 | 11.3 | 6.7 | 0 | 8.05 | 0
2025-05-06 | 14.2 | 3.8 | 0 | 2024-05-06 | 13.8 | 4.2 | 0 | 2023-05-06 | 12.9 | 5.1 | 0 | 2022-05-06 | 10.4 | 7.6 | 0 | 2021-05-06 | 7.4 | 10.6 | 0 | 2020-05-06 | 7.2 | 10.8 | 0 | 2019-05-06 | 15.1 | 2.9 | 0 | 2018-05-06 | 12.1 | 5.9 | 0 | 2017-05-06 | 8.4 | 9.6 | 0 | 2016-05-06 | 12.6 | 5.4 | 0 | 6.59 | 0
2025-05-06 | 16.9 | 1.1 | 0 | 2024-05-06 | 15.2 | 2.8 | 0 | 2023-05-06 | 15.9 | 2.1 | 0 | 2022-05-06 | 11.9 | 6.1 | 0 | 2021-05-06 | 8.9 | 9.1 | 0 | 2020-05-06 | 8.6 | 9.4 | 0 | 2019-05-06 | 18.4 | 0 | 0.4 | 2018-05-06 | 14.6 | 3.4 | 0 | 2017-05-06 | 9.8 | 8.2 | 0 | 2016-05-06 | 14.2 | 3.8 | 0 | 4.6 | 0.04
2025-05-06 | 17.6 | 0.4 | 0 | 2024-05-06 | 17 | 1 | 0 | 2023-05-06 | 18.2 | 0 | 0.2 | 2022-05-06 | 12.5 | 5.5 | 0 | 2021-05-06 | 10 | 8 | 0 | 2020-05-06 | 10.3 | 7.7 | 0 | 2019-05-06 | 20.1 | 0 | 2.1 | 2018-05-06 | 15.4 | 2.6 | 0 | 2017-05-06 | 10.7 | 7.3 | 0 | 2016-05-06 | 16.9 | 1.1 | 0 | 3.36 | 0.23
2025-05-06 | 19.6 | 0 | 1.6 | 2024-05-06 | 18 | 0 | 0 | 2023-05-06 | 19.7 | 0 | 1.7 | 2022-05-06 | 13.1 | 4.9 | 0 | 2021-05-06 | 11.5 | 6.5 | 0 | 2020-05-06 | 10.7 | 7.3 | 0 | 2019-05-06 | 21.5 | 0 | 3.5 | 2018-05-06 | 17.4 | 0.6 | 0 | 2017-05-06 | 12.4 | 5.6 | 0 | 2016-05-06 | 18.2 | 0 | 0.2 | 2.49 | 0.7
2025-05-06 | 19.9 | 0 | 1.9 | 2024-05-06 | 19.4 | 0 | 1.4 | 2023-05-06 | 20.4 | 0 | 2.4 | 2022-05-06 | 15 | 3 | 0 | 2021-05-06 | 13 | 5 | 0 | 2020-05-06 | 11.1 | 6.9 | 0 | 2019-05-06 | 22.3 | 0 | 4.3 | 2018-05-06 | 18 | 0 | 0 | 2017-05-06 | 14.1 | 3.9 | 0 | 2016-05-06 | 19.4 | 0 | 1.4 | 1.88 | 1.14
2025-05-06 | 19.4 | 0 | 1.4 | 2024-05-06 | 19.8 | 0 | 1.8 | 2023-05-06 | 19.8 | 0 | 1.8 | 2022-05-06 | 15.7 | 2.3 | 0 | 2021-05-06 | 12.2 | 5.8 | 0 | 2020-05-06 | 12.1 | 5.9 | 0 | 2019-05-06 | 22.5 | 0 | 4.5 | 2018-05-06 | 19.1 | 0 | 1.1 | 2017-05-06 | 14 | 4 | 0 | 2016-05-06 | 20.6 | 0 | 2.6 | 1.8 | 1.32
2025-05-06 | 20.6 | 0 | 2.6 | 2024-05-06 | 20.4 | 0 | 2.4 | 2023-05-06 | 20.7 | 0 | 2.7 | 2022-05-06 | 15.9 | 2.1 | 0 | 2021-05-06 | 12 | 6 | 0 | 2020-05-06 | 12.3 | 5.7 | 0 | 2019-05-06 | 23.6 | 0 | 5.6 | 2018-05-06 | 19 | 0 | 1 | 2017-05-06 | 11.1 | 6.9 | 0 | 2016-05-06 | 21.3 | 0 | 3.3 | 2.07 | 1.76
2025-05-06 | 20.8 | 0 | 2.8 | 2024-05-06 | 20.9 | 0 | 2.9 | 2023-05-06 | 21.7 | 0 | 3.7 | 2022-05-06 | 16 | 2 | 0 | 2021-05-06 | 13.3 | 4.7 | 0 | 2020-05-06 | 13.4 | 4.6 | 0 | 2019-05-06 | 23 | 0 | 5 | 2018-05-06 | 18.7 | 0 | 0.7 | 2017-05-06 | 10.2 | 7.8 | 0 | 2016-05-06 | 21.4 | 0 | 3.4 | 1.91 | 1.85
2025-05-06 | 21.3 | 0 | 3.3 | 2024-05-06 | 21 | 0 | 3 | 2023-05-06 | 21.5 | 0 | 3.5 | 2022-05-06 | 16.5 | 1.5 | 0 | 2021-05-06 | 13.2 | 4.8 | 0 | 2020-05-06 | 14.3 | 3.7 | 0 | 2019-05-06 | 23.3 | 0 | 5.3 | 2018-05-06 | 16.7 | 1.3 | 0 | 2017-05-06 | 9.9 | 8.1 | 0 | 2016-05-06 | 20.9 | 0 | 2.9 | 1.94 | 1.8
2025-05-06 | 21.9 | 0 | 3.9 | 2024-05-06 | 20.4 | 0 | 2.4 | 2023-05-06 | 20.8 | 0 | 2.8 | 2022-05-06 | 16 | 2 | 0 | 2021-05-06 | 12.5 | 5.5 | 0 | 2020-05-06 | 14.6 | 3.4 | 0 | 2019-05-06 | 21.4 | 0 | 3.4 | 2018-05-06 | 15 | 3 | 0 | 2017-05-06 | 9.7 | 8.3 | 0 | 2016-05-06 | 20.6 | 0 | 2.6 | 2.22 | 1.51
2025-05-06 | 19.7 | 0 | 1.7 | 2024-05-06 | 19.6 | 0 | 1.6 | 2023-05-06 | 19.4 | 0 | 1.4 | 2022-05-06 | 15.2 | 2.8 | 0 | 2021-05-06 | 11.5 | 6.5 | 0 | 2020-05-06 | 13.7 | 4.3 | 0 | 2019-05-06 | 19.9 | 0 | 1.9 | 2018-05-06 | 14.1 | 3.9 | 0 | 2017-05-06 | 10.1 | 7.9 | 0 | 2016-05-06 | 18.7 | 0 | 0.7 | 2.54 | 0.73
2025-05-06 | 18.9 | 0 | 0.9 | 2024-05-06 | 17.4 | 0.6 | 0 | 2023-05-06 | 16.9 | 1.1 | 0 | 2022-05-06 | 13.6 | 4.4 | 0 | 2021-05-06 | 9.6 | 8.4 | 0 | 2020-05-06 | 12.1 | 5.9 | 0 | 2019-05-06 | 18.2 | 0 | 0.2 | 2018-05-06 | 13.8 | 4.2 | 0 | 2017-05-06 | 9.6 | 8.4 | 0 | 2016-05-06 | 17.9 | 0.1 | 0 | 3.31 | 0.11
2025-05-06 | 18 | 0 | 0 | 2024-05-06 | 16.3 | 1.7 | 0 | 2023-05-06 | 15.9 | 2.1 | 0 | 2022-05-06 | 10.2 | 7.8 | 0 | 2021-05-06 | 9.5 | 8.5 | 0 | 2020-05-06 | 10.7 | 7.3 | 0 | 2019-05-06 | 15.4 | 2.6 | 0 | 2018-05-06 | 13.4 | 4.6 | 0 | 2017-05-06 | 8.6 | 9.4 | 0 | 2016-05-06 | 15.9 | 2.1 | 0 | 4.61 | 0
2025-05-06 | 17.2 | 0.8 | 0 | 2024-05-06 | 15.5 | 2.5 | 0 | 2023-05-06 | 13.8 | 4.2 | 0 | 2022-05-06 | 10.6 | 7.4 | 0 | 2021-05-06 | 9 | 9 | 0 | 2020-05-06 | 9.8 | 8.2 | 0 | 2019-05-06 | 14.1 | 3.9 | 0 | 2018-05-06 | 12.9 | 5.1 | 0 | 2017-05-06 | 8 | 10 | 0 | 2016-05-06 | 14 | 4 | 0 | 5.51 | 0
2025-05-06 | 16.7 | 1.3 | 0 | 2024-05-06 | 15 | 3 | 0 | 2023-05-06 | 12.2 | 5.8 | 0 | 2022-05-06 | 9.1 | 8.9 | 0 | 2021-05-06 | 8.7 | 9.3 | 0 | 2020-05-06 | 8.7 | 9.3 | 0 | 2019-05-06 | 13.4 | 4.6 | 0 | 2018-05-06 | 12.2 | 5.8 | 0 | 2017-05-06 | 7.7 | 10.3 | 0 | 2016-05-06 | 13 | 5 | 0 | 6.33 | 0
2025-05-06 | 15.3 | 2.7 | 0 | 2024-05-06 | 13.5 | 4.5 | 0 | 2023-05-06 | 11.9 | 6.1 | 0 | 2022-05-06 | 8.3 | 9.7 | 0 | 2021-05-06 | 7.9 | 10.1 | 0 | 2020-05-06 | 5.7 | 12.3 | 0 | 2019-05-06 | 11.7 | 6.3 | 0 | 2018-05-06 | 10.7 | 7.3 | 0 | 2017-05-06 | 6.9 | 11.1 | 0 | 2016-05-06 | 12.7 | 5.3 | 0 | 7.54 | 0
2025-05-07 | 15.2 | 2.8 | 0 | 2024-05-07 | 12.9 | 5.1 | 0 | 2023-05-07 | 10 | 8 | 0 | 2022-05-07 | 6.9 | 11.1 | 0 | 2021-05-07 | 6.6 | 11.4 | 0 | 2020-05-07 | 7.5 | 10.5 | 0 | 2019-05-07 | 10.6 | 7.4 | 0 | 2018-05-07 | 9.4 | 8.6 | 0 | 2017-05-07 | 5.9 | 12.1 | 0 | 2016-05-07 | 14.8 | 3.2 | 0 | 8.02 | 0
2025-05-07 | 14.6 | 3.4 | 0 | 2024-05-07 | 11.6 | 6.4 | 0 | 2023-05-07 | 9.2 | 8.8 | 0 | 2022-05-07 | 5.7 | 12.3 | 0 | 2021-05-07 | 6.2 | 11.8 | 0 | 2020-05-07 | 4.6 | 13.4 | 0 | 2019-05-07 | 11.2 | 6.8 | 0 | 2018-05-07 | 8.4 | 9.6 | 0 | 2017-05-07 | 5.3 | 12.7 | 0 | 2016-05-07 | 14.1 | 3.9 | 0 | 8.91 | 0
2025-05-07 | 14.8 | 3.2 | 0 | 2024-05-07 | 10.6 | 7.4 | 0 | 2023-05-07 | 8.4 | 9.6 | 0 | 2022-05-07 | 4.6 | 13.4 | 0 | 2021-05-07 | 7.2 | 10.8 | 0 | 2020-05-07 | 5.6 | 12.4 | 0 | 2019-05-07 | 10.6 | 7.4 | 0 | 2018-05-07 | 7.2 | 10.8 | 0 | 2017-05-07 | 5 | 13 | 0 | 2016-05-07 | 13.5 | 4.5 | 0 | 9.25 | 0
2025-05-07 | 13.1 | 4.9 | 0 | 2024-05-07 | 9.1 | 8.9 | 0 | 2023-05-07 | 6.4 | 11.6 | 0 | 2022-05-07 | 4.3 | 13.7 | 0 | 2021-05-07 | 5.4 | 12.6 | 0 | 2020-05-07 | 2.6 | 15.4 | 0 | 2019-05-07 | 10.2 | 7.8 | 0 | 2018-05-07 | 6.4 | 11.6 | 0 | 2017-05-07 | 4.7 | 13.3 | 0 | 2016-05-07 | 12.9 | 5.1 | 0 | 10.49 | 0
2025-05-07 | 13.8 | 4.2 | 0 | 2024-05-07 | 7.5 | 10.5 | 0 | 2023-05-07 | 7.8 | 10.2 | 0 | 2022-05-07 | 3.2 | 14.8 | 0 | 2021-05-07 | 4.6 | 13.4 | 0 | 2020-05-07 | 3.2 | 14.8 | 0 | 2019-05-07 | 9.2 | 8.8 | 0 | 2018-05-07 | 5.5 | 12.5 | 0 | 2017-05-07 | 4.2 | 13.8 | 0 | 2016-05-07 | 12.4 | 5.6 | 0 | 10.86 | 0
2025-05-07 | 13.2 | 4.8 | 0 | 2024-05-07 | 6.7 | 11.3 | 0 | 2023-05-07 | 7 | 11 | 0 | 2022-05-07 | 2.7 | 15.3 | 0 | 2021-05-07 | 2.6 | 15.4 | 0 | 2020-05-07 | 4.3 | 13.7 | 0 | 2019-05-07 | 9.1 | 8.9 | 0 | 2018-05-07 | 4.9 | 13.1 | 0 | 2017-05-07 | 3.8 | 14.2 | 0 | 2016-05-07 | 11.3 | 6.7 | 0 | 11.44 | 0
2025-05-07 | 14.2 | 3.8 | 0 | 2024-05-07 | 9.7 | 8.3 | 0 | 2023-05-07 | 9.3 | 8.7 | 0 | 2022-05-07 | 4.1 | 13.9 | 0 | 2021-05-07 | 5.2 | 12.8 | 0 | 2020-05-07 | 6 | 12 | 0 | 2019-05-07 | 9.3 | 8.7 | 0 | 2018-05-07 | 5.8 | 12.2 | 0 | 2017-05-07 | 3.4 | 14.6 | 0 | 2016-05-07 | 12.6 | 5.4 | 0 | 10.04 | 0
2025-05-07 | 12.5 | 5.5 | 0 | 2024-05-07 | 12.6 | 5.4 | 0 | 2023-05-07 | 12.4 | 5.6 | 0 | 2022-05-07 | 6 | 12 | 0 | 2021-05-07 | 8 | 10 | 0 | 2020-05-07 | 8.9 | 9.1 | 0 | 2019-05-07 | 10.1 | 7.9 | 0 | 2018-05-07 | 7 | 11 | 0 | 2017-05-07 | 3.2 | 14.8 | 0 | 2016-05-07 | 13.2 | 4.8 | 0 | 8.61 | 0
2025-05-07 | 13.2 | 4.8 | 0 | 2024-05-07 | 15.5 | 2.5 | 0 | 2023-05-07 | 15.5 | 2.5 | 0 | 2022-05-07 | 7.9 | 10.1 | 0 | 2021-05-07 | 8 | 10 | 0 | 2020-05-07 | 11.5 | 6.5 | 0 | 2019-05-07 | 11.1 | 6.9 | 0 | 2018-05-07 | 8.4 | 9.6 | 0 | 2017-05-07 | 3.1 | 14.9 | 0 | 2016-05-07 | 15.6 | 2.4 | 0 | 7.02 | 0
2025-05-07 | 14.1 | 3.9 | 0 | 2024-05-07 | 16.8 | 1.2 | 0 | 2023-05-07 | 17.8 | 0.2 | 0 | 2022-05-07 | 9.4 | 8.6 | 0 | 2021-05-07 | 9.1 | 8.9 | 0 | 2020-05-07 | 13.2 | 4.8 | 0 | 2019-05-07 | 12.2 | 5.8 | 0 | 2018-05-07 | 10 | 8 | 0 | 2017-05-07 | 3.2 | 14.8 | 0 | 2016-05-07 | 17.2 | 0.8 | 0 | 5.7 | 0
2025-05-07 | 16 | 2 | 0 | 2024-05-07 | 17.9 | 0.1 | 0 | 2023-05-07 | 19.8 | 0 | 1.8 | 2022-05-07 | 10.2 | 7.8 | 0 | 2021-05-07 | 11.5 | 6.5 | 0 | 2020-05-07 | 14.2 | 3.8 | 0 | 2019-05-07 | 13.8 | 4.2 | 0 | 2018-05-07 | 11.2 | 6.8 | 0 | 2017-05-07 | 4.2 | 13.8 | 0 | 2016-05-07 | 18.5 | 0 | 0.5 | 4.5 | 0.23
2025-05-07 | 18.4 | 0 | 0.4 | 2024-05-07 | 18.2 | 0 | 0.2 | 2023-05-07 | 21.2 | 0 | 3.2 | 2022-05-07 | 11.3 | 6.7 | 0 | 2021-05-07 | 12.2 | 5.8 | 0 | 2020-05-07 | 13.4 | 4.6 | 0 | 2019-05-07 | 14.7 | 3.3 | 0 | 2018-05-07 | 11.8 | 6.2 | 0 | 2017-05-07 | 4.2 | 13.8 | 0 | 2016-05-07 | 20 | 0 | 2 | 4.04 | 0.58
2025-05-07 | 16.3 | 1.7 | 0 | 2024-05-07 | 19.1 | 0 | 1.1 | 2023-05-07 | 21.1 | 0 | 3.1 | 2022-05-07 | 12.1 | 5.9 | 0 | 2021-05-07 | 11.1 | 6.9 | 0 | 2020-05-07 | 13.7 | 4.3 | 0 | 2019-05-07 | 15 | 3 | 0 | 2018-05-07 | 12.5 | 5.5 | 0 | 2017-05-07 | 5.1 | 12.9 | 0 | 2016-05-07 | 19.5 | 0 | 1.5 | 4.02 | 0.57
2025-05-07 | 14 | 4 | 0 | 2024-05-07 | 19.9 | 0 | 1.9 | 2023-05-07 | 21 | 0 | 3 | 2022-05-07 | 13.3 | 4.7 | 0 | 2021-05-07 | 10.8 | 7.2 | 0 | 2020-05-07 | 13 | 5 | 0 | 2019-05-07 | 15.8 | 2.2 | 0 | 2018-05-07 | 14.3 | 3.7 | 0 | 2017-05-07 | 5.5 | 12.5 | 0 | 2016-05-07 | 19.5 | 0 | 1.5 | 3.93 | 0.64
2025-05-07 | 11.6 | 6.4 | 0 | 2024-05-07 | 20.7 | 0 | 2.7 | 2023-05-07 | 20.9 | 0 | 2.9 | 2022-05-07 | 14 | 4 | 0 | 2021-05-07 | 11.4 | 6.6 | 0 | 2020-05-07 | 11.8 | 6.2 | 0 | 2019-05-07 | 14 | 4 | 0 | 2018-05-07 | 13.6 | 4.4 | 0 | 2017-05-07 | 4.5 | 13.5 | 0 | 2016-05-07 | 20.6 | 0 | 2.6 | 4.51 | 0.82
2025-05-07 | 12.2 | 5.8 | 0 | 2024-05-07 | 21.2 | 0 | 3.2 | 2023-05-07 | 20.1 | 0 | 2.1 | 2022-05-07 | 14.8 | 3.2 | 0 | 2021-05-07 | 11.8 | 6.2 | 0 | 2020-05-07 | 11.3 | 6.7 | 0 | 2019-05-07 | 13.4 | 4.6 | 0 | 2018-05-07 | 15 | 3 | 0 | 2017-05-07 | 6.2 | 11.8 | 0 | 2016-05-07 | 19 | 0 | 1 | 4.13 | 0.63
2025-05-07 | 12.6 | 5.4 | 0 | 2024-05-07 | 21.4 | 0 | 3.4 | 2023-05-07 | 19.3 | 0 | 1.3 | 2022-05-07 | 15 | 3 | 0 | 2021-05-07 | 11.2 | 6.8 | 0 | 2020-05-07 | 9.2 | 8.8 | 0 | 2019-05-07 | 13.1 | 4.9 | 0 | 2018-05-07 | 15.1 | 2.9 | 0 | 2017-05-07 | 5.8 | 12.2 | 0 | 2016-05-07 | 19 | 0 | 1 | 4.4 | 0.57
2025-05-07 | 11.1 | 6.9 | 0 | 2024-05-07 | 21.1 | 0 | 3.1 | 2023-05-07 | 19 | 0 | 1 | 2022-05-07 | 14.5 | 3.5 | 0 | 2021-05-07 | 10.3 | 7.7 | 0 | 2020-05-07 | 8.4 | 9.6 | 0 | 2019-05-07 | 13.4 | 4.6 | 0 | 2018-05-07 | 14.8 | 3.2 | 0 | 2017-05-07 | 5.2 | 12.8 | 0 | 2016-05-07 | 17.9 | 0.1 | 0 | 4.84 | 0.41
2025-05-07 | 11.2 | 6.8 | 0 | 2024-05-07 | 19.8 | 0 | 1.8 | 2023-05-07 | 18 | 0 | 0 | 2022-05-07 | 13.2 | 4.8 | 0 | 2021-05-07 | 9.1 | 8.9 | 0 | 2020-05-07 | 7.3 | 10.7 | 0 | 2019-05-07 | 12.2 | 5.8 | 0 | 2018-05-07 | 14.3 | 3.7 | 0 | 2017-05-07 | 4.4 | 13.6 | 0 | 2016-05-07 | 17.5 | 0.5 | 0 | 5.48 | 0.18
2025-05-07 | 11.2 | 6.8 | 0 | 2024-05-07 | 18.3 | 0 | 0.3 | 2023-05-07 | 17 | 1 | 0 | 2022-05-07 | 10.7 | 7.3 | 0 | 2021-05-07 | 8 | 10 | 0 | 2020-05-07 | 6.8 | 11.2 | 0 | 2019-05-07 | 10.4 | 7.6 | 0 | 2018-05-07 | 13.1 | 4.9 | 0 | 2017-05-07 | 4 | 14 | 0 | 2016-05-07 | 16.2 | 1.8 | 0 | 6.46 | 0.03
2025-05-07 | 10.8 | 7.2 | 0 | 2024-05-07 | 17.6 | 0.4 | 0 | 2023-05-07 | 15.5 | 2.5 | 0 | 2022-05-07 | 9.4 | 8.6 | 0 | 2021-05-07 | 7.4 | 10.6 | 0 | 2020-05-07 | 5.3 | 12.7 | 0 | 2019-05-07 | 9.2 | 8.8 | 0 | 2018-05-07 | 10.3 | 7.7 | 0 | 2017-05-07 | 3.2 | 14.8 | 0 | 2016-05-07 | 14.9 | 3.1 | 0 | 7.64 | 0
2025-05-07 | 9.5 | 8.5 | 0 | 2024-05-07 | 15.4 | 2.6 | 0 | 2023-05-07 | 14.5 | 3.5 | 0 | 2022-05-07 | 8.3 | 9.7 | 0 | 2021-05-07 | 7.2 | 10.8 | 0 | 2020-05-07 | 4.2 | 13.8 | 0 | 2019-05-07 | 8.4 | 9.6 | 0 | 2018-05-07 | 9.6 | 8.4 | 0 | 2017-05-07 | 2.6 | 15.4 | 0 | 2016-05-07 | 13.7 | 4.3 | 0 | 8.66 | 0
2025-05-07 | 8.4 | 9.6 | 0 | 2024-05-07 | 12.8 | 5.2 | 0 | 2023-05-07 | 13.9 | 4.1 | 0 | 2022-05-07 | 6.9 | 11.1 | 0 | 2021-05-07 | 7 | 11 | 0 | 2020-05-07 | 4.1 | 13.9 | 0 | 2019-05-07 | 7.4 | 10.6 | 0 | 2018-05-07 | 7.6 | 10.4 | 0 | 2017-05-07 | 2.1 | 15.9 | 0 | 2016-05-07 | 12.9 | 5.1 | 0 | 9.69 | 0
2025-05-07 | 7.8 | 10.2 | 0 | 2024-05-07 | 15 | 3 | 0 | 2023-05-07 | 11.2 | 6.8 | 0 | 2022-05-07 | 5.5 | 12.5 | 0 | 2021-05-07 | 6.9 | 11.1 | 0 | 2020-05-07 | 3.3 | 14.7 | 0 | 2019-05-07 | 6.6 | 11.4 | 0 | 2018-05-07 | 8.9 | 9.1 | 0 | 2017-05-07 | 1.2 | 16.8 | 0 | 2016-05-07 | 11.4 | 6.6 | 0 | 10.22 | 0
2025-05-08 | 7.7 | 10.3 | 0 | 2024-05-08 | 12.3 | 5.7 | 0 | 2023-05-08 | 10.4 | 7.6 | 0 | 2022-05-08 | 4.2 | 13.8 | 0 | 2021-05-08 | 6.8 | 11.2 | 0 | 2020-05-08 | 1.9 | 16.1 | 0 | 2019-05-08 | 5.6 | 12.4 | 0 | 2018-05-08 | 7.6 | 10.4 | 0 | 2017-05-08 | 1.1 | 16.9 | 0 | 2016-05-08 | 10.9 | 7.1 | 0 | 11.15 | 0
2025-05-08 | 7.5 | 10.5 | 0 | 2024-05-08 | 12.7 | 5.3 | 0 | 2023-05-08 | 9 | 9 | 0 | 2022-05-08 | 3.2 | 14.8 | 0 | 2021-05-08 | 6.9 | 11.1 | 0 | 2020-05-08 | 0.9 | 17.1 | 0 | 2019-05-08 | 4.8 | 13.2 | 0 | 2018-05-08 | 7 | 11 | 0 | 2017-05-08 | 0.3 | 17.7 | 0 | 2016-05-08 | 10.9 | 7.1 | 0 | 11.68 | 0
2025-05-08 | 6.7 | 11.3 | 0 | 2024-05-08 | 14.2 | 3.8 | 0 | 2023-05-08 | 10.5 | 7.5 | 0 | 2022-05-08 | 2.7 | 15.3 | 0 | 2021-05-08 | 6.6 | 11.4 | 0 | 2020-05-08 | 0 | 18 | 0 | 2019-05-08 | 3.6 | 14.4 | 0 | 2018-05-08 | 7 | 11 | 0 | 2017-05-08 | 0 | 18 | 0 | 2016-05-08 | 9.2 | 8.8 | 0 | 11.95 | 0
2025-05-08 | 6 | 12 | 0 | 2024-05-08 | 12.6 | 5.4 | 0 | 2023-05-08 | 7 | 11 | 0 | 2022-05-08 | 2.2 | 15.8 | 0 | 2021-05-08 | 6.5 | 11.5 | 0 | 2020-05-08 | 0.2 | 17.8 | 0 | 2019-05-08 | 2.1 | 15.9 | 0 | 2018-05-08 | 6.3 | 11.7 | 0 | 2017-05-08 | 0.1 | 17.9 | 0 | 2016-05-08 | 4.7 | 13.3 | 0 | 13.23 | 0
2025-05-08 | 5.7 | 12.3 | 0 | 2024-05-08 | 11.7 | 6.3 | 0 | 2023-05-08 | 9.3 | 8.7 | 0 | 2022-05-08 | 2 | 16 | 0 | 2021-05-08 | 6.6 | 11.4 | 0 | 2020-05-08 | 0.6 | 17.4 | 0 | 2019-05-08 | 1.8 | 16.2 | 0 | 2018-05-08 | 5.7 | 12.3 | 0 | 2017-05-08 | 0.5 | 17.5 | 0 | 2016-05-08 | 3.5 | 14.5 | 0 | 13.26 | 0
2025-05-08 | 5.2 | 12.8 | 0 | 2024-05-08 | 10.8 | 7.2 | 0 | 2023-05-08 | 9.4 | 8.6 | 0 | 2022-05-08 | 1.4 | 16.6 | 0 | 2021-05-08 | 6.8 | 11.2 | 0 | 2020-05-08 | 0.8 | 17.2 | 0 | 2019-05-08 | 1.9 | 16.1 | 0 | 2018-05-08 | 5.1 | 12.9 | 0 | 2017-05-08 | 0.5 | 17.5 | 0 | 2016-05-08 | 2.8 | 15.2 | 0 | 13.53 | 0
2025-05-08 | 5.2 | 12.8 | 0 | 2024-05-08 | 10.1 | 7.9 | 0 | 2023-05-08 | 10 | 8 | 0 | 2022-05-08 | 6.1 | 11.9 | 0 | 2021-05-08 | 6.6 | 11.4 | 0 | 2020-05-08 | 0.7 | 17.3 | 0 | 2019-05-08 | 3.1 | 14.9 | 0 | 2018-05-08 | 6.5 | 11.5 | 0 | 2017-05-08 | 0.9 | 17.1 | 0 | 2016-05-08 | 2.7 | 15.3 | 0 | 12.81 | 0
2025-05-08 | 5.4 | 12.6 | 0 | 2024-05-08 | 9.8 | 8.2 | 0 | 2023-05-08 | 10.9 | 7.1 | 0 | 2022-05-08 | 7.7 | 10.3 | 0 | 2021-05-08 | 6.5 | 11.5 | 0 | 2020-05-08 | 0.3 | 17.7 | 0 | 2019-05-08 | 4.4 | 13.6 | 0 | 2018-05-08 | 9.7 | 8.3 | 0 | 2017-05-08 | 1 | 17 | 0 | 2016-05-08 | 3 | 15 | 0 | 12.13 | 0
2025-05-08 | 5.9 | 12.1 | 0 | 2024-05-08 | 8.8 | 9.2 | 0 | 2023-05-08 | 12.1 | 5.9 | 0 | 2022-05-08 | 9.8 | 8.2 | 0 | 2021-05-08 | 6.7 | 11.3 | 0 | 2020-05-08 | 0.1 | 17.9 | 0 | 2019-05-08 | 5.8 | 12.2 | 0 | 2018-05-08 | 12.8 | 5.2 | 0 | 2017-05-08 | 1.1 | 16.9 | 0 | 2016-05-08 | 4.8 | 13.2 | 0 | 11.21 | 0
2025-05-08 | 6.8 | 11.2 | 0 | 2024-05-08 | 8.2 | 9.8 | 0 | 2023-05-08 | 13 | 5 | 0 | 2022-05-08 | 12 | 6 | 0 | 2021-05-08 | 7.3 | 10.7 | 0 | 2020-05-08 | 0.4 | 17.6 | 0 | 2019-05-08 | 7.5 | 10.5 | 0 | 2018-05-08 | 16.6 | 1.4 | 0 | 2017-05-08 | 1.6 | 16.4 | 0 | 2016-05-08 | 5.3 | 12.7 | 0 | 10.13 | 0
2025-05-08 | 7.6 | 10.4 | 0 | 2024-05-08 | 8.1 | 9.9 | 0 | 2023-05-08 | 14.2 | 3.8 | 0 | 2022-05-08 | 13.9 | 4.1 | 0 | 2021-05-08 | 7.8 | 10.2 | 0 | 2020-05-08 | 2 | 16 | 0 | 2019-05-08 | 8.7 | 9.3 | 0 | 2018-05-08 | 18.9 | 0 | 0.9 | 2017-05-08 | 2.5 | 15.5 | 0 | 2016-05-08 | 6.2 | 11.8 | 0 | 9.1 | 0.09
2025-05-08 | 8.9 | 9.1 | 0 | 2024-05-08 | 10.9 | 7.1 | 0 | 2023-05-08 | 14.1 | 3.9 | 0 | 2022-05-08 | 15.8 | 2.2 | 0 | 2021-05-08 | 8.2 | 9.8 | 0 | 2020-05-08 | 1.7 | 16.3 | 0 | 2019-05-08 | 10.1 | 7.9 | 0 | 2018-05-08 | 19.6 | 0 | 1.6 | 2017-05-08 | 2.5 | 15.5 | 0 | 2016-05-08 | 6 | 12 | 0 | 8.38 | 0.16
2025-05-08 | 10 | 8 | 0 | 2024-05-08 | 11.3 | 6.7 | 0 | 2023-05-08 | 15.3 | 2.7 | 0 | 2022-05-08 | 16.8 | 1.2 | 0 | 2021-05-08 | 8.5 | 9.5 | 0 | 2020-05-08 | 2.9 | 15.1 | 0 | 2019-05-08 | 10.5 | 7.5 | 0 | 2018-05-08 | 20.8 | 0 | 2.8 | 2017-05-08 | 2.7 | 15.3 | 0 | 2016-05-08 | 7.2 | 10.8 | 0 | 7.68 | 0.28
2025-05-08 | 10.6 | 7.4 | 0 | 2024-05-08 | 10.1 | 7.9 | 0 | 2023-05-08 | 15.6 | 2.4 | 0 | 2022-05-08 | 17.4 | 0.6 | 0 | 2021-05-08 | 8.4 | 9.6 | 0 | 2020-05-08 | 3 | 15 | 0 | 2019-05-08 | 11.7 | 6.3 | 0 | 2018-05-08 | 21.4 | 0 | 3.4 | 2017-05-08 | 2.2 | 15.8 | 0 | 2016-05-08 | 7 | 11 | 0 | 7.6 | 0.34
2025-05-08 | 10.6 | 7.4 | 0 | 2024-05-08 | 10.2 | 7.8 | 0 | 2023-05-08 | 16.4 | 1.6 | 0 | 2022-05-08 | 18.4 | 0 | 0.4 | 2021-05-08 | 9 | 9 | 0 | 2020-05-08 | 3.9 | 14.1 | 0 | 2019-05-08 | 12.9 | 5.1 | 0 | 2018-05-08 | 22.3 | 0 | 4.3 | 2017-05-08 | 3.9 | 14.1 | 0 | 2016-05-08 | 7.5 | 10.5 | 0 | 6.96 | 0.47
2025-05-08 | 11 | 7 | 0 | 2024-05-08 | 10.1 | 7.9 | 0 | 2023-05-08 | 17 | 1 | 0 | 2022-05-08 | 19 | 0 | 1 | 2021-05-08 | 9 | 9 | 0 | 2020-05-08 | 4.5 | 13.5 | 0 | 2019-05-08 | 13.2 | 4.8 | 0 | 2018-05-08 | 22.4 | 0 | 4.4 | 2017-05-08 | 4.3 | 13.7 | 0 | 2016-05-08 | 8.3 | 9.7 | 0 | 6.66 | 0.54
2025-05-08 | 11.9 | 6.1 | 0 | 2024-05-08 | 10.1 | 7.9 | 0 | 2023-05-08 | 16.6 | 1.4 | 0 | 2022-05-08 | 18.5 | 0 | 0.5 | 2021-05-08 | 8.8 | 9.2 | 0 | 2020-05-08 | 5.5 | 12.5 | 0 | 2019-05-08 | 13.2 | 4.8 | 0 | 2018-05-08 | 22.9 | 0 | 4.9 | 2017-05-08 | 4.3 | 13.7 | 0 | 2016-05-08 | 8.4 | 9.6 | 0 | 6.52 | 0.54
2025-05-08 | 11.4 | 6.6 | 0 | 2024-05-08 | 10.4 | 7.6 | 0 | 2023-05-08 | 15.9 | 2.1 | 0 | 2022-05-08 | 18.1 | 0 | 0.1 | 2021-05-08 | 8.4 | 9.6 | 0 | 2020-05-08 | 4.9 | 13.1 | 0 | 2019-05-08 | 13 | 5 | 0 | 2018-05-08 | 22.3 | 0 | 4.3 | 2017-05-08 | 3.8 | 14.2 | 0 | 2016-05-08 | 7.9 | 10.1 | 0 | 6.83 | 0.44
2025-05-08 | 10.7 | 7.3 | 0 | 2024-05-08 | 10.4 | 7.6 | 0 | 2023-05-08 | 15.1 | 2.9 | 0 | 2022-05-08 | 17 | 1 | 0 | 2021-05-08 | 8.1 | 9.9 | 0 | 2020-05-08 | 4.6 | 13.4 | 0 | 2019-05-08 | 12.6 | 5.4 | 0 | 2018-05-08 | 21.4 | 0 | 3.4 | 2017-05-08 | 3.7 | 14.3 | 0 | 2016-05-08 | 6.9 | 11.1 | 0 | 7.29 | 0.34
2025-05-08 | 9.3 | 8.7 | 0 | 2024-05-08 | 10.4 | 7.6 | 0 | 2023-05-08 | 13.5 | 4.5 | 0 | 2022-05-08 | 14 | 4 | 0 | 2021-05-08 | 7.6 | 10.4 | 0 | 2020-05-08 | 3.2 | 14.8 | 0 | 2019-05-08 | 10.8 | 7.2 | 0 | 2018-05-08 | 19.5 | 0 | 1.5 | 2017-05-08 | 3 | 15 | 0 | 2016-05-08 | 5.2 | 12.8 | 0 | 8.5 | 0.15
2025-05-08 | 7.8 | 10.2 | 0 | 2024-05-08 | 10.3 | 7.7 | 0 | 2023-05-08 | 12.3 | 5.7 | 0 | 2022-05-08 | 12.1 | 5.9 | 0 | 2021-05-08 | 7.1 | 10.9 | 0 | 2020-05-08 | 1.8 | 16.2 | 0 | 2019-05-08 | 10.1 | 7.9 | 0 | 2018-05-08 | 17.6 | 0.4 | 0 | 2017-05-08 | 1.3 | 16.7 | 0 | 2016-05-08 | 4.6 | 13.4 | 0 | 9.5 | 0
2025-05-08 | 7.9 | 10.1 | 0 | 2024-05-08 | 10.1 | 7.9 | 0 | 2023-05-08 | 10.7 | 7.3 | 0 | 2022-05-08 | 11.2 | 6.8 | 0 | 2021-05-08 | 6.6 | 11.4 | 0 | 2020-05-08 | 1 | 17 | 0 | 2019-05-08 | 9.3 | 8.7 | 0 | 2018-05-08 | 16.8 | 1.2 | 0 | 2017-05-08 | 0.4 | 17.6 | 0 | 2016-05-08 | 4 | 14 | 0 | 10.2 | 0
2025-05-08 | 6.5 | 11.5 | 0 | 2024-05-08 | 9.8 | 8.2 | 0 | 2023-05-08 | 10.1 | 7.9 | 0 | 2022-05-08 | 8.9 | 9.1 | 0 | 2021-05-08 | 6.5 | 11.5 | 0 | 2020-05-08 | 0.9 | 17.1 | 0 | 2019-05-08 | 6.8 | 11.2 | 0 | 2018-05-08 | 15.4 | 2.6 | 0 | 2017-05-08 | 0.7 | 17.3 | 0 | 2016-05-08 | 3.6 | 14.4 | 0 | 11.08 | 0
2025-05-08 | 5.3 | 12.7 | 0 | 2024-05-08 | 9.6 | 8.4 | 0 | 2023-05-08 | 9.1 | 8.9 | 0 | 2022-05-08 | 8.3 | 9.7 | 0 | 2021-05-08 | 6.4 | 11.6 | 0 | 2020-05-08 | 0.9 | 17.1 | 0 | 2019-05-08 | 5.5 | 12.5 | 0 | 2018-05-08 | 14 | 4 | 0 | 2017-05-08 | 0.2 | 17.8 | 0 | 2016-05-08 | 3.6 | 14.4 | 0 | 11.71 | 0
2025-05-09 | 6.3 | 11.7 | 0 | 2024-05-09 | 8.7 | 9.3 | 0 | 2023-05-09 | 8.5 | 9.5 | 0 | 2022-05-09 | 5.5 | 12.5 | 0 | 2021-05-09 | 6 | 12 | 0 | 2020-05-09 | -0.2 | 18.2 | 0 | 2019-05-09 | 6.3 | 11.7 | 0 | 2018-05-09 | 13 | 5 | 0 | 2017-05-09 | -0.4 | 18.4 | 0 | 2016-05-09 | 2.8 | 15.2 | 0 | 12.35 | 0
2025-05-09 | 6.7 | 11.3 | 0 | 2024-05-09 | 6.9 | 11.1 | 0 | 2023-05-09 | 7.6 | 10.4 | 0 | 2022-05-09 | 6.5 | 11.5 | 0 | 2021-05-09 | 5.4 | 12.6 | 0 | 2020-05-09 | -0.4 | 18.4 | 0 | 2019-05-09 | 5.6 | 12.4 | 0 | 2018-05-09 | 12.9 | 5.1 | 0 | 2017-05-09 | -1.2 | 19.2 | 0 | 2016-05-09 | 1.5 | 16.5 | 0 | 12.85 | 0
2025-05-09 | 6.8 | 11.2 | 0 | 2024-05-09 | 5.8 | 12.2 | 0 | 2023-05-09 | 6.9 | 11.1 | 0 | 2022-05-09 | 7.2 | 10.8 | 0 | 2021-05-09 | 5.3 | 12.7 | 0 | 2020-05-09 | -1.2 | 19.2 | 0 | 2019-05-09 | 6 | 12 | 0 | 2018-05-09 | 12.7 | 5.3 | 0 | 2017-05-09 | 0.1 | 17.9 | 0 | 2016-05-09 | 0.4 | 17.6 | 0 | 13 | 0
2025-05-09 | 6.9 | 11.1 | 0 | 2024-05-09 | 5.8 | 12.2 | 0 | 2023-05-09 | 5.6 | 12.4 | 0 | 2022-05-09 | 3.1 | 14.9 | 0 | 2021-05-09 | 5.2 | 12.8 | 0 | 2020-05-09 | -2.5 | 20.5 | 0 | 2019-05-09 | 6 | 12 | 0 | 2018-05-09 | 11.6 | 6.4 | 0 | 2017-05-09 | -0.5 | 18.5 | 0 | 2016-05-09 | -0.2 | 18.2 | 0 | 13.9 | 0
2025-05-09 | 6.7 | 11.3 | 0 | 2024-05-09 | 4.5 | 13.5 | 0 | 2023-05-09 | 5.6 | 12.4 | 0 | 2022-05-09 | 5.4 | 12.6 | 0 | 2021-05-09 | 5 | 13 | 0 | 2020-05-09 | -2.8 | 20.8 | 0 | 2019-05-09 | 5.6 | 12.4 | 0 | 2018-05-09 | 6.4 | 11.6 | 0 | 2017-05-09 | -1.1 | 19.1 | 0 | 2016-05-09 | -1.2 | 19.2 | 0 | 14.59 | 0
2025-05-09 | 7 | 11 | 0 | 2024-05-09 | 4.2 | 13.8 | 0 | 2023-05-09 | 5.2 | 12.8 | 0 | 2022-05-09 | 3.8 | 14.2 | 0 | 2021-05-09 | 4.9 | 13.1 | 0 | 2020-05-09 | -3 | 21 | 0 | 2019-05-09 | 4.9 | 13.1 | 0 | 2018-05-09 | 8.8 | 9.2 | 0 | 2017-05-09 | -0.7 | 18.7 | 0 | 2016-05-09 | -0.8 | 18.8 | 0 | 14.57 | 0
2025-05-09 | 7.3 | 10.7 | 0 | 2024-05-09 | 6.9 | 11.1 | 0 | 2023-05-09 | 7.2 | 10.8 | 0 | 2022-05-09 | 9 | 9 | 0 | 2021-05-09 | 4.8 | 13.2 | 0 | 2020-05-09 | -2.2 | 20.2 | 0 | 2019-05-09 | 4.9 | 13.1 | 0 | 2018-05-09 | 10.9 | 7.1 | 0 | 2017-05-09 | 0.7 | 17.3 | 0 | 2016-05-09 | 2.1 | 15.9 | 0 | 12.84 | 0
2025-05-09 | 7.6 | 10.4 | 0 | 2024-05-09 | 9.6 | 8.4 | 0 | 2023-05-09 | 9.6 | 8.4 | 0 | 2022-05-09 | 10.7 | 7.3 | 0 | 2021-05-09 | 6.6 | 11.4 | 0 | 2020-05-09 | -0.4 | 18.4 | 0 | 2019-05-09 | 5.1 | 12.9 | 0 | 2018-05-09 | 13.1 | 4.9 | 0 | 2017-05-09 | 1.7 | 16.3 | 0 | 2016-05-09 | 3.8 | 14.2 | 0 | 11.26 | 0
2025-05-09 | 8.1 | 9.9 | 0 | 2024-05-09 | 11.7 | 6.3 | 0 | 2023-05-09 | 10.7 | 7.3 | 0 | 2022-05-09 | 13.3 | 4.7 | 0 | 2021-05-09 | 8.5 | 9.5 | 0 | 2020-05-09 | -0.4 | 18.4 | 0 | 2019-05-09 | 5.4 | 12.6 | 0 | 2018-05-09 | 17 | 1 | 0 | 2017-05-09 | 2.3 | 15.7 | 0 | 2016-05-09 | 5 | 13 | 0 | 9.84 | 0
2025-05-09 | 8.8 | 9.2 | 0 | 2024-05-09 | 13 | 5 | 0 | 2023-05-09 | 12.6 | 5.4 | 0 | 2022-05-09 | 15.5 | 2.5 | 0 | 2021-05-09 | 9.9 | 8.1 | 0 | 2020-05-09 | 0.5 | 17.5 | 0 | 2019-05-09 | 6.8 | 11.2 | 0 | 2018-05-09 | 19.6 | 0 | 1.6 | 2017-05-09 | 3 | 15 | 0 | 2016-05-09 | 6.4 | 11.6 | 0 | 8.55 | 0.16
2025-05-09 | 9.4 | 8.6 | 0 | 2024-05-09 | 13.9 | 4.1 | 0 | 2023-05-09 | 13.3 | 4.7 | 0 | 2022-05-09 | 17.7 | 0.3 | 0 | 2021-05-09 | 12.4 | 5.6 | 0 | 2020-05-09 | 2.1 | 15.9 | 0 | 2019-05-09 | 8.2 | 9.8 | 0 | 2018-05-09 | 21.3 | 0 | 3.3 | 2017-05-09 | 3.7 | 14.3 | 0 | 2016-05-09 | 8.2 | 9.8 | 0 | 7.31 | 0.33
2025-05-09 | 9.6 | 8.4 | 0 | 2024-05-09 | 14.9 | 3.1 | 0 | 2023-05-09 | 14.1 | 3.9 | 0 | 2022-05-09 | 19.9 | 0 | 1.9 | 2021-05-09 | 12.5 | 5.5 | 0 | 2020-05-09 | 2 | 16 | 0 | 2019-05-09 | 10.3 | 7.7 | 0 | 2018-05-09 | 22.9 | 0 | 4.9 | 2017-05-09 | 4.1 | 13.9 | 0 | 2016-05-09 | 8.4 | 9.6 | 0 | 6.81 | 0.68
2025-05-09 | 10.7 | 7.3 | 0 | 2024-05-09 | 15.5 | 2.5 | 0 | 2023-05-09 | 14.7 | 3.3 | 0 | 2022-05-09 | 21.9 | 0 | 3.9 | 2021-05-09 | 13.8 | 4.2 | 0 | 2020-05-09 | 3.8 | 14.2 | 0 | 2019-05-09 | 11.6 | 6.4 | 0 | 2018-05-09 | 24.5 | 0 | 6.5 | 2017-05-09 | 4.2 | 13.8 | 0 | 2016-05-09 | 10.1 | 7.9 | 0 | 5.96 | 1.04
2025-05-09 | 11.5 | 6.5 | 0 | 2024-05-09 | 14.8 | 3.2 | 0 | 2023-05-09 | 16.1 | 1.9 | 0 | 2022-05-09 | 22.3 | 0 | 4.3 | 2021-05-09 | 10.6 | 7.4 | 0 | 2020-05-09 | 3.3 | 14.7 | 0 | 2019-05-09 | 12.5 | 5.5 | 0 | 2018-05-09 | 25.3 | 0 | 7.3 | 2017-05-09 | 4.6 | 13.4 | 0 | 2016-05-09 | 10.5 | 7.5 | 0 | 6.01 | 1.16
2025-05-09 | 12 | 6 | 0 | 2024-05-09 | 14 | 4 | 0 | 2023-05-09 | 15.7 | 2.3 | 0 | 2022-05-09 | 22.5 | 0 | 4.5 | 2021-05-09 | 11.7 | 6.3 | 0 | 2020-05-09 | 4.7 | 13.3 | 0 | 2019-05-09 | 13.1 | 4.9 | 0 | 2018-05-09 | 25.8 | 0 | 7.8 | 2017-05-09 | 5.9 | 12.1 | 0 | 2016-05-09 | 10.5 | 7.5 | 0 | 5.64 | 1.23
2025-05-09 | 11.5 | 6.5 | 0 | 2024-05-09 | 15.1 | 2.9 | 0 | 2023-05-09 | 16.7 | 1.3 | 0 | 2022-05-09 | 22.5 | 0 | 4.5 | 2021-05-09 | 11.9 | 6.1 | 0 | 2020-05-09 | 3.4 | 14.6 | 0 | 2019-05-09 | 13.4 | 4.6 | 0 | 2018-05-09 | 26.5 | 0 | 8.5 | 2017-05-09 | 5.8 | 12.2 | 0 | 2016-05-09 | 12.4 | 5.6 | 0 | 5.38 | 1.3
2025-05-09 | 10.1 | 7.9 | 0 | 2024-05-09 | 17 | 1 | 0 | 2023-05-09 | 17.3 | 0.7 | 0 | 2022-05-09 | 22.4 | 0 | 4.4 | 2021-05-09 | 12.9 | 5.1 | 0 | 2020-05-09 | 4.8 | 13.2 | 0 | 2019-05-09 | 11.8 | 6.2 | 0 | 2018-05-09 | 25.1 | 0 | 7.1 | 2017-05-09 | 5.8 | 12.2 | 0 | 2016-05-09 | 12.3 | 5.7 | 0 | 5.2 | 1.15
2025-05-09 | 9.9 | 8.1 | 0 | 2024-05-09 | 15.4 | 2.6 | 0 | 2023-05-09 | 16.8 | 1.2 | 0 | 2022-05-09 | 22 | 0 | 4 | 2021-05-09 | 13 | 5 | 0 | 2020-05-09 | 4.5 | 13.5 | 0 | 2019-05-09 | 11.9 | 6.1 | 0 | 2018-05-09 | 26.3 | 0 | 8.3 | 2017-05-09 | 5.9 | 12.1 | 0 | 2016-05-09 | 12.3 | 5.7 | 0 | 5.43 | 1.23
2025-05-09 | 8.3 | 9.7 | 0 | 2024-05-09 | 14.5 | 3.5 | 0 | 2023-05-09 | 16.5 | 1.5 | 0 | 2022-05-09 | 21 | 0 | 3 | 2021-05-09 | 12.3 | 5.7 | 0 | 2020-05-09 | 3.9 | 14.1 | 0 | 2019-05-09 | 10.5 | 7.5 | 0 | 2018-05-09 | 25.4 | 0 | 7.4 | 2017-05-09 | 5.7 | 12.3 | 0 | 2016-05-09 | 11.6 | 6.4 | 0 | 6.07 | 1.04
2025-05-09 | 7.9 | 10.1 | 0 | 2024-05-09 | 12.7 | 5.3 | 0 | 2023-05-09 | 14 | 4 | 0 | 2022-05-09 | 18.1 | 0 | 0.1 | 2021-05-09 | 11 | 7 | 0 | 2020-05-09 | 3.6 | 14.4 | 0 | 2019-05-09 | 11.5 | 6.5 | 0 | 2018-05-09 | 23 | 0 | 5 | 2017-05-09 | 5.3 | 12.7 | 0 | 2016-05-09 | 10.4 | 7.6 | 0 | 6.76 | 0.51
2025-05-09 | 7.7 | 10.3 | 0 | 2024-05-09 | 11.7 | 6.3 | 0 | 2023-05-09 | 12.7 | 5.3 | 0 | 2022-05-09 | 15 | 3 | 0 | 2021-05-09 | 10.2 | 7.8 | 0 | 2020-05-09 | 3.5 | 14.5 | 0 | 2019-05-09 | 11 | 7 | 0 | 2018-05-09 | 20.3 | 0 | 2.3 | 2017-05-09 | 4.5 | 13.5 | 0 | 2016-05-09 | 8.5 | 9.5 | 0 | 7.72 | 0.23
2025-05-09 | 7.7 | 10.3 | 0 | 2024-05-09 | 9.9 | 8.1 | 0 | 2023-05-09 | 10.3 | 7.7 | 0 | 2022-05-09 | 15.2 | 2.8 | 0 | 2021-05-09 | 9.4 | 8.6 | 0 | 2020-05-09 | 3.2 | 14.8 | 0 | 2019-05-09 | 9.8 | 8.2 | 0 | 2018-05-09 | 17.9 | 0.1 | 0 | 2017-05-09 | 4.7 | 13.3 | 0 | 2016-05-09 | 7.1 | 10.9 | 0 | 8.48 | 0
2025-05-09 | 7.8 | 10.2 | 0 | 2024-05-09 | 8.5 | 9.5 | 0 | 2023-05-09 | 9.8 | 8.2 | 0 | 2022-05-09 | 14.3 | 3.7 | 0 | 2021-05-09 | 8.4 | 9.6 | 0 | 2020-05-09 | 2.8 | 15.2 | 0 | 2019-05-09 | 9.2 | 8.8 | 0 | 2018-05-09 | 18.9 | 0 | 0.9 | 2017-05-09 | 4.6 | 13.4 | 0 | 2016-05-09 | 7 | 11 | 0 | 8.96 | 0.09
2025-05-09 | 8 | 10 | 0 | 2024-05-09 | 7.2 | 10.8 | 0 | 2023-05-09 | 10.1 | 7.9 | 0 | 2022-05-09 | 13.6 | 4.4 | 0 | 2021-05-09 | 8 | 10 | 0 | 2020-05-09 | 1.8 | 16.2 | 0 | 2019-05-09 | 9.2 | 8.8 | 0 | 2018-05-09 | 19 | 0 | 1 | 2017-05-09 | 2.1 | 15.9 | 0 | 2016-05-09 | 5.5 | 12.5 | 0 | 9.65 | 0.1
2025-05-10 | 8 | 10 | 0 | 2024-05-10 | 6.7 | 11.3 | 0 | 2023-05-10 | 6.6 | 11.4 | 0 | 2022-05-10 | 10.1 | 7.9 | 0 | 2021-05-10 | 6.1 | 11.9 | 0 | 2020-05-10 | 1.4 | 16.6 | 0 | 2019-05-10 | 9.5 | 8.5 | 0 | 2018-05-10 | 17.8 | 0.2 | 0 | 2017-05-10 | 4 | 14 | 0 | 2016-05-10 | 4.7 | 13.3 | 0 | 10.51 | 0
2025-05-10 | 7.6 | 10.4 | 0 | 2024-05-10 | 5.7 | 12.3 | 0 | 2023-05-10 | 5.2 | 12.8 | 0 | 2022-05-10 | 12.2 | 5.8 | 0 | 2021-05-10 | 5.4 | 12.6 | 0 | 2020-05-10 | 1.7 | 16.3 | 0 | 2019-05-10 | 10.5 | 7.5 | 0 | 2018-05-10 | 18.3 | 0 | 0.3 | 2017-05-10 | 3.5 | 14.5 | 0 | 2016-05-10 | 4.1 | 13.9 | 0 | 10.61 | 0.03
2025-05-10 | 7.7 | 10.3 | 0 | 2024-05-10 | 5.4 | 12.6 | 0 | 2023-05-10 | 5 | 13 | 0 | 2022-05-10 | 11.9 | 6.1 | 0 | 2021-05-10 | 5.1 | 12.9 | 0 | 2020-05-10 | 1.3 | 16.7 | 0 | 2019-05-10 | 11.8 | 6.2 | 0 | 2018-05-10 | 18.2 | 0 | 0.2 | 2017-05-10 | 3.5 | 14.5 | 0 | 2016-05-10 | 3.2 | 14.8 | 0 | 10.71 | 0.02
2025-05-10 | 7.6 | 10.4 | 0 | 2024-05-10 | 5.3 | 12.7 | 0 | 2023-05-10 | 5.3 | 12.7 | 0 | 2022-05-10 | 10.7 | 7.3 | 0 | 2021-05-10 | 5.2 | 12.8 | 0 | 2020-05-10 | -0.2 | 18.2 | 0 | 2019-05-10 | 12.3 | 5.7 | 0 | 2018-05-10 | 18.8 | 0 | 0.8 | 2017-05-10 | 2 | 16 | 0 | 2016-05-10 | 3 | 15 | 0 | 11.08 | 0.08
2025-05-10 | 7.2 | 10.8 | 0 | 2024-05-10 | 5.6 | 12.4 | 0 | 2023-05-10 | 5.1 | 12.9 | 0 | 2022-05-10 | 8.3 | 9.7 | 0 | 2021-05-10 | 4.9 | 13.1 | 0 | 2020-05-10 | 0.2 | 17.8 | 0 | 2019-05-10 | 12.5 | 5.5 | 0 | 2018-05-10 | 18.6 | 0 | 0.6 | 2017-05-10 | 1.3 | 16.7 | 0 | 2016-05-10 | 3.2 | 14.8 | 0 | 11.37 | 0.06
2025-05-10 | 6.8 | 11.2 | 0 | 2024-05-10 | 6.1 | 11.9 | 0 | 2023-05-10 | 4 | 14 | 0 | 2022-05-10 | 8.8 | 9.2 | 0 | 2021-05-10 | 4.8 | 13.2 | 0 | 2020-05-10 | 0.8 | 17.2 | 0 | 2019-05-10 | 12.5 | 5.5 | 0 | 2018-05-10 | 17.9 | 0.1 | 0 | 2017-05-10 | 1.4 | 16.6 | 0 | 2016-05-10 | 0.7 | 17.3 | 0 | 11.62 | 0
2025-05-10 | 7.8 | 10.2 | 0 | 2024-05-10 | 6.8 | 11.2 | 0 | 2023-05-10 | 5.3 | 12.7 | 0 | 2022-05-10 | 6 | 12 | 0 | 2021-05-10 | 5.8 | 12.2 | 0 | 2020-05-10 | 1.4 | 16.6 | 0 | 2019-05-10 | 12.9 | 5.1 | 0 | 2018-05-10 | 18.8 | 0 | 0.8 | 2017-05-10 | 4.5 | 13.5 | 0 | 2016-05-10 | 5.4 | 12.6 | 0 | 10.61 | 0.08
2025-05-10 | 10.1 | 7.9 | 0 | 2024-05-10 | 8 | 10 | 0 | 2023-05-10 | 10 | 8 | 0 | 2022-05-10 | 12.7 | 5.3 | 0 | 2021-05-10 | 8.6 | 9.4 | 0 | 2020-05-10 | 3.3 | 14.7 | 0 | 2019-05-10 | 13 | 5 | 0 | 2018-05-10 | 17.9 | 0.1 | 0 | 2017-05-10 | 6.6 | 11.4 | 0 | 2016-05-10 | 7.8 | 10.2 | 0 | 8.2 | 0
2025-05-10 | 12.5 | 5.5 | 0 | 2024-05-10 | 10.4 | 7.6 | 0 | 2023-05-10 | 13.2 | 4.8 | 0 | 2022-05-10 | 16 | 2 | 0 | 2021-05-10 | 10.2 | 7.8 | 0 | 2020-05-10 | 3.9 | 14.1 | 0 | 2019-05-10 | 12.9 | 5.1 | 0 | 2018-05-10 | 15.3 | 2.7 | 0 | 2017-05-10 | 8.1 | 9.9 | 0 | 2016-05-10 | 10 | 8 | 0 | 6.75 | 0
2025-05-10 | 14.5 | 3.5 | 0 | 2024-05-10 | 12.2 | 5.8 | 0 | 2023-05-10 | 15.2 | 2.8 | 0 | 2022-05-10 | 18.1 | 0 | 0.1 | 2021-05-10 | 12.2 | 5.8 | 0 | 2020-05-10 | 4.7 | 13.3 | 0 | 2019-05-10 | 13.2 | 4.8 | 0 | 2018-05-10 | 16.4 | 1.6 | 0 | 2017-05-10 | 9.5 | 8.5 | 0 | 2016-05-10 | 11.8 | 6.2 | 0 | 5.23 | 0.01
2025-05-10 | 16.4 | 1.6 | 0 | 2024-05-10 | 13.9 | 4.1 | 0 | 2023-05-10 | 17.6 | 0.4 | 0 | 2022-05-10 | 19.6 | 0 | 1.6 | 2021-05-10 | 14.2 | 3.8 | 0 | 2020-05-10 | 6 | 12 | 0 | 2019-05-10 | 13.7 | 4.3 | 0 | 2018-05-10 | 16.7 | 1.3 | 0 | 2017-05-10 | 9.9 | 8.1 | 0 | 2016-05-10 | 13.1 | 4.9 | 0 | 4.05 | 0.16
2025-05-10 | 18 | 0 | 0 | 2024-05-10 | 15.3 | 2.7 | 0 | 2023-05-10 | 19.5 | 0 | 1.5 | 2022-05-10 | 21.7 | 0 | 3.7 | 2021-05-10 | 14.8 | 3.2 | 0 | 2020-05-10 | 7.2 | 10.8 | 0 | 2019-05-10 | 14.8 | 3.2 | 0 | 2018-05-10 | 15.8 | 2.2 | 0 | 2017-05-10 | 9 | 9 | 0 | 2016-05-10 | 14.4 | 3.6 | 0 | 3.47 | 0.52
2025-05-10 | 18.7 | 0 | 0.7 | 2024-05-10 | 16.2 | 1.8 | 0 | 2023-05-10 | 20.4 | 0 | 2.4 | 2022-05-10 | 23.1 | 0 | 5.1 | 2021-05-10 | 15.1 | 2.9 | 0 | 2020-05-10 | 8.8 | 9.2 | 0 | 2019-05-10 | 16.5 | 1.5 | 0 | 2018-05-10 | 18.2 | 0 | 0.2 | 2017-05-10 | 10.1 | 7.9 | 0 | 2016-05-10 | 14.5 | 3.5 | 0 | 2.68 | 0.84
2025-05-10 | 19.6 | 0 | 1.6 | 2024-05-10 | 16.3 | 1.7 | 0 | 2023-05-10 | 21.6 | 0 | 3.6 | 2022-05-10 | 23.2 | 0 | 5.2 | 2021-05-10 | 14.4 | 3.6 | 0 | 2020-05-10 | 10.2 | 7.8 | 0 | 2019-05-10 | 17.8 | 0.2 | 0 | 2018-05-10 | 19.9 | 0 | 1.9 | 2017-05-10 | 12.4 | 5.6 | 0 | 2016-05-10 | 16.3 | 1.7 | 0 | 2.06 | 1.23
2025-05-10 | 20.9 | 0 | 2.9 | 2024-05-10 | 15 | 3 | 0 | 2023-05-10 | 21.9 | 0 | 3.9 | 2022-05-10 | 23.7 | 0 | 5.7 | 2021-05-10 | 15.3 | 2.7 | 0 | 2020-05-10 | 10.6 | 7.4 | 0 | 2019-05-10 | 17.4 | 0.6 | 0 | 2018-05-10 | 20 | 0 | 2 | 2017-05-10 | 12.4 | 5.6 | 0 | 2016-05-10 | 16.8 | 1.2 | 0 | 2.05 | 1.45
2025-05-10 | 21 | 0 | 3 | 2024-05-10 | 15.6 | 2.4 | 0 | 2023-05-10 | 22.2 | 0 | 4.2 | 2022-05-10 | 24.7 | 0 | 6.7 | 2021-05-10 | 11.7 | 6.3 | 0 | 2020-05-10 | 10.7 | 7.3 | 0 | 2019-05-10 | 16.2 | 1.8 | 0 | 2018-05-10 | 18.6 | 0 | 0.6 | 2017-05-10 | 13.3 | 4.7 | 0 | 2016-05-10 | 18.1 | 0 | 0.1 | 2.25 | 1.46
2025-05-10 | 21.4 | 0 | 3.4 | 2024-05-10 | 17.5 | 0.5 | 0 | 2023-05-10 | 22.5 | 0 | 4.5 | 2022-05-10 | 24.9 | 0 | 6.9 | 2021-05-10 | 11 | 7 | 0 | 2020-05-10 | 11.1 | 6.9 | 0 | 2019-05-10 | 15.5 | 2.5 | 0 | 2018-05-10 | 17.9 | 0.1 | 0 | 2017-05-10 | 13.8 | 4.2 | 0 | 2016-05-10 | 18.4 | 0 | 0.4 | 2.12 | 1.52
2025-05-10 | 20.1 | 0 | 2.1 | 2024-05-10 | 16.1 | 1.9 | 0 | 2023-05-10 | 22.2 | 0 | 4.2 | 2022-05-10 | 24.7 | 0 | 6.7 | 2021-05-10 | 11.5 | 6.5 | 0 | 2020-05-10 | 11.7 | 6.3 | 0 | 2019-05-10 | 13.3 | 4.7 | 0 | 2018-05-10 | 16.5 | 1.5 | 0 | 2017-05-10 | 13.8 | 4.2 | 0 | 2016-05-10 | 18.2 | 0 | 0.2 | 2.51 | 1.32
2025-05-10 | 18.4 | 0 | 0.4 | 2024-05-10 | 14.3 | 3.7 | 0 | 2023-05-10 | 20.8 | 0 | 2.8 | 2022-05-10 | 23.2 | 0 | 5.2 | 2021-05-10 | 11.9 | 6.1 | 0 | 2020-05-10 | 11 | 7 | 0 | 2019-05-10 | 12 | 6 | 0 | 2018-05-10 | 15.5 | 2.5 | 0 | 2017-05-10 | 13.7 | 4.3 | 0 | 2016-05-10 | 17.5 | 0.5 | 0 | 3.01 | 0.84
2025-05-10 | 16.5 | 1.5 | 0 | 2024-05-10 | 14.2 | 3.8 | 0 | 2023-05-10 | 17.3 | 0.7 | 0 | 2022-05-10 | 22.2 | 0 | 4.2 | 2021-05-10 | 10.3 | 7.7 | 0 | 2020-05-10 | 9.3 | 8.7 | 0 | 2019-05-10 | 11 | 7 | 0 | 2018-05-10 | 13.9 | 4.1 | 0 | 2017-05-10 | 12.1 | 5.9 | 0 | 2016-05-10 | 15 | 3 | 0 | 4.24 | 0.42
2025-05-10 | 13.7 | 4.3 | 0 | 2024-05-10 | 13.5 | 4.5 | 0 | 2023-05-10 | 17.3 | 0.7 | 0 | 2022-05-10 | 19.7 | 0 | 1.7 | 2021-05-10 | 10.2 | 7.8 | 0 | 2020-05-10 | 7.3 | 10.7 | 0 | 2019-05-10 | 10.2 | 7.8 | 0 | 2018-05-10 | 12.8 | 5.2 | 0 | 2017-05-10 | 11.4 | 6.6 | 0 | 2016-05-10 | 14.5 | 3.5 | 0 | 5.11 | 0.17
2025-05-10 | 11.6 | 6.4 | 0 | 2024-05-10 | 10.9 | 7.1 | 0 | 2023-05-10 | 14.9 | 3.1 | 0 | 2022-05-10 | 17.8 | 0.2 | 0 | 2021-05-10 | 9.1 | 8.9 | 0 | 2020-05-10 | 6.5 | 11.5 | 0 | 2019-05-10 | 9.8 | 8.2 | 0 | 2018-05-10 | 10.7 | 7.3 | 0 | 2017-05-10 | 10.7 | 7.3 | 0 | 2016-05-10 | 11.6 | 6.4 | 0 | 6.64 | 0
2025-05-10 | 9.5 | 8.5 | 0 | 2024-05-10 | 9.9 | 8.1 | 0 | 2023-05-10 | 13.5 | 4.5 | 0 | 2022-05-10 | 14.7 | 3.3 | 0 | 2021-05-10 | 7.3 | 10.7 | 0 | 2020-05-10 | 6.3 | 11.7 | 0 | 2019-05-10 | 7.8 | 10.2 | 0 | 2018-05-10 | 9.1 | 8.9 | 0 | 2017-05-10 | 10.8 | 7.2 | 0 | 2016-05-10 | 12.7 | 5.3 | 0 | 7.84 | 0
2025-05-10 | 8.4 | 9.6 | 0 | 2024-05-10 | 12 | 6 | 0 | 2023-05-10 | 11.6 | 6.4 | 0 | 2022-05-10 | 13.8 | 4.2 | 0 | 2021-05-10 | 6.8 | 11.2 | 0 | 2020-05-10 | 4.7 | 13.3 | 0 | 2019-05-10 | 7.4 | 10.6 | 0 | 2018-05-10 | 7.8 | 10.2 | 0 | 2017-05-10 | 9.6 | 8.4 | 0 | 2016-05-10 | 9.9 | 8.1 | 0 | 8.8 | 0
2025-05-11 | 7.2 | 10.8 | 0 | 2024-05-11 | 10.2 | 7.8 | 0 | 2023-05-11 | 11.4 | 6.6 | 0 | 2022-05-11 | 11.9 | 6.1 | 0 | 2021-05-11 | 6.2 | 11.8 | 0 | 2020-05-11 | 3.9 | 14.1 | 0 | 2019-05-11 | 7.2 | 10.8 | 0 | 2018-05-11 | 4.6 | 13.4 | 0 | 2017-05-11 | 8.3 | 9.7 | 0 | 2016-05-11 | 8.2 | 9.8 | 0 | 10.09 | 0
2025-05-11 | 5.7 | 12.3 | 0 | 2024-05-11 | 9.6 | 8.4 | 0 | 2023-05-11 | 10.6 | 7.4 | 0 | 2022-05-11 | 8.4 | 9.6 | 0 | 2021-05-11 | 6.1 | 11.9 | 0 | 2020-05-11 | 1.8 | 16.2 | 0 | 2019-05-11 | 4.9 | 13.1 | 0 | 2018-05-11 | 3.4 | 14.6 | 0 | 2017-05-11 | 8.3 | 9.7 | 0 | 2016-05-11 | 9.1 | 8.9 | 0 | 11.21 | 0
2025-05-11 | 4.3 | 13.7 | 0 | 2024-05-11 | 7.3 | 10.7 | 0 | 2023-05-11 | 9.8 | 8.2 | 0 | 2022-05-11 | 10.5 | 7.5 | 0 | 2021-05-11 | 5 | 13 | 0 | 2020-05-11 | 1.2 | 16.8 | 0 | 2019-05-11 | 4.1 | 13.9 | 0 | 2018-05-11 | 2.9 | 15.1 | 0 | 2017-05-11 | 6.5 | 11.5 | 0 | 2016-05-11 | 7.6 | 10.4 | 0 | 12.08 | 0
2025-05-11 | 3.4 | 14.6 | 0 | 2024-05-11 | 6.8 | 11.2 | 0 | 2023-05-11 | 9.3 | 8.7 | 0 | 2022-05-11 | 9.8 | 8.2 | 0 | 2021-05-11 | 3.8 | 14.2 | 0 | 2020-05-11 | 1.9 | 16.1 | 0 | 2019-05-11 | 4.8 | 13.2 | 0 | 2018-05-11 | 1.3 | 16.7 | 0 | 2017-05-11 | 6.3 | 11.7 | 0 | 2016-05-11 | 6.7 | 11.3 | 0 | 12.59 | 0
2025-05-11 | 2.6 | 15.4 | 0 | 2024-05-11 | 5.3 | 12.7 | 0 | 2023-05-11 | 9.8 | 8.2 | 0 | 2022-05-11 | 6.7 | 11.3 | 0 | 2021-05-11 | 2.9 | 15.1 | 0 | 2020-05-11 | 1.7 | 16.3 | 0 | 2019-05-11 | 5.5 | 12.5 | 0 | 2018-05-11 | 1.1 | 16.9 | 0 | 2017-05-11 | 5.2 | 12.8 | 0 | 2016-05-11 | 4.2 | 13.8 | 0 | 13.5 | 0
2025-05-11 | 2.4 | 15.6 | 0 | 2024-05-11 | 7.3 | 10.7 | 0 | 2023-05-11 | 8.6 | 9.4 | 0 | 2022-05-11 | 6.7 | 11.3 | 0 | 2021-05-11 | 3 | 15 | 0 | 2020-05-11 | 1.9 | 16.1 | 0 | 2019-05-11 | 3.8 | 14.2 | 0 | 2018-05-11 | 0.9 | 17.1 | 0 | 2017-05-11 | 5 | 13 | 0 | 2016-05-11 | 7 | 11 | 0 | 13.34 | 0
2025-05-11 | 3 | 15 | 0 | 2024-05-11 | 7.6 | 10.4 | 0 | 2023-05-11 | 12.1 | 5.9 | 0 | 2022-05-11 | 11.5 | 6.5 | 0 | 2021-05-11 | 4.3 | 13.7 | 0 | 2020-05-11 | 1.9 | 16.1 | 0 | 2019-05-11 | 6.1 | 11.9 | 0 | 2018-05-11 | 2.5 | 15.5 | 0 | 2017-05-11 | 6.5 | 11.5 | 0 | 2016-05-11 | 9.8 | 8.2 | 0 | 11.47 | 0
2025-05-11 | 4.7 | 13.3 | 0 | 2024-05-11 | 9.2 | 8.8 | 0 | 2023-05-11 | 13.1 | 4.9 | 0 | 2022-05-11 | 14.8 | 3.2 | 0 | 2021-05-11 | 5.7 | 12.3 | 0 | 2020-05-11 | 2.3 | 15.7 | 0 | 2019-05-11 | 7 | 11 | 0 | 2018-05-11 | 3.4 | 14.6 | 0 | 2017-05-11 | 8.8 | 9.2 | 0 | 2016-05-11 | 11.8 | 6.2 | 0 | 9.92 | 0
2025-05-11 | 5.8 | 12.2 | 0 | 2024-05-11 | 10.6 | 7.4 | 0 | 2023-05-11 | 16.6 | 1.4 | 0 | 2022-05-11 | 17.8 | 0.2 | 0 | 2021-05-11 | 7 | 11 | 0 | 2020-05-11 | 3.3 | 14.7 | 0 | 2019-05-11 | 8.4 | 9.6 | 0 | 2018-05-11 | 4.3 | 13.7 | 0 | 2017-05-11 | 9.6 | 8.4 | 0 | 2016-05-11 | 14.2 | 3.8 | 0 | 8.24 | 0
2025-05-11 | 7.4 | 10.6 | 0 | 2024-05-11 | 13.5 | 4.5 | 0 | 2023-05-11 | 19 | 0 | 1 | 2022-05-11 | 20.7 | 0 | 2.7 | 2021-05-11 | 7 | 11 | 0 | 2020-05-11 | 4.4 | 13.6 | 0 | 2019-05-11 | 8.8 | 9.2 | 0 | 2018-05-11 | 5.5 | 12.5 | 0 | 2017-05-11 | 11.3 | 6.7 | 0 | 2016-05-11 | 15.9 | 2.1 | 0 | 7.02 | 0.37
2025-05-11 | 10 | 8 | 0 | 2024-05-11 | 15 | 3 | 0 | 2023-05-11 | 21.1 | 0 | 3.1 | 2022-05-11 | 23.2 | 0 | 5.2 | 2021-05-11 | 9.4 | 8.6 | 0 | 2020-05-11 | 6.3 | 11.7 | 0 | 2019-05-11 | 10.5 | 7.5 | 0 | 2018-05-11 | 6.3 | 11.7 | 0 | 2017-05-11 | 10.3 | 7.7 | 0 | 2016-05-11 | 17.2 | 0.8 | 0 | 5.9 | 0.83
2025-05-11 | 11.7 | 6.3 | 0 | 2024-05-11 | 15.4 | 2.6 | 0 | 2023-05-11 | 21.9 | 0 | 3.9 | 2022-05-11 | 25.4 | 0 | 7.4 | 2021-05-11 | 10.5 | 7.5 | 0 | 2020-05-11 | 6 | 12 | 0 | 2019-05-11 | 10.2 | 7.8 | 0 | 2018-05-11 | 6.7 | 11.3 | 0 | 2017-05-11 | 11 | 7 | 0 | 2016-05-11 | 18.2 | 0 | 0.2 | 5.45 | 1.15
2025-05-11 | 13.3 | 4.7 | 0 | 2024-05-11 | 17 | 1 | 0 | 2023-05-11 | 23.1 | 0 | 5.1 | 2022-05-11 | 25.9 | 0 | 7.9 | 2021-05-11 | 9.3 | 8.7 | 0 | 2020-05-11 | 6.8 | 11.2 | 0 | 2019-05-11 | 11 | 7 | 0 | 2018-05-11 | 8.8 | 9.2 | 0 | 2017-05-11 | 11.4 | 6.6 | 0 | 2016-05-11 | 19 | 0 | 1 | 4.84 | 1.4
2025-05-11 | 14.7 | 3.3 | 0 | 2024-05-11 | 16 | 2 | 0 | 2023-05-11 | 24.7 | 0 | 6.7 | 2022-05-11 | 26.6 | 0 | 8.6 | 2021-05-11 | 8.2 | 9.8 | 0 | 2020-05-11 | 7.7 | 10.3 | 0 | 2019-05-11 | 11.7 | 6.3 | 0 | 2018-05-11 | 10.3 | 7.7 | 0 | 2017-05-11 | 10.6 | 7.4 | 0 | 2016-05-11 | 19.8 | 0 | 1.8 | 4.68 | 1.71
2025-05-11 | 16.1 | 1.9 | 0 | 2024-05-11 | 17.7 | 0.3 | 0 | 2023-05-11 | 24.8 | 0 | 6.8 | 2022-05-11 | 27 | 0 | 9 | 2021-05-11 | 9.8 | 8.2 | 0 | 2020-05-11 | 8.6 | 9.4 | 0 | 2019-05-11 | 13.3 | 4.7 | 0 | 2018-05-11 | 11.1 | 6.9 | 0 | 2017-05-11 | 10.8 | 7.2 | 0 | 2016-05-11 | 20.6 | 0 | 2.6 | 3.86 | 1.84
2025-05-11 | 16.6 | 1.4 | 0 | 2024-05-11 | 14.5 | 3.5 | 0 | 2023-05-11 | 25.3 | 0 | 7.3 | 2022-05-11 | 27.8 | 0 | 9.8 | 2021-05-11 | 8.3 | 9.7 | 0 | 2020-05-11 | 9.2 | 8.8 | 0 | 2019-05-11 | 12.9 | 5.1 | 0 | 2018-05-11 | 11.5 | 6.5 | 0 | 2017-05-11 | 10.9 | 7.1 | 0 | 2016-05-11 | 21.3 | 0 | 3.3 | 4.21 | 2.04
2025-05-11 | 17.1 | 0.9 | 0 | 2024-05-11 | 13.6 | 4.4 | 0 | 2023-05-11 | 26 | 0 | 8 | 2022-05-11 | 28.3 | 0 | 10.3 | 2021-05-11 | 6.9 | 11.1 | 0 | 2020-05-11 | 10.2 | 7.8 | 0 | 2019-05-11 | 13.6 | 4.4 | 0 | 2018-05-11 | 11.3 | 6.7 | 0 | 2017-05-11 | 10.9 | 7.1 | 0 | 2016-05-11 | 21.8 | 0 | 3.8 | 4.24 | 2.21
2025-05-11 | 16.9 | 1.1 | 0 | 2024-05-11 | 12.5 | 5.5 | 0 | 2023-05-11 | 23.4 | 0 | 5.4 | 2022-05-11 | 26.9 | 0 | 8.9 | 2021-05-11 | 4.8 | 13.2 | 0 | 2020-05-11 | 9.3 | 8.7 | 0 | 2019-05-11 | 12.8 | 5.2 | 0 | 2018-05-11 | 10.9 | 7.1 | 0 | 2017-05-11 | 11.3 | 6.7 | 0 | 2016-05-11 | 21.7 | 0 | 3.7 | 4.75 | 1.8
2025-05-11 | 15.9 | 2.1 | 0 | 2024-05-11 | 13.1 | 4.9 | 0 | 2023-05-11 | 22.3 | 0 | 4.3 | 2022-05-11 | 26.5 | 0 | 8.5 | 2021-05-11 | 4.9 | 13.1 | 0 | 2020-05-11 | 9 | 9 | 0 | 2019-05-11 | 12.2 | 5.8 | 0 | 2018-05-11 | 10.7 | 7.3 | 0 | 2017-05-11 | 11.1 | 6.9 | 0 | 2016-05-11 | 21.4 | 0 | 3.4 | 4.91 | 1.62
2025-05-11 | 15 | 3 | 0 | 2024-05-11 | 12.2 | 5.8 | 0 | 2023-05-11 | 21.2 | 0 | 3.2 | 2022-05-11 | 25 | 0 | 7 | 2021-05-11 | 5.3 | 12.7 | 0 | 2020-05-11 | 8 | 10 | 0 | 2019-05-11 | 11.5 | 6.5 | 0 | 2018-05-11 | 10 | 8 | 0 | 2017-05-11 | 10.6 | 7.4 | 0 | 2016-05-11 | 20.1 | 0 | 2.1 | 5.34 | 1.23
2025-05-11 | 13 | 5 | 0 | 2024-05-11 | 11.2 | 6.8 | 0 | 2023-05-11 | 18.2 | 0 | 0.2 | 2022-05-11 | 22.8 | 0 | 4.8 | 2021-05-11 | 5.8 | 12.2 | 0 | 2020-05-11 | 7.5 | 10.5 | 0 | 2019-05-11 | 10.4 | 7.6 | 0 | 2018-05-11 | 8.6 | 9.4 | 0 | 2017-05-11 | 9.4 | 8.6 | 0 | 2016-05-11 | 14.4 | 3.6 | 0 | 6.37 | 0.5
2025-05-11 | 11.4 | 6.6 | 0 | 2024-05-11 | 10.6 | 7.4 | 0 | 2023-05-11 | 17.1 | 0.9 | 0 | 2022-05-11 | 22.1 | 0 | 4.1 | 2021-05-11 | 6 | 12 | 0 | 2020-05-11 | 5.8 | 12.2 | 0 | 2019-05-11 | 9.4 | 8.6 | 0 | 2018-05-11 | 7.8 | 10.2 | 0 | 2017-05-11 | 9.5 | 8.5 | 0 | 2016-05-11 | 17.1 | 0.9 | 0 | 6.73 | 0.41
2025-05-11 | 11.8 | 6.2 | 0 | 2024-05-11 | 10.4 | 7.6 | 0 | 2023-05-11 | 16.6 | 1.4 | 0 | 2022-05-11 | 16.5 | 1.5 | 0 | 2021-05-11 | 6.1 | 11.9 | 0 | 2020-05-11 | 5.3 | 12.7 | 0 | 2019-05-11 | 8.5 | 9.5 | 0 | 2018-05-11 | 5.5 | 12.5 | 0 | 2017-05-11 | 9.2 | 8.8 | 0 | 2016-05-11 | 15.4 | 2.6 | 0 | 7.47 | 0
2025-05-11 | 11.1 | 6.9 | 0 | 2024-05-11 | 9.6 | 8.4 | 0 | 2023-05-11 | 17 | 1 | 0 | 2022-05-11 | 17.1 | 0.9 | 0 | 2021-05-11 | 6.4 | 11.6 | 0 | 2020-05-11 | 4.1 | 13.9 | 0 | 2019-05-11 | 8.2 | 9.8 | 0 | 2018-05-11 | 5 | 13 | 0 | 2017-05-11 | 9.2 | 8.8 | 0 | 2016-05-11 | 12.2 | 5.8 | 0 | 8.01 | 0
2025-05-12 | 10.4 | 7.6 | 0 | 2024-05-12 | 9.2 | 8.8 | 0 | 2023-05-12 | 19.8 | 0 | 1.8 | 2022-05-12 | 17.7 | 0.3 | 0 | 2021-05-12 | 6.6 | 11.4 | 0 | 2020-05-12 | 3 | 15 | 0 | 2019-05-12 | 8.1 | 9.9 | 0 | 2018-05-12 | 4.9 | 13.1 | 0 | 2017-05-12 | 8.9 | 9.1 | 0 | 2016-05-12 | 11.7 | 6.3 | 0 | 8.15 | 0.18
2025-05-12 | 9.9 | 8.1 | 0 | 2024-05-12 | 9.8 | 8.2 | 0 | 2023-05-12 | 16.7 | 1.3 | 0 | 2022-05-12 | 16.4 | 1.6 | 0 | 2021-05-12 | 6.3 | 11.7 | 0 | 2020-05-12 | 2 | 16 | 0 | 2019-05-12 | 7.4 | 10.6 | 0 | 2018-05-12 | 3.7 | 14.3 | 0 | 2017-05-12 | 8.4 | 9.6 | 0 | 2016-05-12 | 11.6 | 6.4 | 0 | 8.78 | 0
2025-05-12 | 8.5 | 9.5 | 0 | 2024-05-12 | 9.2 | 8.8 | 0 | 2023-05-12 | 16.5 | 1.5 | 0 | 2022-05-12 | 12.9 | 5.1 | 0 | 2021-05-12 | 5.6 | 12.4 | 0 | 2020-05-12 | 1.7 | 16.3 | 0 | 2019-05-12 | 6.7 | 11.3 | 0 | 2018-05-12 | 3.4 | 14.6 | 0 | 2017-05-12 | 8 | 10 | 0 | 2016-05-12 | 12.6 | 5.4 | 0 | 9.49 | 0
2025-05-12 | 8.2 | 9.8 | 0 | 2024-05-12 | 9.3 | 8.7 | 0 | 2023-05-12 | 13.9 | 4.1 | 0 | 2022-05-12 | 15.1 | 2.9 | 0 | 2021-05-12 | 5 | 13 | 0 | 2020-05-12 | 0.2 | 17.8 | 0 | 2019-05-12 | 6.6 | 11.4 | 0 | 2018-05-12 | 2.1 | 15.9 | 0 | 2017-05-12 | 7.9 | 10.1 | 0 | 2016-05-12 | 10.9 | 7.1 | 0 | 10.08 | 0
2025-05-12 | 7.1 | 10.9 | 0 | 2024-05-12 | 9.1 | 8.9 | 0 | 2023-05-12 | 13.1 | 4.9 | 0 | 2022-05-12 | 11.3 | 6.7 | 0 | 2021-05-12 | 4.6 | 13.4 | 0 | 2020-05-12 | -2.2 | 20.2 | 0 | 2019-05-12 | 6.2 | 11.8 | 0 | 2018-05-12 | 1.4 | 16.6 | 0 | 2017-05-12 | 7.4 | 10.6 | 0 | 2016-05-12 | 9.7 | 8.3 | 0 | 11.23 | 0
2025-05-12 | 6.3 | 11.7 | 0 | 2024-05-12 | 9.6 | 8.4 | 0 | 2023-05-12 | 14.1 | 3.9 | 0 | 2022-05-12 | 12.2 | 5.8 | 0 | 2021-05-12 | 4.4 | 13.6 | 0 | 2020-05-12 | -2.8 | 20.8 | 0 | 2019-05-12 | 6 | 12 | 0 | 2018-05-12 | 1.2 | 16.8 | 0 | 2017-05-12 | 7.2 | 10.8 | 0 | 2016-05-12 | 7.5 | 10.5 | 0 | 11.43 | 0
2025-05-12 | 7.5 | 10.5 | 0 | 2024-05-12 | 9.8 | 8.2 | 0 | 2023-05-12 | 14.6 | 3.4 | 0 | 2022-05-12 | 14.6 | 3.4 | 0 | 2021-05-12 | 5.1 | 12.9 | 0 | 2020-05-12 | -0.1 | 18.1 | 0 | 2019-05-12 | 6.6 | 11.4 | 0 | 2018-05-12 | 4.1 | 13.9 | 0 | 2017-05-12 | 7.8 | 10.2 | 0 | 2016-05-12 | 10.4 | 7.6 | 0 | 9.96 | 0
2025-05-12 | 10.7 | 7.3 | 0 | 2024-05-12 | 10.9 | 7.1 | 0 | 2023-05-12 | 17.2 | 0.8 | 0 | 2022-05-12 | 17.6 | 0.4 | 0 | 2021-05-12 | 7.8 | 10.2 | 0 | 2020-05-12 | 2.2 | 15.8 | 0 | 2019-05-12 | 7.9 | 10.1 | 0 | 2018-05-12 | 6.9 | 11.1 | 0 | 2017-05-12 | 9.5 | 8.5 | 0 | 2016-05-12 | 14.4 | 3.6 | 0 | 7.49 | 0
2025-05-12 | 13.1 | 4.9 | 0 | 2024-05-12 | 12.2 | 5.8 | 0 | 2023-05-12 | 18 | 0 | 0 | 2022-05-12 | 21.7 | 0 | 3.7 | 2021-05-12 | 9.1 | 8.9 | 0 | 2020-05-12 | 3.6 | 14.4 | 0 | 2019-05-12 | 9.4 | 8.6 | 0 | 2018-05-12 | 9.8 | 8.2 | 0 | 2017-05-12 | 11.2 | 6.8 | 0 | 2016-05-12 | 17 | 1 | 0 | 5.86 | 0.37
2025-05-12 | 16.6 | 1.4 | 0 | 2024-05-12 | 12.9 | 5.1 | 0 | 2023-05-12 | 19.5 | 0 | 1.5 | 2022-05-12 | 23.7 | 0 | 5.7 | 2021-05-12 | 10.8 | 7.2 | 0 | 2020-05-12 | 5.2 | 12.8 | 0 | 2019-05-12 | 11.6 | 6.4 | 0 | 2018-05-12 | 12.5 | 5.5 | 0 | 2017-05-12 | 13 | 5 | 0 | 2016-05-12 | 19.5 | 0 | 1.5 | 4.34 | 0.87
2025-05-12 | 18.6 | 0 | 0.6 | 2024-05-12 | 13.8 | 4.2 | 0 | 2023-05-12 | 20.3 | 0 | 2.3 | 2022-05-12 | 26.4 | 0 | 8.4 | 2021-05-12 | 12.3 | 5.7 | 0 | 2020-05-12 | 5.9 | 12.1 | 0 | 2019-05-12 | 12.7 | 5.3 | 0 | 2018-05-12 | 13.6 | 4.4 | 0 | 2017-05-12 | 14.6 | 3.4 | 0 | 2016-05-12 | 21 | 0 | 3 | 3.51 | 1.43
2025-05-12 | 20.2 | 0 | 2.2 | 2024-05-12 | 13.2 | 4.8 | 0 | 2023-05-12 | 21.9 | 0 | 3.9 | 2022-05-12 | 27.6 | 0 | 9.6 | 2021-05-12 | 14.2 | 3.8 | 0 | 2020-05-12 | 6.9 | 11.1 | 0 | 2019-05-12 | 14.6 | 3.4 | 0 | 2018-05-12 | 15.2 | 2.8 | 0 | 2017-05-12 | 16.7 | 1.3 | 0 | 2016-05-12 | 22.7 | 0 | 4.7 | 2.72 | 2.04
2025-05-12 | 22.4 | 0 | 4.4 | 2024-05-12 | 15.7 | 2.3 | 0 | 2023-05-12 | 23.8 | 0 | 5.8 | 2022-05-12 | 28.3 | 0 | 10.3 | 2021-05-12 | 15.7 | 2.3 | 0 | 2020-05-12 | 7.8 | 10.2 | 0 | 2019-05-12 | 14.8 | 3.2 | 0 | 2018-05-12 | 15.4 | 2.6 | 0 | 2017-05-12 | 17.3 | 0.7 | 0 | 2016-05-12 | 23.7 | 0 | 5.7 | 2.13 | 2.62
2025-05-12 | 24.1 | 0 | 6.1 | 2024-05-12 | 10.9 | 7.1 | 0 | 2023-05-12 | 24.9 | 0 | 6.9 | 2022-05-12 | 29.6 | 0 | 11.6 | 2021-05-12 | 16.5 | 1.5 | 0 | 2020-05-12 | 7.5 | 10.5 | 0 | 2019-05-12 | 15.1 | 2.9 | 0 | 2018-05-12 | 16.1 | 1.9 | 0 | 2017-05-12 | 18.4 | 0 | 0.4 | 2016-05-12 | 24.8 | 0 | 6.8 | 2.39 | 3.18
2025-05-12 | 24.8 | 0 | 6.8 | 2024-05-12 | 14.3 | 3.7 | 0 | 2023-05-12 | 25.1 | 0 | 7.1 | 2022-05-12 | 29.5 | 0 | 11.5 | 2021-05-12 | 16.6 | 1.4 | 0 | 2020-05-12 | 6.5 | 11.5 | 0 | 2019-05-12 | 16.3 | 1.7 | 0 | 2018-05-12 | 16.7 | 1.3 | 0 | 2017-05-12 | 18.9 | 0 | 0.9 | 2016-05-12 | 25.8 | 0 | 7.8 | 1.96 | 3.41
2025-05-12 | 25.5 | 0 | 7.5 | 2024-05-12 | 16.1 | 1.9 | 0 | 2023-05-12 | 25.7 | 0 | 7.7 | 2022-05-12 | 29.7 | 0 | 11.7 | 2021-05-12 | 16.8 | 1.2 | 0 | 2020-05-12 | 6.3 | 11.7 | 0 | 2019-05-12 | 15.5 | 2.5 | 0 | 2018-05-12 | 17.7 | 0.3 | 0 | 2017-05-12 | 18.2 | 0 | 0.2 | 2016-05-12 | 26.1 | 0 | 8.1 | 1.76 | 3.52
2025-05-12 | 25.3 | 0 | 7.3 | 2024-05-12 | 15.7 | 2.3 | 0 | 2023-05-12 | 25.5 | 0 | 7.5 | 2022-05-12 | 29.6 | 0 | 11.6 | 2021-05-12 | 17 | 1 | 0 | 2020-05-12 | 6.9 | 11.1 | 0 | 2019-05-12 | 15.2 | 2.8 | 0 | 2018-05-12 | 17.9 | 0.1 | 0 | 2017-05-12 | 19 | 0 | 1 | 2016-05-12 | 26.2 | 0 | 8.2 | 1.73 | 3.56
2025-05-12 | 25.1 | 0 | 7.1 | 2024-05-12 | 15.9 | 2.1 | 0 | 2023-05-12 | 25.2 | 0 | 7.2 | 2022-05-12 | 28.2 | 0 | 10.2 | 2021-05-12 | 16.9 | 1.1 | 0 | 2020-05-12 | 6.8 | 11.2 | 0 | 2019-05-12 | 14.7 | 3.3 | 0 | 2018-05-12 | 17.2 | 0.8 | 0 | 2017-05-12 | 17.1 | 0.9 | 0 | 2016-05-12 | 26 | 0 | 8 | 1.94 | 3.25
2025-05-12 | 24.3 | 0 | 6.3 | 2024-05-12 | 15.1 | 2.9 | 0 | 2023-05-12 | 24.3 | 0 | 6.3 | 2022-05-12 | 27.6 | 0 | 9.6 | 2021-05-12 | 16.3 | 1.7 | 0 | 2020-05-12 | 7 | 11 | 0 | 2019-05-12 | 13.7 | 4.3 | 0 | 2018-05-12 | 17.3 | 0.7 | 0 | 2017-05-12 | 17.3 | 0.7 | 0 | 2016-05-12 | 25.6 | 0 | 7.6 | 2.13 | 2.98
2025-05-12 | 20.9 | 0 | 2.9 | 2024-05-12 | 14.1 | 3.9 | 0 | 2023-05-12 | 22.6 | 0 | 4.6 | 2022-05-12 | 26 | 0 | 8 | 2021-05-12 | 14.9 | 3.1 | 0 | 2020-05-12 | 5.3 | 12.7 | 0 | 2019-05-12 | 12.4 | 5.6 | 0 | 2018-05-12 | 15.4 | 2.6 | 0 | 2017-05-12 | 16.4 | 1.6 | 0 | 2016-05-12 | 22.8 | 0 | 4.8 | 2.95 | 2.03
2025-05-12 | 18.4 | 0 | 0.4 | 2024-05-12 | 13.8 | 4.2 | 0 | 2023-05-12 | 21.2 | 0 | 3.2 | 2022-05-12 | 24.7 | 0 | 6.7 | 2021-05-12 | 12.8 | 5.2 | 0 | 2020-05-12 | 3.1 | 14.9 | 0 | 2019-05-12 | 12.3 | 5.7 | 0 | 2018-05-12 | 14.6 | 3.4 | 0 | 2017-05-12 | 15.5 | 2.5 | 0 | 2016-05-12 | 21.6 | 0 | 3.6 | 3.59 | 1.39
2025-05-12 | 16.6 | 1.4 | 0 | 2024-05-12 | 13.6 | 4.4 | 0 | 2023-05-12 | 18.3 | 0 | 0.3 | 2022-05-12 | 22.7 | 0 | 4.7 | 2021-05-12 | 10.7 | 7.3 | 0 | 2020-05-12 | 2.8 | 15.2 | 0 | 2019-05-12 | 11.5 | 6.5 | 0 | 2018-05-12 | 12.8 | 5.2 | 0 | 2017-05-12 | 15 | 3 | 0 | 2016-05-12 | 20.8 | 0 | 2.8 | 4.3 | 0.78
2025-05-12 | 14.9 | 3.1 | 0 | 2024-05-12 | 10.7 | 7.3 | 0 | 2023-05-12 | 17.6 | 0.4 | 0 | 2022-05-12 | 20.4 | 0 | 2.4 | 2021-05-12 | 10.1 | 7.9 | 0 | 2020-05-12 | 1 | 17 | 0 | 2019-05-12 | 10.6 | 7.4 | 0 | 2018-05-12 | 9.9 | 8.1 | 0 | 2017-05-12 | 14.2 | 3.8 | 0 | 2016-05-12 | 20.6 | 0 | 2.6 | 5.5 | 0.5
2025-05-12 | 14.3 | 3.7 | 0 | 2024-05-12 | 10.6 | 7.4 | 0 | 2023-05-12 | 18 | 0 | 0 | 2022-05-12 | 20.6 | 0 | 2.6 | 2021-05-12 | 8.1 | 9.9 | 0 | 2020-05-12 | 1.1 | 16.9 | 0 | 2019-05-12 | 9 | 9 | 0 | 2018-05-12 | 4.7 | 13.3 | 0 | 2017-05-12 | 13.7 | 4.3 | 0 | 2016-05-12 | 17.9 | 0.1 | 0 | 6.46 | 0.26
2025-05-13 | 13.3 | 4.7 | 0 | 2024-05-13 | 9.9 | 8.1 | 0 | 2023-05-13 | 16.9 | 1.1 | 0 | 2022-05-13 | 18.8 | 0 | 0.8 | 2021-05-13 | 6.9 | 11.1 | 0 | 2020-05-13 | -0.8 | 18.8 | 0 | 2019-05-13 | 8.5 | 9.5 | 0 | 2018-05-13 | 7.8 | 10.2 | 0 | 2017-05-13 | 13.5 | 4.5 | 0 | 2016-05-13 | 18.4 | 0 | 0.4 | 6.8 | 0.12
2025-05-13 | 12.7 | 5.3 | 0 | 2024-05-13 | 9.5 | 8.5 | 0 | 2023-05-13 | 15.1 | 2.9 | 0 | 2022-05-13 | 18.6 | 0 | 0.6 | 2021-05-13 | 6.8 | 11.2 | 0 | 2020-05-13 | 0 | 18 | 0 | 2019-05-13 | 9 | 9 | 0 | 2018-05-13 | 5.9 | 12.1 | 0 | 2017-05-13 | 13.1 | 4.9 | 0 | 2016-05-13 | 19.1 | 0 | 1.1 | 7.19 | 0.17
2025-05-13 | 12 | 6 | 0 | 2024-05-13 | 8.8 | 9.2 | 0 | 2023-05-13 | 13.4 | 4.6 | 0 | 2022-05-13 | 18.3 | 0 | 0.3 | 2021-05-13 | 6.5 | 11.5 | 0 | 2020-05-13 | -1.7 | 19.7 | 0 | 2019-05-13 | 9.1 | 8.9 | 0 | 2018-05-13 | 7.7 | 10.3 | 0 | 2017-05-13 | 12.9 | 5.1 | 0 | 2016-05-13 | 19.1 | 0 | 1.1 | 7.53 | 0.14
2025-05-13 | 11.8 | 6.2 | 0 | 2024-05-13 | 9.5 | 8.5 | 0 | 2023-05-13 | 10 | 8 | 0 | 2022-05-13 | 17 | 1 | 0 | 2021-05-13 | 5.1 | 12.9 | 0 | 2020-05-13 | 0 | 18 | 0 | 2019-05-13 | 9.1 | 8.9 | 0 | 2018-05-13 | 4 | 14 | 0 | 2017-05-13 | 12.4 | 5.6 | 0 | 2016-05-13 | 18.3 | 0 | 0.3 | 8.31 | 0.03
2025-05-13 | 11.3 | 6.7 | 0 | 2024-05-13 | 9.4 | 8.6 | 0 | 2023-05-13 | 9.7 | 8.3 | 0 | 2022-05-13 | 15.3 | 2.7 | 0 | 2021-05-13 | 4.5 | 13.5 | 0 | 2020-05-13 | -0.2 | 18.2 | 0 | 2019-05-13 | 8.6 | 9.4 | 0 | 2018-05-13 | 4.3 | 13.7 | 0 | 2017-05-13 | 11.4 | 6.6 | 0 | 2016-05-13 | 18.2 | 0 | 0.2 | 8.77 | 0.02
2025-05-13 | 10 | 8 | 0 | 2024-05-13 | 9.4 | 8.6 | 0 | 2023-05-13 | 6.5 | 11.5 | 0 | 2022-05-13 | 14.8 | 3.2 | 0 | 2021-05-13 | 5 | 13 | 0 | 2020-05-13 | -0.4 | 18.4 | 0 | 2019-05-13 | 8.9 | 9.1 | 0 | 2018-05-13 | 5.2 | 12.8 | 0 | 2017-05-13 | 10.6 | 7.4 | 0 | 2016-05-13 | 18.5 | 0 | 0.5 | 9.2 | 0.05
2025-05-13 | 12.6 | 5.4 | 0 | 2024-05-13 | 9.9 | 8.1 | 0 | 2023-05-13 | 9.9 | 8.1 | 0 | 2022-05-13 | 16.6 | 1.4 | 0 | 2021-05-13 | 7.6 | 10.4 | 0 | 2020-05-13 | 1.9 | 16.1 | 0 | 2019-05-13 | 9.4 | 8.6 | 0 | 2018-05-13 | 6.7 | 11.3 | 0 | 2017-05-13 | 10.7 | 7.3 | 0 | 2016-05-13 | 18.7 | 0 | 0.7 | 7.67 | 0.07
2025-05-13 | 14.4 | 3.6 | 0 | 2024-05-13 | 10.7 | 7.3 | 0 | 2023-05-13 | 13.7 | 4.3 | 0 | 2022-05-13 | 19.3 | 0 | 1.3 | 2021-05-13 | 10.6 | 7.4 | 0 | 2020-05-13 | 3.9 | 14.1 | 0 | 2019-05-13 | 9.3 | 8.7 | 0 | 2018-05-13 | 10.6 | 7.4 | 0 | 2017-05-13 | 11.7 | 6.3 | 0 | 2016-05-13 | 18.9 | 0 | 0.9 | 5.91 | 0.22
2025-05-13 | 17.2 | 0.8 | 0 | 2024-05-13 | 13.3 | 4.7 | 0 | 2023-05-13 | 15.8 | 2.2 | 0 | 2022-05-13 | 22.5 | 0 | 4.5 | 2021-05-13 | 14.2 | 3.8 | 0 | 2020-05-13 | 6.3 | 11.7 | 0 | 2019-05-13 | 9.7 | 8.3 | 0 | 2018-05-13 | 14 | 4 | 0 | 2017-05-13 | 11.7 | 6.3 | 0 | 2016-05-13 | 19.5 | 0 | 1.5 | 4.18 | 0.6
2025-05-13 | 18.3 | 0 | 0.3 | 2024-05-13 | 16 | 2 | 0 | 2023-05-13 | 17.4 | 0.6 | 0 | 2022-05-13 | 25.7 | 0 | 7.7 | 2021-05-13 | 16.1 | 1.9 | 0 | 2020-05-13 | 7.6 | 10.4 | 0 | 2019-05-13 | 10.2 | 7.8 | 0 | 2018-05-13 | 16.7 | 1.3 | 0 | 2017-05-13 | 11.9 | 6.1 | 0 | 2016-05-13 | 16.7 | 1.3 | 0 | 3.14 | 0.8
2025-05-13 | 19.7 | 0 | 1.7 | 2024-05-13 | 15.3 | 2.7 | 0 | 2023-05-13 | 18.5 | 0 | 0.5 | 2022-05-13 | 26.8 | 0 | 8.8 | 2021-05-13 | 17.9 | 0.1 | 0 | 2020-05-13 | 9 | 9 | 0 | 2019-05-13 | 10.7 | 7.3 | 0 | 2018-05-13 | 18.6 | 0 | 0.6 | 2017-05-13 | 12.4 | 5.6 | 0 | 2016-05-13 | 16.6 | 1.4 | 0 | 2.61 | 1.16
2025-05-13 | 21.5 | 0 | 3.5 | 2024-05-13 | 14.7 | 3.3 | 0 | 2023-05-13 | 19 | 0 | 1 | 2022-05-13 | 27.9 | 0 | 9.9 | 2021-05-13 | 18.4 | 0 | 0.4 | 2020-05-13 | 10.6 | 7.4 | 0 | 2019-05-13 | 14.4 | 3.6 | 0 | 2018-05-13 | 19.1 | 0 | 1.1 | 2017-05-13 | 13.2 | 4.8 | 0 | 2016-05-13 | 17.6 | 0.4 | 0 | 1.95 | 1.59
2025-05-13 | 24 | 0 | 6 | 2024-05-13 | 15.6 | 2.4 | 0 | 2023-05-13 | 20 | 0 | 2 | 2022-05-13 | 29 | 0 | 11 | 2021-05-13 | 19.4 | 0 | 1.4 | 2020-05-13 | 11.9 | 6.1 | 0 | 2019-05-13 | 14.3 | 3.7 | 0 | 2018-05-13 | 19.7 | 0 | 1.7 | 2017-05-13 | 13.3 | 4.7 | 0 | 2016-05-13 | 18.9 | 0 | 0.9 | 1.69 | 2.3
2025-05-13 | 24.6 | 0 | 6.6 | 2024-05-13 | 16.8 | 1.2 | 0 | 2023-05-13 | 19.9 | 0 | 1.9 | 2022-05-13 | 29.8 | 0 | 11.8 | 2021-05-13 | 20.3 | 0 | 2.3 | 2020-05-13 | 12 | 6 | 0 | 2019-05-13 | 14.8 | 3.2 | 0 | 2018-05-13 | 19.9 | 0 | 1.9 | 2017-05-13 | 13.1 | 4.9 | 0 | 2016-05-13 | 20.2 | 0 | 2.2 | 1.53 | 2.67
2025-05-13 | 25.1 | 0 | 7.1 | 2024-05-13 | 18.2 | 0 | 0.2 | 2023-05-13 | 19.7 | 0 | 1.7 | 2022-05-13 | 29.8 | 0 | 11.8 | 2021-05-13 | 20.9 | 0 | 2.9 | 2020-05-13 | 12.8 | 5.2 | 0 | 2019-05-13 | 14 | 4 | 0 | 2018-05-13 | 20.9 | 0 | 2.9 | 2017-05-13 | 13.3 | 4.7 | 0 | 2016-05-13 | 21.7 | 0 | 3.7 | 1.39 | 3.03
2025-05-13 | 26.4 | 0 | 8.4 | 2024-05-13 | 17.6 | 0.4 | 0 | 2023-05-13 | 19 | 0 | 1 | 2022-05-13 | 29.8 | 0 | 11.8 | 2021-05-13 | 20.3 | 0 | 2.3 | 2020-05-13 | 13.7 | 4.3 | 0 | 2019-05-13 | 12 | 6 | 0 | 2018-05-13 | 21.6 | 0 | 3.6 | 2017-05-13 | 13.5 | 4.5 | 0 | 2016-05-13 | 21.6 | 0 | 3.6 | 1.52 | 3.07
2025-05-13 | 26.4 | 0 | 8.4 | 2024-05-13 | 17.9 | 0.1 | 0 | 2023-05-13 | 18.7 | 0 | 0.7 | 2022-05-13 | 29.4 | 0 | 11.4 | 2021-05-13 | 21.2 | 0 | 3.2 | 2020-05-13 | 13.8 | 4.2 | 0 | 2019-05-13 | 11.9 | 6.1 | 0 | 2018-05-13 | 22.1 | 0 | 4.1 | 2017-05-13 | 13.1 | 4.9 | 0 | 2016-05-13 | 21.1 | 0 | 3.1 | 1.53 | 3.09
2025-05-13 | 26.1 | 0 | 8.1 | 2024-05-13 | 16.9 | 1.1 | 0 | 2023-05-13 | 17.7 | 0.3 | 0 | 2022-05-13 | 28.1 | 0 | 10.1 | 2021-05-13 | 20.7 | 0 | 2.7 | 2020-05-13 | 14.3 | 3.7 | 0 | 2019-05-13 | 10.8 | 7.2 | 0 | 2018-05-13 | 21.4 | 0 | 3.4 | 2017-05-13 | 13 | 5 | 0 | 2016-05-13 | 21.3 | 0 | 3.3 | 1.73 | 2.76
2025-05-13 | 24.5 | 0 | 6.5 | 2024-05-13 | 17 | 1 | 0 | 2023-05-13 | 16.5 | 1.5 | 0 | 2022-05-13 | 26.7 | 0 | 8.7 | 2021-05-13 | 19.9 | 0 | 1.9 | 2020-05-13 | 13.7 | 4.3 | 0 | 2019-05-13 | 9.7 | 8.3 | 0 | 2018-05-13 | 20.6 | 0 | 2.6 | 2017-05-13 | 10.1 | 7.9 | 0 | 2016-05-13 | 20.4 | 0 | 2.4 | 2.3 | 2.21
2025-05-13 | 21.5 | 0 | 3.5 | 2024-05-13 | 15.2 | 2.8 | 0 | 2023-05-13 | 14.6 | 3.4 | 0 | 2022-05-13 | 24.9 | 0 | 6.9 | 2021-05-13 | 18.5 | 0 | 0.5 | 2020-05-13 | 11.4 | 6.6 | 0 | 2019-05-13 | 9.6 | 8.4 | 0 | 2018-05-13 | 18.9 | 0 | 0.9 | 2017-05-13 | 10 | 8 | 0 | 2016-05-13 | 18.7 | 0 | 0.7 | 2.92 | 1.25
2025-05-13 | 22.3 | 0 | 4.3 | 2024-05-13 | 16.6 | 1.4 | 0 | 2023-05-13 | 12.9 | 5.1 | 0 | 2022-05-13 | 23 | 0 | 5 | 2021-05-13 | 15.7 | 2.3 | 0 | 2020-05-13 | 10.8 | 7.2 | 0 | 2019-05-13 | 8.2 | 9.8 | 0 | 2018-05-13 | 15.9 | 2.1 | 0 | 2017-05-13 | 9.7 | 8.3 | 0 | 2016-05-13 | 17.1 | 0.9 | 0 | 3.71 | 0.93
2025-05-13 | 20.3 | 0 | 2.3 | 2024-05-13 | 16.1 | 1.9 | 0 | 2023-05-13 | 11.6 | 6.4 | 0 | 2022-05-13 | 21.6 | 0 | 3.6 | 2021-05-13 | 13.1 | 4.9 | 0 | 2020-05-13 | 7.5 | 10.5 | 0 | 2019-05-13 | 7.7 | 10.3 | 0 | 2018-05-13 | 15 | 3 | 0 | 2017-05-13 | 9.9 | 8.1 | 0 | 2016-05-13 | 16 | 2 | 0 | 4.71 | 0.59
2025-05-13 | 19.1 | 0 | 1.1 | 2024-05-13 | 15.8 | 2.2 | 0 | 2023-05-13 | 10.7 | 7.3 | 0 | 2022-05-13 | 20.4 | 0 | 2.4 | 2021-05-13 | 13.7 | 4.3 | 0 | 2020-05-13 | 7 | 11 | 0 | 2019-05-13 | 7.4 | 10.6 | 0 | 2018-05-13 | 14 | 4 | 0 | 2017-05-13 | 9.2 | 8.8 | 0 | 2016-05-13 | 13.5 | 4.5 | 0 | 5.27 | 0.35
2025-05-13 | 18.4 | 0 | 0.4 | 2024-05-13 | 15.8 | 2.2 | 0 | 2023-05-13 | 9.6 | 8.4 | 0 | 2022-05-13 | 19.4 | 0 | 1.4 | 2021-05-13 | 13.2 | 4.8 | 0 | 2020-05-13 | 6.1 | 11.9 | 0 | 2019-05-13 | 6.8 | 11.2 | 0 | 2018-05-13 | 12.5 | 5.5 | 0 | 2017-05-13 | 8.4 | 9.6 | 0 | 2016-05-13 | 12.6 | 5.4 | 0 | 5.9 | 0.18
2025-05-14 | 16 | 2 | 0 | 2024-05-14 | 15.4 | 2.6 | 0 | 2023-05-14 | 9 | 9 | 0 | 2022-05-14 | 18.1 | 0 | 0.1 | 2021-05-14 | 10.5 | 7.5 | 0 | 2020-05-14 | 4.6 | 13.4 | 0 | 2019-05-14 | 6.7 | 11.3 | 0 | 2018-05-14 | 12.3 | 5.7 | 0 | 2017-05-14 | 7.5 | 10.5 | 0 | 2016-05-14 | 10.9 | 7.1 | 0 | 6.91 | 0.01
2025-05-14 | 15.4 | 2.6 | 0 | 2024-05-14 | 14.8 | 3.2 | 0 | 2023-05-14 | 7.8 | 10.2 | 0 | 2022-05-14 | 17.5 | 0.5 | 0 | 2021-05-14 | 9.6 | 8.4 | 0 | 2020-05-14 | 2.6 | 15.4 | 0 | 2019-05-14 | 6.2 | 11.8 | 0 | 2018-05-14 | 11.7 | 6.3 | 0 | 2017-05-14 | 8.7 | 9.3 | 0 | 2016-05-14 | 10.7 | 7.3 | 0 | 7.5 | 0
2025-05-14 | 12.5 | 5.5 | 0 | 2024-05-14 | 14.3 | 3.7 | 0 | 2023-05-14 | 7.3 | 10.7 | 0 | 2022-05-14 | 17.4 | 0.6 | 0 | 2021-05-14 | 10.2 | 7.8 | 0 | 2020-05-14 | 2.1 | 15.9 | 0 | 2019-05-14 | 5.7 | 12.3 | 0 | 2018-05-14 | 10.9 | 7.1 | 0 | 2017-05-14 | 8.8 | 9.2 | 0 | 2016-05-14 | 9.2 | 8.8 | 0 | 8.16 | 0
2025-05-14 | 12.7 | 5.3 | 0 | 2024-05-14 | 14.3 | 3.7 | 0 | 2023-05-14 | 6.2 | 11.8 | 0 | 2022-05-14 | 15.3 | 2.7 | 0 | 2021-05-14 | 9.4 | 8.6 | 0 | 2020-05-14 | 2.8 | 15.2 | 0 | 2019-05-14 | 5.9 | 12.1 | 0 | 2018-05-14 | 10.7 | 7.3 | 0 | 2017-05-14 | 8.2 | 9.8 | 0 | 2016-05-14 | 9.1 | 8.9 | 0 | 8.54 | 0
2025-05-14 | 12.7 | 5.3 | 0 | 2024-05-14 | 14.2 | 3.8 | 0 | 2023-05-14 | 5.5 | 12.5 | 0 | 2022-05-14 | 14.8 | 3.2 | 0 | 2021-05-14 | 6.7 | 11.3 | 0 | 2020-05-14 | 0.6 | 17.4 | 0 | 2019-05-14 | 5.6 | 12.4 | 0 | 2018-05-14 | 10 | 8 | 0 | 2017-05-14 | 8.6 | 9.4 | 0 | 2016-05-14 | 8.4 | 9.6 | 0 | 9.29 | 0
2025-05-14 | 13 | 5 | 0 | 2024-05-14 | 14.1 | 3.9 | 0 | 2023-05-14 | 4.8 | 13.2 | 0 | 2022-05-14 | 15.8 | 2.2 | 0 | 2021-05-14 | 8.4 | 9.6 | 0 | 2020-05-14 | 2.7 | 15.3 | 0 | 2019-05-14 | 5.3 | 12.7 | 0 | 2018-05-14 | 9.8 | 8.2 | 0 | 2017-05-14 | 8.7 | 9.3 | 0 | 2016-05-14 | 7.3 | 10.7 | 0 | 9.01 | 0
2025-05-14 | 16.1 | 1.9 | 0 | 2024-05-14 | 14.2 | 3.8 | 0 | 2023-05-14 | 6.2 | 11.8 | 0 | 2022-05-14 | 17.9 | 0.1 | 0 | 2021-05-14 | 10.9 | 7.1 | 0 | 2020-05-14 | 5.2 | 12.8 | 0 | 2019-05-14 | 5.4 | 12.6 | 0 | 2018-05-14 | 10.8 | 7.2 | 0 | 2017-05-14 | 9.5 | 8.5 | 0 | 2016-05-14 | 10.5 | 7.5 | 0 | 7.33 | 0
2025-05-14 | 19.1 | 0 | 1.1 | 2024-05-14 | 14.3 | 3.7 | 0 | 2023-05-14 | 7.8 | 10.2 | 0 | 2022-05-14 | 20.6 | 0 | 2.6 | 2021-05-14 | 13.3 | 4.7 | 0 | 2020-05-14 | 7.8 | 10.2 | 0 | 2019-05-14 | 5.4 | 12.6 | 0 | 2018-05-14 | 13 | 5 | 0 | 2017-05-14 | 9.7 | 8.3 | 0 | 2016-05-14 | 12 | 6 | 0 | 6.07 | 0.37
2025-05-14 | 20.9 | 0 | 2.9 | 2024-05-14 | 14.4 | 3.6 | 0 | 2023-05-14 | 9.1 | 8.9 | 0 | 2022-05-14 | 22.6 | 0 | 4.6 | 2021-05-14 | 15.2 | 2.8 | 0 | 2020-05-14 | 10.3 | 7.7 | 0 | 2019-05-14 | 6 | 12 | 0 | 2018-05-14 | 15.2 | 2.8 | 0 | 2017-05-14 | 10.2 | 7.8 | 0 | 2016-05-14 | 12.6 | 5.4 | 0 | 5.1 | 0.75
2025-05-14 | 21 | 0 | 3 | 2024-05-14 | 14.9 | 3.1 | 0 | 2023-05-14 | 10.7 | 7.3 | 0 | 2022-05-14 | 24.9 | 0 | 6.9 | 2021-05-14 | 17.2 | 0.8 | 0 | 2020-05-14 | 12.6 | 5.4 | 0 | 2019-05-14 | 6.6 | 11.4 | 0 | 2018-05-14 | 18.5 | 0 | 0.5 | 2017-05-14 | 9.9 | 8.1 | 0 | 2016-05-14 | 14.1 | 3.9 | 0 | 4 | 1.04
2025-05-14 | 22.3 | 0 | 4.3 | 2024-05-14 | 17.8 | 0.2 | 0 | 2023-05-14 | 12 | 6 | 0 | 2022-05-14 | 26.5 | 0 | 8.5 | 2021-05-14 | 19.4 | 0 | 1.4 | 2020-05-14 | 14.3 | 3.7 | 0 | 2019-05-14 | 6.5 | 11.5 | 0 | 2018-05-14 | 21.4 | 0 | 3.4 | 2017-05-14 | 10.3 | 7.7 | 0 | 2016-05-14 | 15.7 | 2.3 | 0 | 3.14 | 1.76
2025-05-14 | 23.1 | 0 | 5.1 | 2024-05-14 | 18.2 | 0 | 0.2 | 2023-05-14 | 12.5 | 5.5 | 0 | 2022-05-14 | 27.8 | 0 | 9.8 | 2021-05-14 | 21.8 | 0 | 3.8 | 2020-05-14 | 15.8 | 2.2 | 0 | 2019-05-14 | 7.7 | 10.3 | 0 | 2018-05-14 | 23.1 | 0 | 5.1 | 2017-05-14 | 10.6 | 7.4 | 0 | 2016-05-14 | 16.6 | 1.4 | 0 | 2.68 | 2.4
2025-05-14 | 23.4 | 0 | 5.4 | 2024-05-14 | 18.2 | 0 | 0.2 | 2023-05-14 | 14.3 | 3.7 | 0 | 2022-05-14 | 29.3 | 0 | 11.3 | 2021-05-14 | 22.4 | 0 | 4.4 | 2020-05-14 | 16.4 | 1.6 | 0 | 2019-05-14 | 8.8 | 9.2 | 0 | 2018-05-14 | 23.9 | 0 | 5.9 | 2017-05-14 | 11.3 | 6.7 | 0 | 2016-05-14 | 17.3 | 0.7 | 0 | 2.19 | 2.72
2025-05-14 | 23.9 | 0 | 5.9 | 2024-05-14 | 19.1 | 0 | 1.1 | 2023-05-14 | 15.6 | 2.4 | 0 | 2022-05-14 | 30.1 | 0 | 12.1 | 2021-05-14 | 21.8 | 0 | 3.8 | 2020-05-14 | 17.6 | 0.4 | 0 | 2019-05-14 | 9.3 | 8.7 | 0 | 2018-05-14 | 24 | 0 | 6 | 2017-05-14 | 13.5 | 4.5 | 0 | 2016-05-14 | 17.1 | 0.9 | 0 | 1.69 | 2.89
2025-05-14 | 23.8 | 0 | 5.8 | 2024-05-14 | 18.9 | 0 | 0.9 | 2023-05-14 | 16.3 | 1.7 | 0 | 2022-05-14 | 29.6 | 0 | 11.6 | 2021-05-14 | 23.2 | 0 | 5.2 | 2020-05-14 | 17.3 | 0.7 | 0 | 2019-05-14 | 7.8 | 10.2 | 0 | 2018-05-14 | 24.2 | 0 | 6.2 | 2017-05-14 | 14 | 4 | 0 | 2016-05-14 | 16 | 2 | 0 | 1.86 | 2.97
2025-05-14 | 22.6 | 0 | 4.6 | 2024-05-14 | 20 | 0 | 2 | 2023-05-14 | 16.7 | 1.3 | 0 | 2022-05-14 | 30.5 | 0 | 12.5 | 2021-05-14 | 23.7 | 0 | 5.7 | 2020-05-14 | 16.4 | 1.6 | 0 | 2019-05-14 | 10.3 | 7.7 | 0 | 2018-05-14 | 25.3 | 0 | 7.3 | 2017-05-14 | 12.7 | 5.3 | 0 | 2016-05-14 | 13.9 | 4.1 | 0 | 2 | 3.21
2025-05-14 | 22.6 | 0 | 4.6 | 2024-05-14 | 20.1 | 0 | 2.1 | 2023-05-14 | 17 | 1 | 0 | 2022-05-14 | 30.2 | 0 | 12.2 | 2021-05-14 | 23.6 | 0 | 5.6 | 2020-05-14 | 15.7 | 2.3 | 0 | 2019-05-14 | 9.6 | 8.4 | 0 | 2018-05-14 | 24.2 | 0 | 6.2 | 2017-05-14 | 11.8 | 6.2 | 0 | 2016-05-14 | 14.5 | 3.5 | 0 | 2.14 | 3.07
2025-05-14 | 22.4 | 0 | 4.4 | 2024-05-14 | 20.5 | 0 | 2.5 | 2023-05-14 | 17.3 | 0.7 | 0 | 2022-05-14 | 29.6 | 0 | 11.6 | 2021-05-14 | 21.4 | 0 | 3.4 | 2020-05-14 | 15.9 | 2.1 | 0 | 2019-05-14 | 9.1 | 8.9 | 0 | 2018-05-14 | 23.3 | 0 | 5.3 | 2017-05-14 | 11.9 | 6.1 | 0 | 2016-05-14 | 16.6 | 1.4 | 0 | 1.92 | 2.72
2025-05-14 | 21.6 | 0 | 3.6 | 2024-05-14 | 20.3 | 0 | 2.3 | 2023-05-14 | 16.6 | 1.4 | 0 | 2022-05-14 | 28.2 | 0 | 10.2 | 2021-05-14 | 21.4 | 0 | 3.4 | 2020-05-14 | 15.5 | 2.5 | 0 | 2019-05-14 | 8.1 | 9.9 | 0 | 2018-05-14 | 22.4 | 0 | 4.4 | 2017-05-14 | 12.7 | 5.3 | 0 | 2016-05-14 | 15.6 | 2.4 | 0 | 2.15 | 2.39
2025-05-14 | 20.7 | 0 | 2.7 | 2024-05-14 | 18.7 | 0 | 0.7 | 2023-05-14 | 15.6 | 2.4 | 0 | 2022-05-14 | 23.1 | 0 | 5.1 | 2021-05-14 | 19.1 | 0 | 1.1 | 2020-05-14 | 14 | 4 | 0 | 2019-05-14 | 7.4 | 10.6 | 0 | 2018-05-14 | 20.8 | 0 | 2.8 | 2017-05-14 | 11.8 | 6.2 | 0 | 2016-05-14 | 13.6 | 4.4 | 0 | 2.76 | 1.24
2025-05-14 | 20.4 | 0 | 2.4 | 2024-05-14 | 16.7 | 1.3 | 0 | 2023-05-14 | 11.8 | 6.2 | 0 | 2022-05-14 | 21.1 | 0 | 3.1 | 2021-05-14 | 16.9 | 1.1 | 0 | 2020-05-14 | 13.7 | 4.3 | 0 | 2019-05-14 | 6.2 | 11.8 | 0 | 2018-05-14 | 19.1 | 0 | 1.1 | 2017-05-14 | 10.5 | 7.5 | 0 | 2016-05-14 | 10.7 | 7.3 | 0 | 3.95 | 0.66
2025-05-14 | 19.5 | 0 | 1.5 | 2024-05-14 | 16.9 | 1.1 | 0 | 2023-05-14 | 11.6 | 6.4 | 0 | 2022-05-14 | 20.2 | 0 | 2.2 | 2021-05-14 | 16.1 | 1.9 | 0 | 2020-05-14 | 12.6 | 5.4 | 0 | 2019-05-14 | 5.7 | 12.3 | 0 | 2018-05-14 | 17.4 | 0.6 | 0 | 2017-05-14 | 10.6 | 7.4 | 0 | 2016-05-14 | 9.1 | 8.9 | 0 | 4.4 | 0.37
2025-05-14 | 18.1 | 0 | 0.1 | 2024-05-14 | 15.7 | 2.3 | 0 | 2023-05-14 | 9.4 | 8.6 | 0 | 2022-05-14 | 18.5 | 0 | 0.5 | 2021-05-14 | 14.5 | 3.5 | 0 | 2020-05-14 | 12.3 | 5.7 | 0 | 2019-05-14 | 6.3 | 11.7 | 0 | 2018-05-14 | 16.6 | 1.4 | 0 | 2017-05-14 | 10.2 | 7.8 | 0 | 2016-05-14 | 7.3 | 10.7 | 0 | 5.17 | 0.06
2025-05-14 | 18.8 | 0 | 0.8 | 2024-05-14 | 14.8 | 3.2 | 0 | 2023-05-14 | 8.4 | 9.6 | 0 | 2022-05-14 | 19.2 | 0 | 1.2 | 2021-05-14 | 13.1 | 4.9 | 0 | 2020-05-14 | 12.7 | 5.3 | 0 | 2019-05-14 | 5.4 | 12.6 | 0 | 2018-05-14 | 15.8 | 2.2 | 0 | 2017-05-14 | 10.1 | 7.9 | 0 | 2016-05-14 | 6.2 | 11.8 | 0 | 5.75 | 0.2
2025-05-15 | 18.3 | 0 | 0.3 | 2024-05-15 | 13.7 | 4.3 | 0 | 2023-05-15 | 6.5 | 11.5 | 0 | 2022-05-15 | 18.3 | 0 | 0.3 | 2021-05-15 | 12.2 | 5.8 | 0 | 2020-05-15 | 12.3 | 5.7 | 0 | 2019-05-15 | 5.3 | 12.7 | 0 | 2018-05-15 | 15.8 | 2.2 | 0 | 2017-05-15 | 10.1 | 7.9 | 0 | 2016-05-15 | 5.8 | 12.2 | 0 | 6.23 | 0.06
2025-05-15 | 16.3 | 1.7 | 0 | 2024-05-15 | 12.9 | 5.1 | 0 | 2023-05-15 | 6 | 12 | 0 | 2022-05-15 | 17.2 | 0.8 | 0 | 2021-05-15 | 9.7 | 8.3 | 0 | 2020-05-15 | 10.9 | 7.1 | 0 | 2019-05-15 | 4.9 | 13.1 | 0 | 2018-05-15 | 14.6 | 3.4 | 0 | 2017-05-15 | 9.6 | 8.4 | 0 | 2016-05-15 | 5.8 | 12.2 | 0 | 7.21 | 0
2025-05-15 | 17.4 | 0.6 | 0 | 2024-05-15 | 12.5 | 5.5 | 0 | 2023-05-15 | 5.4 | 12.6 | 0 | 2022-05-15 | 17.1 | 0.9 | 0 | 2021-05-15 | 12.3 | 5.7 | 0 | 2020-05-15 | 10.6 | 7.4 | 0 | 2019-05-15 | 5.2 | 12.8 | 0 | 2018-05-15 | 13.6 | 4.4 | 0 | 2017-05-15 | 9.1 | 8.9 | 0 | 2016-05-15 | 6.3 | 11.7 | 0 | 7.05 | 0
2025-05-15 | 16.9 | 1.1 | 0 | 2024-05-15 | 12.2 | 5.8 | 0 | 2023-05-15 | 5.6 | 12.4 | 0 | 2022-05-15 | 16.8 | 1.2 | 0 | 2021-05-15 | 11.3 | 6.7 | 0 | 2020-05-15 | 10.9 | 7.1 | 0 | 2019-05-15 | 4.1 | 13.9 | 0 | 2018-05-15 | 12.6 | 5.4 | 0 | 2017-05-15 | 8.8 | 9.2 | 0 | 2016-05-15 | 6 | 12 | 0 | 7.48 | 0
2025-05-15 | 16.7 | 1.3 | 0 | 2024-05-15 | 12 | 6 | 0 | 2023-05-15 | 4.9 | 13.1 | 0 | 2022-05-15 | 16.7 | 1.3 | 0 | 2021-05-15 | 8.3 | 9.7 | 0 | 2020-05-15 | 9.7 | 8.3 | 0 | 2019-05-15 | 3.1 | 14.9 | 0 | 2018-05-15 | 13.3 | 4.7 | 0 | 2017-05-15 | 8.3 | 9.7 | 0 | 2016-05-15 | 5.1 | 12.9 | 0 | 8.19 | 0
2025-05-15 | 16.2 | 1.8 | 0 | 2024-05-15 | 11.4 | 6.6 | 0 | 2023-05-15 | 4.4 | 13.6 | 0 | 2022-05-15 | 16.7 | 1.3 | 0 | 2021-05-15 | 8 | 10 | 0 | 2020-05-15 | 9.2 | 8.8 | 0 | 2019-05-15 | 2.9 | 15.1 | 0 | 2018-05-15 | 13.3 | 4.7 | 0 | 2017-05-15 | 8.1 | 9.9 | 0 | 2016-05-15 | 5 | 13 | 0 | 8.48 | 0
2025-05-15 | 16.2 | 1.8 | 0 | 2024-05-15 | 11 | 7 | 0 | 2023-05-15 | 6.3 | 11.7 | 0 | 2022-05-15 | 17.4 | 0.6 | 0 | 2021-05-15 | 9.6 | 8.4 | 0 | 2020-05-15 | 9.6 | 8.4 | 0 | 2019-05-15 | 3.6 | 14.4 | 0 | 2018-05-15 | 13.8 | 4.2 | 0 | 2017-05-15 | 8.3 | 9.7 | 0 | 2016-05-15 | 5 | 13 | 0 | 7.92 | 0
2025-05-15 | 16.1 | 1.9 | 0 | 2024-05-15 | 11.4 | 6.6 | 0 | 2023-05-15 | 10 | 8 | 0 | 2022-05-15 | 18.9 | 0 | 0.9 | 2021-05-15 | 12.5 | 5.5 | 0 | 2020-05-15 | 9.6 | 8.4 | 0 | 2019-05-15 | 5.6 | 12.4 | 0 | 2018-05-15 | 14.4 | 3.6 | 0 | 2017-05-15 | 8.8 | 9.2 | 0 | 2016-05-15 | 5.5 | 12.5 | 0 | 6.81 | 0.09
2025-05-15 | 16.7 | 1.3 | 0 | 2024-05-15 | 11.8 | 6.2 | 0 | 2023-05-15 | 13.7 | 4.3 | 0 | 2022-05-15 | 20.3 | 0 | 2.3 | 2021-05-15 | 16.5 | 1.5 | 0 | 2020-05-15 | 10.9 | 7.1 | 0 | 2019-05-15 | 8.5 | 9.5 | 0 | 2018-05-15 | 15.8 | 2.2 | 0 | 2017-05-15 | 10 | 8 | 0 | 2016-05-15 | 6 | 12 | 0 | 5.21 | 0.23
2025-05-15 | 17.6 | 0.4 | 0 | 2024-05-15 | 12.8 | 5.2 | 0 | 2023-05-15 | 15.6 | 2.4 | 0 | 2022-05-15 | 20.7 | 0 | 2.7 | 2021-05-15 | 18.2 | 0 | 0.2 | 2020-05-15 | 11.7 | 6.3 | 0 | 2019-05-15 | 10.2 | 7.8 | 0 | 2018-05-15 | 16.9 | 1.1 | 0 | 2017-05-15 | 12.1 | 5.9 | 0 | 2016-05-15 | 7.8 | 10.2 | 0 | 3.93 | 0.29
2025-05-15 | 18.7 | 0 | 0.7 | 2024-05-15 | 14.1 | 3.9 | 0 | 2023-05-15 | 18.5 | 0 | 0.5 | 2022-05-15 | 21.2 | 0 | 3.2 | 2021-05-15 | 20.4 | 0 | 2.4 | 2020-05-15 | 11.2 | 6.8 | 0 | 2019-05-15 | 11.2 | 6.8 | 0 | 2018-05-15 | 16.1 | 1.9 | 0 | 2017-05-15 | 13.8 | 4.2 | 0 | 2016-05-15 | 7.5 | 10.5 | 0 | 3.41 | 0.68
2025-05-15 | 19.5 | 0 | 1.5 | 2024-05-15 | 14.9 | 3.1 | 0 | 2023-05-15 | 20.5 | 0 | 2.5 | 2022-05-15 | 23.8 | 0 | 5.8 | 2021-05-15 | 21.5 | 0 | 3.5 | 2020-05-15 | 11.1 | 6.9 | 0 | 2019-05-15 | 12.3 | 5.7 | 0 | 2018-05-15 | 16.5 | 1.5 | 0 | 2017-05-15 | 15.2 | 2.8 | 0 | 2016-05-15 | 8.4 | 9.6 | 0 | 2.96 | 1.33
2025-05-15 | 19.9 | 0 | 1.9 | 2024-05-15 | 15.6 | 2.4 | 0 | 2023-05-15 | 20 | 0 | 2 | 2022-05-15 | 24.6 | 0 | 6.6 | 2021-05-15 | 22.2 | 0 | 4.2 | 2020-05-15 | 10.9 | 7.1 | 0 | 2019-05-15 | 13.2 | 4.8 | 0 | 2018-05-15 | 17.6 | 0.4 | 0 | 2017-05-15 | 16.2 | 1.8 | 0 | 2016-05-15 | 9.1 | 8.9 | 0 | 2.54 | 1.47
2025-05-15 | 20.9 | 0 | 2.9 | 2024-05-15 | 16.7 | 1.3 | 0 | 2023-05-15 | 21.3 | 0 | 3.3 | 2022-05-15 | 23.3 | 0 | 5.3 | 2021-05-15 | 23 | 0 | 5 | 2020-05-15 | 11 | 7 | 0 | 2019-05-15 | 12 | 6 | 0 | 2018-05-15 | 17.2 | 0.8 | 0 | 2017-05-15 | 17.6 | 0.4 | 0 | 2016-05-15 | 8.7 | 9.3 | 0 | 2.48 | 1.65
2025-05-15 | 21.4 | 0 | 3.4 | 2024-05-15 | 17.9 | 0.1 | 0 | 2023-05-15 | 22.1 | 0 | 4.1 | 2022-05-15 | 21.5 | 0 | 3.5 | 2021-05-15 | 23.1 | 0 | 5.1 | 2020-05-15 | 10.6 | 7.4 | 0 | 2019-05-15 | 11.6 | 6.4 | 0 | 2018-05-15 | 17.7 | 0.3 | 0 | 2017-05-15 | 19.3 | 0 | 1.3 | 2016-05-15 | 8.3 | 9.7 | 0 | 2.39 | 1.74
2025-05-15 | 22.5 | 0 | 4.5 | 2024-05-15 | 19.8 | 0 | 1.8 | 2023-05-15 | 22.3 | 0 | 4.3 | 2022-05-15 | 19.3 | 0 | 1.3 | 2021-05-15 | 22.1 | 0 | 4.1 | 2020-05-15 | 10.7 | 7.3 | 0 | 2019-05-15 | 11.7 | 6.3 | 0 | 2018-05-15 | 19.1 | 0 | 1.1 | 2017-05-15 | 19.9 | 0 | 1.9 | 2016-05-15 | 7.7 | 10.3 | 0 | 2.39 | 1.9
2025-05-15 | 23 | 0 | 5 | 2024-05-15 | 19.2 | 0 | 1.2 | 2023-05-15 | 22.8 | 0 | 4.8 | 2022-05-15 | 19.8 | 0 | 1.8 | 2021-05-15 | 22.9 | 0 | 4.9 | 2020-05-15 | 10.9 | 7.1 | 0 | 2019-05-15 | 11.8 | 6.2 | 0 | 2018-05-15 | 19.6 | 0 | 1.6 | 2017-05-15 | 19.8 | 0 | 1.8 | 2016-05-15 | 7.3 | 10.7 | 0 | 2.4 | 2.11
2025-05-15 | 22.3 | 0 | 4.3 | 2024-05-15 | 19.7 | 0 | 1.7 | 2023-05-15 | 23.4 | 0 | 5.4 | 2022-05-15 | 20.8 | 0 | 2.8 | 2021-05-15 | 21.1 | 0 | 3.1 | 2020-05-15 | 11 | 7 | 0 | 2019-05-15 | 10.6 | 7.4 | 0 | 2018-05-15 | 19.4 | 0 | 1.4 | 2017-05-15 | 18.9 | 0 | 0.9 | 2016-05-15 | 6.7 | 11.3 | 0 | 2.57 | 1.96
2025-05-15 | 21.7 | 0 | 3.7 | 2024-05-15 | 19.1 | 0 | 1.1 | 2023-05-15 | 21.6 | 0 | 3.6 | 2022-05-15 | 20.6 | 0 | 2.6 | 2021-05-15 | 20.8 | 0 | 2.8 | 2020-05-15 | 11.6 | 6.4 | 0 | 2019-05-15 | 10.3 | 7.7 | 0 | 2018-05-15 | 18.1 | 0 | 0.1 | 2017-05-15 | 17.9 | 0.1 | 0 | 2016-05-15 | 5.2 | 12.8 | 0 | 2.7 | 1.39
2025-05-15 | 20.9 | 0 | 2.9 | 2024-05-15 | 17.1 | 0.9 | 0 | 2023-05-15 | 19.8 | 0 | 1.8 | 2022-05-15 | 18.8 | 0 | 0.8 | 2021-05-15 | 19.1 | 0 | 1.1 | 2020-05-15 | 11.9 | 6.1 | 0 | 2019-05-15 | 9.9 | 8.1 | 0 | 2018-05-15 | 16.2 | 1.8 | 0 | 2017-05-15 | 16.5 | 1.5 | 0 | 2016-05-15 | 3.8 | 14.2 | 0 | 3.26 | 0.66
2025-05-15 | 19.4 | 0 | 1.4 | 2024-05-15 | 16.5 | 1.5 | 0 | 2023-05-15 | 18.5 | 0 | 0.5 | 2022-05-15 | 19.4 | 0 | 1.4 | 2021-05-15 | 17.1 | 0.9 | 0 | 2020-05-15 | 10.7 | 7.3 | 0 | 2019-05-15 | 9.6 | 8.4 | 0 | 2018-05-15 | 15.4 | 2.6 | 0 | 2017-05-15 | 14.9 | 3.1 | 0 | 2016-05-15 | 3.8 | 14.2 | 0 | 3.8 | 0.33
2025-05-15 | 18.7 | 0 | 0.7 | 2024-05-15 | 16.8 | 1.2 | 0 | 2023-05-15 | 17.9 | 0.1 | 0 | 2022-05-15 | 17.8 | 0.2 | 0 | 2021-05-15 | 15.1 | 2.9 | 0 | 2020-05-15 | 11 | 7 | 0 | 2019-05-15 | 9.1 | 8.9 | 0 | 2018-05-15 | 13.7 | 4.3 | 0 | 2017-05-15 | 14.3 | 3.7 | 0 | 2016-05-15 | 4 | 14 | 0 | 4.23 | 0.07
2025-05-15 | 16.1 | 1.9 | 0 | 2024-05-15 | 14.6 | 3.4 | 0 | 2023-05-15 | 16.8 | 1.2 | 0 | 2022-05-15 | 16.8 | 1.2 | 0 | 2021-05-15 | 14.9 | 3.1 | 0 | 2020-05-15 | 12 | 6 | 0 | 2019-05-15 | 8.5 | 9.5 | 0 | 2018-05-15 | 12.1 | 5.9 | 0 | 2017-05-15 | 12.8 | 5.2 | 0 | 2016-05-15 | 4.1 | 13.9 | 0 | 5.13 | 0
2025-05-15 | 16.2 | 1.8 | 0 | 2024-05-15 | 14 | 4 | 0 | 2023-05-15 | 15.6 | 2.4 | 0 | 2022-05-15 | 16 | 2 | 0 | 2021-05-15 | 14 | 4 | 0 | 2020-05-15 | 11.6 | 6.4 | 0 | 2019-05-15 | 9.4 | 8.6 | 0 | 2018-05-15 | 10.5 | 7.5 | 0 | 2017-05-15 | 10.4 | 7.6 | 0 | 2016-05-15 | 4 | 14 | 0 | 5.83 | 0
2025-05-16 | 16.6 | 1.4 | 0 | 2024-05-16 | 14.8 | 3.2 | 0 | 2023-05-16 | 14.6 | 3.4 | 0 | 2022-05-16 | 16.4 | 1.6 | 0 | 2021-05-16 | 14.1 | 3.9 | 0 | 2020-05-16 | 11 | 7 | 0 | 2019-05-16 | 7.7 | 10.3 | 0 | 2018-05-16 | 9.3 | 8.7 | 0 | 2017-05-16 | 12.2 | 5.8 | 0 | 2016-05-16 | 3.9 | 14.1 | 0 | 5.94 | 0
2025-05-16 | 15.7 | 2.3 | 0 | 2024-05-16 | 15 | 3 | 0 | 2023-05-16 | 13.7 | 4.3 | 0 | 2022-05-16 | 15.8 | 2.2 | 0 | 2021-05-16 | 12.6 | 5.4 | 0 | 2020-05-16 | 11.1 | 6.9 | 0 | 2019-05-16 | 5.8 | 12.2 | 0 | 2018-05-16 | 7.9 | 10.1 | 0 | 2017-05-16 | 11 | 7 | 0 | 2016-05-16 | 3.8 | 14.2 | 0 | 6.76 | 0
2025-05-16 | 15.1 | 2.9 | 0 | 2024-05-16 | 12.7 | 5.3 | 0 | 2023-05-16 | 13.2 | 4.8 | 0 | 2022-05-16 | 15.7 | 2.3 | 0 | 2021-05-16 | 12.4 | 5.6 | 0 | 2020-05-16 | 10.8 | 7.2 | 0 | 2019-05-16 | 4.3 | 13.7 | 0 | 2018-05-16 | 6.8 | 11.2 | 0 | 2017-05-16 | 10.2 | 7.8 | 0 | 2016-05-16 | 3.7 | 14.3 | 0 | 7.51 | 0
2025-05-16 | 13.9 | 4.1 | 0 | 2024-05-16 | 12.1 | 5.9 | 0 | 2023-05-16 | 12.4 | 5.6 | 0 | 2022-05-16 | 15.4 | 2.6 | 0 | 2021-05-16 | 10.1 | 7.9 | 0 | 2020-05-16 | 10.5 | 7.5 | 0 | 2019-05-16 | 4.1 | 13.9 | 0 | 2018-05-16 | 5.6 | 12.4 | 0 | 2017-05-16 | 9 | 9 | 0 | 2016-05-16 | 3.6 | 14.4 | 0 | 8.33 | 0
2025-05-16 | 13.6 | 4.4 | 0 | 2024-05-16 | 12.2 | 5.8 | 0 | 2023-05-16 | 12.3 | 5.7 | 0 | 2022-05-16 | 15.4 | 2.6 | 0 | 2021-05-16 | 10.6 | 7.4 | 0 | 2020-05-16 | 10.6 | 7.4 | 0 | 2019-05-16 | 2.8 | 15.2 | 0 | 2018-05-16 | 3 | 15 | 0 | 2017-05-16 | 8.4 | 9.6 | 0 | 2016-05-16 | 3.3 | 14.7 | 0 | 8.78 | 0
2025-05-16 | 12.6 | 5.4 | 0 | 2024-05-16 | 12.6 | 5.4 | 0 | 2023-05-16 | 12.2 | 5.8 | 0 | 2022-05-16 | 14.8 | 3.2 | 0 | 2021-05-16 | 12.4 | 5.6 | 0 | 2020-05-16 | 10.3 | 7.7 | 0 | 2019-05-16 | 3.1 | 14.9 | 0 | 2018-05-16 | 5.4 | 12.6 | 0 | 2017-05-16 | 7.6 | 10.4 | 0 | 2016-05-16 | 3.3 | 14.7 | 0 | 8.57 | 0
2025-05-16 | 15.9 | 2.1 | 0 | 2024-05-16 | 13.2 | 4.8 | 0 | 2023-05-16 | 12.3 | 5.7 | 0 | 2022-05-16 | 15.2 | 2.8 | 0 | 2021-05-16 | 12.3 | 5.7 | 0 | 2020-05-16 | 10.4 | 7.6 | 0 | 2019-05-16 | 4.7 | 13.3 | 0 | 2018-05-16 | 6.1 | 11.9 | 0 | 2017-05-16 | 8.6 | 9.4 | 0 | 2016-05-16 | 3.4 | 14.6 | 0 | 7.79 | 0
2025-05-16 | 19.1 | 0 | 1.1 | 2024-05-16 | 14.6 | 3.4 | 0 | 2023-05-16 | 12.5 | 5.5 | 0 | 2022-05-16 | 15.9 | 2.1 | 0 | 2021-05-16 | 15.5 | 2.5 | 0 | 2020-05-16 | 11.3 | 6.7 | 0 | 2019-05-16 | 5.1 | 12.9 | 0 | 2018-05-16 | 7.9 | 10.1 | 0 | 2017-05-16 | 10.8 | 7.2 | 0 | 2016-05-16 | 3.8 | 14.2 | 0 | 6.46 | 0.11
2025-05-16 | 20.2 | 0 | 2.2 | 2024-05-16 | 15.5 | 2.5 | 0 | 2023-05-16 | 13.6 | 4.4 | 0 | 2022-05-16 | 18 | 0 | 0 | 2021-05-16 | 17.1 | 0.9 | 0 | 2020-05-16 | 11.1 | 6.9 | 0 | 2019-05-16 | 6.5 | 11.5 | 0 | 2018-05-16 | 9.7 | 8.3 | 0 | 2017-05-16 | 13.6 | 4.4 | 0 | 2016-05-16 | 4.3 | 13.7 | 0 | 5.26 | 0.22
2025-05-16 | 22.2 | 0 | 4.2 | 2024-05-16 | 17 | 1 | 0 | 2023-05-16 | 15.5 | 2.5 | 0 | 2022-05-16 | 19.3 | 0 | 1.3 | 2021-05-16 | 18.8 | 0 | 0.8 | 2020-05-16 | 13.3 | 4.7 | 0 | 2019-05-16 | 7.3 | 10.7 | 0 | 2018-05-16 | 11.9 | 6.1 | 0 | 2017-05-16 | 14.4 | 3.6 | 0 | 2016-05-16 | 5.2 | 12.8 | 0 | 4.14 | 0.63
2025-05-16 | 23.6 | 0 | 5.6 | 2024-05-16 | 16.9 | 1.1 | 0 | 2023-05-16 | 16.6 | 1.4 | 0 | 2022-05-16 | 20.5 | 0 | 2.5 | 2021-05-16 | 20.2 | 0 | 2.2 | 2020-05-16 | 13.7 | 4.3 | 0 | 2019-05-16 | 7.8 | 10.2 | 0 | 2018-05-16 | 13.8 | 4.2 | 0 | 2017-05-16 | 16.9 | 1.1 | 0 | 2016-05-16 | 7 | 11 | 0 | 3.33 | 1.03
2025-05-16 | 23.3 | 0 | 5.3 | 2024-05-16 | 18.9 | 0 | 0.9 | 2023-05-16 | 17.7 | 0.3 | 0 | 2022-05-16 | 21.1 | 0 | 3.1 | 2021-05-16 | 22.5 | 0 | 4.5 | 2020-05-16 | 14.9 | 3.1 | 0 | 2019-05-16 | 8.7 | 9.3 | 0 | 2018-05-16 | 16.7 | 1.3 | 0 | 2017-05-16 | 17.9 | 0.1 | 0 | 2016-05-16 | 7.2 | 10.8 | 0 | 2.49 | 1.38
2025-05-16 | 24.3 | 0 | 6.3 | 2024-05-16 | 20.2 | 0 | 2.2 | 2023-05-16 | 17.2 | 0.8 | 0 | 2022-05-16 | 21.6 | 0 | 3.6 | 2021-05-16 | 23.1 | 0 | 5.1 | 2020-05-16 | 15 | 3 | 0 | 2019-05-16 | 9.6 | 8.4 | 0 | 2018-05-16 | 19.4 | 0 | 1.4 | 2017-05-16 | 19.5 | 0 | 1.5 | 2016-05-16 | 8.2 | 9.8 | 0 | 2.2 | 2.01
2025-05-16 | 26.3 | 0 | 8.3 | 2024-05-16 | 20.8 | 0 | 2.8 | 2023-05-16 | 12.1 | 5.9 | 0 | 2022-05-16 | 20.8 | 0 | 2.8 | 2021-05-16 | 21.2 | 0 | 3.2 | 2020-05-16 | 15.2 | 2.8 | 0 | 2019-05-16 | 10.6 | 7.4 | 0 | 2018-05-16 | 22.1 | 0 | 4.1 | 2017-05-16 | 19.6 | 0 | 1.6 | 2016-05-16 | 8.9 | 9.1 | 0 | 2.52 | 2.28
2025-05-16 | 27.5 | 0 | 9.5 | 2024-05-16 | 21.6 | 0 | 3.6 | 2023-05-16 | 7.3 | 10.7 | 0 | 2022-05-16 | 20.6 | 0 | 2.6 | 2021-05-16 | 22.9 | 0 | 4.9 | 2020-05-16 | 16.5 | 1.5 | 0 | 2019-05-16 | 11.2 | 6.8 | 0 | 2018-05-16 | 22.8 | 0 | 4.8 | 2017-05-16 | 19.6 | 0 | 1.6 | 2016-05-16 | 10.5 | 7.5 | 0 | 2.65 | 2.7
2025-05-16 | 26.6 | 0 | 8.6 | 2024-05-16 | 22 | 0 | 4 | 2023-05-16 | 7.2 | 10.8 | 0 | 2022-05-16 | 17.4 | 0.6 | 0 | 2021-05-16 | 21.7 | 0 | 3.7 | 2020-05-16 | 16.1 | 1.9 | 0 | 2019-05-16 | 11.6 | 6.4 | 0 | 2018-05-16 | 23.4 | 0 | 5.4 | 2017-05-16 | 20.1 | 0 | 2.1 | 2016-05-16 | 12.1 | 5.9 | 0 | 2.56 | 2.38
2025-05-16 | 26.8 | 0 | 8.8 | 2024-05-16 | 22.9 | 0 | 4.9 | 2023-05-16 | 8 | 10 | 0 | 2022-05-16 | 13.7 | 4.3 | 0 | 2021-05-16 | 22.4 | 0 | 4.4 | 2020-05-16 | 16.2 | 1.8 | 0 | 2019-05-16 | 11.9 | 6.1 | 0 | 2018-05-16 | 23.1 | 0 | 5.1 | 2017-05-16 | 19.8 | 0 | 1.8 | 2016-05-16 | 11 | 7 | 0 | 2.92 | 2.5
2025-05-16 | 26.6 | 0 | 8.6 | 2024-05-16 | 22.2 | 0 | 4.2 | 2023-05-16 | 7.4 | 10.6 | 0 | 2022-05-16 | 13.2 | 4.8 | 0 | 2021-05-16 | 22.8 | 0 | 4.8 | 2020-05-16 | 16.3 | 1.7 | 0 | 2019-05-16 | 11.9 | 6.1 | 0 | 2018-05-16 | 22.3 | 0 | 4.3 | 2017-05-16 | 19.2 | 0 | 1.2 | 2016-05-16 | 12.4 | 5.6 | 0 | 2.88 | 2.31
2025-05-16 | 26 | 0 | 8 | 2024-05-16 | 21.8 | 0 | 3.8 | 2023-05-16 | 7 | 11 | 0 | 2022-05-16 | 12.2 | 5.8 | 0 | 2021-05-16 | 21.5 | 0 | 3.5 | 2020-05-16 | 16.1 | 1.9 | 0 | 2019-05-16 | 11.8 | 6.2 | 0 | 2018-05-16 | 21.4 | 0 | 3.4 | 2017-05-16 | 18.8 | 0 | 0.8 | 2016-05-16 | 11.9 | 6.1 | 0 | 3.1 | 1.95
2025-05-16 | 24.1 | 0 | 6.1 | 2024-05-16 | 20.6 | 0 | 2.6 | 2023-05-16 | 6.3 | 11.7 | 0 | 2022-05-16 | 12.2 | 5.8 | 0 | 2021-05-16 | 19.9 | 0 | 1.9 | 2020-05-16 | 14.3 | 3.7 | 0 | 2019-05-16 | 11.3 | 6.7 | 0 | 2018-05-16 | 20.1 | 0 | 2.1 | 2017-05-16 | 17.9 | 0.1 | 0 | 2016-05-16 | 10.2 | 7.8 | 0 | 3.58 | 1.27
2025-05-16 | 21.7 | 0 | 3.7 | 2024-05-16 | 17.9 | 0.1 | 0 | 2023-05-16 | 5.8 | 12.2 | 0 | 2022-05-16 | 12.3 | 5.7 | 0 | 2021-05-16 | 15.5 | 2.5 | 0 | 2020-05-16 | 13.4 | 4.6 | 0 | 2019-05-16 | 10.4 | 7.6 | 0 | 2018-05-16 | 18.7 | 0 | 0.7 | 2017-05-16 | 17.2 | 0.8 | 0 | 2016-05-16 | 8.7 | 9.3 | 0 | 4.28 | 0.44
2025-05-16 | 21.7 | 0 | 3.7 | 2024-05-16 | 16.1 | 1.9 | 0 | 2023-05-16 | 4.5 | 13.5 | 0 | 2022-05-16 | 11.6 | 6.4 | 0 | 2021-05-16 | 13.9 | 4.1 | 0 | 2020-05-16 | 13.2 | 4.8 | 0 | 2019-05-16 | 10 | 8 | 0 | 2018-05-16 | 17.8 | 0.2 | 0 | 2017-05-16 | 15.9 | 2.1 | 0 | 2016-05-16 | 5.7 | 12.3 | 0 | 5.33 | 0.37
2025-05-16 | 19.5 | 0 | 1.5 | 2024-05-16 | 15.3 | 2.7 | 0 | 2023-05-16 | 3.7 | 14.3 | 0 | 2022-05-16 | 11.3 | 6.7 | 0 | 2021-05-16 | 13.2 | 4.8 | 0 | 2020-05-16 | 12.2 | 5.8 | 0 | 2019-05-16 | 9.3 | 8.7 | 0 | 2018-05-16 | 17.2 | 0.8 | 0 | 2017-05-16 | 15.6 | 2.4 | 0 | 2016-05-16 | 5 | 13 | 0 | 5.92 | 0.15
2025-05-16 | 18.6 | 0 | 0.6 | 2024-05-16 | 15.5 | 2.5 | 0 | 2023-05-16 | 2.6 | 15.4 | 0 | 2022-05-16 | 10.6 | 7.4 | 0 | 2021-05-16 | 13.7 | 4.3 | 0 | 2020-05-16 | 9.8 | 8.2 | 0 | 2019-05-16 | 8.9 | 9.1 | 0 | 2018-05-16 | 16 | 2 | 0 | 2017-05-16 | 15 | 3 | 0 | 2016-05-16 | 3.5 | 14.5 | 0 | 6.64 | 0.06
2025-05-17 | 17.7 | 0.3 | 0 | 2024-05-17 | 14.6 | 3.4 | 0 | 2023-05-17 | 2.6 | 15.4 | 0 | 2022-05-17 | 10.4 | 7.6 | 0 | 2021-05-17 | 12.6 | 5.4 | 0 | 2020-05-17 | 9.2 | 8.8 | 0 | 2019-05-17 | 9 | 9 | 0 | 2018-05-17 | 15.4 | 2.6 | 0 | 2017-05-17 | 14.4 | 3.6 | 0 | 2016-05-17 | 4.7 | 13.3 | 0 | 6.94 | 0
2025-05-17 | 16.7 | 1.3 | 0 | 2024-05-17 | 13.8 | 4.2 | 0 | 2023-05-17 | 2.4 | 15.6 | 0 | 2022-05-17 | 10.3 | 7.7 | 0 | 2021-05-17 | 10.6 | 7.4 | 0 | 2020-05-17 | 10.5 | 7.5 | 0 | 2019-05-17 | 8.4 | 9.6 | 0 | 2018-05-17 | 15.9 | 2.1 | 0 | 2017-05-17 | 12.9 | 5.1 | 0 | 2016-05-17 | 3.7 | 14.3 | 0 | 7.48 | 0
2025-05-17 | 15 | 3 | 0 | 2024-05-17 | 13.4 | 4.6 | 0 | 2023-05-17 | 1.6 | 16.4 | 0 | 2022-05-17 | 10.3 | 7.7 | 0 | 2021-05-17 | 9.7 | 8.3 | 0 | 2020-05-17 | 10.1 | 7.9 | 0 | 2019-05-17 | 8 | 10 | 0 | 2018-05-17 | 15.8 | 2.2 | 0 | 2017-05-17 | 12.7 | 5.3 | 0 | 2016-05-17 | 4.6 | 13.4 | 0 | 7.88 | 0
2025-05-17 | 15 | 3 | 0 | 2024-05-17 | 13.2 | 4.8 | 0 | 2023-05-17 | 0.9 | 17.1 | 0 | 2022-05-17 | 10.3 | 7.7 | 0 | 2021-05-17 | 8.6 | 9.4 | 0 | 2020-05-17 | 8.9 | 9.1 | 0 | 2019-05-17 | 7.9 | 10.1 | 0 | 2018-05-17 | 14.6 | 3.4 | 0 | 2017-05-17 | 11.9 | 6.1 | 0 | 2016-05-17 | 4.3 | 13.7 | 0 | 8.44 | 0
2025-05-17 | 14.6 | 3.4 | 0 | 2024-05-17 | 12.7 | 5.3 | 0 | 2023-05-17 | 0.8 | 17.2 | 0 | 2022-05-17 | 10.4 | 7.6 | 0 | 2021-05-17 | 7.9 | 10.1 | 0 | 2020-05-17 | 8.3 | 9.7 | 0 | 2019-05-17 | 7.8 | 10.2 | 0 | 2018-05-17 | 13.4 | 4.6 | 0 | 2017-05-17 | 12 | 6 | 0 | 2016-05-17 | 1.4 | 16.6 | 0 | 9.07 | 0
2025-05-17 | 14.8 | 3.2 | 0 | 2024-05-17 | 13.4 | 4.6 | 0 | 2023-05-17 | 0.6 | 17.4 | 0 | 2022-05-17 | 9.8 | 8.2 | 0 | 2021-05-17 | 6.9 | 11.1 | 0 | 2020-05-17 | 7.8 | 10.2 | 0 | 2019-05-17 | 7.9 | 10.1 | 0 | 2018-05-17 | 13.9 | 4.1 | 0 | 2017-05-17 | 12 | 6 | 0 | 2016-05-17 | 0.5 | 17.5 | 0 | 9.24 | 0
2025-05-17 | 15 | 3 | 0 | 2024-05-17 | 15.4 | 2.6 | 0 | 2023-05-17 | 1.6 | 16.4 | 0 | 2022-05-17 | 9.9 | 8.1 | 0 | 2021-05-17 | 10.2 | 7.8 | 0 | 2020-05-17 | 9.5 | 8.5 | 0 | 2019-05-17 | 8.6 | 9.4 | 0 | 2018-05-17 | 13.4 | 4.6 | 0 | 2017-05-17 | 12.9 | 5.1 | 0 | 2016-05-17 | 3.4 | 14.6 | 0 | 8.01 | 0
2025-05-17 | 15.8 | 2.2 | 0 | 2024-05-17 | 16.7 | 1.3 | 0 | 2023-05-17 | 1.8 | 16.2 | 0 | 2022-05-17 | 10.4 | 7.6 | 0 | 2021-05-17 | 13.4 | 4.6 | 0 | 2020-05-17 | 11.8 | 6.2 | 0 | 2019-05-17 | 9.2 | 8.8 | 0 | 2018-05-17 | 13.4 | 4.6 | 0 | 2017-05-17 | 16.5 | 1.5 | 0 | 2016-05-17 | 6.7 | 11.3 | 0 | 6.43 | 0
2025-05-17 | 15.9 | 2.1 | 0 | 2024-05-17 | 18.6 | 0 | 0.6 | 2023-05-17 | 2.1 | 15.9 | 0 | 2022-05-17 | 11 | 7 | 0 | 2021-05-17 | 16.6 | 1.4 | 0 | 2020-05-17 | 13.8 | 4.2 | 0 | 2019-05-17 | 9.9 | 8.1 | 0 | 2018-05-17 | 13.8 | 4.2 | 0 | 2017-05-17 | 18.5 | 0 | 0.5 | 2016-05-17 | 7.9 | 10.1 | 0 | 5.3 | 0.11
2025-05-17 | 15.3 | 2.7 | 0 | 2024-05-17 | 21.3 | 0 | 3.3 | 2023-05-17 | 2.6 | 15.4 | 0 | 2022-05-17 | 11.2 | 6.8 | 0 | 2021-05-17 | 19.8 | 0 | 1.8 | 2020-05-17 | 15.1 | 2.9 | 0 | 2019-05-17 | 10.3 | 7.7 | 0 | 2018-05-17 | 14.9 | 3.1 | 0 | 2017-05-17 | 21.6 | 0 | 3.6 | 2016-05-17 | 10.2 | 7.8 | 0 | 4.64 | 0.87
2025-05-17 | 16 | 2 | 0 | 2024-05-17 | 22.4 | 0 | 4.4 | 2023-05-17 | 4.9 | 13.1 | 0 | 2022-05-17 | 12.7 | 5.3 | 0 | 2021-05-17 | 22.1 | 0 | 4.1 | 2020-05-17 | 16.5 | 1.5 | 0 | 2019-05-17 | 10.6 | 7.4 | 0 | 2018-05-17 | 15.7 | 2.3 | 0 | 2017-05-17 | 24.4 | 0 | 6.4 | 2016-05-17 | 11.8 | 6.2 | 0 | 3.78 | 1.49
2025-05-17 | 16.2 | 1.8 | 0 | 2024-05-17 | 23.3 | 0 | 5.3 | 2023-05-17 | 5.6 | 12.4 | 0 | 2022-05-17 | 14.1 | 3.9 | 0 | 2021-05-17 | 23.2 | 0 | 5.2 | 2020-05-17 | 17.1 | 0.9 | 0 | 2019-05-17 | 11.4 | 6.6 | 0 | 2018-05-17 | 16.8 | 1.2 | 0 | 2017-05-17 | 27.2 | 0 | 9.2 | 2016-05-17 | 13.2 | 4.8 | 0 | 3.16 | 1.97
2025-05-17 | 17.9 | 0.1 | 0 | 2024-05-17 | 23.8 | 0 | 5.8 | 2023-05-17 | 7.4 | 10.6 | 0 | 2022-05-17 | 12.6 | 5.4 | 0 | 2021-05-17 | 23.2 | 0 | 5.2 | 2020-05-17 | 17.6 | 0.4 | 0 | 2019-05-17 | 12.1 | 5.9 | 0 | 2018-05-17 | 18.3 | 0 | 0.3 | 2017-05-17 | 28.2 | 0 | 10.2 | 2016-05-17 | 13.5 | 4.5 | 0 | 2.69 | 2.15
2025-05-17 | 18.7 | 0 | 0.7 | 2024-05-17 | 23.5 | 0 | 5.5 | 2023-05-17 | 8.5 | 9.5 | 0 | 2022-05-17 | 13.8 | 4.2 | 0 | 2021-05-17 | 24.8 | 0 | 6.8 | 2020-05-17 | 18.4 | 0 | 0.4 | 2019-05-17 | 12.9 | 5.1 | 0 | 2018-05-17 | 18.2 | 0 | 0.2 | 2017-05-17 | 28.9 | 0 | 10.9 | 2016-05-17 | 14.6 | 3.4 | 0 | 2.22 | 2.45
2025-05-17 | 20.1 | 0 | 2.1 | 2024-05-17 | 23.4 | 0 | 5.4 | 2023-05-17 | 8.7 | 9.3 | 0 | 2022-05-17 | 14.7 | 3.3 | 0 | 2021-05-17 | 24.9 | 0 | 6.9 | 2020-05-17 | 19 | 0 | 1 | 2019-05-17 | 13.1 | 4.9 | 0 | 2018-05-17 | 17.7 | 0.3 | 0 | 2017-05-17 | 29.9 | 0 | 11.9 | 2016-05-17 | 15.2 | 2.8 | 0 | 2.06 | 2.73
2025-05-17 | 21.4 | 0 | 3.4 | 2024-05-17 | 23.2 | 0 | 5.2 | 2023-05-17 | 9.2 | 8.8 | 0 | 2022-05-17 | 14.4 | 3.6 | 0 | 2021-05-17 | 23.5 | 0 | 5.5 | 2020-05-17 | 18.7 | 0 | 0.7 | 2019-05-17 | 12.9 | 5.1 | 0 | 2018-05-17 | 17.1 | 0.9 | 0 | 2017-05-17 | 29.7 | 0 | 11.7 | 2016-05-17 | 15.4 | 2.6 | 0 | 2.1 | 2.65
2025-05-17 | 21.1 | 0 | 3.1 | 2024-05-17 | 22.9 | 0 | 4.9 | 2023-05-17 | 9.8 | 8.2 | 0 | 2022-05-17 | 14.7 | 3.3 | 0 | 2021-05-17 | 24.2 | 0 | 6.2 | 2020-05-17 | 19.1 | 0 | 1.1 | 2019-05-17 | 12.3 | 5.7 | 0 | 2018-05-17 | 17.1 | 0.9 | 0 | 2017-05-17 | 30.1 | 0 | 12.1 | 2016-05-17 | 12.5 | 5.5 | 0 | 2.36 | 2.74
2025-05-17 | 20.9 | 0 | 2.9 | 2024-05-17 | 22.6 | 0 | 4.6 | 2023-05-17 | 9.6 | 8.4 | 0 | 2022-05-17 | 13.4 | 4.6 | 0 | 2021-05-17 | 23.7 | 0 | 5.7 | 2020-05-17 | 18.8 | 0 | 0.8 | 2019-05-17 | 12.8 | 5.2 | 0 | 2018-05-17 | 16.7 | 1.3 | 0 | 2017-05-17 | 29.5 | 0 | 11.5 | 2016-05-17 | 11.1 | 6.9 | 0 | 2.64 | 2.55
2025-05-17 | 16.4 | 1.6 | 0 | 2024-05-17 | 21.5 | 0 | 3.5 | 2023-05-17 | 8.6 | 9.4 | 0 | 2022-05-17 | 12.6 | 5.4 | 0 | 2021-05-17 | 22.2 | 0 | 4.2 | 2020-05-17 | 17.6 | 0.4 | 0 | 2019-05-17 | 11.4 | 6.6 | 0 | 2018-05-17 | 16.1 | 1.9 | 0 | 2017-05-17 | 28.4 | 0 | 10.4 | 2016-05-17 | 10.3 | 7.7 | 0 | 3.3 | 1.81
2025-05-17 | 15.7 | 2.3 | 0 | 2024-05-17 | 21.2 | 0 | 3.2 | 2023-05-17 | 7.6 | 10.4 | 0 | 2022-05-17 | 12.1 | 5.9 | 0 | 2021-05-17 | 20.9 | 0 | 2.9 | 2020-05-17 | 16.4 | 1.6 | 0 | 2019-05-17 | 11.1 | 6.9 | 0 | 2018-05-17 | 14.6 | 3.4 | 0 | 2017-05-17 | 26.6 | 0 | 8.6 | 2016-05-17 | 9.8 | 8.2 | 0 | 3.87 | 1.47
2025-05-17 | 15.7 | 2.3 | 0 | 2024-05-17 | 18.3 | 0 | 0.3 | 2023-05-17 | 4.6 | 13.4 | 0 | 2022-05-17 | 10.9 | 7.1 | 0 | 2021-05-17 | 20 | 0 | 2 | 2020-05-17 | 15.2 | 2.8 | 0 | 2019-05-17 | 10.1 | 7.9 | 0 | 2018-05-17 | 12.6 | 5.4 | 0 | 2017-05-17 | 24.7 | 0 | 6.7 | 2016-05-17 | 9.1 | 8.9 | 0 | 4.78 | 0.9
2025-05-17 | 14.9 | 3.1 | 0 | 2024-05-17 | 17 | 1 | 0 | 2023-05-17 | 4.7 | 13.3 | 0 | 2022-05-17 | 9.8 | 8.2 | 0 | 2021-05-17 | 19.2 | 0 | 1.2 | 2020-05-17 | 15.9 | 2.1 | 0 | 2019-05-17 | 9.2 | 8.8 | 0 | 2018-05-17 | 11.8 | 6.2 | 0 | 2017-05-17 | 24.1 | 0 | 6.1 | 2016-05-17 | 8.6 | 9.4 | 0 | 5.21 | 0.73
2025-05-17 | 13.1 | 4.9 | 0 | 2024-05-17 | 16.3 | 1.7 | 0 | 2023-05-17 | 3 | 15 | 0 | 2022-05-17 | 8.6 | 9.4 | 0 | 2021-05-17 | 19 | 0 | 1 | 2020-05-17 | 15.3 | 2.7 | 0 | 2019-05-17 | 8.6 | 9.4 | 0 | 2018-05-17 | 10.4 | 7.6 | 0 | 2017-05-17 | 23.5 | 0 | 5.5 | 2016-05-17 | 7.9 | 10.1 | 0 | 6.08 | 0.65
2025-05-17 | 13.2 | 4.8 | 0 | 2024-05-17 | 16.6 | 1.4 | 0 | 2023-05-17 | 2.5 | 15.5 | 0 | 2022-05-17 | 6.7 | 11.3 | 0 | 2021-05-17 | 17.9 | 0.1 | 0 | 2020-05-17 | 14.3 | 3.7 | 0 | 2019-05-17 | 7.7 | 10.3 | 0 | 2018-05-17 | 9.5 | 8.5 | 0 | 2017-05-17 | 23 | 0 | 5 | 2016-05-17 | 8.4 | 9.6 | 0 | 6.52 | 0.5
2025-05-18 | 13.2 | 4.8 | 0 | 2024-05-18 | 16.8 | 1.2 | 0 | 2023-05-18 | 1 | 17 | 0 | 2022-05-18 | 8.3 | 9.7 | 0 | 2021-05-18 | 15.9 | 2.1 | 0 | 2020-05-18 | 13.7 | 4.3 | 0 | 2019-05-18 | 6.9 | 11.1 | 0 | 2018-05-18 | 8.5 | 9.5 | 0 | 2017-05-18 | 22.1 | 0 | 4.1 | 2016-05-18 | 7.8 | 10.2 | 0 | 6.99 | 0.41
2025-05-18 | 12.1 | 5.9 | 0 | 2024-05-18 | 16.1 | 1.9 | 0 | 2023-05-18 | 0.8 | 17.2 | 0 | 2022-05-18 | 6 | 12 | 0 | 2021-05-18 | 14.1 | 3.9 | 0 | 2020-05-18 | 13.3 | 4.7 | 0 | 2019-05-18 | 7 | 11 | 0 | 2018-05-18 | 7.6 | 10.4 | 0 | 2017-05-18 | 20.7 | 0 | 2.7 | 2016-05-18 | 7.5 | 10.5 | 0 | 7.75 | 0.27
2025-05-18 | 12 | 6 | 0 | 2024-05-18 | 15.1 | 2.9 | 0 | 2023-05-18 | 0.6 | 17.4 | 0 | 2022-05-18 | 5.3 | 12.7 | 0 | 2021-05-18 | 14.9 | 3.1 | 0 | 2020-05-18 | 13.9 | 4.1 | 0 | 2019-05-18 | 6.9 | 11.1 | 0 | 2018-05-18 | 5.4 | 12.6 | 0 | 2017-05-18 | 20.8 | 0 | 2.8 | 2016-05-18 | 7 | 11 | 0 | 8.09 | 0.28
2025-05-18 | 11.9 | 6.1 | 0 | 2024-05-18 | 15.6 | 2.4 | 0 | 2023-05-18 | -3 | 21 | 0 | 2022-05-18 | 5.5 | 12.5 | 0 | 2021-05-18 | 13 | 5 | 0 | 2020-05-18 | 13.4 | 4.6 | 0 | 2019-05-18 | 6.4 | 11.6 | 0 | 2018-05-18 | 6.3 | 11.7 | 0 | 2017-05-18 | 20.4 | 0 | 2.4 | 2016-05-18 | 6.6 | 11.4 | 0 | 8.63 | 0.24
2025-05-18 | 11.6 | 6.4 | 0 | 2024-05-18 | 14.8 | 3.2 | 0 | 2023-05-18 | -1.3 | 19.3 | 0 | 2022-05-18 | 6 | 12 | 0 | 2021-05-18 | 15.3 | 2.7 | 0 | 2020-05-18 | 12.5 | 5.5 | 0 | 2019-05-18 | 6.5 | 11.5 | 0 | 2018-05-18 | 4.4 | 13.6 | 0 | 2017-05-18 | 20.3 | 0 | 2.3 | 2016-05-18 | 5.9 | 12.1 | 0 | 8.63 | 0.23
2025-05-18 | 11.7 | 6.3 | 0 | 2024-05-18 | 14.9 | 3.1 | 0 | 2023-05-18 | -0.1 | 18.1 | 0 | 2022-05-18 | 4.9 | 13.1 | 0 | 2021-05-18 | 13.2 | 4.8 | 0 | 2020-05-18 | 11 | 7 | 0 | 2019-05-18 | 6 | 12 | 0 | 2018-05-18 | 3.6 | 14.4 | 0 | 2017-05-18 | 20.4 | 0 | 2.4 | 2016-05-18 | 5.5 | 12.5 | 0 | 9.13 | 0.24
2025-05-18 | 11.9 | 6.1 | 0 | 2024-05-18 | 16 | 2 | 0 | 2023-05-18 | 1.1 | 16.9 | 0 | 2022-05-18 | 7.1 | 10.9 | 0 | 2021-05-18 | 14.7 | 3.3 | 0 | 2020-05-18 | 11.3 | 6.7 | 0 | 2019-05-18 | 8 | 10 | 0 | 2018-05-18 | 6.4 | 11.6 | 0 | 2017-05-18 | 21.8 | 0 | 3.8 | 2016-05-18 | 6.6 | 11.4 | 0 | 7.89 | 0.38
2025-05-18 | 12.4 | 5.6 | 0 | 2024-05-18 | 16.7 | 1.3 | 0 | 2023-05-18 | 5.2 | 12.8 | 0 | 2022-05-18 | 8.5 | 9.5 | 0 | 2021-05-18 | 16 | 2 | 0 | 2020-05-18 | 12.4 | 5.6 | 0 | 2019-05-18 | 9.7 | 8.3 | 0 | 2018-05-18 | 7.9 | 10.1 | 0 | 2017-05-18 | 22.9 | 0 | 4.9 | 2016-05-18 | 7.3 | 10.7 | 0 | 6.59 | 0.49
2025-05-18 | 12.2 | 5.8 | 0 | 2024-05-18 | 17.7 | 0.3 | 0 | 2023-05-18 | 6.8 | 11.2 | 0 | 2022-05-18 | 9.1 | 8.9 | 0 | 2021-05-18 | 18.1 | 0 | 0.1 | 2020-05-18 | 13.5 | 4.5 | 0 | 2019-05-18 | 10.9 | 7.1 | 0 | 2018-05-18 | 9.9 | 8.1 | 0 | 2017-05-18 | 24.5 | 0 | 6.5 | 2016-05-18 | 8.3 | 9.7 | 0 | 5.56 | 0.66
2025-05-18 | 11.4 | 6.6 | 0 | 2024-05-18 | 20.2 | 0 | 2.2 | 2023-05-18 | 9.3 | 8.7 | 0 | 2022-05-18 | 10.8 | 7.2 | 0 | 2021-05-18 | 20.2 | 0 | 2.2 | 2020-05-18 | 15.5 | 2.5 | 0 | 2019-05-18 | 11.9 | 6.1 | 0 | 2018-05-18 | 10.8 | 7.2 | 0 | 2017-05-18 | 26.2 | 0 | 8.2 | 2016-05-18 | 10.3 | 7.7 | 0 | 4.6 | 1.26
2025-05-18 | 10.2 | 7.8 | 0 | 2024-05-18 | 20.8 | 0 | 2.8 | 2023-05-18 | 9.6 | 8.4 | 0 | 2022-05-18 | 11.6 | 6.4 | 0 | 2021-05-18 | 21.6 | 0 | 3.6 | 2020-05-18 | 16.2 | 1.8 | 0 | 2019-05-18 | 12.8 | 5.2 | 0 | 2018-05-18 | 12.7 | 5.3 | 0 | 2017-05-18 | 27.3 | 0 | 9.3 | 2016-05-18 | 11.5 | 6.5 | 0 | 4.14 | 1.57
2025-05-18 | 9.7 | 8.3 | 0 | 2024-05-18 | 22.2 | 0 | 4.2 | 2023-05-18 | 11.9 | 6.1 | 0 | 2022-05-18 | 13.2 | 4.8 | 0 | 2021-05-18 | 22.3 | 0 | 4.3 | 2020-05-18 | 17.8 | 0.2 | 0 | 2019-05-18 | 13.1 | 4.9 | 0 | 2018-05-18 | 12.9 | 5.1 | 0 | 2017-05-18 | 28.4 | 0 | 10.4 | 2016-05-18 | 13.1 | 4.9 | 0 | 3.43 | 1.89
2025-05-18 | 10.3 | 7.7 | 0 | 2024-05-18 | 23 | 0 | 5 | 2023-05-18 | 12.6 | 5.4 | 0 | 2022-05-18 | 14.2 | 3.8 | 0 | 2021-05-18 | 23.9 | 0 | 5.9 | 2020-05-18 | 18.9 | 0 | 0.9 | 2019-05-18 | 13.9 | 4.1 | 0 | 2018-05-18 | 14.2 | 3.8 | 0 | 2017-05-18 | 29.5 | 0 | 11.5 | 2016-05-18 | 14.3 | 3.7 | 0 | 2.85 | 2.33
2025-05-18 | 10.8 | 7.2 | 0 | 2024-05-18 | 23.1 | 0 | 5.1 | 2023-05-18 | 13.9 | 4.1 | 0 | 2022-05-18 | 15.5 | 2.5 | 0 | 2021-05-18 | 24.5 | 0 | 6.5 | 2020-05-18 | 18.7 | 0 | 0.7 | 2019-05-18 | 14.2 | 3.8 | 0 | 2018-05-18 | 15.2 | 2.8 | 0 | 2017-05-18 | 29.5 | 0 | 11.5 | 2016-05-18 | 16 | 2 | 0 | 2.24 | 2.38
2025-05-18 | 10.2 | 7.8 | 0 | 2024-05-18 | 22 | 0 | 4 | 2023-05-18 | 14.8 | 3.2 | 0 | 2022-05-18 | 16.1 | 1.9 | 0 | 2021-05-18 | 25.7 | 0 | 7.7 | 2020-05-18 | 19.4 | 0 | 1.4 | 2019-05-18 | 14 | 4 | 0 | 2018-05-18 | 16.1 | 1.9 | 0 | 2017-05-18 | 29.6 | 0 | 11.6 | 2016-05-18 | 15.8 | 2.2 | 0 | 2.1 | 2.47
2025-05-18 | 10.6 | 7.4 | 0 | 2024-05-18 | 22.1 | 0 | 4.1 | 2023-05-18 | 15.6 | 2.4 | 0 | 2022-05-18 | 16.9 | 1.1 | 0 | 2021-05-18 | 25.4 | 0 | 7.4 | 2020-05-18 | 20.6 | 0 | 2.6 | 2019-05-18 | 14.2 | 3.8 | 0 | 2018-05-18 | 16.8 | 1.2 | 0 | 2017-05-18 | 29.9 | 0 | 11.9 | 2016-05-18 | 16.1 | 1.9 | 0 | 1.78 | 2.6
2025-05-18 | 10 | 8 | 0 | 2024-05-18 | 22.7 | 0 | 4.7 | 2023-05-18 | 15.6 | 2.4 | 0 | 2022-05-18 | 17.4 | 0.6 | 0 | 2021-05-18 | 25.5 | 0 | 7.5 | 2020-05-18 | 20.4 | 0 | 2.4 | 2019-05-18 | 14.5 | 3.5 | 0 | 2018-05-18 | 17 | 1 | 0 | 2017-05-18 | 29.5 | 0 | 11.5 | 2016-05-18 | 16.3 | 1.7 | 0 | 1.72 | 2.61
2025-05-18 | 9.3 | 8.7 | 0 | 2024-05-18 | 22.4 | 0 | 4.4 | 2023-05-18 | 15.7 | 2.3 | 0 | 2022-05-18 | 17.3 | 0.7 | 0 | 2021-05-18 | 25 | 0 | 7 | 2020-05-18 | 19.1 | 0 | 1.1 | 2019-05-18 | 14.5 | 3.5 | 0 | 2018-05-18 | 17.2 | 0.8 | 0 | 2017-05-18 | 28.9 | 0 | 10.9 | 2016-05-18 | 16.3 | 1.7 | 0 | 1.77 | 2.34
2025-05-18 | 8.3 | 9.7 | 0 | 2024-05-18 | 23 | 0 | 5 | 2023-05-18 | 14.8 | 3.2 | 0 | 2022-05-18 | 16.3 | 1.7 | 0 | 2021-05-18 | 24.3 | 0 | 6.3 | 2020-05-18 | 18.3 | 0 | 0.3 | 2019-05-18 | 14.2 | 3.8 | 0 | 2018-05-18 | 16.5 | 1.5 | 0 | 2017-05-18 | 27.7 | 0 | 9.7 | 2016-05-18 | 15.8 | 2.2 | 0 | 2.21 | 2.13
2025-05-18 | 8.2 | 9.8 | 0 | 2024-05-18 | 20.3 | 0 | 2.3 | 2023-05-18 | 12.9 | 5.1 | 0 | 2022-05-18 | 14.1 | 3.9 | 0 | 2021-05-18 | 22.4 | 0 | 4.4 | 2020-05-18 | 16.9 | 1.1 | 0 | 2019-05-18 | 13.4 | 4.6 | 0 | 2018-05-18 | 14.8 | 3.2 | 0 | 2017-05-18 | 27 | 0 | 9 | 2016-05-18 | 14.7 | 3.3 | 0 | 3.1 | 1.57
2025-05-18 | 8.1 | 9.9 | 0 | 2024-05-18 | 18.5 | 0 | 0.5 | 2023-05-18 | 11 | 7 | 0 | 2022-05-18 | 12.5 | 5.5 | 0 | 2021-05-18 | 20.4 | 0 | 2.4 | 2020-05-18 | 14.5 | 3.5 | 0 | 2019-05-18 | 12.3 | 5.7 | 0 | 2018-05-18 | 12.3 | 5.7 | 0 | 2017-05-18 | 19.4 | 0 | 1.4 | 2016-05-18 | 13.7 | 4.3 | 0 | 4.16 | 0.43
2025-05-18 | 7.9 | 10.1 | 0 | 2024-05-18 | 17.7 | 0.3 | 0 | 2023-05-18 | 9 | 9 | 0 | 2022-05-18 | 10.3 | 7.7 | 0 | 2021-05-18 | 16.3 | 1.7 | 0 | 2020-05-18 | 12.4 | 5.6 | 0 | 2019-05-18 | 12.8 | 5.2 | 0 | 2018-05-18 | 11.1 | 6.9 | 0 | 2017-05-18 | 20.6 | 0 | 2.6 | 2016-05-18 | 13 | 5 | 0 | 5.15 | 0.26
2025-05-18 | 7.6 | 10.4 | 0 | 2024-05-18 | 16.9 | 1.1 | 0 | 2023-05-18 | 8.1 | 9.9 | 0 | 2022-05-18 | 9 | 9 | 0 | 2021-05-18 | 15.5 | 2.5 | 0 | 2020-05-18 | 11.2 | 6.8 | 0 | 2019-05-18 | 11.3 | 6.7 | 0 | 2018-05-18 | 9.7 | 8.3 | 0 | 2017-05-18 | 19.6 | 0 | 1.6 | 2016-05-18 | 9.1 | 8.9 | 0 | 6.36 | 0.16
2025-05-18 | 7.3 | 10.7 | 0 | 2024-05-18 | 16.4 | 1.6 | 0 | 2023-05-18 | 6.5 | 11.5 | 0 | 2022-05-18 | 7.7 | 10.3 | 0 | 2021-05-18 | 15.2 | 2.8 | 0 | 2020-05-18 | 11.4 | 6.6 | 0 | 2019-05-18 | 11 | 7 | 0 | 2018-05-18 | 8.3 | 9.7 | 0 | 2017-05-18 | 18.8 | 0 | 0.8 | 2016-05-18 | 11.4 | 6.6 | 0 | 6.68 | 0.08
2025-05-19 | 7.3 | 10.7 | 0 | 2024-05-19 | 15.1 | 2.9 | 0 | 2023-05-19 | 6 | 12 | 0 | 2022-05-19 | 7.1 | 10.9 | 0 | 2021-05-19 | 15.7 | 2.3 | 0 | 2020-05-19 | 11.7 | 6.3 | 0 | 2019-05-19 | 11.2 | 6.8 | 0 | 2018-05-19 | 7.2 | 10.8 | 0 | 2017-05-19 | 18.1 | 0 | 0.1 | 2016-05-19 | 10.7 | 7.3 | 0 | 7 | 0.01
2025-05-19 | 7 | 11 | 0 | 2024-05-19 | 13.7 | 4.3 | 0 | 2023-05-19 | 5.6 | 12.4 | 0 | 2022-05-19 | 5.2 | 12.8 | 0 | 2021-05-19 | 14.1 | 3.9 | 0 | 2020-05-19 | 10.7 | 7.3 | 0 | 2019-05-19 | 10.9 | 7.1 | 0 | 2018-05-19 | 8.3 | 9.7 | 0 | 2017-05-19 | 17.5 | 0.5 | 0 | 2016-05-19 | 11 | 7 | 0 | 7.6 | 0
2025-05-19 | 6.6 | 11.4 | 0 | 2024-05-19 | 12.4 | 5.6 | 0 | 2023-05-19 | 5.7 | 12.3 | 0 | 2022-05-19 | 5 | 13 | 0 | 2021-05-19 | 12.7 | 5.3 | 0 | 2020-05-19 | 9.2 | 8.8 | 0 | 2019-05-19 | 10.8 | 7.2 | 0 | 2018-05-19 | 7.6 | 10.4 | 0 | 2017-05-19 | 16 | 2 | 0 | 2016-05-19 | 10.7 | 7.3 | 0 | 8.33 | 0
2025-05-19 | 6.2 | 11.8 | 0 | 2024-05-19 | 12.1 | 5.9 | 0 | 2023-05-19 | 5 | 13 | 0 | 2022-05-19 | 4.1 | 13.9 | 0 | 2021-05-19 | 12.8 | 5.2 | 0 | 2020-05-19 | 8.2 | 9.8 | 0 | 2019-05-19 | 11.1 | 6.9 | 0 | 2018-05-19 | 7 | 11 | 0 | 2017-05-19 | 13.1 | 4.9 | 0 | 2016-05-19 | 9 | 9 | 0 | 9.14 | 0
2025-05-19 | 5.6 | 12.4 | 0 | 2024-05-19 | 12.1 | 5.9 | 0 | 2023-05-19 | 3.3 | 14.7 | 0 | 2022-05-19 | 5.4 | 12.6 | 0 | 2021-05-19 | 12.3 | 5.7 | 0 | 2020-05-19 | 8.1 | 9.9 | 0 | 2019-05-19 | 10.2 | 7.8 | 0 | 2018-05-19 | 6.8 | 11.2 | 0 | 2017-05-19 | 10.9 | 7.1 | 0 | 2016-05-19 | 8.9 | 9.1 | 0 | 9.64 | 0
2025-05-19 | 5.3 | 12.7 | 0 | 2024-05-19 | 12.6 | 5.4 | 0 | 2023-05-19 | 2.8 | 15.2 | 0 | 2022-05-19 | 5.1 | 12.9 | 0 | 2021-05-19 | 10.5 | 7.5 | 0 | 2020-05-19 | 7.9 | 10.1 | 0 | 2019-05-19 | 9.6 | 8.4 | 0 | 2018-05-19 | 7.2 | 10.8 | 0 | 2017-05-19 | 9.4 | 8.6 | 0 | 2016-05-19 | 8.8 | 9.2 | 0 | 10.08 | 0
2025-05-19 | 5.3 | 12.7 | 0 | 2024-05-19 | 14.9 | 3.1 | 0 | 2023-05-19 | 5.6 | 12.4 | 0 | 2022-05-19 | 6.1 | 11.9 | 0 | 2021-05-19 | 13.9 | 4.1 | 0 | 2020-05-19 | 9.7 | 8.3 | 0 | 2019-05-19 | 9.4 | 8.6 | 0 | 2018-05-19 | 8.3 | 9.7 | 0 | 2017-05-19 | 9.3 | 8.7 | 0 | 2016-05-19 | 11.2 | 6.8 | 0 | 8.63 | 0
2025-05-19 | 5.6 | 12.4 | 0 | 2024-05-19 | 16.3 | 1.7 | 0 | 2023-05-19 | 10.2 | 7.8 | 0 | 2022-05-19 | 7.8 | 10.2 | 0 | 2021-05-19 | 17.9 | 0.1 | 0 | 2020-05-19 | 11.8 | 6.2 | 0 | 2019-05-19 | 9.9 | 8.1 | 0 | 2018-05-19 | 10.9 | 7.1 | 0 | 2017-05-19 | 9.1 | 8.9 | 0 | 2016-05-19 | 13.7 | 4.3 | 0 | 6.68 | 0
2025-05-19 | 5.7 | 12.3 | 0 | 2024-05-19 | 17.5 | 0.5 | 0 | 2023-05-19 | 14.8 | 3.2 | 0 | 2022-05-19 | 8.5 | 9.5 | 0 | 2021-05-19 | 19.9 | 0 | 1.9 | 2020-05-19 | 13.6 | 4.4 | 0 | 2019-05-19 | 10.8 | 7.2 | 0 | 2018-05-19 | 13.2 | 4.8 | 0 | 2017-05-19 | 9.6 | 8.4 | 0 | 2016-05-19 | 16.1 | 1.9 | 0 | 5.22 | 0.19
2025-05-19 | 6.2 | 11.8 | 0 | 2024-05-19 | 19.6 | 0 | 1.6 | 2023-05-19 | 17.2 | 0.8 | 0 | 2022-05-19 | 8 | 10 | 0 | 2021-05-19 | 22.6 | 0 | 4.6 | 2020-05-19 | 15 | 3 | 0 | 2019-05-19 | 12.3 | 5.7 | 0 | 2018-05-19 | 15 | 3 | 0 | 2017-05-19 | 11 | 7 | 0 | 2016-05-19 | 18 | 0 | 0 | 4.13 | 0.62
2025-05-19 | 7.2 | 10.8 | 0 | 2024-05-19 | 21.4 | 0 | 3.4 | 2023-05-19 | 18.5 | 0 | 0.5 | 2022-05-19 | 7.8 | 10.2 | 0 | 2021-05-19 | 24.4 | 0 | 6.4 | 2020-05-19 | 15.2 | 2.8 | 0 | 2019-05-19 | 13.1 | 4.9 | 0 | 2018-05-19 | 16.8 | 1.2 | 0 | 2017-05-19 | 11.5 | 6.5 | 0 | 2016-05-19 | 16.6 | 1.4 | 0 | 3.78 | 1.03
2025-05-19 | 7.8 | 10.2 | 0 | 2024-05-19 | 22.6 | 0 | 4.6 | 2023-05-19 | 20.1 | 0 | 2.1 | 2022-05-19 | 8.2 | 9.8 | 0 | 2021-05-19 | 26.9 | 0 | 8.9 | 2020-05-19 | 17.7 | 0.3 | 0 | 2019-05-19 | 14.4 | 3.6 | 0 | 2018-05-19 | 17.6 | 0.4 | 0 | 2017-05-19 | 12.1 | 5.9 | 0 | 2016-05-19 | 17.5 | 0.5 | 0 | 3.07 | 1.56
2025-05-19 | 9.3 | 8.7 | 0 | 2024-05-19 | 24.1 | 0 | 6.1 | 2023-05-19 | 20.9 | 0 | 2.9 | 2022-05-19 | 9.5 | 8.5 | 0 | 2021-05-19 | 27.9 | 0 | 9.9 | 2020-05-19 | 17.7 | 0.3 | 0 | 2019-05-19 | 15.9 | 2.1 | 0 | 2018-05-19 | 16.2 | 1.8 | 0 | 2017-05-19 | 13.1 | 4.9 | 0 | 2016-05-19 | 19.9 | 0 | 1.9 | 2.63 | 2.08
2025-05-19 | 9.9 | 8.1 | 0 | 2024-05-19 | 24.9 | 0 | 6.9 | 2023-05-19 | 21.2 | 0 | 3.2 | 2022-05-19 | 9.9 | 8.1 | 0 | 2021-05-19 | 28.4 | 0 | 10.4 | 2020-05-19 | 18.6 | 0 | 0.6 | 2019-05-19 | 17.5 | 0.5 | 0 | 2018-05-19 | 13.4 | 4.6 | 0 | 2017-05-19 | 14.7 | 3.3 | 0 | 2016-05-19 | 18.5 | 0 | 0.5 | 2.46 | 2.16
2025-05-19 | 10.6 | 7.4 | 0 | 2024-05-19 | 25.8 | 0 | 7.8 | 2023-05-19 | 21.3 | 0 | 3.3 | 2022-05-19 | 10.2 | 7.8 | 0 | 2021-05-19 | 29.5 | 0 | 11.5 | 2020-05-19 | 19.1 | 0 | 1.1 | 2019-05-19 | 18.1 | 0 | 0.1 | 2018-05-19 | 12.9 | 5.1 | 0 | 2017-05-19 | 16 | 2 | 0 | 2016-05-19 | 19.3 | 0 | 1.3 | 2.23 | 2.51
2025-05-19 | 10.3 | 7.7 | 0 | 2024-05-19 | 26.4 | 0 | 8.4 | 2023-05-19 | 21.2 | 0 | 3.2 | 2022-05-19 | 10.5 | 7.5 | 0 | 2021-05-19 | 29.9 | 0 | 11.9 | 2020-05-19 | 18.8 | 0 | 0.8 | 2019-05-19 | 17.9 | 0.1 | 0 | 2018-05-19 | 12.9 | 5.1 | 0 | 2017-05-19 | 16.2 | 1.8 | 0 | 2016-05-19 | 18.6 | 0 | 0.6 | 2.22 | 2.49
2025-05-19 | 9.4 | 8.6 | 0 | 2024-05-19 | 26.5 | 0 | 8.5 | 2023-05-19 | 21.4 | 0 | 3.4 | 2022-05-19 | 10.6 | 7.4 | 0 | 2021-05-19 | 28.7 | 0 | 10.7 | 2020-05-19 | 19.5 | 0 | 1.5 | 2019-05-19 | 16 | 2 | 0 | 2018-05-19 | 13.2 | 4.8 | 0 | 2017-05-19 | 16 | 2 | 0 | 2016-05-19 | 19.1 | 0 | 1.1 | 2.48 | 2.52
2025-05-19 | 7.8 | 10.2 | 0 | 2024-05-19 | 25.9 | 0 | 7.9 | 2023-05-19 | 21.2 | 0 | 3.2 | 2022-05-19 | 11.1 | 6.9 | 0 | 2021-05-19 | 28.2 | 0 | 10.2 | 2020-05-19 | 19.2 | 0 | 1.2 | 2019-05-19 | 16.4 | 1.6 | 0 | 2018-05-19 | 13.4 | 4.6 | 0 | 2017-05-19 | 16.1 | 1.9 | 0 | 2016-05-19 | 18.6 | 0 | 0.6 | 2.52 | 2.31
2025-05-19 | 7.4 | 10.6 | 0 | 2024-05-19 | 25.4 | 0 | 7.4 | 2023-05-19 | 21 | 0 | 3 | 2022-05-19 | 11.1 | 6.9 | 0 | 2021-05-19 | 26.7 | 0 | 8.7 | 2020-05-19 | 19 | 0 | 1 | 2019-05-19 | 15.8 | 2.2 | 0 | 2018-05-19 | 13.3 | 4.7 | 0 | 2017-05-19 | 14.9 | 3.1 | 0 | 2016-05-19 | 18.2 | 0 | 0.2 | 2.75 | 2.03
2025-05-19 | 7 | 11 | 0 | 2024-05-19 | 23.4 | 0 | 5.4 | 2023-05-19 | 20.7 | 0 | 2.7 | 2022-05-19 | 10.7 | 7.3 | 0 | 2021-05-19 | 25.1 | 0 | 7.1 | 2020-05-19 | 17.3 | 0.7 | 0 | 2019-05-19 | 14.8 | 3.2 | 0 | 2018-05-19 | 12.8 | 5.2 | 0 | 2017-05-19 | 13.2 | 4.8 | 0 | 2016-05-19 | 16.2 | 1.8 | 0 | 3.4 | 1.52
2025-05-19 | 6.7 | 11.3 | 0 | 2024-05-19 | 21.7 | 0 | 3.7 | 2023-05-19 | 18.9 | 0 | 0.9 | 2022-05-19 | 9.3 | 8.7 | 0 | 2021-05-19 | 23.7 | 0 | 5.7 | 2020-05-19 | 14.7 | 3.3 | 0 | 2019-05-19 | 13.6 | 4.4 | 0 | 2018-05-19 | 12.8 | 5.2 | 0 | 2017-05-19 | 12.1 | 5.9 | 0 | 2016-05-19 | 14.1 | 3.9 | 0 | 4.27 | 1.03
2025-05-19 | 6.6 | 11.4 | 0 | 2024-05-19 | 20.6 | 0 | 2.6 | 2023-05-19 | 18.4 | 0 | 0.4 | 2022-05-19 | 8.5 | 9.5 | 0 | 2021-05-19 | 21.6 | 0 | 3.6 | 2020-05-19 | 12.2 | 5.8 | 0 | 2019-05-19 | 12.9 | 5.1 | 0 | 2018-05-19 | 12.8 | 5.2 | 0 | 2017-05-19 | 11.3 | 6.7 | 0 | 2016-05-19 | 12.6 | 5.4 | 0 | 4.91 | 0.66
2025-05-19 | 6.1 | 11.9 | 0 | 2024-05-19 | 19.1 | 0 | 1.1 | 2023-05-19 | 17.2 | 0.8 | 0 | 2022-05-19 | 7.7 | 10.3 | 0 | 2021-05-19 | 20.2 | 0 | 2.2 | 2020-05-19 | 12.8 | 5.2 | 0 | 2019-05-19 | 12.5 | 5.5 | 0 | 2018-05-19 | 13.2 | 4.8 | 0 | 2017-05-19 | 10.4 | 7.6 | 0 | 2016-05-19 | 11.7 | 6.3 | 0 | 5.24 | 0.33
2025-05-19 | 5.9 | 12.1 | 0 | 2024-05-19 | 18.1 | 0 | 0.1 | 2023-05-19 | 16.3 | 1.7 | 0 | 2022-05-19 | 7.6 | 10.4 | 0 | 2021-05-19 | 20 | 0 | 2 | 2020-05-19 | 11.6 | 6.4 | 0 | 2019-05-19 | 12.1 | 5.9 | 0 | 2018-05-19 | 13.5 | 4.5 | 0 | 2017-05-19 | 9.7 | 8.3 | 0 | 2016-05-19 | 12.2 | 5.8 | 0 | 5.51 | 0.21
2025-05-20 | 5.2 | 12.8 | 0 | 2024-05-20 | 17.5 | 0.5 | 0 | 2023-05-20 | 16 | 2 | 0 | 2022-05-20 | 7.4 | 10.6 | 0 | 2021-05-20 | 17.7 | 0.3 | 0 | 2020-05-20 | 10.3 | 7.7 | 0 | 2019-05-20 | 12.1 | 5.9 | 0 | 2018-05-20 | 13.8 | 4.2 | 0 | 2017-05-20 | 8.7 | 9.3 | 0 | 2016-05-20 | 8.2 | 9.8 | 0 | 6.31 | 0
2025-05-20 | 5.1 | 12.9 | 0 | 2024-05-20 | 16.7 | 1.3 | 0 | 2023-05-20 | 15.7 | 2.3 | 0 | 2022-05-20 | 8.4 | 9.6 | 0 | 2021-05-20 | 17.8 | 0.2 | 0 | 2020-05-20 | 9.2 | 8.8 | 0 | 2019-05-20 | 11.4 | 6.6 | 0 | 2018-05-20 | 14.5 | 3.5 | 0 | 2017-05-20 | 7.5 | 10.5 | 0 | 2016-05-20 | 10 | 8 | 0 | 6.37 | 0
2025-05-20 | 4 | 14 | 0 | 2024-05-20 | 16.9 | 1.1 | 0 | 2023-05-20 | 15 | 3 | 0 | 2022-05-20 | 8.3 | 9.7 | 0 | 2021-05-20 | 17.2 | 0.8 | 0 | 2020-05-20 | 7.1 | 10.9 | 0 | 2019-05-20 | 12.1 | 5.9 | 0 | 2018-05-20 | 14.2 | 3.8 | 0 | 2017-05-20 | 6.5 | 11.5 | 0 | 2016-05-20 | 7.8 | 10.2 | 0 | 7.09 | 0
2025-05-20 | 3.6 | 14.4 | 0 | 2024-05-20 | 16.4 | 1.6 | 0 | 2023-05-20 | 14.5 | 3.5 | 0 | 2022-05-20 | 7.9 | 10.1 | 0 | 2021-05-20 | 15.8 | 2.2 | 0 | 2020-05-20 | 8.7 | 9.3 | 0 | 2019-05-20 | 12.4 | 5.6 | 0 | 2018-05-20 | 13.8 | 4.2 | 0 | 2017-05-20 | 4.9 | 13.1 | 0 | 2016-05-20 | 8.5 | 9.5 | 0 | 7.35 | 0
2025-05-20 | 2.4 | 15.6 | 0 | 2024-05-20 | 16.2 | 1.8 | 0 | 2023-05-20 | 14.7 | 3.3 | 0 | 2022-05-20 | 7.7 | 10.3 | 0 | 2021-05-20 | 16.5 | 1.5 | 0 | 2020-05-20 | 6 | 12 | 0 | 2019-05-20 | 13.9 | 4.1 | 0 | 2018-05-20 | 13.7 | 4.3 | 0 | 2017-05-20 | 4.7 | 13.3 | 0 | 2016-05-20 | 7.9 | 10.1 | 0 | 7.63 | 0
2025-05-20 | 3.7 | 14.3 | 0 | 2024-05-20 | 16 | 2 | 0 | 2023-05-20 | 14.5 | 3.5 | 0 | 2022-05-20 | 8.2 | 9.8 | 0 | 2021-05-20 | 16.5 | 1.5 | 0 | 2020-05-20 | 7.2 | 10.8 | 0 | 2019-05-20 | 14.7 | 3.3 | 0 | 2018-05-20 | 13.6 | 4.4 | 0 | 2017-05-20 | 4.5 | 13.5 | 0 | 2016-05-20 | 6.3 | 11.7 | 0 | 7.48 | 0
2025-05-20 | 4.5 | 13.5 | 0 | 2024-05-20 | 17.1 | 0.9 | 0 | 2023-05-20 | 15.1 | 2.9 | 0 | 2022-05-20 | 9.3 | 8.7 | 0 | 2021-05-20 | 17 | 1 | 0 | 2020-05-20 | 10.7 | 7.3 | 0 | 2019-05-20 | 15.3 | 2.7 | 0 | 2018-05-20 | 13.6 | 4.4 | 0 | 2017-05-20 | 6.1 | 11.9 | 0 | 2016-05-20 | 9.7 | 8.3 | 0 | 6.16 | 0
2025-05-20 | 6.8 | 11.2 | 0 | 2024-05-20 | 19 | 0 | 1 | 2023-05-20 | 15.8 | 2.2 | 0 | 2022-05-20 | 9.9 | 8.1 | 0 | 2021-05-20 | 19.2 | 0 | 1.2 | 2020-05-20 | 13.6 | 4.4 | 0 | 2019-05-20 | 15.9 | 2.1 | 0 | 2018-05-20 | 14.7 | 3.3 | 0 | 2017-05-20 | 7.2 | 10.8 | 0 | 2016-05-20 | 12.8 | 5.2 | 0 | 4.73 | 0.22
2025-05-20 | 9.9 | 8.1 | 0 | 2024-05-20 | 20.7 | 0 | 2.7 | 2023-05-20 | 15.1 | 2.9 | 0 | 2022-05-20 | 11.4 | 6.6 | 0 | 2021-05-20 | 20.7 | 0 | 2.7 | 2020-05-20 | 15.7 | 2.3 | 0 | 2019-05-20 | 18.3 | 0 | 0.3 | 2018-05-20 | 15.1 | 2.9 | 0 | 2017-05-20 | 8.4 | 9.6 | 0 | 2016-05-20 | 16.6 | 1.4 | 0 | 3.38 | 0.57
2025-05-20 | 9.6 | 8.4 | 0 | 2024-05-20 | 22.5 | 0 | 4.5 | 2023-05-20 | 16 | 2 | 0 | 2022-05-20 | 15.2 | 2.8 | 0 | 2021-05-20 | 23.8 | 0 | 5.8 | 2020-05-20 | 17.5 | 0.5 | 0 | 2019-05-20 | 19.7 | 0 | 1.7 | 2018-05-20 | 14.4 | 3.6 | 0 | 2017-05-20 | 10.1 | 7.9 | 0 | 2016-05-20 | 19.3 | 0 | 1.3 | 2.52 | 1.33
2025-05-20 | 11.4 | 6.6 | 0 | 2024-05-20 | 24 | 0 | 6 | 2023-05-20 | 14.5 | 3.5 | 0 | 2022-05-20 | 18.1 | 0 | 0.1 | 2021-05-20 | 26.1 | 0 | 8.1 | 2020-05-20 | 19.1 | 0 | 1.1 | 2019-05-20 | 19.1 | 0 | 1.1 | 2018-05-20 | 13.8 | 4.2 | 0 | 2017-05-20 | 11.5 | 6.5 | 0 | 2016-05-20 | 20.6 | 0 | 2.6 | 2.08 | 1.9
2025-05-20 | 11.6 | 6.4 | 0 | 2024-05-20 | 24.9 | 0 | 6.9 | 2023-05-20 | 14.4 | 3.6 | 0 | 2022-05-20 | 20.7 | 0 | 2.7 | 2021-05-20 | 27.5 | 0 | 9.5 | 2020-05-20 | 20.6 | 0 | 2.6 | 2019-05-20 | 19.7 | 0 | 1.7 | 2018-05-20 | 13.9 | 4.1 | 0 | 2017-05-20 | 13.3 | 4.7 | 0 | 2016-05-20 | 21.8 | 0 | 3.8 | 1.88 | 2.72
2025-05-20 | 12.7 | 5.3 | 0 | 2024-05-20 | 26.4 | 0 | 8.4 | 2023-05-20 | 14.5 | 3.5 | 0 | 2022-05-20 | 22.7 | 0 | 4.7 | 2021-05-20 | 28.6 | 0 | 10.6 | 2020-05-20 | 21.5 | 0 | 3.5 | 2019-05-20 | 21.4 | 0 | 3.4 | 2018-05-20 | 13.6 | 4.4 | 0 | 2017-05-20 | 13.9 | 4.1 | 0 | 2016-05-20 | 22.6 | 0 | 4.6 | 1.73 | 3.52
2025-05-20 | 13.3 | 4.7 | 0 | 2024-05-20 | 26.6 | 0 | 8.6 | 2023-05-20 | 14.4 | 3.6 | 0 | 2022-05-20 | 24.9 | 0 | 6.9 | 2021-05-20 | 29.1 | 0 | 11.1 | 2020-05-20 | 22.5 | 0 | 4.5 | 2019-05-20 | 19.3 | 0 | 1.3 | 2018-05-20 | 15.3 | 2.7 | 0 | 2017-05-20 | 15.9 | 2.1 | 0 | 2016-05-20 | 23.6 | 0 | 5.6 | 1.31 | 3.8
2025-05-20 | 13.1 | 4.9 | 0 | 2024-05-20 | 27.6 | 0 | 9.6 | 2023-05-20 | 14.6 | 3.4 | 0 | 2022-05-20 | 26.9 | 0 | 8.9 | 2021-05-20 | 28.6 | 0 | 10.6 | 2020-05-20 | 22.9 | 0 | 4.9 | 2019-05-20 | 21.1 | 0 | 3.1 | 2018-05-20 | 16.5 | 1.5 | 0 | 2017-05-20 | 17.1 | 0.9 | 0 | 2016-05-20 | 23.6 | 0 | 5.6 | 1.07 | 4.27
2025-05-20 | 13.4 | 4.6 | 0 | 2024-05-20 | 28.4 | 0 | 10.4 | 2023-05-20 | 14.5 | 3.5 | 0 | 2022-05-20 | 27 | 0 | 9 | 2021-05-20 | 27.5 | 0 | 9.5 | 2020-05-20 | 23.5 | 0 | 5.5 | 2019-05-20 | 20.7 | 0 | 2.7 | 2018-05-20 | 17.4 | 0.6 | 0 | 2017-05-20 | 17.9 | 0.1 | 0 | 2016-05-20 | 23.9 | 0 | 5.9 | 0.88 | 4.3
2025-05-20 | 13.1 | 4.9 | 0 | 2024-05-20 | 27.9 | 0 | 9.9 | 2023-05-20 | 14.8 | 3.2 | 0 | 2022-05-20 | 26.8 | 0 | 8.8 | 2021-05-20 | 26.7 | 0 | 8.7 | 2020-05-20 | 23.3 | 0 | 5.3 | 2019-05-20 | 18.8 | 0 | 0.8 | 2018-05-20 | 17.8 | 0.2 | 0 | 2017-05-20 | 18.1 | 0 | 0.1 | 2016-05-20 | 24.2 | 0 | 6.2 | 0.83 | 3.98
2025-05-20 | 13.2 | 4.8 | 0 | 2024-05-20 | 27.5 | 0 | 9.5 | 2023-05-20 | 14.8 | 3.2 | 0 | 2022-05-20 | 26.4 | 0 | 8.4 | 2021-05-20 | 26.4 | 0 | 8.4 | 2020-05-20 | 23.3 | 0 | 5.3 | 2019-05-20 | 15.6 | 2.4 | 0 | 2018-05-20 | 17.4 | 0.6 | 0 | 2017-05-20 | 18 | 0 | 0 | 2016-05-20 | 24.1 | 0 | 6.1 | 1.1 | 3.77
2025-05-20 | 12.9 | 5.1 | 0 | 2024-05-20 | 26.1 | 0 | 8.1 | 2023-05-20 | 14.6 | 3.4 | 0 | 2022-05-20 | 25.6 | 0 | 7.6 | 2021-05-20 | 25.8 | 0 | 7.8 | 2020-05-20 | 22.8 | 0 | 4.8 | 2019-05-20 | 13.2 | 4.8 | 0 | 2018-05-20 | 16.7 | 1.3 | 0 | 2017-05-20 | 17.3 | 0.7 | 0 | 2016-05-20 | 22.4 | 0 | 4.4 | 1.53 | 3.27
2025-05-20 | 12.3 | 5.7 | 0 | 2024-05-20 | 24.9 | 0 | 6.9 | 2023-05-20 | 14.2 | 3.8 | 0 | 2022-05-20 | 24.1 | 0 | 6.1 | 2021-05-20 | 24 | 0 | 6 | 2020-05-20 | 21.2 | 0 | 3.2 | 2019-05-20 | 12.6 | 5.4 | 0 | 2018-05-20 | 15.2 | 2.8 | 0 | 2017-05-20 | 15.2 | 2.8 | 0 | 2016-05-20 | 20.6 | 0 | 2.6 | 2.05 | 2.48
2025-05-20 | 11.3 | 6.7 | 0 | 2024-05-20 | 23.2 | 0 | 5.2 | 2023-05-20 | 14.1 | 3.9 | 0 | 2022-05-20 | 21.7 | 0 | 3.7 | 2021-05-20 | 22.1 | 0 | 4.1 | 2020-05-20 | 19.2 | 0 | 1.2 | 2019-05-20 | 10.6 | 7.4 | 0 | 2018-05-20 | 12.2 | 5.8 | 0 | 2017-05-20 | 12.8 | 5.2 | 0 | 2016-05-20 | 18.6 | 0 | 0.6 | 2.9 | 1.48
2025-05-20 | 10.6 | 7.4 | 0 | 2024-05-20 | 21 | 0 | 3 | 2023-05-20 | 13.7 | 4.3 | 0 | 2022-05-20 | 22.1 | 0 | 4.1 | 2021-05-20 | 19.6 | 0 | 1.6 | 2020-05-20 | 15.3 | 2.7 | 0 | 2019-05-20 | 9.5 | 8.5 | 0 | 2018-05-20 | 11.1 | 6.9 | 0 | 2017-05-20 | 10.7 | 7.3 | 0 | 2016-05-20 | 16.1 | 1.9 | 0 | 3.9 | 0.87
2025-05-20 | 10.2 | 7.8 | 0 | 2024-05-20 | 19.4 | 0 | 1.4 | 2023-05-20 | 13.6 | 4.4 | 0 | 2022-05-20 | 21.7 | 0 | 3.7 | 2021-05-20 | 20.6 | 0 | 2.6 | 2020-05-20 | 14.4 | 3.6 | 0 | 2019-05-20 | 9.6 | 8.4 | 0 | 2018-05-20 | 11.4 | 6.6 | 0 | 2017-05-20 | 9.2 | 8.8 | 0 | 2016-05-20 | 15.2 | 2.8 | 0 | 4.24 | 0.77
2025-05-20 | 10.1 | 7.9 | 0 | 2024-05-20 | 18.4 | 0 | 0.4 | 2023-05-20 | 13.4 | 4.6 | 0 | 2022-05-20 | 21.2 | 0 | 3.2 | 2021-05-20 | 20.8 | 0 | 2.8 | 2020-05-20 | 13.2 | 4.8 | 0 | 2019-05-20 | 9 | 9 | 0 | 2018-05-20 | 8.7 | 9.3 | 0 | 2017-05-20 | 9.5 | 8.5 | 0 | 2016-05-20 | 14.2 | 3.8 | 0 | 4.79 | 0.64
2025-05-21 | 9.6 | 8.4 | 0 | 2024-05-21 | 17.5 | 0.5 | 0 | 2023-05-21 | 13.2 | 4.8 | 0 | 2022-05-21 | 21.3 | 0 | 3.3 | 2021-05-21 | 20.6 | 0 | 2.6 | 2020-05-21 | 12.5 | 5.5 | 0 | 2019-05-21 | 8.7 | 9.3 | 0 | 2018-05-21 | 8.8 | 9.2 | 0 | 2017-05-21 | 9.5 | 8.5 | 0 | 2016-05-21 | 13.7 | 4.3 | 0 | 5.05 | 0.59
2025-05-21 | 9.2 | 8.8 | 0 | 2024-05-21 | 17.1 | 0.9 | 0 | 2023-05-21 | 12.4 | 5.6 | 0 | 2022-05-21 | 21.3 | 0 | 3.3 | 2021-05-21 | 19.6 | 0 | 1.6 | 2020-05-21 | 10.6 | 7.4 | 0 | 2019-05-21 | 8.4 | 9.6 | 0 | 2018-05-21 | 7.5 | 10.5 | 0 | 2017-05-21 | 9.2 | 8.8 | 0 | 2016-05-21 | 13.2 | 4.8 | 0 | 5.64 | 0.49
2025-05-21 | 8.9 | 9.1 | 0 | 2024-05-21 | 15.9 | 2.1 | 0 | 2023-05-21 | 11 | 7 | 0 | 2022-05-21 | 20.9 | 0 | 2.9 | 2021-05-21 | 18.9 | 0 | 0.9 | 2020-05-21 | 10.4 | 7.6 | 0 | 2019-05-21 | 8 | 10 | 0 | 2018-05-21 | 7.1 | 10.9 | 0 | 2017-05-21 | 8.8 | 9.2 | 0 | 2016-05-21 | 12.6 | 5.4 | 0 | 6.13 | 0.38
2025-05-21 | 8.7 | 9.3 | 0 | 2024-05-21 | 15.7 | 2.3 | 0 | 2023-05-21 | 10.4 | 7.6 | 0 | 2022-05-21 | 20.6 | 0 | 2.6 | 2021-05-21 | 18.1 | 0 | 0.1 | 2020-05-21 | 10 | 8 | 0 | 2019-05-21 | 7.7 | 10.3 | 0 | 2018-05-21 | 7.2 | 10.8 | 0 | 2017-05-21 | 8.3 | 9.7 | 0 | 2016-05-21 | 11.7 | 6.3 | 0 | 6.43 | 0.27
2025-05-21 | 8.3 | 9.7 | 0 | 2024-05-21 | 16.3 | 1.7 | 0 | 2023-05-21 | 10.5 | 7.5 | 0 | 2022-05-21 | 20.3 | 0 | 2.3 | 2021-05-21 | 19.1 | 0 | 1.1 | 2020-05-21 | 10.6 | 7.4 | 0 | 2019-05-21 | 7.6 | 10.4 | 0 | 2018-05-21 | 5.5 | 12.5 | 0 | 2017-05-21 | 8.3 | 9.7 | 0 | 2016-05-21 | 11.7 | 6.3 | 0 | 6.52 | 0.34
2025-05-21 | 7.6 | 10.4 | 0 | 2024-05-21 | 16.4 | 1.6 | 0 | 2023-05-21 | 10.4 | 7.6 | 0 | 2022-05-21 | 20.5 | 0 | 2.5 | 2021-05-21 | 17.3 | 0.7 | 0 | 2020-05-21 | 10.4 | 7.6 | 0 | 2019-05-21 | 8.1 | 9.9 | 0 | 2018-05-21 | 6.3 | 11.7 | 0 | 2017-05-21 | 8.8 | 9.2 | 0 | 2016-05-21 | 10.8 | 7.2 | 0 | 6.59 | 0.25
2025-05-21 | 8.6 | 9.4 | 0 | 2024-05-21 | 16.9 | 1.1 | 0 | 2023-05-21 | 10.9 | 7.1 | 0 | 2022-05-21 | 20.7 | 0 | 2.7 | 2021-05-21 | 19.3 | 0 | 1.3 | 2020-05-21 | 12.4 | 5.6 | 0 | 2019-05-21 | 8.2 | 9.8 | 0 | 2018-05-21 | 10.2 | 7.8 | 0 | 2017-05-21 | 9.7 | 8.3 | 0 | 2016-05-21 | 12.1 | 5.9 | 0 | 5.5 | 0.4
2025-05-21 | 9.4 | 8.6 | 0 | 2024-05-21 | 18.4 | 0 | 0.4 | 2023-05-21 | 12.6 | 5.4 | 0 | 2022-05-21 | 21.5 | 0 | 3.5 | 2021-05-21 | 21.4 | 0 | 3.4 | 2020-05-21 | 14.9 | 3.1 | 0 | 2019-05-21 | 8.8 | 9.2 | 0 | 2018-05-21 | 12.4 | 5.6 | 0 | 2017-05-21 | 11.2 | 6.8 | 0 | 2016-05-21 | 15.2 | 2.8 | 0 | 4.15 | 0.73
2025-05-21 | 10.5 | 7.5 | 0 | 2024-05-21 | 17.9 | 0.1 | 0 | 2023-05-21 | 14.8 | 3.2 | 0 | 2022-05-21 | 23 | 0 | 5 | 2021-05-21 | 23.4 | 0 | 5.4 | 2020-05-21 | 17.6 | 0.4 | 0 | 2019-05-21 | 9.3 | 8.7 | 0 | 2018-05-21 | 14.6 | 3.4 | 0 | 2017-05-21 | 13.2 | 4.8 | 0 | 2016-05-21 | 17.5 | 0.5 | 0 | 2.86 | 1.04
2025-05-21 | 11 | 7 | 0 | 2024-05-21 | 18.9 | 0 | 0.9 | 2023-05-21 | 16 | 2 | 0 | 2022-05-21 | 24.8 | 0 | 6.8 | 2021-05-21 | 26.7 | 0 | 8.7 | 2020-05-21 | 19.5 | 0 | 1.5 | 2019-05-21 | 9.9 | 8.1 | 0 | 2018-05-21 | 17.2 | 0.8 | 0 | 2017-05-21 | 14.2 | 3.8 | 0 | 2016-05-21 | 18.4 | 0 | 0.4 | 2.17 | 1.83
2025-05-21 | 12.3 | 5.7 | 0 | 2024-05-21 | 19.3 | 0 | 1.3 | 2023-05-21 | 17.4 | 0.6 | 0 | 2022-05-21 | 27.1 | 0 | 9.1 | 2021-05-21 | 26.7 | 0 | 8.7 | 2020-05-21 | 20.8 | 0 | 2.8 | 2019-05-21 | 11.9 | 6.1 | 0 | 2018-05-21 | 19.5 | 0 | 1.5 | 2017-05-21 | 15.8 | 2.2 | 0 | 2016-05-21 | 19.6 | 0 | 1.6 | 1.46 | 2.5
2025-05-21 | 12.6 | 5.4 | 0 | 2024-05-21 | 21.2 | 0 | 3.2 | 2023-05-21 | 18.9 | 0 | 0.9 | 2022-05-21 | 26.5 | 0 | 8.5 | 2021-05-21 | 29 | 0 | 11 | 2020-05-21 | 21.6 | 0 | 3.6 | 2019-05-21 | 12.8 | 5.2 | 0 | 2018-05-21 | 21.9 | 0 | 3.9 | 2017-05-21 | 16.4 | 1.6 | 0 | 2016-05-21 | 20.5 | 0 | 2.5 | 1.22 | 3.36
2025-05-21 | 12.8 | 5.2 | 0 | 2024-05-21 | 22.4 | 0 | 4.4 | 2023-05-21 | 20.1 | 0 | 2.1 | 2022-05-21 | 29.3 | 0 | 11.3 | 2021-05-21 | 29.8 | 0 | 11.8 | 2020-05-21 | 22.4 | 0 | 4.4 | 2019-05-21 | 14.3 | 3.7 | 0 | 2018-05-21 | 24.4 | 0 | 6.4 | 2017-05-21 | 16.7 | 1.3 | 0 | 2016-05-21 | 22.3 | 0 | 4.3 | 1.02 | 4.47
2025-05-21 | 13.5 | 4.5 | 0 | 2024-05-21 | 22.9 | 0 | 4.9 | 2023-05-21 | 21 | 0 | 3 | 2022-05-21 | 29.9 | 0 | 11.9 | 2021-05-21 | 30.6 | 0 | 12.6 | 2020-05-21 | 23.5 | 0 | 5.5 | 2019-05-21 | 16.4 | 1.6 | 0 | 2018-05-21 | 24.5 | 0 | 6.5 | 2017-05-21 | 16.6 | 1.4 | 0 | 2016-05-21 | 23.6 | 0 | 5.6 | 0.75 | 5
2025-05-21 | 13.5 | 4.5 | 0 | 2024-05-21 | 21.9 | 0 | 3.9 | 2023-05-21 | 21.8 | 0 | 3.8 | 2022-05-21 | 29.6 | 0 | 11.6 | 2021-05-21 | 32.2 | 0 | 14.2 | 2020-05-21 | 24 | 0 | 6 | 2019-05-21 | 16.6 | 1.4 | 0 | 2018-05-21 | 25.1 | 0 | 7.1 | 2017-05-21 | 16.6 | 1.4 | 0 | 2016-05-21 | 24.7 | 0 | 6.7 | 0.73 | 5.33
2025-05-21 | 13.7 | 4.3 | 0 | 2024-05-21 | 23.1 | 0 | 5.1 | 2023-05-21 | 19 | 0 | 1 | 2022-05-21 | 17.5 | 0.5 | 0 | 2021-05-21 | 31 | 0 | 13 | 2020-05-21 | 24.8 | 0 | 6.8 | 2019-05-21 | 17.7 | 0.3 | 0 | 2018-05-21 | 25.2 | 0 | 7.2 | 2017-05-21 | 16.2 | 1.8 | 0 | 2016-05-21 | 25.3 | 0 | 7.3 | 0.69 | 4.04
2025-05-21 | 13.1 | 4.9 | 0 | 2024-05-21 | 22.9 | 0 | 4.9 | 2023-05-21 | 21.3 | 0 | 3.3 | 2022-05-21 | 18.4 | 0 | 0.4 | 2021-05-21 | 30.2 | 0 | 12.2 | 2020-05-21 | 24.4 | 0 | 6.4 | 2019-05-21 | 17.9 | 0.1 | 0 | 2018-05-21 | 25.5 | 0 | 7.5 | 2017-05-21 | 15.6 | 2.4 | 0 | 2016-05-21 | 24.7 | 0 | 6.7 | 0.74 | 4.14
2025-05-21 | 12.3 | 5.7 | 0 | 2024-05-21 | 17.9 | 0.1 | 0 | 2023-05-21 | 20.4 | 0 | 2.4 | 2022-05-21 | 20.3 | 0 | 2.3 | 2021-05-21 | 31.1 | 0 | 13.1 | 2020-05-21 | 23.9 | 0 | 5.9 | 2019-05-21 | 17 | 1 | 0 | 2018-05-21 | 25.4 | 0 | 7.4 | 2017-05-21 | 15.9 | 2.1 | 0 | 2016-05-21 | 23.7 | 0 | 5.7 | 0.89 | 3.68
2025-05-21 | 12.9 | 5.1 | 0 | 2024-05-21 | 18.1 | 0 | 0.1 | 2023-05-21 | 19 | 0 | 1 | 2022-05-21 | 21.3 | 0 | 3.3 | 2021-05-21 | 28.9 | 0 | 10.9 | 2020-05-21 | 22.7 | 0 | 4.7 | 2019-05-21 | 16.7 | 1.3 | 0 | 2018-05-21 | 23.6 | 0 | 5.6 | 2017-05-21 | 13.9 | 4.1 | 0 | 2016-05-21 | 23.4 | 0 | 5.4 | 1.05 | 3.1
2025-05-21 | 12.4 | 5.6 | 0 | 2024-05-21 | 18.5 | 0 | 0.5 | 2023-05-21 | 17.1 | 0.9 | 0 | 2022-05-21 | 20.1 | 0 | 2.1 | 2021-05-21 | 27.6 | 0 | 9.6 | 2020-05-21 | 20.1 | 0 | 2.1 | 2019-05-21 | 15.8 | 2.2 | 0 | 2018-05-21 | 22.1 | 0 | 4.1 | 2017-05-21 | 13.6 | 4.4 | 0 | 2016-05-21 | 21.3 | 0 | 3.3 | 1.31 | 2.17
2025-05-21 | 12.1 | 5.9 | 0 | 2024-05-21 | 18.1 | 0 | 0.1 | 2023-05-21 | 14.7 | 3.3 | 0 | 2022-05-21 | 19 | 0 | 1 | 2021-05-21 | 25 | 0 | 7 | 2020-05-21 | 17.1 | 0.9 | 0 | 2019-05-21 | 13.4 | 4.6 | 0 | 2018-05-21 | 19.4 | 0 | 1.4 | 2017-05-21 | 12.3 | 5.7 | 0 | 2016-05-21 | 19.5 | 0 | 1.5 | 2.04 | 1.1
2025-05-21 | 11.7 | 6.3 | 0 | 2024-05-21 | 17.7 | 0.3 | 0 | 2023-05-21 | 12.7 | 5.3 | 0 | 2022-05-21 | 17.8 | 0.2 | 0 | 2021-05-21 | 24.3 | 0 | 6.3 | 2020-05-21 | 16.1 | 1.9 | 0 | 2019-05-21 | 11.7 | 6.3 | 0 | 2018-05-21 | 17.7 | 0.3 | 0 | 2017-05-21 | 11.1 | 6.9 | 0 | 2016-05-21 | 17.5 | 0.5 | 0 | 2.8 | 0.63
2025-05-21 | 11.3 | 6.7 | 0 | 2024-05-21 | 17.6 | 0.4 | 0 | 2023-05-21 | 11.8 | 6.2 | 0 | 2022-05-21 | 18.1 | 0 | 0.1 | 2021-05-21 | 24.1 | 0 | 6.1 | 2020-05-21 | 14.6 | 3.4 | 0 | 2019-05-21 | 11.3 | 6.7 | 0 | 2018-05-21 | 14 | 4 | 0 | 2017-05-21 | 11 | 7 | 0 | 2016-05-21 | 15.7 | 2.3 | 0 | 3.67 | 0.62
2025-05-21 | 9.8 | 8.2 | 0 | 2024-05-21 | 16.6 | 1.4 | 0 | 2023-05-21 | 10.2 | 7.8 | 0 | 2022-05-21 | 17.1 | 0.9 | 0 | 2021-05-21 | 23.4 | 0 | 5.4 | 2020-05-21 | 13.7 | 4.3 | 0 | 2019-05-21 | 10.8 | 7.2 | 0 | 2018-05-21 | 15.3 | 2.7 | 0 | 2017-05-21 | 10.9 | 7.1 | 0 | 2016-05-21 | 14.5 | 3.5 | 0 | 4.31 | 0.54
2025-05-22 | 8.9 | 9.1 | 0 | 2024-05-22 | 16.1 | 1.9 | 0 | 2023-05-22 | 8.8 | 9.2 | 0 | 2022-05-22 | 17.3 | 0.7 | 0 | 2021-05-22 | 22.3 | 0 | 4.3 | 2020-05-22 | 11.8 | 6.2 | 0 | 2019-05-22 | 8.9 | 9.1 | 0 | 2018-05-22 | 14.7 | 3.3 | 0 | 2017-05-22 | 10.8 | 7.2 | 0 | 2016-05-22 | 14 | 4 | 0 | 5.07 | 0.43
2025-05-22 | 7.9 | 10.1 | 0 | 2024-05-22 | 15.6 | 2.4 | 0 | 2023-05-22 | 7.9 | 10.1 | 0 | 2022-05-22 | 16.9 | 1.1 | 0 | 2021-05-22 | 21.6 | 0 | 3.6 | 2020-05-22 | 11.9 | 6.1 | 0 | 2019-05-22 | 9.2 | 8.8 | 0 | 2018-05-22 | 13.3 | 4.7 | 0 | 2017-05-22 | 10.9 | 7.1 | 0 | 2016-05-22 | 12.3 | 5.7 | 0 | 5.61 | 0.36
2025-05-22 | 7.8 | 10.2 | 0 | 2024-05-22 | 15.3 | 2.7 | 0 | 2023-05-22 | 6.4 | 11.6 | 0 | 2022-05-22 | 16.7 | 1.3 | 0 | 2021-05-22 | 20 | 0 | 2 | 2020-05-22 | 10.7 | 7.3 | 0 | 2019-05-22 | 8.9 | 9.1 | 0 | 2018-05-22 | 13.2 | 4.8 | 0 | 2017-05-22 | 11 | 7 | 0 | 2016-05-22 | 12.2 | 5.8 | 0 | 5.98 | 0.2
2025-05-22 | 7.9 | 10.1 | 0 | 2024-05-22 | 15.7 | 2.3 | 0 | 2023-05-22 | 5.9 | 12.1 | 0 | 2022-05-22 | 16 | 2 | 0 | 2021-05-22 | 19.9 | 0 | 1.9 | 2020-05-22 | 10.3 | 7.7 | 0 | 2019-05-22 | 7.8 | 10.2 | 0 | 2018-05-22 | 12.3 | 5.7 | 0 | 2017-05-22 | 11.2 | 6.8 | 0 | 2016-05-22 | 13.7 | 4.3 | 0 | 6.12 | 0.19
2025-05-22 | 7.2 | 10.8 | 0 | 2024-05-22 | 15.2 | 2.8 | 0 | 2023-05-22 | 5.4 | 12.6 | 0 | 2022-05-22 | 15.7 | 2.3 | 0 | 2021-05-22 | 18.1 | 0 | 0.1 | 2020-05-22 | 9.2 | 8.8 | 0 | 2019-05-22 | 7.7 | 10.3 | 0 | 2018-05-22 | 12.3 | 5.7 | 0 | 2017-05-22 | 11 | 7 | 0 | 2016-05-22 | 13.3 | 4.7 | 0 | 6.5 | 0.01
2025-05-22 | 6.9 | 11.1 | 0 | 2024-05-22 | 15.4 | 2.6 | 0 | 2023-05-22 | 4.7 | 13.3 | 0 | 2022-05-22 | 14.9 | 3.1 | 0 | 2021-05-22 | 19 | 0 | 1 | 2020-05-22 | 9.6 | 8.4 | 0 | 2019-05-22 | 7.1 | 10.9 | 0 | 2018-05-22 | 12.3 | 5.7 | 0 | 2017-05-22 | 11.3 | 6.7 | 0 | 2016-05-22 | 13 | 5 | 0 | 6.68 | 0.1
2025-05-22 | 6.9 | 11.1 | 0 | 2024-05-22 | 15.5 | 2.5 | 0 | 2023-05-22 | 5.9 | 12.1 | 0 | 2022-05-22 | 16.3 | 1.7 | 0 | 2021-05-22 | 19.9 | 0 | 1.9 | 2020-05-22 | 12.3 | 5.7 | 0 | 2019-05-22 | 9.9 | 8.1 | 0 | 2018-05-22 | 12.7 | 5.3 | 0 | 2017-05-22 | 11.3 | 6.7 | 0 | 2016-05-22 | 13.6 | 4.4 | 0 | 5.76 | 0.19
2025-05-22 | 7.6 | 10.4 | 0 | 2024-05-22 | 16.3 | 1.7 | 0 | 2023-05-22 | 7.2 | 10.8 | 0 | 2022-05-22 | 16.4 | 1.6 | 0 | 2021-05-22 | 20.9 | 0 | 2.9 | 2020-05-22 | 16.4 | 1.6 | 0 | 2019-05-22 | 12.5 | 5.5 | 0 | 2018-05-22 | 14.9 | 3.1 | 0 | 2017-05-22 | 11.1 | 6.9 | 0 | 2016-05-22 | 15.7 | 2.3 | 0 | 4.39 | 0.29
2025-05-22 | 8.1 | 9.9 | 0 | 2024-05-22 | 17.2 | 0.8 | 0 | 2023-05-22 | 8.8 | 9.2 | 0 | 2022-05-22 | 17.5 | 0.5 | 0 | 2021-05-22 | 23.8 | 0 | 5.8 | 2020-05-22 | 19.5 | 0 | 1.5 | 2019-05-22 | 14 | 4 | 0 | 2018-05-22 | 17.1 | 0.9 | 0 | 2017-05-22 | 11.4 | 6.6 | 0 | 2016-05-22 | 17.6 | 0.4 | 0 | 3.23 | 0.73
2025-05-22 | 8.7 | 9.3 | 0 | 2024-05-22 | 19.8 | 0 | 1.8 | 2023-05-22 | 10.2 | 7.8 | 0 | 2022-05-22 | 19.4 | 0 | 1.4 | 2021-05-22 | 24.5 | 0 | 6.5 | 2020-05-22 | 21.5 | 0 | 3.5 | 2019-05-22 | 15.4 | 2.6 | 0 | 2018-05-22 | 18 | 0 | 0 | 2017-05-22 | 11.8 | 6.2 | 0 | 2016-05-22 | 19 | 0 | 1 | 2.59 | 1.42
2025-05-22 | 9.1 | 8.9 | 0 | 2024-05-22 | 22.5 | 0 | 4.5 | 2023-05-22 | 11.7 | 6.3 | 0 | 2022-05-22 | 20.3 | 0 | 2.3 | 2021-05-22 | 24.5 | 0 | 6.5 | 2020-05-22 | 23.7 | 0 | 5.7 | 2019-05-22 | 16.3 | 1.7 | 0 | 2018-05-22 | 16.9 | 1.1 | 0 | 2017-05-22 | 12.5 | 5.5 | 0 | 2016-05-22 | 20.8 | 0 | 2.8 | 2.35 | 2.18
2025-05-22 | 9.4 | 8.6 | 0 | 2024-05-22 | 24.8 | 0 | 6.8 | 2023-05-22 | 12.2 | 5.8 | 0 | 2022-05-22 | 19.8 | 0 | 1.8 | 2021-05-22 | 25.2 | 0 | 7.2 | 2020-05-22 | 25.4 | 0 | 7.4 | 2019-05-22 | 16.8 | 1.2 | 0 | 2018-05-22 | 14.8 | 3.2 | 0 | 2017-05-22 | 13.1 | 4.9 | 0 | 2016-05-22 | 21.9 | 0 | 3.9 | 2.37 | 2.71
2025-05-22 | 9.6 | 8.4 | 0 | 2024-05-22 | 26.9 | 0 | 8.9 | 2023-05-22 | 13.3 | 4.7 | 0 | 2022-05-22 | 15.1 | 2.9 | 0 | 2021-05-22 | 25.2 | 0 | 7.2 | 2020-05-22 | 25.8 | 0 | 7.8 | 2019-05-22 | 17.5 | 0.5 | 0 | 2018-05-22 | 15.7 | 2.3 | 0 | 2017-05-22 | 13.8 | 4.2 | 0 | 2016-05-22 | 22.9 | 0 | 4.9 | 2.3 | 2.88
2025-05-22 | 9.8 | 8.2 | 0 | 2024-05-22 | 29 | 0 | 11 | 2023-05-22 | 14.8 | 3.2 | 0 | 2022-05-22 | 13.6 | 4.4 | 0 | 2021-05-22 | 26.4 | 0 | 8.4 | 2020-05-22 | 26.9 | 0 | 8.9 | 2019-05-22 | 18.5 | 0 | 0.5 | 2018-05-22 | 17.2 | 0.8 | 0 | 2017-05-22 | 14.3 | 3.7 | 0 | 2016-05-22 | 23.9 | 0 | 5.9 | 2.03 | 3.47
2025-05-22 | 10 | 8 | 0 | 2024-05-22 | 30.4 | 0 | 12.4 | 2023-05-22 | 15.8 | 2.2 | 0 | 2022-05-22 | 12.9 | 5.1 | 0 | 2021-05-22 | 26.8 | 0 | 8.8 | 2020-05-22 | 27.3 | 0 | 9.3 | 2019-05-22 | 18.6 | 0 | 0.6 | 2018-05-22 | 16.9 | 1.1 | 0 | 2017-05-22 | 14.5 | 3.5 | 0 | 2016-05-22 | 24.3 | 0 | 6.3 | 1.99 | 3.74
2025-05-22 | 10.2 | 7.8 | 0 | 2024-05-22 | 30.3 | 0 | 12.3 | 2023-05-22 | 15.9 | 2.1 | 0 | 2022-05-22 | 13.1 | 4.9 | 0 | 2021-05-22 | 26.9 | 0 | 8.9 | 2020-05-22 | 27.7 | 0 | 9.7 | 2019-05-22 | 19.3 | 0 | 1.3 | 2018-05-22 | 16.7 | 1.3 | 0 | 2017-05-22 | 15 | 3 | 0 | 2016-05-22 | 25 | 0 | 7 | 1.91 | 3.92
2025-05-22 | 11 | 7 | 0 | 2024-05-22 | 29.8 | 0 | 11.8 | 2023-05-22 | 16.3 | 1.7 | 0 | 2022-05-22 | 13.3 | 4.7 | 0 | 2021-05-22 | 27.8 | 0 | 9.8 | 2020-05-22 | 28.3 | 0 | 10.3 | 2019-05-22 | 17.8 | 0.2 | 0 | 2018-05-22 | 16.2 | 1.8 | 0 | 2017-05-22 | 16.7 | 1.3 | 0 | 2016-05-22 | 25.2 | 0 | 7.2 | 1.67 | 3.91
2025-05-22 | 10.4 | 7.6 | 0 | 2024-05-22 | 29.7 | 0 | 11.7 | 2023-05-22 | 16.5 | 1.5 | 0 | 2022-05-22 | 13.2 | 4.8 | 0 | 2021-05-22 | 26.9 | 0 | 8.9 | 2020-05-22 | 27.8 | 0 | 9.8 | 2019-05-22 | 16.4 | 1.6 | 0 | 2018-05-22 | 14.8 | 3.2 | 0 | 2017-05-22 | 17.3 | 0.7 | 0 | 2016-05-22 | 25.2 | 0 | 7.2 | 1.94 | 3.76
2025-05-22 | 10 | 8 | 0 | 2024-05-22 | 28.2 | 0 | 10.2 | 2023-05-22 | 16.2 | 1.8 | 0 | 2022-05-22 | 12.4 | 5.6 | 0 | 2021-05-22 | 25.2 | 0 | 7.2 | 2020-05-22 | 26.9 | 0 | 8.9 | 2019-05-22 | 16.2 | 1.8 | 0 | 2018-05-22 | 14.4 | 3.6 | 0 | 2017-05-22 | 16.9 | 1.1 | 0 | 2016-05-22 | 24.3 | 0 | 6.3 | 2.19 | 3.26
2025-05-22 | 9.4 | 8.6 | 0 | 2024-05-22 | 26.8 | 0 | 8.8 | 2023-05-22 | 13.6 | 4.4 | 0 | 2022-05-22 | 12 | 6 | 0 | 2021-05-22 | 24.1 | 0 | 6.1 | 2020-05-22 | 24.6 | 0 | 6.6 | 2019-05-22 | 15.5 | 2.5 | 0 | 2018-05-22 | 14.3 | 3.7 | 0 | 2017-05-22 | 14.8 | 3.2 | 0 | 2016-05-22 | 22.7 | 0 | 4.7 | 2.84 | 2.62
2025-05-22 | 8.5 | 9.5 | 0 | 2024-05-22 | 25.4 | 0 | 7.4 | 2023-05-22 | 12 | 6 | 0 | 2022-05-22 | 10.7 | 7.3 | 0 | 2021-05-22 | 23 | 0 | 5 | 2020-05-22 | 22.3 | 0 | 4.3 | 2019-05-22 | 15.1 | 2.9 | 0 | 2018-05-22 | 13.9 | 4.1 | 0 | 2017-05-22 | 12.5 | 5.5 | 0 | 2016-05-22 | 21.2 | 0 | 3.2 | 3.53 | 1.99
2025-05-22 | 7.8 | 10.2 | 0 | 2024-05-22 | 24 | 0 | 6 | 2023-05-22 | 11.5 | 6.5 | 0 | 2022-05-22 | 9.8 | 8.2 | 0 | 2021-05-22 | 22 | 0 | 4 | 2020-05-22 | 20.1 | 0 | 2.1 | 2019-05-22 | 15.4 | 2.6 | 0 | 2018-05-22 | 11.9 | 6.1 | 0 | 2017-05-22 | 11.7 | 6.3 | 0 | 2016-05-22 | 18.3 | 0 | 0.3 | 3.99 | 1.24
2025-05-22 | 7.6 | 10.4 | 0 | 2024-05-22 | 22.4 | 0 | 4.4 | 2023-05-22 | 8.8 | 9.2 | 0 | 2022-05-22 | 9.6 | 8.4 | 0 | 2021-05-22 | 20.5 | 0 | 2.5 | 2020-05-22 | 19 | 0 | 1 | 2019-05-22 | 13.8 | 4.2 | 0 | 2018-05-22 | 11.5 | 6.5 | 0 | 2017-05-22 | 10.1 | 7.9 | 0 | 2016-05-22 | 19.1 | 0 | 1.1 | 4.66 | 0.9
2025-05-22 | 7.6 | 10.4 | 0 | 2024-05-22 | 21.1 | 0 | 3.1 | 2023-05-22 | 9.3 | 8.7 | 0 | 2022-05-22 | 8.1 | 9.9 | 0 | 2021-05-22 | 19.3 | 0 | 1.3 | 2020-05-22 | 17 | 1 | 0 | 2019-05-22 | 13.8 | 4.2 | 0 | 2018-05-22 | 10.6 | 7.4 | 0 | 2017-05-22 | 9.1 | 8.9 | 0 | 2016-05-22 | 18 | 0 | 0 | 5.05 | 0.44
2025-05-23 | 7.4 | 10.6 | 0 | 2024-05-23 | 20.4 | 0 | 2.4 | 2023-05-23 | 6.6 | 11.4 | 0 | 2022-05-23 | 8.1 | 9.9 | 0 | 2021-05-23 | 18.7 | 0 | 0.7 | 2020-05-23 | 16.6 | 1.4 | 0 | 2019-05-23 | 13.9 | 4.1 | 0 | 2018-05-23 | 10.4 | 7.6 | 0 | 2017-05-23 | 9.7 | 8.3 | 0 | 2016-05-23 | 16.1 | 1.9 | 0 | 5.52 | 0.31
2025-05-23 | 7.2 | 10.8 | 0 | 2024-05-23 | 20.2 | 0 | 2.2 | 2023-05-23 | 5.9 | 12.1 | 0 | 2022-05-23 | 8.1 | 9.9 | 0 | 2021-05-23 | 18 | 0 | 0 | 2020-05-23 | 14.8 | 3.2 | 0 | 2019-05-23 | 13.1 | 4.9 | 0 | 2018-05-23 | 10.7 | 7.3 | 0 | 2017-05-23 | 10.4 | 7.6 | 0 | 2016-05-23 | 12.9 | 5.1 | 0 | 6.09 | 0.22
2025-05-23 | 7 | 11 | 0 | 2024-05-23 | 19.5 | 0 | 1.5 | 2023-05-23 | 5.6 | 12.4 | 0 | 2022-05-23 | 7.2 | 10.8 | 0 | 2021-05-23 | 17.5 | 0.5 | 0 | 2020-05-23 | 14.1 | 3.9 | 0 | 2019-05-23 | 13 | 5 | 0 | 2018-05-23 | 10.5 | 7.5 | 0 | 2017-05-23 | 8.8 | 9.2 | 0 | 2016-05-23 | 12.3 | 5.7 | 0 | 6.6 | 0.15
2025-05-23 | 6.8 | 11.2 | 0 | 2024-05-23 | 19 | 0 | 1 | 2023-05-23 | 3.8 | 14.2 | 0 | 2022-05-23 | 6.4 | 11.6 | 0 | 2021-05-23 | 17.2 | 0.8 | 0 | 2020-05-23 | 16.6 | 1.4 | 0 | 2019-05-23 | 10.1 | 7.9 | 0 | 2018-05-23 | 10.6 | 7.4 | 0 | 2017-05-23 | 7.6 | 10.4 | 0 | 2016-05-23 | 13.1 | 4.9 | 0 | 6.98 | 0.1
2025-05-23 | 6.3 | 11.7 | 0 | 2024-05-23 | 18.4 | 0 | 0.4 | 2023-05-23 | 3.9 | 14.1 | 0 | 2022-05-23 | 6.9 | 11.1 | 0 | 2021-05-23 | 16.7 | 1.3 | 0 | 2020-05-23 | 16.6 | 1.4 | 0 | 2019-05-23 | 10.1 | 7.9 | 0 | 2018-05-23 | 10.3 | 7.7 | 0 | 2017-05-23 | 7.4 | 10.6 | 0 | 2016-05-23 | 13.3 | 4.7 | 0 | 7.05 | 0.04
2025-05-23 | 6.3 | 11.7 | 0 | 2024-05-23 | 16.9 | 1.1 | 0 | 2023-05-23 | 4.1 | 13.9 | 0 | 2022-05-23 | 6.9 | 11.1 | 0 | 2021-05-23 | 16.8 | 1.2 | 0 | 2020-05-23 | 16.9 | 1.1 | 0 | 2019-05-23 | 10.1 | 7.9 | 0 | 2018-05-23 | 10.2 | 7.8 | 0 | 2017-05-23 | 6.9 | 11.1 | 0 | 2016-05-23 | 11.6 | 6.4 | 0 | 7.33 | 0
2025-05-23 | 6.7 | 11.3 | 0 | 2024-05-23 | 16.7 | 1.3 | 0 | 2023-05-23 | 7.2 | 10.8 | 0 | 2022-05-23 | 8.3 | 9.7 | 0 | 2021-05-23 | 18.3 | 0 | 0.3 | 2020-05-23 | 16.8 | 1.2 | 0 | 2019-05-23 | 11.2 | 6.8 | 0 | 2018-05-23 | 11.4 | 6.6 | 0 | 2017-05-23 | 9.4 | 8.6 | 0 | 2016-05-23 | 13.4 | 4.6 | 0 | 6.09 | 0.03
2025-05-23 | 7.1 | 10.9 | 0 | 2024-05-23 | 17.7 | 0.3 | 0 | 2023-05-23 | 10.2 | 7.8 | 0 | 2022-05-23 | 9.8 | 8.2 | 0 | 2021-05-23 | 18.8 | 0 | 0.8 | 2020-05-23 | 17.6 | 0.4 | 0 | 2019-05-23 | 12.5 | 5.5 | 0 | 2018-05-23 | 13.4 | 4.6 | 0 | 2017-05-23 | 11.9 | 6.1 | 0 | 2016-05-23 | 17.4 | 0.6 | 0 | 4.44 | 0.08
2025-05-23 | 7.8 | 10.2 | 0 | 2024-05-23 | 19.6 | 0 | 1.6 | 2023-05-23 | 12.9 | 5.1 | 0 | 2022-05-23 | 10.5 | 7.5 | 0 | 2021-05-23 | 16.5 | 1.5 | 0 | 2020-05-23 | 18.4 | 0 | 0.4 | 2019-05-23 | 14 | 4 | 0 | 2018-05-23 | 14.4 | 3.6 | 0 | 2017-05-23 | 14.4 | 3.6 | 0 | 2016-05-23 | 19.2 | 0 | 1.2 | 3.55 | 0.32
2025-05-23 | 8.9 | 9.1 | 0 | 2024-05-23 | 20.9 | 0 | 2.9 | 2023-05-23 | 14.7 | 3.3 | 0 | 2022-05-23 | 11.3 | 6.7 | 0 | 2021-05-23 | 15.3 | 2.7 | 0 | 2020-05-23 | 19.7 | 0 | 1.7 | 2019-05-23 | 14.9 | 3.1 | 0 | 2018-05-23 | 15.6 | 2.4 | 0 | 2017-05-23 | 15.6 | 2.4 | 0 | 2016-05-23 | 21.2 | 0 | 3.2 | 2.97 | 0.78
2025-05-23 | 9.2 | 8.8 | 0 | 2024-05-23 | 21.7 | 0 | 3.7 | 2023-05-23 | 17 | 1 | 0 | 2022-05-23 | 13.1 | 4.9 | 0 | 2021-05-23 | 15.4 | 2.6 | 0 | 2020-05-23 | 21.1 | 0 | 3.1 | 2019-05-23 | 16.2 | 1.8 | 0 | 2018-05-23 | 18.9 | 0 | 0.9 | 2017-05-23 | 17.5 | 0.5 | 0 | 2016-05-23 | 23 | 0 | 5 | 1.96 | 1.27
2025-05-23 | 9.6 | 8.4 | 0 | 2024-05-23 | 21.8 | 0 | 3.8 | 2023-05-23 | 18.2 | 0 | 0.2 | 2022-05-23 | 13.1 | 4.9 | 0 | 2021-05-23 | 14.4 | 3.6 | 0 | 2020-05-23 | 21.6 | 0 | 3.6 | 2019-05-23 | 17.8 | 0.2 | 0 | 2018-05-23 | 21 | 0 | 3 | 2017-05-23 | 18.7 | 0 | 0.7 | 2016-05-23 | 24.3 | 0 | 6.3 | 1.71 | 1.76
2025-05-23 | 9.9 | 8.1 | 0 | 2024-05-23 | 23.8 | 0 | 5.8 | 2023-05-23 | 19.9 | 0 | 1.9 | 2022-05-23 | 14 | 4 | 0 | 2021-05-23 | 15.8 | 2.2 | 0 | 2020-05-23 | 22.4 | 0 | 4.4 | 2019-05-23 | 19.4 | 0 | 1.4 | 2018-05-23 | 21.7 | 0 | 3.7 | 2017-05-23 | 19.4 | 0 | 1.4 | 2016-05-23 | 25.1 | 0 | 7.1 | 1.43 | 2.57
2025-05-23 | 11.4 | 6.6 | 0 | 2024-05-23 | 24.9 | 0 | 6.9 | 2023-05-23 | 20.6 | 0 | 2.6 | 2022-05-23 | 15.8 | 2.2 | 0 | 2021-05-23 | 17 | 1 | 0 | 2020-05-23 | 23 | 0 | 5 | 2019-05-23 | 19.6 | 0 | 1.6 | 2018-05-23 | 22.4 | 0 | 4.4 | 2017-05-23 | 19.4 | 0 | 1.4 | 2016-05-23 | 25.5 | 0 | 7.5 | 0.98 | 2.94
2025-05-23 | 9.7 | 8.3 | 0 | 2024-05-23 | 23.8 | 0 | 5.8 | 2023-05-23 | 21.9 | 0 | 3.9 | 2022-05-23 | 15.8 | 2.2 | 0 | 2021-05-23 | 18 | 0 | 0 | 2020-05-23 | 23.8 | 0 | 5.8 | 2019-05-23 | 19.4 | 0 | 1.4 | 2018-05-23 | 23.6 | 0 | 5.6 | 2017-05-23 | 21.7 | 0 | 3.7 | 2016-05-23 | 26.7 | 0 | 8.7 | 1.05 | 3.49
2025-05-23 | 10.6 | 7.4 | 0 | 2024-05-23 | 24.5 | 0 | 6.5 | 2023-05-23 | 23 | 0 | 5 | 2022-05-23 | 15.6 | 2.4 | 0 | 2021-05-23 | 18.3 | 0 | 0.3 | 2020-05-23 | 23.9 | 0 | 5.9 | 2019-05-23 | 18.1 | 0 | 0.1 | 2018-05-23 | 23.6 | 0 | 5.6 | 2017-05-23 | 21.5 | 0 | 3.5 | 2016-05-23 | 26.2 | 0 | 8.2 | 0.98 | 3.51
2025-05-23 | 9.5 | 8.5 | 0 | 2024-05-23 | 23.8 | 0 | 5.8 | 2023-05-23 | 23.5 | 0 | 5.5 | 2022-05-23 | 15.6 | 2.4 | 0 | 2021-05-23 | 18.5 | 0 | 0.5 | 2020-05-23 | 24.1 | 0 | 6.1 | 2019-05-23 | 16.6 | 1.4 | 0 | 2018-05-23 | 23.2 | 0 | 5.2 | 2017-05-23 | 20.8 | 0 | 2.8 | 2016-05-23 | 26.5 | 0 | 8.5 | 1.23 | 3.44
2025-05-23 | 9.5 | 8.5 | 0 | 2024-05-23 | 23.1 | 0 | 5.1 | 2023-05-23 | 22.9 | 0 | 4.9 | 2022-05-23 | 15.5 | 2.5 | 0 | 2021-05-23 | 17.9 | 0.1 | 0 | 2020-05-23 | 23.3 | 0 | 5.3 | 2019-05-23 | 15.9 | 2.1 | 0 | 2018-05-23 | 23 | 0 | 5 | 2017-05-23 | 20.4 | 0 | 2.4 | 2016-05-23 | 26.3 | 0 | 8.3 | 1.32 | 3.1
2025-05-23 | 8.7 | 9.3 | 0 | 2024-05-23 | 22.4 | 0 | 4.4 | 2023-05-23 | 21.8 | 0 | 3.8 | 2022-05-23 | 14.1 | 3.9 | 0 | 2021-05-23 | 17 | 1 | 0 | 2020-05-23 | 22.2 | 0 | 4.2 | 2019-05-23 | 14.7 | 3.3 | 0 | 2018-05-23 | 21.9 | 0 | 3.9 | 2017-05-23 | 19.1 | 0 | 1.1 | 2016-05-23 | 25.4 | 0 | 7.4 | 1.75 | 2.48
2025-05-23 | 8.4 | 9.6 | 0 | 2024-05-23 | 21.6 | 0 | 3.6 | 2023-05-23 | 19.5 | 0 | 1.5 | 2022-05-23 | 13.6 | 4.4 | 0 | 2021-05-23 | 15.8 | 2.2 | 0 | 2020-05-23 | 20.4 | 0 | 2.4 | 2019-05-23 | 14.7 | 3.3 | 0 | 2018-05-23 | 19.1 | 0 | 1.1 | 2017-05-23 | 18.3 | 0 | 0.3 | 2016-05-23 | 23.9 | 0 | 5.9 | 1.95 | 1.48
2025-05-23 | 8.2 | 9.8 | 0 | 2024-05-23 | 20.4 | 0 | 2.4 | 2023-05-23 | 16.5 | 1.5 | 0 | 2022-05-23 | 12.6 | 5.4 | 0 | 2021-05-23 | 14.9 | 3.1 | 0 | 2020-05-23 | 18.2 | 0 | 0.2 | 2019-05-23 | 14.9 | 3.1 | 0 | 2018-05-23 | 18.2 | 0 | 0.2 | 2017-05-23 | 16.7 | 1.3 | 0 | 2016-05-23 | 20.7 | 0 | 2.7 | 2.42 | 0.55
2025-05-23 | 7.3 | 10.7 | 0 | 2024-05-23 | 19.1 | 0 | 1.1 | 2023-05-23 | 15.9 | 2.1 | 0 | 2022-05-23 | 11.4 | 6.6 | 0 | 2021-05-23 | 13.6 | 4.4 | 0 | 2020-05-23 | 16 | 2 | 0 | 2019-05-23 | 15.4 | 2.6 | 0 | 2018-05-23 | 17.3 | 0.7 | 0 | 2017-05-23 | 15.7 | 2.3 | 0 | 2016-05-23 | 15.8 | 2.2 | 0 | 3.36 | 0.11
2025-05-23 | 6.9 | 11.1 | 0 | 2024-05-23 | 18.4 | 0 | 0.4 | 2023-05-23 | 15.7 | 2.3 | 0 | 2022-05-23 | 10 | 8 | 0 | 2021-05-23 | 12.6 | 5.4 | 0 | 2020-05-23 | 14.8 | 3.2 | 0 | 2019-05-23 | 15.5 | 2.5 | 0 | 2018-05-23 | 15.5 | 2.5 | 0 | 2017-05-23 | 13.3 | 4.7 | 0 | 2016-05-23 | 16.2 | 1.8 | 0 | 4.15 | 0.04
2025-05-23 | 6.1 | 11.9 | 0 | 2024-05-23 | 17.5 | 0.5 | 0 | 2023-05-23 | 14.9 | 3.1 | 0 | 2022-05-23 | 8.3 | 9.7 | 0 | 2021-05-23 | 12 | 6 | 0 | 2020-05-23 | 13.8 | 4.2 | 0 | 2019-05-23 | 15.2 | 2.8 | 0 | 2018-05-23 | 13.6 | 4.4 | 0 | 2017-05-23 | 13.6 | 4.4 | 0 | 2016-05-23 | 15.9 | 2.1 | 0 | 4.91 | 0
2025-05-24 | 6.3 | 11.7 | 0 | 2024-05-24 | 16.4 | 1.6 | 0 | 2023-05-24 | 15.6 | 2.4 | 0 | 2022-05-24 | 8.3 | 9.7 | 0 | 2021-05-24 | 10.8 | 7.2 | 0 | 2020-05-24 | 13 | 5 | 0 | 2019-05-24 | 14.8 | 3.2 | 0 | 2018-05-24 | 13.3 | 4.7 | 0 | 2017-05-24 | 12.4 | 5.6 | 0 | 2016-05-24 | 12.7 | 5.3 | 0 | 5.64 | 0
2025-05-24 | 6.3 | 11.7 | 0 | 2024-05-24 | 15.4 | 2.6 | 0 | 2023-05-24 | 13.7 | 4.3 | 0 | 2022-05-24 | 6.8 | 11.2 | 0 | 2021-05-24 | 9.4 | 8.6 | 0 | 2020-05-24 | 12.2 | 5.8 | 0 | 2019-05-24 | 14.5 | 3.5 | 0 | 2018-05-24 | 11.5 | 6.5 | 0 | 2017-05-24 | 11.8 | 6.2 | 0 | 2016-05-24 | 12 | 6 | 0 | 6.64 | 0
2025-05-24 | 5.8 | 12.2 | 0 | 2024-05-24 | 14.4 | 3.6 | 0 | 2023-05-24 | 13.6 | 4.4 | 0 | 2022-05-24 | 8.7 | 9.3 | 0 | 2021-05-24 | 8.8 | 9.2 | 0 | 2020-05-24 | 11.2 | 6.8 | 0 | 2019-05-24 | 14.4 | 3.6 | 0 | 2018-05-24 | 11.7 | 6.3 | 0 | 2017-05-24 | 11 | 7 | 0 | 2016-05-24 | 12.2 | 5.8 | 0 | 6.82 | 0
2025-05-24 | 5.6 | 12.4 | 0 | 2024-05-24 | 14.4 | 3.6 | 0 | 2023-05-24 | 15.3 | 2.7 | 0 | 2022-05-24 | 7.1 | 10.9 | 0 | 2021-05-24 | 7.8 | 10.2 | 0 | 2020-05-24 | 10.3 | 7.7 | 0 | 2019-05-24 | 14 | 4 | 0 | 2018-05-24 | 10.6 | 7.4 | 0 | 2017-05-24 | 10.6 | 7.4 | 0 | 2016-05-24 | 12.1 | 5.9 | 0 | 7.22 | 0
2025-05-24 | 5.7 | 12.3 | 0 | 2024-05-24 | 13.4 | 4.6 | 0 | 2023-05-24 | 14.1 | 3.9 | 0 | 2022-05-24 | 6.3 | 11.7 | 0 | 2021-05-24 | 5.2 | 12.8 | 0 | 2020-05-24 | 9.3 | 8.7 | 0 | 2019-05-24 | 14 | 4 | 0 | 2018-05-24 | 10.5 | 7.5 | 0 | 2017-05-24 | 10.6 | 7.4 | 0 | 2016-05-24 | 11.1 | 6.9 | 0 | 7.98 | 0
2025-05-24 | 6.1 | 11.9 | 0 | 2024-05-24 | 13.8 | 4.2 | 0 | 2023-05-24 | 14.3 | 3.7 | 0 | 2022-05-24 | 7.2 | 10.8 | 0 | 2021-05-24 | 6.2 | 11.8 | 0 | 2020-05-24 | 9.6 | 8.4 | 0 | 2019-05-24 | 13.4 | 4.6 | 0 | 2018-05-24 | 9.3 | 8.7 | 0 | 2017-05-24 | 10.6 | 7.4 | 0 | 2016-05-24 | 11.2 | 6.8 | 0 | 7.83 | 0
2025-05-24 | 6.5 | 11.5 | 0 | 2024-05-24 | 14.6 | 3.4 | 0 | 2023-05-24 | 13.1 | 4.9 | 0 | 2022-05-24 | 8.7 | 9.3 | 0 | 2021-05-24 | 8.6 | 9.4 | 0 | 2020-05-24 | 11.1 | 6.9 | 0 | 2019-05-24 | 13.2 | 4.8 | 0 | 2018-05-24 | 10.8 | 7.2 | 0 | 2017-05-24 | 12.1 | 5.9 | 0 | 2016-05-24 | 13.3 | 4.7 | 0 | 6.8 | 0
2025-05-24 | 6.9 | 11.1 | 0 | 2024-05-24 | 15.8 | 2.2 | 0 | 2023-05-24 | 11.9 | 6.1 | 0 | 2022-05-24 | 11.7 | 6.3 | 0 | 2021-05-24 | 10.6 | 7.4 | 0 | 2020-05-24 | 12.9 | 5.1 | 0 | 2019-05-24 | 12.9 | 5.1 | 0 | 2018-05-24 | 12.3 | 5.7 | 0 | 2017-05-24 | 13.5 | 4.5 | 0 | 2016-05-24 | 16.5 | 1.5 | 0 | 5.5 | 0
2025-05-24 | 7.8 | 10.2 | 0 | 2024-05-24 | 14.9 | 3.1 | 0 | 2023-05-24 | 10.7 | 7.3 | 0 | 2022-05-24 | 13.5 | 4.5 | 0 | 2021-05-24 | 12 | 6 | 0 | 2020-05-24 | 15.4 | 2.6 | 0 | 2019-05-24 | 13.2 | 4.8 | 0 | 2018-05-24 | 15.1 | 2.9 | 0 | 2017-05-24 | 16 | 2 | 0 | 2016-05-24 | 20.1 | 0 | 2.1 | 4.34 | 0.21
2025-05-24 | 9.2 | 8.8 | 0 | 2024-05-24 | 14.6 | 3.4 | 0 | 2023-05-24 | 9 | 9 | 0 | 2022-05-24 | 15.5 | 2.5 | 0 | 2021-05-24 | 13.8 | 4.2 | 0 | 2020-05-24 | 17.9 | 0.1 | 0 | 2019-05-24 | 13.5 | 4.5 | 0 | 2018-05-24 | 16.8 | 1.2 | 0 | 2017-05-24 | 17.6 | 0.4 | 0 | 2016-05-24 | 22.2 | 0 | 4.2 | 3.41 | 0.42
2025-05-24 | 10.1 | 7.9 | 0 | 2024-05-24 | 15.4 | 2.6 | 0 | 2023-05-24 | 7.7 | 10.3 | 0 | 2022-05-24 | 15.7 | 2.3 | 0 | 2021-05-24 | 16.3 | 1.7 | 0 | 2020-05-24 | 20.3 | 0 | 2.3 | 2019-05-24 | 14.7 | 3.3 | 0 | 2018-05-24 | 18.8 | 0 | 0.8 | 2017-05-24 | 18.1 | 0 | 0.1 | 2016-05-24 | 25.2 | 0 | 7.2 | 2.81 | 1.04
2025-05-24 | 10.4 | 7.6 | 0 | 2024-05-24 | 15.6 | 2.4 | 0 | 2023-05-24 | 7.8 | 10.2 | 0 | 2022-05-24 | 16.1 | 1.9 | 0 | 2021-05-24 | 16.7 | 1.3 | 0 | 2020-05-24 | 22.4 | 0 | 4.4 | 2019-05-24 | 14.9 | 3.1 | 0 | 2018-05-24 | 19.7 | 0 | 1.7 | 2017-05-24 | 20 | 0 | 2 | 2016-05-24 | 27.1 | 0 | 9.1 | 2.65 | 1.72
2025-05-24 | 10.4 | 7.6 | 0 | 2024-05-24 | 16.3 | 1.7 | 0 | 2023-05-24 | 10.4 | 7.6 | 0 | 2022-05-24 | 16.4 | 1.6 | 0 | 2021-05-24 | 18.6 | 0 | 0.6 | 2020-05-24 | 24.7 | 0 | 6.7 | 2019-05-24 | 16.7 | 1.3 | 0 | 2018-05-24 | 21.5 | 0 | 3.5 | 2017-05-24 | 21.1 | 0 | 3.1 | 2016-05-24 | 28.3 | 0 | 10.3 | 1.98 | 2.42
2025-05-24 | 11.4 | 6.6 | 0 | 2024-05-24 | 16.2 | 1.8 | 0 | 2023-05-24 | 11.6 | 6.4 | 0 | 2022-05-24 | 17.2 | 0.8 | 0 | 2021-05-24 | 19.5 | 0 | 1.5 | 2020-05-24 | 26.4 | 0 | 8.4 | 2019-05-24 | 17.2 | 0.8 | 0 | 2018-05-24 | 23.5 | 0 | 5.5 | 2017-05-24 | 21 | 0 | 3 | 2016-05-24 | 28.4 | 0 | 10.4 | 1.64 | 2.88
2025-05-24 | 11.1 | 6.9 | 0 | 2024-05-24 | 16.3 | 1.7 | 0 | 2023-05-24 | 12.7 | 5.3 | 0 | 2022-05-24 | 17.1 | 0.9 | 0 | 2021-05-24 | 20.2 | 0 | 2.2 | 2020-05-24 | 27.1 | 0 | 9.1 | 2019-05-24 | 17.4 | 0.6 | 0 | 2018-05-24 | 24.6 | 0 | 6.6 | 2017-05-24 | 22.8 | 0 | 4.8 | 2016-05-24 | 29 | 0 | 11 | 1.54 | 3.37
2025-05-24 | 12 | 6 | 0 | 2024-05-24 | 16.9 | 1.1 | 0 | 2023-05-24 | 12.5 | 5.5 | 0 | 2022-05-24 | 17.7 | 0.3 | 0 | 2021-05-24 | 21.5 | 0 | 3.5 | 2020-05-24 | 27.9 | 0 | 9.9 | 2019-05-24 | 17.9 | 0.1 | 0 | 2018-05-24 | 25.7 | 0 | 7.7 | 2017-05-24 | 22.7 | 0 | 4.7 | 2016-05-24 | 28.9 | 0 | 10.9 | 1.3 | 3.67
2025-05-24 | 12.4 | 5.6 | 0 | 2024-05-24 | 17.2 | 0.8 | 0 | 2023-05-24 | 12.6 | 5.4 | 0 | 2022-05-24 | 18.4 | 0 | 0.4 | 2021-05-24 | 21.4 | 0 | 3.4 | 2020-05-24 | 27.1 | 0 | 9.1 | 2019-05-24 | 19.3 | 0 | 1.3 | 2018-05-24 | 25.5 | 0 | 7.5 | 2017-05-24 | 23.1 | 0 | 5.1 | 2016-05-24 | 29.2 | 0 | 11.2 | 1.18 | 3.8
2025-05-24 | 11.4 | 6.6 | 0 | 2024-05-24 | 17.3 | 0.7 | 0 | 2023-05-24 | 12.1 | 5.9 | 0 | 2022-05-24 | 17.9 | 0.1 | 0 | 2021-05-24 | 21.6 | 0 | 3.6 | 2020-05-24 | 26.7 | 0 | 8.7 | 2019-05-24 | 19.1 | 0 | 1.1 | 2018-05-24 | 25.3 | 0 | 7.3 | 2017-05-24 | 22.3 | 0 | 4.3 | 2016-05-24 | 28.7 | 0 | 10.7 | 1.33 | 3.57
2025-05-24 | 11.1 | 6.9 | 0 | 2024-05-24 | 17.4 | 0.6 | 0 | 2023-05-24 | 10.6 | 7.4 | 0 | 2022-05-24 | 16.8 | 1.2 | 0 | 2021-05-24 | 20.8 | 0 | 2.8 | 2020-05-24 | 25.1 | 0 | 7.1 | 2019-05-24 | 18 | 0 | 0 | 2018-05-24 | 23.6 | 0 | 5.6 | 2017-05-24 | 21.7 | 0 | 3.7 | 2016-05-24 | 27.8 | 0 | 9.8 | 1.61 | 2.9
2025-05-24 | 10.9 | 7.1 | 0 | 2024-05-24 | 16.4 | 1.6 | 0 | 2023-05-24 | 9.7 | 8.3 | 0 | 2022-05-24 | 15.5 | 2.5 | 0 | 2021-05-24 | 18.3 | 0 | 0.3 | 2020-05-24 | 23.8 | 0 | 5.8 | 2019-05-24 | 16.7 | 1.3 | 0 | 2018-05-24 | 21.9 | 0 | 3.9 | 2017-05-24 | 20.9 | 0 | 2.9 | 2016-05-24 | 26 | 0 | 8 | 2.08 | 2.09
2025-05-24 | 9.9 | 8.1 | 0 | 2024-05-24 | 14.6 | 3.4 | 0 | 2023-05-24 | 8.6 | 9.4 | 0 | 2022-05-24 | 12.9 | 5.1 | 0 | 2021-05-24 | 16.2 | 1.8 | 0 | 2020-05-24 | 21.2 | 0 | 3.2 | 2019-05-24 | 15 | 3 | 0 | 2018-05-24 | 19.5 | 0 | 1.5 | 2017-05-24 | 19.1 | 0 | 1.1 | 2016-05-24 | 22.2 | 0 | 4.2 | 3.08 | 1
2025-05-24 | 9.5 | 8.5 | 0 | 2024-05-24 | 11.6 | 6.4 | 0 | 2023-05-24 | 8.1 | 9.9 | 0 | 2022-05-24 | 11.4 | 6.6 | 0 | 2021-05-24 | 15.3 | 2.7 | 0 | 2020-05-24 | 21 | 0 | 3 | 2019-05-24 | 15 | 3 | 0 | 2018-05-24 | 17.8 | 0.2 | 0 | 2017-05-24 | 18.7 | 0 | 0.7 | 2016-05-24 | 19.9 | 0 | 1.9 | 3.73 | 0.56
2025-05-24 | 9.3 | 8.7 | 0 | 2024-05-24 | 11.5 | 6.5 | 0 | 2023-05-24 | 6.8 | 11.2 | 0 | 2022-05-24 | 10.8 | 7.2 | 0 | 2021-05-24 | 14 | 4 | 0 | 2020-05-24 | 20.9 | 0 | 2.9 | 2019-05-24 | 13.4 | 4.6 | 0 | 2018-05-24 | 17.9 | 0.1 | 0 | 2017-05-24 | 17.9 | 0.1 | 0 | 2016-05-24 | 18.5 | 0 | 0.5 | 4.24 | 0.34
2025-05-24 | 8 | 10 | 0 | 2024-05-24 | 11.4 | 6.6 | 0 | 2023-05-24 | 6.3 | 11.7 | 0 | 2022-05-24 | 9.3 | 8.7 | 0 | 2021-05-24 | 12.4 | 5.6 | 0 | 2020-05-24 | 19.5 | 0 | 1.5 | 2019-05-24 | 10.7 | 7.3 | 0 | 2018-05-24 | 17.2 | 0.8 | 0 | 2017-05-24 | 16.3 | 1.7 | 0 | 2016-05-24 | 17.3 | 0.7 | 0 | 5.31 | 0.15
2025-05-25 | 6.6 | 11.4 | 0 | 2024-05-25 | 10.3 | 7.7 | 0 | 2023-05-25 | 6.3 | 11.7 | 0 | 2022-05-25 | 9.4 | 8.6 | 0 | 2021-05-25 | 12.4 | 5.6 | 0 | 2020-05-25 | 19.4 | 0 | 1.4 | 2019-05-25 | 11 | 7 | 0 | 2018-05-25 | 16.5 | 1.5 | 0 | 2017-05-25 | 15.8 | 2.2 | 0 | 2016-05-25 | 15.8 | 2.2 | 0 | 5.79 | 0.14
2025-05-25 | 6.6 | 11.4 | 0 | 2024-05-25 | 9.7 | 8.3 | 0 | 2023-05-25 | 5.6 | 12.4 | 0 | 2022-05-25 | 6.2 | 11.8 | 0 | 2021-05-25 | 12.4 | 5.6 | 0 | 2020-05-25 | 20.6 | 0 | 2.6 | 2019-05-25 | 10.7 | 7.3 | 0 | 2018-05-25 | 16.1 | 1.9 | 0 | 2017-05-25 | 15.4 | 2.6 | 0 | 2016-05-25 | 16.2 | 1.8 | 0 | 6.31 | 0.26
2025-05-25 | 7.6 | 10.4 | 0 | 2024-05-25 | 9.7 | 8.3 | 0 | 2023-05-25 | 5.1 | 12.9 | 0 | 2022-05-25 | 5.7 | 12.3 | 0 | 2021-05-25 | 11.9 | 6.1 | 0 | 2020-05-25 | 20.7 | 0 | 2.7 | 2019-05-25 | 11 | 7 | 0 | 2018-05-25 | 16.4 | 1.6 | 0 | 2017-05-25 | 15.4 | 2.6 | 0 | 2016-05-25 | 17.3 | 0.7 | 0 | 6.19 | 0.27
2025-05-25 | 6.7 | 11.3 | 0 | 2024-05-25 | 9 | 9 | 0 | 2023-05-25 | 4.7 | 13.3 | 0 | 2022-05-25 | 6.6 | 11.4 | 0 | 2021-05-25 | 11.9 | 6.1 | 0 | 2020-05-25 | 18.1 | 0 | 0.1 | 2019-05-25 | 10.5 | 7.5 | 0 | 2018-05-25 | 15.9 | 2.1 | 0 | 2017-05-25 | 14.9 | 3.1 | 0 | 2016-05-25 | 16 | 2 | 0 | 6.58 | 0.01
2025-05-25 | 7.6 | 10.4 | 0 | 2024-05-25 | 7.8 | 10.2 | 0 | 2023-05-25 | 4.2 | 13.8 | 0 | 2022-05-25 | 6.8 | 11.2 | 0 | 2021-05-25 | 11 | 7 | 0 | 2020-05-25 | 17.1 | 0.9 | 0 | 2019-05-25 | 9.4 | 8.6 | 0 | 2018-05-25 | 15.4 | 2.6 | 0 | 2017-05-25 | 15 | 3 | 0 | 2016-05-25 | 15.7 | 2.3 | 0 | 7 | 0
2025-05-25 | 7.9 | 10.1 | 0 | 2024-05-25 | 7.3 | 10.7 | 0 | 2023-05-25 | 4.2 | 13.8 | 0 | 2022-05-25 | 6.3 | 11.7 | 0 | 2021-05-25 | 12.8 | 5.2 | 0 | 2020-05-25 | 16.8 | 1.2 | 0 | 2019-05-25 | 9.9 | 8.1 | 0 | 2018-05-25 | 14.9 | 3.1 | 0 | 2017-05-25 | 14.4 | 3.6 | 0 | 2016-05-25 | 14.1 | 3.9 | 0 | 7.14 | 0
2025-05-25 | 8.6 | 9.4 | 0 | 2024-05-25 | 11 | 7 | 0 | 2023-05-25 | 5.2 | 12.8 | 0 | 2022-05-25 | 9.9 | 8.1 | 0 | 2021-05-25 | 13.9 | 4.1 | 0 | 2020-05-25 | 16.8 | 1.2 | 0 | 2019-05-25 | 11.2 | 6.8 | 0 | 2018-05-25 | 16.9 | 1.1 | 0 | 2017-05-25 | 13.9 | 4.1 | 0 | 2016-05-25 | 13.8 | 4.2 | 0 | 5.88 | 0
2025-05-25 | 10 | 8 | 0 | 2024-05-25 | 13.2 | 4.8 | 0 | 2023-05-25 | 6.7 | 11.3 | 0 | 2022-05-25 | 13 | 5 | 0 | 2021-05-25 | 15.1 | 2.9 | 0 | 2020-05-25 | 16.7 | 1.3 | 0 | 2019-05-25 | 14.2 | 3.8 | 0 | 2018-05-25 | 19.5 | 0 | 1.5 | 2017-05-25 | 14.2 | 3.8 | 0 | 2016-05-25 | 18.2 | 0 | 0.2 | 4.09 | 0.17
2025-05-25 | 12 | 6 | 0 | 2024-05-25 | 14.7 | 3.3 | 0 | 2023-05-25 | 9 | 9 | 0 | 2022-05-25 | 15.8 | 2.2 | 0 | 2021-05-25 | 16.5 | 1.5 | 0 | 2020-05-25 | 16.5 | 1.5 | 0 | 2019-05-25 | 17 | 1 | 0 | 2018-05-25 | 20.9 | 0 | 2.9 | 2017-05-25 | 14.7 | 3.3 | 0 | 2016-05-25 | 19.9 | 0 | 1.9 | 2.78 | 0.48
2025-05-25 | 12.9 | 5.1 | 0 | 2024-05-25 | 16.2 | 1.8 | 0 | 2023-05-25 | 10.1 | 7.9 | 0 | 2022-05-25 | 17.7 | 0.3 | 0 | 2021-05-25 | 20 | 0 | 2 | 2020-05-25 | 17 | 1 | 0 | 2019-05-25 | 17.9 | 0.1 | 0 | 2018-05-25 | 19.6 | 0 | 1.6 | 2017-05-25 | 15.6 | 2.4 | 0 | 2016-05-25 | 19.1 | 0 | 1.1 | 1.86 | 0.47
2025-05-25 | 13.9 | 4.1 | 0 | 2024-05-25 | 17.5 | 0.5 | 0 | 2023-05-25 | 11.8 | 6.2 | 0 | 2022-05-25 | 19.1 | 0 | 1.1 | 2021-05-25 | 22.7 | 0 | 4.7 | 2020-05-25 | 17.6 | 0.4 | 0 | 2019-05-25 | 18.1 | 0 | 0.1 | 2018-05-25 | 20.4 | 0 | 2.4 | 2017-05-25 | 17 | 1 | 0 | 2016-05-25 | 20.6 | 0 | 2.6 | 1.22 | 1.09
2025-05-25 | 16 | 2 | 0 | 2024-05-25 | 17.2 | 0.8 | 0 | 2023-05-25 | 14.1 | 3.9 | 0 | 2022-05-25 | 19.5 | 0 | 1.5 | 2021-05-25 | 23.1 | 0 | 5.1 | 2020-05-25 | 19.2 | 0 | 1.2 | 2019-05-25 | 17.4 | 0.6 | 0 | 2018-05-25 | 21.9 | 0 | 3.9 | 2017-05-25 | 18.3 | 0 | 0.3 | 2016-05-25 | 22.8 | 0 | 4.8 | 0.73 | 1.68
2025-05-25 | 17.9 | 0.1 | 0 | 2024-05-25 | 18.1 | 0 | 0.1 | 2023-05-25 | 14.7 | 3.3 | 0 | 2022-05-25 | 19.9 | 0 | 1.9 | 2021-05-25 | 22.1 | 0 | 4.1 | 2020-05-25 | 20.4 | 0 | 2.4 | 2019-05-25 | 14.5 | 3.5 | 0 | 2018-05-25 | 24.8 | 0 | 6.8 | 2017-05-25 | 18.4 | 0 | 0.4 | 2016-05-25 | 24.9 | 0 | 6.9 | 0.69 | 2.26
2025-05-25 | 17.5 | 0.5 | 0 | 2024-05-25 | 18.8 | 0 | 0.8 | 2023-05-25 | 15.5 | 2.5 | 0 | 2022-05-25 | 20.9 | 0 | 2.9 | 2021-05-25 | 25.1 | 0 | 7.1 | 2020-05-25 | 21.3 | 0 | 3.3 | 2019-05-25 | 14.4 | 3.6 | 0 | 2018-05-25 | 26.1 | 0 | 8.1 | 2017-05-25 | 18.1 | 0 | 0.1 | 2016-05-25 | 24.8 | 0 | 6.8 | 0.66 | 2.91
2025-05-25 | 19.3 | 0 | 1.3 | 2024-05-25 | 18.1 | 0 | 0.1 | 2023-05-25 | 16.5 | 1.5 | 0 | 2022-05-25 | 20.6 | 0 | 2.6 | 2021-05-25 | 25.5 | 0 | 7.5 | 2020-05-25 | 21.5 | 0 | 3.5 | 2019-05-25 | 15.2 | 2.8 | 0 | 2018-05-25 | 25.2 | 0 | 7.2 | 2017-05-25 | 17.1 | 0.9 | 0 | 2016-05-25 | 26.2 | 0 | 8.2 | 0.52 | 3.04
2025-05-25 | 17.9 | 0.1 | 0 | 2024-05-25 | 17.9 | 0.1 | 0 | 2023-05-25 | 16.7 | 1.3 | 0 | 2022-05-25 | 20.8 | 0 | 2.8 | 2021-05-25 | 26.2 | 0 | 8.2 | 2020-05-25 | 21.7 | 0 | 3.7 | 2019-05-25 | 15.6 | 2.4 | 0 | 2018-05-25 | 25.1 | 0 | 7.1 | 2017-05-25 | 15.7 | 2.3 | 0 | 2016-05-25 | 26 | 0 | 8 | 0.62 | 2.98
2025-05-25 | 18.4 | 0 | 0.4 | 2024-05-25 | 17.8 | 0.2 | 0 | 2023-05-25 | 17.5 | 0.5 | 0 | 2022-05-25 | 20.2 | 0 | 2.2 | 2021-05-25 | 24.9 | 0 | 6.9 | 2020-05-25 | 22.2 | 0 | 4.2 | 2019-05-25 | 16.2 | 1.8 | 0 | 2018-05-25 | 20 | 0 | 2 | 2017-05-25 | 14.3 | 3.7 | 0 | 2016-05-25 | 25.9 | 0 | 7.9 | 0.62 | 2.36
2025-05-25 | 15.8 | 2.2 | 0 | 2024-05-25 | 16.9 | 1.1 | 0 | 2023-05-25 | 17.2 | 0.8 | 0 | 2022-05-25 | 20.6 | 0 | 2.6 | 2021-05-25 | 25.1 | 0 | 7.1 | 2020-05-25 | 23 | 0 | 5 | 2019-05-25 | 16.2 | 1.8 | 0 | 2018-05-25 | 19.4 | 0 | 1.4 | 2017-05-25 | 13.6 | 4.4 | 0 | 2016-05-25 | 25.4 | 0 | 7.4 | 1.03 | 2.35
2025-05-25 | 12.2 | 5.8 | 0 | 2024-05-25 | 16.5 | 1.5 | 0 | 2023-05-25 | 16.8 | 1.2 | 0 | 2022-05-25 | 19.4 | 0 | 1.4 | 2021-05-25 | 25.4 | 0 | 7.4 | 2020-05-25 | 22.5 | 0 | 4.5 | 2019-05-25 | 15.8 | 2.2 | 0 | 2018-05-25 | 18.4 | 0 | 0.4 | 2017-05-25 | 13.7 | 4.3 | 0 | 2016-05-25 | 24 | 0 | 6 | 1.5 | 1.97
2025-05-25 | 12.9 | 5.1 | 0 | 2024-05-25 | 15.8 | 2.2 | 0 | 2023-05-25 | 15.5 | 2.5 | 0 | 2022-05-25 | 17.6 | 0.4 | 0 | 2021-05-25 | 24.4 | 0 | 6.4 | 2020-05-25 | 20.9 | 0 | 2.9 | 2019-05-25 | 15.2 | 2.8 | 0 | 2018-05-25 | 19.2 | 0 | 1.2 | 2017-05-25 | 13 | 5 | 0 | 2016-05-25 | 22.4 | 0 | 4.4 | 1.8 | 1.49
2025-05-25 | 13.1 | 4.9 | 0 | 2024-05-25 | 15.5 | 2.5 | 0 | 2023-05-25 | 14.8 | 3.2 | 0 | 2022-05-25 | 16.6 | 1.4 | 0 | 2021-05-25 | 24.2 | 0 | 6.2 | 2020-05-25 | 19.2 | 0 | 1.2 | 2019-05-25 | 15.1 | 2.9 | 0 | 2018-05-25 | 18.8 | 0 | 0.8 | 2017-05-25 | 12.7 | 5.3 | 0 | 2016-05-25 | 20 | 0 | 2 | 2.02 | 1.02
2025-05-25 | 10.7 | 7.3 | 0 | 2024-05-25 | 15.7 | 2.3 | 0 | 2023-05-25 | 12.8 | 5.2 | 0 | 2022-05-25 | 16.4 | 1.6 | 0 | 2021-05-25 | 24.2 | 0 | 6.2 | 2020-05-25 | 18.5 | 0 | 0.5 | 2019-05-25 | 15.2 | 2.8 | 0 | 2018-05-25 | 18.2 | 0 | 0.2 | 2017-05-25 | 12.8 | 5.2 | 0 | 2016-05-25 | 18.5 | 0 | 0.5 | 2.44 | 0.74
2025-05-25 | 10.8 | 7.2 | 0 | 2024-05-25 | 14.3 | 3.7 | 0 | 2023-05-25 | 10.6 | 7.4 | 0 | 2022-05-25 | 15.8 | 2.2 | 0 | 2021-05-25 | 23.2 | 0 | 5.2 | 2020-05-25 | 18.2 | 0 | 0.2 | 2019-05-25 | 15.5 | 2.5 | 0 | 2018-05-25 | 17.3 | 0.7 | 0 | 2017-05-25 | 12.3 | 5.7 | 0 | 2016-05-25 | 16.6 | 1.4 | 0 | 3.08 | 0.54
2025-05-25 | 10.5 | 7.5 | 0 | 2024-05-25 | 13 | 5 | 0 | 2023-05-25 | 9.1 | 8.9 | 0 | 2022-05-25 | 16.3 | 1.7 | 0 | 2021-05-25 | 22.4 | 0 | 4.4 | 2020-05-25 | 17.2 | 0.8 | 0 | 2019-05-25 | 15.4 | 2.6 | 0 | 2018-05-25 | 17.1 | 0.9 | 0 | 2017-05-25 | 12.4 | 5.6 | 0 | 2016-05-25 | 15.4 | 2.6 | 0 | 3.56 | 0.44
2025-05-26 | 9.7 | 8.3 | 0 | 2024-05-26 | 14 | 4 | 0 | 2023-05-26 | 7.7 | 10.3 | 0 | 2022-05-26 | 16.4 | 1.6 | 0 | 2021-05-26 | 22.7 | 0 | 4.7 | 2020-05-26 | 17.4 | 0.6 | 0 | 2019-05-26 | 15.4 | 2.6 | 0 | 2018-05-26 | 16.7 | 1.3 | 0 | 2017-05-26 | 12.2 | 5.8 | 0 | 2016-05-26 | 14.9 | 3.1 | 0 | 3.76 | 0.47
2025-05-26 | 8.9 | 9.1 | 0 | 2024-05-26 | 13.6 | 4.4 | 0 | 2023-05-26 | 7.4 | 10.6 | 0 | 2022-05-26 | 16.3 | 1.7 | 0 | 2021-05-26 | 21.9 | 0 | 3.9 | 2020-05-26 | 16.6 | 1.4 | 0 | 2019-05-26 | 15.8 | 2.2 | 0 | 2018-05-26 | 17 | 1 | 0 | 2017-05-26 | 12.1 | 5.9 | 0 | 2016-05-26 | 14 | 4 | 0 | 4.03 | 0.39
2025-05-26 | 8.9 | 9.1 | 0 | 2024-05-26 | 13.5 | 4.5 | 0 | 2023-05-26 | 6.1 | 11.9 | 0 | 2022-05-26 | 14.5 | 3.5 | 0 | 2021-05-26 | 20.9 | 0 | 2.9 | 2020-05-26 | 16.3 | 1.7 | 0 | 2019-05-26 | 15.3 | 2.7 | 0 | 2018-05-26 | 17.2 | 0.8 | 0 | 2017-05-26 | 11.9 | 6.1 | 0 | 2016-05-26 | 13.1 | 4.9 | 0 | 4.52 | 0.29
2025-05-26 | 7.7 | 10.3 | 0 | 2024-05-26 | 13.3 | 4.7 | 0 | 2023-05-26 | 5 | 13 | 0 | 2022-05-26 | 13.2 | 4.8 | 0 | 2021-05-26 | 20.1 | 0 | 2.1 | 2020-05-26 | 15.8 | 2.2 | 0 | 2019-05-26 | 15.5 | 2.5 | 0 | 2018-05-26 | 17 | 1 | 0 | 2017-05-26 | 11.9 | 6.1 | 0 | 2016-05-26 | 12.7 | 5.3 | 0 | 4.99 | 0.21
2025-05-26 | 7.8 | 10.2 | 0 | 2024-05-26 | 13.2 | 4.8 | 0 | 2023-05-26 | 4.5 | 13.5 | 0 | 2022-05-26 | 12.7 | 5.3 | 0 | 2021-05-26 | 20.1 | 0 | 2.1 | 2020-05-26 | 14.5 | 3.5 | 0 | 2019-05-26 | 15.3 | 2.7 | 0 | 2018-05-26 | 16.9 | 1.1 | 0 | 2017-05-26 | 12.1 | 5.9 | 0 | 2016-05-26 | 11.7 | 6.3 | 0 | 5.33 | 0.21
2025-05-26 | 7.7 | 10.3 | 0 | 2024-05-26 | 13.4 | 4.6 | 0 | 2023-05-26 | 5.1 | 12.9 | 0 | 2022-05-26 | 13.2 | 4.8 | 0 | 2021-05-26 | 20.6 | 0 | 2.6 | 2020-05-26 | 14.4 | 3.6 | 0 | 2019-05-26 | 15.6 | 2.4 | 0 | 2018-05-26 | 16.7 | 1.3 | 0 | 2017-05-26 | 12.1 | 5.9 | 0 | 2016-05-26 | 11.9 | 6.1 | 0 | 5.19 | 0.26
2025-05-26 | 9.3 | 8.7 | 0 | 2024-05-26 | 14 | 4 | 0 | 2023-05-26 | 8 | 10 | 0 | 2022-05-26 | 13.9 | 4.1 | 0 | 2021-05-26 | 20.9 | 0 | 2.9 | 2020-05-26 | 17.9 | 0.1 | 0 | 2019-05-26 | 16.4 | 1.6 | 0 | 2018-05-26 | 17.6 | 0.4 | 0 | 2017-05-26 | 12 | 6 | 0 | 2016-05-26 | 14.2 | 3.8 | 0 | 3.87 | 0.29
2025-05-26 | 11.4 | 6.6 | 0 | 2024-05-26 | 14.5 | 3.5 | 0 | 2023-05-26 | 11.3 | 6.7 | 0 | 2022-05-26 | 15.2 | 2.8 | 0 | 2021-05-26 | 21.3 | 0 | 3.3 | 2020-05-26 | 20.4 | 0 | 2.4 | 2019-05-26 | 18 | 0 | 0 | 2018-05-26 | 18.9 | 0 | 0.9 | 2017-05-26 | 12 | 6 | 0 | 2016-05-26 | 16.1 | 1.9 | 0 | 2.75 | 0.66
2025-05-26 | 14.3 | 3.7 | 0 | 2024-05-26 | 15.5 | 2.5 | 0 | 2023-05-26 | 14.7 | 3.3 | 0 | 2022-05-26 | 15.9 | 2.1 | 0 | 2021-05-26 | 22.2 | 0 | 4.2 | 2020-05-26 | 24.1 | 0 | 6.1 | 2019-05-26 | 18.6 | 0 | 0.6 | 2018-05-26 | 19.2 | 0 | 1.2 | 2017-05-26 | 12.4 | 5.6 | 0 | 2016-05-26 | 18.2 | 0 | 0.2 | 1.72 | 1.23
2025-05-26 | 16.6 | 1.4 | 0 | 2024-05-26 | 17.7 | 0.3 | 0 | 2023-05-26 | 16.9 | 1.1 | 0 | 2022-05-26 | 17.9 | 0.1 | 0 | 2021-05-26 | 23.9 | 0 | 5.9 | 2020-05-26 | 27.1 | 0 | 9.1 | 2019-05-26 | 19.1 | 0 | 1.1 | 2018-05-26 | 18.5 | 0 | 0.5 | 2017-05-26 | 12.4 | 5.6 | 0 | 2016-05-26 | 20.2 | 0 | 2.2 | 0.85 | 1.88
2025-05-26 | 18.3 | 0 | 0.3 | 2024-05-26 | 19 | 0 | 1 | 2023-05-26 | 17.7 | 0.3 | 0 | 2022-05-26 | 20.2 | 0 | 2.2 | 2021-05-26 | 26.3 | 0 | 8.3 | 2020-05-26 | 28.9 | 0 | 10.9 | 2019-05-26 | 19.3 | 0 | 1.3 | 2018-05-26 | 19.3 | 0 | 1.3 | 2017-05-26 | 13.7 | 4.3 | 0 | 2016-05-26 | 21.9 | 0 | 3.9 | 0.46 | 2.92
2025-05-26 | 20.7 | 0 | 2.7 | 2024-05-26 | 19.3 | 0 | 1.3 | 2023-05-26 | 18.4 | 0 | 0.4 | 2022-05-26 | 20.2 | 0 | 2.2 | 2021-05-26 | 27.2 | 0 | 9.2 | 2020-05-26 | 29.9 | 0 | 11.9 | 2019-05-26 | 20.2 | 0 | 2.2 | 2018-05-26 | 20.7 | 0 | 2.7 | 2017-05-26 | 14.6 | 3.4 | 0 | 2016-05-26 | 22.7 | 0 | 4.7 | 0.34 | 3.73
2025-05-26 | 22.1 | 0 | 4.1 | 2024-05-26 | 19.6 | 0 | 1.6 | 2023-05-26 | 19.3 | 0 | 1.3 | 2022-05-26 | 20.5 | 0 | 2.5 | 2021-05-26 | 27.7 | 0 | 9.7 | 2020-05-26 | 31.4 | 0 | 13.4 | 2019-05-26 | 20.6 | 0 | 2.6 | 2018-05-26 | 21.1 | 0 | 3.1 | 2017-05-26 | 15.9 | 2.1 | 0 | 2016-05-26 | 24.2 | 0 | 6.2 | 0.21 | 4.45
2025-05-26 | 22.8 | 0 | 4.8 | 2024-05-26 | 19.5 | 0 | 1.5 | 2023-05-26 | 19.4 | 0 | 1.4 | 2022-05-26 | 21 | 0 | 3 | 2021-05-26 | 24.4 | 0 | 6.4 | 2020-05-26 | 31.9 | 0 | 13.9 | 2019-05-26 | 21.5 | 0 | 3.5 | 2018-05-26 | 21.1 | 0 | 3.1 | 2017-05-26 | 13.5 | 4.5 | 0 | 2016-05-26 | 24.9 | 0 | 6.9 | 0.45 | 4.45
2025-05-26 | 24 | 0 | 6 | 2024-05-26 | 19.9 | 0 | 1.9 | 2023-05-26 | 20.3 | 0 | 2.3 | 2022-05-26 | 21.2 | 0 | 3.2 | 2021-05-26 | 25.2 | 0 | 7.2 | 2020-05-26 | 33.2 | 0 | 15.2 | 2019-05-26 | 22 | 0 | 4 | 2018-05-26 | 21.3 | 0 | 3.3 | 2017-05-26 | 12.6 | 5.4 | 0 | 2016-05-26 | 25.2 | 0 | 7.2 | 0.54 | 5.03
2025-05-26 | 23.5 | 0 | 5.5 | 2024-05-26 | 20.6 | 0 | 2.6 | 2023-05-26 | 19.9 | 0 | 1.9 | 2022-05-26 | 22.2 | 0 | 4.2 | 2021-05-26 | 26.8 | 0 | 8.8 | 2020-05-26 | 30.8 | 0 | 12.8 | 2019-05-26 | 21.9 | 0 | 3.9 | 2018-05-26 | 20 | 0 | 2 | 2017-05-26 | 13.6 | 4.4 | 0 | 2016-05-26 | 24.9 | 0 | 6.9 | 0.44 | 4.86
2025-05-26 | 23.5 | 0 | 5.5 | 2024-05-26 | 21 | 0 | 3 | 2023-05-26 | 20.1 | 0 | 2.1 | 2022-05-26 | 24.8 | 0 | 6.8 | 2021-05-26 | 25.9 | 0 | 7.9 | 2020-05-26 | 30.8 | 0 | 12.8 | 2019-05-26 | 22.4 | 0 | 4.4 | 2018-05-26 | 20.2 | 0 | 2.2 | 2017-05-26 | 12.8 | 5.2 | 0 | 2016-05-26 | 24.4 | 0 | 6.4 | 0.52 | 5.11
2025-05-26 | 21.9 | 0 | 3.9 | 2024-05-26 | 21.5 | 0 | 3.5 | 2023-05-26 | 20.6 | 0 | 2.6 | 2022-05-26 | 24.2 | 0 | 6.2 | 2021-05-26 | 25 | 0 | 7 | 2020-05-26 | 31.9 | 0 | 13.9 | 2019-05-26 | 22.4 | 0 | 4.4 | 2018-05-26 | 21 | 0 | 3 | 2017-05-26 | 13.4 | 4.6 | 0 | 2016-05-26 | 23.4 | 0 | 5.4 | 0.46 | 4.99
2025-05-26 | 20.9 | 0 | 2.9 | 2024-05-26 | 20.8 | 0 | 2.8 | 2023-05-26 | 21.1 | 0 | 3.1 | 2022-05-26 | 23.6 | 0 | 5.6 | 2021-05-26 | 23.9 | 0 | 5.9 | 2020-05-26 | 30.6 | 0 | 12.6 | 2019-05-26 | 21.7 | 0 | 3.7 | 2018-05-26 | 20.7 | 0 | 2.7 | 2017-05-26 | 13.2 | 4.8 | 0 | 2016-05-26 | 22.6 | 0 | 4.6 | 0.48 | 4.39
2025-05-26 | 18.8 | 0 | 0.8 | 2024-05-26 | 19.2 | 0 | 1.2 | 2023-05-26 | 17.9 | 0.1 | 0 | 2022-05-26 | 23.5 | 0 | 5.5 | 2021-05-26 | 22.4 | 0 | 4.4 | 2020-05-26 | 29.5 | 0 | 11.5 | 2019-05-26 | 20.5 | 0 | 2.5 | 2018-05-26 | 19.9 | 0 | 1.9 | 2017-05-26 | 13 | 5 | 0 | 2016-05-26 | 20.9 | 0 | 2.9 | 0.51 | 3.07
2025-05-26 | 16.6 | 1.4 | 0 | 2024-05-26 | 17.6 | 0.4 | 0 | 2023-05-26 | 17.8 | 0.2 | 0 | 2022-05-26 | 22.9 | 0 | 4.9 | 2021-05-26 | 21.3 | 0 | 3.3 | 2020-05-26 | 27.5 | 0 | 9.5 | 2019-05-26 | 17.7 | 0.3 | 0 | 2018-05-26 | 19.1 | 0 | 1.1 | 2017-05-26 | 12.2 | 5.8 | 0 | 2016-05-26 | 20.3 | 0 | 2.3 | 0.81 | 2.11
2025-05-26 | 14.8 | 3.2 | 0 | 2024-05-26 | 16 | 2 | 0 | 2023-05-26 | 15.9 | 2.1 | 0 | 2022-05-26 | 21.9 | 0 | 3.9 | 2021-05-26 | 19.7 | 0 | 1.7 | 2020-05-26 | 25.3 | 0 | 7.3 | 2019-05-26 | 18.6 | 0 | 0.6 | 2018-05-26 | 18.3 | 0 | 0.3 | 2017-05-26 | 12.2 | 5.8 | 0 | 2016-05-26 | 18.7 | 0 | 0.7 | 1.31 | 1.45
2025-05-26 | 13.9 | 4.1 | 0 | 2024-05-26 | 15.8 | 2.2 | 0 | 2023-05-26 | 11.5 | 6.5 | 0 | 2022-05-26 | 21.2 | 0 | 3.2 | 2021-05-26 | 18.2 | 0 | 0.2 | 2020-05-26 | 25.1 | 0 | 7.1 | 2019-05-26 | 17.1 | 0.9 | 0 | 2018-05-26 | 17.7 | 0.3 | 0 | 2017-05-26 | 11.9 | 6.1 | 0 | 2016-05-26 | 16.7 | 1.3 | 0 | 2.14 | 1.05
2025-05-26 | 12.2 | 5.8 | 0 | 2024-05-26 | 16.3 | 1.7 | 0 | 2023-05-26 | 13 | 5 | 0 | 2022-05-26 | 21.5 | 0 | 3.5 | 2021-05-26 | 17.7 | 0.3 | 0 | 2020-05-26 | 23.9 | 0 | 5.9 | 2019-05-26 | 15.2 | 2.8 | 0 | 2018-05-26 | 16.7 | 1.3 | 0 | 2017-05-26 | 11.7 | 6.3 | 0 | 2016-05-26 | 16.1 | 1.9 | 0 | 2.51 | 0.94
2025-05-27 | 11 | 7 | 0 | 2024-05-27 | 16.7 | 1.3 | 0 | 2023-05-27 | 11.3 | 6.7 | 0 | 2022-05-27 | 20.5 | 0 | 2.5 | 2021-05-27 | 16.8 | 1.2 | 0 | 2020-05-27 | 22.9 | 0 | 4.9 | 2019-05-27 | 12.6 | 5.4 | 0 | 2018-05-27 | 16.3 | 1.7 | 0 | 2017-05-27 | 12.2 | 5.8 | 0 | 2016-05-27 | 15.1 | 2.9 | 0 | 3.2 | 0.74
2025-05-27 | 10.2 | 7.8 | 0 | 2024-05-27 | 16.5 | 1.5 | 0 | 2023-05-27 | 11.3 | 6.7 | 0 | 2022-05-27 | 20.1 | 0 | 2.1 | 2021-05-27 | 14.7 | 3.3 | 0 | 2020-05-27 | 20.2 | 0 | 2.2 | 2019-05-27 | 10.6 | 7.4 | 0 | 2018-05-27 | 16.2 | 1.8 | 0 | 2017-05-27 | 11.6 | 6.4 | 0 | 2016-05-27 | 15.3 | 2.7 | 0 | 3.76 | 0.43
2025-05-27 | 9.7 | 8.3 | 0 | 2024-05-27 | 16.8 | 1.2 | 0 | 2023-05-27 | 9.6 | 8.4 | 0 | 2022-05-27 | 18.3 | 0 | 0.3 | 2021-05-27 | 12.4 | 5.6 | 0 | 2020-05-27 | 19.5 | 0 | 1.5 | 2019-05-27 | 9.9 | 8.1 | 0 | 2018-05-27 | 15.8 | 2.2 | 0 | 2017-05-27 | 11.1 | 6.9 | 0 | 2016-05-27 | 15 | 3 | 0 | 4.37 | 0.18
2025-05-27 | 8.5 | 9.5 | 0 | 2024-05-27 | 16.3 | 1.7 | 0 | 2023-05-27 | 8.8 | 9.2 | 0 | 2022-05-27 | 17.5 | 0.5 | 0 | 2021-05-27 | 10.2 | 7.8 | 0 | 2020-05-27 | 19 | 0 | 1 | 2019-05-27 | 8.7 | 9.3 | 0 | 2018-05-27 | 14.8 | 3.2 | 0 | 2017-05-27 | 9.9 | 8.1 | 0 | 2016-05-27 | 14.5 | 3.5 | 0 | 5.28 | 0.1
2025-05-27 | 8.7 | 9.3 | 0 | 2024-05-27 | 16.9 | 1.1 | 0 | 2023-05-27 | 7.9 | 10.1 | 0 | 2022-05-27 | 17.5 | 0.5 | 0 | 2021-05-27 | 8.9 | 9.1 | 0 | 2020-05-27 | 19.3 | 0 | 1.3 | 2019-05-27 | 10.6 | 7.4 | 0 | 2018-05-27 | 14.1 | 3.9 | 0 | 2017-05-27 | 10.3 | 7.7 | 0 | 2016-05-27 | 13.6 | 4.4 | 0 | 5.35 | 0.13
2025-05-27 | 8.8 | 9.2 | 0 | 2024-05-27 | 16.8 | 1.2 | 0 | 2023-05-27 | 8 | 10 | 0 | 2022-05-27 | 17.7 | 0.3 | 0 | 2021-05-27 | 7.5 | 10.5 | 0 | 2020-05-27 | 20.7 | 0 | 2.7 | 2019-05-27 | 9.3 | 8.7 | 0 | 2018-05-27 | 13.6 | 4.4 | 0 | 2017-05-27 | 9.5 | 8.5 | 0 | 2016-05-27 | 12.5 | 5.5 | 0 | 5.83 | 0.27
2025-05-27 | 10.4 | 7.6 | 0 | 2024-05-27 | 17.4 | 0.6 | 0 | 2023-05-27 | 9.6 | 8.4 | 0 | 2022-05-27 | 18 | 0 | 0 | 2021-05-27 | 7.5 | 10.5 | 0 | 2020-05-27 | 21.7 | 0 | 3.7 | 2019-05-27 | 12.2 | 5.8 | 0 | 2018-05-27 | 13.4 | 4.6 | 0 | 2017-05-27 | 10.9 | 7.1 | 0 | 2016-05-27 | 16.9 | 1.1 | 0 | 4.57 | 0.37
2025-05-27 | 14 | 4 | 0 | 2024-05-27 | 18.5 | 0 | 0.5 | 2023-05-27 | 12.7 | 5.3 | 0 | 2022-05-27 | 18.1 | 0 | 0.1 | 2021-05-27 | 8.5 | 9.5 | 0 | 2020-05-27 | 24.1 | 0 | 6.1 | 2019-05-27 | 13.1 | 4.9 | 0 | 2018-05-27 | 13.8 | 4.2 | 0 | 2017-05-27 | 14.1 | 3.9 | 0 | 2016-05-27 | 17.8 | 0.2 | 0 | 3.2 | 0.67
2025-05-27 | 16.6 | 1.4 | 0 | 2024-05-27 | 21.7 | 0 | 3.7 | 2023-05-27 | 16.3 | 1.7 | 0 | 2022-05-27 | 18.2 | 0 | 0.2 | 2021-05-27 | 8.3 | 9.7 | 0 | 2020-05-27 | 26.4 | 0 | 8.4 | 2019-05-27 | 12.2 | 5.8 | 0 | 2018-05-27 | 14.2 | 3.8 | 0 | 2017-05-27 | 15.3 | 2.7 | 0 | 2016-05-27 | 21.6 | 0 | 3.6 | 2.51 | 1.59
2025-05-27 | 19.1 | 0 | 1.1 | 2024-05-27 | 22.8 | 0 | 4.8 | 2023-05-27 | 19.4 | 0 | 1.4 | 2022-05-27 | 18.6 | 0 | 0.6 | 2021-05-27 | 9.5 | 8.5 | 0 | 2020-05-27 | 28.2 | 0 | 10.2 | 2019-05-27 | 12.6 | 5.4 | 0 | 2018-05-27 | 15.1 | 2.9 | 0 | 2017-05-27 | 16.9 | 1.1 | 0 | 2016-05-27 | 24.9 | 0 | 6.9 | 1.79 | 2.5
2025-05-27 | 21.4 | 0 | 3.4 | 2024-05-27 | 22.7 | 0 | 4.7 | 2023-05-27 | 21.6 | 0 | 3.6 | 2022-05-27 | 18.8 | 0 | 0.8 | 2021-05-27 | 10.7 | 7.3 | 0 | 2020-05-27 | 30.3 | 0 | 12.3 | 2019-05-27 | 10.2 | 7.8 | 0 | 2018-05-27 | 16.2 | 1.8 | 0 | 2017-05-27 | 18.3 | 0 | 0.3 | 2016-05-27 | 26.6 | 0 | 8.6 | 1.69 | 3.37
2025-05-27 | 23.6 | 0 | 5.6 | 2024-05-27 | 23.1 | 0 | 5.1 | 2023-05-27 | 23.9 | 0 | 5.9 | 2022-05-27 | 19.3 | 0 | 1.3 | 2021-05-27 | 11.7 | 6.3 | 0 | 2020-05-27 | 32.4 | 0 | 14.4 | 2019-05-27 | 10.4 | 7.6 | 0 | 2018-05-27 | 17.5 | 0.5 | 0 | 2017-05-27 | 19.4 | 0 | 1.4 | 2016-05-27 | 28.1 | 0 | 10.1 | 1.44 | 4.38
2025-05-27 | 24.1 | 0 | 6.1 | 2024-05-27 | 19.5 | 0 | 1.5 | 2023-05-27 | 25.5 | 0 | 7.5 | 2022-05-27 | 19.9 | 0 | 1.9 | 2021-05-27 | 12.6 | 5.4 | 0 | 2020-05-27 | 33.6 | 0 | 15.6 | 2019-05-27 | 10.8 | 7.2 | 0 | 2018-05-27 | 18.7 | 0 | 0.7 | 2017-05-27 | 20.4 | 0 | 2.4 | 2016-05-27 | 29.6 | 0 | 11.6 | 1.26 | 4.73
2025-05-27 | 24.7 | 0 | 6.7 | 2024-05-27 | 19.7 | 0 | 1.7 | 2023-05-27 | 26.4 | 0 | 8.4 | 2022-05-27 | 20.7 | 0 | 2.7 | 2021-05-27 | 12.8 | 5.2 | 0 | 2020-05-27 | 34.1 | 0 | 16.1 | 2019-05-27 | 13.2 | 4.8 | 0 | 2018-05-27 | 20.7 | 0 | 2.7 | 2017-05-27 | 21 | 0 | 3 | 2016-05-27 | 29.2 | 0 | 11.2 | 1 | 5.25
2025-05-27 | 24.5 | 0 | 6.5 | 2024-05-27 | 19.8 | 0 | 1.8 | 2023-05-27 | 27.5 | 0 | 9.5 | 2022-05-27 | 20.6 | 0 | 2.6 | 2021-05-27 | 12.3 | 5.7 | 0 | 2020-05-27 | 34.8 | 0 | 16.8 | 2019-05-27 | 14.6 | 3.4 | 0 | 2018-05-27 | 21.5 | 0 | 3.5 | 2017-05-27 | 22.2 | 0 | 4.2 | 2016-05-27 | 31.4 | 0 | 13.4 | 0.91 | 5.83
2025-05-27 | 26 | 0 | 8 | 2024-05-27 | 19.5 | 0 | 1.5 | 2023-05-27 | 27.8 | 0 | 9.8 | 2022-05-27 | 20.9 | 0 | 2.9 | 2021-05-27 | 12.1 | 5.9 | 0 | 2020-05-27 | 33.9 | 0 | 15.9 | 2019-05-27 | 14.9 | 3.1 | 0 | 2018-05-27 | 21.7 | 0 | 3.7 | 2017-05-27 | 22.1 | 0 | 4.1 | 2016-05-27 | 31.7 | 0 | 13.7 | 0.9 | 5.96
2025-05-27 | 25.6 | 0 | 7.6 | 2024-05-27 | 20.2 | 0 | 2.2 | 2023-05-27 | 28 | 0 | 10 | 2022-05-27 | 21.4 | 0 | 3.4 | 2021-05-27 | 13.7 | 4.3 | 0 | 2020-05-27 | 33.6 | 0 | 15.6 | 2019-05-27 | 16.2 | 1.8 | 0 | 2018-05-27 | 23.3 | 0 | 5.3 | 2017-05-27 | 22.9 | 0 | 4.9 | 2016-05-27 | 27.3 | 0 | 9.3 | 0.61 | 5.83
2025-05-27 | 25.5 | 0 | 7.5 | 2024-05-27 | 19.9 | 0 | 1.9 | 2023-05-27 | 27.4 | 0 | 9.4 | 2022-05-27 | 21.2 | 0 | 3.2 | 2021-05-27 | 11.9 | 6.1 | 0 | 2020-05-27 | 33 | 0 | 15 | 2019-05-27 | 15.9 | 2.1 | 0 | 2018-05-27 | 23.3 | 0 | 5.3 | 2017-05-27 | 22.2 | 0 | 4.2 | 2016-05-27 | 28.7 | 0 | 10.7 | 0.82 | 5.72
2025-05-27 | 24.7 | 0 | 6.7 | 2024-05-27 | 19.9 | 0 | 1.9 | 2023-05-27 | 26.3 | 0 | 8.3 | 2022-05-27 | 20.1 | 0 | 2.1 | 2021-05-27 | 11.4 | 6.6 | 0 | 2020-05-27 | 31.7 | 0 | 13.7 | 2019-05-27 | 15.9 | 2.1 | 0 | 2018-05-27 | 21.7 | 0 | 3.7 | 2017-05-27 | 20.8 | 0 | 2.8 | 2016-05-27 | 28.7 | 0 | 10.7 | 0.87 | 4.99
2025-05-27 | 23.1 | 0 | 5.1 | 2024-05-27 | 20 | 0 | 2 | 2023-05-27 | 23.9 | 0 | 5.9 | 2022-05-27 | 19.3 | 0 | 1.3 | 2021-05-27 | 10.2 | 7.8 | 0 | 2020-05-27 | 29.9 | 0 | 11.9 | 2019-05-27 | 13.9 | 4.1 | 0 | 2018-05-27 | 21.2 | 0 | 3.2 | 2017-05-27 | 19.5 | 0 | 1.5 | 2016-05-27 | 26.6 | 0 | 8.6 | 1.19 | 3.95
2025-05-27 | 19.7 | 0 | 1.7 | 2024-05-27 | 18.8 | 0 | 0.8 | 2023-05-27 | 20.7 | 0 | 2.7 | 2022-05-27 | 18.7 | 0 | 0.7 | 2021-05-27 | 8.9 | 9.1 | 0 | 2020-05-27 | 27.6 | 0 | 9.6 | 2019-05-27 | 12.1 | 5.9 | 0 | 2018-05-27 | 20.6 | 0 | 2.6 | 2017-05-27 | 17.9 | 0.1 | 0 | 2016-05-27 | 25.6 | 0 | 7.6 | 1.51 | 2.57
2025-05-27 | 19.3 | 0 | 1.3 | 2024-05-27 | 18 | 0 | 0 | 2023-05-27 | 19.1 | 0 | 1.1 | 2022-05-27 | 18.6 | 0 | 0.6 | 2021-05-27 | 7.7 | 10.3 | 0 | 2020-05-27 | 26.3 | 0 | 8.3 | 2019-05-27 | 11.5 | 6.5 | 0 | 2018-05-27 | 19.8 | 0 | 1.8 | 2017-05-27 | 17.5 | 0.5 | 0 | 2016-05-27 | 24.2 | 0 | 6.2 | 1.73 | 1.93
2025-05-27 | 17.4 | 0.6 | 0 | 2024-05-27 | 17.9 | 0.1 | 0 | 2023-05-27 | 17.2 | 0.8 | 0 | 2022-05-27 | 18.4 | 0 | 0.4 | 2021-05-27 | 6.6 | 11.4 | 0 | 2020-05-27 | 25.4 | 0 | 7.4 | 2019-05-27 | 11.2 | 6.8 | 0 | 2018-05-27 | 19.2 | 0 | 1.2 | 2017-05-27 | 16 | 2 | 0 | 2016-05-27 | 22.9 | 0 | 4.9 | 2.17 | 1.39
2025-05-27 | 14.2 | 3.8 | 0 | 2024-05-27 | 17.8 | 0.2 | 0 | 2023-05-27 | 16.6 | 1.4 | 0 | 2022-05-27 | 18 | 0 | 0 | 2021-05-27 | 5.7 | 12.3 | 0 | 2020-05-27 | 24.7 | 0 | 6.7 | 2019-05-27 | 11 | 7 | 0 | 2018-05-27 | 18.4 | 0 | 0.4 | 2017-05-27 | 15 | 3 | 0 | 2016-05-27 | 20.3 | 0 | 2.3 | 2.77 | 0.94
2025-05-28 | 14.8 | 3.2 | 0 | 2024-05-28 | 17.5 | 0.5 | 0 | 2023-05-28 | 14.6 | 3.4 | 0 | 2022-05-28 | 17.5 | 0.5 | 0 | 2021-05-28 | 4.7 | 13.3 | 0 | 2020-05-28 | 23.9 | 0 | 5.9 | 2019-05-28 | 9.8 | 8.2 | 0 | 2018-05-28 | 17.6 | 0.4 | 0 | 2017-05-28 | 13.8 | 4.2 | 0 | 2016-05-28 | 20.2 | 0 | 2.2 | 3.37 | 0.81
2025-05-28 | 11.7 | 6.3 | 0 | 2024-05-28 | 16.9 | 1.1 | 0 | 2023-05-28 | 14.1 | 3.9 | 0 | 2022-05-28 | 17.1 | 0.9 | 0 | 2021-05-28 | 2.5 | 15.5 | 0 | 2020-05-28 | 22.6 | 0 | 4.6 | 2019-05-28 | 8.8 | 9.2 | 0 | 2018-05-28 | 17.8 | 0.2 | 0 | 2017-05-28 | 13.1 | 4.9 | 0 | 2016-05-28 | 20.2 | 0 | 2.2 | 4.2 | 0.68
2025-05-28 | 9.8 | 8.2 | 0 | 2024-05-28 | 17 | 1 | 0 | 2023-05-28 | 12.8 | 5.2 | 0 | 2022-05-28 | 17 | 1 | 0 | 2021-05-28 | 2.8 | 15.2 | 0 | 2020-05-28 | 21 | 0 | 3 | 2019-05-28 | 9.2 | 8.8 | 0 | 2018-05-28 | 17.5 | 0.5 | 0 | 2017-05-28 | 11.5 | 6.5 | 0 | 2016-05-28 | 18.7 | 0 | 0.7 | 4.64 | 0.37
2025-05-28 | 9 | 9 | 0 | 2024-05-28 | 16.5 | 1.5 | 0 | 2023-05-28 | 11.7 | 6.3 | 0 | 2022-05-28 | 16.3 | 1.7 | 0 | 2021-05-28 | 3.2 | 14.8 | 0 | 2020-05-28 | 20.4 | 0 | 2.4 | 2019-05-28 | 9.1 | 8.9 | 0 | 2018-05-28 | 16.1 | 1.9 | 0 | 2017-05-28 | 11 | 7 | 0 | 2016-05-28 | 17.6 | 0.4 | 0 | 5.15 | 0.24
2025-05-28 | 10.1 | 7.9 | 0 | 2024-05-28 | 16.1 | 1.9 | 0 | 2023-05-28 | 10.5 | 7.5 | 0 | 2022-05-28 | 15.4 | 2.6 | 0 | 2021-05-28 | 2.5 | 15.5 | 0 | 2020-05-28 | 19.4 | 0 | 1.4 | 2019-05-28 | 8.8 | 9.2 | 0 | 2018-05-28 | 15.2 | 2.8 | 0 | 2017-05-28 | 10.8 | 7.2 | 0 | 2016-05-28 | 17.5 | 0.5 | 0 | 5.51 | 0.14
2025-05-28 | 8.5 | 9.5 | 0 | 2024-05-28 | 15.8 | 2.2 | 0 | 2023-05-28 | 10.6 | 7.4 | 0 | 2022-05-28 | 14.8 | 3.2 | 0 | 2021-05-28 | 3.1 | 14.9 | 0 | 2020-05-28 | 19.1 | 0 | 1.1 | 2019-05-28 | 9.1 | 8.9 | 0 | 2018-05-28 | 15.5 | 2.5 | 0 | 2017-05-28 | 11.1 | 6.9 | 0 | 2016-05-28 | 18.4 | 0 | 0.4 | 5.55 | 0.15
2025-05-28 | 13.8 | 4.2 | 0 | 2024-05-28 | 15.9 | 2.1 | 0 | 2023-05-28 | 13 | 5 | 0 | 2022-05-28 | 14.3 | 3.7 | 0 | 2021-05-28 | 3.5 | 14.5 | 0 | 2020-05-28 | 21.1 | 0 | 3.1 | 2019-05-28 | 8.3 | 9.7 | 0 | 2018-05-28 | 15.6 | 2.4 | 0 | 2017-05-28 | 12.7 | 5.3 | 0 | 2016-05-28 | 19.8 | 0 | 1.8 | 4.69 | 0.49
2025-05-28 | 15.8 | 2.2 | 0 | 2024-05-28 | 16.2 | 1.8 | 0 | 2023-05-28 | 17.1 | 0.9 | 0 | 2022-05-28 | 14.6 | 3.4 | 0 | 2021-05-28 | 3.9 | 14.1 | 0 | 2020-05-28 | 23.3 | 0 | 5.3 | 2019-05-28 | 8.2 | 9.8 | 0 | 2018-05-28 | 15.9 | 2.1 | 0 | 2017-05-28 | 15.4 | 2.6 | 0 | 2016-05-28 | 20.8 | 0 | 2.8 | 3.69 | 0.81
2025-05-28 | 19.1 | 0 | 1.1 | 2024-05-28 | 16.8 | 1.2 | 0 | 2023-05-28 | 19.2 | 0 | 1.2 | 2022-05-28 | 15.9 | 2.1 | 0 | 2021-05-28 | 4.7 | 13.3 | 0 | 2020-05-28 | 23.6 | 0 | 5.6 | 2019-05-28 | 8.9 | 9.1 | 0 | 2018-05-28 | 15.7 | 2.3 | 0 | 2017-05-28 | 18.3 | 0 | 0.3 | 2016-05-28 | 21.8 | 0 | 3.8 | 2.8 | 1.2
2025-05-28 | 21.6 | 0 | 3.6 | 2024-05-28 | 17.4 | 0.6 | 0 | 2023-05-28 | 20.8 | 0 | 2.8 | 2022-05-28 | 17.6 | 0.4 | 0 | 2021-05-28 | 5.4 | 12.6 | 0 | 2020-05-28 | 24.4 | 0 | 6.4 | 2019-05-28 | 8.2 | 9.8 | 0 | 2018-05-28 | 16.8 | 1.2 | 0 | 2017-05-28 | 20.1 | 0 | 2.1 | 2016-05-28 | 23 | 0 | 5 | 2.46 | 1.99
2025-05-28 | 23 | 0 | 5 | 2024-05-28 | 16.7 | 1.3 | 0 | 2023-05-28 | 23.4 | 0 | 5.4 | 2022-05-28 | 16.9 | 1.1 | 0 | 2021-05-28 | 6.7 | 11.3 | 0 | 2020-05-28 | 24.8 | 0 | 6.8 | 2019-05-28 | 8.5 | 9.5 | 0 | 2018-05-28 | 17.6 | 0.4 | 0 | 2017-05-28 | 21.8 | 0 | 3.8 | 2016-05-28 | 25 | 0 | 7 | 2.36 | 2.8
2025-05-28 | 24.8 | 0 | 6.8 | 2024-05-28 | 17.3 | 0.7 | 0 | 2023-05-28 | 25.3 | 0 | 7.3 | 2022-05-28 | 17.9 | 0.1 | 0 | 2021-05-28 | 9 | 9 | 0 | 2020-05-28 | 26.9 | 0 | 8.9 | 2019-05-28 | 9 | 9 | 0 | 2018-05-28 | 18.9 | 0 | 0.9 | 2017-05-28 | 23.1 | 0 | 5.1 | 2016-05-28 | 27.9 | 0 | 9.9 | 1.88 | 3.89
2025-05-28 | 25.4 | 0 | 7.4 | 2024-05-28 | 19.4 | 0 | 1.4 | 2023-05-28 | 27.4 | 0 | 9.4 | 2022-05-28 | 18.9 | 0 | 0.9 | 2021-05-28 | 9.4 | 8.6 | 0 | 2020-05-28 | 25.8 | 0 | 7.8 | 2019-05-28 | 9.3 | 8.7 | 0 | 2018-05-28 | 20.2 | 0 | 2.2 | 2017-05-28 | 23.8 | 0 | 5.8 | 2016-05-28 | 29.1 | 0 | 11.1 | 1.73 | 4.6
2025-05-28 | 26.1 | 0 | 8.1 | 2024-05-28 | 19.1 | 0 | 1.1 | 2023-05-28 | 29 | 0 | 11 | 2022-05-28 | 19.9 | 0 | 1.9 | 2021-05-28 | 10.5 | 7.5 | 0 | 2020-05-28 | 26.4 | 0 | 8.4 | 2019-05-28 | 10 | 8 | 0 | 2018-05-28 | 21.7 | 0 | 3.7 | 2017-05-28 | 23.6 | 0 | 5.6 | 2016-05-28 | 30.7 | 0 | 12.7 | 1.55 | 5.25
2025-05-28 | 26.3 | 0 | 8.3 | 2024-05-28 | 16.5 | 1.5 | 0 | 2023-05-28 | 29.6 | 0 | 11.6 | 2022-05-28 | 21.2 | 0 | 3.2 | 2021-05-28 | 11.7 | 6.3 | 0 | 2020-05-28 | 26.9 | 0 | 8.9 | 2019-05-28 | 11.1 | 6.9 | 0 | 2018-05-28 | 23.2 | 0 | 5.2 | 2017-05-28 | 25 | 0 | 7 | 2016-05-28 | 32.2 | 0 | 14.2 | 1.47 | 5.84
2025-05-28 | 26.9 | 0 | 8.9 | 2024-05-28 | 17.8 | 0.2 | 0 | 2023-05-28 | 29.9 | 0 | 11.9 | 2022-05-28 | 21.8 | 0 | 3.8 | 2021-05-28 | 12.4 | 5.6 | 0 | 2020-05-28 | 26.9 | 0 | 8.9 | 2019-05-28 | 12.8 | 5.2 | 0 | 2018-05-28 | 24.3 | 0 | 6.3 | 2017-05-28 | 23.4 | 0 | 5.4 | 2016-05-28 | 30.7 | 0 | 12.7 | 1.1 | 5.79
2025-05-28 | 25.9 | 0 | 7.9 | 2024-05-28 | 16.7 | 1.3 | 0 | 2023-05-28 | 30.2 | 0 | 12.2 | 2022-05-28 | 22.2 | 0 | 4.2 | 2021-05-28 | 12.8 | 5.2 | 0 | 2020-05-28 | 26.1 | 0 | 8.1 | 2019-05-28 | 12.9 | 5.1 | 0 | 2018-05-28 | 25.3 | 0 | 7.3 | 2017-05-28 | 23.5 | 0 | 5.5 | 2016-05-28 | 31.3 | 0 | 13.3 | 1.16 | 5.85
2025-05-28 | 25.3 | 0 | 7.3 | 2024-05-28 | 16.1 | 1.9 | 0 | 2023-05-28 | 29.5 | 0 | 11.5 | 2022-05-28 | 21.6 | 0 | 3.6 | 2021-05-28 | 12.2 | 5.8 | 0 | 2020-05-28 | 25.4 | 0 | 7.4 | 2019-05-28 | 12.5 | 5.5 | 0 | 2018-05-28 | 25.4 | 0 | 7.4 | 2017-05-28 | 24.5 | 0 | 6.5 | 2016-05-28 | 29.9 | 0 | 11.9 | 1.32 | 5.56
2025-05-28 | 24.3 | 0 | 6.3 | 2024-05-28 | 16.5 | 1.5 | 0 | 2023-05-28 | 28.7 | 0 | 10.7 | 2022-05-28 | 20.9 | 0 | 2.9 | 2021-05-28 | 12.1 | 5.9 | 0 | 2020-05-28 | 22 | 0 | 4 | 2019-05-28 | 11.7 | 6.3 | 0 | 2018-05-28 | 24.1 | 0 | 6.1 | 2017-05-28 | 22.3 | 0 | 4.3 | 2016-05-28 | 29.3 | 0 | 11.3 | 1.37 | 4.56
2025-05-28 | 21 | 0 | 3 | 2024-05-28 | 16.1 | 1.9 | 0 | 2023-05-28 | 26.1 | 0 | 8.1 | 2022-05-28 | 19.9 | 0 | 1.9 | 2021-05-28 | 11.6 | 6.4 | 0 | 2020-05-28 | 21.8 | 0 | 3.8 | 2019-05-28 | 11.1 | 6.9 | 0 | 2018-05-28 | 22.9 | 0 | 4.9 | 2017-05-28 | 21.2 | 0 | 3.2 | 2016-05-28 | 27.1 | 0 | 9.1 | 1.52 | 3.4
2025-05-28 | 19.6 | 0 | 1.6 | 2024-05-28 | 16.1 | 1.9 | 0 | 2023-05-28 | 26.2 | 0 | 8.2 | 2022-05-28 | 18.3 | 0 | 0.3 | 2021-05-28 | 10.5 | 7.5 | 0 | 2020-05-28 | 21.6 | 0 | 3.6 | 2019-05-28 | 10.6 | 7.4 | 0 | 2018-05-28 | 21.9 | 0 | 3.9 | 2017-05-28 | 19.9 | 0 | 1.9 | 2016-05-28 | 24.3 | 0 | 6.3 | 1.68 | 2.58
2025-05-28 | 19.3 | 0 | 1.3 | 2024-05-28 | 14.9 | 3.1 | 0 | 2023-05-28 | 24.9 | 0 | 6.9 | 2022-05-28 | 16.1 | 1.9 | 0 | 2021-05-28 | 7.7 | 10.3 | 0 | 2020-05-28 | 21.9 | 0 | 3.9 | 2019-05-28 | 10.5 | 7.5 | 0 | 2018-05-28 | 21.3 | 0 | 3.3 | 2017-05-28 | 19.1 | 0 | 1.1 | 2016-05-28 | 22.4 | 0 | 4.4 | 2.28 | 2.09
2025-05-28 | 17.4 | 0.6 | 0 | 2024-05-28 | 14.7 | 3.3 | 0 | 2023-05-28 | 23.1 | 0 | 5.1 | 2022-05-28 | 15.6 | 2.4 | 0 | 2021-05-28 | 6.7 | 11.3 | 0 | 2020-05-28 | 22.2 | 0 | 4.2 | 2019-05-28 | 10.4 | 7.6 | 0 | 2018-05-28 | 20.4 | 0 | 2.4 | 2017-05-28 | 18.9 | 0 | 0.9 | 2016-05-28 | 22 | 0 | 4 | 2.52 | 1.66
2025-05-28 | 16.4 | 1.6 | 0 | 2024-05-28 | 13.4 | 4.6 | 0 | 2023-05-28 | 20.5 | 0 | 2.5 | 2022-05-28 | 15.4 | 2.6 | 0 | 2021-05-28 | 4.9 | 13.1 | 0 | 2020-05-28 | 21.4 | 0 | 3.4 | 2019-05-28 | 10.2 | 7.8 | 0 | 2018-05-28 | 20.4 | 0 | 2.4 | 2017-05-28 | 18.9 | 0 | 0.9 | 2016-05-28 | 22.6 | 0 | 4.6 | 2.97 | 1.38
2025-05-29 | 16.4 | 1.6 | 0 | 2024-05-29 | 12.6 | 5.4 | 0 | 2023-05-29 | 19.3 | 0 | 1.3 | 2022-05-29 | 14 | 4 | 0 | 2021-05-29 | 5.3 | 12.7 | 0 | 2020-05-29 | 21.2 | 0 | 3.2 | 2019-05-29 | 10.2 | 7.8 | 0 | 2018-05-29 | 19.4 | 0 | 1.4 | 2017-05-29 | 18.1 | 0 | 0.1 | 2016-05-29 | 22 | 0 | 4 | 3.15 | 1
2025-05-29 | 16.1 | 1.9 | 0 | 2024-05-29 | 12.4 | 5.6 | 0 | 2023-05-29 | 17.9 | 0.1 | 0 | 2022-05-29 | 13.6 | 4.4 | 0 | 2021-05-29 | 4.5 | 13.5 | 0 | 2020-05-29 | 20.4 | 0 | 2.4 | 2019-05-29 | 8.9 | 9.1 | 0 | 2018-05-29 | 19.4 | 0 | 1.4 | 2017-05-29 | 18.8 | 0 | 0.8 | 2016-05-29 | 20.4 | 0 | 2.4 | 3.46 | 0.7
2025-05-29 | 15.5 | 2.5 | 0 | 2024-05-29 | 11.6 | 6.4 | 0 | 2023-05-29 | 15.5 | 2.5 | 0 | 2022-05-29 | 11.7 | 6.3 | 0 | 2021-05-29 | 4.2 | 13.8 | 0 | 2020-05-29 | 19.9 | 0 | 1.9 | 2019-05-29 | 7.8 | 10.2 | 0 | 2018-05-29 | 18.9 | 0 | 0.9 | 2017-05-29 | 17 | 1 | 0 | 2016-05-29 | 19.9 | 0 | 1.9 | 4.27 | 0.47
2025-05-29 | 14.9 | 3.1 | 0 | 2024-05-29 | 10.4 | 7.6 | 0 | 2023-05-29 | 13.2 | 4.8 | 0 | 2022-05-29 | 10.9 | 7.1 | 0 | 2021-05-29 | 3.7 | 14.3 | 0 | 2020-05-29 | 19.4 | 0 | 1.4 | 2019-05-29 | 8.1 | 9.9 | 0 | 2018-05-29 | 18.4 | 0 | 0.4 | 2017-05-29 | 17.2 | 0.8 | 0 | 2016-05-29 | 19.2 | 0 | 1.2 | 4.76 | 0.3
2025-05-29 | 14 | 4 | 0 | 2024-05-29 | 9.9 | 8.1 | 0 | 2023-05-29 | 14.2 | 3.8 | 0 | 2022-05-29 | 10 | 8 | 0 | 2021-05-29 | 3 | 15 | 0 | 2020-05-29 | 19 | 0 | 1 | 2019-05-29 | 9.1 | 8.9 | 0 | 2018-05-29 | 17.5 | 0.5 | 0 | 2017-05-29 | 17.2 | 0.8 | 0 | 2016-05-29 | 18.4 | 0 | 0.4 | 4.91 | 0.14
2025-05-29 | 14 | 4 | 0 | 2024-05-29 | 9.8 | 8.2 | 0 | 2023-05-29 | 13.6 | 4.4 | 0 | 2022-05-29 | 10 | 8 | 0 | 2021-05-29 | 5.2 | 12.8 | 0 | 2020-05-29 | 18.6 | 0 | 0.6 | 2019-05-29 | 9.5 | 8.5 | 0 | 2018-05-29 | 16.8 | 1.2 | 0 | 2017-05-29 | 16.9 | 1.1 | 0 | 2016-05-29 | 17.9 | 0.1 | 0 | 4.83 | 0.06
2025-05-29 | 14.1 | 3.9 | 0 | 2024-05-29 | 10.1 | 7.9 | 0 | 2023-05-29 | 14.8 | 3.2 | 0 | 2022-05-29 | 13 | 5 | 0 | 2021-05-29 | 7.7 | 10.3 | 0 | 2020-05-29 | 20.1 | 0 | 2.1 | 2019-05-29 | 10.3 | 7.7 | 0 | 2018-05-29 | 17.4 | 0.6 | 0 | 2017-05-29 | 15.1 | 2.9 | 0 | 2016-05-29 | 17.9 | 0.1 | 0 | 4.16 | 0.21
2025-05-29 | 14.1 | 3.9 | 0 | 2024-05-29 | 10.3 | 7.7 | 0 | 2023-05-29 | 16.1 | 1.9 | 0 | 2022-05-29 | 15.7 | 2.3 | 0 | 2021-05-29 | 10 | 8 | 0 | 2020-05-29 | 21.7 | 0 | 3.7 | 2019-05-29 | 10.7 | 7.3 | 0 | 2018-05-29 | 18.1 | 0 | 0.1 | 2017-05-29 | 14.8 | 3.2 | 0 | 2016-05-29 | 19.1 | 0 | 1.1 | 3.43 | 0.49
2025-05-29 | 13.6 | 4.4 | 0 | 2024-05-29 | 11 | 7 | 0 | 2023-05-29 | 17.4 | 0.6 | 0 | 2022-05-29 | 18.2 | 0 | 0.2 | 2021-05-29 | 12.2 | 5.8 | 0 | 2020-05-29 | 23.1 | 0 | 5.1 | 2019-05-29 | 11 | 7 | 0 | 2018-05-29 | 18.9 | 0 | 0.9 | 2017-05-29 | 15.1 | 2.9 | 0 | 2016-05-29 | 19.7 | 0 | 1.7 | 2.77 | 0.79
2025-05-29 | 13.7 | 4.3 | 0 | 2024-05-29 | 11.8 | 6.2 | 0 | 2023-05-29 | 18.9 | 0 | 0.9 | 2022-05-29 | 19.6 | 0 | 1.6 | 2021-05-29 | 14.3 | 3.7 | 0 | 2020-05-29 | 23.7 | 0 | 5.7 | 2019-05-29 | 11.9 | 6.1 | 0 | 2018-05-29 | 20.2 | 0 | 2.2 | 2017-05-29 | 14.3 | 3.7 | 0 | 2016-05-29 | 21 | 0 | 3 | 2.4 | 1.34
2025-05-29 | 14.3 | 3.7 | 0 | 2024-05-29 | 12.6 | 5.4 | 0 | 2023-05-29 | 20.4 | 0 | 2.4 | 2022-05-29 | 21.7 | 0 | 3.7 | 2021-05-29 | 15.2 | 2.8 | 0 | 2020-05-29 | 25.2 | 0 | 7.2 | 2019-05-29 | 13.2 | 4.8 | 0 | 2018-05-29 | 20.9 | 0 | 2.9 | 2017-05-29 | 14.2 | 3.8 | 0 | 2016-05-29 | 22.1 | 0 | 4.1 | 2.05 | 2.03
2025-05-29 | 15.3 | 2.7 | 0 | 2024-05-29 | 13.7 | 4.3 | 0 | 2023-05-29 | 21.4 | 0 | 3.4 | 2022-05-29 | 23.5 | 0 | 5.5 | 2021-05-29 | 16.2 | 1.8 | 0 | 2020-05-29 | 24.9 | 0 | 6.9 | 2019-05-29 | 13.9 | 4.1 | 0 | 2018-05-29 | 21.2 | 0 | 3.2 | 2017-05-29 | 13.5 | 4.5 | 0 | 2016-05-29 | 25.4 | 0 | 7.4 | 1.74 | 2.64
2025-05-29 | 15.8 | 2.2 | 0 | 2024-05-29 | 15.6 | 2.4 | 0 | 2023-05-29 | 22.1 | 0 | 4.1 | 2022-05-29 | 22.9 | 0 | 4.9 | 2021-05-29 | 17 | 1 | 0 | 2020-05-29 | 26.4 | 0 | 8.4 | 2019-05-29 | 15.1 | 2.9 | 0 | 2018-05-29 | 23.9 | 0 | 5.9 | 2017-05-29 | 13.3 | 4.7 | 0 | 2016-05-29 | 27.3 | 0 | 9.3 | 1.32 | 3.26
2025-05-29 | 16.5 | 1.5 | 0 | 2024-05-29 | 16.1 | 1.9 | 0 | 2023-05-29 | 23.1 | 0 | 5.1 | 2022-05-29 | 23.4 | 0 | 5.4 | 2021-05-29 | 17.7 | 0.3 | 0 | 2020-05-29 | 26.7 | 0 | 8.7 | 2019-05-29 | 16.4 | 1.6 | 0 | 2018-05-29 | 24.6 | 0 | 6.6 | 2017-05-29 | 13.9 | 4.1 | 0 | 2016-05-29 | 29 | 0 | 11 | 0.94 | 3.68
2025-05-29 | 16.4 | 1.6 | 0 | 2024-05-29 | 15.6 | 2.4 | 0 | 2023-05-29 | 23.6 | 0 | 5.6 | 2022-05-29 | 25.1 | 0 | 7.1 | 2021-05-29 | 18.4 | 0 | 0.4 | 2020-05-29 | 26.8 | 0 | 8.8 | 2019-05-29 | 17.3 | 0.7 | 0 | 2018-05-29 | 24.7 | 0 | 6.7 | 2017-05-29 | 14.3 | 3.7 | 0 | 2016-05-29 | 31.4 | 0 | 13.4 | 0.84 | 4.2
2025-05-29 | 17.5 | 0.5 | 0 | 2024-05-29 | 16.6 | 1.4 | 0 | 2023-05-29 | 23.9 | 0 | 5.9 | 2022-05-29 | 25.3 | 0 | 7.3 | 2021-05-29 | 18.5 | 0 | 0.5 | 2020-05-29 | 26.4 | 0 | 8.4 | 2019-05-29 | 18.3 | 0 | 0.3 | 2018-05-29 | 24.8 | 0 | 6.8 | 2017-05-29 | 14.9 | 3.1 | 0 | 2016-05-29 | 31.4 | 0 | 13.4 | 0.5 | 4.26
2025-05-29 | 16 | 2 | 0 | 2024-05-29 | 16.3 | 1.7 | 0 | 2023-05-29 | 23.7 | 0 | 5.7 | 2022-05-29 | 23.4 | 0 | 5.4 | 2021-05-29 | 18.3 | 0 | 0.3 | 2020-05-29 | 25.9 | 0 | 7.9 | 2019-05-29 | 18.5 | 0 | 0.5 | 2018-05-29 | 25.3 | 0 | 7.3 | 2017-05-29 | 15.4 | 2.6 | 0 | 2016-05-29 | 32.1 | 0 | 14.1 | 0.63 | 4.12
2025-05-29 | 16.7 | 1.3 | 0 | 2024-05-29 | 16.4 | 1.6 | 0 | 2023-05-29 | 23.4 | 0 | 5.4 | 2022-05-29 | 23.8 | 0 | 5.8 | 2021-05-29 | 18.2 | 0 | 0.2 | 2020-05-29 | 24.7 | 0 | 6.7 | 2019-05-29 | 18.4 | 0 | 0.4 | 2018-05-29 | 25.1 | 0 | 7.1 | 2017-05-29 | 16 | 2 | 0 | 2016-05-29 | 31.7 | 0 | 13.7 | 0.49 | 3.93
2025-05-29 | 16.8 | 1.2 | 0 | 2024-05-29 | 15.4 | 2.6 | 0 | 2023-05-29 | 22.3 | 0 | 4.3 | 2022-05-29 | 22.9 | 0 | 4.9 | 2021-05-29 | 17.6 | 0.4 | 0 | 2020-05-29 | 22.2 | 0 | 4.2 | 2019-05-29 | 18.4 | 0 | 0.4 | 2018-05-29 | 24.4 | 0 | 6.4 | 2017-05-29 | 16.5 | 1.5 | 0 | 2016-05-29 | 29.4 | 0 | 11.4 | 0.57 | 3.16
2025-05-29 | 15.8 | 2.2 | 0 | 2024-05-29 | 14.1 | 3.9 | 0 | 2023-05-29 | 20.3 | 0 | 2.3 | 2022-05-29 | 21.1 | 0 | 3.1 | 2021-05-29 | 16 | 2 | 0 | 2020-05-29 | 21.6 | 0 | 3.6 | 2019-05-29 | 17.1 | 0.9 | 0 | 2018-05-29 | 22.9 | 0 | 4.9 | 2017-05-29 | 16.5 | 1.5 | 0 | 2016-05-29 | 27.6 | 0 | 9.6 | 1.05 | 2.35
2025-05-29 | 15.6 | 2.4 | 0 | 2024-05-29 | 11.6 | 6.4 | 0 | 2023-05-29 | 17.5 | 0.5 | 0 | 2022-05-29 | 18.8 | 0 | 0.8 | 2021-05-29 | 12.6 | 5.4 | 0 | 2020-05-29 | 21 | 0 | 3 | 2019-05-29 | 15.9 | 2.1 | 0 | 2018-05-29 | 18.8 | 0 | 0.8 | 2017-05-29 | 16.3 | 1.7 | 0 | 2016-05-29 | 26.4 | 0 | 8.4 | 1.85 | 1.3
2025-05-29 | 15.5 | 2.5 | 0 | 2024-05-29 | 11 | 7 | 0 | 2023-05-29 | 15.5 | 2.5 | 0 | 2022-05-29 | 17.4 | 0.6 | 0 | 2021-05-29 | 9.9 | 8.1 | 0 | 2020-05-29 | 20.6 | 0 | 2.6 | 2019-05-29 | 14.1 | 3.9 | 0 | 2018-05-29 | 14.7 | 3.3 | 0 | 2017-05-29 | 15.4 | 2.6 | 0 | 2016-05-29 | 25 | 0 | 7 | 3.05 | 0.96
2025-05-29 | 15.2 | 2.8 | 0 | 2024-05-29 | 9.7 | 8.3 | 0 | 2023-05-29 | 13.7 | 4.3 | 0 | 2022-05-29 | 16.9 | 1.1 | 0 | 2021-05-29 | 9.2 | 8.8 | 0 | 2020-05-29 | 19.9 | 0 | 1.9 | 2019-05-29 | 13.7 | 4.3 | 0 | 2018-05-29 | 16.2 | 1.8 | 0 | 2017-05-29 | 14.4 | 3.6 | 0 | 2016-05-29 | 24 | 0 | 6 | 3.5 | 0.79
2025-05-29 | 14.9 | 3.1 | 0 | 2024-05-29 | 9.6 | 8.4 | 0 | 2023-05-29 | 12.2 | 5.8 | 0 | 2022-05-29 | 15.5 | 2.5 | 0 | 2021-05-29 | 9.6 | 8.4 | 0 | 2020-05-29 | 17.9 | 0.1 | 0 | 2019-05-29 | 12.9 | 5.1 | 0 | 2018-05-29 | 16.4 | 1.6 | 0 | 2017-05-29 | 13.7 | 4.3 | 0 | 2016-05-29 | 22.8 | 0 | 4.8 | 3.93 | 0.48
2025-05-30 | 14.5 | 3.5 | 0 | 2024-05-30 | 7.7 | 10.3 | 0 | 2023-05-30 | 10.8 | 7.2 | 0 | 2022-05-30 | 14.9 | 3.1 | 0 | 2021-05-30 | 5.8 | 12.2 | 0 | 2020-05-30 | 14.9 | 3.1 | 0 | 2019-05-30 | 12.1 | 5.9 | 0 | 2018-05-30 | 14.1 | 3.9 | 0 | 2017-05-30 | 12 | 6 | 0 | 2016-05-30 | 21.9 | 0 | 3.9 | 5.52 | 0.39
2025-05-30 | 14.2 | 3.8 | 0 | 2024-05-30 | 8.4 | 9.6 | 0 | 2023-05-30 | 10.4 | 7.6 | 0 | 2022-05-30 | 14.3 | 3.7 | 0 | 2021-05-30 | 5.9 | 12.1 | 0 | 2020-05-30 | 12.9 | 5.1 | 0 | 2019-05-30 | 11.3 | 6.7 | 0 | 2018-05-30 | 12.2 | 5.8 | 0 | 2017-05-30 | 13.4 | 4.6 | 0 | 2016-05-30 | 21.3 | 0 | 3.3 | 5.9 | 0.33
2025-05-30 | 13.8 | 4.2 | 0 | 2024-05-30 | 6.8 | 11.2 | 0 | 2023-05-30 | 9.8 | 8.2 | 0 | 2022-05-30 | 13.6 | 4.4 | 0 | 2021-05-30 | 4.7 | 13.3 | 0 | 2020-05-30 | 12.1 | 5.9 | 0 | 2019-05-30 | 10.6 | 7.4 | 0 | 2018-05-30 | 11.7 | 6.3 | 0 | 2017-05-30 | 13.9 | 4.1 | 0 | 2016-05-30 | 20.9 | 0 | 2.9 | 6.5 | 0.29
2025-05-30 | 13 | 5 | 0 | 2024-05-30 | 5.8 | 12.2 | 0 | 2023-05-30 | 8.3 | 9.7 | 0 | 2022-05-30 | 12.8 | 5.2 | 0 | 2021-05-30 | 3.9 | 14.1 | 0 | 2020-05-30 | 12.3 | 5.7 | 0 | 2019-05-30 | 9.6 | 8.4 | 0 | 2018-05-30 | 10.7 | 7.3 | 0 | 2017-05-30 | 14 | 4 | 0 | 2016-05-30 | 20.3 | 0 | 2.3 | 7.16 | 0.23
2025-05-30 | 13.2 | 4.8 | 0 | 2024-05-30 | 7.5 | 10.5 | 0 | 2023-05-30 | 8.3 | 9.7 | 0 | 2022-05-30 | 12.8 | 5.2 | 0 | 2021-05-30 | 3.3 | 14.7 | 0 | 2020-05-30 | 12.2 | 5.8 | 0 | 2019-05-30 | 9.3 | 8.7 | 0 | 2018-05-30 | 10.7 | 7.3 | 0 | 2017-05-30 | 13.2 | 4.8 | 0 | 2016-05-30 | 19.2 | 0 | 1.2 | 7.15 | 0.12
2025-05-30 | 13.2 | 4.8 | 0 | 2024-05-30 | 7.8 | 10.2 | 0 | 2023-05-30 | 9.3 | 8.7 | 0 | 2022-05-30 | 13.9 | 4.1 | 0 | 2021-05-30 | 4.5 | 13.5 | 0 | 2020-05-30 | 12.3 | 5.7 | 0 | 2019-05-30 | 9.3 | 8.7 | 0 | 2018-05-30 | 11.7 | 6.3 | 0 | 2017-05-30 | 13.2 | 4.8 | 0 | 2016-05-30 | 18.6 | 0 | 0.6 | 6.68 | 0.06
2025-05-30 | 13.5 | 4.5 | 0 | 2024-05-30 | 9.3 | 8.7 | 0 | 2023-05-30 | 12.8 | 5.2 | 0 | 2022-05-30 | 14.9 | 3.1 | 0 | 2021-05-30 | 8.5 | 9.5 | 0 | 2020-05-30 | 12.4 | 5.6 | 0 | 2019-05-30 | 9.8 | 8.2 | 0 | 2018-05-30 | 13.6 | 4.4 | 0 | 2017-05-30 | 13.3 | 4.7 | 0 | 2016-05-30 | 20.2 | 0 | 2.2 | 5.39 | 0.22
2025-05-30 | 14.5 | 3.5 | 0 | 2024-05-30 | 11 | 7 | 0 | 2023-05-30 | 14.9 | 3.1 | 0 | 2022-05-30 | 15.9 | 2.1 | 0 | 2021-05-30 | 11.2 | 6.8 | 0 | 2020-05-30 | 12.8 | 5.2 | 0 | 2019-05-30 | 11.4 | 6.6 | 0 | 2018-05-30 | 15.8 | 2.2 | 0 | 2017-05-30 | 15 | 3 | 0 | 2016-05-30 | 22.3 | 0 | 4.3 | 3.95 | 0.43
2025-05-30 | 15.1 | 2.9 | 0 | 2024-05-30 | 13 | 5 | 0 | 2023-05-30 | 17.9 | 0.1 | 0 | 2022-05-30 | 17.9 | 0.1 | 0 | 2021-05-30 | 13.3 | 4.7 | 0 | 2020-05-30 | 13.7 | 4.3 | 0 | 2019-05-30 | 14.9 | 3.1 | 0 | 2018-05-30 | 18.3 | 0 | 0.3 | 2017-05-30 | 17.2 | 0.8 | 0 | 2016-05-30 | 24 | 0 | 6 | 2.1 | 0.63
2025-05-30 | 16.2 | 1.8 | 0 | 2024-05-30 | 15 | 3 | 0 | 2023-05-30 | 20.4 | 0 | 2.4 | 2022-05-30 | 20.4 | 0 | 2.4 | 2021-05-30 | 15.3 | 2.7 | 0 | 2020-05-30 | 14.8 | 3.2 | 0 | 2019-05-30 | 17.1 | 0.9 | 0 | 2018-05-30 | 20.7 | 0 | 2.7 | 2017-05-30 | 17.5 | 0.5 | 0 | 2016-05-30 | 25.5 | 0 | 7.5 | 1.21 | 1.5
2025-05-30 | 18 | 0 | 0 | 2024-05-30 | 16.5 | 1.5 | 0 | 2023-05-30 | 21.2 | 0 | 3.2 | 2022-05-30 | 23 | 0 | 5 | 2021-05-30 | 16.5 | 1.5 | 0 | 2020-05-30 | 15.5 | 2.5 | 0 | 2019-05-30 | 18.8 | 0 | 0.8 | 2018-05-30 | 22.9 | 0 | 4.9 | 2017-05-30 | 17.9 | 0.1 | 0 | 2016-05-30 | 27 | 0 | 9 | 0.56 | 2.29
2025-05-30 | 17.9 | 0.1 | 0 | 2024-05-30 | 17.6 | 0.4 | 0 | 2023-05-30 | 22.9 | 0 | 4.9 | 2022-05-30 | 25.6 | 0 | 7.6 | 2021-05-30 | 18.8 | 0 | 0.8 | 2020-05-30 | 16.9 | 1.1 | 0 | 2019-05-30 | 17.8 | 0.2 | 0 | 2018-05-30 | 24.6 | 0 | 6.6 | 2017-05-30 | 17.4 | 0.6 | 0 | 2016-05-30 | 27.5 | 0 | 9.5 | 0.24 | 2.94
2025-05-30 | 19.5 | 0 | 1.5 | 2024-05-30 | 18.2 | 0 | 0.2 | 2023-05-30 | 24.4 | 0 | 6.4 | 2022-05-30 | 27.7 | 0 | 9.7 | 2021-05-30 | 19 | 0 | 1 | 2020-05-30 | 17.7 | 0.3 | 0 | 2019-05-30 | 19.2 | 0 | 1.2 | 2018-05-30 | 26.1 | 0 | 8.1 | 2017-05-30 | 17.1 | 0.9 | 0 | 2016-05-30 | 27.4 | 0 | 9.4 | 0.12 | 3.75
2025-05-30 | 19.9 | 0 | 1.9 | 2024-05-30 | 18.7 | 0 | 0.7 | 2023-05-30 | 25 | 0 | 7 | 2022-05-30 | 28.4 | 0 | 10.4 | 2021-05-30 | 19 | 0 | 1 | 2020-05-30 | 20.1 | 0 | 2.1 | 2019-05-30 | 20.8 | 0 | 2.8 | 2018-05-30 | 28 | 0 | 10 | 2017-05-30 | 20.2 | 0 | 2.2 | 2016-05-30 | 27.5 | 0 | 9.5 | 0 | 4.76
2025-05-30 | 21.1 | 0 | 3.1 | 2024-05-30 | 19.7 | 0 | 1.7 | 2023-05-30 | 26.4 | 0 | 8.4 | 2022-05-30 | 28.3 | 0 | 10.3 | 2021-05-30 | 20 | 0 | 2 | 2020-05-30 | 19.9 | 0 | 1.9 | 2019-05-30 | 21.2 | 0 | 3.2 | 2018-05-30 | 28.1 | 0 | 10.1 | 2017-05-30 | 21.3 | 0 | 3.3 | 2016-05-30 | 28.2 | 0 | 10.2 | 0 | 5.42
2025-05-30 | 21.9 | 0 | 3.9 | 2024-05-30 | 19.4 | 0 | 1.4 | 2023-05-30 | 27.3 | 0 | 9.3 | 2022-05-30 | 27.9 | 0 | 9.9 | 2021-05-30 | 19.9 | 0 | 1.9 | 2020-05-30 | 17.4 | 0.6 | 0 | 2019-05-30 | 20.5 | 0 | 2.5 | 2018-05-30 | 28.9 | 0 | 10.9 | 2017-05-30 | 22.1 | 0 | 4.1 | 2016-05-30 | 29.4 | 0 | 11.4 | 0.06 | 5.53
2025-05-30 | 22.3 | 0 | 4.3 | 2024-05-30 | 20 | 0 | 2 | 2023-05-30 | 27.4 | 0 | 9.4 | 2022-05-30 | 26.5 | 0 | 8.5 | 2021-05-30 | 19.4 | 0 | 1.4 | 2020-05-30 | 15.2 | 2.8 | 0 | 2019-05-30 | 19.9 | 0 | 1.9 | 2018-05-30 | 28.3 | 0 | 10.3 | 2017-05-30 | 22.8 | 0 | 4.8 | 2016-05-30 | 27.7 | 0 | 9.7 | 0.28 | 5.23
2025-05-30 | 21.2 | 0 | 3.2 | 2024-05-30 | 19.6 | 0 | 1.6 | 2023-05-30 | 27.2 | 0 | 9.2 | 2022-05-30 | 25.9 | 0 | 7.9 | 2021-05-30 | 18.1 | 0 | 0.1 | 2020-05-30 | 13.5 | 4.5 | 0 | 2019-05-30 | 19.8 | 0 | 1.8 | 2018-05-30 | 28.9 | 0 | 10.9 | 2017-05-30 | 17.1 | 0.9 | 0 | 2016-05-30 | 27.9 | 0 | 9.9 | 0.54 | 4.46
2025-05-30 | 14.3 | 3.7 | 0 | 2024-05-30 | 18.9 | 0 | 0.9 | 2023-05-30 | 26.3 | 0 | 8.3 | 2022-05-30 | 26.4 | 0 | 8.4 | 2021-05-30 | 16.9 | 1.1 | 0 | 2020-05-30 | 10.9 | 7.1 | 0 | 2019-05-30 | 19.6 | 0 | 1.6 | 2018-05-30 | 28.5 | 0 | 10.5 | 2017-05-30 | 16 | 2 | 0 | 2016-05-30 | 26.7 | 0 | 8.7 | 1.39 | 3.84
2025-05-30 | 13.9 | 4.1 | 0 | 2024-05-30 | 16.6 | 1.4 | 0 | 2023-05-30 | 24.7 | 0 | 6.7 | 2022-05-30 | 25.7 | 0 | 7.7 | 2021-05-30 | 14.8 | 3.2 | 0 | 2020-05-30 | 9.9 | 8.1 | 0 | 2019-05-30 | 18.8 | 0 | 0.8 | 2018-05-30 | 26.4 | 0 | 8.4 | 2017-05-30 | 15.2 | 2.8 | 0 | 2016-05-30 | 25.1 | 0 | 7.1 | 1.96 | 3.07
2025-05-30 | 13.9 | 4.1 | 0 | 2024-05-30 | 15.5 | 2.5 | 0 | 2023-05-30 | 20.9 | 0 | 2.9 | 2022-05-30 | 24.7 | 0 | 6.7 | 2021-05-30 | 13.2 | 4.8 | 0 | 2020-05-30 | 8.7 | 9.3 | 0 | 2019-05-30 | 17 | 1 | 0 | 2018-05-30 | 24.4 | 0 | 6.4 | 2017-05-30 | 13.6 | 4.4 | 0 | 2016-05-30 | 22.9 | 0 | 4.9 | 2.61 | 2.09
2025-05-30 | 13.7 | 4.3 | 0 | 2024-05-30 | 14.7 | 3.3 | 0 | 2023-05-30 | 20.9 | 0 | 2.9 | 2022-05-30 | 23.6 | 0 | 5.6 | 2021-05-30 | 11.1 | 6.9 | 0 | 2020-05-30 | 8.4 | 9.6 | 0 | 2019-05-30 | 15.3 | 2.7 | 0 | 2018-05-30 | 21.9 | 0 | 3.9 | 2017-05-30 | 13.2 | 4.8 | 0 | 2016-05-30 | 21.7 | 0 | 3.7 | 3.16 | 1.61
2025-05-30 | 14.3 | 3.7 | 0 | 2024-05-30 | 10.9 | 7.1 | 0 | 2023-05-30 | 19.3 | 0 | 1.3 | 2022-05-30 | 22.8 | 0 | 4.8 | 2021-05-30 | 8.5 | 9.5 | 0 | 2020-05-30 | 7.6 | 10.4 | 0 | 2019-05-30 | 14.6 | 3.4 | 0 | 2018-05-30 | 21.8 | 0 | 3.8 | 2017-05-30 | 13.1 | 4.9 | 0 | 2016-05-30 | 19.6 | 0 | 1.6 | 3.9 | 1.15
2025-05-30 | 14.1 | 3.9 | 0 | 2024-05-30 | 10.3 | 7.7 | 0 | 2023-05-30 | 19 | 0 | 1 | 2022-05-30 | 22.1 | 0 | 4.1 | 2021-05-30 | 7.5 | 10.5 | 0 | 2020-05-30 | 6.2 | 11.8 | 0 | 2019-05-30 | 13.5 | 4.5 | 0 | 2018-05-30 | 22.4 | 0 | 4.4 | 2017-05-30 | 11.8 | 6.2 | 0 | 2016-05-30 | 18.2 | 0 | 0.2 | 4.46 | 0.97
2025-05-31 | 13.7 | 4.3 | 0 | 2024-05-31 | 11.1 | 6.9 | 0 | 2023-05-31 | 15.8 | 2.2 | 0 | 2022-05-31 | 21.3 | 0 | 3.3 | 2021-05-31 | 7.9 | 10.1 | 0 | 2020-05-31 | 5.7 | 12.3 | 0 | 2019-05-31 | 12.2 | 5.8 | 0 | 2018-05-31 | 22.5 | 0 | 4.5 | 2017-05-31 | 11.6 | 6.4 | 0 | 2016-05-31 | 16.9 | 1.1 | 0 | 4.91 | 0.78
2025-05-31 | 13.3 | 4.7 | 0 | 2024-05-31 | 9.2 | 8.8 | 0 | 2023-05-31 | 15.4 | 2.6 | 0 | 2022-05-31 | 20.7 | 0 | 2.7 | 2021-05-31 | 5.2 | 12.8 | 0 | 2020-05-31 | 5.1 | 12.9 | 0 | 2019-05-31 | 10.4 | 7.6 | 0 | 2018-05-31 | 21.2 | 0 | 3.2 | 2017-05-31 | 11.8 | 6.2 | 0 | 2016-05-31 | 15.8 | 2.2 | 0 | 5.78 | 0.59
2025-05-31 | 13.5 | 4.5 | 0 | 2024-05-31 | 9.1 | 8.9 | 0 | 2023-05-31 | 14.9 | 3.1 | 0 | 2022-05-31 | 20.2 | 0 | 2.2 | 2021-05-31 | 7.4 | 10.6 | 0 | 2020-05-31 | 4.7 | 13.3 | 0 | 2019-05-31 | 8.3 | 9.7 | 0 | 2018-05-31 | 20.8 | 0 | 2.8 | 2017-05-31 | 12.1 | 5.9 | 0 | 2016-05-31 | 14.4 | 3.6 | 0 | 5.96 | 0.5
2025-05-31 | 12.8 | 5.2 | 0 | 2024-05-31 | 8.6 | 9.4 | 0 | 2023-05-31 | 11.9 | 6.1 | 0 | 2022-05-31 | 18.9 | 0 | 0.9 | 2021-05-31 | 5.9 | 12.1 | 0 | 2020-05-31 | 4 | 14 | 0 | 2019-05-31 | 8.4 | 9.6 | 0 | 2018-05-31 | 19.9 | 0 | 1.9 | 2017-05-31 | 13.8 | 4.2 | 0 | 2016-05-31 | 14.1 | 3.9 | 0 | 6.45 | 0.28
2025-05-31 | 12.3 | 5.7 | 0 | 2024-05-31 | 7.4 | 10.6 | 0 | 2023-05-31 | 12.2 | 5.8 | 0 | 2022-05-31 | 18.6 | 0 | 0.6 | 2021-05-31 | 6.1 | 11.9 | 0 | 2020-05-31 | 4 | 14 | 0 | 2019-05-31 | 6 | 12 | 0 | 2018-05-31 | 19.5 | 0 | 1.5 | 2017-05-31 | 12.9 | 5.1 | 0 | 2016-05-31 | 13.1 | 4.9 | 0 | 7 | 0.21
2025-05-31 | 10.9 | 7.1 | 0 | 2024-05-31 | 8 | 10 | 0 | 2023-05-31 | 13.2 | 4.8 | 0 | 2022-05-31 | 18.1 | 0 | 0.1 | 2021-05-31 | 6.5 | 11.5 | 0 | 2020-05-31 | 4 | 14 | 0 | 2019-05-31 | 8 | 10 | 0 | 2018-05-31 | 19.8 | 0 | 1.8 | 2017-05-31 | 12.7 | 5.3 | 0 | 2016-05-31 | 13.4 | 4.6 | 0 | 6.73 | 0.19
2025-05-31 | 10.1 | 7.9 | 0 | 2024-05-31 | 10.5 | 7.5 | 0 | 2023-05-31 | 15.6 | 2.4 | 0 | 2022-05-31 | 19.7 | 0 | 1.7 | 2021-05-31 | 10.2 | 7.8 | 0 | 2020-05-31 | 5.9 | 12.1 | 0 | 2019-05-31 | 7.9 | 10.1 | 0 | 2018-05-31 | 21.1 | 0 | 3.1 | 2017-05-31 | 13.1 | 4.9 | 0 | 2016-05-31 | 15.4 | 2.6 | 0 | 5.53 | 0.48
2025-05-31 | 9.3 | 8.7 | 0 | 2024-05-31 | 12.7 | 5.3 | 0 | 2023-05-31 | 19.1 | 0 | 1.1 | 2022-05-31 | 22.5 | 0 | 4.5 | 2021-05-31 | 12.6 | 5.4 | 0 | 2020-05-31 | 6.7 | 11.3 | 0 | 2019-05-31 | 9.6 | 8.4 | 0 | 2018-05-31 | 22.8 | 0 | 4.8 | 2017-05-31 | 15 | 3 | 0 | 2016-05-31 | 18.6 | 0 | 0.6 | 4.21 | 1.1
2025-05-31 | 8.7 | 9.3 | 0 | 2024-05-31 | 15.5 | 2.5 | 0 | 2023-05-31 | 22.4 | 0 | 4.4 | 2022-05-31 | 23.1 | 0 | 5.1 | 2021-05-31 | 14.2 | 3.8 | 0 | 2020-05-31 | 8.2 | 9.8 | 0 | 2019-05-31 | 10.6 | 7.4 | 0 | 2018-05-31 | 22.4 | 0 | 4.4 | 2017-05-31 | 16.7 | 1.3 | 0 | 2016-05-31 | 20 | 0 | 2 | 3.41 | 1.59
2025-05-31 | 7.8 | 10.2 | 0 | 2024-05-31 | 17.4 | 0.6 | 0 | 2023-05-31 | 24.7 | 0 | 6.7 | 2022-05-31 | 21.3 | 0 | 3.3 | 2021-05-31 | 16.2 | 1.8 | 0 | 2020-05-31 | 9.9 | 8.1 | 0 | 2019-05-31 | 11.7 | 6.3 | 0 | 2018-05-31 | 23.6 | 0 | 5.6 | 2017-05-31 | 18.6 | 0 | 0.6 | 2016-05-31 | 21.4 | 0 | 3.4 | 2.7 | 1.96
2025-05-31 | 7.9 | 10.1 | 0 | 2024-05-31 | 19.5 | 0 | 1.5 | 2023-05-31 | 27.1 | 0 | 9.1 | 2022-05-31 | 20.9 | 0 | 2.9 | 2021-05-31 | 17.2 | 0.8 | 0 | 2020-05-31 | 9.8 | 8.2 | 0 | 2019-05-31 | 13 | 5 | 0 | 2018-05-31 | 25.3 | 0 | 7.3 | 2017-05-31 | 18.8 | 0 | 0.8 | 2016-05-31 | 22.5 | 0 | 4.5 | 2.41 | 2.61
2025-05-31 | 7.8 | 10.2 | 0 | 2024-05-31 | 21.4 | 0 | 3.4 | 2023-05-31 | 28 | 0 | 10 | 2022-05-31 | 21.1 | 0 | 3.1 | 2021-05-31 | 19 | 0 | 1 | 2020-05-31 | 9.9 | 8.1 | 0 | 2019-05-31 | 13.6 | 4.4 | 0 | 2018-05-31 | 25.3 | 0 | 7.3 | 2017-05-31 | 19.5 | 0 | 1.5 | 2016-05-31 | 22.9 | 0 | 4.9 | 2.27 | 3.12
2025-05-31 | 8.2 | 9.8 | 0 | 2024-05-31 | 22.1 | 0 | 4.1 | 2023-05-31 | 30.2 | 0 | 12.2 | 2022-05-31 | 21.5 | 0 | 3.5 | 2021-05-31 | 21.1 | 0 | 3.1 | 2020-05-31 | 11.1 | 6.9 | 0 | 2019-05-31 | 14 | 4 | 0 | 2018-05-31 | 24.2 | 0 | 6.2 | 2017-05-31 | 20.6 | 0 | 2.6 | 2016-05-31 | 23 | 0 | 5 | 2.07 | 3.67
2025-05-31 | 8.3 | 9.7 | 0 | 2024-05-31 | 22.8 | 0 | 4.8 | 2023-05-31 | 30.7 | 0 | 12.7 | 2022-05-31 | 21.9 | 0 | 3.9 | 2021-05-31 | 22.9 | 0 | 4.9 | 2020-05-31 | 11.5 | 6.5 | 0 | 2019-05-31 | 13.5 | 4.5 | 0 | 2018-05-31 | 22.9 | 0 | 4.9 | 2017-05-31 | 19.8 | 0 | 1.8 | 2016-05-31 | 23.4 | 0 | 5.4 | 2.07 | 3.84
2025-05-31 | 9.5 | 8.5 | 0 | 2024-05-31 | 23.6 | 0 | 5.6 | 2023-05-31 | 31.3 | 0 | 13.3 | 2022-05-31 | 22.3 | 0 | 4.3 | 2021-05-31 | 22.5 | 0 | 4.5 | 2020-05-31 | 12.8 | 5.2 | 0 | 2019-05-31 | 15 | 3 | 0 | 2018-05-31 | 23.6 | 0 | 5.6 | 2017-05-31 | 21.3 | 0 | 3.3 | 2016-05-31 | 22.9 | 0 | 4.9 | 1.67 | 4.15
2025-05-31 | 10.3 | 7.7 | 0 | 2024-05-31 | 22.5 | 0 | 4.5 | 2023-05-31 | 32 | 0 | 14 | 2022-05-31 | 23.2 | 0 | 5.2 | 2021-05-31 | 23.2 | 0 | 5.2 | 2020-05-31 | 11.9 | 6.1 | 0 | 2019-05-31 | 14.5 | 3.5 | 0 | 2018-05-31 | 22.7 | 0 | 4.7 | 2017-05-31 | 21.2 | 0 | 3.2 | 2016-05-31 | 21.5 | 0 | 3.5 | 1.73 | 4.03
2025-05-31 | 11.9 | 6.1 | 0 | 2024-05-31 | 24.6 | 0 | 6.6 | 2023-05-31 | 31.8 | 0 | 13.8 | 2022-05-31 | 22.1 | 0 | 4.1 | 2021-05-31 | 23.5 | 0 | 5.5 | 2020-05-31 | 11.4 | 6.6 | 0 | 2019-05-31 | 14.2 | 3.8 | 0 | 2018-05-31 | 25.1 | 0 | 7.1 | 2017-05-31 | 15 | 3 | 0 | 2016-05-31 | 20.7 | 0 | 2.7 | 1.95 | 3.98
2025-05-31 | 13.4 | 4.6 | 0 | 2024-05-31 | 25 | 0 | 7 | 2023-05-31 | 31.9 | 0 | 13.9 | 2022-05-31 | 20.9 | 0 | 2.9 | 2021-05-31 | 23.2 | 0 | 5.2 | 2020-05-31 | 11 | 7 | 0 | 2019-05-31 | 14.3 | 3.7 | 0 | 2018-05-31 | 24.9 | 0 | 6.9 | 2017-05-31 | 14.6 | 3.4 | 0 | 2016-05-31 | 19.6 | 0 | 1.6 | 1.87 | 3.75
2025-05-31 | 14.4 | 3.6 | 0 | 2024-05-31 | 23.9 | 0 | 5.9 | 2023-05-31 | 30.5 | 0 | 12.5 | 2022-05-31 | 19.7 | 0 | 1.7 | 2021-05-31 | 22.7 | 0 | 4.7 | 2020-05-31 | 11.1 | 6.9 | 0 | 2019-05-31 | 13.6 | 4.4 | 0 | 2018-05-31 | 25 | 0 | 7 | 2017-05-31 | 16.4 | 1.6 | 0 | 2016-05-31 | 16.3 | 1.7 | 0 | 1.82 | 3.18
2025-05-31 | 13.5 | 4.5 | 0 | 2024-05-31 | 21.6 | 0 | 3.6 | 2023-05-31 | 27.7 | 0 | 9.7 | 2022-05-31 | 18.3 | 0 | 0.3 | 2021-05-31 | 21.2 | 0 | 3.2 | 2020-05-31 | 10.3 | 7.7 | 0 | 2019-05-31 | 12.7 | 5.3 | 0 | 2018-05-31 | 24.6 | 0 | 6.6 | 2017-05-31 | 14.7 | 3.3 | 0 | 2016-05-31 | 15.2 | 2.8 | 0 | 2.36 | 2.34
2025-05-31 | 12.3 | 5.7 | 0 | 2024-05-31 | 19.2 | 0 | 1.2 | 2023-05-31 | 25.3 | 0 | 7.3 | 2022-05-31 | 17.2 | 0.8 | 0 | 2021-05-31 | 18.2 | 0 | 0.2 | 2020-05-31 | 7.9 | 10.1 | 0 | 2019-05-31 | 12.4 | 5.6 | 0 | 2018-05-31 | 23.5 | 0 | 5.5 | 2017-05-31 | 15 | 3 | 0 | 2016-05-31 | 13.9 | 4.1 | 0 | 2.93 | 1.42
2025-05-31 | 10.9 | 7.1 | 0 | 2024-05-31 | 17 | 1 | 0 | 2023-05-31 | 24.3 | 0 | 6.3 | 2022-05-31 | 16.1 | 1.9 | 0 | 2021-05-31 | 15.5 | 2.5 | 0 | 2020-05-31 | 6.3 | 11.7 | 0 | 2019-05-31 | 10.4 | 7.6 | 0 | 2018-05-31 | 22.5 | 0 | 4.5 | 2017-05-31 | 13.9 | 4.1 | 0 | 2016-05-31 | 12.7 | 5.3 | 0 | 4.12 | 1.08
2025-05-31 | 10.2 | 7.8 | 0 | 2024-05-31 | 15.1 | 2.9 | 0 | 2023-05-31 | 22.8 | 0 | 4.8 | 2022-05-31 | 15.2 | 2.8 | 0 | 2021-05-31 | 13.5 | 4.5 | 0 | 2020-05-31 | 5 | 13 | 0 | 2019-05-31 | 11.1 | 6.9 | 0 | 2018-05-31 | 21.8 | 0 | 3.8 | 2017-05-31 | 13.6 | 4.4 | 0 | 2016-05-31 | 11.7 | 6.3 | 0 | 4.86 | 0.86
2025-05-31 | 9.2 | 8.8 | 0 | 2024-05-31 | 14.7 | 3.3 | 0 | 2023-05-31 | 21.5 | 0 | 3.5 | 2022-05-31 | 14.6 | 3.4 | 0 | 2021-05-31 | 13.4 | 4.6 | 0 | 2020-05-31 | 5.4 | 12.6 | 0 | 2019-05-31 | 9.9 | 8.1 | 0 | 2018-05-31 | 20.7 | 0 | 2.7 | 2017-05-31 | 13.7 | 4.3 | 0 | 2016-05-31 | 11.2 | 6.8 | 0 | 5.19 | 0.62
2025-06-01 | 9.1 | 8.9 | 0 | 2024-06-01 | 16.3 | 1.7 | 0 | 2023-06-01 | 19.4 | 0 | 1.4 | 2022-06-01 | 14.3 | 3.7 | 0 | 2021-06-01 | 10.8 | 7.2 | 0 | 2020-06-01 | 5.9 | 12.1 | 0 | 2019-06-01 | 9.9 | 8.1 | 0 | 2018-06-01 | 21.1 | 0 | 3.1 | 2017-06-01 | 13.8 | 4.2 | 0 | 2016-06-01 | 11.8 | 6.2 | 0 | 5.21 | 0.45
2025-06-01 | 8.5 | 9.5 | 0 | 2024-06-01 | 15.3 | 2.7 | 0 | 2023-06-01 | 18.5 | 0 | 0.5 | 2022-06-01 | 14.2 | 3.8 | 0 | 2021-06-01 | 11.5 | 6.5 | 0 | 2020-06-01 | 5.4 | 12.6 | 0 | 2019-06-01 | 10.1 | 7.9 | 0 | 2018-06-01 | 21.1 | 0 | 3.1 | 2017-06-01 | 13.4 | 4.6 | 0 | 2016-06-01 | 11.9 | 6.1 | 0 | 5.37 | 0.36
2025-06-01 | 7.5 | 10.5 | 0 | 2024-06-01 | 14.9 | 3.1 | 0 | 2023-06-01 | 18.5 | 0 | 0.5 | 2022-06-01 | 14.2 | 3.8 | 0 | 2021-06-01 | 12.1 | 5.9 | 0 | 2020-06-01 | 3.7 | 14.3 | 0 | 2019-06-01 | 10.5 | 7.5 | 0 | 2018-06-01 | 20.9 | 0 | 2.9 | 2017-06-01 | 13 | 5 | 0 | 2016-06-01 | 12 | 6 | 0 | 5.61 | 0.34
2025-06-01 | 6.5 | 11.5 | 0 | 2024-06-01 | 13.8 | 4.2 | 0 | 2023-06-01 | 17.1 | 0.9 | 0 | 2022-06-01 | 14.4 | 3.6 | 0 | 2021-06-01 | 12.8 | 5.2 | 0 | 2020-06-01 | 4.4 | 13.6 | 0 | 2019-06-01 | 9.4 | 8.6 | 0 | 2018-06-01 | 20.2 | 0 | 2.2 | 2017-06-01 | 12.4 | 5.6 | 0 | 2016-06-01 | 11.7 | 6.3 | 0 | 5.95 | 0.22
2025-06-01 | 6.9 | 11.1 | 0 | 2024-06-01 | 12.3 | 5.7 | 0 | 2023-06-01 | 15.5 | 2.5 | 0 | 2022-06-01 | 13.1 | 4.9 | 0 | 2021-06-01 | 13.8 | 4.2 | 0 | 2020-06-01 | 2.6 | 15.4 | 0 | 2019-06-01 | 9.1 | 8.9 | 0 | 2018-06-01 | 20.1 | 0 | 2.1 | 2017-06-01 | 11.6 | 6.4 | 0 | 2016-06-01 | 10.6 | 7.4 | 0 | 6.65 | 0.21
2025-06-01 | 6.8 | 11.2 | 0 | 2024-06-01 | 10.8 | 7.2 | 0 | 2023-06-01 | 15.9 | 2.1 | 0 | 2022-06-01 | 13.1 | 4.9 | 0 | 2021-06-01 | 13.3 | 4.7 | 0 | 2020-06-01 | 3.8 | 14.2 | 0 | 2019-06-01 | 9.4 | 8.6 | 0 | 2018-06-01 | 20.4 | 0 | 2.4 | 2017-06-01 | 11.3 | 6.7 | 0 | 2016-06-01 | 10.7 | 7.3 | 0 | 6.69 | 0.24
2025-06-01 | 7.7 | 10.3 | 0 | 2024-06-01 | 14.7 | 3.3 | 0 | 2023-06-01 | 19 | 0 | 1 | 2022-06-01 | 13.3 | 4.7 | 0 | 2021-06-01 | 14 | 4 | 0 | 2020-06-01 | 5.1 | 12.9 | 0 | 2019-06-01 | 10.4 | 7.6 | 0 | 2018-06-01 | 21.1 | 0 | 3.1 | 2017-06-01 | 11.8 | 6.2 | 0 | 2016-06-01 | 12.4 | 5.6 | 0 | 5.46 | 0.41
2025-06-01 | 8.2 | 9.8 | 0 | 2024-06-01 | 16.9 | 1.1 | 0 | 2023-06-01 | 22.1 | 0 | 4.1 | 2022-06-01 | 12.8 | 5.2 | 0 | 2021-06-01 | 14.6 | 3.4 | 0 | 2020-06-01 | 7.6 | 10.4 | 0 | 2019-06-01 | 11.4 | 6.6 | 0 | 2018-06-01 | 22.5 | 0 | 4.5 | 2017-06-01 | 12.3 | 5.7 | 0 | 2016-06-01 | 14.3 | 3.7 | 0 | 4.59 | 0.86
2025-06-01 | 7.4 | 10.6 | 0 | 2024-06-01 | 18.9 | 0 | 0.9 | 2023-06-01 | 24.8 | 0 | 6.8 | 2022-06-01 | 12.9 | 5.1 | 0 | 2021-06-01 | 17.2 | 0.8 | 0 | 2020-06-01 | 9.4 | 8.6 | 0 | 2019-06-01 | 11.8 | 6.2 | 0 | 2018-06-01 | 23.5 | 0 | 5.5 | 2017-06-01 | 13 | 5 | 0 | 2016-06-01 | 16.6 | 1.4 | 0 | 3.77 | 1.32
2025-06-01 | 7.8 | 10.2 | 0 | 2024-06-01 | 20.6 | 0 | 2.6 | 2023-06-01 | 28.4 | 0 | 10.4 | 2022-06-01 | 13.2 | 4.8 | 0 | 2021-06-01 | 19.6 | 0 | 1.6 | 2020-06-01 | 11.1 | 6.9 | 0 | 2019-06-01 | 11.9 | 6.1 | 0 | 2018-06-01 | 24.5 | 0 | 6.5 | 2017-06-01 | 13.7 | 4.3 | 0 | 2016-06-01 | 17.9 | 0.1 | 0 | 3.24 | 2.11
2025-06-01 | 9 | 9 | 0 | 2024-06-01 | 22.2 | 0 | 4.2 | 2023-06-01 | 29.8 | 0 | 11.8 | 2022-06-01 | 14 | 4 | 0 | 2021-06-01 | 21.2 | 0 | 3.2 | 2020-06-01 | 11.8 | 6.2 | 0 | 2019-06-01 | 13.7 | 4.3 | 0 | 2018-06-01 | 26.1 | 0 | 8.1 | 2017-06-01 | 14.8 | 3.2 | 0 | 2016-06-01 | 19.7 | 0 | 1.7 | 2.67 | 2.9
2025-06-01 | 9.9 | 8.1 | 0 | 2024-06-01 | 24.3 | 0 | 6.3 | 2023-06-01 | 31.2 | 0 | 13.2 | 2022-06-01 | 16.8 | 1.2 | 0 | 2021-06-01 | 23 | 0 | 5 | 2020-06-01 | 10.7 | 7.3 | 0 | 2019-06-01 | 15.1 | 2.9 | 0 | 2018-06-01 | 27 | 0 | 9 | 2017-06-01 | 14.7 | 3.3 | 0 | 2016-06-01 | 20.6 | 0 | 2.6 | 2.28 | 3.61
2025-06-01 | 11.1 | 6.9 | 0 | 2024-06-01 | 25.8 | 0 | 7.8 | 2023-06-01 | 32 | 0 | 14 | 2022-06-01 | 18.5 | 0 | 0.5 | 2021-06-01 | 22.5 | 0 | 4.5 | 2020-06-01 | 11.5 | 6.5 | 0 | 2019-06-01 | 16.2 | 1.8 | 0 | 2018-06-01 | 26.9 | 0 | 8.9 | 2017-06-01 | 15.3 | 2.7 | 0 | 2016-06-01 | 22.3 | 0 | 4.3 | 1.79 | 4
2025-06-01 | 12.9 | 5.1 | 0 | 2024-06-01 | 26.1 | 0 | 8.1 | 2023-06-01 | 33.4 | 0 | 15.4 | 2022-06-01 | 18.4 | 0 | 0.4 | 2021-06-01 | 23.4 | 0 | 5.4 | 2020-06-01 | 14 | 4 | 0 | 2019-06-01 | 17.2 | 0.8 | 0 | 2018-06-01 | 26.9 | 0 | 8.9 | 2017-06-01 | 15 | 3 | 0 | 2016-06-01 | 22.9 | 0 | 4.9 | 1.29 | 4.31
2025-06-01 | 12.2 | 5.8 | 0 | 2024-06-01 | 26.3 | 0 | 8.3 | 2023-06-01 | 33.4 | 0 | 15.4 | 2022-06-01 | 17.6 | 0.4 | 0 | 2021-06-01 | 18.1 | 0 | 0.1 | 2020-06-01 | 15.3 | 2.7 | 0 | 2019-06-01 | 17.9 | 0.1 | 0 | 2018-06-01 | 24.6 | 0 | 6.6 | 2017-06-01 | 15 | 3 | 0 | 2016-06-01 | 24.8 | 0 | 6.8 | 1.2 | 3.72
2025-06-01 | 11.6 | 6.4 | 0 | 2024-06-01 | 26.5 | 0 | 8.5 | 2023-06-01 | 34.1 | 0 | 16.1 | 2022-06-01 | 16.9 | 1.1 | 0 | 2021-06-01 | 23.6 | 0 | 5.6 | 2020-06-01 | 16.4 | 1.6 | 0 | 2019-06-01 | 18 | 0 | 0 | 2018-06-01 | 24.7 | 0 | 6.7 | 2017-06-01 | 15.4 | 2.6 | 0 | 2016-06-01 | 23.5 | 0 | 5.5 | 1.17 | 4.24
2025-06-01 | 11 | 7 | 0 | 2024-06-01 | 26.9 | 0 | 8.9 | 2023-06-01 | 33.9 | 0 | 15.9 | 2022-06-01 | 16.5 | 1.5 | 0 | 2021-06-01 | 23.9 | 0 | 5.9 | 2020-06-01 | 17.3 | 0.7 | 0 | 2019-06-01 | 18.2 | 0 | 0.2 | 2018-06-01 | 25.9 | 0 | 7.9 | 2017-06-01 | 15.1 | 2.9 | 0 | 2016-06-01 | 24.8 | 0 | 6.8 | 1.21 | 4.56
2025-06-01 | 10.2 | 7.8 | 0 | 2024-06-01 | 25.5 | 0 | 7.5 | 2023-06-01 | 33.1 | 0 | 15.1 | 2022-06-01 | 16.5 | 1.5 | 0 | 2021-06-01 | 23.3 | 0 | 5.3 | 2020-06-01 | 17.2 | 0.8 | 0 | 2019-06-01 | 18 | 0 | 0 | 2018-06-01 | 26.1 | 0 | 8.1 | 2017-06-01 | 14.6 | 3.4 | 0 | 2016-06-01 | 23.4 | 0 | 5.4 | 1.35 | 4.14
2025-06-01 | 9.5 | 8.5 | 0 | 2024-06-01 | 25.2 | 0 | 7.2 | 2023-06-01 | 32.2 | 0 | 14.2 | 2022-06-01 | 16.4 | 1.6 | 0 | 2021-06-01 | 22.6 | 0 | 4.6 | 2020-06-01 | 16.6 | 1.4 | 0 | 2019-06-01 | 17.1 | 0.9 | 0 | 2018-06-01 | 25 | 0 | 7 | 2017-06-01 | 13 | 5 | 0 | 2016-06-01 | 24.2 | 0 | 6.2 | 1.74 | 3.92
2025-06-01 | 9.3 | 8.7 | 0 | 2024-06-01 | 22.4 | 0 | 4.4 | 2023-06-01 | 30 | 0 | 12 | 2022-06-01 | 16.1 | 1.9 | 0 | 2021-06-01 | 20.5 | 0 | 2.5 | 2020-06-01 | 14.6 | 3.4 | 0 | 2019-06-01 | 16.4 | 1.6 | 0 | 2018-06-01 | 23.1 | 0 | 5.1 | 2017-06-01 | 13.3 | 4.7 | 0 | 2016-06-01 | 21.7 | 0 | 3.7 | 2.03 | 2.77
2025-06-01 | 8.4 | 9.6 | 0 | 2024-06-01 | 20.3 | 0 | 2.3 | 2023-06-01 | 28 | 0 | 10 | 2022-06-01 | 16.3 | 1.7 | 0 | 2021-06-01 | 19.7 | 0 | 1.7 | 2020-06-01 | 12.3 | 5.7 | 0 | 2019-06-01 | 15.8 | 2.2 | 0 | 2018-06-01 | 22.4 | 0 | 4.4 | 2017-06-01 | 10 | 8 | 0 | 2016-06-01 | 19.6 | 0 | 1.6 | 2.72 | 2
2025-06-01 | 8.3 | 9.7 | 0 | 2024-06-01 | 18.5 | 0 | 0.5 | 2023-06-01 | 24.7 | 0 | 6.7 | 2022-06-01 | 16 | 2 | 0 | 2021-06-01 | 17.8 | 0.2 | 0 | 2020-06-01 | 10.8 | 7.2 | 0 | 2019-06-01 | 14.1 | 3.9 | 0 | 2018-06-01 | 21.3 | 0 | 3.3 | 2017-06-01 | 10.3 | 7.7 | 0 | 2016-06-01 | 18.3 | 0 | 0.3 | 3.07 | 1.08
2025-06-01 | 8.8 | 9.2 | 0 | 2024-06-01 | 17.6 | 0.4 | 0 | 2023-06-01 | 21.5 | 0 | 3.5 | 2022-06-01 | 15.9 | 2.1 | 0 | 2021-06-01 | 16.6 | 1.4 | 0 | 2020-06-01 | 9.9 | 8.1 | 0 | 2019-06-01 | 13.5 | 4.5 | 0 | 2018-06-01 | 19.4 | 0 | 1.4 | 2017-06-01 | 7.7 | 10.3 | 0 | 2016-06-01 | 17.7 | 0.3 | 0 | 3.63 | 0.49
2025-06-01 | 9 | 9 | 0 | 2024-06-01 | 16 | 2 | 0 | 2023-06-01 | 22.1 | 0 | 4.1 | 2022-06-01 | 15.7 | 2.3 | 0 | 2021-06-01 | 15.8 | 2.2 | 0 | 2020-06-01 | 9.1 | 8.9 | 0 | 2019-06-01 | 13.9 | 4.1 | 0 | 2018-06-01 | 17.5 | 0.5 | 0 | 2017-06-01 | 8.3 | 9.7 | 0 | 2016-06-01 | 16.9 | 1.1 | 0 | 3.98 | 0.41
2025-06-02 | 8.5 | 9.5 | 0 | 2024-06-02 | 14.8 | 3.2 | 0 | 2023-06-02 | 22.5 | 0 | 4.5 | 2022-06-02 | 15.5 | 2.5 | 0 | 2021-06-02 | 14 | 4 | 0 | 2020-06-02 | 8 | 10 | 0 | 2019-06-02 | 13 | 5 | 0 | 2018-06-02 | 16.1 | 1.9 | 0 | 2017-06-02 | 7.8 | 10.2 | 0 | 2016-06-02 | 15.7 | 2.3 | 0 | 4.86 | 0.45
2025-06-02 | 7.2 | 10.8 | 0 | 2024-06-02 | 14.2 | 3.8 | 0 | 2023-06-02 | 22.1 | 0 | 4.1 | 2022-06-02 | 14.8 | 3.2 | 0 | 2021-06-02 | 13.9 | 4.1 | 0 | 2020-06-02 | 8 | 10 | 0 | 2019-06-02 | 12.3 | 5.7 | 0 | 2018-06-02 | 14.8 | 3.2 | 0 | 2017-06-02 | 7.5 | 10.5 | 0 | 2016-06-02 | 14 | 4 | 0 | 5.53 | 0.41
2025-06-02 | 7 | 11 | 0 | 2024-06-02 | 12 | 6 | 0 | 2023-06-02 | 20.1 | 0 | 2.1 | 2022-06-02 | 13.1 | 4.9 | 0 | 2021-06-02 | 12 | 6 | 0 | 2020-06-02 | 7.9 | 10.1 | 0 | 2019-06-02 | 11.7 | 6.3 | 0 | 2018-06-02 | 13.5 | 4.5 | 0 | 2017-06-02 | 7.2 | 10.8 | 0 | 2016-06-02 | 14.3 | 3.7 | 0 | 6.33 | 0.21
2025-06-02 | 6.5 | 11.5 | 0 | 2024-06-02 | 12.4 | 5.6 | 0 | 2023-06-02 | 20.1 | 0 | 2.1 | 2022-06-02 | 12.6 | 5.4 | 0 | 2021-06-02 | 12.2 | 5.8 | 0 | 2020-06-02 | 8 | 10 | 0 | 2019-06-02 | 12.3 | 5.7 | 0 | 2018-06-02 | 13.1 | 4.9 | 0 | 2017-06-02 | 8.9 | 9.1 | 0 | 2016-06-02 | 14.3 | 3.7 | 0 | 6.17 | 0.21
2025-06-02 | 5.7 | 12.3 | 0 | 2024-06-02 | 12.1 | 5.9 | 0 | 2023-06-02 | 21.9 | 0 | 3.9 | 2022-06-02 | 12.5 | 5.5 | 0 | 2021-06-02 | 9.5 | 8.5 | 0 | 2020-06-02 | 7.9 | 10.1 | 0 | 2019-06-02 | 12.5 | 5.5 | 0 | 2018-06-02 | 12.2 | 5.8 | 0 | 2017-06-02 | 8.4 | 9.6 | 0 | 2016-06-02 | 14.5 | 3.5 | 0 | 6.67 | 0.39
2025-06-02 | 5.3 | 12.7 | 0 | 2024-06-02 | 11.6 | 6.4 | 0 | 2023-06-02 | 21.5 | 0 | 3.5 | 2022-06-02 | 12.6 | 5.4 | 0 | 2021-06-02 | 9.7 | 8.3 | 0 | 2020-06-02 | 7.8 | 10.2 | 0 | 2019-06-02 | 12.5 | 5.5 | 0 | 2018-06-02 | 12.4 | 5.6 | 0 | 2017-06-02 | 8.2 | 9.8 | 0 | 2016-06-02 | 14.8 | 3.2 | 0 | 6.71 | 0.35
2025-06-02 | 8.6 | 9.4 | 0 | 2024-06-02 | 13.5 | 4.5 | 0 | 2023-06-02 | 22.3 | 0 | 4.3 | 2022-06-02 | 12.8 | 5.2 | 0 | 2021-06-02 | 13.4 | 4.6 | 0 | 2020-06-02 | 8.1 | 9.9 | 0 | 2019-06-02 | 12.3 | 5.7 | 0 | 2018-06-02 | 13.2 | 4.8 | 0 | 2017-06-02 | 9.3 | 8.7 | 0 | 2016-06-02 | 15.4 | 2.6 | 0 | 5.54 | 0.43
2025-06-02 | 10 | 8 | 0 | 2024-06-02 | 15.4 | 2.6 | 0 | 2023-06-02 | 23.6 | 0 | 5.6 | 2022-06-02 | 13.1 | 4.9 | 0 | 2021-06-02 | 17 | 1 | 0 | 2020-06-02 | 9.5 | 8.5 | 0 | 2019-06-02 | 12.6 | 5.4 | 0 | 2018-06-02 | 14.1 | 3.9 | 0 | 2017-06-02 | 9.1 | 8.9 | 0 | 2016-06-02 | 15.8 | 2.2 | 0 | 4.54 | 0.56
2025-06-02 | 11.8 | 6.2 | 0 | 2024-06-02 | 17.7 | 0.3 | 0 | 2023-06-02 | 25.7 | 0 | 7.7 | 2022-06-02 | 13.4 | 4.6 | 0 | 2021-06-02 | 18.8 | 0 | 0.8 | 2020-06-02 | 11.1 | 6.9 | 0 | 2019-06-02 | 12.6 | 5.4 | 0 | 2018-06-02 | 14.8 | 3.2 | 0 | 2017-06-02 | 10.4 | 7.6 | 0 | 2016-06-02 | 16.2 | 1.8 | 0 | 3.6 | 0.85
2025-06-02 | 13.7 | 4.3 | 0 | 2024-06-02 | 19.7 | 0 | 1.7 | 2023-06-02 | 26 | 0 | 8 | 2022-06-02 | 14.2 | 3.8 | 0 | 2021-06-02 | 21.7 | 0 | 3.7 | 2020-06-02 | 13.3 | 4.7 | 0 | 2019-06-02 | 12.6 | 5.4 | 0 | 2018-06-02 | 17 | 1 | 0 | 2017-06-02 | 11.4 | 6.6 | 0 | 2016-06-02 | 17.4 | 0.6 | 0 | 2.64 | 1.34
2025-06-02 | 16.5 | 1.5 | 0 | 2024-06-02 | 22.4 | 0 | 4.4 | 2023-06-02 | 29.8 | 0 | 11.8 | 2022-06-02 | 15 | 3 | 0 | 2021-06-02 | 23.1 | 0 | 5.1 | 2020-06-02 | 15 | 3 | 0 | 2019-06-02 | 13 | 5 | 0 | 2018-06-02 | 18.7 | 0 | 0.7 | 2017-06-02 | 13.4 | 4.6 | 0 | 2016-06-02 | 19.7 | 0 | 1.7 | 1.71 | 2.37
2025-06-02 | 18 | 0 | 0 | 2024-06-02 | 24.1 | 0 | 6.1 | 2023-06-02 | 30.1 | 0 | 12.1 | 2022-06-02 | 16.4 | 1.6 | 0 | 2021-06-02 | 24.5 | 0 | 6.5 | 2020-06-02 | 15 | 3 | 0 | 2019-06-02 | 13 | 5 | 0 | 2018-06-02 | 20.1 | 0 | 2.1 | 2017-06-02 | 12.2 | 5.8 | 0 | 2016-06-02 | 19.9 | 0 | 1.9 | 1.54 | 2.87
2025-06-02 | 19 | 0 | 1 | 2024-06-02 | 24.7 | 0 | 6.7 | 2023-06-02 | 31.7 | 0 | 13.7 | 2022-06-02 | 17.5 | 0.5 | 0 | 2021-06-02 | 25.7 | 0 | 7.7 | 2020-06-02 | 15.3 | 2.7 | 0 | 2019-06-02 | 13 | 5 | 0 | 2018-06-02 | 21.4 | 0 | 3.4 | 2017-06-02 | 12.5 | 5.5 | 0 | 2016-06-02 | 20.6 | 0 | 2.6 | 1.37 | 3.51
2025-06-02 | 19.3 | 0 | 1.3 | 2024-06-02 | 25.6 | 0 | 7.6 | 2023-06-02 | 32.1 | 0 | 14.1 | 2022-06-02 | 17.3 | 0.7 | 0 | 2021-06-02 | 25.8 | 0 | 7.8 | 2020-06-02 | 15 | 3 | 0 | 2019-06-02 | 13.8 | 4.2 | 0 | 2018-06-02 | 23.2 | 0 | 5.2 | 2017-06-02 | 13.5 | 4.5 | 0 | 2016-06-02 | 20 | 0 | 2 | 1.24 | 3.8
2025-06-02 | 19.4 | 0 | 1.4 | 2024-06-02 | 25.5 | 0 | 7.5 | 2023-06-02 | 31.2 | 0 | 13.2 | 2022-06-02 | 17.8 | 0.2 | 0 | 2021-06-02 | 26.8 | 0 | 8.8 | 2020-06-02 | 15.2 | 2.8 | 0 | 2019-06-02 | 16.6 | 1.4 | 0 | 2018-06-02 | 24.1 | 0 | 6.1 | 2017-06-02 | 13.6 | 4.4 | 0 | 2016-06-02 | 20.2 | 0 | 2.2 | 0.88 | 3.92
2025-06-02 | 19.2 | 0 | 1.2 | 2024-06-02 | 24.8 | 0 | 6.8 | 2023-06-02 | 31.7 | 0 | 13.7 | 2022-06-02 | 18.1 | 0 | 0.1 | 2021-06-02 | 26.2 | 0 | 8.2 | 2020-06-02 | 15.2 | 2.8 | 0 | 2019-06-02 | 19.4 | 0 | 1.4 | 2018-06-02 | 24.7 | 0 | 6.7 | 2017-06-02 | 14.3 | 3.7 | 0 | 2016-06-02 | 21.5 | 0 | 3.5 | 0.65 | 4.16
2025-06-02 | 20.6 | 0 | 2.6 | 2024-06-02 | 25.2 | 0 | 7.2 | 2023-06-02 | 32.1 | 0 | 14.1 | 2022-06-02 | 17.7 | 0.3 | 0 | 2021-06-02 | 25.6 | 0 | 7.6 | 2020-06-02 | 15.2 | 2.8 | 0 | 2019-06-02 | 18.6 | 0 | 0.6 | 2018-06-02 | 24.6 | 0 | 6.6 | 2017-06-02 | 14.5 | 3.5 | 0 | 2016-06-02 | 22.6 | 0 | 4.6 | 0.66 | 4.33
2025-06-02 | 20.9 | 0 | 2.9 | 2024-06-02 | 24.8 | 0 | 6.8 | 2023-06-02 | 29.6 | 0 | 11.6 | 2022-06-02 | 18.3 | 0 | 0.3 | 2021-06-02 | 26.4 | 0 | 8.4 | 2020-06-02 | 15 | 3 | 0 | 2019-06-02 | 20.6 | 0 | 2.6 | 2018-06-02 | 24.8 | 0 | 6.8 | 2017-06-02 | 14 | 4 | 0 | 2016-06-02 | 22.1 | 0 | 4.1 | 0.7 | 4.35
2025-06-02 | 20.4 | 0 | 2.4 | 2024-06-02 | 24.8 | 0 | 6.8 | 2023-06-02 | 28.6 | 0 | 10.6 | 2022-06-02 | 18 | 0 | 0 | 2021-06-02 | 25 | 0 | 7 | 2020-06-02 | 14.7 | 3.3 | 0 | 2019-06-02 | 18.8 | 0 | 0.8 | 2018-06-02 | 24.3 | 0 | 6.3 | 2017-06-02 | 14.4 | 3.6 | 0 | 2016-06-02 | 22.3 | 0 | 4.3 | 0.69 | 3.82
2025-06-02 | 18.8 | 0 | 0.8 | 2024-06-02 | 22.1 | 0 | 4.1 | 2023-06-02 | 26.9 | 0 | 8.9 | 2022-06-02 | 17 | 1 | 0 | 2021-06-02 | 23.1 | 0 | 5.1 | 2020-06-02 | 14.3 | 3.7 | 0 | 2019-06-02 | 17.8 | 0.2 | 0 | 2018-06-02 | 22.7 | 0 | 4.7 | 2017-06-02 | 13.7 | 4.3 | 0 | 2016-06-02 | 21.5 | 0 | 3.5 | 0.92 | 2.71
2025-06-02 | 15.1 | 2.9 | 0 | 2024-06-02 | 21.1 | 0 | 3.1 | 2023-06-02 | 25.6 | 0 | 7.6 | 2022-06-02 | 16.6 | 1.4 | 0 | 2021-06-02 | 20.5 | 0 | 2.5 | 2020-06-02 | 13.8 | 4.2 | 0 | 2019-06-02 | 16.3 | 1.7 | 0 | 2018-06-02 | 20.9 | 0 | 2.9 | 2017-06-02 | 13.5 | 4.5 | 0 | 2016-06-02 | 20.7 | 0 | 2.7 | 1.47 | 1.88
2025-06-02 | 13.2 | 4.8 | 0 | 2024-06-02 | 20.6 | 0 | 2.6 | 2023-06-02 | 25 | 0 | 7 | 2022-06-02 | 16.4 | 1.6 | 0 | 2021-06-02 | 18.8 | 0 | 0.8 | 2020-06-02 | 13.7 | 4.3 | 0 | 2019-06-02 | 14.5 | 3.5 | 0 | 2018-06-02 | 16.4 | 1.6 | 0 | 2017-06-02 | 13.2 | 4.8 | 0 | 2016-06-02 | 20 | 0 | 2 | 2.06 | 1.24
2025-06-02 | 12.2 | 5.8 | 0 | 2024-06-02 | 19.6 | 0 | 1.6 | 2023-06-02 | 19.7 | 0 | 1.7 | 2022-06-02 | 15.8 | 2.2 | 0 | 2021-06-02 | 18.2 | 0 | 0.2 | 2020-06-02 | 13.4 | 4.6 | 0 | 2019-06-02 | 13.3 | 4.7 | 0 | 2018-06-02 | 13.9 | 4.1 | 0 | 2017-06-02 | 12.1 | 5.9 | 0 | 2016-06-02 | 19.7 | 0 | 1.7 | 2.73 | 0.52
2025-06-02 | 11.2 | 6.8 | 0 | 2024-06-02 | 18.7 | 0 | 0.7 | 2023-06-02 | 16.9 | 1.1 | 0 | 2022-06-02 | 15.3 | 2.7 | 0 | 2021-06-02 | 17.7 | 0.3 | 0 | 2020-06-02 | 13.5 | 4.5 | 0 | 2019-06-02 | 11.3 | 6.7 | 0 | 2018-06-02 | 15 | 3 | 0 | 2017-06-02 | 11.6 | 6.4 | 0 | 2016-06-02 | 18.9 | 0 | 0.9 | 3.15 | 0.16
2025-06-03 | 9.9 | 8.1 | 0 | 2024-06-03 | 17.8 | 0.2 | 0 | 2023-06-03 | 15.6 | 2.4 | 0 | 2022-06-03 | 14.8 | 3.2 | 0 | 2021-06-03 | 17.2 | 0.8 | 0 | 2020-06-03 | 13.5 | 4.5 | 0 | 2019-06-03 | 9.3 | 8.7 | 0 | 2018-06-03 | 14.2 | 3.8 | 0 | 2017-06-03 | 10.1 | 7.9 | 0 | 2016-06-03 | 17.8 | 0.2 | 0 | 3.98 | 0
2025-06-03 | 8.2 | 9.8 | 0 | 2024-06-03 | 15.1 | 2.9 | 0 | 2023-06-03 | 14.5 | 3.5 | 0 | 2022-06-03 | 15.6 | 2.4 | 0 | 2021-06-03 | 16.1 | 1.9 | 0 | 2020-06-03 | 13.2 | 4.8 | 0 | 2019-06-03 | 8.1 | 9.9 | 0 | 2018-06-03 | 13.9 | 4.1 | 0 | 2017-06-03 | 7.3 | 10.7 | 0 | 2016-06-03 | 16 | 2 | 0 | 5.2 | 0
2025-06-03 | 9 | 9 | 0 | 2024-06-03 | 15.4 | 2.6 | 0 | 2023-06-03 | 13.6 | 4.4 | 0 | 2022-06-03 | 14.2 | 3.8 | 0 | 2021-06-03 | 15.1 | 2.9 | 0 | 2020-06-03 | 12.6 | 5.4 | 0 | 2019-06-03 | 6.8 | 11.2 | 0 | 2018-06-03 | 12.2 | 5.8 | 0 | 2017-06-03 | 7.8 | 10.2 | 0 | 2016-06-03 | 13.8 | 4.2 | 0 | 5.95 | 0
2025-06-03 | 9.3 | 8.7 | 0 | 2024-06-03 | 14.4 | 3.6 | 0 | 2023-06-03 | 12.8 | 5.2 | 0 | 2022-06-03 | 13.3 | 4.7 | 0 | 2021-06-03 | 15.5 | 2.5 | 0 | 2020-06-03 | 12.4 | 5.6 | 0 | 2019-06-03 | 6.6 | 11.4 | 0 | 2018-06-03 | 11.8 | 6.2 | 0 | 2017-06-03 | 7.2 | 10.8 | 0 | 2016-06-03 | 13.4 | 4.6 | 0 | 6.33 | 0
2025-06-03 | 9.5 | 8.5 | 0 | 2024-06-03 | 12.2 | 5.8 | 0 | 2023-06-03 | 11.7 | 6.3 | 0 | 2022-06-03 | 12.2 | 5.8 | 0 | 2021-06-03 | 15.7 | 2.3 | 0 | 2020-06-03 | 12.4 | 5.6 | 0 | 2019-06-03 | 7.6 | 10.4 | 0 | 2018-06-03 | 10.4 | 7.6 | 0 | 2017-06-03 | 5.8 | 12.2 | 0 | 2016-06-03 | 12.6 | 5.4 | 0 | 6.99 | 0
2025-06-03 | 9.4 | 8.6 | 0 | 2024-06-03 | 11.9 | 6.1 | 0 | 2023-06-03 | 12.3 | 5.7 | 0 | 2022-06-03 | 12.6 | 5.4 | 0 | 2021-06-03 | 15.7 | 2.3 | 0 | 2020-06-03 | 12.4 | 5.6 | 0 | 2019-06-03 | 6.7 | 11.3 | 0 | 2018-06-03 | 10.8 | 7.2 | 0 | 2017-06-03 | 7.3 | 10.7 | 0 | 2016-06-03 | 12.6 | 5.4 | 0 | 6.83 | 0
2025-06-03 | 9.9 | 8.1 | 0 | 2024-06-03 | 16.6 | 1.4 | 0 | 2023-06-03 | 13.6 | 4.4 | 0 | 2022-06-03 | 13.7 | 4.3 | 0 | 2021-06-03 | 15.7 | 2.3 | 0 | 2020-06-03 | 12.5 | 5.5 | 0 | 2019-06-03 | 8 | 10 | 0 | 2018-06-03 | 12.4 | 5.6 | 0 | 2017-06-03 | 9.1 | 8.9 | 0 | 2016-06-03 | 14.9 | 3.1 | 0 | 5.36 | 0
2025-06-03 | 12.2 | 5.8 | 0 | 2024-06-03 | 20.1 | 0 | 2.1 | 2023-06-03 | 14.3 | 3.7 | 0 | 2022-06-03 | 13.1 | 4.9 | 0 | 2021-06-03 | 16 | 2 | 0 | 2020-06-03 | 12.3 | 5.7 | 0 | 2019-06-03 | 10 | 8 | 0 | 2018-06-03 | 14.4 | 3.6 | 0 | 2017-06-03 | 9.9 | 8.1 | 0 | 2016-06-03 | 17.2 | 0.8 | 0 | 4.26 | 0.21
2025-06-03 | 15.5 | 2.5 | 0 | 2024-06-03 | 22.1 | 0 | 4.1 | 2023-06-03 | 15.6 | 2.4 | 0 | 2022-06-03 | 14 | 4 | 0 | 2021-06-03 | 16.1 | 1.9 | 0 | 2020-06-03 | 12.5 | 5.5 | 0 | 2019-06-03 | 7.8 | 10.2 | 0 | 2018-06-03 | 16.7 | 1.3 | 0 | 2017-06-03 | 12 | 6 | 0 | 2016-06-03 | 18.8 | 0 | 0.8 | 3.38 | 0.49
2025-06-03 | 16.5 | 1.5 | 0 | 2024-06-03 | 23.6 | 0 | 5.6 | 2023-06-03 | 17.2 | 0.8 | 0 | 2022-06-03 | 15.7 | 2.3 | 0 | 2021-06-03 | 16.2 | 1.8 | 0 | 2020-06-03 | 13.4 | 4.6 | 0 | 2019-06-03 | 6.2 | 11.8 | 0 | 2018-06-03 | 18.3 | 0 | 0.3 | 2017-06-03 | 12 | 6 | 0 | 2016-06-03 | 20.7 | 0 | 2.7 | 2.88 | 0.86
2025-06-03 | 19 | 0 | 1 | 2024-06-03 | 25 | 0 | 7 | 2023-06-03 | 18 | 0 | 0 | 2022-06-03 | 18.6 | 0 | 0.6 | 2021-06-03 | 16.7 | 1.3 | 0 | 2020-06-03 | 14.3 | 3.7 | 0 | 2019-06-03 | 6.8 | 11.2 | 0 | 2018-06-03 | 20.2 | 0 | 2.2 | 2017-06-03 | 13 | 5 | 0 | 2016-06-03 | 22.5 | 0 | 4.5 | 2.12 | 1.53
2025-06-03 | 20.9 | 0 | 2.9 | 2024-06-03 | 26.1 | 0 | 8.1 | 2023-06-03 | 19.8 | 0 | 1.8 | 2022-06-03 | 20.9 | 0 | 2.9 | 2021-06-03 | 16.7 | 1.3 | 0 | 2020-06-03 | 15.2 | 2.8 | 0 | 2019-06-03 | 7.1 | 10.9 | 0 | 2018-06-03 | 21.6 | 0 | 3.6 | 2017-06-03 | 13.9 | 4.1 | 0 | 2016-06-03 | 23.4 | 0 | 5.4 | 1.91 | 2.47
2025-06-03 | 23.1 | 0 | 5.1 | 2024-06-03 | 27.1 | 0 | 9.1 | 2023-06-03 | 19.6 | 0 | 1.6 | 2022-06-03 | 21.8 | 0 | 3.8 | 2021-06-03 | 18.2 | 0 | 0.2 | 2020-06-03 | 15.7 | 2.3 | 0 | 2019-06-03 | 8.2 | 9.8 | 0 | 2018-06-03 | 22.5 | 0 | 4.5 | 2017-06-03 | 15.8 | 2.2 | 0 | 2016-06-03 | 25.6 | 0 | 7.6 | 1.43 | 3.19
2025-06-03 | 23.9 | 0 | 5.9 | 2024-06-03 | 27.2 | 0 | 9.2 | 2023-06-03 | 20.4 | 0 | 2.4 | 2022-06-03 | 22.5 | 0 | 4.5 | 2021-06-03 | 18.7 | 0 | 0.7 | 2020-06-03 | 16.3 | 1.7 | 0 | 2019-06-03 | 8.6 | 9.4 | 0 | 2018-06-03 | 22.6 | 0 | 4.6 | 2017-06-03 | 16.3 | 1.7 | 0 | 2016-06-03 | 25.4 | 0 | 7.4 | 1.28 | 3.47
2025-06-03 | 25.2 | 0 | 7.2 | 2024-06-03 | 27.8 | 0 | 9.8 | 2023-06-03 | 21.3 | 0 | 3.3 | 2022-06-03 | 23 | 0 | 5 | 2021-06-03 | 19.8 | 0 | 1.8 | 2020-06-03 | 17.4 | 0.6 | 0 | 2019-06-03 | 8.3 | 9.7 | 0 | 2018-06-03 | 23.5 | 0 | 5.5 | 2017-06-03 | 18.3 | 0 | 0.3 | 2016-06-03 | 25.6 | 0 | 7.6 | 1.03 | 4.05
2025-06-03 | 25.4 | 0 | 7.4 | 2024-06-03 | 27.8 | 0 | 9.8 | 2023-06-03 | 21.1 | 0 | 3.1 | 2022-06-03 | 23.4 | 0 | 5.4 | 2021-06-03 | 20.7 | 0 | 2.7 | 2020-06-03 | 18.2 | 0 | 0.2 | 2019-06-03 | 9.1 | 8.9 | 0 | 2018-06-03 | 22.2 | 0 | 4.2 | 2017-06-03 | 18.6 | 0 | 0.6 | 2016-06-03 | 26.3 | 0 | 8.3 | 0.89 | 4.17
2025-06-03 | 24.6 | 0 | 6.6 | 2024-06-03 | 28.4 | 0 | 10.4 | 2023-06-03 | 21 | 0 | 3 | 2022-06-03 | 22.8 | 0 | 4.8 | 2021-06-03 | 20.3 | 0 | 2.3 | 2020-06-03 | 17.9 | 0.1 | 0 | 2019-06-03 | 13 | 5 | 0 | 2018-06-03 | 21.6 | 0 | 3.6 | 2017-06-03 | 19.1 | 0 | 1.1 | 2016-06-03 | 26.1 | 0 | 8.1 | 0.51 | 3.99
2025-06-03 | 23.9 | 0 | 5.9 | 2024-06-03 | 28 | 0 | 10 | 2023-06-03 | 20.3 | 0 | 2.3 | 2022-06-03 | 20.6 | 0 | 2.6 | 2021-06-03 | 20.8 | 0 | 2.8 | 2020-06-03 | 19.4 | 0 | 1.4 | 2019-06-03 | 15.2 | 2.8 | 0 | 2018-06-03 | 20.6 | 0 | 2.6 | 2017-06-03 | 19.9 | 0 | 1.9 | 2016-06-03 | 25.3 | 0 | 7.3 | 0.28 | 3.68
2025-06-03 | 22.5 | 0 | 4.5 | 2024-06-03 | 27.1 | 0 | 9.1 | 2023-06-03 | 19.4 | 0 | 1.4 | 2022-06-03 | 18.6 | 0 | 0.6 | 2021-06-03 | 21.5 | 0 | 3.5 | 2020-06-03 | 18.2 | 0 | 0.2 | 2019-06-03 | 15 | 3 | 0 | 2018-06-03 | 19.3 | 0 | 1.3 | 2017-06-03 | 19.7 | 0 | 1.7 | 2016-06-03 | 24.9 | 0 | 6.9 | 0.3 | 2.92
2025-06-03 | 21.1 | 0 | 3.1 | 2024-06-03 | 26 | 0 | 8 | 2023-06-03 | 16.8 | 1.2 | 0 | 2022-06-03 | 16.7 | 1.3 | 0 | 2021-06-03 | 19.9 | 0 | 1.9 | 2020-06-03 | 17.5 | 0.5 | 0 | 2019-06-03 | 13.3 | 4.7 | 0 | 2018-06-03 | 16.3 | 1.7 | 0 | 2017-06-03 | 18.5 | 0 | 0.5 | 2016-06-03 | 23.3 | 0 | 5.3 | 0.94 | 1.88
2025-06-03 | 19.2 | 0 | 1.2 | 2024-06-03 | 21.6 | 0 | 3.6 | 2023-06-03 | 15.9 | 2.1 | 0 | 2022-06-03 | 16.8 | 1.2 | 0 | 2021-06-03 | 18.6 | 0 | 0.6 | 2020-06-03 | 16.3 | 1.7 | 0 | 2019-06-03 | 11.6 | 6.4 | 0 | 2018-06-03 | 16 | 2 | 0 | 2017-06-03 | 15.9 | 2.1 | 0 | 2016-06-03 | 22.4 | 0 | 4.4 | 1.55 | 0.98
2025-06-03 | 17.9 | 0.1 | 0 | 2024-06-03 | 22 | 0 | 4 | 2023-06-03 | 13.3 | 4.7 | 0 | 2022-06-03 | 14.6 | 3.4 | 0 | 2021-06-03 | 18.2 | 0 | 0.2 | 2020-06-03 | 14.2 | 3.8 | 0 | 2019-06-03 | 10.2 | 7.8 | 0 | 2018-06-03 | 15 | 3 | 0 | 2017-06-03 | 13.8 | 4.2 | 0 | 2016-06-03 | 21.4 | 0 | 3.4 | 2.7 | 0.76
2025-06-03 | 17.3 | 0.7 | 0 | 2024-06-03 | 19.9 | 0 | 1.9 | 2023-06-03 | 14.4 | 3.6 | 0 | 2022-06-03 | 14.5 | 3.5 | 0 | 2021-06-03 | 17.4 | 0.6 | 0 | 2020-06-03 | 13.6 | 4.4 | 0 | 2019-06-03 | 10.6 | 7.4 | 0 | 2018-06-03 | 14.9 | 3.1 | 0 | 2017-06-03 | 12.2 | 5.8 | 0 | 2016-06-03 | 20.1 | 0 | 2.1 | 2.91 | 0.4
2025-06-03 | 14.9 | 3.1 | 0 | 2024-06-03 | 19.5 | 0 | 1.5 | 2023-06-03 | 12.6 | 5.4 | 0 | 2022-06-03 | 13.8 | 4.2 | 0 | 2021-06-03 | 16.7 | 1.3 | 0 | 2020-06-03 | 12.4 | 5.6 | 0 | 2019-06-03 | 9.9 | 8.1 | 0 | 2018-06-03 | 14.8 | 3.2 | 0 | 2017-06-03 | 11.2 | 6.8 | 0 | 2016-06-03 | 19.5 | 0 | 1.5 | 3.77 | 0.3
2025-06-04 | 13.5 | 4.5 | 0 | 2024-06-04 | 18.9 | 0 | 0.9 | 2023-06-04 | 11 | 7 | 0 | 2022-06-04 | 13.5 | 4.5 | 0 | 2021-06-04 | 16.4 | 1.6 | 0 | 2020-06-04 | 11.2 | 6.8 | 0 | 2019-06-04 | 7.8 | 10.2 | 0 | 2018-06-04 | 14.7 | 3.3 | 0 | 2017-06-04 | 11.2 | 6.8 | 0 | 2016-06-04 | 19 | 0 | 1 | 4.47 | 0.19
2025-06-04 | 15.6 | 2.4 | 0 | 2024-06-04 | 17.1 | 0.9 | 0 | 2023-06-04 | 9.7 | 8.3 | 0 | 2022-06-04 | 12.9 | 5.1 | 0 | 2021-06-04 | 15.9 | 2.1 | 0 | 2020-06-04 | 10.5 | 7.5 | 0 | 2019-06-04 | 6 | 12 | 0 | 2018-06-04 | 14.5 | 3.5 | 0 | 2017-06-04 | 9.7 | 8.3 | 0 | 2016-06-04 | 17.6 | 0.4 | 0 | 5.05 | 0
2025-06-04 | 15.4 | 2.6 | 0 | 2024-06-04 | 17 | 1 | 0 | 2023-06-04 | 9.1 | 8.9 | 0 | 2022-06-04 | 11.7 | 6.3 | 0 | 2021-06-04 | 15.8 | 2.2 | 0 | 2020-06-04 | 10.4 | 7.6 | 0 | 2019-06-04 | 5.6 | 12.4 | 0 | 2018-06-04 | 14.4 | 3.6 | 0 | 2017-06-04 | 10 | 8 | 0 | 2016-06-04 | 17.4 | 0.6 | 0 | 5.32 | 0
2025-06-04 | 15.2 | 2.8 | 0 | 2024-06-04 | 14.3 | 3.7 | 0 | 2023-06-04 | 7.7 | 10.3 | 0 | 2022-06-04 | 12.1 | 5.9 | 0 | 2021-06-04 | 15.1 | 2.9 | 0 | 2020-06-04 | 11.7 | 6.3 | 0 | 2019-06-04 | 3.5 | 14.5 | 0 | 2018-06-04 | 13.9 | 4.1 | 0 | 2017-06-04 | 9.1 | 8.9 | 0 | 2016-06-04 | 15.7 | 2.3 | 0 | 6.17 | 0
2025-06-04 | 15.3 | 2.7 | 0 | 2024-06-04 | 13.9 | 4.1 | 0 | 2023-06-04 | 8.2 | 9.8 | 0 | 2022-06-04 | 12.7 | 5.3 | 0 | 2021-06-04 | 15.1 | 2.9 | 0 | 2020-06-04 | 10.9 | 7.1 | 0 | 2019-06-04 | 3.9 | 14.1 | 0 | 2018-06-04 | 13.5 | 4.5 | 0 | 2017-06-04 | 9.1 | 8.9 | 0 | 2016-06-04 | 15.3 | 2.7 | 0 | 6.21 | 0
2025-06-04 | 15.8 | 2.2 | 0 | 2024-06-04 | 14.5 | 3.5 | 0 | 2023-06-04 | 6.5 | 11.5 | 0 | 2022-06-04 | 12.4 | 5.6 | 0 | 2021-06-04 | 15.1 | 2.9 | 0 | 2020-06-04 | 10.9 | 7.1 | 0 | 2019-06-04 | 3.5 | 14.5 | 0 | 2018-06-04 | 13 | 5 | 0 | 2017-06-04 | 8.9 | 9.1 | 0 | 2016-06-04 | 15.2 | 2.8 | 0 | 6.42 | 0
2025-06-04 | 17.9 | 0.1 | 0 | 2024-06-04 | 16 | 2 | 0 | 2023-06-04 | 11 | 7 | 0 | 2022-06-04 | 13.9 | 4.1 | 0 | 2021-06-04 | 15.3 | 2.7 | 0 | 2020-06-04 | 13.5 | 4.5 | 0 | 2019-06-04 | 6.6 | 11.4 | 0 | 2018-06-04 | 12.8 | 5.2 | 0 | 2017-06-04 | 10.7 | 7.3 | 0 | 2016-06-04 | 16.9 | 1.1 | 0 | 4.54 | 0
2025-06-04 | 19.2 | 0 | 1.2 | 2024-06-04 | 20.2 | 0 | 2.2 | 2023-06-04 | 13.5 | 4.5 | 0 | 2022-06-04 | 15.6 | 2.4 | 0 | 2021-06-04 | 16.2 | 1.8 | 0 | 2020-06-04 | 15.8 | 2.2 | 0 | 2019-06-04 | 8.7 | 9.3 | 0 | 2018-06-04 | 12.5 | 5.5 | 0 | 2017-06-04 | 13.4 | 4.6 | 0 | 2016-06-04 | 18.5 | 0 | 0.5 | 3.03 | 0.39
2025-06-04 | 20.1 | 0 | 2.1 | 2024-06-04 | 22.5 | 0 | 4.5 | 2023-06-04 | 15.2 | 2.8 | 0 | 2022-06-04 | 16.7 | 1.3 | 0 | 2021-06-04 | 18 | 0 | 0 | 2020-06-04 | 18.9 | 0 | 0.9 | 2019-06-04 | 11.3 | 6.7 | 0 | 2018-06-04 | 12.3 | 5.7 | 0 | 2017-06-04 | 15.6 | 2.4 | 0 | 2016-06-04 | 20.6 | 0 | 2.6 | 1.89 | 1.01
2025-06-04 | 23.2 | 0 | 5.2 | 2024-06-04 | 24.2 | 0 | 6.2 | 2023-06-04 | 16.8 | 1.2 | 0 | 2022-06-04 | 15.5 | 2.5 | 0 | 2021-06-04 | 18.8 | 0 | 0.8 | 2020-06-04 | 19.8 | 0 | 1.8 | 2019-06-04 | 13.4 | 4.6 | 0 | 2018-06-04 | 12.9 | 5.1 | 0 | 2017-06-04 | 16.6 | 1.4 | 0 | 2016-06-04 | 22.4 | 0 | 4.4 | 1.48 | 1.84
2025-06-04 | 25.2 | 0 | 7.2 | 2024-06-04 | 26.4 | 0 | 8.4 | 2023-06-04 | 17.7 | 0.3 | 0 | 2022-06-04 | 16.9 | 1.1 | 0 | 2021-06-04 | 22.2 | 0 | 4.2 | 2020-06-04 | 20.1 | 0 | 2.1 | 2019-06-04 | 15.1 | 2.9 | 0 | 2018-06-04 | 12.8 | 5.2 | 0 | 2017-06-04 | 17 | 1 | 0 | 2016-06-04 | 23.4 | 0 | 5.4 | 1.05 | 2.73
2025-06-04 | 27 | 0 | 9 | 2024-06-04 | 26.9 | 0 | 8.9 | 2023-06-04 | 19.8 | 0 | 1.8 | 2022-06-04 | 16.2 | 1.8 | 0 | 2021-06-04 | 23.8 | 0 | 5.8 | 2020-06-04 | 21.2 | 0 | 3.2 | 2019-06-04 | 15.8 | 2.2 | 0 | 2018-06-04 | 12.8 | 5.2 | 0 | 2017-06-04 | 16.4 | 1.6 | 0 | 2016-06-04 | 24.6 | 0 | 6.6 | 1.08 | 3.53
2025-06-04 | 28.6 | 0 | 10.6 | 2024-06-04 | 27.1 | 0 | 9.1 | 2023-06-04 | 21.2 | 0 | 3.2 | 2022-06-04 | 17.7 | 0.3 | 0 | 2021-06-04 | 24.5 | 0 | 6.5 | 2020-06-04 | 22.5 | 0 | 4.5 | 2019-06-04 | 17.9 | 0.1 | 0 | 2018-06-04 | 15.2 | 2.8 | 0 | 2017-06-04 | 17 | 1 | 0 | 2016-06-04 | 23.8 | 0 | 5.8 | 0.42 | 3.97
2025-06-04 | 29.2 | 0 | 11.2 | 2024-06-04 | 28.1 | 0 | 10.1 | 2023-06-04 | 21.8 | 0 | 3.8 | 2022-06-04 | 17.1 | 0.9 | 0 | 2021-06-04 | 25.2 | 0 | 7.2 | 2020-06-04 | 24.1 | 0 | 6.1 | 2019-06-04 | 18.7 | 0 | 0.7 | 2018-06-04 | 16.5 | 1.5 | 0 | 2017-06-04 | 17.4 | 0.6 | 0 | 2016-06-04 | 25.3 | 0 | 7.3 | 0.3 | 4.64
2025-06-04 | 30.2 | 0 | 12.2 | 2024-06-04 | 28.8 | 0 | 10.8 | 2023-06-04 | 22.1 | 0 | 4.1 | 2022-06-04 | 17.8 | 0.2 | 0 | 2021-06-04 | 24.3 | 0 | 6.3 | 2020-06-04 | 24.9 | 0 | 6.9 | 2019-06-04 | 17.5 | 0.5 | 0 | 2018-06-04 | 16.2 | 1.8 | 0 | 2017-06-04 | 15.2 | 2.8 | 0 | 2016-06-04 | 26 | 0 | 8 | 0.53 | 4.83
2025-06-04 | 30.2 | 0 | 12.2 | 2024-06-04 | 28.9 | 0 | 10.9 | 2023-06-04 | 22.7 | 0 | 4.7 | 2022-06-04 | 18.2 | 0 | 0.2 | 2021-06-04 | 25.2 | 0 | 7.2 | 2020-06-04 | 23.6 | 0 | 5.6 | 2019-06-04 | 14.5 | 3.5 | 0 | 2018-06-04 | 15.9 | 2.1 | 0 | 2017-06-04 | 14.9 | 3.1 | 0 | 2016-06-04 | 26.6 | 0 | 8.6 | 0.87 | 4.94
2025-06-04 | 29.9 | 0 | 11.9 | 2024-06-04 | 29.4 | 0 | 11.4 | 2023-06-04 | 21.5 | 0 | 3.5 | 2022-06-04 | 17.9 | 0.1 | 0 | 2021-06-04 | 25.7 | 0 | 7.7 | 2020-06-04 | 23.9 | 0 | 5.9 | 2019-06-04 | 12.6 | 5.4 | 0 | 2018-06-04 | 17.4 | 0.6 | 0 | 2017-06-04 | 15.2 | 2.8 | 0 | 2016-06-04 | 25.9 | 0 | 7.9 | 0.89 | 4.83
2025-06-04 | 29.2 | 0 | 11.2 | 2024-06-04 | 28.8 | 0 | 10.8 | 2023-06-04 | 21.9 | 0 | 3.9 | 2022-06-04 | 17.2 | 0.8 | 0 | 2021-06-04 | 21.6 | 0 | 3.6 | 2020-06-04 | 25.1 | 0 | 7.1 | 2019-06-04 | 12.1 | 5.9 | 0 | 2018-06-04 | 16.9 | 1.1 | 0 | 2017-06-04 | 14.9 | 3.1 | 0 | 2016-06-04 | 24.4 | 0 | 6.4 | 1.09 | 4.3
2025-06-04 | 28.4 | 0 | 10.4 | 2024-06-04 | 27.3 | 0 | 9.3 | 2023-06-04 | 20.3 | 0 | 2.3 | 2022-06-04 | 16.6 | 1.4 | 0 | 2021-06-04 | 20.7 | 0 | 2.7 | 2020-06-04 | 24.5 | 0 | 6.5 | 2019-06-04 | 11.8 | 6.2 | 0 | 2018-06-04 | 16.5 | 1.5 | 0 | 2017-06-04 | 14.8 | 3.2 | 0 | 2016-06-04 | 24 | 0 | 6 | 1.23 | 3.72
2025-06-04 | 27.4 | 0 | 9.4 | 2024-06-04 | 25.8 | 0 | 7.8 | 2023-06-04 | 18.1 | 0 | 0.1 | 2022-06-04 | 15.2 | 2.8 | 0 | 2021-06-04 | 20.6 | 0 | 2.6 | 2020-06-04 | 21.6 | 0 | 3.6 | 2019-06-04 | 10.9 | 7.1 | 0 | 2018-06-04 | 14.1 | 3.9 | 0 | 2017-06-04 | 14.5 | 3.5 | 0 | 2016-06-04 | 22 | 0 | 4 | 1.73 | 2.75
2025-06-04 | 26.5 | 0 | 8.5 | 2024-06-04 | 22.5 | 0 | 4.5 | 2023-06-04 | 14.5 | 3.5 | 0 | 2022-06-04 | 11.6 | 6.4 | 0 | 2021-06-04 | 19.8 | 0 | 1.8 | 2020-06-04 | 20.6 | 0 | 2.6 | 2019-06-04 | 10.2 | 7.8 | 0 | 2018-06-04 | 13.2 | 4.8 | 0 | 2017-06-04 | 14.2 | 3.8 | 0 | 2016-06-04 | 19.9 | 0 | 1.9 | 2.63 | 1.93
2025-06-04 | 25 | 0 | 7 | 2024-06-04 | 21.3 | 0 | 3.3 | 2023-06-04 | 14.5 | 3.5 | 0 | 2022-06-04 | 12.2 | 5.8 | 0 | 2021-06-04 | 19.6 | 0 | 1.6 | 2020-06-04 | 18.9 | 0 | 0.9 | 2019-06-04 | 9.9 | 8.1 | 0 | 2018-06-04 | 12.9 | 5.1 | 0 | 2017-06-04 | 13.5 | 4.5 | 0 | 2016-06-04 | 19 | 0 | 1 | 2.7 | 1.38
2025-06-04 | 22.8 | 0 | 4.8 | 2024-06-04 | 22.7 | 0 | 4.7 | 2023-06-04 | 13 | 5 | 0 | 2022-06-04 | 10.5 | 7.5 | 0 | 2021-06-04 | 19.5 | 0 | 1.5 | 2020-06-04 | 17.4 | 0.6 | 0 | 2019-06-04 | 9.8 | 8.2 | 0 | 2018-06-04 | 12.4 | 5.6 | 0 | 2017-06-04 | 13.1 | 4.9 | 0 | 2016-06-04 | 17.9 | 0.1 | 0 | 3.19 | 1.1
2025-06-04 | 21.4 | 0 | 3.4 | 2024-06-04 | 20 | 0 | 2 | 2023-06-04 | 12.7 | 5.3 | 0 | 2022-06-04 | 10.4 | 7.6 | 0 | 2021-06-04 | 18.9 | 0 | 0.9 | 2020-06-04 | 17.4 | 0.6 | 0 | 2019-06-04 | 9.7 | 8.3 | 0 | 2018-06-04 | 11.6 | 6.4 | 0 | 2017-06-04 | 13.2 | 4.8 | 0 | 2016-06-04 | 17.2 | 0.8 | 0 | 3.38 | 0.63
2025-06-05 | 20.2 | 0 | 2.2 | 2024-06-05 | 19.8 | 0 | 1.8 | 2023-06-05 | 9.9 | 8.1 | 0 | 2022-06-05 | 8 | 10 | 0 | 2021-06-05 | 18 | 0 | 0 | 2020-06-05 | 16.1 | 1.9 | 0 | 2019-06-05 | 9.6 | 8.4 | 0 | 2018-06-05 | 10.6 | 7.4 | 0 | 2017-06-05 | 12.9 | 5.1 | 0 | 2016-06-05 | 16.9 | 1.1 | 0 | 4.2 | 0.4
2025-06-05 | 19.7 | 0 | 1.7 | 2024-06-05 | 18.9 | 0 | 0.9 | 2023-06-05 | 7.7 | 10.3 | 0 | 2022-06-05 | 8.1 | 9.9 | 0 | 2021-06-05 | 17.2 | 0.8 | 0 | 2020-06-05 | 16.4 | 1.6 | 0 | 2019-06-05 | 9.6 | 8.4 | 0 | 2018-06-05 | 10.2 | 7.8 | 0 | 2017-06-05 | 12.6 | 5.4 | 0 | 2016-06-05 | 15.5 | 2.5 | 0 | 4.67 | 0.26
2025-06-05 | 19.6 | 0 | 1.6 | 2024-06-05 | 18.5 | 0 | 0.5 | 2023-06-05 | 11.3 | 6.7 | 0 | 2022-06-05 | 8 | 10 | 0 | 2021-06-05 | 16.9 | 1.1 | 0 | 2020-06-05 | 15.2 | 2.8 | 0 | 2019-06-05 | 9.7 | 8.3 | 0 | 2018-06-05 | 10.6 | 7.4 | 0 | 2017-06-05 | 12.2 | 5.8 | 0 | 2016-06-05 | 15.9 | 2.1 | 0 | 4.42 | 0.21
2025-06-05 | 19.4 | 0 | 1.4 | 2024-06-05 | 18.4 | 0 | 0.4 | 2023-06-05 | 11.4 | 6.6 | 0 | 2022-06-05 | 7.3 | 10.7 | 0 | 2021-06-05 | 16.1 | 1.9 | 0 | 2020-06-05 | 12.9 | 5.1 | 0 | 2019-06-05 | 9.7 | 8.3 | 0 | 2018-06-05 | 10 | 8 | 0 | 2017-06-05 | 12.8 | 5.2 | 0 | 2016-06-05 | 15.4 | 2.6 | 0 | 4.84 | 0.18
2025-06-05 | 19 | 0 | 1 | 2024-06-05 | 18.4 | 0 | 0.4 | 2023-06-05 | 11.3 | 6.7 | 0 | 2022-06-05 | 6.6 | 11.4 | 0 | 2021-06-05 | 15.8 | 2.2 | 0 | 2020-06-05 | 12.9 | 5.1 | 0 | 2019-06-05 | 9.7 | 8.3 | 0 | 2018-06-05 | 10.6 | 7.4 | 0 | 2017-06-05 | 12.8 | 5.2 | 0 | 2016-06-05 | 15.3 | 2.7 | 0 | 4.9 | 0.14
2025-06-05 | 19.2 | 0 | 1.2 | 2024-06-05 | 18 | 0 | 0 | 2023-06-05 | 8.4 | 9.6 | 0 | 2022-06-05 | 7.2 | 10.8 | 0 | 2021-06-05 | 16.4 | 1.6 | 0 | 2020-06-05 | 13.7 | 4.3 | 0 | 2019-06-05 | 9.7 | 8.3 | 0 | 2018-06-05 | 10.7 | 7.3 | 0 | 2017-06-05 | 13.3 | 4.7 | 0 | 2016-06-05 | 15.6 | 2.4 | 0 | 4.9 | 0.12
2025-06-05 | 19.1 | 0 | 1.1 | 2024-06-05 | 19.9 | 0 | 1.9 | 2023-06-05 | 11 | 7 | 0 | 2022-06-05 | 9.5 | 8.5 | 0 | 2021-06-05 | 17.4 | 0.6 | 0 | 2020-06-05 | 15.8 | 2.2 | 0 | 2019-06-05 | 10.1 | 7.9 | 0 | 2018-06-05 | 11.1 | 6.9 | 0 | 2017-06-05 | 13.6 | 4.4 | 0 | 2016-06-05 | 15.9 | 2.1 | 0 | 3.96 | 0.3
2025-06-05 | 19.6 | 0 | 1.6 | 2024-06-05 | 21.3 | 0 | 3.3 | 2023-06-05 | 12.8 | 5.2 | 0 | 2022-06-05 | 12.4 | 5.6 | 0 | 2021-06-05 | 18.4 | 0 | 0.4 | 2020-06-05 | 17.6 | 0.4 | 0 | 2019-06-05 | 10.6 | 7.4 | 0 | 2018-06-05 | 11.9 | 6.1 | 0 | 2017-06-05 | 14.1 | 3.9 | 0 | 2016-06-05 | 14.4 | 3.6 | 0 | 3.22 | 0.53
2025-06-05 | 20.5 | 0 | 2.5 | 2024-06-05 | 24 | 0 | 6 | 2023-06-05 | 15.6 | 2.4 | 0 | 2022-06-05 | 13.9 | 4.1 | 0 | 2021-06-05 | 21.6 | 0 | 3.6 | 2020-06-05 | 20 | 0 | 2 | 2019-06-05 | 11.1 | 6.9 | 0 | 2018-06-05 | 12.3 | 5.7 | 0 | 2017-06-05 | 14.3 | 3.7 | 0 | 2016-06-05 | 14.8 | 3.2 | 0 | 2.6 | 1.41
2025-06-05 | 20.3 | 0 | 2.3 | 2024-06-05 | 25.4 | 0 | 7.4 | 2023-06-05 | 17.1 | 0.9 | 0 | 2022-06-05 | 15.6 | 2.4 | 0 | 2021-06-05 | 23.5 | 0 | 5.5 | 2020-06-05 | 21.4 | 0 | 3.4 | 2019-06-05 | 11.7 | 6.3 | 0 | 2018-06-05 | 12.8 | 5.2 | 0 | 2017-06-05 | 14.7 | 3.3 | 0 | 2016-06-05 | 15 | 3 | 0 | 2.11 | 1.86
2025-06-05 | 20.6 | 0 | 2.6 | 2024-06-05 | 26.8 | 0 | 8.8 | 2023-06-05 | 19.4 | 0 | 1.4 | 2022-06-05 | 17.1 | 0.9 | 0 | 2021-06-05 | 22.2 | 0 | 4.2 | 2020-06-05 | 23.2 | 0 | 5.2 | 2019-06-05 | 12.3 | 5.7 | 0 | 2018-06-05 | 13.1 | 4.9 | 0 | 2017-06-05 | 14.6 | 3.4 | 0 | 2016-06-05 | 14.8 | 3.2 | 0 | 1.81 | 2.22
2025-06-05 | 22 | 0 | 4 | 2024-06-05 | 28.1 | 0 | 10.1 | 2023-06-05 | 19.6 | 0 | 1.6 | 2022-06-05 | 18.5 | 0 | 0.5 | 2021-06-05 | 22.7 | 0 | 4.7 | 2020-06-05 | 25.3 | 0 | 7.3 | 2019-06-05 | 12.9 | 5.1 | 0 | 2018-06-05 | 12 | 6 | 0 | 2017-06-05 | 14.3 | 3.7 | 0 | 2016-06-05 | 15.4 | 2.6 | 0 | 1.74 | 2.82
2025-06-05 | 22.1 | 0 | 4.1 | 2024-06-05 | 28.9 | 0 | 10.9 | 2023-06-05 | 20.3 | 0 | 2.3 | 2022-06-05 | 19.7 | 0 | 1.7 | 2021-06-05 | 26.2 | 0 | 8.2 | 2020-06-05 | 26.7 | 0 | 8.7 | 2019-06-05 | 14.8 | 3.2 | 0 | 2018-06-05 | 12.8 | 5.2 | 0 | 2017-06-05 | 14 | 4 | 0 | 2016-06-05 | 16.9 | 1.1 | 0 | 1.35 | 3.59
2025-06-05 | 22.8 | 0 | 4.8 | 2024-06-05 | 29.6 | 0 | 11.6 | 2023-06-05 | 20.7 | 0 | 2.7 | 2022-06-05 | 20.5 | 0 | 2.5 | 2021-06-05 | 26.7 | 0 | 8.7 | 2020-06-05 | 27.8 | 0 | 9.8 | 2019-06-05 | 15 | 3 | 0 | 2018-06-05 | 12.3 | 5.7 | 0 | 2017-06-05 | 14.6 | 3.4 | 0 | 2016-06-05 | 18.7 | 0 | 0.7 | 1.21 | 4.08
2025-06-05 | 23.8 | 0 | 5.8 | 2024-06-05 | 30.1 | 0 | 12.1 | 2023-06-05 | 20 | 0 | 2 | 2022-06-05 | 20.9 | 0 | 2.9 | 2021-06-05 | 28.8 | 0 | 10.8 | 2020-06-05 | 28.7 | 0 | 10.7 | 2019-06-05 | 15.6 | 2.4 | 0 | 2018-06-05 | 12.8 | 5.2 | 0 | 2017-06-05 | 15 | 3 | 0 | 2016-06-05 | 20.2 | 0 | 2.2 | 1.06 | 4.65
2025-06-05 | 22.9 | 0 | 4.9 | 2024-06-05 | 30.9 | 0 | 12.9 | 2023-06-05 | 21.4 | 0 | 3.4 | 2022-06-05 | 21.8 | 0 | 3.8 | 2021-06-05 | 28 | 0 | 10 | 2020-06-05 | 27.9 | 0 | 9.9 | 2019-06-05 | 15.7 | 2.3 | 0 | 2018-06-05 | 13.7 | 4.3 | 0 | 2017-06-05 | 15.1 | 2.9 | 0 | 2016-06-05 | 20.1 | 0 | 2.1 | 0.95 | 4.7
2025-06-05 | 22 | 0 | 4 | 2024-06-05 | 30.5 | 0 | 12.5 | 2023-06-05 | 21.8 | 0 | 3.8 | 2022-06-05 | 22.2 | 0 | 4.2 | 2021-06-05 | 26.6 | 0 | 8.6 | 2020-06-05 | 28.1 | 0 | 10.1 | 2019-06-05 | 15.3 | 2.7 | 0 | 2018-06-05 | 12.4 | 5.6 | 0 | 2017-06-05 | 15.1 | 2.9 | 0 | 2016-06-05 | 19.7 | 0 | 1.7 | 1.12 | 4.49
2025-06-05 | 21.9 | 0 | 3.9 | 2024-06-05 | 29 | 0 | 11 | 2023-06-05 | 21.8 | 0 | 3.8 | 2022-06-05 | 22.2 | 0 | 4.2 | 2021-06-05 | 22.1 | 0 | 4.1 | 2020-06-05 | 28.7 | 0 | 10.7 | 2019-06-05 | 15.3 | 2.7 | 0 | 2018-06-05 | 13.4 | 4.6 | 0 | 2017-06-05 | 14.6 | 3.4 | 0 | 2016-06-05 | 19.6 | 0 | 1.6 | 1.07 | 3.93
2025-06-05 | 20.9 | 0 | 2.9 | 2024-06-05 | 28.1 | 0 | 10.1 | 2023-06-05 | 21 | 0 | 3 | 2022-06-05 | 21.4 | 0 | 3.4 | 2021-06-05 | 20.8 | 0 | 2.8 | 2020-06-05 | 23.4 | 0 | 5.4 | 2019-06-05 | 14.6 | 3.4 | 0 | 2018-06-05 | 13.8 | 4.2 | 0 | 2017-06-05 | 14.5 | 3.5 | 0 | 2016-06-05 | 18.9 | 0 | 0.9 | 1.11 | 2.85
2025-06-05 | 20.7 | 0 | 2.7 | 2024-06-05 | 26.8 | 0 | 8.8 | 2023-06-05 | 19 | 0 | 1 | 2022-06-05 | 18.2 | 0 | 0.2 | 2021-06-05 | 19.7 | 0 | 1.7 | 2020-06-05 | 18 | 0 | 0 | 2019-06-05 | 14.1 | 3.9 | 0 | 2018-06-05 | 13.7 | 4.3 | 0 | 2017-06-05 | 13.6 | 4.4 | 0 | 2016-06-05 | 18.5 | 0 | 0.5 | 1.26 | 1.49
2025-06-05 | 20 | 0 | 2 | 2024-06-05 | 25.6 | 0 | 7.6 | 2023-06-05 | 18.4 | 0 | 0.4 | 2022-06-05 | 16.1 | 1.9 | 0 | 2021-06-05 | 19.2 | 0 | 1.2 | 2020-06-05 | 18.4 | 0 | 0.4 | 2019-06-05 | 13.6 | 4.4 | 0 | 2018-06-05 | 12.3 | 5.7 | 0 | 2017-06-05 | 13.4 | 4.6 | 0 | 2016-06-05 | 18.2 | 0 | 0.2 | 1.66 | 1.18
2025-06-05 | 18.9 | 0 | 0.9 | 2024-06-05 | 23.9 | 0 | 5.9 | 2023-06-05 | 19.6 | 0 | 1.6 | 2022-06-05 | 15.7 | 2.3 | 0 | 2021-06-05 | 19.3 | 0 | 1.3 | 2020-06-05 | 17.9 | 0.1 | 0 | 2019-06-05 | 14 | 4 | 0 | 2018-06-05 | 12.4 | 5.6 | 0 | 2017-06-05 | 13.1 | 4.9 | 0 | 2016-06-05 | 18.2 | 0 | 0.2 | 1.69 | 0.99
2025-06-05 | 16.4 | 1.6 | 0 | 2024-06-05 | 23.1 | 0 | 5.1 | 2023-06-05 | 18 | 0 | 0 | 2022-06-05 | 12.8 | 5.2 | 0 | 2021-06-05 | 19.1 | 0 | 1.1 | 2020-06-05 | 17.8 | 0.2 | 0 | 2019-06-05 | 14.1 | 3.9 | 0 | 2018-06-05 | 12.2 | 5.8 | 0 | 2017-06-05 | 12.9 | 5.1 | 0 | 2016-06-05 | 18.2 | 0 | 0.2 | 2.18 | 0.64
2025-06-05 | 15.6 | 2.4 | 0 | 2024-06-05 | 22.1 | 0 | 4.1 | 2023-06-05 | 16.1 | 1.9 | 0 | 2022-06-05 | 14.5 | 3.5 | 0 | 2021-06-05 | 19.5 | 0 | 1.5 | 2020-06-05 | 18 | 0 | 0 | 2019-06-05 | 14 | 4 | 0 | 2018-06-05 | 11.9 | 6.1 | 0 | 2017-06-05 | 12.9 | 5.1 | 0 | 2016-06-05 | 18 | 0 | 0 | 2.3 | 0.56
2025-06-06 | 15.1 | 2.9 | 0 | 2024-06-06 | 22 | 0 | 4 | 2023-06-06 | 16.1 | 1.9 | 0 | 2022-06-06 | 14.8 | 3.2 | 0 | 2021-06-06 | 19.2 | 0 | 1.2 | 2020-06-06 | 17.1 | 0.9 | 0 | 2019-06-06 | 13.7 | 4.3 | 0 | 2018-06-06 | 11.7 | 6.3 | 0 | 2017-06-06 | 12.7 | 5.3 | 0 | 2016-06-06 | 17.4 | 0.6 | 0 | 2.54 | 0.52
2025-06-06 | 13.2 | 4.8 | 0 | 2024-06-06 | 22.1 | 0 | 4.1 | 2023-06-06 | 14 | 4 | 0 | 2022-06-06 | 10.8 | 7.2 | 0 | 2021-06-06 | 19.2 | 0 | 1.2 | 2020-06-06 | 16.3 | 1.7 | 0 | 2019-06-06 | 12.2 | 5.8 | 0 | 2018-06-06 | 11.2 | 6.8 | 0 | 2017-06-06 | 12.5 | 5.5 | 0 | 2016-06-06 | 17.3 | 0.7 | 0 | 3.65 | 0.53
2025-06-06 | 13 | 5 | 0 | 2024-06-06 | 22 | 0 | 4 | 2023-06-06 | 15.6 | 2.4 | 0 | 2022-06-06 | 12 | 6 | 0 | 2021-06-06 | 18.6 | 0 | 0.6 | 2020-06-06 | 17.4 | 0.6 | 0 | 2019-06-06 | 10.1 | 7.9 | 0 | 2018-06-06 | 11.3 | 6.7 | 0 | 2017-06-06 | 12.1 | 5.9 | 0 | 2016-06-06 | 16.8 | 1.2 | 0 | 3.57 | 0.46
2025-06-06 | 13.1 | 4.9 | 0 | 2024-06-06 | 21.7 | 0 | 3.7 | 2023-06-06 | 14.5 | 3.5 | 0 | 2022-06-06 | 8.6 | 9.4 | 0 | 2021-06-06 | 17.8 | 0.2 | 0 | 2020-06-06 | 17.2 | 0.8 | 0 | 2019-06-06 | 9.3 | 8.7 | 0 | 2018-06-06 | 11.3 | 6.7 | 0 | 2017-06-06 | 11.8 | 6.2 | 0 | 2016-06-06 | 16.4 | 1.6 | 0 | 4.2 | 0.37
2025-06-06 | 13.9 | 4.1 | 0 | 2024-06-06 | 20.9 | 0 | 2.9 | 2023-06-06 | 12.8 | 5.2 | 0 | 2022-06-06 | 8.5 | 9.5 | 0 | 2021-06-06 | 17.8 | 0.2 | 0 | 2020-06-06 | 16.6 | 1.4 | 0 | 2019-06-06 | 9.2 | 8.8 | 0 | 2018-06-06 | 11.9 | 6.1 | 0 | 2017-06-06 | 11.3 | 6.7 | 0 | 2016-06-06 | 16.2 | 1.8 | 0 | 4.38 | 0.29
2025-06-06 | 13 | 5 | 0 | 2024-06-06 | 20.5 | 0 | 2.5 | 2023-06-06 | 13.9 | 4.1 | 0 | 2022-06-06 | 9.5 | 8.5 | 0 | 2021-06-06 | 18.5 | 0 | 0.5 | 2020-06-06 | 14.9 | 3.1 | 0 | 2019-06-06 | 9.7 | 8.3 | 0 | 2018-06-06 | 12 | 6 | 0 | 2017-06-06 | 10.8 | 7.2 | 0 | 2016-06-06 | 16.4 | 1.6 | 0 | 4.38 | 0.3
2025-06-06 | 14.4 | 3.6 | 0 | 2024-06-06 | 20.5 | 0 | 2.5 | 2023-06-06 | 13.8 | 4.2 | 0 | 2022-06-06 | 12.1 | 5.9 | 0 | 2021-06-06 | 18.7 | 0 | 0.7 | 2020-06-06 | 16.3 | 1.7 | 0 | 2019-06-06 | 12 | 6 | 0 | 2018-06-06 | 12.1 | 5.9 | 0 | 2017-06-06 | 10.7 | 7.3 | 0 | 2016-06-06 | 16.6 | 1.4 | 0 | 3.6 | 0.32
2025-06-06 | 16.7 | 1.3 | 0 | 2024-06-06 | 20.8 | 0 | 2.8 | 2023-06-06 | 14.1 | 3.9 | 0 | 2022-06-06 | 13.4 | 4.6 | 0 | 2021-06-06 | 21.5 | 0 | 3.5 | 2020-06-06 | 18.3 | 0 | 0.3 | 2019-06-06 | 14.3 | 3.7 | 0 | 2018-06-06 | 12.4 | 5.6 | 0 | 2017-06-06 | 11.1 | 6.9 | 0 | 2016-06-06 | 17.4 | 0.6 | 0 | 2.66 | 0.66
2025-06-06 | 18.1 | 0 | 0.1 | 2024-06-06 | 21.2 | 0 | 3.2 | 2023-06-06 | 15.3 | 2.7 | 0 | 2022-06-06 | 15.8 | 2.2 | 0 | 2021-06-06 | 23.4 | 0 | 5.4 | 2020-06-06 | 19.5 | 0 | 1.5 | 2019-06-06 | 15.1 | 2.9 | 0 | 2018-06-06 | 12.8 | 5.2 | 0 | 2017-06-06 | 11.4 | 6.6 | 0 | 2016-06-06 | 18.3 | 0 | 0.3 | 1.96 | 1.05
2025-06-06 | 20.5 | 0 | 2.5 | 2024-06-06 | 20.9 | 0 | 2.9 | 2023-06-06 | 17.1 | 0.9 | 0 | 2022-06-06 | 17.9 | 0.1 | 0 | 2021-06-06 | 25.9 | 0 | 7.9 | 2020-06-06 | 21.5 | 0 | 3.5 | 2019-06-06 | 16.9 | 1.1 | 0 | 2018-06-06 | 14 | 4 | 0 | 2017-06-06 | 11.4 | 6.6 | 0 | 2016-06-06 | 17.8 | 0.2 | 0 | 1.29 | 1.68
2025-06-06 | 21.2 | 0 | 3.2 | 2024-06-06 | 20.9 | 0 | 2.9 | 2023-06-06 | 19 | 0 | 1 | 2022-06-06 | 19.7 | 0 | 1.7 | 2021-06-06 | 27.8 | 0 | 9.8 | 2020-06-06 | 22.7 | 0 | 4.7 | 2019-06-06 | 19.1 | 0 | 1.1 | 2018-06-06 | 15.3 | 2.7 | 0 | 2017-06-06 | 11.2 | 6.8 | 0 | 2016-06-06 | 18.6 | 0 | 0.6 | 0.95 | 2.5
2025-06-06 | 23.2 | 0 | 5.2 | 2024-06-06 | 21.1 | 0 | 3.1 | 2023-06-06 | 19.4 | 0 | 1.4 | 2022-06-06 | 20.1 | 0 | 2.1 | 2021-06-06 | 29.2 | 0 | 11.2 | 2020-06-06 | 23.2 | 0 | 5.2 | 2019-06-06 | 19.9 | 0 | 1.9 | 2018-06-06 | 14.4 | 3.6 | 0 | 2017-06-06 | 11 | 7 | 0 | 2016-06-06 | 19.4 | 0 | 1.4 | 1.06 | 3.15
2025-06-06 | 23.6 | 0 | 5.6 | 2024-06-06 | 20.3 | 0 | 2.3 | 2023-06-06 | 20.1 | 0 | 2.1 | 2022-06-06 | 20.6 | 0 | 2.6 | 2021-06-06 | 30.7 | 0 | 12.7 | 2020-06-06 | 24.1 | 0 | 6.1 | 2019-06-06 | 21.2 | 0 | 3.2 | 2018-06-06 | 14.8 | 3.2 | 0 | 2017-06-06 | 10.9 | 7.1 | 0 | 2016-06-06 | 21.1 | 0 | 3.1 | 1.03 | 3.77
2025-06-06 | 24.7 | 0 | 6.7 | 2024-06-06 | 22.1 | 0 | 4.1 | 2023-06-06 | 19.9 | 0 | 1.9 | 2022-06-06 | 20.5 | 0 | 2.5 | 2021-06-06 | 30.8 | 0 | 12.8 | 2020-06-06 | 23.7 | 0 | 5.7 | 2019-06-06 | 21.6 | 0 | 3.6 | 2018-06-06 | 15.2 | 2.8 | 0 | 2017-06-06 | 11.3 | 6.7 | 0 | 2016-06-06 | 22.4 | 0 | 4.4 | 0.95 | 4.17
2025-06-06 | 25.9 | 0 | 7.9 | 2024-06-06 | 21.9 | 0 | 3.9 | 2023-06-06 | 20.8 | 0 | 2.8 | 2022-06-06 | 18.8 | 0 | 0.8 | 2021-06-06 | 30.1 | 0 | 12.1 | 2020-06-06 | 19.8 | 0 | 1.8 | 2019-06-06 | 21.8 | 0 | 3.8 | 2018-06-06 | 16.4 | 1.6 | 0 | 2017-06-06 | 12.1 | 5.9 | 0 | 2016-06-06 | 22.5 | 0 | 4.5 | 0.75 | 3.76
2025-06-06 | 25.5 | 0 | 7.5 | 2024-06-06 | 17.3 | 0.7 | 0 | 2023-06-06 | 17.7 | 0.3 | 0 | 2022-06-06 | 18.8 | 0 | 0.8 | 2021-06-06 | 31.9 | 0 | 13.9 | 2020-06-06 | 18.2 | 0 | 0.2 | 2019-06-06 | 22.3 | 0 | 4.3 | 2018-06-06 | 17 | 1 | 0 | 2017-06-06 | 10.8 | 7.2 | 0 | 2016-06-06 | 21.9 | 0 | 3.9 | 0.92 | 3.06
2025-06-06 | 25.3 | 0 | 7.3 | 2024-06-06 | 17.7 | 0.3 | 0 | 2023-06-06 | 15.2 | 2.8 | 0 | 2022-06-06 | 20.2 | 0 | 2.2 | 2021-06-06 | 31.9 | 0 | 13.9 | 2020-06-06 | 20.9 | 0 | 2.9 | 2019-06-06 | 22.5 | 0 | 4.5 | 2018-06-06 | 17 | 1 | 0 | 2017-06-06 | 10.8 | 7.2 | 0 | 2016-06-06 | 22.8 | 0 | 4.8 | 1.13 | 3.56
2025-06-06 | 24.9 | 0 | 6.9 | 2024-06-06 | 18.7 | 0 | 0.7 | 2023-06-06 | 15.9 | 2.1 | 0 | 2022-06-06 | 20.6 | 0 | 2.6 | 2021-06-06 | 31.5 | 0 | 13.5 | 2020-06-06 | 18.4 | 0 | 0.4 | 2019-06-06 | 22.4 | 0 | 4.4 | 2018-06-06 | 16.9 | 1.1 | 0 | 2017-06-06 | 11.8 | 6.2 | 0 | 2016-06-06 | 22.1 | 0 | 4.1 | 0.94 | 3.26
2025-06-06 | 22.5 | 0 | 4.5 | 2024-06-06 | 18.9 | 0 | 0.9 | 2023-06-06 | 15.9 | 2.1 | 0 | 2022-06-06 | 20 | 0 | 2 | 2021-06-06 | 30.4 | 0 | 12.4 | 2020-06-06 | 18.3 | 0 | 0.3 | 2019-06-06 | 21.9 | 0 | 3.9 | 2018-06-06 | 17.1 | 0.9 | 0 | 2017-06-06 | 12.8 | 5.2 | 0 | 2016-06-06 | 21.8 | 0 | 3.8 | 0.82 | 2.78
2025-06-06 | 21.8 | 0 | 3.8 | 2024-06-06 | 19.4 | 0 | 1.4 | 2023-06-06 | 14.7 | 3.3 | 0 | 2022-06-06 | 19.5 | 0 | 1.5 | 2021-06-06 | 28.9 | 0 | 10.9 | 2020-06-06 | 17.3 | 0.7 | 0 | 2019-06-06 | 19.4 | 0 | 1.4 | 2018-06-06 | 16.2 | 1.8 | 0 | 2017-06-06 | 13.5 | 4.5 | 0 | 2016-06-06 | 19.7 | 0 | 1.7 | 1.03 | 2.07
2025-06-06 | 20.8 | 0 | 2.8 | 2024-06-06 | 17.1 | 0.9 | 0 | 2023-06-06 | 13.4 | 4.6 | 0 | 2022-06-06 | 19.4 | 0 | 1.4 | 2021-06-06 | 27.6 | 0 | 9.6 | 2020-06-06 | 16.9 | 1.1 | 0 | 2019-06-06 | 17.5 | 0.5 | 0 | 2018-06-06 | 14.2 | 3.8 | 0 | 2017-06-06 | 11.4 | 6.6 | 0 | 2016-06-06 | 18.5 | 0 | 0.5 | 1.75 | 1.43
2025-06-06 | 19.6 | 0 | 1.6 | 2024-06-06 | 17.8 | 0.2 | 0 | 2023-06-06 | 13.8 | 4.2 | 0 | 2022-06-06 | 18.4 | 0 | 0.4 | 2021-06-06 | 26.4 | 0 | 8.4 | 2020-06-06 | 16.6 | 1.4 | 0 | 2019-06-06 | 13.4 | 4.6 | 0 | 2018-06-06 | 14.3 | 3.7 | 0 | 2017-06-06 | 9.7 | 8.3 | 0 | 2016-06-06 | 17.7 | 0.3 | 0 | 2.27 | 1.04
2025-06-06 | 19.1 | 0 | 1.1 | 2024-06-06 | 17.2 | 0.8 | 0 | 2023-06-06 | 13.7 | 4.3 | 0 | 2022-06-06 | 17.8 | 0.2 | 0 | 2021-06-06 | 24.9 | 0 | 6.9 | 2020-06-06 | 15.4 | 2.6 | 0 | 2019-06-06 | 12.7 | 5.3 | 0 | 2018-06-06 | 11.3 | 6.7 | 0 | 2017-06-06 | 9.2 | 8.8 | 0 | 2016-06-06 | 18.4 | 0 | 0.4 | 2.87 | 0.84
2025-06-06 | 18.2 | 0 | 0.2 | 2024-06-06 | 17.1 | 0.9 | 0 | 2023-06-06 | 13.6 | 4.4 | 0 | 2022-06-06 | 16.2 | 1.8 | 0 | 2021-06-06 | 24.7 | 0 | 6.7 | 2020-06-06 | 15 | 3 | 0 | 2019-06-06 | 14.2 | 3.8 | 0 | 2018-06-06 | 13.1 | 4.9 | 0 | 2017-06-06 | 9.5 | 8.5 | 0 | 2016-06-06 | 17.6 | 0.4 | 0 | 2.77 | 0.69
2025-06-07 | 17.9 | 0.1 | 0 | 2024-06-07 | 16.4 | 1.6 | 0 | 2023-06-07 | 12.5 | 5.5 | 0 | 2022-06-07 | 15.4 | 2.6 | 0 | 2021-06-07 | 24.3 | 0 | 6.3 | 2020-06-07 | 13.9 | 4.1 | 0 | 2019-06-07 | 9.2 | 8.8 | 0 | 2018-06-07 | 12.7 | 5.3 | 0 | 2017-06-07 | 8.8 | 9.2 | 0 | 2016-06-07 | 16.7 | 1.3 | 0 | 3.85 | 0.63
2025-06-07 | 17.3 | 0.7 | 0 | 2024-06-07 | 15.5 | 2.5 | 0 | 2023-06-07 | 12.3 | 5.7 | 0 | 2022-06-07 | 14.9 | 3.1 | 0 | 2021-06-07 | 23.2 | 0 | 5.2 | 2020-06-07 | 13.1 | 4.9 | 0 | 2019-06-07 | 10.5 | 7.5 | 0 | 2018-06-07 | 12.2 | 5.8 | 0 | 2017-06-07 | 7.1 | 10.9 | 0 | 2016-06-07 | 15.1 | 2.9 | 0 | 4.4 | 0.52
2025-06-07 | 18.6 | 0 | 0.6 | 2024-06-07 | 15.1 | 2.9 | 0 | 2023-06-07 | 11 | 7 | 0 | 2022-06-07 | 15 | 3 | 0 | 2021-06-07 | 21.7 | 0 | 3.7 | 2020-06-07 | 12.6 | 5.4 | 0 | 2019-06-07 | 9.6 | 8.4 | 0 | 2018-06-07 | 11.6 | 6.4 | 0 | 2017-06-07 | 6.3 | 11.7 | 0 | 2016-06-07 | 13.8 | 4.2 | 0 | 4.9 | 0.43
2025-06-07 | 18 | 0 | 0 | 2024-06-07 | 14.5 | 3.5 | 0 | 2023-06-07 | 11.4 | 6.6 | 0 | 2022-06-07 | 15.3 | 2.7 | 0 | 2021-06-07 | 20.2 | 0 | 2.2 | 2020-06-07 | 11.8 | 6.2 | 0 | 2019-06-07 | 10.1 | 7.9 | 0 | 2018-06-07 | 11 | 7 | 0 | 2017-06-07 | 6.5 | 11.5 | 0 | 2016-06-07 | 12.4 | 5.6 | 0 | 5.1 | 0.22
2025-06-07 | 16.2 | 1.8 | 0 | 2024-06-07 | 13.9 | 4.1 | 0 | 2023-06-07 | 10.5 | 7.5 | 0 | 2022-06-07 | 15.2 | 2.8 | 0 | 2021-06-07 | 19.5 | 0 | 1.5 | 2020-06-07 | 11 | 7 | 0 | 2019-06-07 | 8.6 | 9.4 | 0 | 2018-06-07 | 10.6 | 7.4 | 0 | 2017-06-07 | 5.9 | 12.1 | 0 | 2016-06-07 | 12.2 | 5.8 | 0 | 5.79 | 0.15
2025-06-07 | 16.1 | 1.9 | 0 | 2024-06-07 | 14.6 | 3.4 | 0 | 2023-06-07 | 11.5 | 6.5 | 0 | 2022-06-07 | 15.3 | 2.7 | 0 | 2021-06-07 | 19.1 | 0 | 1.1 | 2020-06-07 | 11.1 | 6.9 | 0 | 2019-06-07 | 7.7 | 10.3 | 0 | 2018-06-07 | 10.7 | 7.3 | 0 | 2017-06-07 | 6.8 | 11.2 | 0 | 2016-06-07 | 12.5 | 5.5 | 0 | 5.57 | 0.11
2025-06-07 | 18.1 | 0 | 0.1 | 2024-06-07 | 14.7 | 3.3 | 0 | 2023-06-07 | 12.3 | 5.7 | 0 | 2022-06-07 | 15.4 | 2.6 | 0 | 2021-06-07 | 21.5 | 0 | 3.5 | 2020-06-07 | 12.4 | 5.6 | 0 | 2019-06-07 | 10.2 | 7.8 | 0 | 2018-06-07 | 11.5 | 6.5 | 0 | 2017-06-07 | 9.6 | 8.4 | 0 | 2016-06-07 | 14.4 | 3.6 | 0 | 4.35 | 0.36
2025-06-07 | 18.2 | 0 | 0.2 | 2024-06-07 | 15.7 | 2.3 | 0 | 2023-06-07 | 13.3 | 4.7 | 0 | 2022-06-07 | 15.6 | 2.4 | 0 | 2021-06-07 | 23.8 | 0 | 5.8 | 2020-06-07 | 14 | 4 | 0 | 2019-06-07 | 13.7 | 4.3 | 0 | 2018-06-07 | 12.5 | 5.5 | 0 | 2017-06-07 | 12.5 | 5.5 | 0 | 2016-06-07 | 15.5 | 2.5 | 0 | 3.12 | 0.6
2025-06-07 | 19.3 | 0 | 1.3 | 2024-06-07 | 18 | 0 | 0 | 2023-06-07 | 14.1 | 3.9 | 0 | 2022-06-07 | 16 | 2 | 0 | 2021-06-07 | 25.6 | 0 | 7.6 | 2020-06-07 | 15.4 | 2.6 | 0 | 2019-06-07 | 16.9 | 1.1 | 0 | 2018-06-07 | 14.3 | 3.7 | 0 | 2017-06-07 | 14.4 | 3.6 | 0 | 2016-06-07 | 16.5 | 1.5 | 0 | 1.84 | 0.89
2025-06-07 | 21 | 0 | 3 | 2024-06-07 | 18 | 0 | 0 | 2023-06-07 | 13.4 | 4.6 | 0 | 2022-06-07 | 16.9 | 1.1 | 0 | 2021-06-07 | 28 | 0 | 10 | 2020-06-07 | 17.2 | 0.8 | 0 | 2019-06-07 | 19.6 | 0 | 1.6 | 2018-06-07 | 16.1 | 1.9 | 0 | 2017-06-07 | 15.5 | 2.5 | 0 | 2016-06-07 | 17.4 | 0.6 | 0 | 1.15 | 1.46
2025-06-07 | 22.6 | 0 | 4.6 | 2024-06-07 | 18 | 0 | 0 | 2023-06-07 | 14.8 | 3.2 | 0 | 2022-06-07 | 17.8 | 0.2 | 0 | 2021-06-07 | 29.7 | 0 | 11.7 | 2020-06-07 | 18.8 | 0 | 0.8 | 2019-06-07 | 20.8 | 0 | 2.8 | 2018-06-07 | 17.8 | 0.2 | 0 | 2017-06-07 | 17.5 | 0.5 | 0 | 2016-06-07 | 19.5 | 0 | 1.5 | 0.41 | 2.14
2025-06-07 | 23.7 | 0 | 5.7 | 2024-06-07 | 15.4 | 2.6 | 0 | 2023-06-07 | 15.4 | 2.6 | 0 | 2022-06-07 | 18.5 | 0 | 0.5 | 2021-06-07 | 30.9 | 0 | 12.9 | 2020-06-07 | 19.5 | 0 | 1.5 | 2019-06-07 | 22.4 | 0 | 4.4 | 2018-06-07 | 17.6 | 0.4 | 0 | 2017-06-07 | 20 | 0 | 2 | 2016-06-07 | 18.6 | 0 | 0.6 | 0.56 | 2.76
2025-06-07 | 24.3 | 0 | 6.3 | 2024-06-07 | 16.6 | 1.4 | 0 | 2023-06-07 | 15.5 | 2.5 | 0 | 2022-06-07 | 18.3 | 0 | 0.3 | 2021-06-07 | 32.5 | 0 | 14.5 | 2020-06-07 | 19.3 | 0 | 1.3 | 2019-06-07 | 23.6 | 0 | 5.6 | 2018-06-07 | 19.8 | 0 | 1.8 | 2017-06-07 | 21.8 | 0 | 3.8 | 2016-06-07 | 20.7 | 0 | 2.7 | 0.39 | 3.63
2025-06-07 | 24.6 | 0 | 6.6 | 2024-06-07 | 17.6 | 0.4 | 0 | 2023-06-07 | 14.9 | 3.1 | 0 | 2022-06-07 | 18.5 | 0 | 0.5 | 2021-06-07 | 32.5 | 0 | 14.5 | 2020-06-07 | 20.4 | 0 | 2.4 | 2019-06-07 | 24 | 0 | 6 | 2018-06-07 | 19.9 | 0 | 1.9 | 2017-06-07 | 23.2 | 0 | 5.2 | 2016-06-07 | 21.8 | 0 | 3.8 | 0.35 | 4.09
2025-06-07 | 25.3 | 0 | 7.3 | 2024-06-07 | 18.2 | 0 | 0.2 | 2023-06-07 | 15.4 | 2.6 | 0 | 2022-06-07 | 18.7 | 0 | 0.7 | 2021-06-07 | 32.9 | 0 | 14.9 | 2020-06-07 | 20.1 | 0 | 2.1 | 2019-06-07 | 24.4 | 0 | 6.4 | 2018-06-07 | 19.7 | 0 | 1.7 | 2017-06-07 | 24.4 | 0 | 6.4 | 2016-06-07 | 15.8 | 2.2 | 0 | 0.48 | 3.97
2025-06-07 | 25 | 0 | 7 | 2024-06-07 | 16.1 | 1.9 | 0 | 2023-06-07 | 15.4 | 2.6 | 0 | 2022-06-07 | 17.4 | 0.6 | 0 | 2021-06-07 | 31.6 | 0 | 13.6 | 2020-06-07 | 19.5 | 0 | 1.5 | 2019-06-07 | 25.2 | 0 | 7.2 | 2018-06-07 | 20.9 | 0 | 2.9 | 2017-06-07 | 25.2 | 0 | 7.2 | 2016-06-07 | 15.2 | 2.8 | 0 | 0.79 | 3.94
2025-06-07 | 23.8 | 0 | 5.8 | 2024-06-07 | 17.6 | 0.4 | 0 | 2023-06-07 | 15.8 | 2.2 | 0 | 2022-06-07 | 17 | 1 | 0 | 2021-06-07 | 30.9 | 0 | 12.9 | 2020-06-07 | 21.2 | 0 | 3.2 | 2019-06-07 | 25.5 | 0 | 7.5 | 2018-06-07 | 20.1 | 0 | 2.1 | 2017-06-07 | 25.5 | 0 | 7.5 | 2016-06-07 | 15.7 | 2.3 | 0 | 0.59 | 3.9
2025-06-07 | 22.7 | 0 | 4.7 | 2024-06-07 | 17.9 | 0.1 | 0 | 2023-06-07 | 15.5 | 2.5 | 0 | 2022-06-07 | 17.1 | 0.9 | 0 | 2021-06-07 | 29.5 | 0 | 11.5 | 2020-06-07 | 20.7 | 0 | 2.7 | 2019-06-07 | 24.1 | 0 | 6.1 | 2018-06-07 | 21.1 | 0 | 3.1 | 2017-06-07 | 25.1 | 0 | 7.1 | 2016-06-07 | 16 | 2 | 0 | 0.55 | 3.52
2025-06-07 | 21.9 | 0 | 3.9 | 2024-06-07 | 15.8 | 2.2 | 0 | 2023-06-07 | 14.1 | 3.9 | 0 | 2022-06-07 | 17.4 | 0.6 | 0 | 2021-06-07 | 29.4 | 0 | 11.4 | 2020-06-07 | 20 | 0 | 2 | 2019-06-07 | 24 | 0 | 6 | 2018-06-07 | 20.5 | 0 | 2.5 | 2017-06-07 | 24.1 | 0 | 6.1 | 2016-06-07 | 15.1 | 2.9 | 0 | 0.96 | 3.19
2025-06-07 | 20.5 | 0 | 2.5 | 2024-06-07 | 14.9 | 3.1 | 0 | 2023-06-07 | 13.2 | 4.8 | 0 | 2022-06-07 | 17.4 | 0.6 | 0 | 2021-06-07 | 28.1 | 0 | 10.1 | 2020-06-07 | 19 | 0 | 1 | 2019-06-07 | 22.7 | 0 | 4.7 | 2018-06-07 | 19.2 | 0 | 1.2 | 2017-06-07 | 21.5 | 0 | 3.5 | 2016-06-07 | 14.7 | 3.3 | 0 | 1.18 | 2.3
2025-06-07 | 18.9 | 0 | 0.9 | 2024-06-07 | 14 | 4 | 0 | 2023-06-07 | 12.6 | 5.4 | 0 | 2022-06-07 | 17.4 | 0.6 | 0 | 2021-06-07 | 27.3 | 0 | 9.3 | 2020-06-07 | 17.3 | 0.7 | 0 | 2019-06-07 | 21.1 | 0 | 3.1 | 2018-06-07 | 17.3 | 0.7 | 0 | 2017-06-07 | 19.7 | 0 | 1.7 | 2016-06-07 | 14.9 | 3.1 | 0 | 1.45 | 1.5
2025-06-07 | 17.5 | 0.5 | 0 | 2024-06-07 | 14 | 4 | 0 | 2023-06-07 | 13.3 | 4.7 | 0 | 2022-06-07 | 17.5 | 0.5 | 0 | 2021-06-07 | 26.4 | 0 | 8.4 | 2020-06-07 | 16.6 | 1.4 | 0 | 2019-06-07 | 18.6 | 0 | 0.6 | 2018-06-07 | 15.8 | 2.2 | 0 | 2017-06-07 | 18.6 | 0 | 0.6 | 2016-06-07 | 14.1 | 3.9 | 0 | 1.72 | 0.96
2025-06-07 | 17.1 | 0.9 | 0 | 2024-06-07 | 13.9 | 4.1 | 0 | 2023-06-07 | 12.7 | 5.3 | 0 | 2022-06-07 | 17.5 | 0.5 | 0 | 2021-06-07 | 25.5 | 0 | 7.5 | 2020-06-07 | 15.7 | 2.3 | 0 | 2019-06-07 | 16.8 | 1.2 | 0 | 2018-06-07 | 14.7 | 3.3 | 0 | 2017-06-07 | 16.9 | 1.1 | 0 | 2016-06-07 | 13.7 | 4.3 | 0 | 2.3 | 0.75
2025-06-07 | 16 | 2 | 0 | 2024-06-07 | 14.1 | 3.9 | 0 | 2023-06-07 | 12.3 | 5.7 | 0 | 2022-06-07 | 16.8 | 1.2 | 0 | 2021-06-07 | 24.1 | 0 | 6.1 | 2020-06-07 | 15.1 | 2.9 | 0 | 2019-06-07 | 15.8 | 2.2 | 0 | 2018-06-07 | 14.3 | 3.7 | 0 | 2017-06-07 | 15.5 | 2.5 | 0 | 2016-06-07 | 12.6 | 5.4 | 0 | 2.95 | 0.61
2025-06-08 | 15.5 | 2.5 | 0 | 2024-06-08 | 13.9 | 4.1 | 0 | 2023-06-08 | 12.3 | 5.7 | 0 | 2022-06-08 | 15.7 | 2.3 | 0 | 2021-06-08 | 23.6 | 0 | 5.6 | 2020-06-08 | 14 | 4 | 0 | 2019-06-08 | 14.9 | 3.1 | 0 | 2018-06-08 | 15.3 | 2.7 | 0 | 2017-06-08 | 14.3 | 3.7 | 0 | 2016-06-08 | 11.7 | 6.3 | 0 | 3.44 | 0.56
2025-06-08 | 14.6 | 3.4 | 0 | 2024-06-08 | 13.4 | 4.6 | 0 | 2023-06-08 | 12.1 | 5.9 | 0 | 2022-06-08 | 15.4 | 2.6 | 0 | 2021-06-08 | 22 | 0 | 4 | 2020-06-08 | 13.3 | 4.7 | 0 | 2019-06-08 | 14.2 | 3.8 | 0 | 2018-06-08 | 13.3 | 4.7 | 0 | 2017-06-08 | 13.2 | 4.8 | 0 | 2016-06-08 | 10.4 | 7.6 | 0 | 4.21 | 0.4
2025-06-08 | 12.9 | 5.1 | 0 | 2024-06-08 | 13.2 | 4.8 | 0 | 2023-06-08 | 11.4 | 6.6 | 0 | 2022-06-08 | 15 | 3 | 0 | 2021-06-08 | 21.9 | 0 | 3.9 | 2020-06-08 | 12.1 | 5.9 | 0 | 2019-06-08 | 12.1 | 5.9 | 0 | 2018-06-08 | 13.7 | 4.3 | 0 | 2017-06-08 | 12.5 | 5.5 | 0 | 2016-06-08 | 11 | 7 | 0 | 4.81 | 0.39
2025-06-08 | 12.1 | 5.9 | 0 | 2024-06-08 | 12.9 | 5.1 | 0 | 2023-06-08 | 11.6 | 6.4 | 0 | 2022-06-08 | 14.8 | 3.2 | 0 | 2021-06-08 | 21.7 | 0 | 3.7 | 2020-06-08 | 10.4 | 7.6 | 0 | 2019-06-08 | 11.4 | 6.6 | 0 | 2018-06-08 | 13.8 | 4.2 | 0 | 2017-06-08 | 12 | 6 | 0 | 2016-06-08 | 9.7 | 8.3 | 0 | 5.33 | 0.37
2025-06-08 | 11.9 | 6.1 | 0 | 2024-06-08 | 13 | 5 | 0 | 2023-06-08 | 11.5 | 6.5 | 0 | 2022-06-08 | 14.7 | 3.3 | 0 | 2021-06-08 | 21.7 | 0 | 3.7 | 2020-06-08 | 10.3 | 7.7 | 0 | 2019-06-08 | 11.3 | 6.7 | 0 | 2018-06-08 | 12.1 | 5.9 | 0 | 2017-06-08 | 11.7 | 6.3 | 0 | 2016-06-08 | 9.2 | 8.8 | 0 | 5.63 | 0.37
2025-06-08 | 10.5 | 7.5 | 0 | 2024-06-08 | 13.3 | 4.7 | 0 | 2023-06-08 | 11.6 | 6.4 | 0 | 2022-06-08 | 14.6 | 3.4 | 0 | 2021-06-08 | 22 | 0 | 4 | 2020-06-08 | 9.6 | 8.4 | 0 | 2019-06-08 | 10.6 | 7.4 | 0 | 2018-06-08 | 11.3 | 6.7 | 0 | 2017-06-08 | 12 | 6 | 0 | 2016-06-08 | 8.9 | 9.1 | 0 | 5.96 | 0.4
2025-06-08 | 12.8 | 5.2 | 0 | 2024-06-08 | 13.8 | 4.2 | 0 | 2023-06-08 | 12.8 | 5.2 | 0 | 2022-06-08 | 14.6 | 3.4 | 0 | 2021-06-08 | 22.6 | 0 | 4.6 | 2020-06-08 | 12.6 | 5.4 | 0 | 2019-06-08 | 13.5 | 4.5 | 0 | 2018-06-08 | 14 | 4 | 0 | 2017-06-08 | 14.6 | 3.4 | 0 | 2016-06-08 | 9.1 | 8.9 | 0 | 4.42 | 0.46
2025-06-08 | 15.4 | 2.6 | 0 | 2024-06-08 | 14.9 | 3.1 | 0 | 2023-06-08 | 13.4 | 4.6 | 0 | 2022-06-08 | 16.2 | 1.8 | 0 | 2021-06-08 | 24.9 | 0 | 6.9 | 2020-06-08 | 14.4 | 3.6 | 0 | 2019-06-08 | 15.8 | 2.2 | 0 | 2018-06-08 | 15.6 | 2.4 | 0 | 2017-06-08 | 17.4 | 0.6 | 0 | 2016-06-08 | 9.7 | 8.3 | 0 | 2.92 | 0.69
2025-06-08 | 17.7 | 0.3 | 0 | 2024-06-08 | 16 | 2 | 0 | 2023-06-08 | 13.6 | 4.4 | 0 | 2022-06-08 | 16.6 | 1.4 | 0 | 2021-06-08 | 25.9 | 0 | 7.9 | 2020-06-08 | 15.9 | 2.1 | 0 | 2019-06-08 | 17.7 | 0.3 | 0 | 2018-06-08 | 17.1 | 0.9 | 0 | 2017-06-08 | 19.8 | 0 | 1.8 | 2016-06-08 | 10.1 | 7.9 | 0 | 1.93 | 0.97
2025-06-08 | 19.6 | 0 | 1.6 | 2024-06-08 | 17.1 | 0.9 | 0 | 2023-06-08 | 14.4 | 3.6 | 0 | 2022-06-08 | 18.4 | 0 | 0.4 | 2021-06-08 | 28.4 | 0 | 10.4 | 2020-06-08 | 16.7 | 1.3 | 0 | 2019-06-08 | 18.9 | 0 | 0.9 | 2018-06-08 | 18.1 | 0 | 0.1 | 2017-06-08 | 22.2 | 0 | 4.2 | 2016-06-08 | 11.8 | 6.2 | 0 | 1.2 | 1.76
2025-06-08 | 21.6 | 0 | 3.6 | 2024-06-08 | 18 | 0 | 0 | 2023-06-08 | 14.4 | 3.6 | 0 | 2022-06-08 | 19.6 | 0 | 1.6 | 2021-06-08 | 28.8 | 0 | 10.8 | 2020-06-08 | 18 | 0 | 0 | 2019-06-08 | 21.1 | 0 | 3.1 | 2018-06-08 | 18.6 | 0 | 0.6 | 2017-06-08 | 24.2 | 0 | 6.2 | 2016-06-08 | 11 | 7 | 0 | 1.06 | 2.59
2025-06-08 | 22.9 | 0 | 4.9 | 2024-06-08 | 18.4 | 0 | 0.4 | 2023-06-08 | 16.5 | 1.5 | 0 | 2022-06-08 | 20.4 | 0 | 2.4 | 2021-06-08 | 30.1 | 0 | 12.1 | 2020-06-08 | 18.9 | 0 | 0.9 | 2019-06-08 | 21.9 | 0 | 3.9 | 2018-06-08 | 19.6 | 0 | 1.6 | 2017-06-08 | 26.2 | 0 | 8.2 | 2016-06-08 | 12.2 | 5.8 | 0 | 0.73 | 3.44
2025-06-08 | 23.5 | 0 | 5.5 | 2024-06-08 | 17.9 | 0.1 | 0 | 2023-06-08 | 15.2 | 2.8 | 0 | 2022-06-08 | 21.5 | 0 | 3.5 | 2021-06-08 | 29.7 | 0 | 11.7 | 2020-06-08 | 20.2 | 0 | 2.2 | 2019-06-08 | 22.4 | 0 | 4.4 | 2018-06-08 | 20.8 | 0 | 2.8 | 2017-06-08 | 26.9 | 0 | 8.9 | 2016-06-08 | 12.3 | 5.7 | 0 | 0.86 | 3.9
2025-06-08 | 23.9 | 0 | 5.9 | 2024-06-08 | 19.3 | 0 | 1.3 | 2023-06-08 | 16.1 | 1.9 | 0 | 2022-06-08 | 22.2 | 0 | 4.2 | 2021-06-08 | 29.3 | 0 | 11.3 | 2020-06-08 | 20.5 | 0 | 2.5 | 2019-06-08 | 23.4 | 0 | 5.4 | 2018-06-08 | 21 | 0 | 3 | 2017-06-08 | 26.9 | 0 | 8.9 | 2016-06-08 | 12 | 6 | 0 | 0.79 | 4.25
2025-06-08 | 24.4 | 0 | 6.4 | 2024-06-08 | 18.1 | 0 | 0.1 | 2023-06-08 | 16.1 | 1.9 | 0 | 2022-06-08 | 23 | 0 | 5 | 2021-06-08 | 29.5 | 0 | 11.5 | 2020-06-08 | 21.5 | 0 | 3.5 | 2019-06-08 | 24.8 | 0 | 6.8 | 2018-06-08 | 21.6 | 0 | 3.6 | 2017-06-08 | 27.2 | 0 | 9.2 | 2016-06-08 | 12.1 | 5.9 | 0 | 0.78 | 4.61
2025-06-08 | 23.6 | 0 | 5.6 | 2024-06-08 | 19.1 | 0 | 1.1 | 2023-06-08 | 16.3 | 1.7 | 0 | 2022-06-08 | 23.4 | 0 | 5.4 | 2021-06-08 | 29.8 | 0 | 11.8 | 2020-06-08 | 22.1 | 0 | 4.1 | 2019-06-08 | 25.3 | 0 | 7.3 | 2018-06-08 | 22.2 | 0 | 4.2 | 2017-06-08 | 27.6 | 0 | 9.6 | 2016-06-08 | 12 | 6 | 0 | 0.77 | 4.91
2025-06-08 | 23.4 | 0 | 5.4 | 2024-06-08 | 17.6 | 0.4 | 0 | 2023-06-08 | 16.5 | 1.5 | 0 | 2022-06-08 | 23.6 | 0 | 5.6 | 2021-06-08 | 30.5 | 0 | 12.5 | 2020-06-08 | 21.4 | 0 | 3.4 | 2019-06-08 | 25.7 | 0 | 7.7 | 2018-06-08 | 22.5 | 0 | 4.5 | 2017-06-08 | 26.9 | 0 | 8.9 | 2016-06-08 | 12.2 | 5.8 | 0 | 0.77 | 4.8
2025-06-08 | 23.1 | 0 | 5.1 | 2024-06-08 | 18.9 | 0 | 0.9 | 2023-06-08 | 16.9 | 1.1 | 0 | 2022-06-08 | 23.2 | 0 | 5.2 | 2021-06-08 | 29.7 | 0 | 11.7 | 2020-06-08 | 21.3 | 0 | 3.3 | 2019-06-08 | 25.1 | 0 | 7.1 | 2018-06-08 | 21.9 | 0 | 3.9 | 2017-06-08 | 26.6 | 0 | 8.6 | 2016-06-08 | 12.4 | 5.6 | 0 | 0.67 | 4.58
2025-06-08 | 21.6 | 0 | 3.6 | 2024-06-08 | 18.5 | 0 | 0.5 | 2023-06-08 | 13.7 | 4.3 | 0 | 2022-06-08 | 22.9 | 0 | 4.9 | 2021-06-08 | 27.9 | 0 | 9.9 | 2020-06-08 | 20.9 | 0 | 2.9 | 2019-06-08 | 23.8 | 0 | 5.8 | 2018-06-08 | 21.3 | 0 | 3.3 | 2017-06-08 | 25.5 | 0 | 7.5 | 2016-06-08 | 11.4 | 6.6 | 0 | 1.09 | 3.84
2025-06-08 | 20.8 | 0 | 2.8 | 2024-06-08 | 17.7 | 0.3 | 0 | 2023-06-08 | 14.2 | 3.8 | 0 | 2022-06-08 | 19.9 | 0 | 1.9 | 2021-06-08 | 27.1 | 0 | 9.1 | 2020-06-08 | 20.3 | 0 | 2.3 | 2019-06-08 | 22.1 | 0 | 4.1 | 2018-06-08 | 19.8 | 0 | 1.8 | 2017-06-08 | 23.9 | 0 | 5.9 | 2016-06-08 | 11.3 | 6.7 | 0 | 1.08 | 2.79
2025-06-08 | 19.1 | 0 | 1.1 | 2024-06-08 | 16.6 | 1.4 | 0 | 2023-06-08 | 13.2 | 4.8 | 0 | 2022-06-08 | 18.6 | 0 | 0.6 | 2021-06-08 | 25.4 | 0 | 7.4 | 2020-06-08 | 18.9 | 0 | 0.9 | 2019-06-08 | 20.8 | 0 | 2.8 | 2018-06-08 | 17.7 | 0.3 | 0 | 2017-06-08 | 21.1 | 0 | 3.1 | 2016-06-08 | 10.8 | 7.2 | 0 | 1.37 | 1.59
2025-06-08 | 18.7 | 0 | 0.7 | 2024-06-08 | 16.3 | 1.7 | 0 | 2023-06-08 | 13.3 | 4.7 | 0 | 2022-06-08 | 16.5 | 1.5 | 0 | 2021-06-08 | 24.2 | 0 | 6.2 | 2020-06-08 | 17.7 | 0.3 | 0 | 2019-06-08 | 16.1 | 1.9 | 0 | 2018-06-08 | 15 | 3 | 0 | 2017-06-08 | 20.5 | 0 | 2.5 | 2016-06-08 | 10.3 | 7.7 | 0 | 2.08 | 0.94
2025-06-08 | 17.1 | 0.9 | 0 | 2024-06-08 | 16 | 2 | 0 | 2023-06-08 | 13.1 | 4.9 | 0 | 2022-06-08 | 16.2 | 1.8 | 0 | 2021-06-08 | 23.4 | 0 | 5.4 | 2020-06-08 | 17.7 | 0.3 | 0 | 2019-06-08 | 16.3 | 1.7 | 0 | 2018-06-08 | 15.9 | 2.1 | 0 | 2017-06-08 | 19.5 | 0 | 1.5 | 2016-06-08 | 10.1 | 7.9 | 0 | 2.16 | 0.69
2025-06-08 | 16.7 | 1.3 | 0 | 2024-06-08 | 15.3 | 2.7 | 0 | 2023-06-08 | 12 | 6 | 0 | 2022-06-08 | 15.8 | 2.2 | 0 | 2021-06-08 | 23 | 0 | 5 | 2020-06-08 | 16.9 | 1.1 | 0 | 2019-06-08 | 14.1 | 3.9 | 0 | 2018-06-08 | 14.2 | 3.8 | 0 | 2017-06-08 | 17.8 | 0.2 | 0 | 2016-06-08 | 9.3 | 8.7 | 0 | 2.99 | 0.5
2025-06-09 | 16.1 | 1.9 | 0 | 2024-06-09 | 14.8 | 3.2 | 0 | 2023-06-09 | 10.2 | 7.8 | 0 | 2022-06-09 | 15.8 | 2.2 | 0 | 2021-06-09 | 22.6 | 0 | 4.6 | 2020-06-09 | 16.3 | 1.7 | 0 | 2019-06-09 | 15.6 | 2.4 | 0 | 2018-06-09 | 13 | 5 | 0 | 2017-06-09 | 17.6 | 0.4 | 0 | 2016-06-09 | 8.8 | 9.2 | 0 | 3.38 | 0.46
2025-06-09 | 15.8 | 2.2 | 0 | 2024-06-09 | 14.4 | 3.6 | 0 | 2023-06-09 | 9.6 | 8.4 | 0 | 2022-06-09 | 15 | 3 | 0 | 2021-06-09 | 22.1 | 0 | 4.1 | 2020-06-09 | 16.3 | 1.7 | 0 | 2019-06-09 | 12.2 | 5.8 | 0 | 2018-06-09 | 12.2 | 5.8 | 0 | 2017-06-09 | 16.3 | 1.7 | 0 | 2016-06-09 | 8.9 | 9.1 | 0 | 4.13 | 0.41
2025-06-09 | 16.5 | 1.5 | 0 | 2024-06-09 | 13.9 | 4.1 | 0 | 2023-06-09 | 9.8 | 8.2 | 0 | 2022-06-09 | 14.4 | 3.6 | 0 | 2021-06-09 | 22.4 | 0 | 4.4 | 2020-06-09 | 15.9 | 2.1 | 0 | 2019-06-09 | 12.3 | 5.7 | 0 | 2018-06-09 | 11.9 | 6.1 | 0 | 2017-06-09 | 15.4 | 2.6 | 0 | 2016-06-09 | 8.6 | 9.4 | 0 | 4.33 | 0.44
2025-06-09 | 16.8 | 1.2 | 0 | 2024-06-09 | 13.7 | 4.3 | 0 | 2023-06-09 | 10.3 | 7.7 | 0 | 2022-06-09 | 14.1 | 3.9 | 0 | 2021-06-09 | 23.1 | 0 | 5.1 | 2020-06-09 | 15.8 | 2.2 | 0 | 2019-06-09 | 10.6 | 7.4 | 0 | 2018-06-09 | 10.7 | 7.3 | 0 | 2017-06-09 | 13.9 | 4.1 | 0 | 2016-06-09 | 7.9 | 10.1 | 0 | 4.82 | 0.51
2025-06-09 | 16.5 | 1.5 | 0 | 2024-06-09 | 13.4 | 4.6 | 0 | 2023-06-09 | 10.6 | 7.4 | 0 | 2022-06-09 | 14.1 | 3.9 | 0 | 2021-06-09 | 22.2 | 0 | 4.2 | 2020-06-09 | 14.2 | 3.8 | 0 | 2019-06-09 | 10.5 | 7.5 | 0 | 2018-06-09 | 8.8 | 9.2 | 0 | 2017-06-09 | 13.9 | 4.1 | 0 | 2016-06-09 | 7.7 | 10.3 | 0 | 5.23 | 0.42
2025-06-09 | 16.6 | 1.4 | 0 | 2024-06-09 | 13.2 | 4.8 | 0 | 2023-06-09 | 10.7 | 7.3 | 0 | 2022-06-09 | 13.5 | 4.5 | 0 | 2021-06-09 | 22.1 | 0 | 4.1 | 2020-06-09 | 13.6 | 4.4 | 0 | 2019-06-09 | 10.8 | 7.2 | 0 | 2018-06-09 | 11.1 | 6.9 | 0 | 2017-06-09 | 14.8 | 3.2 | 0 | 2016-06-09 | 7.3 | 10.7 | 0 | 5.04 | 0.41
2025-06-09 | 17.5 | 0.5 | 0 | 2024-06-09 | 13.1 | 4.9 | 0 | 2023-06-09 | 11.1 | 6.9 | 0 | 2022-06-09 | 13.2 | 4.8 | 0 | 2021-06-09 | 22.4 | 0 | 4.4 | 2020-06-09 | 12.8 | 5.2 | 0 | 2019-06-09 | 15 | 3 | 0 | 2018-06-09 | 14.1 | 3.9 | 0 | 2017-06-09 | 16.2 | 1.8 | 0 | 2016-06-09 | 8 | 10 | 0 | 4.1 | 0.44
2025-06-09 | 18.7 | 0 | 0.7 | 2024-06-09 | 13.6 | 4.4 | 0 | 2023-06-09 | 12.3 | 5.7 | 0 | 2022-06-09 | 13.4 | 4.6 | 0 | 2021-06-09 | 23.1 | 0 | 5.1 | 2020-06-09 | 13.5 | 4.5 | 0 | 2019-06-09 | 17.3 | 0.7 | 0 | 2018-06-09 | 16.1 | 1.9 | 0 | 2017-06-09 | 17.2 | 0.8 | 0 | 2016-06-09 | 8.5 | 9.5 | 0 | 3.21 | 0.58
2025-06-09 | 16.9 | 1.1 | 0 | 2024-06-09 | 14.5 | 3.5 | 0 | 2023-06-09 | 13.2 | 4.8 | 0 | 2022-06-09 | 13.6 | 4.4 | 0 | 2021-06-09 | 24.2 | 0 | 6.2 | 2020-06-09 | 14.7 | 3.3 | 0 | 2019-06-09 | 19.7 | 0 | 1.7 | 2018-06-09 | 17.8 | 0.2 | 0 | 2017-06-09 | 18.6 | 0 | 0.6 | 2016-06-09 | 9.6 | 8.4 | 0 | 2.57 | 0.85
2025-06-09 | 16.6 | 1.4 | 0 | 2024-06-09 | 15.5 | 2.5 | 0 | 2023-06-09 | 14.2 | 3.8 | 0 | 2022-06-09 | 13.6 | 4.4 | 0 | 2021-06-09 | 25.5 | 0 | 7.5 | 2020-06-09 | 15.6 | 2.4 | 0 | 2019-06-09 | 21.9 | 0 | 3.9 | 2018-06-09 | 19.3 | 0 | 1.3 | 2017-06-09 | 20 | 0 | 2 | 2016-06-09 | 10 | 8 | 0 | 2.25 | 1.47
2025-06-09 | 16.4 | 1.6 | 0 | 2024-06-09 | 16.9 | 1.1 | 0 | 2023-06-09 | 16.1 | 1.9 | 0 | 2022-06-09 | 14 | 4 | 0 | 2021-06-09 | 26.9 | 0 | 8.9 | 2020-06-09 | 17.7 | 0.3 | 0 | 2019-06-09 | 24.9 | 0 | 6.9 | 2018-06-09 | 19.6 | 0 | 1.6 | 2017-06-09 | 20.6 | 0 | 2.6 | 2016-06-09 | 11.2 | 6.8 | 0 | 1.57 | 2
2025-06-09 | 16.4 | 1.6 | 0 | 2024-06-09 | 17.5 | 0.5 | 0 | 2023-06-09 | 16.1 | 1.9 | 0 | 2022-06-09 | 13.7 | 4.3 | 0 | 2021-06-09 | 27.6 | 0 | 9.6 | 2020-06-09 | 17.9 | 0.1 | 0 | 2019-06-09 | 26.6 | 0 | 8.6 | 2018-06-09 | 20.5 | 0 | 2.5 | 2017-06-09 | 22.1 | 0 | 4.1 | 2016-06-09 | 14.1 | 3.9 | 0 | 1.23 | 2.48
2025-06-09 | 16.6 | 1.4 | 0 | 2024-06-09 | 15.9 | 2.1 | 0 | 2023-06-09 | 16.7 | 1.3 | 0 | 2022-06-09 | 14.5 | 3.5 | 0 | 2021-06-09 | 27.7 | 0 | 9.7 | 2020-06-09 | 18.8 | 0 | 0.8 | 2019-06-09 | 27.9 | 0 | 9.9 | 2018-06-09 | 21.4 | 0 | 3.4 | 2017-06-09 | 21.9 | 0 | 3.9 | 2016-06-09 | 14.8 | 3.2 | 0 | 1.15 | 2.77
2025-06-09 | 16.8 | 1.2 | 0 | 2024-06-09 | 13.4 | 4.6 | 0 | 2023-06-09 | 17.8 | 0.2 | 0 | 2022-06-09 | 16.7 | 1.3 | 0 | 2021-06-09 | 27.9 | 0 | 9.9 | 2020-06-09 | 19.7 | 0 | 1.7 | 2019-06-09 | 28.8 | 0 | 10.8 | 2018-06-09 | 22.2 | 0 | 4.2 | 2017-06-09 | 22.5 | 0 | 4.5 | 2016-06-09 | 15.9 | 2.1 | 0 | 0.94 | 3.11
2025-06-09 | 17.5 | 0.5 | 0 | 2024-06-09 | 17.8 | 0.2 | 0 | 2023-06-09 | 17.1 | 0.9 | 0 | 2022-06-09 | 17.4 | 0.6 | 0 | 2021-06-09 | 28.6 | 0 | 10.6 | 2020-06-09 | 20.6 | 0 | 2.6 | 2019-06-09 | 29.2 | 0 | 11.2 | 2018-06-09 | 23.2 | 0 | 5.2 | 2017-06-09 | 23.4 | 0 | 5.4 | 2016-06-09 | 17.3 | 0.7 | 0 | 0.29 | 3.5
2025-06-09 | 18.2 | 0 | 0.2 | 2024-06-09 | 17.8 | 0.2 | 0 | 2023-06-09 | 17.9 | 0.1 | 0 | 2022-06-09 | 17.8 | 0.2 | 0 | 2021-06-09 | 28.8 | 0 | 10.8 | 2020-06-09 | 20.5 | 0 | 2.5 | 2019-06-09 | 29.2 | 0 | 11.2 | 2018-06-09 | 23.4 | 0 | 5.4 | 2017-06-09 | 23 | 0 | 5 | 2016-06-09 | 18.1 | 0 | 0.1 | 0.05 | 3.52
2025-06-09 | 18.1 | 0 | 0.1 | 2024-06-09 | 15.4 | 2.6 | 0 | 2023-06-09 | 18.1 | 0 | 0.1 | 2022-06-09 | 18.4 | 0 | 0.4 | 2021-06-09 | 28.4 | 0 | 10.4 | 2020-06-09 | 21 | 0 | 3 | 2019-06-09 | 29.6 | 0 | 11.6 | 2018-06-09 | 23.2 | 0 | 5.2 | 2017-06-09 | 23 | 0 | 5 | 2016-06-09 | 17 | 1 | 0 | 0.36 | 3.58
2025-06-09 | 17.7 | 0.3 | 0 | 2024-06-09 | 17.6 | 0.4 | 0 | 2023-06-09 | 19.1 | 0 | 1.1 | 2022-06-09 | 17.8 | 0.2 | 0 | 2021-06-09 | 27.6 | 0 | 9.6 | 2020-06-09 | 21.3 | 0 | 3.3 | 2019-06-09 | 29.5 | 0 | 11.5 | 2018-06-09 | 23.1 | 0 | 5.1 | 2017-06-09 | 22.5 | 0 | 4.5 | 2016-06-09 | 17.8 | 0.2 | 0 | 0.11 | 3.51
2025-06-09 | 18.6 | 0 | 0.6 | 2024-06-09 | 16.8 | 1.2 | 0 | 2023-06-09 | 18.4 | 0 | 0.4 | 2022-06-09 | 17.2 | 0.8 | 0 | 2021-06-09 | 26.4 | 0 | 8.4 | 2020-06-09 | 20.8 | 0 | 2.8 | 2019-06-09 | 28.6 | 0 | 10.6 | 2018-06-09 | 22.1 | 0 | 4.1 | 2017-06-09 | 22.2 | 0 | 4.2 | 2016-06-09 | 16.8 | 1.2 | 0 | 0.32 | 3.11
2025-06-09 | 18.6 | 0 | 0.6 | 2024-06-09 | 16 | 2 | 0 | 2023-06-09 | 16.9 | 1.1 | 0 | 2022-06-09 | 15.8 | 2.2 | 0 | 2021-06-09 | 25 | 0 | 7 | 2020-06-09 | 19.7 | 0 | 1.7 | 2019-06-09 | 26.1 | 0 | 8.1 | 2018-06-09 | 20.4 | 0 | 2.4 | 2017-06-09 | 20.7 | 0 | 2.7 | 2016-06-09 | 15.6 | 2.4 | 0 | 0.77 | 2.25
2025-06-09 | 18.3 | 0 | 0.3 | 2024-06-09 | 14.3 | 3.7 | 0 | 2023-06-09 | 14.2 | 3.8 | 0 | 2022-06-09 | 15.3 | 2.7 | 0 | 2021-06-09 | 23.1 | 0 | 5.1 | 2020-06-09 | 18 | 0 | 0 | 2019-06-09 | 24.6 | 0 | 6.6 | 2018-06-09 | 18.5 | 0 | 0.5 | 2017-06-09 | 17.2 | 0.8 | 0 | 2016-06-09 | 14.9 | 3.1 | 0 | 1.41 | 1.25
2025-06-09 | 17.9 | 0.1 | 0 | 2024-06-09 | 14.7 | 3.3 | 0 | 2023-06-09 | 15 | 3 | 0 | 2022-06-09 | 14.6 | 3.4 | 0 | 2021-06-09 | 21.7 | 0 | 3.7 | 2020-06-09 | 16.3 | 1.7 | 0 | 2019-06-09 | 19.8 | 0 | 1.8 | 2018-06-09 | 15.1 | 2.9 | 0 | 2017-06-09 | 18.1 | 0 | 0.1 | 2016-06-09 | 14.1 | 3.9 | 0 | 1.83 | 0.56
2025-06-09 | 17.9 | 0.1 | 0 | 2024-06-09 | 14 | 4 | 0 | 2023-06-09 | 14.4 | 3.6 | 0 | 2022-06-09 | 13.6 | 4.4 | 0 | 2021-06-09 | 20.8 | 0 | 2.8 | 2020-06-09 | 15.9 | 2.1 | 0 | 2019-06-09 | 19.9 | 0 | 1.9 | 2018-06-09 | 13.8 | 4.2 | 0 | 2017-06-09 | 17.2 | 0.8 | 0 | 2016-06-09 | 13.3 | 4.7 | 0 | 2.39 | 0.47
2025-06-09 | 17.8 | 0.2 | 0 | 2024-06-09 | 14.2 | 3.8 | 0 | 2023-06-09 | 13.1 | 4.9 | 0 | 2022-06-09 | 13.3 | 4.7 | 0 | 2021-06-09 | 19.9 | 0 | 1.9 | 2020-06-09 | 15.7 | 2.3 | 0 | 2019-06-09 | 17.4 | 0.6 | 0 | 2018-06-09 | 12.2 | 5.8 | 0 | 2017-06-09 | 14.3 | 3.7 | 0 | 2016-06-09 | 12.3 | 5.7 | 0 | 3.17 | 0.19
2025-06-10 | 17.5 | 0.5 | 0 | 2024-06-10 | 13.9 | 4.1 | 0 | 2023-06-10 | 12.1 | 5.9 | 0 | 2022-06-10 | 13.4 | 4.6 | 0 | 2021-06-10 | 18.8 | 0 | 0.8 | 2020-06-10 | 15.2 | 2.8 | 0 | 2019-06-10 | 18.4 | 0 | 0.4 | 2018-06-10 | 11.2 | 6.8 | 0 | 2017-06-10 | 14.2 | 3.8 | 0 | 2016-06-10 | 10.9 | 7.1 | 0 | 3.56 | 0.12
2025-06-10 | 16.9 | 1.1 | 0 | 2024-06-10 | 14 | 4 | 0 | 2023-06-10 | 10.7 | 7.3 | 0 | 2022-06-10 | 13.6 | 4.4 | 0 | 2021-06-10 | 17.6 | 0.4 | 0 | 2020-06-10 | 15.7 | 2.3 | 0 | 2019-06-10 | 17.9 | 0.1 | 0 | 2018-06-10 | 8 | 10 | 0 | 2017-06-10 | 14.7 | 3.3 | 0 | 2016-06-10 | 10.3 | 7.7 | 0 | 4.06 | 0
2025-06-10 | 16.6 | 1.4 | 0 | 2024-06-10 | 14.1 | 3.9 | 0 | 2023-06-10 | 10.8 | 7.2 | 0 | 2022-06-10 | 13.1 | 4.9 | 0 | 2021-06-10 | 16 | 2 | 0 | 2020-06-10 | 15.1 | 2.9 | 0 | 2019-06-10 | 17 | 1 | 0 | 2018-06-10 | 10.8 | 7.2 | 0 | 2017-06-10 | 14.7 | 3.3 | 0 | 2016-06-10 | 9.5 | 8.5 | 0 | 4.23 | 0
2025-06-10 | 16.9 | 1.1 | 0 | 2024-06-10 | 14 | 4 | 0 | 2023-06-10 | 10 | 8 | 0 | 2022-06-10 | 13 | 5 | 0 | 2021-06-10 | 15.1 | 2.9 | 0 | 2020-06-10 | 14.4 | 3.6 | 0 | 2019-06-10 | 15.9 | 2.1 | 0 | 2018-06-10 | 11.7 | 6.3 | 0 | 2017-06-10 | 12.3 | 5.7 | 0 | 2016-06-10 | 8.3 | 9.7 | 0 | 4.84 | 0
2025-06-10 | 16.9 | 1.1 | 0 | 2024-06-10 | 11.3 | 6.7 | 0 | 2023-06-10 | 9.3 | 8.7 | 0 | 2022-06-10 | 12.4 | 5.6 | 0 | 2021-06-10 | 13.4 | 4.6 | 0 | 2020-06-10 | 14.3 | 3.7 | 0 | 2019-06-10 | 15.1 | 2.9 | 0 | 2018-06-10 | 8.2 | 9.8 | 0 | 2017-06-10 | 13.6 | 4.4 | 0 | 2016-06-10 | 8.4 | 9.6 | 0 | 5.71 | 0
2025-06-10 | 16.6 | 1.4 | 0 | 2024-06-10 | 10.5 | 7.5 | 0 | 2023-06-10 | 10.5 | 7.5 | 0 | 2022-06-10 | 12.2 | 5.8 | 0 | 2021-06-10 | 13.7 | 4.3 | 0 | 2020-06-10 | 14.1 | 3.9 | 0 | 2019-06-10 | 15.6 | 2.4 | 0 | 2018-06-10 | 11.8 | 6.2 | 0 | 2017-06-10 | 12.8 | 5.2 | 0 | 2016-06-10 | 8.3 | 9.7 | 0 | 5.39 | 0
2025-06-10 | 17.3 | 0.7 | 0 | 2024-06-10 | 10.4 | 7.6 | 0 | 2023-06-10 | 12.6 | 5.4 | 0 | 2022-06-10 | 12.4 | 5.6 | 0 | 2021-06-10 | 15.5 | 2.5 | 0 | 2020-06-10 | 15.5 | 2.5 | 0 | 2019-06-10 | 17.4 | 0.6 | 0 | 2018-06-10 | 13.3 | 4.7 | 0 | 2017-06-10 | 13.7 | 4.3 | 0 | 2016-06-10 | 9.4 | 8.6 | 0 | 4.25 | 0
2025-06-10 | 18.1 | 0 | 0.1 | 2024-06-10 | 10.5 | 7.5 | 0 | 2023-06-10 | 13.8 | 4.2 | 0 | 2022-06-10 | 14.3 | 3.7 | 0 | 2021-06-10 | 16.1 | 1.9 | 0 | 2020-06-10 | 16.4 | 1.6 | 0 | 2019-06-10 | 19.4 | 0 | 1.4 | 2018-06-10 | 15.1 | 2.9 | 0 | 2017-06-10 | 15.7 | 2.3 | 0 | 2016-06-10 | 10 | 8 | 0 | 3.21 | 0.15
2025-06-10 | 19.6 | 0 | 1.6 | 2024-06-10 | 11.1 | 6.9 | 0 | 2023-06-10 | 15.3 | 2.7 | 0 | 2022-06-10 | 15.4 | 2.6 | 0 | 2021-06-10 | 17.4 | 0.6 | 0 | 2020-06-10 | 17.8 | 0.2 | 0 | 2019-06-10 | 20.7 | 0 | 2.7 | 2018-06-10 | 16.3 | 1.7 | 0 | 2017-06-10 | 17.8 | 0.2 | 0 | 2016-06-10 | 11 | 7 | 0 | 2.19 | 0.43
2025-06-10 | 21 | 0 | 3 | 2024-06-10 | 11.6 | 6.4 | 0 | 2023-06-10 | 17.5 | 0.5 | 0 | 2022-06-10 | 15.7 | 2.3 | 0 | 2021-06-10 | 18 | 0 | 0 | 2020-06-10 | 18.2 | 0 | 0.2 | 2019-06-10 | 21.2 | 0 | 3.2 | 2018-06-10 | 17.9 | 0.1 | 0 | 2017-06-10 | 19.7 | 0 | 1.7 | 2016-06-10 | 12.1 | 5.9 | 0 | 1.52 | 0.81
2025-06-10 | 22.4 | 0 | 4.4 | 2024-06-10 | 12.6 | 5.4 | 0 | 2023-06-10 | 18.8 | 0 | 0.8 | 2022-06-10 | 16.8 | 1.2 | 0 | 2021-06-10 | 19.4 | 0 | 1.4 | 2020-06-10 | 19 | 0 | 1 | 2019-06-10 | 22.9 | 0 | 4.9 | 2018-06-10 | 18.5 | 0 | 0.5 | 2017-06-10 | 20.8 | 0 | 2.8 | 2016-06-10 | 13.6 | 4.4 | 0 | 1.1 | 1.58
2025-06-10 | 21.3 | 0 | 3.3 | 2024-06-10 | 12.7 | 5.3 | 0 | 2023-06-10 | 20.2 | 0 | 2.2 | 2022-06-10 | 17.8 | 0.2 | 0 | 2021-06-10 | 20.2 | 0 | 2.2 | 2020-06-10 | 18.8 | 0 | 0.8 | 2019-06-10 | 26.9 | 0 | 8.9 | 2018-06-10 | 19.3 | 0 | 1.3 | 2017-06-10 | 22.9 | 0 | 4.9 | 2016-06-10 | 14.6 | 3.4 | 0 | 0.89 | 2.36
2025-06-10 | 22.6 | 0 | 4.6 | 2024-06-10 | 13.6 | 4.4 | 0 | 2023-06-10 | 20.5 | 0 | 2.5 | 2022-06-10 | 18.7 | 0 | 0.7 | 2021-06-10 | 20.3 | 0 | 2.3 | 2020-06-10 | 20.4 | 0 | 2.4 | 2019-06-10 | 26.6 | 0 | 8.6 | 2018-06-10 | 19.6 | 0 | 1.6 | 2017-06-10 | 23.6 | 0 | 5.6 | 2016-06-10 | 16.2 | 1.8 | 0 | 0.62 | 2.83
2025-06-10 | 23.5 | 0 | 5.5 | 2024-06-10 | 14.1 | 3.9 | 0 | 2023-06-10 | 22.1 | 0 | 4.1 | 2022-06-10 | 19.9 | 0 | 1.9 | 2021-06-10 | 21.6 | 0 | 3.6 | 2020-06-10 | 23.8 | 0 | 5.8 | 2019-06-10 | 26.9 | 0 | 8.9 | 2018-06-10 | 21.2 | 0 | 3.2 | 2017-06-10 | 24.9 | 0 | 6.9 | 2016-06-10 | 17.5 | 0.5 | 0 | 0.44 | 3.99
2025-06-10 | 23.9 | 0 | 5.9 | 2024-06-10 | 13.7 | 4.3 | 0 | 2023-06-10 | 21.6 | 0 | 3.6 | 2022-06-10 | 18 | 0 | 0 | 2021-06-10 | 22.5 | 0 | 4.5 | 2020-06-10 | 26.3 | 0 | 8.3 | 2019-06-10 | 27 | 0 | 9 | 2018-06-10 | 21.7 | 0 | 3.7 | 2017-06-10 | 25.8 | 0 | 7.8 | 2016-06-10 | 17.8 | 0.2 | 0 | 0.45 | 4.28
2025-06-10 | 22.6 | 0 | 4.6 | 2024-06-10 | 13.3 | 4.7 | 0 | 2023-06-10 | 22.2 | 0 | 4.2 | 2022-06-10 | 20.7 | 0 | 2.7 | 2021-06-10 | 23.2 | 0 | 5.2 | 2020-06-10 | 27.4 | 0 | 9.4 | 2019-06-10 | 26.5 | 0 | 8.5 | 2018-06-10 | 21.5 | 0 | 3.5 | 2017-06-10 | 26.2 | 0 | 8.2 | 2016-06-10 | 18.8 | 0 | 0.8 | 0.47 | 4.71
2025-06-10 | 23 | 0 | 5 | 2024-06-10 | 13.2 | 4.8 | 0 | 2023-06-10 | 23.5 | 0 | 5.5 | 2022-06-10 | 20.8 | 0 | 2.8 | 2021-06-10 | 23.4 | 0 | 5.4 | 2020-06-10 | 28.9 | 0 | 10.9 | 2019-06-10 | 25 | 0 | 7 | 2018-06-10 | 21.7 | 0 | 3.7 | 2017-06-10 | 25.4 | 0 | 7.4 | 2016-06-10 | 19 | 0 | 1 | 0.48 | 4.87
2025-06-10 | 22.3 | 0 | 4.3 | 2024-06-10 | 12.8 | 5.2 | 0 | 2023-06-10 | 23.6 | 0 | 5.6 | 2022-06-10 | 20.9 | 0 | 2.9 | 2021-06-10 | 22.9 | 0 | 4.9 | 2020-06-10 | 28.3 | 0 | 10.3 | 2019-06-10 | 23.4 | 0 | 5.4 | 2018-06-10 | 21.4 | 0 | 3.4 | 2017-06-10 | 24.6 | 0 | 6.6 | 2016-06-10 | 19.1 | 0 | 1.1 | 0.52 | 4.45
2025-06-10 | 20.6 | 0 | 2.6 | 2024-06-10 | 12.3 | 5.7 | 0 | 2023-06-10 | 22.9 | 0 | 4.9 | 2022-06-10 | 19.4 | 0 | 1.4 | 2021-06-10 | 22.6 | 0 | 4.6 | 2020-06-10 | 28.3 | 0 | 10.3 | 2019-06-10 | 18.6 | 0 | 0.6 | 2018-06-10 | 20.7 | 0 | 2.7 | 2017-06-10 | 23.4 | 0 | 5.4 | 2016-06-10 | 19.3 | 0 | 1.3 | 0.57 | 3.38
2025-06-10 | 19.1 | 0 | 1.1 | 2024-06-10 | 11.8 | 6.2 | 0 | 2023-06-10 | 21.1 | 0 | 3.1 | 2022-06-10 | 19.4 | 0 | 1.4 | 2021-06-10 | 19.8 | 0 | 1.8 | 2020-06-10 | 26.7 | 0 | 8.7 | 2019-06-10 | 17 | 1 | 0 | 2018-06-10 | 19.8 | 0 | 1.8 | 2017-06-10 | 23.3 | 0 | 5.3 | 2016-06-10 | 18.1 | 0 | 0.1 | 0.72 | 2.33
2025-06-10 | 17.5 | 0.5 | 0 | 2024-06-10 | 11.2 | 6.8 | 0 | 2023-06-10 | 19.1 | 0 | 1.1 | 2022-06-10 | 17.2 | 0.8 | 0 | 2021-06-10 | 19.4 | 0 | 1.4 | 2020-06-10 | 26.2 | 0 | 8.2 | 2019-06-10 | 16.8 | 1.2 | 0 | 2018-06-10 | 18.1 | 0 | 0.1 | 2017-06-10 | 22.3 | 0 | 4.3 | 2016-06-10 | 16.2 | 1.8 | 0 | 1.11 | 1.51
2025-06-10 | 16.4 | 1.6 | 0 | 2024-06-10 | 10.8 | 7.2 | 0 | 2023-06-10 | 18 | 0 | 0 | 2022-06-10 | 14.6 | 3.4 | 0 | 2021-06-10 | 19 | 0 | 1 | 2020-06-10 | 25.9 | 0 | 7.9 | 2019-06-10 | 16.3 | 1.7 | 0 | 2018-06-10 | 16.1 | 1.9 | 0 | 2017-06-10 | 21.4 | 0 | 3.4 | 2016-06-10 | 11.4 | 6.6 | 0 | 2.24 | 1.23
2025-06-10 | 15.8 | 2.2 | 0 | 2024-06-10 | 10.3 | 7.7 | 0 | 2023-06-10 | 16.3 | 1.7 | 0 | 2022-06-10 | 13.2 | 4.8 | 0 | 2021-06-10 | 17.6 | 0.4 | 0 | 2020-06-10 | 25.8 | 0 | 7.8 | 2019-06-10 | 15.8 | 2.2 | 0 | 2018-06-10 | 15.4 | 2.6 | 0 | 2017-06-10 | 21.1 | 0 | 3.1 | 2016-06-10 | 9.8 | 8.2 | 0 | 2.98 | 1.09
2025-06-10 | 15.4 | 2.6 | 0 | 2024-06-10 | 10.1 | 7.9 | 0 | 2023-06-10 | 14.3 | 3.7 | 0 | 2022-06-10 | 12.7 | 5.3 | 0 | 2021-06-10 | 18 | 0 | 0 | 2020-06-10 | 24.1 | 0 | 6.1 | 2019-06-10 | 15.4 | 2.6 | 0 | 2018-06-10 | 14.5 | 3.5 | 0 | 2017-06-10 | 20.9 | 0 | 2.9 | 2016-06-10 | 9.7 | 8.3 | 0 | 3.39 | 0.9
2025-06-11 | 14.1 | 3.9 | 0 | 2024-06-11 | 10 | 8 | 0 | 2023-06-11 | 14.4 | 3.6 | 0 | 2022-06-11 | 13.1 | 4.9 | 0 | 2021-06-11 | 16.3 | 1.7 | 0 | 2020-06-11 | 22.8 | 0 | 4.8 | 2019-06-11 | 15.4 | 2.6 | 0 | 2018-06-11 | 13.5 | 4.5 | 0 | 2017-06-11 | 20.9 | 0 | 2.9 | 2016-06-11 | 10.6 | 7.4 | 0 | 3.66 | 0.77
2025-06-11 | 13.2 | 4.8 | 0 | 2024-06-11 | 9.5 | 8.5 | 0 | 2023-06-11 | 12.7 | 5.3 | 0 | 2022-06-11 | 11.6 | 6.4 | 0 | 2021-06-11 | 15.3 | 2.7 | 0 | 2020-06-11 | 21 | 0 | 3 | 2019-06-11 | 15.8 | 2.2 | 0 | 2018-06-11 | 12.7 | 5.3 | 0 | 2017-06-11 | 20.7 | 0 | 2.7 | 2016-06-11 | 9.7 | 8.3 | 0 | 4.35 | 0.57
2025-06-11 | 12.7 | 5.3 | 0 | 2024-06-11 | 9.3 | 8.7 | 0 | 2023-06-11 | 12.1 | 5.9 | 0 | 2022-06-11 | 10.8 | 7.2 | 0 | 2021-06-11 | 14.3 | 3.7 | 0 | 2020-06-11 | 20.6 | 0 | 2.6 | 2019-06-11 | 15.9 | 2.1 | 0 | 2018-06-11 | 9.7 | 8.3 | 0 | 2017-06-11 | 20.5 | 0 | 2.5 | 2016-06-11 | 9.7 | 8.3 | 0 | 4.95 | 0.51
2025-06-11 | 12.1 | 5.9 | 0 | 2024-06-11 | 9 | 9 | 0 | 2023-06-11 | 11.8 | 6.2 | 0 | 2022-06-11 | 10.7 | 7.3 | 0 | 2021-06-11 | 14.1 | 3.9 | 0 | 2020-06-11 | 20.2 | 0 | 2.2 | 2019-06-11 | 16.6 | 1.4 | 0 | 2018-06-11 | 8.6 | 9.4 | 0 | 2017-06-11 | 20.1 | 0 | 2.1 | 2016-06-11 | 9.6 | 8.4 | 0 | 5.15 | 0.43
2025-06-11 | 12.2 | 5.8 | 0 | 2024-06-11 | 9.1 | 8.9 | 0 | 2023-06-11 | 11.4 | 6.6 | 0 | 2022-06-11 | 10.5 | 7.5 | 0 | 2021-06-11 | 13.4 | 4.6 | 0 | 2020-06-11 | 19.5 | 0 | 1.5 | 2019-06-11 | 15.5 | 2.5 | 0 | 2018-06-11 | 8.2 | 9.8 | 0 | 2017-06-11 | 21.2 | 0 | 3.2 | 2016-06-11 | 9.6 | 8.4 | 0 | 5.41 | 0.47
2025-06-11 | 12.4 | 5.6 | 0 | 2024-06-11 | 9.5 | 8.5 | 0 | 2023-06-11 | 12.6 | 5.4 | 0 | 2022-06-11 | 10.8 | 7.2 | 0 | 2021-06-11 | 14 | 4 | 0 | 2020-06-11 | 19.4 | 0 | 1.4 | 2019-06-11 | 14.6 | 3.4 | 0 | 2018-06-11 | 9.1 | 8.9 | 0 | 2017-06-11 | 21.7 | 0 | 3.7 | 2016-06-11 | 10.2 | 7.8 | 0 | 5.08 | 0.51
2025-06-11 | 13.8 | 4.2 | 0 | 2024-06-11 | 9.9 | 8.1 | 0 | 2023-06-11 | 13.8 | 4.2 | 0 | 2022-06-11 | 12.4 | 5.6 | 0 | 2021-06-11 | 14.9 | 3.1 | 0 | 2020-06-11 | 20.6 | 0 | 2.6 | 2019-06-11 | 13.6 | 4.4 | 0 | 2018-06-11 | 12.1 | 5.9 | 0 | 2017-06-11 | 22.1 | 0 | 4.1 | 2016-06-11 | 11.6 | 6.4 | 0 | 4.19 | 0.67
2025-06-11 | 16 | 2 | 0 | 2024-06-11 | 10.4 | 7.6 | 0 | 2023-06-11 | 16.2 | 1.8 | 0 | 2022-06-11 | 14.8 | 3.2 | 0 | 2021-06-11 | 15.9 | 2.1 | 0 | 2020-06-11 | 21.5 | 0 | 3.5 | 2019-06-11 | 13.4 | 4.6 | 0 | 2018-06-11 | 14.1 | 3.9 | 0 | 2017-06-11 | 23.7 | 0 | 5.7 | 2016-06-11 | 11 | 7 | 0 | 3.22 | 0.92
2025-06-11 | 17.8 | 0.2 | 0 | 2024-06-11 | 11.2 | 6.8 | 0 | 2023-06-11 | 18.7 | 0 | 0.7 | 2022-06-11 | 17.3 | 0.7 | 0 | 2021-06-11 | 17.8 | 0.2 | 0 | 2020-06-11 | 22.5 | 0 | 4.5 | 2019-06-11 | 14.3 | 3.7 | 0 | 2018-06-11 | 16.4 | 1.6 | 0 | 2017-06-11 | 24.5 | 0 | 6.5 | 2016-06-11 | 9.9 | 8.1 | 0 | 2.13 | 1.17
2025-06-11 | 19.6 | 0 | 1.6 | 2024-06-11 | 12.3 | 5.7 | 0 | 2023-06-11 | 19.9 | 0 | 1.9 | 2022-06-11 | 19.6 | 0 | 1.6 | 2021-06-11 | 19.6 | 0 | 1.6 | 2020-06-11 | 22.3 | 0 | 4.3 | 2019-06-11 | 14.6 | 3.4 | 0 | 2018-06-11 | 18 | 0 | 0 | 2017-06-11 | 26.6 | 0 | 8.6 | 2016-06-11 | 10 | 8 | 0 | 1.71 | 1.96
2025-06-11 | 20.9 | 0 | 2.9 | 2024-06-11 | 13.3 | 4.7 | 0 | 2023-06-11 | 20.7 | 0 | 2.7 | 2022-06-11 | 21.4 | 0 | 3.4 | 2021-06-11 | 20.4 | 0 | 2.4 | 2020-06-11 | 22 | 0 | 4 | 2019-06-11 | 15 | 3 | 0 | 2018-06-11 | 19 | 0 | 1 | 2017-06-11 | 27.8 | 0 | 9.8 | 2016-06-11 | 11 | 7 | 0 | 1.47 | 2.62
2025-06-11 | 21.8 | 0 | 3.8 | 2024-06-11 | 14.6 | 3.4 | 0 | 2023-06-11 | 21.7 | 0 | 3.7 | 2022-06-11 | 22.4 | 0 | 4.4 | 2021-06-11 | 22.6 | 0 | 4.6 | 2020-06-11 | 21.1 | 0 | 3.1 | 2019-06-11 | 15.9 | 2.1 | 0 | 2018-06-11 | 19.5 | 0 | 1.5 | 2017-06-11 | 28.9 | 0 | 10.9 | 2016-06-11 | 11.8 | 6.2 | 0 | 1.17 | 3.2
2025-06-11 | 21.6 | 0 | 3.6 | 2024-06-11 | 14.8 | 3.2 | 0 | 2023-06-11 | 22.2 | 0 | 4.2 | 2022-06-11 | 22.8 | 0 | 4.8 | 2021-06-11 | 23.1 | 0 | 5.1 | 2020-06-11 | 22.7 | 0 | 4.7 | 2019-06-11 | 16.4 | 1.6 | 0 | 2018-06-11 | 20.8 | 0 | 2.8 | 2017-06-11 | 30.5 | 0 | 12.5 | 2016-06-11 | 12.3 | 5.7 | 0 | 1.05 | 3.77
2025-06-11 | 23.1 | 0 | 5.1 | 2024-06-11 | 15 | 3 | 0 | 2023-06-11 | 22.5 | 0 | 4.5 | 2022-06-11 | 22.7 | 0 | 4.7 | 2021-06-11 | 23.3 | 0 | 5.3 | 2020-06-11 | 23.1 | 0 | 5.1 | 2019-06-11 | 17.6 | 0.4 | 0 | 2018-06-11 | 21.2 | 0 | 3.2 | 2017-06-11 | 31.2 | 0 | 13.2 | 2016-06-11 | 13.1 | 4.9 | 0 | 0.83 | 4.11
2025-06-11 | 23.8 | 0 | 5.8 | 2024-06-11 | 15.3 | 2.7 | 0 | 2023-06-11 | 22.8 | 0 | 4.8 | 2022-06-11 | 23.6 | 0 | 5.6 | 2021-06-11 | 23.1 | 0 | 5.1 | 2020-06-11 | 21.3 | 0 | 3.3 | 2019-06-11 | 18.6 | 0 | 0.6 | 2018-06-11 | 21.5 | 0 | 3.5 | 2017-06-11 | 32.2 | 0 | 14.2 | 2016-06-11 | 13.6 | 4.4 | 0 | 0.71 | 4.29
2025-06-11 | 24.4 | 0 | 6.4 | 2024-06-11 | 15.8 | 2.2 | 0 | 2023-06-11 | 22.7 | 0 | 4.7 | 2022-06-11 | 24.6 | 0 | 6.6 | 2021-06-11 | 23.3 | 0 | 5.3 | 2020-06-11 | 22 | 0 | 4 | 2019-06-11 | 19.7 | 0 | 1.7 | 2018-06-11 | 22.3 | 0 | 4.3 | 2017-06-11 | 30.8 | 0 | 12.8 | 2016-06-11 | 13.2 | 4.8 | 0 | 0.7 | 4.58
2025-06-11 | 23.1 | 0 | 5.1 | 2024-06-11 | 15.8 | 2.2 | 0 | 2023-06-11 | 21.2 | 0 | 3.2 | 2022-06-11 | 23.1 | 0 | 5.1 | 2021-06-11 | 23.7 | 0 | 5.7 | 2020-06-11 | 22.6 | 0 | 4.6 | 2019-06-11 | 20.2 | 0 | 2.2 | 2018-06-11 | 22.3 | 0 | 4.3 | 2017-06-11 | 32.4 | 0 | 14.4 | 2016-06-11 | 13.1 | 4.9 | 0 | 0.71 | 4.46
2025-06-11 | 22.3 | 0 | 4.3 | 2024-06-11 | 15.5 | 2.5 | 0 | 2023-06-11 | 20.1 | 0 | 2.1 | 2022-06-11 | 20.6 | 0 | 2.6 | 2021-06-11 | 24.1 | 0 | 6.1 | 2020-06-11 | 21.8 | 0 | 3.8 | 2019-06-11 | 20.2 | 0 | 2.2 | 2018-06-11 | 22.4 | 0 | 4.4 | 2017-06-11 | 30.4 | 0 | 12.4 | 2016-06-11 | 13.2 | 4.8 | 0 | 0.73 | 3.79
2025-06-11 | 20.8 | 0 | 2.8 | 2024-06-11 | 15.4 | 2.6 | 0 | 2023-06-11 | 19.2 | 0 | 1.2 | 2022-06-11 | 21 | 0 | 3 | 2021-06-11 | 23.5 | 0 | 5.5 | 2020-06-11 | 20.9 | 0 | 2.9 | 2019-06-11 | 19.2 | 0 | 1.2 | 2018-06-11 | 22 | 0 | 4 | 2017-06-11 | 29.1 | 0 | 11.1 | 2016-06-11 | 13.2 | 4.8 | 0 | 0.74 | 3.17
2025-06-11 | 20.7 | 0 | 2.7 | 2024-06-11 | 15.2 | 2.8 | 0 | 2023-06-11 | 19.1 | 0 | 1.1 | 2022-06-11 | 18.8 | 0 | 0.8 | 2021-06-11 | 21.5 | 0 | 3.5 | 2020-06-11 | 20 | 0 | 2 | 2019-06-11 | 18.1 | 0 | 0.1 | 2018-06-11 | 19.7 | 0 | 1.7 | 2017-06-11 | 28 | 0 | 10 | 2016-06-11 | 13.4 | 4.6 | 0 | 0.74 | 2.19
2025-06-11 | 19.8 | 0 | 1.8 | 2024-06-11 | 14.5 | 3.5 | 0 | 2023-06-11 | 17.8 | 0.2 | 0 | 2022-06-11 | 17 | 1 | 0 | 2021-06-11 | 18.6 | 0 | 0.6 | 2020-06-11 | 17.4 | 0.6 | 0 | 2019-06-11 | 13.5 | 4.5 | 0 | 2018-06-11 | 19.1 | 0 | 1.1 | 2017-06-11 | 26.4 | 0 | 8.4 | 2016-06-11 | 13.4 | 4.6 | 0 | 1.44 | 1.19
2025-06-11 | 17.9 | 0.1 | 0 | 2024-06-11 | 14.3 | 3.7 | 0 | 2023-06-11 | 18.2 | 0 | 0.2 | 2022-06-11 | 14.1 | 3.9 | 0 | 2021-06-11 | 17 | 1 | 0 | 2020-06-11 | 17 | 1 | 0 | 2019-06-11 | 13.5 | 4.5 | 0 | 2018-06-11 | 14 | 4 | 0 | 2017-06-11 | 24.8 | 0 | 6.8 | 2016-06-11 | 13.2 | 4.8 | 0 | 2.3 | 0.7
2025-06-11 | 17.3 | 0.7 | 0 | 2024-06-11 | 14 | 4 | 0 | 2023-06-11 | 18.1 | 0 | 0.1 | 2022-06-11 | 14.6 | 3.4 | 0 | 2021-06-11 | 15.1 | 2.9 | 0 | 2020-06-11 | 15.6 | 2.4 | 0 | 2019-06-11 | 12.3 | 5.7 | 0 | 2018-06-11 | 15.4 | 2.6 | 0 | 2017-06-11 | 24.4 | 0 | 6.4 | 2016-06-11 | 13.9 | 4.1 | 0 | 2.58 | 0.65
2025-06-11 | 16.9 | 1.1 | 0 | 2024-06-11 | 14.2 | 3.8 | 0 | 2023-06-11 | 17.4 | 0.6 | 0 | 2022-06-11 | 15.4 | 2.6 | 0 | 2021-06-11 | 13.7 | 4.3 | 0 | 2020-06-11 | 15.3 | 2.7 | 0 | 2019-06-11 | 11.6 | 6.4 | 0 | 2018-06-11 | 15.1 | 2.9 | 0 | 2017-06-11 | 23.1 | 0 | 5.1 | 2016-06-11 | 12.7 | 5.3 | 0 | 2.97 | 0.51
2025-06-12 | 15.6 | 2.4 | 0 | 2024-06-12 | 13.8 | 4.2 | 0 | 2023-06-12 | 17.4 | 0.6 | 0 | 2022-06-12 | 14 | 4 | 0 | 2021-06-12 | 15.4 | 2.6 | 0 | 2020-06-12 | 14.3 | 3.7 | 0 | 2019-06-12 | 10.4 | 7.6 | 0 | 2018-06-12 | 13.4 | 4.6 | 0 | 2017-06-12 | 22.5 | 0 | 4.5 | 2016-06-12 | 14 | 4 | 0 | 3.37 | 0.45
2025-06-12 | 14.2 | 3.8 | 0 | 2024-06-12 | 13.7 | 4.3 | 0 | 2023-06-12 | 16.8 | 1.2 | 0 | 2022-06-12 | 14 | 4 | 0 | 2021-06-12 | 12.3 | 5.7 | 0 | 2020-06-12 | 14.9 | 3.1 | 0 | 2019-06-12 | 8.7 | 9.3 | 0 | 2018-06-12 | 12.8 | 5.2 | 0 | 2017-06-12 | 23.2 | 0 | 5.2 | 2016-06-12 | 16 | 2 | 0 | 3.86 | 0.52
2025-06-12 | 14.5 | 3.5 | 0 | 2024-06-12 | 13.6 | 4.4 | 0 | 2023-06-12 | 16.5 | 1.5 | 0 | 2022-06-12 | 13.3 | 4.7 | 0 | 2021-06-12 | 13.7 | 4.3 | 0 | 2020-06-12 | 14.9 | 3.1 | 0 | 2019-06-12 | 9 | 9 | 0 | 2018-06-12 | 11.3 | 6.7 | 0 | 2017-06-12 | 22.5 | 0 | 4.5 | 2016-06-12 | 14.2 | 3.8 | 0 | 4.1 | 0.45
2025-06-12 | 14.7 | 3.3 | 0 | 2024-06-12 | 13.4 | 4.6 | 0 | 2023-06-12 | 16.1 | 1.9 | 0 | 2022-06-12 | 13.9 | 4.1 | 0 | 2021-06-12 | 13.3 | 4.7 | 0 | 2020-06-12 | 14.3 | 3.7 | 0 | 2019-06-12 | 7.4 | 10.6 | 0 | 2018-06-12 | 10.3 | 7.7 | 0 | 2017-06-12 | 22.6 | 0 | 4.6 | 2016-06-12 | 12.4 | 5.6 | 0 | 4.62 | 0.46
2025-06-12 | 14.3 | 3.7 | 0 | 2024-06-12 | 13.3 | 4.7 | 0 | 2023-06-12 | 16.6 | 1.4 | 0 | 2022-06-12 | 14.3 | 3.7 | 0 | 2021-06-12 | 12.1 | 5.9 | 0 | 2020-06-12 | 14.5 | 3.5 | 0 | 2019-06-12 | 8 | 10 | 0 | 2018-06-12 | 9 | 9 | 0 | 2017-06-12 | 22.4 | 0 | 4.4 | 2016-06-12 | 11 | 7 | 0 | 4.89 | 0.44
2025-06-12 | 15.1 | 2.9 | 0 | 2024-06-12 | 13.3 | 4.7 | 0 | 2023-06-12 | 17.2 | 0.8 | 0 | 2022-06-12 | 13.9 | 4.1 | 0 | 2021-06-12 | 14.6 | 3.4 | 0 | 2020-06-12 | 14.9 | 3.1 | 0 | 2019-06-12 | 7.4 | 10.6 | 0 | 2018-06-12 | 11 | 7 | 0 | 2017-06-12 | 22 | 0 | 4 | 2016-06-12 | 10.8 | 7.2 | 0 | 4.38 | 0.4
2025-06-12 | 15.4 | 2.6 | 0 | 2024-06-12 | 13.9 | 4.1 | 0 | 2023-06-12 | 16.8 | 1.2 | 0 | 2022-06-12 | 16.1 | 1.9 | 0 | 2021-06-12 | 16.4 | 1.6 | 0 | 2020-06-12 | 15.1 | 2.9 | 0 | 2019-06-12 | 10 | 8 | 0 | 2018-06-12 | 11.2 | 6.8 | 0 | 2017-06-12 | 23 | 0 | 5 | 2016-06-12 | 10.8 | 7.2 | 0 | 3.63 | 0.5
2025-06-12 | 16.1 | 1.9 | 0 | 2024-06-12 | 14.7 | 3.3 | 0 | 2023-06-12 | 16.9 | 1.1 | 0 | 2022-06-12 | 15.7 | 2.3 | 0 | 2021-06-12 | 18.7 | 0 | 0.7 | 2020-06-12 | 16.7 | 1.3 | 0 | 2019-06-12 | 13.3 | 4.7 | 0 | 2018-06-12 | 16 | 2 | 0 | 2017-06-12 | 24.2 | 0 | 6.2 | 2016-06-12 | 10.8 | 7.2 | 0 | 2.38 | 0.69
2025-06-12 | 16.9 | 1.1 | 0 | 2024-06-12 | 15.4 | 2.6 | 0 | 2023-06-12 | 17 | 1 | 0 | 2022-06-12 | 16.5 | 1.5 | 0 | 2021-06-12 | 21.1 | 0 | 3.1 | 2020-06-12 | 17.2 | 0.8 | 0 | 2019-06-12 | 16 | 2 | 0 | 2018-06-12 | 18.2 | 0 | 0.2 | 2017-06-12 | 25.5 | 0 | 7.5 | 2016-06-12 | 10.4 | 7.6 | 0 | 1.66 | 1.08
2025-06-12 | 17.9 | 0.1 | 0 | 2024-06-12 | 15.8 | 2.2 | 0 | 2023-06-12 | 17.8 | 0.2 | 0 | 2022-06-12 | 16.3 | 1.7 | 0 | 2021-06-12 | 22.5 | 0 | 4.5 | 2020-06-12 | 15.2 | 2.8 | 0 | 2019-06-12 | 18.7 | 0 | 0.7 | 2018-06-12 | 21.5 | 0 | 3.5 | 2017-06-12 | 27.1 | 0 | 9.1 | 2016-06-12 | 9.5 | 8.5 | 0 | 1.55 | 1.78
2025-06-12 | 18.1 | 0 | 0.1 | 2024-06-12 | 16.7 | 1.3 | 0 | 2023-06-12 | 19 | 0 | 1 | 2022-06-12 | 16.2 | 1.8 | 0 | 2021-06-12 | 23.5 | 0 | 5.5 | 2020-06-12 | 15.4 | 2.6 | 0 | 2019-06-12 | 20.5 | 0 | 2.5 | 2018-06-12 | 23.1 | 0 | 5.1 | 2017-06-12 | 28.9 | 0 | 10.9 | 2016-06-12 | 11.2 | 6.8 | 0 | 1.25 | 2.51
2025-06-12 | 18.5 | 0 | 0.5 | 2024-06-12 | 18.4 | 0 | 0.4 | 2023-06-12 | 20 | 0 | 2 | 2022-06-12 | 17 | 1 | 0 | 2021-06-12 | 24.8 | 0 | 6.8 | 2020-06-12 | 15.8 | 2.2 | 0 | 2019-06-12 | 21.5 | 0 | 3.5 | 2018-06-12 | 24.4 | 0 | 6.4 | 2017-06-12 | 30.3 | 0 | 12.3 | 2016-06-12 | 11.8 | 6.2 | 0 | 0.94 | 3.19
2025-06-12 | 18.9 | 0 | 0.9 | 2024-06-12 | 18.7 | 0 | 0.7 | 2023-06-12 | 23.2 | 0 | 5.2 | 2022-06-12 | 17.8 | 0.2 | 0 | 2021-06-12 | 24.8 | 0 | 6.8 | 2020-06-12 | 17.1 | 0.9 | 0 | 2019-06-12 | 22.2 | 0 | 4.2 | 2018-06-12 | 25.5 | 0 | 7.5 | 2017-06-12 | 30 | 0 | 12 | 2016-06-12 | 11.7 | 6.3 | 0 | 0.74 | 3.73
2025-06-12 | 19.3 | 0 | 1.3 | 2024-06-12 | 19.1 | 0 | 1.1 | 2023-06-12 | 24.5 | 0 | 6.5 | 2022-06-12 | 17.9 | 0.1 | 0 | 2021-06-12 | 25.6 | 0 | 7.6 | 2020-06-12 | 16.9 | 1.1 | 0 | 2019-06-12 | 23.1 | 0 | 5.1 | 2018-06-12 | 25.4 | 0 | 7.4 | 2017-06-12 | 31.9 | 0 | 13.9 | 2016-06-12 | 11.3 | 6.7 | 0 | 0.79 | 4.29
2025-06-12 | 19.4 | 0 | 1.4 | 2024-06-12 | 19.6 | 0 | 1.6 | 2023-06-12 | 26.7 | 0 | 8.7 | 2022-06-12 | 19.8 | 0 | 1.8 | 2021-06-12 | 26.6 | 0 | 8.6 | 2020-06-12 | 17 | 1 | 0 | 2019-06-12 | 23.2 | 0 | 5.2 | 2018-06-12 | 27 | 0 | 9 | 2017-06-12 | 31.7 | 0 | 13.7 | 2016-06-12 | 12.3 | 5.7 | 0 | 0.67 | 5
2025-06-12 | 19.4 | 0 | 1.4 | 2024-06-12 | 19.9 | 0 | 1.9 | 2023-06-12 | 27 | 0 | 9 | 2022-06-12 | 20.9 | 0 | 2.9 | 2021-06-12 | 26.7 | 0 | 8.7 | 2020-06-12 | 16.5 | 1.5 | 0 | 2019-06-12 | 23 | 0 | 5 | 2018-06-12 | 26.8 | 0 | 8.8 | 2017-06-12 | 32.1 | 0 | 14.1 | 2016-06-12 | 12.4 | 5.6 | 0 | 0.71 | 5.18
2025-06-12 | 19.4 | 0 | 1.4 | 2024-06-12 | 20.7 | 0 | 2.7 | 2023-06-12 | 26.8 | 0 | 8.8 | 2022-06-12 | 22.7 | 0 | 4.7 | 2021-06-12 | 26.6 | 0 | 8.6 | 2020-06-12 | 15.9 | 2.1 | 0 | 2019-06-12 | 23.1 | 0 | 5.1 | 2018-06-12 | 26 | 0 | 8 | 2017-06-12 | 30.9 | 0 | 12.9 | 2016-06-12 | 12.6 | 5.4 | 0 | 0.75 | 5.22
2025-06-12 | 18.6 | 0 | 0.6 | 2024-06-12 | 20.3 | 0 | 2.3 | 2023-06-12 | 26.3 | 0 | 8.3 | 2022-06-12 | 21.6 | 0 | 3.6 | 2021-06-12 | 25.4 | 0 | 7.4 | 2020-06-12 | 15.7 | 2.3 | 0 | 2019-06-12 | 22.7 | 0 | 4.7 | 2018-06-12 | 25.9 | 0 | 7.9 | 2017-06-12 | 30.5 | 0 | 12.5 | 2016-06-12 | 13 | 5 | 0 | 0.73 | 4.73
2025-06-12 | 17.4 | 0.6 | 0 | 2024-06-12 | 20.2 | 0 | 2.2 | 2023-06-12 | 25.9 | 0 | 7.9 | 2022-06-12 | 21.2 | 0 | 3.2 | 2021-06-12 | 24.8 | 0 | 6.8 | 2020-06-12 | 13.6 | 4.4 | 0 | 2019-06-12 | 22.1 | 0 | 4.1 | 2018-06-12 | 24.6 | 0 | 6.6 | 2017-06-12 | 29.4 | 0 | 11.4 | 2016-06-12 | 12.9 | 5.1 | 0 | 1.01 | 4.22
2025-06-12 | 15.5 | 2.5 | 0 | 2024-06-12 | 19.2 | 0 | 1.2 | 2023-06-12 | 23.1 | 0 | 5.1 | 2022-06-12 | 20.8 | 0 | 2.8 | 2021-06-12 | 23.8 | 0 | 5.8 | 2020-06-12 | 12 | 6 | 0 | 2019-06-12 | 19.8 | 0 | 1.8 | 2018-06-12 | 23.4 | 0 | 5.4 | 2017-06-12 | 27.7 | 0 | 9.7 | 2016-06-12 | 12.1 | 5.9 | 0 | 1.44 | 3.18
2025-06-12 | 13.8 | 4.2 | 0 | 2024-06-12 | 17.4 | 0.6 | 0 | 2023-06-12 | 22.2 | 0 | 4.2 | 2022-06-12 | 19 | 0 | 1 | 2021-06-12 | 21.7 | 0 | 3.7 | 2020-06-12 | 10.6 | 7.4 | 0 | 2019-06-12 | 18 | 0 | 0 | 2018-06-12 | 21.7 | 0 | 3.7 | 2017-06-12 | 26.9 | 0 | 8.9 | 2016-06-12 | 11.1 | 6.9 | 0 | 1.91 | 2.15
2025-06-12 | 12 | 6 | 0 | 2024-06-12 | 15.7 | 2.3 | 0 | 2023-06-12 | 22.6 | 0 | 4.6 | 2022-06-12 | 17.9 | 0.1 | 0 | 2021-06-12 | 21.1 | 0 | 3.1 | 2020-06-12 | 8.7 | 9.3 | 0 | 2019-06-12 | 13.2 | 4.8 | 0 | 2018-06-12 | 20.5 | 0 | 2.5 | 2017-06-12 | 25.7 | 0 | 7.7 | 2016-06-12 | 10.8 | 7.2 | 0 | 2.97 | 1.79
2025-06-12 | 11.4 | 6.6 | 0 | 2024-06-12 | 14.7 | 3.3 | 0 | 2023-06-12 | 20.1 | 0 | 2.1 | 2022-06-12 | 16.3 | 1.7 | 0 | 2021-06-12 | 19.1 | 0 | 1.1 | 2020-06-12 | 7.8 | 10.2 | 0 | 2019-06-12 | 13.5 | 4.5 | 0 | 2018-06-12 | 19.5 | 0 | 1.5 | 2017-06-12 | 24.8 | 0 | 6.8 | 2016-06-12 | 10.3 | 7.7 | 0 | 3.4 | 1.15
2025-06-12 | 11.4 | 6.6 | 0 | 2024-06-12 | 13.7 | 4.3 | 0 | 2023-06-12 | 19.7 | 0 | 1.7 | 2022-06-12 | 15.5 | 2.5 | 0 | 2021-06-12 | 15.1 | 2.9 | 0 | 2020-06-12 | 6.5 | 11.5 | 0 | 2019-06-12 | 12.6 | 5.4 | 0 | 2018-06-12 | 18.8 | 0 | 0.8 | 2017-06-12 | 24.2 | 0 | 6.2 | 2016-06-12 | 10.6 | 7.4 | 0 | 4.06 | 0.87
2025-06-13 | 11 | 7 | 0 | 2024-06-13 | 13.3 | 4.7 | 0 | 2023-06-13 | 18.7 | 0 | 0.7 | 2022-06-13 | 16.3 | 1.7 | 0 | 2021-06-13 | 15 | 3 | 0 | 2020-06-13 | 5.6 | 12.4 | 0 | 2019-06-13 | 12.8 | 5.2 | 0 | 2018-06-13 | 17.2 | 0.8 | 0 | 2017-06-13 | 23.1 | 0 | 5.1 | 2016-06-13 | 10.8 | 7.2 | 0 | 4.2 | 0.58
2025-06-13 | 9.8 | 8.2 | 0 | 2024-06-13 | 12.5 | 5.5 | 0 | 2023-06-13 | 18.3 | 0 | 0.3 | 2022-06-13 | 14.7 | 3.3 | 0 | 2021-06-13 | 13 | 5 | 0 | 2020-06-13 | 5.6 | 12.4 | 0 | 2019-06-13 | 14.6 | 3.4 | 0 | 2018-06-13 | 16.3 | 1.7 | 0 | 2017-06-13 | 21.5 | 0 | 3.5 | 2016-06-13 | 10.8 | 7.2 | 0 | 4.67 | 0.38
2025-06-13 | 8.2 | 9.8 | 0 | 2024-06-13 | 12.2 | 5.8 | 0 | 2023-06-13 | 17.7 | 0.3 | 0 | 2022-06-13 | 14.8 | 3.2 | 0 | 2021-06-13 | 11.9 | 6.1 | 0 | 2020-06-13 | 5.5 | 12.5 | 0 | 2019-06-13 | 13.6 | 4.4 | 0 | 2018-06-13 | 15.1 | 2.9 | 0 | 2017-06-13 | 20.9 | 0 | 2.9 | 2016-06-13 | 10.8 | 7.2 | 0 | 5.22 | 0.29
2025-06-13 | 7.3 | 10.7 | 0 | 2024-06-13 | 11.4 | 6.6 | 0 | 2023-06-13 | 16.9 | 1.1 | 0 | 2022-06-13 | 14.1 | 3.9 | 0 | 2021-06-13 | 12.7 | 5.3 | 0 | 2020-06-13 | 5.5 | 12.5 | 0 | 2019-06-13 | 13.5 | 4.5 | 0 | 2018-06-13 | 14.6 | 3.4 | 0 | 2017-06-13 | 19.7 | 0 | 1.7 | 2016-06-13 | 10.8 | 7.2 | 0 | 5.52 | 0.17
2025-06-13 | 7.4 | 10.6 | 0 | 2024-06-13 | 10.7 | 7.3 | 0 | 2023-06-13 | 16.7 | 1.3 | 0 | 2022-06-13 | 13.3 | 4.7 | 0 | 2021-06-13 | 13.1 | 4.9 | 0 | 2020-06-13 | 5.7 | 12.3 | 0 | 2019-06-13 | 13.7 | 4.3 | 0 | 2018-06-13 | 13.7 | 4.3 | 0 | 2017-06-13 | 19 | 0 | 1 | 2016-06-13 | 10.8 | 7.2 | 0 | 5.69 | 0.1
2025-06-13 | 7.5 | 10.5 | 0 | 2024-06-13 | 12.8 | 5.2 | 0 | 2023-06-13 | 15.6 | 2.4 | 0 | 2022-06-13 | 13 | 5 | 0 | 2021-06-13 | 13.7 | 4.3 | 0 | 2020-06-13 | 6.3 | 11.7 | 0 | 2019-06-13 | 14 | 4 | 0 | 2018-06-13 | 14.5 | 3.5 | 0 | 2017-06-13 | 21.6 | 0 | 3.6 | 2016-06-13 | 10.6 | 7.4 | 0 | 5.4 | 0.36
2025-06-13 | 10.1 | 7.9 | 0 | 2024-06-13 | 14.7 | 3.3 | 0 | 2023-06-13 | 15.2 | 2.8 | 0 | 2022-06-13 | 14.3 | 3.7 | 0 | 2021-06-13 | 14.8 | 3.2 | 0 | 2020-06-13 | 7 | 11 | 0 | 2019-06-13 | 14.8 | 3.2 | 0 | 2018-06-13 | 16.9 | 1.1 | 0 | 2017-06-13 | 21.6 | 0 | 3.6 | 2016-06-13 | 10.6 | 7.4 | 0 | 4.36 | 0.36
2025-06-13 | 11.7 | 6.3 | 0 | 2024-06-13 | 16.8 | 1.2 | 0 | 2023-06-13 | 15.3 | 2.7 | 0 | 2022-06-13 | 16 | 2 | 0 | 2021-06-13 | 17.6 | 0.4 | 0 | 2020-06-13 | 7.6 | 10.4 | 0 | 2019-06-13 | 15.7 | 2.3 | 0 | 2018-06-13 | 20.6 | 0 | 2.6 | 2017-06-13 | 22.6 | 0 | 4.6 | 2016-06-13 | 10.8 | 7.2 | 0 | 3.25 | 0.72
2025-06-13 | 12.1 | 5.9 | 0 | 2024-06-13 | 19.1 | 0 | 1.1 | 2023-06-13 | 15.9 | 2.1 | 0 | 2022-06-13 | 17.8 | 0.2 | 0 | 2021-06-13 | 20.2 | 0 | 2.2 | 2020-06-13 | 8.5 | 9.5 | 0 | 2019-06-13 | 16.9 | 1.1 | 0 | 2018-06-13 | 19.7 | 0 | 1.7 | 2017-06-13 | 23.3 | 0 | 5.3 | 2016-06-13 | 11.5 | 6.5 | 0 | 2.53 | 1.03
2025-06-13 | 13.8 | 4.2 | 0 | 2024-06-13 | 21.9 | 0 | 3.9 | 2023-06-13 | 16.6 | 1.4 | 0 | 2022-06-13 | 18.5 | 0 | 0.5 | 2021-06-13 | 22.5 | 0 | 4.5 | 2020-06-13 | 8.9 | 9.1 | 0 | 2019-06-13 | 17.6 | 0.4 | 0 | 2018-06-13 | 17.5 | 0.5 | 0 | 2017-06-13 | 22 | 0 | 4 | 2016-06-13 | 12.5 | 5.5 | 0 | 2.11 | 1.29
2025-06-13 | 14.5 | 3.5 | 0 | 2024-06-13 | 23.8 | 0 | 5.8 | 2023-06-13 | 16.4 | 1.6 | 0 | 2022-06-13 | 18.6 | 0 | 0.6 | 2021-06-13 | 25.5 | 0 | 7.5 | 2020-06-13 | 9.8 | 8.2 | 0 | 2019-06-13 | 18.4 | 0 | 0.4 | 2018-06-13 | 18.1 | 0 | 0.1 | 2017-06-13 | 21.6 | 0 | 3.6 | 2016-06-13 | 14.6 | 3.4 | 0 | 1.67 | 1.8
2025-06-13 | 15.3 | 2.7 | 0 | 2024-06-13 | 25.8 | 0 | 7.8 | 2023-06-13 | 16.5 | 1.5 | 0 | 2022-06-13 | 18.9 | 0 | 0.9 | 2021-06-13 | 26.3 | 0 | 8.3 | 2020-06-13 | 11.6 | 6.4 | 0 | 2019-06-13 | 17.6 | 0.4 | 0 | 2018-06-13 | 19.4 | 0 | 1.4 | 2017-06-13 | 22 | 0 | 4 | 2016-06-13 | 16.1 | 1.9 | 0 | 1.29 | 2.24
2025-06-13 | 15.8 | 2.2 | 0 | 2024-06-13 | 25.4 | 0 | 7.4 | 2023-06-13 | 18.9 | 0 | 0.9 | 2022-06-13 | 20.1 | 0 | 2.1 | 2021-06-13 | 28.1 | 0 | 10.1 | 2020-06-13 | 12.1 | 5.9 | 0 | 2019-06-13 | 19 | 0 | 1 | 2018-06-13 | 20.1 | 0 | 2.1 | 2017-06-13 | 21.9 | 0 | 3.9 | 2016-06-13 | 18.2 | 0 | 0.2 | 0.81 | 2.77
2025-06-13 | 16.6 | 1.4 | 0 | 2024-06-13 | 22.8 | 0 | 4.8 | 2023-06-13 | 20 | 0 | 2 | 2022-06-13 | 20.4 | 0 | 2.4 | 2021-06-13 | 27.9 | 0 | 9.9 | 2020-06-13 | 14 | 4 | 0 | 2019-06-13 | 19.3 | 0 | 1.3 | 2018-06-13 | 19 | 0 | 1 | 2017-06-13 | 22.2 | 0 | 4.2 | 2016-06-13 | 19.1 | 0 | 1.1 | 0.54 | 2.67
2025-06-13 | 17.1 | 0.9 | 0 | 2024-06-13 | 22.9 | 0 | 4.9 | 2023-06-13 | 20.3 | 0 | 2.3 | 2022-06-13 | 21.3 | 0 | 3.3 | 2021-06-13 | 27.2 | 0 | 9.2 | 2020-06-13 | 14.6 | 3.4 | 0 | 2019-06-13 | 18.3 | 0 | 0.3 | 2018-06-13 | 19.6 | 0 | 1.6 | 2017-06-13 | 22.2 | 0 | 4.2 | 2016-06-13 | 20.2 | 0 | 2.2 | 0.43 | 2.8
2025-06-13 | 18.5 | 0 | 0.5 | 2024-06-13 | 22.7 | 0 | 4.7 | 2023-06-13 | 20.8 | 0 | 2.8 | 2022-06-13 | 20.6 | 0 | 2.6 | 2021-06-13 | 27.1 | 0 | 9.1 | 2020-06-13 | 15.3 | 2.7 | 0 | 2019-06-13 | 17.6 | 0.4 | 0 | 2018-06-13 | 20.1 | 0 | 2.1 | 2017-06-13 | 22.4 | 0 | 4.4 | 2016-06-13 | 20.6 | 0 | 2.6 | 0.31 | 2.88
2025-06-13 | 18.9 | 0 | 0.9 | 2024-06-13 | 21.8 | 0 | 3.8 | 2023-06-13 | 21.1 | 0 | 3.1 | 2022-06-13 | 20.5 | 0 | 2.5 | 2021-06-13 | 25.9 | 0 | 7.9 | 2020-06-13 | 16.7 | 1.3 | 0 | 2019-06-13 | 14.4 | 3.6 | 0 | 2018-06-13 | 20.3 | 0 | 2.3 | 2017-06-13 | 24.4 | 0 | 6.4 | 2016-06-13 | 20.6 | 0 | 2.6 | 0.49 | 2.95
2025-06-13 | 18.4 | 0 | 0.4 | 2024-06-13 | 20.4 | 0 | 2.4 | 2023-06-13 | 20.5 | 0 | 2.5 | 2022-06-13 | 20.8 | 0 | 2.8 | 2021-06-13 | 26.9 | 0 | 8.9 | 2020-06-13 | 15.9 | 2.1 | 0 | 2019-06-13 | 12.4 | 5.6 | 0 | 2018-06-13 | 19.6 | 0 | 1.6 | 2017-06-13 | 24.5 | 0 | 6.5 | 2016-06-13 | 19.2 | 0 | 1.2 | 0.77 | 2.63
2025-06-13 | 17.4 | 0.6 | 0 | 2024-06-13 | 21.2 | 0 | 3.2 | 2023-06-13 | 20.6 | 0 | 2.6 | 2022-06-13 | 20 | 0 | 2 | 2021-06-13 | 25.5 | 0 | 7.5 | 2020-06-13 | 14.9 | 3.1 | 0 | 2019-06-13 | 12.2 | 5.8 | 0 | 2018-06-13 | 17.4 | 0.6 | 0 | 2017-06-13 | 24 | 0 | 6 | 2016-06-13 | 17.8 | 0.2 | 0 | 1.03 | 2.13
2025-06-13 | 16.3 | 1.7 | 0 | 2024-06-13 | 21.5 | 0 | 3.5 | 2023-06-13 | 18.8 | 0 | 0.8 | 2022-06-13 | 19.8 | 0 | 1.8 | 2021-06-13 | 24.5 | 0 | 6.5 | 2020-06-13 | 14.1 | 3.9 | 0 | 2019-06-13 | 12.4 | 5.6 | 0 | 2018-06-13 | 17.1 | 0.9 | 0 | 2017-06-13 | 22.9 | 0 | 4.9 | 2016-06-13 | 16.6 | 1.4 | 0 | 1.35 | 1.75
2025-06-13 | 14.9 | 3.1 | 0 | 2024-06-13 | 21.8 | 0 | 3.8 | 2023-06-13 | 16.3 | 1.7 | 0 | 2022-06-13 | 18.2 | 0 | 0.2 | 2021-06-13 | 23.1 | 0 | 5.1 | 2020-06-13 | 11.7 | 6.3 | 0 | 2019-06-13 | 11.8 | 6.2 | 0 | 2018-06-13 | 16.3 | 1.7 | 0 | 2017-06-13 | 21.2 | 0 | 3.2 | 2016-06-13 | 14.5 | 3.5 | 0 | 2.25 | 1.23
2025-06-13 | 14.6 | 3.4 | 0 | 2024-06-13 | 20.9 | 0 | 2.9 | 2023-06-13 | 14.8 | 3.2 | 0 | 2022-06-13 | 17.2 | 0.8 | 0 | 2021-06-13 | 22.4 | 0 | 4.4 | 2020-06-13 | 10.1 | 7.9 | 0 | 2019-06-13 | 11.7 | 6.3 | 0 | 2018-06-13 | 16.1 | 1.9 | 0 | 2017-06-13 | 20.1 | 0 | 2.1 | 2016-06-13 | 12.6 | 5.4 | 0 | 2.89 | 0.94
2025-06-13 | 13.5 | 4.5 | 0 | 2024-06-13 | 17.8 | 0.2 | 0 | 2023-06-13 | 14.2 | 3.8 | 0 | 2022-06-13 | 14.9 | 3.1 | 0 | 2021-06-13 | 21 | 0 | 3 | 2020-06-13 | 10.8 | 7.2 | 0 | 2019-06-13 | 11.8 | 6.2 | 0 | 2018-06-13 | 16.1 | 1.9 | 0 | 2017-06-13 | 18.7 | 0 | 0.7 | 2016-06-13 | 12.2 | 5.8 | 0 | 3.27 | 0.37
2025-06-13 | 13.1 | 4.9 | 0 | 2024-06-13 | 17.4 | 0.6 | 0 | 2023-06-13 | 13.9 | 4.1 | 0 | 2022-06-13 | 12.4 | 5.6 | 0 | 2021-06-13 | 19.1 | 0 | 1.1 | 2020-06-13 | 8.1 | 9.9 | 0 | 2019-06-13 | 11.8 | 6.2 | 0 | 2018-06-13 | 15.4 | 2.6 | 0 | 2017-06-13 | 18.3 | 0 | 0.3 | 2016-06-13 | 9.4 | 8.6 | 0 | 4.25 | 0.14
2025-06-14 | 12.3 | 5.7 | 0 | 2024-06-14 | 16.8 | 1.2 | 0 | 2023-06-14 | 12.8 | 5.2 | 0 | 2022-06-14 | 12.4 | 5.6 | 0 | 2021-06-14 | 17.6 | 0.4 | 0 | 2020-06-14 | 8.8 | 9.2 | 0 | 2019-06-14 | 11.9 | 6.1 | 0 | 2018-06-14 | 14.8 | 3.2 | 0 | 2017-06-14 | 16.9 | 1.1 | 0 | 2016-06-14 | 10.4 | 7.6 | 0 | 4.53 | 0
2025-06-14 | 10.7 | 7.3 | 0 | 2024-06-14 | 16.5 | 1.5 | 0 | 2023-06-14 | 9.3 | 8.7 | 0 | 2022-06-14 | 11.9 | 6.1 | 0 | 2021-06-14 | 17.2 | 0.8 | 0 | 2020-06-14 | 8.8 | 9.2 | 0 | 2019-06-14 | 12.2 | 5.8 | 0 | 2018-06-14 | 14.7 | 3.3 | 0 | 2017-06-14 | 15.7 | 2.3 | 0 | 2016-06-14 | 9.6 | 8.4 | 0 | 5.34 | 0
2025-06-14 | 11.5 | 6.5 | 0 | 2024-06-14 | 16.9 | 1.1 | 0 | 2023-06-14 | 9.2 | 8.8 | 0 | 2022-06-14 | 13.2 | 4.8 | 0 | 2021-06-14 | 17.4 | 0.6 | 0 | 2020-06-14 | 8.3 | 9.7 | 0 | 2019-06-14 | 12.7 | 5.3 | 0 | 2018-06-14 | 15.3 | 2.7 | 0 | 2017-06-14 | 14.5 | 3.5 | 0 | 2016-06-14 | 8.8 | 9.2 | 0 | 5.22 | 0
2025-06-14 | 9.6 | 8.4 | 0 | 2024-06-14 | 17.1 | 0.9 | 0 | 2023-06-14 | 9.3 | 8.7 | 0 | 2022-06-14 | 11.7 | 6.3 | 0 | 2021-06-14 | 17.4 | 0.6 | 0 | 2020-06-14 | 7.9 | 10.1 | 0 | 2019-06-14 | 12.8 | 5.2 | 0 | 2018-06-14 | 15.6 | 2.4 | 0 | 2017-06-14 | 13.2 | 4.8 | 0 | 2016-06-14 | 8.3 | 9.7 | 0 | 5.71 | 0
2025-06-14 | 8.9 | 9.1 | 0 | 2024-06-14 | 16.8 | 1.2 | 0 | 2023-06-14 | 8.4 | 9.6 | 0 | 2022-06-14 | 11.1 | 6.9 | 0 | 2021-06-14 | 16.9 | 1.1 | 0 | 2020-06-14 | 8 | 10 | 0 | 2019-06-14 | 13.4 | 4.6 | 0 | 2018-06-14 | 15.2 | 2.8 | 0 | 2017-06-14 | 12 | 6 | 0 | 2016-06-14 | 6.2 | 11.8 | 0 | 6.31 | 0
2025-06-14 | 9.1 | 8.9 | 0 | 2024-06-14 | 16.7 | 1.3 | 0 | 2023-06-14 | 9.7 | 8.3 | 0 | 2022-06-14 | 12 | 6 | 0 | 2021-06-14 | 16.8 | 1.2 | 0 | 2020-06-14 | 8.4 | 9.6 | 0 | 2019-06-14 | 13.5 | 4.5 | 0 | 2018-06-14 | 14.5 | 3.5 | 0 | 2017-06-14 | 11.9 | 6.1 | 0 | 2016-06-14 | 7.4 | 10.6 | 0 | 6 | 0
2025-06-14 | 11.3 | 6.7 | 0 | 2024-06-14 | 17.7 | 0.3 | 0 | 2023-06-14 | 12.9 | 5.1 | 0 | 2022-06-14 | 14.5 | 3.5 | 0 | 2021-06-14 | 16.9 | 1.1 | 0 | 2020-06-14 | 9.5 | 8.5 | 0 | 2019-06-14 | 13.1 | 4.9 | 0 | 2018-06-14 | 14.3 | 3.7 | 0 | 2017-06-14 | 12.7 | 5.3 | 0 | 2016-06-14 | 10.1 | 7.9 | 0 | 4.7 | 0
2025-06-14 | 13.6 | 4.4 | 0 | 2024-06-14 | 17.6 | 0.4 | 0 | 2023-06-14 | 15.2 | 2.8 | 0 | 2022-06-14 | 16.6 | 1.4 | 0 | 2021-06-14 | 19.4 | 0 | 1.4 | 2020-06-14 | 12.3 | 5.7 | 0 | 2019-06-14 | 13.1 | 4.9 | 0 | 2018-06-14 | 13.9 | 4.1 | 0 | 2017-06-14 | 13.8 | 4.2 | 0 | 2016-06-14 | 11.7 | 6.3 | 0 | 3.42 | 0.14
2025-06-14 | 15 | 3 | 0 | 2024-06-14 | 17.6 | 0.4 | 0 | 2023-06-14 | 16.8 | 1.2 | 0 | 2022-06-14 | 18.9 | 0 | 0.9 | 2021-06-14 | 18.7 | 0 | 0.7 | 2020-06-14 | 14.7 | 3.3 | 0 | 2019-06-14 | 12.7 | 5.3 | 0 | 2018-06-14 | 13.8 | 4.2 | 0 | 2017-06-14 | 14.6 | 3.4 | 0 | 2016-06-14 | 14.5 | 3.5 | 0 | 2.43 | 0.16
2025-06-14 | 16.2 | 1.8 | 0 | 2024-06-14 | 19.6 | 0 | 1.6 | 2023-06-14 | 17.5 | 0.5 | 0 | 2022-06-14 | 22.1 | 0 | 4.1 | 2021-06-14 | 19.8 | 0 | 1.8 | 2020-06-14 | 16.6 | 1.4 | 0 | 2019-06-14 | 13.5 | 4.5 | 0 | 2018-06-14 | 13.4 | 4.6 | 0 | 2017-06-14 | 15.7 | 2.3 | 0 | 2016-06-14 | 15.4 | 2.6 | 0 | 1.77 | 0.75
2025-06-14 | 18 | 0 | 0 | 2024-06-14 | 20.5 | 0 | 2.5 | 2023-06-14 | 17.7 | 0.3 | 0 | 2022-06-14 | 23.6 | 0 | 5.6 | 2021-06-14 | 20.6 | 0 | 2.6 | 2020-06-14 | 16.6 | 1.4 | 0 | 2019-06-14 | 14 | 4 | 0 | 2018-06-14 | 14.2 | 3.8 | 0 | 2017-06-14 | 16.7 | 1.3 | 0 | 2016-06-14 | 17.6 | 0.4 | 0 | 1.12 | 1.07
2025-06-14 | 19.5 | 0 | 1.5 | 2024-06-14 | 21.6 | 0 | 3.6 | 2023-06-14 | 17.6 | 0.4 | 0 | 2022-06-14 | 24.6 | 0 | 6.6 | 2021-06-14 | 23 | 0 | 5 | 2020-06-14 | 17.7 | 0.3 | 0 | 2019-06-14 | 14.4 | 3.6 | 0 | 2018-06-14 | 15.1 | 2.9 | 0 | 2017-06-14 | 18.6 | 0 | 0.6 | 2016-06-14 | 20.1 | 0 | 2.1 | 0.72 | 1.94
2025-06-14 | 19.8 | 0 | 1.8 | 2024-06-14 | 21 | 0 | 3 | 2023-06-14 | 17.9 | 0.1 | 0 | 2022-06-14 | 25.6 | 0 | 7.6 | 2021-06-14 | 23 | 0 | 5 | 2020-06-14 | 18.7 | 0 | 0.7 | 2019-06-14 | 14.3 | 3.7 | 0 | 2018-06-14 | 14.9 | 3.1 | 0 | 2017-06-14 | 19.6 | 0 | 1.6 | 2016-06-14 | 21.1 | 0 | 3.1 | 0.69 | 2.28
2025-06-14 | 20.2 | 0 | 2.2 | 2024-06-14 | 21.3 | 0 | 3.3 | 2023-06-14 | 17.2 | 0.8 | 0 | 2022-06-14 | 27.5 | 0 | 9.5 | 2021-06-14 | 21.9 | 0 | 3.9 | 2020-06-14 | 18.6 | 0 | 0.6 | 2019-06-14 | 14.1 | 3.9 | 0 | 2018-06-14 | 15.3 | 2.7 | 0 | 2017-06-14 | 20.1 | 0 | 2.1 | 2016-06-14 | 22.5 | 0 | 4.5 | 0.74 | 2.61
2025-06-14 | 21.4 | 0 | 3.4 | 2024-06-14 | 22.1 | 0 | 4.1 | 2023-06-14 | 16.5 | 1.5 | 0 | 2022-06-14 | 25.8 | 0 | 7.8 | 2021-06-14 | 21.1 | 0 | 3.1 | 2020-06-14 | 20.3 | 0 | 2.3 | 2019-06-14 | 14.8 | 3.2 | 0 | 2018-06-14 | 15.4 | 2.6 | 0 | 2017-06-14 | 21.5 | 0 | 3.5 | 2016-06-14 | 23.8 | 0 | 5.8 | 0.73 | 3
2025-06-14 | 21.5 | 0 | 3.5 | 2024-06-14 | 22.4 | 0 | 4.4 | 2023-06-14 | 16.2 | 1.8 | 0 | 2022-06-14 | 27.1 | 0 | 9.1 | 2021-06-14 | 17.8 | 0.2 | 0 | 2020-06-14 | 20.2 | 0 | 2.2 | 2019-06-14 | 16.7 | 1.3 | 0 | 2018-06-14 | 16.5 | 1.5 | 0 | 2017-06-14 | 22.1 | 0 | 4.1 | 2016-06-14 | 24.6 | 0 | 6.6 | 0.48 | 2.99
2025-06-14 | 21.8 | 0 | 3.8 | 2024-06-14 | 22.4 | 0 | 4.4 | 2023-06-14 | 16.5 | 1.5 | 0 | 2022-06-14 | 25.8 | 0 | 7.8 | 2021-06-14 | 18.3 | 0 | 0.3 | 2020-06-14 | 20.4 | 0 | 2.4 | 2019-06-14 | 16.3 | 1.7 | 0 | 2018-06-14 | 16.1 | 1.9 | 0 | 2017-06-14 | 22.3 | 0 | 4.3 | 2016-06-14 | 24.7 | 0 | 6.7 | 0.51 | 2.97
2025-06-14 | 21.1 | 0 | 3.1 | 2024-06-14 | 20.4 | 0 | 2.4 | 2023-06-14 | 16.4 | 1.6 | 0 | 2022-06-14 | 27.3 | 0 | 9.3 | 2021-06-14 | 19.1 | 0 | 1.1 | 2020-06-14 | 20.2 | 0 | 2.2 | 2019-06-14 | 17.3 | 0.7 | 0 | 2018-06-14 | 15.1 | 2.9 | 0 | 2017-06-14 | 22.1 | 0 | 4.1 | 2016-06-14 | 24.7 | 0 | 6.7 | 0.52 | 2.89
2025-06-14 | 20.5 | 0 | 2.5 | 2024-06-14 | 20.1 | 0 | 2.1 | 2023-06-14 | 16.6 | 1.4 | 0 | 2022-06-14 | 26.6 | 0 | 8.6 | 2021-06-14 | 17.5 | 0.5 | 0 | 2020-06-14 | 18.2 | 0 | 0.2 | 2019-06-14 | 18.6 | 0 | 0.6 | 2018-06-14 | 14.6 | 3.4 | 0 | 2017-06-14 | 21.4 | 0 | 3.4 | 2016-06-14 | 23.8 | 0 | 5.8 | 0.53 | 2.32
2025-06-14 | 18.9 | 0 | 0.9 | 2024-06-14 | 19.2 | 0 | 1.2 | 2023-06-14 | 16.2 | 1.8 | 0 | 2022-06-14 | 25.3 | 0 | 7.3 | 2021-06-14 | 17.7 | 0.3 | 0 | 2020-06-14 | 17.1 | 0.9 | 0 | 2019-06-14 | 16.9 | 1.1 | 0 | 2018-06-14 | 14.2 | 3.8 | 0 | 2017-06-14 | 19.9 | 0 | 1.9 | 2016-06-14 | 22.4 | 0 | 4.4 | 0.79 | 1.57
2025-06-14 | 16.7 | 1.3 | 0 | 2024-06-14 | 17.4 | 0.6 | 0 | 2023-06-14 | 16.2 | 1.8 | 0 | 2022-06-14 | 23.1 | 0 | 5.1 | 2021-06-14 | 17.2 | 0.8 | 0 | 2020-06-14 | 14.2 | 3.8 | 0 | 2019-06-14 | 14.5 | 3.5 | 0 | 2018-06-14 | 13.6 | 4.4 | 0 | 2017-06-14 | 17.2 | 0.8 | 0 | 2016-06-14 | 19.9 | 0 | 1.9 | 1.7 | 0.7
2025-06-14 | 15.4 | 2.6 | 0 | 2024-06-14 | 15.7 | 2.3 | 0 | 2023-06-14 | 16.1 | 1.9 | 0 | 2022-06-14 | 19.1 | 0 | 1.1 | 2021-06-14 | 17.2 | 0.8 | 0 | 2020-06-14 | 12.9 | 5.1 | 0 | 2019-06-14 | 14.2 | 3.8 | 0 | 2018-06-14 | 13.4 | 4.6 | 0 | 2017-06-14 | 16.3 | 1.7 | 0 | 2016-06-14 | 16.6 | 1.4 | 0 | 2.42 | 0.11
2025-06-14 | 14.7 | 3.3 | 0 | 2024-06-14 | 13.6 | 4.4 | 0 | 2023-06-14 | 15.6 | 2.4 | 0 | 2022-06-14 | 17.1 | 0.9 | 0 | 2021-06-14 | 16.2 | 1.8 | 0 | 2020-06-14 | 11.8 | 6.2 | 0 | 2019-06-14 | 14.3 | 3.7 | 0 | 2018-06-14 | 13.2 | 4.8 | 0 | 2017-06-14 | 16.3 | 1.7 | 0 | 2016-06-14 | 15.7 | 2.3 | 0 | 3.15 | 0
2025-06-14 | 13.4 | 4.6 | 0 | 2024-06-14 | 12.7 | 5.3 | 0 | 2023-06-14 | 15.4 | 2.6 | 0 | 2022-06-14 | 16.2 | 1.8 | 0 | 2021-06-14 | 16.4 | 1.6 | 0 | 2020-06-14 | 12.1 | 5.9 | 0 | 2019-06-14 | 13.8 | 4.2 | 0 | 2018-06-14 | 12.9 | 5.1 | 0 | 2017-06-14 | 14.6 | 3.4 | 0 | 2016-06-14 | 15.1 | 2.9 | 0 | 3.74 | 0
2025-06-15 | 13.9 | 4.1 | 0 | 2024-06-15 | 12.2 | 5.8 | 0 | 2023-06-15 | 14.8 | 3.2 | 0 | 2022-06-15 | 18 | 0 | 0 | 2021-06-15 | 16.1 | 1.9 | 0 | 2020-06-15 | 10.8 | 7.2 | 0 | 2019-06-15 | 14.3 | 3.7 | 0 | 2018-06-15 | 12.8 | 5.2 | 0 | 2017-06-15 | 13 | 5 | 0 | 2016-06-15 | 15.2 | 2.8 | 0 | 3.89 | 0
2025-06-15 | 9.8 | 8.2 | 0 | 2024-06-15 | 11.7 | 6.3 | 0 | 2023-06-15 | 14.8 | 3.2 | 0 | 2022-06-15 | 15.7 | 2.3 | 0 | 2021-06-15 | 16.1 | 1.9 | 0 | 2020-06-15 | 8.3 | 9.7 | 0 | 2019-06-15 | 13.2 | 4.8 | 0 | 2018-06-15 | 11.9 | 6.1 | 0 | 2017-06-15 | 10.9 | 7.1 | 0 | 2016-06-15 | 14 | 4 | 0 | 5.36 | 0
2025-06-15 | 9.1 | 8.9 | 0 | 2024-06-15 | 10.3 | 7.7 | 0 | 2023-06-15 | 15.3 | 2.7 | 0 | 2022-06-15 | 15.4 | 2.6 | 0 | 2021-06-15 | 15.7 | 2.3 | 0 | 2020-06-15 | 8.3 | 9.7 | 0 | 2019-06-15 | 12.7 | 5.3 | 0 | 2018-06-15 | 11.2 | 6.8 | 0 | 2017-06-15 | 11.8 | 6.2 | 0 | 2016-06-15 | 14.3 | 3.7 | 0 | 5.59 | 0
2025-06-15 | 8.4 | 9.6 | 0 | 2024-06-15 | 11.4 | 6.6 | 0 | 2023-06-15 | 14.6 | 3.4 | 0 | 2022-06-15 | 15.7 | 2.3 | 0 | 2021-06-15 | 15.9 | 2.1 | 0 | 2020-06-15 | 8.5 | 9.5 | 0 | 2019-06-15 | 12.8 | 5.2 | 0 | 2018-06-15 | 10.5 | 7.5 | 0 | 2017-06-15 | 10.8 | 7.2 | 0 | 2016-06-15 | 11.6 | 6.4 | 0 | 5.98 | 0
2025-06-15 | 8.4 | 9.6 | 0 | 2024-06-15 | 11.8 | 6.2 | 0 | 2023-06-15 | 15.2 | 2.8 | 0 | 2022-06-15 | 15.5 | 2.5 | 0 | 2021-06-15 | 16.3 | 1.7 | 0 | 2020-06-15 | 7.4 | 10.6 | 0 | 2019-06-15 | 13.2 | 4.8 | 0 | 2018-06-15 | 10.8 | 7.2 | 0 | 2017-06-15 | 10 | 8 | 0 | 2016-06-15 | 11.5 | 6.5 | 0 | 5.99 | 0
2025-06-15 | 9.1 | 8.9 | 0 | 2024-06-15 | 12.1 | 5.9 | 0 | 2023-06-15 | 14.8 | 3.2 | 0 | 2022-06-15 | 16.2 | 1.8 | 0 | 2021-06-15 | 16.1 | 1.9 | 0 | 2020-06-15 | 7.8 | 10.2 | 0 | 2019-06-15 | 13.4 | 4.6 | 0 | 2018-06-15 | 9.3 | 8.7 | 0 | 2017-06-15 | 10.1 | 7.9 | 0 | 2016-06-15 | 11.5 | 6.5 | 0 | 5.96 | 0
2025-06-15 | 12.1 | 5.9 | 0 | 2024-06-15 | 12.1 | 5.9 | 0 | 2023-06-15 | 15.8 | 2.2 | 0 | 2022-06-15 | 16.5 | 1.5 | 0 | 2021-06-15 | 16.8 | 1.2 | 0 | 2020-06-15 | 12.2 | 5.8 | 0 | 2019-06-15 | 14.3 | 3.7 | 0 | 2018-06-15 | 12 | 6 | 0 | 2017-06-15 | 12 | 6 | 0 | 2016-06-15 | 15.2 | 2.8 | 0 | 4.1 | 0
2025-06-15 | 15.2 | 2.8 | 0 | 2024-06-15 | 12.2 | 5.8 | 0 | 2023-06-15 | 18.5 | 0 | 0.5 | 2022-06-15 | 17.9 | 0.1 | 0 | 2021-06-15 | 16.8 | 1.2 | 0 | 2020-06-15 | 14.7 | 3.3 | 0 | 2019-06-15 | 15.7 | 2.3 | 0 | 2018-06-15 | 13.4 | 4.6 | 0 | 2017-06-15 | 14.7 | 3.3 | 0 | 2016-06-15 | 17.8 | 0.2 | 0 | 2.36 | 0.05
2025-06-15 | 17.4 | 0.6 | 0 | 2024-06-15 | 12.8 | 5.2 | 0 | 2023-06-15 | 19.3 | 0 | 1.3 | 2022-06-15 | 19 | 0 | 1 | 2021-06-15 | 17.3 | 0.7 | 0 | 2020-06-15 | 17.7 | 0.3 | 0 | 2019-06-15 | 15.2 | 2.8 | 0 | 2018-06-15 | 15.2 | 2.8 | 0 | 2017-06-15 | 17.1 | 0.9 | 0 | 2016-06-15 | 20 | 0 | 2 | 1.33 | 0.43
2025-06-15 | 19.9 | 0 | 1.9 | 2024-06-15 | 14.7 | 3.3 | 0 | 2023-06-15 | 20.1 | 0 | 2.1 | 2022-06-15 | 21.1 | 0 | 3.1 | 2021-06-15 | 16.4 | 1.6 | 0 | 2020-06-15 | 19.4 | 0 | 1.4 | 2019-06-15 | 14.5 | 3.5 | 0 | 2018-06-15 | 16.8 | 1.2 | 0 | 2017-06-15 | 18.8 | 0 | 0.8 | 2016-06-15 | 22.2 | 0 | 4.2 | 0.96 | 1.35
2025-06-15 | 21.4 | 0 | 3.4 | 2024-06-15 | 14.9 | 3.1 | 0 | 2023-06-15 | 22.1 | 0 | 4.1 | 2022-06-15 | 22.4 | 0 | 4.4 | 2021-06-15 | 14.7 | 3.3 | 0 | 2020-06-15 | 21.1 | 0 | 3.1 | 2019-06-15 | 15.6 | 2.4 | 0 | 2018-06-15 | 18.3 | 0 | 0.3 | 2017-06-15 | 20.3 | 0 | 2.3 | 2016-06-15 | 24.6 | 0 | 6.6 | 0.88 | 2.42
2025-06-15 | 22.6 | 0 | 4.6 | 2024-06-15 | 16.1 | 1.9 | 0 | 2023-06-15 | 22.9 | 0 | 4.9 | 2022-06-15 | 22 | 0 | 4 | 2021-06-15 | 13.8 | 4.2 | 0 | 2020-06-15 | 21.1 | 0 | 3.1 | 2019-06-15 | 15.2 | 2.8 | 0 | 2018-06-15 | 20 | 0 | 2 | 2017-06-15 | 21.2 | 0 | 3.2 | 2016-06-15 | 25.9 | 0 | 7.9 | 0.89 | 2.97
2025-06-15 | 23.3 | 0 | 5.3 | 2024-06-15 | 16.6 | 1.4 | 0 | 2023-06-15 | 24.2 | 0 | 6.2 | 2022-06-15 | 21.6 | 0 | 3.6 | 2021-06-15 | 15.9 | 2.1 | 0 | 2020-06-15 | 21.9 | 0 | 3.9 | 2019-06-15 | 16.6 | 1.4 | 0 | 2018-06-15 | 21.5 | 0 | 3.5 | 2017-06-15 | 22.3 | 0 | 4.3 | 2016-06-15 | 26.1 | 0 | 8.1 | 0.49 | 3.49
2025-06-15 | 23.1 | 0 | 5.1 | 2024-06-15 | 17.2 | 0.8 | 0 | 2023-06-15 | 25.3 | 0 | 7.3 | 2022-06-15 | 21.9 | 0 | 3.9 | 2021-06-15 | 16.7 | 1.3 | 0 | 2020-06-15 | 22 | 0 | 4 | 2019-06-15 | 18.7 | 0 | 0.7 | 2018-06-15 | 23.6 | 0 | 5.6 | 2017-06-15 | 22.1 | 0 | 4.1 | 2016-06-15 | 26.3 | 0 | 8.3 | 0.21 | 3.9
2025-06-15 | 24.2 | 0 | 6.2 | 2024-06-15 | 18.4 | 0 | 0.4 | 2023-06-15 | 25.8 | 0 | 7.8 | 2022-06-15 | 22.1 | 0 | 4.1 | 2021-06-15 | 16.4 | 1.6 | 0 | 2020-06-15 | 23.3 | 0 | 5.3 | 2019-06-15 | 16.4 | 1.6 | 0 | 2018-06-15 | 25.1 | 0 | 7.1 | 2017-06-15 | 22.1 | 0 | 4.1 | 2016-06-15 | 27 | 0 | 9 | 0.32 | 4.4
2025-06-15 | 24.1 | 0 | 6.1 | 2024-06-15 | 18.8 | 0 | 0.8 | 2023-06-15 | 26.4 | 0 | 8.4 | 2022-06-15 | 22.9 | 0 | 4.9 | 2021-06-15 | 20.1 | 0 | 2.1 | 2020-06-15 | 23.4 | 0 | 5.4 | 2019-06-15 | 15.7 | 2.3 | 0 | 2018-06-15 | 25.1 | 0 | 7.1 | 2017-06-15 | 21.9 | 0 | 3.9 | 2016-06-15 | 27.7 | 0 | 9.7 | 0.23 | 4.84
2025-06-15 | 24.7 | 0 | 6.7 | 2024-06-15 | 18.8 | 0 | 0.8 | 2023-06-15 | 25.9 | 0 | 7.9 | 2022-06-15 | 22.5 | 0 | 4.5 | 2021-06-15 | 22.7 | 0 | 4.7 | 2020-06-15 | 22.9 | 0 | 4.9 | 2019-06-15 | 15.5 | 2.5 | 0 | 2018-06-15 | 24.9 | 0 | 6.9 | 2017-06-15 | 21 | 0 | 3 | 2016-06-15 | 27 | 0 | 9 | 0.25 | 4.84
2025-06-15 | 24.6 | 0 | 6.6 | 2024-06-15 | 18.9 | 0 | 0.9 | 2023-06-15 | 25.5 | 0 | 7.5 | 2022-06-15 | 23.4 | 0 | 5.4 | 2021-06-15 | 23.2 | 0 | 5.2 | 2020-06-15 | 23 | 0 | 5 | 2019-06-15 | 15.2 | 2.8 | 0 | 2018-06-15 | 24.7 | 0 | 6.7 | 2017-06-15 | 20.8 | 0 | 2.8 | 2016-06-15 | 26.6 | 0 | 8.6 | 0.28 | 4.87
2025-06-15 | 23.6 | 0 | 5.6 | 2024-06-15 | 18.7 | 0 | 0.7 | 2023-06-15 | 24.6 | 0 | 6.6 | 2022-06-15 | 22.3 | 0 | 4.3 | 2021-06-15 | 21.9 | 0 | 3.9 | 2020-06-15 | 22.6 | 0 | 4.6 | 2019-06-15 | 15 | 3 | 0 | 2018-06-15 | 24.1 | 0 | 6.1 | 2017-06-15 | 20.6 | 0 | 2.6 | 2016-06-15 | 25.8 | 0 | 7.8 | 0.3 | 4.22
2025-06-15 | 22 | 0 | 4 | 2024-06-15 | 17.7 | 0.3 | 0 | 2023-06-15 | 23.4 | 0 | 5.4 | 2022-06-15 | 21.3 | 0 | 3.3 | 2021-06-15 | 20.4 | 0 | 2.4 | 2020-06-15 | 20.5 | 0 | 2.5 | 2019-06-15 | 15.1 | 2.9 | 0 | 2018-06-15 | 21.9 | 0 | 3.9 | 2017-06-15 | 19.8 | 0 | 1.8 | 2016-06-15 | 24.2 | 0 | 6.2 | 0.32 | 2.95
2025-06-15 | 19.6 | 0 | 1.6 | 2024-06-15 | 15.6 | 2.4 | 0 | 2023-06-15 | 21.2 | 0 | 3.2 | 2022-06-15 | 19.2 | 0 | 1.2 | 2021-06-15 | 18.3 | 0 | 0.3 | 2020-06-15 | 16.8 | 1.2 | 0 | 2019-06-15 | 14.9 | 3.1 | 0 | 2018-06-15 | 20.1 | 0 | 2.1 | 2017-06-15 | 19.2 | 0 | 1.2 | 2016-06-15 | 21.8 | 0 | 3.8 | 0.67 | 1.34
2025-06-15 | 18.7 | 0 | 0.7 | 2024-06-15 | 11.5 | 6.5 | 0 | 2023-06-15 | 19.5 | 0 | 1.5 | 2022-06-15 | 20 | 0 | 2 | 2021-06-15 | 17 | 1 | 0 | 2020-06-15 | 15.6 | 2.4 | 0 | 2019-06-15 | 14.1 | 3.9 | 0 | 2018-06-15 | 18.6 | 0 | 0.6 | 2017-06-15 | 14.2 | 3.8 | 0 | 2016-06-15 | 19.8 | 0 | 1.8 | 1.76 | 0.66
2025-06-15 | 14.2 | 3.8 | 0 | 2024-06-15 | 11.1 | 6.9 | 0 | 2023-06-15 | 18.5 | 0 | 0.5 | 2022-06-15 | 20 | 0 | 2 | 2021-06-15 | 15.9 | 2.1 | 0 | 2020-06-15 | 15.2 | 2.8 | 0 | 2019-06-15 | 13.2 | 4.8 | 0 | 2018-06-15 | 16.4 | 1.6 | 0 | 2017-06-15 | 13.6 | 4.4 | 0 | 2016-06-15 | 18.9 | 0 | 0.9 | 2.64 | 0.34
2025-06-15 | 14.7 | 3.3 | 0 | 2024-06-15 | 10.5 | 7.5 | 0 | 2023-06-15 | 18 | 0 | 0 | 2022-06-15 | 19.7 | 0 | 1.7 | 2021-06-15 | 14.8 | 3.2 | 0 | 2020-06-15 | 15.4 | 2.6 | 0 | 2019-06-15 | 11.7 | 6.3 | 0 | 2018-06-15 | 14.8 | 3.2 | 0 | 2017-06-15 | 13.2 | 4.8 | 0 | 2016-06-15 | 19.6 | 0 | 1.6 | 3.09 | 0.33
2025-06-16 | 13.5 | 4.5 | 0 | 2024-06-16 | 10.9 | 7.1 | 0 | 2023-06-16 | 17.7 | 0.3 | 0 | 2022-06-16 | 19.2 | 0 | 1.2 | 2021-06-16 | 14.1 | 3.9 | 0 | 2020-06-16 | 11.2 | 6.8 | 0 | 2019-06-16 | 10.6 | 7.4 | 0 | 2018-06-16 | 12.8 | 5.2 | 0 | 2017-06-16 | 13.3 | 4.7 | 0 | 2016-06-16 | 15.3 | 2.7 | 0 | 4.26 | 0.12
2025-06-16 | 12.5 | 5.5 | 0 | 2024-06-16 | 9 | 9 | 0 | 2023-06-16 | 18.2 | 0 | 0.2 | 2022-06-16 | 19.3 | 0 | 1.3 | 2021-06-16 | 12.8 | 5.2 | 0 | 2020-06-16 | 12.7 | 5.3 | 0 | 2019-06-16 | 9.8 | 8.2 | 0 | 2018-06-16 | 12.7 | 5.3 | 0 | 2017-06-16 | 13.4 | 4.6 | 0 | 2016-06-16 | 14.6 | 3.4 | 0 | 4.65 | 0.15
2025-06-16 | 12.6 | 5.4 | 0 | 2024-06-16 | 8 | 10 | 0 | 2023-06-16 | 18.6 | 0 | 0.6 | 2022-06-16 | 18.3 | 0 | 0.3 | 2021-06-16 | 12.6 | 5.4 | 0 | 2020-06-16 | 10.7 | 7.3 | 0 | 2019-06-16 | 9.1 | 8.9 | 0 | 2018-06-16 | 13.4 | 4.6 | 0 | 2017-06-16 | 13.6 | 4.4 | 0 | 2016-06-16 | 14.1 | 3.9 | 0 | 4.99 | 0.09
2025-06-16 | 7.6 | 10.4 | 0 | 2024-06-16 | 6.8 | 11.2 | 0 | 2023-06-16 | 17.9 | 0.1 | 0 | 2022-06-16 | 17.6 | 0.4 | 0 | 2021-06-16 | 11.6 | 6.4 | 0 | 2020-06-16 | 9.1 | 8.9 | 0 | 2019-06-16 | 9 | 9 | 0 | 2018-06-16 | 11.3 | 6.7 | 0 | 2017-06-16 | 14.2 | 3.8 | 0 | 2016-06-16 | 14.3 | 3.7 | 0 | 6.06 | 0
2025-06-16 | 11.1 | 6.9 | 0 | 2024-06-16 | 8.4 | 9.6 | 0 | 2023-06-16 | 17.3 | 0.7 | 0 | 2022-06-16 | 17.6 | 0.4 | 0 | 2021-06-16 | 11 | 7 | 0 | 2020-06-16 | 8.7 | 9.3 | 0 | 2019-06-16 | 7.2 | 10.8 | 0 | 2018-06-16 | 11.4 | 6.6 | 0 | 2017-06-16 | 13.8 | 4.2 | 0 | 2016-06-16 | 13.6 | 4.4 | 0 | 5.99 | 0
2025-06-16 | 10.8 | 7.2 | 0 | 2024-06-16 | 7.2 | 10.8 | 0 | 2023-06-16 | 16.3 | 1.7 | 0 | 2022-06-16 | 19.1 | 0 | 1.1 | 2021-06-16 | 10.4 | 7.6 | 0 | 2020-06-16 | 9.9 | 8.1 | 0 | 2019-06-16 | 9.2 | 8.8 | 0 | 2018-06-16 | 10.5 | 7.5 | 0 | 2017-06-16 | 14.1 | 3.9 | 0 | 2016-06-16 | 13.5 | 4.5 | 0 | 6.01 | 0.11
2025-06-16 | 13.6 | 4.4 | 0 | 2024-06-16 | 12.1 | 5.9 | 0 | 2023-06-16 | 16.8 | 1.2 | 0 | 2022-06-16 | 19.9 | 0 | 1.9 | 2021-06-16 | 12 | 6 | 0 | 2020-06-16 | 13.6 | 4.4 | 0 | 2019-06-16 | 11 | 7 | 0 | 2018-06-16 | 12.6 | 5.4 | 0 | 2017-06-16 | 14.2 | 3.8 | 0 | 2016-06-16 | 14.8 | 3.2 | 0 | 4.13 | 0.19
2025-06-16 | 16.2 | 1.8 | 0 | 2024-06-16 | 14.7 | 3.3 | 0 | 2023-06-16 | 17.1 | 0.9 | 0 | 2022-06-16 | 20.4 | 0 | 2.4 | 2021-06-16 | 12.8 | 5.2 | 0 | 2020-06-16 | 17.1 | 0.9 | 0 | 2019-06-16 | 13.4 | 4.6 | 0 | 2018-06-16 | 17.6 | 0.4 | 0 | 2017-06-16 | 14.3 | 3.7 | 0 | 2016-06-16 | 17.9 | 0.1 | 0 | 2.09 | 0.24
2025-06-16 | 19.4 | 0 | 1.4 | 2024-06-16 | 16.8 | 1.2 | 0 | 2023-06-16 | 17.4 | 0.6 | 0 | 2022-06-16 | 22.2 | 0 | 4.2 | 2021-06-16 | 13.5 | 4.5 | 0 | 2020-06-16 | 20.1 | 0 | 2.1 | 2019-06-16 | 14.9 | 3.1 | 0 | 2018-06-16 | 19.7 | 0 | 1.7 | 2017-06-16 | 15.3 | 2.7 | 0 | 2016-06-16 | 21.4 | 0 | 3.4 | 1.21 | 1.28
2025-06-16 | 22 | 0 | 4 | 2024-06-16 | 18.1 | 0 | 0.1 | 2023-06-16 | 18.9 | 0 | 0.9 | 2022-06-16 | 25.5 | 0 | 7.5 | 2021-06-16 | 14.4 | 3.6 | 0 | 2020-06-16 | 22.2 | 0 | 4.2 | 2019-06-16 | 16.2 | 1.8 | 0 | 2018-06-16 | 21.5 | 0 | 3.5 | 2017-06-16 | 15.9 | 2.1 | 0 | 2016-06-16 | 23.2 | 0 | 5.2 | 0.75 | 2.54
2025-06-16 | 23.5 | 0 | 5.5 | 2024-06-16 | 18.9 | 0 | 0.9 | 2023-06-16 | 19.7 | 0 | 1.7 | 2022-06-16 | 26.1 | 0 | 8.1 | 2021-06-16 | 15.9 | 2.1 | 0 | 2020-06-16 | 23.2 | 0 | 5.2 | 2019-06-16 | 17.7 | 0.3 | 0 | 2018-06-16 | 23.3 | 0 | 5.3 | 2017-06-16 | 16.2 | 1.8 | 0 | 2016-06-16 | 25.3 | 0 | 7.3 | 0.42 | 3.4
2025-06-16 | 24.1 | 0 | 6.1 | 2024-06-16 | 19.5 | 0 | 1.5 | 2023-06-16 | 22 | 0 | 4 | 2022-06-16 | 27.3 | 0 | 9.3 | 2021-06-16 | 18.2 | 0 | 0.2 | 2020-06-16 | 24.1 | 0 | 6.1 | 2019-06-16 | 18.5 | 0 | 0.5 | 2018-06-16 | 25.6 | 0 | 7.6 | 2017-06-16 | 16.4 | 1.6 | 0 | 2016-06-16 | 26.7 | 0 | 8.7 | 0.16 | 4.4
2025-06-16 | 24.9 | 0 | 6.9 | 2024-06-16 | 20.1 | 0 | 2.1 | 2023-06-16 | 23.4 | 0 | 5.4 | 2022-06-16 | 21.9 | 0 | 3.9 | 2021-06-16 | 17.5 | 0.5 | 0 | 2020-06-16 | 24.7 | 0 | 6.7 | 2019-06-16 | 18.5 | 0 | 0.5 | 2018-06-16 | 26.4 | 0 | 8.4 | 2017-06-16 | 17.2 | 0.8 | 0 | 2016-06-16 | 27.2 | 0 | 9.2 | 0.13 | 4.31
2025-06-16 | 25.7 | 0 | 7.7 | 2024-06-16 | 20.5 | 0 | 2.5 | 2023-06-16 | 24.8 | 0 | 6.8 | 2022-06-16 | 28.8 | 0 | 10.8 | 2021-06-16 | 19.3 | 0 | 1.3 | 2020-06-16 | 26.1 | 0 | 8.1 | 2019-06-16 | 19.9 | 0 | 1.9 | 2018-06-16 | 26.7 | 0 | 8.7 | 2017-06-16 | 18.7 | 0 | 0.7 | 2016-06-16 | 27.7 | 0 | 9.7 | 0 | 5.82
2025-06-16 | 26.4 | 0 | 8.4 | 2024-06-16 | 20.8 | 0 | 2.8 | 2023-06-16 | 24.5 | 0 | 6.5 | 2022-06-16 | 28 | 0 | 10 | 2021-06-16 | 19.3 | 0 | 1.3 | 2020-06-16 | 26.5 | 0 | 8.5 | 2019-06-16 | 19.9 | 0 | 1.9 | 2018-06-16 | 27.5 | 0 | 9.5 | 2017-06-16 | 20.2 | 0 | 2.2 | 2016-06-16 | 28 | 0 | 10 | 0 | 6.11
2025-06-16 | 27.1 | 0 | 9.1 | 2024-06-16 | 20.3 | 0 | 2.3 | 2023-06-16 | 24.8 | 0 | 6.8 | 2022-06-16 | 26.8 | 0 | 8.8 | 2021-06-16 | 20.5 | 0 | 2.5 | 2020-06-16 | 27.3 | 0 | 9.3 | 2019-06-16 | 18.9 | 0 | 0.9 | 2018-06-16 | 27.9 | 0 | 9.9 | 2017-06-16 | 20.6 | 0 | 2.6 | 2016-06-16 | 28.7 | 0 | 10.7 | 0 | 6.29
2025-06-16 | 26.8 | 0 | 8.8 | 2024-06-16 | 20.5 | 0 | 2.5 | 2023-06-16 | 24.4 | 0 | 6.4 | 2022-06-16 | 25.3 | 0 | 7.3 | 2021-06-16 | 21.6 | 0 | 3.6 | 2020-06-16 | 27.1 | 0 | 9.1 | 2019-06-16 | 18.6 | 0 | 0.6 | 2018-06-16 | 27.6 | 0 | 9.6 | 2017-06-16 | 21.2 | 0 | 3.2 | 2016-06-16 | 28.5 | 0 | 10.5 | 0 | 6.16
2025-06-16 | 26 | 0 | 8 | 2024-06-16 | 19.6 | 0 | 1.6 | 2023-06-16 | 23.6 | 0 | 5.6 | 2022-06-16 | 26.7 | 0 | 8.7 | 2021-06-16 | 20.8 | 0 | 2.8 | 2020-06-16 | 27.1 | 0 | 9.1 | 2019-06-16 | 19 | 0 | 1 | 2018-06-16 | 27.7 | 0 | 9.7 | 2017-06-16 | 21.7 | 0 | 3.7 | 2016-06-16 | 28 | 0 | 10 | 0 | 6.02
2025-06-16 | 24.7 | 0 | 6.7 | 2024-06-16 | 19.1 | 0 | 1.1 | 2023-06-16 | 23.1 | 0 | 5.1 | 2022-06-16 | 25.7 | 0 | 7.7 | 2021-06-16 | 20.7 | 0 | 2.7 | 2020-06-16 | 26 | 0 | 8 | 2019-06-16 | 18.6 | 0 | 0.6 | 2018-06-16 | 26.6 | 0 | 8.6 | 2017-06-16 | 22.6 | 0 | 4.6 | 2016-06-16 | 27.2 | 0 | 9.2 | 0 | 5.43
2025-06-16 | 23.9 | 0 | 5.9 | 2024-06-16 | 18.6 | 0 | 0.6 | 2023-06-16 | 21.7 | 0 | 3.7 | 2022-06-16 | 24.3 | 0 | 6.3 | 2021-06-16 | 19.4 | 0 | 1.4 | 2020-06-16 | 23.8 | 0 | 5.8 | 2019-06-16 | 18 | 0 | 0 | 2018-06-16 | 25 | 0 | 7 | 2017-06-16 | 21.6 | 0 | 3.6 | 2016-06-16 | 26 | 0 | 8 | 0 | 4.23
2025-06-16 | 22.3 | 0 | 4.3 | 2024-06-16 | 14.5 | 3.5 | 0 | 2023-06-16 | 20.4 | 0 | 2.4 | 2022-06-16 | 22.8 | 0 | 4.8 | 2021-06-16 | 16.1 | 1.9 | 0 | 2020-06-16 | 22.4 | 0 | 4.4 | 2019-06-16 | 15.6 | 2.4 | 0 | 2018-06-16 | 22.8 | 0 | 4.8 | 2017-06-16 | 20.2 | 0 | 2.2 | 2016-06-16 | 22.5 | 0 | 4.5 | 0.78 | 2.74
2025-06-16 | 20.8 | 0 | 2.8 | 2024-06-16 | 14.2 | 3.8 | 0 | 2023-06-16 | 19.5 | 0 | 1.5 | 2022-06-16 | 21.7 | 0 | 3.7 | 2021-06-16 | 14.4 | 3.6 | 0 | 2020-06-16 | 21 | 0 | 3 | 2019-06-16 | 14.2 | 3.8 | 0 | 2018-06-16 | 21.6 | 0 | 3.6 | 2017-06-16 | 20.2 | 0 | 2.2 | 2016-06-16 | 19 | 0 | 1 | 1.12 | 1.78
2025-06-16 | 20.3 | 0 | 2.3 | 2024-06-16 | 15.2 | 2.8 | 0 | 2023-06-16 | 18.1 | 0 | 0.1 | 2022-06-16 | 21.1 | 0 | 3.1 | 2021-06-16 | 13.4 | 4.6 | 0 | 2020-06-16 | 19.1 | 0 | 1.1 | 2019-06-16 | 13.1 | 4.9 | 0 | 2018-06-16 | 19.1 | 0 | 1.1 | 2017-06-16 | 18.9 | 0 | 0.9 | 2016-06-16 | 16.9 | 1.1 | 0 | 1.34 | 0.86
2025-06-16 | 19.7 | 0 | 1.7 | 2024-06-16 | 15.4 | 2.6 | 0 | 2023-06-16 | 16.8 | 1.2 | 0 | 2022-06-16 | 20.9 | 0 | 2.9 | 2021-06-16 | 11.3 | 6.7 | 0 | 2020-06-16 | 17.9 | 0.1 | 0 | 2019-06-16 | 12.5 | 5.5 | 0 | 2018-06-16 | 18.1 | 0 | 0.1 | 2017-06-16 | 18 | 0 | 0 | 2016-06-16 | 16.9 | 1.1 | 0 | 1.72 | 0.47
2025-06-17 | 18.5 | 0 | 0.5 | 2024-06-17 | 15.7 | 2.3 | 0 | 2023-06-17 | 16 | 2 | 0 | 2022-06-17 | 20.5 | 0 | 2.5 | 2021-06-17 | 11.2 | 6.8 | 0 | 2020-06-17 | 16.4 | 1.6 | 0 | 2019-06-17 | 12.4 | 5.6 | 0 | 2018-06-17 | 16.7 | 1.3 | 0 | 2017-06-17 | 17.3 | 0.7 | 0 | 2016-06-17 | 15.1 | 2.9 | 0 | 2.32 | 0.3
2025-06-17 | 17.7 | 0.3 | 0 | 2024-06-17 | 15.2 | 2.8 | 0 | 2023-06-17 | 15.8 | 2.2 | 0 | 2022-06-17 | 20.8 | 0 | 2.8 | 2021-06-17 | 9.5 | 8.5 | 0 | 2020-06-17 | 17.4 | 0.6 | 0 | 2019-06-17 | 10.8 | 7.2 | 0 | 2018-06-17 | 15.9 | 2.1 | 0 | 2017-06-17 | 16.9 | 1.1 | 0 | 2016-06-17 | 15.1 | 2.9 | 0 | 2.77 | 0.28
2025-06-17 | 17.1 | 0.9 | 0 | 2024-06-17 | 15.1 | 2.9 | 0 | 2023-06-17 | 15.1 | 2.9 | 0 | 2022-06-17 | 21.6 | 0 | 3.6 | 2021-06-17 | 8.9 | 9.1 | 0 | 2020-06-17 | 13.9 | 4.1 | 0 | 2019-06-17 | 10.5 | 7.5 | 0 | 2018-06-17 | 15.3 | 2.7 | 0 | 2017-06-17 | 16.4 | 1.6 | 0 | 2016-06-17 | 14 | 4 | 0 | 3.57 | 0.36
2025-06-17 | 17.6 | 0.4 | 0 | 2024-06-17 | 15.2 | 2.8 | 0 | 2023-06-17 | 14.7 | 3.3 | 0 | 2022-06-17 | 20.1 | 0 | 2.1 | 2021-06-17 | 9.2 | 8.8 | 0 | 2020-06-17 | 13.9 | 4.1 | 0 | 2019-06-17 | 9.4 | 8.6 | 0 | 2018-06-17 | 14.2 | 3.8 | 0 | 2017-06-17 | 15.9 | 2.1 | 0 | 2016-06-17 | 13.8 | 4.2 | 0 | 3.81 | 0.21
2025-06-17 | 17.7 | 0.3 | 0 | 2024-06-17 | 15.2 | 2.8 | 0 | 2023-06-17 | 14.5 | 3.5 | 0 | 2022-06-17 | 19.6 | 0 | 1.6 | 2021-06-17 | 8.4 | 9.6 | 0 | 2020-06-17 | 11.2 | 6.8 | 0 | 2019-06-17 | 8.1 | 9.9 | 0 | 2018-06-17 | 14.2 | 3.8 | 0 | 2017-06-17 | 16.3 | 1.7 | 0 | 2016-06-17 | 10.1 | 7.9 | 0 | 4.63 | 0.16
2025-06-17 | 18.1 | 0 | 0.1 | 2024-06-17 | 14.9 | 3.1 | 0 | 2023-06-17 | 13.9 | 4.1 | 0 | 2022-06-17 | 19.6 | 0 | 1.6 | 2021-06-17 | 8.7 | 9.3 | 0 | 2020-06-17 | 12.1 | 5.9 | 0 | 2019-06-17 | 8.1 | 9.9 | 0 | 2018-06-17 | 14.1 | 3.9 | 0 | 2017-06-17 | 16.7 | 1.3 | 0 | 2016-06-17 | 12.3 | 5.7 | 0 | 4.32 | 0.17
2025-06-17 | 19.1 | 0 | 1.1 | 2024-06-17 | 14.3 | 3.7 | 0 | 2023-06-17 | 13.8 | 4.2 | 0 | 2022-06-17 | 19.8 | 0 | 1.8 | 2021-06-17 | 12.4 | 5.6 | 0 | 2020-06-17 | 14.7 | 3.3 | 0 | 2019-06-17 | 12.7 | 5.3 | 0 | 2018-06-17 | 16 | 2 | 0 | 2017-06-17 | 16.7 | 1.3 | 0 | 2016-06-17 | 17 | 1 | 0 | 2.64 | 0.29
2025-06-17 | 19.4 | 0 | 1.4 | 2024-06-17 | 15 | 3 | 0 | 2023-06-17 | 14.2 | 3.8 | 0 | 2022-06-17 | 20.9 | 0 | 2.9 | 2021-06-17 | 14.5 | 3.5 | 0 | 2020-06-17 | 18.3 | 0 | 0.3 | 2019-06-17 | 15.1 | 2.9 | 0 | 2018-06-17 | 19 | 0 | 1 | 2017-06-17 | 17.1 | 0.9 | 0 | 2016-06-17 | 19.4 | 0 | 1.4 | 1.41 | 0.7
2025-06-17 | 19.1 | 0 | 1.1 | 2024-06-17 | 17.5 | 0.5 | 0 | 2023-06-17 | 15.3 | 2.7 | 0 | 2022-06-17 | 21.7 | 0 | 3.7 | 2021-06-17 | 16.3 | 1.7 | 0 | 2020-06-17 | 21.3 | 0 | 3.3 | 2019-06-17 | 16.9 | 1.1 | 0 | 2018-06-17 | 21.7 | 0 | 3.7 | 2017-06-17 | 18.6 | 0 | 0.6 | 2016-06-17 | 22.2 | 0 | 4.2 | 0.6 | 1.66
2025-06-17 | 19.9 | 0 | 1.9 | 2024-06-17 | 20.3 | 0 | 2.3 | 2023-06-17 | 16.4 | 1.6 | 0 | 2022-06-17 | 23.1 | 0 | 5.1 | 2021-06-17 | 18.6 | 0 | 0.6 | 2020-06-17 | 23.2 | 0 | 5.2 | 2019-06-17 | 18.1 | 0 | 0.1 | 2018-06-17 | 23.8 | 0 | 5.8 | 2017-06-17 | 20.1 | 0 | 2.1 | 2016-06-17 | 23.8 | 0 | 5.8 | 0.16 | 2.89
2025-06-17 | 21.8 | 0 | 3.8 | 2024-06-17 | 23.2 | 0 | 5.2 | 2023-06-17 | 17.4 | 0.6 | 0 | 2022-06-17 | 24.1 | 0 | 6.1 | 2021-06-17 | 20.8 | 0 | 2.8 | 2020-06-17 | 25.9 | 0 | 7.9 | 2019-06-17 | 19.3 | 0 | 1.3 | 2018-06-17 | 26.2 | 0 | 8.2 | 2017-06-17 | 20.3 | 0 | 2.3 | 2016-06-17 | 26 | 0 | 8 | 0.06 | 4.56
2025-06-17 | 21.9 | 0 | 3.9 | 2024-06-17 | 25.3 | 0 | 7.3 | 2023-06-17 | 19.7 | 0 | 1.7 | 2022-06-17 | 23.9 | 0 | 5.9 | 2021-06-17 | 22 | 0 | 4 | 2020-06-17 | 26.9 | 0 | 8.9 | 2019-06-17 | 20.7 | 0 | 2.7 | 2018-06-17 | 28.2 | 0 | 10.2 | 2017-06-17 | 20.1 | 0 | 2.1 | 2016-06-17 | 27 | 0 | 9 | 0 | 5.57
2025-06-17 | 23.8 | 0 | 5.8 | 2024-06-17 | 26.3 | 0 | 8.3 | 2023-06-17 | 20.2 | 0 | 2.2 | 2022-06-17 | 24.2 | 0 | 6.2 | 2021-06-17 | 23 | 0 | 5 | 2020-06-17 | 27.9 | 0 | 9.9 | 2019-06-17 | 21.3 | 0 | 3.3 | 2018-06-17 | 28.8 | 0 | 10.8 | 2017-06-17 | 20.4 | 0 | 2.4 | 2016-06-17 | 28.1 | 0 | 10.1 | 0 | 6.4
2025-06-17 | 24.1 | 0 | 6.1 | 2024-06-17 | 27.8 | 0 | 9.8 | 2023-06-17 | 19.1 | 0 | 1.1 | 2022-06-17 | 26.4 | 0 | 8.4 | 2021-06-17 | 24.2 | 0 | 6.2 | 2020-06-17 | 28.5 | 0 | 10.5 | 2019-06-17 | 21.7 | 0 | 3.7 | 2018-06-17 | 29.4 | 0 | 11.4 | 2017-06-17 | 21.7 | 0 | 3.7 | 2016-06-17 | 28.8 | 0 | 10.8 | 0 | 7.17
2025-06-17 | 25.7 | 0 | 7.7 | 2024-06-17 | 28.4 | 0 | 10.4 | 2023-06-17 | 18.9 | 0 | 0.9 | 2022-06-17 | 25.4 | 0 | 7.4 | 2021-06-17 | 25.1 | 0 | 7.1 | 2020-06-17 | 29.1 | 0 | 11.1 | 2019-06-17 | 22.9 | 0 | 4.9 | 2018-06-17 | 29.9 | 0 | 11.9 | 2017-06-17 | 23.9 | 0 | 5.9 | 2016-06-17 | 28.5 | 0 | 10.5 | 0 | 7.78
2025-06-17 | 25.6 | 0 | 7.6 | 2024-06-17 | 29.1 | 0 | 11.1 | 2023-06-17 | 18.9 | 0 | 0.9 | 2022-06-17 | 24.7 | 0 | 6.7 | 2021-06-17 | 26.1 | 0 | 8.1 | 2020-06-17 | 29.5 | 0 | 11.5 | 2019-06-17 | 22.9 | 0 | 4.9 | 2018-06-17 | 29.4 | 0 | 11.4 | 2017-06-17 | 24.5 | 0 | 6.5 | 2016-06-17 | 28 | 0 | 10 | 0 | 7.87
2025-06-17 | 25 | 0 | 7 | 2024-06-17 | 30.2 | 0 | 12.2 | 2023-06-17 | 17.4 | 0.6 | 0 | 2022-06-17 | 23.3 | 0 | 5.3 | 2021-06-17 | 26.1 | 0 | 8.1 | 2020-06-17 | 29.6 | 0 | 11.6 | 2019-06-17 | 23.1 | 0 | 5.1 | 2018-06-17 | 28.4 | 0 | 10.4 | 2017-06-17 | 25.6 | 0 | 7.6 | 2016-06-17 | 29.2 | 0 | 11.2 | 0.06 | 7.85
2025-06-17 | 25.9 | 0 | 7.9 | 2024-06-17 | 29.6 | 0 | 11.6 | 2023-06-17 | 18.2 | 0 | 0.2 | 2022-06-17 | 18.6 | 0 | 0.6 | 2021-06-17 | 25.7 | 0 | 7.7 | 2020-06-17 | 29.4 | 0 | 11.4 | 2019-06-17 | 23.2 | 0 | 5.2 | 2018-06-17 | 27 | 0 | 9 | 2017-06-17 | 25.5 | 0 | 7.5 | 2016-06-17 | 28.7 | 0 | 10.7 | 0 | 7.18
2025-06-17 | 25 | 0 | 7 | 2024-06-17 | 29.3 | 0 | 11.3 | 2023-06-17 | 18.1 | 0 | 0.1 | 2022-06-17 | 17.5 | 0.5 | 0 | 2021-06-17 | 24.2 | 0 | 6.2 | 2020-06-17 | 28.4 | 0 | 10.4 | 2019-06-17 | 22.6 | 0 | 4.6 | 2018-06-17 | 26.2 | 0 | 8.2 | 2017-06-17 | 24.7 | 0 | 6.7 | 2016-06-17 | 27.8 | 0 | 9.8 | 0.05 | 6.43
2025-06-17 | 23.5 | 0 | 5.5 | 2024-06-17 | 27.8 | 0 | 9.8 | 2023-06-17 | 17.9 | 0.1 | 0 | 2022-06-17 | 16.8 | 1.2 | 0 | 2021-06-17 | 22.2 | 0 | 4.2 | 2020-06-17 | 26.1 | 0 | 8.1 | 2019-06-17 | 21 | 0 | 3 | 2018-06-17 | 24.8 | 0 | 6.8 | 2017-06-17 | 24 | 0 | 6 | 2016-06-17 | 26.2 | 0 | 8.2 | 0.13 | 5.16
2025-06-17 | 22 | 0 | 4 | 2024-06-17 | 26.3 | 0 | 8.3 | 2023-06-17 | 17.6 | 0.4 | 0 | 2022-06-17 | 13.9 | 4.1 | 0 | 2021-06-17 | 19.4 | 0 | 1.4 | 2020-06-17 | 24.8 | 0 | 6.8 | 2019-06-17 | 17.9 | 0.1 | 0 | 2018-06-17 | 23.9 | 0 | 5.9 | 2017-06-17 | 22.1 | 0 | 4.1 | 2016-06-17 | 24.7 | 0 | 6.7 | 0.46 | 3.72
2025-06-17 | 20.7 | 0 | 2.7 | 2024-06-17 | 24.8 | 0 | 6.8 | 2023-06-17 | 17.6 | 0.4 | 0 | 2022-06-17 | 12.5 | 5.5 | 0 | 2021-06-17 | 18.7 | 0 | 0.7 | 2020-06-17 | 22.5 | 0 | 4.5 | 2019-06-17 | 14.8 | 3.2 | 0 | 2018-06-17 | 23.5 | 0 | 5.5 | 2017-06-17 | 21.1 | 0 | 3.1 | 2016-06-17 | 22.4 | 0 | 4.4 | 0.91 | 2.77
2025-06-17 | 19.3 | 0 | 1.3 | 2024-06-17 | 23.8 | 0 | 5.8 | 2023-06-17 | 17.2 | 0.8 | 0 | 2022-06-17 | 11.5 | 6.5 | 0 | 2021-06-17 | 17.9 | 0.1 | 0 | 2020-06-17 | 20.7 | 0 | 2.7 | 2019-06-17 | 14.4 | 3.6 | 0 | 2018-06-17 | 23.5 | 0 | 5.5 | 2017-06-17 | 21.1 | 0 | 3.1 | 2016-06-17 | 19.4 | 0 | 1.4 | 1.1 | 1.98
2025-06-17 | 19.4 | 0 | 1.4 | 2024-06-17 | 22.9 | 0 | 4.9 | 2023-06-17 | 16.8 | 1.2 | 0 | 2022-06-17 | 10.7 | 7.3 | 0 | 2021-06-17 | 18 | 0 | 0 | 2020-06-17 | 19.7 | 0 | 1.7 | 2019-06-17 | 15.5 | 2.5 | 0 | 2018-06-17 | 23.3 | 0 | 5.3 | 2017-06-17 | 20.9 | 0 | 2.9 | 2016-06-17 | 19.5 | 0 | 1.5 | 1.1 | 1.77
2025-06-18 | 19.6 | 0 | 1.6 | 2024-06-18 | 22.6 | 0 | 4.6 | 2023-06-18 | 16 | 2 | 0 | 2022-06-18 | 10.4 | 7.6 | 0 | 2021-06-18 | 16.3 | 1.7 | 0 | 2020-06-18 | 19 | 0 | 1 | 2019-06-18 | 15.4 | 2.6 | 0 | 2018-06-18 | 23.2 | 0 | 5.2 | 2017-06-18 | 21.4 | 0 | 3.4 | 2016-06-18 | 18.4 | 0 | 0.4 | 1.39 | 1.62
2025-06-18 | 20 | 0 | 2 | 2024-06-18 | 22.2 | 0 | 4.2 | 2023-06-18 | 15.4 | 2.6 | 0 | 2022-06-18 | 10.9 | 7.1 | 0 | 2021-06-18 | 16 | 2 | 0 | 2020-06-18 | 17.6 | 0.4 | 0 | 2019-06-18 | 13.9 | 4.1 | 0 | 2018-06-18 | 23.1 | 0 | 5.1 | 2017-06-18 | 22.4 | 0 | 4.4 | 2016-06-18 | 13.5 | 4.5 | 0 | 2.07 | 1.57
2025-06-18 | 19.9 | 0 | 1.9 | 2024-06-18 | 21.3 | 0 | 3.3 | 2023-06-18 | 14.2 | 3.8 | 0 | 2022-06-18 | 10.9 | 7.1 | 0 | 2021-06-18 | 13.9 | 4.1 | 0 | 2020-06-18 | 15.7 | 2.3 | 0 | 2019-06-18 | 12.9 | 5.1 | 0 | 2018-06-18 | 23 | 0 | 5 | 2017-06-18 | 20.4 | 0 | 2.4 | 2016-06-18 | 13.6 | 4.4 | 0 | 2.68 | 1.26
2025-06-18 | 19.8 | 0 | 1.8 | 2024-06-18 | 20.9 | 0 | 2.9 | 2023-06-18 | 14.3 | 3.7 | 0 | 2022-06-18 | 10.1 | 7.9 | 0 | 2021-06-18 | 13.8 | 4.2 | 0 | 2020-06-18 | 13.2 | 4.8 | 0 | 2019-06-18 | 12.6 | 5.4 | 0 | 2018-06-18 | 22.5 | 0 | 4.5 | 2017-06-18 | 19.7 | 0 | 1.7 | 2016-06-18 | 14.5 | 3.5 | 0 | 2.95 | 1.09
2025-06-18 | 19.6 | 0 | 1.6 | 2024-06-18 | 20.3 | 0 | 2.3 | 2023-06-18 | 14.4 | 3.6 | 0 | 2022-06-18 | 9.4 | 8.6 | 0 | 2021-06-18 | 14.1 | 3.9 | 0 | 2020-06-18 | 13.3 | 4.7 | 0 | 2019-06-18 | 11 | 7 | 0 | 2018-06-18 | 22 | 0 | 4 | 2017-06-18 | 21.3 | 0 | 3.3 | 2016-06-18 | 13.4 | 4.6 | 0 | 3.24 | 1.12
2025-06-18 | 19.8 | 0 | 1.8 | 2024-06-18 | 20.3 | 0 | 2.3 | 2023-06-18 | 14.3 | 3.7 | 0 | 2022-06-18 | 9.3 | 8.7 | 0 | 2021-06-18 | 14.6 | 3.4 | 0 | 2020-06-18 | 14.7 | 3.3 | 0 | 2019-06-18 | 11.9 | 6.1 | 0 | 2018-06-18 | 22.1 | 0 | 4.1 | 2017-06-18 | 19.9 | 0 | 1.9 | 2016-06-18 | 14.3 | 3.7 | 0 | 2.89 | 1.01
2025-06-18 | 20.4 | 0 | 2.4 | 2024-06-18 | 21.1 | 0 | 3.1 | 2023-06-18 | 14.7 | 3.3 | 0 | 2022-06-18 | 9.7 | 8.3 | 0 | 2021-06-18 | 17 | 1 | 0 | 2020-06-18 | 16.5 | 1.5 | 0 | 2019-06-18 | 15.7 | 2.3 | 0 | 2018-06-18 | 22.8 | 0 | 4.8 | 2017-06-18 | 21.7 | 0 | 3.7 | 2016-06-18 | 17.7 | 0.3 | 0 | 1.67 | 1.4
2025-06-18 | 21 | 0 | 3 | 2024-06-18 | 22.5 | 0 | 4.5 | 2023-06-18 | 15.6 | 2.4 | 0 | 2022-06-18 | 9.7 | 8.3 | 0 | 2021-06-18 | 17.2 | 0.8 | 0 | 2020-06-18 | 19.2 | 0 | 1.2 | 2019-06-18 | 18 | 0 | 0 | 2018-06-18 | 23.9 | 0 | 5.9 | 2017-06-18 | 23.4 | 0 | 5.4 | 2016-06-18 | 18.9 | 0 | 0.9 | 1.15 | 2.09
2025-06-18 | 21.7 | 0 | 3.7 | 2024-06-18 | 24.1 | 0 | 6.1 | 2023-06-18 | 16.7 | 1.3 | 0 | 2022-06-18 | 9.9 | 8.1 | 0 | 2021-06-18 | 18.6 | 0 | 0.6 | 2020-06-18 | 22.5 | 0 | 4.5 | 2019-06-18 | 20.9 | 0 | 2.9 | 2018-06-18 | 24.6 | 0 | 6.6 | 2017-06-18 | 25.5 | 0 | 7.5 | 2016-06-18 | 21.4 | 0 | 3.4 | 0.94 | 3.53
2025-06-18 | 22.4 | 0 | 4.4 | 2024-06-18 | 26.1 | 0 | 8.1 | 2023-06-18 | 17.4 | 0.6 | 0 | 2022-06-18 | 10.8 | 7.2 | 0 | 2021-06-18 | 16.8 | 1.2 | 0 | 2020-06-18 | 25.8 | 0 | 7.8 | 2019-06-18 | 22.7 | 0 | 4.7 | 2018-06-18 | 23.7 | 0 | 5.7 | 2017-06-18 | 26.5 | 0 | 8.5 | 2016-06-18 | 23.9 | 0 | 5.9 | 0.9 | 4.51
2025-06-18 | 23.3 | 0 | 5.3 | 2024-06-18 | 27.5 | 0 | 9.5 | 2023-06-18 | 17.7 | 0.3 | 0 | 2022-06-18 | 10.5 | 7.5 | 0 | 2021-06-18 | 19.7 | 0 | 1.7 | 2020-06-18 | 27.9 | 0 | 9.9 | 2019-06-18 | 23.9 | 0 | 5.9 | 2018-06-18 | 24.2 | 0 | 6.2 | 2017-06-18 | 28.7 | 0 | 10.7 | 2016-06-18 | 26.7 | 0 | 8.7 | 0.78 | 5.79
2025-06-18 | 25 | 0 | 7 | 2024-06-18 | 29.3 | 0 | 11.3 | 2023-06-18 | 18.8 | 0 | 0.8 | 2022-06-18 | 10.9 | 7.1 | 0 | 2021-06-18 | 19.9 | 0 | 1.9 | 2020-06-18 | 29.5 | 0 | 11.5 | 2019-06-18 | 24.4 | 0 | 6.4 | 2018-06-18 | 24.5 | 0 | 6.5 | 2017-06-18 | 29 | 0 | 11 | 2016-06-18 | 28.2 | 0 | 10.2 | 0.71 | 6.66
2025-06-18 | 26 | 0 | 8 | 2024-06-18 | 30.5 | 0 | 12.5 | 2023-06-18 | 19.6 | 0 | 1.6 | 2022-06-18 | 12.5 | 5.5 | 0 | 2021-06-18 | 19.3 | 0 | 1.3 | 2020-06-18 | 30.1 | 0 | 12.1 | 2019-06-18 | 25.5 | 0 | 7.5 | 2018-06-18 | 26.4 | 0 | 8.4 | 2017-06-18 | 24.7 | 0 | 6.7 | 2016-06-18 | 29.9 | 0 | 11.9 | 0.55 | 7
2025-06-18 | 26.9 | 0 | 8.9 | 2024-06-18 | 31.5 | 0 | 13.5 | 2023-06-18 | 21.1 | 0 | 3.1 | 2022-06-18 | 13.2 | 4.8 | 0 | 2021-06-18 | 18 | 0 | 0 | 2020-06-18 | 30.6 | 0 | 12.6 | 2019-06-18 | 24.8 | 0 | 6.8 | 2018-06-18 | 28.9 | 0 | 10.9 | 2017-06-18 | 29.6 | 0 | 11.6 | 2016-06-18 | 30.3 | 0 | 12.3 | 0.48 | 7.97
2025-06-18 | 26.8 | 0 | 8.8 | 2024-06-18 | 32 | 0 | 14 | 2023-06-18 | 22.3 | 0 | 4.3 | 2022-06-18 | 14.6 | 3.4 | 0 | 2021-06-18 | 17.3 | 0.7 | 0 | 2020-06-18 | 31.3 | 0 | 13.3 | 2019-06-18 | 25.9 | 0 | 7.9 | 2018-06-18 | 28.8 | 0 | 10.8 | 2017-06-18 | 28.7 | 0 | 10.7 | 2016-06-18 | 31.2 | 0 | 13.2 | 0.41 | 8.3
2025-06-18 | 28.4 | 0 | 10.4 | 2024-06-18 | 31.2 | 0 | 13.2 | 2023-06-18 | 21.3 | 0 | 3.3 | 2022-06-18 | 16.4 | 1.6 | 0 | 2021-06-18 | 16.9 | 1.1 | 0 | 2020-06-18 | 31.8 | 0 | 13.8 | 2019-06-18 | 25.9 | 0 | 7.9 | 2018-06-18 | 30.1 | 0 | 12.1 | 2017-06-18 | 30.8 | 0 | 12.8 | 2016-06-18 | 31.1 | 0 | 13.1 | 0.27 | 8.66
2025-06-18 | 28.6 | 0 | 10.6 | 2024-06-18 | 31.9 | 0 | 13.9 | 2023-06-18 | 21.2 | 0 | 3.2 | 2022-06-18 | 16.1 | 1.9 | 0 | 2021-06-18 | 17.4 | 0.6 | 0 | 2020-06-18 | 31.4 | 0 | 13.4 | 2019-06-18 | 26.3 | 0 | 8.3 | 2018-06-18 | 27.3 | 0 | 9.3 | 2017-06-18 | 29.4 | 0 | 11.4 | 2016-06-18 | 30.9 | 0 | 12.9 | 0.25 | 8.3
2025-06-18 | 29.2 | 0 | 11.2 | 2024-06-18 | 31.5 | 0 | 13.5 | 2023-06-18 | 21.5 | 0 | 3.5 | 2022-06-18 | 15.7 | 2.3 | 0 | 2021-06-18 | 17.2 | 0.8 | 0 | 2020-06-18 | 31 | 0 | 13 | 2019-06-18 | 25.9 | 0 | 7.9 | 2018-06-18 | 25.5 | 0 | 7.5 | 2017-06-18 | 29.7 | 0 | 11.7 | 2016-06-18 | 30.2 | 0 | 12.2 | 0.31 | 8.05
2025-06-18 | 28.9 | 0 | 10.9 | 2024-06-18 | 30.5 | 0 | 12.5 | 2023-06-18 | 21.5 | 0 | 3.5 | 2022-06-18 | 15 | 3 | 0 | 2021-06-18 | 17.2 | 0.8 | 0 | 2020-06-18 | 29.9 | 0 | 11.9 | 2019-06-18 | 24.8 | 0 | 6.8 | 2018-06-18 | 22.6 | 0 | 4.6 | 2017-06-18 | 28.8 | 0 | 10.8 | 2016-06-18 | 27.9 | 0 | 9.9 | 0.38 | 7.09
2025-06-18 | 27.4 | 0 | 9.4 | 2024-06-18 | 28.3 | 0 | 10.3 | 2023-06-18 | 20.2 | 0 | 2.2 | 2022-06-18 | 13.6 | 4.4 | 0 | 2021-06-18 | 17 | 1 | 0 | 2020-06-18 | 27.8 | 0 | 9.8 | 2019-06-18 | 22.7 | 0 | 4.7 | 2018-06-18 | 21.8 | 0 | 3.8 | 2017-06-18 | 26.7 | 0 | 8.7 | 2016-06-18 | 27.2 | 0 | 9.2 | 0.54 | 5.81
2025-06-18 | 25.4 | 0 | 7.4 | 2024-06-18 | 26.8 | 0 | 8.8 | 2023-06-18 | 17 | 1 | 0 | 2022-06-18 | 12.6 | 5.4 | 0 | 2021-06-18 | 16.9 | 1.1 | 0 | 2020-06-18 | 25.4 | 0 | 7.4 | 2019-06-18 | 21 | 0 | 3 | 2018-06-18 | 20.9 | 0 | 2.9 | 2017-06-18 | 25.7 | 0 | 7.7 | 2016-06-18 | 25.1 | 0 | 7.1 | 0.75 | 4.43
2025-06-18 | 22.2 | 0 | 4.2 | 2024-06-18 | 25.5 | 0 | 7.5 | 2023-06-18 | 16.4 | 1.6 | 0 | 2022-06-18 | 11.7 | 6.3 | 0 | 2021-06-18 | 17.1 | 0.9 | 0 | 2020-06-18 | 24.9 | 0 | 6.9 | 2019-06-18 | 19.9 | 0 | 1.9 | 2018-06-18 | 20 | 0 | 2 | 2017-06-18 | 24.8 | 0 | 6.8 | 2016-06-18 | 23.7 | 0 | 5.7 | 0.88 | 3.5
2025-06-18 | 22.9 | 0 | 4.9 | 2024-06-18 | 24.8 | 0 | 6.8 | 2023-06-18 | 15.8 | 2.2 | 0 | 2022-06-18 | 11.5 | 6.5 | 0 | 2021-06-18 | 17.1 | 0.9 | 0 | 2020-06-18 | 22.2 | 0 | 4.2 | 2019-06-18 | 18.8 | 0 | 0.8 | 2018-06-18 | 18 | 0 | 0 | 2017-06-18 | 22.9 | 0 | 4.9 | 2016-06-18 | 22.1 | 0 | 4.1 | 0.96 | 2.57
2025-06-18 | 23 | 0 | 5 | 2024-06-18 | 24.5 | 0 | 6.5 | 2023-06-18 | 16.3 | 1.7 | 0 | 2022-06-18 | 11.2 | 6.8 | 0 | 2021-06-18 | 17.1 | 0.9 | 0 | 2020-06-18 | 21.2 | 0 | 3.2 | 2019-06-18 | 18.6 | 0 | 0.6 | 2018-06-18 | 17.4 | 0.6 | 0 | 2017-06-18 | 22.1 | 0 | 4.1 | 2016-06-18 | 21.1 | 0 | 3.1 | 1 | 2.25
2025-06-19 | 22.7 | 0 | 4.7 | 2024-06-19 | 24 | 0 | 6 | 2023-06-19 | 16.1 | 1.9 | 0 | 2022-06-19 | 10.9 | 7.1 | 0 | 2021-06-19 | 16.4 | 1.6 | 0 | 2020-06-19 | 20.6 | 0 | 2.6 | 2019-06-19 | 18.6 | 0 | 0.6 | 2018-06-19 | 17.2 | 0.8 | 0 | 2017-06-19 | 21.8 | 0 | 3.8 | 2016-06-19 | 19.9 | 0 | 1.9 | 1.14 | 1.96
2025-06-19 | 20.5 | 0 | 2.5 | 2024-06-19 | 22.9 | 0 | 4.9 | 2023-06-19 | 15.7 | 2.3 | 0 | 2022-06-19 | 10.3 | 7.7 | 0 | 2021-06-19 | 16.2 | 1.8 | 0 | 2020-06-19 | 18.9 | 0 | 0.9 | 2019-06-19 | 17.6 | 0.4 | 0 | 2018-06-19 | 16.7 | 1.3 | 0 | 2017-06-19 | 21.6 | 0 | 3.6 | 2016-06-19 | 18.8 | 0 | 0.8 | 1.35 | 1.27
2025-06-19 | 20.5 | 0 | 2.5 | 2024-06-19 | 22.7 | 0 | 4.7 | 2023-06-19 | 15.4 | 2.6 | 0 | 2022-06-19 | 8.9 | 9.1 | 0 | 2021-06-19 | 16.2 | 1.8 | 0 | 2020-06-19 | 17.9 | 0.1 | 0 | 2019-06-19 | 17.3 | 0.7 | 0 | 2018-06-19 | 15.7 | 2.3 | 0 | 2017-06-19 | 21.2 | 0 | 3.2 | 2016-06-19 | 16.9 | 1.1 | 0 | 1.77 | 1.04
2025-06-19 | 20.4 | 0 | 2.4 | 2024-06-19 | 22.7 | 0 | 4.7 | 2023-06-19 | 15 | 3 | 0 | 2022-06-19 | 8.8 | 9.2 | 0 | 2021-06-19 | 16 | 2 | 0 | 2020-06-19 | 18 | 0 | 0 | 2019-06-19 | 16.3 | 1.7 | 0 | 2018-06-19 | 14.3 | 3.7 | 0 | 2017-06-19 | 20.8 | 0 | 2.8 | 2016-06-19 | 16.3 | 1.7 | 0 | 2.13 | 0.99
2025-06-19 | 20.4 | 0 | 2.4 | 2024-06-19 | 22 | 0 | 4 | 2023-06-19 | 14.5 | 3.5 | 0 | 2022-06-19 | 8.5 | 9.5 | 0 | 2021-06-19 | 15.2 | 2.8 | 0 | 2020-06-19 | 17.5 | 0.5 | 0 | 2019-06-19 | 16.8 | 1.2 | 0 | 2018-06-19 | 13.5 | 4.5 | 0 | 2017-06-19 | 20.6 | 0 | 2.6 | 2016-06-19 | 16.1 | 1.9 | 0 | 2.39 | 0.9
2025-06-19 | 20.1 | 0 | 2.1 | 2024-06-19 | 22.4 | 0 | 4.4 | 2023-06-19 | 14.2 | 3.8 | 0 | 2022-06-19 | 8.7 | 9.3 | 0 | 2021-06-19 | 15.3 | 2.7 | 0 | 2020-06-19 | 17.9 | 0.1 | 0 | 2019-06-19 | 14.3 | 3.7 | 0 | 2018-06-19 | 12.6 | 5.4 | 0 | 2017-06-19 | 20 | 0 | 2 | 2016-06-19 | 16.5 | 1.5 | 0 | 2.65 | 0.85
2025-06-19 | 20.2 | 0 | 2.2 | 2024-06-19 | 23 | 0 | 5 | 2023-06-19 | 14.4 | 3.6 | 0 | 2022-06-19 | 9.9 | 8.1 | 0 | 2021-06-19 | 16.6 | 1.4 | 0 | 2020-06-19 | 20.1 | 0 | 2.1 | 2019-06-19 | 17.5 | 0.5 | 0 | 2018-06-19 | 13.8 | 4.2 | 0 | 2017-06-19 | 21 | 0 | 3 | 2016-06-19 | 19.1 | 0 | 1.1 | 1.78 | 1.34
2025-06-19 | 21.2 | 0 | 3.2 | 2024-06-19 | 25.8 | 0 | 7.8 | 2023-06-19 | 14 | 4 | 0 | 2022-06-19 | 11.3 | 6.7 | 0 | 2021-06-19 | 19.3 | 0 | 1.3 | 2020-06-19 | 22 | 0 | 4 | 2019-06-19 | 19.9 | 0 | 1.9 | 2018-06-19 | 14.7 | 3.3 | 0 | 2017-06-19 | 21.1 | 0 | 3.1 | 2016-06-19 | 20.9 | 0 | 2.9 | 1.4 | 2.42
2025-06-19 | 21.9 | 0 | 3.9 | 2024-06-19 | 28.5 | 0 | 10.5 | 2023-06-19 | 14.5 | 3.5 | 0 | 2022-06-19 | 12.6 | 5.4 | 0 | 2021-06-19 | 20.9 | 0 | 2.9 | 2020-06-19 | 23.9 | 0 | 5.9 | 2019-06-19 | 22.5 | 0 | 4.5 | 2018-06-19 | 15.8 | 2.2 | 0 | 2017-06-19 | 21.8 | 0 | 3.8 | 2016-06-19 | 24.4 | 0 | 6.4 | 1.11 | 3.79
2025-06-19 | 22.3 | 0 | 4.3 | 2024-06-19 | 29.6 | 0 | 11.6 | 2023-06-19 | 16.2 | 1.8 | 0 | 2022-06-19 | 14.8 | 3.2 | 0 | 2021-06-19 | 22.6 | 0 | 4.6 | 2020-06-19 | 25.8 | 0 | 7.8 | 2019-06-19 | 23.4 | 0 | 5.4 | 2018-06-19 | 17 | 1 | 0 | 2017-06-19 | 21.2 | 0 | 3.2 | 2016-06-19 | 26.4 | 0 | 8.4 | 0.6 | 4.53
2025-06-19 | 22.9 | 0 | 4.9 | 2024-06-19 | 30.1 | 0 | 12.1 | 2023-06-19 | 17 | 1 | 0 | 2022-06-19 | 16.2 | 1.8 | 0 | 2021-06-19 | 23.1 | 0 | 5.1 | 2020-06-19 | 27.4 | 0 | 9.4 | 2019-06-19 | 24.7 | 0 | 6.7 | 2018-06-19 | 18.3 | 0 | 0.3 | 2017-06-19 | 21.9 | 0 | 3.9 | 2016-06-19 | 28.8 | 0 | 10.8 | 0.28 | 5.32
2025-06-19 | 22.7 | 0 | 4.7 | 2024-06-19 | 31.1 | 0 | 13.1 | 2023-06-19 | 18.2 | 0 | 0.2 | 2022-06-19 | 17.1 | 0.9 | 0 | 2021-06-19 | 23.6 | 0 | 5.6 | 2020-06-19 | 28.7 | 0 | 10.7 | 2019-06-19 | 25.7 | 0 | 7.7 | 2018-06-19 | 19.6 | 0 | 1.6 | 2017-06-19 | 24.8 | 0 | 6.8 | 2016-06-19 | 29.5 | 0 | 11.5 | 0.09 | 6.19
2025-06-19 | 24.2 | 0 | 6.2 | 2024-06-19 | 30.2 | 0 | 12.2 | 2023-06-19 | 19.4 | 0 | 1.4 | 2022-06-19 | 18.3 | 0 | 0.3 | 2021-06-19 | 24.4 | 0 | 6.4 | 2020-06-19 | 29.4 | 0 | 11.4 | 2019-06-19 | 25.2 | 0 | 7.2 | 2018-06-19 | 21.1 | 0 | 3.1 | 2017-06-19 | 24.5 | 0 | 6.5 | 2016-06-19 | 31.2 | 0 | 13.2 | 0 | 6.79
2025-06-19 | 24.4 | 0 | 6.4 | 2024-06-19 | 32.3 | 0 | 14.3 | 2023-06-19 | 20.8 | 0 | 2.8 | 2022-06-19 | 19.6 | 0 | 1.6 | 2021-06-19 | 24.2 | 0 | 6.2 | 2020-06-19 | 29.4 | 0 | 11.4 | 2019-06-19 | 26.7 | 0 | 8.7 | 2018-06-19 | 22.2 | 0 | 4.2 | 2017-06-19 | 24.2 | 0 | 6.2 | 2016-06-19 | 32.4 | 0 | 14.4 | 0 | 7.62
2025-06-19 | 25.1 | 0 | 7.1 | 2024-06-19 | 32.2 | 0 | 14.2 | 2023-06-19 | 20.8 | 0 | 2.8 | 2022-06-19 | 20.6 | 0 | 2.6 | 2021-06-19 | 25.4 | 0 | 7.4 | 2020-06-19 | 30.3 | 0 | 12.3 | 2019-06-19 | 23 | 0 | 5 | 2018-06-19 | 23.3 | 0 | 5.3 | 2017-06-19 | 25.4 | 0 | 7.4 | 2016-06-19 | 32.8 | 0 | 14.8 | 0 | 7.89
2025-06-19 | 26.5 | 0 | 8.5 | 2024-06-19 | 33.2 | 0 | 15.2 | 2023-06-19 | 21.4 | 0 | 3.4 | 2022-06-19 | 21.5 | 0 | 3.5 | 2021-06-19 | 26.2 | 0 | 8.2 | 2020-06-19 | 30.2 | 0 | 12.2 | 2019-06-19 | 23.1 | 0 | 5.1 | 2018-06-19 | 24 | 0 | 6 | 2017-06-19 | 26.3 | 0 | 8.3 | 2016-06-19 | 32.9 | 0 | 14.9 | 0 | 8.53
2025-06-19 | 26.5 | 0 | 8.5 | 2024-06-19 | 30.7 | 0 | 12.7 | 2023-06-19 | 22 | 0 | 4 | 2022-06-19 | 21.6 | 0 | 3.6 | 2021-06-19 | 25.9 | 0 | 7.9 | 2020-06-19 | 30.5 | 0 | 12.5 | 2019-06-19 | 19.6 | 0 | 1.6 | 2018-06-19 | 23.9 | 0 | 5.9 | 2017-06-19 | 25.5 | 0 | 7.5 | 2016-06-19 | 33 | 0 | 15 | 0 | 7.92
2025-06-19 | 26.4 | 0 | 8.4 | 2024-06-19 | 31.5 | 0 | 13.5 | 2023-06-19 | 22 | 0 | 4 | 2022-06-19 | 21.3 | 0 | 3.3 | 2021-06-19 | 25.8 | 0 | 7.8 | 2020-06-19 | 30.2 | 0 | 12.2 | 2019-06-19 | 21.3 | 0 | 3.3 | 2018-06-19 | 23.9 | 0 | 5.9 | 2017-06-19 | 25.5 | 0 | 7.5 | 2016-06-19 | 31.4 | 0 | 13.4 | 0 | 7.93
2025-06-19 | 26.2 | 0 | 8.2 | 2024-06-19 | 30.6 | 0 | 12.6 | 2023-06-19 | 22.1 | 0 | 4.1 | 2022-06-19 | 20.8 | 0 | 2.8 | 2021-06-19 | 25.2 | 0 | 7.2 | 2020-06-19 | 29.3 | 0 | 11.3 | 2019-06-19 | 21.6 | 0 | 3.6 | 2018-06-19 | 23.4 | 0 | 5.4 | 2017-06-19 | 24.8 | 0 | 6.8 | 2016-06-19 | 30.2 | 0 | 12.2 | 0 | 7.42
2025-06-19 | 24.3 | 0 | 6.3 | 2024-06-19 | 29.3 | 0 | 11.3 | 2023-06-19 | 20.6 | 0 | 2.6 | 2022-06-19 | 19.6 | 0 | 1.6 | 2021-06-19 | 23.7 | 0 | 5.7 | 2020-06-19 | 27.6 | 0 | 9.6 | 2019-06-19 | 22.4 | 0 | 4.4 | 2018-06-19 | 22 | 0 | 4 | 2017-06-19 | 23.5 | 0 | 5.5 | 2016-06-19 | 28.1 | 0 | 10.1 | 0 | 6.11
2025-06-19 | 22.7 | 0 | 4.7 | 2024-06-19 | 28 | 0 | 10 | 2023-06-19 | 18.4 | 0 | 0.4 | 2022-06-19 | 16.1 | 1.9 | 0 | 2021-06-19 | 22.2 | 0 | 4.2 | 2020-06-19 | 24.6 | 0 | 6.6 | 2019-06-19 | 21.1 | 0 | 3.1 | 2018-06-19 | 19.9 | 0 | 1.9 | 2017-06-19 | 22.6 | 0 | 4.6 | 2016-06-19 | 26.2 | 0 | 8.2 | 0.19 | 4.37
2025-06-19 | 21.8 | 0 | 3.8 | 2024-06-19 | 26.8 | 0 | 8.8 | 2023-06-19 | 17.8 | 0.2 | 0 | 2022-06-19 | 14.2 | 3.8 | 0 | 2021-06-19 | 19.1 | 0 | 1.1 | 2020-06-19 | 23.9 | 0 | 5.9 | 2019-06-19 | 21.1 | 0 | 3.1 | 2018-06-19 | 18 | 0 | 0 | 2017-06-19 | 21.1 | 0 | 3.1 | 2016-06-19 | 24.8 | 0 | 6.8 | 0.4 | 3.26
2025-06-19 | 20 | 0 | 2 | 2024-06-19 | 26.6 | 0 | 8.6 | 2023-06-19 | 15 | 3 | 0 | 2022-06-19 | 13.9 | 4.1 | 0 | 2021-06-19 | 18.6 | 0 | 0.6 | 2020-06-19 | 23.1 | 0 | 5.1 | 2019-06-19 | 20.1 | 0 | 2.1 | 2018-06-19 | 16.1 | 1.9 | 0 | 2017-06-19 | 20.5 | 0 | 2.5 | 2016-06-19 | 23.4 | 0 | 5.4 | 0.9 | 2.63
2025-06-19 | 18.1 | 0 | 0.1 | 2024-06-19 | 26 | 0 | 8 | 2023-06-19 | 14.8 | 3.2 | 0 | 2022-06-19 | 14.2 | 3.8 | 0 | 2021-06-19 | 19.6 | 0 | 1.6 | 2020-06-19 | 21.8 | 0 | 3.8 | 2019-06-19 | 19.1 | 0 | 1.1 | 2018-06-19 | 13.4 | 4.6 | 0 | 2017-06-19 | 20.4 | 0 | 2.4 | 2016-06-19 | 22.4 | 0 | 4.4 | 1.16 | 2.14
2025-06-20 | 15.9 | 2.1 | 0 | 2024-06-20 | 24.8 | 0 | 6.8 | 2023-06-20 | 14.3 | 3.7 | 0 | 2022-06-20 | 14.6 | 3.4 | 0 | 2021-06-20 | 17.8 | 0.2 | 0 | 2020-06-20 | 19.9 | 0 | 1.9 | 2019-06-20 | 18.3 | 0 | 0.3 | 2018-06-20 | 13.8 | 4.2 | 0 | 2017-06-20 | 18.3 | 0 | 0.3 | 2016-06-20 | 21.9 | 0 | 3.9 | 1.36 | 1.32
2025-06-20 | 15.4 | 2.6 | 0 | 2024-06-20 | 24.3 | 0 | 6.3 | 2023-06-20 | 13.7 | 4.3 | 0 | 2022-06-20 | 13.9 | 4.1 | 0 | 2021-06-20 | 17.7 | 0.3 | 0 | 2020-06-20 | 19.5 | 0 | 1.5 | 2019-06-20 | 18.4 | 0 | 0.4 | 2018-06-20 | 12.7 | 5.3 | 0 | 2017-06-20 | 17.5 | 0.5 | 0 | 2016-06-20 | 20.7 | 0 | 2.7 | 1.71 | 1.09
2025-06-20 | 15.2 | 2.8 | 0 | 2024-06-20 | 23.9 | 0 | 5.9 | 2023-06-20 | 12.4 | 5.6 | 0 | 2022-06-20 | 11.3 | 6.7 | 0 | 2021-06-20 | 16 | 2 | 0 | 2020-06-20 | 18.8 | 0 | 0.8 | 2019-06-20 | 17.8 | 0.2 | 0 | 2018-06-20 | 12.1 | 5.9 | 0 | 2017-06-20 | 17.2 | 0.8 | 0 | 2016-06-20 | 20.2 | 0 | 2.2 | 2.4 | 0.89
2025-06-20 | 15 | 3 | 0 | 2024-06-20 | 23.3 | 0 | 5.3 | 2023-06-20 | 12 | 6 | 0 | 2022-06-20 | 10.5 | 7.5 | 0 | 2021-06-20 | 16 | 2 | 0 | 2020-06-20 | 18.5 | 0 | 0.5 | 2019-06-20 | 17.6 | 0.4 | 0 | 2018-06-20 | 10.9 | 7.1 | 0 | 2017-06-20 | 17.1 | 0.9 | 0 | 2016-06-20 | 17.9 | 0.1 | 0 | 2.7 | 0.58
2025-06-20 | 14.8 | 3.2 | 0 | 2024-06-20 | 23.3 | 0 | 5.3 | 2023-06-20 | 12.1 | 5.9 | 0 | 2022-06-20 | 9.9 | 8.1 | 0 | 2021-06-20 | 14.5 | 3.5 | 0 | 2020-06-20 | 17.7 | 0.3 | 0 | 2019-06-20 | 17.6 | 0.4 | 0 | 2018-06-20 | 10.6 | 7.4 | 0 | 2017-06-20 | 16.5 | 1.5 | 0 | 2016-06-20 | 18.3 | 0 | 0.3 | 3.03 | 0.56
2025-06-20 | 14.3 | 3.7 | 0 | 2024-06-20 | 23.2 | 0 | 5.2 | 2023-06-20 | 12.6 | 5.4 | 0 | 2022-06-20 | 9.4 | 8.6 | 0 | 2021-06-20 | 14 | 4 | 0 | 2020-06-20 | 18.1 | 0 | 0.1 | 2019-06-20 | 17.2 | 0.8 | 0 | 2018-06-20 | 10.8 | 7.2 | 0 | 2017-06-20 | 15.8 | 2.2 | 0 | 2016-06-20 | 18.1 | 0 | 0.1 | 3.19 | 0.54
2025-06-20 | 14.2 | 3.8 | 0 | 2024-06-20 | 24.5 | 0 | 6.5 | 2023-06-20 | 14.4 | 3.6 | 0 | 2022-06-20 | 12 | 6 | 0 | 2021-06-20 | 17.8 | 0.2 | 0 | 2020-06-20 | 20 | 0 | 2 | 2019-06-20 | 17.5 | 0.5 | 0 | 2018-06-20 | 13.4 | 4.6 | 0 | 2017-06-20 | 15.5 | 2.5 | 0 | 2016-06-20 | 19.7 | 0 | 1.7 | 2.12 | 1.02
2025-06-20 | 13.9 | 4.1 | 0 | 2024-06-20 | 27.2 | 0 | 9.2 | 2023-06-20 | 16.8 | 1.2 | 0 | 2022-06-20 | 14.4 | 3.6 | 0 | 2021-06-20 | 19.2 | 0 | 1.2 | 2020-06-20 | 22.7 | 0 | 4.7 | 2019-06-20 | 18.2 | 0 | 0.2 | 2018-06-20 | 17.2 | 0.8 | 0 | 2017-06-20 | 16.4 | 1.6 | 0 | 2016-06-20 | 23.1 | 0 | 5.1 | 1.13 | 2.04
2025-06-20 | 13.9 | 4.1 | 0 | 2024-06-20 | 27.8 | 0 | 9.8 | 2023-06-20 | 19.7 | 0 | 1.7 | 2022-06-20 | 15.5 | 2.5 | 0 | 2021-06-20 | 21 | 0 | 3 | 2020-06-20 | 25.1 | 0 | 7.1 | 2019-06-20 | 18.7 | 0 | 0.7 | 2018-06-20 | 19.2 | 0 | 1.2 | 2017-06-20 | 17.9 | 0.1 | 0 | 2016-06-20 | 25.6 | 0 | 7.6 | 0.67 | 3.11
2025-06-20 | 15.3 | 2.7 | 0 | 2024-06-20 | 27.2 | 0 | 9.2 | 2023-06-20 | 21.4 | 0 | 3.4 | 2022-06-20 | 18.2 | 0 | 0.2 | 2021-06-20 | 21.8 | 0 | 3.8 | 2020-06-20 | 27.2 | 0 | 9.2 | 2019-06-20 | 18.4 | 0 | 0.4 | 2018-06-20 | 22 | 0 | 4 | 2017-06-20 | 19.3 | 0 | 1.3 | 2016-06-20 | 27.1 | 0 | 9.1 | 0.27 | 4.06
2025-06-20 | 17.2 | 0.8 | 0 | 2024-06-20 | 27.9 | 0 | 9.9 | 2023-06-20 | 23 | 0 | 5 | 2022-06-20 | 20.4 | 0 | 2.4 | 2021-06-20 | 24.3 | 0 | 6.3 | 2020-06-20 | 29.4 | 0 | 11.4 | 2019-06-20 | 18.1 | 0 | 0.1 | 2018-06-20 | 23.9 | 0 | 5.9 | 2017-06-20 | 20.5 | 0 | 2.5 | 2016-06-20 | 28.5 | 0 | 10.5 | 0.08 | 5.4
2025-06-20 | 18.8 | 0 | 0.8 | 2024-06-20 | 28.3 | 0 | 10.3 | 2023-06-20 | 24.4 | 0 | 6.4 | 2022-06-20 | 21.6 | 0 | 3.6 | 2021-06-20 | 24.4 | 0 | 6.4 | 2020-06-20 | 29.8 | 0 | 11.8 | 2019-06-20 | 17.8 | 0.2 | 0 | 2018-06-20 | 24.9 | 0 | 6.9 | 2017-06-20 | 22.2 | 0 | 4.2 | 2016-06-20 | 29.8 | 0 | 11.8 | 0.02 | 6.22
2025-06-20 | 20 | 0 | 2 | 2024-06-20 | 29.1 | 0 | 11.1 | 2023-06-20 | 24.8 | 0 | 6.8 | 2022-06-20 | 22.3 | 0 | 4.3 | 2021-06-20 | 25 | 0 | 7 | 2020-06-20 | 31.2 | 0 | 13.2 | 2019-06-20 | 17.2 | 0.8 | 0 | 2018-06-20 | 26.4 | 0 | 8.4 | 2017-06-20 | 23.9 | 0 | 5.9 | 2016-06-20 | 31.2 | 0 | 13.2 | 0.08 | 7.19
2025-06-20 | 21.4 | 0 | 3.4 | 2024-06-20 | 29.1 | 0 | 11.1 | 2023-06-20 | 26.1 | 0 | 8.1 | 2022-06-20 | 22.8 | 0 | 4.8 | 2021-06-20 | 26.8 | 0 | 8.8 | 2020-06-20 | 30.9 | 0 | 12.9 | 2019-06-20 | 17 | 1 | 0 | 2018-06-20 | 27 | 0 | 9 | 2017-06-20 | 22.7 | 0 | 4.7 | 2016-06-20 | 31.5 | 0 | 13.5 | 0.1 | 7.63
2025-06-20 | 21.9 | 0 | 3.9 | 2024-06-20 | 28.8 | 0 | 10.8 | 2023-06-20 | 27.4 | 0 | 9.4 | 2022-06-20 | 23.8 | 0 | 5.8 | 2021-06-20 | 26.8 | 0 | 8.8 | 2020-06-20 | 31.5 | 0 | 13.5 | 2019-06-20 | 17.1 | 0.9 | 0 | 2018-06-20 | 27.7 | 0 | 9.7 | 2017-06-20 | 23.8 | 0 | 5.8 | 2016-06-20 | 31.6 | 0 | 13.6 | 0.09 | 8.13
2025-06-20 | 22.2 | 0 | 4.2 | 2024-06-20 | 27.6 | 0 | 9.6 | 2023-06-20 | 27.5 | 0 | 9.5 | 2022-06-20 | 24.3 | 0 | 6.3 | 2021-06-20 | 27.5 | 0 | 9.5 | 2020-06-20 | 31.5 | 0 | 13.5 | 2019-06-20 | 17.9 | 0.1 | 0 | 2018-06-20 | 28.3 | 0 | 10.3 | 2017-06-20 | 21.5 | 0 | 3.5 | 2016-06-20 | 30.7 | 0 | 12.7 | 0.01 | 7.91
2025-06-20 | 22.1 | 0 | 4.1 | 2024-06-20 | 27.1 | 0 | 9.1 | 2023-06-20 | 28.1 | 0 | 10.1 | 2022-06-20 | 24.5 | 0 | 6.5 | 2021-06-20 | 26.9 | 0 | 8.9 | 2020-06-20 | 32.1 | 0 | 14.1 | 2019-06-20 | 17.9 | 0.1 | 0 | 2018-06-20 | 25.8 | 0 | 7.8 | 2017-06-20 | 22.4 | 0 | 4.4 | 2016-06-20 | 31.5 | 0 | 13.5 | 0.01 | 7.85
2025-06-20 | 22.1 | 0 | 4.1 | 2024-06-20 | 25.5 | 0 | 7.5 | 2023-06-20 | 27.3 | 0 | 9.3 | 2022-06-20 | 24.7 | 0 | 6.7 | 2021-06-20 | 26.9 | 0 | 8.9 | 2020-06-20 | 31.4 | 0 | 13.4 | 2019-06-20 | 18.3 | 0 | 0.3 | 2018-06-20 | 25.2 | 0 | 7.2 | 2017-06-20 | 23.7 | 0 | 5.7 | 2016-06-20 | 29.6 | 0 | 11.6 | 0 | 7.47
2025-06-20 | 21.7 | 0 | 3.7 | 2024-06-20 | 22.8 | 0 | 4.8 | 2023-06-20 | 23.5 | 0 | 5.5 | 2022-06-20 | 24.1 | 0 | 6.1 | 2021-06-20 | 25.8 | 0 | 7.8 | 2020-06-20 | 30.7 | 0 | 12.7 | 2019-06-20 | 18.1 | 0 | 0.1 | 2018-06-20 | 22.9 | 0 | 4.9 | 2017-06-20 | 22.5 | 0 | 4.5 | 2016-06-20 | 28.7 | 0 | 10.7 | 0 | 6.08
2025-06-20 | 20.6 | 0 | 2.6 | 2024-06-20 | 23.4 | 0 | 5.4 | 2023-06-20 | 23.4 | 0 | 5.4 | 2022-06-20 | 22.5 | 0 | 4.5 | 2021-06-20 | 25 | 0 | 7 | 2020-06-20 | 26.7 | 0 | 8.7 | 2019-06-20 | 18.2 | 0 | 0.2 | 2018-06-20 | 22.9 | 0 | 4.9 | 2017-06-20 | 21.4 | 0 | 3.4 | 2016-06-20 | 27.8 | 0 | 9.8 | 0 | 5.19
2025-06-20 | 18 | 0 | 0 | 2024-06-20 | 22.5 | 0 | 4.5 | 2023-06-20 | 20.4 | 0 | 2.4 | 2022-06-20 | 18.8 | 0 | 0.8 | 2021-06-20 | 23 | 0 | 5 | 2020-06-20 | 25.6 | 0 | 7.6 | 2019-06-20 | 17 | 1 | 0 | 2018-06-20 | 20.8 | 0 | 2.8 | 2017-06-20 | 20 | 0 | 2 | 2016-06-20 | 26.9 | 0 | 8.9 | 0.1 | 3.4
2025-06-20 | 18.1 | 0 | 0.1 | 2024-06-20 | 22.4 | 0 | 4.4 | 2023-06-20 | 19.1 | 0 | 1.1 | 2022-06-20 | 18.8 | 0 | 0.8 | 2021-06-20 | 20.9 | 0 | 2.9 | 2020-06-20 | 24.1 | 0 | 6.1 | 2019-06-20 | 16.5 | 1.5 | 0 | 2018-06-20 | 19.9 | 0 | 1.9 | 2017-06-20 | 19.1 | 0 | 1.1 | 2016-06-20 | 25.9 | 0 | 7.9 | 0.15 | 2.63
2025-06-20 | 15.2 | 2.8 | 0 | 2024-06-20 | 21.6 | 0 | 3.6 | 2023-06-20 | 18 | 0 | 0 | 2022-06-20 | 16.2 | 1.8 | 0 | 2021-06-20 | 19.9 | 0 | 1.9 | 2020-06-20 | 23.1 | 0 | 5.1 | 2019-06-20 | 16.8 | 1.2 | 0 | 2018-06-20 | 18.6 | 0 | 0.6 | 2017-06-20 | 17.7 | 0.3 | 0 | 2016-06-20 | 24.3 | 0 | 6.3 | 0.61 | 1.75
2025-06-20 | 14.3 | 3.7 | 0 | 2024-06-20 | 20.7 | 0 | 2.7 | 2023-06-20 | 16.4 | 1.6 | 0 | 2022-06-20 | 15.6 | 2.4 | 0 | 2021-06-20 | 19.8 | 0 | 1.8 | 2020-06-20 | 21.9 | 0 | 3.9 | 2019-06-20 | 16.5 | 1.5 | 0 | 2018-06-20 | 18.3 | 0 | 0.3 | 2017-06-20 | 17.5 | 0.5 | 0 | 2016-06-20 | 23.7 | 0 | 5.7 | 0.97 | 1.44
2025-06-21 | 14.3 | 3.7 | 0 | 2024-06-21 | 19.4 | 0 | 1.4 | 2023-06-21 | 17.2 | 0.8 | 0 | 2022-06-21 | 15.1 | 2.9 | 0 | 2021-06-21 | 19 | 0 | 1 | 2020-06-21 | 18.6 | 0 | 0.6 | 2019-06-21 | 16.5 | 1.5 | 0 | 2018-06-21 | 17.3 | 0.7 | 0 | 2017-06-21 | 17.4 | 0.6 | 0 | 2016-06-21 | 21.8 | 0 | 3.8 | 1.02 | 0.68
2025-06-21 | 13.3 | 4.7 | 0 | 2024-06-21 | 18.9 | 0 | 0.9 | 2023-06-21 | 16.6 | 1.4 | 0 | 2022-06-21 | 14.5 | 3.5 | 0 | 2021-06-21 | 18.1 | 0 | 0.1 | 2020-06-21 | 19.3 | 0 | 1.3 | 2019-06-21 | 16.4 | 1.6 | 0 | 2018-06-21 | 16.3 | 1.7 | 0 | 2017-06-21 | 15 | 3 | 0 | 2016-06-21 | 20.2 | 0 | 2.2 | 1.59 | 0.45
2025-06-21 | 12.4 | 5.6 | 0 | 2024-06-21 | 18.4 | 0 | 0.4 | 2023-06-21 | 15.1 | 2.9 | 0 | 2022-06-21 | 13.6 | 4.4 | 0 | 2021-06-21 | 17.2 | 0.8 | 0 | 2020-06-21 | 20.1 | 0 | 2.1 | 2019-06-21 | 16.1 | 1.9 | 0 | 2018-06-21 | 14.9 | 3.1 | 0 | 2017-06-21 | 14.5 | 3.5 | 0 | 2016-06-21 | 18.4 | 0 | 0.4 | 2.22 | 0.29
2025-06-21 | 10.8 | 7.2 | 0 | 2024-06-21 | 18.2 | 0 | 0.2 | 2023-06-21 | 14.7 | 3.3 | 0 | 2022-06-21 | 14.3 | 3.7 | 0 | 2021-06-21 | 17.1 | 0.9 | 0 | 2020-06-21 | 19.6 | 0 | 1.6 | 2019-06-21 | 15.9 | 2.1 | 0 | 2018-06-21 | 13.2 | 4.8 | 0 | 2017-06-21 | 14.2 | 3.8 | 0 | 2016-06-21 | 16.9 | 1.1 | 0 | 2.69 | 0.18
2025-06-21 | 9.8 | 8.2 | 0 | 2024-06-21 | 17.9 | 0.1 | 0 | 2023-06-21 | 14.3 | 3.7 | 0 | 2022-06-21 | 13.9 | 4.1 | 0 | 2021-06-21 | 17 | 1 | 0 | 2020-06-21 | 18.9 | 0 | 0.9 | 2019-06-21 | 15.6 | 2.4 | 0 | 2018-06-21 | 11.9 | 6.1 | 0 | 2017-06-21 | 14 | 4 | 0 | 2016-06-21 | 15.7 | 2.3 | 0 | 3.19 | 0.09
2025-06-21 | 10.8 | 7.2 | 0 | 2024-06-21 | 18.4 | 0 | 0.4 | 2023-06-21 | 14.9 | 3.1 | 0 | 2022-06-21 | 13.9 | 4.1 | 0 | 2021-06-21 | 16.9 | 1.1 | 0 | 2020-06-21 | 17.9 | 0.1 | 0 | 2019-06-21 | 15.7 | 2.3 | 0 | 2018-06-21 | 11.4 | 6.6 | 0 | 2017-06-21 | 14 | 4 | 0 | 2016-06-21 | 15.1 | 2.9 | 0 | 3.14 | 0.04
2025-06-21 | 14.2 | 3.8 | 0 | 2024-06-21 | 18.2 | 0 | 0.2 | 2023-06-21 | 16.2 | 1.8 | 0 | 2022-06-21 | 14 | 4 | 0 | 2021-06-21 | 18.1 | 0 | 0.1 | 2020-06-21 | 20.3 | 0 | 2.3 | 2019-06-21 | 15.7 | 2.3 | 0 | 2018-06-21 | 12.2 | 5.8 | 0 | 2017-06-21 | 14.7 | 3.3 | 0 | 2016-06-21 | 16.7 | 1.3 | 0 | 2.23 | 0.26
2025-06-21 | 16.3 | 1.7 | 0 | 2024-06-21 | 18.9 | 0 | 0.9 | 2023-06-21 | 17.2 | 0.8 | 0 | 2022-06-21 | 14.2 | 3.8 | 0 | 2021-06-21 | 18.5 | 0 | 0.5 | 2020-06-21 | 22.7 | 0 | 4.7 | 2019-06-21 | 16.5 | 1.5 | 0 | 2018-06-21 | 13.2 | 4.8 | 0 | 2017-06-21 | 15.2 | 2.8 | 0 | 2016-06-21 | 18.1 | 0 | 0.1 | 1.54 | 0.62
2025-06-21 | 20.3 | 0 | 2.3 | 2024-06-21 | 20.9 | 0 | 2.9 | 2023-06-21 | 19.2 | 0 | 1.2 | 2022-06-21 | 15.2 | 2.8 | 0 | 2021-06-21 | 20.3 | 0 | 2.3 | 2020-06-21 | 25.2 | 0 | 7.2 | 2019-06-21 | 18.3 | 0 | 0.3 | 2018-06-21 | 14.6 | 3.4 | 0 | 2017-06-21 | 16.5 | 1.5 | 0 | 2016-06-21 | 18.8 | 0 | 0.8 | 0.77 | 1.7
2025-06-21 | 21.6 | 0 | 3.6 | 2024-06-21 | 21.4 | 0 | 3.4 | 2023-06-21 | 20.4 | 0 | 2.4 | 2022-06-21 | 15.6 | 2.4 | 0 | 2021-06-21 | 22.2 | 0 | 4.2 | 2020-06-21 | 27 | 0 | 9 | 2019-06-21 | 19.1 | 0 | 1.1 | 2018-06-21 | 15.6 | 2.4 | 0 | 2017-06-21 | 16.9 | 1.1 | 0 | 2016-06-21 | 19.3 | 0 | 1.3 | 0.59 | 2.5
2025-06-21 | 23 | 0 | 5 | 2024-06-21 | 21.2 | 0 | 3.2 | 2023-06-21 | 23.1 | 0 | 5.1 | 2022-06-21 | 16.6 | 1.4 | 0 | 2021-06-21 | 22.8 | 0 | 4.8 | 2020-06-21 | 28.3 | 0 | 10.3 | 2019-06-21 | 21.1 | 0 | 3.1 | 2018-06-21 | 16.6 | 1.4 | 0 | 2017-06-21 | 18.8 | 0 | 0.8 | 2016-06-21 | 20.2 | 0 | 2.2 | 0.28 | 3.45
2025-06-21 | 23.9 | 0 | 5.9 | 2024-06-21 | 21.1 | 0 | 3.1 | 2023-06-21 | 24.7 | 0 | 6.7 | 2022-06-21 | 17.1 | 0.9 | 0 | 2021-06-21 | 24 | 0 | 6 | 2020-06-21 | 30.1 | 0 | 12.1 | 2019-06-21 | 21.3 | 0 | 3.3 | 2018-06-21 | 17.8 | 0.2 | 0 | 2017-06-21 | 20.2 | 0 | 2.2 | 2016-06-21 | 21 | 0 | 3 | 0.11 | 4.23
2025-06-21 | 25.5 | 0 | 7.5 | 2024-06-21 | 20.8 | 0 | 2.8 | 2023-06-21 | 26.1 | 0 | 8.1 | 2022-06-21 | 15.2 | 2.8 | 0 | 2021-06-21 | 23.1 | 0 | 5.1 | 2020-06-21 | 31.4 | 0 | 13.4 | 2019-06-21 | 23.7 | 0 | 5.7 | 2018-06-21 | 18.3 | 0 | 0.3 | 2017-06-21 | 21.4 | 0 | 3.4 | 2016-06-21 | 21.5 | 0 | 3.5 | 0.28 | 4.98
2025-06-21 | 26 | 0 | 8 | 2024-06-21 | 20.9 | 0 | 2.9 | 2023-06-21 | 26.9 | 0 | 8.9 | 2022-06-21 | 14.7 | 3.3 | 0 | 2021-06-21 | 25.9 | 0 | 7.9 | 2020-06-21 | 31.8 | 0 | 13.8 | 2019-06-21 | 22 | 0 | 4 | 2018-06-21 | 19.6 | 0 | 1.6 | 2017-06-21 | 22 | 0 | 4 | 2016-06-21 | 22.3 | 0 | 4.3 | 0.33 | 5.54
2025-06-21 | 26.6 | 0 | 8.6 | 2024-06-21 | 20.8 | 0 | 2.8 | 2023-06-21 | 27.5 | 0 | 9.5 | 2022-06-21 | 14.4 | 3.6 | 0 | 2021-06-21 | 27.8 | 0 | 9.8 | 2020-06-21 | 29.5 | 0 | 11.5 | 2019-06-21 | 23.1 | 0 | 5.1 | 2018-06-21 | 19.6 | 0 | 1.6 | 2017-06-21 | 22.6 | 0 | 4.6 | 2016-06-21 | 23.2 | 0 | 5.2 | 0.36 | 5.87
2025-06-21 | 26.6 | 0 | 8.6 | 2024-06-21 | 21.3 | 0 | 3.3 | 2023-06-21 | 26.9 | 0 | 8.9 | 2022-06-21 | 14.2 | 3.8 | 0 | 2021-06-21 | 28.6 | 0 | 10.6 | 2020-06-21 | 30.6 | 0 | 12.6 | 2019-06-21 | 23.4 | 0 | 5.4 | 2018-06-21 | 20.4 | 0 | 2.4 | 2017-06-21 | 23.1 | 0 | 5.1 | 2016-06-21 | 23.7 | 0 | 5.7 | 0.38 | 6.26
2025-06-21 | 25.9 | 0 | 7.9 | 2024-06-21 | 21.5 | 0 | 3.5 | 2023-06-21 | 25.9 | 0 | 7.9 | 2022-06-21 | 15.4 | 2.6 | 0 | 2021-06-21 | 28.8 | 0 | 10.8 | 2020-06-21 | 31.4 | 0 | 13.4 | 2019-06-21 | 23.1 | 0 | 5.1 | 2018-06-21 | 20.6 | 0 | 2.6 | 2017-06-21 | 22.8 | 0 | 4.8 | 2016-06-21 | 23.8 | 0 | 5.8 | 0.26 | 6.18
2025-06-21 | 24.5 | 0 | 6.5 | 2024-06-21 | 21.1 | 0 | 3.1 | 2023-06-21 | 27 | 0 | 9 | 2022-06-21 | 16.2 | 1.8 | 0 | 2021-06-21 | 28.3 | 0 | 10.3 | 2020-06-21 | 31.6 | 0 | 13.6 | 2019-06-21 | 22.7 | 0 | 4.7 | 2018-06-21 | 20.7 | 0 | 2.7 | 2017-06-21 | 22.7 | 0 | 4.7 | 2016-06-21 | 24.1 | 0 | 6.1 | 0.18 | 6.07
2025-06-21 | 23.9 | 0 | 5.9 | 2024-06-21 | 20.6 | 0 | 2.6 | 2023-06-21 | 26.3 | 0 | 8.3 | 2022-06-21 | 15.8 | 2.2 | 0 | 2021-06-21 | 28 | 0 | 10 | 2020-06-21 | 30.4 | 0 | 12.4 | 2019-06-21 | 23.3 | 0 | 5.3 | 2018-06-21 | 19.9 | 0 | 1.9 | 2017-06-21 | 22.1 | 0 | 4.1 | 2016-06-21 | 22.1 | 0 | 4.1 | 0.22 | 5.46
2025-06-21 | 22.9 | 0 | 4.9 | 2024-06-21 | 19.8 | 0 | 1.8 | 2023-06-21 | 24.8 | 0 | 6.8 | 2022-06-21 | 15.9 | 2.1 | 0 | 2021-06-21 | 24.2 | 0 | 6.2 | 2020-06-21 | 28.6 | 0 | 10.6 | 2019-06-21 | 22.2 | 0 | 4.2 | 2018-06-21 | 19 | 0 | 1 | 2017-06-21 | 21.3 | 0 | 3.3 | 2016-06-21 | 21.1 | 0 | 3.1 | 0.21 | 4.19
2025-06-21 | 22.6 | 0 | 4.6 | 2024-06-21 | 19.4 | 0 | 1.4 | 2023-06-21 | 22.2 | 0 | 4.2 | 2022-06-21 | 15.7 | 2.3 | 0 | 2021-06-21 | 22.1 | 0 | 4.1 | 2020-06-21 | 26 | 0 | 8 | 2019-06-21 | 19.7 | 0 | 1.7 | 2018-06-21 | 17.5 | 0.5 | 0 | 2017-06-21 | 17.7 | 0.3 | 0 | 2016-06-21 | 19.4 | 0 | 1.4 | 0.31 | 2.54
2025-06-21 | 23.4 | 0 | 5.4 | 2024-06-21 | 18.9 | 0 | 0.9 | 2023-06-21 | 20.5 | 0 | 2.5 | 2022-06-21 | 15.8 | 2.2 | 0 | 2021-06-21 | 21.9 | 0 | 3.9 | 2020-06-21 | 24.7 | 0 | 6.7 | 2019-06-21 | 18.4 | 0 | 0.4 | 2018-06-21 | 16.2 | 1.8 | 0 | 2017-06-21 | 17.7 | 0.3 | 0 | 2016-06-21 | 15.1 | 2.9 | 0 | 0.72 | 1.98
2025-06-21 | 23.5 | 0 | 5.5 | 2024-06-21 | 18 | 0 | 0 | 2023-06-21 | 19.9 | 0 | 1.9 | 2022-06-21 | 15.8 | 2.2 | 0 | 2021-06-21 | 21.4 | 0 | 3.4 | 2020-06-21 | 23.6 | 0 | 5.6 | 2019-06-21 | 19.1 | 0 | 1.1 | 2018-06-21 | 14.5 | 3.5 | 0 | 2017-06-21 | 15.4 | 2.6 | 0 | 2016-06-21 | 17 | 1 | 0 | 0.93 | 1.75
2025-06-21 | 21.2 | 0 | 3.2 | 2024-06-21 | 18.1 | 0 | 0.1 | 2023-06-21 | 17.6 | 0.4 | 0 | 2022-06-21 | 15.4 | 2.6 | 0 | 2021-06-21 | 19.1 | 0 | 1.1 | 2020-06-21 | 22.4 | 0 | 4.4 | 2019-06-21 | 17.3 | 0.7 | 0 | 2018-06-21 | 12.6 | 5.4 | 0 | 2017-06-21 | 14.6 | 3.4 | 0 | 2016-06-21 | 16.1 | 1.9 | 0 | 1.44 | 0.88
2025-06-22 | 21 | 0 | 3 | 2024-06-22 | 18.4 | 0 | 0.4 | 2023-06-22 | 18.2 | 0 | 0.2 | 2022-06-22 | 15 | 3 | 0 | 2021-06-22 | 17.6 | 0.4 | 0 | 2020-06-22 | 21.6 | 0 | 3.6 | 2019-06-22 | 15.4 | 2.6 | 0 | 2018-06-22 | 11.6 | 6.4 | 0 | 2017-06-22 | 13.4 | 4.6 | 0 | 2016-06-22 | 14.4 | 3.6 | 0 | 2.06 | 0.72
2025-06-22 | 21.5 | 0 | 3.5 | 2024-06-22 | 17.7 | 0.3 | 0 | 2023-06-22 | 17.6 | 0.4 | 0 | 2022-06-22 | 14.8 | 3.2 | 0 | 2021-06-22 | 16.2 | 1.8 | 0 | 2020-06-22 | 21 | 0 | 3 | 2019-06-22 | 16.2 | 1.8 | 0 | 2018-06-22 | 11.8 | 6.2 | 0 | 2017-06-22 | 13.2 | 4.8 | 0 | 2016-06-22 | 15.3 | 2.7 | 0 | 2.12 | 0.65
2025-06-22 | 20.2 | 0 | 2.2 | 2024-06-22 | 18.2 | 0 | 0.2 | 2023-06-22 | 16 | 2 | 0 | 2022-06-22 | 14.6 | 3.4 | 0 | 2021-06-22 | 14.2 | 3.8 | 0 | 2020-06-22 | 19.9 | 0 | 1.9 | 2019-06-22 | 15.4 | 2.6 | 0 | 2018-06-22 | 9.6 | 8.4 | 0 | 2017-06-22 | 14.6 | 3.4 | 0 | 2016-06-22 | 14.8 | 3.2 | 0 | 2.68 | 0.43
2025-06-22 | 19.3 | 0 | 1.3 | 2024-06-22 | 17.1 | 0.9 | 0 | 2023-06-22 | 15.6 | 2.4 | 0 | 2022-06-22 | 14.5 | 3.5 | 0 | 2021-06-22 | 12.7 | 5.3 | 0 | 2020-06-22 | 19.7 | 0 | 1.7 | 2019-06-22 | 15.3 | 2.7 | 0 | 2018-06-22 | 8.8 | 9.2 | 0 | 2017-06-22 | 13.3 | 4.7 | 0 | 2016-06-22 | 15.4 | 2.6 | 0 | 3.13 | 0.3
2025-06-22 | 19.4 | 0 | 1.4 | 2024-06-22 | 17.3 | 0.7 | 0 | 2023-06-22 | 15.4 | 2.6 | 0 | 2022-06-22 | 14.4 | 3.6 | 0 | 2021-06-22 | 11.8 | 6.2 | 0 | 2020-06-22 | 19.5 | 0 | 1.5 | 2019-06-22 | 14 | 4 | 0 | 2018-06-22 | 8.8 | 9.2 | 0 | 2017-06-22 | 11.8 | 6.2 | 0 | 2016-06-22 | 14.3 | 3.7 | 0 | 3.62 | 0.29
2025-06-22 | 19.2 | 0 | 1.2 | 2024-06-22 | 16.6 | 1.4 | 0 | 2023-06-22 | 15.2 | 2.8 | 0 | 2022-06-22 | 14.8 | 3.2 | 0 | 2021-06-22 | 11 | 7 | 0 | 2020-06-22 | 20.4 | 0 | 2.4 | 2019-06-22 | 15.3 | 2.7 | 0 | 2018-06-22 | 9.7 | 8.3 | 0 | 2017-06-22 | 12.3 | 5.7 | 0 | 2016-06-22 | 13.7 | 4.3 | 0 | 3.54 | 0.36
2025-06-22 | 19.8 | 0 | 1.8 | 2024-06-22 | 17.4 | 0.6 | 0 | 2023-06-22 | 17.6 | 0.4 | 0 | 2022-06-22 | 16.9 | 1.1 | 0 | 2021-06-22 | 10.5 | 7.5 | 0 | 2020-06-22 | 21.4 | 0 | 3.4 | 2019-06-22 | 16.5 | 1.5 | 0 | 2018-06-22 | 13.5 | 4.5 | 0 | 2017-06-22 | 15 | 3 | 0 | 2016-06-22 | 13.6 | 4.4 | 0 | 2.3 | 0.52
2025-06-22 | 21.1 | 0 | 3.1 | 2024-06-22 | 18 | 0 | 0 | 2023-06-22 | 20.1 | 0 | 2.1 | 2022-06-22 | 18.2 | 0 | 0.2 | 2021-06-22 | 10.7 | 7.3 | 0 | 2020-06-22 | 23.1 | 0 | 5.1 | 2019-06-22 | 17.5 | 0.5 | 0 | 2018-06-22 | 15.2 | 2.8 | 0 | 2017-06-22 | 17.1 | 0.9 | 0 | 2016-06-22 | 16.1 | 1.9 | 0 | 1.34 | 1.05
2025-06-22 | 23.6 | 0 | 5.6 | 2024-06-22 | 18.7 | 0 | 0.7 | 2023-06-22 | 22.2 | 0 | 4.2 | 2022-06-22 | 19.9 | 0 | 1.9 | 2021-06-22 | 11.8 | 6.2 | 0 | 2020-06-22 | 25.4 | 0 | 7.4 | 2019-06-22 | 18.6 | 0 | 0.6 | 2018-06-22 | 16.9 | 1.1 | 0 | 2017-06-22 | 19 | 0 | 1 | 2016-06-22 | 16.8 | 1.2 | 0 | 0.85 | 2.14
2025-06-22 | 25.1 | 0 | 7.1 | 2024-06-22 | 18.6 | 0 | 0.6 | 2023-06-22 | 23.9 | 0 | 5.9 | 2022-06-22 | 21.4 | 0 | 3.4 | 2021-06-22 | 13.6 | 4.4 | 0 | 2020-06-22 | 27.1 | 0 | 9.1 | 2019-06-22 | 20 | 0 | 2 | 2018-06-22 | 18.9 | 0 | 0.9 | 2017-06-22 | 20.6 | 0 | 2.6 | 2016-06-22 | 17.9 | 0.1 | 0 | 0.45 | 3.16
2025-06-22 | 26.3 | 0 | 8.3 | 2024-06-22 | 19.1 | 0 | 1.1 | 2023-06-22 | 24.6 | 0 | 6.6 | 2022-06-22 | 23.6 | 0 | 5.6 | 2021-06-22 | 14.2 | 3.8 | 0 | 2020-06-22 | 28.5 | 0 | 10.5 | 2019-06-22 | 22.1 | 0 | 4.1 | 2018-06-22 | 20.8 | 0 | 2.8 | 2017-06-22 | 22.6 | 0 | 4.6 | 2016-06-22 | 17.5 | 0.5 | 0 | 0.43 | 4.36
2025-06-22 | 27.6 | 0 | 9.6 | 2024-06-22 | 20.2 | 0 | 2.2 | 2023-06-22 | 25.9 | 0 | 7.9 | 2022-06-22 | 24.5 | 0 | 6.5 | 2021-06-22 | 15.3 | 2.7 | 0 | 2020-06-22 | 30.1 | 0 | 12.1 | 2019-06-22 | 22.7 | 0 | 4.7 | 2018-06-22 | 22.1 | 0 | 4.1 | 2017-06-22 | 22.8 | 0 | 4.8 | 2016-06-22 | 18 | 0 | 0 | 0.27 | 5.19
2025-06-22 | 27.7 | 0 | 9.7 | 2024-06-22 | 20.4 | 0 | 2.4 | 2023-06-22 | 26.4 | 0 | 8.4 | 2022-06-22 | 25.9 | 0 | 7.9 | 2021-06-22 | 15.3 | 2.7 | 0 | 2020-06-22 | 31.8 | 0 | 13.8 | 2019-06-22 | 24 | 0 | 6 | 2018-06-22 | 23.1 | 0 | 5.1 | 2017-06-22 | 23.2 | 0 | 5.2 | 2016-06-22 | 18.8 | 0 | 0.8 | 0.27 | 5.93
2025-06-22 | 28.1 | 0 | 10.1 | 2024-06-22 | 21.1 | 0 | 3.1 | 2023-06-22 | 27.3 | 0 | 9.3 | 2022-06-22 | 27.4 | 0 | 9.4 | 2021-06-22 | 14.8 | 3.2 | 0 | 2020-06-22 | 32.1 | 0 | 14.1 | 2019-06-22 | 24.1 | 0 | 6.1 | 2018-06-22 | 24.5 | 0 | 6.5 | 2017-06-22 | 23.2 | 0 | 5.2 | 2016-06-22 | 21.1 | 0 | 3.1 | 0.32 | 6.69
2025-06-22 | 29.1 | 0 | 11.1 | 2024-06-22 | 20.7 | 0 | 2.7 | 2023-06-22 | 28.5 | 0 | 10.5 | 2022-06-22 | 28.4 | 0 | 10.4 | 2021-06-22 | 15.2 | 2.8 | 0 | 2020-06-22 | 32.4 | 0 | 14.4 | 2019-06-22 | 24.9 | 0 | 6.9 | 2018-06-22 | 24.9 | 0 | 6.9 | 2017-06-22 | 23.7 | 0 | 5.7 | 2016-06-22 | 21.3 | 0 | 3.3 | 0.28 | 7.19
2025-06-22 | 29.1 | 0 | 11.1 | 2024-06-22 | 20 | 0 | 2 | 2023-06-22 | 28.9 | 0 | 10.9 | 2022-06-22 | 27.8 | 0 | 9.8 | 2021-06-22 | 15.1 | 2.9 | 0 | 2020-06-22 | 30.5 | 0 | 12.5 | 2019-06-22 | 25.6 | 0 | 7.6 | 2018-06-22 | 25.6 | 0 | 7.6 | 2017-06-22 | 24.5 | 0 | 6.5 | 2016-06-22 | 22.2 | 0 | 4.2 | 0.29 | 7.22
2025-06-22 | 28.4 | 0 | 10.4 | 2024-06-22 | 19.8 | 0 | 1.8 | 2023-06-22 | 29.2 | 0 | 11.2 | 2022-06-22 | 27.8 | 0 | 9.8 | 2021-06-22 | 15.6 | 2.4 | 0 | 2020-06-22 | 25.5 | 0 | 7.5 | 2019-06-22 | 25.7 | 0 | 7.7 | 2018-06-22 | 24.9 | 0 | 6.9 | 2017-06-22 | 22.7 | 0 | 4.7 | 2016-06-22 | 21.8 | 0 | 3.8 | 0.24 | 6.38
2025-06-22 | 28.5 | 0 | 10.5 | 2024-06-22 | 19.1 | 0 | 1.1 | 2023-06-22 | 28.6 | 0 | 10.6 | 2022-06-22 | 28.1 | 0 | 10.1 | 2021-06-22 | 16.4 | 1.6 | 0 | 2020-06-22 | 23.4 | 0 | 5.4 | 2019-06-22 | 25.5 | 0 | 7.5 | 2018-06-22 | 24.5 | 0 | 6.5 | 2017-06-22 | 22.2 | 0 | 4.2 | 2016-06-22 | 21.9 | 0 | 3.9 | 0.16 | 5.98
2025-06-22 | 28.1 | 0 | 10.1 | 2024-06-22 | 18.6 | 0 | 0.6 | 2023-06-22 | 27.7 | 0 | 9.7 | 2022-06-22 | 26.6 | 0 | 8.6 | 2021-06-22 | 15.7 | 2.3 | 0 | 2020-06-22 | 25.3 | 0 | 7.3 | 2019-06-22 | 24.8 | 0 | 6.8 | 2018-06-22 | 24.7 | 0 | 6.7 | 2017-06-22 | 21.8 | 0 | 3.8 | 2016-06-22 | 20.4 | 0 | 2.4 | 0.23 | 5.6
2025-06-22 | 26.9 | 0 | 8.9 | 2024-06-22 | 17.9 | 0.1 | 0 | 2023-06-22 | 26.2 | 0 | 8.2 | 2022-06-22 | 25.1 | 0 | 7.1 | 2021-06-22 | 16.2 | 1.8 | 0 | 2020-06-22 | 23.1 | 0 | 5.1 | 2019-06-22 | 23.8 | 0 | 5.8 | 2018-06-22 | 22.2 | 0 | 4.2 | 2017-06-22 | 20.7 | 0 | 2.7 | 2016-06-22 | 20 | 0 | 2 | 0.19 | 4.4
2025-06-22 | 25.4 | 0 | 7.4 | 2024-06-22 | 17.8 | 0.2 | 0 | 2023-06-22 | 24.1 | 0 | 6.1 | 2022-06-22 | 23.6 | 0 | 5.6 | 2021-06-22 | 14 | 4 | 0 | 2020-06-22 | 20.9 | 0 | 2.9 | 2019-06-22 | 21 | 0 | 3 | 2018-06-22 | 19.9 | 0 | 1.9 | 2017-06-22 | 19.9 | 0 | 1.9 | 2016-06-22 | 19 | 0 | 1 | 0.42 | 2.98
2025-06-22 | 23.7 | 0 | 5.7 | 2024-06-22 | 17.2 | 0.8 | 0 | 2023-06-22 | 21.1 | 0 | 3.1 | 2022-06-22 | 23.4 | 0 | 5.4 | 2021-06-22 | 11.9 | 6.1 | 0 | 2020-06-22 | 20 | 0 | 2 | 2019-06-22 | 18.5 | 0 | 0.5 | 2018-06-22 | 18.4 | 0 | 0.4 | 2017-06-22 | 19.6 | 0 | 1.6 | 2016-06-22 | 18.3 | 0 | 0.3 | 0.69 | 1.9
2025-06-22 | 24 | 0 | 6 | 2024-06-22 | 16.9 | 1.1 | 0 | 2023-06-22 | 19.7 | 0 | 1.7 | 2022-06-22 | 22.4 | 0 | 4.4 | 2021-06-22 | 10.8 | 7.2 | 0 | 2020-06-22 | 20.6 | 0 | 2.6 | 2019-06-22 | 16.9 | 1.1 | 0 | 2018-06-22 | 17.3 | 0.7 | 0 | 2017-06-22 | 19.6 | 0 | 1.6 | 2016-06-22 | 18.4 | 0 | 0.4 | 1.01 | 1.67
2025-06-22 | 24.1 | 0 | 6.1 | 2024-06-22 | 16.8 | 1.2 | 0 | 2023-06-22 | 18.1 | 0 | 0.1 | 2022-06-22 | 21.2 | 0 | 3.2 | 2021-06-22 | 10.8 | 7.2 | 0 | 2020-06-22 | 20.2 | 0 | 2.2 | 2019-06-22 | 15.6 | 2.4 | 0 | 2018-06-22 | 18.1 | 0 | 0.1 | 2017-06-22 | 16.9 | 1.1 | 0 | 2016-06-22 | 15.6 | 2.4 | 0 | 1.43 | 1.17
2025-06-23 | 23.6 | 0 | 5.6 | 2024-06-23 | 16.6 | 1.4 | 0 | 2023-06-23 | 19.5 | 0 | 1.5 | 2022-06-23 | 20.2 | 0 | 2.2 | 2021-06-23 | 8.7 | 9.3 | 0 | 2020-06-23 | 20.1 | 0 | 2.1 | 2019-06-23 | 14.4 | 3.6 | 0 | 2018-06-23 | 17.1 | 0.9 | 0 | 2017-06-23 | 16.6 | 1.4 | 0 | 2016-06-23 | 14 | 4 | 0 | 2.06 | 1.14
2025-06-23 | 22.4 | 0 | 4.4 | 2024-06-23 | 16.8 | 1.2 | 0 | 2023-06-23 | 16.2 | 1.8 | 0 | 2022-06-23 | 19.6 | 0 | 1.6 | 2021-06-23 | 7.6 | 10.4 | 0 | 2020-06-23 | 20.3 | 0 | 2.3 | 2019-06-23 | 14.2 | 3.8 | 0 | 2018-06-23 | 16.4 | 1.6 | 0 | 2017-06-23 | 16.1 | 1.9 | 0 | 2016-06-23 | 13.2 | 4.8 | 0 | 2.55 | 0.83
2025-06-23 | 22.5 | 0 | 4.5 | 2024-06-23 | 17 | 1 | 0 | 2023-06-23 | 16.8 | 1.2 | 0 | 2022-06-23 | 19.1 | 0 | 1.1 | 2021-06-23 | 5.9 | 12.1 | 0 | 2020-06-23 | 19.7 | 0 | 1.7 | 2019-06-23 | 13.5 | 4.5 | 0 | 2018-06-23 | 15.2 | 2.8 | 0 | 2017-06-23 | 16.1 | 1.9 | 0 | 2016-06-23 | 13.1 | 4.9 | 0 | 2.84 | 0.73
2025-06-23 | 21.5 | 0 | 3.5 | 2024-06-23 | 16.9 | 1.1 | 0 | 2023-06-23 | 15.6 | 2.4 | 0 | 2022-06-23 | 18.4 | 0 | 0.4 | 2021-06-23 | 7.3 | 10.7 | 0 | 2020-06-23 | 19.5 | 0 | 1.5 | 2019-06-23 | 13.2 | 4.8 | 0 | 2018-06-23 | 15.2 | 2.8 | 0 | 2017-06-23 | 15.9 | 2.1 | 0 | 2016-06-23 | 11.2 | 6.8 | 0 | 3.07 | 0.54
2025-06-23 | 20.9 | 0 | 2.9 | 2024-06-23 | 17.2 | 0.8 | 0 | 2023-06-23 | 15.2 | 2.8 | 0 | 2022-06-23 | 17.7 | 0.3 | 0 | 2021-06-23 | 6.4 | 11.6 | 0 | 2020-06-23 | 19.4 | 0 | 1.4 | 2019-06-23 | 12.7 | 5.3 | 0 | 2018-06-23 | 16.4 | 1.6 | 0 | 2017-06-23 | 16.4 | 1.6 | 0 | 2016-06-23 | 10.1 | 7.9 | 0 | 3.19 | 0.43
2025-06-23 | 21.3 | 0 | 3.3 | 2024-06-23 | 18 | 0 | 0 | 2023-06-23 | 15.4 | 2.6 | 0 | 2022-06-23 | 17.9 | 0.1 | 0 | 2021-06-23 | 8.1 | 9.9 | 0 | 2020-06-23 | 19.7 | 0 | 1.7 | 2019-06-23 | 13.7 | 4.3 | 0 | 2018-06-23 | 17.1 | 0.9 | 0 | 2017-06-23 | 16.6 | 1.4 | 0 | 2016-06-23 | 10.7 | 7.3 | 0 | 2.65 | 0.5
2025-06-23 | 23.2 | 0 | 5.2 | 2024-06-23 | 18.6 | 0 | 0.6 | 2023-06-23 | 18.1 | 0 | 0.1 | 2022-06-23 | 17.6 | 0.4 | 0 | 2021-06-23 | 10.5 | 7.5 | 0 | 2020-06-23 | 20.7 | 0 | 2.7 | 2019-06-23 | 15.4 | 2.6 | 0 | 2018-06-23 | 17.2 | 0.8 | 0 | 2017-06-23 | 17.4 | 0.6 | 0 | 2016-06-23 | 13.8 | 4.2 | 0 | 1.61 | 0.86
2025-06-23 | 24.9 | 0 | 6.9 | 2024-06-23 | 19.3 | 0 | 1.3 | 2023-06-23 | 21 | 0 | 3 | 2022-06-23 | 17.9 | 0.1 | 0 | 2021-06-23 | 13.3 | 4.7 | 0 | 2020-06-23 | 22.4 | 0 | 4.4 | 2019-06-23 | 17.5 | 0.5 | 0 | 2018-06-23 | 18.2 | 0 | 0.2 | 2017-06-23 | 18.6 | 0 | 0.6 | 2016-06-23 | 17.1 | 0.9 | 0 | 0.62 | 1.64
2025-06-23 | 27.9 | 0 | 9.9 | 2024-06-23 | 19.6 | 0 | 1.6 | 2023-06-23 | 24.4 | 0 | 6.4 | 2022-06-23 | 17.8 | 0.2 | 0 | 2021-06-23 | 14.7 | 3.3 | 0 | 2020-06-23 | 25 | 0 | 7 | 2019-06-23 | 19.8 | 0 | 1.8 | 2018-06-23 | 19.4 | 0 | 1.4 | 2017-06-23 | 19.2 | 0 | 1.2 | 2016-06-23 | 19.2 | 0 | 1.2 | 0.35 | 3.05
2025-06-23 | 31.1 | 0 | 13.1 | 2024-06-23 | 20.5 | 0 | 2.5 | 2023-06-23 | 26.2 | 0 | 8.2 | 2022-06-23 | 17.7 | 0.3 | 0 | 2021-06-23 | 16.6 | 1.4 | 0 | 2020-06-23 | 27.3 | 0 | 9.3 | 2019-06-23 | 21.9 | 0 | 3.9 | 2018-06-23 | 20.5 | 0 | 2.5 | 2017-06-23 | 20.1 | 0 | 2.1 | 2016-06-23 | 20.2 | 0 | 2.2 | 0.17 | 4.38
2025-06-23 | 32.6 | 0 | 14.6 | 2024-06-23 | 21.8 | 0 | 3.8 | 2023-06-23 | 27.6 | 0 | 9.6 | 2022-06-23 | 17.6 | 0.4 | 0 | 2021-06-23 | 18.1 | 0 | 0.1 | 2020-06-23 | 28.8 | 0 | 10.8 | 2019-06-23 | 23.5 | 0 | 5.5 | 2018-06-23 | 21.1 | 0 | 3.1 | 2017-06-23 | 20.9 | 0 | 2.9 | 2016-06-23 | 20.9 | 0 | 2.9 | 0.04 | 5.33
2025-06-23 | 33.6 | 0 | 15.6 | 2024-06-23 | 22.6 | 0 | 4.6 | 2023-06-23 | 28.1 | 0 | 10.1 | 2022-06-23 | 18.8 | 0 | 0.8 | 2021-06-23 | 17.9 | 0.1 | 0 | 2020-06-23 | 30.1 | 0 | 12.1 | 2019-06-23 | 24.9 | 0 | 6.9 | 2018-06-23 | 21.1 | 0 | 3.1 | 2017-06-23 | 21.8 | 0 | 3.8 | 2016-06-23 | 21.8 | 0 | 3.8 | 0.01 | 6.08
2025-06-23 | 34.2 | 0 | 16.2 | 2024-06-23 | 22.6 | 0 | 4.6 | 2023-06-23 | 29.8 | 0 | 11.8 | 2022-06-23 | 18.6 | 0 | 0.6 | 2021-06-23 | 18.4 | 0 | 0.4 | 2020-06-23 | 29.1 | 0 | 11.1 | 2019-06-23 | 26 | 0 | 8 | 2018-06-23 | 22 | 0 | 4 | 2017-06-23 | 23.3 | 0 | 5.3 | 2016-06-23 | 22.4 | 0 | 4.4 | 0 | 6.64
2025-06-23 | 34.4 | 0 | 16.4 | 2024-06-23 | 24.3 | 0 | 6.3 | 2023-06-23 | 29.1 | 0 | 11.1 | 2022-06-23 | 18.6 | 0 | 0.6 | 2021-06-23 | 19.7 | 0 | 1.7 | 2020-06-23 | 30.1 | 0 | 12.1 | 2019-06-23 | 26.6 | 0 | 8.6 | 2018-06-23 | 21.3 | 0 | 3.3 | 2017-06-23 | 23.3 | 0 | 5.3 | 2016-06-23 | 23.4 | 0 | 5.4 | 0 | 7.08
2025-06-23 | 34.9 | 0 | 16.9 | 2024-06-23 | 26 | 0 | 8 | 2023-06-23 | 29 | 0 | 11 | 2022-06-23 | 18.5 | 0 | 0.5 | 2021-06-23 | 20.6 | 0 | 2.6 | 2020-06-23 | 30.4 | 0 | 12.4 | 2019-06-23 | 27.2 | 0 | 9.2 | 2018-06-23 | 21.6 | 0 | 3.6 | 2017-06-23 | 23.9 | 0 | 5.9 | 2016-06-23 | 24.4 | 0 | 6.4 | 0 | 7.65
2025-06-23 | 35 | 0 | 17 | 2024-06-23 | 25.5 | 0 | 7.5 | 2023-06-23 | 29.9 | 0 | 11.9 | 2022-06-23 | 18.8 | 0 | 0.8 | 2021-06-23 | 20.8 | 0 | 2.8 | 2020-06-23 | 30.2 | 0 | 12.2 | 2019-06-23 | 27.3 | 0 | 9.3 | 2018-06-23 | 20.6 | 0 | 2.6 | 2017-06-23 | 23.8 | 0 | 5.8 | 2016-06-23 | 24.3 | 0 | 6.3 | 0 | 7.62
2025-06-23 | 34.2 | 0 | 16.2 | 2024-06-23 | 24.5 | 0 | 6.5 | 2023-06-23 | 29.1 | 0 | 11.1 | 2022-06-23 | 19.5 | 0 | 1.5 | 2021-06-23 | 21.6 | 0 | 3.6 | 2020-06-23 | 29.9 | 0 | 11.9 | 2019-06-23 | 27.7 | 0 | 9.7 | 2018-06-23 | 18.7 | 0 | 0.7 | 2017-06-23 | 23.2 | 0 | 5.2 | 2016-06-23 | 24.6 | 0 | 6.6 | 0 | 7.3
2025-06-23 | 33.8 | 0 | 15.8 | 2024-06-23 | 26.2 | 0 | 8.2 | 2023-06-23 | 27.2 | 0 | 9.2 | 2022-06-23 | 19.3 | 0 | 1.3 | 2021-06-23 | 20.8 | 0 | 2.8 | 2020-06-23 | 28.2 | 0 | 10.2 | 2019-06-23 | 27.2 | 0 | 9.2 | 2018-06-23 | 17.2 | 0.8 | 0 | 2017-06-23 | 21.3 | 0 | 3.3 | 2016-06-23 | 24.2 | 0 | 6.2 | 0.08 | 6.62
2025-06-23 | 33 | 0 | 15 | 2024-06-23 | 24.7 | 0 | 6.7 | 2023-06-23 | 27 | 0 | 9 | 2022-06-23 | 20.2 | 0 | 2.2 | 2021-06-23 | 21.6 | 0 | 3.6 | 2020-06-23 | 27.4 | 0 | 9.4 | 2019-06-23 | 26.2 | 0 | 8.2 | 2018-06-23 | 15.9 | 2.1 | 0 | 2017-06-23 | 21.9 | 0 | 3.9 | 2016-06-23 | 23.2 | 0 | 5.2 | 0.21 | 6.32
2025-06-23 | 31.4 | 0 | 13.4 | 2024-06-23 | 23.1 | 0 | 5.1 | 2023-06-23 | 25.7 | 0 | 7.7 | 2022-06-23 | 19 | 0 | 1 | 2021-06-23 | 18.8 | 0 | 0.8 | 2020-06-23 | 26.1 | 0 | 8.1 | 2019-06-23 | 23.7 | 0 | 5.7 | 2018-06-23 | 15.3 | 2.7 | 0 | 2017-06-23 | 21.9 | 0 | 3.9 | 2016-06-23 | 22.9 | 0 | 4.9 | 0.27 | 5.06
2025-06-23 | 30.2 | 0 | 12.2 | 2024-06-23 | 21.9 | 0 | 3.9 | 2023-06-23 | 24.3 | 0 | 6.3 | 2022-06-23 | 17.9 | 0.1 | 0 | 2021-06-23 | 17.2 | 0.8 | 0 | 2020-06-23 | 24.5 | 0 | 6.5 | 2019-06-23 | 22.2 | 0 | 4.2 | 2018-06-23 | 14.8 | 3.2 | 0 | 2017-06-23 | 21.1 | 0 | 3.1 | 2016-06-23 | 19.4 | 0 | 1.4 | 0.41 | 3.76
2025-06-23 | 29.1 | 0 | 11.1 | 2024-06-23 | 21.7 | 0 | 3.7 | 2023-06-23 | 24.2 | 0 | 6.2 | 2022-06-23 | 17.3 | 0.7 | 0 | 2021-06-23 | 16.1 | 1.9 | 0 | 2020-06-23 | 24.5 | 0 | 6.5 | 2019-06-23 | 19.9 | 0 | 1.9 | 2018-06-23 | 14.6 | 3.4 | 0 | 2017-06-23 | 21.3 | 0 | 3.3 | 2016-06-23 | 19.7 | 0 | 1.7 | 0.6 | 3.44
2025-06-23 | 27.8 | 0 | 9.8 | 2024-06-23 | 19.9 | 0 | 1.9 | 2023-06-23 | 22.8 | 0 | 4.8 | 2022-06-23 | 16.2 | 1.8 | 0 | 2021-06-23 | 14.9 | 3.1 | 0 | 2020-06-23 | 21.6 | 0 | 3.6 | 2019-06-23 | 19.4 | 0 | 1.4 | 2018-06-23 | 14.5 | 3.5 | 0 | 2017-06-23 | 20.2 | 0 | 2.2 | 2016-06-23 | 16.7 | 1.3 | 0 | 0.97 | 2.37
2025-06-23 | 27.2 | 0 | 9.2 | 2024-06-23 | 17.3 | 0.7 | 0 | 2023-06-23 | 22.4 | 0 | 4.4 | 2022-06-23 | 15.4 | 2.6 | 0 | 2021-06-23 | 14.4 | 3.6 | 0 | 2020-06-23 | 20.6 | 0 | 2.6 | 2019-06-23 | 16.3 | 1.7 | 0 | 2018-06-23 | 14.6 | 3.4 | 0 | 2017-06-23 | 20.4 | 0 | 2.4 | 2016-06-23 | 15.4 | 2.6 | 0 | 1.46 | 1.86
2025-06-24 | 27.1 | 0 | 9.1 | 2024-06-24 | 16.2 | 1.8 | 0 | 2023-06-24 | 22.8 | 0 | 4.8 | 2022-06-24 | 16 | 2 | 0 | 2021-06-24 | 13.4 | 4.6 | 0 | 2020-06-24 | 20.1 | 0 | 2.1 | 2019-06-24 | 17.8 | 0.2 | 0 | 2018-06-24 | 14.8 | 3.2 | 0 | 2017-06-24 | 20.2 | 0 | 2.2 | 2016-06-24 | 14 | 4 | 0 | 1.58 | 1.82
2025-06-24 | 26.1 | 0 | 8.1 | 2024-06-24 | 15.7 | 2.3 | 0 | 2023-06-24 | 22.8 | 0 | 4.8 | 2022-06-24 | 15.2 | 2.8 | 0 | 2021-06-24 | 11.7 | 6.3 | 0 | 2020-06-24 | 20 | 0 | 2 | 2019-06-24 | 15 | 3 | 0 | 2018-06-24 | 14.5 | 3.5 | 0 | 2017-06-24 | 18.8 | 0 | 0.8 | 2016-06-24 | 11.5 | 6.5 | 0 | 2.44 | 1.57
2025-06-24 | 25.6 | 0 | 7.6 | 2024-06-24 | 15.3 | 2.7 | 0 | 2023-06-24 | 19.9 | 0 | 1.9 | 2022-06-24 | 13.8 | 4.2 | 0 | 2021-06-24 | 11 | 7 | 0 | 2020-06-24 | 20.1 | 0 | 2.1 | 2019-06-24 | 14.9 | 3.1 | 0 | 2018-06-24 | 14.4 | 3.6 | 0 | 2017-06-24 | 17.1 | 0.9 | 0 | 2016-06-24 | 13.8 | 4.2 | 0 | 2.57 | 1.16
2025-06-24 | 24.9 | 0 | 6.9 | 2024-06-24 | 15.1 | 2.9 | 0 | 2023-06-24 | 19.7 | 0 | 1.7 | 2022-06-24 | 14.5 | 3.5 | 0 | 2021-06-24 | 10.9 | 7.1 | 0 | 2020-06-24 | 19.8 | 0 | 1.8 | 2019-06-24 | 13.5 | 4.5 | 0 | 2018-06-24 | 15 | 3 | 0 | 2017-06-24 | 15.6 | 2.4 | 0 | 2016-06-24 | 11.6 | 6.4 | 0 | 2.98 | 1.04
2025-06-24 | 24.1 | 0 | 6.1 | 2024-06-24 | 14.8 | 3.2 | 0 | 2023-06-24 | 19.5 | 0 | 1.5 | 2022-06-24 | 14 | 4 | 0 | 2021-06-24 | 10.5 | 7.5 | 0 | 2020-06-24 | 18.9 | 0 | 0.9 | 2019-06-24 | 13.8 | 4.2 | 0 | 2018-06-24 | 14.9 | 3.1 | 0 | 2017-06-24 | 13.8 | 4.2 | 0 | 2016-06-24 | 10.1 | 7.9 | 0 | 3.41 | 0.85
2025-06-24 | 24.4 | 0 | 6.4 | 2024-06-24 | 14.6 | 3.4 | 0 | 2023-06-24 | 19.5 | 0 | 1.5 | 2022-06-24 | 14 | 4 | 0 | 2021-06-24 | 11.3 | 6.7 | 0 | 2020-06-24 | 18 | 0 | 0 | 2019-06-24 | 14.1 | 3.9 | 0 | 2018-06-24 | 15.1 | 2.9 | 0 | 2017-06-24 | 15.2 | 2.8 | 0 | 2016-06-24 | 10.3 | 7.7 | 0 | 3.14 | 0.79
2025-06-24 | 25.9 | 0 | 7.9 | 2024-06-24 | 14.8 | 3.2 | 0 | 2023-06-24 | 19.7 | 0 | 1.7 | 2022-06-24 | 16.3 | 1.7 | 0 | 2021-06-24 | 14.1 | 3.9 | 0 | 2020-06-24 | 18.3 | 0 | 0.3 | 2019-06-24 | 16.3 | 1.7 | 0 | 2018-06-24 | 15.8 | 2.2 | 0 | 2017-06-24 | 16 | 2 | 0 | 2016-06-24 | 15.7 | 2.3 | 0 | 1.7 | 0.99
2025-06-24 | 28 | 0 | 10 | 2024-06-24 | 15.2 | 2.8 | 0 | 2023-06-24 | 19.8 | 0 | 1.8 | 2022-06-24 | 18.1 | 0 | 0.1 | 2021-06-24 | 16.8 | 1.2 | 0 | 2020-06-24 | 19 | 0 | 1 | 2019-06-24 | 18.8 | 0 | 0.8 | 2018-06-24 | 16.2 | 1.8 | 0 | 2017-06-24 | 17.1 | 0.9 | 0 | 2016-06-24 | 17.8 | 0.2 | 0 | 0.69 | 1.37
2025-06-24 | 29.5 | 0 | 11.5 | 2024-06-24 | 15.2 | 2.8 | 0 | 2023-06-24 | 20.3 | 0 | 2.3 | 2022-06-24 | 18.7 | 0 | 0.7 | 2021-06-24 | 18.8 | 0 | 0.8 | 2020-06-24 | 18.9 | 0 | 0.9 | 2019-06-24 | 20.4 | 0 | 2.4 | 2018-06-24 | 16.7 | 1.3 | 0 | 2017-06-24 | 19.9 | 0 | 1.9 | 2016-06-24 | 20.2 | 0 | 2.2 | 0.41 | 2.27
2025-06-24 | 30.6 | 0 | 12.6 | 2024-06-24 | 16.1 | 1.9 | 0 | 2023-06-24 | 21.6 | 0 | 3.6 | 2022-06-24 | 20.9 | 0 | 2.9 | 2021-06-24 | 22.1 | 0 | 4.1 | 2020-06-24 | 19.1 | 0 | 1.1 | 2019-06-24 | 21.8 | 0 | 3.8 | 2018-06-24 | 18.5 | 0 | 0.5 | 2017-06-24 | 21.7 | 0 | 3.7 | 2016-06-24 | 21.9 | 0 | 3.9 | 0.19 | 3.62
2025-06-24 | 31.3 | 0 | 13.3 | 2024-06-24 | 16.8 | 1.2 | 0 | 2023-06-24 | 23.6 | 0 | 5.6 | 2022-06-24 | 21.9 | 0 | 3.9 | 2021-06-24 | 24.4 | 0 | 6.4 | 2020-06-24 | 19.7 | 0 | 1.7 | 2019-06-24 | 22.9 | 0 | 4.9 | 2018-06-24 | 21.5 | 0 | 3.5 | 2017-06-24 | 23.5 | 0 | 5.5 | 2016-06-24 | 22.6 | 0 | 4.6 | 0.12 | 4.94
2025-06-24 | 32.5 | 0 | 14.5 | 2024-06-24 | 19.2 | 0 | 1.2 | 2023-06-24 | 23.6 | 0 | 5.6 | 2022-06-24 | 23.8 | 0 | 5.8 | 2021-06-24 | 25.4 | 0 | 7.4 | 2020-06-24 | 20.6 | 0 | 2.6 | 2019-06-24 | 24.6 | 0 | 6.6 | 2018-06-24 | 23 | 0 | 5 | 2017-06-24 | 23.4 | 0 | 5.4 | 2016-06-24 | 24.5 | 0 | 6.5 | 0 | 6.06
2025-06-24 | 32.7 | 0 | 14.7 | 2024-06-24 | 23 | 0 | 5 | 2023-06-24 | 24.1 | 0 | 6.1 | 2022-06-24 | 25.4 | 0 | 7.4 | 2021-06-24 | 26.3 | 0 | 8.3 | 2020-06-24 | 19.8 | 0 | 1.8 | 2019-06-24 | 25.7 | 0 | 7.7 | 2018-06-24 | 23.9 | 0 | 5.9 | 2017-06-24 | 24.8 | 0 | 6.8 | 2016-06-24 | 24.6 | 0 | 6.6 | 0 | 7.03
2025-06-24 | 33.3 | 0 | 15.3 | 2024-06-24 | 24.4 | 0 | 6.4 | 2023-06-24 | 24.7 | 0 | 6.7 | 2022-06-24 | 26.3 | 0 | 8.3 | 2021-06-24 | 26.5 | 0 | 8.5 | 2020-06-24 | 20 | 0 | 2 | 2019-06-24 | 26.7 | 0 | 8.7 | 2018-06-24 | 22.4 | 0 | 4.4 | 2017-06-24 | 26.2 | 0 | 8.2 | 2016-06-24 | 26.6 | 0 | 8.6 | 0 | 7.71
2025-06-24 | 33.2 | 0 | 15.2 | 2024-06-24 | 24.9 | 0 | 6.9 | 2023-06-24 | 25.9 | 0 | 7.9 | 2022-06-24 | 26.7 | 0 | 8.7 | 2021-06-24 | 26.8 | 0 | 8.8 | 2020-06-24 | 21.1 | 0 | 3.1 | 2019-06-24 | 26.8 | 0 | 8.8 | 2018-06-24 | 21.4 | 0 | 3.4 | 2017-06-24 | 26 | 0 | 8 | 2016-06-24 | 26.6 | 0 | 8.6 | 0 | 7.94
2025-06-24 | 28.4 | 0 | 10.4 | 2024-06-24 | 24.5 | 0 | 6.5 | 2023-06-24 | 27.5 | 0 | 9.5 | 2022-06-24 | 27 | 0 | 9 | 2021-06-24 | 27.2 | 0 | 9.2 | 2020-06-24 | 20.3 | 0 | 2.3 | 2019-06-24 | 27.2 | 0 | 9.2 | 2018-06-24 | 21.1 | 0 | 3.1 | 2017-06-24 | 26.5 | 0 | 8.5 | 2016-06-24 | 27.1 | 0 | 9.1 | 0 | 7.68
2025-06-24 | 28.8 | 0 | 10.8 | 2024-06-24 | 26 | 0 | 8 | 2023-06-24 | 26 | 0 | 8 | 2022-06-24 | 27 | 0 | 9 | 2021-06-24 | 26.6 | 0 | 8.6 | 2020-06-24 | 19.5 | 0 | 1.5 | 2019-06-24 | 26.6 | 0 | 8.6 | 2018-06-24 | 20.4 | 0 | 2.4 | 2017-06-24 | 24.8 | 0 | 6.8 | 2016-06-24 | 27.8 | 0 | 9.8 | 0 | 7.35
2025-06-24 | 26.8 | 0 | 8.8 | 2024-06-24 | 26.2 | 0 | 8.2 | 2023-06-24 | 26.7 | 0 | 8.7 | 2022-06-24 | 26.2 | 0 | 8.2 | 2021-06-24 | 25.7 | 0 | 7.7 | 2020-06-24 | 19.9 | 0 | 1.9 | 2019-06-24 | 25.4 | 0 | 7.4 | 2018-06-24 | 19.2 | 0 | 1.2 | 2017-06-24 | 23.8 | 0 | 5.8 | 2016-06-24 | 27 | 0 | 9 | 0 | 6.69
2025-06-24 | 27 | 0 | 9 | 2024-06-24 | 26.3 | 0 | 8.3 | 2023-06-24 | 26.1 | 0 | 8.1 | 2022-06-24 | 25.4 | 0 | 7.4 | 2021-06-24 | 24.8 | 0 | 6.8 | 2020-06-24 | 20.7 | 0 | 2.7 | 2019-06-24 | 24.7 | 0 | 6.7 | 2018-06-24 | 16.9 | 1.1 | 0 | 2017-06-24 | 20.2 | 0 | 2.2 | 2016-06-24 | 26.9 | 0 | 8.9 | 0.11 | 6.01
2025-06-24 | 26.1 | 0 | 8.1 | 2024-06-24 | 23.6 | 0 | 5.6 | 2023-06-24 | 25.1 | 0 | 7.1 | 2022-06-24 | 24.7 | 0 | 6.7 | 2021-06-24 | 24 | 0 | 6 | 2020-06-24 | 19.3 | 0 | 1.3 | 2019-06-24 | 22.8 | 0 | 4.8 | 2018-06-24 | 16.3 | 1.7 | 0 | 2017-06-24 | 17.4 | 0.6 | 0 | 2016-06-24 | 24.2 | 0 | 6.2 | 0.23 | 4.58
2025-06-24 | 25.5 | 0 | 7.5 | 2024-06-24 | 21.7 | 0 | 3.7 | 2023-06-24 | 23.3 | 0 | 5.3 | 2022-06-24 | 22.4 | 0 | 4.4 | 2021-06-24 | 22.3 | 0 | 4.3 | 2020-06-24 | 18.4 | 0 | 0.4 | 2019-06-24 | 21.4 | 0 | 3.4 | 2018-06-24 | 14.7 | 3.3 | 0 | 2017-06-24 | 16.3 | 1.7 | 0 | 2016-06-24 | 20.8 | 0 | 2.8 | 0.5 | 3.18
2025-06-24 | 27.6 | 0 | 9.6 | 2024-06-24 | 19.8 | 0 | 1.8 | 2023-06-24 | 23.1 | 0 | 5.1 | 2022-06-24 | 21.6 | 0 | 3.6 | 2021-06-24 | 20.9 | 0 | 2.9 | 2020-06-24 | 17.4 | 0.6 | 0 | 2019-06-24 | 20.6 | 0 | 2.6 | 2018-06-24 | 14.4 | 3.6 | 0 | 2017-06-24 | 16.3 | 1.7 | 0 | 2016-06-24 | 19.6 | 0 | 1.6 | 0.59 | 2.72
2025-06-24 | 24.8 | 0 | 6.8 | 2024-06-24 | 19.5 | 0 | 1.5 | 2023-06-24 | 21.3 | 0 | 3.3 | 2022-06-24 | 20.9 | 0 | 2.9 | 2021-06-24 | 19.5 | 0 | 1.5 | 2020-06-24 | 16.4 | 1.6 | 0 | 2019-06-24 | 20.5 | 0 | 2.5 | 2018-06-24 | 13.9 | 4.1 | 0 | 2017-06-24 | 15.2 | 2.8 | 0 | 2016-06-24 | 19.2 | 0 | 1.2 | 0.85 | 1.97
2025-06-24 | 23.7 | 0 | 5.7 | 2024-06-24 | 19.1 | 0 | 1.1 | 2023-06-24 | 21.3 | 0 | 3.3 | 2022-06-24 | 19.9 | 0 | 1.9 | 2021-06-24 | 20.8 | 0 | 2.8 | 2020-06-24 | 16.1 | 1.9 | 0 | 2019-06-24 | 20 | 0 | 2 | 2018-06-24 | 13 | 5 | 0 | 2017-06-24 | 13.8 | 4.2 | 0 | 2016-06-24 | 18.1 | 0 | 0.1 | 1.11 | 1.69
2025-06-25 | 22 | 0 | 4 | 2024-06-25 | 18.7 | 0 | 0.7 | 2023-06-25 | 20.7 | 0 | 2.7 | 2022-06-25 | 17.6 | 0.4 | 0 | 2021-06-25 | 21.2 | 0 | 3.2 | 2020-06-25 | 16.1 | 1.9 | 0 | 2019-06-25 | 18.7 | 0 | 0.7 | 2018-06-25 | 11.6 | 6.4 | 0 | 2017-06-25 | 13.7 | 4.3 | 0 | 2016-06-25 | 17.3 | 0.7 | 0 | 1.37 | 1.13
2025-06-25 | 22.3 | 0 | 4.3 | 2024-06-25 | 18.8 | 0 | 0.8 | 2023-06-25 | 18.6 | 0 | 0.6 | 2022-06-25 | 17.5 | 0.5 | 0 | 2021-06-25 | 20.4 | 0 | 2.4 | 2020-06-25 | 16 | 2 | 0 | 2019-06-25 | 18 | 0 | 0 | 2018-06-25 | 10.5 | 7.5 | 0 | 2017-06-25 | 13.7 | 4.3 | 0 | 2016-06-25 | 16.5 | 1.5 | 0 | 1.58 | 0.81
2025-06-25 | 20.3 | 0 | 2.3 | 2024-06-25 | 18.4 | 0 | 0.4 | 2023-06-25 | 17.9 | 0.1 | 0 | 2022-06-25 | 17.2 | 0.8 | 0 | 2021-06-25 | 20 | 0 | 2 | 2020-06-25 | 15.7 | 2.3 | 0 | 2019-06-25 | 18.1 | 0 | 0.1 | 2018-06-25 | 12.3 | 5.7 | 0 | 2017-06-25 | 12.6 | 5.4 | 0 | 2016-06-25 | 16.7 | 1.3 | 0 | 1.56 | 0.48
2025-06-25 | 19.2 | 0 | 1.2 | 2024-06-25 | 18.1 | 0 | 0.1 | 2023-06-25 | 17.7 | 0.3 | 0 | 2022-06-25 | 17.1 | 0.9 | 0 | 2021-06-25 | 19.8 | 0 | 1.8 | 2020-06-25 | 16.6 | 1.4 | 0 | 2019-06-25 | 18.4 | 0 | 0.4 | 2018-06-25 | 12.3 | 5.7 | 0 | 2017-06-25 | 12.9 | 5.1 | 0 | 2016-06-25 | 16.7 | 1.3 | 0 | 1.47 | 0.35
2025-06-25 | 20.8 | 0 | 2.8 | 2024-06-25 | 17 | 1 | 0 | 2023-06-25 | 17.6 | 0.4 | 0 | 2022-06-25 | 16.2 | 1.8 | 0 | 2021-06-25 | 19.6 | 0 | 1.6 | 2020-06-25 | 16.3 | 1.7 | 0 | 2019-06-25 | 18.3 | 0 | 0.3 | 2018-06-25 | 11.8 | 6.2 | 0 | 2017-06-25 | 11.5 | 6.5 | 0 | 2016-06-25 | 13.4 | 4.6 | 0 | 2.22 | 0.47
2025-06-25 | 20.4 | 0 | 2.4 | 2024-06-25 | 16.4 | 1.6 | 0 | 2023-06-25 | 19.3 | 0 | 1.3 | 2022-06-25 | 16.9 | 1.1 | 0 | 2021-06-25 | 19.2 | 0 | 1.2 | 2020-06-25 | 15.9 | 2.1 | 0 | 2019-06-25 | 15.6 | 2.4 | 0 | 2018-06-25 | 12 | 6 | 0 | 2017-06-25 | 11.9 | 6.1 | 0 | 2016-06-25 | 14.4 | 3.6 | 0 | 2.29 | 0.49
2025-06-25 | 22.6 | 0 | 4.6 | 2024-06-25 | 17.9 | 0.1 | 0 | 2023-06-25 | 19.5 | 0 | 1.5 | 2022-06-25 | 18.4 | 0 | 0.4 | 2021-06-25 | 19.3 | 0 | 1.3 | 2020-06-25 | 16 | 2 | 0 | 2019-06-25 | 14.5 | 3.5 | 0 | 2018-06-25 | 13.2 | 4.8 | 0 | 2017-06-25 | 13.8 | 4.2 | 0 | 2016-06-25 | 16.5 | 1.5 | 0 | 1.61 | 0.78
2025-06-25 | 23.9 | 0 | 5.9 | 2024-06-25 | 20.4 | 0 | 2.4 | 2023-06-25 | 20.6 | 0 | 2.6 | 2022-06-25 | 20.5 | 0 | 2.5 | 2021-06-25 | 19.6 | 0 | 1.6 | 2020-06-25 | 16.9 | 1.1 | 0 | 2019-06-25 | 14.5 | 3.5 | 0 | 2018-06-25 | 14.5 | 3.5 | 0 | 2017-06-25 | 15.7 | 2.3 | 0 | 2016-06-25 | 18.9 | 0 | 0.9 | 1.04 | 1.59
2025-06-25 | 24.9 | 0 | 6.9 | 2024-06-25 | 22 | 0 | 4 | 2023-06-25 | 21.7 | 0 | 3.7 | 2022-06-25 | 23.2 | 0 | 5.2 | 2021-06-25 | 19.9 | 0 | 1.9 | 2020-06-25 | 18.1 | 0 | 0.1 | 2019-06-25 | 15 | 3 | 0 | 2018-06-25 | 16.4 | 1.6 | 0 | 2017-06-25 | 17.4 | 0.6 | 0 | 2016-06-25 | 22.5 | 0 | 4.5 | 0.52 | 2.63
2025-06-25 | 25.3 | 0 | 7.3 | 2024-06-25 | 24.1 | 0 | 6.1 | 2023-06-25 | 23 | 0 | 5 | 2022-06-25 | 24.8 | 0 | 6.8 | 2021-06-25 | 21.1 | 0 | 3.1 | 2020-06-25 | 19.9 | 0 | 1.9 | 2019-06-25 | 15.9 | 2.1 | 0 | 2018-06-25 | 17.9 | 0.1 | 0 | 2017-06-25 | 19.5 | 0 | 1.5 | 2016-06-25 | 25.3 | 0 | 7.3 | 0.22 | 3.9
2025-06-25 | 25.5 | 0 | 7.5 | 2024-06-25 | 25.5 | 0 | 7.5 | 2023-06-25 | 23.2 | 0 | 5.2 | 2022-06-25 | 26.3 | 0 | 8.3 | 2021-06-25 | 21.3 | 0 | 3.3 | 2020-06-25 | 20.1 | 0 | 2.1 | 2019-06-25 | 17.8 | 0.2 | 0 | 2018-06-25 | 18.7 | 0 | 0.7 | 2017-06-25 | 20.7 | 0 | 2.7 | 2016-06-25 | 27.1 | 0 | 9.1 | 0.02 | 4.64
2025-06-25 | 26.5 | 0 | 8.5 | 2024-06-25 | 25.8 | 0 | 7.8 | 2023-06-25 | 23.9 | 0 | 5.9 | 2022-06-25 | 27.5 | 0 | 9.5 | 2021-06-25 | 22 | 0 | 4 | 2020-06-25 | 21.5 | 0 | 3.5 | 2019-06-25 | 20.2 | 0 | 2.2 | 2018-06-25 | 19.5 | 0 | 1.5 | 2017-06-25 | 20.2 | 0 | 2.2 | 2016-06-25 | 27.9 | 0 | 9.9 | 0 | 5.5
2025-06-25 | 26 | 0 | 8 | 2024-06-25 | 26.1 | 0 | 8.1 | 2023-06-25 | 24.8 | 0 | 6.8 | 2022-06-25 | 28.5 | 0 | 10.5 | 2021-06-25 | 21.9 | 0 | 3.9 | 2020-06-25 | 21.7 | 0 | 3.7 | 2019-06-25 | 22.8 | 0 | 4.8 | 2018-06-25 | 20 | 0 | 2 | 2017-06-25 | 17.5 | 0.5 | 0 | 2016-06-25 | 29.1 | 0 | 11.1 | 0.05 | 5.89
2025-06-25 | 27.2 | 0 | 9.2 | 2024-06-25 | 27.1 | 0 | 9.1 | 2023-06-25 | 25.8 | 0 | 7.8 | 2022-06-25 | 29.3 | 0 | 11.3 | 2021-06-25 | 22.6 | 0 | 4.6 | 2020-06-25 | 22.2 | 0 | 4.2 | 2019-06-25 | 26 | 0 | 8 | 2018-06-25 | 21.1 | 0 | 3.1 | 2017-06-25 | 20.7 | 0 | 2.7 | 2016-06-25 | 29.6 | 0 | 11.6 | 0 | 7.16
2025-06-25 | 27.5 | 0 | 9.5 | 2024-06-25 | 26.8 | 0 | 8.8 | 2023-06-25 | 25.6 | 0 | 7.6 | 2022-06-25 | 30 | 0 | 12 | 2021-06-25 | 22.9 | 0 | 4.9 | 2020-06-25 | 23.4 | 0 | 5.4 | 2019-06-25 | 28.1 | 0 | 10.1 | 2018-06-25 | 21.8 | 0 | 3.8 | 2017-06-25 | 13 | 5 | 0 | 2016-06-25 | 30.9 | 0 | 12.9 | 0.5 | 7.5
2025-06-25 | 27.5 | 0 | 9.5 | 2024-06-25 | 25 | 0 | 7 | 2023-06-25 | 25.7 | 0 | 7.7 | 2022-06-25 | 30.5 | 0 | 12.5 | 2021-06-25 | 23.8 | 0 | 5.8 | 2020-06-25 | 23 | 0 | 5 | 2019-06-25 | 28.6 | 0 | 10.6 | 2018-06-25 | 21.9 | 0 | 3.9 | 2017-06-25 | 14.7 | 3.3 | 0 | 2016-06-25 | 30.6 | 0 | 12.6 | 0.33 | 7.46
2025-06-25 | 27 | 0 | 9 | 2024-06-25 | 24.1 | 0 | 6.1 | 2023-06-25 | 26.1 | 0 | 8.1 | 2022-06-25 | 30.4 | 0 | 12.4 | 2021-06-25 | 24.1 | 0 | 6.1 | 2020-06-25 | 19.7 | 0 | 1.7 | 2019-06-25 | 28.4 | 0 | 10.4 | 2018-06-25 | 22 | 0 | 4 | 2017-06-25 | 12.6 | 5.4 | 0 | 2016-06-25 | 30.3 | 0 | 12.3 | 0.54 | 7.01
2025-06-25 | 26.6 | 0 | 8.6 | 2024-06-25 | 22.5 | 0 | 4.5 | 2023-06-25 | 25.2 | 0 | 7.2 | 2022-06-25 | 30.3 | 0 | 12.3 | 2021-06-25 | 23.9 | 0 | 5.9 | 2020-06-25 | 22.8 | 0 | 4.8 | 2019-06-25 | 26.4 | 0 | 8.4 | 2018-06-25 | 21.9 | 0 | 3.9 | 2017-06-25 | 15 | 3 | 0 | 2016-06-25 | 30 | 0 | 12 | 0.3 | 6.76
2025-06-25 | 25.6 | 0 | 7.6 | 2024-06-25 | 22.4 | 0 | 4.4 | 2023-06-25 | 24.6 | 0 | 6.6 | 2022-06-25 | 29.1 | 0 | 11.1 | 2021-06-25 | 23.1 | 0 | 5.1 | 2020-06-25 | 23.1 | 0 | 5.1 | 2019-06-25 | 25.6 | 0 | 7.6 | 2018-06-25 | 21 | 0 | 3 | 2017-06-25 | 14.9 | 3.1 | 0 | 2016-06-25 | 29.2 | 0 | 11.2 | 0.31 | 6.17
2025-06-25 | 24 | 0 | 6 | 2024-06-25 | 21.7 | 0 | 3.7 | 2023-06-25 | 23 | 0 | 5 | 2022-06-25 | 26.7 | 0 | 8.7 | 2021-06-25 | 21.9 | 0 | 3.9 | 2020-06-25 | 22.1 | 0 | 4.1 | 2019-06-25 | 23.4 | 0 | 5.4 | 2018-06-25 | 19.9 | 0 | 1.9 | 2017-06-25 | 14.7 | 3.3 | 0 | 2016-06-25 | 27.2 | 0 | 9.2 | 0.33 | 4.79
2025-06-25 | 23 | 0 | 5 | 2024-06-25 | 18.2 | 0 | 0.2 | 2023-06-25 | 20.8 | 0 | 2.8 | 2022-06-25 | 25.2 | 0 | 7.2 | 2021-06-25 | 20.7 | 0 | 2.7 | 2020-06-25 | 21.1 | 0 | 3.1 | 2019-06-25 | 21.2 | 0 | 3.2 | 2018-06-25 | 17.9 | 0.1 | 0 | 2017-06-25 | 13.8 | 4.2 | 0 | 2016-06-25 | 22.5 | 0 | 4.5 | 0.43 | 2.87
2025-06-25 | 22.2 | 0 | 4.2 | 2024-06-25 | 18.2 | 0 | 0.2 | 2023-06-25 | 20.8 | 0 | 2.8 | 2022-06-25 | 23.7 | 0 | 5.7 | 2021-06-25 | 20.2 | 0 | 2.2 | 2020-06-25 | 19.7 | 0 | 1.7 | 2019-06-25 | 19.3 | 0 | 1.3 | 2018-06-25 | 16.9 | 1.1 | 0 | 2017-06-25 | 13.1 | 4.9 | 0 | 2016-06-25 | 21.9 | 0 | 3.9 | 0.6 | 2.2
2025-06-25 | 21.4 | 0 | 3.4 | 2024-06-25 | 18.8 | 0 | 0.8 | 2023-06-25 | 20.7 | 0 | 2.7 | 2022-06-25 | 21 | 0 | 3 | 2021-06-25 | 20 | 0 | 2 | 2020-06-25 | 18.4 | 0 | 0.4 | 2019-06-25 | 18.8 | 0 | 0.8 | 2018-06-25 | 13 | 5 | 0 | 2017-06-25 | 13.2 | 4.8 | 0 | 2016-06-25 | 21.4 | 0 | 3.4 | 0.98 | 1.65
2025-06-25 | 20.9 | 0 | 2.9 | 2024-06-25 | 18.9 | 0 | 0.9 | 2023-06-25 | 20.5 | 0 | 2.5 | 2022-06-25 | 21.8 | 0 | 3.8 | 2021-06-25 | 20 | 0 | 2 | 2020-06-25 | 17.4 | 0.6 | 0 | 2019-06-25 | 17.7 | 0.3 | 0 | 2018-06-25 | 11.4 | 6.6 | 0 | 2017-06-25 | 13 | 5 | 0 | 2016-06-25 | 20.4 | 0 | 2.4 | 1.25 | 1.45
2025-06-26 | 20.2 | 0 | 2.2 | 2024-06-26 | 19.2 | 0 | 1.2 | 2023-06-26 | 19.8 | 0 | 1.8 | 2022-06-26 | 21 | 0 | 3 | 2021-06-26 | 19.2 | 0 | 1.2 | 2020-06-26 | 16.1 | 1.9 | 0 | 2019-06-26 | 15.4 | 2.6 | 0 | 2018-06-26 | 11.6 | 6.4 | 0 | 2017-06-26 | 12.6 | 5.4 | 0 | 2016-06-26 | 19.2 | 0 | 1.2 | 1.63 | 1.06
2025-06-26 | 19.2 | 0 | 1.2 | 2024-06-26 | 19.6 | 0 | 1.6 | 2023-06-26 | 19.5 | 0 | 1.5 | 2022-06-26 | 20.5 | 0 | 2.5 | 2021-06-26 | 18.6 | 0 | 0.6 | 2020-06-26 | 15.5 | 2.5 | 0 | 2019-06-26 | 15.9 | 2.1 | 0 | 2018-06-26 | 11.8 | 6.2 | 0 | 2017-06-26 | 12.1 | 5.9 | 0 | 2016-06-26 | 18 | 0 | 0 | 1.67 | 0.74
2025-06-26 | 17.8 | 0.2 | 0 | 2024-06-26 | 19.5 | 0 | 1.5 | 2023-06-26 | 18.9 | 0 | 0.9 | 2022-06-26 | 19.6 | 0 | 1.6 | 2021-06-26 | 18.3 | 0 | 0.3 | 2020-06-26 | 14.4 | 3.6 | 0 | 2019-06-26 | 15.6 | 2.4 | 0 | 2018-06-26 | 8.6 | 9.4 | 0 | 2017-06-26 | 12.8 | 5.2 | 0 | 2016-06-26 | 15.9 | 2.1 | 0 | 2.29 | 0.43
2025-06-26 | 16.7 | 1.3 | 0 | 2024-06-26 | 19.4 | 0 | 1.4 | 2023-06-26 | 18.4 | 0 | 0.4 | 2022-06-26 | 18.6 | 0 | 0.6 | 2021-06-26 | 18.1 | 0 | 0.1 | 2020-06-26 | 13.8 | 4.2 | 0 | 2019-06-26 | 15.5 | 2.5 | 0 | 2018-06-26 | 8.6 | 9.4 | 0 | 2017-06-26 | 12.4 | 5.6 | 0 | 2016-06-26 | 17.4 | 0.6 | 0 | 2.36 | 0.25
2025-06-26 | 16.5 | 1.5 | 0 | 2024-06-26 | 19.4 | 0 | 1.4 | 2023-06-26 | 18.1 | 0 | 0.1 | 2022-06-26 | 16.4 | 1.6 | 0 | 2021-06-26 | 17.7 | 0.3 | 0 | 2020-06-26 | 13.8 | 4.2 | 0 | 2019-06-26 | 15 | 3 | 0 | 2018-06-26 | 8 | 10 | 0 | 2017-06-26 | 12.7 | 5.3 | 0 | 2016-06-26 | 14.2 | 3.8 | 0 | 2.97 | 0.15
2025-06-26 | 16.2 | 1.8 | 0 | 2024-06-26 | 19.2 | 0 | 1.2 | 2023-06-26 | 18 | 0 | 0 | 2022-06-26 | 17.7 | 0.3 | 0 | 2021-06-26 | 17.3 | 0.7 | 0 | 2020-06-26 | 13.7 | 4.3 | 0 | 2019-06-26 | 15.3 | 2.7 | 0 | 2018-06-26 | 6.7 | 11.3 | 0 | 2017-06-26 | 12.7 | 5.3 | 0 | 2016-06-26 | 16 | 2 | 0 | 2.84 | 0.12
2025-06-26 | 16.4 | 1.6 | 0 | 2024-06-26 | 20.1 | 0 | 2.1 | 2023-06-26 | 19 | 0 | 1 | 2022-06-26 | 20 | 0 | 2 | 2021-06-26 | 16.9 | 1.1 | 0 | 2020-06-26 | 15.9 | 2.1 | 0 | 2019-06-26 | 16.1 | 1.9 | 0 | 2018-06-26 | 11.3 | 6.7 | 0 | 2017-06-26 | 13.4 | 4.6 | 0 | 2016-06-26 | 16.9 | 1.1 | 0 | 1.91 | 0.51
2025-06-26 | 16.7 | 1.3 | 0 | 2024-06-26 | 21.7 | 0 | 3.7 | 2023-06-26 | 20.4 | 0 | 2.4 | 2022-06-26 | 22.2 | 0 | 4.2 | 2021-06-26 | 16.7 | 1.3 | 0 | 2020-06-26 | 17.6 | 0.4 | 0 | 2019-06-26 | 18.7 | 0 | 0.7 | 2018-06-26 | 15.3 | 2.7 | 0 | 2017-06-26 | 14.2 | 3.8 | 0 | 2016-06-26 | 19.7 | 0 | 1.7 | 0.95 | 1.27
2025-06-26 | 16.7 | 1.3 | 0 | 2024-06-26 | 22.7 | 0 | 4.7 | 2023-06-26 | 20.9 | 0 | 2.9 | 2022-06-26 | 24.6 | 0 | 6.6 | 2021-06-26 | 17.3 | 0.7 | 0 | 2020-06-26 | 19.9 | 0 | 1.9 | 2019-06-26 | 17.6 | 0.4 | 0 | 2018-06-26 | 18.2 | 0 | 0.2 | 2017-06-26 | 15.6 | 2.4 | 0 | 2016-06-26 | 22.3 | 0 | 4.3 | 0.48 | 2.06
2025-06-26 | 16.8 | 1.2 | 0 | 2024-06-26 | 23.6 | 0 | 5.6 | 2023-06-26 | 23.5 | 0 | 5.5 | 2022-06-26 | 26.9 | 0 | 8.9 | 2021-06-26 | 18.1 | 0 | 0.1 | 2020-06-26 | 22.4 | 0 | 4.4 | 2019-06-26 | 17.6 | 0.4 | 0 | 2018-06-26 | 19.6 | 0 | 1.6 | 2017-06-26 | 17.9 | 0.1 | 0 | 2016-06-26 | 25.6 | 0 | 7.6 | 0.17 | 3.37
2025-06-26 | 15.9 | 2.1 | 0 | 2024-06-26 | 25.1 | 0 | 7.1 | 2023-06-26 | 24.3 | 0 | 6.3 | 2022-06-26 | 28.6 | 0 | 10.6 | 2021-06-26 | 19 | 0 | 1 | 2020-06-26 | 23.5 | 0 | 5.5 | 2019-06-26 | 19.4 | 0 | 1.4 | 2018-06-26 | 21.6 | 0 | 3.6 | 2017-06-26 | 18.5 | 0 | 0.5 | 2016-06-26 | 27.7 | 0 | 9.7 | 0.21 | 4.57
2025-06-26 | 16.4 | 1.6 | 0 | 2024-06-26 | 25.5 | 0 | 7.5 | 2023-06-26 | 26.9 | 0 | 8.9 | 2022-06-26 | 29.8 | 0 | 11.8 | 2021-06-26 | 20.2 | 0 | 2.2 | 2020-06-26 | 26.2 | 0 | 8.2 | 2019-06-26 | 22 | 0 | 4 | 2018-06-26 | 21.6 | 0 | 3.6 | 2017-06-26 | 19.9 | 0 | 1.9 | 2016-06-26 | 29.2 | 0 | 11.2 | 0.16 | 5.93
2025-06-26 | 17.1 | 0.9 | 0 | 2024-06-26 | 26.3 | 0 | 8.3 | 2023-06-26 | 26.6 | 0 | 8.6 | 2022-06-26 | 31.2 | 0 | 13.2 | 2021-06-26 | 21.4 | 0 | 3.4 | 2020-06-26 | 24.4 | 0 | 6.4 | 2019-06-26 | 24 | 0 | 6 | 2018-06-26 | 23.2 | 0 | 5.2 | 2017-06-26 | 20.3 | 0 | 2.3 | 2016-06-26 | 31 | 0 | 13 | 0.09 | 6.64
2025-06-26 | 17.2 | 0.8 | 0 | 2024-06-26 | 26.3 | 0 | 8.3 | 2023-06-26 | 26.2 | 0 | 8.2 | 2022-06-26 | 30.6 | 0 | 12.6 | 2021-06-26 | 22.7 | 0 | 4.7 | 2020-06-26 | 23.7 | 0 | 5.7 | 2019-06-26 | 26.6 | 0 | 8.6 | 2018-06-26 | 23.8 | 0 | 5.8 | 2017-06-26 | 20.5 | 0 | 2.5 | 2016-06-26 | 32 | 0 | 14 | 0.08 | 7.04
2025-06-26 | 17.9 | 0.1 | 0 | 2024-06-26 | 26.5 | 0 | 8.5 | 2023-06-26 | 25.4 | 0 | 7.4 | 2022-06-26 | 28.8 | 0 | 10.8 | 2021-06-26 | 24 | 0 | 6 | 2020-06-26 | 23.5 | 0 | 5.5 | 2019-06-26 | 27.5 | 0 | 9.5 | 2018-06-26 | 24.6 | 0 | 6.6 | 2017-06-26 | 19.9 | 0 | 1.9 | 2016-06-26 | 31.9 | 0 | 13.9 | 0.01 | 7.01
2025-06-26 | 18.4 | 0 | 0.4 | 2024-06-26 | 24.7 | 0 | 6.7 | 2023-06-26 | 20.6 | 0 | 2.6 | 2022-06-26 | 27.2 | 0 | 9.2 | 2021-06-26 | 23.2 | 0 | 5.2 | 2020-06-26 | 23 | 0 | 5 | 2019-06-26 | 26.8 | 0 | 8.8 | 2018-06-26 | 24.4 | 0 | 6.4 | 2017-06-26 | 20.4 | 0 | 2.4 | 2016-06-26 | 32.6 | 0 | 14.6 | 0 | 6.13
2025-06-26 | 19.2 | 0 | 1.2 | 2024-06-26 | 23.5 | 0 | 5.5 | 2023-06-26 | 22.4 | 0 | 4.4 | 2022-06-26 | 26.6 | 0 | 8.6 | 2021-06-26 | 23.7 | 0 | 5.7 | 2020-06-26 | 24.4 | 0 | 6.4 | 2019-06-26 | 26.4 | 0 | 8.4 | 2018-06-26 | 24.9 | 0 | 6.9 | 2017-06-26 | 20.8 | 0 | 2.8 | 2016-06-26 | 30.3 | 0 | 12.3 | 0 | 6.22
2025-06-26 | 20.3 | 0 | 2.3 | 2024-06-26 | 23.4 | 0 | 5.4 | 2023-06-26 | 21 | 0 | 3 | 2022-06-26 | 24.5 | 0 | 6.5 | 2021-06-26 | 23.2 | 0 | 5.2 | 2020-06-26 | 25.8 | 0 | 7.8 | 2019-06-26 | 26.4 | 0 | 8.4 | 2018-06-26 | 24.8 | 0 | 6.8 | 2017-06-26 | 20.4 | 0 | 2.4 | 2016-06-26 | 29.9 | 0 | 11.9 | 0 | 5.97
2025-06-26 | 19.6 | 0 | 1.6 | 2024-06-26 | 21.1 | 0 | 3.1 | 2023-06-26 | 20.8 | 0 | 2.8 | 2022-06-26 | 23.7 | 0 | 5.7 | 2021-06-26 | 22.3 | 0 | 4.3 | 2020-06-26 | 25.4 | 0 | 7.4 | 2019-06-26 | 26.6 | 0 | 8.6 | 2018-06-26 | 23.9 | 0 | 5.9 | 2017-06-26 | 18.9 | 0 | 0.9 | 2016-06-26 | 29.6 | 0 | 11.6 | 0 | 5.19
2025-06-26 | 18.6 | 0 | 0.6 | 2024-06-26 | 19.9 | 0 | 1.9 | 2023-06-26 | 19.9 | 0 | 1.9 | 2022-06-26 | 23.4 | 0 | 5.4 | 2021-06-26 | 22 | 0 | 4 | 2020-06-26 | 23.9 | 0 | 5.9 | 2019-06-26 | 25.1 | 0 | 7.1 | 2018-06-26 | 21.7 | 0 | 3.7 | 2017-06-26 | 17.4 | 0.6 | 0 | 2016-06-26 | 28.1 | 0 | 10.1 | 0.06 | 4.06
2025-06-26 | 14.7 | 3.3 | 0 | 2024-06-26 | 18.5 | 0 | 0.5 | 2023-06-26 | 20.1 | 0 | 2.1 | 2022-06-26 | 23.2 | 0 | 5.2 | 2021-06-26 | 21.2 | 0 | 3.2 | 2020-06-26 | 21 | 0 | 3 | 2019-06-26 | 24.1 | 0 | 6.1 | 2018-06-26 | 19.7 | 0 | 1.7 | 2017-06-26 | 16.6 | 1.4 | 0 | 2016-06-26 | 26.4 | 0 | 8.4 | 0.47 | 3.02
2025-06-26 | 12.9 | 5.1 | 0 | 2024-06-26 | 16.7 | 1.3 | 0 | 2023-06-26 | 19.7 | 0 | 1.7 | 2022-06-26 | 21.6 | 0 | 3.6 | 2021-06-26 | 21.5 | 0 | 3.5 | 2020-06-26 | 20.5 | 0 | 2.5 | 2019-06-26 | 22.1 | 0 | 4.1 | 2018-06-26 | 18 | 0 | 0 | 2017-06-26 | 15.4 | 2.6 | 0 | 2016-06-26 | 25.1 | 0 | 7.1 | 0.9 | 2.25
2025-06-26 | 13.8 | 4.2 | 0 | 2024-06-26 | 16.6 | 1.4 | 0 | 2023-06-26 | 19.4 | 0 | 1.4 | 2022-06-26 | 21 | 0 | 3 | 2021-06-26 | 21.9 | 0 | 3.9 | 2020-06-26 | 20.1 | 0 | 2.1 | 2019-06-26 | 20.8 | 0 | 2.8 | 2018-06-26 | 16.6 | 1.4 | 0 | 2017-06-26 | 14.9 | 3.1 | 0 | 2016-06-26 | 24.6 | 0 | 6.6 | 1.01 | 1.98
2025-06-26 | 13.3 | 4.7 | 0 | 2024-06-26 | 16.4 | 1.6 | 0 | 2023-06-26 | 19.7 | 0 | 1.7 | 2022-06-26 | 21.1 | 0 | 3.1 | 2021-06-26 | 22.1 | 0 | 4.1 | 2020-06-26 | 18.9 | 0 | 0.9 | 2019-06-26 | 19.7 | 0 | 1.7 | 2018-06-26 | 16.2 | 1.8 | 0 | 2017-06-26 | 14.1 | 3.9 | 0 | 2016-06-26 | 23.7 | 0 | 5.7 | 1.2 | 1.72
2025-06-27 | 11.9 | 6.1 | 0 | 2024-06-27 | 14.8 | 3.2 | 0 | 2023-06-27 | 19.2 | 0 | 1.2 | 2022-06-27 | 21 | 0 | 3 | 2021-06-27 | 21.8 | 0 | 3.8 | 2020-06-27 | 18.4 | 0 | 0.4 | 2019-06-27 | 18.6 | 0 | 0.6 | 2018-06-27 | 15.3 | 2.7 | 0 | 2017-06-27 | 13.4 | 4.6 | 0 | 2016-06-27 | 23.7 | 0 | 5.7 | 1.66 | 1.47
2025-06-27 | 13.1 | 4.9 | 0 | 2024-06-27 | 14.5 | 3.5 | 0 | 2023-06-27 | 19.1 | 0 | 1.1 | 2022-06-27 | 21.3 | 0 | 3.3 | 2021-06-27 | 22 | 0 | 4 | 2020-06-27 | 17.3 | 0.7 | 0 | 2019-06-27 | 17.3 | 0.7 | 0 | 2018-06-27 | 13 | 5 | 0 | 2017-06-27 | 12.4 | 5.6 | 0 | 2016-06-27 | 22.5 | 0 | 4.5 | 2.04 | 1.29
2025-06-27 | 13.1 | 4.9 | 0 | 2024-06-27 | 14.6 | 3.4 | 0 | 2023-06-27 | 18.3 | 0 | 0.3 | 2022-06-27 | 20.8 | 0 | 2.8 | 2021-06-27 | 22.1 | 0 | 4.1 | 2020-06-27 | 17.2 | 0.8 | 0 | 2019-06-27 | 15.9 | 2.1 | 0 | 2018-06-27 | 14.2 | 3.8 | 0 | 2017-06-27 | 11.3 | 6.7 | 0 | 2016-06-27 | 20.3 | 0 | 2.3 | 2.17 | 0.95
2025-06-27 | 13.1 | 4.9 | 0 | 2024-06-27 | 13.7 | 4.3 | 0 | 2023-06-27 | 18.2 | 0 | 0.2 | 2022-06-27 | 20.2 | 0 | 2.2 | 2021-06-27 | 22.4 | 0 | 4.4 | 2020-06-27 | 17 | 1 | 0 | 2019-06-27 | 15.2 | 2.8 | 0 | 2018-06-27 | 12.3 | 5.7 | 0 | 2017-06-27 | 10 | 8 | 0 | 2016-06-27 | 20.1 | 0 | 2.1 | 2.67 | 0.89
2025-06-27 | 11.7 | 6.3 | 0 | 2024-06-27 | 13.5 | 4.5 | 0 | 2023-06-27 | 18 | 0 | 0 | 2022-06-27 | 20.6 | 0 | 2.6 | 2021-06-27 | 23 | 0 | 5 | 2020-06-27 | 17 | 1 | 0 | 2019-06-27 | 15.3 | 2.7 | 0 | 2018-06-27 | 12.6 | 5.4 | 0 | 2017-06-27 | 10.6 | 7.4 | 0 | 2016-06-27 | 20.2 | 0 | 2.2 | 2.73 | 0.98
2025-06-27 | 12.4 | 5.6 | 0 | 2024-06-27 | 12.9 | 5.1 | 0 | 2023-06-27 | 18.4 | 0 | 0.4 | 2022-06-27 | 19.4 | 0 | 1.4 | 2021-06-27 | 22.9 | 0 | 4.9 | 2020-06-27 | 16.9 | 1.1 | 0 | 2019-06-27 | 15.1 | 2.9 | 0 | 2018-06-27 | 13 | 5 | 0 | 2017-06-27 | 11 | 7 | 0 | 2016-06-27 | 20.5 | 0 | 2.5 | 2.67 | 0.92
2025-06-27 | 14.3 | 3.7 | 0 | 2024-06-27 | 13.4 | 4.6 | 0 | 2023-06-27 | 19.1 | 0 | 1.1 | 2022-06-27 | 18.7 | 0 | 0.7 | 2021-06-27 | 24 | 0 | 6 | 2020-06-27 | 16.9 | 1.1 | 0 | 2019-06-27 | 17.6 | 0.4 | 0 | 2018-06-27 | 14.7 | 3.3 | 0 | 2017-06-27 | 11.5 | 6.5 | 0 | 2016-06-27 | 20.3 | 0 | 2.3 | 1.96 | 1.01
2025-06-27 | 16.6 | 1.4 | 0 | 2024-06-27 | 14.4 | 3.6 | 0 | 2023-06-27 | 19.9 | 0 | 1.9 | 2022-06-27 | 18.8 | 0 | 0.8 | 2021-06-27 | 24.5 | 0 | 6.5 | 2020-06-27 | 16.8 | 1.2 | 0 | 2019-06-27 | 20.6 | 0 | 2.6 | 2018-06-27 | 16.6 | 1.4 | 0 | 2017-06-27 | 12.9 | 5.1 | 0 | 2016-06-27 | 20.8 | 0 | 2.8 | 1.27 | 1.46
2025-06-27 | 17.8 | 0.2 | 0 | 2024-06-27 | 14.3 | 3.7 | 0 | 2023-06-27 | 20.3 | 0 | 2.3 | 2022-06-27 | 20.3 | 0 | 2.3 | 2021-06-27 | 26.2 | 0 | 8.2 | 2020-06-27 | 19.1 | 0 | 1.1 | 2019-06-27 | 21.8 | 0 | 3.8 | 2018-06-27 | 18.9 | 0 | 0.9 | 2017-06-27 | 15.2 | 2.8 | 0 | 2016-06-27 | 20.8 | 0 | 2.8 | 0.67 | 2.14
2025-06-27 | 19.6 | 0 | 1.6 | 2024-06-27 | 15.1 | 2.9 | 0 | 2023-06-27 | 21.6 | 0 | 3.6 | 2022-06-27 | 21 | 0 | 3 | 2021-06-27 | 27.1 | 0 | 9.1 | 2020-06-27 | 21 | 0 | 3 | 2019-06-27 | 23 | 0 | 5 | 2018-06-27 | 19.9 | 0 | 1.9 | 2017-06-27 | 15.7 | 2.3 | 0 | 2016-06-27 | 20.8 | 0 | 2.8 | 0.52 | 3
2025-06-27 | 22 | 0 | 4 | 2024-06-27 | 15.6 | 2.4 | 0 | 2023-06-27 | 23 | 0 | 5 | 2022-06-27 | 21.9 | 0 | 3.9 | 2021-06-27 | 27.8 | 0 | 9.8 | 2020-06-27 | 22 | 0 | 4 | 2019-06-27 | 25.2 | 0 | 7.2 | 2018-06-27 | 21.6 | 0 | 3.6 | 2017-06-27 | 17 | 1 | 0 | 2016-06-27 | 21.6 | 0 | 3.6 | 0.34 | 4.11
2025-06-27 | 22.6 | 0 | 4.6 | 2024-06-27 | 17.7 | 0.3 | 0 | 2023-06-27 | 24 | 0 | 6 | 2022-06-27 | 21.3 | 0 | 3.3 | 2021-06-27 | 29.6 | 0 | 11.6 | 2020-06-27 | 22.4 | 0 | 4.4 | 2019-06-27 | 26.8 | 0 | 8.8 | 2018-06-27 | 23.5 | 0 | 5.5 | 2017-06-27 | 17.4 | 0.6 | 0 | 2016-06-27 | 22.9 | 0 | 4.9 | 0.09 | 4.91
2025-06-27 | 24.5 | 0 | 6.5 | 2024-06-27 | 17.9 | 0.1 | 0 | 2023-06-27 | 24.3 | 0 | 6.3 | 2022-06-27 | 21.1 | 0 | 3.1 | 2021-06-27 | 29.9 | 0 | 11.9 | 2020-06-27 | 26.2 | 0 | 8.2 | 2019-06-27 | 28.1 | 0 | 10.1 | 2018-06-27 | 23.4 | 0 | 5.4 | 2017-06-27 | 11.8 | 6.2 | 0 | 2016-06-27 | 25.4 | 0 | 7.4 | 0.63 | 5.89
2025-06-27 | 23.6 | 0 | 5.6 | 2024-06-27 | 18.8 | 0 | 0.8 | 2023-06-27 | 25.6 | 0 | 7.6 | 2022-06-27 | 22.3 | 0 | 4.3 | 2021-06-27 | 30.6 | 0 | 12.6 | 2020-06-27 | 25.7 | 0 | 7.7 | 2019-06-27 | 28.7 | 0 | 10.7 | 2018-06-27 | 22.7 | 0 | 4.7 | 2017-06-27 | 13.5 | 4.5 | 0 | 2016-06-27 | 27.4 | 0 | 9.4 | 0.45 | 6.34
2025-06-27 | 22.4 | 0 | 4.4 | 2024-06-27 | 18.3 | 0 | 0.3 | 2023-06-27 | 24.3 | 0 | 6.3 | 2022-06-27 | 21.3 | 0 | 3.3 | 2021-06-27 | 31.1 | 0 | 13.1 | 2020-06-27 | 24.4 | 0 | 6.4 | 2019-06-27 | 28.7 | 0 | 10.7 | 2018-06-27 | 22.6 | 0 | 4.6 | 2017-06-27 | 14.2 | 3.8 | 0 | 2016-06-27 | 28.6 | 0 | 10.6 | 0.38 | 5.97
2025-06-27 | 20.5 | 0 | 2.5 | 2024-06-27 | 17.4 | 0.6 | 0 | 2023-06-27 | 24.3 | 0 | 6.3 | 2022-06-27 | 21.1 | 0 | 3.1 | 2021-06-27 | 30.2 | 0 | 12.2 | 2020-06-27 | 22 | 0 | 4 | 2019-06-27 | 28.4 | 0 | 10.4 | 2018-06-27 | 22.6 | 0 | 4.6 | 2017-06-27 | 15.7 | 2.3 | 0 | 2016-06-27 | 28.5 | 0 | 10.5 | 0.29 | 5.36
2025-06-27 | 17.7 | 0.3 | 0 | 2024-06-27 | 17.9 | 0.1 | 0 | 2023-06-27 | 25.3 | 0 | 7.3 | 2022-06-27 | 20.7 | 0 | 2.7 | 2021-06-27 | 29.2 | 0 | 11.2 | 2020-06-27 | 21.1 | 0 | 3.1 | 2019-06-27 | 28.3 | 0 | 10.3 | 2018-06-27 | 21.3 | 0 | 3.3 | 2017-06-27 | 15.1 | 2.9 | 0 | 2016-06-27 | 28.5 | 0 | 10.5 | 0.33 | 4.84
2025-06-27 | 16.3 | 1.7 | 0 | 2024-06-27 | 17.2 | 0.8 | 0 | 2023-06-27 | 20.3 | 0 | 2.3 | 2022-06-27 | 20.6 | 0 | 2.6 | 2021-06-27 | 29.3 | 0 | 11.3 | 2020-06-27 | 21.5 | 0 | 3.5 | 2019-06-27 | 28.5 | 0 | 10.5 | 2018-06-27 | 18.5 | 0 | 0.5 | 2017-06-27 | 15.6 | 2.4 | 0 | 2016-06-27 | 28.7 | 0 | 10.7 | 0.49 | 4.14
2025-06-27 | 17 | 1 | 0 | 2024-06-27 | 17.3 | 0.7 | 0 | 2023-06-27 | 22.9 | 0 | 4.9 | 2022-06-27 | 19.6 | 0 | 1.6 | 2021-06-27 | 28.4 | 0 | 10.4 | 2020-06-27 | 21.2 | 0 | 3.2 | 2019-06-27 | 26.5 | 0 | 8.5 | 2018-06-27 | 18.8 | 0 | 0.8 | 2017-06-27 | 14.9 | 3.1 | 0 | 2016-06-27 | 27.5 | 0 | 9.5 | 0.48 | 3.89
2025-06-27 | 17.5 | 0.5 | 0 | 2024-06-27 | 16.6 | 1.4 | 0 | 2023-06-27 | 21 | 0 | 3 | 2022-06-27 | 18.8 | 0 | 0.8 | 2021-06-27 | 28 | 0 | 10 | 2020-06-27 | 21 | 0 | 3 | 2019-06-27 | 24.6 | 0 | 6.6 | 2018-06-27 | 18.3 | 0 | 0.3 | 2017-06-27 | 14.2 | 3.8 | 0 | 2016-06-27 | 27.7 | 0 | 9.7 | 0.57 | 3.34
2025-06-27 | 17.6 | 0.4 | 0 | 2024-06-27 | 15.4 | 2.6 | 0 | 2023-06-27 | 20.2 | 0 | 2.2 | 2022-06-27 | 18.4 | 0 | 0.4 | 2021-06-27 | 27.5 | 0 | 9.5 | 2020-06-27 | 20.1 | 0 | 2.1 | 2019-06-27 | 23.1 | 0 | 5.1 | 2018-06-27 | 17.5 | 0.5 | 0 | 2017-06-27 | 12.9 | 5.1 | 0 | 2016-06-27 | 23.6 | 0 | 5.6 | 0.86 | 2.49
2025-06-27 | 17.6 | 0.4 | 0 | 2024-06-27 | 12.2 | 5.8 | 0 | 2023-06-27 | 21.6 | 0 | 3.6 | 2022-06-27 | 16.8 | 1.2 | 0 | 2021-06-27 | 26.5 | 0 | 8.5 | 2020-06-27 | 18.7 | 0 | 0.7 | 2019-06-27 | 22 | 0 | 4 | 2018-06-27 | 17.6 | 0.4 | 0 | 2017-06-27 | 12.4 | 5.6 | 0 | 2016-06-27 | 23.7 | 0 | 5.7 | 1.34 | 2.25
2025-06-27 | 17.7 | 0.3 | 0 | 2024-06-27 | 12.9 | 5.1 | 0 | 2023-06-27 | 20.4 | 0 | 2.4 | 2022-06-27 | 15.8 | 2.2 | 0 | 2021-06-27 | 25.9 | 0 | 7.9 | 2020-06-27 | 16.9 | 1.1 | 0 | 2019-06-27 | 19.8 | 0 | 1.8 | 2018-06-27 | 17.7 | 0.3 | 0 | 2017-06-27 | 11.7 | 6.3 | 0 | 2016-06-27 | 23.2 | 0 | 5.2 | 1.53 | 1.73
2025-06-27 | 18 | 0 | 0 | 2024-06-27 | 11.1 | 6.9 | 0 | 2023-06-27 | 20.1 | 0 | 2.1 | 2022-06-27 | 15.2 | 2.8 | 0 | 2021-06-27 | 25.6 | 0 | 7.6 | 2020-06-27 | 17.3 | 0.7 | 0 | 2019-06-27 | 19.7 | 0 | 1.7 | 2018-06-27 | 17.7 | 0.3 | 0 | 2017-06-27 | 10.7 | 7.3 | 0 | 2016-06-27 | 21.9 | 0 | 3.9 | 1.8 | 1.53
2025-06-28 | 18.1 | 0 | 0.1 | 2024-06-28 | 10.4 | 7.6 | 0 | 2023-06-28 | 20 | 0 | 2 | 2022-06-28 | 14.9 | 3.1 | 0 | 2021-06-28 | 23.5 | 0 | 5.5 | 2020-06-28 | 16.5 | 1.5 | 0 | 2019-06-28 | 18 | 0 | 0 | 2018-06-28 | 17.7 | 0.3 | 0 | 2017-06-28 | 12 | 6 | 0 | 2016-06-28 | 22.4 | 0 | 4.4 | 1.85 | 1.2
2025-06-28 | 18.1 | 0 | 0.1 | 2024-06-28 | 9.4 | 8.6 | 0 | 2023-06-28 | 19.5 | 0 | 1.5 | 2022-06-28 | 15.2 | 2.8 | 0 | 2021-06-28 | 22.9 | 0 | 4.9 | 2020-06-28 | 17 | 1 | 0 | 2019-06-28 | 17.1 | 0.9 | 0 | 2018-06-28 | 17.8 | 0.2 | 0 | 2017-06-28 | 11.5 | 6.5 | 0 | 2016-06-28 | 22.1 | 0 | 4.1 | 2 | 1.06
2025-06-28 | 18.9 | 0 | 0.9 | 2024-06-28 | 8.9 | 9.1 | 0 | 2023-06-28 | 19.5 | 0 | 1.5 | 2022-06-28 | 15.1 | 2.9 | 0 | 2021-06-28 | 22.8 | 0 | 4.8 | 2020-06-28 | 17.1 | 0.9 | 0 | 2019-06-28 | 17.3 | 0.7 | 0 | 2018-06-28 | 17.8 | 0.2 | 0 | 2017-06-28 | 11 | 7 | 0 | 2016-06-28 | 21.7 | 0 | 3.7 | 2.08 | 1.09
2025-06-28 | 19 | 0 | 1 | 2024-06-28 | 9.6 | 8.4 | 0 | 2023-06-28 | 17.1 | 0.9 | 0 | 2022-06-28 | 14.9 | 3.1 | 0 | 2021-06-28 | 22.7 | 0 | 4.7 | 2020-06-28 | 16.9 | 1.1 | 0 | 2019-06-28 | 16.7 | 1.3 | 0 | 2018-06-28 | 17.8 | 0.2 | 0 | 2017-06-28 | 10.2 | 7.8 | 0 | 2016-06-28 | 20.2 | 0 | 2.2 | 2.28 | 0.79
2025-06-28 | 18.8 | 0 | 0.8 | 2024-06-28 | 6.7 | 11.3 | 0 | 2023-06-28 | 15.9 | 2.1 | 0 | 2022-06-28 | 13.3 | 4.7 | 0 | 2021-06-28 | 22.1 | 0 | 4.1 | 2020-06-28 | 17.2 | 0.8 | 0 | 2019-06-28 | 16.4 | 1.6 | 0 | 2018-06-28 | 17.8 | 0.2 | 0 | 2017-06-28 | 9.7 | 8.3 | 0 | 2016-06-28 | 20.4 | 0 | 2.4 | 2.9 | 0.73
2025-06-28 | 18.3 | 0 | 0.3 | 2024-06-28 | 8.1 | 9.9 | 0 | 2023-06-28 | 15.2 | 2.8 | 0 | 2022-06-28 | 14.4 | 3.6 | 0 | 2021-06-28 | 22.1 | 0 | 4.1 | 2020-06-28 | 17.4 | 0.6 | 0 | 2019-06-28 | 16.6 | 1.4 | 0 | 2018-06-28 | 17.8 | 0.2 | 0 | 2017-06-28 | 10.2 | 7.8 | 0 | 2016-06-28 | 19.8 | 0 | 1.8 | 2.63 | 0.62
2025-06-28 | 18.6 | 0 | 0.6 | 2024-06-28 | 10.7 | 7.3 | 0 | 2023-06-28 | 15.2 | 2.8 | 0 | 2022-06-28 | 14.9 | 3.1 | 0 | 2021-06-28 | 22.7 | 0 | 4.7 | 2020-06-28 | 17.6 | 0.4 | 0 | 2019-06-28 | 17.6 | 0.4 | 0 | 2018-06-28 | 17.9 | 0.1 | 0 | 2017-06-28 | 11.6 | 6.4 | 0 | 2016-06-28 | 20.5 | 0 | 2.5 | 2.05 | 0.78
2025-06-28 | 19.1 | 0 | 1.1 | 2024-06-28 | 14.1 | 3.9 | 0 | 2023-06-28 | 15.4 | 2.6 | 0 | 2022-06-28 | 15.9 | 2.1 | 0 | 2021-06-28 | 23.5 | 0 | 5.5 | 2020-06-28 | 17.8 | 0.2 | 0 | 2019-06-28 | 19.9 | 0 | 1.9 | 2018-06-28 | 18.1 | 0 | 0.1 | 2017-06-28 | 12.5 | 5.5 | 0 | 2016-06-28 | 20.9 | 0 | 2.9 | 1.43 | 1.15
2025-06-28 | 18.7 | 0 | 0.7 | 2024-06-28 | 17 | 1 | 0 | 2023-06-28 | 15.3 | 2.7 | 0 | 2022-06-28 | 17.7 | 0.3 | 0 | 2021-06-28 | 24.3 | 0 | 6.3 | 2020-06-28 | 18.5 | 0 | 0.5 | 2019-06-28 | 21.9 | 0 | 3.9 | 2018-06-28 | 18.7 | 0 | 0.7 | 2017-06-28 | 14.4 | 3.6 | 0 | 2016-06-28 | 21.8 | 0 | 3.8 | 0.76 | 1.59
2025-06-28 | 19.2 | 0 | 1.2 | 2024-06-28 | 18.8 | 0 | 0.8 | 2023-06-28 | 15.8 | 2.2 | 0 | 2022-06-28 | 19.3 | 0 | 1.3 | 2021-06-28 | 25.6 | 0 | 7.6 | 2020-06-28 | 19.7 | 0 | 1.7 | 2019-06-28 | 24.1 | 0 | 6.1 | 2018-06-28 | 18.9 | 0 | 0.9 | 2017-06-28 | 16 | 2 | 0 | 2016-06-28 | 22 | 0 | 4 | 0.42 | 2.36
2025-06-28 | 21.8 | 0 | 3.8 | 2024-06-28 | 20.6 | 0 | 2.6 | 2023-06-28 | 15.1 | 2.9 | 0 | 2022-06-28 | 20.6 | 0 | 2.6 | 2021-06-28 | 26.2 | 0 | 8.2 | 2020-06-28 | 22.8 | 0 | 4.8 | 2019-06-28 | 26.8 | 0 | 8.8 | 2018-06-28 | 19.4 | 0 | 1.4 | 2017-06-28 | 18.2 | 0 | 0.2 | 2016-06-28 | 22.3 | 0 | 4.3 | 0.29 | 3.67
2025-06-28 | 23.4 | 0 | 5.4 | 2024-06-28 | 21.3 | 0 | 3.3 | 2023-06-28 | 16.1 | 1.9 | 0 | 2022-06-28 | 20.8 | 0 | 2.8 | 2021-06-28 | 28.7 | 0 | 10.7 | 2020-06-28 | 23.9 | 0 | 5.9 | 2019-06-28 | 27.2 | 0 | 9.2 | 2018-06-28 | 19.6 | 0 | 1.6 | 2017-06-28 | 20.7 | 0 | 2.7 | 2016-06-28 | 23.6 | 0 | 5.6 | 0.19 | 4.72
2025-06-28 | 26.4 | 0 | 8.4 | 2024-06-28 | 21.9 | 0 | 3.9 | 2023-06-28 | 16.2 | 1.8 | 0 | 2022-06-28 | 22.1 | 0 | 4.1 | 2021-06-28 | 29 | 0 | 11 | 2020-06-28 | 23.1 | 0 | 5.1 | 2019-06-28 | 27.4 | 0 | 9.4 | 2018-06-28 | 19.5 | 0 | 1.5 | 2017-06-28 | 22 | 0 | 4 | 2016-06-28 | 24.7 | 0 | 6.7 | 0.18 | 5.41
2025-06-28 | 27.7 | 0 | 9.7 | 2024-06-28 | 22.8 | 0 | 4.8 | 2023-06-28 | 16.1 | 1.9 | 0 | 2022-06-28 | 22.4 | 0 | 4.4 | 2021-06-28 | 30.5 | 0 | 12.5 | 2020-06-28 | 26.7 | 0 | 8.7 | 2019-06-28 | 25.9 | 0 | 7.9 | 2018-06-28 | 21 | 0 | 3 | 2017-06-28 | 23 | 0 | 5 | 2016-06-28 | 24.8 | 0 | 6.8 | 0.19 | 6.28
2025-06-28 | 27.9 | 0 | 9.9 | 2024-06-28 | 23.5 | 0 | 5.5 | 2023-06-28 | 15.9 | 2.1 | 0 | 2022-06-28 | 22.1 | 0 | 4.1 | 2021-06-28 | 30.8 | 0 | 12.8 | 2020-06-28 | 23.4 | 0 | 5.4 | 2019-06-28 | 22.5 | 0 | 4.5 | 2018-06-28 | 22.8 | 0 | 4.8 | 2017-06-28 | 23.2 | 0 | 5.2 | 2016-06-28 | 24.9 | 0 | 6.9 | 0.21 | 5.91
2025-06-28 | 29 | 0 | 11 | 2024-06-28 | 23.5 | 0 | 5.5 | 2023-06-28 | 16.3 | 1.7 | 0 | 2022-06-28 | 24.3 | 0 | 6.3 | 2021-06-28 | 30.9 | 0 | 12.9 | 2020-06-28 | 26.1 | 0 | 8.1 | 2019-06-28 | 19.4 | 0 | 1.4 | 2018-06-28 | 23.5 | 0 | 5.5 | 2017-06-28 | 18.6 | 0 | 0.6 | 2016-06-28 | 23.9 | 0 | 5.9 | 0.17 | 5.72
2025-06-28 | 28 | 0 | 10 | 2024-06-28 | 22.2 | 0 | 4.2 | 2023-06-28 | 17.4 | 0.6 | 0 | 2022-06-28 | 24.3 | 0 | 6.3 | 2021-06-28 | 31.8 | 0 | 13.8 | 2020-06-28 | 24.9 | 0 | 6.9 | 2019-06-28 | 19.1 | 0 | 1.1 | 2018-06-28 | 24.9 | 0 | 6.9 | 2017-06-28 | 20.5 | 0 | 2.5 | 2016-06-28 | 23.8 | 0 | 5.8 | 0.06 | 5.75
2025-06-28 | 27 | 0 | 9 | 2024-06-28 | 21.7 | 0 | 3.7 | 2023-06-28 | 17.9 | 0.1 | 0 | 2022-06-28 | 23.9 | 0 | 5.9 | 2021-06-28 | 31.5 | 0 | 13.5 | 2020-06-28 | 27.2 | 0 | 9.2 | 2019-06-28 | 20.6 | 0 | 2.6 | 2018-06-28 | 24.9 | 0 | 6.9 | 2017-06-28 | 19.1 | 0 | 1.1 | 2016-06-28 | 23.5 | 0 | 5.5 | 0.01 | 5.74
2025-06-28 | 23.8 | 0 | 5.8 | 2024-06-28 | 20.4 | 0 | 2.4 | 2023-06-28 | 17.8 | 0.2 | 0 | 2022-06-28 | 23 | 0 | 5 | 2021-06-28 | 30.8 | 0 | 12.8 | 2020-06-28 | 18.8 | 0 | 0.8 | 2019-06-28 | 20.5 | 0 | 2.5 | 2018-06-28 | 24.8 | 0 | 6.8 | 2017-06-28 | 16.9 | 1.1 | 0 | 2016-06-28 | 22.4 | 0 | 4.4 | 0.13 | 4.05
2025-06-28 | 21.2 | 0 | 3.2 | 2024-06-28 | 19.8 | 0 | 1.8 | 2023-06-28 | 18.1 | 0 | 0.1 | 2022-06-28 | 21.5 | 0 | 3.5 | 2021-06-28 | 29.4 | 0 | 11.4 | 2020-06-28 | 18.7 | 0 | 0.7 | 2019-06-28 | 20.3 | 0 | 2.3 | 2018-06-28 | 23.8 | 0 | 5.8 | 2017-06-28 | 16.5 | 1.5 | 0 | 2016-06-28 | 21.2 | 0 | 3.2 | 0.15 | 3.2
2025-06-28 | 19.9 | 0 | 1.9 | 2024-06-28 | 19.3 | 0 | 1.3 | 2023-06-28 | 17.7 | 0.3 | 0 | 2022-06-28 | 19.5 | 0 | 1.5 | 2021-06-28 | 27.7 | 0 | 9.7 | 2020-06-28 | 19.9 | 0 | 1.9 | 2019-06-28 | 19.9 | 0 | 1.9 | 2018-06-28 | 21.9 | 0 | 3.9 | 2017-06-28 | 15.1 | 2.9 | 0 | 2016-06-28 | 20.9 | 0 | 2.9 | 0.32 | 2.5
2025-06-28 | 18.8 | 0 | 0.8 | 2024-06-28 | 17.1 | 0.9 | 0 | 2023-06-28 | 18.1 | 0 | 0.1 | 2022-06-28 | 18 | 0 | 0 | 2021-06-28 | 24.6 | 0 | 6.6 | 2020-06-28 | 18.3 | 0 | 0.3 | 2019-06-28 | 20 | 0 | 2 | 2018-06-28 | 21.1 | 0 | 3.1 | 2017-06-28 | 14.7 | 3.3 | 0 | 2016-06-28 | 19.1 | 0 | 1.1 | 0.42 | 1.4
2025-06-28 | 17.6 | 0.4 | 0 | 2024-06-28 | 17.7 | 0.3 | 0 | 2023-06-28 | 18.3 | 0 | 0.3 | 2022-06-28 | 16.8 | 1.2 | 0 | 2021-06-28 | 24.2 | 0 | 6.2 | 2020-06-28 | 17.3 | 0.7 | 0 | 2019-06-28 | 19.7 | 0 | 1.7 | 2018-06-28 | 20.5 | 0 | 2.5 | 2017-06-28 | 14.9 | 3.1 | 0 | 2016-06-28 | 18.6 | 0 | 0.6 | 0.57 | 1.13
2025-06-28 | 17.3 | 0.7 | 0 | 2024-06-28 | 16.2 | 1.8 | 0 | 2023-06-28 | 18 | 0 | 0 | 2022-06-28 | 16.1 | 1.9 | 0 | 2021-06-28 | 23.2 | 0 | 5.2 | 2020-06-28 | 17.7 | 0.3 | 0 | 2019-06-28 | 19.6 | 0 | 1.6 | 2018-06-28 | 19.6 | 0 | 1.6 | 2017-06-28 | 15 | 3 | 0 | 2016-06-28 | 18.4 | 0 | 0.4 | 0.77 | 0.88
2025-06-29 | 17.9 | 0.1 | 0 | 2024-06-29 | 17.1 | 0.9 | 0 | 2023-06-29 | 17.9 | 0.1 | 0 | 2022-06-29 | 15.5 | 2.5 | 0 | 2021-06-29 | 23.1 | 0 | 5.1 | 2020-06-29 | 19 | 0 | 1 | 2019-06-29 | 19.6 | 0 | 1.6 | 2018-06-29 | 19.5 | 0 | 1.5 | 2017-06-29 | 14.9 | 3.1 | 0 | 2016-06-29 | 18.2 | 0 | 0.2 | 0.67 | 0.94
2025-06-29 | 17.8 | 0.2 | 0 | 2024-06-29 | 16.8 | 1.2 | 0 | 2023-06-29 | 18.1 | 0 | 0.1 | 2022-06-29 | 14.6 | 3.4 | 0 | 2021-06-29 | 22.6 | 0 | 4.6 | 2020-06-29 | 17.5 | 0.5 | 0 | 2019-06-29 | 19.1 | 0 | 1.1 | 2018-06-29 | 19.2 | 0 | 1.2 | 2017-06-29 | 14.7 | 3.3 | 0 | 2016-06-29 | 17.7 | 0.3 | 0 | 0.89 | 0.7
2025-06-29 | 17.2 | 0.8 | 0 | 2024-06-29 | 16.8 | 1.2 | 0 | 2023-06-29 | 18.4 | 0 | 0.4 | 2022-06-29 | 14.4 | 3.6 | 0 | 2021-06-29 | 21.8 | 0 | 3.8 | 2020-06-29 | 17.6 | 0.4 | 0 | 2019-06-29 | 19 | 0 | 1 | 2018-06-29 | 18.1 | 0 | 0.1 | 2017-06-29 | 14 | 4 | 0 | 2016-06-29 | 17.1 | 0.9 | 0 | 1.09 | 0.53
2025-06-29 | 16.3 | 1.7 | 0 | 2024-06-29 | 17.8 | 0.2 | 0 | 2023-06-29 | 18.3 | 0 | 0.3 | 2022-06-29 | 13.6 | 4.4 | 0 | 2021-06-29 | 20.5 | 0 | 2.5 | 2020-06-29 | 16.6 | 1.4 | 0 | 2019-06-29 | 18.7 | 0 | 0.7 | 2018-06-29 | 17.6 | 0.4 | 0 | 2017-06-29 | 13.9 | 4.1 | 0 | 2016-06-29 | 17 | 1 | 0 | 1.32 | 0.35
2025-06-29 | 16.8 | 1.2 | 0 | 2024-06-29 | 18.2 | 0 | 0.2 | 2023-06-29 | 18.2 | 0 | 0.2 | 2022-06-29 | 13.4 | 4.6 | 0 | 2021-06-29 | 20.1 | 0 | 2.1 | 2020-06-29 | 16.9 | 1.1 | 0 | 2019-06-29 | 18.8 | 0 | 0.8 | 2018-06-29 | 17 | 1 | 0 | 2017-06-29 | 14.5 | 3.5 | 0 | 2016-06-29 | 17 | 1 | 0 | 1.24 | 0.33
2025-06-29 | 17 | 1 | 0 | 2024-06-29 | 18 | 0 | 0 | 2023-06-29 | 17.8 | 0.2 | 0 | 2022-06-29 | 14 | 4 | 0 | 2021-06-29 | 19.3 | 0 | 1.3 | 2020-06-29 | 16.9 | 1.1 | 0 | 2019-06-29 | 18.5 | 0 | 0.5 | 2018-06-29 | 17.1 | 0.9 | 0 | 2017-06-29 | 14.7 | 3.3 | 0 | 2016-06-29 | 17.1 | 0.9 | 0 | 1.14 | 0.18
2025-06-29 | 17.4 | 0.6 | 0 | 2024-06-29 | 17.3 | 0.7 | 0 | 2023-06-29 | 18.3 | 0 | 0.3 | 2022-06-29 | 15 | 3 | 0 | 2021-06-29 | 20.9 | 0 | 2.9 | 2020-06-29 | 17.9 | 0.1 | 0 | 2019-06-29 | 20 | 0 | 2 | 2018-06-29 | 18.4 | 0 | 0.4 | 2017-06-29 | 15.3 | 2.7 | 0 | 2016-06-29 | 17.2 | 0.8 | 0 | 0.79 | 0.56
2025-06-29 | 18.1 | 0 | 0.1 | 2024-06-29 | 16.8 | 1.2 | 0 | 2023-06-29 | 19.8 | 0 | 1.8 | 2022-06-29 | 16.8 | 1.2 | 0 | 2021-06-29 | 22.4 | 0 | 4.4 | 2020-06-29 | 19.4 | 0 | 1.4 | 2019-06-29 | 20.9 | 0 | 2.9 | 2018-06-29 | 21.1 | 0 | 3.1 | 2017-06-29 | 16.1 | 1.9 | 0 | 2016-06-29 | 17.4 | 0.6 | 0 | 0.49 | 1.37
2025-06-29 | 18.3 | 0 | 0.3 | 2024-06-29 | 16.9 | 1.1 | 0 | 2023-06-29 | 20.8 | 0 | 2.8 | 2022-06-29 | 18.7 | 0 | 0.7 | 2021-06-29 | 23.7 | 0 | 5.7 | 2020-06-29 | 20.9 | 0 | 2.9 | 2019-06-29 | 22.4 | 0 | 4.4 | 2018-06-29 | 23.1 | 0 | 5.1 | 2017-06-29 | 16.5 | 1.5 | 0 | 2016-06-29 | 18.1 | 0 | 0.1 | 0.26 | 2.2
2025-06-29 | 19 | 0 | 1 | 2024-06-29 | 17.1 | 0.9 | 0 | 2023-06-29 | 22 | 0 | 4 | 2022-06-29 | 20.4 | 0 | 2.4 | 2021-06-29 | 24.7 | 0 | 6.7 | 2020-06-29 | 22.9 | 0 | 4.9 | 2019-06-29 | 23.4 | 0 | 5.4 | 2018-06-29 | 24.2 | 0 | 6.2 | 2017-06-29 | 16.6 | 1.4 | 0 | 2016-06-29 | 19.4 | 0 | 1.4 | 0.23 | 3.2
2025-06-29 | 18.9 | 0 | 0.9 | 2024-06-29 | 17.3 | 0.7 | 0 | 2023-06-29 | 23.2 | 0 | 5.2 | 2022-06-29 | 22.5 | 0 | 4.5 | 2021-06-29 | 26.8 | 0 | 8.8 | 2020-06-29 | 24.2 | 0 | 6.2 | 2019-06-29 | 24.1 | 0 | 6.1 | 2018-06-29 | 26.7 | 0 | 8.7 | 2017-06-29 | 15.7 | 2.3 | 0 | 2016-06-29 | 20.9 | 0 | 2.9 | 0.3 | 4.33
2025-06-29 | 18.8 | 0 | 0.8 | 2024-06-29 | 17.9 | 0.1 | 0 | 2023-06-29 | 24.4 | 0 | 6.4 | 2022-06-29 | 21.8 | 0 | 3.8 | 2021-06-29 | 27.3 | 0 | 9.3 | 2020-06-29 | 25 | 0 | 7 | 2019-06-29 | 24.6 | 0 | 6.6 | 2018-06-29 | 28 | 0 | 10 | 2017-06-29 | 15.7 | 2.3 | 0 | 2016-06-29 | 21 | 0 | 3 | 0.24 | 4.69
2025-06-29 | 20.8 | 0 | 2.8 | 2024-06-29 | 17.9 | 0.1 | 0 | 2023-06-29 | 25.6 | 0 | 7.6 | 2022-06-29 | 18.3 | 0 | 0.3 | 2021-06-29 | 23.9 | 0 | 5.9 | 2020-06-29 | 26.4 | 0 | 8.4 | 2019-06-29 | 25 | 0 | 7 | 2018-06-29 | 29.4 | 0 | 11.4 | 2017-06-29 | 15.8 | 2.2 | 0 | 2016-06-29 | 21.8 | 0 | 3.8 | 0.23 | 4.72
2025-06-29 | 23 | 0 | 5 | 2024-06-29 | 18.3 | 0 | 0.3 | 2023-06-29 | 26.2 | 0 | 8.2 | 2022-06-29 | 18.3 | 0 | 0.3 | 2021-06-29 | 19.8 | 0 | 1.8 | 2020-06-29 | 27.4 | 0 | 9.4 | 2019-06-29 | 25.7 | 0 | 7.7 | 2018-06-29 | 30.5 | 0 | 12.5 | 2017-06-29 | 16 | 2 | 0 | 2016-06-29 | 23.4 | 0 | 5.4 | 0.2 | 5.06
2025-06-29 | 24.4 | 0 | 6.4 | 2024-06-29 | 18.7 | 0 | 0.7 | 2023-06-29 | 26.4 | 0 | 8.4 | 2022-06-29 | 17.4 | 0.6 | 0 | 2021-06-29 | 20.3 | 0 | 2.3 | 2020-06-29 | 25.1 | 0 | 7.1 | 2019-06-29 | 26.8 | 0 | 8.8 | 2018-06-29 | 31.1 | 0 | 13.1 | 2017-06-29 | 16.1 | 1.9 | 0 | 2016-06-29 | 22.9 | 0 | 4.9 | 0.25 | 5.17
2025-06-29 | 24.7 | 0 | 6.7 | 2024-06-29 | 19.9 | 0 | 1.9 | 2023-06-29 | 26.1 | 0 | 8.1 | 2022-06-29 | 17.8 | 0.2 | 0 | 2021-06-29 | 22.2 | 0 | 4.2 | 2020-06-29 | 20.3 | 0 | 2.3 | 2019-06-29 | 27.5 | 0 | 9.5 | 2018-06-29 | 32.1 | 0 | 14.1 | 2017-06-29 | 16.3 | 1.7 | 0 | 2016-06-29 | 23.5 | 0 | 5.5 | 0.19 | 5.23
2025-06-29 | 25.6 | 0 | 7.6 | 2024-06-29 | 21 | 0 | 3 | 2023-06-29 | 26.2 | 0 | 8.2 | 2022-06-29 | 18.4 | 0 | 0.4 | 2021-06-29 | 22.7 | 0 | 4.7 | 2020-06-29 | 24 | 0 | 6 | 2019-06-29 | 27 | 0 | 9 | 2018-06-29 | 31.4 | 0 | 13.4 | 2017-06-29 | 16 | 2 | 0 | 2016-06-29 | 24.9 | 0 | 6.9 | 0.2 | 5.92
2025-06-29 | 26.1 | 0 | 8.1 | 2024-06-29 | 21.3 | 0 | 3.3 | 2023-06-29 | 25.7 | 0 | 7.7 | 2022-06-29 | 17.4 | 0.6 | 0 | 2021-06-29 | 23.7 | 0 | 5.7 | 2020-06-29 | 25.1 | 0 | 7.1 | 2019-06-29 | 23.9 | 0 | 5.9 | 2018-06-29 | 31.7 | 0 | 13.7 | 2017-06-29 | 16.4 | 1.6 | 0 | 2016-06-29 | 23.8 | 0 | 5.8 | 0.22 | 5.73
2025-06-29 | 26 | 0 | 8 | 2024-06-29 | 22.2 | 0 | 4.2 | 2023-06-29 | 24.7 | 0 | 6.7 | 2022-06-29 | 18.4 | 0 | 0.4 | 2021-06-29 | 24.4 | 0 | 6.4 | 2020-06-29 | 24.3 | 0 | 6.3 | 2019-06-29 | 17.8 | 0.2 | 0 | 2018-06-29 | 30.8 | 0 | 12.8 | 2017-06-29 | 16.5 | 1.5 | 0 | 2016-06-29 | 22.7 | 0 | 4.7 | 0.17 | 4.95
2025-06-29 | 24 | 0 | 6 | 2024-06-29 | 21.9 | 0 | 3.9 | 2023-06-29 | 22.6 | 0 | 4.6 | 2022-06-29 | 18.1 | 0 | 0.1 | 2021-06-29 | 23.4 | 0 | 5.4 | 2020-06-29 | 22.9 | 0 | 4.9 | 2019-06-29 | 17.3 | 0.7 | 0 | 2018-06-29 | 28.8 | 0 | 10.8 | 2017-06-29 | 16.3 | 1.7 | 0 | 2016-06-29 | 23.1 | 0 | 5.1 | 0.24 | 4.08
2025-06-29 | 22 | 0 | 4 | 2024-06-29 | 21.7 | 0 | 3.7 | 2023-06-29 | 21.9 | 0 | 3.9 | 2022-06-29 | 16.1 | 1.9 | 0 | 2021-06-29 | 22 | 0 | 4 | 2020-06-29 | 22.2 | 0 | 4.2 | 2019-06-29 | 15.8 | 2.2 | 0 | 2018-06-29 | 24.4 | 0 | 6.4 | 2017-06-29 | 16.2 | 1.8 | 0 | 2016-06-29 | 19.5 | 0 | 1.5 | 0.59 | 2.77
2025-06-29 | 19.9 | 0 | 1.9 | 2024-06-29 | 21.7 | 0 | 3.7 | 2023-06-29 | 19.8 | 0 | 1.8 | 2022-06-29 | 15.1 | 2.9 | 0 | 2021-06-29 | 21.7 | 0 | 3.7 | 2020-06-29 | 20.2 | 0 | 2.2 | 2019-06-29 | 17.3 | 0.7 | 0 | 2018-06-29 | 24.6 | 0 | 6.6 | 2017-06-29 | 16 | 2 | 0 | 2016-06-29 | 18.1 | 0 | 0.1 | 0.56 | 2
2025-06-29 | 18.7 | 0 | 0.7 | 2024-06-29 | 21.5 | 0 | 3.5 | 2023-06-29 | 18.6 | 0 | 0.6 | 2022-06-29 | 14.4 | 3.6 | 0 | 2021-06-29 | 21.4 | 0 | 3.4 | 2020-06-29 | 18.9 | 0 | 0.9 | 2019-06-29 | 17 | 1 | 0 | 2018-06-29 | 22.9 | 0 | 4.9 | 2017-06-29 | 15.5 | 2.5 | 0 | 2016-06-29 | 16.8 | 1.2 | 0 | 0.83 | 1.4
2025-06-29 | 17.6 | 0.4 | 0 | 2024-06-29 | 21.4 | 0 | 3.4 | 2023-06-29 | 17.9 | 0.1 | 0 | 2022-06-29 | 12.3 | 5.7 | 0 | 2021-06-29 | 21 | 0 | 3 | 2020-06-29 | 18.6 | 0 | 0.6 | 2019-06-29 | 16.7 | 1.3 | 0 | 2018-06-29 | 22.6 | 0 | 4.6 | 2017-06-29 | 15.4 | 2.6 | 0 | 2016-06-29 | 15.8 | 2.2 | 0 | 1.23 | 1.16
2025-06-30 | 17.1 | 0.9 | 0 | 2024-06-30 | 21.1 | 0 | 3.1 | 2023-06-30 | 17.3 | 0.7 | 0 | 2022-06-30 | 12.8 | 5.2 | 0 | 2021-06-30 | 20.9 | 0 | 2.9 | 2020-06-30 | 18.4 | 0 | 0.4 | 2019-06-30 | 16.3 | 1.7 | 0 | 2018-06-30 | 22.8 | 0 | 4.8 | 2017-06-30 | 15.5 | 2.5 | 0 | 2016-06-30 | 15.2 | 2.8 | 0 | 1.38 | 1.12
2025-06-30 | 16.4 | 1.6 | 0 | 2024-06-30 | 20.9 | 0 | 2.9 | 2023-06-30 | 17.1 | 0.9 | 0 | 2022-06-30 | 11.9 | 6.1 | 0 | 2021-06-30 | 21.7 | 0 | 3.7 | 2020-06-30 | 18.9 | 0 | 0.9 | 2019-06-30 | 16 | 2 | 0 | 2018-06-30 | 22.6 | 0 | 4.6 | 2017-06-30 | 15.4 | 2.6 | 0 | 2016-06-30 | 14.5 | 3.5 | 0 | 1.67 | 1.21
2025-06-30 | 15.4 | 2.6 | 0 | 2024-06-30 | 20.3 | 0 | 2.3 | 2023-06-30 | 16.7 | 1.3 | 0 | 2022-06-30 | 11 | 7 | 0 | 2021-06-30 | 22.3 | 0 | 4.3 | 2020-06-30 | 19.1 | 0 | 1.1 | 2019-06-30 | 16.3 | 1.7 | 0 | 2018-06-30 | 20.9 | 0 | 2.9 | 2017-06-30 | 15.4 | 2.6 | 0 | 2016-06-30 | 14.3 | 3.7 | 0 | 1.89 | 1.06
2025-06-30 | 15.1 | 2.9 | 0 | 2024-06-30 | 20.1 | 0 | 2.1 | 2023-06-30 | 15 | 3 | 0 | 2022-06-30 | 10.7 | 7.3 | 0 | 2021-06-30 | 22.4 | 0 | 4.4 | 2020-06-30 | 18.8 | 0 | 0.8 | 2019-06-30 | 16.6 | 1.4 | 0 | 2018-06-30 | 21.9 | 0 | 3.9 | 2017-06-30 | 15.5 | 2.5 | 0 | 2016-06-30 | 13.2 | 4.8 | 0 | 2.19 | 1.12
2025-06-30 | 14.5 | 3.5 | 0 | 2024-06-30 | 20.1 | 0 | 2.1 | 2023-06-30 | 13.4 | 4.6 | 0 | 2022-06-30 | 11.1 | 6.9 | 0 | 2021-06-30 | 22.2 | 0 | 4.2 | 2020-06-30 | 18.7 | 0 | 0.7 | 2019-06-30 | 16.2 | 1.8 | 0 | 2018-06-30 | 21.6 | 0 | 3.6 | 2017-06-30 | 15.5 | 2.5 | 0 | 2016-06-30 | 11.8 | 6.2 | 0 | 2.55 | 1.06
2025-06-30 | 15.2 | 2.8 | 0 | 2024-06-30 | 19.9 | 0 | 1.9 | 2023-06-30 | 14.8 | 3.2 | 0 | 2022-06-30 | 11.1 | 6.9 | 0 | 2021-06-30 | 22.1 | 0 | 4.1 | 2020-06-30 | 18.8 | 0 | 0.8 | 2019-06-30 | 16.2 | 1.8 | 0 | 2018-06-30 | 20.7 | 0 | 2.7 | 2017-06-30 | 15.6 | 2.4 | 0 | 2016-06-30 | 14.1 | 3.9 | 0 | 2.1 | 0.95
2025-06-30 | 16.4 | 1.6 | 0 | 2024-06-30 | 20.8 | 0 | 2.8 | 2023-06-30 | 15.7 | 2.3 | 0 | 2022-06-30 | 13.3 | 4.7 | 0 | 2021-06-30 | 22.2 | 0 | 4.2 | 2020-06-30 | 20.2 | 0 | 2.2 | 2019-06-30 | 15.8 | 2.2 | 0 | 2018-06-30 | 20.8 | 0 | 2.8 | 2017-06-30 | 15.8 | 2.2 | 0 | 2016-06-30 | 16.7 | 1.3 | 0 | 1.43 | 1.2
2025-06-30 | 19.1 | 0 | 1.1 | 2024-06-30 | 21.9 | 0 | 3.9 | 2023-06-30 | 18.3 | 0 | 0.3 | 2022-06-30 | 13.8 | 4.2 | 0 | 2021-06-30 | 23 | 0 | 5 | 2020-06-30 | 20.1 | 0 | 2.1 | 2019-06-30 | 15.6 | 2.4 | 0 | 2018-06-30 | 22.1 | 0 | 4.1 | 2017-06-30 | 16.3 | 1.7 | 0 | 2016-06-30 | 18.4 | 0 | 0.4 | 0.83 | 1.69
2025-06-30 | 21.9 | 0 | 3.9 | 2024-06-30 | 22.9 | 0 | 4.9 | 2023-06-30 | 21.3 | 0 | 3.3 | 2022-06-30 | 15 | 3 | 0 | 2021-06-30 | 24.5 | 0 | 6.5 | 2020-06-30 | 21.5 | 0 | 3.5 | 2019-06-30 | 16.9 | 1.1 | 0 | 2018-06-30 | 23.6 | 0 | 5.6 | 2017-06-30 | 16.6 | 1.4 | 0 | 2016-06-30 | 20.8 | 0 | 2.8 | 0.55 | 3.05
2025-06-30 | 23.9 | 0 | 5.9 | 2024-06-30 | 22.7 | 0 | 4.7 | 2023-06-30 | 22.6 | 0 | 4.6 | 2022-06-30 | 15.7 | 2.3 | 0 | 2021-06-30 | 24.6 | 0 | 6.6 | 2020-06-30 | 21.6 | 0 | 3.6 | 2019-06-30 | 17.3 | 0.7 | 0 | 2018-06-30 | 26.7 | 0 | 8.7 | 2017-06-30 | 17.6 | 0.4 | 0 | 2016-06-30 | 22.7 | 0 | 4.7 | 0.34 | 3.88
2025-06-30 | 25.7 | 0 | 7.7 | 2024-06-30 | 23.6 | 0 | 5.6 | 2023-06-30 | 22.4 | 0 | 4.4 | 2022-06-30 | 19.5 | 0 | 1.5 | 2021-06-30 | 25.4 | 0 | 7.4 | 2020-06-30 | 21.8 | 0 | 3.8 | 2019-06-30 | 18.3 | 0 | 0.3 | 2018-06-30 | 28.3 | 0 | 10.3 | 2017-06-30 | 18.1 | 0 | 0.1 | 2016-06-30 | 25.2 | 0 | 7.2 | 0 | 4.83
2025-06-30 | 26.5 | 0 | 8.5 | 2024-06-30 | 24.7 | 0 | 6.7 | 2023-06-30 | 22 | 0 | 4 | 2022-06-30 | 21.3 | 0 | 3.3 | 2021-06-30 | 27.3 | 0 | 9.3 | 2020-06-30 | 22.5 | 0 | 4.5 | 2019-06-30 | 17.9 | 0.1 | 0 | 2018-06-30 | 30.1 | 0 | 12.1 | 2017-06-30 | 19 | 0 | 1 | 2016-06-30 | 27 | 0 | 9 | 0.01 | 5.84
2025-06-30 | 28 | 0 | 10 | 2024-06-30 | 24.9 | 0 | 6.9 | 2023-06-30 | 22.2 | 0 | 4.2 | 2022-06-30 | 22.2 | 0 | 4.2 | 2021-06-30 | 27.9 | 0 | 9.9 | 2020-06-30 | 23.9 | 0 | 5.9 | 2019-06-30 | 20.1 | 0 | 2.1 | 2018-06-30 | 29.9 | 0 | 11.9 | 2017-06-30 | 20.1 | 0 | 2.1 | 2016-06-30 | 27.3 | 0 | 9.3 | 0 | 6.65
2025-06-30 | 28.5 | 0 | 10.5 | 2024-06-30 | 24.7 | 0 | 6.7 | 2023-06-30 | 23.7 | 0 | 5.7 | 2022-06-30 | 21.3 | 0 | 3.3 | 2021-06-30 | 29.1 | 0 | 11.1 | 2020-06-30 | 24.1 | 0 | 6.1 | 2019-06-30 | 21.7 | 0 | 3.7 | 2018-06-30 | 29.3 | 0 | 11.3 | 2017-06-30 | 21.4 | 0 | 3.4 | 2016-06-30 | 28.2 | 0 | 10.2 | 0 | 7.2
2025-06-30 | 29.5 | 0 | 11.5 | 2024-06-30 | 23.7 | 0 | 5.7 | 2023-06-30 | 24.5 | 0 | 6.5 | 2022-06-30 | 22.6 | 0 | 4.6 | 2021-06-30 | 29.9 | 0 | 11.9 | 2020-06-30 | 25.4 | 0 | 7.4 | 2019-06-30 | 22.5 | 0 | 4.5 | 2018-06-30 | 31.9 | 0 | 13.9 | 2017-06-30 | 21.1 | 0 | 3.1 | 2016-06-30 | 29.3 | 0 | 11.3 | 0 | 8.04
2025-06-30 | 30.1 | 0 | 12.1 | 2024-06-30 | 23.1 | 0 | 5.1 | 2023-06-30 | 24.9 | 0 | 6.9 | 2022-06-30 | 23.8 | 0 | 5.8 | 2021-06-30 | 24.5 | 0 | 6.5 | 2020-06-30 | 26.9 | 0 | 8.9 | 2019-06-30 | 22.3 | 0 | 4.3 | 2018-06-30 | 33.6 | 0 | 15.6 | 2017-06-30 | 21.1 | 0 | 3.1 | 2016-06-30 | 28.7 | 0 | 10.7 | 0 | 7.9
2025-06-30 | 30 | 0 | 12 | 2024-06-30 | 21.7 | 0 | 3.7 | 2023-06-30 | 25.7 | 0 | 7.7 | 2022-06-30 | 23.8 | 0 | 5.8 | 2021-06-30 | 25.1 | 0 | 7.1 | 2020-06-30 | 25.8 | 0 | 7.8 | 2019-06-30 | 23.4 | 0 | 5.4 | 2018-06-30 | 32.9 | 0 | 14.9 | 2017-06-30 | 22.1 | 0 | 4.1 | 2016-06-30 | 28.7 | 0 | 10.7 | 0 | 7.92
2025-06-30 | 29.6 | 0 | 11.6 | 2024-06-30 | 20 | 0 | 2 | 2023-06-30 | 25.7 | 0 | 7.7 | 2022-06-30 | 24.1 | 0 | 6.1 | 2021-06-30 | 26.3 | 0 | 8.3 | 2020-06-30 | 24.9 | 0 | 6.9 | 2019-06-30 | 23.6 | 0 | 5.6 | 2018-06-30 | 30.9 | 0 | 12.9 | 2017-06-30 | 22.1 | 0 | 4.1 | 2016-06-30 | 28.1 | 0 | 10.1 | 0 | 7.53
2025-06-30 | 29.1 | 0 | 11.1 | 2024-06-30 | 19.5 | 0 | 1.5 | 2023-06-30 | 25.4 | 0 | 7.4 | 2022-06-30 | 22.2 | 0 | 4.2 | 2021-06-30 | 23.9 | 0 | 5.9 | 2020-06-30 | 24.3 | 0 | 6.3 | 2019-06-30 | 23 | 0 | 5 | 2018-06-30 | 31 | 0 | 13 | 2017-06-30 | 22.9 | 0 | 4.9 | 2016-06-30 | 27 | 0 | 9 | 0 | 6.83
2025-06-30 | 26.5 | 0 | 8.5 | 2024-06-30 | 18.2 | 0 | 0.2 | 2023-06-30 | 23.9 | 0 | 5.9 | 2022-06-30 | 21.1 | 0 | 3.1 | 2021-06-30 | 23.1 | 0 | 5.1 | 2020-06-30 | 23.2 | 0 | 5.2 | 2019-06-30 | 21.5 | 0 | 3.5 | 2018-06-30 | 30.4 | 0 | 12.4 | 2017-06-30 | 22.3 | 0 | 4.3 | 2016-06-30 | 25.1 | 0 | 7.1 | 0 | 5.53
2025-06-30 | 25.5 | 0 | 7.5 | 2024-06-30 | 16.6 | 1.4 | 0 | 2023-06-30 | 21.7 | 0 | 3.7 | 2022-06-30 | 20.1 | 0 | 2.1 | 2021-06-30 | 21.6 | 0 | 3.6 | 2020-06-30 | 21.5 | 0 | 3.5 | 2019-06-30 | 19.7 | 0 | 1.7 | 2018-06-30 | 29.1 | 0 | 11.1 | 2017-06-30 | 20.4 | 0 | 2.4 | 2016-06-30 | 22.2 | 0 | 4.2 | 0.14 | 3.98
2025-06-30 | 24.7 | 0 | 6.7 | 2024-06-30 | 15.5 | 2.5 | 0 | 2023-06-30 | 20.5 | 0 | 2.5 | 2022-06-30 | 19.3 | 0 | 1.3 | 2021-06-30 | 20.4 | 0 | 2.4 | 2020-06-30 | 19.6 | 0 | 1.6 | 2019-06-30 | 18.1 | 0 | 0.1 | 2018-06-30 | 28.3 | 0 | 10.3 | 2017-06-30 | 20.5 | 0 | 2.5 | 2016-06-30 | 20.2 | 0 | 2.2 | 0.25 | 2.96
2025-06-30 | 24.8 | 0 | 6.8 | 2024-06-30 | 16.2 | 1.8 | 0 | 2023-06-30 | 20.4 | 0 | 2.4 | 2022-06-30 | 17.3 | 0.7 | 0 | 2021-06-30 | 19.6 | 0 | 1.6 | 2020-06-30 | 20 | 0 | 2 | 2019-06-30 | 18.2 | 0 | 0.2 | 2018-06-30 | 27.6 | 0 | 9.6 | 2017-06-30 | 20.4 | 0 | 2.4 | 2016-06-30 | 18.7 | 0 | 0.7 | 0.25 | 2.57
2025-06-30 | 24.1 | 0 | 6.1 | 2024-06-30 | 16.3 | 1.7 | 0 | 2023-06-30 | 20.3 | 0 | 2.3 | 2022-06-30 | 18.5 | 0 | 0.5 | 2021-06-30 | 18.5 | 0 | 0.5 | 2020-06-30 | 19 | 0 | 1 | 2019-06-30 | 16.9 | 1.1 | 0 | 2018-06-30 | 26.7 | 0 | 8.7 | 2017-06-30 | 20.5 | 0 | 2.5 | 2016-06-30 | 17.3 | 0.7 | 0 | 0.35 | 2.16
2025-07-01 | 22.2 | 0 | 4.2 | 2024-07-01 | 16.2 | 1.8 | 0 | 2023-07-01 | 19.7 | 0 | 1.7 | 2022-07-01 | 19.4 | 0 | 1.4 | 2021-07-01 | 17.3 | 0.7 | 0 | 2020-07-01 | 18.4 | 0 | 0.4 | 2019-07-01 | 15.1 | 2.9 | 0 | 2018-07-01 | 25.5 | 0 | 7.5 | 2017-07-01 | 19.8 | 0 | 1.8 | 2016-07-01 | 15.8 | 2.2 | 0 | 0.76 | 1.7
2025-07-01 | 21.9 | 0 | 3.9 | 2024-07-01 | 15.9 | 2.1 | 0 | 2023-07-01 | 19.4 | 0 | 1.4 | 2022-07-01 | 19.7 | 0 | 1.7 | 2021-07-01 | 16.1 | 1.9 | 0 | 2020-07-01 | 17.7 | 0.3 | 0 | 2019-07-01 | 14.6 | 3.4 | 0 | 2018-07-01 | 25.3 | 0 | 7.3 | 2017-07-01 | 19.3 | 0 | 1.3 | 2016-07-01 | 14.7 | 3.3 | 0 | 1.1 | 1.56
2025-07-01 | 21.7 | 0 | 3.7 | 2024-07-01 | 15.5 | 2.5 | 0 | 2023-07-01 | 19.6 | 0 | 1.6 | 2022-07-01 | 19.1 | 0 | 1.1 | 2021-07-01 | 16.2 | 1.8 | 0 | 2020-07-01 | 19.1 | 0 | 1.1 | 2019-07-01 | 14.8 | 3.2 | 0 | 2018-07-01 | 24.4 | 0 | 6.4 | 2017-07-01 | 19.4 | 0 | 1.4 | 2016-07-01 | 13.8 | 4.2 | 0 | 1.17 | 1.53
2025-07-01 | 21.7 | 0 | 3.7 | 2024-07-01 | 14.6 | 3.4 | 0 | 2023-07-01 | 19.1 | 0 | 1.1 | 2022-07-01 | 20 | 0 | 2 | 2021-07-01 | 16.4 | 1.6 | 0 | 2020-07-01 | 16.8 | 1.2 | 0 | 2019-07-01 | 13 | 5 | 0 | 2018-07-01 | 24.2 | 0 | 6.2 | 2017-07-01 | 19.4 | 0 | 1.4 | 2016-07-01 | 12.9 | 5.1 | 0 | 1.63 | 1.44
2025-07-01 | 21.5 | 0 | 3.5 | 2024-07-01 | 14 | 4 | 0 | 2023-07-01 | 18.9 | 0 | 0.9 | 2022-07-01 | 20.7 | 0 | 2.7 | 2021-07-01 | 15.8 | 2.2 | 0 | 2020-07-01 | 17.6 | 0.4 | 0 | 2019-07-01 | 12.8 | 5.2 | 0 | 2018-07-01 | 23.6 | 0 | 5.6 | 2017-07-01 | 19.1 | 0 | 1.1 | 2016-07-01 | 12.1 | 5.9 | 0 | 1.77 | 1.38
2025-07-01 | 21.6 | 0 | 3.6 | 2024-07-01 | 13 | 5 | 0 | 2023-07-01 | 18.6 | 0 | 0.6 | 2022-07-01 | 20.6 | 0 | 2.6 | 2021-07-01 | 14.6 | 3.4 | 0 | 2020-07-01 | 18.8 | 0 | 0.8 | 2019-07-01 | 13 | 5 | 0 | 2018-07-01 | 23.5 | 0 | 5.5 | 2017-07-01 | 19.3 | 0 | 1.3 | 2016-07-01 | 12.9 | 5.1 | 0 | 1.85 | 1.44
2025-07-01 | 22.1 | 0 | 4.1 | 2024-07-01 | 14.2 | 3.8 | 0 | 2023-07-01 | 19.6 | 0 | 1.6 | 2022-07-01 | 21.6 | 0 | 3.6 | 2021-07-01 | 17 | 1 | 0 | 2020-07-01 | 20 | 0 | 2 | 2019-07-01 | 15.8 | 2.2 | 0 | 2018-07-01 | 24.4 | 0 | 6.4 | 2017-07-01 | 19.4 | 0 | 1.4 | 2016-07-01 | 14.3 | 3.7 | 0 | 1.07 | 1.91
2025-07-01 | 23.9 | 0 | 5.9 | 2024-07-01 | 16.3 | 1.7 | 0 | 2023-07-01 | 20.7 | 0 | 2.7 | 2022-07-01 | 22.1 | 0 | 4.1 | 2021-07-01 | 17.9 | 0.1 | 0 | 2020-07-01 | 21.5 | 0 | 3.5 | 2019-07-01 | 18.1 | 0 | 0.1 | 2018-07-01 | 26.4 | 0 | 8.4 | 2017-07-01 | 19.5 | 0 | 1.5 | 2016-07-01 | 16.2 | 1.8 | 0 | 0.36 | 2.62
2025-07-01 | 24.4 | 0 | 6.4 | 2024-07-01 | 17.9 | 0.1 | 0 | 2023-07-01 | 21.6 | 0 | 3.6 | 2022-07-01 | 21.9 | 0 | 3.9 | 2021-07-01 | 19.3 | 0 | 1.3 | 2020-07-01 | 23.1 | 0 | 5.1 | 2019-07-01 | 20.5 | 0 | 2.5 | 2018-07-01 | 28.4 | 0 | 10.4 | 2017-07-01 | 19 | 0 | 1 | 2016-07-01 | 19.6 | 0 | 1.6 | 0.01 | 3.58
2025-07-01 | 24.6 | 0 | 6.6 | 2024-07-01 | 19.2 | 0 | 1.2 | 2023-07-01 | 24.5 | 0 | 6.5 | 2022-07-01 | 22.2 | 0 | 4.2 | 2021-07-01 | 20.1 | 0 | 2.1 | 2020-07-01 | 23.9 | 0 | 5.9 | 2019-07-01 | 21.7 | 0 | 3.7 | 2018-07-01 | 30.3 | 0 | 12.3 | 2017-07-01 | 18.9 | 0 | 0.9 | 2016-07-01 | 23.4 | 0 | 5.4 | 0 | 4.88
2025-07-01 | 26 | 0 | 8 | 2024-07-01 | 20.6 | 0 | 2.6 | 2023-07-01 | 25.1 | 0 | 7.1 | 2022-07-01 | 22.8 | 0 | 4.8 | 2021-07-01 | 19.2 | 0 | 1.2 | 2020-07-01 | 26 | 0 | 8 | 2019-07-01 | 22.9 | 0 | 4.9 | 2018-07-01 | 31.8 | 0 | 13.8 | 2017-07-01 | 19.3 | 0 | 1.3 | 2016-07-01 | 26.1 | 0 | 8.1 | 0 | 5.98
2025-07-01 | 26.6 | 0 | 8.6 | 2024-07-01 | 22.3 | 0 | 4.3 | 2023-07-01 | 26.4 | 0 | 8.4 | 2022-07-01 | 23.8 | 0 | 5.8 | 2021-07-01 | 20.3 | 0 | 2.3 | 2020-07-01 | 27.4 | 0 | 9.4 | 2019-07-01 | 23.8 | 0 | 5.8 | 2018-07-01 | 33.5 | 0 | 15.5 | 2017-07-01 | 19.7 | 0 | 1.7 | 2016-07-01 | 27 | 0 | 9 | 0 | 7.08
2025-07-01 | 28.1 | 0 | 10.1 | 2024-07-01 | 23.4 | 0 | 5.4 | 2023-07-01 | 26.9 | 0 | 8.9 | 2022-07-01 | 24.4 | 0 | 6.4 | 2021-07-01 | 22.4 | 0 | 4.4 | 2020-07-01 | 27.9 | 0 | 9.9 | 2019-07-01 | 24.7 | 0 | 6.7 | 2018-07-01 | 33.9 | 0 | 15.9 | 2017-07-01 | 20.1 | 0 | 2.1 | 2016-07-01 | 27.7 | 0 | 9.7 | 0 | 7.95
2025-07-01 | 28 | 0 | 10 | 2024-07-01 | 24 | 0 | 6 | 2023-07-01 | 27 | 0 | 9 | 2022-07-01 | 24.3 | 0 | 6.3 | 2021-07-01 | 22.9 | 0 | 4.9 | 2020-07-01 | 29.3 | 0 | 11.3 | 2019-07-01 | 25.5 | 0 | 7.5 | 2018-07-01 | 34.4 | 0 | 16.4 | 2017-07-01 | 21.3 | 0 | 3.3 | 2016-07-01 | 24.9 | 0 | 6.9 | 0 | 8.16
2025-07-01 | 24.7 | 0 | 6.7 | 2024-07-01 | 25 | 0 | 7 | 2023-07-01 | 26.4 | 0 | 8.4 | 2022-07-01 | 25.4 | 0 | 7.4 | 2021-07-01 | 23.9 | 0 | 5.9 | 2020-07-01 | 30.2 | 0 | 12.2 | 2019-07-01 | 26.6 | 0 | 8.6 | 2018-07-01 | 34.7 | 0 | 16.7 | 2017-07-01 | 22.7 | 0 | 4.7 | 2016-07-01 | 24.6 | 0 | 6.6 | 0 | 8.42
2025-07-01 | 28.6 | 0 | 10.6 | 2024-07-01 | 25 | 0 | 7 | 2023-07-01 | 25.9 | 0 | 7.9 | 2022-07-01 | 26.9 | 0 | 8.9 | 2021-07-01 | 25.3 | 0 | 7.3 | 2020-07-01 | 29.5 | 0 | 11.5 | 2019-07-01 | 26.7 | 0 | 8.7 | 2018-07-01 | 34.3 | 0 | 16.3 | 2017-07-01 | 22.3 | 0 | 4.3 | 2016-07-01 | 17.8 | 0.2 | 0 | 0.02 | 8.25
2025-07-01 | 28.1 | 0 | 10.1 | 2024-07-01 | 25 | 0 | 7 | 2023-07-01 | 20.3 | 0 | 2.3 | 2022-07-01 | 27.6 | 0 | 9.6 | 2021-07-01 | 23.7 | 0 | 5.7 | 2020-07-01 | 30.5 | 0 | 12.5 | 2019-07-01 | 27 | 0 | 9 | 2018-07-01 | 33.8 | 0 | 15.8 | 2017-07-01 | 22.4 | 0 | 4.4 | 2016-07-01 | 20.5 | 0 | 2.5 | 0 | 7.89
2025-07-01 | 24.7 | 0 | 6.7 | 2024-07-01 | 25.1 | 0 | 7.1 | 2023-07-01 | 21.7 | 0 | 3.7 | 2022-07-01 | 27.6 | 0 | 9.6 | 2021-07-01 | 23.7 | 0 | 5.7 | 2020-07-01 | 30.3 | 0 | 12.3 | 2019-07-01 | 26.2 | 0 | 8.2 | 2018-07-01 | 33.4 | 0 | 15.4 | 2017-07-01 | 23.6 | 0 | 5.6 | 2016-07-01 | 20.4 | 0 | 2.4 | 0 | 7.67
2025-07-01 | 26.4 | 0 | 8.4 | 2024-07-01 | 24.3 | 0 | 6.3 | 2023-07-01 | 21.1 | 0 | 3.1 | 2022-07-01 | 27.2 | 0 | 9.2 | 2021-07-01 | 22.7 | 0 | 4.7 | 2020-07-01 | 28.8 | 0 | 10.8 | 2019-07-01 | 25.5 | 0 | 7.5 | 2018-07-01 | 32.6 | 0 | 14.6 | 2017-07-01 | 23.4 | 0 | 5.4 | 2016-07-01 | 19.6 | 0 | 1.6 | 0 | 7.16
2025-07-01 | 24.7 | 0 | 6.7 | 2024-07-01 | 23.4 | 0 | 5.4 | 2023-07-01 | 20.8 | 0 | 2.8 | 2022-07-01 | 25.9 | 0 | 7.9 | 2021-07-01 | 22.2 | 0 | 4.2 | 2020-07-01 | 26.9 | 0 | 8.9 | 2019-07-01 | 24.2 | 0 | 6.2 | 2018-07-01 | 30.5 | 0 | 12.5 | 2017-07-01 | 20.3 | 0 | 2.3 | 2016-07-01 | 14.4 | 3.6 | 0 | 0.36 | 5.69
2025-07-01 | 21.7 | 0 | 3.7 | 2024-07-01 | 19 | 0 | 1 | 2023-07-01 | 20.7 | 0 | 2.7 | 2022-07-01 | 23.6 | 0 | 5.6 | 2021-07-01 | 21.4 | 0 | 3.4 | 2020-07-01 | 25.3 | 0 | 7.3 | 2019-07-01 | 22.7 | 0 | 4.7 | 2018-07-01 | 28.8 | 0 | 10.8 | 2017-07-01 | 18.3 | 0 | 0.3 | 2016-07-01 | 14.7 | 3.3 | 0 | 0.33 | 3.95
2025-07-01 | 22.6 | 0 | 4.6 | 2024-07-01 | 19.9 | 0 | 1.9 | 2023-07-01 | 20 | 0 | 2 | 2022-07-01 | 23 | 0 | 5 | 2021-07-01 | 21.1 | 0 | 3.1 | 2020-07-01 | 22.7 | 0 | 4.7 | 2019-07-01 | 21.6 | 0 | 3.6 | 2018-07-01 | 26.7 | 0 | 8.7 | 2017-07-01 | 18.3 | 0 | 0.3 | 2016-07-01 | 15.6 | 2.4 | 0 | 0.24 | 3.39
2025-07-01 | 20.6 | 0 | 2.6 | 2024-07-01 | 16.2 | 1.8 | 0 | 2023-07-01 | 19.9 | 0 | 1.9 | 2022-07-01 | 22.1 | 0 | 4.1 | 2021-07-01 | 20.3 | 0 | 2.3 | 2020-07-01 | 22.4 | 0 | 4.4 | 2019-07-01 | 21 | 0 | 3 | 2018-07-01 | 25.5 | 0 | 7.5 | 2017-07-01 | 18.5 | 0 | 0.5 | 2016-07-01 | 15.2 | 2.8 | 0 | 0.46 | 2.63
2025-07-01 | 20.3 | 0 | 2.3 | 2024-07-01 | 15.6 | 2.4 | 0 | 2023-07-01 | 19.5 | 0 | 1.5 | 2022-07-01 | 21 | 0 | 3 | 2021-07-01 | 19.6 | 0 | 1.6 | 2020-07-01 | 22.9 | 0 | 4.9 | 2019-07-01 | 20.8 | 0 | 2.8 | 2018-07-01 | 23.7 | 0 | 5.7 | 2017-07-01 | 18 | 0 | 0 | 2016-07-01 | 14.9 | 3.1 | 0 | 0.55 | 2.18
2025-07-02 | 20.3 | 0 | 2.3 | 2024-07-02 | 15.1 | 2.9 | 0 | 2023-07-02 | 19.9 | 0 | 1.9 | 2022-07-02 | 22.3 | 0 | 4.3 | 2021-07-02 | 18.3 | 0 | 0.3 | 2020-07-02 | 20.6 | 0 | 2.6 | 2019-07-02 | 20.5 | 0 | 2.5 | 2018-07-02 | 23.5 | 0 | 5.5 | 2017-07-02 | 17.8 | 0.2 | 0 | 2016-07-02 | 15.1 | 2.9 | 0 | 0.6 | 1.94
2025-07-02 | 19.4 | 0 | 1.4 | 2024-07-02 | 13.5 | 4.5 | 0 | 2023-07-02 | 19.7 | 0 | 1.7 | 2022-07-02 | 19.6 | 0 | 1.6 | 2021-07-02 | 18.4 | 0 | 0.4 | 2020-07-02 | 20.7 | 0 | 2.7 | 2019-07-02 | 20 | 0 | 2 | 2018-07-02 | 23.2 | 0 | 5.2 | 2017-07-02 | 17.3 | 0.7 | 0 | 2016-07-02 | 14.7 | 3.3 | 0 | 0.85 | 1.5
2025-07-02 | 18.1 | 0 | 0.1 | 2024-07-02 | 15.1 | 2.9 | 0 | 2023-07-02 | 19.8 | 0 | 1.8 | 2022-07-02 | 20 | 0 | 2 | 2021-07-02 | 17.6 | 0.4 | 0 | 2020-07-02 | 21.1 | 0 | 3.1 | 2019-07-02 | 19.5 | 0 | 1.5 | 2018-07-02 | 22.6 | 0 | 4.6 | 2017-07-02 | 16.8 | 1.2 | 0 | 2016-07-02 | 14.1 | 3.9 | 0 | 0.84 | 1.31
2025-07-02 | 17.1 | 0.9 | 0 | 2024-07-02 | 15.4 | 2.6 | 0 | 2023-07-02 | 19.7 | 0 | 1.7 | 2022-07-02 | 18.6 | 0 | 0.6 | 2021-07-02 | 16.8 | 1.2 | 0 | 2020-07-02 | 21.4 | 0 | 3.4 | 2019-07-02 | 19.3 | 0 | 1.3 | 2018-07-02 | 22.4 | 0 | 4.4 | 2017-07-02 | 16.4 | 1.6 | 0 | 2016-07-02 | 13.4 | 4.6 | 0 | 1.09 | 1.14
2025-07-02 | 16.7 | 1.3 | 0 | 2024-07-02 | 12.6 | 5.4 | 0 | 2023-07-02 | 19.2 | 0 | 1.2 | 2022-07-02 | 16.4 | 1.6 | 0 | 2021-07-02 | 16.5 | 1.5 | 0 | 2020-07-02 | 21.1 | 0 | 3.1 | 2019-07-02 | 19.1 | 0 | 1.1 | 2018-07-02 | 22.7 | 0 | 4.7 | 2017-07-02 | 16.1 | 1.9 | 0 | 2016-07-02 | 13.4 | 4.6 | 0 | 1.63 | 1.01
2025-07-02 | 16.7 | 1.3 | 0 | 2024-07-02 | 12.4 | 5.6 | 0 | 2023-07-02 | 19.1 | 0 | 1.1 | 2022-07-02 | 15.9 | 2.1 | 0 | 2021-07-02 | 16.2 | 1.8 | 0 | 2020-07-02 | 21.2 | 0 | 3.2 | 2019-07-02 | 19.2 | 0 | 1.2 | 2018-07-02 | 22.4 | 0 | 4.4 | 2017-07-02 | 16 | 2 | 0 | 2016-07-02 | 12.8 | 5.2 | 0 | 1.8 | 0.99
2025-07-02 | 18.7 | 0 | 0.7 | 2024-07-02 | 15.7 | 2.3 | 0 | 2023-07-02 | 19.7 | 0 | 1.7 | 2022-07-02 | 17.6 | 0.4 | 0 | 2021-07-02 | 16.5 | 1.5 | 0 | 2020-07-02 | 22.4 | 0 | 4.4 | 2019-07-02 | 20.7 | 0 | 2.7 | 2018-07-02 | 24.5 | 0 | 6.5 | 2017-07-02 | 16.3 | 1.7 | 0 | 2016-07-02 | 13.2 | 4.8 | 0 | 1.07 | 1.6
2025-07-02 | 20.9 | 0 | 2.9 | 2024-07-02 | 18.8 | 0 | 0.8 | 2023-07-02 | 20.4 | 0 | 2.4 | 2022-07-02 | 18.6 | 0 | 0.6 | 2021-07-02 | 18 | 0 | 0 | 2020-07-02 | 23.4 | 0 | 5.4 | 2019-07-02 | 22.7 | 0 | 4.7 | 2018-07-02 | 27.1 | 0 | 9.1 | 2017-07-02 | 16.8 | 1.2 | 0 | 2016-07-02 | 14.1 | 3.9 | 0 | 0.51 | 2.59
2025-07-02 | 22 | 0 | 4 | 2024-07-02 | 21.6 | 0 | 3.6 | 2023-07-02 | 21.2 | 0 | 3.2 | 2022-07-02 | 20.1 | 0 | 2.1 | 2021-07-02 | 17.9 | 0.1 | 0 | 2020-07-02 | 26 | 0 | 8 | 2019-07-02 | 23.3 | 0 | 5.3 | 2018-07-02 | 29.4 | 0 | 11.4 | 2017-07-02 | 18.4 | 0 | 0.4 | 2016-07-02 | 14.7 | 3.3 | 0 | 0.34 | 3.8
2025-07-02 | 23 | 0 | 5 | 2024-07-02 | 23.9 | 0 | 5.9 | 2023-07-02 | 21.4 | 0 | 3.4 | 2022-07-02 | 22 | 0 | 4 | 2021-07-02 | 18.2 | 0 | 0.2 | 2020-07-02 | 27.4 | 0 | 9.4 | 2019-07-02 | 24.1 | 0 | 6.1 | 2018-07-02 | 31.1 | 0 | 13.1 | 2017-07-02 | 19.2 | 0 | 1.2 | 2016-07-02 | 15.9 | 2.1 | 0 | 0.21 | 4.83
2025-07-02 | 24.5 | 0 | 6.5 | 2024-07-02 | 25 | 0 | 7 | 2023-07-02 | 22.6 | 0 | 4.6 | 2022-07-02 | 23.8 | 0 | 5.8 | 2021-07-02 | 19.2 | 0 | 1.2 | 2020-07-02 | 26.6 | 0 | 8.6 | 2019-07-02 | 25.9 | 0 | 7.9 | 2018-07-02 | 33.3 | 0 | 15.3 | 2017-07-02 | 19.4 | 0 | 1.4 | 2016-07-02 | 15.9 | 2.1 | 0 | 0.21 | 5.83
2025-07-02 | 26 | 0 | 8 | 2024-07-02 | 25.8 | 0 | 7.8 | 2023-07-02 | 23.4 | 0 | 5.4 | 2022-07-02 | 25.1 | 0 | 7.1 | 2021-07-02 | 21 | 0 | 3 | 2020-07-02 | 27.7 | 0 | 9.7 | 2019-07-02 | 27.1 | 0 | 9.1 | 2018-07-02 | 33.7 | 0 | 15.7 | 2017-07-02 | 20.5 | 0 | 2.5 | 2016-07-02 | 16.6 | 1.4 | 0 | 0.14 | 6.83
2025-07-02 | 27 | 0 | 9 | 2024-07-02 | 26.3 | 0 | 8.3 | 2023-07-02 | 25.3 | 0 | 7.3 | 2022-07-02 | 24.2 | 0 | 6.2 | 2021-07-02 | 21.2 | 0 | 3.2 | 2020-07-02 | 30.4 | 0 | 12.4 | 2019-07-02 | 28.1 | 0 | 10.1 | 2018-07-02 | 34.6 | 0 | 16.6 | 2017-07-02 | 21.5 | 0 | 3.5 | 2016-07-02 | 18.7 | 0 | 0.7 | 0 | 7.73
2025-07-02 | 27.7 | 0 | 9.7 | 2024-07-02 | 26.7 | 0 | 8.7 | 2023-07-02 | 25.8 | 0 | 7.8 | 2022-07-02 | 26.1 | 0 | 8.1 | 2021-07-02 | 22.2 | 0 | 4.2 | 2020-07-02 | 28.7 | 0 | 10.7 | 2019-07-02 | 28.7 | 0 | 10.7 | 2018-07-02 | 34.6 | 0 | 16.6 | 2017-07-02 | 22.1 | 0 | 4.1 | 2016-07-02 | 19.4 | 0 | 1.4 | 0 | 8.2
2025-07-02 | 28.5 | 0 | 10.5 | 2024-07-02 | 26.8 | 0 | 8.8 | 2023-07-02 | 26.3 | 0 | 8.3 | 2022-07-02 | 26.8 | 0 | 8.8 | 2021-07-02 | 22.2 | 0 | 4.2 | 2020-07-02 | 28.5 | 0 | 10.5 | 2019-07-02 | 29.2 | 0 | 11.2 | 2018-07-02 | 35.5 | 0 | 17.5 | 2017-07-02 | 22.7 | 0 | 4.7 | 2016-07-02 | 20.7 | 0 | 2.7 | 0 | 8.72
2025-07-02 | 28.9 | 0 | 10.9 | 2024-07-02 | 26.7 | 0 | 8.7 | 2023-07-02 | 26.3 | 0 | 8.3 | 2022-07-02 | 25.5 | 0 | 7.5 | 2021-07-02 | 20.3 | 0 | 2.3 | 2020-07-02 | 30.3 | 0 | 12.3 | 2019-07-02 | 29.2 | 0 | 11.2 | 2018-07-02 | 27 | 0 | 9 | 2017-07-02 | 18.4 | 0 | 0.4 | 2016-07-02 | 21.9 | 0 | 3.9 | 0 | 7.45
2025-07-02 | 27.2 | 0 | 9.2 | 2024-07-02 | 26.1 | 0 | 8.1 | 2023-07-02 | 26.4 | 0 | 8.4 | 2022-07-02 | 27.4 | 0 | 9.4 | 2021-07-02 | 21.2 | 0 | 3.2 | 2020-07-02 | 28.3 | 0 | 10.3 | 2019-07-02 | 28.8 | 0 | 10.8 | 2018-07-02 | 31.9 | 0 | 13.9 | 2017-07-02 | 19.4 | 0 | 1.4 | 2016-07-02 | 22.4 | 0 | 4.4 | 0 | 7.91
2025-07-02 | 27.4 | 0 | 9.4 | 2024-07-02 | 25.9 | 0 | 7.9 | 2023-07-02 | 26.1 | 0 | 8.1 | 2022-07-02 | 26.4 | 0 | 8.4 | 2021-07-02 | 20.8 | 0 | 2.8 | 2020-07-02 | 23.4 | 0 | 5.4 | 2019-07-02 | 28.9 | 0 | 10.9 | 2018-07-02 | 29.3 | 0 | 11.3 | 2017-07-02 | 21.1 | 0 | 3.1 | 2016-07-02 | 22 | 0 | 4 | 0 | 7.13
2025-07-02 | 24.1 | 0 | 6.1 | 2024-07-02 | 23.8 | 0 | 5.8 | 2023-07-02 | 25.7 | 0 | 7.7 | 2022-07-02 | 25.8 | 0 | 7.8 | 2021-07-02 | 19.9 | 0 | 1.9 | 2020-07-02 | 23.2 | 0 | 5.2 | 2019-07-02 | 28.2 | 0 | 10.2 | 2018-07-02 | 29.7 | 0 | 11.7 | 2017-07-02 | 22.4 | 0 | 4.4 | 2016-07-02 | 21.7 | 0 | 3.7 | 0 | 6.45
2025-07-02 | 25.5 | 0 | 7.5 | 2024-07-02 | 22.8 | 0 | 4.8 | 2023-07-02 | 24.5 | 0 | 6.5 | 2022-07-02 | 24 | 0 | 6 | 2021-07-02 | 18.2 | 0 | 0.2 | 2020-07-02 | 23.2 | 0 | 5.2 | 2019-07-02 | 26.2 | 0 | 8.2 | 2018-07-02 | 28.4 | 0 | 10.4 | 2017-07-02 | 21.6 | 0 | 3.6 | 2016-07-02 | 20.1 | 0 | 2.1 | 0 | 5.45
2025-07-02 | 25 | 0 | 7 | 2024-07-02 | 21.3 | 0 | 3.3 | 2023-07-02 | 22.6 | 0 | 4.6 | 2022-07-02 | 22.2 | 0 | 4.2 | 2021-07-02 | 17.1 | 0.9 | 0 | 2020-07-02 | 22.4 | 0 | 4.4 | 2019-07-02 | 25.4 | 0 | 7.4 | 2018-07-02 | 27.6 | 0 | 9.6 | 2017-07-02 | 20 | 0 | 2 | 2016-07-02 | 18.9 | 0 | 0.9 | 0.09 | 4.34
2025-07-02 | 23.7 | 0 | 5.7 | 2024-07-02 | 19.4 | 0 | 1.4 | 2023-07-02 | 21.4 | 0 | 3.4 | 2022-07-02 | 19.7 | 0 | 1.7 | 2021-07-02 | 16.7 | 1.3 | 0 | 2020-07-02 | 22.8 | 0 | 4.8 | 2019-07-02 | 23.3 | 0 | 5.3 | 2018-07-02 | 26.8 | 0 | 8.8 | 2017-07-02 | 16.7 | 1.3 | 0 | 2016-07-02 | 17 | 1 | 0 | 0.36 | 3.11
2025-07-02 | 22.4 | 0 | 4.4 | 2024-07-02 | 18 | 0 | 0 | 2023-07-02 | 20.4 | 0 | 2.4 | 2022-07-02 | 17.2 | 0.8 | 0 | 2021-07-02 | 16.5 | 1.5 | 0 | 2020-07-02 | 22.9 | 0 | 4.9 | 2019-07-02 | 21.4 | 0 | 3.4 | 2018-07-02 | 25.9 | 0 | 7.9 | 2017-07-02 | 15.9 | 2.1 | 0 | 2016-07-02 | 15.9 | 2.1 | 0 | 0.65 | 2.3
2025-07-02 | 20.7 | 0 | 2.7 | 2024-07-02 | 18.7 | 0 | 0.7 | 2023-07-02 | 20.2 | 0 | 2.2 | 2022-07-02 | 15.3 | 2.7 | 0 | 2021-07-02 | 15.1 | 2.9 | 0 | 2020-07-02 | 22.7 | 0 | 4.7 | 2019-07-02 | 20.9 | 0 | 2.9 | 2018-07-02 | 24.9 | 0 | 6.9 | 2017-07-02 | 15.6 | 2.4 | 0 | 2016-07-02 | 13.3 | 4.7 | 0 | 1.27 | 2.01
2025-07-03 | 19.6 | 0 | 1.6 | 2024-07-03 | 18.9 | 0 | 0.9 | 2023-07-03 | 18.4 | 0 | 0.4 | 2022-07-03 | 14.9 | 3.1 | 0 | 2021-07-03 | 15.6 | 2.4 | 0 | 2020-07-03 | 22.7 | 0 | 4.7 | 2019-07-03 | 19.4 | 0 | 1.4 | 2018-07-03 | 23 | 0 | 5 | 2017-07-03 | 14.6 | 3.4 | 0 | 2016-07-03 | 12.5 | 5.5 | 0 | 1.44 | 1.4
2025-07-03 | 19 | 0 | 1 | 2024-07-03 | 17.9 | 0.1 | 0 | 2023-07-03 | 19.1 | 0 | 1.1 | 2022-07-03 | 14.6 | 3.4 | 0 | 2021-07-03 | 15.1 | 2.9 | 0 | 2020-07-03 | 22.4 | 0 | 4.4 | 2019-07-03 | 19.4 | 0 | 1.4 | 2018-07-03 | 21.4 | 0 | 3.4 | 2017-07-03 | 14.8 | 3.2 | 0 | 2016-07-03 | 12.1 | 5.9 | 0 | 1.55 | 1.13
2025-07-03 | 18.2 | 0 | 0.2 | 2024-07-03 | 19.1 | 0 | 1.1 | 2023-07-03 | 19.4 | 0 | 1.4 | 2022-07-03 | 13.3 | 4.7 | 0 | 2021-07-03 | 14 | 4 | 0 | 2020-07-03 | 22.1 | 0 | 4.1 | 2019-07-03 | 18.4 | 0 | 0.4 | 2018-07-03 | 21.3 | 0 | 3.3 | 2017-07-03 | 14.2 | 3.8 | 0 | 2016-07-03 | 11.2 | 6.8 | 0 | 1.93 | 1.05
2025-07-03 | 17.4 | 0.6 | 0 | 2024-07-03 | 19.3 | 0 | 1.3 | 2023-07-03 | 19.2 | 0 | 1.2 | 2022-07-03 | 14.4 | 3.6 | 0 | 2021-07-03 | 13.5 | 4.5 | 0 | 2020-07-03 | 21.3 | 0 | 3.3 | 2019-07-03 | 17.2 | 0.8 | 0 | 2018-07-03 | 20.1 | 0 | 2.1 | 2017-07-03 | 13.6 | 4.4 | 0 | 2016-07-03 | 11.4 | 6.6 | 0 | 2.05 | 0.79
2025-07-03 | 17.8 | 0.2 | 0 | 2024-07-03 | 18.7 | 0 | 0.7 | 2023-07-03 | 19.1 | 0 | 1.1 | 2022-07-03 | 13.5 | 4.5 | 0 | 2021-07-03 | 14.1 | 3.9 | 0 | 2020-07-03 | 20.8 | 0 | 2.8 | 2019-07-03 | 16.2 | 1.8 | 0 | 2018-07-03 | 18.1 | 0 | 0.1 | 2017-07-03 | 13.5 | 4.5 | 0 | 2016-07-03 | 11.4 | 6.6 | 0 | 2.15 | 0.47
2025-07-03 | 17.8 | 0.2 | 0 | 2024-07-03 | 18.2 | 0 | 0.2 | 2023-07-03 | 19.2 | 0 | 1.2 | 2022-07-03 | 12.1 | 5.9 | 0 | 2021-07-03 | 12.8 | 5.2 | 0 | 2020-07-03 | 20.4 | 0 | 2.4 | 2019-07-03 | 16.2 | 1.8 | 0 | 2018-07-03 | 17.6 | 0.4 | 0 | 2017-07-03 | 13.9 | 4.1 | 0 | 2016-07-03 | 11.9 | 6.1 | 0 | 2.37 | 0.38
2025-07-03 | 18.1 | 0 | 0.1 | 2024-07-03 | 19.8 | 0 | 1.8 | 2023-07-03 | 19.4 | 0 | 1.4 | 2022-07-03 | 14.2 | 3.8 | 0 | 2021-07-03 | 14.4 | 3.6 | 0 | 2020-07-03 | 20.9 | 0 | 2.9 | 2019-07-03 | 18.9 | 0 | 0.9 | 2018-07-03 | 20.9 | 0 | 2.9 | 2017-07-03 | 14.9 | 3.1 | 0 | 2016-07-03 | 13.8 | 4.2 | 0 | 1.47 | 1
2025-07-03 | 18.1 | 0 | 0.1 | 2024-07-03 | 20.3 | 0 | 2.3 | 2023-07-03 | 20 | 0 | 2 | 2022-07-03 | 17.8 | 0.2 | 0 | 2021-07-03 | 15.2 | 2.8 | 0 | 2020-07-03 | 22.4 | 0 | 4.4 | 2019-07-03 | 21.6 | 0 | 3.6 | 2018-07-03 | 22.4 | 0 | 4.4 | 2017-07-03 | 15.9 | 2.1 | 0 | 2016-07-03 | 16.6 | 1.4 | 0 | 0.65 | 1.68
2025-07-03 | 18 | 0 | 0 | 2024-07-03 | 20.8 | 0 | 2.8 | 2023-07-03 | 20.6 | 0 | 2.6 | 2022-07-03 | 19.1 | 0 | 1.1 | 2021-07-03 | 16.3 | 1.7 | 0 | 2020-07-03 | 22.9 | 0 | 4.9 | 2019-07-03 | 23.6 | 0 | 5.6 | 2018-07-03 | 24 | 0 | 6 | 2017-07-03 | 16.3 | 1.7 | 0 | 2016-07-03 | 19.4 | 0 | 1.4 | 0.34 | 2.44
2025-07-03 | 18.2 | 0 | 0.2 | 2024-07-03 | 23.1 | 0 | 5.1 | 2023-07-03 | 21.4 | 0 | 3.4 | 2022-07-03 | 19.6 | 0 | 1.6 | 2021-07-03 | 17.6 | 0.4 | 0 | 2020-07-03 | 25.1 | 0 | 7.1 | 2019-07-03 | 25.5 | 0 | 7.5 | 2018-07-03 | 25.7 | 0 | 7.7 | 2017-07-03 | 17.3 | 0.7 | 0 | 2016-07-03 | 21 | 0 | 3 | 0.11 | 3.56
2025-07-03 | 18.5 | 0 | 0.5 | 2024-07-03 | 24.8 | 0 | 6.8 | 2023-07-03 | 24.1 | 0 | 6.1 | 2022-07-03 | 20.8 | 0 | 2.8 | 2021-07-03 | 17.8 | 0.2 | 0 | 2020-07-03 | 26.4 | 0 | 8.4 | 2019-07-03 | 27.4 | 0 | 9.4 | 2018-07-03 | 27.2 | 0 | 9.2 | 2017-07-03 | 19 | 0 | 1 | 2016-07-03 | 23.9 | 0 | 5.9 | 0.02 | 5.01
2025-07-03 | 20 | 0 | 2 | 2024-07-03 | 26.3 | 0 | 8.3 | 2023-07-03 | 25.4 | 0 | 7.4 | 2022-07-03 | 21.4 | 0 | 3.4 | 2021-07-03 | 18.7 | 0 | 0.7 | 2020-07-03 | 27.3 | 0 | 9.3 | 2019-07-03 | 28.2 | 0 | 10.2 | 2018-07-03 | 29 | 0 | 11 | 2017-07-03 | 21 | 0 | 3 | 2016-07-03 | 25 | 0 | 7 | 0 | 6.23
2025-07-03 | 22.9 | 0 | 4.9 | 2024-07-03 | 26.2 | 0 | 8.2 | 2023-07-03 | 26.2 | 0 | 8.2 | 2022-07-03 | 22.5 | 0 | 4.5 | 2021-07-03 | 19.1 | 0 | 1.1 | 2020-07-03 | 27.9 | 0 | 9.9 | 2019-07-03 | 28.4 | 0 | 10.4 | 2018-07-03 | 29.8 | 0 | 11.8 | 2017-07-03 | 22.6 | 0 | 4.6 | 2016-07-03 | 26.2 | 0 | 8.2 | 0 | 7.18
2025-07-03 | 23.3 | 0 | 5.3 | 2024-07-03 | 26.9 | 0 | 8.9 | 2023-07-03 | 27.7 | 0 | 9.7 | 2022-07-03 | 23.2 | 0 | 5.2 | 2021-07-03 | 21.2 | 0 | 3.2 | 2020-07-03 | 29.7 | 0 | 11.7 | 2019-07-03 | 30 | 0 | 12 | 2018-07-03 | 31 | 0 | 13 | 2017-07-03 | 23 | 0 | 5 | 2016-07-03 | 25.2 | 0 | 7.2 | 0 | 8.12
2025-07-03 | 18.6 | 0 | 0.6 | 2024-07-03 | 27.4 | 0 | 9.4 | 2023-07-03 | 27.7 | 0 | 9.7 | 2022-07-03 | 23.8 | 0 | 5.8 | 2021-07-03 | 20.8 | 0 | 2.8 | 2020-07-03 | 29.6 | 0 | 11.6 | 2019-07-03 | 28.6 | 0 | 10.6 | 2018-07-03 | 31.8 | 0 | 13.8 | 2017-07-03 | 24.3 | 0 | 6.3 | 2016-07-03 | 27 | 0 | 9 | 0 | 7.96
2025-07-03 | 21.8 | 0 | 3.8 | 2024-07-03 | 27.4 | 0 | 9.4 | 2023-07-03 | 27.6 | 0 | 9.6 | 2022-07-03 | 24.7 | 0 | 6.7 | 2021-07-03 | 20.6 | 0 | 2.6 | 2020-07-03 | 28.7 | 0 | 10.7 | 2019-07-03 | 29 | 0 | 11 | 2018-07-03 | 33 | 0 | 15 | 2017-07-03 | 24.4 | 0 | 6.4 | 2016-07-03 | 25.5 | 0 | 7.5 | 0 | 8.27
2025-07-03 | 23.8 | 0 | 5.8 | 2024-07-03 | 27.1 | 0 | 9.1 | 2023-07-03 | 27.5 | 0 | 9.5 | 2022-07-03 | 24.6 | 0 | 6.6 | 2021-07-03 | 21.1 | 0 | 3.1 | 2020-07-03 | 30.1 | 0 | 12.1 | 2019-07-03 | 30.5 | 0 | 12.5 | 2018-07-03 | 32.6 | 0 | 14.6 | 2017-07-03 | 24.7 | 0 | 6.7 | 2016-07-03 | 26.7 | 0 | 8.7 | 0 | 8.87
2025-07-03 | 24.1 | 0 | 6.1 | 2024-07-03 | 26.6 | 0 | 8.6 | 2023-07-03 | 27.2 | 0 | 9.2 | 2022-07-03 | 24.6 | 0 | 6.6 | 2021-07-03 | 20.7 | 0 | 2.7 | 2020-07-03 | 30.5 | 0 | 12.5 | 2019-07-03 | 30.2 | 0 | 12.2 | 2018-07-03 | 32.4 | 0 | 14.4 | 2017-07-03 | 24.7 | 0 | 6.7 | 2016-07-03 | 26.6 | 0 | 8.6 | 0 | 8.76
2025-07-03 | 22.7 | 0 | 4.7 | 2024-07-03 | 23.5 | 0 | 5.5 | 2023-07-03 | 26.6 | 0 | 8.6 | 2022-07-03 | 23.9 | 0 | 5.9 | 2021-07-03 | 20.2 | 0 | 2.2 | 2020-07-03 | 29.6 | 0 | 11.6 | 2019-07-03 | 28.9 | 0 | 10.9 | 2018-07-03 | 31.6 | 0 | 13.6 | 2017-07-03 | 24.1 | 0 | 6.1 | 2016-07-03 | 26.6 | 0 | 8.6 | 0 | 7.77
2025-07-03 | 21 | 0 | 3 | 2024-07-03 | 21.6 | 0 | 3.6 | 2023-07-03 | 25.8 | 0 | 7.8 | 2022-07-03 | 22.3 | 0 | 4.3 | 2021-07-03 | 19.1 | 0 | 1.1 | 2020-07-03 | 27.3 | 0 | 9.3 | 2019-07-03 | 26.4 | 0 | 8.4 | 2018-07-03 | 30.1 | 0 | 12.1 | 2017-07-03 | 21.6 | 0 | 3.6 | 2016-07-03 | 24.1 | 0 | 6.1 | 0 | 5.93
2025-07-03 | 19.3 | 0 | 1.3 | 2024-07-03 | 21.9 | 0 | 3.9 | 2023-07-03 | 25.7 | 0 | 7.7 | 2022-07-03 | 21 | 0 | 3 | 2021-07-03 | 17.3 | 0.7 | 0 | 2020-07-03 | 25.2 | 0 | 7.2 | 2019-07-03 | 25.7 | 0 | 7.7 | 2018-07-03 | 27.9 | 0 | 9.9 | 2017-07-03 | 20 | 0 | 2 | 2016-07-03 | 20.8 | 0 | 2.8 | 0.07 | 4.55
2025-07-03 | 18 | 0 | 0 | 2024-07-03 | 22.2 | 0 | 4.2 | 2023-07-03 | 23.2 | 0 | 5.2 | 2022-07-03 | 20.1 | 0 | 2.1 | 2021-07-03 | 16 | 2 | 0 | 2020-07-03 | 24 | 0 | 6 | 2019-07-03 | 24.5 | 0 | 6.5 | 2018-07-03 | 24.8 | 0 | 6.8 | 2017-07-03 | 18.8 | 0 | 0.8 | 2016-07-03 | 18.6 | 0 | 0.6 | 0.2 | 3.22
2025-07-03 | 16.9 | 1.1 | 0 | 2024-07-03 | 22.1 | 0 | 4.1 | 2023-07-03 | 20.6 | 0 | 2.6 | 2022-07-03 | 18.8 | 0 | 0.8 | 2021-07-03 | 15.3 | 2.7 | 0 | 2020-07-03 | 21.5 | 0 | 3.5 | 2019-07-03 | 21.8 | 0 | 3.8 | 2018-07-03 | 22.3 | 0 | 4.3 | 2017-07-03 | 17.7 | 0.3 | 0 | 2016-07-03 | 18.2 | 0 | 0.2 | 0.41 | 1.93
2025-07-03 | 14.8 | 3.2 | 0 | 2024-07-03 | 21.7 | 0 | 3.7 | 2023-07-03 | 20.1 | 0 | 2.1 | 2022-07-03 | 16.2 | 1.8 | 0 | 2021-07-03 | 14.2 | 3.8 | 0 | 2020-07-03 | 20.1 | 0 | 2.1 | 2019-07-03 | 21.8 | 0 | 3.8 | 2018-07-03 | 19.7 | 0 | 1.7 | 2017-07-03 | 15.6 | 2.4 | 0 | 2016-07-03 | 18.4 | 0 | 0.4 | 1.12 | 1.38
2025-07-04 | 14.3 | 3.7 | 0 | 2024-07-04 | 21 | 0 | 3 | 2023-07-04 | 20.6 | 0 | 2.6 | 2022-07-04 | 18.1 | 0 | 0.1 | 2021-07-04 | 14.2 | 3.8 | 0 | 2020-07-04 | 21.5 | 0 | 3.5 | 2019-07-04 | 21.5 | 0 | 3.5 | 2018-07-04 | 21.1 | 0 | 3.1 | 2017-07-04 | 15.5 | 2.5 | 0 | 2016-07-04 | 16.5 | 1.5 | 0 | 1.15 | 1.58
2025-07-04 | 12.5 | 5.5 | 0 | 2024-07-04 | 20.7 | 0 | 2.7 | 2023-07-04 | 19.3 | 0 | 1.3 | 2022-07-04 | 17 | 1 | 0 | 2021-07-04 | 12.7 | 5.3 | 0 | 2020-07-04 | 20.7 | 0 | 2.7 | 2019-07-04 | 20.4 | 0 | 2.4 | 2018-07-04 | 22 | 0 | 4 | 2017-07-04 | 13.9 | 4.1 | 0 | 2016-07-04 | 15.3 | 2.7 | 0 | 1.86 | 1.31
2025-07-04 | 11.3 | 6.7 | 0 | 2024-07-04 | 19.9 | 0 | 1.9 | 2023-07-04 | 19.3 | 0 | 1.3 | 2022-07-04 | 13.8 | 4.2 | 0 | 2021-07-04 | 13.8 | 4.2 | 0 | 2020-07-04 | 20.7 | 0 | 2.7 | 2019-07-04 | 17.8 | 0.2 | 0 | 2018-07-04 | 20.1 | 0 | 2.1 | 2017-07-04 | 12.5 | 5.5 | 0 | 2016-07-04 | 15.2 | 2.8 | 0 | 2.36 | 0.8
2025-07-04 | 11.4 | 6.6 | 0 | 2024-07-04 | 19 | 0 | 1 | 2023-07-04 | 18.2 | 0 | 0.2 | 2022-07-04 | 14.5 | 3.5 | 0 | 2021-07-04 | 12.4 | 5.6 | 0 | 2020-07-04 | 20.2 | 0 | 2.2 | 2019-07-04 | 17.4 | 0.6 | 0 | 2018-07-04 | 19.8 | 0 | 1.8 | 2017-07-04 | 12.7 | 5.3 | 0 | 2016-07-04 | 14.8 | 3.2 | 0 | 2.48 | 0.52
2025-07-04 | 11.1 | 6.9 | 0 | 2024-07-04 | 18.4 | 0 | 0.4 | 2023-07-04 | 18.6 | 0 | 0.6 | 2022-07-04 | 14.2 | 3.8 | 0 | 2021-07-04 | 12.8 | 5.2 | 0 | 2020-07-04 | 19.2 | 0 | 1.2 | 2019-07-04 | 17.3 | 0.7 | 0 | 2018-07-04 | 16.6 | 1.4 | 0 | 2017-07-04 | 9.9 | 8.1 | 0 | 2016-07-04 | 13.7 | 4.3 | 0 | 3.04 | 0.22
2025-07-04 | 12.1 | 5.9 | 0 | 2024-07-04 | 18.7 | 0 | 0.7 | 2023-07-04 | 18.8 | 0 | 0.8 | 2022-07-04 | 13.9 | 4.1 | 0 | 2021-07-04 | 12.3 | 5.7 | 0 | 2020-07-04 | 19 | 0 | 1 | 2019-07-04 | 18 | 0 | 0 | 2018-07-04 | 17.9 | 0.1 | 0 | 2017-07-04 | 12.2 | 5.8 | 0 | 2016-07-04 | 13.8 | 4.2 | 0 | 2.58 | 0.25
2025-07-04 | 13.9 | 4.1 | 0 | 2024-07-04 | 19.3 | 0 | 1.3 | 2023-07-04 | 21 | 0 | 3 | 2022-07-04 | 16.4 | 1.6 | 0 | 2021-07-04 | 14.5 | 3.5 | 0 | 2020-07-04 | 20.2 | 0 | 2.2 | 2019-07-04 | 20.6 | 0 | 2.6 | 2018-07-04 | 21.7 | 0 | 3.7 | 2017-07-04 | 14.6 | 3.4 | 0 | 2016-07-04 | 16.2 | 1.8 | 0 | 1.44 | 1.28
2025-07-04 | 16.1 | 1.9 | 0 | 2024-07-04 | 20.6 | 0 | 2.6 | 2023-07-04 | 23.5 | 0 | 5.5 | 2022-07-04 | 18.1 | 0 | 0.1 | 2021-07-04 | 16.3 | 1.7 | 0 | 2020-07-04 | 21.6 | 0 | 3.6 | 2019-07-04 | 21.7 | 0 | 3.7 | 2018-07-04 | 24.5 | 0 | 6.5 | 2017-07-04 | 17.1 | 0.9 | 0 | 2016-07-04 | 18.8 | 0 | 0.8 | 0.45 | 2.28
2025-07-04 | 16.5 | 1.5 | 0 | 2024-07-04 | 22.3 | 0 | 4.3 | 2023-07-04 | 25 | 0 | 7 | 2022-07-04 | 19.7 | 0 | 1.7 | 2021-07-04 | 17.9 | 0.1 | 0 | 2020-07-04 | 22.9 | 0 | 4.9 | 2019-07-04 | 23.7 | 0 | 5.7 | 2018-07-04 | 27.2 | 0 | 9.2 | 2017-07-04 | 20 | 0 | 2 | 2016-07-04 | 21.5 | 0 | 3.5 | 0.16 | 3.83
2025-07-04 | 17.7 | 0.3 | 0 | 2024-07-04 | 24.8 | 0 | 6.8 | 2023-07-04 | 27.1 | 0 | 9.1 | 2022-07-04 | 21.4 | 0 | 3.4 | 2021-07-04 | 19.4 | 0 | 1.4 | 2020-07-04 | 24.6 | 0 | 6.6 | 2019-07-04 | 25.8 | 0 | 7.8 | 2018-07-04 | 29.9 | 0 | 11.9 | 2017-07-04 | 21.7 | 0 | 3.7 | 2016-07-04 | 22.9 | 0 | 4.9 | 0.03 | 5.56
2025-07-04 | 19.1 | 0 | 1.1 | 2024-07-04 | 25.9 | 0 | 7.9 | 2023-07-04 | 28.2 | 0 | 10.2 | 2022-07-04 | 23.3 | 0 | 5.3 | 2021-07-04 | 20.4 | 0 | 2.4 | 2020-07-04 | 26.6 | 0 | 8.6 | 2019-07-04 | 27.3 | 0 | 9.3 | 2018-07-04 | 31.5 | 0 | 13.5 | 2017-07-04 | 23.3 | 0 | 5.3 | 2016-07-04 | 24.6 | 0 | 6.6 | 0 | 7.02
2025-07-04 | 20.2 | 0 | 2.2 | 2024-07-04 | 27.2 | 0 | 9.2 | 2023-07-04 | 29.5 | 0 | 11.5 | 2022-07-04 | 22.5 | 0 | 4.5 | 2021-07-04 | 21.1 | 0 | 3.1 | 2020-07-04 | 27.4 | 0 | 9.4 | 2019-07-04 | 28.9 | 0 | 10.9 | 2018-07-04 | 33.7 | 0 | 15.7 | 2017-07-04 | 24.2 | 0 | 6.2 | 2016-07-04 | 25.5 | 0 | 7.5 | 0 | 8.02
2025-07-04 | 21.6 | 0 | 3.6 | 2024-07-04 | 28 | 0 | 10 | 2023-07-04 | 29.7 | 0 | 11.7 | 2022-07-04 | 25.1 | 0 | 7.1 | 2021-07-04 | 21 | 0 | 3 | 2020-07-04 | 28.5 | 0 | 10.5 | 2019-07-04 | 30.1 | 0 | 12.1 | 2018-07-04 | 33.5 | 0 | 15.5 | 2017-07-04 | 25.3 | 0 | 7.3 | 2016-07-04 | 27.3 | 0 | 9.3 | 0 | 9.01
2025-07-04 | 23 | 0 | 5 | 2024-07-04 | 29 | 0 | 11 | 2023-07-04 | 29.5 | 0 | 11.5 | 2022-07-04 | 25.4 | 0 | 7.4 | 2021-07-04 | 22.9 | 0 | 4.9 | 2020-07-04 | 28.9 | 0 | 10.9 | 2019-07-04 | 30.9 | 0 | 12.9 | 2018-07-04 | 34.2 | 0 | 16.2 | 2017-07-04 | 25.5 | 0 | 7.5 | 2016-07-04 | 28.1 | 0 | 10.1 | 0 | 9.74
2025-07-04 | 23.6 | 0 | 5.6 | 2024-07-04 | 29.4 | 0 | 11.4 | 2023-07-04 | 30.7 | 0 | 12.7 | 2022-07-04 | 26.5 | 0 | 8.5 | 2021-07-04 | 23.5 | 0 | 5.5 | 2020-07-04 | 29.4 | 0 | 11.4 | 2019-07-04 | 31.8 | 0 | 13.8 | 2018-07-04 | 33.8 | 0 | 15.8 | 2017-07-04 | 25.6 | 0 | 7.6 | 2016-07-04 | 28.9 | 0 | 10.9 | 0 | 10.32
2025-07-04 | 24.4 | 0 | 6.4 | 2024-07-04 | 28 | 0 | 10 | 2023-07-04 | 26.6 | 0 | 8.6 | 2022-07-04 | 26.4 | 0 | 8.4 | 2021-07-04 | 24.3 | 0 | 6.3 | 2020-07-04 | 29.9 | 0 | 11.9 | 2019-07-04 | 31.9 | 0 | 13.9 | 2018-07-04 | 34.2 | 0 | 16.2 | 2017-07-04 | 26 | 0 | 8 | 2016-07-04 | 29.3 | 0 | 11.3 | 0 | 10.1
2025-07-04 | 24.1 | 0 | 6.1 | 2024-07-04 | 28.3 | 0 | 10.3 | 2023-07-04 | 25.8 | 0 | 7.8 | 2022-07-04 | 25.5 | 0 | 7.5 | 2021-07-04 | 22.9 | 0 | 4.9 | 2020-07-04 | 29.4 | 0 | 11.4 | 2019-07-04 | 31.6 | 0 | 13.6 | 2018-07-04 | 34.2 | 0 | 16.2 | 2017-07-04 | 24.8 | 0 | 6.8 | 2016-07-04 | 29.9 | 0 | 11.9 | 0 | 9.65
2025-07-04 | 24.3 | 0 | 6.3 | 2024-07-04 | 29.3 | 0 | 11.3 | 2023-07-04 | 26.8 | 0 | 8.8 | 2022-07-04 | 24.9 | 0 | 6.9 | 2021-07-04 | 24.5 | 0 | 6.5 | 2020-07-04 | 28 | 0 | 10 | 2019-07-04 | 31.2 | 0 | 13.2 | 2018-07-04 | 33.5 | 0 | 15.5 | 2017-07-04 | 25.6 | 0 | 7.6 | 2016-07-04 | 28.8 | 0 | 10.8 | 0 | 9.69
2025-07-04 | 23.6 | 0 | 5.6 | 2024-07-04 | 27.6 | 0 | 9.6 | 2023-07-04 | 27.6 | 0 | 9.6 | 2022-07-04 | 23.9 | 0 | 5.9 | 2021-07-04 | 23.6 | 0 | 5.6 | 2020-07-04 | 27.2 | 0 | 9.2 | 2019-07-04 | 29.7 | 0 | 11.7 | 2018-07-04 | 33.1 | 0 | 15.1 | 2017-07-04 | 25.2 | 0 | 7.2 | 2016-07-04 | 27.5 | 0 | 9.5 | 0 | 8.9
2025-07-04 | 21.9 | 0 | 3.9 | 2024-07-04 | 26.9 | 0 | 8.9 | 2023-07-04 | 25.8 | 0 | 7.8 | 2022-07-04 | 23 | 0 | 5 | 2021-07-04 | 21.4 | 0 | 3.4 | 2020-07-04 | 25.6 | 0 | 7.6 | 2019-07-04 | 27.2 | 0 | 9.2 | 2018-07-04 | 30.2 | 0 | 12.2 | 2017-07-04 | 23.9 | 0 | 5.9 | 2016-07-04 | 25.5 | 0 | 7.5 | 0 | 7.14
2025-07-04 | 20.1 | 0 | 2.1 | 2024-07-04 | 25.3 | 0 | 7.3 | 2023-07-04 | 23.4 | 0 | 5.4 | 2022-07-04 | 20.1 | 0 | 2.1 | 2021-07-04 | 19.4 | 0 | 1.4 | 2020-07-04 | 23.8 | 0 | 5.8 | 2019-07-04 | 25.5 | 0 | 7.5 | 2018-07-04 | 28.5 | 0 | 10.5 | 2017-07-04 | 21 | 0 | 3 | 2016-07-04 | 23 | 0 | 5 | 0 | 5.01
2025-07-04 | 19.6 | 0 | 1.6 | 2024-07-04 | 23.6 | 0 | 5.6 | 2023-07-04 | 22 | 0 | 4 | 2022-07-04 | 19.4 | 0 | 1.4 | 2021-07-04 | 18.4 | 0 | 0.4 | 2020-07-04 | 22.4 | 0 | 4.4 | 2019-07-04 | 24.4 | 0 | 6.4 | 2018-07-04 | 25.1 | 0 | 7.1 | 2017-07-04 | 18.8 | 0 | 0.8 | 2016-07-04 | 20.7 | 0 | 2.7 | 0 | 3.44
2025-07-04 | 17.1 | 0.9 | 0 | 2024-07-04 | 21.9 | 0 | 3.9 | 2023-07-04 | 21.7 | 0 | 3.7 | 2022-07-04 | 18.9 | 0 | 0.9 | 2021-07-04 | 16 | 2 | 0 | 2020-07-04 | 18.8 | 0 | 0.8 | 2019-07-04 | 21.9 | 0 | 3.9 | 2018-07-04 | 25.5 | 0 | 7.5 | 2017-07-04 | 17.1 | 0.9 | 0 | 2016-07-04 | 20 | 0 | 2 | 0.38 | 2.27
2025-07-04 | 16.1 | 1.9 | 0 | 2024-07-04 | 21.6 | 0 | 3.6 | 2023-07-04 | 20.5 | 0 | 2.5 | 2022-07-04 | 17.7 | 0.3 | 0 | 2021-07-04 | 15.2 | 2.8 | 0 | 2020-07-04 | 19.9 | 0 | 1.9 | 2019-07-04 | 22.1 | 0 | 4.1 | 2018-07-04 | 25 | 0 | 7 | 2017-07-04 | 14.6 | 3.4 | 0 | 2016-07-04 | 18.2 | 0 | 0.2 | 0.84 | 1.93
2025-07-05 | 15.9 | 2.1 | 0 | 2024-07-05 | 21.3 | 0 | 3.3 | 2023-07-05 | 20.5 | 0 | 2.5 | 2022-07-05 | 17.9 | 0.1 | 0 | 2021-07-05 | 14.6 | 3.4 | 0 | 2020-07-05 | 18.2 | 0 | 0.2 | 2019-07-05 | 20.9 | 0 | 2.9 | 2018-07-05 | 24.5 | 0 | 6.5 | 2017-07-05 | 14.6 | 3.4 | 0 | 2016-07-05 | 17.1 | 0.9 | 0 | 0.99 | 1.54
2025-07-05 | 15.2 | 2.8 | 0 | 2024-07-05 | 20.8 | 0 | 2.8 | 2023-07-05 | 20.2 | 0 | 2.2 | 2022-07-05 | 18.1 | 0 | 0.1 | 2021-07-05 | 15.6 | 2.4 | 0 | 2020-07-05 | 16.7 | 1.3 | 0 | 2019-07-05 | 20.9 | 0 | 2.9 | 2018-07-05 | 23.2 | 0 | 5.2 | 2017-07-05 | 14.4 | 3.6 | 0 | 2016-07-05 | 15.5 | 2.5 | 0 | 1.26 | 1.32
2025-07-05 | 14.2 | 3.8 | 0 | 2024-07-05 | 20.4 | 0 | 2.4 | 2023-07-05 | 19.6 | 0 | 1.6 | 2022-07-05 | 17 | 1 | 0 | 2021-07-05 | 15.5 | 2.5 | 0 | 2020-07-05 | 14 | 4 | 0 | 2019-07-05 | 21.2 | 0 | 3.2 | 2018-07-05 | 22 | 0 | 4 | 2017-07-05 | 13.8 | 4.2 | 0 | 2016-07-05 | 13.6 | 4.4 | 0 | 1.99 | 1.12
2025-07-05 | 14.2 | 3.8 | 0 | 2024-07-05 | 20.1 | 0 | 2.1 | 2023-07-05 | 18.9 | 0 | 0.9 | 2022-07-05 | 17.1 | 0.9 | 0 | 2021-07-05 | 14.9 | 3.1 | 0 | 2020-07-05 | 16.2 | 1.8 | 0 | 2019-07-05 | 20.1 | 0 | 2.1 | 2018-07-05 | 21.6 | 0 | 3.6 | 2017-07-05 | 13.2 | 4.8 | 0 | 2016-07-05 | 14.1 | 3.9 | 0 | 1.83 | 0.87
2025-07-05 | 14.1 | 3.9 | 0 | 2024-07-05 | 19.9 | 0 | 1.9 | 2023-07-05 | 19.2 | 0 | 1.2 | 2022-07-05 | 16.5 | 1.5 | 0 | 2021-07-05 | 12.6 | 5.4 | 0 | 2020-07-05 | 17.5 | 0.5 | 0 | 2019-07-05 | 20.7 | 0 | 2.7 | 2018-07-05 | 21.4 | 0 | 3.4 | 2017-07-05 | 11.7 | 6.3 | 0 | 2016-07-05 | 13.7 | 4.3 | 0 | 2.19 | 0.92
2025-07-05 | 13.8 | 4.2 | 0 | 2024-07-05 | 19.7 | 0 | 1.7 | 2023-07-05 | 18.4 | 0 | 0.4 | 2022-07-05 | 17 | 1 | 0 | 2021-07-05 | 13.9 | 4.1 | 0 | 2020-07-05 | 15.6 | 2.4 | 0 | 2019-07-05 | 21 | 0 | 3 | 2018-07-05 | 21.2 | 0 | 3.2 | 2017-07-05 | 13.3 | 4.7 | 0 | 2016-07-05 | 13.6 | 4.4 | 0 | 2.08 | 0.83
2025-07-05 | 15.7 | 2.3 | 0 | 2024-07-05 | 20.5 | 0 | 2.5 | 2023-07-05 | 20.3 | 0 | 2.3 | 2022-07-05 | 17.2 | 0.8 | 0 | 2021-07-05 | 15.5 | 2.5 | 0 | 2020-07-05 | 16.6 | 1.4 | 0 | 2019-07-05 | 22.3 | 0 | 4.3 | 2018-07-05 | 23.5 | 0 | 5.5 | 2017-07-05 | 16.2 | 1.8 | 0 | 2016-07-05 | 17.4 | 0.6 | 0 | 0.94 | 1.46
2025-07-05 | 17.6 | 0.4 | 0 | 2024-07-05 | 22 | 0 | 4 | 2023-07-05 | 23.1 | 0 | 5.1 | 2022-07-05 | 17.5 | 0.5 | 0 | 2021-07-05 | 17.6 | 0.4 | 0 | 2020-07-05 | 19.8 | 0 | 1.8 | 2019-07-05 | 24.4 | 0 | 6.4 | 2018-07-05 | 25.5 | 0 | 7.5 | 2017-07-05 | 19.1 | 0 | 1.1 | 2016-07-05 | 20.1 | 0 | 2.1 | 0.13 | 2.8
2025-07-05 | 20.1 | 0 | 2.1 | 2024-07-05 | 23.5 | 0 | 5.5 | 2023-07-05 | 25.6 | 0 | 7.6 | 2022-07-05 | 17.7 | 0.3 | 0 | 2021-07-05 | 19.5 | 0 | 1.5 | 2020-07-05 | 22.4 | 0 | 4.4 | 2019-07-05 | 25.7 | 0 | 7.7 | 2018-07-05 | 26.5 | 0 | 8.5 | 2017-07-05 | 22.1 | 0 | 4.1 | 2016-07-05 | 22.5 | 0 | 4.5 | 0.03 | 4.59
2025-07-05 | 22.7 | 0 | 4.7 | 2024-07-05 | 24.6 | 0 | 6.6 | 2023-07-05 | 27.2 | 0 | 9.2 | 2022-07-05 | 18.8 | 0 | 0.8 | 2021-07-05 | 21.7 | 0 | 3.7 | 2020-07-05 | 24.8 | 0 | 6.8 | 2019-07-05 | 26.8 | 0 | 8.8 | 2018-07-05 | 28.4 | 0 | 10.4 | 2017-07-05 | 24.2 | 0 | 6.2 | 2016-07-05 | 24.9 | 0 | 6.9 | 0 | 6.41
2025-07-05 | 24.6 | 0 | 6.6 | 2024-07-05 | 25.8 | 0 | 7.8 | 2023-07-05 | 28.8 | 0 | 10.8 | 2022-07-05 | 19.6 | 0 | 1.6 | 2021-07-05 | 23.6 | 0 | 5.6 | 2020-07-05 | 26.2 | 0 | 8.2 | 2019-07-05 | 28.6 | 0 | 10.6 | 2018-07-05 | 30.2 | 0 | 12.2 | 2017-07-05 | 25.5 | 0 | 7.5 | 2016-07-05 | 27.1 | 0 | 9.1 | 0 | 8
2025-07-05 | 24.3 | 0 | 6.3 | 2024-07-05 | 26.6 | 0 | 8.6 | 2023-07-05 | 29.9 | 0 | 11.9 | 2022-07-05 | 20 | 0 | 2 | 2021-07-05 | 24.7 | 0 | 6.7 | 2020-07-05 | 26.7 | 0 | 8.7 | 2019-07-05 | 29.4 | 0 | 11.4 | 2018-07-05 | 31.5 | 0 | 13.5 | 2017-07-05 | 25.8 | 0 | 7.8 | 2016-07-05 | 28.3 | 0 | 10.3 | 0 | 8.72
2025-07-05 | 24.6 | 0 | 6.6 | 2024-07-05 | 27 | 0 | 9 | 2023-07-05 | 31.4 | 0 | 13.4 | 2022-07-05 | 20.1 | 0 | 2.1 | 2021-07-05 | 25.7 | 0 | 7.7 | 2020-07-05 | 28.4 | 0 | 10.4 | 2019-07-05 | 30 | 0 | 12 | 2018-07-05 | 32.4 | 0 | 14.4 | 2017-07-05 | 26.3 | 0 | 8.3 | 2016-07-05 | 29.4 | 0 | 11.4 | 0 | 9.53
2025-07-05 | 26.8 | 0 | 8.8 | 2024-07-05 | 27.7 | 0 | 9.7 | 2023-07-05 | 31.9 | 0 | 13.9 | 2022-07-05 | 20.3 | 0 | 2.3 | 2021-07-05 | 26 | 0 | 8 | 2020-07-05 | 28.4 | 0 | 10.4 | 2019-07-05 | 30.5 | 0 | 12.5 | 2018-07-05 | 34.5 | 0 | 16.5 | 2017-07-05 | 26.6 | 0 | 8.6 | 2016-07-05 | 29.9 | 0 | 11.9 | 0 | 10.26
2025-07-05 | 27.6 | 0 | 9.6 | 2024-07-05 | 28.4 | 0 | 10.4 | 2023-07-05 | 32.8 | 0 | 14.8 | 2022-07-05 | 20 | 0 | 2 | 2021-07-05 | 26 | 0 | 8 | 2020-07-05 | 28.1 | 0 | 10.1 | 2019-07-05 | 31.2 | 0 | 13.2 | 2018-07-05 | 32.8 | 0 | 14.8 | 2017-07-05 | 26.9 | 0 | 8.9 | 2016-07-05 | 31.2 | 0 | 13.2 | 0 | 10.5
2025-07-05 | 28.2 | 0 | 10.2 | 2024-07-05 | 29.2 | 0 | 11.2 | 2023-07-05 | 32.5 | 0 | 14.5 | 2022-07-05 | 19.7 | 0 | 1.7 | 2021-07-05 | 26.7 | 0 | 8.7 | 2020-07-05 | 29.9 | 0 | 11.9 | 2019-07-05 | 32 | 0 | 14 | 2018-07-05 | 34 | 0 | 16 | 2017-07-05 | 27.5 | 0 | 9.5 | 2016-07-05 | 31.5 | 0 | 13.5 | 0 | 11.12
2025-07-05 | 28.6 | 0 | 10.6 | 2024-07-05 | 28.3 | 0 | 10.3 | 2023-07-05 | 32.8 | 0 | 14.8 | 2022-07-05 | 20 | 0 | 2 | 2021-07-05 | 26.5 | 0 | 8.5 | 2020-07-05 | 28.2 | 0 | 10.2 | 2019-07-05 | 31.5 | 0 | 13.5 | 2018-07-05 | 32.9 | 0 | 14.9 | 2017-07-05 | 27.6 | 0 | 9.6 | 2016-07-05 | 31.9 | 0 | 13.9 | 0 | 10.83
2025-07-05 | 28.1 | 0 | 10.1 | 2024-07-05 | 28.3 | 0 | 10.3 | 2023-07-05 | 32.3 | 0 | 14.3 | 2022-07-05 | 19.6 | 0 | 1.6 | 2021-07-05 | 26.8 | 0 | 8.8 | 2020-07-05 | 28.9 | 0 | 10.9 | 2019-07-05 | 29.2 | 0 | 11.2 | 2018-07-05 | 32.9 | 0 | 14.9 | 2017-07-05 | 26.9 | 0 | 8.9 | 2016-07-05 | 31.3 | 0 | 13.3 | 0 | 10.43
2025-07-05 | 26.8 | 0 | 8.8 | 2024-07-05 | 27 | 0 | 9 | 2023-07-05 | 31.4 | 0 | 13.4 | 2022-07-05 | 18.3 | 0 | 0.3 | 2021-07-05 | 26.4 | 0 | 8.4 | 2020-07-05 | 27.2 | 0 | 9.2 | 2019-07-05 | 23.6 | 0 | 5.6 | 2018-07-05 | 31.1 | 0 | 13.1 | 2017-07-05 | 26.3 | 0 | 8.3 | 2016-07-05 | 30.4 | 0 | 12.4 | 0 | 8.85
2025-07-05 | 26.2 | 0 | 8.2 | 2024-07-05 | 26.3 | 0 | 8.3 | 2023-07-05 | 29.2 | 0 | 11.2 | 2022-07-05 | 17.6 | 0.4 | 0 | 2021-07-05 | 24.7 | 0 | 6.7 | 2020-07-05 | 26.1 | 0 | 8.1 | 2019-07-05 | 24.3 | 0 | 6.3 | 2018-07-05 | 29.9 | 0 | 11.9 | 2017-07-05 | 24.2 | 0 | 6.2 | 2016-07-05 | 28.5 | 0 | 10.5 | 0.04 | 7.74
2025-07-05 | 24.6 | 0 | 6.6 | 2024-07-05 | 24.9 | 0 | 6.9 | 2023-07-05 | 27.7 | 0 | 9.7 | 2022-07-05 | 17.3 | 0.7 | 0 | 2021-07-05 | 23.9 | 0 | 5.9 | 2020-07-05 | 24.3 | 0 | 6.3 | 2019-07-05 | 23.9 | 0 | 5.9 | 2018-07-05 | 28.8 | 0 | 10.8 | 2017-07-05 | 21.6 | 0 | 3.6 | 2016-07-05 | 24.3 | 0 | 6.3 | 0.07 | 6.2
2025-07-05 | 24.1 | 0 | 6.1 | 2024-07-05 | 24.7 | 0 | 6.7 | 2023-07-05 | 25.1 | 0 | 7.1 | 2022-07-05 | 16.9 | 1.1 | 0 | 2021-07-05 | 23.3 | 0 | 5.3 | 2020-07-05 | 22.9 | 0 | 4.9 | 2019-07-05 | 24.9 | 0 | 6.9 | 2018-07-05 | 28.1 | 0 | 10.1 | 2017-07-05 | 20.1 | 0 | 2.1 | 2016-07-05 | 25.5 | 0 | 7.5 | 0.11 | 5.67
2025-07-05 | 23.9 | 0 | 5.9 | 2024-07-05 | 23.9 | 0 | 5.9 | 2023-07-05 | 24.2 | 0 | 6.2 | 2022-07-05 | 17.1 | 0.9 | 0 | 2021-07-05 | 20.9 | 0 | 2.9 | 2020-07-05 | 20 | 0 | 2 | 2019-07-05 | 24.8 | 0 | 6.8 | 2018-07-05 | 27.7 | 0 | 9.7 | 2017-07-05 | 19.9 | 0 | 1.9 | 2016-07-05 | 24.2 | 0 | 6.2 | 0.09 | 4.75
2025-07-05 | 24.1 | 0 | 6.1 | 2024-07-05 | 23.5 | 0 | 5.5 | 2023-07-05 | 23.4 | 0 | 5.4 | 2022-07-05 | 16.8 | 1.2 | 0 | 2021-07-05 | 20.4 | 0 | 2.4 | 2020-07-05 | 18.7 | 0 | 0.7 | 2019-07-05 | 24.4 | 0 | 6.4 | 2018-07-05 | 27.1 | 0 | 9.1 | 2017-07-05 | 18.6 | 0 | 0.6 | 2016-07-05 | 21.9 | 0 | 3.9 | 0.12 | 4.01
2025-07-06 | 23.6 | 0 | 5.6 | 2024-07-06 | 22.9 | 0 | 4.9 | 2023-07-06 | 22.4 | 0 | 4.4 | 2022-07-06 | 16.9 | 1.1 | 0 | 2021-07-06 | 19.9 | 0 | 1.9 | 2020-07-06 | 18.5 | 0 | 0.5 | 2019-07-06 | 24.3 | 0 | 6.3 | 2018-07-06 | 26.8 | 0 | 8.8 | 2017-07-06 | 18.1 | 0 | 0.1 | 2016-07-06 | 20.6 | 0 | 2.6 | 0.11 | 3.51
2025-07-06 | 23.2 | 0 | 5.2 | 2024-07-06 | 20.8 | 0 | 2.8 | 2023-07-06 | 21.9 | 0 | 3.9 | 2022-07-06 | 17.2 | 0.8 | 0 | 2021-07-06 | 20.1 | 0 | 2.1 | 2020-07-06 | 18 | 0 | 0 | 2019-07-06 | 23.9 | 0 | 5.9 | 2018-07-06 | 25.5 | 0 | 7.5 | 2017-07-06 | 16.6 | 1.4 | 0 | 2016-07-06 | 20.5 | 0 | 2.5 | 0.22 | 2.99
2025-07-06 | 22.7 | 0 | 4.7 | 2024-07-06 | 19.1 | 0 | 1.1 | 2023-07-06 | 21.4 | 0 | 3.4 | 2022-07-06 | 16.9 | 1.1 | 0 | 2021-07-06 | 19.9 | 0 | 1.9 | 2020-07-06 | 16.6 | 1.4 | 0 | 2019-07-06 | 23.1 | 0 | 5.1 | 2018-07-06 | 24.8 | 0 | 6.8 | 2017-07-06 | 17.2 | 0.8 | 0 | 2016-07-06 | 18.8 | 0 | 0.8 | 0.33 | 2.38
2025-07-06 | 22.8 | 0 | 4.8 | 2024-07-06 | 18.7 | 0 | 0.7 | 2023-07-06 | 20.7 | 0 | 2.7 | 2022-07-06 | 16.8 | 1.2 | 0 | 2021-07-06 | 20.3 | 0 | 2.3 | 2020-07-06 | 16.6 | 1.4 | 0 | 2019-07-06 | 23.1 | 0 | 5.1 | 2018-07-06 | 24.6 | 0 | 6.6 | 2017-07-06 | 16 | 2 | 0 | 2016-07-06 | 17.9 | 0.1 | 0 | 0.47 | 2.22
2025-07-06 | 23.3 | 0 | 5.3 | 2024-07-06 | 18.3 | 0 | 0.3 | 2023-07-06 | 20 | 0 | 2 | 2022-07-06 | 16.1 | 1.9 | 0 | 2021-07-06 | 20.3 | 0 | 2.3 | 2020-07-06 | 15.9 | 2.1 | 0 | 2019-07-06 | 22.8 | 0 | 4.8 | 2018-07-06 | 23.4 | 0 | 5.4 | 2017-07-06 | 15.8 | 2.2 | 0 | 2016-07-06 | 17.5 | 0.5 | 0 | 0.67 | 2.01
2025-07-06 | 22.9 | 0 | 4.9 | 2024-07-06 | 19.1 | 0 | 1.1 | 2023-07-06 | 20 | 0 | 2 | 2022-07-06 | 16 | 2 | 0 | 2021-07-06 | 20.4 | 0 | 2.4 | 2020-07-06 | 15.8 | 2.2 | 0 | 2019-07-06 | 23 | 0 | 5 | 2018-07-06 | 21.5 | 0 | 3.5 | 2017-07-06 | 16.1 | 1.9 | 0 | 2016-07-06 | 17.7 | 0.3 | 0 | 0.64 | 1.89
2025-07-06 | 23.4 | 0 | 5.4 | 2024-07-06 | 19.6 | 0 | 1.6 | 2023-07-06 | 21.6 | 0 | 3.6 | 2022-07-06 | 17 | 1 | 0 | 2021-07-06 | 20.9 | 0 | 2.9 | 2020-07-06 | 17.9 | 0.1 | 0 | 2019-07-06 | 24.2 | 0 | 6.2 | 2018-07-06 | 20.3 | 0 | 2.3 | 2017-07-06 | 17.6 | 0.4 | 0 | 2016-07-06 | 19.4 | 0 | 1.4 | 0.15 | 2.34
2025-07-06 | 24.5 | 0 | 6.5 | 2024-07-06 | 21.1 | 0 | 3.1 | 2023-07-06 | 24.6 | 0 | 6.6 | 2022-07-06 | 17.7 | 0.3 | 0 | 2021-07-06 | 21.7 | 0 | 3.7 | 2020-07-06 | 20.4 | 0 | 2.4 | 2019-07-06 | 24.8 | 0 | 6.8 | 2018-07-06 | 21.1 | 0 | 3.1 | 2017-07-06 | 19.6 | 0 | 1.6 | 2016-07-06 | 21.8 | 0 | 3.8 | 0.03 | 3.76
2025-07-06 | 25.7 | 0 | 7.7 | 2024-07-06 | 22.6 | 0 | 4.6 | 2023-07-06 | 26.3 | 0 | 8.3 | 2022-07-06 | 18.5 | 0 | 0.5 | 2021-07-06 | 22.3 | 0 | 4.3 | 2020-07-06 | 23.2 | 0 | 5.2 | 2019-07-06 | 25.5 | 0 | 7.5 | 2018-07-06 | 20.7 | 0 | 2.7 | 2017-07-06 | 21.7 | 0 | 3.7 | 2016-07-06 | 23.6 | 0 | 5.6 | 0 | 5.01
2025-07-06 | 27.1 | 0 | 9.1 | 2024-07-06 | 22.8 | 0 | 4.8 | 2023-07-06 | 28.3 | 0 | 10.3 | 2022-07-06 | 18.9 | 0 | 0.9 | 2021-07-06 | 23.5 | 0 | 5.5 | 2020-07-06 | 24.9 | 0 | 6.9 | 2019-07-06 | 27.3 | 0 | 9.3 | 2018-07-06 | 19.6 | 0 | 1.6 | 2017-07-06 | 23.9 | 0 | 5.9 | 2016-07-06 | 25.1 | 0 | 7.1 | 0 | 6.14
2025-07-06 | 28.6 | 0 | 10.6 | 2024-07-06 | 22.9 | 0 | 4.9 | 2023-07-06 | 29.7 | 0 | 11.7 | 2022-07-06 | 20.3 | 0 | 2.3 | 2021-07-06 | 24 | 0 | 6 | 2020-07-06 | 26.2 | 0 | 8.2 | 2019-07-06 | 26.1 | 0 | 8.1 | 2018-07-06 | 18.6 | 0 | 0.6 | 2017-07-06 | 26.6 | 0 | 8.6 | 2016-07-06 | 27.3 | 0 | 9.3 | 0 | 7.03
2025-07-06 | 31.5 | 0 | 13.5 | 2024-07-06 | 25 | 0 | 7 | 2023-07-06 | 30.9 | 0 | 12.9 | 2022-07-06 | 21.8 | 0 | 3.8 | 2021-07-06 | 26 | 0 | 8 | 2020-07-06 | 27.6 | 0 | 9.6 | 2019-07-06 | 27.2 | 0 | 9.2 | 2018-07-06 | 19.3 | 0 | 1.3 | 2017-07-06 | 28 | 0 | 10 | 2016-07-06 | 28.7 | 0 | 10.7 | 0 | 8.6
2025-07-06 | 32.5 | 0 | 14.5 | 2024-07-06 | 25.7 | 0 | 7.7 | 2023-07-06 | 31.7 | 0 | 13.7 | 2022-07-06 | 23 | 0 | 5 | 2021-07-06 | 27.7 | 0 | 9.7 | 2020-07-06 | 28.7 | 0 | 10.7 | 2019-07-06 | 29.1 | 0 | 11.1 | 2018-07-06 | 19 | 0 | 1 | 2017-07-06 | 27.3 | 0 | 9.3 | 2016-07-06 | 28.6 | 0 | 10.6 | 0 | 9.33
2025-07-06 | 30.5 | 0 | 12.5 | 2024-07-06 | 27 | 0 | 9 | 2023-07-06 | 32.8 | 0 | 14.8 | 2022-07-06 | 21.5 | 0 | 3.5 | 2021-07-06 | 29.1 | 0 | 11.1 | 2020-07-06 | 30 | 0 | 12 | 2019-07-06 | 27.9 | 0 | 9.9 | 2018-07-06 | 19.1 | 0 | 1.1 | 2017-07-06 | 26.6 | 0 | 8.6 | 2016-07-06 | 30.3 | 0 | 12.3 | 0 | 9.48
2025-07-06 | 24.7 | 0 | 6.7 | 2024-07-06 | 27.8 | 0 | 9.8 | 2023-07-06 | 33 | 0 | 15 | 2022-07-06 | 23.3 | 0 | 5.3 | 2021-07-06 | 29.2 | 0 | 11.2 | 2020-07-06 | 29.6 | 0 | 11.6 | 2019-07-06 | 29.5 | 0 | 11.5 | 2018-07-06 | 20.1 | 0 | 2.1 | 2017-07-06 | 26.9 | 0 | 8.9 | 2016-07-06 | 29 | 0 | 11 | 0 | 9.31
2025-07-06 | 26.4 | 0 | 8.4 | 2024-07-06 | 27.4 | 0 | 9.4 | 2023-07-06 | 33.4 | 0 | 15.4 | 2022-07-06 | 22.6 | 0 | 4.6 | 2021-07-06 | 30.1 | 0 | 12.1 | 2020-07-06 | 30.2 | 0 | 12.2 | 2019-07-06 | 28.3 | 0 | 10.3 | 2018-07-06 | 22 | 0 | 4 | 2017-07-06 | 27.2 | 0 | 9.2 | 2016-07-06 | 26 | 0 | 8 | 0 | 9.36
2025-07-06 | 28.8 | 0 | 10.8 | 2024-07-06 | 26.2 | 0 | 8.2 | 2023-07-06 | 32.5 | 0 | 14.5 | 2022-07-06 | 22.9 | 0 | 4.9 | 2021-07-06 | 30.2 | 0 | 12.2 | 2020-07-06 | 30.2 | 0 | 12.2 | 2019-07-06 | 27.8 | 0 | 9.8 | 2018-07-06 | 20.2 | 0 | 2.2 | 2017-07-06 | 27.8 | 0 | 9.8 | 2016-07-06 | 27.3 | 0 | 9.3 | 0 | 9.39
2025-07-06 | 29.6 | 0 | 11.6 | 2024-07-06 | 26.6 | 0 | 8.6 | 2023-07-06 | 31.3 | 0 | 13.3 | 2022-07-06 | 22.7 | 0 | 4.7 | 2021-07-06 | 29.5 | 0 | 11.5 | 2020-07-06 | 30.2 | 0 | 12.2 | 2019-07-06 | 27 | 0 | 9 | 2018-07-06 | 20 | 0 | 2 | 2017-07-06 | 27 | 0 | 9 | 2016-07-06 | 29.3 | 0 | 11.3 | 0 | 9.32
2025-07-06 | 26.8 | 0 | 8.8 | 2024-07-06 | 22.6 | 0 | 4.6 | 2023-07-06 | 29.5 | 0 | 11.5 | 2022-07-06 | 23.4 | 0 | 5.4 | 2021-07-06 | 28.5 | 0 | 10.5 | 2020-07-06 | 29.2 | 0 | 11.2 | 2019-07-06 | 25.7 | 0 | 7.7 | 2018-07-06 | 20.3 | 0 | 2.3 | 2017-07-06 | 26.5 | 0 | 8.5 | 2016-07-06 | 29.8 | 0 | 11.8 | 0 | 8.23
2025-07-06 | 26.1 | 0 | 8.1 | 2024-07-06 | 20.4 | 0 | 2.4 | 2023-07-06 | 25.3 | 0 | 7.3 | 2022-07-06 | 21.6 | 0 | 3.6 | 2021-07-06 | 26.9 | 0 | 8.9 | 2020-07-06 | 25.7 | 0 | 7.7 | 2019-07-06 | 24.1 | 0 | 6.1 | 2018-07-06 | 19.5 | 0 | 1.5 | 2017-07-06 | 24.8 | 0 | 6.8 | 2016-07-06 | 25.1 | 0 | 7.1 | 0 | 5.95
2025-07-06 | 25.2 | 0 | 7.2 | 2024-07-06 | 20.2 | 0 | 2.2 | 2023-07-06 | 24.7 | 0 | 6.7 | 2022-07-06 | 19.5 | 0 | 1.5 | 2021-07-06 | 25.4 | 0 | 7.4 | 2020-07-06 | 21.8 | 0 | 3.8 | 2019-07-06 | 23 | 0 | 5 | 2018-07-06 | 17.4 | 0.6 | 0 | 2017-07-06 | 23.6 | 0 | 5.6 | 2016-07-06 | 23.8 | 0 | 5.8 | 0.06 | 4.52
2025-07-06 | 24.1 | 0 | 6.1 | 2024-07-06 | 19.2 | 0 | 1.2 | 2023-07-06 | 24.4 | 0 | 6.4 | 2022-07-06 | 19 | 0 | 1 | 2021-07-06 | 24.2 | 0 | 6.2 | 2020-07-06 | 20.5 | 0 | 2.5 | 2019-07-06 | 21.6 | 0 | 3.6 | 2018-07-06 | 15.6 | 2.4 | 0 | 2017-07-06 | 22.8 | 0 | 4.8 | 2016-07-06 | 24 | 0 | 6 | 0.24 | 3.78
2025-07-06 | 23.3 | 0 | 5.3 | 2024-07-06 | 18.6 | 0 | 0.6 | 2023-07-06 | 22.5 | 0 | 4.5 | 2022-07-06 | 18 | 0 | 0 | 2021-07-06 | 22.3 | 0 | 4.3 | 2020-07-06 | 21.4 | 0 | 3.4 | 2019-07-06 | 20.4 | 0 | 2.4 | 2018-07-06 | 14.5 | 3.5 | 0 | 2017-07-06 | 22.4 | 0 | 4.4 | 2016-07-06 | 23.9 | 0 | 5.9 | 0.35 | 3.08
2025-07-06 | 22.9 | 0 | 4.9 | 2024-07-06 | 18 | 0 | 0 | 2023-07-06 | 22.3 | 0 | 4.3 | 2022-07-06 | 16 | 2 | 0 | 2021-07-06 | 20.6 | 0 | 2.6 | 2020-07-06 | 20.6 | 0 | 2.6 | 2019-07-06 | 19.2 | 0 | 1.2 | 2018-07-06 | 13.1 | 4.9 | 0 | 2017-07-06 | 21.9 | 0 | 3.9 | 2016-07-06 | 23.4 | 0 | 5.4 | 0.69 | 2.49
2025-07-07 | 22.5 | 0 | 4.5 | 2024-07-07 | 18.4 | 0 | 0.4 | 2023-07-07 | 21.8 | 0 | 3.8 | 2022-07-07 | 14.1 | 3.9 | 0 | 2021-07-07 | 18.8 | 0 | 0.8 | 2020-07-07 | 19.9 | 0 | 1.9 | 2019-07-07 | 18.1 | 0 | 0.1 | 2018-07-07 | 12.6 | 5.4 | 0 | 2017-07-07 | 21.6 | 0 | 3.6 | 2016-07-07 | 22.6 | 0 | 4.6 | 0.93 | 1.97
2025-07-07 | 21.4 | 0 | 3.4 | 2024-07-07 | 18.6 | 0 | 0.6 | 2023-07-07 | 20.8 | 0 | 2.8 | 2022-07-07 | 12.7 | 5.3 | 0 | 2021-07-07 | 17.7 | 0.3 | 0 | 2020-07-07 | 19.6 | 0 | 1.6 | 2019-07-07 | 16.7 | 1.3 | 0 | 2018-07-07 | 11.1 | 6.9 | 0 | 2017-07-07 | 21.2 | 0 | 3.2 | 2016-07-07 | 22.4 | 0 | 4.4 | 1.38 | 1.6
2025-07-07 | 21.1 | 0 | 3.1 | 2024-07-07 | 18.7 | 0 | 0.7 | 2023-07-07 | 20.7 | 0 | 2.7 | 2022-07-07 | 14.5 | 3.5 | 0 | 2021-07-07 | 16.8 | 1.2 | 0 | 2020-07-07 | 18.5 | 0 | 0.5 | 2019-07-07 | 15.5 | 2.5 | 0 | 2018-07-07 | 10.5 | 7.5 | 0 | 2017-07-07 | 21.4 | 0 | 3.4 | 2016-07-07 | 22.1 | 0 | 4.1 | 1.47 | 1.45
2025-07-07 | 20.6 | 0 | 2.6 | 2024-07-07 | 18.3 | 0 | 0.3 | 2023-07-07 | 20.8 | 0 | 2.8 | 2022-07-07 | 12.7 | 5.3 | 0 | 2021-07-07 | 16.2 | 1.8 | 0 | 2020-07-07 | 17.3 | 0.7 | 0 | 2019-07-07 | 15.2 | 2.8 | 0 | 2018-07-07 | 11.6 | 6.4 | 0 | 2017-07-07 | 20.6 | 0 | 2.6 | 2016-07-07 | 21.6 | 0 | 3.6 | 1.7 | 1.19
2025-07-07 | 20.8 | 0 | 2.8 | 2024-07-07 | 18.4 | 0 | 0.4 | 2023-07-07 | 20.3 | 0 | 2.3 | 2022-07-07 | 11.4 | 6.6 | 0 | 2021-07-07 | 15.6 | 2.4 | 0 | 2020-07-07 | 16.4 | 1.6 | 0 | 2019-07-07 | 14.8 | 3.2 | 0 | 2018-07-07 | 11.3 | 6.7 | 0 | 2017-07-07 | 19.4 | 0 | 1.4 | 2016-07-07 | 21.3 | 0 | 3.3 | 2.05 | 1.02
2025-07-07 | 20.8 | 0 | 2.8 | 2024-07-07 | 18.1 | 0 | 0.1 | 2023-07-07 | 20.8 | 0 | 2.8 | 2022-07-07 | 12.2 | 5.8 | 0 | 2021-07-07 | 14.9 | 3.1 | 0 | 2020-07-07 | 16.8 | 1.2 | 0 | 2019-07-07 | 14.8 | 3.2 | 0 | 2018-07-07 | 11.7 | 6.3 | 0 | 2017-07-07 | 19.2 | 0 | 1.2 | 2016-07-07 | 20.5 | 0 | 2.5 | 1.96 | 0.94
2025-07-07 | 21.3 | 0 | 3.3 | 2024-07-07 | 18.4 | 0 | 0.4 | 2023-07-07 | 21 | 0 | 3 | 2022-07-07 | 15.2 | 2.8 | 0 | 2021-07-07 | 13.8 | 4.2 | 0 | 2020-07-07 | 17.7 | 0.3 | 0 | 2019-07-07 | 15.9 | 2.1 | 0 | 2018-07-07 | 13.9 | 4.1 | 0 | 2017-07-07 | 20.3 | 0 | 2.3 | 2016-07-07 | 20.1 | 0 | 2.1 | 1.35 | 1.11
2025-07-07 | 21.8 | 0 | 3.8 | 2024-07-07 | 18.8 | 0 | 0.8 | 2023-07-07 | 22.4 | 0 | 4.4 | 2022-07-07 | 17.5 | 0.5 | 0 | 2021-07-07 | 13.4 | 4.6 | 0 | 2020-07-07 | 20.5 | 0 | 2.5 | 2019-07-07 | 17.4 | 0.6 | 0 | 2018-07-07 | 18 | 0 | 0 | 2017-07-07 | 20.5 | 0 | 2.5 | 2016-07-07 | 21.7 | 0 | 3.7 | 0.57 | 1.77
2025-07-07 | 21.6 | 0 | 3.6 | 2024-07-07 | 19.2 | 0 | 1.2 | 2023-07-07 | 23.8 | 0 | 5.8 | 2022-07-07 | 18.9 | 0 | 0.9 | 2021-07-07 | 12.4 | 5.6 | 0 | 2020-07-07 | 23.6 | 0 | 5.6 | 2019-07-07 | 19.1 | 0 | 1.1 | 2018-07-07 | 20.1 | 0 | 2.1 | 2017-07-07 | 21.4 | 0 | 3.4 | 2016-07-07 | 23 | 0 | 5 | 0.56 | 2.87
2025-07-07 | 21.8 | 0 | 3.8 | 2024-07-07 | 20 | 0 | 2 | 2023-07-07 | 23.4 | 0 | 5.4 | 2022-07-07 | 20.6 | 0 | 2.6 | 2021-07-07 | 13 | 5 | 0 | 2020-07-07 | 25 | 0 | 7 | 2019-07-07 | 20.3 | 0 | 2.3 | 2018-07-07 | 22.5 | 0 | 4.5 | 2017-07-07 | 21 | 0 | 3 | 2016-07-07 | 25 | 0 | 7 | 0.5 | 3.76
2025-07-07 | 19.9 | 0 | 1.9 | 2024-07-07 | 20.9 | 0 | 2.9 | 2023-07-07 | 24.2 | 0 | 6.2 | 2022-07-07 | 22.6 | 0 | 4.6 | 2021-07-07 | 13.2 | 4.8 | 0 | 2020-07-07 | 27.2 | 0 | 9.2 | 2019-07-07 | 20.9 | 0 | 2.9 | 2018-07-07 | 24 | 0 | 6 | 2017-07-07 | 21.5 | 0 | 3.5 | 2016-07-07 | 26.3 | 0 | 8.3 | 0.48 | 4.55
2025-07-07 | 19.9 | 0 | 1.9 | 2024-07-07 | 22.4 | 0 | 4.4 | 2023-07-07 | 24 | 0 | 6 | 2022-07-07 | 23.7 | 0 | 5.7 | 2021-07-07 | 13.5 | 4.5 | 0 | 2020-07-07 | 29 | 0 | 11 | 2019-07-07 | 21.9 | 0 | 3.9 | 2018-07-07 | 25.8 | 0 | 7.8 | 2017-07-07 | 22.6 | 0 | 4.6 | 2016-07-07 | 27.2 | 0 | 9.2 | 0.45 | 5.45
2025-07-07 | 19.6 | 0 | 1.6 | 2024-07-07 | 24.3 | 0 | 6.3 | 2023-07-07 | 25.4 | 0 | 7.4 | 2022-07-07 | 23.9 | 0 | 5.9 | 2021-07-07 | 14.7 | 3.3 | 0 | 2020-07-07 | 31.6 | 0 | 13.6 | 2019-07-07 | 22.7 | 0 | 4.7 | 2018-07-07 | 26.4 | 0 | 8.4 | 2017-07-07 | 25.3 | 0 | 7.3 | 2016-07-07 | 27.8 | 0 | 9.8 | 0.33 | 6.5
2025-07-07 | 19.6 | 0 | 1.6 | 2024-07-07 | 25.9 | 0 | 7.9 | 2023-07-07 | 26.4 | 0 | 8.4 | 2022-07-07 | 24.2 | 0 | 6.2 | 2021-07-07 | 15.8 | 2.2 | 0 | 2020-07-07 | 31.8 | 0 | 13.8 | 2019-07-07 | 24 | 0 | 6 | 2018-07-07 | 27.6 | 0 | 9.6 | 2017-07-07 | 26.1 | 0 | 8.1 | 2016-07-07 | 28.9 | 0 | 10.9 | 0.22 | 7.25
2025-07-07 | 19.2 | 0 | 1.2 | 2024-07-07 | 25.8 | 0 | 7.8 | 2023-07-07 | 27.8 | 0 | 9.8 | 2022-07-07 | 24.7 | 0 | 6.7 | 2021-07-07 | 16.7 | 1.3 | 0 | 2020-07-07 | 33.8 | 0 | 15.8 | 2019-07-07 | 24.1 | 0 | 6.1 | 2018-07-07 | 27.7 | 0 | 9.7 | 2017-07-07 | 26.3 | 0 | 8.3 | 2016-07-07 | 29.7 | 0 | 11.7 | 0.13 | 7.71
2025-07-07 | 18.7 | 0 | 0.7 | 2024-07-07 | 27.3 | 0 | 9.3 | 2023-07-07 | 28.4 | 0 | 10.4 | 2022-07-07 | 24.9 | 0 | 6.9 | 2021-07-07 | 17.3 | 0.7 | 0 | 2020-07-07 | 33.9 | 0 | 15.9 | 2019-07-07 | 24.4 | 0 | 6.4 | 2018-07-07 | 29.3 | 0 | 11.3 | 2017-07-07 | 25.9 | 0 | 7.9 | 2016-07-07 | 29.3 | 0 | 11.3 | 0.07 | 8.01
2025-07-07 | 18.8 | 0 | 0.8 | 2024-07-07 | 26.4 | 0 | 8.4 | 2023-07-07 | 29 | 0 | 11 | 2022-07-07 | 24.9 | 0 | 6.9 | 2021-07-07 | 17.4 | 0.6 | 0 | 2020-07-07 | 32.7 | 0 | 14.7 | 2019-07-07 | 24.8 | 0 | 6.8 | 2018-07-07 | 28.6 | 0 | 10.6 | 2017-07-07 | 20.4 | 0 | 2.4 | 2016-07-07 | 29.4 | 0 | 11.4 | 0.06 | 7.3
2025-07-07 | 19 | 0 | 1 | 2024-07-07 | 26.3 | 0 | 8.3 | 2023-07-07 | 28.7 | 0 | 10.7 | 2022-07-07 | 25.8 | 0 | 7.8 | 2021-07-07 | 17.5 | 0.5 | 0 | 2020-07-07 | 32.4 | 0 | 14.4 | 2019-07-07 | 24.9 | 0 | 6.9 | 2018-07-07 | 28.8 | 0 | 10.8 | 2017-07-07 | 20.5 | 0 | 2.5 | 2016-07-07 | 28.7 | 0 | 10.7 | 0.05 | 7.31
2025-07-07 | 19.2 | 0 | 1.2 | 2024-07-07 | 26.4 | 0 | 8.4 | 2023-07-07 | 27.8 | 0 | 9.8 | 2022-07-07 | 24.4 | 0 | 6.4 | 2021-07-07 | 17.6 | 0.4 | 0 | 2020-07-07 | 30.9 | 0 | 12.9 | 2019-07-07 | 24.2 | 0 | 6.2 | 2018-07-07 | 26.7 | 0 | 8.7 | 2017-07-07 | 21.2 | 0 | 3.2 | 2016-07-07 | 26.6 | 0 | 8.6 | 0.04 | 6.54
2025-07-07 | 18.6 | 0 | 0.6 | 2024-07-07 | 24.9 | 0 | 6.9 | 2023-07-07 | 25.5 | 0 | 7.5 | 2022-07-07 | 23 | 0 | 5 | 2021-07-07 | 16.4 | 1.6 | 0 | 2020-07-07 | 28.8 | 0 | 10.8 | 2019-07-07 | 22.9 | 0 | 4.9 | 2018-07-07 | 24.8 | 0 | 6.8 | 2017-07-07 | 20.7 | 0 | 2.7 | 2016-07-07 | 26.3 | 0 | 8.3 | 0.16 | 5.35
2025-07-07 | 18.5 | 0 | 0.5 | 2024-07-07 | 23.5 | 0 | 5.5 | 2023-07-07 | 24.4 | 0 | 6.4 | 2022-07-07 | 19.7 | 0 | 1.7 | 2021-07-07 | 14.7 | 3.3 | 0 | 2020-07-07 | 27.5 | 0 | 9.5 | 2019-07-07 | 21.1 | 0 | 3.1 | 2018-07-07 | 22.4 | 0 | 4.4 | 2017-07-07 | 20.2 | 0 | 2.2 | 2016-07-07 | 24.1 | 0 | 6.1 | 0.33 | 3.94
2025-07-07 | 18.2 | 0 | 0.2 | 2024-07-07 | 22 | 0 | 4 | 2023-07-07 | 23.9 | 0 | 5.9 | 2022-07-07 | 20.1 | 0 | 2.1 | 2021-07-07 | 14.2 | 3.8 | 0 | 2020-07-07 | 26 | 0 | 8 | 2019-07-07 | 20.4 | 0 | 2.4 | 2018-07-07 | 20.8 | 0 | 2.8 | 2017-07-07 | 18.9 | 0 | 0.9 | 2016-07-07 | 22.5 | 0 | 4.5 | 0.38 | 3.08
2025-07-07 | 18.2 | 0 | 0.2 | 2024-07-07 | 21.6 | 0 | 3.6 | 2023-07-07 | 22.8 | 0 | 4.8 | 2022-07-07 | 19 | 0 | 1 | 2021-07-07 | 14.7 | 3.3 | 0 | 2020-07-07 | 25.5 | 0 | 7.5 | 2019-07-07 | 18.5 | 0 | 0.5 | 2018-07-07 | 19.8 | 0 | 1.8 | 2017-07-07 | 18.8 | 0 | 0.8 | 2016-07-07 | 21.5 | 0 | 3.5 | 0.33 | 2.37
2025-07-07 | 18.1 | 0 | 0.1 | 2024-07-07 | 20.5 | 0 | 2.5 | 2023-07-07 | 22 | 0 | 4 | 2022-07-07 | 19 | 0 | 1 | 2021-07-07 | 15.3 | 2.7 | 0 | 2020-07-07 | 26 | 0 | 8 | 2019-07-07 | 15.9 | 2.1 | 0 | 2018-07-07 | 18.5 | 0 | 0.5 | 2017-07-07 | 17.9 | 0.1 | 0 | 2016-07-07 | 20.4 | 0 | 2.4 | 0.49 | 1.85
2025-07-08 | 18 | 0 | 0 | 2024-07-08 | 20.2 | 0 | 2.2 | 2023-07-08 | 21 | 0 | 3 | 2022-07-08 | 18.5 | 0 | 0.5 | 2021-07-08 | 14 | 4 | 0 | 2020-07-08 | 25.6 | 0 | 7.6 | 2019-07-08 | 16.2 | 1.8 | 0 | 2018-07-08 | 16.8 | 1.2 | 0 | 2017-07-08 | 17.9 | 0.1 | 0 | 2016-07-08 | 19.2 | 0 | 1.2 | 0.71 | 1.45
2025-07-08 | 17.8 | 0.2 | 0 | 2024-07-08 | 19.4 | 0 | 1.4 | 2023-07-08 | 21 | 0 | 3 | 2022-07-08 | 17.1 | 0.9 | 0 | 2021-07-08 | 14.8 | 3.2 | 0 | 2020-07-08 | 24.9 | 0 | 6.9 | 2019-07-08 | 15 | 3 | 0 | 2018-07-08 | 16.5 | 1.5 | 0 | 2017-07-08 | 17.8 | 0.2 | 0 | 2016-07-08 | 18.5 | 0 | 0.5 | 0.9 | 1.18
2025-07-08 | 17.1 | 0.9 | 0 | 2024-07-08 | 18.6 | 0 | 0.6 | 2023-07-08 | 21.4 | 0 | 3.4 | 2022-07-08 | 15.5 | 2.5 | 0 | 2021-07-08 | 14.9 | 3.1 | 0 | 2020-07-08 | 23.7 | 0 | 5.7 | 2019-07-08 | 12.4 | 5.6 | 0 | 2018-07-08 | 15.3 | 2.7 | 0 | 2017-07-08 | 18.6 | 0 | 0.6 | 2016-07-08 | 18.4 | 0 | 0.4 | 1.48 | 1.07
2025-07-08 | 16.7 | 1.3 | 0 | 2024-07-08 | 17.7 | 0.3 | 0 | 2023-07-08 | 19.5 | 0 | 1.5 | 2022-07-08 | 15.3 | 2.7 | 0 | 2021-07-08 | 15.1 | 2.9 | 0 | 2020-07-08 | 22.4 | 0 | 4.4 | 2019-07-08 | 13.4 | 4.6 | 0 | 2018-07-08 | 14.6 | 3.4 | 0 | 2017-07-08 | 17.2 | 0.8 | 0 | 2016-07-08 | 17.9 | 0.1 | 0 | 1.61 | 0.59
2025-07-08 | 16.6 | 1.4 | 0 | 2024-07-08 | 18.2 | 0 | 0.2 | 2023-07-08 | 19.6 | 0 | 1.6 | 2022-07-08 | 14.5 | 3.5 | 0 | 2021-07-08 | 14.6 | 3.4 | 0 | 2020-07-08 | 20.7 | 0 | 2.7 | 2019-07-08 | 11.7 | 6.3 | 0 | 2018-07-08 | 13.8 | 4.2 | 0 | 2017-07-08 | 17.2 | 0.8 | 0 | 2016-07-08 | 17.6 | 0.4 | 0 | 2 | 0.45
2025-07-08 | 16.9 | 1.1 | 0 | 2024-07-08 | 18.1 | 0 | 0.1 | 2023-07-08 | 19.8 | 0 | 1.8 | 2022-07-08 | 15.5 | 2.5 | 0 | 2021-07-08 | 13.5 | 4.5 | 0 | 2020-07-08 | 21.3 | 0 | 3.3 | 2019-07-08 | 10.9 | 7.1 | 0 | 2018-07-08 | 14.4 | 3.6 | 0 | 2017-07-08 | 17.1 | 0.9 | 0 | 2016-07-08 | 17.8 | 0.2 | 0 | 1.99 | 0.52
2025-07-08 | 17.4 | 0.6 | 0 | 2024-07-08 | 19.4 | 0 | 1.4 | 2023-07-08 | 19.8 | 0 | 1.8 | 2022-07-08 | 17.3 | 0.7 | 0 | 2021-07-08 | 13.8 | 4.2 | 0 | 2020-07-08 | 23 | 0 | 5 | 2019-07-08 | 15.4 | 2.6 | 0 | 2018-07-08 | 15.5 | 2.5 | 0 | 2017-07-08 | 17.1 | 0.9 | 0 | 2016-07-08 | 18 | 0 | 0 | 1.15 | 0.82
2025-07-08 | 17.9 | 0.1 | 0 | 2024-07-08 | 20.5 | 0 | 2.5 | 2023-07-08 | 19.9 | 0 | 1.9 | 2022-07-08 | 18.6 | 0 | 0.6 | 2021-07-08 | 14.3 | 3.7 | 0 | 2020-07-08 | 24.4 | 0 | 6.4 | 2019-07-08 | 18.5 | 0 | 0.5 | 2018-07-08 | 18.1 | 0 | 0.1 | 2017-07-08 | 17.8 | 0.2 | 0 | 2016-07-08 | 18 | 0 | 0 | 0.4 | 1.2
2025-07-08 | 19.6 | 0 | 1.6 | 2024-07-08 | 22 | 0 | 4 | 2023-07-08 | 22.8 | 0 | 4.8 | 2022-07-08 | 20.7 | 0 | 2.7 | 2021-07-08 | 15.1 | 2.9 | 0 | 2020-07-08 | 25.9 | 0 | 7.9 | 2019-07-08 | 20.1 | 0 | 2.1 | 2018-07-08 | 21.4 | 0 | 3.4 | 2017-07-08 | 18.8 | 0 | 0.8 | 2016-07-08 | 19 | 0 | 1 | 0.29 | 2.83
2025-07-08 | 21.1 | 0 | 3.1 | 2024-07-08 | 24.8 | 0 | 6.8 | 2023-07-08 | 25.1 | 0 | 7.1 | 2022-07-08 | 21.9 | 0 | 3.9 | 2021-07-08 | 16.3 | 1.7 | 0 | 2020-07-08 | 28.4 | 0 | 10.4 | 2019-07-08 | 22.1 | 0 | 4.1 | 2018-07-08 | 24.9 | 0 | 6.9 | 2017-07-08 | 19.8 | 0 | 1.8 | 2016-07-08 | 18.3 | 0 | 0.3 | 0.17 | 4.44
2025-07-08 | 22.8 | 0 | 4.8 | 2024-07-08 | 26.5 | 0 | 8.5 | 2023-07-08 | 25.9 | 0 | 7.9 | 2022-07-08 | 23.2 | 0 | 5.2 | 2021-07-08 | 16.7 | 1.3 | 0 | 2020-07-08 | 29 | 0 | 11 | 2019-07-08 | 23.7 | 0 | 5.7 | 2018-07-08 | 26.7 | 0 | 8.7 | 2017-07-08 | 21.1 | 0 | 3.1 | 2016-07-08 | 18.3 | 0 | 0.3 | 0.13 | 5.52
2025-07-08 | 23.7 | 0 | 5.7 | 2024-07-08 | 26.4 | 0 | 8.4 | 2023-07-08 | 26.3 | 0 | 8.3 | 2022-07-08 | 22.8 | 0 | 4.8 | 2021-07-08 | 16.9 | 1.1 | 0 | 2020-07-08 | 29.8 | 0 | 11.8 | 2019-07-08 | 24.6 | 0 | 6.6 | 2018-07-08 | 27.6 | 0 | 9.6 | 2017-07-08 | 19.8 | 0 | 1.8 | 2016-07-08 | 19.1 | 0 | 1.1 | 0.11 | 5.81
2025-07-08 | 24.2 | 0 | 6.2 | 2024-07-08 | 27.1 | 0 | 9.1 | 2023-07-08 | 27.2 | 0 | 9.2 | 2022-07-08 | 24.6 | 0 | 6.6 | 2021-07-08 | 17.5 | 0.5 | 0 | 2020-07-08 | 31.4 | 0 | 13.4 | 2019-07-08 | 25.6 | 0 | 7.6 | 2018-07-08 | 28.8 | 0 | 10.8 | 2017-07-08 | 20.5 | 0 | 2.5 | 2016-07-08 | 20.4 | 0 | 2.4 | 0.05 | 6.78
2025-07-08 | 24.8 | 0 | 6.8 | 2024-07-08 | 27.3 | 0 | 9.3 | 2023-07-08 | 27 | 0 | 9 | 2022-07-08 | 24.4 | 0 | 6.4 | 2021-07-08 | 17.2 | 0.8 | 0 | 2020-07-08 | 32.3 | 0 | 14.3 | 2019-07-08 | 26.6 | 0 | 8.6 | 2018-07-08 | 29.3 | 0 | 11.3 | 2017-07-08 | 21.2 | 0 | 3.2 | 2016-07-08 | 20.4 | 0 | 2.4 | 0.08 | 7.13
2025-07-08 | 24.9 | 0 | 6.9 | 2024-07-08 | 28.4 | 0 | 10.4 | 2023-07-08 | 27.5 | 0 | 9.5 | 2022-07-08 | 24.5 | 0 | 6.5 | 2021-07-08 | 16.5 | 1.5 | 0 | 2020-07-08 | 29.9 | 0 | 11.9 | 2019-07-08 | 26.3 | 0 | 8.3 | 2018-07-08 | 29.9 | 0 | 11.9 | 2017-07-08 | 22.8 | 0 | 4.8 | 2016-07-08 | 20.4 | 0 | 2.4 | 0.15 | 7.26
2025-07-08 | 24.4 | 0 | 6.4 | 2024-07-08 | 28.3 | 0 | 10.3 | 2023-07-08 | 27.4 | 0 | 9.4 | 2022-07-08 | 24.9 | 0 | 6.9 | 2021-07-08 | 14.2 | 3.8 | 0 | 2020-07-08 | 32.3 | 0 | 14.3 | 2019-07-08 | 26.8 | 0 | 8.8 | 2018-07-08 | 30.5 | 0 | 12.5 | 2017-07-08 | 22.4 | 0 | 4.4 | 2016-07-08 | 21.6 | 0 | 3.6 | 0.38 | 7.66
2025-07-08 | 24.3 | 0 | 6.3 | 2024-07-08 | 28.5 | 0 | 10.5 | 2023-07-08 | 27.6 | 0 | 9.6 | 2022-07-08 | 23.4 | 0 | 5.4 | 2021-07-08 | 14.2 | 3.8 | 0 | 2020-07-08 | 32.8 | 0 | 14.8 | 2019-07-08 | 27 | 0 | 9 | 2018-07-08 | 29.3 | 0 | 11.3 | 2017-07-08 | 21.4 | 0 | 3.4 | 2016-07-08 | 21.5 | 0 | 3.5 | 0.38 | 7.38
2025-07-08 | 23.1 | 0 | 5.1 | 2024-07-08 | 28.2 | 0 | 10.2 | 2023-07-08 | 26.4 | 0 | 8.4 | 2022-07-08 | 24.1 | 0 | 6.1 | 2021-07-08 | 14.5 | 3.5 | 0 | 2020-07-08 | 33.4 | 0 | 15.4 | 2019-07-08 | 26.4 | 0 | 8.4 | 2018-07-08 | 29.1 | 0 | 11.1 | 2017-07-08 | 21.8 | 0 | 3.8 | 2016-07-08 | 21.5 | 0 | 3.5 | 0.35 | 7.2
2025-07-08 | 24 | 0 | 6 | 2024-07-08 | 27.5 | 0 | 9.5 | 2023-07-08 | 24.7 | 0 | 6.7 | 2022-07-08 | 24 | 0 | 6 | 2021-07-08 | 14.4 | 3.6 | 0 | 2020-07-08 | 32.5 | 0 | 14.5 | 2019-07-08 | 25.7 | 0 | 7.7 | 2018-07-08 | 27.7 | 0 | 9.7 | 2017-07-08 | 21.7 | 0 | 3.7 | 2016-07-08 | 21 | 0 | 3 | 0.36 | 6.68
2025-07-08 | 22 | 0 | 4 | 2024-07-08 | 25.5 | 0 | 7.5 | 2023-07-08 | 22.9 | 0 | 4.9 | 2022-07-08 | 22.3 | 0 | 4.3 | 2021-07-08 | 14.6 | 3.4 | 0 | 2020-07-08 | 29.9 | 0 | 11.9 | 2019-07-08 | 23.9 | 0 | 5.9 | 2018-07-08 | 26 | 0 | 8 | 2017-07-08 | 20.4 | 0 | 2.4 | 2016-07-08 | 20.3 | 0 | 2.3 | 0.34 | 5.12
2025-07-08 | 21 | 0 | 3 | 2024-07-08 | 24.2 | 0 | 6.2 | 2023-07-08 | 21.6 | 0 | 3.6 | 2022-07-08 | 20.2 | 0 | 2.2 | 2021-07-08 | 14.9 | 3.1 | 0 | 2020-07-08 | 26.5 | 0 | 8.5 | 2019-07-08 | 22.1 | 0 | 4.1 | 2018-07-08 | 23.7 | 0 | 5.7 | 2017-07-08 | 16.9 | 1.1 | 0 | 2016-07-08 | 19.7 | 0 | 1.7 | 0.42 | 3.5
2025-07-08 | 20.4 | 0 | 2.4 | 2024-07-08 | 23.2 | 0 | 5.2 | 2023-07-08 | 21.1 | 0 | 3.1 | 2022-07-08 | 18.3 | 0 | 0.3 | 2021-07-08 | 14.9 | 3.1 | 0 | 2020-07-08 | 25.4 | 0 | 7.4 | 2019-07-08 | 21.1 | 0 | 3.1 | 2018-07-08 | 21.8 | 0 | 3.8 | 2017-07-08 | 17.7 | 0.3 | 0 | 2016-07-08 | 19.6 | 0 | 1.6 | 0.34 | 2.69
2025-07-08 | 19.9 | 0 | 1.9 | 2024-07-08 | 22.7 | 0 | 4.7 | 2023-07-08 | 19.7 | 0 | 1.7 | 2022-07-08 | 16.9 | 1.1 | 0 | 2021-07-08 | 14.5 | 3.5 | 0 | 2020-07-08 | 24.5 | 0 | 6.5 | 2019-07-08 | 18.5 | 0 | 0.5 | 2018-07-08 | 20.5 | 0 | 2.5 | 2017-07-08 | 15.7 | 2.3 | 0 | 2016-07-08 | 18.4 | 0 | 0.4 | 0.69 | 1.82
2025-07-08 | 18.7 | 0 | 0.7 | 2024-07-08 | 22 | 0 | 4 | 2023-07-08 | 19.6 | 0 | 1.6 | 2022-07-08 | 16.1 | 1.9 | 0 | 2021-07-08 | 14.1 | 3.9 | 0 | 2020-07-08 | 24.7 | 0 | 6.7 | 2019-07-08 | 16.9 | 1.1 | 0 | 2018-07-08 | 19.8 | 0 | 1.8 | 2017-07-08 | 15.3 | 2.7 | 0 | 2016-07-08 | 17.5 | 0.5 | 0 | 1.01 | 1.48
2025-07-09 | 18 | 0 | 0 | 2024-07-09 | 21.5 | 0 | 3.5 | 2023-07-09 | 19.7 | 0 | 1.7 | 2022-07-09 | 15 | 3 | 0 | 2021-07-09 | 13.9 | 4.1 | 0 | 2020-07-09 | 23.1 | 0 | 5.1 | 2019-07-09 | 14.4 | 3.6 | 0 | 2018-07-09 | 19.2 | 0 | 1.2 | 2017-07-09 | 14.3 | 3.7 | 0 | 2016-07-09 | 17.7 | 0.3 | 0 | 1.47 | 1.15
2025-07-09 | 17.7 | 0.3 | 0 | 2024-07-09 | 20.2 | 0 | 2.2 | 2023-07-09 | 19.5 | 0 | 1.5 | 2022-07-09 | 14.1 | 3.9 | 0 | 2021-07-09 | 13.8 | 4.2 | 0 | 2020-07-09 | 22.4 | 0 | 4.4 | 2019-07-09 | 14.4 | 3.6 | 0 | 2018-07-09 | 18.1 | 0 | 0.1 | 2017-07-09 | 13.2 | 4.8 | 0 | 2016-07-09 | 17.8 | 0.2 | 0 | 1.7 | 0.82
2025-07-09 | 17.2 | 0.8 | 0 | 2024-07-09 | 19.7 | 0 | 1.7 | 2023-07-09 | 18.6 | 0 | 0.6 | 2022-07-09 | 13.1 | 4.9 | 0 | 2021-07-09 | 13.8 | 4.2 | 0 | 2020-07-09 | 22 | 0 | 4 | 2019-07-09 | 15.9 | 2.1 | 0 | 2018-07-09 | 17.3 | 0.7 | 0 | 2017-07-09 | 13 | 5 | 0 | 2016-07-09 | 16.6 | 1.4 | 0 | 1.91 | 0.63
2025-07-09 | 16.2 | 1.8 | 0 | 2024-07-09 | 19 | 0 | 1 | 2023-07-09 | 18 | 0 | 0 | 2022-07-09 | 12.1 | 5.9 | 0 | 2021-07-09 | 13.6 | 4.4 | 0 | 2020-07-09 | 20.5 | 0 | 2.5 | 2019-07-09 | 15.6 | 2.4 | 0 | 2018-07-09 | 17 | 1 | 0 | 2017-07-09 | 13.3 | 4.7 | 0 | 2016-07-09 | 16.4 | 1.6 | 0 | 2.18 | 0.35
2025-07-09 | 16.5 | 1.5 | 0 | 2024-07-09 | 19.2 | 0 | 1.2 | 2023-07-09 | 17.5 | 0.5 | 0 | 2022-07-09 | 11.6 | 6.4 | 0 | 2021-07-09 | 13.6 | 4.4 | 0 | 2020-07-09 | 19.8 | 0 | 1.8 | 2019-07-09 | 14.3 | 3.7 | 0 | 2018-07-09 | 16.1 | 1.9 | 0 | 2017-07-09 | 12.4 | 5.6 | 0 | 2016-07-09 | 16.3 | 1.7 | 0 | 2.57 | 0.3
2025-07-09 | 15.5 | 2.5 | 0 | 2024-07-09 | 19.2 | 0 | 1.2 | 2023-07-09 | 17.1 | 0.9 | 0 | 2022-07-09 | 11.7 | 6.3 | 0 | 2021-07-09 | 13.6 | 4.4 | 0 | 2020-07-09 | 20 | 0 | 2 | 2019-07-09 | 14.8 | 3.2 | 0 | 2018-07-09 | 15.7 | 2.3 | 0 | 2017-07-09 | 12.9 | 5.1 | 0 | 2016-07-09 | 16.4 | 1.6 | 0 | 2.63 | 0.32
2025-07-09 | 17.1 | 0.9 | 0 | 2024-07-09 | 19.9 | 0 | 1.9 | 2023-07-09 | 19.1 | 0 | 1.1 | 2022-07-09 | 13.1 | 4.9 | 0 | 2021-07-09 | 14.1 | 3.9 | 0 | 2020-07-09 | 22.4 | 0 | 4.4 | 2019-07-09 | 16.8 | 1.2 | 0 | 2018-07-09 | 18.5 | 0 | 0.5 | 2017-07-09 | 14.8 | 3.2 | 0 | 2016-07-09 | 16.3 | 1.7 | 0 | 1.58 | 0.79
2025-07-09 | 19.4 | 0 | 1.4 | 2024-07-09 | 21.8 | 0 | 3.8 | 2023-07-09 | 19.7 | 0 | 1.7 | 2022-07-09 | 14.8 | 3.2 | 0 | 2021-07-09 | 15 | 3 | 0 | 2020-07-09 | 24.3 | 0 | 6.3 | 2019-07-09 | 19.4 | 0 | 1.4 | 2018-07-09 | 21.5 | 0 | 3.5 | 2017-07-09 | 16.5 | 1.5 | 0 | 2016-07-09 | 16.6 | 1.4 | 0 | 0.91 | 1.81
2025-07-09 | 22.4 | 0 | 4.4 | 2024-07-09 | 22.7 | 0 | 4.7 | 2023-07-09 | 20.7 | 0 | 2.7 | 2022-07-09 | 16.1 | 1.9 | 0 | 2021-07-09 | 16.2 | 1.8 | 0 | 2020-07-09 | 26.5 | 0 | 8.5 | 2019-07-09 | 21.5 | 0 | 3.5 | 2018-07-09 | 24.4 | 0 | 6.4 | 2017-07-09 | 18.3 | 0 | 0.3 | 2016-07-09 | 16.9 | 1.1 | 0 | 0.48 | 3.05
2025-07-09 | 24.1 | 0 | 6.1 | 2024-07-09 | 23 | 0 | 5 | 2023-07-09 | 21.7 | 0 | 3.7 | 2022-07-09 | 17.6 | 0.4 | 0 | 2021-07-09 | 16.9 | 1.1 | 0 | 2020-07-09 | 29 | 0 | 11 | 2019-07-09 | 23.7 | 0 | 5.7 | 2018-07-09 | 26.8 | 0 | 8.8 | 2017-07-09 | 19.1 | 0 | 1.1 | 2016-07-09 | 17.1 | 0.9 | 0 | 0.24 | 4.14
2025-07-09 | 24.4 | 0 | 6.4 | 2024-07-09 | 23 | 0 | 5 | 2023-07-09 | 22.5 | 0 | 4.5 | 2022-07-09 | 18.1 | 0 | 0.1 | 2021-07-09 | 17.4 | 0.6 | 0 | 2020-07-09 | 30.5 | 0 | 12.5 | 2019-07-09 | 25.9 | 0 | 7.9 | 2018-07-09 | 29.7 | 0 | 11.7 | 2017-07-09 | 22.2 | 0 | 4.2 | 2016-07-09 | 16.8 | 1.2 | 0 | 0.18 | 5.23
2025-07-09 | 26.4 | 0 | 8.4 | 2024-07-09 | 24.5 | 0 | 6.5 | 2023-07-09 | 23.3 | 0 | 5.3 | 2022-07-09 | 19.5 | 0 | 1.5 | 2021-07-09 | 18.5 | 0 | 0.5 | 2020-07-09 | 33.5 | 0 | 15.5 | 2019-07-09 | 27.5 | 0 | 9.5 | 2018-07-09 | 30.7 | 0 | 12.7 | 2017-07-09 | 23.5 | 0 | 5.5 | 2016-07-09 | 17.2 | 0.8 | 0 | 0.08 | 6.54
2025-07-09 | 26.4 | 0 | 8.4 | 2024-07-09 | 26.2 | 0 | 8.2 | 2023-07-09 | 24.1 | 0 | 6.1 | 2022-07-09 | 20.3 | 0 | 2.3 | 2021-07-09 | 18.3 | 0 | 0.3 | 2020-07-09 | 34.2 | 0 | 16.2 | 2019-07-09 | 28.5 | 0 | 10.5 | 2018-07-09 | 31.3 | 0 | 13.3 | 2017-07-09 | 23.2 | 0 | 5.2 | 2016-07-09 | 17.5 | 0.5 | 0 | 0.05 | 7.05
2025-07-09 | 27.3 | 0 | 9.3 | 2024-07-09 | 27.8 | 0 | 9.8 | 2023-07-09 | 25.3 | 0 | 7.3 | 2022-07-09 | 20.8 | 0 | 2.8 | 2021-07-09 | 18.5 | 0 | 0.5 | 2020-07-09 | 34.8 | 0 | 16.8 | 2019-07-09 | 28.6 | 0 | 10.6 | 2018-07-09 | 31.4 | 0 | 13.4 | 2017-07-09 | 23.4 | 0 | 5.4 | 2016-07-09 | 17.9 | 0.1 | 0 | 0.01 | 7.59
2025-07-09 | 25.7 | 0 | 7.7 | 2024-07-09 | 27.5 | 0 | 9.5 | 2023-07-09 | 26.5 | 0 | 8.5 | 2022-07-09 | 22.1 | 0 | 4.1 | 2021-07-09 | 19.3 | 0 | 1.3 | 2020-07-09 | 33.5 | 0 | 15.5 | 2019-07-09 | 29.5 | 0 | 11.5 | 2018-07-09 | 32.8 | 0 | 14.8 | 2017-07-09 | 23.1 | 0 | 5.1 | 2016-07-09 | 17.8 | 0.2 | 0 | 0.02 | 7.8
2025-07-09 | 25.6 | 0 | 7.6 | 2024-07-09 | 25.5 | 0 | 7.5 | 2023-07-09 | 26.5 | 0 | 8.5 | 2022-07-09 | 23 | 0 | 5 | 2021-07-09 | 19.8 | 0 | 1.8 | 2020-07-09 | 33.8 | 0 | 15.8 | 2019-07-09 | 29.6 | 0 | 11.6 | 2018-07-09 | 33.3 | 0 | 15.3 | 2017-07-09 | 21.2 | 0 | 3.2 | 2016-07-09 | 18.4 | 0 | 0.4 | 0 | 7.67
2025-07-09 | 24.9 | 0 | 6.9 | 2024-07-09 | 25.3 | 0 | 7.3 | 2023-07-09 | 26.3 | 0 | 8.3 | 2022-07-09 | 22.9 | 0 | 4.9 | 2021-07-09 | 20.7 | 0 | 2.7 | 2020-07-09 | 33.5 | 0 | 15.5 | 2019-07-09 | 29.4 | 0 | 11.4 | 2018-07-09 | 32.4 | 0 | 14.4 | 2017-07-09 | 22.4 | 0 | 4.4 | 2016-07-09 | 18.3 | 0 | 0.3 | 0 | 7.61
2025-07-09 | 22.4 | 0 | 4.4 | 2024-07-09 | 26.7 | 0 | 8.7 | 2023-07-09 | 25.9 | 0 | 7.9 | 2022-07-09 | 22.9 | 0 | 4.9 | 2021-07-09 | 20.9 | 0 | 2.9 | 2020-07-09 | 32.9 | 0 | 14.9 | 2019-07-09 | 29 | 0 | 11 | 2018-07-09 | 33.1 | 0 | 15.1 | 2017-07-09 | 21.7 | 0 | 3.7 | 2016-07-09 | 18.2 | 0 | 0.2 | 0 | 7.37
2025-07-09 | 20.2 | 0 | 2.2 | 2024-07-09 | 25.2 | 0 | 7.2 | 2023-07-09 | 25 | 0 | 7 | 2022-07-09 | 22.3 | 0 | 4.3 | 2021-07-09 | 20.9 | 0 | 2.9 | 2020-07-09 | 31.2 | 0 | 13.2 | 2019-07-09 | 28.2 | 0 | 10.2 | 2018-07-09 | 30.8 | 0 | 12.8 | 2017-07-09 | 20.9 | 0 | 2.9 | 2016-07-09 | 17.6 | 0.4 | 0 | 0.04 | 6.27
2025-07-09 | 20.1 | 0 | 2.1 | 2024-07-09 | 25.3 | 0 | 7.3 | 2023-07-09 | 24.3 | 0 | 6.3 | 2022-07-09 | 21.2 | 0 | 3.2 | 2021-07-09 | 19.9 | 0 | 1.9 | 2020-07-09 | 29.9 | 0 | 11.9 | 2019-07-09 | 26.2 | 0 | 8.2 | 2018-07-09 | 28.9 | 0 | 10.9 | 2017-07-09 | 17.1 | 0.9 | 0 | 2016-07-09 | 17.3 | 0.7 | 0 | 0.16 | 5.18
2025-07-09 | 19.8 | 0 | 1.8 | 2024-07-09 | 24.3 | 0 | 6.3 | 2023-07-09 | 23.7 | 0 | 5.7 | 2022-07-09 | 19.4 | 0 | 1.4 | 2021-07-09 | 18.4 | 0 | 0.4 | 2020-07-09 | 26.4 | 0 | 8.4 | 2019-07-09 | 23.2 | 0 | 5.2 | 2018-07-09 | 27.2 | 0 | 9.2 | 2017-07-09 | 16.6 | 1.4 | 0 | 2016-07-09 | 17 | 1 | 0 | 0.24 | 3.84
2025-07-09 | 19.4 | 0 | 1.4 | 2024-07-09 | 22.9 | 0 | 4.9 | 2023-07-09 | 22.9 | 0 | 4.9 | 2022-07-09 | 16.8 | 1.2 | 0 | 2021-07-09 | 17.5 | 0.5 | 0 | 2020-07-09 | 24.5 | 0 | 6.5 | 2019-07-09 | 22.9 | 0 | 4.9 | 2018-07-09 | 25.4 | 0 | 7.4 | 2017-07-09 | 16.5 | 1.5 | 0 | 2016-07-09 | 16.6 | 1.4 | 0 | 0.46 | 3
2025-07-09 | 19.4 | 0 | 1.4 | 2024-07-09 | 21.9 | 0 | 3.9 | 2023-07-09 | 21.8 | 0 | 3.8 | 2022-07-09 | 14.1 | 3.9 | 0 | 2021-07-09 | 16.5 | 1.5 | 0 | 2020-07-09 | 26 | 0 | 8 | 2019-07-09 | 21.3 | 0 | 3.3 | 2018-07-09 | 24.1 | 0 | 6.1 | 2017-07-09 | 15.9 | 2.1 | 0 | 2016-07-09 | 16.1 | 1.9 | 0 | 0.94 | 2.65
2025-07-09 | 19.2 | 0 | 1.2 | 2024-07-09 | 21.1 | 0 | 3.1 | 2023-07-09 | 20.9 | 0 | 2.9 | 2022-07-09 | 12.8 | 5.2 | 0 | 2021-07-09 | 15 | 3 | 0 | 2020-07-09 | 25.4 | 0 | 7.4 | 2019-07-09 | 20.6 | 0 | 2.6 | 2018-07-09 | 23.2 | 0 | 5.2 | 2017-07-09 | 16.5 | 1.5 | 0 | 2016-07-09 | 16.1 | 1.9 | 0 | 1.16 | 2.24
2025-07-10 | 18.5 | 0 | 0.5 | 2024-07-10 | 18.6 | 0 | 0.6 | 2023-07-10 | 20.1 | 0 | 2.1 | 2022-07-10 | 13.3 | 4.7 | 0 | 2021-07-10 | 15.2 | 2.8 | 0 | 2020-07-10 | 22.7 | 0 | 4.7 | 2019-07-10 | 19.9 | 0 | 1.9 | 2018-07-10 | 21.1 | 0 | 3.1 | 2017-07-10 | 16.5 | 1.5 | 0 | 2016-07-10 | 15.6 | 2.4 | 0 | 1.14 | 1.29
2025-07-10 | 18.1 | 0 | 0.1 | 2024-07-10 | 19 | 0 | 1 | 2023-07-10 | 19.9 | 0 | 1.9 | 2022-07-10 | 11.8 | 6.2 | 0 | 2021-07-10 | 14.4 | 3.6 | 0 | 2020-07-10 | 22.1 | 0 | 4.1 | 2019-07-10 | 18.8 | 0 | 0.8 | 2018-07-10 | 20.8 | 0 | 2.8 | 2017-07-10 | 16.6 | 1.4 | 0 | 2016-07-10 | 15.3 | 2.7 | 0 | 1.39 | 1.07
2025-07-10 | 16.8 | 1.2 | 0 | 2024-07-10 | 19.2 | 0 | 1.2 | 2023-07-10 | 19.4 | 0 | 1.4 | 2022-07-10 | 13.8 | 4.2 | 0 | 2021-07-10 | 13.3 | 4.7 | 0 | 2020-07-10 | 22.3 | 0 | 4.3 | 2019-07-10 | 18.6 | 0 | 0.6 | 2018-07-10 | 19.4 | 0 | 1.4 | 2017-07-10 | 16.9 | 1.1 | 0 | 2016-07-10 | 15.2 | 2.8 | 0 | 1.4 | 0.89
2025-07-10 | 17.3 | 0.7 | 0 | 2024-07-10 | 18 | 0 | 0 | 2023-07-10 | 19.6 | 0 | 1.6 | 2022-07-10 | 13.6 | 4.4 | 0 | 2021-07-10 | 11.9 | 6.1 | 0 | 2020-07-10 | 22.8 | 0 | 4.8 | 2019-07-10 | 17.8 | 0.2 | 0 | 2018-07-10 | 18.9 | 0 | 0.9 | 2017-07-10 | 16.7 | 1.3 | 0 | 2016-07-10 | 14.8 | 3.2 | 0 | 1.59 | 0.73
2025-07-10 | 16.6 | 1.4 | 0 | 2024-07-10 | 19.3 | 0 | 1.3 | 2023-07-10 | 19.4 | 0 | 1.4 | 2022-07-10 | 12.8 | 5.2 | 0 | 2021-07-10 | 11.5 | 6.5 | 0 | 2020-07-10 | 22.2 | 0 | 4.2 | 2019-07-10 | 16.8 | 1.2 | 0 | 2018-07-10 | 18 | 0 | 0 | 2017-07-10 | 16.7 | 1.3 | 0 | 2016-07-10 | 14.7 | 3.3 | 0 | 1.89 | 0.69
2025-07-10 | 16.5 | 1.5 | 0 | 2024-07-10 | 19.5 | 0 | 1.5 | 2023-07-10 | 19.8 | 0 | 1.8 | 2022-07-10 | 12.3 | 5.7 | 0 | 2021-07-10 | 12.4 | 5.6 | 0 | 2020-07-10 | 21.2 | 0 | 3.2 | 2019-07-10 | 16.8 | 1.2 | 0 | 2018-07-10 | 19.5 | 0 | 1.5 | 2017-07-10 | 16.5 | 1.5 | 0 | 2016-07-10 | 14.6 | 3.4 | 0 | 1.89 | 0.8
2025-07-10 | 18.8 | 0 | 0.8 | 2024-07-10 | 20.3 | 0 | 2.3 | 2023-07-10 | 20.2 | 0 | 2.2 | 2022-07-10 | 14.9 | 3.1 | 0 | 2021-07-10 | 14.8 | 3.2 | 0 | 2020-07-10 | 23.8 | 0 | 5.8 | 2019-07-10 | 17.9 | 0.1 | 0 | 2018-07-10 | 20.7 | 0 | 2.7 | 2017-07-10 | 16.7 | 1.3 | 0 | 2016-07-10 | 14.7 | 3.3 | 0 | 1.1 | 1.38
2025-07-10 | 20 | 0 | 2 | 2024-07-10 | 20.6 | 0 | 2.6 | 2023-07-10 | 21.1 | 0 | 3.1 | 2022-07-10 | 17.1 | 0.9 | 0 | 2021-07-10 | 17.5 | 0.5 | 0 | 2020-07-10 | 25.7 | 0 | 7.7 | 2019-07-10 | 20.7 | 0 | 2.7 | 2018-07-10 | 23.1 | 0 | 5.1 | 2017-07-10 | 17.2 | 0.8 | 0 | 2016-07-10 | 15.2 | 2.8 | 0 | 0.5 | 2.32
2025-07-10 | 22 | 0 | 4 | 2024-07-10 | 20.9 | 0 | 2.9 | 2023-07-10 | 22.1 | 0 | 4.1 | 2022-07-10 | 19.3 | 0 | 1.3 | 2021-07-10 | 19.5 | 0 | 1.5 | 2020-07-10 | 28.2 | 0 | 10.2 | 2019-07-10 | 23.1 | 0 | 5.1 | 2018-07-10 | 24.4 | 0 | 6.4 | 2017-07-10 | 18.7 | 0 | 0.7 | 2016-07-10 | 15.3 | 2.7 | 0 | 0.27 | 3.62
2025-07-10 | 23.2 | 0 | 5.2 | 2024-07-10 | 21.1 | 0 | 3.1 | 2023-07-10 | 23.8 | 0 | 5.8 | 2022-07-10 | 21.6 | 0 | 3.6 | 2021-07-10 | 22 | 0 | 4 | 2020-07-10 | 30.2 | 0 | 12.2 | 2019-07-10 | 25.1 | 0 | 7.1 | 2018-07-10 | 26.2 | 0 | 8.2 | 2017-07-10 | 20.8 | 0 | 2.8 | 2016-07-10 | 16.1 | 1.9 | 0 | 0.19 | 5.2
2025-07-10 | 24.4 | 0 | 6.4 | 2024-07-10 | 21.2 | 0 | 3.2 | 2023-07-10 | 24.1 | 0 | 6.1 | 2022-07-10 | 24 | 0 | 6 | 2021-07-10 | 23.1 | 0 | 5.1 | 2020-07-10 | 32 | 0 | 14 | 2019-07-10 | 27.2 | 0 | 9.2 | 2018-07-10 | 26.9 | 0 | 8.9 | 2017-07-10 | 21.8 | 0 | 3.8 | 2016-07-10 | 17 | 1 | 0 | 0.1 | 6.27
2025-07-10 | 25.7 | 0 | 7.7 | 2024-07-10 | 20.8 | 0 | 2.8 | 2023-07-10 | 24.5 | 0 | 6.5 | 2022-07-10 | 24.8 | 0 | 6.8 | 2021-07-10 | 24.7 | 0 | 6.7 | 2020-07-10 | 33.5 | 0 | 15.5 | 2019-07-10 | 28.3 | 0 | 10.3 | 2018-07-10 | 27.5 | 0 | 9.5 | 2017-07-10 | 21.5 | 0 | 3.5 | 2016-07-10 | 18.6 | 0 | 0.6 | 0 | 6.99
2025-07-10 | 26.1 | 0 | 8.1 | 2024-07-10 | 20.9 | 0 | 2.9 | 2023-07-10 | 24.5 | 0 | 6.5 | 2022-07-10 | 26.8 | 0 | 8.8 | 2021-07-10 | 25.3 | 0 | 7.3 | 2020-07-10 | 34.8 | 0 | 16.8 | 2019-07-10 | 29.1 | 0 | 11.1 | 2018-07-10 | 28 | 0 | 10 | 2017-07-10 | 21.4 | 0 | 3.4 | 2016-07-10 | 19.6 | 0 | 1.6 | 0 | 7.65
2025-07-10 | 27.4 | 0 | 9.4 | 2024-07-10 | 21 | 0 | 3 | 2023-07-10 | 24.8 | 0 | 6.8 | 2022-07-10 | 27 | 0 | 9 | 2021-07-10 | 24.8 | 0 | 6.8 | 2020-07-10 | 34.7 | 0 | 16.7 | 2019-07-10 | 30.2 | 0 | 12.2 | 2018-07-10 | 28.7 | 0 | 10.7 | 2017-07-10 | 21.9 | 0 | 3.9 | 2016-07-10 | 20.4 | 0 | 2.4 | 0 | 8.09
2025-07-10 | 26.8 | 0 | 8.8 | 2024-07-10 | 20.7 | 0 | 2.7 | 2023-07-10 | 26.6 | 0 | 8.6 | 2022-07-10 | 27.1 | 0 | 9.1 | 2021-07-10 | 25.5 | 0 | 7.5 | 2020-07-10 | 34.2 | 0 | 16.2 | 2019-07-10 | 29.9 | 0 | 11.9 | 2018-07-10 | 28.3 | 0 | 10.3 | 2017-07-10 | 22.6 | 0 | 4.6 | 2016-07-10 | 19.8 | 0 | 1.8 | 0 | 8.15
2025-07-10 | 27 | 0 | 9 | 2024-07-10 | 20.9 | 0 | 2.9 | 2023-07-10 | 26.8 | 0 | 8.8 | 2022-07-10 | 28.2 | 0 | 10.2 | 2021-07-10 | 26.1 | 0 | 8.1 | 2020-07-10 | 36.4 | 0 | 18.4 | 2019-07-10 | 30.2 | 0 | 12.2 | 2018-07-10 | 26.9 | 0 | 8.9 | 2017-07-10 | 22 | 0 | 4 | 2016-07-10 | 20.3 | 0 | 2.3 | 0 | 8.48
2025-07-10 | 27 | 0 | 9 | 2024-07-10 | 20.5 | 0 | 2.5 | 2023-07-10 | 25.8 | 0 | 7.8 | 2022-07-10 | 27.3 | 0 | 9.3 | 2021-07-10 | 26.3 | 0 | 8.3 | 2020-07-10 | 35.4 | 0 | 17.4 | 2019-07-10 | 30 | 0 | 12 | 2018-07-10 | 27.7 | 0 | 9.7 | 2017-07-10 | 22.5 | 0 | 4.5 | 2016-07-10 | 20.9 | 0 | 2.9 | 0 | 8.34
2025-07-10 | 27.4 | 0 | 9.4 | 2024-07-10 | 20.2 | 0 | 2.2 | 2023-07-10 | 24.2 | 0 | 6.2 | 2022-07-10 | 25.4 | 0 | 7.4 | 2021-07-10 | 25.6 | 0 | 7.6 | 2020-07-10 | 33.2 | 0 | 15.2 | 2019-07-10 | 28.4 | 0 | 10.4 | 2018-07-10 | 26.9 | 0 | 8.9 | 2017-07-10 | 23.9 | 0 | 5.9 | 2016-07-10 | 20.3 | 0 | 2.3 | 0 | 7.55
2025-07-10 | 26.5 | 0 | 8.5 | 2024-07-10 | 19.5 | 0 | 1.5 | 2023-07-10 | 23 | 0 | 5 | 2022-07-10 | 24.9 | 0 | 6.9 | 2021-07-10 | 25 | 0 | 7 | 2020-07-10 | 31.5 | 0 | 13.5 | 2019-07-10 | 28.1 | 0 | 10.1 | 2018-07-10 | 26.1 | 0 | 8.1 | 2017-07-10 | 23.8 | 0 | 5.8 | 2016-07-10 | 20.9 | 0 | 2.9 | 0 | 6.93
2025-07-10 | 25.4 | 0 | 7.4 | 2024-07-10 | 19.4 | 0 | 1.4 | 2023-07-10 | 21.6 | 0 | 3.6 | 2022-07-10 | 22.8 | 0 | 4.8 | 2021-07-10 | 22.5 | 0 | 4.5 | 2020-07-10 | 30.1 | 0 | 12.1 | 2019-07-10 | 25.4 | 0 | 7.4 | 2018-07-10 | 23.5 | 0 | 5.5 | 2017-07-10 | 23.1 | 0 | 5.1 | 2016-07-10 | 20 | 0 | 2 | 0 | 5.38
2025-07-10 | 23.3 | 0 | 5.3 | 2024-07-10 | 19.6 | 0 | 1.6 | 2023-07-10 | 21.2 | 0 | 3.2 | 2022-07-10 | 22 | 0 | 4 | 2021-07-10 | 19.8 | 0 | 1.8 | 2020-07-10 | 27.5 | 0 | 9.5 | 2019-07-10 | 22.4 | 0 | 4.4 | 2018-07-10 | 22.3 | 0 | 4.3 | 2017-07-10 | 21 | 0 | 3 | 2016-07-10 | 17.2 | 0.8 | 0 | 0.08 | 3.71
2025-07-10 | 22 | 0 | 4 | 2024-07-10 | 19.2 | 0 | 1.2 | 2023-07-10 | 19.8 | 0 | 1.8 | 2022-07-10 | 20.7 | 0 | 2.7 | 2021-07-10 | 19.3 | 0 | 1.3 | 2020-07-10 | 28 | 0 | 10 | 2019-07-10 | 21.6 | 0 | 3.6 | 2018-07-10 | 21.5 | 0 | 3.5 | 2017-07-10 | 19.9 | 0 | 1.9 | 2016-07-10 | 16.9 | 1.1 | 0 | 0.11 | 3
2025-07-10 | 21 | 0 | 3 | 2024-07-10 | 18.8 | 0 | 0.8 | 2023-07-10 | 19.1 | 0 | 1.1 | 2022-07-10 | 19.6 | 0 | 1.6 | 2021-07-10 | 18.6 | 0 | 0.6 | 2020-07-10 | 25.6 | 0 | 7.6 | 2019-07-10 | 21.1 | 0 | 3.1 | 2018-07-10 | 20.2 | 0 | 2.2 | 2017-07-10 | 18.9 | 0 | 0.9 | 2016-07-10 | 13.8 | 4.2 | 0 | 0.42 | 2.09
2025-07-10 | 20.3 | 0 | 2.3 | 2024-07-10 | 18.8 | 0 | 0.8 | 2023-07-10 | 18.9 | 0 | 0.9 | 2022-07-10 | 18.6 | 0 | 0.6 | 2021-07-10 | 18.4 | 0 | 0.4 | 2020-07-10 | 25.2 | 0 | 7.2 | 2019-07-10 | 20.4 | 0 | 2.4 | 2018-07-10 | 19.5 | 0 | 1.5 | 2017-07-10 | 19 | 0 | 1 | 2016-07-10 | 14.4 | 3.6 | 0 | 0.36 | 1.71
2025-07-11 | 19.3 | 0 | 1.3 | 2024-07-11 | 18.7 | 0 | 0.7 | 2023-07-11 | 18.3 | 0 | 0.3 | 2022-07-11 | 18 | 0 | 0 | 2021-07-11 | 17.2 | 0.8 | 0 | 2020-07-11 | 24.6 | 0 | 6.6 | 2019-07-11 | 22.1 | 0 | 4.1 | 2018-07-11 | 18.3 | 0 | 0.3 | 2017-07-11 | 17.9 | 0.1 | 0 | 2016-07-11 | 13.9 | 4.1 | 0 | 0.5 | 1.33
2025-07-11 | 19 | 0 | 1 | 2024-07-11 | 18.5 | 0 | 0.5 | 2023-07-11 | 18 | 0 | 0 | 2022-07-11 | 17.1 | 0.9 | 0 | 2021-07-11 | 16.2 | 1.8 | 0 | 2020-07-11 | 24.1 | 0 | 6.1 | 2019-07-11 | 20.8 | 0 | 2.8 | 2018-07-11 | 17.7 | 0.3 | 0 | 2017-07-11 | 17.6 | 0.4 | 0 | 2016-07-11 | 12.4 | 5.6 | 0 | 0.9 | 1.04
2025-07-11 | 18.2 | 0 | 0.2 | 2024-07-11 | 18.8 | 0 | 0.8 | 2023-07-11 | 18.3 | 0 | 0.3 | 2022-07-11 | 16.2 | 1.8 | 0 | 2021-07-11 | 16 | 2 | 0 | 2020-07-11 | 22.1 | 0 | 4.1 | 2019-07-11 | 21.2 | 0 | 3.2 | 2018-07-11 | 16.6 | 1.4 | 0 | 2017-07-11 | 17 | 1 | 0 | 2016-07-11 | 12.6 | 5.4 | 0 | 1.16 | 0.86
2025-07-11 | 17.5 | 0.5 | 0 | 2024-07-11 | 18.9 | 0 | 0.9 | 2023-07-11 | 18.2 | 0 | 0.2 | 2022-07-11 | 16.4 | 1.6 | 0 | 2021-07-11 | 15.4 | 2.6 | 0 | 2020-07-11 | 21.9 | 0 | 3.9 | 2019-07-11 | 20.2 | 0 | 2.2 | 2018-07-11 | 15.3 | 2.7 | 0 | 2017-07-11 | 16.9 | 1.1 | 0 | 2016-07-11 | 12.1 | 5.9 | 0 | 1.44 | 0.72
2025-07-11 | 15.8 | 2.2 | 0 | 2024-07-11 | 18.9 | 0 | 0.9 | 2023-07-11 | 18.5 | 0 | 0.5 | 2022-07-11 | 16.3 | 1.7 | 0 | 2021-07-11 | 13.6 | 4.4 | 0 | 2020-07-11 | 21.5 | 0 | 3.5 | 2019-07-11 | 19.7 | 0 | 1.7 | 2018-07-11 | 13.6 | 4.4 | 0 | 2017-07-11 | 17.6 | 0.4 | 0 | 2016-07-11 | 12.7 | 5.3 | 0 | 1.84 | 0.66
2025-07-11 | 17.2 | 0.8 | 0 | 2024-07-11 | 18.9 | 0 | 0.9 | 2023-07-11 | 18.7 | 0 | 0.7 | 2022-07-11 | 15.8 | 2.2 | 0 | 2021-07-11 | 13.4 | 4.6 | 0 | 2020-07-11 | 21.7 | 0 | 3.7 | 2019-07-11 | 19.9 | 0 | 1.9 | 2018-07-11 | 14.1 | 3.9 | 0 | 2017-07-11 | 18.2 | 0 | 0.2 | 2016-07-11 | 11.9 | 6.1 | 0 | 1.76 | 0.74
2025-07-11 | 19.4 | 0 | 1.4 | 2024-07-11 | 18.6 | 0 | 0.6 | 2023-07-11 | 18.9 | 0 | 0.9 | 2022-07-11 | 16.6 | 1.4 | 0 | 2021-07-11 | 15.2 | 2.8 | 0 | 2020-07-11 | 22.1 | 0 | 4.1 | 2019-07-11 | 20.6 | 0 | 2.6 | 2018-07-11 | 16.3 | 1.7 | 0 | 2017-07-11 | 18.9 | 0 | 0.9 | 2016-07-11 | 14.4 | 3.6 | 0 | 0.95 | 1.05
2025-07-11 | 21 | 0 | 3 | 2024-07-11 | 18.7 | 0 | 0.7 | 2023-07-11 | 19.1 | 0 | 1.1 | 2022-07-11 | 18.4 | 0 | 0.4 | 2021-07-11 | 17.4 | 0.6 | 0 | 2020-07-11 | 22.2 | 0 | 4.2 | 2019-07-11 | 22.1 | 0 | 4.1 | 2018-07-11 | 18.8 | 0 | 0.8 | 2017-07-11 | 19.6 | 0 | 1.6 | 2016-07-11 | 17.6 | 0.4 | 0 | 0.1 | 1.59
2025-07-11 | 22.8 | 0 | 4.8 | 2024-07-11 | 18.9 | 0 | 0.9 | 2023-07-11 | 21.8 | 0 | 3.8 | 2022-07-11 | 21.2 | 0 | 3.2 | 2021-07-11 | 20.1 | 0 | 2.1 | 2020-07-11 | 22.3 | 0 | 4.3 | 2019-07-11 | 22.7 | 0 | 4.7 | 2018-07-11 | 19.8 | 0 | 1.8 | 2017-07-11 | 21.3 | 0 | 3.3 | 2016-07-11 | 20.2 | 0 | 2.2 | 0 | 3.11
2025-07-11 | 24 | 0 | 6 | 2024-07-11 | 19.7 | 0 | 1.7 | 2023-07-11 | 24 | 0 | 6 | 2022-07-11 | 23.1 | 0 | 5.1 | 2021-07-11 | 21.9 | 0 | 3.9 | 2020-07-11 | 22.5 | 0 | 4.5 | 2019-07-11 | 23.4 | 0 | 5.4 | 2018-07-11 | 21.5 | 0 | 3.5 | 2017-07-11 | 22.7 | 0 | 4.7 | 2016-07-11 | 22.2 | 0 | 4.2 | 0 | 4.5
2025-07-11 | 25.5 | 0 | 7.5 | 2024-07-11 | 20.1 | 0 | 2.1 | 2023-07-11 | 25.3 | 0 | 7.3 | 2022-07-11 | 23.6 | 0 | 5.6 | 2021-07-11 | 23.4 | 0 | 5.4 | 2020-07-11 | 22.6 | 0 | 4.6 | 2019-07-11 | 24 | 0 | 6 | 2018-07-11 | 23.2 | 0 | 5.2 | 2017-07-11 | 23 | 0 | 5 | 2016-07-11 | 23.4 | 0 | 5.4 | 0 | 5.41
2025-07-11 | 27.3 | 0 | 9.3 | 2024-07-11 | 20.1 | 0 | 2.1 | 2023-07-11 | 27.3 | 0 | 9.3 | 2022-07-11 | 26.5 | 0 | 8.5 | 2021-07-11 | 24.7 | 0 | 6.7 | 2020-07-11 | 23.2 | 0 | 5.2 | 2019-07-11 | 25.6 | 0 | 7.6 | 2018-07-11 | 24.5 | 0 | 6.5 | 2017-07-11 | 24.3 | 0 | 6.3 | 2016-07-11 | 25.2 | 0 | 7.2 | 0 | 6.87
2025-07-11 | 28.7 | 0 | 10.7 | 2024-07-11 | 20.8 | 0 | 2.8 | 2023-07-11 | 28.6 | 0 | 10.6 | 2022-07-11 | 28.1 | 0 | 10.1 | 2021-07-11 | 25.3 | 0 | 7.3 | 2020-07-11 | 23.8 | 0 | 5.8 | 2019-07-11 | 28 | 0 | 10 | 2018-07-11 | 25.2 | 0 | 7.2 | 2017-07-11 | 24.6 | 0 | 6.6 | 2016-07-11 | 25.7 | 0 | 7.7 | 0 | 7.88
2025-07-11 | 29 | 0 | 11 | 2024-07-11 | 20.9 | 0 | 2.9 | 2023-07-11 | 28.2 | 0 | 10.2 | 2022-07-11 | 28.5 | 0 | 10.5 | 2021-07-11 | 25.9 | 0 | 7.9 | 2020-07-11 | 24.5 | 0 | 6.5 | 2019-07-11 | 29.1 | 0 | 11.1 | 2018-07-11 | 25.5 | 0 | 7.5 | 2017-07-11 | 26.7 | 0 | 8.7 | 2016-07-11 | 27.2 | 0 | 9.2 | 0 | 8.55
2025-07-11 | 29.1 | 0 | 11.1 | 2024-07-11 | 20.8 | 0 | 2.8 | 2023-07-11 | 31.3 | 0 | 13.3 | 2022-07-11 | 28.9 | 0 | 10.9 | 2021-07-11 | 26 | 0 | 8 | 2020-07-11 | 25.2 | 0 | 7.2 | 2019-07-11 | 28.4 | 0 | 10.4 | 2018-07-11 | 25.6 | 0 | 7.6 | 2017-07-11 | 27.3 | 0 | 9.3 | 2016-07-11 | 26.9 | 0 | 8.9 | 0 | 8.95
2025-07-11 | 30.1 | 0 | 12.1 | 2024-07-11 | 21.1 | 0 | 3.1 | 2023-07-11 | 31.4 | 0 | 13.4 | 2022-07-11 | 28.8 | 0 | 10.8 | 2021-07-11 | 25.6 | 0 | 7.6 | 2020-07-11 | 26.6 | 0 | 8.6 | 2019-07-11 | 27.9 | 0 | 9.9 | 2018-07-11 | 26.7 | 0 | 8.7 | 2017-07-11 | 23.1 | 0 | 5.1 | 2016-07-11 | 27.3 | 0 | 9.3 | 0 | 8.86
2025-07-11 | 30.1 | 0 | 12.1 | 2024-07-11 | 21.6 | 0 | 3.6 | 2023-07-11 | 31.1 | 0 | 13.1 | 2022-07-11 | 28 | 0 | 10 | 2021-07-11 | 25.4 | 0 | 7.4 | 2020-07-11 | 27.4 | 0 | 9.4 | 2019-07-11 | 19.2 | 0 | 1.2 | 2018-07-11 | 26.5 | 0 | 8.5 | 2017-07-11 | 20.8 | 0 | 2.8 | 2016-07-11 | 27.6 | 0 | 9.6 | 0 | 7.77
2025-07-11 | 29.5 | 0 | 11.5 | 2024-07-11 | 21.4 | 0 | 3.4 | 2023-07-11 | 25.6 | 0 | 7.6 | 2022-07-11 | 27.4 | 0 | 9.4 | 2021-07-11 | 24.9 | 0 | 6.9 | 2020-07-11 | 26 | 0 | 8 | 2019-07-11 | 19.5 | 0 | 1.5 | 2018-07-11 | 25.6 | 0 | 7.6 | 2017-07-11 | 21.7 | 0 | 3.7 | 2016-07-11 | 27.5 | 0 | 9.5 | 0 | 6.91
2025-07-11 | 29.3 | 0 | 11.3 | 2024-07-11 | 21.1 | 0 | 3.1 | 2023-07-11 | 21.2 | 0 | 3.2 | 2022-07-11 | 26 | 0 | 8 | 2021-07-11 | 24.4 | 0 | 6.4 | 2020-07-11 | 25.2 | 0 | 7.2 | 2019-07-11 | 19.6 | 0 | 1.6 | 2018-07-11 | 25.3 | 0 | 7.3 | 2017-07-11 | 21.3 | 0 | 3.3 | 2016-07-11 | 26.6 | 0 | 8.6 | 0 | 6
2025-07-11 | 28 | 0 | 10 | 2024-07-11 | 20.5 | 0 | 2.5 | 2023-07-11 | 21.7 | 0 | 3.7 | 2022-07-11 | 23.5 | 0 | 5.5 | 2021-07-11 | 22.5 | 0 | 4.5 | 2020-07-11 | 25.1 | 0 | 7.1 | 2019-07-11 | 20.3 | 0 | 2.3 | 2018-07-11 | 24 | 0 | 6 | 2017-07-11 | 19.9 | 0 | 1.9 | 2016-07-11 | 24.6 | 0 | 6.6 | 0 | 5.01
2025-07-11 | 25.6 | 0 | 7.6 | 2024-07-11 | 19.8 | 0 | 1.8 | 2023-07-11 | 17.8 | 0.2 | 0 | 2022-07-11 | 24.5 | 0 | 6.5 | 2021-07-11 | 21.6 | 0 | 3.6 | 2020-07-11 | 21.4 | 0 | 3.4 | 2019-07-11 | 19.5 | 0 | 1.5 | 2018-07-11 | 20.7 | 0 | 2.7 | 2017-07-11 | 19.5 | 0 | 1.5 | 2016-07-11 | 22.6 | 0 | 4.6 | 0.02 | 3.32
2025-07-11 | 22.9 | 0 | 4.9 | 2024-07-11 | 19.4 | 0 | 1.4 | 2023-07-11 | 18 | 0 | 0 | 2022-07-11 | 23.2 | 0 | 5.2 | 2021-07-11 | 20.6 | 0 | 2.6 | 2020-07-11 | 20.5 | 0 | 2.5 | 2019-07-11 | 18.9 | 0 | 0.9 | 2018-07-11 | 18.4 | 0 | 0.4 | 2017-07-11 | 18.8 | 0 | 0.8 | 2016-07-11 | 20 | 0 | 2 | 0 | 2.07
2025-07-11 | 21.9 | 0 | 3.9 | 2024-07-11 | 19.4 | 0 | 1.4 | 2023-07-11 | 17.7 | 0.3 | 0 | 2022-07-11 | 23.1 | 0 | 5.1 | 2021-07-11 | 18.2 | 0 | 0.2 | 2020-07-11 | 20.8 | 0 | 2.8 | 2019-07-11 | 19.5 | 0 | 1.5 | 2018-07-11 | 16.1 | 1.9 | 0 | 2017-07-11 | 18.1 | 0 | 0.1 | 2016-07-11 | 19.8 | 0 | 1.8 | 0.22 | 1.68
2025-07-11 | 21.4 | 0 | 3.4 | 2024-07-11 | 19.6 | 0 | 1.6 | 2023-07-11 | 17.3 | 0.7 | 0 | 2022-07-11 | 22 | 0 | 4 | 2021-07-11 | 19.4 | 0 | 1.4 | 2020-07-11 | 21.1 | 0 | 3.1 | 2019-07-11 | 18.8 | 0 | 0.8 | 2018-07-11 | 15.5 | 2.5 | 0 | 2017-07-11 | 18 | 0 | 0 | 2016-07-11 | 19 | 0 | 1 | 0.32 | 1.53
2025-07-12 | 21.1 | 0 | 3.1 | 2024-07-12 | 19.7 | 0 | 1.7 | 2023-07-12 | 17 | 1 | 0 | 2022-07-12 | 18.9 | 0 | 0.9 | 2021-07-12 | 18.5 | 0 | 0.5 | 2020-07-12 | 21.3 | 0 | 3.3 | 2019-07-12 | 18.9 | 0 | 0.9 | 2018-07-12 | 16.6 | 1.4 | 0 | 2017-07-12 | 17.6 | 0.4 | 0 | 2016-07-12 | 18.8 | 0 | 0.8 | 0.28 | 1.12
2025-07-12 | 20.5 | 0 | 2.5 | 2024-07-12 | 19.5 | 0 | 1.5 | 2023-07-12 | 16.9 | 1.1 | 0 | 2022-07-12 | 19 | 0 | 1 | 2021-07-12 | 18.8 | 0 | 0.8 | 2020-07-12 | 20.9 | 0 | 2.9 | 2019-07-12 | 19.6 | 0 | 1.6 | 2018-07-12 | 16.9 | 1.1 | 0 | 2017-07-12 | 16.9 | 1.1 | 0 | 2016-07-12 | 18 | 0 | 0 | 0.33 | 1.03
2025-07-12 | 20.7 | 0 | 2.7 | 2024-07-12 | 19.4 | 0 | 1.4 | 2023-07-12 | 16.6 | 1.4 | 0 | 2022-07-12 | 19.5 | 0 | 1.5 | 2021-07-12 | 17.4 | 0.6 | 0 | 2020-07-12 | 21.1 | 0 | 3.1 | 2019-07-12 | 19.9 | 0 | 1.9 | 2018-07-12 | 15.4 | 2.6 | 0 | 2017-07-12 | 16.1 | 1.9 | 0 | 2016-07-12 | 16.8 | 1.2 | 0 | 0.77 | 1.06
2025-07-12 | 20 | 0 | 2 | 2024-07-12 | 19.2 | 0 | 1.2 | 2023-07-12 | 16 | 2 | 0 | 2022-07-12 | 19.8 | 0 | 1.8 | 2021-07-12 | 17.2 | 0.8 | 0 | 2020-07-12 | 21.3 | 0 | 3.3 | 2019-07-12 | 19.9 | 0 | 1.9 | 2018-07-12 | 16.8 | 1.2 | 0 | 2017-07-12 | 17.6 | 0.4 | 0 | 2016-07-12 | 15.9 | 2.1 | 0 | 0.65 | 1.02
2025-07-12 | 18.7 | 0 | 0.7 | 2024-07-12 | 19 | 0 | 1 | 2023-07-12 | 15.2 | 2.8 | 0 | 2022-07-12 | 19.6 | 0 | 1.6 | 2021-07-12 | 16.2 | 1.8 | 0 | 2020-07-12 | 21.1 | 0 | 3.1 | 2019-07-12 | 19.9 | 0 | 1.9 | 2018-07-12 | 16.6 | 1.4 | 0 | 2017-07-12 | 16.6 | 1.4 | 0 | 2016-07-12 | 14.3 | 3.7 | 0 | 1.11 | 0.83
2025-07-12 | 18.1 | 0 | 0.1 | 2024-07-12 | 18.9 | 0 | 0.9 | 2023-07-12 | 14.3 | 3.7 | 0 | 2022-07-12 | 19.4 | 0 | 1.4 | 2021-07-12 | 17.1 | 0.9 | 0 | 2020-07-12 | 21 | 0 | 3 | 2019-07-12 | 20.1 | 0 | 2.1 | 2018-07-12 | 16.5 | 1.5 | 0 | 2017-07-12 | 16.8 | 1.2 | 0 | 2016-07-12 | 13.8 | 4.2 | 0 | 1.15 | 0.75
2025-07-12 | 20.2 | 0 | 2.2 | 2024-07-12 | 19.4 | 0 | 1.4 | 2023-07-12 | 15.6 | 2.4 | 0 | 2022-07-12 | 19.8 | 0 | 1.8 | 2021-07-12 | 17.7 | 0.3 | 0 | 2020-07-12 | 20.6 | 0 | 2.6 | 2019-07-12 | 19.8 | 0 | 1.8 | 2018-07-12 | 17.8 | 0.2 | 0 | 2017-07-12 | 17.1 | 0.9 | 0 | 2016-07-12 | 17 | 1 | 0 | 0.48 | 0.98
2025-07-12 | 23.1 | 0 | 5.1 | 2024-07-12 | 21.2 | 0 | 3.2 | 2023-07-12 | 16.9 | 1.1 | 0 | 2022-07-12 | 20.6 | 0 | 2.6 | 2021-07-12 | 18.8 | 0 | 0.8 | 2020-07-12 | 20.5 | 0 | 2.5 | 2019-07-12 | 19.6 | 0 | 1.6 | 2018-07-12 | 19.2 | 0 | 1.2 | 2017-07-12 | 17.4 | 0.6 | 0 | 2016-07-12 | 19.7 | 0 | 1.7 | 0.17 | 1.87
2025-07-12 | 25.2 | 0 | 7.2 | 2024-07-12 | 22 | 0 | 4 | 2023-07-12 | 18.4 | 0 | 0.4 | 2022-07-12 | 22.3 | 0 | 4.3 | 2021-07-12 | 20.5 | 0 | 2.5 | 2020-07-12 | 21.1 | 0 | 3.1 | 2019-07-12 | 20.3 | 0 | 2.3 | 2018-07-12 | 20.7 | 0 | 2.7 | 2017-07-12 | 18 | 0 | 0 | 2016-07-12 | 22.5 | 0 | 4.5 | 0 | 3.1
2025-07-12 | 26.8 | 0 | 8.8 | 2024-07-12 | 24.2 | 0 | 6.2 | 2023-07-12 | 19.3 | 0 | 1.3 | 2022-07-12 | 24.4 | 0 | 6.4 | 2021-07-12 | 22.5 | 0 | 4.5 | 2020-07-12 | 22.2 | 0 | 4.2 | 2019-07-12 | 20.1 | 0 | 2.1 | 2018-07-12 | 23 | 0 | 5 | 2017-07-12 | 18.1 | 0 | 0.1 | 2016-07-12 | 23.7 | 0 | 5.7 | 0 | 4.43
2025-07-12 | 28.6 | 0 | 10.6 | 2024-07-12 | 24.1 | 0 | 6.1 | 2023-07-12 | 21.1 | 0 | 3.1 | 2022-07-12 | 25 | 0 | 7 | 2021-07-12 | 23.1 | 0 | 5.1 | 2020-07-12 | 22.3 | 0 | 4.3 | 2019-07-12 | 20.1 | 0 | 2.1 | 2018-07-12 | 23.9 | 0 | 5.9 | 2017-07-12 | 17.1 | 0.9 | 0 | 2016-07-12 | 25.2 | 0 | 7.2 | 0.09 | 5.14
2025-07-12 | 29.4 | 0 | 11.4 | 2024-07-12 | 25.7 | 0 | 7.7 | 2023-07-12 | 21.6 | 0 | 3.6 | 2022-07-12 | 26.5 | 0 | 8.5 | 2021-07-12 | 24.4 | 0 | 6.4 | 2020-07-12 | 23.3 | 0 | 5.3 | 2019-07-12 | 20.1 | 0 | 2.1 | 2018-07-12 | 25.1 | 0 | 7.1 | 2017-07-12 | 18.6 | 0 | 0.6 | 2016-07-12 | 26.4 | 0 | 8.4 | 0 | 6.11
2025-07-12 | 30.8 | 0 | 12.8 | 2024-07-12 | 26.5 | 0 | 8.5 | 2023-07-12 | 22.7 | 0 | 4.7 | 2022-07-12 | 26 | 0 | 8 | 2021-07-12 | 25.7 | 0 | 7.7 | 2020-07-12 | 24.2 | 0 | 6.2 | 2019-07-12 | 21 | 0 | 3 | 2018-07-12 | 26.8 | 0 | 8.8 | 2017-07-12 | 19.5 | 0 | 1.5 | 2016-07-12 | 26.8 | 0 | 8.8 | 0 | 7
2025-07-12 | 32.1 | 0 | 14.1 | 2024-07-12 | 26.2 | 0 | 8.2 | 2023-07-12 | 24.2 | 0 | 6.2 | 2022-07-12 | 16.7 | 1.3 | 0 | 2021-07-12 | 26.5 | 0 | 8.5 | 2020-07-12 | 25.6 | 0 | 7.6 | 2019-07-12 | 21.5 | 0 | 3.5 | 2018-07-12 | 28.2 | 0 | 10.2 | 2017-07-12 | 20.4 | 0 | 2.4 | 2016-07-12 | 28 | 0 | 10 | 0.13 | 7.07
2025-07-12 | 30.5 | 0 | 12.5 | 2024-07-12 | 26.3 | 0 | 8.3 | 2023-07-12 | 24.6 | 0 | 6.6 | 2022-07-12 | 21.1 | 0 | 3.1 | 2021-07-12 | 27.3 | 0 | 9.3 | 2020-07-12 | 25 | 0 | 7 | 2019-07-12 | 23.5 | 0 | 5.5 | 2018-07-12 | 28.2 | 0 | 10.2 | 2017-07-12 | 20.7 | 0 | 2.7 | 2016-07-12 | 28.6 | 0 | 10.6 | 0 | 7.58
2025-07-12 | 31.9 | 0 | 13.9 | 2024-07-12 | 26.8 | 0 | 8.8 | 2023-07-12 | 25.7 | 0 | 7.7 | 2022-07-12 | 22.7 | 0 | 4.7 | 2021-07-12 | 27.6 | 0 | 9.6 | 2020-07-12 | 26.4 | 0 | 8.4 | 2019-07-12 | 23.3 | 0 | 5.3 | 2018-07-12 | 28.3 | 0 | 10.3 | 2017-07-12 | 21.3 | 0 | 3.3 | 2016-07-12 | 28.8 | 0 | 10.8 | 0 | 8.28
2025-07-12 | 30.4 | 0 | 12.4 | 2024-07-12 | 26.4 | 0 | 8.4 | 2023-07-12 | 25.9 | 0 | 7.9 | 2022-07-12 | 24.2 | 0 | 6.2 | 2021-07-12 | 27.5 | 0 | 9.5 | 2020-07-12 | 27.2 | 0 | 9.2 | 2019-07-12 | 23.1 | 0 | 5.1 | 2018-07-12 | 28.6 | 0 | 10.6 | 2017-07-12 | 21 | 0 | 3 | 2016-07-12 | 29.3 | 0 | 11.3 | 0 | 8.36
2025-07-12 | 31.2 | 0 | 13.2 | 2024-07-12 | 26.6 | 0 | 8.6 | 2023-07-12 | 25.7 | 0 | 7.7 | 2022-07-12 | 23.4 | 0 | 5.4 | 2021-07-12 | 27.3 | 0 | 9.3 | 2020-07-12 | 26.4 | 0 | 8.4 | 2019-07-12 | 23.8 | 0 | 5.8 | 2018-07-12 | 28.4 | 0 | 10.4 | 2017-07-12 | 19.9 | 0 | 1.9 | 2016-07-12 | 29.3 | 0 | 11.3 | 0 | 8.2
2025-07-12 | 30.1 | 0 | 12.1 | 2024-07-12 | 26.8 | 0 | 8.8 | 2023-07-12 | 25.6 | 0 | 7.6 | 2022-07-12 | 22.5 | 0 | 4.5 | 2021-07-12 | 26.4 | 0 | 8.4 | 2020-07-12 | 26.1 | 0 | 8.1 | 2019-07-12 | 24 | 0 | 6 | 2018-07-12 | 27.8 | 0 | 9.8 | 2017-07-12 | 19 | 0 | 1 | 2016-07-12 | 28.2 | 0 | 10.2 | 0 | 7.65
2025-07-12 | 28.7 | 0 | 10.7 | 2024-07-12 | 25.5 | 0 | 7.5 | 2023-07-12 | 24.1 | 0 | 6.1 | 2022-07-12 | 21.5 | 0 | 3.5 | 2021-07-12 | 25.1 | 0 | 7.1 | 2020-07-12 | 25.1 | 0 | 7.1 | 2019-07-12 | 22.3 | 0 | 4.3 | 2018-07-12 | 24.8 | 0 | 6.8 | 2017-07-12 | 18.4 | 0 | 0.4 | 2016-07-12 | 26 | 0 | 8 | 0 | 6.15
2025-07-12 | 26.8 | 0 | 8.8 | 2024-07-12 | 21.9 | 0 | 3.9 | 2023-07-12 | 21.6 | 0 | 3.6 | 2022-07-12 | 20.1 | 0 | 2.1 | 2021-07-12 | 22.9 | 0 | 4.9 | 2020-07-12 | 23.4 | 0 | 5.4 | 2019-07-12 | 20.6 | 0 | 2.6 | 2018-07-12 | 22.3 | 0 | 4.3 | 2017-07-12 | 17.5 | 0.5 | 0 | 2016-07-12 | 23.5 | 0 | 5.5 | 0.05 | 4.11
2025-07-12 | 25.3 | 0 | 7.3 | 2024-07-12 | 22.3 | 0 | 4.3 | 2023-07-12 | 20.1 | 0 | 2.1 | 2022-07-12 | 19.6 | 0 | 1.6 | 2021-07-12 | 22.4 | 0 | 4.4 | 2020-07-12 | 22.8 | 0 | 4.8 | 2019-07-12 | 19.7 | 0 | 1.7 | 2018-07-12 | 18.4 | 0 | 0.4 | 2017-07-12 | 16.2 | 1.8 | 0 | 2016-07-12 | 22 | 0 | 4 | 0.18 | 3.06
2025-07-12 | 24.5 | 0 | 6.5 | 2024-07-12 | 21.7 | 0 | 3.7 | 2023-07-12 | 19.5 | 0 | 1.5 | 2022-07-12 | 19.1 | 0 | 1.1 | 2021-07-12 | 22 | 0 | 4 | 2020-07-12 | 21.4 | 0 | 3.4 | 2019-07-12 | 18 | 0 | 0 | 2018-07-12 | 20.3 | 0 | 2.3 | 2017-07-12 | 15.6 | 2.4 | 0 | 2016-07-12 | 21.3 | 0 | 3.3 | 0.24 | 2.58
2025-07-12 | 23.5 | 0 | 5.5 | 2024-07-12 | 21.1 | 0 | 3.1 | 2023-07-12 | 18.4 | 0 | 0.4 | 2022-07-12 | 17.9 | 0.1 | 0 | 2021-07-12 | 21.1 | 0 | 3.1 | 2020-07-12 | 20.2 | 0 | 2.2 | 2019-07-12 | 18.4 | 0 | 0.4 | 2018-07-12 | 18.7 | 0 | 0.7 | 2017-07-12 | 15.2 | 2.8 | 0 | 2016-07-12 | 20.7 | 0 | 2.7 | 0.29 | 1.81
2025-07-13 | 23.3 | 0 | 5.3 | 2024-07-13 | 20.6 | 0 | 2.6 | 2023-07-13 | 18.1 | 0 | 0.1 | 2022-07-13 | 17.3 | 0.7 | 0 | 2021-07-13 | 20.4 | 0 | 2.4 | 2020-07-13 | 18.5 | 0 | 0.5 | 2019-07-13 | 18 | 0 | 0 | 2018-07-13 | 18.6 | 0 | 0.6 | 2017-07-13 | 14.7 | 3.3 | 0 | 2016-07-13 | 20.9 | 0 | 2.9 | 0.4 | 1.44
2025-07-13 | 23.6 | 0 | 5.6 | 2024-07-13 | 20.2 | 0 | 2.2 | 2023-07-13 | 17.8 | 0.2 | 0 | 2022-07-13 | 14.9 | 3.1 | 0 | 2021-07-13 | 19.8 | 0 | 1.8 | 2020-07-13 | 18.7 | 0 | 0.7 | 2019-07-13 | 17.1 | 0.9 | 0 | 2018-07-13 | 16.5 | 1.5 | 0 | 2017-07-13 | 14.2 | 3.8 | 0 | 2016-07-13 | 20.9 | 0 | 2.9 | 0.95 | 1.32
2025-07-13 | 23.2 | 0 | 5.2 | 2024-07-13 | 20 | 0 | 2 | 2023-07-13 | 19.1 | 0 | 1.1 | 2022-07-13 | 15.1 | 2.9 | 0 | 2021-07-13 | 20 | 0 | 2 | 2020-07-13 | 17.1 | 0.9 | 0 | 2019-07-13 | 17.6 | 0.4 | 0 | 2018-07-13 | 14.8 | 3.2 | 0 | 2017-07-13 | 13.7 | 4.3 | 0 | 2016-07-13 | 19.6 | 0 | 1.6 | 1.17 | 1.19
2025-07-13 | 22.6 | 0 | 4.6 | 2024-07-13 | 20 | 0 | 2 | 2023-07-13 | 16.9 | 1.1 | 0 | 2022-07-13 | 14 | 4 | 0 | 2021-07-13 | 19.5 | 0 | 1.5 | 2020-07-13 | 18.6 | 0 | 0.6 | 2019-07-13 | 16.8 | 1.2 | 0 | 2018-07-13 | 14.3 | 3.7 | 0 | 2017-07-13 | 12.1 | 5.9 | 0 | 2016-07-13 | 18.6 | 0 | 0.6 | 1.59 | 0.93
2025-07-13 | 22.5 | 0 | 4.5 | 2024-07-13 | 20.4 | 0 | 2.4 | 2023-07-13 | 16.8 | 1.2 | 0 | 2022-07-13 | 14.9 | 3.1 | 0 | 2021-07-13 | 19.6 | 0 | 1.6 | 2020-07-13 | 19 | 0 | 1 | 2019-07-13 | 15.8 | 2.2 | 0 | 2018-07-13 | 12.5 | 5.5 | 0 | 2017-07-13 | 12 | 6 | 0 | 2016-07-13 | 19.3 | 0 | 1.3 | 1.8 | 1.08
2025-07-13 | 22.6 | 0 | 4.6 | 2024-07-13 | 19.7 | 0 | 1.7 | 2023-07-13 | 16.5 | 1.5 | 0 | 2022-07-13 | 14.8 | 3.2 | 0 | 2021-07-13 | 19.3 | 0 | 1.3 | 2020-07-13 | 17.8 | 0.2 | 0 | 2019-07-13 | 16.1 | 1.9 | 0 | 2018-07-13 | 12.2 | 5.8 | 0 | 2017-07-13 | 12.3 | 5.7 | 0 | 2016-07-13 | 19.8 | 0 | 1.8 | 1.83 | 0.94
2025-07-13 | 24 | 0 | 6 | 2024-07-13 | 19.6 | 0 | 1.6 | 2023-07-13 | 17.6 | 0.4 | 0 | 2022-07-13 | 16.2 | 1.8 | 0 | 2021-07-13 | 19.3 | 0 | 1.3 | 2020-07-13 | 19.5 | 0 | 1.5 | 2019-07-13 | 17.5 | 0.5 | 0 | 2018-07-13 | 16.1 | 1.9 | 0 | 2017-07-13 | 12.8 | 5.2 | 0 | 2016-07-13 | 21.4 | 0 | 3.4 | 0.98 | 1.38
2025-07-13 | 25.4 | 0 | 7.4 | 2024-07-13 | 20.5 | 0 | 2.5 | 2023-07-13 | 17 | 1 | 0 | 2022-07-13 | 18.7 | 0 | 0.7 | 2021-07-13 | 19.9 | 0 | 1.9 | 2020-07-13 | 20.8 | 0 | 2.8 | 2019-07-13 | 19.6 | 0 | 1.6 | 2018-07-13 | 18.9 | 0 | 0.9 | 2017-07-13 | 13.6 | 4.4 | 0 | 2016-07-13 | 23.6 | 0 | 5.6 | 0.54 | 2.34
2025-07-13 | 25.9 | 0 | 7.9 | 2024-07-13 | 21.8 | 0 | 3.8 | 2023-07-13 | 16.1 | 1.9 | 0 | 2022-07-13 | 20.5 | 0 | 2.5 | 2021-07-13 | 20.1 | 0 | 2.1 | 2020-07-13 | 22.7 | 0 | 4.7 | 2019-07-13 | 21.1 | 0 | 3.1 | 2018-07-13 | 21.7 | 0 | 3.7 | 2017-07-13 | 15.3 | 2.7 | 0 | 2016-07-13 | 25.6 | 0 | 7.6 | 0.46 | 3.54
2025-07-13 | 27.5 | 0 | 9.5 | 2024-07-13 | 23.7 | 0 | 5.7 | 2023-07-13 | 17.6 | 0.4 | 0 | 2022-07-13 | 21.4 | 0 | 3.4 | 2021-07-13 | 22.3 | 0 | 4.3 | 2020-07-13 | 22.8 | 0 | 4.8 | 2019-07-13 | 22.9 | 0 | 4.9 | 2018-07-13 | 25.3 | 0 | 7.3 | 2017-07-13 | 16.6 | 1.4 | 0 | 2016-07-13 | 26.5 | 0 | 8.5 | 0.18 | 4.84
2025-07-13 | 29.9 | 0 | 11.9 | 2024-07-13 | 25.3 | 0 | 7.3 | 2023-07-13 | 20 | 0 | 2 | 2022-07-13 | 23.2 | 0 | 5.2 | 2021-07-13 | 23.2 | 0 | 5.2 | 2020-07-13 | 23 | 0 | 5 | 2019-07-13 | 24.1 | 0 | 6.1 | 2018-07-13 | 27.2 | 0 | 9.2 | 2017-07-13 | 17.9 | 0.1 | 0 | 2016-07-13 | 28.9 | 0 | 10.9 | 0.01 | 6.28
2025-07-13 | 30.4 | 0 | 12.4 | 2024-07-13 | 26.1 | 0 | 8.1 | 2023-07-13 | 23.4 | 0 | 5.4 | 2022-07-13 | 23.5 | 0 | 5.5 | 2021-07-13 | 24.5 | 0 | 6.5 | 2020-07-13 | 24.3 | 0 | 6.3 | 2019-07-13 | 25.8 | 0 | 7.8 | 2018-07-13 | 28.2 | 0 | 10.2 | 2017-07-13 | 19.5 | 0 | 1.5 | 2016-07-13 | 30.8 | 0 | 12.8 | 0 | 7.65
2025-07-13 | 30.5 | 0 | 12.5 | 2024-07-13 | 27.5 | 0 | 9.5 | 2023-07-13 | 21.9 | 0 | 3.9 | 2022-07-13 | 24.1 | 0 | 6.1 | 2021-07-13 | 25.3 | 0 | 7.3 | 2020-07-13 | 24.7 | 0 | 6.7 | 2019-07-13 | 26.9 | 0 | 8.9 | 2018-07-13 | 28.6 | 0 | 10.6 | 2017-07-13 | 19.3 | 0 | 1.3 | 2016-07-13 | 31.4 | 0 | 13.4 | 0 | 8.02
2025-07-13 | 31.2 | 0 | 13.2 | 2024-07-13 | 28.1 | 0 | 10.1 | 2023-07-13 | 21.4 | 0 | 3.4 | 2022-07-13 | 24.5 | 0 | 6.5 | 2021-07-13 | 24.7 | 0 | 6.7 | 2020-07-13 | 26 | 0 | 8 | 2019-07-13 | 26.6 | 0 | 8.6 | 2018-07-13 | 28.8 | 0 | 10.8 | 2017-07-13 | 22 | 0 | 4 | 2016-07-13 | 30.8 | 0 | 12.8 | 0 | 8.41
2025-07-13 | 29.2 | 0 | 11.2 | 2024-07-13 | 28.5 | 0 | 10.5 | 2023-07-13 | 21.8 | 0 | 3.8 | 2022-07-13 | 25.2 | 0 | 7.2 | 2021-07-13 | 26.8 | 0 | 8.8 | 2020-07-13 | 25.1 | 0 | 7.1 | 2019-07-13 | 26.5 | 0 | 8.5 | 2018-07-13 | 29.3 | 0 | 11.3 | 2017-07-13 | 22.9 | 0 | 4.9 | 2016-07-13 | 32.4 | 0 | 14.4 | 0 | 8.77
2025-07-13 | 21.9 | 0 | 3.9 | 2024-07-13 | 28.8 | 0 | 10.8 | 2023-07-13 | 24.6 | 0 | 6.6 | 2022-07-13 | 25.9 | 0 | 7.9 | 2021-07-13 | 28.1 | 0 | 10.1 | 2020-07-13 | 26.4 | 0 | 8.4 | 2019-07-13 | 26.3 | 0 | 8.3 | 2018-07-13 | 28.6 | 0 | 10.6 | 2017-07-13 | 23.2 | 0 | 5.2 | 2016-07-13 | 30.8 | 0 | 12.8 | 0 | 8.46
2025-07-13 | 23.6 | 0 | 5.6 | 2024-07-13 | 28.9 | 0 | 10.9 | 2023-07-13 | 23.1 | 0 | 5.1 | 2022-07-13 | 23.9 | 0 | 5.9 | 2021-07-13 | 26.9 | 0 | 8.9 | 2020-07-13 | 24.8 | 0 | 6.8 | 2019-07-13 | 25.9 | 0 | 7.9 | 2018-07-13 | 28.1 | 0 | 10.1 | 2017-07-13 | 23.1 | 0 | 5.1 | 2016-07-13 | 29.1 | 0 | 11.1 | 0 | 7.74
2025-07-13 | 24.8 | 0 | 6.8 | 2024-07-13 | 28.6 | 0 | 10.6 | 2023-07-13 | 20.5 | 0 | 2.5 | 2022-07-13 | 23.9 | 0 | 5.9 | 2021-07-13 | 26 | 0 | 8 | 2020-07-13 | 26.6 | 0 | 8.6 | 2019-07-13 | 26.4 | 0 | 8.4 | 2018-07-13 | 27.7 | 0 | 9.7 | 2017-07-13 | 22.8 | 0 | 4.8 | 2016-07-13 | 31.7 | 0 | 13.7 | 0 | 7.9
2025-07-13 | 26.3 | 0 | 8.3 | 2024-07-13 | 27.8 | 0 | 9.8 | 2023-07-13 | 20.4 | 0 | 2.4 | 2022-07-13 | 22.9 | 0 | 4.9 | 2021-07-13 | 25.1 | 0 | 7.1 | 2020-07-13 | 25.2 | 0 | 7.2 | 2019-07-13 | 25.2 | 0 | 7.2 | 2018-07-13 | 26.6 | 0 | 8.6 | 2017-07-13 | 21.6 | 0 | 3.6 | 2016-07-13 | 31.3 | 0 | 13.3 | 0 | 7.24
2025-07-13 | 25.2 | 0 | 7.2 | 2024-07-13 | 25.9 | 0 | 7.9 | 2023-07-13 | 20.1 | 0 | 2.1 | 2022-07-13 | 22 | 0 | 4 | 2021-07-13 | 24.8 | 0 | 6.8 | 2020-07-13 | 23.8 | 0 | 5.8 | 2019-07-13 | 23.9 | 0 | 5.9 | 2018-07-13 | 25.5 | 0 | 7.5 | 2017-07-13 | 20.4 | 0 | 2.4 | 2016-07-13 | 29.7 | 0 | 11.7 | 0 | 6.13
2025-07-13 | 23.8 | 0 | 5.8 | 2024-07-13 | 25.1 | 0 | 7.1 | 2023-07-13 | 18.7 | 0 | 0.7 | 2022-07-13 | 20.8 | 0 | 2.8 | 2021-07-13 | 23.4 | 0 | 5.4 | 2020-07-13 | 23 | 0 | 5 | 2019-07-13 | 18.6 | 0 | 0.6 | 2018-07-13 | 24.6 | 0 | 6.6 | 2017-07-13 | 18.6 | 0 | 0.6 | 2016-07-13 | 27.6 | 0 | 9.6 | 0 | 4.42
2025-07-13 | 25.2 | 0 | 7.2 | 2024-07-13 | 23.1 | 0 | 5.1 | 2023-07-13 | 17.8 | 0.2 | 0 | 2022-07-13 | 19.2 | 0 | 1.2 | 2021-07-13 | 21.4 | 0 | 3.4 | 2020-07-13 | 22 | 0 | 4 | 2019-07-13 | 17.4 | 0.6 | 0 | 2018-07-13 | 24.1 | 0 | 6.1 | 2017-07-13 | 17.5 | 0.5 | 0 | 2016-07-13 | 26.8 | 0 | 8.8 | 0.13 | 3.58
2025-07-13 | 23.8 | 0 | 5.8 | 2024-07-13 | 21.7 | 0 | 3.7 | 2023-07-13 | 17.9 | 0.1 | 0 | 2022-07-13 | 17.5 | 0.5 | 0 | 2021-07-13 | 21.1 | 0 | 3.1 | 2020-07-13 | 19.9 | 0 | 1.9 | 2019-07-13 | 17.4 | 0.6 | 0 | 2018-07-13 | 23.7 | 0 | 5.7 | 2017-07-13 | 16.6 | 1.4 | 0 | 2016-07-13 | 25.8 | 0 | 7.8 | 0.26 | 2.8
2025-07-13 | 24.1 | 0 | 6.1 | 2024-07-13 | 20.8 | 0 | 2.8 | 2023-07-13 | 16.4 | 1.6 | 0 | 2022-07-13 | 17.2 | 0.8 | 0 | 2021-07-13 | 21.6 | 0 | 3.6 | 2020-07-13 | 21.2 | 0 | 3.2 | 2019-07-13 | 17.8 | 0.2 | 0 | 2018-07-13 | 23.4 | 0 | 5.4 | 2017-07-13 | 16.1 | 1.9 | 0 | 2016-07-13 | 25.3 | 0 | 7.3 | 0.45 | 2.84
2025-07-14 | 23.4 | 0 | 5.4 | 2024-07-14 | 19.4 | 0 | 1.4 | 2023-07-14 | 16.2 | 1.8 | 0 | 2022-07-14 | 16 | 2 | 0 | 2021-07-14 | 20.5 | 0 | 2.5 | 2020-07-14 | 20 | 0 | 2 | 2019-07-14 | 18.4 | 0 | 0.4 | 2018-07-14 | 22.6 | 0 | 4.6 | 2017-07-14 | 15.9 | 2.1 | 0 | 2016-07-14 | 24.1 | 0 | 6.1 | 0.59 | 2.24
2025-07-14 | 22.8 | 0 | 4.8 | 2024-07-14 | 19.5 | 0 | 1.5 | 2023-07-14 | 15.2 | 2.8 | 0 | 2022-07-14 | 15.9 | 2.1 | 0 | 2021-07-14 | 20 | 0 | 2 | 2020-07-14 | 19.3 | 0 | 1.3 | 2019-07-14 | 17.5 | 0.5 | 0 | 2018-07-14 | 22.7 | 0 | 4.7 | 2017-07-14 | 15.3 | 2.7 | 0 | 2016-07-14 | 23.2 | 0 | 5.2 | 0.81 | 1.95
2025-07-14 | 21.7 | 0 | 3.7 | 2024-07-14 | 19.2 | 0 | 1.2 | 2023-07-14 | 14.4 | 3.6 | 0 | 2022-07-14 | 15.8 | 2.2 | 0 | 2021-07-14 | 20.3 | 0 | 2.3 | 2020-07-14 | 18.6 | 0 | 0.6 | 2019-07-14 | 17.9 | 0.1 | 0 | 2018-07-14 | 19.9 | 0 | 1.9 | 2017-07-14 | 14.9 | 3.1 | 0 | 2016-07-14 | 22.8 | 0 | 4.8 | 0.9 | 1.45
2025-07-14 | 20.6 | 0 | 2.6 | 2024-07-14 | 18.3 | 0 | 0.3 | 2023-07-14 | 14.6 | 3.4 | 0 | 2022-07-14 | 15.3 | 2.7 | 0 | 2021-07-14 | 20.6 | 0 | 2.6 | 2020-07-14 | 17.5 | 0.5 | 0 | 2019-07-14 | 18 | 0 | 0 | 2018-07-14 | 19.2 | 0 | 1.2 | 2017-07-14 | 15.2 | 2.8 | 0 | 2016-07-14 | 22.5 | 0 | 4.5 | 0.94 | 1.12
2025-07-14 | 20 | 0 | 2 | 2024-07-14 | 18 | 0 | 0 | 2023-07-14 | 13.9 | 4.1 | 0 | 2022-07-14 | 14.6 | 3.4 | 0 | 2021-07-14 | 20.4 | 0 | 2.4 | 2020-07-14 | 17.5 | 0.5 | 0 | 2019-07-14 | 17.6 | 0.4 | 0 | 2018-07-14 | 18.9 | 0 | 0.9 | 2017-07-14 | 15 | 3 | 0 | 2016-07-14 | 22.2 | 0 | 4.2 | 1.14 | 0.95
2025-07-14 | 19.2 | 0 | 1.2 | 2024-07-14 | 17.6 | 0.4 | 0 | 2023-07-14 | 14.4 | 3.6 | 0 | 2022-07-14 | 15.2 | 2.8 | 0 | 2021-07-14 | 20.5 | 0 | 2.5 | 2020-07-14 | 16.9 | 1.1 | 0 | 2019-07-14 | 17.5 | 0.5 | 0 | 2018-07-14 | 18.5 | 0 | 0.5 | 2017-07-14 | 14.8 | 3.2 | 0 | 2016-07-14 | 22.4 | 0 | 4.4 | 1.16 | 0.86
2025-07-14 | 19.6 | 0 | 1.6 | 2024-07-14 | 18.6 | 0 | 0.6 | 2023-07-14 | 15.5 | 2.5 | 0 | 2022-07-14 | 15.8 | 2.2 | 0 | 2021-07-14 | 20.6 | 0 | 2.6 | 2020-07-14 | 19.8 | 0 | 1.8 | 2019-07-14 | 18.1 | 0 | 0.1 | 2018-07-14 | 18.4 | 0 | 0.4 | 2017-07-14 | 16.4 | 1.6 | 0 | 2016-07-14 | 22.9 | 0 | 4.9 | 0.63 | 1.2
2025-07-14 | 20.5 | 0 | 2.5 | 2024-07-14 | 20.9 | 0 | 2.9 | 2023-07-14 | 17.8 | 0.2 | 0 | 2022-07-14 | 16.8 | 1.2 | 0 | 2021-07-14 | 21 | 0 | 3 | 2020-07-14 | 21.5 | 0 | 3.5 | 2019-07-14 | 18.9 | 0 | 0.9 | 2018-07-14 | 19.3 | 0 | 1.3 | 2017-07-14 | 17.1 | 0.9 | 0 | 2016-07-14 | 23.4 | 0 | 5.4 | 0.23 | 1.95
2025-07-14 | 21 | 0 | 3 | 2024-07-14 | 23.7 | 0 | 5.7 | 2023-07-14 | 19.8 | 0 | 1.8 | 2022-07-14 | 17.7 | 0.3 | 0 | 2021-07-14 | 21.6 | 0 | 3.6 | 2020-07-14 | 23.3 | 0 | 5.3 | 2019-07-14 | 19.4 | 0 | 1.4 | 2018-07-14 | 20.5 | 0 | 2.5 | 2017-07-14 | 18.1 | 0 | 0.1 | 2016-07-14 | 23.8 | 0 | 5.8 | 0.03 | 2.92
2025-07-14 | 22.2 | 0 | 4.2 | 2024-07-14 | 25.5 | 0 | 7.5 | 2023-07-14 | 22.3 | 0 | 4.3 | 2022-07-14 | 19.7 | 0 | 1.7 | 2021-07-14 | 23.3 | 0 | 5.3 | 2020-07-14 | 22.8 | 0 | 4.8 | 2019-07-14 | 21.1 | 0 | 3.1 | 2018-07-14 | 22.8 | 0 | 4.8 | 2017-07-14 | 19.6 | 0 | 1.6 | 2016-07-14 | 24.2 | 0 | 6.2 | 0 | 4.35
2025-07-14 | 23.9 | 0 | 5.9 | 2024-07-14 | 27 | 0 | 9 | 2023-07-14 | 22.5 | 0 | 4.5 | 2022-07-14 | 21.6 | 0 | 3.6 | 2021-07-14 | 24.9 | 0 | 6.9 | 2020-07-14 | 25.7 | 0 | 7.7 | 2019-07-14 | 21.1 | 0 | 3.1 | 2018-07-14 | 24.4 | 0 | 6.4 | 2017-07-14 | 20.2 | 0 | 2.2 | 2016-07-14 | 23.4 | 0 | 5.4 | 0 | 5.47
2025-07-14 | 25.5 | 0 | 7.5 | 2024-07-14 | 27.9 | 0 | 9.9 | 2023-07-14 | 23.1 | 0 | 5.1 | 2022-07-14 | 23.1 | 0 | 5.1 | 2021-07-14 | 24.6 | 0 | 6.6 | 2020-07-14 | 25.4 | 0 | 7.4 | 2019-07-14 | 20.6 | 0 | 2.6 | 2018-07-14 | 26 | 0 | 8 | 2017-07-14 | 19.2 | 0 | 1.2 | 2016-07-14 | 21.6 | 0 | 3.6 | 0 | 5.7
2025-07-14 | 27.3 | 0 | 9.3 | 2024-07-14 | 28.5 | 0 | 10.5 | 2023-07-14 | 23.8 | 0 | 5.8 | 2022-07-14 | 23.8 | 0 | 5.8 | 2021-07-14 | 26 | 0 | 8 | 2020-07-14 | 25.7 | 0 | 7.7 | 2019-07-14 | 22.4 | 0 | 4.4 | 2018-07-14 | 26 | 0 | 8 | 2017-07-14 | 18.6 | 0 | 0.6 | 2016-07-14 | 21.6 | 0 | 3.6 | 0 | 6.37
2025-07-14 | 27.4 | 0 | 9.4 | 2024-07-14 | 29 | 0 | 11 | 2023-07-14 | 22.9 | 0 | 4.9 | 2022-07-14 | 23.9 | 0 | 5.9 | 2021-07-14 | 27.9 | 0 | 9.9 | 2020-07-14 | 28.6 | 0 | 10.6 | 2019-07-14 | 22.9 | 0 | 4.9 | 2018-07-14 | 26.1 | 0 | 8.1 | 2017-07-14 | 19.2 | 0 | 1.2 | 2016-07-14 | 23.7 | 0 | 5.7 | 0 | 7.16
2025-07-14 | 27.2 | 0 | 9.2 | 2024-07-14 | 29.7 | 0 | 11.7 | 2023-07-14 | 23.6 | 0 | 5.6 | 2022-07-14 | 24.3 | 0 | 6.3 | 2021-07-14 | 28 | 0 | 10 | 2020-07-14 | 27.1 | 0 | 9.1 | 2019-07-14 | 23.9 | 0 | 5.9 | 2018-07-14 | 27.7 | 0 | 9.7 | 2017-07-14 | 19.9 | 0 | 1.9 | 2016-07-14 | 25.3 | 0 | 7.3 | 0 | 7.67
2025-07-14 | 28.9 | 0 | 10.9 | 2024-07-14 | 29.7 | 0 | 11.7 | 2023-07-14 | 23.9 | 0 | 5.9 | 2022-07-14 | 24.3 | 0 | 6.3 | 2021-07-14 | 28.7 | 0 | 10.7 | 2020-07-14 | 27.3 | 0 | 9.3 | 2019-07-14 | 23.8 | 0 | 5.8 | 2018-07-14 | 28.8 | 0 | 10.8 | 2017-07-14 | 19.6 | 0 | 1.6 | 2016-07-14 | 26.3 | 0 | 8.3 | 0 | 8.13
2025-07-14 | 28.5 | 0 | 10.5 | 2024-07-14 | 29.2 | 0 | 11.2 | 2023-07-14 | 25.2 | 0 | 7.2 | 2022-07-14 | 23.4 | 0 | 5.4 | 2021-07-14 | 28.9 | 0 | 10.9 | 2020-07-14 | 26.1 | 0 | 8.1 | 2019-07-14 | 23.4 | 0 | 5.4 | 2018-07-14 | 29.7 | 0 | 11.7 | 2017-07-14 | 19.2 | 0 | 1.2 | 2016-07-14 | 27.7 | 0 | 9.7 | 0 | 8.13
2025-07-14 | 28 | 0 | 10 | 2024-07-14 | 28.1 | 0 | 10.1 | 2023-07-14 | 25.1 | 0 | 7.1 | 2022-07-14 | 24 | 0 | 6 | 2021-07-14 | 28.5 | 0 | 10.5 | 2020-07-14 | 25.6 | 0 | 7.6 | 2019-07-14 | 23 | 0 | 5 | 2018-07-14 | 29.7 | 0 | 11.7 | 2017-07-14 | 18.9 | 0 | 0.9 | 2016-07-14 | 27.6 | 0 | 9.6 | 0 | 7.85
2025-07-14 | 27.4 | 0 | 9.4 | 2024-07-14 | 26.8 | 0 | 8.8 | 2023-07-14 | 23.4 | 0 | 5.4 | 2022-07-14 | 24.1 | 0 | 6.1 | 2021-07-14 | 27.9 | 0 | 9.9 | 2020-07-14 | 24.7 | 0 | 6.7 | 2019-07-14 | 22 | 0 | 4 | 2018-07-14 | 29 | 0 | 11 | 2017-07-14 | 18.7 | 0 | 0.7 | 2016-07-14 | 26.5 | 0 | 8.5 | 0 | 7.05
2025-07-14 | 25.8 | 0 | 7.8 | 2024-07-14 | 25.4 | 0 | 7.4 | 2023-07-14 | 22 | 0 | 4 | 2022-07-14 | 22.8 | 0 | 4.8 | 2021-07-14 | 25.9 | 0 | 7.9 | 2020-07-14 | 23.9 | 0 | 5.9 | 2019-07-14 | 21.1 | 0 | 3.1 | 2018-07-14 | 27.4 | 0 | 9.4 | 2017-07-14 | 18.5 | 0 | 0.5 | 2016-07-14 | 24.5 | 0 | 6.5 | 0 | 5.73
2025-07-14 | 23.4 | 0 | 5.4 | 2024-07-14 | 24 | 0 | 6 | 2023-07-14 | 20.1 | 0 | 2.1 | 2022-07-14 | 19.8 | 0 | 1.8 | 2021-07-14 | 24.5 | 0 | 6.5 | 2020-07-14 | 21.3 | 0 | 3.3 | 2019-07-14 | 19.3 | 0 | 1.3 | 2018-07-14 | 23.3 | 0 | 5.3 | 2017-07-14 | 17.5 | 0.5 | 0 | 2016-07-14 | 23.4 | 0 | 5.4 | 0.05 | 3.71
2025-07-14 | 22.5 | 0 | 4.5 | 2024-07-14 | 23.4 | 0 | 5.4 | 2023-07-14 | 18.8 | 0 | 0.8 | 2022-07-14 | 19.8 | 0 | 1.8 | 2021-07-14 | 21.4 | 0 | 3.4 | 2020-07-14 | 20.2 | 0 | 2.2 | 2019-07-14 | 17.9 | 0.1 | 0 | 2018-07-14 | 22.6 | 0 | 4.6 | 2017-07-14 | 17.5 | 0.5 | 0 | 2016-07-14 | 23 | 0 | 5 | 0.06 | 2.77
2025-07-14 | 21.9 | 0 | 3.9 | 2024-07-14 | 23.4 | 0 | 5.4 | 2023-07-14 | 18.4 | 0 | 0.4 | 2022-07-14 | 17.2 | 0.8 | 0 | 2021-07-14 | 21.3 | 0 | 3.3 | 2020-07-14 | 19.9 | 0 | 1.9 | 2019-07-14 | 16.7 | 1.3 | 0 | 2018-07-14 | 21.8 | 0 | 3.8 | 2017-07-14 | 17.4 | 0.6 | 0 | 2016-07-14 | 19.1 | 0 | 1.1 | 0.27 | 1.98
2025-07-14 | 20.8 | 0 | 2.8 | 2024-07-14 | 22.9 | 0 | 4.9 | 2023-07-14 | 18.3 | 0 | 0.3 | 2022-07-14 | 16.4 | 1.6 | 0 | 2021-07-14 | 20.6 | 0 | 2.6 | 2020-07-14 | 19.2 | 0 | 1.2 | 2019-07-14 | 15.8 | 2.2 | 0 | 2018-07-14 | 20.7 | 0 | 2.7 | 2017-07-14 | 17.5 | 0.5 | 0 | 2016-07-14 | 19.6 | 0 | 1.6 | 0.43 | 1.61
2025-07-15 | 20 | 0 | 2 | 2024-07-15 | 22.2 | 0 | 4.2 | 2023-07-15 | 17.5 | 0.5 | 0 | 2022-07-15 | 16.9 | 1.1 | 0 | 2021-07-15 | 19.9 | 0 | 1.9 | 2020-07-15 | 18.7 | 0 | 0.7 | 2019-07-15 | 14.8 | 3.2 | 0 | 2018-07-15 | 20 | 0 | 2 | 2017-07-15 | 17.4 | 0.6 | 0 | 2016-07-15 | 19.7 | 0 | 1.7 | 0.54 | 1.25
2025-07-15 | 19.6 | 0 | 1.6 | 2024-07-15 | 21.9 | 0 | 3.9 | 2023-07-15 | 16.3 | 1.7 | 0 | 2022-07-15 | 16.1 | 1.9 | 0 | 2021-07-15 | 19.4 | 0 | 1.4 | 2020-07-15 | 18 | 0 | 0 | 2019-07-15 | 14.1 | 3.9 | 0 | 2018-07-15 | 22.6 | 0 | 4.6 | 2017-07-15 | 17.4 | 0.6 | 0 | 2016-07-15 | 19.4 | 0 | 1.4 | 0.81 | 1.29
2025-07-15 | 18.1 | 0 | 0.1 | 2024-07-15 | 22.2 | 0 | 4.2 | 2023-07-15 | 16.2 | 1.8 | 0 | 2022-07-15 | 14.9 | 3.1 | 0 | 2021-07-15 | 19 | 0 | 1 | 2020-07-15 | 16.9 | 1.1 | 0 | 2019-07-15 | 13.6 | 4.4 | 0 | 2018-07-15 | 20.1 | 0 | 2.1 | 2017-07-15 | 17.5 | 0.5 | 0 | 2016-07-15 | 19.2 | 0 | 1.2 | 1.09 | 0.86
2025-07-15 | 17.1 | 0.9 | 0 | 2024-07-15 | 21.3 | 0 | 3.3 | 2023-07-15 | 14.9 | 3.1 | 0 | 2022-07-15 | 14.8 | 3.2 | 0 | 2021-07-15 | 18.8 | 0 | 0.8 | 2020-07-15 | 16.3 | 1.7 | 0 | 2019-07-15 | 13.7 | 4.3 | 0 | 2018-07-15 | 18.5 | 0 | 0.5 | 2017-07-15 | 17.6 | 0.4 | 0 | 2016-07-15 | 18.4 | 0 | 0.4 | 1.36 | 0.5
2025-07-15 | 16.6 | 1.4 | 0 | 2024-07-15 | 20.7 | 0 | 2.7 | 2023-07-15 | 14.7 | 3.3 | 0 | 2022-07-15 | 13.5 | 4.5 | 0 | 2021-07-15 | 18.1 | 0 | 0.1 | 2020-07-15 | 14.7 | 3.3 | 0 | 2019-07-15 | 12.6 | 5.4 | 0 | 2018-07-15 | 18.5 | 0 | 0.5 | 2017-07-15 | 17.4 | 0.6 | 0 | 2016-07-15 | 18.3 | 0 | 0.3 | 1.85 | 0.36
2025-07-15 | 16.7 | 1.3 | 0 | 2024-07-15 | 20.3 | 0 | 2.3 | 2023-07-15 | 13.7 | 4.3 | 0 | 2022-07-15 | 13 | 5 | 0 | 2021-07-15 | 18.1 | 0 | 0.1 | 2020-07-15 | 14.7 | 3.3 | 0 | 2019-07-15 | 11.7 | 6.3 | 0 | 2018-07-15 | 19.4 | 0 | 1.4 | 2017-07-15 | 17.5 | 0.5 | 0 | 2016-07-15 | 17.7 | 0.3 | 0 | 2.1 | 0.38
2025-07-15 | 18.6 | 0 | 0.6 | 2024-07-15 | 21.4 | 0 | 3.4 | 2023-07-15 | 17.5 | 0.5 | 0 | 2022-07-15 | 15.3 | 2.7 | 0 | 2021-07-15 | 19.1 | 0 | 1.1 | 2020-07-15 | 16.6 | 1.4 | 0 | 2019-07-15 | 14.1 | 3.9 | 0 | 2018-07-15 | 21.3 | 0 | 3.3 | 2017-07-15 | 17.7 | 0.3 | 0 | 2016-07-15 | 19.4 | 0 | 1.4 | 0.88 | 0.98
2025-07-15 | 21.3 | 0 | 3.3 | 2024-07-15 | 23.1 | 0 | 5.1 | 2023-07-15 | 18.5 | 0 | 0.5 | 2022-07-15 | 17.2 | 0.8 | 0 | 2021-07-15 | 21 | 0 | 3 | 2020-07-15 | 18.9 | 0 | 0.9 | 2019-07-15 | 16.2 | 1.8 | 0 | 2018-07-15 | 23 | 0 | 5 | 2017-07-15 | 18.2 | 0 | 0.2 | 2016-07-15 | 21.2 | 0 | 3.2 | 0.26 | 2.12
2025-07-15 | 24 | 0 | 6 | 2024-07-15 | 24.9 | 0 | 6.9 | 2023-07-15 | 21.4 | 0 | 3.4 | 2022-07-15 | 20.6 | 0 | 2.6 | 2021-07-15 | 23.3 | 0 | 5.3 | 2020-07-15 | 20.9 | 0 | 2.9 | 2019-07-15 | 20.1 | 0 | 2.1 | 2018-07-15 | 24.1 | 0 | 6.1 | 2017-07-15 | 18.9 | 0 | 0.9 | 2016-07-15 | 22.8 | 0 | 4.8 | 0 | 4.1
2025-07-15 | 24.5 | 0 | 6.5 | 2024-07-15 | 25.5 | 0 | 7.5 | 2023-07-15 | 23.7 | 0 | 5.7 | 2022-07-15 | 22.7 | 0 | 4.7 | 2021-07-15 | 25.5 | 0 | 7.5 | 2020-07-15 | 22 | 0 | 4 | 2019-07-15 | 22.3 | 0 | 4.3 | 2018-07-15 | 26.3 | 0 | 8.3 | 2017-07-15 | 20.1 | 0 | 2.1 | 2016-07-15 | 24.1 | 0 | 6.1 | 0 | 5.67
2025-07-15 | 26.3 | 0 | 8.3 | 2024-07-15 | 26.8 | 0 | 8.8 | 2023-07-15 | 24.5 | 0 | 6.5 | 2022-07-15 | 24.5 | 0 | 6.5 | 2021-07-15 | 26.7 | 0 | 8.7 | 2020-07-15 | 23.6 | 0 | 5.6 | 2019-07-15 | 23.3 | 0 | 5.3 | 2018-07-15 | 26.7 | 0 | 8.7 | 2017-07-15 | 21.9 | 0 | 3.9 | 2016-07-15 | 24.9 | 0 | 6.9 | 0 | 6.92
2025-07-15 | 28.1 | 0 | 10.1 | 2024-07-15 | 28 | 0 | 10 | 2023-07-15 | 25.5 | 0 | 7.5 | 2022-07-15 | 24.9 | 0 | 6.9 | 2021-07-15 | 27.8 | 0 | 9.8 | 2020-07-15 | 25.2 | 0 | 7.2 | 2019-07-15 | 23.8 | 0 | 5.8 | 2018-07-15 | 28.5 | 0 | 10.5 | 2017-07-15 | 23.6 | 0 | 5.6 | 2016-07-15 | 26.1 | 0 | 8.1 | 0 | 8.15
2025-07-15 | 30.2 | 0 | 12.2 | 2024-07-15 | 28.2 | 0 | 10.2 | 2023-07-15 | 26.5 | 0 | 8.5 | 2022-07-15 | 24.7 | 0 | 6.7 | 2021-07-15 | 27.6 | 0 | 9.6 | 2020-07-15 | 27.1 | 0 | 9.1 | 2019-07-15 | 24.6 | 0 | 6.6 | 2018-07-15 | 29.4 | 0 | 11.4 | 2017-07-15 | 25.6 | 0 | 7.6 | 2016-07-15 | 25.2 | 0 | 7.2 | 0 | 8.91
2025-07-15 | 30.2 | 0 | 12.2 | 2024-07-15 | 29.6 | 0 | 11.6 | 2023-07-15 | 26 | 0 | 8 | 2022-07-15 | 25.6 | 0 | 7.6 | 2021-07-15 | 28.3 | 0 | 10.3 | 2020-07-15 | 27.7 | 0 | 9.7 | 2019-07-15 | 26.2 | 0 | 8.2 | 2018-07-15 | 31 | 0 | 13 | 2017-07-15 | 26.6 | 0 | 8.6 | 2016-07-15 | 27.9 | 0 | 9.9 | 0 | 9.91
2025-07-15 | 31.3 | 0 | 13.3 | 2024-07-15 | 30.2 | 0 | 12.2 | 2023-07-15 | 26 | 0 | 8 | 2022-07-15 | 26.4 | 0 | 8.4 | 2021-07-15 | 28 | 0 | 10 | 2020-07-15 | 27.6 | 0 | 9.6 | 2019-07-15 | 26.4 | 0 | 8.4 | 2018-07-15 | 31.2 | 0 | 13.2 | 2017-07-15 | 27.5 | 0 | 9.5 | 2016-07-15 | 29.7 | 0 | 11.7 | 0 | 10.43
2025-07-15 | 31.3 | 0 | 13.3 | 2024-07-15 | 29.8 | 0 | 11.8 | 2023-07-15 | 25.7 | 0 | 7.7 | 2022-07-15 | 25.9 | 0 | 7.9 | 2021-07-15 | 27.9 | 0 | 9.9 | 2020-07-15 | 27.6 | 0 | 9.6 | 2019-07-15 | 26.7 | 0 | 8.7 | 2018-07-15 | 32 | 0 | 14 | 2017-07-15 | 27.8 | 0 | 9.8 | 2016-07-15 | 27.5 | 0 | 9.5 | 0 | 10.22
2025-07-15 | 30.9 | 0 | 12.9 | 2024-07-15 | 28.5 | 0 | 10.5 | 2023-07-15 | 26 | 0 | 8 | 2022-07-15 | 26.3 | 0 | 8.3 | 2021-07-15 | 27.3 | 0 | 9.3 | 2020-07-15 | 27.8 | 0 | 9.8 | 2019-07-15 | 27.5 | 0 | 9.5 | 2018-07-15 | 32.1 | 0 | 14.1 | 2017-07-15 | 27.5 | 0 | 9.5 | 2016-07-15 | 19.7 | 0 | 1.7 | 0 | 9.36
2025-07-15 | 30.4 | 0 | 12.4 | 2024-07-15 | 23.4 | 0 | 5.4 | 2023-07-15 | 25.5 | 0 | 7.5 | 2022-07-15 | 26.6 | 0 | 8.6 | 2021-07-15 | 25.9 | 0 | 7.9 | 2020-07-15 | 27.5 | 0 | 9.5 | 2019-07-15 | 26.7 | 0 | 8.7 | 2018-07-15 | 31.8 | 0 | 13.8 | 2017-07-15 | 27.3 | 0 | 9.3 | 2016-07-15 | 20.4 | 0 | 2.4 | 0 | 8.55
2025-07-15 | 29.9 | 0 | 11.9 | 2024-07-15 | 21.1 | 0 | 3.1 | 2023-07-15 | 25 | 0 | 7 | 2022-07-15 | 24.6 | 0 | 6.6 | 2021-07-15 | 25.6 | 0 | 7.6 | 2020-07-15 | 25 | 0 | 7 | 2019-07-15 | 26.4 | 0 | 8.4 | 2018-07-15 | 31.3 | 0 | 13.3 | 2017-07-15 | 26.5 | 0 | 8.5 | 2016-07-15 | 20.6 | 0 | 2.6 | 0 | 7.6
2025-07-15 | 28.1 | 0 | 10.1 | 2024-07-15 | 21.1 | 0 | 3.1 | 2023-07-15 | 24.1 | 0 | 6.1 | 2022-07-15 | 23.8 | 0 | 5.8 | 2021-07-15 | 25.4 | 0 | 7.4 | 2020-07-15 | 23.6 | 0 | 5.6 | 2019-07-15 | 24.4 | 0 | 6.4 | 2018-07-15 | 29.1 | 0 | 11.1 | 2017-07-15 | 24.3 | 0 | 6.3 | 2016-07-15 | 20.2 | 0 | 2.2 | 0 | 6.41
2025-07-15 | 25.4 | 0 | 7.4 | 2024-07-15 | 20.6 | 0 | 2.6 | 2023-07-15 | 23.8 | 0 | 5.8 | 2022-07-15 | 22.1 | 0 | 4.1 | 2021-07-15 | 24 | 0 | 6 | 2020-07-15 | 22.1 | 0 | 4.1 | 2019-07-15 | 22.2 | 0 | 4.2 | 2018-07-15 | 25.3 | 0 | 7.3 | 2017-07-15 | 23.4 | 0 | 5.4 | 2016-07-15 | 18.6 | 0 | 0.6 | 0 | 4.75
2025-07-15 | 24.3 | 0 | 6.3 | 2024-07-15 | 20.6 | 0 | 2.6 | 2023-07-15 | 22.6 | 0 | 4.6 | 2022-07-15 | 21.2 | 0 | 3.2 | 2021-07-15 | 22.3 | 0 | 4.3 | 2020-07-15 | 20.8 | 0 | 2.8 | 2019-07-15 | 20.6 | 0 | 2.6 | 2018-07-15 | 24.3 | 0 | 6.3 | 2017-07-15 | 20.9 | 0 | 2.9 | 2016-07-15 | 18.4 | 0 | 0.4 | 0 | 3.6
2025-07-15 | 23.9 | 0 | 5.9 | 2024-07-15 | 20.1 | 0 | 2.1 | 2023-07-15 | 21.9 | 0 | 3.9 | 2022-07-15 | 20.3 | 0 | 2.3 | 2021-07-15 | 22 | 0 | 4 | 2020-07-15 | 19.6 | 0 | 1.6 | 2019-07-15 | 19.8 | 0 | 1.8 | 2018-07-15 | 23.1 | 0 | 5.1 | 2017-07-15 | 20.9 | 0 | 2.9 | 2016-07-15 | 17.4 | 0.6 | 0 | 0.06 | 2.96
2025-07-15 | 22.8 | 0 | 4.8 | 2024-07-15 | 20.1 | 0 | 2.1 | 2023-07-15 | 22.3 | 0 | 4.3 | 2022-07-15 | 19.4 | 0 | 1.4 | 2021-07-15 | 22.1 | 0 | 4.1 | 2020-07-15 | 19 | 0 | 1 | 2019-07-15 | 18.8 | 0 | 0.8 | 2018-07-15 | 21.1 | 0 | 3.1 | 2017-07-15 | 21.2 | 0 | 3.2 | 2016-07-15 | 16.5 | 1.5 | 0 | 0.15 | 2.48
2025-07-16 | 22 | 0 | 4 | 2024-07-16 | 19.5 | 0 | 1.5 | 2023-07-16 | 22.1 | 0 | 4.1 | 2022-07-16 | 19.2 | 0 | 1.2 | 2021-07-16 | 21.9 | 0 | 3.9 | 2020-07-16 | 18.5 | 0 | 0.5 | 2019-07-16 | 17.8 | 0.2 | 0 | 2018-07-16 | 19.7 | 0 | 1.7 | 2017-07-16 | 20.8 | 0 | 2.8 | 2016-07-16 | 16 | 2 | 0 | 0.22 | 1.97
2025-07-16 | 21.4 | 0 | 3.4 | 2024-07-16 | 19.4 | 0 | 1.4 | 2023-07-16 | 22 | 0 | 4 | 2022-07-16 | 19.2 | 0 | 1.2 | 2021-07-16 | 21.5 | 0 | 3.5 | 2020-07-16 | 18 | 0 | 0 | 2019-07-16 | 17.3 | 0.7 | 0 | 2018-07-16 | 21.9 | 0 | 3.9 | 2017-07-16 | 18.5 | 0 | 0.5 | 2016-07-16 | 16.1 | 1.9 | 0 | 0.26 | 1.79
2025-07-16 | 20.9 | 0 | 2.9 | 2024-07-16 | 19.5 | 0 | 1.5 | 2023-07-16 | 21.7 | 0 | 3.7 | 2022-07-16 | 17.3 | 0.7 | 0 | 2021-07-16 | 20.7 | 0 | 2.7 | 2020-07-16 | 17.4 | 0.6 | 0 | 2019-07-16 | 16.6 | 1.4 | 0 | 2018-07-16 | 19.3 | 0 | 1.3 | 2017-07-16 | 18.9 | 0 | 0.9 | 2016-07-16 | 15.7 | 2.3 | 0 | 0.5 | 1.3
2025-07-16 | 19.5 | 0 | 1.5 | 2024-07-16 | 19.8 | 0 | 1.8 | 2023-07-16 | 19.2 | 0 | 1.2 | 2022-07-16 | 17 | 1 | 0 | 2021-07-16 | 20.1 | 0 | 2.1 | 2020-07-16 | 17.2 | 0.8 | 0 | 2019-07-16 | 15.8 | 2.2 | 0 | 2018-07-16 | 20.1 | 0 | 2.1 | 2017-07-16 | 18.1 | 0 | 0.1 | 2016-07-16 | 15.8 | 2.2 | 0 | 0.62 | 0.88
2025-07-16 | 19.8 | 0 | 1.8 | 2024-07-16 | 19.3 | 0 | 1.3 | 2023-07-16 | 19.4 | 0 | 1.4 | 2022-07-16 | 16 | 2 | 0 | 2021-07-16 | 19.4 | 0 | 1.4 | 2020-07-16 | 17.1 | 0.9 | 0 | 2019-07-16 | 15.9 | 2.1 | 0 | 2018-07-16 | 18.5 | 0 | 0.5 | 2017-07-16 | 16.9 | 1.1 | 0 | 2016-07-16 | 14.7 | 3.3 | 0 | 0.94 | 0.64
2025-07-16 | 19.6 | 0 | 1.6 | 2024-07-16 | 19.3 | 0 | 1.3 | 2023-07-16 | 19.3 | 0 | 1.3 | 2022-07-16 | 15.6 | 2.4 | 0 | 2021-07-16 | 18.5 | 0 | 0.5 | 2020-07-16 | 17.2 | 0.8 | 0 | 2019-07-16 | 16.7 | 1.3 | 0 | 2018-07-16 | 19.2 | 0 | 1.2 | 2017-07-16 | 17.1 | 0.9 | 0 | 2016-07-16 | 14.1 | 3.9 | 0 | 0.93 | 0.59
2025-07-16 | 21.1 | 0 | 3.1 | 2024-07-16 | 20.1 | 0 | 2.1 | 2023-07-16 | 19.3 | 0 | 1.3 | 2022-07-16 | 17.5 | 0.5 | 0 | 2021-07-16 | 18.4 | 0 | 0.4 | 2020-07-16 | 19.7 | 0 | 1.7 | 2019-07-16 | 17.7 | 0.3 | 0 | 2018-07-16 | 20 | 0 | 2 | 2017-07-16 | 18.4 | 0 | 0.4 | 2016-07-16 | 15.7 | 2.3 | 0 | 0.31 | 1.1
2025-07-16 | 23.2 | 0 | 5.2 | 2024-07-16 | 21.7 | 0 | 3.7 | 2023-07-16 | 19.4 | 0 | 1.4 | 2022-07-16 | 20.1 | 0 | 2.1 | 2021-07-16 | 18.2 | 0 | 0.2 | 2020-07-16 | 21.4 | 0 | 3.4 | 2019-07-16 | 18.7 | 0 | 0.7 | 2018-07-16 | 22.1 | 0 | 4.1 | 2017-07-16 | 19.6 | 0 | 1.6 | 2016-07-16 | 17.5 | 0.5 | 0 | 0.05 | 2.24
2025-07-16 | 25.8 | 0 | 7.8 | 2024-07-16 | 22.4 | 0 | 4.4 | 2023-07-16 | 20.5 | 0 | 2.5 | 2022-07-16 | 22 | 0 | 4 | 2021-07-16 | 18.7 | 0 | 0.7 | 2020-07-16 | 23.9 | 0 | 5.9 | 2019-07-16 | 19.5 | 0 | 1.5 | 2018-07-16 | 25.3 | 0 | 7.3 | 2017-07-16 | 20.7 | 0 | 2.7 | 2016-07-16 | 18.9 | 0 | 0.9 | 0 | 3.77
2025-07-16 | 28.2 | 0 | 10.2 | 2024-07-16 | 24.1 | 0 | 6.1 | 2023-07-16 | 22.3 | 0 | 4.3 | 2022-07-16 | 23.2 | 0 | 5.2 | 2021-07-16 | 20.3 | 0 | 2.3 | 2020-07-16 | 26.3 | 0 | 8.3 | 2019-07-16 | 20.9 | 0 | 2.9 | 2018-07-16 | 28 | 0 | 10 | 2017-07-16 | 22.6 | 0 | 4.6 | 2016-07-16 | 19.5 | 0 | 1.5 | 0 | 5.54
2025-07-16 | 29.8 | 0 | 11.8 | 2024-07-16 | 24 | 0 | 6 | 2023-07-16 | 23.1 | 0 | 5.1 | 2022-07-16 | 25.4 | 0 | 7.4 | 2021-07-16 | 21.6 | 0 | 3.6 | 2020-07-16 | 27.4 | 0 | 9.4 | 2019-07-16 | 24.5 | 0 | 6.5 | 2018-07-16 | 29.6 | 0 | 11.6 | 2017-07-16 | 23.7 | 0 | 5.7 | 2016-07-16 | 21.4 | 0 | 3.4 | 0 | 7.05
2025-07-16 | 31.2 | 0 | 13.2 | 2024-07-16 | 24.7 | 0 | 6.7 | 2023-07-16 | 23.7 | 0 | 5.7 | 2022-07-16 | 26.4 | 0 | 8.4 | 2021-07-16 | 22.8 | 0 | 4.8 | 2020-07-16 | 26.4 | 0 | 8.4 | 2019-07-16 | 25.4 | 0 | 7.4 | 2018-07-16 | 31 | 0 | 13 | 2017-07-16 | 24.4 | 0 | 6.4 | 2016-07-16 | 22 | 0 | 4 | 0 | 7.8
2025-07-16 | 32.5 | 0 | 14.5 | 2024-07-16 | 25.3 | 0 | 7.3 | 2023-07-16 | 23.5 | 0 | 5.5 | 2022-07-16 | 27.6 | 0 | 9.6 | 2021-07-16 | 24.1 | 0 | 6.1 | 2020-07-16 | 26.2 | 0 | 8.2 | 2019-07-16 | 26.5 | 0 | 8.5 | 2018-07-16 | 32 | 0 | 14 | 2017-07-16 | 25.2 | 0 | 7.2 | 2016-07-16 | 21.7 | 0 | 3.7 | 0 | 8.46
2025-07-16 | 33.1 | 0 | 15.1 | 2024-07-16 | 24.7 | 0 | 6.7 | 2023-07-16 | 25.2 | 0 | 7.2 | 2022-07-16 | 27.7 | 0 | 9.7 | 2021-07-16 | 25 | 0 | 7 | 2020-07-16 | 26.6 | 0 | 8.6 | 2019-07-16 | 27.9 | 0 | 9.9 | 2018-07-16 | 33.5 | 0 | 15.5 | 2017-07-16 | 26.4 | 0 | 8.4 | 2016-07-16 | 21.8 | 0 | 3.8 | 0 | 9.19
2025-07-16 | 33.5 | 0 | 15.5 | 2024-07-16 | 24.9 | 0 | 6.9 | 2023-07-16 | 24.8 | 0 | 6.8 | 2022-07-16 | 28 | 0 | 10 | 2021-07-16 | 25.3 | 0 | 7.3 | 2020-07-16 | 24.7 | 0 | 6.7 | 2019-07-16 | 27.7 | 0 | 9.7 | 2018-07-16 | 32.6 | 0 | 14.6 | 2017-07-16 | 25.5 | 0 | 7.5 | 2016-07-16 | 21.7 | 0 | 3.7 | 0 | 8.87
2025-07-16 | 33.2 | 0 | 15.2 | 2024-07-16 | 24.6 | 0 | 6.6 | 2023-07-16 | 26.1 | 0 | 8.1 | 2022-07-16 | 27.2 | 0 | 9.2 | 2021-07-16 | 25.6 | 0 | 7.6 | 2020-07-16 | 24.6 | 0 | 6.6 | 2019-07-16 | 30.2 | 0 | 12.2 | 2018-07-16 | 32.5 | 0 | 14.5 | 2017-07-16 | 23.8 | 0 | 5.8 | 2016-07-16 | 22.8 | 0 | 4.8 | 0 | 9.06
2025-07-16 | 31.9 | 0 | 13.9 | 2024-07-16 | 25.1 | 0 | 7.1 | 2023-07-16 | 25.9 | 0 | 7.9 | 2022-07-16 | 28.8 | 0 | 10.8 | 2021-07-16 | 25.1 | 0 | 7.1 | 2020-07-16 | 24 | 0 | 6 | 2019-07-16 | 29.9 | 0 | 11.9 | 2018-07-16 | 30.6 | 0 | 12.6 | 2017-07-16 | 23 | 0 | 5 | 2016-07-16 | 21.1 | 0 | 3.1 | 0 | 8.54
2025-07-16 | 32.8 | 0 | 14.8 | 2024-07-16 | 25.6 | 0 | 7.6 | 2023-07-16 | 26.1 | 0 | 8.1 | 2022-07-16 | 28.3 | 0 | 10.3 | 2021-07-16 | 24.6 | 0 | 6.6 | 2020-07-16 | 23.4 | 0 | 5.4 | 2019-07-16 | 29.6 | 0 | 11.6 | 2018-07-16 | 27.3 | 0 | 9.3 | 2017-07-16 | 21.9 | 0 | 3.9 | 2016-07-16 | 21.5 | 0 | 3.5 | 0 | 8.11
2025-07-16 | 31.5 | 0 | 13.5 | 2024-07-16 | 25.7 | 0 | 7.7 | 2023-07-16 | 25.6 | 0 | 7.6 | 2022-07-16 | 27.3 | 0 | 9.3 | 2021-07-16 | 24 | 0 | 6 | 2020-07-16 | 23.6 | 0 | 5.6 | 2019-07-16 | 30.1 | 0 | 12.1 | 2018-07-16 | 27 | 0 | 9 | 2017-07-16 | 21 | 0 | 3 | 2016-07-16 | 21 | 0 | 3 | 0 | 7.68
2025-07-16 | 30.1 | 0 | 12.1 | 2024-07-16 | 24.8 | 0 | 6.8 | 2023-07-16 | 24.5 | 0 | 6.5 | 2022-07-16 | 25.5 | 0 | 7.5 | 2021-07-16 | 23.2 | 0 | 5.2 | 2020-07-16 | 22.9 | 0 | 4.9 | 2019-07-16 | 28.5 | 0 | 10.5 | 2018-07-16 | 26.8 | 0 | 8.8 | 2017-07-16 | 20.6 | 0 | 2.6 | 2016-07-16 | 20.2 | 0 | 2.2 | 0 | 6.71
2025-07-16 | 27.7 | 0 | 9.7 | 2024-07-16 | 23.7 | 0 | 5.7 | 2023-07-16 | 23.4 | 0 | 5.4 | 2022-07-16 | 23.8 | 0 | 5.8 | 2021-07-16 | 20.5 | 0 | 2.5 | 2020-07-16 | 22.4 | 0 | 4.4 | 2019-07-16 | 27.5 | 0 | 9.5 | 2018-07-16 | 25.1 | 0 | 7.1 | 2017-07-16 | 19.7 | 0 | 1.7 | 2016-07-16 | 19 | 0 | 1 | 0 | 5.28
2025-07-16 | 26.2 | 0 | 8.2 | 2024-07-16 | 23.1 | 0 | 5.1 | 2023-07-16 | 21.8 | 0 | 3.8 | 2022-07-16 | 22.3 | 0 | 4.3 | 2021-07-16 | 18.4 | 0 | 0.4 | 2020-07-16 | 22.2 | 0 | 4.2 | 2019-07-16 | 26.6 | 0 | 8.6 | 2018-07-16 | 24.7 | 0 | 6.7 | 2017-07-16 | 19.5 | 0 | 1.5 | 2016-07-16 | 18.4 | 0 | 0.4 | 0 | 4.32
2025-07-16 | 25.7 | 0 | 7.7 | 2024-07-16 | 23.2 | 0 | 5.2 | 2023-07-16 | 20.8 | 0 | 2.8 | 2022-07-16 | 21.6 | 0 | 3.6 | 2021-07-16 | 19.7 | 0 | 1.7 | 2020-07-16 | 21.9 | 0 | 3.9 | 2019-07-16 | 26 | 0 | 8 | 2018-07-16 | 23.2 | 0 | 5.2 | 2017-07-16 | 19.8 | 0 | 1.8 | 2016-07-16 | 18.4 | 0 | 0.4 | 0 | 4.03
2025-07-16 | 24.5 | 0 | 6.5 | 2024-07-16 | 22.7 | 0 | 4.7 | 2023-07-16 | 20.5 | 0 | 2.5 | 2022-07-16 | 20.4 | 0 | 2.4 | 2021-07-16 | 18.8 | 0 | 0.8 | 2020-07-16 | 21.7 | 0 | 3.7 | 2019-07-16 | 25 | 0 | 7 | 2018-07-16 | 23.8 | 0 | 5.8 | 2017-07-16 | 19.2 | 0 | 1.2 | 2016-07-16 | 18.1 | 0 | 0.1 | 0 | 3.47
2025-07-17 | 23.3 | 0 | 5.3 | 2024-07-17 | 21.9 | 0 | 3.9 | 2023-07-17 | 20.1 | 0 | 2.1 | 2022-07-17 | 20.4 | 0 | 2.4 | 2021-07-17 | 16.8 | 1.2 | 0 | 2020-07-17 | 21.5 | 0 | 3.5 | 2019-07-17 | 23.5 | 0 | 5.5 | 2018-07-17 | 24.3 | 0 | 6.3 | 2017-07-17 | 18.5 | 0 | 0.5 | 2016-07-17 | 17.5 | 0.5 | 0 | 0.17 | 2.95
2025-07-17 | 22.8 | 0 | 4.8 | 2024-07-17 | 21.5 | 0 | 3.5 | 2023-07-17 | 19.4 | 0 | 1.4 | 2022-07-17 | 18.5 | 0 | 0.5 | 2021-07-17 | 17.5 | 0.5 | 0 | 2020-07-17 | 21.2 | 0 | 3.2 | 2019-07-17 | 23.1 | 0 | 5.1 | 2018-07-17 | 21.9 | 0 | 3.9 | 2017-07-17 | 17.8 | 0.2 | 0 | 2016-07-17 | 17.3 | 0.7 | 0 | 0.14 | 2.24
2025-07-17 | 21.8 | 0 | 3.8 | 2024-07-17 | 21.2 | 0 | 3.2 | 2023-07-17 | 19.1 | 0 | 1.1 | 2022-07-17 | 17.7 | 0.3 | 0 | 2021-07-17 | 18.8 | 0 | 0.8 | 2020-07-17 | 21.2 | 0 | 3.2 | 2019-07-17 | 22.5 | 0 | 4.5 | 2018-07-17 | 21.6 | 0 | 3.6 | 2017-07-17 | 17.5 | 0.5 | 0 | 2016-07-17 | 17.4 | 0.6 | 0 | 0.14 | 2.02
2025-07-17 | 21.4 | 0 | 3.4 | 2024-07-17 | 20.4 | 0 | 2.4 | 2023-07-17 | 18.7 | 0 | 0.7 | 2022-07-17 | 18.1 | 0 | 0.1 | 2021-07-17 | 18.5 | 0 | 0.5 | 2020-07-17 | 20.8 | 0 | 2.8 | 2019-07-17 | 22 | 0 | 4 | 2018-07-17 | 21.4 | 0 | 3.4 | 2017-07-17 | 17.7 | 0.3 | 0 | 2016-07-17 | 17.1 | 0.9 | 0 | 0.12 | 1.73
2025-07-17 | 22.3 | 0 | 4.3 | 2024-07-17 | 19.9 | 0 | 1.9 | 2023-07-17 | 18.6 | 0 | 0.6 | 2022-07-17 | 17.8 | 0.2 | 0 | 2021-07-17 | 16.5 | 1.5 | 0 | 2020-07-17 | 20.4 | 0 | 2.4 | 2019-07-17 | 21.8 | 0 | 3.8 | 2018-07-17 | 21.9 | 0 | 3.9 | 2017-07-17 | 17.5 | 0.5 | 0 | 2016-07-17 | 16.9 | 1.1 | 0 | 0.33 | 1.69
2025-07-17 | 22.1 | 0 | 4.1 | 2024-07-17 | 20.1 | 0 | 2.1 | 2023-07-17 | 19 | 0 | 1 | 2022-07-17 | 16.3 | 1.7 | 0 | 2021-07-17 | 16.3 | 1.7 | 0 | 2020-07-17 | 20.5 | 0 | 2.5 | 2019-07-17 | 22.1 | 0 | 4.1 | 2018-07-17 | 22 | 0 | 4 | 2017-07-17 | 17.4 | 0.6 | 0 | 2016-07-17 | 16.9 | 1.1 | 0 | 0.51 | 1.78
2025-07-17 | 22.8 | 0 | 4.8 | 2024-07-17 | 20.8 | 0 | 2.8 | 2023-07-17 | 19.6 | 0 | 1.6 | 2022-07-17 | 19.3 | 0 | 1.3 | 2021-07-17 | 17.9 | 0.1 | 0 | 2020-07-17 | 20.1 | 0 | 2.1 | 2019-07-17 | 22.6 | 0 | 4.6 | 2018-07-17 | 21.9 | 0 | 3.9 | 2017-07-17 | 18.2 | 0 | 0.2 | 2016-07-17 | 16.9 | 1.1 | 0 | 0.12 | 2.13
2025-07-17 | 22.9 | 0 | 4.9 | 2024-07-17 | 21.4 | 0 | 3.4 | 2023-07-17 | 19.9 | 0 | 1.9 | 2022-07-17 | 21.8 | 0 | 3.8 | 2021-07-17 | 19.2 | 0 | 1.2 | 2020-07-17 | 20.6 | 0 | 2.6 | 2019-07-17 | 23.2 | 0 | 5.2 | 2018-07-17 | 22.4 | 0 | 4.4 | 2017-07-17 | 18.7 | 0 | 0.7 | 2016-07-17 | 19.5 | 0 | 1.5 | 0 | 2.96
2025-07-17 | 24.2 | 0 | 6.2 | 2024-07-17 | 22.8 | 0 | 4.8 | 2023-07-17 | 21 | 0 | 3 | 2022-07-17 | 24 | 0 | 6 | 2021-07-17 | 21.2 | 0 | 3.2 | 2020-07-17 | 21.6 | 0 | 3.6 | 2019-07-17 | 24.6 | 0 | 6.6 | 2018-07-17 | 23.7 | 0 | 5.7 | 2017-07-17 | 19 | 0 | 1 | 2016-07-17 | 21 | 0 | 3 | 0 | 4.31
2025-07-17 | 25.8 | 0 | 7.8 | 2024-07-17 | 23.9 | 0 | 5.9 | 2023-07-17 | 22.6 | 0 | 4.6 | 2022-07-17 | 26 | 0 | 8 | 2021-07-17 | 22.4 | 0 | 4.4 | 2020-07-17 | 23 | 0 | 5 | 2019-07-17 | 25.1 | 0 | 7.1 | 2018-07-17 | 25.2 | 0 | 7.2 | 2017-07-17 | 21 | 0 | 3 | 2016-07-17 | 21.8 | 0 | 3.8 | 0 | 5.68
2025-07-17 | 26.5 | 0 | 8.5 | 2024-07-17 | 23.9 | 0 | 5.9 | 2023-07-17 | 24.1 | 0 | 6.1 | 2022-07-17 | 27.3 | 0 | 9.3 | 2021-07-17 | 22.9 | 0 | 4.9 | 2020-07-17 | 24.1 | 0 | 6.1 | 2019-07-17 | 26 | 0 | 8 | 2018-07-17 | 26.2 | 0 | 8.2 | 2017-07-17 | 22.2 | 0 | 4.2 | 2016-07-17 | 22.2 | 0 | 4.2 | 0 | 6.54
2025-07-17 | 27.8 | 0 | 9.8 | 2024-07-17 | 24.2 | 0 | 6.2 | 2023-07-17 | 25.8 | 0 | 7.8 | 2022-07-17 | 28.6 | 0 | 10.6 | 2021-07-17 | 23.2 | 0 | 5.2 | 2020-07-17 | 25.4 | 0 | 7.4 | 2019-07-17 | 27.8 | 0 | 9.8 | 2018-07-17 | 27.5 | 0 | 9.5 | 2017-07-17 | 23.9 | 0 | 5.9 | 2016-07-17 | 24.7 | 0 | 6.7 | 0 | 7.89
2025-07-17 | 25.5 | 0 | 7.5 | 2024-07-17 | 23.9 | 0 | 5.9 | 2023-07-17 | 26.2 | 0 | 8.2 | 2022-07-17 | 29.3 | 0 | 11.3 | 2021-07-17 | 23.6 | 0 | 5.6 | 2020-07-17 | 27 | 0 | 9 | 2019-07-17 | 28.3 | 0 | 10.3 | 2018-07-17 | 27.6 | 0 | 9.6 | 2017-07-17 | 24.6 | 0 | 6.6 | 2016-07-17 | 25.3 | 0 | 7.3 | 0 | 8.13
2025-07-17 | 27 | 0 | 9 | 2024-07-17 | 25.1 | 0 | 7.1 | 2023-07-17 | 27.1 | 0 | 9.1 | 2022-07-17 | 29.1 | 0 | 11.1 | 2021-07-17 | 24 | 0 | 6 | 2020-07-17 | 29.2 | 0 | 11.2 | 2019-07-17 | 27.8 | 0 | 9.8 | 2018-07-17 | 27.9 | 0 | 9.9 | 2017-07-17 | 24.3 | 0 | 6.3 | 2016-07-17 | 25.7 | 0 | 7.7 | 0 | 8.72
2025-07-17 | 25.5 | 0 | 7.5 | 2024-07-17 | 26.7 | 0 | 8.7 | 2023-07-17 | 27.8 | 0 | 9.8 | 2022-07-17 | 28.9 | 0 | 10.9 | 2021-07-17 | 24.7 | 0 | 6.7 | 2020-07-17 | 29.8 | 0 | 11.8 | 2019-07-17 | 27.8 | 0 | 9.8 | 2018-07-17 | 28.1 | 0 | 10.1 | 2017-07-17 | 25.8 | 0 | 7.8 | 2016-07-17 | 26.7 | 0 | 8.7 | 0 | 9.18
2025-07-17 | 26.2 | 0 | 8.2 | 2024-07-17 | 27.1 | 0 | 9.1 | 2023-07-17 | 27.2 | 0 | 9.2 | 2022-07-17 | 28.7 | 0 | 10.7 | 2021-07-17 | 25.3 | 0 | 7.3 | 2020-07-17 | 31 | 0 | 13 | 2019-07-17 | 27.2 | 0 | 9.2 | 2018-07-17 | 28.2 | 0 | 10.2 | 2017-07-17 | 25.4 | 0 | 7.4 | 2016-07-17 | 26.5 | 0 | 8.5 | 0 | 9.28
2025-07-17 | 23.6 | 0 | 5.6 | 2024-07-17 | 26.2 | 0 | 8.2 | 2023-07-17 | 26.8 | 0 | 8.8 | 2022-07-17 | 28.7 | 0 | 10.7 | 2021-07-17 | 24.8 | 0 | 6.8 | 2020-07-17 | 31.2 | 0 | 13.2 | 2019-07-17 | 27.9 | 0 | 9.9 | 2018-07-17 | 26.9 | 0 | 8.9 | 2017-07-17 | 26.1 | 0 | 8.1 | 2016-07-17 | 26.5 | 0 | 8.5 | 0 | 8.87
2025-07-17 | 21.6 | 0 | 3.6 | 2024-07-17 | 18.9 | 0 | 0.9 | 2023-07-17 | 26.4 | 0 | 8.4 | 2022-07-17 | 30.1 | 0 | 12.1 | 2021-07-17 | 24.2 | 0 | 6.2 | 2020-07-17 | 31.5 | 0 | 13.5 | 2019-07-17 | 27.4 | 0 | 9.4 | 2018-07-17 | 27 | 0 | 9 | 2017-07-17 | 25.2 | 0 | 7.2 | 2016-07-17 | 25.4 | 0 | 7.4 | 0 | 7.77
2025-07-17 | 21 | 0 | 3 | 2024-07-17 | 21.6 | 0 | 3.6 | 2023-07-17 | 25.4 | 0 | 7.4 | 2022-07-17 | 29.1 | 0 | 11.1 | 2021-07-17 | 23.2 | 0 | 5.2 | 2020-07-17 | 29.4 | 0 | 11.4 | 2019-07-17 | 26.2 | 0 | 8.2 | 2018-07-17 | 25.2 | 0 | 7.2 | 2017-07-17 | 24.9 | 0 | 6.9 | 2016-07-17 | 24.3 | 0 | 6.3 | 0 | 7.03
2025-07-17 | 19.8 | 0 | 1.8 | 2024-07-17 | 20.6 | 0 | 2.6 | 2023-07-17 | 24.2 | 0 | 6.2 | 2022-07-17 | 26.3 | 0 | 8.3 | 2021-07-17 | 22.4 | 0 | 4.4 | 2020-07-17 | 27.9 | 0 | 9.9 | 2019-07-17 | 25 | 0 | 7 | 2018-07-17 | 23.9 | 0 | 5.9 | 2017-07-17 | 23.8 | 0 | 5.8 | 2016-07-17 | 23.1 | 0 | 5.1 | 0 | 5.7
2025-07-17 | 18.7 | 0 | 0.7 | 2024-07-17 | 20.2 | 0 | 2.2 | 2023-07-17 | 21.9 | 0 | 3.9 | 2022-07-17 | 24.1 | 0 | 6.1 | 2021-07-17 | 19.9 | 0 | 1.9 | 2020-07-17 | 26 | 0 | 8 | 2019-07-17 | 22.1 | 0 | 4.1 | 2018-07-17 | 22.1 | 0 | 4.1 | 2017-07-17 | 22.1 | 0 | 4.1 | 2016-07-17 | 21.4 | 0 | 3.4 | 0 | 3.85
2025-07-17 | 16.3 | 1.7 | 0 | 2024-07-17 | 20.1 | 0 | 2.1 | 2023-07-17 | 20.9 | 0 | 2.9 | 2022-07-17 | 23.1 | 0 | 5.1 | 2021-07-17 | 20.7 | 0 | 2.7 | 2020-07-17 | 24.4 | 0 | 6.4 | 2019-07-17 | 22 | 0 | 4 | 2018-07-17 | 21.2 | 0 | 3.2 | 2017-07-17 | 19.9 | 0 | 1.9 | 2016-07-17 | 20.1 | 0 | 2.1 | 0.17 | 3.04
2025-07-17 | 16.1 | 1.9 | 0 | 2024-07-17 | 20 | 0 | 2 | 2023-07-17 | 20.4 | 0 | 2.4 | 2022-07-17 | 21.6 | 0 | 3.6 | 2021-07-17 | 20.1 | 0 | 2.1 | 2020-07-17 | 22.2 | 0 | 4.2 | 2019-07-17 | 21 | 0 | 3 | 2018-07-17 | 20.1 | 0 | 2.1 | 2017-07-17 | 20.8 | 0 | 2.8 | 2016-07-17 | 20.2 | 0 | 2.2 | 0.19 | 2.44
2025-07-17 | 16 | 2 | 0 | 2024-07-17 | 17.9 | 0.1 | 0 | 2023-07-17 | 19.8 | 0 | 1.8 | 2022-07-17 | 20.5 | 0 | 2.5 | 2021-07-17 | 19.4 | 0 | 1.4 | 2020-07-17 | 21.6 | 0 | 3.6 | 2019-07-17 | 20.1 | 0 | 2.1 | 2018-07-17 | 19.2 | 0 | 1.2 | 2017-07-17 | 19.8 | 0 | 1.8 | 2016-07-17 | 19.7 | 0 | 1.7 | 0.21 | 1.61
2025-07-18 | 15.2 | 2.8 | 0 | 2024-07-18 | 16.7 | 1.3 | 0 | 2023-07-18 | 20 | 0 | 2 | 2022-07-18 | 20.8 | 0 | 2.8 | 2021-07-18 | 19.4 | 0 | 1.4 | 2020-07-18 | 21.3 | 0 | 3.3 | 2019-07-18 | 19.1 | 0 | 1.1 | 2018-07-18 | 17.9 | 0.1 | 0 | 2017-07-18 | 18.7 | 0 | 0.7 | 2016-07-18 | 18.9 | 0 | 0.9 | 0.42 | 1.22
2025-07-18 | 15.1 | 2.9 | 0 | 2024-07-18 | 16.2 | 1.8 | 0 | 2023-07-18 | 18.5 | 0 | 0.5 | 2022-07-18 | 20.3 | 0 | 2.3 | 2021-07-18 | 18.9 | 0 | 0.9 | 2020-07-18 | 20.4 | 0 | 2.4 | 2019-07-18 | 16 | 2 | 0 | 2018-07-18 | 17.4 | 0.6 | 0 | 2017-07-18 | 17.9 | 0.1 | 0 | 2016-07-18 | 17.1 | 0.9 | 0 | 0.83 | 0.61
2025-07-18 | 14 | 4 | 0 | 2024-07-18 | 15.9 | 2.1 | 0 | 2023-07-18 | 18.9 | 0 | 0.9 | 2022-07-18 | 20.4 | 0 | 2.4 | 2021-07-18 | 19.8 | 0 | 1.8 | 2020-07-18 | 19.8 | 0 | 1.8 | 2019-07-18 | 16.6 | 1.4 | 0 | 2018-07-18 | 16.5 | 1.5 | 0 | 2017-07-18 | 18 | 0 | 0 | 2016-07-18 | 17.6 | 0.4 | 0 | 0.94 | 0.69
2025-07-18 | 12.8 | 5.2 | 0 | 2024-07-18 | 15.2 | 2.8 | 0 | 2023-07-18 | 18 | 0 | 0 | 2022-07-18 | 19.7 | 0 | 1.7 | 2021-07-18 | 17.6 | 0.4 | 0 | 2020-07-18 | 18.2 | 0 | 0.2 | 2019-07-18 | 15.6 | 2.4 | 0 | 2018-07-18 | 15 | 3 | 0 | 2017-07-18 | 17.4 | 0.6 | 0 | 2016-07-18 | 16.3 | 1.7 | 0 | 1.61 | 0.19
2025-07-18 | 11.3 | 6.7 | 0 | 2024-07-18 | 14.7 | 3.3 | 0 | 2023-07-18 | 17.7 | 0.3 | 0 | 2022-07-18 | 18.1 | 0 | 0.1 | 2021-07-18 | 17.3 | 0.7 | 0 | 2020-07-18 | 17.2 | 0.8 | 0 | 2019-07-18 | 16.6 | 1.4 | 0 | 2018-07-18 | 13 | 5 | 0 | 2017-07-18 | 16.4 | 1.6 | 0 | 2016-07-18 | 17.1 | 0.9 | 0 | 2.07 | 0.01
2025-07-18 | 10.6 | 7.4 | 0 | 2024-07-18 | 14.7 | 3.3 | 0 | 2023-07-18 | 17.9 | 0.1 | 0 | 2022-07-18 | 18.3 | 0 | 0.3 | 2021-07-18 | 17.5 | 0.5 | 0 | 2020-07-18 | 17.2 | 0.8 | 0 | 2019-07-18 | 16.3 | 1.7 | 0 | 2018-07-18 | 13.9 | 4.1 | 0 | 2017-07-18 | 16.6 | 1.4 | 0 | 2016-07-18 | 18.9 | 0 | 0.9 | 1.93 | 0.12
2025-07-18 | 12.5 | 5.5 | 0 | 2024-07-18 | 16.5 | 1.5 | 0 | 2023-07-18 | 17.8 | 0.2 | 0 | 2022-07-18 | 19.8 | 0 | 1.8 | 2021-07-18 | 17.5 | 0.5 | 0 | 2020-07-18 | 20.1 | 0 | 2.1 | 2019-07-18 | 16.9 | 1.1 | 0 | 2018-07-18 | 15.7 | 2.3 | 0 | 2017-07-18 | 18.5 | 0 | 0.5 | 2016-07-18 | 20.9 | 0 | 2.9 | 1.11 | 0.73
2025-07-18 | 14.6 | 3.4 | 0 | 2024-07-18 | 16.7 | 1.3 | 0 | 2023-07-18 | 18.3 | 0 | 0.3 | 2022-07-18 | 21.1 | 0 | 3.1 | 2021-07-18 | 19.8 | 0 | 1.8 | 2020-07-18 | 22.8 | 0 | 4.8 | 2019-07-18 | 18.5 | 0 | 0.5 | 2018-07-18 | 16.6 | 1.4 | 0 | 2017-07-18 | 20.2 | 0 | 2.2 | 2016-07-18 | 23.4 | 0 | 5.4 | 0.61 | 1.81
2025-07-18 | 16.4 | 1.6 | 0 | 2024-07-18 | 18 | 0 | 0 | 2023-07-18 | 19.9 | 0 | 1.9 | 2022-07-18 | 22.3 | 0 | 4.3 | 2021-07-18 | 22.3 | 0 | 4.3 | 2020-07-18 | 25.9 | 0 | 7.9 | 2019-07-18 | 20.4 | 0 | 2.4 | 2018-07-18 | 18.1 | 0 | 0.1 | 2017-07-18 | 22.6 | 0 | 4.6 | 2016-07-18 | 24.4 | 0 | 6.4 | 0.16 | 3.19
2025-07-18 | 18.4 | 0 | 0.4 | 2024-07-18 | 19 | 0 | 1 | 2023-07-18 | 22.6 | 0 | 4.6 | 2022-07-18 | 22.8 | 0 | 4.8 | 2021-07-18 | 23.1 | 0 | 5.1 | 2020-07-18 | 27.1 | 0 | 9.1 | 2019-07-18 | 21.7 | 0 | 3.7 | 2018-07-18 | 19.2 | 0 | 1.2 | 2017-07-18 | 24.4 | 0 | 6.4 | 2016-07-18 | 26.2 | 0 | 8.2 | 0 | 4.45
2025-07-18 | 19.6 | 0 | 1.6 | 2024-07-18 | 19 | 0 | 1 | 2023-07-18 | 23.6 | 0 | 5.6 | 2022-07-18 | 22.9 | 0 | 4.9 | 2021-07-18 | 24.3 | 0 | 6.3 | 2020-07-18 | 28.6 | 0 | 10.6 | 2019-07-18 | 23.4 | 0 | 5.4 | 2018-07-18 | 19.9 | 0 | 1.9 | 2017-07-18 | 24.8 | 0 | 6.8 | 2016-07-18 | 27.2 | 0 | 9.2 | 0 | 5.33
2025-07-18 | 21.7 | 0 | 3.7 | 2024-07-18 | 18.6 | 0 | 0.6 | 2023-07-18 | 24.9 | 0 | 6.9 | 2022-07-18 | 22.3 | 0 | 4.3 | 2021-07-18 | 25 | 0 | 7 | 2020-07-18 | 30.8 | 0 | 12.8 | 2019-07-18 | 24.6 | 0 | 6.6 | 2018-07-18 | 21 | 0 | 3 | 2017-07-18 | 26.9 | 0 | 8.9 | 2016-07-18 | 28.1 | 0 | 10.1 | 0 | 6.39
2025-07-18 | 22.6 | 0 | 4.6 | 2024-07-18 | 19 | 0 | 1 | 2023-07-18 | 26.2 | 0 | 8.2 | 2022-07-18 | 21.4 | 0 | 3.4 | 2021-07-18 | 26.2 | 0 | 8.2 | 2020-07-18 | 29.9 | 0 | 11.9 | 2019-07-18 | 25.4 | 0 | 7.4 | 2018-07-18 | 21.9 | 0 | 3.9 | 2017-07-18 | 27.4 | 0 | 9.4 | 2016-07-18 | 28.9 | 0 | 10.9 | 0 | 6.89
2025-07-18 | 23.7 | 0 | 5.7 | 2024-07-18 | 18.9 | 0 | 0.9 | 2023-07-18 | 26.8 | 0 | 8.8 | 2022-07-18 | 21.1 | 0 | 3.1 | 2021-07-18 | 27.1 | 0 | 9.1 | 2020-07-18 | 29.8 | 0 | 11.8 | 2019-07-18 | 26 | 0 | 8 | 2018-07-18 | 22.2 | 0 | 4.2 | 2017-07-18 | 28.2 | 0 | 10.2 | 2016-07-18 | 28.5 | 0 | 10.5 | 0 | 7.23
2025-07-18 | 24.3 | 0 | 6.3 | 2024-07-18 | 18 | 0 | 0 | 2023-07-18 | 27 | 0 | 9 | 2022-07-18 | 21.1 | 0 | 3.1 | 2021-07-18 | 27.6 | 0 | 9.6 | 2020-07-18 | 31.3 | 0 | 13.3 | 2019-07-18 | 26.7 | 0 | 8.7 | 2018-07-18 | 22.7 | 0 | 4.7 | 2017-07-18 | 28.9 | 0 | 10.9 | 2016-07-18 | 29.4 | 0 | 11.4 | 0 | 7.7
2025-07-18 | 25 | 0 | 7 | 2024-07-18 | 18.3 | 0 | 0.3 | 2023-07-18 | 27.2 | 0 | 9.2 | 2022-07-18 | 21.1 | 0 | 3.1 | 2021-07-18 | 28.5 | 0 | 10.5 | 2020-07-18 | 31.9 | 0 | 13.9 | 2019-07-18 | 27.3 | 0 | 9.3 | 2018-07-18 | 23.2 | 0 | 5.2 | 2017-07-18 | 28.8 | 0 | 10.8 | 2016-07-18 | 29 | 0 | 11 | 0 | 8.03
2025-07-18 | 25.6 | 0 | 7.6 | 2024-07-18 | 19.1 | 0 | 1.1 | 2023-07-18 | 26.9 | 0 | 8.9 | 2022-07-18 | 21.1 | 0 | 3.1 | 2021-07-18 | 28.7 | 0 | 10.7 | 2020-07-18 | 31.7 | 0 | 13.7 | 2019-07-18 | 27.2 | 0 | 9.2 | 2018-07-18 | 23.5 | 0 | 5.5 | 2017-07-18 | 27.9 | 0 | 9.9 | 2016-07-18 | 29 | 0 | 11 | 0 | 8.07
2025-07-18 | 25 | 0 | 7 | 2024-07-18 | 19 | 0 | 1 | 2023-07-18 | 26.3 | 0 | 8.3 | 2022-07-18 | 20.7 | 0 | 2.7 | 2021-07-18 | 28.3 | 0 | 10.3 | 2020-07-18 | 31.2 | 0 | 13.2 | 2019-07-18 | 27.1 | 0 | 9.1 | 2018-07-18 | 23.5 | 0 | 5.5 | 2017-07-18 | 28.4 | 0 | 10.4 | 2016-07-18 | 28.1 | 0 | 10.1 | 0 | 7.76
2025-07-18 | 24.5 | 0 | 6.5 | 2024-07-18 | 19.5 | 0 | 1.5 | 2023-07-18 | 20.7 | 0 | 2.7 | 2022-07-18 | 20.5 | 0 | 2.5 | 2021-07-18 | 26.8 | 0 | 8.8 | 2020-07-18 | 29.6 | 0 | 11.6 | 2019-07-18 | 25.9 | 0 | 7.9 | 2018-07-18 | 23.2 | 0 | 5.2 | 2017-07-18 | 27.6 | 0 | 9.6 | 2016-07-18 | 26.9 | 0 | 8.9 | 0 | 6.52
2025-07-18 | 22.4 | 0 | 4.4 | 2024-07-18 | 18.4 | 0 | 0.4 | 2023-07-18 | 19.1 | 0 | 1.1 | 2022-07-18 | 20.7 | 0 | 2.7 | 2021-07-18 | 24.1 | 0 | 6.1 | 2020-07-18 | 27.8 | 0 | 9.8 | 2019-07-18 | 23.6 | 0 | 5.6 | 2018-07-18 | 22.2 | 0 | 4.2 | 2017-07-18 | 25.8 | 0 | 7.8 | 2016-07-18 | 24 | 0 | 6 | 0 | 4.81
2025-07-18 | 20.4 | 0 | 2.4 | 2024-07-18 | 16.8 | 1.2 | 0 | 2023-07-18 | 17.8 | 0.2 | 0 | 2022-07-18 | 20.9 | 0 | 2.9 | 2021-07-18 | 21.9 | 0 | 3.9 | 2020-07-18 | 26.3 | 0 | 8.3 | 2019-07-18 | 21.3 | 0 | 3.3 | 2018-07-18 | 20.5 | 0 | 2.5 | 2017-07-18 | 24.2 | 0 | 6.2 | 2016-07-18 | 21.4 | 0 | 3.4 | 0.14 | 3.29
2025-07-18 | 18.9 | 0 | 0.9 | 2024-07-18 | 16.3 | 1.7 | 0 | 2023-07-18 | 17.2 | 0.8 | 0 | 2022-07-18 | 20.9 | 0 | 2.9 | 2021-07-18 | 20.6 | 0 | 2.6 | 2020-07-18 | 25.9 | 0 | 7.9 | 2019-07-18 | 21.2 | 0 | 3.2 | 2018-07-18 | 16.1 | 1.9 | 0 | 2017-07-18 | 23 | 0 | 5 | 2016-07-18 | 20.8 | 0 | 2.8 | 0.44 | 2.53
2025-07-18 | 17.9 | 0.1 | 0 | 2024-07-18 | 15.5 | 2.5 | 0 | 2023-07-18 | 17.1 | 0.9 | 0 | 2022-07-18 | 20.1 | 0 | 2.1 | 2021-07-18 | 19.9 | 0 | 1.9 | 2020-07-18 | 24.7 | 0 | 6.7 | 2019-07-18 | 19.8 | 0 | 1.8 | 2018-07-18 | 15.4 | 2.6 | 0 | 2017-07-18 | 21.9 | 0 | 3.9 | 2016-07-18 | 20.1 | 0 | 2.1 | 0.61 | 1.85
2025-07-18 | 16.7 | 1.3 | 0 | 2024-07-18 | 14.8 | 3.2 | 0 | 2023-07-18 | 17 | 1 | 0 | 2022-07-18 | 19.3 | 0 | 1.3 | 2021-07-18 | 19.4 | 0 | 1.4 | 2020-07-18 | 24.2 | 0 | 6.2 | 2019-07-18 | 19.8 | 0 | 1.8 | 2018-07-18 | 13.6 | 4.4 | 0 | 2017-07-18 | 21.2 | 0 | 3.2 | 2016-07-18 | 18.8 | 0 | 0.8 | 0.99 | 1.47
2025-07-19 | 16.1 | 1.9 | 0 | 2024-07-19 | 14.2 | 3.8 | 0 | 2023-07-19 | 16 | 2 | 0 | 2022-07-19 | 19.2 | 0 | 1.2 | 2021-07-19 | 17.9 | 0.1 | 0 | 2020-07-19 | 23.7 | 0 | 5.7 | 2019-07-19 | 19.1 | 0 | 1.1 | 2018-07-19 | 13.4 | 4.6 | 0 | 2017-07-19 | 20.4 | 0 | 2.4 | 2016-07-19 | 18.2 | 0 | 0.2 | 1.24 | 1.06
2025-07-19 | 14.5 | 3.5 | 0 | 2024-07-19 | 13.1 | 4.9 | 0 | 2023-07-19 | 15.9 | 2.1 | 0 | 2022-07-19 | 19 | 0 | 1 | 2021-07-19 | 17.8 | 0.2 | 0 | 2020-07-19 | 22.9 | 0 | 4.9 | 2019-07-19 | 18.9 | 0 | 0.9 | 2018-07-19 | 12.8 | 5.2 | 0 | 2017-07-19 | 18.9 | 0 | 0.9 | 2016-07-19 | 17.6 | 0.4 | 0 | 1.63 | 0.77
2025-07-19 | 14.7 | 3.3 | 0 | 2024-07-19 | 13.1 | 4.9 | 0 | 2023-07-19 | 15.6 | 2.4 | 0 | 2022-07-19 | 18.9 | 0 | 0.9 | 2021-07-19 | 18.6 | 0 | 0.6 | 2020-07-19 | 22.6 | 0 | 4.6 | 2019-07-19 | 19.6 | 0 | 1.6 | 2018-07-19 | 13.6 | 4.4 | 0 | 2017-07-19 | 19.2 | 0 | 1.2 | 2016-07-19 | 16.6 | 1.4 | 0 | 1.64 | 0.89
2025-07-19 | 14.1 | 3.9 | 0 | 2024-07-19 | 12.8 | 5.2 | 0 | 2023-07-19 | 15.1 | 2.9 | 0 | 2022-07-19 | 18.6 | 0 | 0.6 | 2021-07-19 | 18 | 0 | 0 | 2020-07-19 | 22.5 | 0 | 4.5 | 2019-07-19 | 20.5 | 0 | 2.5 | 2018-07-19 | 11.5 | 6.5 | 0 | 2017-07-19 | 18 | 0 | 0 | 2016-07-19 | 13.9 | 4.1 | 0 | 2.26 | 0.76
2025-07-19 | 13.3 | 4.7 | 0 | 2024-07-19 | 12.3 | 5.7 | 0 | 2023-07-19 | 13.9 | 4.1 | 0 | 2022-07-19 | 18.2 | 0 | 0.2 | 2021-07-19 | 17.6 | 0.4 | 0 | 2020-07-19 | 22 | 0 | 4 | 2019-07-19 | 21.5 | 0 | 3.5 | 2018-07-19 | 11.3 | 6.7 | 0 | 2017-07-19 | 17.7 | 0.3 | 0 | 2016-07-19 | 12.1 | 5.9 | 0 | 2.78 | 0.77
2025-07-19 | 13 | 5 | 0 | 2024-07-19 | 13.1 | 4.9 | 0 | 2023-07-19 | 13.1 | 4.9 | 0 | 2022-07-19 | 18.1 | 0 | 0.1 | 2021-07-19 | 17.5 | 0.5 | 0 | 2020-07-19 | 23.1 | 0 | 5.1 | 2019-07-19 | 21.6 | 0 | 3.6 | 2018-07-19 | 11.3 | 6.7 | 0 | 2017-07-19 | 17.2 | 0.8 | 0 | 2016-07-19 | 11.1 | 6.9 | 0 | 2.97 | 0.88
2025-07-19 | 15.3 | 2.7 | 0 | 2024-07-19 | 15.5 | 2.5 | 0 | 2023-07-19 | 15.9 | 2.1 | 0 | 2022-07-19 | 18.6 | 0 | 0.6 | 2021-07-19 | 18.8 | 0 | 0.8 | 2020-07-19 | 21.7 | 0 | 3.7 | 2019-07-19 | 22 | 0 | 4 | 2018-07-19 | 13.7 | 4.3 | 0 | 2017-07-19 | 18.4 | 0 | 0.4 | 2016-07-19 | 14.5 | 3.5 | 0 | 1.51 | 0.95
2025-07-19 | 17.6 | 0.4 | 0 | 2024-07-19 | 17.3 | 0.7 | 0 | 2023-07-19 | 16.9 | 1.1 | 0 | 2022-07-19 | 20 | 0 | 2 | 2021-07-19 | 20.3 | 0 | 2.3 | 2020-07-19 | 22.6 | 0 | 4.6 | 2019-07-19 | 23.9 | 0 | 5.9 | 2018-07-19 | 16.4 | 1.6 | 0 | 2017-07-19 | 20.4 | 0 | 2.4 | 2016-07-19 | 16.7 | 1.3 | 0 | 0.51 | 1.72
2025-07-19 | 19 | 0 | 1 | 2024-07-19 | 19.5 | 0 | 1.5 | 2023-07-19 | 18.8 | 0 | 0.8 | 2022-07-19 | 21.8 | 0 | 3.8 | 2021-07-19 | 21.8 | 0 | 3.8 | 2020-07-19 | 25.6 | 0 | 7.6 | 2019-07-19 | 25.5 | 0 | 7.5 | 2018-07-19 | 20.2 | 0 | 2.2 | 2017-07-19 | 22 | 0 | 4 | 2016-07-19 | 18.5 | 0 | 0.5 | 0 | 3.27
2025-07-19 | 21.5 | 0 | 3.5 | 2024-07-19 | 20.8 | 0 | 2.8 | 2023-07-19 | 20.9 | 0 | 2.9 | 2022-07-19 | 23.7 | 0 | 5.7 | 2021-07-19 | 23.6 | 0 | 5.6 | 2020-07-19 | 28.9 | 0 | 10.9 | 2019-07-19 | 27.4 | 0 | 9.4 | 2018-07-19 | 22.5 | 0 | 4.5 | 2017-07-19 | 22.9 | 0 | 4.9 | 2016-07-19 | 19.4 | 0 | 1.4 | 0 | 5.16
2025-07-19 | 23.1 | 0 | 5.1 | 2024-07-19 | 22.4 | 0 | 4.4 | 2023-07-19 | 22 | 0 | 4 | 2022-07-19 | 25 | 0 | 7 | 2021-07-19 | 24.7 | 0 | 6.7 | 2020-07-19 | 30.4 | 0 | 12.4 | 2019-07-19 | 27.8 | 0 | 9.8 | 2018-07-19 | 25 | 0 | 7 | 2017-07-19 | 24.4 | 0 | 6.4 | 2016-07-19 | 20.8 | 0 | 2.8 | 0 | 6.56
2025-07-19 | 24.6 | 0 | 6.6 | 2024-07-19 | 23.8 | 0 | 5.8 | 2023-07-19 | 23.1 | 0 | 5.1 | 2022-07-19 | 27.3 | 0 | 9.3 | 2021-07-19 | 26 | 0 | 8 | 2020-07-19 | 31.1 | 0 | 13.1 | 2019-07-19 | 30 | 0 | 12 | 2018-07-19 | 25.9 | 0 | 7.9 | 2017-07-19 | 24.1 | 0 | 6.1 | 2016-07-19 | 21.6 | 0 | 3.6 | 0 | 7.75
2025-07-19 | 25.1 | 0 | 7.1 | 2024-07-19 | 24.5 | 0 | 6.5 | 2023-07-19 | 23.9 | 0 | 5.9 | 2022-07-19 | 28.6 | 0 | 10.6 | 2021-07-19 | 27.2 | 0 | 9.2 | 2020-07-19 | 30.8 | 0 | 12.8 | 2019-07-19 | 30.4 | 0 | 12.4 | 2018-07-19 | 27.4 | 0 | 9.4 | 2017-07-19 | 26.1 | 0 | 8.1 | 2016-07-19 | 20.9 | 0 | 2.9 | 0 | 8.49
2025-07-19 | 25.7 | 0 | 7.7 | 2024-07-19 | 24.1 | 0 | 6.1 | 2023-07-19 | 24.8 | 0 | 6.8 | 2022-07-19 | 28.9 | 0 | 10.9 | 2021-07-19 | 28.4 | 0 | 10.4 | 2020-07-19 | 29.9 | 0 | 11.9 | 2019-07-19 | 30.5 | 0 | 12.5 | 2018-07-19 | 28.1 | 0 | 10.1 | 2017-07-19 | 25.6 | 0 | 7.6 | 2016-07-19 | 20.9 | 0 | 2.9 | 0 | 8.69
2025-07-19 | 26.4 | 0 | 8.4 | 2024-07-19 | 24.3 | 0 | 6.3 | 2023-07-19 | 25.6 | 0 | 7.6 | 2022-07-19 | 29.8 | 0 | 11.8 | 2021-07-19 | 28.9 | 0 | 10.9 | 2020-07-19 | 28.8 | 0 | 10.8 | 2019-07-19 | 30.9 | 0 | 12.9 | 2018-07-19 | 27.9 | 0 | 9.9 | 2017-07-19 | 26.3 | 0 | 8.3 | 2016-07-19 | 22.3 | 0 | 4.3 | 0 | 9.12
2025-07-19 | 26 | 0 | 8 | 2024-07-19 | 24.7 | 0 | 6.7 | 2023-07-19 | 25.8 | 0 | 7.8 | 2022-07-19 | 29.9 | 0 | 11.9 | 2021-07-19 | 28.3 | 0 | 10.3 | 2020-07-19 | 25.9 | 0 | 7.9 | 2019-07-19 | 31.3 | 0 | 13.3 | 2018-07-19 | 29 | 0 | 11 | 2017-07-19 | 26.4 | 0 | 8.4 | 2016-07-19 | 22.7 | 0 | 4.7 | 0 | 9
2025-07-19 | 26.4 | 0 | 8.4 | 2024-07-19 | 24.7 | 0 | 6.7 | 2023-07-19 | 25.9 | 0 | 7.9 | 2022-07-19 | 30.3 | 0 | 12.3 | 2021-07-19 | 28.5 | 0 | 10.5 | 2020-07-19 | 24.2 | 0 | 6.2 | 2019-07-19 | 32.1 | 0 | 14.1 | 2018-07-19 | 29.1 | 0 | 11.1 | 2017-07-19 | 26.6 | 0 | 8.6 | 2016-07-19 | 22.1 | 0 | 4.1 | 0 | 8.99
2025-07-19 | 25.8 | 0 | 7.8 | 2024-07-19 | 24.6 | 0 | 6.6 | 2023-07-19 | 25.5 | 0 | 7.5 | 2022-07-19 | 30.2 | 0 | 12.2 | 2021-07-19 | 27 | 0 | 9 | 2020-07-19 | 25.8 | 0 | 7.8 | 2019-07-19 | 31.9 | 0 | 13.9 | 2018-07-19 | 29 | 0 | 11 | 2017-07-19 | 27.2 | 0 | 9.2 | 2016-07-19 | 22.9 | 0 | 4.9 | 0 | 8.99
2025-07-19 | 23.5 | 0 | 5.5 | 2024-07-19 | 23.6 | 0 | 5.6 | 2023-07-19 | 25.2 | 0 | 7.2 | 2022-07-19 | 29.4 | 0 | 11.4 | 2021-07-19 | 25.9 | 0 | 7.9 | 2020-07-19 | 26.6 | 0 | 8.6 | 2019-07-19 | 30.5 | 0 | 12.5 | 2018-07-19 | 27.9 | 0 | 9.9 | 2017-07-19 | 26.1 | 0 | 8.1 | 2016-07-19 | 22.4 | 0 | 4.4 | 0 | 8.11
2025-07-19 | 22.1 | 0 | 4.1 | 2024-07-19 | 22.3 | 0 | 4.3 | 2023-07-19 | 23.1 | 0 | 5.1 | 2022-07-19 | 26.9 | 0 | 8.9 | 2021-07-19 | 24.6 | 0 | 6.6 | 2020-07-19 | 25.5 | 0 | 7.5 | 2019-07-19 | 30 | 0 | 12 | 2018-07-19 | 25.5 | 0 | 7.5 | 2017-07-19 | 25.5 | 0 | 7.5 | 2016-07-19 | 21 | 0 | 3 | 0 | 6.65
2025-07-19 | 20.8 | 0 | 2.8 | 2024-07-19 | 20.5 | 0 | 2.5 | 2023-07-19 | 22.2 | 0 | 4.2 | 2022-07-19 | 24.9 | 0 | 6.9 | 2021-07-19 | 23.6 | 0 | 5.6 | 2020-07-19 | 24.6 | 0 | 6.6 | 2019-07-19 | 28.1 | 0 | 10.1 | 2018-07-19 | 22.9 | 0 | 4.9 | 2017-07-19 | 23.5 | 0 | 5.5 | 2016-07-19 | 19.2 | 0 | 1.2 | 0 | 5.03
2025-07-19 | 20.1 | 0 | 2.1 | 2024-07-19 | 19.4 | 0 | 1.4 | 2023-07-19 | 18.2 | 0 | 0.2 | 2022-07-19 | 24.4 | 0 | 6.4 | 2021-07-19 | 22.3 | 0 | 4.3 | 2020-07-19 | 23.8 | 0 | 5.8 | 2019-07-19 | 27 | 0 | 9 | 2018-07-19 | 21.2 | 0 | 3.2 | 2017-07-19 | 22.8 | 0 | 4.8 | 2016-07-19 | 16.6 | 1.4 | 0 | 0.14 | 3.72
2025-07-19 | 20.6 | 0 | 2.6 | 2024-07-19 | 18.4 | 0 | 0.4 | 2023-07-19 | 17.9 | 0.1 | 0 | 2022-07-19 | 23.9 | 0 | 5.9 | 2021-07-19 | 19.8 | 0 | 1.8 | 2020-07-19 | 23.9 | 0 | 5.9 | 2019-07-19 | 26.6 | 0 | 8.6 | 2018-07-19 | 19.3 | 0 | 1.3 | 2017-07-19 | 20 | 0 | 2 | 2016-07-19 | 15.3 | 2.7 | 0 | 0.28 | 2.85
2025-07-19 | 18.6 | 0 | 0.6 | 2024-07-19 | 18 | 0 | 0 | 2023-07-19 | 18.5 | 0 | 0.5 | 2022-07-19 | 22.8 | 0 | 4.8 | 2021-07-19 | 19.9 | 0 | 1.9 | 2020-07-19 | 23.4 | 0 | 5.4 | 2019-07-19 | 25.7 | 0 | 7.7 | 2018-07-19 | 18.7 | 0 | 0.7 | 2017-07-19 | 19.1 | 0 | 1.1 | 2016-07-19 | 13.1 | 4.9 | 0 | 0.49 | 2.27
2025-07-20 | 18 | 0 | 0 | 2024-07-20 | 16.8 | 1.2 | 0 | 2023-07-20 | 18.4 | 0 | 0.4 | 2022-07-20 | 22.1 | 0 | 4.1 | 2021-07-20 | 18.7 | 0 | 0.7 | 2020-07-20 | 22.6 | 0 | 4.6 | 2019-07-20 | 24.6 | 0 | 6.6 | 2018-07-20 | 18.1 | 0 | 0.1 | 2017-07-20 | 19 | 0 | 1 | 2016-07-20 | 13.7 | 4.3 | 0 | 0.55 | 1.75
2025-07-20 | 17 | 1 | 0 | 2024-07-20 | 16.3 | 1.7 | 0 | 2023-07-20 | 17.8 | 0.2 | 0 | 2022-07-20 | 21.6 | 0 | 3.6 | 2021-07-20 | 19.1 | 0 | 1.1 | 2020-07-20 | 22.1 | 0 | 4.1 | 2019-07-20 | 23 | 0 | 5 | 2018-07-20 | 16.4 | 1.6 | 0 | 2017-07-20 | 19.1 | 0 | 1.1 | 2016-07-20 | 12.7 | 5.3 | 0 | 0.98 | 1.49
2025-07-20 | 17 | 1 | 0 | 2024-07-20 | 15.8 | 2.2 | 0 | 2023-07-20 | 16.6 | 1.4 | 0 | 2022-07-20 | 21.2 | 0 | 3.2 | 2021-07-20 | 20.9 | 0 | 2.9 | 2020-07-20 | 21.9 | 0 | 3.9 | 2019-07-20 | 22.7 | 0 | 4.7 | 2018-07-20 | 14.8 | 3.2 | 0 | 2017-07-20 | 20.1 | 0 | 2.1 | 2016-07-20 | 11.8 | 6.2 | 0 | 1.4 | 1.68
2025-07-20 | 15.9 | 2.1 | 0 | 2024-07-20 | 14.7 | 3.3 | 0 | 2023-07-20 | 16 | 2 | 0 | 2022-07-20 | 21 | 0 | 3 | 2021-07-20 | 20.6 | 0 | 2.6 | 2020-07-20 | 21.4 | 0 | 3.4 | 2019-07-20 | 21.4 | 0 | 3.4 | 2018-07-20 | 13.9 | 4.1 | 0 | 2017-07-20 | 19.5 | 0 | 1.5 | 2016-07-20 | 11.7 | 6.3 | 0 | 1.78 | 1.39
2025-07-20 | 16.2 | 1.8 | 0 | 2024-07-20 | 14.1 | 3.9 | 0 | 2023-07-20 | 15.7 | 2.3 | 0 | 2022-07-20 | 21.1 | 0 | 3.1 | 2021-07-20 | 20 | 0 | 2 | 2020-07-20 | 20.6 | 0 | 2.6 | 2019-07-20 | 21.4 | 0 | 3.4 | 2018-07-20 | 14.6 | 3.4 | 0 | 2017-07-20 | 17.8 | 0.2 | 0 | 2016-07-20 | 11.6 | 6.4 | 0 | 1.8 | 1.11
2025-07-20 | 16.1 | 1.9 | 0 | 2024-07-20 | 13.6 | 4.4 | 0 | 2023-07-20 | 15.6 | 2.4 | 0 | 2022-07-20 | 21.2 | 0 | 3.2 | 2021-07-20 | 19 | 0 | 1 | 2020-07-20 | 20.3 | 0 | 2.3 | 2019-07-20 | 21.4 | 0 | 3.4 | 2018-07-20 | 14.4 | 3.6 | 0 | 2017-07-20 | 18.8 | 0 | 0.8 | 2016-07-20 | 10.9 | 7.1 | 0 | 1.94 | 1.07
2025-07-20 | 16.5 | 1.5 | 0 | 2024-07-20 | 15.3 | 2.7 | 0 | 2023-07-20 | 16.4 | 1.6 | 0 | 2022-07-20 | 21.8 | 0 | 3.8 | 2021-07-20 | 19.7 | 0 | 1.7 | 2020-07-20 | 21.1 | 0 | 3.1 | 2019-07-20 | 22.4 | 0 | 4.4 | 2018-07-20 | 15.6 | 2.4 | 0 | 2017-07-20 | 19.2 | 0 | 1.2 | 2016-07-20 | 12.7 | 5.3 | 0 | 1.35 | 1.42
2025-07-20 | 16.8 | 1.2 | 0 | 2024-07-20 | 18.2 | 0 | 0.2 | 2023-07-20 | 18.4 | 0 | 0.4 | 2022-07-20 | 22.4 | 0 | 4.4 | 2021-07-20 | 20.8 | 0 | 2.8 | 2020-07-20 | 22.9 | 0 | 4.9 | 2019-07-20 | 23.9 | 0 | 5.9 | 2018-07-20 | 19.7 | 0 | 1.7 | 2017-07-20 | 20.6 | 0 | 2.6 | 2016-07-20 | 16.6 | 1.4 | 0 | 0.26 | 2.29
2025-07-20 | 17.3 | 0.7 | 0 | 2024-07-20 | 20.4 | 0 | 2.4 | 2023-07-20 | 20.5 | 0 | 2.5 | 2022-07-20 | 24.1 | 0 | 6.1 | 2021-07-20 | 21.3 | 0 | 3.3 | 2020-07-20 | 24.8 | 0 | 6.8 | 2019-07-20 | 25.9 | 0 | 7.9 | 2018-07-20 | 20.9 | 0 | 2.9 | 2017-07-20 | 21.1 | 0 | 3.1 | 2016-07-20 | 19.2 | 0 | 1.2 | 0.07 | 3.62
2025-07-20 | 18 | 0 | 0 | 2024-07-20 | 22.5 | 0 | 4.5 | 2023-07-20 | 22.9 | 0 | 4.9 | 2022-07-20 | 25.4 | 0 | 7.4 | 2021-07-20 | 22.8 | 0 | 4.8 | 2020-07-20 | 25.9 | 0 | 7.9 | 2019-07-20 | 27.6 | 0 | 9.6 | 2018-07-20 | 24.1 | 0 | 6.1 | 2017-07-20 | 24.8 | 0 | 6.8 | 2016-07-20 | 20.6 | 0 | 2.6 | 0 | 5.46
2025-07-20 | 20.3 | 0 | 2.3 | 2024-07-20 | 24.1 | 0 | 6.1 | 2023-07-20 | 24.8 | 0 | 6.8 | 2022-07-20 | 27.6 | 0 | 9.6 | 2021-07-20 | 23 | 0 | 5 | 2020-07-20 | 26.7 | 0 | 8.7 | 2019-07-20 | 28.8 | 0 | 10.8 | 2018-07-20 | 26.4 | 0 | 8.4 | 2017-07-20 | 25.5 | 0 | 7.5 | 2016-07-20 | 22.9 | 0 | 4.9 | 0 | 7.01
2025-07-20 | 21.1 | 0 | 3.1 | 2024-07-20 | 25.6 | 0 | 7.6 | 2023-07-20 | 24.3 | 0 | 6.3 | 2022-07-20 | 28.7 | 0 | 10.7 | 2021-07-20 | 23.6 | 0 | 5.6 | 2020-07-20 | 28.4 | 0 | 10.4 | 2019-07-20 | 31.6 | 0 | 13.6 | 2018-07-20 | 28.6 | 0 | 10.6 | 2017-07-20 | 26.4 | 0 | 8.4 | 2016-07-20 | 24.3 | 0 | 6.3 | 0 | 8.26
2025-07-20 | 22.6 | 0 | 4.6 | 2024-07-20 | 26.1 | 0 | 8.1 | 2023-07-20 | 25.9 | 0 | 7.9 | 2022-07-20 | 28.6 | 0 | 10.6 | 2021-07-20 | 25.3 | 0 | 7.3 | 2020-07-20 | 28.6 | 0 | 10.6 | 2019-07-20 | 32 | 0 | 14 | 2018-07-20 | 28.8 | 0 | 10.8 | 2017-07-20 | 27.5 | 0 | 9.5 | 2016-07-20 | 25.5 | 0 | 7.5 | 0 | 9.09
2025-07-20 | 24.3 | 0 | 6.3 | 2024-07-20 | 26.4 | 0 | 8.4 | 2023-07-20 | 26.1 | 0 | 8.1 | 2022-07-20 | 29.2 | 0 | 11.2 | 2021-07-20 | 26.1 | 0 | 8.1 | 2020-07-20 | 28.1 | 0 | 10.1 | 2019-07-20 | 33.6 | 0 | 15.6 | 2018-07-20 | 30.3 | 0 | 12.3 | 2017-07-20 | 26.8 | 0 | 8.8 | 2016-07-20 | 26.1 | 0 | 8.1 | 0 | 9.7
2025-07-20 | 25.3 | 0 | 7.3 | 2024-07-20 | 26.5 | 0 | 8.5 | 2023-07-20 | 26 | 0 | 8 | 2022-07-20 | 31.1 | 0 | 13.1 | 2021-07-20 | 24.2 | 0 | 6.2 | 2020-07-20 | 27.4 | 0 | 9.4 | 2019-07-20 | 31.9 | 0 | 13.9 | 2018-07-20 | 30.2 | 0 | 12.2 | 2017-07-20 | 27.8 | 0 | 9.8 | 2016-07-20 | 26.6 | 0 | 8.6 | 0 | 9.7
2025-07-20 | 24.4 | 0 | 6.4 | 2024-07-20 | 27.8 | 0 | 9.8 | 2023-07-20 | 26.9 | 0 | 8.9 | 2022-07-20 | 29 | 0 | 11 | 2021-07-20 | 16.9 | 1.1 | 0 | 2020-07-20 | 26.8 | 0 | 8.8 | 2019-07-20 | 33.2 | 0 | 15.2 | 2018-07-20 | 30.7 | 0 | 12.7 | 2017-07-20 | 28.1 | 0 | 10.1 | 2016-07-20 | 26.1 | 0 | 8.1 | 0.11 | 9.1
2025-07-20 | 24.2 | 0 | 6.2 | 2024-07-20 | 26.1 | 0 | 8.1 | 2023-07-20 | 26.2 | 0 | 8.2 | 2022-07-20 | 29.9 | 0 | 11.9 | 2021-07-20 | 17.3 | 0.7 | 0 | 2020-07-20 | 26.9 | 0 | 8.9 | 2019-07-20 | 30.3 | 0 | 12.3 | 2018-07-20 | 31 | 0 | 13 | 2017-07-20 | 27.4 | 0 | 9.4 | 2016-07-20 | 26.5 | 0 | 8.5 | 0.07 | 8.65
2025-07-20 | 24 | 0 | 6 | 2024-07-20 | 23.6 | 0 | 5.6 | 2023-07-20 | 26 | 0 | 8 | 2022-07-20 | 27.9 | 0 | 9.9 | 2021-07-20 | 18.1 | 0 | 0.1 | 2020-07-20 | 27.3 | 0 | 9.3 | 2019-07-20 | 28.1 | 0 | 10.1 | 2018-07-20 | 30.7 | 0 | 12.7 | 2017-07-20 | 26.1 | 0 | 8.1 | 2016-07-20 | 26.9 | 0 | 8.9 | 0 | 7.87
2025-07-20 | 23.7 | 0 | 5.7 | 2024-07-20 | 22.7 | 0 | 4.7 | 2023-07-20 | 25.2 | 0 | 7.2 | 2022-07-20 | 27.6 | 0 | 9.6 | 2021-07-20 | 18.3 | 0 | 0.3 | 2020-07-20 | 25.3 | 0 | 7.3 | 2019-07-20 | 26.4 | 0 | 8.4 | 2018-07-20 | 30.2 | 0 | 12.2 | 2017-07-20 | 26.1 | 0 | 8.1 | 2016-07-20 | 26.5 | 0 | 8.5 | 0 | 7.2
2025-07-20 | 22.4 | 0 | 4.4 | 2024-07-20 | 21.2 | 0 | 3.2 | 2023-07-20 | 23.2 | 0 | 5.2 | 2022-07-20 | 26.2 | 0 | 8.2 | 2021-07-20 | 17.9 | 0.1 | 0 | 2020-07-20 | 24.4 | 0 | 6.4 | 2019-07-20 | 25.7 | 0 | 7.7 | 2018-07-20 | 27.6 | 0 | 9.6 | 2017-07-20 | 24.4 | 0 | 6.4 | 2016-07-20 | 24.1 | 0 | 6.1 | 0.01 | 5.72
2025-07-20 | 18 | 0 | 0 | 2024-07-20 | 18.9 | 0 | 0.9 | 2023-07-20 | 20.6 | 0 | 2.6 | 2022-07-20 | 25 | 0 | 7 | 2021-07-20 | 17.6 | 0.4 | 0 | 2020-07-20 | 23.6 | 0 | 5.6 | 2019-07-20 | 24.8 | 0 | 6.8 | 2018-07-20 | 25 | 0 | 7 | 2017-07-20 | 22.5 | 0 | 4.5 | 2016-07-20 | 22.5 | 0 | 4.5 | 0.04 | 3.89
2025-07-20 | 18.7 | 0 | 0.7 | 2024-07-20 | 18.5 | 0 | 0.5 | 2023-07-20 | 20.9 | 0 | 2.9 | 2022-07-20 | 24.4 | 0 | 6.4 | 2021-07-20 | 17.4 | 0.6 | 0 | 2020-07-20 | 22.7 | 0 | 4.7 | 2019-07-20 | 25.4 | 0 | 7.4 | 2018-07-20 | 23.2 | 0 | 5.2 | 2017-07-20 | 21.3 | 0 | 3.3 | 2016-07-20 | 21.1 | 0 | 3.1 | 0.06 | 3.42
2025-07-20 | 17.9 | 0.1 | 0 | 2024-07-20 | 18.7 | 0 | 0.7 | 2023-07-20 | 20.9 | 0 | 2.9 | 2022-07-20 | 25 | 0 | 7 | 2021-07-20 | 17.1 | 0.9 | 0 | 2020-07-20 | 21.7 | 0 | 3.7 | 2019-07-20 | 25.1 | 0 | 7.1 | 2018-07-20 | 21.1 | 0 | 3.1 | 2017-07-20 | 20.1 | 0 | 2.1 | 2016-07-20 | 19.7 | 0 | 1.7 | 0.1 | 2.83
2025-07-20 | 17.1 | 0.9 | 0 | 2024-07-20 | 18.4 | 0 | 0.4 | 2023-07-20 | 21 | 0 | 3 | 2022-07-20 | 24.7 | 0 | 6.7 | 2021-07-20 | 16.7 | 1.3 | 0 | 2020-07-20 | 21.3 | 0 | 3.3 | 2019-07-20 | 24.6 | 0 | 6.6 | 2018-07-20 | 20.1 | 0 | 2.1 | 2017-07-20 | 19.2 | 0 | 1.2 | 2016-07-20 | 17.9 | 0.1 | 0 | 0.23 | 2.33
2025-07-21 | 16.6 | 1.4 | 0 | 2024-07-21 | 18.7 | 0 | 0.7 | 2023-07-21 | 19.9 | 0 | 1.9 | 2022-07-21 | 25.6 | 0 | 7.6 | 2021-07-21 | 16.4 | 1.6 | 0 | 2020-07-21 | 20.5 | 0 | 2.5 | 2019-07-21 | 23.5 | 0 | 5.5 | 2018-07-21 | 20.3 | 0 | 2.3 | 2017-07-21 | 17.8 | 0.2 | 0 | 2016-07-21 | 16.3 | 1.7 | 0 | 0.49 | 2.05
2025-07-21 | 15.7 | 2.3 | 0 | 2024-07-21 | 18.1 | 0 | 0.1 | 2023-07-21 | 18.7 | 0 | 0.7 | 2022-07-21 | 26.5 | 0 | 8.5 | 2021-07-21 | 16 | 2 | 0 | 2020-07-21 | 19.8 | 0 | 1.8 | 2019-07-21 | 23.4 | 0 | 5.4 | 2018-07-21 | 20.2 | 0 | 2.2 | 2017-07-21 | 18 | 0 | 0 | 2016-07-21 | 15.8 | 2.2 | 0 | 0.65 | 1.87
2025-07-21 | 14.5 | 3.5 | 0 | 2024-07-21 | 16.4 | 1.6 | 0 | 2023-07-21 | 18 | 0 | 0 | 2022-07-21 | 23.6 | 0 | 5.6 | 2021-07-21 | 16.1 | 1.9 | 0 | 2020-07-21 | 19.4 | 0 | 1.4 | 2019-07-21 | 23.7 | 0 | 5.7 | 2018-07-21 | 19.9 | 0 | 1.9 | 2017-07-21 | 16.9 | 1.1 | 0 | 2016-07-21 | 14.8 | 3.2 | 0 | 1.13 | 1.46
2025-07-21 | 13.7 | 4.3 | 0 | 2024-07-21 | 16 | 2 | 0 | 2023-07-21 | 18.1 | 0 | 0.1 | 2022-07-21 | 23.5 | 0 | 5.5 | 2021-07-21 | 16.2 | 1.8 | 0 | 2020-07-21 | 18.6 | 0 | 0.6 | 2019-07-21 | 23.2 | 0 | 5.2 | 2018-07-21 | 19.1 | 0 | 1.1 | 2017-07-21 | 16.6 | 1.4 | 0 | 2016-07-21 | 14.6 | 3.4 | 0 | 1.29 | 1.25
2025-07-21 | 13.1 | 4.9 | 0 | 2024-07-21 | 15.6 | 2.4 | 0 | 2023-07-21 | 17.7 | 0.3 | 0 | 2022-07-21 | 23.3 | 0 | 5.3 | 2021-07-21 | 16.2 | 1.8 | 0 | 2020-07-21 | 17.3 | 0.7 | 0 | 2019-07-21 | 23.2 | 0 | 5.2 | 2018-07-21 | 17.6 | 0.4 | 0 | 2017-07-21 | 16.2 | 1.8 | 0 | 2016-07-21 | 13.5 | 4.5 | 0 | 1.68 | 1.05
2025-07-21 | 12.7 | 5.3 | 0 | 2024-07-21 | 15 | 3 | 0 | 2023-07-21 | 18 | 0 | 0 | 2022-07-21 | 22.2 | 0 | 4.2 | 2021-07-21 | 16 | 2 | 0 | 2020-07-21 | 17.5 | 0.5 | 0 | 2019-07-21 | 23.9 | 0 | 5.9 | 2018-07-21 | 16.9 | 1.1 | 0 | 2017-07-21 | 16.4 | 1.6 | 0 | 2016-07-21 | 13.9 | 4.1 | 0 | 1.76 | 1.01
2025-07-21 | 13.9 | 4.1 | 0 | 2024-07-21 | 15.1 | 2.9 | 0 | 2023-07-21 | 18.1 | 0 | 0.1 | 2022-07-21 | 22.5 | 0 | 4.5 | 2021-07-21 | 15.9 | 2.1 | 0 | 2020-07-21 | 18.2 | 0 | 0.2 | 2019-07-21 | 24 | 0 | 6 | 2018-07-21 | 19.7 | 0 | 1.7 | 2017-07-21 | 17.3 | 0.7 | 0 | 2016-07-21 | 15.6 | 2.4 | 0 | 1.22 | 1.25
2025-07-21 | 15.1 | 2.9 | 0 | 2024-07-21 | 16.6 | 1.4 | 0 | 2023-07-21 | 18.7 | 0 | 0.7 | 2022-07-21 | 23 | 0 | 5 | 2021-07-21 | 17.5 | 0.5 | 0 | 2020-07-21 | 19.6 | 0 | 1.6 | 2019-07-21 | 24.4 | 0 | 6.4 | 2018-07-21 | 22.1 | 0 | 4.1 | 2017-07-21 | 19.7 | 0 | 1.7 | 2016-07-21 | 18.1 | 0 | 0.1 | 0.48 | 1.96
2025-07-21 | 16.4 | 1.6 | 0 | 2024-07-21 | 18.3 | 0 | 0.3 | 2023-07-21 | 18.9 | 0 | 0.9 | 2022-07-21 | 23.7 | 0 | 5.7 | 2021-07-21 | 18.5 | 0 | 0.5 | 2020-07-21 | 21.4 | 0 | 3.4 | 2019-07-21 | 26.1 | 0 | 8.1 | 2018-07-21 | 24.4 | 0 | 6.4 | 2017-07-21 | 21.2 | 0 | 3.2 | 2016-07-21 | 21 | 0 | 3 | 0.16 | 3.15
2025-07-21 | 16.7 | 1.3 | 0 | 2024-07-21 | 19.7 | 0 | 1.7 | 2023-07-21 | 20.6 | 0 | 2.6 | 2022-07-21 | 26.3 | 0 | 8.3 | 2021-07-21 | 19.9 | 0 | 1.9 | 2020-07-21 | 21.3 | 0 | 3.3 | 2019-07-21 | 26.7 | 0 | 8.7 | 2018-07-21 | 25.9 | 0 | 7.9 | 2017-07-21 | 22.8 | 0 | 4.8 | 2016-07-21 | 24 | 0 | 6 | 0.13 | 4.52
2025-07-21 | 18.2 | 0 | 0.2 | 2024-07-21 | 20.8 | 0 | 2.8 | 2023-07-21 | 19.7 | 0 | 1.7 | 2022-07-21 | 26.9 | 0 | 8.9 | 2021-07-21 | 20.2 | 0 | 2.2 | 2020-07-21 | 23.4 | 0 | 5.4 | 2019-07-21 | 27.9 | 0 | 9.9 | 2018-07-21 | 27.4 | 0 | 9.4 | 2017-07-21 | 22.9 | 0 | 4.9 | 2016-07-21 | 26.2 | 0 | 8.2 | 0 | 5.36
2025-07-21 | 19.4 | 0 | 1.4 | 2024-07-21 | 22.1 | 0 | 4.1 | 2023-07-21 | 19.8 | 0 | 1.8 | 2022-07-21 | 23.1 | 0 | 5.1 | 2021-07-21 | 21.3 | 0 | 3.3 | 2020-07-21 | 21.9 | 0 | 3.9 | 2019-07-21 | 29 | 0 | 11 | 2018-07-21 | 27.9 | 0 | 9.9 | 2017-07-21 | 23.7 | 0 | 5.7 | 2016-07-21 | 28.1 | 0 | 10.1 | 0 | 5.63
2025-07-21 | 19.7 | 0 | 1.7 | 2024-07-21 | 23.2 | 0 | 5.2 | 2023-07-21 | 21.1 | 0 | 3.1 | 2022-07-21 | 27.5 | 0 | 9.5 | 2021-07-21 | 21.6 | 0 | 3.6 | 2020-07-21 | 23.4 | 0 | 5.4 | 2019-07-21 | 29.4 | 0 | 11.4 | 2018-07-21 | 27.4 | 0 | 9.4 | 2017-07-21 | 25.2 | 0 | 7.2 | 2016-07-21 | 29.6 | 0 | 11.6 | 0 | 6.81
2025-07-21 | 20.3 | 0 | 2.3 | 2024-07-21 | 23.4 | 0 | 5.4 | 2023-07-21 | 21 | 0 | 3 | 2022-07-21 | 27.6 | 0 | 9.6 | 2021-07-21 | 23.6 | 0 | 5.6 | 2020-07-21 | 23.2 | 0 | 5.2 | 2019-07-21 | 29.8 | 0 | 11.8 | 2018-07-21 | 29.3 | 0 | 11.3 | 2017-07-21 | 26.4 | 0 | 8.4 | 2016-07-21 | 31 | 0 | 13 | 0 | 7.56
2025-07-21 | 19.8 | 0 | 1.8 | 2024-07-21 | 23.7 | 0 | 5.7 | 2023-07-21 | 22.2 | 0 | 4.2 | 2022-07-21 | 27.1 | 0 | 9.1 | 2021-07-21 | 24.7 | 0 | 6.7 | 2020-07-21 | 25.8 | 0 | 7.8 | 2019-07-21 | 28.6 | 0 | 10.6 | 2018-07-21 | 30.1 | 0 | 12.1 | 2017-07-21 | 27.4 | 0 | 9.4 | 2016-07-21 | 31.7 | 0 | 13.7 | 0 | 8.11
2025-07-21 | 21 | 0 | 3 | 2024-07-21 | 24.1 | 0 | 6.1 | 2023-07-21 | 22.5 | 0 | 4.5 | 2022-07-21 | 22.3 | 0 | 4.3 | 2021-07-21 | 25.6 | 0 | 7.6 | 2020-07-21 | 24.9 | 0 | 6.9 | 2019-07-21 | 30.2 | 0 | 12.2 | 2018-07-21 | 31.2 | 0 | 13.2 | 2017-07-21 | 28.3 | 0 | 10.3 | 2016-07-21 | 31.2 | 0 | 13.2 | 0 | 8.13
2025-07-21 | 20.3 | 0 | 2.3 | 2024-07-21 | 24 | 0 | 6 | 2023-07-21 | 21.6 | 0 | 3.6 | 2022-07-21 | 25.8 | 0 | 7.8 | 2021-07-21 | 24.4 | 0 | 6.4 | 2020-07-21 | 25.6 | 0 | 7.6 | 2019-07-21 | 28.9 | 0 | 10.9 | 2018-07-21 | 31 | 0 | 13 | 2017-07-21 | 27.9 | 0 | 9.9 | 2016-07-21 | 30.7 | 0 | 12.7 | 0 | 8.02
2025-07-21 | 19.6 | 0 | 1.6 | 2024-07-21 | 23.8 | 0 | 5.8 | 2023-07-21 | 20.5 | 0 | 2.5 | 2022-07-21 | 25.5 | 0 | 7.5 | 2021-07-21 | 24.9 | 0 | 6.9 | 2020-07-21 | 25.6 | 0 | 7.6 | 2019-07-21 | 28.1 | 0 | 10.1 | 2018-07-21 | 30.2 | 0 | 12.2 | 2017-07-21 | 27.6 | 0 | 9.6 | 2016-07-21 | 28.9 | 0 | 10.9 | 0 | 7.47
2025-07-21 | 19.5 | 0 | 1.5 | 2024-07-21 | 23.1 | 0 | 5.1 | 2023-07-21 | 19.2 | 0 | 1.2 | 2022-07-21 | 25 | 0 | 7 | 2021-07-21 | 24.3 | 0 | 6.3 | 2020-07-21 | 24.7 | 0 | 6.7 | 2019-07-21 | 27 | 0 | 9 | 2018-07-21 | 28.5 | 0 | 10.5 | 2017-07-21 | 26.7 | 0 | 8.7 | 2016-07-21 | 27.7 | 0 | 9.7 | 0 | 6.57
2025-07-21 | 18.2 | 0 | 0.2 | 2024-07-21 | 21.3 | 0 | 3.3 | 2023-07-21 | 17.5 | 0.5 | 0 | 2022-07-21 | 24.1 | 0 | 6.1 | 2021-07-21 | 22.9 | 0 | 4.9 | 2020-07-21 | 23 | 0 | 5 | 2019-07-21 | 25.7 | 0 | 7.7 | 2018-07-21 | 27.4 | 0 | 9.4 | 2017-07-21 | 24.2 | 0 | 6.2 | 2016-07-21 | 26.4 | 0 | 8.4 | 0.05 | 5.12
2025-07-21 | 16.4 | 1.6 | 0 | 2024-07-21 | 19.7 | 0 | 1.7 | 2023-07-21 | 17.6 | 0.4 | 0 | 2022-07-21 | 22.9 | 0 | 4.9 | 2021-07-21 | 21.1 | 0 | 3.1 | 2020-07-21 | 19.4 | 0 | 1.4 | 2019-07-21 | 23.9 | 0 | 5.9 | 2018-07-21 | 25.6 | 0 | 7.6 | 2017-07-21 | 23 | 0 | 5 | 2016-07-21 | 25.4 | 0 | 7.4 | 0.2 | 3.7
2025-07-21 | 15 | 3 | 0 | 2024-07-21 | 19.3 | 0 | 1.3 | 2023-07-21 | 17.8 | 0.2 | 0 | 2022-07-21 | 23.6 | 0 | 5.6 | 2021-07-21 | 18.8 | 0 | 0.8 | 2020-07-21 | 18.8 | 0 | 0.8 | 2019-07-21 | 23 | 0 | 5 | 2018-07-21 | 23.9 | 0 | 5.9 | 2017-07-21 | 22.1 | 0 | 4.1 | 2016-07-21 | 25.2 | 0 | 7.2 | 0.32 | 3.07
2025-07-21 | 14.7 | 3.3 | 0 | 2024-07-21 | 16 | 2 | 0 | 2023-07-21 | 17.5 | 0.5 | 0 | 2022-07-21 | 22 | 0 | 4 | 2021-07-21 | 18.3 | 0 | 0.3 | 2020-07-21 | 18.3 | 0 | 0.3 | 2019-07-21 | 21.8 | 0 | 3.8 | 2018-07-21 | 22.2 | 0 | 4.2 | 2017-07-21 | 19.6 | 0 | 1.6 | 2016-07-21 | 24.5 | 0 | 6.5 | 0.58 | 2.07
2025-07-21 | 12.7 | 5.3 | 0 | 2024-07-21 | 15.1 | 2.9 | 0 | 2023-07-21 | 17.4 | 0.6 | 0 | 2022-07-21 | 20.9 | 0 | 2.9 | 2021-07-21 | 17 | 1 | 0 | 2020-07-21 | 17.8 | 0.2 | 0 | 2019-07-21 | 20.4 | 0 | 2.4 | 2018-07-21 | 21.2 | 0 | 3.2 | 2017-07-21 | 18.3 | 0 | 0.3 | 2016-07-21 | 24.7 | 0 | 6.7 | 1 | 1.55
2025-07-22 | 11.6 | 6.4 | 0 | 2024-07-22 | 13.7 | 4.3 | 0 | 2023-07-22 | 17.7 | 0.3 | 0 | 2022-07-22 | 20.1 | 0 | 2.1 | 2021-07-22 | 16.3 | 1.7 | 0 | 2020-07-22 | 17.1 | 0.9 | 0 | 2019-07-22 | 18.4 | 0 | 0.4 | 2018-07-22 | 18.9 | 0 | 0.9 | 2017-07-22 | 19.7 | 0 | 1.7 | 2016-07-22 | 25.1 | 0 | 7.1 | 1.36 | 1.22
2025-07-22 | 11.1 | 6.9 | 0 | 2024-07-22 | 15.6 | 2.4 | 0 | 2023-07-22 | 17.5 | 0.5 | 0 | 2022-07-22 | 19.1 | 0 | 1.1 | 2021-07-22 | 16.1 | 1.9 | 0 | 2020-07-22 | 17.1 | 0.9 | 0 | 2019-07-22 | 17.2 | 0.8 | 0 | 2018-07-22 | 19.3 | 0 | 1.3 | 2017-07-22 | 17.5 | 0.5 | 0 | 2016-07-22 | 24.5 | 0 | 6.5 | 1.39 | 0.89
2025-07-22 | 11 | 7 | 0 | 2024-07-22 | 13.4 | 4.6 | 0 | 2023-07-22 | 16.8 | 1.2 | 0 | 2022-07-22 | 18 | 0 | 0 | 2021-07-22 | 14.3 | 3.7 | 0 | 2020-07-22 | 16.4 | 1.6 | 0 | 2019-07-22 | 16.7 | 1.3 | 0 | 2018-07-22 | 17.3 | 0.7 | 0 | 2017-07-22 | 17.2 | 0.8 | 0 | 2016-07-22 | 23.9 | 0 | 5.9 | 2.09 | 0.59
2025-07-22 | 11.5 | 6.5 | 0 | 2024-07-22 | 12.9 | 5.1 | 0 | 2023-07-22 | 16.8 | 1.2 | 0 | 2022-07-22 | 17.6 | 0.4 | 0 | 2021-07-22 | 15 | 3 | 0 | 2020-07-22 | 15.9 | 2.1 | 0 | 2019-07-22 | 16.4 | 1.6 | 0 | 2018-07-22 | 17.8 | 0.2 | 0 | 2017-07-22 | 16.7 | 1.3 | 0 | 2016-07-22 | 23.4 | 0 | 5.4 | 2.14 | 0.54
2025-07-22 | 9.8 | 8.2 | 0 | 2024-07-22 | 12.3 | 5.7 | 0 | 2023-07-22 | 16.7 | 1.3 | 0 | 2022-07-22 | 17.1 | 0.9 | 0 | 2021-07-22 | 14.2 | 3.8 | 0 | 2020-07-22 | 15.9 | 2.1 | 0 | 2019-07-22 | 17.2 | 0.8 | 0 | 2018-07-22 | 17.2 | 0.8 | 0 | 2017-07-22 | 17.1 | 0.9 | 0 | 2016-07-22 | 23.4 | 0 | 5.4 | 2.45 | 0.54
2025-07-22 | 11.6 | 6.4 | 0 | 2024-07-22 | 11.9 | 6.1 | 0 | 2023-07-22 | 16.2 | 1.8 | 0 | 2022-07-22 | 16.9 | 1.1 | 0 | 2021-07-22 | 14.5 | 3.5 | 0 | 2020-07-22 | 15.8 | 2.2 | 0 | 2019-07-22 | 16.5 | 1.5 | 0 | 2018-07-22 | 16.9 | 1.1 | 0 | 2017-07-22 | 17.4 | 0.6 | 0 | 2016-07-22 | 23.2 | 0 | 5.2 | 2.43 | 0.52
2025-07-22 | 13.3 | 4.7 | 0 | 2024-07-22 | 14 | 4 | 0 | 2023-07-22 | 16.4 | 1.6 | 0 | 2022-07-22 | 18.3 | 0 | 0.3 | 2021-07-22 | 15.1 | 2.9 | 0 | 2020-07-22 | 16.9 | 1.1 | 0 | 2019-07-22 | 16.8 | 1.2 | 0 | 2018-07-22 | 17.5 | 0.5 | 0 | 2017-07-22 | 18 | 0 | 0 | 2016-07-22 | 23.6 | 0 | 5.6 | 1.6 | 0.59
2025-07-22 | 15.5 | 2.5 | 0 | 2024-07-22 | 17.2 | 0.8 | 0 | 2023-07-22 | 18 | 0 | 0 | 2022-07-22 | 20.2 | 0 | 2.2 | 2021-07-22 | 16.9 | 1.1 | 0 | 2020-07-22 | 18 | 0 | 0 | 2019-07-22 | 17.6 | 0.4 | 0 | 2018-07-22 | 18.4 | 0 | 0.4 | 2017-07-22 | 19.3 | 0 | 1.3 | 2016-07-22 | 24.7 | 0 | 6.7 | 0.48 | 1.06
2025-07-22 | 17.6 | 0.4 | 0 | 2024-07-22 | 19.4 | 0 | 1.4 | 2023-07-22 | 18.9 | 0 | 0.9 | 2022-07-22 | 22.2 | 0 | 4.2 | 2021-07-22 | 18.5 | 0 | 0.5 | 2020-07-22 | 20.2 | 0 | 2.2 | 2019-07-22 | 18.1 | 0 | 0.1 | 2018-07-22 | 19.1 | 0 | 1.1 | 2017-07-22 | 19.8 | 0 | 1.8 | 2016-07-22 | 25.2 | 0 | 7.2 | 0.04 | 1.94
2025-07-22 | 19.2 | 0 | 1.2 | 2024-07-22 | 21.8 | 0 | 3.8 | 2023-07-22 | 20.2 | 0 | 2.2 | 2022-07-22 | 23.5 | 0 | 5.5 | 2021-07-22 | 20.2 | 0 | 2.2 | 2020-07-22 | 22.2 | 0 | 4.2 | 2019-07-22 | 19.1 | 0 | 1.1 | 2018-07-22 | 17.9 | 0.1 | 0 | 2017-07-22 | 21.3 | 0 | 3.3 | 2016-07-22 | 27.1 | 0 | 9.1 | 0.01 | 3.26
2025-07-22 | 19.3 | 0 | 1.3 | 2024-07-22 | 23.4 | 0 | 5.4 | 2023-07-22 | 21.2 | 0 | 3.2 | 2022-07-22 | 24.9 | 0 | 6.9 | 2021-07-22 | 22.3 | 0 | 4.3 | 2020-07-22 | 23.3 | 0 | 5.3 | 2019-07-22 | 19.6 | 0 | 1.6 | 2018-07-22 | 17.1 | 0.9 | 0 | 2017-07-22 | 22.6 | 0 | 4.6 | 2016-07-22 | 28.6 | 0 | 10.6 | 0.09 | 4.32
2025-07-22 | 19.5 | 0 | 1.5 | 2024-07-22 | 24.6 | 0 | 6.6 | 2023-07-22 | 22.5 | 0 | 4.5 | 2022-07-22 | 27 | 0 | 9 | 2021-07-22 | 23.2 | 0 | 5.2 | 2020-07-22 | 25.4 | 0 | 7.4 | 2019-07-22 | 20 | 0 | 2 | 2018-07-22 | 17.2 | 0.8 | 0 | 2017-07-22 | 23.2 | 0 | 5.2 | 2016-07-22 | 30 | 0 | 12 | 0.08 | 5.34
2025-07-22 | 20.4 | 0 | 2.4 | 2024-07-22 | 25.6 | 0 | 7.6 | 2023-07-22 | 24 | 0 | 6 | 2022-07-22 | 28.6 | 0 | 10.6 | 2021-07-22 | 24.4 | 0 | 6.4 | 2020-07-22 | 25 | 0 | 7 | 2019-07-22 | 21.1 | 0 | 3.1 | 2018-07-22 | 17.9 | 0.1 | 0 | 2017-07-22 | 24.5 | 0 | 6.5 | 2016-07-22 | 31.5 | 0 | 13.5 | 0.01 | 6.31
2025-07-22 | 20.9 | 0 | 2.9 | 2024-07-22 | 25.9 | 0 | 7.9 | 2023-07-22 | 24.4 | 0 | 6.4 | 2022-07-22 | 28.5 | 0 | 10.5 | 2021-07-22 | 24 | 0 | 6 | 2020-07-22 | 24.8 | 0 | 6.8 | 2019-07-22 | 21.7 | 0 | 3.7 | 2018-07-22 | 19.9 | 0 | 1.9 | 2017-07-22 | 24.5 | 0 | 6.5 | 2016-07-22 | 32.4 | 0 | 14.4 | 0 | 6.7
2025-07-22 | 22.3 | 0 | 4.3 | 2024-07-22 | 26.1 | 0 | 8.1 | 2023-07-22 | 25 | 0 | 7 | 2022-07-22 | 28.9 | 0 | 10.9 | 2021-07-22 | 25.3 | 0 | 7.3 | 2020-07-22 | 23.8 | 0 | 5.8 | 2019-07-22 | 22.9 | 0 | 4.9 | 2018-07-22 | 22.1 | 0 | 4.1 | 2017-07-22 | 25.1 | 0 | 7.1 | 2016-07-22 | 33.1 | 0 | 15.1 | 0 | 7.46
2025-07-22 | 22.5 | 0 | 4.5 | 2024-07-22 | 26.2 | 0 | 8.2 | 2023-07-22 | 25.2 | 0 | 7.2 | 2022-07-22 | 28.9 | 0 | 10.9 | 2021-07-22 | 24.8 | 0 | 6.8 | 2020-07-22 | 19 | 0 | 1 | 2019-07-22 | 22.8 | 0 | 4.8 | 2018-07-22 | 23.5 | 0 | 5.5 | 2017-07-22 | 25.6 | 0 | 7.6 | 2016-07-22 | 33.4 | 0 | 15.4 | 0 | 7.19
2025-07-22 | 23.1 | 0 | 5.1 | 2024-07-22 | 26.7 | 0 | 8.7 | 2023-07-22 | 25.4 | 0 | 7.4 | 2022-07-22 | 28.1 | 0 | 10.1 | 2021-07-22 | 22.2 | 0 | 4.2 | 2020-07-22 | 19.7 | 0 | 1.7 | 2019-07-22 | 22.7 | 0 | 4.7 | 2018-07-22 | 23.9 | 0 | 5.9 | 2017-07-22 | 24.7 | 0 | 6.7 | 2016-07-22 | 33.7 | 0 | 15.7 | 0 | 7.02
2025-07-22 | 22.4 | 0 | 4.4 | 2024-07-22 | 26.5 | 0 | 8.5 | 2023-07-22 | 24.9 | 0 | 6.9 | 2022-07-22 | 27.8 | 0 | 9.8 | 2021-07-22 | 22.8 | 0 | 4.8 | 2020-07-22 | 19.6 | 0 | 1.6 | 2019-07-22 | 22.9 | 0 | 4.9 | 2018-07-22 | 24.4 | 0 | 6.4 | 2017-07-22 | 24.2 | 0 | 6.2 | 2016-07-22 | 31.6 | 0 | 13.6 | 0 | 6.71
2025-07-22 | 22.1 | 0 | 4.1 | 2024-07-22 | 25.6 | 0 | 7.6 | 2023-07-22 | 23.9 | 0 | 5.9 | 2022-07-22 | 24.9 | 0 | 6.9 | 2021-07-22 | 16.9 | 1.1 | 0 | 2020-07-22 | 19 | 0 | 1 | 2019-07-22 | 21.7 | 0 | 3.7 | 2018-07-22 | 24.3 | 0 | 6.3 | 2017-07-22 | 24.1 | 0 | 6.1 | 2016-07-22 | 30.7 | 0 | 12.7 | 0.11 | 5.43
2025-07-22 | 20 | 0 | 2 | 2024-07-22 | 24.3 | 0 | 6.3 | 2023-07-22 | 21.4 | 0 | 3.4 | 2022-07-22 | 23.4 | 0 | 5.4 | 2021-07-22 | 17.2 | 0.8 | 0 | 2020-07-22 | 18.8 | 0 | 0.8 | 2019-07-22 | 20.2 | 0 | 2.2 | 2018-07-22 | 23 | 0 | 5 | 2017-07-22 | 22.2 | 0 | 4.2 | 2016-07-22 | 27.9 | 0 | 9.9 | 0.08 | 3.92
2025-07-22 | 17.5 | 0.5 | 0 | 2024-07-22 | 22.2 | 0 | 4.2 | 2023-07-22 | 20.1 | 0 | 2.1 | 2022-07-22 | 22.2 | 0 | 4.2 | 2021-07-22 | 16.7 | 1.3 | 0 | 2020-07-22 | 18.4 | 0 | 0.4 | 2019-07-22 | 18.5 | 0 | 0.5 | 2018-07-22 | 22.5 | 0 | 4.5 | 2017-07-22 | 21.1 | 0 | 3.1 | 2016-07-22 | 21.6 | 0 | 3.6 | 0.18 | 2.26
2025-07-22 | 16.8 | 1.2 | 0 | 2024-07-22 | 20.3 | 0 | 2.3 | 2023-07-22 | 19.2 | 0 | 1.2 | 2022-07-22 | 21 | 0 | 3 | 2021-07-22 | 14.6 | 3.4 | 0 | 2020-07-22 | 18.1 | 0 | 0.1 | 2019-07-22 | 17.6 | 0.4 | 0 | 2018-07-22 | 21.5 | 0 | 3.5 | 2017-07-22 | 20.7 | 0 | 2.7 | 2016-07-22 | 21.3 | 0 | 3.3 | 0.5 | 1.61
2025-07-22 | 16.9 | 1.1 | 0 | 2024-07-22 | 20.1 | 0 | 2.1 | 2023-07-22 | 16.7 | 1.3 | 0 | 2022-07-22 | 20.7 | 0 | 2.7 | 2021-07-22 | 15.6 | 2.4 | 0 | 2020-07-22 | 17.9 | 0.1 | 0 | 2019-07-22 | 17 | 1 | 0 | 2018-07-22 | 20.9 | 0 | 2.9 | 2017-07-22 | 19.5 | 0 | 1.5 | 2016-07-22 | 21.6 | 0 | 3.6 | 0.59 | 1.28
2025-07-22 | 14.8 | 3.2 | 0 | 2024-07-22 | 19.4 | 0 | 1.4 | 2023-07-22 | 16.5 | 1.5 | 0 | 2022-07-22 | 20.2 | 0 | 2.2 | 2021-07-22 | 14.5 | 3.5 | 0 | 2020-07-22 | 18.1 | 0 | 0.1 | 2019-07-22 | 16.6 | 1.4 | 0 | 2018-07-22 | 21.5 | 0 | 3.5 | 2017-07-22 | 19.1 | 0 | 1.1 | 2016-07-22 | 21.1 | 0 | 3.1 | 0.96 | 1.14
2025-07-23 | 14.9 | 3.1 | 0 | 2024-07-23 | 18.5 | 0 | 0.5 | 2023-07-23 | 14.1 | 3.9 | 0 | 2022-07-23 | 19.8 | 0 | 1.8 | 2021-07-23 | 13.9 | 4.1 | 0 | 2020-07-23 | 18.1 | 0 | 0.1 | 2019-07-23 | 14.4 | 3.6 | 0 | 2018-07-23 | 20.7 | 0 | 2.7 | 2017-07-23 | 17.5 | 0.5 | 0 | 2016-07-23 | 21 | 0 | 3 | 1.52 | 0.81
2025-07-23 | 15.1 | 2.9 | 0 | 2024-07-23 | 18.1 | 0 | 0.1 | 2023-07-23 | 14.3 | 3.7 | 0 | 2022-07-23 | 19.2 | 0 | 1.2 | 2021-07-23 | 14.2 | 3.8 | 0 | 2020-07-23 | 18.2 | 0 | 0.2 | 2019-07-23 | 14 | 4 | 0 | 2018-07-23 | 20.5 | 0 | 2.5 | 2017-07-23 | 17.2 | 0.8 | 0 | 2016-07-23 | 21.1 | 0 | 3.1 | 1.52 | 0.71
2025-07-23 | 13.6 | 4.4 | 0 | 2024-07-23 | 17.9 | 0.1 | 0 | 2023-07-23 | 14.1 | 3.9 | 0 | 2022-07-23 | 18.6 | 0 | 0.6 | 2021-07-23 | 15.1 | 2.9 | 0 | 2020-07-23 | 18.2 | 0 | 0.2 | 2019-07-23 | 13.3 | 4.7 | 0 | 2018-07-23 | 20.5 | 0 | 2.5 | 2017-07-23 | 17.2 | 0.8 | 0 | 2016-07-23 | 20.1 | 0 | 2.1 | 1.68 | 0.54
2025-07-23 | 12.5 | 5.5 | 0 | 2024-07-23 | 18.3 | 0 | 0.3 | 2023-07-23 | 13.2 | 4.8 | 0 | 2022-07-23 | 19.2 | 0 | 1.2 | 2021-07-23 | 14.2 | 3.8 | 0 | 2020-07-23 | 18.1 | 0 | 0.1 | 2019-07-23 | 12.5 | 5.5 | 0 | 2018-07-23 | 20 | 0 | 2 | 2017-07-23 | 17.5 | 0.5 | 0 | 2016-07-23 | 19.6 | 0 | 1.6 | 2.01 | 0.52
2025-07-23 | 12.3 | 5.7 | 0 | 2024-07-23 | 17.3 | 0.7 | 0 | 2023-07-23 | 14.5 | 3.5 | 0 | 2022-07-23 | 19 | 0 | 1 | 2021-07-23 | 14.8 | 3.2 | 0 | 2020-07-23 | 18 | 0 | 0 | 2019-07-23 | 11.9 | 6.1 | 0 | 2018-07-23 | 19.8 | 0 | 1.8 | 2017-07-23 | 16.5 | 1.5 | 0 | 2016-07-23 | 19 | 0 | 1 | 2.07 | 0.38
2025-07-23 | 11.3 | 6.7 | 0 | 2024-07-23 | 18 | 0 | 0 | 2023-07-23 | 12.2 | 5.8 | 0 | 2022-07-23 | 18.9 | 0 | 0.9 | 2021-07-23 | 14.2 | 3.8 | 0 | 2020-07-23 | 17.8 | 0.2 | 0 | 2019-07-23 | 12.8 | 5.2 | 0 | 2018-07-23 | 19.7 | 0 | 1.7 | 2017-07-23 | 15.9 | 2.1 | 0 | 2016-07-23 | 19.1 | 0 | 1.1 | 2.38 | 0.37
2025-07-23 | 14.2 | 3.8 | 0 | 2024-07-23 | 18.1 | 0 | 0.1 | 2023-07-23 | 14.9 | 3.1 | 0 | 2022-07-23 | 20.4 | 0 | 2.4 | 2021-07-23 | 15.2 | 2.8 | 0 | 2020-07-23 | 17.9 | 0.1 | 0 | 2019-07-23 | 15.2 | 2.8 | 0 | 2018-07-23 | 20.3 | 0 | 2.3 | 2017-07-23 | 15.8 | 2.2 | 0 | 2016-07-23 | 20.1 | 0 | 2.1 | 1.48 | 0.69
2025-07-23 | 16.7 | 1.3 | 0 | 2024-07-23 | 18.2 | 0 | 0.2 | 2023-07-23 | 17.9 | 0.1 | 0 | 2022-07-23 | 22.1 | 0 | 4.1 | 2021-07-23 | 17.1 | 0.9 | 0 | 2020-07-23 | 18.4 | 0 | 0.4 | 2019-07-23 | 18.2 | 0 | 0.2 | 2018-07-23 | 21.6 | 0 | 3.6 | 2017-07-23 | 16.5 | 1.5 | 0 | 2016-07-23 | 21.2 | 0 | 3.2 | 0.38 | 1.17
2025-07-23 | 19.9 | 0 | 1.9 | 2024-07-23 | 18.8 | 0 | 0.8 | 2023-07-23 | 20.6 | 0 | 2.6 | 2022-07-23 | 24.1 | 0 | 6.1 | 2021-07-23 | 19.3 | 0 | 1.3 | 2020-07-23 | 18.9 | 0 | 0.9 | 2019-07-23 | 20.5 | 0 | 2.5 | 2018-07-23 | 23.2 | 0 | 5.2 | 2017-07-23 | 17.2 | 0.8 | 0 | 2016-07-23 | 22.8 | 0 | 4.8 | 0.08 | 2.61
2025-07-23 | 22 | 0 | 4 | 2024-07-23 | 20.8 | 0 | 2.8 | 2023-07-23 | 23 | 0 | 5 | 2022-07-23 | 25.8 | 0 | 7.8 | 2021-07-23 | 20.5 | 0 | 2.5 | 2020-07-23 | 19.2 | 0 | 1.2 | 2019-07-23 | 21.1 | 0 | 3.1 | 2018-07-23 | 26 | 0 | 8 | 2017-07-23 | 17.7 | 0.3 | 0 | 2016-07-23 | 24.6 | 0 | 6.6 | 0.03 | 4.1
2025-07-23 | 23.9 | 0 | 5.9 | 2024-07-23 | 22.6 | 0 | 4.6 | 2023-07-23 | 24.9 | 0 | 6.9 | 2022-07-23 | 26.9 | 0 | 8.9 | 2021-07-23 | 21.9 | 0 | 3.9 | 2020-07-23 | 19.6 | 0 | 1.6 | 2019-07-23 | 22.6 | 0 | 4.6 | 2018-07-23 | 28 | 0 | 10 | 2017-07-23 | 18.6 | 0 | 0.6 | 2016-07-23 | 26.2 | 0 | 8.2 | 0 | 5.52
2025-07-23 | 24.6 | 0 | 6.6 | 2024-07-23 | 24 | 0 | 6 | 2023-07-23 | 25.7 | 0 | 7.7 | 2022-07-23 | 28.2 | 0 | 10.2 | 2021-07-23 | 22.8 | 0 | 4.8 | 2020-07-23 | 21.2 | 0 | 3.2 | 2019-07-23 | 24.2 | 0 | 6.2 | 2018-07-23 | 29 | 0 | 11 | 2017-07-23 | 18.8 | 0 | 0.8 | 2016-07-23 | 27.4 | 0 | 9.4 | 0 | 6.59
2025-07-23 | 25.3 | 0 | 7.3 | 2024-07-23 | 25.4 | 0 | 7.4 | 2023-07-23 | 26.7 | 0 | 8.7 | 2022-07-23 | 29 | 0 | 11 | 2021-07-23 | 23.9 | 0 | 5.9 | 2020-07-23 | 22.6 | 0 | 4.6 | 2019-07-23 | 25.2 | 0 | 7.2 | 2018-07-23 | 30.1 | 0 | 12.1 | 2017-07-23 | 20.1 | 0 | 2.1 | 2016-07-23 | 28.9 | 0 | 10.9 | 0 | 7.72
2025-07-23 | 26.4 | 0 | 8.4 | 2024-07-23 | 26.4 | 0 | 8.4 | 2023-07-23 | 26.9 | 0 | 8.9 | 2022-07-23 | 29.9 | 0 | 11.9 | 2021-07-23 | 25.1 | 0 | 7.1 | 2020-07-23 | 24 | 0 | 6 | 2019-07-23 | 25.2 | 0 | 7.2 | 2018-07-23 | 31.1 | 0 | 13.1 | 2017-07-23 | 19.7 | 0 | 1.7 | 2016-07-23 | 28.2 | 0 | 10.2 | 0 | 8.29
2025-07-23 | 26.6 | 0 | 8.6 | 2024-07-23 | 26.5 | 0 | 8.5 | 2023-07-23 | 28.4 | 0 | 10.4 | 2022-07-23 | 30.2 | 0 | 12.2 | 2021-07-23 | 25.5 | 0 | 7.5 | 2020-07-23 | 25.5 | 0 | 7.5 | 2019-07-23 | 25.6 | 0 | 7.6 | 2018-07-23 | 29.8 | 0 | 11.8 | 2017-07-23 | 20.1 | 0 | 2.1 | 2016-07-23 | 27.8 | 0 | 9.8 | 0 | 8.6
2025-07-23 | 27 | 0 | 9 | 2024-07-23 | 26.5 | 0 | 8.5 | 2023-07-23 | 27.7 | 0 | 9.7 | 2022-07-23 | 29.7 | 0 | 11.7 | 2021-07-23 | 24.4 | 0 | 6.4 | 2020-07-23 | 26.4 | 0 | 8.4 | 2019-07-23 | 25.1 | 0 | 7.1 | 2018-07-23 | 28.4 | 0 | 10.4 | 2017-07-23 | 20.5 | 0 | 2.5 | 2016-07-23 | 26.3 | 0 | 8.3 | 0 | 8.2
2025-07-23 | 28.1 | 0 | 10.1 | 2024-07-23 | 26.4 | 0 | 8.4 | 2023-07-23 | 28.2 | 0 | 10.2 | 2022-07-23 | 26.8 | 0 | 8.8 | 2021-07-23 | 24.4 | 0 | 6.4 | 2020-07-23 | 24.5 | 0 | 6.5 | 2019-07-23 | 24.4 | 0 | 6.4 | 2018-07-23 | 27.8 | 0 | 9.8 | 2017-07-23 | 20.3 | 0 | 2.3 | 2016-07-23 | 26.6 | 0 | 8.6 | 0 | 7.75
2025-07-23 | 27.9 | 0 | 9.9 | 2024-07-23 | 26.1 | 0 | 8.1 | 2023-07-23 | 27.6 | 0 | 9.6 | 2022-07-23 | 25.7 | 0 | 7.7 | 2021-07-23 | 24.6 | 0 | 6.6 | 2020-07-23 | 25 | 0 | 7 | 2019-07-23 | 24.4 | 0 | 6.4 | 2018-07-23 | 23.1 | 0 | 5.1 | 2017-07-23 | 20.3 | 0 | 2.3 | 2016-07-23 | 26.8 | 0 | 8.8 | 0 | 7.15
2025-07-23 | 26.9 | 0 | 8.9 | 2024-07-23 | 25 | 0 | 7 | 2023-07-23 | 26.3 | 0 | 8.3 | 2022-07-23 | 27 | 0 | 9 | 2021-07-23 | 24.5 | 0 | 6.5 | 2020-07-23 | 23.8 | 0 | 5.8 | 2019-07-23 | 23.7 | 0 | 5.7 | 2018-07-23 | 23.3 | 0 | 5.3 | 2017-07-23 | 19.6 | 0 | 1.6 | 2016-07-23 | 26.9 | 0 | 8.9 | 0 | 6.7
2025-07-23 | 25.1 | 0 | 7.1 | 2024-07-23 | 21.4 | 0 | 3.4 | 2023-07-23 | 24.6 | 0 | 6.6 | 2022-07-23 | 26.3 | 0 | 8.3 | 2021-07-23 | 23.5 | 0 | 5.5 | 2020-07-23 | 22.6 | 0 | 4.6 | 2019-07-23 | 21.8 | 0 | 3.8 | 2018-07-23 | 23 | 0 | 5 | 2017-07-23 | 18.4 | 0 | 0.4 | 2016-07-23 | 25.9 | 0 | 7.9 | 0 | 5.26
2025-07-23 | 22.6 | 0 | 4.6 | 2024-07-23 | 20.6 | 0 | 2.6 | 2023-07-23 | 22.7 | 0 | 4.7 | 2022-07-23 | 25.4 | 0 | 7.4 | 2021-07-23 | 19 | 0 | 1 | 2020-07-23 | 21.1 | 0 | 3.1 | 2019-07-23 | 20.5 | 0 | 2.5 | 2018-07-23 | 22.9 | 0 | 4.9 | 2017-07-23 | 17.5 | 0.5 | 0 | 2016-07-23 | 24.5 | 0 | 6.5 | 0.05 | 3.73
2025-07-23 | 21.1 | 0 | 3.1 | 2024-07-23 | 20.1 | 0 | 2.1 | 2023-07-23 | 21.1 | 0 | 3.1 | 2022-07-23 | 24.9 | 0 | 6.9 | 2021-07-23 | 18.2 | 0 | 0.2 | 2020-07-23 | 19.6 | 0 | 1.6 | 2019-07-23 | 18.8 | 0 | 0.8 | 2018-07-23 | 22.1 | 0 | 4.1 | 2017-07-23 | 17.3 | 0.7 | 0 | 2016-07-23 | 23.5 | 0 | 5.5 | 0.07 | 2.74
2025-07-23 | 19.8 | 0 | 1.8 | 2024-07-23 | 19.7 | 0 | 1.7 | 2023-07-23 | 20.6 | 0 | 2.6 | 2022-07-23 | 23.5 | 0 | 5.5 | 2021-07-23 | 16.5 | 1.5 | 0 | 2020-07-23 | 19.4 | 0 | 1.4 | 2019-07-23 | 17.4 | 0.6 | 0 | 2018-07-23 | 22.3 | 0 | 4.3 | 2017-07-23 | 17.1 | 0.9 | 0 | 2016-07-23 | 22.4 | 0 | 4.4 | 0.3 | 2.17
2025-07-23 | 18.4 | 0 | 0.4 | 2024-07-23 | 19.4 | 0 | 1.4 | 2023-07-23 | 19.6 | 0 | 1.6 | 2022-07-23 | 22.3 | 0 | 4.3 | 2021-07-23 | 16.1 | 1.9 | 0 | 2020-07-23 | 19 | 0 | 1 | 2019-07-23 | 15.8 | 2.2 | 0 | 2018-07-23 | 22.3 | 0 | 4.3 | 2017-07-23 | 17.1 | 0.9 | 0 | 2016-07-23 | 20.5 | 0 | 2.5 | 0.5 | 1.55
2025-07-24 | 18 | 0 | 0 | 2024-07-24 | 19.3 | 0 | 1.3 | 2023-07-24 | 19.1 | 0 | 1.1 | 2022-07-24 | 21.8 | 0 | 3.8 | 2021-07-24 | 15.4 | 2.6 | 0 | 2020-07-24 | 18.6 | 0 | 0.6 | 2019-07-24 | 15.2 | 2.8 | 0 | 2018-07-24 | 22.2 | 0 | 4.2 | 2017-07-24 | 16.4 | 1.6 | 0 | 2016-07-24 | 20.1 | 0 | 2.1 | 0.7 | 1.31
2025-07-24 | 16.9 | 1.1 | 0 | 2024-07-24 | 19.6 | 0 | 1.6 | 2023-07-24 | 18.2 | 0 | 0.2 | 2022-07-24 | 21.9 | 0 | 3.9 | 2021-07-24 | 15.5 | 2.5 | 0 | 2020-07-24 | 17.1 | 0.9 | 0 | 2019-07-24 | 15.4 | 2.6 | 0 | 2018-07-24 | 22.7 | 0 | 4.7 | 2017-07-24 | 16.7 | 1.3 | 0 | 2016-07-24 | 18.1 | 0 | 0.1 | 0.84 | 1.05
2025-07-24 | 17.5 | 0.5 | 0 | 2024-07-24 | 18.6 | 0 | 0.6 | 2023-07-24 | 17.7 | 0.3 | 0 | 2022-07-24 | 20.8 | 0 | 2.8 | 2021-07-24 | 14.1 | 3.9 | 0 | 2020-07-24 | 16.2 | 1.8 | 0 | 2019-07-24 | 15.3 | 2.7 | 0 | 2018-07-24 | 22.5 | 0 | 4.5 | 2017-07-24 | 17.2 | 0.8 | 0 | 2016-07-24 | 18.1 | 0 | 0.1 | 1 | 0.8
2025-07-24 | 16.3 | 1.7 | 0 | 2024-07-24 | 17.9 | 0.1 | 0 | 2023-07-24 | 17.1 | 0.9 | 0 | 2022-07-24 | 20.3 | 0 | 2.3 | 2021-07-24 | 13 | 5 | 0 | 2020-07-24 | 17.1 | 0.9 | 0 | 2019-07-24 | 14.7 | 3.3 | 0 | 2018-07-24 | 22.5 | 0 | 4.5 | 2017-07-24 | 17.3 | 0.7 | 0 | 2016-07-24 | 13.7 | 4.3 | 0 | 1.69 | 0.68
2025-07-24 | 14.8 | 3.2 | 0 | 2024-07-24 | 17.6 | 0.4 | 0 | 2023-07-24 | 16.4 | 1.6 | 0 | 2022-07-24 | 19.9 | 0 | 1.9 | 2021-07-24 | 12.8 | 5.2 | 0 | 2020-07-24 | 15.5 | 2.5 | 0 | 2019-07-24 | 13.8 | 4.2 | 0 | 2018-07-24 | 22.3 | 0 | 4.3 | 2017-07-24 | 15.2 | 2.8 | 0 | 2016-07-24 | 15.1 | 2.9 | 0 | 2.28 | 0.62
2025-07-24 | 15.1 | 2.9 | 0 | 2024-07-24 | 17.2 | 0.8 | 0 | 2023-07-24 | 16.8 | 1.2 | 0 | 2022-07-24 | 19.8 | 0 | 1.8 | 2021-07-24 | 12.8 | 5.2 | 0 | 2020-07-24 | 15.8 | 2.2 | 0 | 2019-07-24 | 13.6 | 4.4 | 0 | 2018-07-24 | 22.1 | 0 | 4.1 | 2017-07-24 | 14 | 4 | 0 | 2016-07-24 | 13.8 | 4.2 | 0 | 2.49 | 0.59
2025-07-24 | 18.6 | 0 | 0.6 | 2024-07-24 | 17.8 | 0.2 | 0 | 2023-07-24 | 17.4 | 0.6 | 0 | 2022-07-24 | 21.4 | 0 | 3.4 | 2021-07-24 | 15.8 | 2.2 | 0 | 2020-07-24 | 17.5 | 0.5 | 0 | 2019-07-24 | 15.8 | 2.2 | 0 | 2018-07-24 | 22.5 | 0 | 4.5 | 2017-07-24 | 13.3 | 4.7 | 0 | 2016-07-24 | 16.6 | 1.4 | 0 | 1.18 | 0.85
2025-07-24 | 22 | 0 | 4 | 2024-07-24 | 19.5 | 0 | 1.5 | 2023-07-24 | 19.8 | 0 | 1.8 | 2022-07-24 | 22.5 | 0 | 4.5 | 2021-07-24 | 17.7 | 0.3 | 0 | 2020-07-24 | 20 | 0 | 2 | 2019-07-24 | 17.5 | 0.5 | 0 | 2018-07-24 | 22.5 | 0 | 4.5 | 2017-07-24 | 13.3 | 4.7 | 0 | 2016-07-24 | 18.6 | 0 | 0.6 | 0.55 | 1.89
2025-07-24 | 24 | 0 | 6 | 2024-07-24 | 20.6 | 0 | 2.6 | 2023-07-24 | 22.8 | 0 | 4.8 | 2022-07-24 | 23.3 | 0 | 5.3 | 2021-07-24 | 20.5 | 0 | 2.5 | 2020-07-24 | 22.3 | 0 | 4.3 | 2019-07-24 | 19 | 0 | 1 | 2018-07-24 | 23.1 | 0 | 5.1 | 2017-07-24 | 13.4 | 4.6 | 0 | 2016-07-24 | 19.8 | 0 | 1.8 | 0.46 | 3.34
2025-07-24 | 27.2 | 0 | 9.2 | 2024-07-24 | 21.3 | 0 | 3.3 | 2023-07-24 | 24.4 | 0 | 6.4 | 2022-07-24 | 25.3 | 0 | 7.3 | 2021-07-24 | 21.6 | 0 | 3.6 | 2020-07-24 | 24.5 | 0 | 6.5 | 2019-07-24 | 20.2 | 0 | 2.2 | 2018-07-24 | 23.5 | 0 | 5.5 | 2017-07-24 | 13.5 | 4.5 | 0 | 2016-07-24 | 20.6 | 0 | 2.6 | 0.45 | 4.66
2025-07-24 | 29.2 | 0 | 11.2 | 2024-07-24 | 20.8 | 0 | 2.8 | 2023-07-24 | 26.1 | 0 | 8.1 | 2022-07-24 | 25.8 | 0 | 7.8 | 2021-07-24 | 23.6 | 0 | 5.6 | 2020-07-24 | 26.9 | 0 | 8.9 | 2019-07-24 | 20.8 | 0 | 2.8 | 2018-07-24 | 24.6 | 0 | 6.6 | 2017-07-24 | 13.5 | 4.5 | 0 | 2016-07-24 | 21.8 | 0 | 3.8 | 0.45 | 5.76
2025-07-24 | 29.4 | 0 | 11.4 | 2024-07-24 | 22.6 | 0 | 4.6 | 2023-07-24 | 27.2 | 0 | 9.2 | 2022-07-24 | 26 | 0 | 8 | 2021-07-24 | 25.3 | 0 | 7.3 | 2020-07-24 | 27.7 | 0 | 9.7 | 2019-07-24 | 21.9 | 0 | 3.9 | 2018-07-24 | 25.6 | 0 | 7.6 | 2017-07-24 | 13.7 | 4.3 | 0 | 2016-07-24 | 23 | 0 | 5 | 0.43 | 6.67
2025-07-24 | 31 | 0 | 13 | 2024-07-24 | 23.9 | 0 | 5.9 | 2023-07-24 | 27.1 | 0 | 9.1 | 2022-07-24 | 25.3 | 0 | 7.3 | 2021-07-24 | 25.3 | 0 | 7.3 | 2020-07-24 | 29.1 | 0 | 11.1 | 2019-07-24 | 22.9 | 0 | 4.9 | 2018-07-24 | 27 | 0 | 9 | 2017-07-24 | 14.4 | 3.6 | 0 | 2016-07-24 | 24.1 | 0 | 6.1 | 0.36 | 7.37
2025-07-24 | 32.3 | 0 | 14.3 | 2024-07-24 | 23.9 | 0 | 5.9 | 2023-07-24 | 27.6 | 0 | 9.6 | 2022-07-24 | 23.8 | 0 | 5.8 | 2021-07-24 | 26.2 | 0 | 8.2 | 2020-07-24 | 29.8 | 0 | 11.8 | 2019-07-24 | 23.7 | 0 | 5.7 | 2018-07-24 | 27.1 | 0 | 9.1 | 2017-07-24 | 14.6 | 3.4 | 0 | 2016-07-24 | 26 | 0 | 8 | 0.34 | 7.84
2025-07-24 | 33.1 | 0 | 15.1 | 2024-07-24 | 22.8 | 0 | 4.8 | 2023-07-24 | 28.5 | 0 | 10.5 | 2022-07-24 | 24.4 | 0 | 6.4 | 2021-07-24 | 26.2 | 0 | 8.2 | 2020-07-24 | 27.6 | 0 | 9.6 | 2019-07-24 | 24 | 0 | 6 | 2018-07-24 | 26.2 | 0 | 8.2 | 2017-07-24 | 14.7 | 3.3 | 0 | 2016-07-24 | 26.3 | 0 | 8.3 | 0.33 | 7.71
2025-07-24 | 33.3 | 0 | 15.3 | 2024-07-24 | 22.6 | 0 | 4.6 | 2023-07-24 | 28 | 0 | 10 | 2022-07-24 | 24.4 | 0 | 6.4 | 2021-07-24 | 26.1 | 0 | 8.1 | 2020-07-24 | 29.6 | 0 | 11.6 | 2019-07-24 | 24.1 | 0 | 6.1 | 2018-07-24 | 24.1 | 0 | 6.1 | 2017-07-24 | 14.5 | 3.5 | 0 | 2016-07-24 | 26.4 | 0 | 8.4 | 0.35 | 7.66
2025-07-24 | 33.3 | 0 | 15.3 | 2024-07-24 | 18.8 | 0 | 0.8 | 2023-07-24 | 25 | 0 | 7 | 2022-07-24 | 20.1 | 0 | 2.1 | 2021-07-24 | 24.9 | 0 | 6.9 | 2020-07-24 | 28.7 | 0 | 10.7 | 2019-07-24 | 24.3 | 0 | 6.3 | 2018-07-24 | 23 | 0 | 5 | 2017-07-24 | 14.1 | 3.9 | 0 | 2016-07-24 | 25.9 | 0 | 7.9 | 0.39 | 6.2
2025-07-24 | 32.3 | 0 | 14.3 | 2024-07-24 | 19.4 | 0 | 1.4 | 2023-07-24 | 23.5 | 0 | 5.5 | 2022-07-24 | 23 | 0 | 5 | 2021-07-24 | 24.1 | 0 | 6.1 | 2020-07-24 | 29.5 | 0 | 11.5 | 2019-07-24 | 24.3 | 0 | 6.3 | 2018-07-24 | 22.5 | 0 | 4.5 | 2017-07-24 | 14 | 4 | 0 | 2016-07-24 | 26 | 0 | 8 | 0.4 | 6.26
2025-07-24 | 31.2 | 0 | 13.2 | 2024-07-24 | 19.7 | 0 | 1.7 | 2023-07-24 | 23.1 | 0 | 5.1 | 2022-07-24 | 23.7 | 0 | 5.7 | 2021-07-24 | 23.4 | 0 | 5.4 | 2020-07-24 | 29.1 | 0 | 11.1 | 2019-07-24 | 23.7 | 0 | 5.7 | 2018-07-24 | 22.1 | 0 | 4.1 | 2017-07-24 | 13.9 | 4.1 | 0 | 2016-07-24 | 24.7 | 0 | 6.7 | 0.41 | 5.87
2025-07-24 | 29.8 | 0 | 11.8 | 2024-07-24 | 19.3 | 0 | 1.3 | 2023-07-24 | 20.9 | 0 | 2.9 | 2022-07-24 | 23.4 | 0 | 5.4 | 2021-07-24 | 22.6 | 0 | 4.6 | 2020-07-24 | 27.1 | 0 | 9.1 | 2019-07-24 | 22.6 | 0 | 4.6 | 2018-07-24 | 21.7 | 0 | 3.7 | 2017-07-24 | 13.7 | 4.3 | 0 | 2016-07-24 | 23 | 0 | 5 | 0.43 | 4.84
2025-07-24 | 23.5 | 0 | 5.5 | 2024-07-24 | 18.6 | 0 | 0.6 | 2023-07-24 | 19.4 | 0 | 1.4 | 2022-07-24 | 22.7 | 0 | 4.7 | 2021-07-24 | 21.9 | 0 | 3.9 | 2020-07-24 | 24.6 | 0 | 6.6 | 2019-07-24 | 21.5 | 0 | 3.5 | 2018-07-24 | 21.8 | 0 | 3.8 | 2017-07-24 | 13.9 | 4.1 | 0 | 2016-07-24 | 21.9 | 0 | 3.9 | 0.41 | 3.39
2025-07-24 | 22.4 | 0 | 4.4 | 2024-07-24 | 18 | 0 | 0 | 2023-07-24 | 18.9 | 0 | 0.9 | 2022-07-24 | 22.2 | 0 | 4.2 | 2021-07-24 | 20.2 | 0 | 2.2 | 2020-07-24 | 21.4 | 0 | 3.4 | 2019-07-24 | 17 | 1 | 0 | 2018-07-24 | 21.9 | 0 | 3.9 | 2017-07-24 | 13.8 | 4.2 | 0 | 2016-07-24 | 21.3 | 0 | 3.3 | 0.52 | 2.23
2025-07-24 | 21.9 | 0 | 3.9 | 2024-07-24 | 17.5 | 0.5 | 0 | 2023-07-24 | 18.4 | 0 | 0.4 | 2022-07-24 | 21.9 | 0 | 3.9 | 2021-07-24 | 19.7 | 0 | 1.7 | 2020-07-24 | 21.7 | 0 | 3.7 | 2019-07-24 | 17.2 | 0.8 | 0 | 2018-07-24 | 22.1 | 0 | 4.1 | 2017-07-24 | 13.4 | 4.6 | 0 | 2016-07-24 | 20 | 0 | 2 | 0.59 | 1.97
2025-07-24 | 22 | 0 | 4 | 2024-07-24 | 17.5 | 0.5 | 0 | 2023-07-24 | 18.2 | 0 | 0.2 | 2022-07-24 | 21.8 | 0 | 3.8 | 2021-07-24 | 18.7 | 0 | 0.7 | 2020-07-24 | 20.8 | 0 | 2.8 | 2019-07-24 | 15.8 | 2.2 | 0 | 2018-07-24 | 22.3 | 0 | 4.3 | 2017-07-24 | 13.2 | 4.8 | 0 | 2016-07-24 | 19.3 | 0 | 1.3 | 0.75 | 1.71
2025-07-25 | 22.1 | 0 | 4.1 | 2024-07-25 | 17.6 | 0.4 | 0 | 2023-07-25 | 18.2 | 0 | 0.2 | 2022-07-25 | 21.6 | 0 | 3.6 | 2021-07-25 | 18.5 | 0 | 0.5 | 2020-07-25 | 20.4 | 0 | 2.4 | 2019-07-25 | 15.5 | 2.5 | 0 | 2018-07-25 | 22.3 | 0 | 4.3 | 2017-07-25 | 13.4 | 4.6 | 0 | 2016-07-25 | 19.2 | 0 | 1.2 | 0.75 | 1.63
2025-07-25 | 22 | 0 | 4 | 2024-07-25 | 17.7 | 0.3 | 0 | 2023-07-25 | 17.8 | 0.2 | 0 | 2022-07-25 | 21.4 | 0 | 3.4 | 2021-07-25 | 19 | 0 | 1 | 2020-07-25 | 17.8 | 0.2 | 0 | 2019-07-25 | 15.4 | 2.6 | 0 | 2018-07-25 | 22.5 | 0 | 4.5 | 2017-07-25 | 13.3 | 4.7 | 0 | 2016-07-25 | 19 | 0 | 1 | 0.8 | 1.39
2025-07-25 | 21.7 | 0 | 3.7 | 2024-07-25 | 17.6 | 0.4 | 0 | 2023-07-25 | 17 | 1 | 0 | 2022-07-25 | 21 | 0 | 3 | 2021-07-25 | 19.6 | 0 | 1.6 | 2020-07-25 | 18.1 | 0 | 0.1 | 2019-07-25 | 16 | 2 | 0 | 2018-07-25 | 22.3 | 0 | 4.3 | 2017-07-25 | 13.3 | 4.7 | 0 | 2016-07-25 | 19.3 | 0 | 1.3 | 0.81 | 1.4
2025-07-25 | 21.5 | 0 | 3.5 | 2024-07-25 | 17.3 | 0.7 | 0 | 2023-07-25 | 16.9 | 1.1 | 0 | 2022-07-25 | 21.3 | 0 | 3.3 | 2021-07-25 | 20.1 | 0 | 2.1 | 2020-07-25 | 16.9 | 1.1 | 0 | 2019-07-25 | 16.1 | 1.9 | 0 | 2018-07-25 | 22.2 | 0 | 4.2 | 2017-07-25 | 13.3 | 4.7 | 0 | 2016-07-25 | 19.7 | 0 | 1.7 | 0.95 | 1.48
2025-07-25 | 21.8 | 0 | 3.8 | 2024-07-25 | 17.1 | 0.9 | 0 | 2023-07-25 | 16.6 | 1.4 | 0 | 2022-07-25 | 21.3 | 0 | 3.3 | 2021-07-25 | 20.6 | 0 | 2.6 | 2020-07-25 | 16.2 | 1.8 | 0 | 2019-07-25 | 14.7 | 3.3 | 0 | 2018-07-25 | 19.6 | 0 | 1.6 | 2017-07-25 | 13.2 | 4.8 | 0 | 2016-07-25 | 19.7 | 0 | 1.7 | 1.22 | 1.3
2025-07-25 | 21.3 | 0 | 3.3 | 2024-07-25 | 16.8 | 1.2 | 0 | 2023-07-25 | 17.2 | 0.8 | 0 | 2022-07-25 | 20.8 | 0 | 2.8 | 2021-07-25 | 20.7 | 0 | 2.7 | 2020-07-25 | 15 | 3 | 0 | 2019-07-25 | 15.2 | 2.8 | 0 | 2018-07-25 | 19.5 | 0 | 1.5 | 2017-07-25 | 13.3 | 4.7 | 0 | 2016-07-25 | 18.5 | 0 | 0.5 | 1.25 | 1.08
2025-07-25 | 21.8 | 0 | 3.8 | 2024-07-25 | 17.2 | 0.8 | 0 | 2023-07-25 | 17.4 | 0.6 | 0 | 2022-07-25 | 20.9 | 0 | 2.9 | 2021-07-25 | 20.8 | 0 | 2.8 | 2020-07-25 | 18 | 0 | 0 | 2019-07-25 | 15.9 | 2.1 | 0 | 2018-07-25 | 20.1 | 0 | 2.1 | 2017-07-25 | 13.6 | 4.4 | 0 | 2016-07-25 | 19.2 | 0 | 1.2 | 0.79 | 1.28
2025-07-25 | 22.3 | 0 | 4.3 | 2024-07-25 | 17.1 | 0.9 | 0 | 2023-07-25 | 17.9 | 0.1 | 0 | 2022-07-25 | 21.7 | 0 | 3.7 | 2021-07-25 | 21.5 | 0 | 3.5 | 2020-07-25 | 20 | 0 | 2 | 2019-07-25 | 18 | 0 | 0 | 2018-07-25 | 21.4 | 0 | 3.4 | 2017-07-25 | 14.4 | 3.6 | 0 | 2016-07-25 | 17.8 | 0.2 | 0 | 0.48 | 1.69
2025-07-25 | 23.6 | 0 | 5.6 | 2024-07-25 | 17.9 | 0.1 | 0 | 2023-07-25 | 18.4 | 0 | 0.4 | 2022-07-25 | 22.2 | 0 | 4.2 | 2021-07-25 | 22.7 | 0 | 4.7 | 2020-07-25 | 23.3 | 0 | 5.3 | 2019-07-25 | 20.5 | 0 | 2.5 | 2018-07-25 | 21.9 | 0 | 3.9 | 2017-07-25 | 15.3 | 2.7 | 0 | 2016-07-25 | 19.2 | 0 | 1.2 | 0.28 | 2.78
2025-07-25 | 24.7 | 0 | 6.7 | 2024-07-25 | 18 | 0 | 0 | 2023-07-25 | 21 | 0 | 3 | 2022-07-25 | 22.2 | 0 | 4.2 | 2021-07-25 | 23.8 | 0 | 5.8 | 2020-07-25 | 25.4 | 0 | 7.4 | 2019-07-25 | 22.4 | 0 | 4.4 | 2018-07-25 | 22.2 | 0 | 4.2 | 2017-07-25 | 16.6 | 1.4 | 0 | 2016-07-25 | 20.6 | 0 | 2.6 | 0.14 | 3.83
2025-07-25 | 24.7 | 0 | 6.7 | 2024-07-25 | 17.7 | 0.3 | 0 | 2023-07-25 | 22.5 | 0 | 4.5 | 2022-07-25 | 23.7 | 0 | 5.7 | 2021-07-25 | 24 | 0 | 6 | 2020-07-25 | 27 | 0 | 9 | 2019-07-25 | 24.4 | 0 | 6.4 | 2018-07-25 | 22.5 | 0 | 4.5 | 2017-07-25 | 17.5 | 0.5 | 0 | 2016-07-25 | 22 | 0 | 4 | 0.08 | 4.68
2025-07-25 | 25.5 | 0 | 7.5 | 2024-07-25 | 18.9 | 0 | 0.9 | 2023-07-25 | 23.1 | 0 | 5.1 | 2022-07-25 | 23.6 | 0 | 5.6 | 2021-07-25 | 24 | 0 | 6 | 2020-07-25 | 28.3 | 0 | 10.3 | 2019-07-25 | 26.2 | 0 | 8.2 | 2018-07-25 | 22.8 | 0 | 4.8 | 2017-07-25 | 18.5 | 0 | 0.5 | 2016-07-25 | 22.9 | 0 | 4.9 | 0 | 5.38
2025-07-25 | 27.7 | 0 | 9.7 | 2024-07-25 | 18.9 | 0 | 0.9 | 2023-07-25 | 24.2 | 0 | 6.2 | 2022-07-25 | 23.9 | 0 | 5.9 | 2021-07-25 | 25.1 | 0 | 7.1 | 2020-07-25 | 31.4 | 0 | 13.4 | 2019-07-25 | 27.4 | 0 | 9.4 | 2018-07-25 | 22.4 | 0 | 4.4 | 2017-07-25 | 20.5 | 0 | 2.5 | 2016-07-25 | 25.3 | 0 | 7.3 | 0 | 6.68
2025-07-25 | 27.9 | 0 | 9.9 | 2024-07-25 | 19.6 | 0 | 1.6 | 2023-07-25 | 25 | 0 | 7 | 2022-07-25 | 24.1 | 0 | 6.1 | 2021-07-25 | 25.1 | 0 | 7.1 | 2020-07-25 | 30.7 | 0 | 12.7 | 2019-07-25 | 27.9 | 0 | 9.9 | 2018-07-25 | 22.8 | 0 | 4.8 | 2017-07-25 | 21.4 | 0 | 3.4 | 2016-07-25 | 25.4 | 0 | 7.4 | 0 | 6.99
2025-07-25 | 28.6 | 0 | 10.6 | 2024-07-25 | 19.6 | 0 | 1.6 | 2023-07-25 | 25.6 | 0 | 7.6 | 2022-07-25 | 22.9 | 0 | 4.9 | 2021-07-25 | 25.8 | 0 | 7.8 | 2020-07-25 | 31.1 | 0 | 13.1 | 2019-07-25 | 29.2 | 0 | 11.2 | 2018-07-25 | 23.1 | 0 | 5.1 | 2017-07-25 | 21.7 | 0 | 3.7 | 2016-07-25 | 25.5 | 0 | 7.5 | 0 | 7.31
2025-07-25 | 29.1 | 0 | 11.1 | 2024-07-25 | 19.6 | 0 | 1.6 | 2023-07-25 | 26.1 | 0 | 8.1 | 2022-07-25 | 24.1 | 0 | 6.1 | 2021-07-25 | 25.9 | 0 | 7.9 | 2020-07-25 | 31.8 | 0 | 13.8 | 2019-07-25 | 29.4 | 0 | 11.4 | 2018-07-25 | 23.8 | 0 | 5.8 | 2017-07-25 | 22.6 | 0 | 4.6 | 2016-07-25 | 26.5 | 0 | 8.5 | 0 | 7.89
2025-07-25 | 28.8 | 0 | 10.8 | 2024-07-25 | 19.5 | 0 | 1.5 | 2023-07-25 | 26.6 | 0 | 8.6 | 2022-07-25 | 23 | 0 | 5 | 2021-07-25 | 26.5 | 0 | 8.5 | 2020-07-25 | 30.5 | 0 | 12.5 | 2019-07-25 | 29.3 | 0 | 11.3 | 2018-07-25 | 24.3 | 0 | 6.3 | 2017-07-25 | 22.6 | 0 | 4.6 | 2016-07-25 | 27.4 | 0 | 9.4 | 0 | 7.85
2025-07-25 | 27.9 | 0 | 9.9 | 2024-07-25 | 18.9 | 0 | 0.9 | 2023-07-25 | 25.9 | 0 | 7.9 | 2022-07-25 | 22.9 | 0 | 4.9 | 2021-07-25 | 26.3 | 0 | 8.3 | 2020-07-25 | 30.6 | 0 | 12.6 | 2019-07-25 | 28.9 | 0 | 10.9 | 2018-07-25 | 24.4 | 0 | 6.4 | 2017-07-25 | 22.1 | 0 | 4.1 | 2016-07-25 | 26.4 | 0 | 8.4 | 0 | 7.43
2025-07-25 | 27.2 | 0 | 9.2 | 2024-07-25 | 17.2 | 0.8 | 0 | 2023-07-25 | 25.9 | 0 | 7.9 | 2022-07-25 | 22.6 | 0 | 4.6 | 2021-07-25 | 25.9 | 0 | 7.9 | 2020-07-25 | 29.6 | 0 | 11.6 | 2019-07-25 | 27.4 | 0 | 9.4 | 2018-07-25 | 23.5 | 0 | 5.5 | 2017-07-25 | 21.6 | 0 | 3.6 | 2016-07-25 | 26.3 | 0 | 8.3 | 0.08 | 6.8
2025-07-25 | 25.3 | 0 | 7.3 | 2024-07-25 | 16.5 | 1.5 | 0 | 2023-07-25 | 23.5 | 0 | 5.5 | 2022-07-25 | 21.5 | 0 | 3.5 | 2021-07-25 | 22.2 | 0 | 4.2 | 2020-07-25 | 27.4 | 0 | 9.4 | 2019-07-25 | 25.1 | 0 | 7.1 | 2018-07-25 | 23 | 0 | 5 | 2017-07-25 | 19.8 | 0 | 1.8 | 2016-07-25 | 23.5 | 0 | 5.5 | 0.15 | 4.93
2025-07-25 | 24 | 0 | 6 | 2024-07-25 | 16.8 | 1.2 | 0 | 2023-07-25 | 22.3 | 0 | 4.3 | 2022-07-25 | 19 | 0 | 1 | 2021-07-25 | 19.6 | 0 | 1.6 | 2020-07-25 | 25.4 | 0 | 7.4 | 2019-07-25 | 22.3 | 0 | 4.3 | 2018-07-25 | 21.7 | 0 | 3.7 | 2017-07-25 | 17.6 | 0.4 | 0 | 2016-07-25 | 22.5 | 0 | 4.5 | 0.16 | 3.28
2025-07-25 | 21.8 | 0 | 3.8 | 2024-07-25 | 17.1 | 0.9 | 0 | 2023-07-25 | 21.1 | 0 | 3.1 | 2022-07-25 | 18.5 | 0 | 0.5 | 2021-07-25 | 20.4 | 0 | 2.4 | 2020-07-25 | 24.1 | 0 | 6.1 | 2019-07-25 | 20.7 | 0 | 2.7 | 2018-07-25 | 21.4 | 0 | 3.4 | 2017-07-25 | 16.6 | 1.4 | 0 | 2016-07-25 | 22.1 | 0 | 4.1 | 0.23 | 2.61
2025-07-25 | 20.5 | 0 | 2.5 | 2024-07-25 | 17.3 | 0.7 | 0 | 2023-07-25 | 19.6 | 0 | 1.6 | 2022-07-25 | 17.5 | 0.5 | 0 | 2021-07-25 | 18.6 | 0 | 0.6 | 2020-07-25 | 24.1 | 0 | 6.1 | 2019-07-25 | 19.5 | 0 | 1.5 | 2018-07-25 | 21.2 | 0 | 3.2 | 2017-07-25 | 15.9 | 2.1 | 0 | 2016-07-25 | 22.2 | 0 | 4.2 | 0.33 | 1.97
2025-07-25 | 19.7 | 0 | 1.7 | 2024-07-25 | 17.2 | 0.8 | 0 | 2023-07-25 | 19.2 | 0 | 1.2 | 2022-07-25 | 15.9 | 2.1 | 0 | 2021-07-25 | 16.8 | 1.2 | 0 | 2020-07-25 | 23.3 | 0 | 5.3 | 2019-07-25 | 18.6 | 0 | 0.6 | 2018-07-25 | 21.2 | 0 | 3.2 | 2017-07-25 | 15.9 | 2.1 | 0 | 2016-07-25 | 23 | 0 | 5 | 0.62 | 1.7
2025-07-26 | 18.3 | 0 | 0.3 | 2024-07-26 | 16.6 | 1.4 | 0 | 2023-07-26 | 19.4 | 0 | 1.4 | 2022-07-26 | 15.6 | 2.4 | 0 | 2021-07-26 | 15.5 | 2.5 | 0 | 2020-07-26 | 22.1 | 0 | 4.1 | 2019-07-26 | 17.7 | 0.3 | 0 | 2018-07-26 | 20.9 | 0 | 2.9 | 2017-07-26 | 14.7 | 3.3 | 0 | 2016-07-26 | 21 | 0 | 3 | 0.99 | 1.17
2025-07-26 | 18.6 | 0 | 0.6 | 2024-07-26 | 16.4 | 1.6 | 0 | 2023-07-26 | 18.9 | 0 | 0.9 | 2022-07-26 | 14.8 | 3.2 | 0 | 2021-07-26 | 16.2 | 1.8 | 0 | 2020-07-26 | 22 | 0 | 4 | 2019-07-26 | 17.2 | 0.8 | 0 | 2018-07-26 | 19.7 | 0 | 1.7 | 2017-07-26 | 11.9 | 6.1 | 0 | 2016-07-26 | 20.5 | 0 | 2.5 | 1.35 | 0.97
2025-07-26 | 16.8 | 1.2 | 0 | 2024-07-26 | 14.9 | 3.1 | 0 | 2023-07-26 | 17.7 | 0.3 | 0 | 2022-07-26 | 14.2 | 3.8 | 0 | 2021-07-26 | 16.4 | 1.6 | 0 | 2020-07-26 | 21.5 | 0 | 3.5 | 2019-07-26 | 16.6 | 1.4 | 0 | 2018-07-26 | 20.6 | 0 | 2.6 | 2017-07-26 | 13.3 | 4.7 | 0 | 2016-07-26 | 19.1 | 0 | 1.1 | 1.61 | 0.72
2025-07-26 | 16.8 | 1.2 | 0 | 2024-07-26 | 15.2 | 2.8 | 0 | 2023-07-26 | 17.9 | 0.1 | 0 | 2022-07-26 | 13.7 | 4.3 | 0 | 2021-07-26 | 16.3 | 1.7 | 0 | 2020-07-26 | 21.5 | 0 | 3.5 | 2019-07-26 | 16.6 | 1.4 | 0 | 2018-07-26 | 20.8 | 0 | 2.8 | 2017-07-26 | 11.2 | 6.8 | 0 | 2016-07-26 | 18.4 | 0 | 0.4 | 1.83 | 0.67
2025-07-26 | 17 | 1 | 0 | 2024-07-26 | 14.7 | 3.3 | 0 | 2023-07-26 | 17 | 1 | 0 | 2022-07-26 | 13.3 | 4.7 | 0 | 2021-07-26 | 15.1 | 2.9 | 0 | 2020-07-26 | 21.2 | 0 | 3.2 | 2019-07-26 | 15.6 | 2.4 | 0 | 2018-07-26 | 20.9 | 0 | 2.9 | 2017-07-26 | 12.2 | 5.8 | 0 | 2016-07-26 | 18.5 | 0 | 0.5 | 2.11 | 0.66
2025-07-26 | 15.7 | 2.3 | 0 | 2024-07-26 | 14.1 | 3.9 | 0 | 2023-07-26 | 17 | 1 | 0 | 2022-07-26 | 12.8 | 5.2 | 0 | 2021-07-26 | 15.3 | 2.7 | 0 | 2020-07-26 | 21.5 | 0 | 3.5 | 2019-07-26 | 15.1 | 2.9 | 0 | 2018-07-26 | 21 | 0 | 3 | 2017-07-26 | 11.7 | 6.3 | 0 | 2016-07-26 | 18 | 0 | 0 | 2.43 | 0.65
2025-07-26 | 17.5 | 0.5 | 0 | 2024-07-26 | 15.3 | 2.7 | 0 | 2023-07-26 | 17.5 | 0.5 | 0 | 2022-07-26 | 14.7 | 3.3 | 0 | 2021-07-26 | 16.1 | 1.9 | 0 | 2020-07-26 | 21.4 | 0 | 3.4 | 2019-07-26 | 16.6 | 1.4 | 0 | 2018-07-26 | 21.1 | 0 | 3.1 | 2017-07-26 | 14.2 | 3.8 | 0 | 2016-07-26 | 20.5 | 0 | 2.5 | 1.41 | 0.9
2025-07-26 | 19.2 | 0 | 1.2 | 2024-07-26 | 17.1 | 0.9 | 0 | 2023-07-26 | 19.4 | 0 | 1.4 | 2022-07-26 | 17.1 | 0.9 | 0 | 2021-07-26 | 17.8 | 0.2 | 0 | 2020-07-26 | 22.8 | 0 | 4.8 | 2019-07-26 | 18.6 | 0 | 0.6 | 2018-07-26 | 21.2 | 0 | 3.2 | 2017-07-26 | 16.7 | 1.3 | 0 | 2016-07-26 | 21.7 | 0 | 3.7 | 0.33 | 1.49
2025-07-26 | 22.2 | 0 | 4.2 | 2024-07-26 | 18.6 | 0 | 0.6 | 2023-07-26 | 21.6 | 0 | 3.6 | 2022-07-26 | 19.4 | 0 | 1.4 | 2021-07-26 | 20.2 | 0 | 2.2 | 2020-07-26 | 24.4 | 0 | 6.4 | 2019-07-26 | 21.4 | 0 | 3.4 | 2018-07-26 | 20.5 | 0 | 2.5 | 2017-07-26 | 18.8 | 0 | 0.8 | 2016-07-26 | 22.7 | 0 | 4.7 | 0 | 2.98
2025-07-26 | 24.7 | 0 | 6.7 | 2024-07-26 | 20.3 | 0 | 2.3 | 2023-07-26 | 23.2 | 0 | 5.2 | 2022-07-26 | 20.6 | 0 | 2.6 | 2021-07-26 | 22.9 | 0 | 4.9 | 2020-07-26 | 27.6 | 0 | 9.6 | 2019-07-26 | 23.5 | 0 | 5.5 | 2018-07-26 | 21.9 | 0 | 3.9 | 2017-07-26 | 19.6 | 0 | 1.6 | 2016-07-26 | 23 | 0 | 5 | 0 | 4.73
2025-07-26 | 27.1 | 0 | 9.1 | 2024-07-26 | 22.6 | 0 | 4.6 | 2023-07-26 | 25.6 | 0 | 7.6 | 2022-07-26 | 22 | 0 | 4 | 2021-07-26 | 24.3 | 0 | 6.3 | 2020-07-26 | 30.2 | 0 | 12.2 | 2019-07-26 | 26.1 | 0 | 8.1 | 2018-07-26 | 23.9 | 0 | 5.9 | 2017-07-26 | 19.9 | 0 | 1.9 | 2016-07-26 | 25.5 | 0 | 7.5 | 0 | 6.72
2025-07-26 | 27.8 | 0 | 9.8 | 2024-07-26 | 23.5 | 0 | 5.5 | 2023-07-26 | 25 | 0 | 7 | 2022-07-26 | 22.8 | 0 | 4.8 | 2021-07-26 | 25.2 | 0 | 7.2 | 2020-07-26 | 32.5 | 0 | 14.5 | 2019-07-26 | 27.9 | 0 | 9.9 | 2018-07-26 | 26.3 | 0 | 8.3 | 2017-07-26 | 20.3 | 0 | 2.3 | 2016-07-26 | 25.2 | 0 | 7.2 | 0 | 7.65
2025-07-26 | 28.7 | 0 | 10.7 | 2024-07-26 | 24.6 | 0 | 6.6 | 2023-07-26 | 26.7 | 0 | 8.7 | 2022-07-26 | 23.8 | 0 | 5.8 | 2021-07-26 | 26.7 | 0 | 8.7 | 2020-07-26 | 33.7 | 0 | 15.7 | 2019-07-26 | 29.2 | 0 | 11.2 | 2018-07-26 | 27.4 | 0 | 9.4 | 2017-07-26 | 21.6 | 0 | 3.6 | 2016-07-26 | 25.7 | 0 | 7.7 | 0 | 8.81
2025-07-26 | 28.9 | 0 | 10.9 | 2024-07-26 | 25.3 | 0 | 7.3 | 2023-07-26 | 28.2 | 0 | 10.2 | 2022-07-26 | 24.6 | 0 | 6.6 | 2021-07-26 | 27.6 | 0 | 9.6 | 2020-07-26 | 33.4 | 0 | 15.4 | 2019-07-26 | 31.1 | 0 | 13.1 | 2018-07-26 | 28.2 | 0 | 10.2 | 2017-07-26 | 21 | 0 | 3 | 2016-07-26 | 28.3 | 0 | 10.3 | 0 | 9.66
2025-07-26 | 29.9 | 0 | 11.9 | 2024-07-26 | 26 | 0 | 8 | 2023-07-26 | 27.9 | 0 | 9.9 | 2022-07-26 | 24.9 | 0 | 6.9 | 2021-07-26 | 28.5 | 0 | 10.5 | 2020-07-26 | 34.4 | 0 | 16.4 | 2019-07-26 | 31.2 | 0 | 13.2 | 2018-07-26 | 28.6 | 0 | 10.6 | 2017-07-26 | 22.1 | 0 | 4.1 | 2016-07-26 | 28.6 | 0 | 10.6 | 0 | 10.21
2025-07-26 | 29.5 | 0 | 11.5 | 2024-07-26 | 26.3 | 0 | 8.3 | 2023-07-26 | 25.3 | 0 | 7.3 | 2022-07-26 | 25.6 | 0 | 7.6 | 2021-07-26 | 27.2 | 0 | 9.2 | 2020-07-26 | 34.1 | 0 | 16.1 | 2019-07-26 | 31.5 | 0 | 13.5 | 2018-07-26 | 29.6 | 0 | 11.6 | 2017-07-26 | 21.6 | 0 | 3.6 | 2016-07-26 | 29.3 | 0 | 11.3 | 0 | 10
2025-07-26 | 29.5 | 0 | 11.5 | 2024-07-26 | 26.6 | 0 | 8.6 | 2023-07-26 | 28.1 | 0 | 10.1 | 2022-07-26 | 23.5 | 0 | 5.5 | 2021-07-26 | 28.1 | 0 | 10.1 | 2020-07-26 | 34.5 | 0 | 16.5 | 2019-07-26 | 31 | 0 | 13 | 2018-07-26 | 29.4 | 0 | 11.4 | 2017-07-26 | 20.8 | 0 | 2.8 | 2016-07-26 | 29.4 | 0 | 11.4 | 0 | 10.09
2025-07-26 | 28.6 | 0 | 10.6 | 2024-07-26 | 26.1 | 0 | 8.1 | 2023-07-26 | 27 | 0 | 9 | 2022-07-26 | 22.9 | 0 | 4.9 | 2021-07-26 | 27.7 | 0 | 9.7 | 2020-07-26 | 34.2 | 0 | 16.2 | 2019-07-26 | 30.2 | 0 | 12.2 | 2018-07-26 | 28.9 | 0 | 10.9 | 2017-07-26 | 20.6 | 0 | 2.6 | 2016-07-26 | 29.2 | 0 | 11.2 | 0 | 9.54
2025-07-26 | 27.6 | 0 | 9.6 | 2024-07-26 | 25 | 0 | 7 | 2023-07-26 | 26.9 | 0 | 8.9 | 2022-07-26 | 23.4 | 0 | 5.4 | 2021-07-26 | 26.4 | 0 | 8.4 | 2020-07-26 | 32.4 | 0 | 14.4 | 2019-07-26 | 29.1 | 0 | 11.1 | 2018-07-26 | 27 | 0 | 9 | 2017-07-26 | 19.9 | 0 | 1.9 | 2016-07-26 | 28.5 | 0 | 10.5 | 0 | 8.62
2025-07-26 | 25.9 | 0 | 7.9 | 2024-07-26 | 22 | 0 | 4 | 2023-07-26 | 26.1 | 0 | 8.1 | 2022-07-26 | 21.8 | 0 | 3.8 | 2021-07-26 | 24.3 | 0 | 6.3 | 2020-07-26 | 31.5 | 0 | 13.5 | 2019-07-26 | 26.1 | 0 | 8.1 | 2018-07-26 | 22.6 | 0 | 4.6 | 2017-07-26 | 18.9 | 0 | 0.9 | 2016-07-26 | 27.1 | 0 | 9.1 | 0 | 6.63
2025-07-26 | 23.9 | 0 | 5.9 | 2024-07-26 | 20.7 | 0 | 2.7 | 2023-07-26 | 24.6 | 0 | 6.6 | 2022-07-26 | 19.9 | 0 | 1.9 | 2021-07-26 | 22.7 | 0 | 4.7 | 2020-07-26 | 30.1 | 0 | 12.1 | 2019-07-26 | 24.2 | 0 | 6.2 | 2018-07-26 | 20.3 | 0 | 2.3 | 2017-07-26 | 18.3 | 0 | 0.3 | 2016-07-26 | 24.5 | 0 | 6.5 | 0 | 4.92
2025-07-26 | 23.6 | 0 | 5.6 | 2024-07-26 | 20.6 | 0 | 2.6 | 2023-07-26 | 24.4 | 0 | 6.4 | 2022-07-26 | 18.2 | 0 | 0.2 | 2021-07-26 | 21.6 | 0 | 3.6 | 2020-07-26 | 28.9 | 0 | 10.9 | 2019-07-26 | 22.7 | 0 | 4.7 | 2018-07-26 | 19.7 | 0 | 1.7 | 2017-07-26 | 17.9 | 0.1 | 0 | 2016-07-26 | 21.5 | 0 | 3.5 | 0.01 | 3.92
2025-07-26 | 21.7 | 0 | 3.7 | 2024-07-26 | 18.6 | 0 | 0.6 | 2023-07-26 | 21.7 | 0 | 3.7 | 2022-07-26 | 17.7 | 0.3 | 0 | 2021-07-26 | 20.2 | 0 | 2.2 | 2020-07-26 | 28.2 | 0 | 10.2 | 2019-07-26 | 21.4 | 0 | 3.4 | 2018-07-26 | 19.4 | 0 | 1.4 | 2017-07-26 | 17.7 | 0.3 | 0 | 2016-07-26 | 19 | 0 | 1 | 0.06 | 2.62
2025-07-26 | 21.6 | 0 | 3.6 | 2024-07-26 | 18.9 | 0 | 0.9 | 2023-07-26 | 21 | 0 | 3 | 2022-07-26 | 17.3 | 0.7 | 0 | 2021-07-26 | 19.8 | 0 | 1.8 | 2020-07-26 | 28.3 | 0 | 10.3 | 2019-07-26 | 20.1 | 0 | 2.1 | 2018-07-26 | 18.3 | 0 | 0.3 | 2017-07-26 | 17.9 | 0.1 | 0 | 2016-07-26 | 19.2 | 0 | 1.2 | 0.08 | 2.32
2025-07-27 | 20.4 | 0 | 2.4 | 2024-07-27 | 17.8 | 0.2 | 0 | 2023-07-27 | 20.7 | 0 | 2.7 | 2022-07-27 | 16.2 | 1.8 | 0 | 2021-07-27 | 19.1 | 0 | 1.1 | 2020-07-27 | 27.9 | 0 | 9.9 | 2019-07-27 | 19.5 | 0 | 1.5 | 2018-07-27 | 18.9 | 0 | 0.9 | 2017-07-27 | 18 | 0 | 0 | 2016-07-27 | 18.8 | 0 | 0.8 | 0.2 | 1.93
2025-07-27 | 20.5 | 0 | 2.5 | 2024-07-27 | 16.6 | 1.4 | 0 | 2023-07-27 | 20 | 0 | 2 | 2022-07-27 | 15.7 | 2.3 | 0 | 2021-07-27 | 16.1 | 1.9 | 0 | 2020-07-27 | 26.8 | 0 | 8.8 | 2019-07-27 | 18.7 | 0 | 0.7 | 2018-07-27 | 17.1 | 0.9 | 0 | 2017-07-27 | 17 | 1 | 0 | 2016-07-27 | 19 | 0 | 1 | 0.75 | 1.5
2025-07-27 | 20.5 | 0 | 2.5 | 2024-07-27 | 16.4 | 1.6 | 0 | 2023-07-27 | 19.4 | 0 | 1.4 | 2022-07-27 | 15.5 | 2.5 | 0 | 2021-07-27 | 16.2 | 1.8 | 0 | 2020-07-27 | 26.3 | 0 | 8.3 | 2019-07-27 | 15.9 | 2.1 | 0 | 2018-07-27 | 17.1 | 0.9 | 0 | 2017-07-27 | 16.7 | 1.3 | 0 | 2016-07-27 | 18.3 | 0 | 0.3 | 1.02 | 1.25
2025-07-27 | 20.1 | 0 | 2.1 | 2024-07-27 | 15.9 | 2.1 | 0 | 2023-07-27 | 19 | 0 | 1 | 2022-07-27 | 14.8 | 3.2 | 0 | 2021-07-27 | 15.9 | 2.1 | 0 | 2020-07-27 | 25.2 | 0 | 7.2 | 2019-07-27 | 16.9 | 1.1 | 0 | 2018-07-27 | 17.4 | 0.6 | 0 | 2017-07-27 | 16.8 | 1.2 | 0 | 2016-07-27 | 17.2 | 0.8 | 0 | 1.11 | 1.03
2025-07-27 | 20.4 | 0 | 2.4 | 2024-07-27 | 16.3 | 1.7 | 0 | 2023-07-27 | 18.9 | 0 | 0.9 | 2022-07-27 | 14.3 | 3.7 | 0 | 2021-07-27 | 14.7 | 3.3 | 0 | 2020-07-27 | 24.3 | 0 | 6.3 | 2019-07-27 | 16.3 | 1.7 | 0 | 2018-07-27 | 16 | 2 | 0 | 2017-07-27 | 17.1 | 0.9 | 0 | 2016-07-27 | 16.6 | 1.4 | 0 | 1.47 | 0.96
2025-07-27 | 20.3 | 0 | 2.3 | 2024-07-27 | 15.8 | 2.2 | 0 | 2023-07-27 | 18.7 | 0 | 0.7 | 2022-07-27 | 13.7 | 4.3 | 0 | 2021-07-27 | 14.9 | 3.1 | 0 | 2020-07-27 | 23.7 | 0 | 5.7 | 2019-07-27 | 15.5 | 2.5 | 0 | 2018-07-27 | 15.8 | 2.2 | 0 | 2017-07-27 | 17.5 | 0.5 | 0 | 2016-07-27 | 16.4 | 1.6 | 0 | 1.64 | 0.87
2025-07-27 | 21 | 0 | 3 | 2024-07-27 | 17.9 | 0.1 | 0 | 2023-07-27 | 18.5 | 0 | 0.5 | 2022-07-27 | 15.3 | 2.7 | 0 | 2021-07-27 | 15.2 | 2.8 | 0 | 2020-07-27 | 24.2 | 0 | 6.2 | 2019-07-27 | 17.4 | 0.6 | 0 | 2018-07-27 | 17.8 | 0.2 | 0 | 2017-07-27 | 17.6 | 0.4 | 0 | 2016-07-27 | 17.5 | 0.5 | 0 | 0.73 | 0.97
2025-07-27 | 21.9 | 0 | 3.9 | 2024-07-27 | 19.2 | 0 | 1.2 | 2023-07-27 | 18.8 | 0 | 0.8 | 2022-07-27 | 18 | 0 | 0 | 2021-07-27 | 16.8 | 1.2 | 0 | 2020-07-27 | 24.3 | 0 | 6.3 | 2019-07-27 | 19.5 | 0 | 1.5 | 2018-07-27 | 20.4 | 0 | 2.4 | 2017-07-27 | 19.6 | 0 | 1.6 | 2016-07-27 | 20.1 | 0 | 2.1 | 0.12 | 1.98
2025-07-27 | 23.5 | 0 | 5.5 | 2024-07-27 | 21.3 | 0 | 3.3 | 2023-07-27 | 19.1 | 0 | 1.1 | 2022-07-27 | 20 | 0 | 2 | 2021-07-27 | 17.5 | 0.5 | 0 | 2020-07-27 | 24.2 | 0 | 6.2 | 2019-07-27 | 23.3 | 0 | 5.3 | 2018-07-27 | 21.4 | 0 | 3.4 | 2017-07-27 | 20.4 | 0 | 2.4 | 2016-07-27 | 23.1 | 0 | 5.1 | 0.05 | 3.43
2025-07-27 | 24.9 | 0 | 6.9 | 2024-07-27 | 23.1 | 0 | 5.1 | 2023-07-27 | 19.1 | 0 | 1.1 | 2022-07-27 | 22.9 | 0 | 4.9 | 2021-07-27 | 16.8 | 1.2 | 0 | 2020-07-27 | 25.9 | 0 | 7.9 | 2019-07-27 | 26.1 | 0 | 8.1 | 2018-07-27 | 23.1 | 0 | 5.1 | 2017-07-27 | 21.6 | 0 | 3.6 | 2016-07-27 | 25.5 | 0 | 7.5 | 0.12 | 5.02
2025-07-27 | 25.5 | 0 | 7.5 | 2024-07-27 | 24.8 | 0 | 6.8 | 2023-07-27 | 19.7 | 0 | 1.7 | 2022-07-27 | 23.7 | 0 | 5.7 | 2021-07-27 | 16.3 | 1.7 | 0 | 2020-07-27 | 28.3 | 0 | 10.3 | 2019-07-27 | 28.1 | 0 | 10.1 | 2018-07-27 | 24.3 | 0 | 6.3 | 2017-07-27 | 21.8 | 0 | 3.8 | 2016-07-27 | 27 | 0 | 9 | 0.17 | 6.12
2025-07-27 | 25.5 | 0 | 7.5 | 2024-07-27 | 25.8 | 0 | 7.8 | 2023-07-27 | 21.6 | 0 | 3.6 | 2022-07-27 | 24.9 | 0 | 6.9 | 2021-07-27 | 16.5 | 1.5 | 0 | 2020-07-27 | 29.7 | 0 | 11.7 | 2019-07-27 | 29.7 | 0 | 11.7 | 2018-07-27 | 25.6 | 0 | 7.6 | 2017-07-27 | 21.6 | 0 | 3.6 | 2016-07-27 | 27.6 | 0 | 9.6 | 0.15 | 7
2025-07-27 | 27.2 | 0 | 9.2 | 2024-07-27 | 26.4 | 0 | 8.4 | 2023-07-27 | 23.2 | 0 | 5.2 | 2022-07-27 | 24.5 | 0 | 6.5 | 2021-07-27 | 16.4 | 1.6 | 0 | 2020-07-27 | 26.4 | 0 | 8.4 | 2019-07-27 | 30.3 | 0 | 12.3 | 2018-07-27 | 27.3 | 0 | 9.3 | 2017-07-27 | 21.7 | 0 | 3.7 | 2016-07-27 | 29.2 | 0 | 11.2 | 0.16 | 7.42
2025-07-27 | 28.4 | 0 | 10.4 | 2024-07-27 | 27.1 | 0 | 9.1 | 2023-07-27 | 25 | 0 | 7 | 2022-07-27 | 26.2 | 0 | 8.2 | 2021-07-27 | 16.6 | 1.4 | 0 | 2020-07-27 | 28.2 | 0 | 10.2 | 2019-07-27 | 29.8 | 0 | 11.8 | 2018-07-27 | 27.7 | 0 | 9.7 | 2017-07-27 | 22.8 | 0 | 4.8 | 2016-07-27 | 28.9 | 0 | 10.9 | 0.14 | 8.21
2025-07-27 | 30.1 | 0 | 12.1 | 2024-07-27 | 27.3 | 0 | 9.3 | 2023-07-27 | 26.1 | 0 | 8.1 | 2022-07-27 | 25.1 | 0 | 7.1 | 2021-07-27 | 17.3 | 0.7 | 0 | 2020-07-27 | 27.6 | 0 | 9.6 | 2019-07-27 | 31.1 | 0 | 13.1 | 2018-07-27 | 25.9 | 0 | 7.9 | 2017-07-27 | 25.1 | 0 | 7.1 | 2016-07-27 | 29.8 | 0 | 11.8 | 0.07 | 8.61
2025-07-27 | 30.5 | 0 | 12.5 | 2024-07-27 | 27.1 | 0 | 9.1 | 2023-07-27 | 27.1 | 0 | 9.1 | 2022-07-27 | 25.8 | 0 | 7.8 | 2021-07-27 | 17 | 1 | 0 | 2020-07-27 | 30.6 | 0 | 12.6 | 2019-07-27 | 30.9 | 0 | 12.9 | 2018-07-27 | 22.3 | 0 | 4.3 | 2017-07-27 | 25.2 | 0 | 7.2 | 2016-07-27 | 30.1 | 0 | 12.1 | 0.1 | 8.76
2025-07-27 | 30.9 | 0 | 12.9 | 2024-07-27 | 27.5 | 0 | 9.5 | 2023-07-27 | 28 | 0 | 10 | 2022-07-27 | 25.6 | 0 | 7.6 | 2021-07-27 | 17.4 | 0.6 | 0 | 2020-07-27 | 30.6 | 0 | 12.6 | 2019-07-27 | 30.8 | 0 | 12.8 | 2018-07-27 | 24.1 | 0 | 6.1 | 2017-07-27 | 25.8 | 0 | 7.8 | 2016-07-27 | 30.4 | 0 | 12.4 | 0.06 | 9.17
2025-07-27 | 30.7 | 0 | 12.7 | 2024-07-27 | 26.7 | 0 | 8.7 | 2023-07-27 | 27.2 | 0 | 9.2 | 2022-07-27 | 25.5 | 0 | 7.5 | 2021-07-27 | 17.8 | 0.2 | 0 | 2020-07-27 | 31.1 | 0 | 13.1 | 2019-07-27 | 30 | 0 | 12 | 2018-07-27 | 26.2 | 0 | 8.2 | 2017-07-27 | 21.9 | 0 | 3.9 | 2016-07-27 | 30.8 | 0 | 12.8 | 0.02 | 8.81
2025-07-27 | 30 | 0 | 12 | 2024-07-27 | 25.5 | 0 | 7.5 | 2023-07-27 | 26.6 | 0 | 8.6 | 2022-07-27 | 24.6 | 0 | 6.6 | 2021-07-27 | 17.3 | 0.7 | 0 | 2020-07-27 | 28.7 | 0 | 10.7 | 2019-07-27 | 27.3 | 0 | 9.3 | 2018-07-27 | 25.6 | 0 | 7.6 | 2017-07-27 | 21.7 | 0 | 3.7 | 2016-07-27 | 29.4 | 0 | 11.4 | 0.07 | 7.74
2025-07-27 | 28.6 | 0 | 10.6 | 2024-07-27 | 24 | 0 | 6 | 2023-07-27 | 24.6 | 0 | 6.6 | 2022-07-27 | 22.9 | 0 | 4.9 | 2021-07-27 | 17.7 | 0.3 | 0 | 2020-07-27 | 24.3 | 0 | 6.3 | 2019-07-27 | 26.4 | 0 | 8.4 | 2018-07-27 | 23.5 | 0 | 5.5 | 2017-07-27 | 22.1 | 0 | 4.1 | 2016-07-27 | 26.6 | 0 | 8.6 | 0.03 | 6.1
2025-07-27 | 26.4 | 0 | 8.4 | 2024-07-27 | 22.6 | 0 | 4.6 | 2023-07-27 | 23.7 | 0 | 5.7 | 2022-07-27 | 20.7 | 0 | 2.7 | 2021-07-27 | 16.9 | 1.1 | 0 | 2020-07-27 | 23.6 | 0 | 5.6 | 2019-07-27 | 25.4 | 0 | 7.4 | 2018-07-27 | 21.4 | 0 | 3.4 | 2017-07-27 | 20.1 | 0 | 2.1 | 2016-07-27 | 23.4 | 0 | 5.4 | 0.11 | 4.53
2025-07-27 | 24.4 | 0 | 6.4 | 2024-07-27 | 21 | 0 | 3 | 2023-07-27 | 22.6 | 0 | 4.6 | 2022-07-27 | 21.4 | 0 | 3.4 | 2021-07-27 | 15.5 | 2.5 | 0 | 2020-07-27 | 24.5 | 0 | 6.5 | 2019-07-27 | 23.6 | 0 | 5.6 | 2018-07-27 | 21.4 | 0 | 3.4 | 2017-07-27 | 19.6 | 0 | 1.6 | 2016-07-27 | 21.9 | 0 | 3.9 | 0.25 | 3.84
2025-07-27 | 22.4 | 0 | 4.4 | 2024-07-27 | 19.9 | 0 | 1.9 | 2023-07-27 | 21.9 | 0 | 3.9 | 2022-07-27 | 21.1 | 0 | 3.1 | 2021-07-27 | 15.1 | 2.9 | 0 | 2020-07-27 | 24.2 | 0 | 6.2 | 2019-07-27 | 23.1 | 0 | 5.1 | 2018-07-27 | 21 | 0 | 3 | 2017-07-27 | 19.9 | 0 | 1.9 | 2016-07-27 | 20.8 | 0 | 2.8 | 0.29 | 3.23
2025-07-27 | 22.3 | 0 | 4.3 | 2024-07-27 | 19.2 | 0 | 1.2 | 2023-07-27 | 21.9 | 0 | 3.9 | 2022-07-27 | 19.9 | 0 | 1.9 | 2021-07-27 | 14.7 | 3.3 | 0 | 2020-07-27 | 23.6 | 0 | 5.6 | 2019-07-27 | 23.3 | 0 | 5.3 | 2018-07-27 | 20.3 | 0 | 2.3 | 2017-07-27 | 19.6 | 0 | 1.6 | 2016-07-27 | 20.3 | 0 | 2.3 | 0.33 | 2.84
2025-07-28 | 22.5 | 0 | 4.5 | 2024-07-28 | 18.8 | 0 | 0.8 | 2023-07-28 | 21.2 | 0 | 3.2 | 2022-07-28 | 19.6 | 0 | 1.6 | 2021-07-28 | 13.9 | 4.1 | 0 | 2020-07-28 | 24.2 | 0 | 6.2 | 2019-07-28 | 22.7 | 0 | 4.7 | 2018-07-28 | 18.8 | 0 | 0.8 | 2017-07-28 | 18.8 | 0 | 0.8 | 2016-07-28 | 20.6 | 0 | 2.6 | 0.41 | 2.52
2025-07-28 | 22.1 | 0 | 4.1 | 2024-07-28 | 17 | 1 | 0 | 2023-07-28 | 20.8 | 0 | 2.8 | 2022-07-28 | 18.9 | 0 | 0.9 | 2021-07-28 | 13.5 | 4.5 | 0 | 2020-07-28 | 23.5 | 0 | 5.5 | 2019-07-28 | 22.2 | 0 | 4.2 | 2018-07-28 | 18.5 | 0 | 0.5 | 2017-07-28 | 17.1 | 0.9 | 0 | 2016-07-28 | 21.3 | 0 | 3.3 | 0.64 | 2.13
2025-07-28 | 21 | 0 | 3 | 2024-07-28 | 16.7 | 1.3 | 0 | 2023-07-28 | 20.9 | 0 | 2.9 | 2022-07-28 | 17.8 | 0.2 | 0 | 2021-07-28 | 13 | 5 | 0 | 2020-07-28 | 23.1 | 0 | 5.1 | 2019-07-28 | 21.7 | 0 | 3.7 | 2018-07-28 | 18.1 | 0 | 0.1 | 2017-07-28 | 15.4 | 2.6 | 0 | 2016-07-28 | 21 | 0 | 3 | 0.91 | 1.78
2025-07-28 | 20.1 | 0 | 2.1 | 2024-07-28 | 16.6 | 1.4 | 0 | 2023-07-28 | 20.4 | 0 | 2.4 | 2022-07-28 | 17.6 | 0.4 | 0 | 2021-07-28 | 13.3 | 4.7 | 0 | 2020-07-28 | 23 | 0 | 5 | 2019-07-28 | 21.6 | 0 | 3.6 | 2018-07-28 | 17.1 | 0.9 | 0 | 2017-07-28 | 14.9 | 3.1 | 0 | 2016-07-28 | 20.9 | 0 | 2.9 | 1.05 | 1.6
2025-07-28 | 20.2 | 0 | 2.2 | 2024-07-28 | 15.6 | 2.4 | 0 | 2023-07-28 | 19.8 | 0 | 1.8 | 2022-07-28 | 17.6 | 0.4 | 0 | 2021-07-28 | 12.8 | 5.2 | 0 | 2020-07-28 | 21.4 | 0 | 3.4 | 2019-07-28 | 21.9 | 0 | 3.9 | 2018-07-28 | 16.1 | 1.9 | 0 | 2017-07-28 | 14.6 | 3.4 | 0 | 2016-07-28 | 20.8 | 0 | 2.8 | 1.33 | 1.41
2025-07-28 | 19.9 | 0 | 1.9 | 2024-07-28 | 15.5 | 2.5 | 0 | 2023-07-28 | 19.4 | 0 | 1.4 | 2022-07-28 | 16.9 | 1.1 | 0 | 2021-07-28 | 13.6 | 4.4 | 0 | 2020-07-28 | 19.3 | 0 | 1.3 | 2019-07-28 | 21.1 | 0 | 3.1 | 2018-07-28 | 16.4 | 1.6 | 0 | 2017-07-28 | 14.4 | 3.6 | 0 | 2016-07-28 | 20.4 | 0 | 2.4 | 1.32 | 1.01
2025-07-28 | 21.2 | 0 | 3.2 | 2024-07-28 | 16.7 | 1.3 | 0 | 2023-07-28 | 20.1 | 0 | 2.1 | 2022-07-28 | 18.2 | 0 | 0.2 | 2021-07-28 | 14.4 | 3.6 | 0 | 2020-07-28 | 20.9 | 0 | 2.9 | 2019-07-28 | 21.7 | 0 | 3.7 | 2018-07-28 | 17.2 | 0.8 | 0 | 2017-07-28 | 15 | 3 | 0 | 2016-07-28 | 20.5 | 0 | 2.5 | 0.87 | 1.46
2025-07-28 | 22.2 | 0 | 4.2 | 2024-07-28 | 18.8 | 0 | 0.8 | 2023-07-28 | 22.2 | 0 | 4.2 | 2022-07-28 | 18.9 | 0 | 0.9 | 2021-07-28 | 16.3 | 1.7 | 0 | 2020-07-28 | 21.9 | 0 | 3.9 | 2019-07-28 | 22.3 | 0 | 4.3 | 2018-07-28 | 18.3 | 0 | 0.3 | 2017-07-28 | 16 | 2 | 0 | 2016-07-28 | 21.3 | 0 | 3.3 | 0.37 | 2.19
2025-07-28 | 25.3 | 0 | 7.3 | 2024-07-28 | 21.5 | 0 | 3.5 | 2023-07-28 | 24.2 | 0 | 6.2 | 2022-07-28 | 21.2 | 0 | 3.2 | 2021-07-28 | 17.9 | 0.1 | 0 | 2020-07-28 | 23.1 | 0 | 5.1 | 2019-07-28 | 23.6 | 0 | 5.6 | 2018-07-28 | 20.6 | 0 | 2.6 | 2017-07-28 | 16.8 | 1.2 | 0 | 2016-07-28 | 21.9 | 0 | 3.9 | 0.13 | 3.74
2025-07-28 | 26.9 | 0 | 8.9 | 2024-07-28 | 23.7 | 0 | 5.7 | 2023-07-28 | 25.3 | 0 | 7.3 | 2022-07-28 | 23 | 0 | 5 | 2021-07-28 | 19.2 | 0 | 1.2 | 2020-07-28 | 24.6 | 0 | 6.6 | 2019-07-28 | 25.9 | 0 | 7.9 | 2018-07-28 | 21.8 | 0 | 3.8 | 2017-07-28 | 17.9 | 0.1 | 0 | 2016-07-28 | 22.3 | 0 | 4.3 | 0.01 | 5.07
2025-07-28 | 29 | 0 | 11 | 2024-07-28 | 25.7 | 0 | 7.7 | 2023-07-28 | 26.6 | 0 | 8.6 | 2022-07-28 | 25 | 0 | 7 | 2021-07-28 | 20.8 | 0 | 2.8 | 2020-07-28 | 26.6 | 0 | 8.6 | 2019-07-28 | 26.6 | 0 | 8.6 | 2018-07-28 | 21.9 | 0 | 3.9 | 2017-07-28 | 18.7 | 0 | 0.7 | 2016-07-28 | 23 | 0 | 5 | 0 | 6.39
2025-07-28 | 30.4 | 0 | 12.4 | 2024-07-28 | 26.7 | 0 | 8.7 | 2023-07-28 | 25.8 | 0 | 7.8 | 2022-07-28 | 26.1 | 0 | 8.1 | 2021-07-28 | 22 | 0 | 4 | 2020-07-28 | 27.6 | 0 | 9.6 | 2019-07-28 | 26.9 | 0 | 8.9 | 2018-07-28 | 22.6 | 0 | 4.6 | 2017-07-28 | 19.9 | 0 | 1.9 | 2016-07-28 | 24.4 | 0 | 6.4 | 0 | 7.24
2025-07-28 | 31.4 | 0 | 13.4 | 2024-07-28 | 27.7 | 0 | 9.7 | 2023-07-28 | 25.4 | 0 | 7.4 | 2022-07-28 | 26 | 0 | 8 | 2021-07-28 | 21.5 | 0 | 3.5 | 2020-07-28 | 28.5 | 0 | 10.5 | 2019-07-28 | 27.8 | 0 | 9.8 | 2018-07-28 | 22.9 | 0 | 4.9 | 2017-07-28 | 21 | 0 | 3 | 2016-07-28 | 26.2 | 0 | 8.2 | 0 | 7.84
2025-07-28 | 32.1 | 0 | 14.1 | 2024-07-28 | 28.1 | 0 | 10.1 | 2023-07-28 | 25.9 | 0 | 7.9 | 2022-07-28 | 26.2 | 0 | 8.2 | 2021-07-28 | 22.1 | 0 | 4.1 | 2020-07-28 | 29.4 | 0 | 11.4 | 2019-07-28 | 27.7 | 0 | 9.7 | 2018-07-28 | 24.4 | 0 | 6.4 | 2017-07-28 | 22.1 | 0 | 4.1 | 2016-07-28 | 27.4 | 0 | 9.4 | 0 | 8.54
2025-07-28 | 33.2 | 0 | 15.2 | 2024-07-28 | 28.6 | 0 | 10.6 | 2023-07-28 | 28.1 | 0 | 10.1 | 2022-07-28 | 25.2 | 0 | 7.2 | 2021-07-28 | 23.1 | 0 | 5.1 | 2020-07-28 | 30.5 | 0 | 12.5 | 2019-07-28 | 29.3 | 0 | 11.3 | 2018-07-28 | 23.9 | 0 | 5.9 | 2017-07-28 | 22.4 | 0 | 4.4 | 2016-07-28 | 28.8 | 0 | 10.8 | 0 | 9.31
2025-07-28 | 33.9 | 0 | 15.9 | 2024-07-28 | 28.7 | 0 | 10.7 | 2023-07-28 | 22.1 | 0 | 4.1 | 2022-07-28 | 24.6 | 0 | 6.6 | 2021-07-28 | 22.9 | 0 | 4.9 | 2020-07-28 | 29 | 0 | 11 | 2019-07-28 | 21.4 | 0 | 3.4 | 2018-07-28 | 26.7 | 0 | 8.7 | 2017-07-28 | 22.4 | 0 | 4.4 | 2016-07-28 | 26.9 | 0 | 8.9 | 0 | 7.86
2025-07-28 | 32.4 | 0 | 14.4 | 2024-07-28 | 28.7 | 0 | 10.7 | 2023-07-28 | 24.8 | 0 | 6.8 | 2022-07-28 | 25 | 0 | 7 | 2021-07-28 | 23.8 | 0 | 5.8 | 2020-07-28 | 30.2 | 0 | 12.2 | 2019-07-28 | 28 | 0 | 10 | 2018-07-28 | 19 | 0 | 1 | 2017-07-28 | 23 | 0 | 5 | 2016-07-28 | 28.4 | 0 | 10.4 | 0 | 8.33
2025-07-28 | 32.9 | 0 | 14.9 | 2024-07-28 | 28 | 0 | 10 | 2023-07-28 | 24.8 | 0 | 6.8 | 2022-07-28 | 23.3 | 0 | 5.3 | 2021-07-28 | 23.4 | 0 | 5.4 | 2020-07-28 | 28.2 | 0 | 10.2 | 2019-07-28 | 29.1 | 0 | 11.1 | 2018-07-28 | 18.9 | 0 | 0.9 | 2017-07-28 | 23.6 | 0 | 5.6 | 2016-07-28 | 27.6 | 0 | 9.6 | 0 | 7.98
2025-07-28 | 30.6 | 0 | 12.6 | 2024-07-28 | 26.9 | 0 | 8.9 | 2023-07-28 | 25.3 | 0 | 7.3 | 2022-07-28 | 25.3 | 0 | 7.3 | 2021-07-28 | 21.2 | 0 | 3.2 | 2020-07-28 | 28.7 | 0 | 10.7 | 2019-07-28 | 28.9 | 0 | 10.9 | 2018-07-28 | 19.9 | 0 | 1.9 | 2017-07-28 | 22.5 | 0 | 4.5 | 2016-07-28 | 27.2 | 0 | 9.2 | 0 | 7.65
2025-07-28 | 29.6 | 0 | 11.6 | 2024-07-28 | 25.7 | 0 | 7.7 | 2023-07-28 | 20.3 | 0 | 2.3 | 2022-07-28 | 23.5 | 0 | 5.5 | 2021-07-28 | 20.8 | 0 | 2.8 | 2020-07-28 | 26.3 | 0 | 8.3 | 2019-07-28 | 25.2 | 0 | 7.2 | 2018-07-28 | 18.8 | 0 | 0.8 | 2017-07-28 | 21.7 | 0 | 3.7 | 2016-07-28 | 25.5 | 0 | 7.5 | 0 | 5.74
2025-07-28 | 28.2 | 0 | 10.2 | 2024-07-28 | 23.8 | 0 | 5.8 | 2023-07-28 | 20.5 | 0 | 2.5 | 2022-07-28 | 21.4 | 0 | 3.4 | 2021-07-28 | 17.7 | 0.3 | 0 | 2020-07-28 | 23.4 | 0 | 5.4 | 2019-07-28 | 23.2 | 0 | 5.2 | 2018-07-28 | 18.4 | 0 | 0.4 | 2017-07-28 | 20.2 | 0 | 2.2 | 2016-07-28 | 23.1 | 0 | 5.1 | 0.03 | 4.02
2025-07-28 | 27.1 | 0 | 9.1 | 2024-07-28 | 22.6 | 0 | 4.6 | 2023-07-28 | 20.9 | 0 | 2.9 | 2022-07-28 | 20.7 | 0 | 2.7 | 2021-07-28 | 15.5 | 2.5 | 0 | 2020-07-28 | 21.6 | 0 | 3.6 | 2019-07-28 | 22.6 | 0 | 4.6 | 2018-07-28 | 17.3 | 0.7 | 0 | 2017-07-28 | 18.5 | 0 | 0.5 | 2016-07-28 | 21.5 | 0 | 3.5 | 0.32 | 3.15
2025-07-28 | 26.3 | 0 | 8.3 | 2024-07-28 | 22 | 0 | 4 | 2023-07-28 | 21.2 | 0 | 3.2 | 2022-07-28 | 20.6 | 0 | 2.6 | 2021-07-28 | 15.8 | 2.2 | 0 | 2020-07-28 | 20.5 | 0 | 2.5 | 2019-07-28 | 22.6 | 0 | 4.6 | 2018-07-28 | 17.2 | 0.8 | 0 | 2017-07-28 | 18.2 | 0 | 0.2 | 2016-07-28 | 20.4 | 0 | 2.4 | 0.3 | 2.78
2025-07-28 | 25.3 | 0 | 7.3 | 2024-07-28 | 20.5 | 0 | 2.5 | 2023-07-28 | 20.3 | 0 | 2.3 | 2022-07-28 | 19.8 | 0 | 1.8 | 2021-07-28 | 15.7 | 2.3 | 0 | 2020-07-28 | 20.6 | 0 | 2.6 | 2019-07-28 | 21.3 | 0 | 3.3 | 2018-07-28 | 17.7 | 0.3 | 0 | 2017-07-28 | 14.7 | 3.3 | 0 | 2016-07-28 | 21.2 | 0 | 3.2 | 0.59 | 2.3
2025-07-29 | 24.2 | 0 | 6.2 | 2024-07-29 | 17.8 | 0.2 | 0 | 2023-07-29 | 20 | 0 | 2 | 2022-07-29 | 18.9 | 0 | 0.9 | 2021-07-29 | 15 | 3 | 0 | 2020-07-29 | 18.4 | 0 | 0.4 | 2019-07-29 | 20.7 | 0 | 2.7 | 2018-07-29 | 17.4 | 0.6 | 0 | 2017-07-29 | 15 | 3 | 0 | 2016-07-29 | 19.8 | 0 | 1.8 | 0.68 | 1.4
2025-07-29 | 24.6 | 0 | 6.6 | 2024-07-29 | 18.6 | 0 | 0.6 | 2023-07-29 | 18.3 | 0 | 0.3 | 2022-07-29 | 17.8 | 0.2 | 0 | 2021-07-29 | 14.2 | 3.8 | 0 | 2020-07-29 | 18.2 | 0 | 0.2 | 2019-07-29 | 19.9 | 0 | 1.9 | 2018-07-29 | 16.9 | 1.1 | 0 | 2017-07-29 | 14.2 | 3.8 | 0 | 2016-07-29 | 18.9 | 0 | 0.9 | 0.89 | 1.05
2025-07-29 | 23.9 | 0 | 5.9 | 2024-07-29 | 16.2 | 1.8 | 0 | 2023-07-29 | 17.3 | 0.7 | 0 | 2022-07-29 | 17.5 | 0.5 | 0 | 2021-07-29 | 14.4 | 3.6 | 0 | 2020-07-29 | 17.8 | 0.2 | 0 | 2019-07-29 | 18.9 | 0 | 0.9 | 2018-07-29 | 16.6 | 1.4 | 0 | 2017-07-29 | 13.2 | 4.8 | 0 | 2016-07-29 | 18.5 | 0 | 0.5 | 1.3 | 0.73
2025-07-29 | 22.1 | 0 | 4.1 | 2024-07-29 | 16.8 | 1.2 | 0 | 2023-07-29 | 16.5 | 1.5 | 0 | 2022-07-29 | 16.8 | 1.2 | 0 | 2021-07-29 | 14.3 | 3.7 | 0 | 2020-07-29 | 18.3 | 0 | 0.3 | 2019-07-29 | 18.4 | 0 | 0.4 | 2018-07-29 | 16.1 | 1.9 | 0 | 2017-07-29 | 14.8 | 3.2 | 0 | 2016-07-29 | 18 | 0 | 0 | 1.27 | 0.48
2025-07-29 | 22.1 | 0 | 4.1 | 2024-07-29 | 15.8 | 2.2 | 0 | 2023-07-29 | 16.9 | 1.1 | 0 | 2022-07-29 | 15.7 | 2.3 | 0 | 2021-07-29 | 14.3 | 3.7 | 0 | 2020-07-29 | 18.3 | 0 | 0.3 | 2019-07-29 | 18.9 | 0 | 0.9 | 2018-07-29 | 15.1 | 2.9 | 0 | 2017-07-29 | 14.3 | 3.7 | 0 | 2016-07-29 | 17 | 1 | 0 | 1.69 | 0.53
2025-07-29 | 21.2 | 0 | 3.2 | 2024-07-29 | 16 | 2 | 0 | 2023-07-29 | 16.4 | 1.6 | 0 | 2022-07-29 | 15.2 | 2.8 | 0 | 2021-07-29 | 14.3 | 3.7 | 0 | 2020-07-29 | 18.5 | 0 | 0.5 | 2019-07-29 | 18 | 0 | 0 | 2018-07-29 | 14.1 | 3.9 | 0 | 2017-07-29 | 13.9 | 4.1 | 0 | 2016-07-29 | 17 | 1 | 0 | 1.91 | 0.37
2025-07-29 | 22.5 | 0 | 4.5 | 2024-07-29 | 17.4 | 0.6 | 0 | 2023-07-29 | 16.5 | 1.5 | 0 | 2022-07-29 | 16.3 | 1.7 | 0 | 2021-07-29 | 15.1 | 2.9 | 0 | 2020-07-29 | 19.1 | 0 | 1.1 | 2019-07-29 | 19.2 | 0 | 1.2 | 2018-07-29 | 15.1 | 2.9 | 0 | 2017-07-29 | 15 | 3 | 0 | 2016-07-29 | 17.8 | 0.2 | 0 | 1.28 | 0.68
2025-07-29 | 23.5 | 0 | 5.5 | 2024-07-29 | 20.5 | 0 | 2.5 | 2023-07-29 | 16.2 | 1.8 | 0 | 2022-07-29 | 17.7 | 0.3 | 0 | 2021-07-29 | 15.6 | 2.4 | 0 | 2020-07-29 | 20.3 | 0 | 2.3 | 2019-07-29 | 21.1 | 0 | 3.1 | 2018-07-29 | 17.1 | 0.9 | 0 | 2017-07-29 | 17 | 1 | 0 | 2016-07-29 | 18.8 | 0 | 0.8 | 0.64 | 1.42
2025-07-29 | 24.1 | 0 | 6.1 | 2024-07-29 | 22.6 | 0 | 4.6 | 2023-07-29 | 16.7 | 1.3 | 0 | 2022-07-29 | 19.5 | 0 | 1.5 | 2021-07-29 | 16.3 | 1.7 | 0 | 2020-07-29 | 22.1 | 0 | 4.1 | 2019-07-29 | 23.3 | 0 | 5.3 | 2018-07-29 | 18.9 | 0 | 0.9 | 2017-07-29 | 18.9 | 0 | 0.9 | 2016-07-29 | 20.1 | 0 | 2.1 | 0.3 | 2.55
2025-07-29 | 25.4 | 0 | 7.4 | 2024-07-29 | 24.5 | 0 | 6.5 | 2023-07-29 | 18 | 0 | 0 | 2022-07-29 | 21.2 | 0 | 3.2 | 2021-07-29 | 16.4 | 1.6 | 0 | 2020-07-29 | 20.1 | 0 | 2.1 | 2019-07-29 | 25.6 | 0 | 7.6 | 2018-07-29 | 20.5 | 0 | 2.5 | 2017-07-29 | 21.1 | 0 | 3.1 | 2016-07-29 | 22.4 | 0 | 4.4 | 0.16 | 3.68
2025-07-29 | 26.1 | 0 | 8.1 | 2024-07-29 | 25.1 | 0 | 7.1 | 2023-07-29 | 17.2 | 0.8 | 0 | 2022-07-29 | 22.5 | 0 | 4.5 | 2021-07-29 | 15.9 | 2.1 | 0 | 2020-07-29 | 22.4 | 0 | 4.4 | 2019-07-29 | 27.3 | 0 | 9.3 | 2018-07-29 | 22.4 | 0 | 4.4 | 2017-07-29 | 22.8 | 0 | 4.8 | 2016-07-29 | 22.6 | 0 | 4.6 | 0.29 | 4.72
2025-07-29 | 27.4 | 0 | 9.4 | 2024-07-29 | 25.2 | 0 | 7.2 | 2023-07-29 | 17.6 | 0.4 | 0 | 2022-07-29 | 22.3 | 0 | 4.3 | 2021-07-29 | 16.2 | 1.8 | 0 | 2020-07-29 | 24.9 | 0 | 6.9 | 2019-07-29 | 29.1 | 0 | 11.1 | 2018-07-29 | 24.2 | 0 | 6.2 | 2017-07-29 | 23.3 | 0 | 5.3 | 2016-07-29 | 23.3 | 0 | 5.3 | 0.22 | 5.57
2025-07-29 | 27.5 | 0 | 9.5 | 2024-07-29 | 25.3 | 0 | 7.3 | 2023-07-29 | 17.6 | 0.4 | 0 | 2022-07-29 | 22.3 | 0 | 4.3 | 2021-07-29 | 16.4 | 1.6 | 0 | 2020-07-29 | 24.3 | 0 | 6.3 | 2019-07-29 | 28.9 | 0 | 10.9 | 2018-07-29 | 24.7 | 0 | 6.7 | 2017-07-29 | 23.1 | 0 | 5.1 | 2016-07-29 | 24.7 | 0 | 6.7 | 0.2 | 5.68
2025-07-29 | 28.9 | 0 | 10.9 | 2024-07-29 | 24.8 | 0 | 6.8 | 2023-07-29 | 18.1 | 0 | 0.1 | 2022-07-29 | 23.6 | 0 | 5.6 | 2021-07-29 | 16.6 | 1.4 | 0 | 2020-07-29 | 25.6 | 0 | 7.6 | 2019-07-29 | 30.6 | 0 | 12.6 | 2018-07-29 | 26.4 | 0 | 8.4 | 2017-07-29 | 24.4 | 0 | 6.4 | 2016-07-29 | 25.5 | 0 | 7.5 | 0.14 | 6.59
2025-07-29 | 29.6 | 0 | 11.6 | 2024-07-29 | 24.3 | 0 | 6.3 | 2023-07-29 | 17.6 | 0.4 | 0 | 2022-07-29 | 23.8 | 0 | 5.8 | 2021-07-29 | 17.1 | 0.9 | 0 | 2020-07-29 | 27 | 0 | 9 | 2019-07-29 | 29.7 | 0 | 11.7 | 2018-07-29 | 25.4 | 0 | 7.4 | 2017-07-29 | 25 | 0 | 7 | 2016-07-29 | 24.9 | 0 | 6.9 | 0.13 | 6.57
2025-07-29 | 29.9 | 0 | 11.9 | 2024-07-29 | 25.1 | 0 | 7.1 | 2023-07-29 | 17.3 | 0.7 | 0 | 2022-07-29 | 24.7 | 0 | 6.7 | 2021-07-29 | 18.1 | 0 | 0.1 | 2020-07-29 | 27.1 | 0 | 9.1 | 2019-07-29 | 30 | 0 | 12 | 2018-07-29 | 26.6 | 0 | 8.6 | 2017-07-29 | 24.7 | 0 | 6.7 | 2016-07-29 | 25.7 | 0 | 7.7 | 0.07 | 6.99
2025-07-29 | 27.9 | 0 | 9.9 | 2024-07-29 | 26.1 | 0 | 8.1 | 2023-07-29 | 18.1 | 0 | 0.1 | 2022-07-29 | 25.1 | 0 | 7.1 | 2021-07-29 | 18.6 | 0 | 0.6 | 2020-07-29 | 23.7 | 0 | 5.7 | 2019-07-29 | 27.7 | 0 | 9.7 | 2018-07-29 | 26.8 | 0 | 8.8 | 2017-07-29 | 24.4 | 0 | 6.4 | 2016-07-29 | 26.1 | 0 | 8.1 | 0 | 6.45
2025-07-29 | 27.9 | 0 | 9.9 | 2024-07-29 | 26.4 | 0 | 8.4 | 2023-07-29 | 18.8 | 0 | 0.8 | 2022-07-29 | 25.1 | 0 | 7.1 | 2021-07-29 | 18.7 | 0 | 0.7 | 2020-07-29 | 21 | 0 | 3 | 2019-07-29 | 28 | 0 | 10 | 2018-07-29 | 25.4 | 0 | 7.4 | 2017-07-29 | 24.4 | 0 | 6.4 | 2016-07-29 | 24.6 | 0 | 6.6 | 0 | 6.03
2025-07-29 | 27.2 | 0 | 9.2 | 2024-07-29 | 25.4 | 0 | 7.4 | 2023-07-29 | 18.1 | 0 | 0.1 | 2022-07-29 | 24.3 | 0 | 6.3 | 2021-07-29 | 18.5 | 0 | 0.5 | 2020-07-29 | 19.2 | 0 | 1.2 | 2019-07-29 | 28.2 | 0 | 10.2 | 2018-07-29 | 18 | 0 | 0 | 2017-07-29 | 23.5 | 0 | 5.5 | 2016-07-29 | 23.9 | 0 | 5.9 | 0 | 4.63
2025-07-29 | 25.6 | 0 | 7.6 | 2024-07-29 | 23.9 | 0 | 5.9 | 2023-07-29 | 17.6 | 0.4 | 0 | 2022-07-29 | 23.1 | 0 | 5.1 | 2021-07-29 | 17.4 | 0.6 | 0 | 2020-07-29 | 17.5 | 0.5 | 0 | 2019-07-29 | 26.7 | 0 | 8.7 | 2018-07-29 | 18.7 | 0 | 0.7 | 2017-07-29 | 21.6 | 0 | 3.6 | 2016-07-29 | 22.3 | 0 | 4.3 | 0.15 | 3.59
2025-07-29 | 24.9 | 0 | 6.9 | 2024-07-29 | 19.6 | 0 | 1.6 | 2023-07-29 | 15.5 | 2.5 | 0 | 2022-07-29 | 21.5 | 0 | 3.5 | 2021-07-29 | 15.9 | 2.1 | 0 | 2020-07-29 | 18.1 | 0 | 0.1 | 2019-07-29 | 25.7 | 0 | 7.7 | 2018-07-29 | 18.2 | 0 | 0.2 | 2017-07-29 | 18.5 | 0 | 0.5 | 2016-07-29 | 20.8 | 0 | 2.8 | 0.46 | 2.33
2025-07-29 | 23.1 | 0 | 5.1 | 2024-07-29 | 21.1 | 0 | 3.1 | 2023-07-29 | 14.4 | 3.6 | 0 | 2022-07-29 | 19.8 | 0 | 1.8 | 2021-07-29 | 16 | 2 | 0 | 2020-07-29 | 18.7 | 0 | 0.7 | 2019-07-29 | 25.6 | 0 | 7.6 | 2018-07-29 | 17.2 | 0.8 | 0 | 2017-07-29 | 18.2 | 0 | 0.2 | 2016-07-29 | 19.4 | 0 | 1.4 | 0.64 | 1.99
2025-07-29 | 22.8 | 0 | 4.8 | 2024-07-29 | 20.2 | 0 | 2.2 | 2023-07-29 | 14.1 | 3.9 | 0 | 2022-07-29 | 18 | 0 | 0 | 2021-07-29 | 16.4 | 1.6 | 0 | 2020-07-29 | 17.2 | 0.8 | 0 | 2019-07-29 | 24.7 | 0 | 6.7 | 2018-07-29 | 17.1 | 0.9 | 0 | 2017-07-29 | 16.7 | 1.3 | 0 | 2016-07-29 | 18.5 | 0 | 0.5 | 0.85 | 1.42
2025-07-29 | 21.6 | 0 | 3.6 | 2024-07-29 | 19.2 | 0 | 1.2 | 2023-07-29 | 12.6 | 5.4 | 0 | 2022-07-29 | 16.9 | 1.1 | 0 | 2021-07-29 | 16.5 | 1.5 | 0 | 2020-07-29 | 17.3 | 0.7 | 0 | 2019-07-29 | 24.2 | 0 | 6.2 | 2018-07-29 | 17.1 | 0.9 | 0 | 2017-07-29 | 15.8 | 2.2 | 0 | 2016-07-29 | 17.6 | 0.4 | 0 | 1.22 | 1.1
2025-07-30 | 20.1 | 0 | 2.1 | 2024-07-30 | 19.2 | 0 | 1.2 | 2023-07-30 | 12.4 | 5.6 | 0 | 2022-07-30 | 16.5 | 1.5 | 0 | 2021-07-30 | 16.1 | 1.9 | 0 | 2020-07-30 | 17.1 | 0.9 | 0 | 2019-07-30 | 23.6 | 0 | 5.6 | 2018-07-30 | 17.4 | 0.6 | 0 | 2017-07-30 | 14.9 | 3.1 | 0 | 2016-07-30 | 16.9 | 1.1 | 0 | 1.47 | 0.89
2025-07-30 | 19.6 | 0 | 1.6 | 2024-07-30 | 17.1 | 0.9 | 0 | 2023-07-30 | 11.3 | 6.7 | 0 | 2022-07-30 | 16.3 | 1.7 | 0 | 2021-07-30 | 15.4 | 2.6 | 0 | 2020-07-30 | 16.9 | 1.1 | 0 | 2019-07-30 | 23.2 | 0 | 5.2 | 2018-07-30 | 17.2 | 0.8 | 0 | 2017-07-30 | 10.9 | 7.1 | 0 | 2016-07-30 | 16 | 2 | 0 | 2.29 | 0.68
2025-07-30 | 19.1 | 0 | 1.1 | 2024-07-30 | 15.6 | 2.4 | 0 | 2023-07-30 | 10.6 | 7.4 | 0 | 2022-07-30 | 15.6 | 2.4 | 0 | 2021-07-30 | 16.6 | 1.4 | 0 | 2020-07-30 | 16.7 | 1.3 | 0 | 2019-07-30 | 22.8 | 0 | 4.8 | 2018-07-30 | 15.9 | 2.1 | 0 | 2017-07-30 | 14.3 | 3.7 | 0 | 2016-07-30 | 14.4 | 3.6 | 0 | 2.43 | 0.59
2025-07-30 | 19 | 0 | 1 | 2024-07-30 | 15.7 | 2.3 | 0 | 2023-07-30 | 10 | 8 | 0 | 2022-07-30 | 15.8 | 2.2 | 0 | 2021-07-30 | 15.9 | 2.1 | 0 | 2020-07-30 | 15.9 | 2.1 | 0 | 2019-07-30 | 22.8 | 0 | 4.8 | 2018-07-30 | 15.6 | 2.4 | 0 | 2017-07-30 | 13.5 | 4.5 | 0 | 2016-07-30 | 15.3 | 2.7 | 0 | 2.63 | 0.58
2025-07-30 | 19.6 | 0 | 1.6 | 2024-07-30 | 15.3 | 2.7 | 0 | 2023-07-30 | 9.2 | 8.8 | 0 | 2022-07-30 | 14.6 | 3.4 | 0 | 2021-07-30 | 15.3 | 2.7 | 0 | 2020-07-30 | 15.5 | 2.5 | 0 | 2019-07-30 | 22 | 0 | 4 | 2018-07-30 | 15.1 | 2.9 | 0 | 2017-07-30 | 12.3 | 5.7 | 0 | 2016-07-30 | 13.9 | 4.1 | 0 | 3.28 | 0.56
2025-07-30 | 20 | 0 | 2 | 2024-07-30 | 16 | 2 | 0 | 2023-07-30 | 9.7 | 8.3 | 0 | 2022-07-30 | 14.8 | 3.2 | 0 | 2021-07-30 | 14.6 | 3.4 | 0 | 2020-07-30 | 15.1 | 2.9 | 0 | 2019-07-30 | 21.6 | 0 | 3.6 | 2018-07-30 | 14.4 | 3.6 | 0 | 2017-07-30 | 12.9 | 5.1 | 0 | 2016-07-30 | 14.5 | 3.5 | 0 | 3.2 | 0.56
2025-07-30 | 19.2 | 0 | 1.2 | 2024-07-30 | 16.8 | 1.2 | 0 | 2023-07-30 | 12.1 | 5.9 | 0 | 2022-07-30 | 16.7 | 1.3 | 0 | 2021-07-30 | 14 | 4 | 0 | 2020-07-30 | 16.2 | 1.8 | 0 | 2019-07-30 | 21.8 | 0 | 3.8 | 2018-07-30 | 15.9 | 2.1 | 0 | 2017-07-30 | 14 | 4 | 0 | 2016-07-30 | 16.2 | 1.8 | 0 | 2.21 | 0.5
2025-07-30 | 21.4 | 0 | 3.4 | 2024-07-30 | 18.5 | 0 | 0.5 | 2023-07-30 | 14.4 | 3.6 | 0 | 2022-07-30 | 18.2 | 0 | 0.2 | 2021-07-30 | 13.5 | 4.5 | 0 | 2020-07-30 | 18.8 | 0 | 0.8 | 2019-07-30 | 22.3 | 0 | 4.3 | 2018-07-30 | 17.7 | 0.3 | 0 | 2017-07-30 | 16.4 | 1.6 | 0 | 2016-07-30 | 18.5 | 0 | 0.5 | 1 | 0.97
2025-07-30 | 23.3 | 0 | 5.3 | 2024-07-30 | 22.1 | 0 | 4.1 | 2023-07-30 | 16.9 | 1.1 | 0 | 2022-07-30 | 19.2 | 0 | 1.2 | 2021-07-30 | 13.7 | 4.3 | 0 | 2020-07-30 | 21.1 | 0 | 3.1 | 2019-07-30 | 24.6 | 0 | 6.6 | 2018-07-30 | 19.7 | 0 | 1.7 | 2017-07-30 | 19 | 0 | 1 | 2016-07-30 | 20.5 | 0 | 2.5 | 0.54 | 2.55
2025-07-30 | 25.3 | 0 | 7.3 | 2024-07-30 | 23.9 | 0 | 5.9 | 2023-07-30 | 18.9 | 0 | 0.9 | 2022-07-30 | 19.1 | 0 | 1.1 | 2021-07-30 | 14.8 | 3.2 | 0 | 2020-07-30 | 22.5 | 0 | 4.5 | 2019-07-30 | 25.2 | 0 | 7.2 | 2018-07-30 | 21.9 | 0 | 3.9 | 2017-07-30 | 21.4 | 0 | 3.4 | 2016-07-30 | 21.8 | 0 | 3.8 | 0.32 | 3.8
2025-07-30 | 26.8 | 0 | 8.8 | 2024-07-30 | 25.5 | 0 | 7.5 | 2023-07-30 | 20.4 | 0 | 2.4 | 2022-07-30 | 19.9 | 0 | 1.9 | 2021-07-30 | 15.5 | 2.5 | 0 | 2020-07-30 | 24.2 | 0 | 6.2 | 2019-07-30 | 23 | 0 | 5 | 2018-07-30 | 23.4 | 0 | 5.4 | 2017-07-30 | 23.1 | 0 | 5.1 | 2016-07-30 | 23.8 | 0 | 5.8 | 0.25 | 4.81
2025-07-30 | 27.1 | 0 | 9.1 | 2024-07-30 | 26.7 | 0 | 8.7 | 2023-07-30 | 21.7 | 0 | 3.7 | 2022-07-30 | 19.8 | 0 | 1.8 | 2021-07-30 | 17.1 | 0.9 | 0 | 2020-07-30 | 26 | 0 | 8 | 2019-07-30 | 23.4 | 0 | 5.4 | 2018-07-30 | 24.7 | 0 | 6.7 | 2017-07-30 | 25.1 | 0 | 7.1 | 2016-07-30 | 24.4 | 0 | 6.4 | 0.09 | 5.69
2025-07-30 | 26.9 | 0 | 8.9 | 2024-07-30 | 28.6 | 0 | 10.6 | 2023-07-30 | 22.7 | 0 | 4.7 | 2022-07-30 | 21 | 0 | 3 | 2021-07-30 | 17.4 | 0.6 | 0 | 2020-07-30 | 26.3 | 0 | 8.3 | 2019-07-30 | 21.5 | 0 | 3.5 | 2018-07-30 | 26.1 | 0 | 8.1 | 2017-07-30 | 26.1 | 0 | 8.1 | 2016-07-30 | 25.4 | 0 | 7.4 | 0.06 | 6.26
2025-07-30 | 27.6 | 0 | 9.6 | 2024-07-30 | 29.2 | 0 | 11.2 | 2023-07-30 | 23.7 | 0 | 5.7 | 2022-07-30 | 21.3 | 0 | 3.3 | 2021-07-30 | 17.7 | 0.3 | 0 | 2020-07-30 | 26.4 | 0 | 8.4 | 2019-07-30 | 23.9 | 0 | 5.9 | 2018-07-30 | 26.4 | 0 | 8.4 | 2017-07-30 | 26.9 | 0 | 8.9 | 2016-07-30 | 25.2 | 0 | 7.2 | 0.03 | 6.86
2025-07-30 | 27.2 | 0 | 9.2 | 2024-07-30 | 28.7 | 0 | 10.7 | 2023-07-30 | 24.2 | 0 | 6.2 | 2022-07-30 | 22.7 | 0 | 4.7 | 2021-07-30 | 17.6 | 0.4 | 0 | 2020-07-30 | 25.9 | 0 | 7.9 | 2019-07-30 | 25.4 | 0 | 7.4 | 2018-07-30 | 27.4 | 0 | 9.4 | 2017-07-30 | 27.4 | 0 | 9.4 | 2016-07-30 | 26.2 | 0 | 8.2 | 0.04 | 7.31
2025-07-30 | 26.8 | 0 | 8.8 | 2024-07-30 | 29.7 | 0 | 11.7 | 2023-07-30 | 24.6 | 0 | 6.6 | 2022-07-30 | 23.1 | 0 | 5.1 | 2021-07-30 | 18.4 | 0 | 0.4 | 2020-07-30 | 21.5 | 0 | 3.5 | 2019-07-30 | 26.2 | 0 | 8.2 | 2018-07-30 | 27.4 | 0 | 9.4 | 2017-07-30 | 28 | 0 | 10 | 2016-07-30 | 26.5 | 0 | 8.5 | 0 | 7.22
2025-07-30 | 26.6 | 0 | 8.6 | 2024-07-30 | 29.6 | 0 | 11.6 | 2023-07-30 | 23.9 | 0 | 5.9 | 2022-07-30 | 24 | 0 | 6 | 2021-07-30 | 19.2 | 0 | 1.2 | 2020-07-30 | 21.1 | 0 | 3.1 | 2019-07-30 | 27.4 | 0 | 9.4 | 2018-07-30 | 27.9 | 0 | 9.9 | 2017-07-30 | 28.4 | 0 | 10.4 | 2016-07-30 | 26.5 | 0 | 8.5 | 0 | 7.46
2025-07-30 | 25.5 | 0 | 7.5 | 2024-07-30 | 29.1 | 0 | 11.1 | 2023-07-30 | 24 | 0 | 6 | 2022-07-30 | 24.1 | 0 | 6.1 | 2021-07-30 | 17.9 | 0.1 | 0 | 2020-07-30 | 21.2 | 0 | 3.2 | 2019-07-30 | 26.6 | 0 | 8.6 | 2018-07-30 | 27.3 | 0 | 9.3 | 2017-07-30 | 28.4 | 0 | 10.4 | 2016-07-30 | 26.3 | 0 | 8.3 | 0.01 | 7.05
2025-07-30 | 24.3 | 0 | 6.3 | 2024-07-30 | 27 | 0 | 9 | 2023-07-30 | 22.3 | 0 | 4.3 | 2022-07-30 | 24 | 0 | 6 | 2021-07-30 | 16.5 | 1.5 | 0 | 2020-07-30 | 23.4 | 0 | 5.4 | 2019-07-30 | 26.5 | 0 | 8.5 | 2018-07-30 | 26.1 | 0 | 8.1 | 2017-07-30 | 27.4 | 0 | 9.4 | 2016-07-30 | 25.6 | 0 | 7.6 | 0.15 | 6.46
2025-07-30 | 23.4 | 0 | 5.4 | 2024-07-30 | 25.3 | 0 | 7.3 | 2023-07-30 | 20.7 | 0 | 2.7 | 2022-07-30 | 23.1 | 0 | 5.1 | 2021-07-30 | 15.6 | 2.4 | 0 | 2020-07-30 | 21.3 | 0 | 3.3 | 2019-07-30 | 24.6 | 0 | 6.6 | 2018-07-30 | 24 | 0 | 6 | 2017-07-30 | 22.7 | 0 | 4.7 | 2016-07-30 | 23.4 | 0 | 5.4 | 0.24 | 4.65
2025-07-30 | 22.6 | 0 | 4.6 | 2024-07-30 | 23.2 | 0 | 5.2 | 2023-07-30 | 19.2 | 0 | 1.2 | 2022-07-30 | 21.5 | 0 | 3.5 | 2021-07-30 | 15.1 | 2.9 | 0 | 2020-07-30 | 19.4 | 0 | 1.4 | 2019-07-30 | 23.3 | 0 | 5.3 | 2018-07-30 | 22 | 0 | 4 | 2017-07-30 | 20.6 | 0 | 2.6 | 2016-07-30 | 20.1 | 0 | 2.1 | 0.29 | 2.99
2025-07-30 | 21.6 | 0 | 3.6 | 2024-07-30 | 22.2 | 0 | 4.2 | 2023-07-30 | 17.9 | 0.1 | 0 | 2022-07-30 | 18.3 | 0 | 0.3 | 2021-07-30 | 14.2 | 3.8 | 0 | 2020-07-30 | 18.2 | 0 | 0.2 | 2019-07-30 | 22.7 | 0 | 4.7 | 2018-07-30 | 20.8 | 0 | 2.8 | 2017-07-30 | 20.3 | 0 | 2.3 | 2016-07-30 | 18.9 | 0 | 0.9 | 0.39 | 1.9
2025-07-30 | 20.1 | 0 | 2.1 | 2024-07-30 | 21.3 | 0 | 3.3 | 2023-07-30 | 17.4 | 0.6 | 0 | 2022-07-30 | 16.3 | 1.7 | 0 | 2021-07-30 | 12.8 | 5.2 | 0 | 2020-07-30 | 18.4 | 0 | 0.4 | 2019-07-30 | 20.4 | 0 | 2.4 | 2018-07-30 | 20.1 | 0 | 2.1 | 2017-07-30 | 19.6 | 0 | 1.6 | 2016-07-30 | 16.9 | 1.1 | 0 | 0.86 | 1.19
2025-07-30 | 18.4 | 0 | 0.4 | 2024-07-30 | 21.2 | 0 | 3.2 | 2023-07-30 | 15.3 | 2.7 | 0 | 2022-07-30 | 18.1 | 0 | 0.1 | 2021-07-30 | 10.2 | 7.8 | 0 | 2020-07-30 | 17.6 | 0.4 | 0 | 2019-07-30 | 19.6 | 0 | 1.6 | 2018-07-30 | 19.3 | 0 | 1.3 | 2017-07-30 | 17.8 | 0.2 | 0 | 2016-07-30 | 18.6 | 0 | 0.6 | 1.11 | 0.72
2025-07-31 | 18.9 | 0 | 0.9 | 2024-07-31 | 21 | 0 | 3 | 2023-07-31 | 12.7 | 5.3 | 0 | 2022-07-31 | 14.7 | 3.3 | 0 | 2021-07-31 | 10.4 | 7.6 | 0 | 2020-07-31 | 16.5 | 1.5 | 0 | 2019-07-31 | 19.1 | 0 | 1.1 | 2018-07-31 | 19 | 0 | 1 | 2017-07-31 | 18.4 | 0 | 0.4 | 2016-07-31 | 16.3 | 1.7 | 0 | 1.94 | 0.64
2025-07-31 | 18.3 | 0 | 0.3 | 2024-07-31 | 20.9 | 0 | 2.9 | 2023-07-31 | 13.9 | 4.1 | 0 | 2022-07-31 | 16.6 | 1.4 | 0 | 2021-07-31 | 8.8 | 9.2 | 0 | 2020-07-31 | 16.5 | 1.5 | 0 | 2019-07-31 | 19.5 | 0 | 1.5 | 2018-07-31 | 17.9 | 0.1 | 0 | 2017-07-31 | 17.6 | 0.4 | 0 | 2016-07-31 | 16 | 2 | 0 | 1.87 | 0.47
2025-07-31 | 17.7 | 0.3 | 0 | 2024-07-31 | 21.2 | 0 | 3.2 | 2023-07-31 | 14.3 | 3.7 | 0 | 2022-07-31 | 15.1 | 2.9 | 0 | 2021-07-31 | 9.3 | 8.7 | 0 | 2020-07-31 | 16.8 | 1.2 | 0 | 2019-07-31 | 18.3 | 0 | 0.3 | 2018-07-31 | 18.2 | 0 | 0.2 | 2017-07-31 | 15.7 | 2.3 | 0 | 2016-07-31 | 14.9 | 3.1 | 0 | 2.22 | 0.37
2025-07-31 | 17.4 | 0.6 | 0 | 2024-07-31 | 21 | 0 | 3 | 2023-07-31 | 14.4 | 3.6 | 0 | 2022-07-31 | 14.4 | 3.6 | 0 | 2021-07-31 | 10.2 | 7.8 | 0 | 2020-07-31 | 15.7 | 2.3 | 0 | 2019-07-31 | 17.9 | 0.1 | 0 | 2018-07-31 | 17.3 | 0.7 | 0 | 2017-07-31 | 14.1 | 3.9 | 0 | 2016-07-31 | 14.6 | 3.4 | 0 | 2.6 | 0.3
2025-07-31 | 17.1 | 0.9 | 0 | 2024-07-31 | 20.8 | 0 | 2.8 | 2023-07-31 | 14.3 | 3.7 | 0 | 2022-07-31 | 14.7 | 3.3 | 0 | 2021-07-31 | 10.8 | 7.2 | 0 | 2020-07-31 | 16.1 | 1.9 | 0 | 2019-07-31 | 17.5 | 0.5 | 0 | 2018-07-31 | 17.6 | 0.4 | 0 | 2017-07-31 | 14.5 | 3.5 | 0 | 2016-07-31 | 13.9 | 4.1 | 0 | 2.55 | 0.28
2025-07-31 | 16.7 | 1.3 | 0 | 2024-07-31 | 21.1 | 0 | 3.1 | 2023-07-31 | 14.2 | 3.8 | 0 | 2022-07-31 | 14.3 | 3.7 | 0 | 2021-07-31 | 10.9 | 7.1 | 0 | 2020-07-31 | 16 | 2 | 0 | 2019-07-31 | 16.9 | 1.1 | 0 | 2018-07-31 | 17.4 | 0.6 | 0 | 2017-07-31 | 14.9 | 3.1 | 0 | 2016-07-31 | 14.2 | 3.8 | 0 | 2.65 | 0.31
2025-07-31 | 16.7 | 1.3 | 0 | 2024-07-31 | 21.6 | 0 | 3.6 | 2023-07-31 | 14.5 | 3.5 | 0 | 2022-07-31 | 15.7 | 2.3 | 0 | 2021-07-31 | 11.9 | 6.1 | 0 | 2020-07-31 | 17.7 | 0.3 | 0 | 2019-07-31 | 18.2 | 0 | 0.2 | 2018-07-31 | 18.3 | 0 | 0.3 | 2017-07-31 | 16.3 | 1.7 | 0 | 2016-07-31 | 16.2 | 1.8 | 0 | 1.7 | 0.41
2025-07-31 | 16.9 | 1.1 | 0 | 2024-07-31 | 22.1 | 0 | 4.1 | 2023-07-31 | 15.3 | 2.7 | 0 | 2022-07-31 | 18.7 | 0 | 0.7 | 2021-07-31 | 14 | 4 | 0 | 2020-07-31 | 20.3 | 0 | 2.3 | 2019-07-31 | 19.6 | 0 | 1.6 | 2018-07-31 | 20.1 | 0 | 2.1 | 2017-07-31 | 19 | 0 | 1 | 2016-07-31 | 18.5 | 0 | 0.5 | 0.78 | 1.23
2025-07-31 | 18.2 | 0 | 0.2 | 2024-07-31 | 22.9 | 0 | 4.9 | 2023-07-31 | 16.5 | 1.5 | 0 | 2022-07-31 | 19.6 | 0 | 1.6 | 2021-07-31 | 15.7 | 2.3 | 0 | 2020-07-31 | 22.2 | 0 | 4.2 | 2019-07-31 | 20.9 | 0 | 2.9 | 2018-07-31 | 21.5 | 0 | 3.5 | 2017-07-31 | 22.1 | 0 | 4.1 | 2016-07-31 | 21.8 | 0 | 3.8 | 0.38 | 2.52
2025-07-31 | 19.9 | 0 | 1.9 | 2024-07-31 | 24.6 | 0 | 6.6 | 2023-07-31 | 17.8 | 0.2 | 0 | 2022-07-31 | 21.7 | 0 | 3.7 | 2021-07-31 | 17.8 | 0.2 | 0 | 2020-07-31 | 23.7 | 0 | 5.7 | 2019-07-31 | 22.5 | 0 | 4.5 | 2018-07-31 | 23.3 | 0 | 5.3 | 2017-07-31 | 22.8 | 0 | 4.8 | 2016-07-31 | 24.5 | 0 | 6.5 | 0.04 | 3.9
2025-07-31 | 21.1 | 0 | 3.1 | 2024-07-31 | 25.1 | 0 | 7.1 | 2023-07-31 | 19.3 | 0 | 1.3 | 2022-07-31 | 22.9 | 0 | 4.9 | 2021-07-31 | 18.9 | 0 | 0.9 | 2020-07-31 | 25.3 | 0 | 7.3 | 2019-07-31 | 23.6 | 0 | 5.6 | 2018-07-31 | 24.9 | 0 | 6.9 | 2017-07-31 | 24 | 0 | 6 | 2016-07-31 | 26.1 | 0 | 8.1 | 0 | 5.12
2025-07-31 | 20.8 | 0 | 2.8 | 2024-07-31 | 25.9 | 0 | 7.9 | 2023-07-31 | 20 | 0 | 2 | 2022-07-31 | 23.9 | 0 | 5.9 | 2021-07-31 | 20.9 | 0 | 2.9 | 2020-07-31 | 25.8 | 0 | 7.8 | 2019-07-31 | 25.3 | 0 | 7.3 | 2018-07-31 | 25.8 | 0 | 7.8 | 2017-07-31 | 25.8 | 0 | 7.8 | 2016-07-31 | 26.8 | 0 | 8.8 | 0 | 6.1
2025-07-31 | 22.8 | 0 | 4.8 | 2024-07-31 | 25.9 | 0 | 7.9 | 2023-07-31 | 19.5 | 0 | 1.5 | 2022-07-31 | 24.6 | 0 | 6.6 | 2021-07-31 | 21.7 | 0 | 3.7 | 2020-07-31 | 26.2 | 0 | 8.2 | 2019-07-31 | 26.3 | 0 | 8.3 | 2018-07-31 | 26.4 | 0 | 8.4 | 2017-07-31 | 26.7 | 0 | 8.7 | 2016-07-31 | 28 | 0 | 10 | 0 | 6.81
2025-07-31 | 21.4 | 0 | 3.4 | 2024-07-31 | 26.1 | 0 | 8.1 | 2023-07-31 | 20 | 0 | 2 | 2022-07-31 | 25.4 | 0 | 7.4 | 2021-07-31 | 22.5 | 0 | 4.5 | 2020-07-31 | 27.6 | 0 | 9.6 | 2019-07-31 | 27.4 | 0 | 9.4 | 2018-07-31 | 27.1 | 0 | 9.1 | 2017-07-31 | 27.1 | 0 | 9.1 | 2016-07-31 | 29.3 | 0 | 11.3 | 0 | 7.39
2025-07-31 | 21.5 | 0 | 3.5 | 2024-07-31 | 27.3 | 0 | 9.3 | 2023-07-31 | 21 | 0 | 3 | 2022-07-31 | 26.9 | 0 | 8.9 | 2021-07-31 | 22.6 | 0 | 4.6 | 2020-07-31 | 28.7 | 0 | 10.7 | 2019-07-31 | 26.5 | 0 | 8.5 | 2018-07-31 | 27.9 | 0 | 9.9 | 2017-07-31 | 26.5 | 0 | 8.5 | 2016-07-31 | 29.4 | 0 | 11.4 | 0 | 7.83
2025-07-31 | 23.1 | 0 | 5.1 | 2024-07-31 | 27.6 | 0 | 9.6 | 2023-07-31 | 19.2 | 0 | 1.2 | 2022-07-31 | 27.2 | 0 | 9.2 | 2021-07-31 | 21.3 | 0 | 3.3 | 2020-07-31 | 28.6 | 0 | 10.6 | 2019-07-31 | 27.8 | 0 | 9.8 | 2018-07-31 | 27.9 | 0 | 9.9 | 2017-07-31 | 26.5 | 0 | 8.5 | 2016-07-31 | 29.2 | 0 | 11.2 | 0 | 7.84
2025-07-31 | 22.1 | 0 | 4.1 | 2024-07-31 | 27.9 | 0 | 9.9 | 2023-07-31 | 19.8 | 0 | 1.8 | 2022-07-31 | 26.4 | 0 | 8.4 | 2021-07-31 | 22.4 | 0 | 4.4 | 2020-07-31 | 28.1 | 0 | 10.1 | 2019-07-31 | 27 | 0 | 9 | 2018-07-31 | 27.6 | 0 | 9.6 | 2017-07-31 | 27.1 | 0 | 9.1 | 2016-07-31 | 28.6 | 0 | 10.6 | 0 | 7.7
2025-07-31 | 22.2 | 0 | 4.2 | 2024-07-31 | 27.1 | 0 | 9.1 | 2023-07-31 | 20.5 | 0 | 2.5 | 2022-07-31 | 25.4 | 0 | 7.4 | 2021-07-31 | 20.6 | 0 | 2.6 | 2020-07-31 | 28.5 | 0 | 10.5 | 2019-07-31 | 26.7 | 0 | 8.7 | 2018-07-31 | 27.3 | 0 | 9.3 | 2017-07-31 | 26.6 | 0 | 8.6 | 2016-07-31 | 26.9 | 0 | 8.9 | 0 | 7.18
2025-07-31 | 21.3 | 0 | 3.3 | 2024-07-31 | 27.5 | 0 | 9.5 | 2023-07-31 | 19.6 | 0 | 1.6 | 2022-07-31 | 25.1 | 0 | 7.1 | 2021-07-31 | 19.5 | 0 | 1.5 | 2020-07-31 | 27.7 | 0 | 9.7 | 2019-07-31 | 25.7 | 0 | 7.7 | 2018-07-31 | 26.1 | 0 | 8.1 | 2017-07-31 | 26.4 | 0 | 8.4 | 2016-07-31 | 26.8 | 0 | 8.8 | 0 | 6.57
2025-07-31 | 20.9 | 0 | 2.9 | 2024-07-31 | 25.8 | 0 | 7.8 | 2023-07-31 | 17.6 | 0.4 | 0 | 2022-07-31 | 23.8 | 0 | 5.8 | 2021-07-31 | 18.5 | 0 | 0.5 | 2020-07-31 | 26 | 0 | 8 | 2019-07-31 | 24.1 | 0 | 6.1 | 2018-07-31 | 23.9 | 0 | 5.9 | 2017-07-31 | 24.4 | 0 | 6.4 | 2016-07-31 | 24.7 | 0 | 6.7 | 0.04 | 5.01
2025-07-31 | 18.8 | 0 | 0.8 | 2024-07-31 | 24 | 0 | 6 | 2023-07-31 | 15.6 | 2.4 | 0 | 2022-07-31 | 22.3 | 0 | 4.3 | 2021-07-31 | 17 | 1 | 0 | 2020-07-31 | 23.7 | 0 | 5.7 | 2019-07-31 | 21.4 | 0 | 3.4 | 2018-07-31 | 22.2 | 0 | 4.2 | 2017-07-31 | 22.6 | 0 | 4.6 | 2016-07-31 | 22.8 | 0 | 4.8 | 0.34 | 3.38
2025-07-31 | 17.8 | 0.2 | 0 | 2024-07-31 | 23.3 | 0 | 5.3 | 2023-07-31 | 14.7 | 3.3 | 0 | 2022-07-31 | 20.9 | 0 | 2.9 | 2021-07-31 | 15.6 | 2.4 | 0 | 2020-07-31 | 23 | 0 | 5 | 2019-07-31 | 21.7 | 0 | 3.7 | 2018-07-31 | 21.6 | 0 | 3.6 | 2017-07-31 | 20.3 | 0 | 2.3 | 2016-07-31 | 21.2 | 0 | 3.2 | 0.59 | 2.6
2025-07-31 | 17.3 | 0.7 | 0 | 2024-07-31 | 23.2 | 0 | 5.2 | 2023-07-31 | 14.1 | 3.9 | 0 | 2022-07-31 | 20.1 | 0 | 2.1 | 2021-07-31 | 15.2 | 2.8 | 0 | 2020-07-31 | 22.1 | 0 | 4.1 | 2019-07-31 | 20.6 | 0 | 2.6 | 2018-07-31 | 21.9 | 0 | 3.9 | 2017-07-31 | 19.6 | 0 | 1.6 | 2016-07-31 | 21 | 0 | 3 | 0.74 | 2.25
2025-07-31 | 15.7 | 2.3 | 0 | 2024-07-31 | 22.1 | 0 | 4.1 | 2023-07-31 | 13.6 | 4.4 | 0 | 2022-07-31 | 19.4 | 0 | 1.4 | 2021-07-31 | 14.8 | 3.2 | 0 | 2020-07-31 | 18.5 | 0 | 0.5 | 2019-07-31 | 19.2 | 0 | 1.2 | 2018-07-31 | 21.7 | 0 | 3.7 | 2017-07-31 | 20 | 0 | 2 | 2016-07-31 | 19.4 | 0 | 1.4 | 0.99 | 1.43
2025-08-01 | 15.2 | 2.8 | 0 | 2024-08-01 | 21.3 | 0 | 3.3 | 2023-08-01 | 13.1 | 4.9 | 0 | 2022-08-01 | 18.5 | 0 | 0.5 | 2021-08-01 | 15 | 3 | 0 | 2020-08-01 | 20.7 | 0 | 2.7 | 2019-08-01 | 15.4 | 2.6 | 0 | 2018-08-01 | 21.6 | 0 | 3.6 | 2017-08-01 | 19.4 | 0 | 1.4 | 2016-08-01 | 18.2 | 0 | 0.2 | 1.33 | 1.17
2025-08-01 | 14.4 | 3.6 | 0 | 2024-08-01 | 21.6 | 0 | 3.6 | 2023-08-01 | 11.2 | 6.8 | 0 | 2022-08-01 | 17.9 | 0.1 | 0 | 2021-08-01 | 13.9 | 4.1 | 0 | 2020-08-01 | 20.4 | 0 | 2.4 | 2019-08-01 | 14.4 | 3.6 | 0 | 2018-08-01 | 21.6 | 0 | 3.6 | 2017-08-01 | 18.6 | 0 | 0.6 | 2016-08-01 | 19.6 | 0 | 1.6 | 1.82 | 1.18
2025-08-01 | 13.3 | 4.7 | 0 | 2024-08-01 | 20.4 | 0 | 2.4 | 2023-08-01 | 10.1 | 7.9 | 0 | 2022-08-01 | 17.7 | 0.3 | 0 | 2021-08-01 | 12.2 | 5.8 | 0 | 2020-08-01 | 17.6 | 0.4 | 0 | 2019-08-01 | 13.9 | 4.1 | 0 | 2018-08-01 | 21.8 | 0 | 3.8 | 2017-08-01 | 18.2 | 0 | 0.2 | 2016-08-01 | 17.9 | 0.1 | 0 | 2.33 | 0.64
2025-08-01 | 12.5 | 5.5 | 0 | 2024-08-01 | 21.1 | 0 | 3.1 | 2023-08-01 | 10.4 | 7.6 | 0 | 2022-08-01 | 17.2 | 0.8 | 0 | 2021-08-01 | 12.7 | 5.3 | 0 | 2020-08-01 | 16.3 | 1.7 | 0 | 2019-08-01 | 14.7 | 3.3 | 0 | 2018-08-01 | 21.2 | 0 | 3.2 | 2017-08-01 | 17.6 | 0.4 | 0 | 2016-08-01 | 18.5 | 0 | 0.5 | 2.46 | 0.68
2025-08-01 | 11.3 | 6.7 | 0 | 2024-08-01 | 20.8 | 0 | 2.8 | 2023-08-01 | 10.3 | 7.7 | 0 | 2022-08-01 | 17 | 1 | 0 | 2021-08-01 | 12.8 | 5.2 | 0 | 2020-08-01 | 16.2 | 1.8 | 0 | 2019-08-01 | 13.9 | 4.1 | 0 | 2018-08-01 | 21.1 | 0 | 3.1 | 2017-08-01 | 15.5 | 2.5 | 0 | 2016-08-01 | 18.4 | 0 | 0.4 | 2.9 | 0.63
2025-08-01 | 11.7 | 6.3 | 0 | 2024-08-01 | 20.4 | 0 | 2.4 | 2023-08-01 | 10 | 8 | 0 | 2022-08-01 | 17.1 | 0.9 | 0 | 2021-08-01 | 13 | 5 | 0 | 2020-08-01 | 16.8 | 1.2 | 0 | 2019-08-01 | 12.5 | 5.5 | 0 | 2018-08-01 | 21 | 0 | 3 | 2017-08-01 | 15.8 | 2.2 | 0 | 2016-08-01 | 18.9 | 0 | 0.9 | 2.91 | 0.63
2025-08-01 | 13.2 | 4.8 | 0 | 2024-08-01 | 21.2 | 0 | 3.2 | 2023-08-01 | 11.6 | 6.4 | 0 | 2022-08-01 | 18.3 | 0 | 0.3 | 2021-08-01 | 13.5 | 4.5 | 0 | 2020-08-01 | 18 | 0 | 0 | 2019-08-01 | 15.3 | 2.7 | 0 | 2018-08-01 | 21.2 | 0 | 3.2 | 2017-08-01 | 15.5 | 2.5 | 0 | 2016-08-01 | 19.1 | 0 | 1.1 | 2.09 | 0.78
2025-08-01 | 15 | 3 | 0 | 2024-08-01 | 22.6 | 0 | 4.6 | 2023-08-01 | 13.8 | 4.2 | 0 | 2022-08-01 | 19.7 | 0 | 1.7 | 2021-08-01 | 13.9 | 4.1 | 0 | 2020-08-01 | 20.9 | 0 | 2.9 | 2019-08-01 | 18.6 | 0 | 0.6 | 2018-08-01 | 21.8 | 0 | 3.8 | 2017-08-01 | 19.7 | 0 | 1.7 | 2016-08-01 | 20 | 0 | 2 | 1.13 | 1.73
2025-08-01 | 17.1 | 0.9 | 0 | 2024-08-01 | 24.6 | 0 | 6.6 | 2023-08-01 | 16 | 2 | 0 | 2022-08-01 | 22.1 | 0 | 4.1 | 2021-08-01 | 14.3 | 3.7 | 0 | 2020-08-01 | 23.9 | 0 | 5.9 | 2019-08-01 | 21.2 | 0 | 3.2 | 2018-08-01 | 22.1 | 0 | 4.1 | 2017-08-01 | 21.8 | 0 | 3.8 | 2016-08-01 | 21.8 | 0 | 3.8 | 0.66 | 3.15
2025-08-01 | 18.2 | 0 | 0.2 | 2024-08-01 | 26.5 | 0 | 8.5 | 2023-08-01 | 17.8 | 0.2 | 0 | 2022-08-01 | 24.1 | 0 | 6.1 | 2021-08-01 | 14.2 | 3.8 | 0 | 2020-08-01 | 25.5 | 0 | 7.5 | 2019-08-01 | 22.6 | 0 | 4.6 | 2018-08-01 | 24 | 0 | 6 | 2017-08-01 | 23.4 | 0 | 5.4 | 2016-08-01 | 25.7 | 0 | 7.7 | 0.4 | 4.6
2025-08-01 | 19.3 | 0 | 1.3 | 2024-08-01 | 27.6 | 0 | 9.6 | 2023-08-01 | 19.6 | 0 | 1.6 | 2022-08-01 | 26.5 | 0 | 8.5 | 2021-08-01 | 14.2 | 3.8 | 0 | 2020-08-01 | 26.4 | 0 | 8.4 | 2019-08-01 | 24 | 0 | 6 | 2018-08-01 | 24.6 | 0 | 6.6 | 2017-08-01 | 25.4 | 0 | 7.4 | 2016-08-01 | 26.8 | 0 | 8.8 | 0.38 | 5.82
2025-08-01 | 20.2 | 0 | 2.2 | 2024-08-01 | 29.5 | 0 | 11.5 | 2023-08-01 | 19.2 | 0 | 1.2 | 2022-08-01 | 27.9 | 0 | 9.9 | 2021-08-01 | 14.9 | 3.1 | 0 | 2020-08-01 | 28 | 0 | 10 | 2019-08-01 | 25.2 | 0 | 7.2 | 2018-08-01 | 25.4 | 0 | 7.4 | 2017-08-01 | 25.9 | 0 | 7.9 | 2016-08-01 | 28.4 | 0 | 10.4 | 0.31 | 6.77
2025-08-01 | 21.1 | 0 | 3.1 | 2024-08-01 | 30.1 | 0 | 12.1 | 2023-08-01 | 19.1 | 0 | 1.1 | 2022-08-01 | 28.2 | 0 | 10.2 | 2021-08-01 | 15.2 | 2.8 | 0 | 2020-08-01 | 28.3 | 0 | 10.3 | 2019-08-01 | 26.8 | 0 | 8.8 | 2018-08-01 | 25.4 | 0 | 7.4 | 2017-08-01 | 26.9 | 0 | 8.9 | 2016-08-01 | 29.1 | 0 | 11.1 | 0.28 | 7.3
2025-08-01 | 21.3 | 0 | 3.3 | 2024-08-01 | 30.5 | 0 | 12.5 | 2023-08-01 | 20.4 | 0 | 2.4 | 2022-08-01 | 28.5 | 0 | 10.5 | 2021-08-01 | 15.7 | 2.3 | 0 | 2020-08-01 | 29.4 | 0 | 11.4 | 2019-08-01 | 26.6 | 0 | 8.6 | 2018-08-01 | 26 | 0 | 8 | 2017-08-01 | 27.8 | 0 | 9.8 | 2016-08-01 | 29.1 | 0 | 11.1 | 0.23 | 7.76
2025-08-01 | 22 | 0 | 4 | 2024-08-01 | 29.7 | 0 | 11.7 | 2023-08-01 | 21.4 | 0 | 3.4 | 2022-08-01 | 28.4 | 0 | 10.4 | 2021-08-01 | 16.2 | 1.8 | 0 | 2020-08-01 | 29.8 | 0 | 11.8 | 2019-08-01 | 27.1 | 0 | 9.1 | 2018-08-01 | 26.6 | 0 | 8.6 | 2017-08-01 | 28 | 0 | 10 | 2016-08-01 | 29.2 | 0 | 11.2 | 0.18 | 8.02
2025-08-01 | 22.9 | 0 | 4.9 | 2024-08-01 | 31.5 | 0 | 13.5 | 2023-08-01 | 21.8 | 0 | 3.8 | 2022-08-01 | 27 | 0 | 9 | 2021-08-01 | 17.4 | 0.6 | 0 | 2020-08-01 | 30.1 | 0 | 12.1 | 2019-08-01 | 27.2 | 0 | 9.2 | 2018-08-01 | 26.4 | 0 | 8.4 | 2017-08-01 | 28.5 | 0 | 10.5 | 2016-08-01 | 30.1 | 0 | 12.1 | 0.06 | 8.35
2025-08-01 | 22.1 | 0 | 4.1 | 2024-08-01 | 31.5 | 0 | 13.5 | 2023-08-01 | 22.1 | 0 | 4.1 | 2022-08-01 | 27.5 | 0 | 9.5 | 2021-08-01 | 17.7 | 0.3 | 0 | 2020-08-01 | 28.8 | 0 | 10.8 | 2019-08-01 | 27.1 | 0 | 9.1 | 2018-08-01 | 25.5 | 0 | 7.5 | 2017-08-01 | 28.5 | 0 | 10.5 | 2016-08-01 | 28.2 | 0 | 10.2 | 0.03 | 7.93
2025-08-01 | 22.9 | 0 | 4.9 | 2024-08-01 | 30.4 | 0 | 12.4 | 2023-08-01 | 21.1 | 0 | 3.1 | 2022-08-01 | 27 | 0 | 9 | 2021-08-01 | 17.4 | 0.6 | 0 | 2020-08-01 | 29.4 | 0 | 11.4 | 2019-08-01 | 26.8 | 0 | 8.8 | 2018-08-01 | 24.8 | 0 | 6.8 | 2017-08-01 | 27.9 | 0 | 9.9 | 2016-08-01 | 28.2 | 0 | 10.2 | 0.06 | 7.65
2025-08-01 | 22.4 | 0 | 4.4 | 2024-08-01 | 29.8 | 0 | 11.8 | 2023-08-01 | 20.6 | 0 | 2.6 | 2022-08-01 | 25.5 | 0 | 7.5 | 2021-08-01 | 17.3 | 0.7 | 0 | 2020-08-01 | 27.3 | 0 | 9.3 | 2019-08-01 | 24.9 | 0 | 6.9 | 2018-08-01 | 24.7 | 0 | 6.7 | 2017-08-01 | 26.9 | 0 | 8.9 | 2016-08-01 | 27.1 | 0 | 9.1 | 0.07 | 6.72
2025-08-01 | 20.6 | 0 | 2.6 | 2024-08-01 | 27.2 | 0 | 9.2 | 2023-08-01 | 18.9 | 0 | 0.9 | 2022-08-01 | 24.6 | 0 | 6.6 | 2021-08-01 | 16.5 | 1.5 | 0 | 2020-08-01 | 24.7 | 0 | 6.7 | 2019-08-01 | 22.8 | 0 | 4.8 | 2018-08-01 | 23.8 | 0 | 5.8 | 2017-08-01 | 24.8 | 0 | 6.8 | 2016-08-01 | 25.4 | 0 | 7.4 | 0.15 | 5.08
2025-08-01 | 19.7 | 0 | 1.7 | 2024-08-01 | 27.1 | 0 | 9.1 | 2023-08-01 | 17.3 | 0.7 | 0 | 2022-08-01 | 24.1 | 0 | 6.1 | 2021-08-01 | 15.8 | 2.2 | 0 | 2020-08-01 | 22.1 | 0 | 4.1 | 2019-08-01 | 19.8 | 0 | 1.8 | 2018-08-01 | 23.8 | 0 | 5.8 | 2017-08-01 | 23.6 | 0 | 5.6 | 2016-08-01 | 22.5 | 0 | 4.5 | 0.29 | 3.87
2025-08-01 | 15.7 | 2.3 | 0 | 2024-08-01 | 23.8 | 0 | 5.8 | 2023-08-01 | 15.2 | 2.8 | 0 | 2022-08-01 | 23.8 | 0 | 5.8 | 2021-08-01 | 14.9 | 3.1 | 0 | 2020-08-01 | 22.7 | 0 | 4.7 | 2019-08-01 | 18.9 | 0 | 0.9 | 2018-08-01 | 23.4 | 0 | 5.4 | 2017-08-01 | 21.6 | 0 | 3.6 | 2016-08-01 | 21.1 | 0 | 3.1 | 0.82 | 2.93
2025-08-01 | 12.6 | 5.4 | 0 | 2024-08-01 | 23.7 | 0 | 5.7 | 2023-08-01 | 15.5 | 2.5 | 0 | 2022-08-01 | 23.6 | 0 | 5.6 | 2021-08-01 | 15.8 | 2.2 | 0 | 2020-08-01 | 21.4 | 0 | 3.4 | 2019-08-01 | 15.2 | 2.8 | 0 | 2018-08-01 | 23.3 | 0 | 5.3 | 2017-08-01 | 21.4 | 0 | 3.4 | 2016-08-01 | 19.4 | 0 | 1.4 | 1.29 | 2.48
2025-08-01 | 12.4 | 5.6 | 0 | 2024-08-01 | 23.4 | 0 | 5.4 | 2023-08-01 | 13.7 | 4.3 | 0 | 2022-08-01 | 22.7 | 0 | 4.7 | 2021-08-01 | 15.7 | 2.3 | 0 | 2020-08-01 | 21.1 | 0 | 3.1 | 2019-08-01 | 15.7 | 2.3 | 0 | 2018-08-01 | 22.8 | 0 | 4.8 | 2017-08-01 | 20.7 | 0 | 2.7 | 2016-08-01 | 18.9 | 0 | 0.9 | 1.45 | 2.16
2025-08-02 | 12.2 | 5.8 | 0 | 2024-08-02 | 22.8 | 0 | 4.8 | 2023-08-02 | 11.2 | 6.8 | 0 | 2022-08-02 | 22.6 | 0 | 4.6 | 2021-08-02 | 14.4 | 3.6 | 0 | 2020-08-02 | 21.3 | 0 | 3.3 | 2019-08-02 | 16.8 | 1.2 | 0 | 2018-08-02 | 22.4 | 0 | 4.4 | 2017-08-02 | 19.8 | 0 | 1.8 | 2016-08-02 | 17.7 | 0.3 | 0 | 1.77 | 1.89
2025-08-02 | 10.4 | 7.6 | 0 | 2024-08-02 | 21.8 | 0 | 3.8 | 2023-08-02 | 11.9 | 6.1 | 0 | 2022-08-02 | 22.4 | 0 | 4.4 | 2021-08-02 | 14.6 | 3.4 | 0 | 2020-08-02 | 20.2 | 0 | 2.2 | 2019-08-02 | 16.4 | 1.6 | 0 | 2018-08-02 | 22.2 | 0 | 4.2 | 2017-08-02 | 19.9 | 0 | 1.9 | 2016-08-02 | 17 | 1 | 0 | 1.97 | 1.65
2025-08-02 | 11 | 7 | 0 | 2024-08-02 | 20.3 | 0 | 2.3 | 2023-08-02 | 10 | 8 | 0 | 2022-08-02 | 21.8 | 0 | 3.8 | 2021-08-02 | 14.7 | 3.3 | 0 | 2020-08-02 | 20.3 | 0 | 2.3 | 2019-08-02 | 15.3 | 2.7 | 0 | 2018-08-02 | 21.8 | 0 | 3.8 | 2017-08-02 | 19.2 | 0 | 1.2 | 2016-08-02 | 17 | 1 | 0 | 2.2 | 1.34
2025-08-02 | 11 | 7 | 0 | 2024-08-02 | 20.2 | 0 | 2.2 | 2023-08-02 | 10.2 | 7.8 | 0 | 2022-08-02 | 21.7 | 0 | 3.7 | 2021-08-02 | 15.1 | 2.9 | 0 | 2020-08-02 | 19.3 | 0 | 1.3 | 2019-08-02 | 11.9 | 6.1 | 0 | 2018-08-02 | 21.3 | 0 | 3.3 | 2017-08-02 | 19 | 0 | 1 | 2016-08-02 | 16.4 | 1.6 | 0 | 2.54 | 1.15
2025-08-02 | 10.6 | 7.4 | 0 | 2024-08-02 | 20.2 | 0 | 2.2 | 2023-08-02 | 8.6 | 9.4 | 0 | 2022-08-02 | 21.2 | 0 | 3.2 | 2021-08-02 | 13.8 | 4.2 | 0 | 2020-08-02 | 19.4 | 0 | 1.4 | 2019-08-02 | 12.4 | 5.6 | 0 | 2018-08-02 | 20.9 | 0 | 2.9 | 2017-08-02 | 18.1 | 0 | 0.1 | 2016-08-02 | 16.1 | 1.9 | 0 | 2.85 | 0.98
2025-08-02 | 10.2 | 7.8 | 0 | 2024-08-02 | 19.7 | 0 | 1.7 | 2023-08-02 | 9.5 | 8.5 | 0 | 2022-08-02 | 20.6 | 0 | 2.6 | 2021-08-02 | 13.2 | 4.8 | 0 | 2020-08-02 | 19 | 0 | 1 | 2019-08-02 | 10.7 | 7.3 | 0 | 2018-08-02 | 20 | 0 | 2 | 2017-08-02 | 17.9 | 0.1 | 0 | 2016-08-02 | 15.8 | 2.2 | 0 | 3.07 | 0.73
2025-08-02 | 12.1 | 5.9 | 0 | 2024-08-02 | 21.3 | 0 | 3.3 | 2023-08-02 | 13 | 5 | 0 | 2022-08-02 | 20.9 | 0 | 2.9 | 2021-08-02 | 14 | 4 | 0 | 2020-08-02 | 19.9 | 0 | 1.9 | 2019-08-02 | 13.6 | 4.4 | 0 | 2018-08-02 | 20.3 | 0 | 2.3 | 2017-08-02 | 18.8 | 0 | 0.8 | 2016-08-02 | 18.3 | 0 | 0.3 | 1.93 | 1.15
2025-08-02 | 15.4 | 2.6 | 0 | 2024-08-02 | 23.1 | 0 | 5.1 | 2023-08-02 | 15 | 3 | 0 | 2022-08-02 | 22 | 0 | 4 | 2021-08-02 | 15.1 | 2.9 | 0 | 2020-08-02 | 20.5 | 0 | 2.5 | 2019-08-02 | 16.3 | 1.7 | 0 | 2018-08-02 | 21.4 | 0 | 3.4 | 2017-08-02 | 20.4 | 0 | 2.4 | 2016-08-02 | 20.7 | 0 | 2.7 | 1.02 | 2.01
2025-08-02 | 17.5 | 0.5 | 0 | 2024-08-02 | 24.3 | 0 | 6.3 | 2023-08-02 | 17.1 | 0.9 | 0 | 2022-08-02 | 23.7 | 0 | 5.7 | 2021-08-02 | 16.4 | 1.6 | 0 | 2020-08-02 | 20.3 | 0 | 2.3 | 2019-08-02 | 19.6 | 0 | 1.6 | 2018-08-02 | 22.4 | 0 | 4.4 | 2017-08-02 | 22.8 | 0 | 4.8 | 2016-08-02 | 22.6 | 0 | 4.6 | 0.3 | 2.97
2025-08-02 | 20.6 | 0 | 2.6 | 2024-08-02 | 25.6 | 0 | 7.6 | 2023-08-02 | 20.4 | 0 | 2.4 | 2022-08-02 | 25.1 | 0 | 7.1 | 2021-08-02 | 18.1 | 0 | 0.1 | 2020-08-02 | 19.7 | 0 | 1.7 | 2019-08-02 | 22.9 | 0 | 4.9 | 2018-08-02 | 23.6 | 0 | 5.6 | 2017-08-02 | 24.4 | 0 | 6.4 | 2016-08-02 | 23.6 | 0 | 5.6 | 0 | 4.4
2025-08-02 | 22.7 | 0 | 4.7 | 2024-08-02 | 26.9 | 0 | 8.9 | 2023-08-02 | 21.7 | 0 | 3.7 | 2022-08-02 | 20.4 | 0 | 2.4 | 2021-08-02 | 19.2 | 0 | 1.2 | 2020-08-02 | 19.6 | 0 | 1.6 | 2019-08-02 | 25.4 | 0 | 7.4 | 2018-08-02 | 25.5 | 0 | 7.5 | 2017-08-02 | 26.3 | 0 | 8.3 | 2016-08-02 | 26.1 | 0 | 8.1 | 0 | 5.38
2025-08-02 | 25.1 | 0 | 7.1 | 2024-08-02 | 28 | 0 | 10 | 2023-08-02 | 23.2 | 0 | 5.2 | 2022-08-02 | 20.9 | 0 | 2.9 | 2021-08-02 | 20.2 | 0 | 2.2 | 2020-08-02 | 19.3 | 0 | 1.3 | 2019-08-02 | 26.9 | 0 | 8.9 | 2018-08-02 | 26.5 | 0 | 8.5 | 2017-08-02 | 27.7 | 0 | 9.7 | 2016-08-02 | 27.4 | 0 | 9.4 | 0 | 6.52
2025-08-02 | 26.2 | 0 | 8.2 | 2024-08-02 | 30.3 | 0 | 12.3 | 2023-08-02 | 22.5 | 0 | 4.5 | 2022-08-02 | 21.9 | 0 | 3.9 | 2021-08-02 | 21.4 | 0 | 3.4 | 2020-08-02 | 19.2 | 0 | 1.2 | 2019-08-02 | 28.3 | 0 | 10.3 | 2018-08-02 | 26.8 | 0 | 8.8 | 2017-08-02 | 29 | 0 | 11 | 2016-08-02 | 28 | 0 | 10 | 0 | 7.36
2025-08-02 | 26.9 | 0 | 8.9 | 2024-08-02 | 30.1 | 0 | 12.1 | 2023-08-02 | 24.7 | 0 | 6.7 | 2022-08-02 | 22.6 | 0 | 4.6 | 2021-08-02 | 21.9 | 0 | 3.9 | 2020-08-02 | 19.3 | 0 | 1.3 | 2019-08-02 | 28.7 | 0 | 10.7 | 2018-08-02 | 27.3 | 0 | 9.3 | 2017-08-02 | 28.9 | 0 | 10.9 | 2016-08-02 | 28.8 | 0 | 10.8 | 0 | 7.92
2025-08-02 | 27.3 | 0 | 9.3 | 2024-08-02 | 30.7 | 0 | 12.7 | 2023-08-02 | 24.5 | 0 | 6.5 | 2022-08-02 | 24.5 | 0 | 6.5 | 2021-08-02 | 22.4 | 0 | 4.4 | 2020-08-02 | 21.6 | 0 | 3.6 | 2019-08-02 | 28.3 | 0 | 10.3 | 2018-08-02 | 27.4 | 0 | 9.4 | 2017-08-02 | 29.5 | 0 | 11.5 | 2016-08-02 | 29.2 | 0 | 11.2 | 0 | 8.54
2025-08-02 | 27 | 0 | 9 | 2024-08-02 | 30.1 | 0 | 12.1 | 2023-08-02 | 24.7 | 0 | 6.7 | 2022-08-02 | 24.2 | 0 | 6.2 | 2021-08-02 | 23.1 | 0 | 5.1 | 2020-08-02 | 22 | 0 | 4 | 2019-08-02 | 29.1 | 0 | 11.1 | 2018-08-02 | 27.9 | 0 | 9.9 | 2017-08-02 | 29.3 | 0 | 11.3 | 2016-08-02 | 29.8 | 0 | 11.8 | 0 | 8.72
2025-08-02 | 27.8 | 0 | 9.8 | 2024-08-02 | 29.9 | 0 | 11.9 | 2023-08-02 | 25 | 0 | 7 | 2022-08-02 | 23.6 | 0 | 5.6 | 2021-08-02 | 22.7 | 0 | 4.7 | 2020-08-02 | 21.2 | 0 | 3.2 | 2019-08-02 | 29.3 | 0 | 11.3 | 2018-08-02 | 28.2 | 0 | 10.2 | 2017-08-02 | 29.6 | 0 | 11.6 | 2016-08-02 | 29.8 | 0 | 11.8 | 0 | 8.71
2025-08-02 | 27.1 | 0 | 9.1 | 2024-08-02 | 29.9 | 0 | 11.9 | 2023-08-02 | 23.9 | 0 | 5.9 | 2022-08-02 | 23.1 | 0 | 5.1 | 2021-08-02 | 22.7 | 0 | 4.7 | 2020-08-02 | 22.2 | 0 | 4.2 | 2019-08-02 | 28.9 | 0 | 10.9 | 2018-08-02 | 27.8 | 0 | 9.8 | 2017-08-02 | 26.8 | 0 | 8.8 | 2016-08-02 | 29.3 | 0 | 11.3 | 0 | 8.17
2025-08-02 | 26 | 0 | 8 | 2024-08-02 | 27.8 | 0 | 9.8 | 2023-08-02 | 22.7 | 0 | 4.7 | 2022-08-02 | 22.6 | 0 | 4.6 | 2021-08-02 | 21.9 | 0 | 3.9 | 2020-08-02 | 23.1 | 0 | 5.1 | 2019-08-02 | 27.4 | 0 | 9.4 | 2018-08-02 | 27 | 0 | 9 | 2017-08-02 | 22.2 | 0 | 4.2 | 2016-08-02 | 28.1 | 0 | 10.1 | 0 | 6.88
2025-08-02 | 23.1 | 0 | 5.1 | 2024-08-02 | 27.3 | 0 | 9.3 | 2023-08-02 | 20.6 | 0 | 2.6 | 2022-08-02 | 20.9 | 0 | 2.9 | 2021-08-02 | 20.4 | 0 | 2.4 | 2020-08-02 | 23.6 | 0 | 5.6 | 2019-08-02 | 24.8 | 0 | 6.8 | 2018-08-02 | 24.9 | 0 | 6.9 | 2017-08-02 | 20 | 0 | 2 | 2016-08-02 | 26 | 0 | 8 | 0 | 5.16
2025-08-02 | 21.6 | 0 | 3.6 | 2024-08-02 | 26.1 | 0 | 8.1 | 2023-08-02 | 19.4 | 0 | 1.4 | 2022-08-02 | 18.6 | 0 | 0.6 | 2021-08-02 | 18.6 | 0 | 0.6 | 2020-08-02 | 22.4 | 0 | 4.4 | 2019-08-02 | 22.6 | 0 | 4.6 | 2018-08-02 | 23.5 | 0 | 5.5 | 2017-08-02 | 19.6 | 0 | 1.6 | 2016-08-02 | 23.2 | 0 | 5.2 | 0 | 3.56
2025-08-02 | 19.4 | 0 | 1.4 | 2024-08-02 | 25.2 | 0 | 7.2 | 2023-08-02 | 18.3 | 0 | 0.3 | 2022-08-02 | 15.6 | 2.4 | 0 | 2021-08-02 | 16.8 | 1.2 | 0 | 2020-08-02 | 21.9 | 0 | 3.9 | 2019-08-02 | 21.4 | 0 | 3.4 | 2018-08-02 | 22.9 | 0 | 4.9 | 2017-08-02 | 17.6 | 0.4 | 0 | 2016-08-02 | 21.8 | 0 | 3.8 | 0.4 | 2.49
2025-08-02 | 18.6 | 0 | 0.6 | 2024-08-02 | 24.2 | 0 | 6.2 | 2023-08-02 | 18.2 | 0 | 0.2 | 2022-08-02 | 14.8 | 3.2 | 0 | 2021-08-02 | 15.9 | 2.1 | 0 | 2020-08-02 | 21.1 | 0 | 3.1 | 2019-08-02 | 20.3 | 0 | 2.3 | 2018-08-02 | 22 | 0 | 4 | 2017-08-02 | 18.3 | 0 | 0.3 | 2016-08-02 | 19.7 | 0 | 1.7 | 0.53 | 1.84
2025-08-02 | 17.6 | 0.4 | 0 | 2024-08-02 | 23.1 | 0 | 5.1 | 2023-08-02 | 18.4 | 0 | 0.4 | 2022-08-02 | 14.2 | 3.8 | 0 | 2021-08-02 | 15.9 | 2.1 | 0 | 2020-08-02 | 21 | 0 | 3 | 2019-08-02 | 20.3 | 0 | 2.3 | 2018-08-02 | 21 | 0 | 3 | 2017-08-02 | 18.4 | 0 | 0.4 | 2016-08-02 | 18.8 | 0 | 0.8 | 0.63 | 1.5
2025-08-03 | 16.5 | 1.5 | 0 | 2024-08-03 | 23 | 0 | 5 | 2023-08-03 | 17.1 | 0.9 | 0 | 2022-08-03 | 14.6 | 3.4 | 0 | 2021-08-03 | 15.1 | 2.9 | 0 | 2020-08-03 | 20.7 | 0 | 2.7 | 2019-08-03 | 19.6 | 0 | 1.6 | 2018-08-03 | 20.5 | 0 | 2.5 | 2017-08-03 | 18.4 | 0 | 0.4 | 2016-08-03 | 19.1 | 0 | 1.1 | 0.87 | 1.33
2025-08-03 | 16.3 | 1.7 | 0 | 2024-08-03 | 22.1 | 0 | 4.1 | 2023-08-03 | 17.2 | 0.8 | 0 | 2022-08-03 | 11.6 | 6.4 | 0 | 2021-08-03 | 13.8 | 4.2 | 0 | 2020-08-03 | 21.6 | 0 | 3.6 | 2019-08-03 | 16.8 | 1.2 | 0 | 2018-08-03 | 20.4 | 0 | 2.4 | 2017-08-03 | 18.9 | 0 | 0.9 | 2016-08-03 | 17.8 | 0.2 | 0 | 1.45 | 1.1
2025-08-03 | 15.8 | 2.2 | 0 | 2024-08-03 | 21.7 | 0 | 3.7 | 2023-08-03 | 17.2 | 0.8 | 0 | 2022-08-03 | 10.5 | 7.5 | 0 | 2021-08-03 | 13.2 | 4.8 | 0 | 2020-08-03 | 20.9 | 0 | 2.9 | 2019-08-03 | 16.8 | 1.2 | 0 | 2018-08-03 | 20 | 0 | 2 | 2017-08-03 | 19 | 0 | 1 | 2016-08-03 | 17 | 1 | 0 | 1.75 | 0.96
2025-08-03 | 15.3 | 2.7 | 0 | 2024-08-03 | 21.2 | 0 | 3.2 | 2023-08-03 | 17.6 | 0.4 | 0 | 2022-08-03 | 10 | 8 | 0 | 2021-08-03 | 12.8 | 5.2 | 0 | 2020-08-03 | 20.6 | 0 | 2.6 | 2019-08-03 | 15.5 | 2.5 | 0 | 2018-08-03 | 19.6 | 0 | 1.6 | 2017-08-03 | 17.1 | 0.9 | 0 | 2016-08-03 | 17.2 | 0.8 | 0 | 2.05 | 0.74
2025-08-03 | 15.1 | 2.9 | 0 | 2024-08-03 | 21.4 | 0 | 3.4 | 2023-08-03 | 16 | 2 | 0 | 2022-08-03 | 10.2 | 7.8 | 0 | 2021-08-03 | 12.3 | 5.7 | 0 | 2020-08-03 | 19.2 | 0 | 1.2 | 2019-08-03 | 15.3 | 2.7 | 0 | 2018-08-03 | 19.2 | 0 | 1.2 | 2017-08-03 | 17.3 | 0.7 | 0 | 2016-08-03 | 16.6 | 1.4 | 0 | 2.32 | 0.58
2025-08-03 | 14.7 | 3.3 | 0 | 2024-08-03 | 21 | 0 | 3 | 2023-08-03 | 16.2 | 1.8 | 0 | 2022-08-03 | 10.3 | 7.7 | 0 | 2021-08-03 | 11.4 | 6.6 | 0 | 2020-08-03 | 18.5 | 0 | 0.5 | 2019-08-03 | 15.1 | 2.9 | 0 | 2018-08-03 | 18.2 | 0 | 0.2 | 2017-08-03 | 18.3 | 0 | 0.3 | 2016-08-03 | 14.2 | 3.8 | 0 | 2.61 | 0.4
2025-08-03 | 15.5 | 2.5 | 0 | 2024-08-03 | 21.2 | 0 | 3.2 | 2023-08-03 | 17.1 | 0.9 | 0 | 2022-08-03 | 12.9 | 5.1 | 0 | 2021-08-03 | 12.9 | 5.1 | 0 | 2020-08-03 | 16.9 | 1.1 | 0 | 2019-08-03 | 15.6 | 2.4 | 0 | 2018-08-03 | 19.6 | 0 | 1.6 | 2017-08-03 | 18.6 | 0 | 0.6 | 2016-08-03 | 17.4 | 0.6 | 0 | 1.77 | 0.54
2025-08-03 | 17 | 1 | 0 | 2024-08-03 | 23.3 | 0 | 5.3 | 2023-08-03 | 18.8 | 0 | 0.8 | 2022-08-03 | 15.4 | 2.6 | 0 | 2021-08-03 | 15.6 | 2.4 | 0 | 2020-08-03 | 16.6 | 1.4 | 0 | 2019-08-03 | 17.6 | 0.4 | 0 | 2018-08-03 | 20.8 | 0 | 2.8 | 2017-08-03 | 19.3 | 0 | 1.3 | 2016-08-03 | 20.2 | 0 | 2.2 | 0.78 | 1.24
2025-08-03 | 18.8 | 0 | 0.8 | 2024-08-03 | 24.8 | 0 | 6.8 | 2023-08-03 | 19.7 | 0 | 1.7 | 2022-08-03 | 17 | 1 | 0 | 2021-08-03 | 19 | 0 | 1 | 2020-08-03 | 17.4 | 0.6 | 0 | 2019-08-03 | 20.8 | 0 | 2.8 | 2018-08-03 | 22.5 | 0 | 4.5 | 2017-08-03 | 20.6 | 0 | 2.6 | 2016-08-03 | 22.8 | 0 | 4.8 | 0.16 | 2.5
2025-08-03 | 20.6 | 0 | 2.6 | 2024-08-03 | 26.9 | 0 | 8.9 | 2023-08-03 | 20.8 | 0 | 2.8 | 2022-08-03 | 19 | 0 | 1 | 2021-08-03 | 21.2 | 0 | 3.2 | 2020-08-03 | 18.4 | 0 | 0.4 | 2019-08-03 | 23.3 | 0 | 5.3 | 2018-08-03 | 24 | 0 | 6 | 2017-08-03 | 21.7 | 0 | 3.7 | 2016-08-03 | 24.9 | 0 | 6.9 | 0 | 4.08
2025-08-03 | 22.7 | 0 | 4.7 | 2024-08-03 | 28.7 | 0 | 10.7 | 2023-08-03 | 21.8 | 0 | 3.8 | 2022-08-03 | 20.8 | 0 | 2.8 | 2021-08-03 | 22.7 | 0 | 4.7 | 2020-08-03 | 19.2 | 0 | 1.2 | 2019-08-03 | 25.4 | 0 | 7.4 | 2018-08-03 | 24.7 | 0 | 6.7 | 2017-08-03 | 22.2 | 0 | 4.2 | 2016-08-03 | 25.7 | 0 | 7.7 | 0 | 5.39
2025-08-03 | 24.6 | 0 | 6.6 | 2024-08-03 | 29.7 | 0 | 11.7 | 2023-08-03 | 22.6 | 0 | 4.6 | 2022-08-03 | 22.3 | 0 | 4.3 | 2021-08-03 | 23.8 | 0 | 5.8 | 2020-08-03 | 20.8 | 0 | 2.8 | 2019-08-03 | 26.2 | 0 | 8.2 | 2018-08-03 | 25.7 | 0 | 7.7 | 2017-08-03 | 22.5 | 0 | 4.5 | 2016-08-03 | 28.5 | 0 | 10.5 | 0 | 6.67
2025-08-03 | 26.7 | 0 | 8.7 | 2024-08-03 | 30.6 | 0 | 12.6 | 2023-08-03 | 23.9 | 0 | 5.9 | 2022-08-03 | 23.9 | 0 | 5.9 | 2021-08-03 | 23.9 | 0 | 5.9 | 2020-08-03 | 21.6 | 0 | 3.6 | 2019-08-03 | 24.3 | 0 | 6.3 | 2018-08-03 | 26.4 | 0 | 8.4 | 2017-08-03 | 23.1 | 0 | 5.1 | 2016-08-03 | 27.9 | 0 | 9.9 | 0 | 7.23
2025-08-03 | 28.2 | 0 | 10.2 | 2024-08-03 | 30.2 | 0 | 12.2 | 2023-08-03 | 23.4 | 0 | 5.4 | 2022-08-03 | 25.4 | 0 | 7.4 | 2021-08-03 | 25.2 | 0 | 7.2 | 2020-08-03 | 22.2 | 0 | 4.2 | 2019-08-03 | 24.2 | 0 | 6.2 | 2018-08-03 | 27.4 | 0 | 9.4 | 2017-08-03 | 23.9 | 0 | 5.9 | 2016-08-03 | 29.1 | 0 | 11.1 | 0 | 7.92
2025-08-03 | 28.6 | 0 | 10.6 | 2024-08-03 | 31.3 | 0 | 13.3 | 2023-08-03 | 25.8 | 0 | 7.8 | 2022-08-03 | 26.3 | 0 | 8.3 | 2021-08-03 | 26 | 0 | 8 | 2020-08-03 | 22.9 | 0 | 4.9 | 2019-08-03 | 25.6 | 0 | 7.6 | 2018-08-03 | 28.4 | 0 | 10.4 | 2017-08-03 | 23.9 | 0 | 5.9 | 2016-08-03 | 30.1 | 0 | 12.1 | 0 | 8.89
2025-08-03 | 28.6 | 0 | 10.6 | 2024-08-03 | 30.9 | 0 | 12.9 | 2023-08-03 | 25.3 | 0 | 7.3 | 2022-08-03 | 27.3 | 0 | 9.3 | 2021-08-03 | 25.4 | 0 | 7.4 | 2020-08-03 | 24 | 0 | 6 | 2019-08-03 | 27.7 | 0 | 9.7 | 2018-08-03 | 28.2 | 0 | 10.2 | 2017-08-03 | 25 | 0 | 7 | 2016-08-03 | 31.4 | 0 | 13.4 | 0 | 9.38
2025-08-03 | 28.8 | 0 | 10.8 | 2024-08-03 | 29.4 | 0 | 11.4 | 2023-08-03 | 24.8 | 0 | 6.8 | 2022-08-03 | 25.6 | 0 | 7.6 | 2021-08-03 | 24.6 | 0 | 6.6 | 2020-08-03 | 24.6 | 0 | 6.6 | 2019-08-03 | 26.4 | 0 | 8.4 | 2018-08-03 | 27.1 | 0 | 9.1 | 2017-08-03 | 25.5 | 0 | 7.5 | 2016-08-03 | 30.6 | 0 | 12.6 | 0 | 8.74
2025-08-03 | 27.9 | 0 | 9.9 | 2024-08-03 | 28.2 | 0 | 10.2 | 2023-08-03 | 23.6 | 0 | 5.6 | 2022-08-03 | 24.6 | 0 | 6.6 | 2021-08-03 | 25 | 0 | 7 | 2020-08-03 | 24.7 | 0 | 6.7 | 2019-08-03 | 26.1 | 0 | 8.1 | 2018-08-03 | 26.8 | 0 | 8.8 | 2017-08-03 | 24.5 | 0 | 6.5 | 2016-08-03 | 28.7 | 0 | 10.7 | 0 | 8.01
2025-08-03 | 26.7 | 0 | 8.7 | 2024-08-03 | 27.7 | 0 | 9.7 | 2023-08-03 | 19 | 0 | 1 | 2022-08-03 | 23.7 | 0 | 5.7 | 2021-08-03 | 24.1 | 0 | 6.1 | 2020-08-03 | 24.5 | 0 | 6.5 | 2019-08-03 | 25.8 | 0 | 7.8 | 2018-08-03 | 25.8 | 0 | 7.8 | 2017-08-03 | 23.9 | 0 | 5.9 | 2016-08-03 | 27.8 | 0 | 9.8 | 0 | 6.9
2025-08-03 | 24.8 | 0 | 6.8 | 2024-08-03 | 25.7 | 0 | 7.7 | 2023-08-03 | 20.2 | 0 | 2.2 | 2022-08-03 | 22.9 | 0 | 4.9 | 2021-08-03 | 22.5 | 0 | 4.5 | 2020-08-03 | 22.9 | 0 | 4.9 | 2019-08-03 | 23.8 | 0 | 5.8 | 2018-08-03 | 24.4 | 0 | 6.4 | 2017-08-03 | 22.9 | 0 | 4.9 | 2016-08-03 | 23.4 | 0 | 5.4 | 0 | 5.35
2025-08-03 | 22.5 | 0 | 4.5 | 2024-08-03 | 21.4 | 0 | 3.4 | 2023-08-03 | 20.4 | 0 | 2.4 | 2022-08-03 | 22.4 | 0 | 4.4 | 2021-08-03 | 20.5 | 0 | 2.5 | 2020-08-03 | 20.9 | 0 | 2.9 | 2019-08-03 | 23.7 | 0 | 5.7 | 2018-08-03 | 23.5 | 0 | 5.5 | 2017-08-03 | 21.4 | 0 | 3.4 | 2016-08-03 | 22.8 | 0 | 4.8 | 0 | 3.95
2025-08-03 | 20.8 | 0 | 2.8 | 2024-08-03 | 21.8 | 0 | 3.8 | 2023-08-03 | 19.7 | 0 | 1.7 | 2022-08-03 | 22.3 | 0 | 4.3 | 2021-08-03 | 18.8 | 0 | 0.8 | 2020-08-03 | 19.4 | 0 | 1.4 | 2019-08-03 | 22.7 | 0 | 4.7 | 2018-08-03 | 22.3 | 0 | 4.3 | 2017-08-03 | 20.5 | 0 | 2.5 | 2016-08-03 | 22.3 | 0 | 4.3 | 0 | 3.06
2025-08-03 | 19.3 | 0 | 1.3 | 2024-08-03 | 21.2 | 0 | 3.2 | 2023-08-03 | 18.8 | 0 | 0.8 | 2022-08-03 | 21.8 | 0 | 3.8 | 2021-08-03 | 18 | 0 | 0 | 2020-08-03 | 18.9 | 0 | 0.9 | 2019-08-03 | 21.1 | 0 | 3.1 | 2018-08-03 | 22.1 | 0 | 4.1 | 2017-08-03 | 19.7 | 0 | 1.7 | 2016-08-03 | 21 | 0 | 3 | 0 | 2.19
2025-08-03 | 17.5 | 0.5 | 0 | 2024-08-03 | 22.1 | 0 | 4.1 | 2023-08-03 | 17 | 1 | 0 | 2022-08-03 | 21.7 | 0 | 3.7 | 2021-08-03 | 17.2 | 0.8 | 0 | 2020-08-03 | 18.8 | 0 | 0.8 | 2019-08-03 | 19.8 | 0 | 1.8 | 2018-08-03 | 22.3 | 0 | 4.3 | 2017-08-03 | 19.6 | 0 | 1.6 | 2016-08-03 | 20 | 0 | 2 | 0.23 | 1.83
2025-08-04 | 17.4 | 0.6 | 0 | 2024-08-04 | 21.8 | 0 | 3.8 | 2023-08-04 | 17.4 | 0.6 | 0 | 2022-08-04 | 21.4 | 0 | 3.4 | 2021-08-04 | 16.9 | 1.1 | 0 | 2020-08-04 | 18.2 | 0 | 0.2 | 2019-08-04 | 18.3 | 0 | 0.3 | 2018-08-04 | 21.9 | 0 | 3.9 | 2017-08-04 | 18.7 | 0 | 0.7 | 2016-08-04 | 20.1 | 0 | 2.1 | 0.23 | 1.44
2025-08-04 | 17.5 | 0.5 | 0 | 2024-08-04 | 19.9 | 0 | 1.9 | 2023-08-04 | 17.2 | 0.8 | 0 | 2022-08-04 | 21.4 | 0 | 3.4 | 2021-08-04 | 15.8 | 2.2 | 0 | 2020-08-04 | 17.8 | 0.2 | 0 | 2019-08-04 | 17.7 | 0.3 | 0 | 2018-08-04 | 20.9 | 0 | 2.9 | 2017-08-04 | 17.9 | 0.1 | 0 | 2016-08-04 | 20 | 0 | 2 | 0.41 | 1.02
2025-08-04 | 16.9 | 1.1 | 0 | 2024-08-04 | 19.5 | 0 | 1.5 | 2023-08-04 | 16.9 | 1.1 | 0 | 2022-08-04 | 21.5 | 0 | 3.5 | 2021-08-04 | 14.9 | 3.1 | 0 | 2020-08-04 | 17.5 | 0.5 | 0 | 2019-08-04 | 16.6 | 1.4 | 0 | 2018-08-04 | 20.2 | 0 | 2.2 | 2017-08-04 | 18.1 | 0 | 0.1 | 2016-08-04 | 19.9 | 0 | 1.9 | 0.72 | 0.92
2025-08-04 | 15.9 | 2.1 | 0 | 2024-08-04 | 19.2 | 0 | 1.2 | 2023-08-04 | 16.7 | 1.3 | 0 | 2022-08-04 | 20.6 | 0 | 2.6 | 2021-08-04 | 14.8 | 3.2 | 0 | 2020-08-04 | 17.3 | 0.7 | 0 | 2019-08-04 | 15.2 | 2.8 | 0 | 2018-08-04 | 20.2 | 0 | 2.2 | 2017-08-04 | 18 | 0 | 0 | 2016-08-04 | 19 | 0 | 1 | 1.01 | 0.7
2025-08-04 | 16.5 | 1.5 | 0 | 2024-08-04 | 19 | 0 | 1 | 2023-08-04 | 16.3 | 1.7 | 0 | 2022-08-04 | 20.3 | 0 | 2.3 | 2021-08-04 | 14.2 | 3.8 | 0 | 2020-08-04 | 17.1 | 0.9 | 0 | 2019-08-04 | 14.2 | 3.8 | 0 | 2018-08-04 | 19.7 | 0 | 1.7 | 2017-08-04 | 17.8 | 0.2 | 0 | 2016-08-04 | 18.9 | 0 | 0.9 | 1.19 | 0.59
2025-08-04 | 17.1 | 0.9 | 0 | 2024-08-04 | 18.8 | 0 | 0.8 | 2023-08-04 | 16.6 | 1.4 | 0 | 2022-08-04 | 20.4 | 0 | 2.4 | 2021-08-04 | 14 | 4 | 0 | 2020-08-04 | 16.9 | 1.1 | 0 | 2019-08-04 | 14.1 | 3.9 | 0 | 2018-08-04 | 19 | 0 | 1 | 2017-08-04 | 17.5 | 0.5 | 0 | 2016-08-04 | 18.4 | 0 | 0.4 | 1.18 | 0.46
2025-08-04 | 16.8 | 1.2 | 0 | 2024-08-04 | 18.5 | 0 | 0.5 | 2023-08-04 | 16.8 | 1.2 | 0 | 2022-08-04 | 20.6 | 0 | 2.6 | 2021-08-04 | 14.7 | 3.3 | 0 | 2020-08-04 | 17.1 | 0.9 | 0 | 2019-08-04 | 14.7 | 3.3 | 0 | 2018-08-04 | 20.3 | 0 | 2.3 | 2017-08-04 | 18.1 | 0 | 0.1 | 2016-08-04 | 19.4 | 0 | 1.4 | 0.99 | 0.69
2025-08-04 | 19.8 | 0 | 1.8 | 2024-08-04 | 20.6 | 0 | 2.6 | 2023-08-04 | 17.6 | 0.4 | 0 | 2022-08-04 | 21.4 | 0 | 3.4 | 2021-08-04 | 16.7 | 1.3 | 0 | 2020-08-04 | 17.6 | 0.4 | 0 | 2019-08-04 | 16.4 | 1.6 | 0 | 2018-08-04 | 22.6 | 0 | 4.6 | 2017-08-04 | 18.4 | 0 | 0.4 | 2016-08-04 | 21.7 | 0 | 3.7 | 0.37 | 1.65
2025-08-04 | 21.5 | 0 | 3.5 | 2024-08-04 | 21.4 | 0 | 3.4 | 2023-08-04 | 18.3 | 0 | 0.3 | 2022-08-04 | 21.7 | 0 | 3.7 | 2021-08-04 | 19.7 | 0 | 1.7 | 2020-08-04 | 18 | 0 | 0 | 2019-08-04 | 18.2 | 0 | 0.2 | 2018-08-04 | 24.2 | 0 | 6.2 | 2017-08-04 | 19.8 | 0 | 1.8 | 2016-08-04 | 24.3 | 0 | 6.3 | 0 | 2.71
2025-08-04 | 22.3 | 0 | 4.3 | 2024-08-04 | 23.7 | 0 | 5.7 | 2023-08-04 | 20.9 | 0 | 2.9 | 2022-08-04 | 22 | 0 | 4 | 2021-08-04 | 22 | 0 | 4 | 2020-08-04 | 18.2 | 0 | 0.2 | 2019-08-04 | 19.6 | 0 | 1.6 | 2018-08-04 | 26 | 0 | 8 | 2017-08-04 | 21.5 | 0 | 3.5 | 2016-08-04 | 26.3 | 0 | 8.3 | 0 | 4.25
2025-08-04 | 22.8 | 0 | 4.8 | 2024-08-04 | 26.4 | 0 | 8.4 | 2023-08-04 | 22.1 | 0 | 4.1 | 2022-08-04 | 22 | 0 | 4 | 2021-08-04 | 23.9 | 0 | 5.9 | 2020-08-04 | 18.5 | 0 | 0.5 | 2019-08-04 | 20.1 | 0 | 2.1 | 2018-08-04 | 27.4 | 0 | 9.4 | 2017-08-04 | 24.1 | 0 | 6.1 | 2016-08-04 | 27.5 | 0 | 9.5 | 0 | 5.48
2025-08-04 | 23.2 | 0 | 5.2 | 2024-08-04 | 28 | 0 | 10 | 2023-08-04 | 23.4 | 0 | 5.4 | 2022-08-04 | 21.9 | 0 | 3.9 | 2021-08-04 | 25.1 | 0 | 7.1 | 2020-08-04 | 18.9 | 0 | 0.9 | 2019-08-04 | 21.4 | 0 | 3.4 | 2018-08-04 | 26.5 | 0 | 8.5 | 2017-08-04 | 24.9 | 0 | 6.9 | 2016-08-04 | 30 | 0 | 12 | 0 | 6.33
2025-08-04 | 22.9 | 0 | 4.9 | 2024-08-04 | 29.7 | 0 | 11.7 | 2023-08-04 | 23.1 | 0 | 5.1 | 2022-08-04 | 22.7 | 0 | 4.7 | 2021-08-04 | 25.4 | 0 | 7.4 | 2020-08-04 | 20 | 0 | 2 | 2019-08-04 | 22.2 | 0 | 4.2 | 2018-08-04 | 27.2 | 0 | 9.2 | 2017-08-04 | 25.7 | 0 | 7.7 | 2016-08-04 | 31.4 | 0 | 13.4 | 0 | 7.03
2025-08-04 | 24.5 | 0 | 6.5 | 2024-08-04 | 29.8 | 0 | 11.8 | 2023-08-04 | 25.2 | 0 | 7.2 | 2022-08-04 | 24.7 | 0 | 6.7 | 2021-08-04 | 26.1 | 0 | 8.1 | 2020-08-04 | 20.9 | 0 | 2.9 | 2019-08-04 | 22.9 | 0 | 4.9 | 2018-08-04 | 28.2 | 0 | 10.2 | 2017-08-04 | 26.7 | 0 | 8.7 | 2016-08-04 | 32.6 | 0 | 14.6 | 0 | 8.16
2025-08-04 | 25.1 | 0 | 7.1 | 2024-08-04 | 31.6 | 0 | 13.6 | 2023-08-04 | 25.3 | 0 | 7.3 | 2022-08-04 | 26 | 0 | 8 | 2021-08-04 | 26.6 | 0 | 8.6 | 2020-08-04 | 20.8 | 0 | 2.8 | 2019-08-04 | 23.6 | 0 | 5.6 | 2018-08-04 | 27.2 | 0 | 9.2 | 2017-08-04 | 28.2 | 0 | 10.2 | 2016-08-04 | 33 | 0 | 15 | 0 | 8.74
2025-08-04 | 25.1 | 0 | 7.1 | 2024-08-04 | 31.3 | 0 | 13.3 | 2023-08-04 | 25.4 | 0 | 7.4 | 2022-08-04 | 27.3 | 0 | 9.3 | 2021-08-04 | 27.2 | 0 | 9.2 | 2020-08-04 | 20.8 | 0 | 2.8 | 2019-08-04 | 23.5 | 0 | 5.5 | 2018-08-04 | 29.7 | 0 | 11.7 | 2017-08-04 | 27.6 | 0 | 9.6 | 2016-08-04 | 33.7 | 0 | 15.7 | 0 | 9.16
2025-08-04 | 25 | 0 | 7 | 2024-08-04 | 30.8 | 0 | 12.8 | 2023-08-04 | 24.3 | 0 | 6.3 | 2022-08-04 | 27.9 | 0 | 9.9 | 2021-08-04 | 26.8 | 0 | 8.8 | 2020-08-04 | 20.5 | 0 | 2.5 | 2019-08-04 | 24.1 | 0 | 6.1 | 2018-08-04 | 27.9 | 0 | 9.9 | 2017-08-04 | 28 | 0 | 10 | 2016-08-04 | 33 | 0 | 15 | 0 | 8.83
2025-08-04 | 23.8 | 0 | 5.8 | 2024-08-04 | 29.9 | 0 | 11.9 | 2023-08-04 | 24.3 | 0 | 6.3 | 2022-08-04 | 27.6 | 0 | 9.6 | 2021-08-04 | 26.5 | 0 | 8.5 | 2020-08-04 | 20.6 | 0 | 2.6 | 2019-08-04 | 24.5 | 0 | 6.5 | 2018-08-04 | 27.6 | 0 | 9.6 | 2017-08-04 | 27.7 | 0 | 9.7 | 2016-08-04 | 32.4 | 0 | 14.4 | 0 | 8.49
2025-08-04 | 22.6 | 0 | 4.6 | 2024-08-04 | 28.1 | 0 | 10.1 | 2023-08-04 | 23.6 | 0 | 5.6 | 2022-08-04 | 26.8 | 0 | 8.8 | 2021-08-04 | 24.9 | 0 | 6.9 | 2020-08-04 | 20.2 | 0 | 2.2 | 2019-08-04 | 23.7 | 0 | 5.7 | 2018-08-04 | 26.9 | 0 | 8.9 | 2017-08-04 | 23.9 | 0 | 5.9 | 2016-08-04 | 30.9 | 0 | 12.9 | 0 | 7.16
2025-08-04 | 21.2 | 0 | 3.2 | 2024-08-04 | 26.5 | 0 | 8.5 | 2023-08-04 | 21.9 | 0 | 3.9 | 2022-08-04 | 25.4 | 0 | 7.4 | 2021-08-04 | 22.4 | 0 | 4.4 | 2020-08-04 | 20.2 | 0 | 2.2 | 2019-08-04 | 21.8 | 0 | 3.8 | 2018-08-04 | 24.2 | 0 | 6.2 | 2017-08-04 | 21.7 | 0 | 3.7 | 2016-08-04 | 28.6 | 0 | 10.6 | 0 | 5.39
2025-08-04 | 20.6 | 0 | 2.6 | 2024-08-04 | 25.3 | 0 | 7.3 | 2023-08-04 | 20.8 | 0 | 2.8 | 2022-08-04 | 24.4 | 0 | 6.4 | 2021-08-04 | 20.7 | 0 | 2.7 | 2020-08-04 | 19.9 | 0 | 1.9 | 2019-08-04 | 20.1 | 0 | 2.1 | 2018-08-04 | 23.6 | 0 | 5.6 | 2017-08-04 | 21.3 | 0 | 3.3 | 2016-08-04 | 27.2 | 0 | 9.2 | 0 | 4.39
2025-08-04 | 19.5 | 0 | 1.5 | 2024-08-04 | 23.9 | 0 | 5.9 | 2023-08-04 | 18.2 | 0 | 0.2 | 2022-08-04 | 23.7 | 0 | 5.7 | 2021-08-04 | 20.1 | 0 | 2.1 | 2020-08-04 | 19.4 | 0 | 1.4 | 2019-08-04 | 18.3 | 0 | 0.3 | 2018-08-04 | 23.1 | 0 | 5.1 | 2017-08-04 | 20.6 | 0 | 2.6 | 2016-08-04 | 25.3 | 0 | 7.3 | 0 | 3.21
2025-08-04 | 18.2 | 0 | 0.2 | 2024-08-04 | 22.7 | 0 | 4.7 | 2023-08-04 | 17.7 | 0.3 | 0 | 2022-08-04 | 23.4 | 0 | 5.4 | 2021-08-04 | 19.3 | 0 | 1.3 | 2020-08-04 | 19.2 | 0 | 1.2 | 2019-08-04 | 16.7 | 1.3 | 0 | 2018-08-04 | 21.3 | 0 | 3.3 | 2017-08-04 | 19.6 | 0 | 1.6 | 2016-08-04 | 23.9 | 0 | 5.9 | 0.16 | 2.36
2025-08-04 | 17.7 | 0.3 | 0 | 2024-08-04 | 21 | 0 | 3 | 2023-08-04 | 17 | 1 | 0 | 2022-08-04 | 23.6 | 0 | 5.6 | 2021-08-04 | 18.8 | 0 | 0.8 | 2020-08-04 | 19.2 | 0 | 1.2 | 2019-08-04 | 12.9 | 5.1 | 0 | 2018-08-04 | 21.6 | 0 | 3.6 | 2017-08-04 | 19.4 | 0 | 1.4 | 2016-08-04 | 23.4 | 0 | 5.4 | 0.64 | 2.1
2025-08-05 | 17.3 | 0.7 | 0 | 2024-08-05 | 19.9 | 0 | 1.9 | 2023-08-05 | 17.6 | 0.4 | 0 | 2022-08-05 | 22.5 | 0 | 4.5 | 2021-08-05 | 19.1 | 0 | 1.1 | 2020-08-05 | 18.3 | 0 | 0.3 | 2019-08-05 | 13.7 | 4.3 | 0 | 2018-08-05 | 19.9 | 0 | 1.9 | 2017-08-05 | 19.2 | 0 | 1.2 | 2016-08-05 | 22 | 0 | 4 | 0.54 | 1.49
2025-08-05 | 15.9 | 2.1 | 0 | 2024-08-05 | 17.8 | 0.2 | 0 | 2023-08-05 | 16.6 | 1.4 | 0 | 2022-08-05 | 21.9 | 0 | 3.9 | 2021-08-05 | 18.7 | 0 | 0.7 | 2020-08-05 | 18 | 0 | 0 | 2019-08-05 | 12.7 | 5.3 | 0 | 2018-08-05 | 20.4 | 0 | 2.4 | 2017-08-05 | 18.7 | 0 | 0.7 | 2016-08-05 | 21.2 | 0 | 3.2 | 0.9 | 1.09
2025-08-05 | 15.2 | 2.8 | 0 | 2024-08-05 | 17.8 | 0.2 | 0 | 2023-08-05 | 15.9 | 2.1 | 0 | 2022-08-05 | 21.4 | 0 | 3.4 | 2021-08-05 | 18.2 | 0 | 0.2 | 2020-08-05 | 17.8 | 0.2 | 0 | 2019-08-05 | 11.7 | 6.3 | 0 | 2018-08-05 | 19.9 | 0 | 1.9 | 2017-08-05 | 18.7 | 0 | 0.7 | 2016-08-05 | 21 | 0 | 3 | 1.16 | 0.92
2025-08-05 | 14.5 | 3.5 | 0 | 2024-08-05 | 15.8 | 2.2 | 0 | 2023-08-05 | 14.3 | 3.7 | 0 | 2022-08-05 | 20.7 | 0 | 2.7 | 2021-08-05 | 17.4 | 0.6 | 0 | 2020-08-05 | 17.5 | 0.5 | 0 | 2019-08-05 | 11 | 7 | 0 | 2018-08-05 | 19.5 | 0 | 1.5 | 2017-08-05 | 19 | 0 | 1 | 2016-08-05 | 20.6 | 0 | 2.6 | 1.75 | 0.78
2025-08-05 | 14.8 | 3.2 | 0 | 2024-08-05 | 16.8 | 1.2 | 0 | 2023-08-05 | 13.2 | 4.8 | 0 | 2022-08-05 | 19.8 | 0 | 1.8 | 2021-08-05 | 15.5 | 2.5 | 0 | 2020-08-05 | 17.5 | 0.5 | 0 | 2019-08-05 | 10.4 | 7.6 | 0 | 2018-08-05 | 18.4 | 0 | 0.4 | 2017-08-05 | 18.8 | 0 | 0.8 | 2016-08-05 | 19.6 | 0 | 1.6 | 1.98 | 0.46
2025-08-05 | 14.4 | 3.6 | 0 | 2024-08-05 | 17.1 | 0.9 | 0 | 2023-08-05 | 13.1 | 4.9 | 0 | 2022-08-05 | 19.4 | 0 | 1.4 | 2021-08-05 | 14.6 | 3.4 | 0 | 2020-08-05 | 17.4 | 0.6 | 0 | 2019-08-05 | 9.7 | 8.3 | 0 | 2018-08-05 | 18.7 | 0 | 0.7 | 2017-08-05 | 17.3 | 0.7 | 0 | 2016-08-05 | 19 | 0 | 1 | 2.24 | 0.31
2025-08-05 | 14.8 | 3.2 | 0 | 2024-08-05 | 17.8 | 0.2 | 0 | 2023-08-05 | 14.6 | 3.4 | 0 | 2022-08-05 | 19.1 | 0 | 1.1 | 2021-08-05 | 16.1 | 1.9 | 0 | 2020-08-05 | 17.3 | 0.7 | 0 | 2019-08-05 | 14.2 | 3.8 | 0 | 2018-08-05 | 19.3 | 0 | 1.3 | 2017-08-05 | 17.1 | 0.9 | 0 | 2016-08-05 | 20.7 | 0 | 2.7 | 1.41 | 0.51
2025-08-05 | 15.9 | 2.1 | 0 | 2024-08-05 | 19.1 | 0 | 1.1 | 2023-08-05 | 16.6 | 1.4 | 0 | 2022-08-05 | 20.4 | 0 | 2.4 | 2021-08-05 | 18.6 | 0 | 0.6 | 2020-08-05 | 17.7 | 0.3 | 0 | 2019-08-05 | 17.1 | 0.9 | 0 | 2018-08-05 | 21.4 | 0 | 3.4 | 2017-08-05 | 18.3 | 0 | 0.3 | 2016-08-05 | 23.1 | 0 | 5.1 | 0.47 | 1.29
2025-08-05 | 17.6 | 0.4 | 0 | 2024-08-05 | 18.9 | 0 | 0.9 | 2023-08-05 | 17.4 | 0.6 | 0 | 2022-08-05 | 22.2 | 0 | 4.2 | 2021-08-05 | 20.6 | 0 | 2.6 | 2020-08-05 | 18.7 | 0 | 0.7 | 2019-08-05 | 19.1 | 0 | 1.1 | 2018-08-05 | 23.3 | 0 | 5.3 | 2017-08-05 | 19.3 | 0 | 1.3 | 2016-08-05 | 25.9 | 0 | 7.9 | 0.1 | 2.4
2025-08-05 | 20.3 | 0 | 2.3 | 2024-08-05 | 18.5 | 0 | 0.5 | 2023-08-05 | 19 | 0 | 1 | 2022-08-05 | 23.5 | 0 | 5.5 | 2021-08-05 | 22.6 | 0 | 4.6 | 2020-08-05 | 19.6 | 0 | 1.6 | 2019-08-05 | 21.8 | 0 | 3.8 | 2018-08-05 | 25.9 | 0 | 7.9 | 2017-08-05 | 19.6 | 0 | 1.6 | 2016-08-05 | 28.2 | 0 | 10.2 | 0 | 3.9
2025-08-05 | 21.3 | 0 | 3.3 | 2024-08-05 | 18.5 | 0 | 0.5 | 2023-08-05 | 20.2 | 0 | 2.2 | 2022-08-05 | 25 | 0 | 7 | 2021-08-05 | 25.1 | 0 | 7.1 | 2020-08-05 | 19 | 0 | 1 | 2019-08-05 | 24.5 | 0 | 6.5 | 2018-08-05 | 27.5 | 0 | 9.5 | 2017-08-05 | 19.7 | 0 | 1.7 | 2016-08-05 | 29 | 0 | 11 | 0 | 4.98
2025-08-05 | 22.9 | 0 | 4.9 | 2024-08-05 | 18.6 | 0 | 0.6 | 2023-08-05 | 21.3 | 0 | 3.3 | 2022-08-05 | 25.3 | 0 | 7.3 | 2021-08-05 | 26.6 | 0 | 8.6 | 2020-08-05 | 20.5 | 0 | 2.5 | 2019-08-05 | 25.4 | 0 | 7.4 | 2018-08-05 | 28.7 | 0 | 10.7 | 2017-08-05 | 20.7 | 0 | 2.7 | 2016-08-05 | 31 | 0 | 13 | 0 | 6.1
2025-08-05 | 23.5 | 0 | 5.5 | 2024-08-05 | 18.8 | 0 | 0.8 | 2023-08-05 | 22.4 | 0 | 4.4 | 2022-08-05 | 25.7 | 0 | 7.7 | 2021-08-05 | 27.3 | 0 | 9.3 | 2020-08-05 | 22 | 0 | 4 | 2019-08-05 | 26.6 | 0 | 8.6 | 2018-08-05 | 29.8 | 0 | 11.8 | 2017-08-05 | 21.3 | 0 | 3.3 | 2016-08-05 | 31.6 | 0 | 13.6 | 0 | 6.9
2025-08-05 | 24.2 | 0 | 6.2 | 2024-08-05 | 18.9 | 0 | 0.9 | 2023-08-05 | 23.2 | 0 | 5.2 | 2022-08-05 | 27.4 | 0 | 9.4 | 2021-08-05 | 26.9 | 0 | 8.9 | 2020-08-05 | 22 | 0 | 4 | 2019-08-05 | 27.8 | 0 | 9.8 | 2018-08-05 | 30.8 | 0 | 12.8 | 2017-08-05 | 22.3 | 0 | 4.3 | 2016-08-05 | 32.4 | 0 | 14.4 | 0 | 7.59
2025-08-05 | 24.6 | 0 | 6.6 | 2024-08-05 | 19.1 | 0 | 1.1 | 2023-08-05 | 23.9 | 0 | 5.9 | 2022-08-05 | 27.5 | 0 | 9.5 | 2021-08-05 | 28.2 | 0 | 10.2 | 2020-08-05 | 22.8 | 0 | 4.8 | 2019-08-05 | 28.6 | 0 | 10.6 | 2018-08-05 | 31.4 | 0 | 13.4 | 2017-08-05 | 21.7 | 0 | 3.7 | 2016-08-05 | 32.5 | 0 | 14.5 | 0 | 8.03
2025-08-05 | 24.4 | 0 | 6.4 | 2024-08-05 | 17.2 | 0.8 | 0 | 2023-08-05 | 23.2 | 0 | 5.2 | 2022-08-05 | 27.8 | 0 | 9.8 | 2021-08-05 | 28.3 | 0 | 10.3 | 2020-08-05 | 22.2 | 0 | 4.2 | 2019-08-05 | 28.6 | 0 | 10.6 | 2018-08-05 | 31.6 | 0 | 13.6 | 2017-08-05 | 22.9 | 0 | 4.9 | 2016-08-05 | 30.9 | 0 | 12.9 | 0.08 | 7.79
2025-08-05 | 24.4 | 0 | 6.4 | 2024-08-05 | 16 | 2 | 0 | 2023-08-05 | 25.2 | 0 | 7.2 | 2022-08-05 | 26.8 | 0 | 8.8 | 2021-08-05 | 28.3 | 0 | 10.3 | 2020-08-05 | 22.8 | 0 | 4.8 | 2019-08-05 | 28.9 | 0 | 10.9 | 2018-08-05 | 31 | 0 | 13 | 2017-08-05 | 19.1 | 0 | 1.1 | 2016-08-05 | 30.2 | 0 | 12.2 | 0.2 | 7.47
2025-08-05 | 24.4 | 0 | 6.4 | 2024-08-05 | 15.4 | 2.6 | 0 | 2023-08-05 | 24.6 | 0 | 6.6 | 2022-08-05 | 28.1 | 0 | 10.1 | 2021-08-05 | 28 | 0 | 10 | 2020-08-05 | 22.5 | 0 | 4.5 | 2019-08-05 | 28.2 | 0 | 10.2 | 2018-08-05 | 29.4 | 0 | 11.4 | 2017-08-05 | 20.7 | 0 | 2.7 | 2016-08-05 | 28.5 | 0 | 10.5 | 0.26 | 7.24
2025-08-05 | 23.8 | 0 | 5.8 | 2024-08-05 | 15.4 | 2.6 | 0 | 2023-08-05 | 23.3 | 0 | 5.3 | 2022-08-05 | 27.2 | 0 | 9.2 | 2021-08-05 | 26.9 | 0 | 8.9 | 2020-08-05 | 21.8 | 0 | 3.8 | 2019-08-05 | 26.4 | 0 | 8.4 | 2018-08-05 | 28.3 | 0 | 10.3 | 2017-08-05 | 19.7 | 0 | 1.7 | 2016-08-05 | 25.6 | 0 | 7.6 | 0.26 | 6.1
2025-08-05 | 21.5 | 0 | 3.5 | 2024-08-05 | 15.1 | 2.9 | 0 | 2023-08-05 | 21.5 | 0 | 3.5 | 2022-08-05 | 25.9 | 0 | 7.9 | 2021-08-05 | 24.3 | 0 | 6.3 | 2020-08-05 | 20.2 | 0 | 2.2 | 2019-08-05 | 23.9 | 0 | 5.9 | 2018-08-05 | 26.3 | 0 | 8.3 | 2017-08-05 | 18.6 | 0 | 0.6 | 2016-08-05 | 25.4 | 0 | 7.4 | 0.29 | 4.56
2025-08-05 | 20.2 | 0 | 2.2 | 2024-08-05 | 14.3 | 3.7 | 0 | 2023-08-05 | 19.4 | 0 | 1.4 | 2022-08-05 | 21.8 | 0 | 3.8 | 2021-08-05 | 22.9 | 0 | 4.9 | 2020-08-05 | 17.9 | 0.1 | 0 | 2019-08-05 | 21.4 | 0 | 3.4 | 2018-08-05 | 24.7 | 0 | 6.7 | 2017-08-05 | 17 | 1 | 0 | 2016-08-05 | 23.9 | 0 | 5.9 | 0.48 | 2.83
2025-08-05 | 18.6 | 0 | 0.6 | 2024-08-05 | 14.4 | 3.6 | 0 | 2023-08-05 | 19.1 | 0 | 1.1 | 2022-08-05 | 22 | 0 | 4 | 2021-08-05 | 21.6 | 0 | 3.6 | 2020-08-05 | 16.1 | 1.9 | 0 | 2019-08-05 | 20.3 | 0 | 2.3 | 2018-08-05 | 23.7 | 0 | 5.7 | 2017-08-05 | 16.3 | 1.7 | 0 | 2016-08-05 | 22.4 | 0 | 4.4 | 0.72 | 2.17
2025-08-05 | 17.5 | 0.5 | 0 | 2024-08-05 | 14.5 | 3.5 | 0 | 2023-08-05 | 17.8 | 0.2 | 0 | 2022-08-05 | 20.4 | 0 | 2.4 | 2021-08-05 | 20.8 | 0 | 2.8 | 2020-08-05 | 16.5 | 1.5 | 0 | 2019-08-05 | 20.1 | 0 | 2.1 | 2018-08-05 | 22.6 | 0 | 4.6 | 2017-08-05 | 14.6 | 3.4 | 0 | 2016-08-05 | 21.9 | 0 | 3.9 | 0.91 | 1.58
2025-08-05 | 17.6 | 0.4 | 0 | 2024-08-05 | 14 | 4 | 0 | 2023-08-05 | 15.8 | 2.2 | 0 | 2022-08-05 | 18.8 | 0 | 0.8 | 2021-08-05 | 20.2 | 0 | 2.2 | 2020-08-05 | 15.5 | 2.5 | 0 | 2019-08-05 | 19.7 | 0 | 1.7 | 2018-08-05 | 22.2 | 0 | 4.2 | 2017-08-05 | 14.2 | 3.8 | 0 | 2016-08-05 | 21 | 0 | 3 | 1.29 | 1.19
2025-08-06 | 16.7 | 1.3 | 0 | 2024-08-06 | 13 | 5 | 0 | 2023-08-06 | 16.3 | 1.7 | 0 | 2022-08-06 | 17.7 | 0.3 | 0 | 2021-08-06 | 19.5 | 0 | 1.5 | 2020-08-06 | 14 | 4 | 0 | 2019-08-06 | 19.1 | 0 | 1.1 | 2018-08-06 | 21.6 | 0 | 3.6 | 2017-08-06 | 13.9 | 4.1 | 0 | 2016-08-06 | 20.6 | 0 | 2.6 | 1.64 | 0.88
2025-08-06 | 15.1 | 2.9 | 0 | 2024-08-06 | 14.2 | 3.8 | 0 | 2023-08-06 | 14.8 | 3.2 | 0 | 2022-08-06 | 17.9 | 0.1 | 0 | 2021-08-06 | 19.2 | 0 | 1.2 | 2020-08-06 | 13.5 | 4.5 | 0 | 2019-08-06 | 17.1 | 0.9 | 0 | 2018-08-06 | 21 | 0 | 3 | 2017-08-06 | 13.9 | 4.1 | 0 | 2016-08-06 | 20.1 | 0 | 2.1 | 1.95 | 0.63
2025-08-06 | 14.3 | 3.7 | 0 | 2024-08-06 | 13.9 | 4.1 | 0 | 2023-08-06 | 15.6 | 2.4 | 0 | 2022-08-06 | 17.3 | 0.7 | 0 | 2021-08-06 | 17.6 | 0.4 | 0 | 2020-08-06 | 13.2 | 4.8 | 0 | 2019-08-06 | 17.3 | 0.7 | 0 | 2018-08-06 | 21.9 | 0 | 3.9 | 2017-08-06 | 12.4 | 5.6 | 0 | 2016-08-06 | 19.3 | 0 | 1.3 | 2.24 | 0.52
2025-08-06 | 13.7 | 4.3 | 0 | 2024-08-06 | 13.8 | 4.2 | 0 | 2023-08-06 | 13.7 | 4.3 | 0 | 2022-08-06 | 17.4 | 0.6 | 0 | 2021-08-06 | 16.5 | 1.5 | 0 | 2020-08-06 | 13.4 | 4.6 | 0 | 2019-08-06 | 17 | 1 | 0 | 2018-08-06 | 22.4 | 0 | 4.4 | 2017-08-06 | 10.7 | 7.3 | 0 | 2016-08-06 | 18.6 | 0 | 0.6 | 2.78 | 0.5
2025-08-06 | 13.3 | 4.7 | 0 | 2024-08-06 | 14 | 4 | 0 | 2023-08-06 | 14.1 | 3.9 | 0 | 2022-08-06 | 16.3 | 1.7 | 0 | 2021-08-06 | 16.4 | 1.6 | 0 | 2020-08-06 | 13 | 5 | 0 | 2019-08-06 | 15.6 | 2.4 | 0 | 2018-08-06 | 21.8 | 0 | 3.8 | 2017-08-06 | 11.2 | 6.8 | 0 | 2016-08-06 | 19.8 | 0 | 1.8 | 3.01 | 0.56
2025-08-06 | 13.3 | 4.7 | 0 | 2024-08-06 | 13.3 | 4.7 | 0 | 2023-08-06 | 13.9 | 4.1 | 0 | 2022-08-06 | 16.5 | 1.5 | 0 | 2021-08-06 | 15.7 | 2.3 | 0 | 2020-08-06 | 11.9 | 6.1 | 0 | 2019-08-06 | 16.4 | 1.6 | 0 | 2018-08-06 | 21.2 | 0 | 3.2 | 2017-08-06 | 11 | 7 | 0 | 2016-08-06 | 19.7 | 0 | 1.7 | 3.2 | 0.49
2025-08-06 | 14.9 | 3.1 | 0 | 2024-08-06 | 13.4 | 4.6 | 0 | 2023-08-06 | 14.4 | 3.6 | 0 | 2022-08-06 | 17.4 | 0.6 | 0 | 2021-08-06 | 16.5 | 1.5 | 0 | 2020-08-06 | 12.9 | 5.1 | 0 | 2019-08-06 | 17.7 | 0.3 | 0 | 2018-08-06 | 22.1 | 0 | 4.1 | 2017-08-06 | 12.6 | 5.4 | 0 | 2016-08-06 | 20.1 | 0 | 2.1 | 2.42 | 0.62
2025-08-06 | 17.4 | 0.6 | 0 | 2024-08-06 | 14 | 4 | 0 | 2023-08-06 | 17.4 | 0.6 | 0 | 2022-08-06 | 19.3 | 0 | 1.3 | 2021-08-06 | 18.9 | 0 | 0.9 | 2020-08-06 | 15.6 | 2.4 | 0 | 2019-08-06 | 19.3 | 0 | 1.3 | 2018-08-06 | 23.8 | 0 | 5.8 | 2017-08-06 | 13.3 | 4.7 | 0 | 2016-08-06 | 22 | 0 | 4 | 1.23 | 1.33
2025-08-06 | 19.6 | 0 | 1.6 | 2024-08-06 | 15 | 3 | 0 | 2023-08-06 | 19.7 | 0 | 1.7 | 2022-08-06 | 21.9 | 0 | 3.9 | 2021-08-06 | 22 | 0 | 4 | 2020-08-06 | 17.4 | 0.6 | 0 | 2019-08-06 | 22.6 | 0 | 4.6 | 2018-08-06 | 25.6 | 0 | 7.6 | 2017-08-06 | 14.6 | 3.4 | 0 | 2016-08-06 | 22.3 | 0 | 4.3 | 0.7 | 2.77
2025-08-06 | 21.9 | 0 | 3.9 | 2024-08-06 | 17 | 1 | 0 | 2023-08-06 | 21.6 | 0 | 3.6 | 2022-08-06 | 24.4 | 0 | 6.4 | 2021-08-06 | 24.6 | 0 | 6.6 | 2020-08-06 | 19.6 | 0 | 1.6 | 2019-08-06 | 24.3 | 0 | 6.3 | 2018-08-06 | 27.5 | 0 | 9.5 | 2017-08-06 | 17.1 | 0.9 | 0 | 2016-08-06 | 24.6 | 0 | 6.6 | 0.19 | 4.45
2025-08-06 | 23.8 | 0 | 5.8 | 2024-08-06 | 19 | 0 | 1 | 2023-08-06 | 23.5 | 0 | 5.5 | 2022-08-06 | 26.5 | 0 | 8.5 | 2021-08-06 | 26.1 | 0 | 8.1 | 2020-08-06 | 20.5 | 0 | 2.5 | 2019-08-06 | 26.8 | 0 | 8.8 | 2018-08-06 | 28.8 | 0 | 10.8 | 2017-08-06 | 18.4 | 0 | 0.4 | 2016-08-06 | 26.4 | 0 | 8.4 | 0 | 5.98
2025-08-06 | 25.1 | 0 | 7.1 | 2024-08-06 | 20.4 | 0 | 2.4 | 2023-08-06 | 24.4 | 0 | 6.4 | 2022-08-06 | 29 | 0 | 11 | 2021-08-06 | 27.9 | 0 | 9.9 | 2020-08-06 | 21.1 | 0 | 3.1 | 2019-08-06 | 28.3 | 0 | 10.3 | 2018-08-06 | 30.2 | 0 | 12.2 | 2017-08-06 | 18.7 | 0 | 0.7 | 2016-08-06 | 26.4 | 0 | 8.4 | 0 | 7.15
2025-08-06 | 26.6 | 0 | 8.6 | 2024-08-06 | 21.5 | 0 | 3.5 | 2023-08-06 | 25.7 | 0 | 7.7 | 2022-08-06 | 29.8 | 0 | 11.8 | 2021-08-06 | 28.7 | 0 | 10.7 | 2020-08-06 | 22.7 | 0 | 4.7 | 2019-08-06 | 29.5 | 0 | 11.5 | 2018-08-06 | 31.9 | 0 | 13.9 | 2017-08-06 | 19.8 | 0 | 1.8 | 2016-08-06 | 26.5 | 0 | 8.5 | 0 | 8.27
2025-08-06 | 27.1 | 0 | 9.1 | 2024-08-06 | 22.6 | 0 | 4.6 | 2023-08-06 | 25.6 | 0 | 7.6 | 2022-08-06 | 30.4 | 0 | 12.4 | 2021-08-06 | 29.6 | 0 | 11.6 | 2020-08-06 | 23.3 | 0 | 5.3 | 2019-08-06 | 21.5 | 0 | 3.5 | 2018-08-06 | 31.7 | 0 | 13.7 | 2017-08-06 | 19.3 | 0 | 1.3 | 2016-08-06 | 28.2 | 0 | 10.2 | 0 | 7.93
2025-08-06 | 27.9 | 0 | 9.9 | 2024-08-06 | 23.4 | 0 | 5.4 | 2023-08-06 | 26.3 | 0 | 8.3 | 2022-08-06 | 31.6 | 0 | 13.6 | 2021-08-06 | 29.4 | 0 | 11.4 | 2020-08-06 | 24.3 | 0 | 6.3 | 2019-08-06 | 20.1 | 0 | 2.1 | 2018-08-06 | 30.2 | 0 | 12.2 | 2017-08-06 | 20.7 | 0 | 2.7 | 2016-08-06 | 28 | 0 | 10 | 0 | 8.19
2025-08-06 | 27.6 | 0 | 9.6 | 2024-08-06 | 23.4 | 0 | 5.4 | 2023-08-06 | 26.6 | 0 | 8.6 | 2022-08-06 | 31.7 | 0 | 13.7 | 2021-08-06 | 29.4 | 0 | 11.4 | 2020-08-06 | 24.9 | 0 | 6.9 | 2019-08-06 | 21.1 | 0 | 3.1 | 2018-08-06 | 32.3 | 0 | 14.3 | 2017-08-06 | 21.8 | 0 | 3.8 | 2016-08-06 | 27.8 | 0 | 9.8 | 0 | 8.66
2025-08-06 | 27.8 | 0 | 9.8 | 2024-08-06 | 22.8 | 0 | 4.8 | 2023-08-06 | 25.5 | 0 | 7.5 | 2022-08-06 | 31.6 | 0 | 13.6 | 2021-08-06 | 28.3 | 0 | 10.3 | 2020-08-06 | 25.2 | 0 | 7.2 | 2019-08-06 | 20.9 | 0 | 2.9 | 2018-08-06 | 29.4 | 0 | 11.4 | 2017-08-06 | 21.9 | 0 | 3.9 | 2016-08-06 | 28 | 0 | 10 | 0 | 8.14
2025-08-06 | 27.6 | 0 | 9.6 | 2024-08-06 | 22.3 | 0 | 4.3 | 2023-08-06 | 24.9 | 0 | 6.9 | 2022-08-06 | 31.2 | 0 | 13.2 | 2021-08-06 | 28.4 | 0 | 10.4 | 2020-08-06 | 24.9 | 0 | 6.9 | 2019-08-06 | 21.3 | 0 | 3.3 | 2018-08-06 | 25.8 | 0 | 7.8 | 2017-08-06 | 21.6 | 0 | 3.6 | 2016-08-06 | 27.4 | 0 | 9.4 | 0 | 7.54
2025-08-06 | 26 | 0 | 8 | 2024-08-06 | 21.2 | 0 | 3.2 | 2023-08-06 | 23.6 | 0 | 5.6 | 2022-08-06 | 29.4 | 0 | 11.4 | 2021-08-06 | 27 | 0 | 9 | 2020-08-06 | 24 | 0 | 6 | 2019-08-06 | 21.1 | 0 | 3.1 | 2018-08-06 | 22.9 | 0 | 4.9 | 2017-08-06 | 20.5 | 0 | 2.5 | 2016-08-06 | 26.3 | 0 | 8.3 | 0 | 6.2
2025-08-06 | 23.5 | 0 | 5.5 | 2024-08-06 | 21.1 | 0 | 3.1 | 2023-08-06 | 21.5 | 0 | 3.5 | 2022-08-06 | 27.9 | 0 | 9.9 | 2021-08-06 | 25 | 0 | 7 | 2020-08-06 | 20.9 | 0 | 2.9 | 2019-08-06 | 20.7 | 0 | 2.7 | 2018-08-06 | 21.6 | 0 | 3.6 | 2017-08-06 | 17.7 | 0.3 | 0 | 2016-08-06 | 24.8 | 0 | 6.8 | 0.03 | 4.5
2025-08-06 | 21.2 | 0 | 3.2 | 2024-08-06 | 17.6 | 0.4 | 0 | 2023-08-06 | 21.3 | 0 | 3.3 | 2022-08-06 | 26.6 | 0 | 8.6 | 2021-08-06 | 22.3 | 0 | 4.3 | 2020-08-06 | 18.6 | 0 | 0.6 | 2019-08-06 | 19.7 | 0 | 1.7 | 2018-08-06 | 21.1 | 0 | 3.1 | 2017-08-06 | 17.4 | 0.6 | 0 | 2016-08-06 | 23.5 | 0 | 5.5 | 0.1 | 3.03
2025-08-06 | 20 | 0 | 2 | 2024-08-06 | 15.7 | 2.3 | 0 | 2023-08-06 | 19.2 | 0 | 1.2 | 2022-08-06 | 25.6 | 0 | 7.6 | 2021-08-06 | 20.6 | 0 | 2.6 | 2020-08-06 | 18.1 | 0 | 0.1 | 2019-08-06 | 19.2 | 0 | 1.2 | 2018-08-06 | 21.1 | 0 | 3.1 | 2017-08-06 | 17.1 | 0.9 | 0 | 2016-08-06 | 21.8 | 0 | 3.8 | 0.32 | 2.16
2025-08-06 | 20.2 | 0 | 2.2 | 2024-08-06 | 15.2 | 2.8 | 0 | 2023-08-06 | 19.8 | 0 | 1.8 | 2022-08-06 | 24.9 | 0 | 6.9 | 2021-08-06 | 20.4 | 0 | 2.4 | 2020-08-06 | 18.2 | 0 | 0.2 | 2019-08-06 | 19.1 | 0 | 1.1 | 2018-08-06 | 20.7 | 0 | 2.7 | 2017-08-06 | 16.4 | 1.6 | 0 | 2016-08-06 | 19.6 | 0 | 1.6 | 0.44 | 1.89
2025-08-06 | 20.3 | 0 | 2.3 | 2024-08-06 | 16.4 | 1.6 | 0 | 2023-08-06 | 18.7 | 0 | 0.7 | 2022-08-06 | 24.4 | 0 | 6.4 | 2021-08-06 | 19.6 | 0 | 1.6 | 2020-08-06 | 16.5 | 1.5 | 0 | 2019-08-06 | 18.4 | 0 | 0.4 | 2018-08-06 | 21.1 | 0 | 3.1 | 2017-08-06 | 14.9 | 3.1 | 0 | 2016-08-06 | 19 | 0 | 1 | 0.62 | 1.55
2025-08-07 | 18.9 | 0 | 0.9 | 2024-08-07 | 12.5 | 5.5 | 0 | 2023-08-07 | 18 | 0 | 0 | 2022-08-07 | 24 | 0 | 6 | 2021-08-07 | 19.9 | 0 | 1.9 | 2020-08-07 | 16.1 | 1.9 | 0 | 2019-08-07 | 18.3 | 0 | 0.3 | 2018-08-07 | 21.5 | 0 | 3.5 | 2017-08-07 | 12.9 | 5.1 | 0 | 2016-08-07 | 18.9 | 0 | 0.9 | 1.25 | 1.35
2025-08-07 | 18.2 | 0 | 0.2 | 2024-08-07 | 14.8 | 3.2 | 0 | 2023-08-07 | 17.1 | 0.9 | 0 | 2022-08-07 | 23.9 | 0 | 5.9 | 2021-08-07 | 19.8 | 0 | 1.8 | 2020-08-07 | 15 | 3 | 0 | 2019-08-07 | 18.3 | 0 | 0.3 | 2018-08-07 | 21.1 | 0 | 3.1 | 2017-08-07 | 13 | 5 | 0 | 2016-08-07 | 16.3 | 1.7 | 0 | 1.38 | 1.13
2025-08-07 | 15.9 | 2.1 | 0 | 2024-08-07 | 14.9 | 3.1 | 0 | 2023-08-07 | 17.6 | 0.4 | 0 | 2022-08-07 | 23.4 | 0 | 5.4 | 2021-08-07 | 19.5 | 0 | 1.5 | 2020-08-07 | 13.4 | 4.6 | 0 | 2019-08-07 | 17.3 | 0.7 | 0 | 2018-08-07 | 21.1 | 0 | 3.1 | 2017-08-07 | 11.3 | 6.7 | 0 | 2016-08-07 | 19 | 0 | 1 | 1.76 | 1.1
2025-08-07 | 14.7 | 3.3 | 0 | 2024-08-07 | 14.8 | 3.2 | 0 | 2023-08-07 | 16.4 | 1.6 | 0 | 2022-08-07 | 23.2 | 0 | 5.2 | 2021-08-07 | 17 | 1 | 0 | 2020-08-07 | 13.9 | 4.1 | 0 | 2019-08-07 | 18.8 | 0 | 0.8 | 2018-08-07 | 21 | 0 | 3 | 2017-08-07 | 10.6 | 7.4 | 0 | 2016-08-07 | 18.2 | 0 | 0.2 | 2.06 | 0.92
2025-08-07 | 14.7 | 3.3 | 0 | 2024-08-07 | 14.2 | 3.8 | 0 | 2023-08-07 | 16.7 | 1.3 | 0 | 2022-08-07 | 22.6 | 0 | 4.6 | 2021-08-07 | 15.5 | 2.5 | 0 | 2020-08-07 | 12.2 | 5.8 | 0 | 2019-08-07 | 19.2 | 0 | 1.2 | 2018-08-07 | 20.9 | 0 | 2.9 | 2017-08-07 | 11 | 7 | 0 | 2016-08-07 | 15.9 | 2.1 | 0 | 2.58 | 0.87
2025-08-07 | 14.1 | 3.9 | 0 | 2024-08-07 | 13.7 | 4.3 | 0 | 2023-08-07 | 16.8 | 1.2 | 0 | 2022-08-07 | 22 | 0 | 4 | 2021-08-07 | 17.2 | 0.8 | 0 | 2020-08-07 | 12.3 | 5.7 | 0 | 2019-08-07 | 19.3 | 0 | 1.3 | 2018-08-07 | 20.6 | 0 | 2.6 | 2017-08-07 | 11.1 | 6.9 | 0 | 2016-08-07 | 16.3 | 1.7 | 0 | 2.45 | 0.79
2025-08-07 | 15.8 | 2.2 | 0 | 2024-08-07 | 14.8 | 3.2 | 0 | 2023-08-07 | 17.1 | 0.9 | 0 | 2022-08-07 | 22.8 | 0 | 4.8 | 2021-08-07 | 18.2 | 0 | 0.2 | 2020-08-07 | 14.4 | 3.6 | 0 | 2019-08-07 | 19.5 | 0 | 1.5 | 2018-08-07 | 20.1 | 0 | 2.1 | 2017-08-07 | 12.4 | 5.6 | 0 | 2016-08-07 | 17.6 | 0.4 | 0 | 1.59 | 0.86
2025-08-07 | 18.2 | 0 | 0.2 | 2024-08-07 | 17.2 | 0.8 | 0 | 2023-08-07 | 17.5 | 0.5 | 0 | 2022-08-07 | 24.8 | 0 | 6.8 | 2021-08-07 | 19 | 0 | 1 | 2020-08-07 | 16.3 | 1.7 | 0 | 2019-08-07 | 19.8 | 0 | 1.8 | 2018-08-07 | 20.3 | 0 | 2.3 | 2017-08-07 | 13.3 | 4.7 | 0 | 2016-08-07 | 19.4 | 0 | 1.4 | 0.77 | 1.35
2025-08-07 | 20 | 0 | 2 | 2024-08-07 | 19 | 0 | 1 | 2023-08-07 | 17.2 | 0.8 | 0 | 2022-08-07 | 26.2 | 0 | 8.2 | 2021-08-07 | 20.9 | 0 | 2.9 | 2020-08-07 | 18.7 | 0 | 0.7 | 2019-08-07 | 20.4 | 0 | 2.4 | 2018-08-07 | 20.6 | 0 | 2.6 | 2017-08-07 | 14.5 | 3.5 | 0 | 2016-08-07 | 20.6 | 0 | 2.6 | 0.43 | 2.24
2025-08-07 | 22.1 | 0 | 4.1 | 2024-08-07 | 20.8 | 0 | 2.8 | 2023-08-07 | 16.5 | 1.5 | 0 | 2022-08-07 | 28.3 | 0 | 10.3 | 2021-08-07 | 23 | 0 | 5 | 2020-08-07 | 21.4 | 0 | 3.4 | 2019-08-07 | 20.9 | 0 | 2.9 | 2018-08-07 | 22.3 | 0 | 4.3 | 2017-08-07 | 15.5 | 2.5 | 0 | 2016-08-07 | 23.3 | 0 | 5.3 | 0.4 | 3.81
2025-08-07 | 24.3 | 0 | 6.3 | 2024-08-07 | 22 | 0 | 4 | 2023-08-07 | 16.7 | 1.3 | 0 | 2022-08-07 | 29.6 | 0 | 11.6 | 2021-08-07 | 23.4 | 0 | 5.4 | 2020-08-07 | 23.5 | 0 | 5.5 | 2019-08-07 | 21.9 | 0 | 3.9 | 2018-08-07 | 23.3 | 0 | 5.3 | 2017-08-07 | 16.6 | 1.4 | 0 | 2016-08-07 | 24 | 0 | 6 | 0.27 | 4.8
2025-08-07 | 27.1 | 0 | 9.1 | 2024-08-07 | 22.4 | 0 | 4.4 | 2023-08-07 | 17.5 | 0.5 | 0 | 2022-08-07 | 30.2 | 0 | 12.2 | 2021-08-07 | 24.6 | 0 | 6.6 | 2020-08-07 | 24.6 | 0 | 6.6 | 2019-08-07 | 22.3 | 0 | 4.3 | 2018-08-07 | 25.5 | 0 | 7.5 | 2017-08-07 | 18.1 | 0 | 0.1 | 2016-08-07 | 25.2 | 0 | 7.2 | 0.05 | 5.8
2025-08-07 | 28 | 0 | 10 | 2024-08-07 | 23.5 | 0 | 5.5 | 2023-08-07 | 17.5 | 0.5 | 0 | 2022-08-07 | 30.4 | 0 | 12.4 | 2021-08-07 | 25.2 | 0 | 7.2 | 2020-08-07 | 25.4 | 0 | 7.4 | 2019-08-07 | 21.9 | 0 | 3.9 | 2018-08-07 | 26.4 | 0 | 8.4 | 2017-08-07 | 19.2 | 0 | 1.2 | 2016-08-07 | 26.6 | 0 | 8.6 | 0.05 | 6.46
2025-08-07 | 28.5 | 0 | 10.5 | 2024-08-07 | 23.9 | 0 | 5.9 | 2023-08-07 | 19.1 | 0 | 1.1 | 2022-08-07 | 24.9 | 0 | 6.9 | 2021-08-07 | 26.1 | 0 | 8.1 | 2020-08-07 | 25.8 | 0 | 7.8 | 2019-08-07 | 23.4 | 0 | 5.4 | 2018-08-07 | 26.2 | 0 | 8.2 | 2017-08-07 | 20.3 | 0 | 2.3 | 2016-08-07 | 25.6 | 0 | 7.6 | 0 | 6.38
2025-08-07 | 28.8 | 0 | 10.8 | 2024-08-07 | 24.6 | 0 | 6.6 | 2023-08-07 | 19 | 0 | 1 | 2022-08-07 | 29.3 | 0 | 11.3 | 2021-08-07 | 26 | 0 | 8 | 2020-08-07 | 26.9 | 0 | 8.9 | 2019-08-07 | 23.6 | 0 | 5.6 | 2018-08-07 | 27.5 | 0 | 9.5 | 2017-08-07 | 21.3 | 0 | 3.3 | 2016-08-07 | 27 | 0 | 9 | 0 | 7.4
2025-08-07 | 29.1 | 0 | 11.1 | 2024-08-07 | 24.8 | 0 | 6.8 | 2023-08-07 | 19.5 | 0 | 1.5 | 2022-08-07 | 23.6 | 0 | 5.6 | 2021-08-07 | 26.3 | 0 | 8.3 | 2020-08-07 | 26.9 | 0 | 8.9 | 2019-08-07 | 24.6 | 0 | 6.6 | 2018-08-07 | 27.9 | 0 | 9.9 | 2017-08-07 | 20.8 | 0 | 2.8 | 2016-08-07 | 27.3 | 0 | 9.3 | 0 | 7.08
2025-08-07 | 29.5 | 0 | 11.5 | 2024-08-07 | 24.4 | 0 | 6.4 | 2023-08-07 | 19.8 | 0 | 1.8 | 2022-08-07 | 25.3 | 0 | 7.3 | 2021-08-07 | 27.4 | 0 | 9.4 | 2020-08-07 | 26.7 | 0 | 8.7 | 2019-08-07 | 24.4 | 0 | 6.4 | 2018-08-07 | 27.6 | 0 | 9.6 | 2017-08-07 | 19.7 | 0 | 1.7 | 2016-08-07 | 26.9 | 0 | 8.9 | 0 | 7.17
2025-08-07 | 26.9 | 0 | 8.9 | 2024-08-07 | 24.3 | 0 | 6.3 | 2023-08-07 | 20.1 | 0 | 2.1 | 2022-08-07 | 24.5 | 0 | 6.5 | 2021-08-07 | 23.5 | 0 | 5.5 | 2020-08-07 | 25.9 | 0 | 7.9 | 2019-08-07 | 24.8 | 0 | 6.8 | 2018-08-07 | 26.6 | 0 | 8.6 | 2017-08-07 | 19.2 | 0 | 1.2 | 2016-08-07 | 26 | 0 | 8 | 0 | 6.18
2025-08-07 | 26 | 0 | 8 | 2024-08-07 | 23 | 0 | 5 | 2023-08-07 | 19.4 | 0 | 1.4 | 2022-08-07 | 23.4 | 0 | 5.4 | 2021-08-07 | 23.2 | 0 | 5.2 | 2020-08-07 | 25.3 | 0 | 7.3 | 2019-08-07 | 23.6 | 0 | 5.6 | 2018-08-07 | 26 | 0 | 8 | 2017-08-07 | 18.4 | 0 | 0.4 | 2016-08-07 | 25 | 0 | 7 | 0 | 5.33
2025-08-07 | 24.6 | 0 | 6.6 | 2024-08-07 | 20.7 | 0 | 2.7 | 2023-08-07 | 18.5 | 0 | 0.5 | 2022-08-07 | 23 | 0 | 5 | 2021-08-07 | 22.5 | 0 | 4.5 | 2020-08-07 | 23.1 | 0 | 5.1 | 2019-08-07 | 22 | 0 | 4 | 2018-08-07 | 24.9 | 0 | 6.9 | 2017-08-07 | 17.3 | 0.7 | 0 | 2016-08-07 | 23.4 | 0 | 5.4 | 0.07 | 4.07
2025-08-07 | 22.5 | 0 | 4.5 | 2024-08-07 | 18.7 | 0 | 0.7 | 2023-08-07 | 18.4 | 0 | 0.4 | 2022-08-07 | 22.8 | 0 | 4.8 | 2021-08-07 | 22.8 | 0 | 4.8 | 2020-08-07 | 20.6 | 0 | 2.6 | 2019-08-07 | 20.7 | 0 | 2.7 | 2018-08-07 | 23.8 | 0 | 5.8 | 2017-08-07 | 16.5 | 1.5 | 0 | 2016-08-07 | 22.1 | 0 | 4.1 | 0.15 | 3.04
2025-08-07 | 22.4 | 0 | 4.4 | 2024-08-07 | 16.2 | 1.8 | 0 | 2023-08-07 | 18.2 | 0 | 0.2 | 2022-08-07 | 22.6 | 0 | 4.6 | 2021-08-07 | 21.7 | 0 | 3.7 | 2020-08-07 | 19.2 | 0 | 1.2 | 2019-08-07 | 19.5 | 0 | 1.5 | 2018-08-07 | 22.8 | 0 | 4.8 | 2017-08-07 | 15.7 | 2.3 | 0 | 2016-08-07 | 21.1 | 0 | 3.1 | 0.41 | 2.35
2025-08-07 | 21.2 | 0 | 3.2 | 2024-08-07 | 14.3 | 3.7 | 0 | 2023-08-07 | 18.2 | 0 | 0.2 | 2022-08-07 | 21.7 | 0 | 3.7 | 2021-08-07 | 21 | 0 | 3 | 2020-08-07 | 18.2 | 0 | 0.2 | 2019-08-07 | 19.7 | 0 | 1.7 | 2018-08-07 | 21.3 | 0 | 3.3 | 2017-08-07 | 15.5 | 2.5 | 0 | 2016-08-07 | 18.5 | 0 | 0.5 | 0.62 | 1.58
2025-08-07 | 18.4 | 0 | 0.4 | 2024-08-07 | 15.1 | 2.9 | 0 | 2023-08-07 | 17.9 | 0.1 | 0 | 2022-08-07 | 21.5 | 0 | 3.5 | 2021-08-07 | 20.2 | 0 | 2.2 | 2020-08-07 | 16.9 | 1.1 | 0 | 2019-08-07 | 19.1 | 0 | 1.1 | 2018-08-07 | 21 | 0 | 3 | 2017-08-07 | 15 | 3 | 0 | 2016-08-07 | 16.7 | 1.3 | 0 | 0.84 | 1.02
2025-08-08 | 20.3 | 0 | 2.3 | 2024-08-08 | 14.6 | 3.4 | 0 | 2023-08-08 | 18.2 | 0 | 0.2 | 2022-08-08 | 20.9 | 0 | 2.9 | 2021-08-08 | 18.8 | 0 | 0.8 | 2020-08-08 | 18.2 | 0 | 0.2 | 2019-08-08 | 19.3 | 0 | 1.3 | 2018-08-08 | 21.2 | 0 | 3.2 | 2017-08-08 | 14.8 | 3.2 | 0 | 2016-08-08 | 15.7 | 2.3 | 0 | 0.89 | 1.09
2025-08-08 | 17 | 1 | 0 | 2024-08-08 | 13.2 | 4.8 | 0 | 2023-08-08 | 18.6 | 0 | 0.6 | 2022-08-08 | 20.6 | 0 | 2.6 | 2021-08-08 | 18.4 | 0 | 0.4 | 2020-08-08 | 15.5 | 2.5 | 0 | 2019-08-08 | 18.9 | 0 | 0.9 | 2018-08-08 | 20.3 | 0 | 2.3 | 2017-08-08 | 14.8 | 3.2 | 0 | 2016-08-08 | 14.5 | 3.5 | 0 | 1.5 | 0.68
2025-08-08 | 17.5 | 0.5 | 0 | 2024-08-08 | 12.9 | 5.1 | 0 | 2023-08-08 | 18.6 | 0 | 0.6 | 2022-08-08 | 20.2 | 0 | 2.2 | 2021-08-08 | 18.3 | 0 | 0.3 | 2020-08-08 | 15.6 | 2.4 | 0 | 2019-08-08 | 18.9 | 0 | 0.9 | 2018-08-08 | 20.5 | 0 | 2.5 | 2017-08-08 | 14.8 | 3.2 | 0 | 2016-08-08 | 13.5 | 4.5 | 0 | 1.57 | 0.65
2025-08-08 | 18 | 0 | 0 | 2024-08-08 | 12.1 | 5.9 | 0 | 2023-08-08 | 18.1 | 0 | 0.1 | 2022-08-08 | 19.2 | 0 | 1.2 | 2021-08-08 | 18.1 | 0 | 0.1 | 2020-08-08 | 15.1 | 2.9 | 0 | 2019-08-08 | 18 | 0 | 0 | 2018-08-08 | 20.4 | 0 | 2.4 | 2017-08-08 | 13.9 | 4.1 | 0 | 2016-08-08 | 13.2 | 4.8 | 0 | 1.77 | 0.38
2025-08-08 | 15.8 | 2.2 | 0 | 2024-08-08 | 12.2 | 5.8 | 0 | 2023-08-08 | 18 | 0 | 0 | 2022-08-08 | 16.2 | 1.8 | 0 | 2021-08-08 | 18.7 | 0 | 0.7 | 2020-08-08 | 15.1 | 2.9 | 0 | 2019-08-08 | 18.4 | 0 | 0.4 | 2018-08-08 | 20.4 | 0 | 2.4 | 2017-08-08 | 12.7 | 5.3 | 0 | 2016-08-08 | 12.8 | 5.2 | 0 | 2.32 | 0.35
2025-08-08 | 14.4 | 3.6 | 0 | 2024-08-08 | 12.3 | 5.7 | 0 | 2023-08-08 | 18 | 0 | 0 | 2022-08-08 | 16 | 2 | 0 | 2021-08-08 | 18.4 | 0 | 0.4 | 2020-08-08 | 14.1 | 3.9 | 0 | 2019-08-08 | 18.7 | 0 | 0.7 | 2018-08-08 | 20.2 | 0 | 2.2 | 2017-08-08 | 13.8 | 4.2 | 0 | 2016-08-08 | 12.4 | 5.6 | 0 | 2.5 | 0.33
2025-08-08 | 17 | 1 | 0 | 2024-08-08 | 14.1 | 3.9 | 0 | 2023-08-08 | 18.2 | 0 | 0.2 | 2022-08-08 | 15.7 | 2.3 | 0 | 2021-08-08 | 18.8 | 0 | 0.8 | 2020-08-08 | 15.8 | 2.2 | 0 | 2019-08-08 | 18.6 | 0 | 0.6 | 2018-08-08 | 20.1 | 0 | 2.1 | 2017-08-08 | 13.9 | 4.1 | 0 | 2016-08-08 | 14.2 | 3.8 | 0 | 1.73 | 0.37
2025-08-08 | 18.8 | 0 | 0.8 | 2024-08-08 | 15.6 | 2.4 | 0 | 2023-08-08 | 18.6 | 0 | 0.6 | 2022-08-08 | 15.8 | 2.2 | 0 | 2021-08-08 | 19.8 | 0 | 1.8 | 2020-08-08 | 18.9 | 0 | 0.9 | 2019-08-08 | 19.1 | 0 | 1.1 | 2018-08-08 | 20.5 | 0 | 2.5 | 2017-08-08 | 15.3 | 2.7 | 0 | 2016-08-08 | 17.9 | 0.1 | 0 | 0.74 | 0.77
2025-08-08 | 20.6 | 0 | 2.6 | 2024-08-08 | 17.9 | 0.1 | 0 | 2023-08-08 | 19.8 | 0 | 1.8 | 2022-08-08 | 15.7 | 2.3 | 0 | 2021-08-08 | 21.4 | 0 | 3.4 | 2020-08-08 | 21.5 | 0 | 3.5 | 2019-08-08 | 21.6 | 0 | 3.6 | 2018-08-08 | 20.7 | 0 | 2.7 | 2017-08-08 | 16.4 | 1.6 | 0 | 2016-08-08 | 20.8 | 0 | 2.8 | 0.4 | 2.04
2025-08-08 | 23.6 | 0 | 5.6 | 2024-08-08 | 19.2 | 0 | 1.2 | 2023-08-08 | 20.3 | 0 | 2.3 | 2022-08-08 | 15.5 | 2.5 | 0 | 2021-08-08 | 22.2 | 0 | 4.2 | 2020-08-08 | 23.6 | 0 | 5.6 | 2019-08-08 | 23.5 | 0 | 5.5 | 2018-08-08 | 21.1 | 0 | 3.1 | 2017-08-08 | 18.7 | 0 | 0.7 | 2016-08-08 | 22.8 | 0 | 4.8 | 0.25 | 3.3
2025-08-08 | 26.3 | 0 | 8.3 | 2024-08-08 | 21.7 | 0 | 3.7 | 2023-08-08 | 20.3 | 0 | 2.3 | 2022-08-08 | 15.2 | 2.8 | 0 | 2021-08-08 | 23.9 | 0 | 5.9 | 2020-08-08 | 25.4 | 0 | 7.4 | 2019-08-08 | 26 | 0 | 8 | 2018-08-08 | 22.1 | 0 | 4.1 | 2017-08-08 | 20.9 | 0 | 2.9 | 2016-08-08 | 24.9 | 0 | 6.9 | 0.28 | 4.95
2025-08-08 | 28 | 0 | 10 | 2024-08-08 | 22.9 | 0 | 4.9 | 2023-08-08 | 20.8 | 0 | 2.8 | 2022-08-08 | 15.3 | 2.7 | 0 | 2021-08-08 | 25.1 | 0 | 7.1 | 2020-08-08 | 26 | 0 | 8 | 2019-08-08 | 26.8 | 0 | 8.8 | 2018-08-08 | 23.3 | 0 | 5.3 | 2017-08-08 | 22.4 | 0 | 4.4 | 2016-08-08 | 27.6 | 0 | 9.6 | 0.27 | 6.09
2025-08-08 | 29.3 | 0 | 11.3 | 2024-08-08 | 24.2 | 0 | 6.2 | 2023-08-08 | 21.1 | 0 | 3.1 | 2022-08-08 | 15.8 | 2.2 | 0 | 2021-08-08 | 25.7 | 0 | 7.7 | 2020-08-08 | 27.2 | 0 | 9.2 | 2019-08-08 | 27.6 | 0 | 9.6 | 2018-08-08 | 24.3 | 0 | 6.3 | 2017-08-08 | 23.1 | 0 | 5.1 | 2016-08-08 | 28.7 | 0 | 10.7 | 0.22 | 6.92
2025-08-08 | 30.6 | 0 | 12.6 | 2024-08-08 | 25.5 | 0 | 7.5 | 2023-08-08 | 21.6 | 0 | 3.6 | 2022-08-08 | 16.3 | 1.7 | 0 | 2021-08-08 | 27 | 0 | 9 | 2020-08-08 | 28.4 | 0 | 10.4 | 2019-08-08 | 27 | 0 | 9 | 2018-08-08 | 24.9 | 0 | 6.9 | 2017-08-08 | 23.5 | 0 | 5.5 | 2016-08-08 | 29.6 | 0 | 11.6 | 0.17 | 7.61
2025-08-08 | 31.2 | 0 | 13.2 | 2024-08-08 | 25.2 | 0 | 7.2 | 2023-08-08 | 21.8 | 0 | 3.8 | 2022-08-08 | 16.4 | 1.6 | 0 | 2021-08-08 | 26.6 | 0 | 8.6 | 2020-08-08 | 27 | 0 | 9 | 2019-08-08 | 26.8 | 0 | 8.8 | 2018-08-08 | 23.7 | 0 | 5.7 | 2017-08-08 | 23.8 | 0 | 5.8 | 2016-08-08 | 30 | 0 | 12 | 0.16 | 7.41
2025-08-08 | 30.7 | 0 | 12.7 | 2024-08-08 | 24.6 | 0 | 6.6 | 2023-08-08 | 21.1 | 0 | 3.1 | 2022-08-08 | 16.8 | 1.2 | 0 | 2021-08-08 | 26.5 | 0 | 8.5 | 2020-08-08 | 27.3 | 0 | 9.3 | 2019-08-08 | 18.9 | 0 | 0.9 | 2018-08-08 | 22.6 | 0 | 4.6 | 2017-08-08 | 24.7 | 0 | 6.7 | 2016-08-08 | 29.9 | 0 | 11.9 | 0.12 | 6.43
2025-08-08 | 30.3 | 0 | 12.3 | 2024-08-08 | 24.3 | 0 | 6.3 | 2023-08-08 | 21.4 | 0 | 3.4 | 2022-08-08 | 16.3 | 1.7 | 0 | 2021-08-08 | 26.2 | 0 | 8.2 | 2020-08-08 | 27.6 | 0 | 9.6 | 2019-08-08 | 19.6 | 0 | 1.6 | 2018-08-08 | 21.7 | 0 | 3.7 | 2017-08-08 | 24.3 | 0 | 6.3 | 2016-08-08 | 29.9 | 0 | 11.9 | 0.17 | 6.33
2025-08-08 | 29.7 | 0 | 11.7 | 2024-08-08 | 21.9 | 0 | 3.9 | 2023-08-08 | 20.4 | 0 | 2.4 | 2022-08-08 | 16.5 | 1.5 | 0 | 2021-08-08 | 25.4 | 0 | 7.4 | 2020-08-08 | 28.5 | 0 | 10.5 | 2019-08-08 | 19.7 | 0 | 1.7 | 2018-08-08 | 21.5 | 0 | 3.5 | 2017-08-08 | 23.9 | 0 | 5.9 | 2016-08-08 | 29.7 | 0 | 11.7 | 0.15 | 5.87
2025-08-08 | 28.1 | 0 | 10.1 | 2024-08-08 | 21 | 0 | 3 | 2023-08-08 | 20 | 0 | 2 | 2022-08-08 | 16.5 | 1.5 | 0 | 2021-08-08 | 24.9 | 0 | 6.9 | 2020-08-08 | 26.7 | 0 | 8.7 | 2019-08-08 | 21.5 | 0 | 3.5 | 2018-08-08 | 22.3 | 0 | 4.3 | 2017-08-08 | 22.8 | 0 | 4.8 | 2016-08-08 | 28.5 | 0 | 10.5 | 0.15 | 5.38
2025-08-08 | 26.1 | 0 | 8.1 | 2024-08-08 | 20.2 | 0 | 2.2 | 2023-08-08 | 19.8 | 0 | 1.8 | 2022-08-08 | 16.2 | 1.8 | 0 | 2021-08-08 | 23.9 | 0 | 5.9 | 2020-08-08 | 23.8 | 0 | 5.8 | 2019-08-08 | 20.2 | 0 | 2.2 | 2018-08-08 | 22.2 | 0 | 4.2 | 2017-08-08 | 20.3 | 0 | 2.3 | 2016-08-08 | 26.4 | 0 | 8.4 | 0.18 | 4.09
2025-08-08 | 23.6 | 0 | 5.6 | 2024-08-08 | 18.8 | 0 | 0.8 | 2023-08-08 | 19.4 | 0 | 1.4 | 2022-08-08 | 15.5 | 2.5 | 0 | 2021-08-08 | 23.2 | 0 | 5.2 | 2020-08-08 | 23.3 | 0 | 5.3 | 2019-08-08 | 18 | 0 | 0 | 2018-08-08 | 21.6 | 0 | 3.6 | 2017-08-08 | 18.4 | 0 | 0.4 | 2016-08-08 | 25.3 | 0 | 7.3 | 0.25 | 2.96
2025-08-08 | 22.6 | 0 | 4.6 | 2024-08-08 | 18.8 | 0 | 0.8 | 2023-08-08 | 19.5 | 0 | 1.5 | 2022-08-08 | 15 | 3 | 0 | 2021-08-08 | 22.2 | 0 | 4.2 | 2020-08-08 | 23.1 | 0 | 5.1 | 2019-08-08 | 17.4 | 0.6 | 0 | 2018-08-08 | 21.2 | 0 | 3.2 | 2017-08-08 | 18.4 | 0 | 0.4 | 2016-08-08 | 21.6 | 0 | 3.6 | 0.36 | 2.34
2025-08-08 | 21.9 | 0 | 3.9 | 2024-08-08 | 19 | 0 | 1 | 2023-08-08 | 18.2 | 0 | 0.2 | 2022-08-08 | 15.1 | 2.9 | 0 | 2021-08-08 | 21.4 | 0 | 3.4 | 2020-08-08 | 21.5 | 0 | 3.5 | 2019-08-08 | 16.9 | 1.1 | 0 | 2018-08-08 | 21.5 | 0 | 3.5 | 2017-08-08 | 19 | 0 | 1 | 2016-08-08 | 20.4 | 0 | 2.4 | 0.4 | 1.89
2025-08-08 | 21.7 | 0 | 3.7 | 2024-08-08 | 19 | 0 | 1 | 2023-08-08 | 17.7 | 0.3 | 0 | 2022-08-08 | 15.3 | 2.7 | 0 | 2021-08-08 | 20.4 | 0 | 2.4 | 2020-08-08 | 20.5 | 0 | 2.5 | 2019-08-08 | 16.5 | 1.5 | 0 | 2018-08-08 | 20.3 | 0 | 2.3 | 2017-08-08 | 16.7 | 1.3 | 0 | 2016-08-08 | 18 | 0 | 0 | 0.58 | 1.19
2025-08-09 | 19.2 | 0 | 1.2 | 2024-08-09 | 19.1 | 0 | 1.1 | 2023-08-09 | 17.5 | 0.5 | 0 | 2022-08-09 | 15.3 | 2.7 | 0 | 2021-08-09 | 20.1 | 0 | 2.1 | 2020-08-09 | 20.8 | 0 | 2.8 | 2019-08-09 | 15.7 | 2.3 | 0 | 2018-08-09 | 19.7 | 0 | 1.7 | 2017-08-09 | 15.6 | 2.4 | 0 | 2016-08-09 | 16.6 | 1.4 | 0 | 0.93 | 0.89
2025-08-09 | 19.3 | 0 | 1.3 | 2024-08-09 | 19 | 0 | 1 | 2023-08-09 | 16.2 | 1.8 | 0 | 2022-08-09 | 14.9 | 3.1 | 0 | 2021-08-09 | 19.9 | 0 | 1.9 | 2020-08-09 | 19.7 | 0 | 1.7 | 2019-08-09 | 15.2 | 2.8 | 0 | 2018-08-09 | 19.3 | 0 | 1.3 | 2017-08-09 | 16.1 | 1.9 | 0 | 2016-08-09 | 18.1 | 0 | 0.1 | 0.96 | 0.73
2025-08-09 | 19.6 | 0 | 1.6 | 2024-08-09 | 18.9 | 0 | 0.9 | 2023-08-09 | 16.8 | 1.2 | 0 | 2022-08-09 | 14.5 | 3.5 | 0 | 2021-08-09 | 19.8 | 0 | 1.8 | 2020-08-09 | 19.3 | 0 | 1.3 | 2019-08-09 | 15.1 | 2.9 | 0 | 2018-08-09 | 18.9 | 0 | 0.9 | 2017-08-09 | 15.7 | 2.3 | 0 | 2016-08-09 | 16.4 | 1.6 | 0 | 1.15 | 0.65
2025-08-09 | 19.4 | 0 | 1.4 | 2024-08-09 | 18.9 | 0 | 0.9 | 2023-08-09 | 15.9 | 2.1 | 0 | 2022-08-09 | 14.3 | 3.7 | 0 | 2021-08-09 | 19.8 | 0 | 1.8 | 2020-08-09 | 19.1 | 0 | 1.1 | 2019-08-09 | 14.3 | 3.7 | 0 | 2018-08-09 | 18.7 | 0 | 0.7 | 2017-08-09 | 14.9 | 3.1 | 0 | 2016-08-09 | 14.6 | 3.4 | 0 | 1.6 | 0.59
2025-08-09 | 19.2 | 0 | 1.2 | 2024-08-09 | 18.9 | 0 | 0.9 | 2023-08-09 | 15.1 | 2.9 | 0 | 2022-08-09 | 14.3 | 3.7 | 0 | 2021-08-09 | 19.9 | 0 | 1.9 | 2020-08-09 | 18.9 | 0 | 0.9 | 2019-08-09 | 14.4 | 3.6 | 0 | 2018-08-09 | 19.1 | 0 | 1.1 | 2017-08-09 | 14.9 | 3.1 | 0 | 2016-08-09 | 13.4 | 4.6 | 0 | 1.79 | 0.6
2025-08-09 | 18.9 | 0 | 0.9 | 2024-08-09 | 18.9 | 0 | 0.9 | 2023-08-09 | 15 | 3 | 0 | 2022-08-09 | 14.8 | 3.2 | 0 | 2021-08-09 | 20.1 | 0 | 2.1 | 2020-08-09 | 18.7 | 0 | 0.7 | 2019-08-09 | 13.5 | 4.5 | 0 | 2018-08-09 | 18.3 | 0 | 0.3 | 2017-08-09 | 14 | 4 | 0 | 2016-08-09 | 14.2 | 3.8 | 0 | 1.85 | 0.49
2025-08-09 | 19.8 | 0 | 1.8 | 2024-08-09 | 19 | 0 | 1 | 2023-08-09 | 16.2 | 1.8 | 0 | 2022-08-09 | 15.1 | 2.9 | 0 | 2021-08-09 | 20.2 | 0 | 2.2 | 2020-08-09 | 19 | 0 | 1 | 2019-08-09 | 14.4 | 3.6 | 0 | 2018-08-09 | 18.7 | 0 | 0.7 | 2017-08-09 | 16.5 | 1.5 | 0 | 2016-08-09 | 15.7 | 2.3 | 0 | 1.21 | 0.67
2025-08-09 | 21.8 | 0 | 3.8 | 2024-08-09 | 19.4 | 0 | 1.4 | 2023-08-09 | 17.6 | 0.4 | 0 | 2022-08-09 | 15.5 | 2.5 | 0 | 2021-08-09 | 20.9 | 0 | 2.9 | 2020-08-09 | 19.9 | 0 | 1.9 | 2019-08-09 | 16.6 | 1.4 | 0 | 2018-08-09 | 19.8 | 0 | 1.8 | 2017-08-09 | 17.6 | 0.4 | 0 | 2016-08-09 | 18 | 0 | 0 | 0.47 | 1.18
2025-08-09 | 23.9 | 0 | 5.9 | 2024-08-09 | 20 | 0 | 2 | 2023-08-09 | 19.4 | 0 | 1.4 | 2022-08-09 | 16 | 2 | 0 | 2021-08-09 | 21.8 | 0 | 3.8 | 2020-08-09 | 21.5 | 0 | 3.5 | 2019-08-09 | 18.7 | 0 | 0.7 | 2018-08-09 | 21.1 | 0 | 3.1 | 2017-08-09 | 19 | 0 | 1 | 2016-08-09 | 20.3 | 0 | 2.3 | 0.2 | 2.37
2025-08-09 | 26.4 | 0 | 8.4 | 2024-08-09 | 20.7 | 0 | 2.7 | 2023-08-09 | 21.2 | 0 | 3.2 | 2022-08-09 | 16.9 | 1.1 | 0 | 2021-08-09 | 23.6 | 0 | 5.6 | 2020-08-09 | 23.2 | 0 | 5.2 | 2019-08-09 | 20.4 | 0 | 2.4 | 2018-08-09 | 22 | 0 | 4 | 2017-08-09 | 20 | 0 | 2 | 2016-08-09 | 22.7 | 0 | 4.7 | 0.11 | 3.82
2025-08-09 | 29.5 | 0 | 11.5 | 2024-08-09 | 20.4 | 0 | 2.4 | 2023-08-09 | 23.1 | 0 | 5.1 | 2022-08-09 | 16.4 | 1.6 | 0 | 2021-08-09 | 25.4 | 0 | 7.4 | 2020-08-09 | 22.7 | 0 | 4.7 | 2019-08-09 | 20.6 | 0 | 2.6 | 2018-08-09 | 23.5 | 0 | 5.5 | 2017-08-09 | 21.1 | 0 | 3.1 | 2016-08-09 | 26.2 | 0 | 8.2 | 0.16 | 5.05
2025-08-09 | 30.3 | 0 | 12.3 | 2024-08-09 | 20.9 | 0 | 2.9 | 2023-08-09 | 24.9 | 0 | 6.9 | 2022-08-09 | 17.4 | 0.6 | 0 | 2021-08-09 | 27.3 | 0 | 9.3 | 2020-08-09 | 22.9 | 0 | 4.9 | 2019-08-09 | 21.3 | 0 | 3.3 | 2018-08-09 | 24.6 | 0 | 6.6 | 2017-08-09 | 21.6 | 0 | 3.6 | 2016-08-09 | 27.9 | 0 | 9.9 | 0.06 | 5.97
2025-08-09 | 31.3 | 0 | 13.3 | 2024-08-09 | 20.7 | 0 | 2.7 | 2023-08-09 | 26.4 | 0 | 8.4 | 2022-08-09 | 17.3 | 0.7 | 0 | 2021-08-09 | 28.1 | 0 | 10.1 | 2020-08-09 | 21.4 | 0 | 3.4 | 2019-08-09 | 21.1 | 0 | 3.1 | 2018-08-09 | 25.4 | 0 | 7.4 | 2017-08-09 | 22.3 | 0 | 4.3 | 2016-08-09 | 28.7 | 0 | 10.7 | 0.07 | 6.34
2025-08-09 | 32.3 | 0 | 14.3 | 2024-08-09 | 20.7 | 0 | 2.7 | 2023-08-09 | 26.9 | 0 | 8.9 | 2022-08-09 | 18.3 | 0 | 0.3 | 2021-08-09 | 29.3 | 0 | 11.3 | 2020-08-09 | 19.7 | 0 | 1.7 | 2019-08-09 | 18.3 | 0 | 0.3 | 2018-08-09 | 26.7 | 0 | 8.7 | 2017-08-09 | 23 | 0 | 5 | 2016-08-09 | 29.9 | 0 | 11.9 | 0 | 6.51
2025-08-09 | 33.1 | 0 | 15.1 | 2024-08-09 | 21.4 | 0 | 3.4 | 2023-08-09 | 27.5 | 0 | 9.5 | 2022-08-09 | 18.9 | 0 | 0.9 | 2021-08-09 | 30 | 0 | 12 | 2020-08-09 | 19.5 | 0 | 1.5 | 2019-08-09 | 23.8 | 0 | 5.8 | 2018-08-09 | 26.7 | 0 | 8.7 | 2017-08-09 | 23.9 | 0 | 5.9 | 2016-08-09 | 31.6 | 0 | 13.6 | 0 | 7.64
2025-08-09 | 32.3 | 0 | 14.3 | 2024-08-09 | 19.8 | 0 | 1.8 | 2023-08-09 | 27.8 | 0 | 9.8 | 2022-08-09 | 19.6 | 0 | 1.6 | 2021-08-09 | 30.5 | 0 | 12.5 | 2020-08-09 | 21 | 0 | 3 | 2019-08-09 | 24.4 | 0 | 6.4 | 2018-08-09 | 26.6 | 0 | 8.6 | 2017-08-09 | 23 | 0 | 5 | 2016-08-09 | 32.2 | 0 | 14.2 | 0 | 7.72
2025-08-09 | 32.6 | 0 | 14.6 | 2024-08-09 | 18.5 | 0 | 0.5 | 2023-08-09 | 26.4 | 0 | 8.4 | 2022-08-09 | 18.3 | 0 | 0.3 | 2021-08-09 | 30.4 | 0 | 12.4 | 2020-08-09 | 21.6 | 0 | 3.6 | 2019-08-09 | 23.4 | 0 | 5.4 | 2018-08-09 | 24.4 | 0 | 6.4 | 2017-08-09 | 22.9 | 0 | 4.9 | 2016-08-09 | 32.2 | 0 | 14.2 | 0 | 7.07
2025-08-09 | 32.5 | 0 | 14.5 | 2024-08-09 | 18.8 | 0 | 0.8 | 2023-08-09 | 26 | 0 | 8 | 2022-08-09 | 19.2 | 0 | 1.2 | 2021-08-09 | 29.1 | 0 | 11.1 | 2020-08-09 | 21.5 | 0 | 3.5 | 2019-08-09 | 21.9 | 0 | 3.9 | 2018-08-09 | 24.7 | 0 | 6.7 | 2017-08-09 | 22.9 | 0 | 4.9 | 2016-08-09 | 31.5 | 0 | 13.5 | 0 | 6.81
2025-08-09 | 30.6 | 0 | 12.6 | 2024-08-09 | 19.3 | 0 | 1.3 | 2023-08-09 | 25.8 | 0 | 7.8 | 2022-08-09 | 18.1 | 0 | 0.1 | 2021-08-09 | 28.2 | 0 | 10.2 | 2020-08-09 | 20.8 | 0 | 2.8 | 2019-08-09 | 20.7 | 0 | 2.7 | 2018-08-09 | 23.5 | 0 | 5.5 | 2017-08-09 | 22.3 | 0 | 4.3 | 2016-08-09 | 29.8 | 0 | 11.8 | 0 | 5.91
2025-08-09 | 28.5 | 0 | 10.5 | 2024-08-09 | 19.2 | 0 | 1.2 | 2023-08-09 | 23.7 | 0 | 5.7 | 2022-08-09 | 17.3 | 0.7 | 0 | 2021-08-09 | 26.3 | 0 | 8.3 | 2020-08-09 | 20.8 | 0 | 2.8 | 2019-08-09 | 19 | 0 | 1 | 2018-08-09 | 23 | 0 | 5 | 2017-08-09 | 21.2 | 0 | 3.2 | 2016-08-09 | 26.6 | 0 | 8.6 | 0.07 | 4.63
2025-08-09 | 26.6 | 0 | 8.6 | 2024-08-09 | 19 | 0 | 1 | 2023-08-09 | 22.6 | 0 | 4.6 | 2022-08-09 | 17.1 | 0.9 | 0 | 2021-08-09 | 24.1 | 0 | 6.1 | 2020-08-09 | 20.1 | 0 | 2.1 | 2019-08-09 | 16.5 | 1.5 | 0 | 2018-08-09 | 22.9 | 0 | 4.9 | 2017-08-09 | 18.9 | 0 | 0.9 | 2016-08-09 | 22.8 | 0 | 4.8 | 0.24 | 3.3
2025-08-09 | 26 | 0 | 8 | 2024-08-09 | 19 | 0 | 1 | 2023-08-09 | 20.4 | 0 | 2.4 | 2022-08-09 | 16.7 | 1.3 | 0 | 2021-08-09 | 23.2 | 0 | 5.2 | 2020-08-09 | 19.6 | 0 | 1.6 | 2019-08-09 | 16.6 | 1.4 | 0 | 2018-08-09 | 23.1 | 0 | 5.1 | 2017-08-09 | 18.9 | 0 | 0.9 | 2016-08-09 | 21.6 | 0 | 3.6 | 0.27 | 2.78
2025-08-09 | 25.3 | 0 | 7.3 | 2024-08-09 | 19.1 | 0 | 1.1 | 2023-08-09 | 20.1 | 0 | 2.1 | 2022-08-09 | 16.6 | 1.4 | 0 | 2021-08-09 | 23.1 | 0 | 5.1 | 2020-08-09 | 17.5 | 0.5 | 0 | 2019-08-09 | 16.2 | 1.8 | 0 | 2018-08-09 | 22 | 0 | 4 | 2017-08-09 | 16.7 | 1.3 | 0 | 2016-08-09 | 20.9 | 0 | 2.9 | 0.5 | 2.25
2025-08-09 | 24.5 | 0 | 6.5 | 2024-08-09 | 19 | 0 | 1 | 2023-08-09 | 19.6 | 0 | 1.6 | 2022-08-09 | 16.6 | 1.4 | 0 | 2021-08-09 | 23.2 | 0 | 5.2 | 2020-08-09 | 18 | 0 | 0 | 2019-08-09 | 15.7 | 2.3 | 0 | 2018-08-09 | 20.6 | 0 | 2.6 | 2017-08-09 | 15.8 | 2.2 | 0 | 2016-08-09 | 20.8 | 0 | 2.8 | 0.59 | 1.97
2025-08-10 | 24.3 | 0 | 6.3 | 2024-08-10 | 18.1 | 0 | 0.1 | 2023-08-10 | 18.9 | 0 | 0.9 | 2022-08-10 | 16.4 | 1.6 | 0 | 2021-08-10 | 22 | 0 | 4 | 2020-08-10 | 18.1 | 0 | 0.1 | 2019-08-10 | 16 | 2 | 0 | 2018-08-10 | 19.5 | 0 | 1.5 | 2017-08-10 | 15.8 | 2.2 | 0 | 2016-08-10 | 21.2 | 0 | 3.2 | 0.58 | 1.61
2025-08-10 | 23.9 | 0 | 5.9 | 2024-08-10 | 17.8 | 0.2 | 0 | 2023-08-10 | 17.3 | 0.7 | 0 | 2022-08-10 | 16.4 | 1.6 | 0 | 2021-08-10 | 22.2 | 0 | 4.2 | 2020-08-10 | 16.2 | 1.8 | 0 | 2019-08-10 | 14.9 | 3.1 | 0 | 2018-08-10 | 18 | 0 | 0 | 2017-08-10 | 14.5 | 3.5 | 0 | 2016-08-10 | 21.9 | 0 | 3.9 | 1.09 | 1.4
2025-08-10 | 23 | 0 | 5 | 2024-08-10 | 17.4 | 0.6 | 0 | 2023-08-10 | 16.5 | 1.5 | 0 | 2022-08-10 | 16.4 | 1.6 | 0 | 2021-08-10 | 22 | 0 | 4 | 2020-08-10 | 18.2 | 0 | 0.2 | 2019-08-10 | 14.2 | 3.8 | 0 | 2018-08-10 | 17.4 | 0.6 | 0 | 2017-08-10 | 13.8 | 4.2 | 0 | 2016-08-10 | 21.3 | 0 | 3.3 | 1.23 | 1.25
2025-08-10 | 21.7 | 0 | 3.7 | 2024-08-10 | 16.5 | 1.5 | 0 | 2023-08-10 | 16.7 | 1.3 | 0 | 2022-08-10 | 16.4 | 1.6 | 0 | 2021-08-10 | 21 | 0 | 3 | 2020-08-10 | 18.4 | 0 | 0.4 | 2019-08-10 | 12.9 | 5.1 | 0 | 2018-08-10 | 15.4 | 2.6 | 0 | 2017-08-10 | 13.7 | 4.3 | 0 | 2016-08-10 | 21.7 | 0 | 3.7 | 1.64 | 1.08
2025-08-10 | 19.7 | 0 | 1.7 | 2024-08-10 | 15.4 | 2.6 | 0 | 2023-08-10 | 14.3 | 3.7 | 0 | 2022-08-10 | 16.4 | 1.6 | 0 | 2021-08-10 | 20.8 | 0 | 2.8 | 2020-08-10 | 18.3 | 0 | 0.3 | 2019-08-10 | 13.4 | 4.6 | 0 | 2018-08-10 | 16.3 | 1.7 | 0 | 2017-08-10 | 14.7 | 3.3 | 0 | 2016-08-10 | 20.2 | 0 | 2.2 | 1.75 | 0.7
2025-08-10 | 19.4 | 0 | 1.4 | 2024-08-10 | 14.9 | 3.1 | 0 | 2023-08-10 | 16 | 2 | 0 | 2022-08-10 | 16.5 | 1.5 | 0 | 2021-08-10 | 19.9 | 0 | 1.9 | 2020-08-10 | 18.3 | 0 | 0.3 | 2019-08-10 | 12 | 6 | 0 | 2018-08-10 | 15.3 | 2.7 | 0 | 2017-08-10 | 15.1 | 2.9 | 0 | 2016-08-10 | 19.4 | 0 | 1.4 | 1.82 | 0.5
2025-08-10 | 20.3 | 0 | 2.3 | 2024-08-10 | 15.1 | 2.9 | 0 | 2023-08-10 | 16.6 | 1.4 | 0 | 2022-08-10 | 16.5 | 1.5 | 0 | 2021-08-10 | 20.7 | 0 | 2.7 | 2020-08-10 | 18.5 | 0 | 0.5 | 2019-08-10 | 12.8 | 5.2 | 0 | 2018-08-10 | 16.5 | 1.5 | 0 | 2017-08-10 | 15.2 | 2.8 | 0 | 2016-08-10 | 20.8 | 0 | 2.8 | 1.53 | 0.83
2025-08-10 | 23.1 | 0 | 5.1 | 2024-08-10 | 16.4 | 1.6 | 0 | 2023-08-10 | 18.4 | 0 | 0.4 | 2022-08-10 | 18.3 | 0 | 0.3 | 2021-08-10 | 22.4 | 0 | 4.4 | 2020-08-10 | 19.1 | 0 | 1.1 | 2019-08-10 | 14 | 4 | 0 | 2018-08-10 | 18.3 | 0 | 0.3 | 2017-08-10 | 16.8 | 1.2 | 0 | 2016-08-10 | 23.5 | 0 | 5.5 | 0.68 | 1.71
2025-08-10 | 25.2 | 0 | 7.2 | 2024-08-10 | 18.5 | 0 | 0.5 | 2023-08-10 | 20 | 0 | 2 | 2022-08-10 | 19.3 | 0 | 1.3 | 2021-08-10 | 25 | 0 | 7 | 2020-08-10 | 20.1 | 0 | 2.1 | 2019-08-10 | 15.1 | 2.9 | 0 | 2018-08-10 | 19.6 | 0 | 1.6 | 2017-08-10 | 18.9 | 0 | 0.9 | 2016-08-10 | 26.7 | 0 | 8.7 | 0.29 | 3.13
2025-08-10 | 27.4 | 0 | 9.4 | 2024-08-10 | 19.8 | 0 | 1.8 | 2023-08-10 | 20.4 | 0 | 2.4 | 2022-08-10 | 20.5 | 0 | 2.5 | 2021-08-10 | 25.8 | 0 | 7.8 | 2020-08-10 | 21.6 | 0 | 3.6 | 2019-08-10 | 16.3 | 1.7 | 0 | 2018-08-10 | 21 | 0 | 3 | 2017-08-10 | 20.4 | 0 | 2.4 | 2016-08-10 | 28.2 | 0 | 10.2 | 0.17 | 4.31
2025-08-10 | 30.2 | 0 | 12.2 | 2024-08-10 | 22 | 0 | 4 | 2023-08-10 | 23.4 | 0 | 5.4 | 2022-08-10 | 20.3 | 0 | 2.3 | 2021-08-10 | 26.6 | 0 | 8.6 | 2020-08-10 | 24.4 | 0 | 6.4 | 2019-08-10 | 18.2 | 0 | 0.2 | 2018-08-10 | 21.8 | 0 | 3.8 | 2017-08-10 | 21.9 | 0 | 3.9 | 2016-08-10 | 29.9 | 0 | 11.9 | 0 | 5.87
2025-08-10 | 31.5 | 0 | 13.5 | 2024-08-10 | 22 | 0 | 4 | 2023-08-10 | 23.4 | 0 | 5.4 | 2022-08-10 | 22.4 | 0 | 4.4 | 2021-08-10 | 28.3 | 0 | 10.3 | 2020-08-10 | 26.2 | 0 | 8.2 | 2019-08-10 | 19.1 | 0 | 1.1 | 2018-08-10 | 23.3 | 0 | 5.3 | 2017-08-10 | 22.9 | 0 | 4.9 | 2016-08-10 | 30.4 | 0 | 12.4 | 0 | 6.95
2025-08-10 | 33.2 | 0 | 15.2 | 2024-08-10 | 24 | 0 | 6 | 2023-08-10 | 17.1 | 0.9 | 0 | 2022-08-10 | 22.7 | 0 | 4.7 | 2021-08-10 | 30.7 | 0 | 12.7 | 2020-08-10 | 27.2 | 0 | 9.2 | 2019-08-10 | 21.3 | 0 | 3.3 | 2018-08-10 | 23.6 | 0 | 5.6 | 2017-08-10 | 23.3 | 0 | 5.3 | 2016-08-10 | 32.1 | 0 | 14.1 | 0.09 | 7.61
2025-08-10 | 33.8 | 0 | 15.8 | 2024-08-10 | 25 | 0 | 7 | 2023-08-10 | 16.2 | 1.8 | 0 | 2022-08-10 | 24.2 | 0 | 6.2 | 2021-08-10 | 29.6 | 0 | 11.6 | 2020-08-10 | 28.8 | 0 | 10.8 | 2019-08-10 | 21.8 | 0 | 3.8 | 2018-08-10 | 24.5 | 0 | 6.5 | 2017-08-10 | 22.9 | 0 | 4.9 | 2016-08-10 | 32.8 | 0 | 14.8 | 0.18 | 8.14
2025-08-10 | 34.3 | 0 | 16.3 | 2024-08-10 | 24.3 | 0 | 6.3 | 2023-08-10 | 16.9 | 1.1 | 0 | 2022-08-10 | 23.6 | 0 | 5.6 | 2021-08-10 | 30.4 | 0 | 12.4 | 2020-08-10 | 28.5 | 0 | 10.5 | 2019-08-10 | 19.5 | 0 | 1.5 | 2018-08-10 | 24.8 | 0 | 6.8 | 2017-08-10 | 23.6 | 0 | 5.6 | 2016-08-10 | 34 | 0 | 16 | 0.11 | 8.1
2025-08-10 | 34.2 | 0 | 16.2 | 2024-08-10 | 21.1 | 0 | 3.1 | 2023-08-10 | 17.3 | 0.7 | 0 | 2022-08-10 | 24.4 | 0 | 6.4 | 2021-08-10 | 29.4 | 0 | 11.4 | 2020-08-10 | 27.1 | 0 | 9.1 | 2019-08-10 | 21.8 | 0 | 3.8 | 2018-08-10 | 25.8 | 0 | 7.8 | 2017-08-10 | 25.2 | 0 | 7.2 | 2016-08-10 | 32.5 | 0 | 14.5 | 0.07 | 7.95
2025-08-10 | 33.9 | 0 | 15.9 | 2024-08-10 | 23.4 | 0 | 5.4 | 2023-08-10 | 17.6 | 0.4 | 0 | 2022-08-10 | 24.9 | 0 | 6.9 | 2021-08-10 | 27.9 | 0 | 9.9 | 2020-08-10 | 24.2 | 0 | 6.2 | 2019-08-10 | 22.8 | 0 | 4.8 | 2018-08-10 | 25.6 | 0 | 7.6 | 2017-08-10 | 20.8 | 0 | 2.8 | 2016-08-10 | 33.8 | 0 | 15.8 | 0.04 | 7.53
2025-08-10 | 32.8 | 0 | 14.8 | 2024-08-10 | 23.2 | 0 | 5.2 | 2023-08-10 | 17.7 | 0.3 | 0 | 2022-08-10 | 24.8 | 0 | 6.8 | 2021-08-10 | 25.3 | 0 | 7.3 | 2020-08-10 | 23.8 | 0 | 5.8 | 2019-08-10 | 20.9 | 0 | 2.9 | 2018-08-10 | 25.5 | 0 | 7.5 | 2017-08-10 | 22 | 0 | 4 | 2016-08-10 | 32.8 | 0 | 14.8 | 0.03 | 6.91
2025-08-10 | 31.5 | 0 | 13.5 | 2024-08-10 | 20.6 | 0 | 2.6 | 2023-08-10 | 18.2 | 0 | 0.2 | 2022-08-10 | 23.8 | 0 | 5.8 | 2021-08-10 | 25.4 | 0 | 7.4 | 2020-08-10 | 24.6 | 0 | 6.6 | 2019-08-10 | 20.1 | 0 | 2.1 | 2018-08-10 | 23.8 | 0 | 5.8 | 2017-08-10 | 22.6 | 0 | 4.6 | 2016-08-10 | 31.8 | 0 | 13.8 | 0 | 6.24
2025-08-10 | 29.6 | 0 | 11.6 | 2024-08-10 | 20.4 | 0 | 2.4 | 2023-08-10 | 17.3 | 0.7 | 0 | 2022-08-10 | 21.1 | 0 | 3.1 | 2021-08-10 | 24.9 | 0 | 6.9 | 2020-08-10 | 23 | 0 | 5 | 2019-08-10 | 19 | 0 | 1 | 2018-08-10 | 21 | 0 | 3 | 2017-08-10 | 19.7 | 0 | 1.7 | 2016-08-10 | 28.8 | 0 | 10.8 | 0.07 | 4.55
2025-08-10 | 28 | 0 | 10 | 2024-08-10 | 18.1 | 0 | 0.1 | 2023-08-10 | 16.4 | 1.6 | 0 | 2022-08-10 | 20 | 0 | 2 | 2021-08-10 | 23.6 | 0 | 5.6 | 2020-08-10 | 21.9 | 0 | 3.9 | 2019-08-10 | 16.4 | 1.6 | 0 | 2018-08-10 | 20.9 | 0 | 2.9 | 2017-08-10 | 17.8 | 0.2 | 0 | 2016-08-10 | 26.9 | 0 | 8.9 | 0.34 | 3.34
2025-08-10 | 26.5 | 0 | 8.5 | 2024-08-10 | 16.3 | 1.7 | 0 | 2023-08-10 | 16.3 | 1.7 | 0 | 2022-08-10 | 19.2 | 0 | 1.2 | 2021-08-10 | 23.9 | 0 | 5.9 | 2020-08-10 | 21.3 | 0 | 3.3 | 2019-08-10 | 14.5 | 3.5 | 0 | 2018-08-10 | 19.6 | 0 | 1.6 | 2017-08-10 | 16.7 | 1.3 | 0 | 2016-08-10 | 25.7 | 0 | 7.7 | 0.82 | 2.82
2025-08-10 | 25.3 | 0 | 7.3 | 2024-08-10 | 16.5 | 1.5 | 0 | 2023-08-10 | 15.9 | 2.1 | 0 | 2022-08-10 | 18.8 | 0 | 0.8 | 2021-08-10 | 23.9 | 0 | 5.9 | 2020-08-10 | 22 | 0 | 4 | 2019-08-10 | 12.9 | 5.1 | 0 | 2018-08-10 | 18 | 0 | 0 | 2017-08-10 | 16.7 | 1.3 | 0 | 2016-08-10 | 24.3 | 0 | 6.3 | 1 | 2.43
2025-08-10 | 24.3 | 0 | 6.3 | 2024-08-10 | 15 | 3 | 0 | 2023-08-10 | 15.3 | 2.7 | 0 | 2022-08-10 | 18.1 | 0 | 0.1 | 2021-08-10 | 23.4 | 0 | 5.4 | 2020-08-10 | 21.6 | 0 | 3.6 | 2019-08-10 | 12.3 | 5.7 | 0 | 2018-08-10 | 17.6 | 0.4 | 0 | 2017-08-10 | 18 | 0 | 0 | 2016-08-10 | 23 | 0 | 5 | 1.18 | 2.04
2025-08-11 | 23.4 | 0 | 5.4 | 2024-08-11 | 14.3 | 3.7 | 0 | 2023-08-11 | 15.2 | 2.8 | 0 | 2022-08-11 | 17.3 | 0.7 | 0 | 2021-08-11 | 22.9 | 0 | 4.9 | 2020-08-11 | 21.8 | 0 | 3.8 | 2019-08-11 | 11.8 | 6.2 | 0 | 2018-08-11 | 17.6 | 0.4 | 0 | 2017-08-11 | 17.9 | 0.1 | 0 | 2016-08-11 | 22.8 | 0 | 4.8 | 1.39 | 1.89
2025-08-11 | 22.1 | 0 | 4.1 | 2024-08-11 | 14.9 | 3.1 | 0 | 2023-08-11 | 14.6 | 3.4 | 0 | 2022-08-11 | 16.9 | 1.1 | 0 | 2021-08-11 | 22.7 | 0 | 4.7 | 2020-08-11 | 21.5 | 0 | 3.5 | 2019-08-11 | 11.7 | 6.3 | 0 | 2018-08-11 | 15.8 | 2.2 | 0 | 2017-08-11 | 17.7 | 0.3 | 0 | 2016-08-11 | 21.9 | 0 | 3.9 | 1.64 | 1.62
2025-08-11 | 21.7 | 0 | 3.7 | 2024-08-11 | 14 | 4 | 0 | 2023-08-11 | 14.3 | 3.7 | 0 | 2022-08-11 | 15.9 | 2.1 | 0 | 2021-08-11 | 22.4 | 0 | 4.4 | 2020-08-11 | 21.8 | 0 | 3.8 | 2019-08-11 | 11.5 | 6.5 | 0 | 2018-08-11 | 13.2 | 4.8 | 0 | 2017-08-11 | 16.5 | 1.5 | 0 | 2016-08-11 | 20.5 | 0 | 2.5 | 2.26 | 1.44
2025-08-11 | 21.2 | 0 | 3.2 | 2024-08-11 | 14.1 | 3.9 | 0 | 2023-08-11 | 13.9 | 4.1 | 0 | 2022-08-11 | 15.8 | 2.2 | 0 | 2021-08-11 | 22.1 | 0 | 4.1 | 2020-08-11 | 21.5 | 0 | 3.5 | 2019-08-11 | 11.1 | 6.9 | 0 | 2018-08-11 | 15 | 3 | 0 | 2017-08-11 | 15.3 | 2.7 | 0 | 2016-08-11 | 20 | 0 | 2 | 2.28 | 1.28
2025-08-11 | 20.1 | 0 | 2.1 | 2024-08-11 | 14 | 4 | 0 | 2023-08-11 | 13.1 | 4.9 | 0 | 2022-08-11 | 15.3 | 2.7 | 0 | 2021-08-11 | 22.3 | 0 | 4.3 | 2020-08-11 | 20.9 | 0 | 2.9 | 2019-08-11 | 11.3 | 6.7 | 0 | 2018-08-11 | 13 | 5 | 0 | 2017-08-11 | 15.9 | 2.1 | 0 | 2016-08-11 | 21.2 | 0 | 3.2 | 2.54 | 1.25
2025-08-11 | 18.9 | 0 | 0.9 | 2024-08-11 | 14.3 | 3.7 | 0 | 2023-08-11 | 14.5 | 3.5 | 0 | 2022-08-11 | 15.6 | 2.4 | 0 | 2021-08-11 | 22.5 | 0 | 4.5 | 2020-08-11 | 19.7 | 0 | 1.7 | 2019-08-11 | 11.2 | 6.8 | 0 | 2018-08-11 | 13.9 | 4.1 | 0 | 2017-08-11 | 14.4 | 3.6 | 0 | 2016-08-11 | 21.7 | 0 | 3.7 | 2.41 | 1.08
2025-08-11 | 19.7 | 0 | 1.7 | 2024-08-11 | 15 | 3 | 0 | 2023-08-11 | 14.5 | 3.5 | 0 | 2022-08-11 | 16.3 | 1.7 | 0 | 2021-08-11 | 23 | 0 | 5 | 2020-08-11 | 20.9 | 0 | 2.9 | 2019-08-11 | 12.1 | 5.9 | 0 | 2018-08-11 | 16.3 | 1.7 | 0 | 2017-08-11 | 15.9 | 2.1 | 0 | 2016-08-11 | 21.3 | 0 | 3.3 | 1.79 | 1.29
2025-08-11 | 22.6 | 0 | 4.6 | 2024-08-11 | 15.8 | 2.2 | 0 | 2023-08-11 | 15.4 | 2.6 | 0 | 2022-08-11 | 18.5 | 0 | 0.5 | 2021-08-11 | 23.1 | 0 | 5.1 | 2020-08-11 | 23.4 | 0 | 5.4 | 2019-08-11 | 14.7 | 3.3 | 0 | 2018-08-11 | 18 | 0 | 0 | 2017-08-11 | 17.6 | 0.4 | 0 | 2016-08-11 | 24.4 | 0 | 6.4 | 0.85 | 2.2
2025-08-11 | 25.5 | 0 | 7.5 | 2024-08-11 | 17.6 | 0.4 | 0 | 2023-08-11 | 16.8 | 1.2 | 0 | 2022-08-11 | 20.8 | 0 | 2.8 | 2021-08-11 | 24.6 | 0 | 6.6 | 2020-08-11 | 25.4 | 0 | 7.4 | 2019-08-11 | 18.2 | 0 | 0.2 | 2018-08-11 | 21.5 | 0 | 3.5 | 2017-08-11 | 20.3 | 0 | 2.3 | 2016-08-11 | 26.1 | 0 | 8.1 | 0.16 | 3.84
2025-08-11 | 27.3 | 0 | 9.3 | 2024-08-11 | 18.5 | 0 | 0.5 | 2023-08-11 | 18 | 0 | 0 | 2022-08-11 | 22.1 | 0 | 4.1 | 2021-08-11 | 25.7 | 0 | 7.7 | 2020-08-11 | 26.8 | 0 | 8.8 | 2019-08-11 | 20.3 | 0 | 2.3 | 2018-08-11 | 23.7 | 0 | 5.7 | 2017-08-11 | 22.8 | 0 | 4.8 | 2016-08-11 | 27.5 | 0 | 9.5 | 0 | 5.27
2025-08-11 | 29.9 | 0 | 11.9 | 2024-08-11 | 20.9 | 0 | 2.9 | 2023-08-11 | 18.1 | 0 | 0.1 | 2022-08-11 | 23.1 | 0 | 5.1 | 2021-08-11 | 27 | 0 | 9 | 2020-08-11 | 27.1 | 0 | 9.1 | 2019-08-11 | 22 | 0 | 4 | 2018-08-11 | 25.2 | 0 | 7.2 | 2017-08-11 | 24.3 | 0 | 6.3 | 2016-08-11 | 28.3 | 0 | 10.3 | 0 | 6.59
2025-08-11 | 31.4 | 0 | 13.4 | 2024-08-11 | 19.6 | 0 | 1.6 | 2023-08-11 | 18.6 | 0 | 0.6 | 2022-08-11 | 24.1 | 0 | 6.1 | 2021-08-11 | 28.5 | 0 | 10.5 | 2020-08-11 | 29 | 0 | 11 | 2019-08-11 | 23.9 | 0 | 5.9 | 2018-08-11 | 26 | 0 | 8 | 2017-08-11 | 25.8 | 0 | 7.8 | 2016-08-11 | 30.7 | 0 | 12.7 | 0 | 7.76
2025-08-11 | 32.4 | 0 | 14.4 | 2024-08-11 | 19.3 | 0 | 1.3 | 2023-08-11 | 20.9 | 0 | 2.9 | 2022-08-11 | 24.6 | 0 | 6.6 | 2021-08-11 | 29.2 | 0 | 11.2 | 2020-08-11 | 30 | 0 | 12 | 2019-08-11 | 26.4 | 0 | 8.4 | 2018-08-11 | 26.2 | 0 | 8.2 | 2017-08-11 | 27 | 0 | 9 | 2016-08-11 | 30.4 | 0 | 12.4 | 0 | 8.64
2025-08-11 | 33.6 | 0 | 15.6 | 2024-08-11 | 20.6 | 0 | 2.6 | 2023-08-11 | 21.5 | 0 | 3.5 | 2022-08-11 | 23.3 | 0 | 5.3 | 2021-08-11 | 29.9 | 0 | 11.9 | 2020-08-11 | 30.4 | 0 | 12.4 | 2019-08-11 | 26.4 | 0 | 8.4 | 2018-08-11 | 26.7 | 0 | 8.7 | 2017-08-11 | 25.9 | 0 | 7.9 | 2016-08-11 | 32.7 | 0 | 14.7 | 0 | 9.1
2025-08-11 | 33.5 | 0 | 15.5 | 2024-08-11 | 20.6 | 0 | 2.6 | 2023-08-11 | 21.6 | 0 | 3.6 | 2022-08-11 | 24.8 | 0 | 6.8 | 2021-08-11 | 28.5 | 0 | 10.5 | 2020-08-11 | 29.2 | 0 | 11.2 | 2019-08-11 | 25.9 | 0 | 7.9 | 2018-08-11 | 26.5 | 0 | 8.5 | 2017-08-11 | 26.4 | 0 | 8.4 | 2016-08-11 | 33.3 | 0 | 15.3 | 0 | 9.03
2025-08-11 | 33.1 | 0 | 15.1 | 2024-08-11 | 18.2 | 0 | 0.2 | 2023-08-11 | 22.6 | 0 | 4.6 | 2022-08-11 | 24.5 | 0 | 6.5 | 2021-08-11 | 28.2 | 0 | 10.2 | 2020-08-11 | 25.4 | 0 | 7.4 | 2019-08-11 | 26.7 | 0 | 8.7 | 2018-08-11 | 26.8 | 0 | 8.8 | 2017-08-11 | 26.3 | 0 | 8.3 | 2016-08-11 | 33 | 0 | 15 | 0 | 8.48
2025-08-11 | 34.2 | 0 | 16.2 | 2024-08-11 | 18.4 | 0 | 0.4 | 2023-08-11 | 22.6 | 0 | 4.6 | 2022-08-11 | 24.2 | 0 | 6.2 | 2021-08-11 | 28.9 | 0 | 10.9 | 2020-08-11 | 26.9 | 0 | 8.9 | 2019-08-11 | 28.5 | 0 | 10.5 | 2018-08-11 | 26.8 | 0 | 8.8 | 2017-08-11 | 25.4 | 0 | 7.4 | 2016-08-11 | 33.7 | 0 | 15.7 | 0 | 8.96
2025-08-11 | 33.4 | 0 | 15.4 | 2024-08-11 | 18.3 | 0 | 0.3 | 2023-08-11 | 22.4 | 0 | 4.4 | 2022-08-11 | 23.8 | 0 | 5.8 | 2021-08-11 | 28.1 | 0 | 10.1 | 2020-08-11 | 22.7 | 0 | 4.7 | 2019-08-11 | 26.1 | 0 | 8.1 | 2018-08-11 | 26.5 | 0 | 8.5 | 2017-08-11 | 24.9 | 0 | 6.9 | 2016-08-11 | 33.8 | 0 | 15.8 | 0 | 8
2025-08-11 | 31.9 | 0 | 13.9 | 2024-08-11 | 17.9 | 0.1 | 0 | 2023-08-11 | 21.6 | 0 | 3.6 | 2022-08-11 | 22.7 | 0 | 4.7 | 2021-08-11 | 28.4 | 0 | 10.4 | 2020-08-11 | 22.5 | 0 | 4.5 | 2019-08-11 | 26.4 | 0 | 8.4 | 2018-08-11 | 25.2 | 0 | 7.2 | 2017-08-11 | 23.8 | 0 | 5.8 | 2016-08-11 | 32.6 | 0 | 14.6 | 0.01 | 7.31
2025-08-11 | 29 | 0 | 11 | 2024-08-11 | 16.8 | 1.2 | 0 | 2023-08-11 | 18.8 | 0 | 0.8 | 2022-08-11 | 21.3 | 0 | 3.3 | 2021-08-11 | 26.8 | 0 | 8.8 | 2020-08-11 | 22.3 | 0 | 4.3 | 2019-08-11 | 24 | 0 | 6 | 2018-08-11 | 22.6 | 0 | 4.6 | 2017-08-11 | 22.6 | 0 | 4.6 | 2016-08-11 | 29.6 | 0 | 11.6 | 0.12 | 5.5
2025-08-11 | 27.1 | 0 | 9.1 | 2024-08-11 | 17 | 1 | 0 | 2023-08-11 | 17.2 | 0.8 | 0 | 2022-08-11 | 19.8 | 0 | 1.8 | 2021-08-11 | 25 | 0 | 7 | 2020-08-11 | 20.6 | 0 | 2.6 | 2019-08-11 | 22.8 | 0 | 4.8 | 2018-08-11 | 21.9 | 0 | 3.9 | 2017-08-11 | 20.6 | 0 | 2.6 | 2016-08-11 | 28.8 | 0 | 10.8 | 0.18 | 4.26
2025-08-11 | 24.7 | 0 | 6.7 | 2024-08-11 | 16.1 | 1.9 | 0 | 2023-08-11 | 16.3 | 1.7 | 0 | 2022-08-11 | 19.1 | 0 | 1.1 | 2021-08-11 | 25.4 | 0 | 7.4 | 2020-08-11 | 19.9 | 0 | 1.9 | 2019-08-11 | 21.1 | 0 | 3.1 | 2018-08-11 | 19 | 0 | 1 | 2017-08-11 | 20 | 0 | 2 | 2016-08-11 | 28.4 | 0 | 10.4 | 0.36 | 3.36
2025-08-11 | 23.4 | 0 | 5.4 | 2024-08-11 | 14.6 | 3.4 | 0 | 2023-08-11 | 15.5 | 2.5 | 0 | 2022-08-11 | 18.5 | 0 | 0.5 | 2021-08-11 | 24.6 | 0 | 6.6 | 2020-08-11 | 19.8 | 0 | 1.8 | 2019-08-11 | 19.1 | 0 | 1.1 | 2018-08-11 | 19.1 | 0 | 1.1 | 2017-08-11 | 19.4 | 0 | 1.4 | 2016-08-11 | 27.5 | 0 | 9.5 | 0.59 | 2.74
2025-08-11 | 22.6 | 0 | 4.6 | 2024-08-11 | 14.1 | 3.9 | 0 | 2023-08-11 | 14.1 | 3.9 | 0 | 2022-08-11 | 17.6 | 0.4 | 0 | 2021-08-11 | 23.8 | 0 | 5.8 | 2020-08-11 | 19.9 | 0 | 1.9 | 2019-08-11 | 18.6 | 0 | 0.6 | 2018-08-11 | 18.4 | 0 | 0.4 | 2017-08-11 | 19.1 | 0 | 1.1 | 2016-08-11 | 26.9 | 0 | 8.9 | 0.82 | 2.33
2025-08-12 | 22.2 | 0 | 4.2 | 2024-08-12 | 13.9 | 4.1 | 0 | 2023-08-12 | 14 | 4 | 0 | 2022-08-12 | 16.4 | 1.6 | 0 | 2021-08-12 | 23.9 | 0 | 5.9 | 2020-08-12 | 19.2 | 0 | 1.2 | 2019-08-12 | 17.9 | 0.1 | 0 | 2018-08-12 | 17.5 | 0.5 | 0 | 2017-08-12 | 19.1 | 0 | 1.1 | 2016-08-12 | 26.2 | 0 | 8.2 | 1.03 | 2.06
2025-08-12 | 21.9 | 0 | 3.9 | 2024-08-12 | 13.1 | 4.9 | 0 | 2023-08-12 | 13.9 | 4.1 | 0 | 2022-08-12 | 14.3 | 3.7 | 0 | 2021-08-12 | 23.8 | 0 | 5.8 | 2020-08-12 | 18.4 | 0 | 0.4 | 2019-08-12 | 16.3 | 1.7 | 0 | 2018-08-12 | 16.7 | 1.3 | 0 | 2017-08-12 | 18.6 | 0 | 0.6 | 2016-08-12 | 25.2 | 0 | 7.2 | 1.57 | 1.79
2025-08-12 | 20.6 | 0 | 2.6 | 2024-08-12 | 12.4 | 5.6 | 0 | 2023-08-12 | 14.4 | 3.6 | 0 | 2022-08-12 | 14.4 | 3.6 | 0 | 2021-08-12 | 23.9 | 0 | 5.9 | 2020-08-12 | 17.8 | 0.2 | 0 | 2019-08-12 | 16.4 | 1.6 | 0 | 2018-08-12 | 16.6 | 1.4 | 0 | 2017-08-12 | 18.1 | 0 | 0.1 | 2016-08-12 | 25.4 | 0 | 7.4 | 1.6 | 1.6
2025-08-12 | 19.9 | 0 | 1.9 | 2024-08-12 | 13.3 | 4.7 | 0 | 2023-08-12 | 13.8 | 4.2 | 0 | 2022-08-12 | 11.4 | 6.6 | 0 | 2021-08-12 | 23.7 | 0 | 5.7 | 2020-08-12 | 19.4 | 0 | 1.4 | 2019-08-12 | 17 | 1 | 0 | 2018-08-12 | 16.6 | 1.4 | 0 | 2017-08-12 | 18 | 0 | 0 | 2016-08-12 | 24.8 | 0 | 6.8 | 1.79 | 1.58
2025-08-12 | 17.4 | 0.6 | 0 | 2024-08-12 | 13.2 | 4.8 | 0 | 2023-08-12 | 13.6 | 4.4 | 0 | 2022-08-12 | 11.6 | 6.4 | 0 | 2021-08-12 | 23.5 | 0 | 5.5 | 2020-08-12 | 17.4 | 0.6 | 0 | 2019-08-12 | 16.6 | 1.4 | 0 | 2018-08-12 | 16.2 | 1.8 | 0 | 2017-08-12 | 17.4 | 0.6 | 0 | 2016-08-12 | 23.3 | 0 | 5.3 | 2.06 | 1.08
2025-08-12 | 18.3 | 0 | 0.3 | 2024-08-12 | 13.7 | 4.3 | 0 | 2023-08-12 | 14.1 | 3.9 | 0 | 2022-08-12 | 10.8 | 7.2 | 0 | 2021-08-12 | 22.7 | 0 | 4.7 | 2020-08-12 | 15.9 | 2.1 | 0 | 2019-08-12 | 16.9 | 1.1 | 0 | 2018-08-12 | 16 | 2 | 0 | 2017-08-12 | 16.9 | 1.1 | 0 | 2016-08-12 | 23.5 | 0 | 5.5 | 2.17 | 1.05
2025-08-12 | 19.4 | 0 | 1.4 | 2024-08-12 | 14.4 | 3.6 | 0 | 2023-08-12 | 14.8 | 3.2 | 0 | 2022-08-12 | 12.3 | 5.7 | 0 | 2021-08-12 | 22.6 | 0 | 4.6 | 2020-08-12 | 16.7 | 1.3 | 0 | 2019-08-12 | 17.4 | 0.6 | 0 | 2018-08-12 | 17.7 | 0.3 | 0 | 2017-08-12 | 16.4 | 1.6 | 0 | 2016-08-12 | 23.9 | 0 | 5.9 | 1.63 | 1.19
2025-08-12 | 22 | 0 | 4 | 2024-08-12 | 15.4 | 2.6 | 0 | 2023-08-12 | 15.3 | 2.7 | 0 | 2022-08-12 | 15.5 | 2.5 | 0 | 2021-08-12 | 24.1 | 0 | 6.1 | 2020-08-12 | 19.3 | 0 | 1.3 | 2019-08-12 | 18.8 | 0 | 0.8 | 2018-08-12 | 20.1 | 0 | 2.1 | 2017-08-12 | 17.8 | 0.2 | 0 | 2016-08-12 | 23.4 | 0 | 5.4 | 0.8 | 1.97
2025-08-12 | 24.7 | 0 | 6.7 | 2024-08-12 | 15.8 | 2.2 | 0 | 2023-08-12 | 16.9 | 1.1 | 0 | 2022-08-12 | 16.3 | 1.7 | 0 | 2021-08-12 | 25.7 | 0 | 7.7 | 2020-08-12 | 21 | 0 | 3 | 2019-08-12 | 22.3 | 0 | 4.3 | 2018-08-12 | 21.7 | 0 | 3.7 | 2017-08-12 | 18.6 | 0 | 0.6 | 2016-08-12 | 23 | 0 | 5 | 0.5 | 3.1
2025-08-12 | 27.5 | 0 | 9.5 | 2024-08-12 | 17 | 1 | 0 | 2023-08-12 | 18.4 | 0 | 0.4 | 2022-08-12 | 17.4 | 0.6 | 0 | 2021-08-12 | 25.4 | 0 | 7.4 | 2020-08-12 | 22.7 | 0 | 4.7 | 2019-08-12 | 23 | 0 | 5 | 2018-08-12 | 23.5 | 0 | 5.5 | 2017-08-12 | 20.1 | 0 | 2.1 | 2016-08-12 | 24.5 | 0 | 6.5 | 0.16 | 4.11
2025-08-12 | 30.4 | 0 | 12.4 | 2024-08-12 | 18.1 | 0 | 0.1 | 2023-08-12 | 21.1 | 0 | 3.1 | 2022-08-12 | 18.4 | 0 | 0.4 | 2021-08-12 | 26.7 | 0 | 8.7 | 2020-08-12 | 24.6 | 0 | 6.6 | 2019-08-12 | 24.2 | 0 | 6.2 | 2018-08-12 | 25 | 0 | 7 | 2017-08-12 | 21.6 | 0 | 3.6 | 2016-08-12 | 25.2 | 0 | 7.2 | 0 | 5.53
2025-08-12 | 32.3 | 0 | 14.3 | 2024-08-12 | 19.5 | 0 | 1.5 | 2023-08-12 | 21.9 | 0 | 3.9 | 2022-08-12 | 19.6 | 0 | 1.6 | 2021-08-12 | 27.3 | 0 | 9.3 | 2020-08-12 | 26.7 | 0 | 8.7 | 2019-08-12 | 25.7 | 0 | 7.7 | 2018-08-12 | 26.3 | 0 | 8.3 | 2017-08-12 | 23.8 | 0 | 5.8 | 2016-08-12 | 24.7 | 0 | 6.7 | 0 | 6.78
2025-08-12 | 32.6 | 0 | 14.6 | 2024-08-12 | 19.8 | 0 | 1.8 | 2023-08-12 | 21.9 | 0 | 3.9 | 2022-08-12 | 20.9 | 0 | 2.9 | 2021-08-12 | 27.9 | 0 | 9.9 | 2020-08-12 | 27.9 | 0 | 9.9 | 2019-08-12 | 27.3 | 0 | 9.3 | 2018-08-12 | 27.4 | 0 | 9.4 | 2017-08-12 | 24.7 | 0 | 6.7 | 2016-08-12 | 24.1 | 0 | 6.1 | 0 | 7.45
2025-08-12 | 33.7 | 0 | 15.7 | 2024-08-12 | 21 | 0 | 3 | 2023-08-12 | 21.9 | 0 | 3.9 | 2022-08-12 | 21.2 | 0 | 3.2 | 2021-08-12 | 28.5 | 0 | 10.5 | 2020-08-12 | 28.7 | 0 | 10.7 | 2019-08-12 | 27.7 | 0 | 9.7 | 2018-08-12 | 27.4 | 0 | 9.4 | 2017-08-12 | 26.8 | 0 | 8.8 | 2016-08-12 | 22.1 | 0 | 4.1 | 0 | 7.9
2025-08-12 | 33.6 | 0 | 15.6 | 2024-08-12 | 21.8 | 0 | 3.8 | 2023-08-12 | 22.1 | 0 | 4.1 | 2022-08-12 | 22 | 0 | 4 | 2021-08-12 | 29.7 | 0 | 11.7 | 2020-08-12 | 29.4 | 0 | 11.4 | 2019-08-12 | 27.8 | 0 | 9.8 | 2018-08-12 | 28 | 0 | 10 | 2017-08-12 | 25.5 | 0 | 7.5 | 2016-08-12 | 21.1 | 0 | 3.1 | 0 | 8.1
2025-08-12 | 35.1 | 0 | 17.1 | 2024-08-12 | 21.9 | 0 | 3.9 | 2023-08-12 | 20.7 | 0 | 2.7 | 2022-08-12 | 21.6 | 0 | 3.6 | 2021-08-12 | 29.4 | 0 | 11.4 | 2020-08-12 | 30 | 0 | 12 | 2019-08-12 | 23.9 | 0 | 5.9 | 2018-08-12 | 28.3 | 0 | 10.3 | 2017-08-12 | 17.2 | 0.8 | 0 | 2016-08-12 | 20.2 | 0 | 2.2 | 0.08 | 6.91
2025-08-12 | 34.6 | 0 | 16.6 | 2024-08-12 | 22 | 0 | 4 | 2023-08-12 | 19.5 | 0 | 1.5 | 2022-08-12 | 21 | 0 | 3 | 2021-08-12 | 29.8 | 0 | 11.8 | 2020-08-12 | 29.5 | 0 | 11.5 | 2019-08-12 | 22.7 | 0 | 4.7 | 2018-08-12 | 27 | 0 | 9 | 2017-08-12 | 18.5 | 0 | 0.5 | 2016-08-12 | 19.3 | 0 | 1.3 | 0 | 6.39
2025-08-12 | 33.1 | 0 | 15.1 | 2024-08-12 | 21.1 | 0 | 3.1 | 2023-08-12 | 20.5 | 0 | 2.5 | 2022-08-12 | 22.1 | 0 | 4.1 | 2021-08-12 | 29.3 | 0 | 11.3 | 2020-08-12 | 29.4 | 0 | 11.4 | 2019-08-12 | 22.7 | 0 | 4.7 | 2018-08-12 | 27.7 | 0 | 9.7 | 2017-08-12 | 19.8 | 0 | 1.8 | 2016-08-12 | 18.6 | 0 | 0.6 | 0 | 6.43
2025-08-12 | 32 | 0 | 14 | 2024-08-12 | 20 | 0 | 2 | 2023-08-12 | 20.2 | 0 | 2.2 | 2022-08-12 | 21.9 | 0 | 3.9 | 2021-08-12 | 28.2 | 0 | 10.2 | 2020-08-12 | 27.6 | 0 | 9.6 | 2019-08-12 | 22.2 | 0 | 4.2 | 2018-08-12 | 26.3 | 0 | 8.3 | 2017-08-12 | 19.4 | 0 | 1.4 | 2016-08-12 | 18.2 | 0 | 0.2 | 0 | 5.6
2025-08-12 | 30.4 | 0 | 12.4 | 2024-08-12 | 18.5 | 0 | 0.5 | 2023-08-12 | 19.4 | 0 | 1.4 | 2022-08-12 | 16.7 | 1.3 | 0 | 2021-08-12 | 27 | 0 | 9 | 2020-08-12 | 26 | 0 | 8 | 2019-08-12 | 20.8 | 0 | 2.8 | 2018-08-12 | 24.2 | 0 | 6.2 | 2017-08-12 | 19.6 | 0 | 1.6 | 2016-08-12 | 17.9 | 0.1 | 0 | 0.14 | 4.19
2025-08-12 | 27.5 | 0 | 9.5 | 2024-08-12 | 16.2 | 1.8 | 0 | 2023-08-12 | 18.7 | 0 | 0.7 | 2022-08-12 | 15.5 | 2.5 | 0 | 2021-08-12 | 25 | 0 | 7 | 2020-08-12 | 24.9 | 0 | 6.9 | 2019-08-12 | 19.9 | 0 | 1.9 | 2018-08-12 | 21.8 | 0 | 3.8 | 2017-08-12 | 19.1 | 0 | 1.1 | 2016-08-12 | 17.7 | 0.3 | 0 | 0.46 | 3.09
2025-08-12 | 26.3 | 0 | 8.3 | 2024-08-12 | 15.1 | 2.9 | 0 | 2023-08-12 | 19.2 | 0 | 1.2 | 2022-08-12 | 14.8 | 3.2 | 0 | 2021-08-12 | 24.6 | 0 | 6.6 | 2020-08-12 | 22.8 | 0 | 4.8 | 2019-08-12 | 19.5 | 0 | 1.5 | 2018-08-12 | 22.5 | 0 | 4.5 | 2017-08-12 | 18.2 | 0 | 0.2 | 2016-08-12 | 17.4 | 0.6 | 0 | 0.67 | 2.71
2025-08-12 | 25.8 | 0 | 7.8 | 2024-08-12 | 14.1 | 3.9 | 0 | 2023-08-12 | 19 | 0 | 1 | 2022-08-12 | 13.3 | 4.7 | 0 | 2021-08-12 | 23.2 | 0 | 5.2 | 2020-08-12 | 21.5 | 0 | 3.5 | 2019-08-12 | 19.6 | 0 | 1.6 | 2018-08-12 | 20.9 | 0 | 2.9 | 2017-08-12 | 18.8 | 0 | 0.8 | 2016-08-12 | 17.8 | 0.2 | 0 | 0.88 | 2.28
2025-08-12 | 24.9 | 0 | 6.9 | 2024-08-12 | 13.8 | 4.2 | 0 | 2023-08-12 | 18.5 | 0 | 0.5 | 2022-08-12 | 12.9 | 5.1 | 0 | 2021-08-12 | 22.6 | 0 | 4.6 | 2020-08-12 | 19.9 | 0 | 1.9 | 2019-08-12 | 19.9 | 0 | 1.9 | 2018-08-12 | 19.5 | 0 | 1.5 | 2017-08-12 | 17.5 | 0.5 | 0 | 2016-08-12 | 17.8 | 0.2 | 0 | 1 | 1.73
2025-08-13 | 24.3 | 0 | 6.3 | 2024-08-13 | 13.8 | 4.2 | 0 | 2023-08-13 | 18.6 | 0 | 0.6 | 2022-08-13 | 12.9 | 5.1 | 0 | 2021-08-13 | 22.1 | 0 | 4.1 | 2020-08-13 | 18.7 | 0 | 0.7 | 2019-08-13 | 19.7 | 0 | 1.7 | 2018-08-13 | 18.5 | 0 | 0.5 | 2017-08-13 | 17.2 | 0.8 | 0 | 2016-08-13 | 17.8 | 0.2 | 0 | 1.03 | 1.39
2025-08-13 | 24.1 | 0 | 6.1 | 2024-08-13 | 14.1 | 3.9 | 0 | 2023-08-13 | 18.5 | 0 | 0.5 | 2022-08-13 | 12.5 | 5.5 | 0 | 2021-08-13 | 21.2 | 0 | 3.2 | 2020-08-13 | 17.2 | 0.8 | 0 | 2019-08-13 | 17.9 | 0.1 | 0 | 2018-08-13 | 19.7 | 0 | 1.7 | 2017-08-13 | 17.1 | 0.9 | 0 | 2016-08-13 | 17.4 | 0.6 | 0 | 1.18 | 1.15
2025-08-13 | 23.7 | 0 | 5.7 | 2024-08-13 | 13.3 | 4.7 | 0 | 2023-08-13 | 18.2 | 0 | 0.2 | 2022-08-13 | 11.7 | 6.3 | 0 | 2021-08-13 | 20.5 | 0 | 2.5 | 2020-08-13 | 17.5 | 0.5 | 0 | 2019-08-13 | 17.7 | 0.3 | 0 | 2018-08-13 | 19.3 | 0 | 1.3 | 2017-08-13 | 16.9 | 1.1 | 0 | 2016-08-13 | 17.9 | 0.1 | 0 | 1.3 | 0.97
2025-08-13 | 23.9 | 0 | 5.9 | 2024-08-13 | 13.1 | 4.9 | 0 | 2023-08-13 | 17.7 | 0.3 | 0 | 2022-08-13 | 12.4 | 5.6 | 0 | 2021-08-13 | 19.1 | 0 | 1.1 | 2020-08-13 | 17.4 | 0.6 | 0 | 2019-08-13 | 16.7 | 1.3 | 0 | 2018-08-13 | 18.3 | 0 | 0.3 | 2017-08-13 | 16 | 2 | 0 | 2016-08-13 | 17.4 | 0.6 | 0 | 1.53 | 0.73
2025-08-13 | 23.6 | 0 | 5.6 | 2024-08-13 | 12.7 | 5.3 | 0 | 2023-08-13 | 18.3 | 0 | 0.3 | 2022-08-13 | 10.5 | 7.5 | 0 | 2021-08-13 | 20.1 | 0 | 2.1 | 2020-08-13 | 17.5 | 0.5 | 0 | 2019-08-13 | 17.1 | 0.9 | 0 | 2018-08-13 | 17.5 | 0.5 | 0 | 2017-08-13 | 16 | 2 | 0 | 2016-08-13 | 17.1 | 0.9 | 0 | 1.76 | 0.8
2025-08-13 | 23.2 | 0 | 5.2 | 2024-08-13 | 13.3 | 4.7 | 0 | 2023-08-13 | 18.1 | 0 | 0.1 | 2022-08-13 | 9.7 | 8.3 | 0 | 2021-08-13 | 20.2 | 0 | 2.2 | 2020-08-13 | 17.9 | 0.1 | 0 | 2019-08-13 | 16.6 | 1.4 | 0 | 2018-08-13 | 17.3 | 0.7 | 0 | 2017-08-13 | 15.6 | 2.4 | 0 | 2016-08-13 | 16.9 | 1.1 | 0 | 1.87 | 0.75
2025-08-13 | 23.9 | 0 | 5.9 | 2024-08-13 | 14.4 | 3.6 | 0 | 2023-08-13 | 17.7 | 0.3 | 0 | 2022-08-13 | 11.2 | 6.8 | 0 | 2021-08-13 | 20.7 | 0 | 2.7 | 2020-08-13 | 18.5 | 0 | 0.5 | 2019-08-13 | 17.5 | 0.5 | 0 | 2018-08-13 | 18.2 | 0 | 0.2 | 2017-08-13 | 16.4 | 1.6 | 0 | 2016-08-13 | 16.8 | 1.2 | 0 | 1.4 | 0.93
2025-08-13 | 24.5 | 0 | 6.5 | 2024-08-13 | 16.4 | 1.6 | 0 | 2023-08-13 | 18.5 | 0 | 0.5 | 2022-08-13 | 14.7 | 3.3 | 0 | 2021-08-13 | 22 | 0 | 4 | 2020-08-13 | 21.4 | 0 | 3.4 | 2019-08-13 | 18.5 | 0 | 0.5 | 2018-08-13 | 19.7 | 0 | 1.7 | 2017-08-13 | 16.9 | 1.1 | 0 | 2016-08-13 | 16.6 | 1.4 | 0 | 0.74 | 1.66
2025-08-13 | 21.2 | 0 | 3.2 | 2024-08-13 | 18.4 | 0 | 0.4 | 2023-08-13 | 19.8 | 0 | 1.8 | 2022-08-13 | 17.1 | 0.9 | 0 | 2021-08-13 | 24.2 | 0 | 6.2 | 2020-08-13 | 23.1 | 0 | 5.1 | 2019-08-13 | 19.9 | 0 | 1.9 | 2018-08-13 | 22.5 | 0 | 4.5 | 2017-08-13 | 18.4 | 0 | 0.4 | 2016-08-13 | 16.3 | 1.7 | 0 | 0.26 | 2.35
2025-08-13 | 21.9 | 0 | 3.9 | 2024-08-13 | 20.1 | 0 | 2.1 | 2023-08-13 | 20.5 | 0 | 2.5 | 2022-08-13 | 19.8 | 0 | 1.8 | 2021-08-13 | 25.6 | 0 | 7.6 | 2020-08-13 | 25.6 | 0 | 7.6 | 2019-08-13 | 21.9 | 0 | 3.9 | 2018-08-13 | 24.2 | 0 | 6.2 | 2017-08-13 | 19.8 | 0 | 1.8 | 2016-08-13 | 16.1 | 1.9 | 0 | 0.19 | 3.74
2025-08-13 | 23.5 | 0 | 5.5 | 2024-08-13 | 22.3 | 0 | 4.3 | 2023-08-13 | 21.5 | 0 | 3.5 | 2022-08-13 | 21.3 | 0 | 3.3 | 2021-08-13 | 25.7 | 0 | 7.7 | 2020-08-13 | 27.9 | 0 | 9.9 | 2019-08-13 | 23.6 | 0 | 5.6 | 2018-08-13 | 24.9 | 0 | 6.9 | 2017-08-13 | 21.8 | 0 | 3.8 | 2016-08-13 | 16.4 | 1.6 | 0 | 0.16 | 5.05
2025-08-13 | 24.1 | 0 | 6.1 | 2024-08-13 | 24.1 | 0 | 6.1 | 2023-08-13 | 21.1 | 0 | 3.1 | 2022-08-13 | 23.8 | 0 | 5.8 | 2021-08-13 | 28.2 | 0 | 10.2 | 2020-08-13 | 29.5 | 0 | 11.5 | 2019-08-13 | 24.9 | 0 | 6.9 | 2018-08-13 | 26 | 0 | 8 | 2017-08-13 | 23.6 | 0 | 5.6 | 2016-08-13 | 16.3 | 1.7 | 0 | 0.17 | 6.33
2025-08-13 | 25 | 0 | 7 | 2024-08-13 | 24.9 | 0 | 6.9 | 2023-08-13 | 22.3 | 0 | 4.3 | 2022-08-13 | 23.7 | 0 | 5.7 | 2021-08-13 | 28.3 | 0 | 10.3 | 2020-08-13 | 30.8 | 0 | 12.8 | 2019-08-13 | 24.9 | 0 | 6.9 | 2018-08-13 | 26.4 | 0 | 8.4 | 2017-08-13 | 24.5 | 0 | 6.5 | 2016-08-13 | 16.9 | 1.1 | 0 | 0.11 | 6.88
2025-08-13 | 26.2 | 0 | 8.2 | 2024-08-13 | 25.9 | 0 | 7.9 | 2023-08-13 | 22.9 | 0 | 4.9 | 2022-08-13 | 22.9 | 0 | 4.9 | 2021-08-13 | 29.2 | 0 | 11.2 | 2020-08-13 | 30.9 | 0 | 12.9 | 2019-08-13 | 25.4 | 0 | 7.4 | 2018-08-13 | 27.4 | 0 | 9.4 | 2017-08-13 | 25.2 | 0 | 7.2 | 2016-08-13 | 17.8 | 0.2 | 0 | 0.02 | 7.4
2025-08-13 | 27.9 | 0 | 9.9 | 2024-08-13 | 26.7 | 0 | 8.7 | 2023-08-13 | 22.8 | 0 | 4.8 | 2022-08-13 | 24.1 | 0 | 6.1 | 2021-08-13 | 28.8 | 0 | 10.8 | 2020-08-13 | 30.1 | 0 | 12.1 | 2019-08-13 | 24.9 | 0 | 6.9 | 2018-08-13 | 28.4 | 0 | 10.4 | 2017-08-13 | 26.1 | 0 | 8.1 | 2016-08-13 | 18.4 | 0 | 0.4 | 0 | 7.82
2025-08-13 | 27.8 | 0 | 9.8 | 2024-08-13 | 27.6 | 0 | 9.6 | 2023-08-13 | 23.6 | 0 | 5.6 | 2022-08-13 | 24 | 0 | 6 | 2021-08-13 | 29.7 | 0 | 11.7 | 2020-08-13 | 30.2 | 0 | 12.2 | 2019-08-13 | 24.8 | 0 | 6.8 | 2018-08-13 | 27.5 | 0 | 9.5 | 2017-08-13 | 25.8 | 0 | 7.8 | 2016-08-13 | 18.2 | 0 | 0.2 | 0 | 7.92
2025-08-13 | 29.3 | 0 | 11.3 | 2024-08-13 | 26.1 | 0 | 8.1 | 2023-08-13 | 20 | 0 | 2 | 2022-08-13 | 24.1 | 0 | 6.1 | 2021-08-13 | 29.6 | 0 | 11.6 | 2020-08-13 | 29.2 | 0 | 11.2 | 2019-08-13 | 25.6 | 0 | 7.6 | 2018-08-13 | 27.6 | 0 | 9.6 | 2017-08-13 | 25.5 | 0 | 7.5 | 2016-08-13 | 17.9 | 0.1 | 0 | 0.01 | 7.5
2025-08-13 | 29.1 | 0 | 11.1 | 2024-08-13 | 26.4 | 0 | 8.4 | 2023-08-13 | 22.3 | 0 | 4.3 | 2022-08-13 | 24.3 | 0 | 6.3 | 2021-08-13 | 28.4 | 0 | 10.4 | 2020-08-13 | 28.8 | 0 | 10.8 | 2019-08-13 | 24.6 | 0 | 6.6 | 2018-08-13 | 26.6 | 0 | 8.6 | 2017-08-13 | 25.2 | 0 | 7.2 | 2016-08-13 | 18 | 0 | 0 | 0 | 7.37
2025-08-13 | 28.1 | 0 | 10.1 | 2024-08-13 | 24.7 | 0 | 6.7 | 2023-08-13 | 21.5 | 0 | 3.5 | 2022-08-13 | 23.1 | 0 | 5.1 | 2021-08-13 | 25.8 | 0 | 7.8 | 2020-08-13 | 27.3 | 0 | 9.3 | 2019-08-13 | 23.9 | 0 | 5.9 | 2018-08-13 | 26 | 0 | 8 | 2017-08-13 | 24.3 | 0 | 6.3 | 2016-08-13 | 18.5 | 0 | 0.5 | 0 | 6.32
2025-08-13 | 26.4 | 0 | 8.4 | 2024-08-13 | 22.1 | 0 | 4.1 | 2023-08-13 | 19.9 | 0 | 1.9 | 2022-08-13 | 21.8 | 0 | 3.8 | 2021-08-13 | 23.9 | 0 | 5.9 | 2020-08-13 | 25.3 | 0 | 7.3 | 2019-08-13 | 22.3 | 0 | 4.3 | 2018-08-13 | 24.9 | 0 | 6.9 | 2017-08-13 | 22.5 | 0 | 4.5 | 2016-08-13 | 18.4 | 0 | 0.4 | 0 | 4.75
2025-08-13 | 26.1 | 0 | 8.1 | 2024-08-13 | 20.2 | 0 | 2.2 | 2023-08-13 | 18.2 | 0 | 0.2 | 2022-08-13 | 19.9 | 0 | 1.9 | 2021-08-13 | 22.6 | 0 | 4.6 | 2020-08-13 | 23.1 | 0 | 5.1 | 2019-08-13 | 20.4 | 0 | 2.4 | 2018-08-13 | 23.3 | 0 | 5.3 | 2017-08-13 | 18.1 | 0 | 0.1 | 2016-08-13 | 18.5 | 0 | 0.5 | 0 | 3.04
2025-08-13 | 26 | 0 | 8 | 2024-08-13 | 19.6 | 0 | 1.6 | 2023-08-13 | 17.1 | 0.9 | 0 | 2022-08-13 | 15.4 | 2.6 | 0 | 2021-08-13 | 23.4 | 0 | 5.4 | 2020-08-13 | 22 | 0 | 4 | 2019-08-13 | 20.1 | 0 | 2.1 | 2018-08-13 | 23.2 | 0 | 5.2 | 2017-08-13 | 18.7 | 0 | 0.7 | 2016-08-13 | 18.6 | 0 | 0.6 | 0.35 | 2.76
2025-08-13 | 24.3 | 0 | 6.3 | 2024-08-13 | 18.3 | 0 | 0.3 | 2023-08-13 | 16.7 | 1.3 | 0 | 2022-08-13 | 18.2 | 0 | 0.2 | 2021-08-13 | 23.8 | 0 | 5.8 | 2020-08-13 | 21.2 | 0 | 3.2 | 2019-08-13 | 19.4 | 0 | 1.4 | 2018-08-13 | 22.5 | 0 | 4.5 | 2017-08-13 | 17.7 | 0.3 | 0 | 2016-08-13 | 18.8 | 0 | 0.8 | 0.16 | 2.25
2025-08-13 | 23.8 | 0 | 5.8 | 2024-08-13 | 18.1 | 0 | 0.1 | 2023-08-13 | 15.9 | 2.1 | 0 | 2022-08-13 | 16.7 | 1.3 | 0 | 2021-08-13 | 23.9 | 0 | 5.9 | 2020-08-13 | 20.3 | 0 | 2.3 | 2019-08-13 | 18.7 | 0 | 0.7 | 2018-08-13 | 21.1 | 0 | 3.1 | 2017-08-13 | 17.5 | 0.5 | 0 | 2016-08-13 | 19.1 | 0 | 1.1 | 0.39 | 1.9
2025-08-14 | 22.5 | 0 | 4.5 | 2024-08-14 | 16.8 | 1.2 | 0 | 2023-08-14 | 16.1 | 1.9 | 0 | 2022-08-14 | 16.4 | 1.6 | 0 | 2021-08-14 | 21.8 | 0 | 3.8 | 2020-08-14 | 20.2 | 0 | 2.2 | 2019-08-14 | 18 | 0 | 0 | 2018-08-14 | 21.7 | 0 | 3.7 | 2017-08-14 | 16.4 | 1.6 | 0 | 2016-08-14 | 19.3 | 0 | 1.3 | 0.63 | 1.55
2025-08-14 | 21.6 | 0 | 3.6 | 2024-08-14 | 16.9 | 1.1 | 0 | 2023-08-14 | 15.8 | 2.2 | 0 | 2022-08-14 | 14.8 | 3.2 | 0 | 2021-08-14 | 20.9 | 0 | 2.9 | 2020-08-14 | 19.9 | 0 | 1.9 | 2019-08-14 | 17 | 1 | 0 | 2018-08-14 | 21.9 | 0 | 3.9 | 2017-08-14 | 15.7 | 2.3 | 0 | 2016-08-14 | 19.8 | 0 | 1.8 | 0.98 | 1.41
2025-08-14 | 20.9 | 0 | 2.9 | 2024-08-14 | 17.9 | 0.1 | 0 | 2023-08-14 | 15.8 | 2.2 | 0 | 2022-08-14 | 14.3 | 3.7 | 0 | 2021-08-14 | 21.6 | 0 | 3.6 | 2020-08-14 | 19.7 | 0 | 1.7 | 2019-08-14 | 16 | 2 | 0 | 2018-08-14 | 21.8 | 0 | 3.8 | 2017-08-14 | 14.5 | 3.5 | 0 | 2016-08-14 | 20.5 | 0 | 2.5 | 1.15 | 1.45
2025-08-14 | 20.2 | 0 | 2.2 | 2024-08-14 | 17.2 | 0.8 | 0 | 2023-08-14 | 15.7 | 2.3 | 0 | 2022-08-14 | 12.5 | 5.5 | 0 | 2021-08-14 | 20.4 | 0 | 2.4 | 2020-08-14 | 18 | 0 | 0 | 2019-08-14 | 15.2 | 2.8 | 0 | 2018-08-14 | 21.6 | 0 | 3.6 | 2017-08-14 | 14.5 | 3.5 | 0 | 2016-08-14 | 22.1 | 0 | 4.1 | 1.49 | 1.23
2025-08-14 | 19.6 | 0 | 1.6 | 2024-08-14 | 17.3 | 0.7 | 0 | 2023-08-14 | 14.9 | 3.1 | 0 | 2022-08-14 | 12.3 | 5.7 | 0 | 2021-08-14 | 19.4 | 0 | 1.4 | 2020-08-14 | 17.6 | 0.4 | 0 | 2019-08-14 | 14.4 | 3.6 | 0 | 2018-08-14 | 21.7 | 0 | 3.7 | 2017-08-14 | 14.4 | 3.6 | 0 | 2016-08-14 | 22.9 | 0 | 4.9 | 1.71 | 1.16
2025-08-14 | 18.9 | 0 | 0.9 | 2024-08-14 | 16.5 | 1.5 | 0 | 2023-08-14 | 14.1 | 3.9 | 0 | 2022-08-14 | 10.6 | 7.4 | 0 | 2021-08-14 | 17.8 | 0.2 | 0 | 2020-08-14 | 16.4 | 1.6 | 0 | 2019-08-14 | 13.7 | 4.3 | 0 | 2018-08-14 | 21.2 | 0 | 3.2 | 2017-08-14 | 14.2 | 3.8 | 0 | 2016-08-14 | 22.4 | 0 | 4.4 | 2.27 | 0.85
2025-08-14 | 18.9 | 0 | 0.9 | 2024-08-14 | 17.1 | 0.9 | 0 | 2023-08-14 | 15.1 | 2.9 | 0 | 2022-08-14 | 12.9 | 5.1 | 0 | 2021-08-14 | 16.7 | 1.3 | 0 | 2020-08-14 | 18.2 | 0 | 0.2 | 2019-08-14 | 14 | 4 | 0 | 2018-08-14 | 21.7 | 0 | 3.7 | 2017-08-14 | 14.2 | 3.8 | 0 | 2016-08-14 | 21.6 | 0 | 3.6 | 1.8 | 0.84
2025-08-14 | 20.3 | 0 | 2.3 | 2024-08-14 | 18.9 | 0 | 0.9 | 2023-08-14 | 16.4 | 1.6 | 0 | 2022-08-14 | 15.7 | 2.3 | 0 | 2021-08-14 | 17.5 | 0.5 | 0 | 2020-08-14 | 20.1 | 0 | 2.1 | 2019-08-14 | 15.7 | 2.3 | 0 | 2018-08-14 | 22.8 | 0 | 4.8 | 2017-08-14 | 16.8 | 1.2 | 0 | 2016-08-14 | 21 | 0 | 3 | 0.79 | 1.31
2025-08-14 | 21.6 | 0 | 3.6 | 2024-08-14 | 20.3 | 0 | 2.3 | 2023-08-14 | 17.2 | 0.8 | 0 | 2022-08-14 | 18.5 | 0 | 0.5 | 2021-08-14 | 19.7 | 0 | 1.7 | 2020-08-14 | 21.4 | 0 | 3.4 | 2019-08-14 | 17.2 | 0.8 | 0 | 2018-08-14 | 25.3 | 0 | 7.3 | 2017-08-14 | 18.6 | 0 | 0.6 | 2016-08-14 | 21.4 | 0 | 3.4 | 0.16 | 2.28
2025-08-14 | 23 | 0 | 5 | 2024-08-14 | 22.4 | 0 | 4.4 | 2023-08-14 | 17.2 | 0.8 | 0 | 2022-08-14 | 21.6 | 0 | 3.6 | 2021-08-14 | 21.3 | 0 | 3.3 | 2020-08-14 | 23 | 0 | 5 | 2019-08-14 | 19.2 | 0 | 1.2 | 2018-08-14 | 25.3 | 0 | 7.3 | 2017-08-14 | 20.4 | 0 | 2.4 | 2016-08-14 | 22.3 | 0 | 4.3 | 0.08 | 3.65
2025-08-14 | 24.3 | 0 | 6.3 | 2024-08-14 | 24.3 | 0 | 6.3 | 2023-08-14 | 18.9 | 0 | 0.9 | 2022-08-14 | 23.6 | 0 | 5.6 | 2021-08-14 | 23.2 | 0 | 5.2 | 2020-08-14 | 24.6 | 0 | 6.6 | 2019-08-14 | 20 | 0 | 2 | 2018-08-14 | 26.1 | 0 | 8.1 | 2017-08-14 | 22.1 | 0 | 4.1 | 2016-08-14 | 22.1 | 0 | 4.1 | 0 | 4.92
2025-08-14 | 25.1 | 0 | 7.1 | 2024-08-14 | 25.9 | 0 | 7.9 | 2023-08-14 | 20.2 | 0 | 2.2 | 2022-08-14 | 24.6 | 0 | 6.6 | 2021-08-14 | 23.6 | 0 | 5.6 | 2020-08-14 | 25.1 | 0 | 7.1 | 2019-08-14 | 21.4 | 0 | 3.4 | 2018-08-14 | 26 | 0 | 8 | 2017-08-14 | 23.5 | 0 | 5.5 | 2016-08-14 | 22.9 | 0 | 4.9 | 0 | 5.83
2025-08-14 | 25.9 | 0 | 7.9 | 2024-08-14 | 27.2 | 0 | 9.2 | 2023-08-14 | 21.4 | 0 | 3.4 | 2022-08-14 | 24.6 | 0 | 6.6 | 2021-08-14 | 23.4 | 0 | 5.4 | 2020-08-14 | 26.4 | 0 | 8.4 | 2019-08-14 | 22.9 | 0 | 4.9 | 2018-08-14 | 25.9 | 0 | 7.9 | 2017-08-14 | 24.7 | 0 | 6.7 | 2016-08-14 | 24.1 | 0 | 6.1 | 0 | 6.65
2025-08-14 | 26.4 | 0 | 8.4 | 2024-08-14 | 28.5 | 0 | 10.5 | 2023-08-14 | 21.9 | 0 | 3.9 | 2022-08-14 | 25.7 | 0 | 7.7 | 2021-08-14 | 23 | 0 | 5 | 2020-08-14 | 26.9 | 0 | 8.9 | 2019-08-14 | 22 | 0 | 4 | 2018-08-14 | 25.9 | 0 | 7.9 | 2017-08-14 | 25.1 | 0 | 7.1 | 2016-08-14 | 23.9 | 0 | 5.9 | 0 | 6.93
2025-08-14 | 25.9 | 0 | 7.9 | 2024-08-14 | 28.6 | 0 | 10.6 | 2023-08-14 | 21.5 | 0 | 3.5 | 2022-08-14 | 25.8 | 0 | 7.8 | 2021-08-14 | 23.2 | 0 | 5.2 | 2020-08-14 | 27.2 | 0 | 9.2 | 2019-08-14 | 22 | 0 | 4 | 2018-08-14 | 24.1 | 0 | 6.1 | 2017-08-14 | 26.3 | 0 | 8.3 | 2016-08-14 | 23.6 | 0 | 5.6 | 0 | 6.82
2025-08-14 | 26.2 | 0 | 8.2 | 2024-08-14 | 29.1 | 0 | 11.1 | 2023-08-14 | 21.7 | 0 | 3.7 | 2022-08-14 | 26.2 | 0 | 8.2 | 2021-08-14 | 23.1 | 0 | 5.1 | 2020-08-14 | 26.5 | 0 | 8.5 | 2019-08-14 | 23.1 | 0 | 5.1 | 2018-08-14 | 25.6 | 0 | 7.6 | 2017-08-14 | 25.9 | 0 | 7.9 | 2016-08-14 | 24.6 | 0 | 6.6 | 0 | 7.2
2025-08-14 | 26.1 | 0 | 8.1 | 2024-08-14 | 28.4 | 0 | 10.4 | 2023-08-14 | 22.8 | 0 | 4.8 | 2022-08-14 | 25.5 | 0 | 7.5 | 2021-08-14 | 22.7 | 0 | 4.7 | 2020-08-14 | 26.9 | 0 | 8.9 | 2019-08-14 | 21.9 | 0 | 3.9 | 2018-08-14 | 25.5 | 0 | 7.5 | 2017-08-14 | 24.9 | 0 | 6.9 | 2016-08-14 | 23 | 0 | 5 | 0 | 6.77
2025-08-14 | 25.7 | 0 | 7.7 | 2024-08-14 | 27.7 | 0 | 9.7 | 2023-08-14 | 22.6 | 0 | 4.6 | 2022-08-14 | 25.4 | 0 | 7.4 | 2021-08-14 | 22.5 | 0 | 4.5 | 2020-08-14 | 26.4 | 0 | 8.4 | 2019-08-14 | 22.7 | 0 | 4.7 | 2018-08-14 | 25.3 | 0 | 7.3 | 2017-08-14 | 25.3 | 0 | 7.3 | 2016-08-14 | 22.1 | 0 | 4.1 | 0 | 6.57
2025-08-14 | 24.6 | 0 | 6.6 | 2024-08-14 | 25.2 | 0 | 7.2 | 2023-08-14 | 21.5 | 0 | 3.5 | 2022-08-14 | 23.7 | 0 | 5.7 | 2021-08-14 | 21.6 | 0 | 3.6 | 2020-08-14 | 25.2 | 0 | 7.2 | 2019-08-14 | 21.9 | 0 | 3.9 | 2018-08-14 | 24.3 | 0 | 6.3 | 2017-08-14 | 23.7 | 0 | 5.7 | 2016-08-14 | 21.2 | 0 | 3.2 | 0 | 5.29
2025-08-14 | 22.6 | 0 | 4.6 | 2024-08-14 | 22.9 | 0 | 4.9 | 2023-08-14 | 19.7 | 0 | 1.7 | 2022-08-14 | 21.4 | 0 | 3.4 | 2021-08-14 | 20.1 | 0 | 2.1 | 2020-08-14 | 21.8 | 0 | 3.8 | 2019-08-14 | 19.8 | 0 | 1.8 | 2018-08-14 | 23.8 | 0 | 5.8 | 2017-08-14 | 21.8 | 0 | 3.8 | 2016-08-14 | 20.7 | 0 | 2.7 | 0 | 3.46
2025-08-14 | 20.8 | 0 | 2.8 | 2024-08-14 | 22.9 | 0 | 4.9 | 2023-08-14 | 19.3 | 0 | 1.3 | 2022-08-14 | 18.9 | 0 | 0.9 | 2021-08-14 | 17.9 | 0.1 | 0 | 2020-08-14 | 20.3 | 0 | 2.3 | 2019-08-14 | 18.4 | 0 | 0.4 | 2018-08-14 | 22.7 | 0 | 4.7 | 2017-08-14 | 20 | 0 | 2 | 2016-08-14 | 20.2 | 0 | 2.2 | 0.01 | 2.15
2025-08-14 | 19.7 | 0 | 1.7 | 2024-08-14 | 20.8 | 0 | 2.8 | 2023-08-14 | 17.7 | 0.3 | 0 | 2022-08-14 | 16.4 | 1.6 | 0 | 2021-08-14 | 17.4 | 0.6 | 0 | 2020-08-14 | 16.5 | 1.5 | 0 | 2019-08-14 | 16.1 | 1.9 | 0 | 2018-08-14 | 21.9 | 0 | 3.9 | 2017-08-14 | 19.4 | 0 | 1.4 | 2016-08-14 | 18.8 | 0 | 0.8 | 0.59 | 1.06
2025-08-14 | 16.5 | 1.5 | 0 | 2024-08-14 | 20.2 | 0 | 2.2 | 2023-08-14 | 17.9 | 0.1 | 0 | 2022-08-14 | 17.2 | 0.8 | 0 | 2021-08-14 | 17.1 | 0.9 | 0 | 2020-08-14 | 17.6 | 0.4 | 0 | 2019-08-14 | 15.8 | 2.2 | 0 | 2018-08-14 | 21.9 | 0 | 3.9 | 2017-08-14 | 19.1 | 0 | 1.1 | 2016-08-14 | 18.2 | 0 | 0.2 | 0.59 | 0.74
2025-08-14 | 16.2 | 1.8 | 0 | 2024-08-14 | 20.3 | 0 | 2.3 | 2023-08-14 | 15.7 | 2.3 | 0 | 2022-08-14 | 16.7 | 1.3 | 0 | 2021-08-14 | 17.3 | 0.7 | 0 | 2020-08-14 | 18.1 | 0 | 0.1 | 2019-08-14 | 15.3 | 2.7 | 0 | 2018-08-14 | 21 | 0 | 3 | 2017-08-14 | 18.6 | 0 | 0.6 | 2016-08-14 | 17.8 | 0.2 | 0 | 0.9 | 0.6
2025-08-15 | 16.1 | 1.9 | 0 | 2024-08-15 | 19.1 | 0 | 1.1 | 2023-08-15 | 15.4 | 2.6 | 0 | 2022-08-15 | 16.9 | 1.1 | 0 | 2021-08-15 | 14.9 | 3.1 | 0 | 2020-08-15 | 17.4 | 0.6 | 0 | 2019-08-15 | 12.5 | 5.5 | 0 | 2018-08-15 | 20.2 | 0 | 2.2 | 2017-08-15 | 18.8 | 0 | 0.8 | 2016-08-15 | 15.5 | 2.5 | 0 | 1.73 | 0.41
2025-08-15 | 15.7 | 2.3 | 0 | 2024-08-15 | 17.9 | 0.1 | 0 | 2023-08-15 | 15.7 | 2.3 | 0 | 2022-08-15 | 16 | 2 | 0 | 2021-08-15 | 12.1 | 5.9 | 0 | 2020-08-15 | 15.9 | 2.1 | 0 | 2019-08-15 | 12.7 | 5.3 | 0 | 2018-08-15 | 20.1 | 0 | 2.1 | 2017-08-15 | 17.2 | 0.8 | 0 | 2016-08-15 | 15.4 | 2.6 | 0 | 2.34 | 0.21
2025-08-15 | 15.3 | 2.7 | 0 | 2024-08-15 | 19.7 | 0 | 1.7 | 2023-08-15 | 16.4 | 1.6 | 0 | 2022-08-15 | 14.4 | 3.6 | 0 | 2021-08-15 | 12.8 | 5.2 | 0 | 2020-08-15 | 15 | 3 | 0 | 2019-08-15 | 11.9 | 6.1 | 0 | 2018-08-15 | 19.9 | 0 | 1.9 | 2017-08-15 | 17.4 | 0.6 | 0 | 2016-08-15 | 15.7 | 2.3 | 0 | 2.51 | 0.36
2025-08-15 | 14.3 | 3.7 | 0 | 2024-08-15 | 19.5 | 0 | 1.5 | 2023-08-15 | 15.9 | 2.1 | 0 | 2022-08-15 | 12.6 | 5.4 | 0 | 2021-08-15 | 12 | 6 | 0 | 2020-08-15 | 14.9 | 3.1 | 0 | 2019-08-15 | 10.4 | 7.6 | 0 | 2018-08-15 | 19.1 | 0 | 1.1 | 2017-08-15 | 16.8 | 1.2 | 0 | 2016-08-15 | 15 | 3 | 0 | 3.21 | 0.26
2025-08-15 | 13.8 | 4.2 | 0 | 2024-08-15 | 18.4 | 0 | 0.4 | 2023-08-15 | 15.4 | 2.6 | 0 | 2022-08-15 | 11.6 | 6.4 | 0 | 2021-08-15 | 11.8 | 6.2 | 0 | 2020-08-15 | 14.2 | 3.8 | 0 | 2019-08-15 | 9.9 | 8.1 | 0 | 2018-08-15 | 17.9 | 0.1 | 0 | 2017-08-15 | 16.6 | 1.4 | 0 | 2016-08-15 | 15.7 | 2.3 | 0 | 3.51 | 0.04
2025-08-15 | 11.7 | 6.3 | 0 | 2024-08-15 | 17.6 | 0.4 | 0 | 2023-08-15 | 15.7 | 2.3 | 0 | 2022-08-15 | 12.9 | 5.1 | 0 | 2021-08-15 | 11.7 | 6.3 | 0 | 2020-08-15 | 14.1 | 3.9 | 0 | 2019-08-15 | 10 | 8 | 0 | 2018-08-15 | 17.9 | 0.1 | 0 | 2017-08-15 | 17.3 | 0.7 | 0 | 2016-08-15 | 15.3 | 2.7 | 0 | 3.58 | 0
2025-08-15 | 14 | 4 | 0 | 2024-08-15 | 17.8 | 0.2 | 0 | 2023-08-15 | 16.1 | 1.9 | 0 | 2022-08-15 | 14.4 | 3.6 | 0 | 2021-08-15 | 12.7 | 5.3 | 0 | 2020-08-15 | 15.2 | 2.8 | 0 | 2019-08-15 | 11.7 | 6.3 | 0 | 2018-08-15 | 18.9 | 0 | 0.9 | 2017-08-15 | 16.9 | 1.1 | 0 | 2016-08-15 | 16.2 | 1.8 | 0 | 2.7 | 0.09
2025-08-15 | 16.8 | 1.2 | 0 | 2024-08-15 | 19.8 | 0 | 1.8 | 2023-08-15 | 16.9 | 1.1 | 0 | 2022-08-15 | 18 | 0 | 0 | 2021-08-15 | 13.9 | 4.1 | 0 | 2020-08-15 | 17.8 | 0.2 | 0 | 2019-08-15 | 14.5 | 3.5 | 0 | 2018-08-15 | 20.3 | 0 | 2.3 | 2017-08-15 | 17.7 | 0.3 | 0 | 2016-08-15 | 18 | 0 | 0 | 1.04 | 0.41
2025-08-15 | 18.8 | 0 | 0.8 | 2024-08-15 | 21.4 | 0 | 3.4 | 2023-08-15 | 17.8 | 0.2 | 0 | 2022-08-15 | 20.2 | 0 | 2.2 | 2021-08-15 | 16.9 | 1.1 | 0 | 2020-08-15 | 19.4 | 0 | 1.4 | 2019-08-15 | 17.6 | 0.4 | 0 | 2018-08-15 | 22.3 | 0 | 4.3 | 2017-08-15 | 19 | 0 | 1 | 2016-08-15 | 19.9 | 0 | 1.9 | 0.17 | 1.5
2025-08-15 | 20.4 | 0 | 2.4 | 2024-08-15 | 23.4 | 0 | 5.4 | 2023-08-15 | 18.7 | 0 | 0.7 | 2022-08-15 | 22.2 | 0 | 4.2 | 2021-08-15 | 19.6 | 0 | 1.6 | 2020-08-15 | 21.5 | 0 | 3.5 | 2019-08-15 | 19.5 | 0 | 1.5 | 2018-08-15 | 23.5 | 0 | 5.5 | 2017-08-15 | 21.5 | 0 | 3.5 | 2016-08-15 | 22.4 | 0 | 4.4 | 0 | 3.27
2025-08-15 | 23.2 | 0 | 5.2 | 2024-08-15 | 24.9 | 0 | 6.9 | 2023-08-15 | 20.3 | 0 | 2.3 | 2022-08-15 | 23.9 | 0 | 5.9 | 2021-08-15 | 20.7 | 0 | 2.7 | 2020-08-15 | 23.1 | 0 | 5.1 | 2019-08-15 | 20.7 | 0 | 2.7 | 2018-08-15 | 22.1 | 0 | 4.1 | 2017-08-15 | 23 | 0 | 5 | 2016-08-15 | 24.4 | 0 | 6.4 | 0 | 4.63
2025-08-15 | 23.7 | 0 | 5.7 | 2024-08-15 | 26.3 | 0 | 8.3 | 2023-08-15 | 21.3 | 0 | 3.3 | 2022-08-15 | 25.2 | 0 | 7.2 | 2021-08-15 | 21.7 | 0 | 3.7 | 2020-08-15 | 24.7 | 0 | 6.7 | 2019-08-15 | 21.7 | 0 | 3.7 | 2018-08-15 | 22.9 | 0 | 4.9 | 2017-08-15 | 24 | 0 | 6 | 2016-08-15 | 25.2 | 0 | 7.2 | 0 | 5.67
2025-08-15 | 25.4 | 0 | 7.4 | 2024-08-15 | 27.9 | 0 | 9.9 | 2023-08-15 | 21.7 | 0 | 3.7 | 2022-08-15 | 26.6 | 0 | 8.6 | 2021-08-15 | 22.7 | 0 | 4.7 | 2020-08-15 | 26.1 | 0 | 8.1 | 2019-08-15 | 23.3 | 0 | 5.3 | 2018-08-15 | 23.5 | 0 | 5.5 | 2017-08-15 | 24.7 | 0 | 6.7 | 2016-08-15 | 25.8 | 0 | 7.8 | 0 | 6.77
2025-08-15 | 26.5 | 0 | 8.5 | 2024-08-15 | 28.8 | 0 | 10.8 | 2023-08-15 | 22.4 | 0 | 4.4 | 2022-08-15 | 26.9 | 0 | 8.9 | 2021-08-15 | 23.6 | 0 | 5.6 | 2020-08-15 | 27.6 | 0 | 9.6 | 2019-08-15 | 22.9 | 0 | 4.9 | 2018-08-15 | 24.5 | 0 | 6.5 | 2017-08-15 | 24.2 | 0 | 6.2 | 2016-08-15 | 26.6 | 0 | 8.6 | 0 | 7.4
2025-08-15 | 26.7 | 0 | 8.7 | 2024-08-15 | 29.5 | 0 | 11.5 | 2023-08-15 | 23 | 0 | 5 | 2022-08-15 | 26.2 | 0 | 8.2 | 2021-08-15 | 23.3 | 0 | 5.3 | 2020-08-15 | 28.1 | 0 | 10.1 | 2019-08-15 | 23.8 | 0 | 5.8 | 2018-08-15 | 24.6 | 0 | 6.6 | 2017-08-15 | 21.5 | 0 | 3.5 | 2016-08-15 | 27.4 | 0 | 9.4 | 0 | 7.41
2025-08-15 | 27.6 | 0 | 9.6 | 2024-08-15 | 29.8 | 0 | 11.8 | 2023-08-15 | 23.1 | 0 | 5.1 | 2022-08-15 | 25.7 | 0 | 7.7 | 2021-08-15 | 23.9 | 0 | 5.9 | 2020-08-15 | 28.3 | 0 | 10.3 | 2019-08-15 | 24 | 0 | 6 | 2018-08-15 | 25 | 0 | 7 | 2017-08-15 | 18.3 | 0 | 0.3 | 2016-08-15 | 27 | 0 | 9 | 0 | 7.27
2025-08-15 | 28.2 | 0 | 10.2 | 2024-08-15 | 29.3 | 0 | 11.3 | 2023-08-15 | 23 | 0 | 5 | 2022-08-15 | 26.2 | 0 | 8.2 | 2021-08-15 | 23.7 | 0 | 5.7 | 2020-08-15 | 28.3 | 0 | 10.3 | 2019-08-15 | 23.5 | 0 | 5.5 | 2018-08-15 | 25.2 | 0 | 7.2 | 2017-08-15 | 18.6 | 0 | 0.6 | 2016-08-15 | 27.2 | 0 | 9.2 | 0 | 7.32
2025-08-15 | 27.6 | 0 | 9.6 | 2024-08-15 | 28.8 | 0 | 10.8 | 2023-08-15 | 23.4 | 0 | 5.4 | 2022-08-15 | 25.5 | 0 | 7.5 | 2021-08-15 | 23.5 | 0 | 5.5 | 2020-08-15 | 27.7 | 0 | 9.7 | 2019-08-15 | 22.1 | 0 | 4.1 | 2018-08-15 | 24.7 | 0 | 6.7 | 2017-08-15 | 20.5 | 0 | 2.5 | 2016-08-15 | 27.5 | 0 | 9.5 | 0 | 7.13
2025-08-15 | 26.7 | 0 | 8.7 | 2024-08-15 | 27.7 | 0 | 9.7 | 2023-08-15 | 23.1 | 0 | 5.1 | 2022-08-15 | 24.5 | 0 | 6.5 | 2021-08-15 | 22.4 | 0 | 4.4 | 2020-08-15 | 26.3 | 0 | 8.3 | 2019-08-15 | 21.9 | 0 | 3.9 | 2018-08-15 | 23.8 | 0 | 5.8 | 2017-08-15 | 20.2 | 0 | 2.2 | 2016-08-15 | 25 | 0 | 7 | 0 | 6.16
2025-08-15 | 23.6 | 0 | 5.6 | 2024-08-15 | 25.4 | 0 | 7.4 | 2023-08-15 | 21.3 | 0 | 3.3 | 2022-08-15 | 22.3 | 0 | 4.3 | 2021-08-15 | 20.5 | 0 | 2.5 | 2020-08-15 | 23.7 | 0 | 5.7 | 2019-08-15 | 20.9 | 0 | 2.9 | 2018-08-15 | 23.3 | 0 | 5.3 | 2017-08-15 | 18.8 | 0 | 0.8 | 2016-08-15 | 22 | 0 | 4 | 0 | 4.18
2025-08-15 | 20 | 0 | 2 | 2024-08-15 | 22.7 | 0 | 4.7 | 2023-08-15 | 19.4 | 0 | 1.4 | 2022-08-15 | 22.1 | 0 | 4.1 | 2021-08-15 | 16.4 | 1.6 | 0 | 2020-08-15 | 22.9 | 0 | 4.9 | 2019-08-15 | 18.8 | 0 | 0.8 | 2018-08-15 | 22.2 | 0 | 4.2 | 2017-08-15 | 18.4 | 0 | 0.4 | 2016-08-15 | 21.6 | 0 | 3.6 | 0.16 | 2.61
2025-08-15 | 19.9 | 0 | 1.9 | 2024-08-15 | 22 | 0 | 4 | 2023-08-15 | 19.2 | 0 | 1.2 | 2022-08-15 | 21.4 | 0 | 3.4 | 2021-08-15 | 16.4 | 1.6 | 0 | 2020-08-15 | 21.4 | 0 | 3.4 | 2019-08-15 | 17.9 | 0.1 | 0 | 2018-08-15 | 21.9 | 0 | 3.9 | 2017-08-15 | 18.8 | 0 | 0.8 | 2016-08-15 | 20.6 | 0 | 2.6 | 0.17 | 2.12
2025-08-15 | 19.6 | 0 | 1.6 | 2024-08-15 | 20.4 | 0 | 2.4 | 2023-08-15 | 18.2 | 0 | 0.2 | 2022-08-15 | 21.4 | 0 | 3.4 | 2021-08-15 | 16.1 | 1.9 | 0 | 2020-08-15 | 21 | 0 | 3 | 2019-08-15 | 17.4 | 0.6 | 0 | 2018-08-15 | 21.5 | 0 | 3.5 | 2017-08-15 | 19.3 | 0 | 1.3 | 2016-08-15 | 20 | 0 | 2 | 0.25 | 1.74
2025-08-15 | 18.2 | 0 | 0.2 | 2024-08-15 | 19.5 | 0 | 1.5 | 2023-08-15 | 17.8 | 0.2 | 0 | 2022-08-15 | 20.5 | 0 | 2.5 | 2021-08-15 | 15.1 | 2.9 | 0 | 2020-08-15 | 19.9 | 0 | 1.9 | 2019-08-15 | 17.8 | 0.2 | 0 | 2018-08-15 | 21.1 | 0 | 3.1 | 2017-08-15 | 19.1 | 0 | 1.1 | 2016-08-15 | 19.5 | 0 | 1.5 | 0.33 | 1.18
2025-08-16 | 18.5 | 0 | 0.5 | 2024-08-16 | 18.3 | 0 | 0.3 | 2023-08-16 | 19.3 | 0 | 1.3 | 2022-08-16 | 19.1 | 0 | 1.1 | 2021-08-16 | 15.1 | 2.9 | 0 | 2020-08-16 | 19.8 | 0 | 1.8 | 2019-08-16 | 16.3 | 1.7 | 0 | 2018-08-16 | 20.6 | 0 | 2.6 | 2017-08-16 | 18 | 0 | 0 | 2016-08-16 | 18.2 | 0 | 0.2 | 0.46 | 0.78
2025-08-16 | 17.8 | 0.2 | 0 | 2024-08-16 | 18.3 | 0 | 0.3 | 2023-08-16 | 18.5 | 0 | 0.5 | 2022-08-16 | 19.2 | 0 | 1.2 | 2021-08-16 | 14.1 | 3.9 | 0 | 2020-08-16 | 18.6 | 0 | 0.6 | 2019-08-16 | 15.4 | 2.6 | 0 | 2018-08-16 | 20.1 | 0 | 2.1 | 2017-08-16 | 16.3 | 1.7 | 0 | 2016-08-16 | 17.7 | 0.3 | 0 | 0.87 | 0.47
2025-08-16 | 14.6 | 3.4 | 0 | 2024-08-16 | 16.9 | 1.1 | 0 | 2023-08-16 | 18.6 | 0 | 0.6 | 2022-08-16 | 18.1 | 0 | 0.1 | 2021-08-16 | 13.4 | 4.6 | 0 | 2020-08-16 | 17.2 | 0.8 | 0 | 2019-08-16 | 15.7 | 2.3 | 0 | 2018-08-16 | 18.3 | 0 | 0.3 | 2017-08-16 | 15.6 | 2.4 | 0 | 2016-08-16 | 16.2 | 1.8 | 0 | 1.64 | 0.1
2025-08-16 | 15.6 | 2.4 | 0 | 2024-08-16 | 17.6 | 0.4 | 0 | 2023-08-16 | 16.9 | 1.1 | 0 | 2022-08-16 | 17.5 | 0.5 | 0 | 2021-08-16 | 12.3 | 5.7 | 0 | 2020-08-16 | 17.3 | 0.7 | 0 | 2019-08-16 | 15.3 | 2.7 | 0 | 2018-08-16 | 16 | 2 | 0 | 2017-08-16 | 13.4 | 4.6 | 0 | 2016-08-16 | 17 | 1 | 0 | 2.11 | 0
2025-08-16 | 14.2 | 3.8 | 0 | 2024-08-16 | 18.2 | 0 | 0.2 | 2023-08-16 | 17.3 | 0.7 | 0 | 2022-08-16 | 16.3 | 1.7 | 0 | 2021-08-16 | 10.9 | 7.1 | 0 | 2020-08-16 | 16.8 | 1.2 | 0 | 2019-08-16 | 15.1 | 2.9 | 0 | 2018-08-16 | 14.5 | 3.5 | 0 | 2017-08-16 | 13.7 | 4.3 | 0 | 2016-08-16 | 16.6 | 1.4 | 0 | 2.66 | 0.02
2025-08-16 | 13.8 | 4.2 | 0 | 2024-08-16 | 17.1 | 0.9 | 0 | 2023-08-16 | 17.5 | 0.5 | 0 | 2022-08-16 | 16.9 | 1.1 | 0 | 2021-08-16 | 10.1 | 7.9 | 0 | 2020-08-16 | 15.8 | 2.2 | 0 | 2019-08-16 | 14.2 | 3.8 | 0 | 2018-08-16 | 14.4 | 3.6 | 0 | 2017-08-16 | 12.1 | 5.9 | 0 | 2016-08-16 | 16.6 | 1.4 | 0 | 3.15 | 0
2025-08-16 | 15.2 | 2.8 | 0 | 2024-08-16 | 18 | 0 | 0 | 2023-08-16 | 17.2 | 0.8 | 0 | 2022-08-16 | 17.6 | 0.4 | 0 | 2021-08-16 | 12.2 | 5.8 | 0 | 2020-08-16 | 16.6 | 1.4 | 0 | 2019-08-16 | 15.3 | 2.7 | 0 | 2018-08-16 | 15.3 | 2.7 | 0 | 2017-08-16 | 13.8 | 4.2 | 0 | 2016-08-16 | 17.3 | 0.7 | 0 | 2.15 | 0
2025-08-16 | 17.9 | 0.1 | 0 | 2024-08-16 | 19.2 | 0 | 1.2 | 2023-08-16 | 17.8 | 0.2 | 0 | 2022-08-16 | 19.1 | 0 | 1.1 | 2021-08-16 | 16.1 | 1.9 | 0 | 2020-08-16 | 17.9 | 0.1 | 0 | 2019-08-16 | 17.4 | 0.6 | 0 | 2018-08-16 | 16.4 | 1.6 | 0 | 2017-08-16 | 15.6 | 2.4 | 0 | 2016-08-16 | 18.7 | 0 | 0.7 | 0.69 | 0.3
2025-08-16 | 20.4 | 0 | 2.4 | 2024-08-16 | 21.3 | 0 | 3.3 | 2023-08-16 | 19.9 | 0 | 1.9 | 2022-08-16 | 21 | 0 | 3 | 2021-08-16 | 18.7 | 0 | 0.7 | 2020-08-16 | 21.2 | 0 | 3.2 | 2019-08-16 | 19.3 | 0 | 1.3 | 2018-08-16 | 17.7 | 0.3 | 0 | 2017-08-16 | 16.9 | 1.1 | 0 | 2016-08-16 | 20.4 | 0 | 2.4 | 0.14 | 1.82
2025-08-16 | 24.3 | 0 | 6.3 | 2024-08-16 | 23.7 | 0 | 5.7 | 2023-08-16 | 22.3 | 0 | 4.3 | 2022-08-16 | 22.2 | 0 | 4.2 | 2021-08-16 | 21.5 | 0 | 3.5 | 2020-08-16 | 22.6 | 0 | 4.6 | 2019-08-16 | 20.2 | 0 | 2.2 | 2018-08-16 | 19.1 | 0 | 1.1 | 2017-08-16 | 18.5 | 0 | 0.5 | 2016-08-16 | 20.9 | 0 | 2.9 | 0 | 3.53
2025-08-16 | 27.4 | 0 | 9.4 | 2024-08-16 | 25.6 | 0 | 7.6 | 2023-08-16 | 22.5 | 0 | 4.5 | 2022-08-16 | 24.3 | 0 | 6.3 | 2021-08-16 | 23.1 | 0 | 5.1 | 2020-08-16 | 23.8 | 0 | 5.8 | 2019-08-16 | 22.1 | 0 | 4.1 | 2018-08-16 | 20.1 | 0 | 2.1 | 2017-08-16 | 19.5 | 0 | 1.5 | 2016-08-16 | 22 | 0 | 4 | 0 | 5.04
2025-08-16 | 28.8 | 0 | 10.8 | 2024-08-16 | 27.4 | 0 | 9.4 | 2023-08-16 | 24.9 | 0 | 6.9 | 2022-08-16 | 26 | 0 | 8 | 2021-08-16 | 23.6 | 0 | 5.6 | 2020-08-16 | 26.1 | 0 | 8.1 | 2019-08-16 | 23.5 | 0 | 5.5 | 2018-08-16 | 20.9 | 0 | 2.9 | 2017-08-16 | 20.2 | 0 | 2.2 | 2016-08-16 | 20.7 | 0 | 2.7 | 0 | 6.21
2025-08-16 | 30.4 | 0 | 12.4 | 2024-08-16 | 28.8 | 0 | 10.8 | 2023-08-16 | 25.4 | 0 | 7.4 | 2022-08-16 | 26.7 | 0 | 8.7 | 2021-08-16 | 23.9 | 0 | 5.9 | 2020-08-16 | 27.1 | 0 | 9.1 | 2019-08-16 | 24.6 | 0 | 6.6 | 2018-08-16 | 22.3 | 0 | 4.3 | 2017-08-16 | 21.4 | 0 | 3.4 | 2016-08-16 | 19.3 | 0 | 1.3 | 0 | 6.99
2025-08-16 | 31.5 | 0 | 13.5 | 2024-08-16 | 29.7 | 0 | 11.7 | 2023-08-16 | 26.4 | 0 | 8.4 | 2022-08-16 | 26.7 | 0 | 8.7 | 2021-08-16 | 24.8 | 0 | 6.8 | 2020-08-16 | 28.1 | 0 | 10.1 | 2019-08-16 | 24.5 | 0 | 6.5 | 2018-08-16 | 22.5 | 0 | 4.5 | 2017-08-16 | 22.3 | 0 | 4.3 | 2016-08-16 | 18.8 | 0 | 0.8 | 0 | 7.53
2025-08-16 | 31.4 | 0 | 13.4 | 2024-08-16 | 29.1 | 0 | 11.1 | 2023-08-16 | 27.2 | 0 | 9.2 | 2022-08-16 | 25.9 | 0 | 7.9 | 2021-08-16 | 25.8 | 0 | 7.8 | 2020-08-16 | 27.6 | 0 | 9.6 | 2019-08-16 | 25.8 | 0 | 7.8 | 2018-08-16 | 23.5 | 0 | 5.5 | 2017-08-16 | 23 | 0 | 5 | 2016-08-16 | 18 | 0 | 0 | 0 | 7.73
2025-08-16 | 32.2 | 0 | 14.2 | 2024-08-16 | 29.2 | 0 | 11.2 | 2023-08-16 | 27.4 | 0 | 9.4 | 2022-08-16 | 26.5 | 0 | 8.5 | 2021-08-16 | 25 | 0 | 7 | 2020-08-16 | 22 | 0 | 4 | 2019-08-16 | 25.5 | 0 | 7.5 | 2018-08-16 | 24.4 | 0 | 6.4 | 2017-08-16 | 23.5 | 0 | 5.5 | 2016-08-16 | 18.4 | 0 | 0.4 | 0 | 7.41
2025-08-16 | 31.4 | 0 | 13.4 | 2024-08-16 | 28.7 | 0 | 10.7 | 2023-08-16 | 27.2 | 0 | 9.2 | 2022-08-16 | 26.6 | 0 | 8.6 | 2021-08-16 | 25.3 | 0 | 7.3 | 2020-08-16 | 19.4 | 0 | 1.4 | 2019-08-16 | 26.1 | 0 | 8.1 | 2018-08-16 | 24.5 | 0 | 6.5 | 2017-08-16 | 22.9 | 0 | 4.9 | 2016-08-16 | 17.9 | 0.1 | 0 | 0.01 | 7.01
2025-08-16 | 31.6 | 0 | 13.6 | 2024-08-16 | 27.9 | 0 | 9.9 | 2023-08-16 | 25.9 | 0 | 7.9 | 2022-08-16 | 26.1 | 0 | 8.1 | 2021-08-16 | 24.6 | 0 | 6.6 | 2020-08-16 | 18.8 | 0 | 0.8 | 2019-08-16 | 25.6 | 0 | 7.6 | 2018-08-16 | 24.9 | 0 | 6.9 | 2017-08-16 | 22.7 | 0 | 4.7 | 2016-08-16 | 17 | 1 | 0 | 0.1 | 6.61
2025-08-16 | 30.4 | 0 | 12.4 | 2024-08-16 | 25.9 | 0 | 7.9 | 2023-08-16 | 24.6 | 0 | 6.6 | 2022-08-16 | 25.4 | 0 | 7.4 | 2021-08-16 | 23.2 | 0 | 5.2 | 2020-08-16 | 18.4 | 0 | 0.4 | 2019-08-16 | 24.3 | 0 | 6.3 | 2018-08-16 | 24.2 | 0 | 6.2 | 2017-08-16 | 21.2 | 0 | 3.2 | 2016-08-16 | 17.2 | 0.8 | 0 | 0.08 | 5.56
2025-08-16 | 27.7 | 0 | 9.7 | 2024-08-16 | 22.5 | 0 | 4.5 | 2023-08-16 | 22.4 | 0 | 4.4 | 2022-08-16 | 23.3 | 0 | 5.3 | 2021-08-16 | 19.6 | 0 | 1.6 | 2020-08-16 | 18.6 | 0 | 0.6 | 2019-08-16 | 22.6 | 0 | 4.6 | 2018-08-16 | 20.5 | 0 | 2.5 | 2017-08-16 | 17.9 | 0.1 | 0 | 2016-08-16 | 17.2 | 0.8 | 0 | 0.09 | 3.32
2025-08-16 | 26 | 0 | 8 | 2024-08-16 | 22.2 | 0 | 4.2 | 2023-08-16 | 21.1 | 0 | 3.1 | 2022-08-16 | 22.1 | 0 | 4.1 | 2021-08-16 | 18.5 | 0 | 0.5 | 2020-08-16 | 17.9 | 0.1 | 0 | 2019-08-16 | 21.1 | 0 | 3.1 | 2018-08-16 | 19.4 | 0 | 1.4 | 2017-08-16 | 17.1 | 0.9 | 0 | 2016-08-16 | 17.9 | 0.1 | 0 | 0.11 | 2.44
2025-08-16 | 24.5 | 0 | 6.5 | 2024-08-16 | 20 | 0 | 2 | 2023-08-16 | 20.6 | 0 | 2.6 | 2022-08-16 | 20.7 | 0 | 2.7 | 2021-08-16 | 17.7 | 0.3 | 0 | 2020-08-16 | 17.5 | 0.5 | 0 | 2019-08-16 | 20.5 | 0 | 2.5 | 2018-08-16 | 18.6 | 0 | 0.6 | 2017-08-16 | 15 | 3 | 0 | 2016-08-16 | 17.5 | 0.5 | 0 | 0.43 | 1.69
2025-08-16 | 23.9 | 0 | 5.9 | 2024-08-16 | 20.2 | 0 | 2.2 | 2023-08-16 | 20.1 | 0 | 2.1 | 2022-08-16 | 19 | 0 | 1 | 2021-08-16 | 17.7 | 0.3 | 0 | 2020-08-16 | 17.8 | 0.2 | 0 | 2019-08-16 | 20 | 0 | 2 | 2018-08-16 | 18.7 | 0 | 0.7 | 2017-08-16 | 14.2 | 3.8 | 0 | 2016-08-16 | 17.6 | 0.4 | 0 | 0.47 | 1.39
2025-08-16 | 23.1 | 0 | 5.1 | 2024-08-16 | 19.6 | 0 | 1.6 | 2023-08-16 | 19.3 | 0 | 1.3 | 2022-08-16 | 18.1 | 0 | 0.1 | 2021-08-16 | 16.9 | 1.1 | 0 | 2020-08-16 | 17.9 | 0.1 | 0 | 2019-08-16 | 19 | 0 | 1 | 2018-08-16 | 17.9 | 0.1 | 0 | 2017-08-16 | 14.3 | 3.7 | 0 | 2016-08-16 | 17.4 | 0.6 | 0 | 0.56 | 0.91
2025-08-17 | 21.4 | 0 | 3.4 | 2024-08-17 | 19.7 | 0 | 1.7 | 2023-08-17 | 19 | 0 | 1 | 2022-08-17 | 18.8 | 0 | 0.8 | 2021-08-17 | 15.5 | 2.5 | 0 | 2020-08-17 | 17.5 | 0.5 | 0 | 2019-08-17 | 18.6 | 0 | 0.6 | 2018-08-17 | 17.8 | 0.2 | 0 | 2017-08-17 | 12.7 | 5.3 | 0 | 2016-08-17 | 17.1 | 0.9 | 0 | 0.94 | 0.75
2025-08-17 | 20.5 | 0 | 2.5 | 2024-08-17 | 21.1 | 0 | 3.1 | 2023-08-17 | 18.2 | 0 | 0.2 | 2022-08-17 | 17.5 | 0.5 | 0 | 2021-08-17 | 15.5 | 2.5 | 0 | 2020-08-17 | 17.2 | 0.8 | 0 | 2019-08-17 | 18.6 | 0 | 0.6 | 2018-08-17 | 17.6 | 0.4 | 0 | 2017-08-17 | 11.6 | 6.4 | 0 | 2016-08-17 | 16.7 | 1.3 | 0 | 1.19 | 0.64
2025-08-17 | 20.5 | 0 | 2.5 | 2024-08-17 | 20.5 | 0 | 2.5 | 2023-08-17 | 17.5 | 0.5 | 0 | 2022-08-17 | 17.6 | 0.4 | 0 | 2021-08-17 | 15.9 | 2.1 | 0 | 2020-08-17 | 17.3 | 0.7 | 0 | 2019-08-17 | 18.1 | 0 | 0.1 | 2018-08-17 | 17.7 | 0.3 | 0 | 2017-08-17 | 12.5 | 5.5 | 0 | 2016-08-17 | 16.7 | 1.3 | 0 | 1.08 | 0.51
2025-08-17 | 20.2 | 0 | 2.2 | 2024-08-17 | 19.9 | 0 | 1.9 | 2023-08-17 | 16.9 | 1.1 | 0 | 2022-08-17 | 17.3 | 0.7 | 0 | 2021-08-17 | 16.1 | 1.9 | 0 | 2020-08-17 | 17.2 | 0.8 | 0 | 2019-08-17 | 18.4 | 0 | 0.4 | 2018-08-17 | 16.1 | 1.9 | 0 | 2017-08-17 | 12.2 | 5.8 | 0 | 2016-08-17 | 16.2 | 1.8 | 0 | 1.4 | 0.45
2025-08-17 | 19.7 | 0 | 1.7 | 2024-08-17 | 19.9 | 0 | 1.9 | 2023-08-17 | 16.7 | 1.3 | 0 | 2022-08-17 | 18.4 | 0 | 0.4 | 2021-08-17 | 15.9 | 2.1 | 0 | 2020-08-17 | 17.3 | 0.7 | 0 | 2019-08-17 | 18.1 | 0 | 0.1 | 2018-08-17 | 16.8 | 1.2 | 0 | 2017-08-17 | 11.4 | 6.6 | 0 | 2016-08-17 | 16.2 | 1.8 | 0 | 1.37 | 0.41
2025-08-17 | 19.5 | 0 | 1.5 | 2024-08-17 | 19.4 | 0 | 1.4 | 2023-08-17 | 16.5 | 1.5 | 0 | 2022-08-17 | 17.7 | 0.3 | 0 | 2021-08-17 | 16.3 | 1.7 | 0 | 2020-08-17 | 17.4 | 0.6 | 0 | 2019-08-17 | 17.1 | 0.9 | 0 | 2018-08-17 | 16.6 | 1.4 | 0 | 2017-08-17 | 10.5 | 7.5 | 0 | 2016-08-17 | 16.3 | 1.7 | 0 | 1.56 | 0.29
2025-08-17 | 21.8 | 0 | 3.8 | 2024-08-17 | 19 | 0 | 1 | 2023-08-17 | 17.3 | 0.7 | 0 | 2022-08-17 | 18 | 0 | 0 | 2021-08-17 | 16.5 | 1.5 | 0 | 2020-08-17 | 17.4 | 0.6 | 0 | 2019-08-17 | 17.6 | 0.4 | 0 | 2018-08-17 | 16.8 | 1.2 | 0 | 2017-08-17 | 11.7 | 6.3 | 0 | 2016-08-17 | 16.5 | 1.5 | 0 | 1.22 | 0.48
2025-08-17 | 19.1 | 0 | 1.1 | 2024-08-17 | 19 | 0 | 1 | 2023-08-17 | 18.7 | 0 | 0.7 | 2022-08-17 | 18.8 | 0 | 0.8 | 2021-08-17 | 17.1 | 0.9 | 0 | 2020-08-17 | 18.1 | 0 | 0.1 | 2019-08-17 | 18.5 | 0 | 0.5 | 2018-08-17 | 17.8 | 0.2 | 0 | 2017-08-17 | 14.2 | 3.8 | 0 | 2016-08-17 | 18.4 | 0 | 0.4 | 0.49 | 0.46
2025-08-17 | 18.1 | 0 | 0.1 | 2024-08-17 | 19.3 | 0 | 1.3 | 2023-08-17 | 21.2 | 0 | 3.2 | 2022-08-17 | 20.9 | 0 | 2.9 | 2021-08-17 | 17.7 | 0.3 | 0 | 2020-08-17 | 18.8 | 0 | 0.8 | 2019-08-17 | 20 | 0 | 2 | 2018-08-17 | 18.9 | 0 | 0.9 | 2017-08-17 | 17 | 1 | 0 | 2016-08-17 | 19.6 | 0 | 1.6 | 0.13 | 1.28
2025-08-17 | 17.9 | 0.1 | 0 | 2024-08-17 | 19.5 | 0 | 1.5 | 2023-08-17 | 23.1 | 0 | 5.1 | 2022-08-17 | 22.4 | 0 | 4.4 | 2021-08-17 | 18.4 | 0 | 0.4 | 2020-08-17 | 19.6 | 0 | 1.6 | 2019-08-17 | 20.7 | 0 | 2.7 | 2018-08-17 | 21 | 0 | 3 | 2017-08-17 | 20.6 | 0 | 2.6 | 2016-08-17 | 21 | 0 | 3 | 0.01 | 2.43
2025-08-17 | 17.1 | 0.9 | 0 | 2024-08-17 | 20.1 | 0 | 2.1 | 2023-08-17 | 24.6 | 0 | 6.6 | 2022-08-17 | 23.7 | 0 | 5.7 | 2021-08-17 | 19.6 | 0 | 1.6 | 2020-08-17 | 21.7 | 0 | 3.7 | 2019-08-17 | 22.1 | 0 | 4.1 | 2018-08-17 | 21.6 | 0 | 3.6 | 2017-08-17 | 22 | 0 | 4 | 2016-08-17 | 21.5 | 0 | 3.5 | 0.09 | 3.49
2025-08-17 | 16.2 | 1.8 | 0 | 2024-08-17 | 21.1 | 0 | 3.1 | 2023-08-17 | 24.5 | 0 | 6.5 | 2022-08-17 | 25.2 | 0 | 7.2 | 2021-08-17 | 20.5 | 0 | 2.5 | 2020-08-17 | 22.6 | 0 | 4.6 | 2019-08-17 | 23.1 | 0 | 5.1 | 2018-08-17 | 23.2 | 0 | 5.2 | 2017-08-17 | 23.5 | 0 | 5.5 | 2016-08-17 | 24 | 0 | 6 | 0.18 | 4.57
2025-08-17 | 16.2 | 1.8 | 0 | 2024-08-17 | 21.8 | 0 | 3.8 | 2023-08-17 | 25.7 | 0 | 7.7 | 2022-08-17 | 25.6 | 0 | 7.6 | 2021-08-17 | 22.2 | 0 | 4.2 | 2020-08-17 | 23.6 | 0 | 5.6 | 2019-08-17 | 21.9 | 0 | 3.9 | 2018-08-17 | 22.4 | 0 | 4.4 | 2017-08-17 | 23.9 | 0 | 5.9 | 2016-08-17 | 25.4 | 0 | 7.4 | 0.18 | 5.05
2025-08-17 | 18.3 | 0 | 0.3 | 2024-08-17 | 22.5 | 0 | 4.5 | 2023-08-17 | 27.1 | 0 | 9.1 | 2022-08-17 | 26.6 | 0 | 8.6 | 2021-08-17 | 21.4 | 0 | 3.4 | 2020-08-17 | 24.6 | 0 | 6.6 | 2019-08-17 | 21.5 | 0 | 3.5 | 2018-08-17 | 21.8 | 0 | 3.8 | 2017-08-17 | 24.9 | 0 | 6.9 | 2016-08-17 | 26.1 | 0 | 8.1 | 0 | 5.48
2025-08-17 | 19.9 | 0 | 1.9 | 2024-08-17 | 24 | 0 | 6 | 2023-08-17 | 26.9 | 0 | 8.9 | 2022-08-17 | 26.9 | 0 | 8.9 | 2021-08-17 | 21.4 | 0 | 3.4 | 2020-08-17 | 24.6 | 0 | 6.6 | 2019-08-17 | 21.5 | 0 | 3.5 | 2018-08-17 | 21.7 | 0 | 3.7 | 2017-08-17 | 24.4 | 0 | 6.4 | 2016-08-17 | 26.5 | 0 | 8.5 | 0 | 5.78
2025-08-17 | 22.1 | 0 | 4.1 | 2024-08-17 | 25 | 0 | 7 | 2023-08-17 | 26 | 0 | 8 | 2022-08-17 | 26.9 | 0 | 8.9 | 2021-08-17 | 21.6 | 0 | 3.6 | 2020-08-17 | 25 | 0 | 7 | 2019-08-17 | 22.1 | 0 | 4.1 | 2018-08-17 | 23.3 | 0 | 5.3 | 2017-08-17 | 24.1 | 0 | 6.1 | 2016-08-17 | 27.1 | 0 | 9.1 | 0 | 6.32
2025-08-17 | 22.3 | 0 | 4.3 | 2024-08-17 | 23.6 | 0 | 5.6 | 2023-08-17 | 26.8 | 0 | 8.8 | 2022-08-17 | 23.3 | 0 | 5.3 | 2021-08-17 | 21.7 | 0 | 3.7 | 2020-08-17 | 24.5 | 0 | 6.5 | 2019-08-17 | 24.1 | 0 | 6.1 | 2018-08-17 | 23.3 | 0 | 5.3 | 2017-08-17 | 24 | 0 | 6 | 2016-08-17 | 26.8 | 0 | 8.8 | 0 | 6.04
2025-08-17 | 22.1 | 0 | 4.1 | 2024-08-17 | 22.3 | 0 | 4.3 | 2023-08-17 | 24.9 | 0 | 6.9 | 2022-08-17 | 20.6 | 0 | 2.6 | 2021-08-17 | 22.1 | 0 | 4.1 | 2020-08-17 | 23.4 | 0 | 5.4 | 2019-08-17 | 23.1 | 0 | 5.1 | 2018-08-17 | 22 | 0 | 4 | 2017-08-17 | 23.1 | 0 | 5.1 | 2016-08-17 | 26.8 | 0 | 8.8 | 0 | 5.04
2025-08-17 | 21 | 0 | 3 | 2024-08-17 | 22.8 | 0 | 4.8 | 2023-08-17 | 24.4 | 0 | 6.4 | 2022-08-17 | 20.9 | 0 | 2.9 | 2021-08-17 | 21.9 | 0 | 3.9 | 2020-08-17 | 18.1 | 0 | 0.1 | 2019-08-17 | 22.8 | 0 | 4.8 | 2018-08-17 | 20.6 | 0 | 2.6 | 2017-08-17 | 21.6 | 0 | 3.6 | 2016-08-17 | 24.6 | 0 | 6.6 | 0 | 3.87
2025-08-17 | 19.3 | 0 | 1.3 | 2024-08-17 | 21.8 | 0 | 3.8 | 2023-08-17 | 22.9 | 0 | 4.9 | 2022-08-17 | 20.4 | 0 | 2.4 | 2021-08-17 | 21.9 | 0 | 3.9 | 2020-08-17 | 18.1 | 0 | 0.1 | 2019-08-17 | 21.6 | 0 | 3.6 | 2018-08-17 | 20.1 | 0 | 2.1 | 2017-08-17 | 19.9 | 0 | 1.9 | 2016-08-17 | 23.5 | 0 | 5.5 | 0 | 2.95
2025-08-17 | 17.9 | 0.1 | 0 | 2024-08-17 | 21.9 | 0 | 3.9 | 2023-08-17 | 20.5 | 0 | 2.5 | 2022-08-17 | 19.6 | 0 | 1.6 | 2021-08-17 | 21.6 | 0 | 3.6 | 2020-08-17 | 16.6 | 1.4 | 0 | 2019-08-17 | 20.1 | 0 | 2.1 | 2018-08-17 | 19.3 | 0 | 1.3 | 2017-08-17 | 19.9 | 0 | 1.9 | 2016-08-17 | 22.5 | 0 | 4.5 | 0.15 | 2.14
2025-08-17 | 16.9 | 1.1 | 0 | 2024-08-17 | 21.8 | 0 | 3.8 | 2023-08-17 | 21.5 | 0 | 3.5 | 2022-08-17 | 19 | 0 | 1 | 2021-08-17 | 21.3 | 0 | 3.3 | 2020-08-17 | 18.2 | 0 | 0.2 | 2019-08-17 | 19.9 | 0 | 1.9 | 2018-08-17 | 18.8 | 0 | 0.8 | 2017-08-17 | 19.7 | 0 | 1.7 | 2016-08-17 | 22 | 0 | 4 | 0.11 | 2.02
2025-08-17 | 15.8 | 2.2 | 0 | 2024-08-17 | 21.8 | 0 | 3.8 | 2023-08-17 | 21.4 | 0 | 3.4 | 2022-08-17 | 18.6 | 0 | 0.6 | 2021-08-17 | 21.2 | 0 | 3.2 | 2020-08-17 | 16.8 | 1.2 | 0 | 2019-08-17 | 19.9 | 0 | 1.9 | 2018-08-17 | 18 | 0 | 0 | 2017-08-17 | 20.1 | 0 | 2.1 | 2016-08-17 | 21.1 | 0 | 3.1 | 0.34 | 1.81
2025-08-17 | 14.6 | 3.4 | 0 | 2024-08-17 | 21.6 | 0 | 3.6 | 2023-08-17 | 20.2 | 0 | 2.2 | 2022-08-17 | 18 | 0 | 0 | 2021-08-17 | 20.9 | 0 | 2.9 | 2020-08-17 | 15.2 | 2.8 | 0 | 2019-08-17 | 19.1 | 0 | 1.1 | 2018-08-17 | 17.9 | 0.1 | 0 | 2017-08-17 | 18.4 | 0 | 0.4 | 2016-08-17 | 20.3 | 0 | 2.3 | 0.63 | 1.25
2025-08-18 | 13.8 | 4.2 | 0 | 2024-08-18 | 21.4 | 0 | 3.4 | 2023-08-18 | 19.6 | 0 | 1.6 | 2022-08-18 | 17.7 | 0.3 | 0 | 2021-08-18 | 21 | 0 | 3 | 2020-08-18 | 15.5 | 2.5 | 0 | 2019-08-18 | 18.4 | 0 | 0.4 | 2018-08-18 | 17.5 | 0.5 | 0 | 2017-08-18 | 17.7 | 0.3 | 0 | 2016-08-18 | 19.4 | 0 | 1.4 | 0.78 | 0.98
2025-08-18 | 13.1 | 4.9 | 0 | 2024-08-18 | 21.2 | 0 | 3.2 | 2023-08-18 | 19.5 | 0 | 1.5 | 2022-08-18 | 17.2 | 0.8 | 0 | 2021-08-18 | 20.8 | 0 | 2.8 | 2020-08-18 | 14.5 | 3.5 | 0 | 2019-08-18 | 18.2 | 0 | 0.2 | 2018-08-18 | 17 | 1 | 0 | 2017-08-18 | 16.9 | 1.1 | 0 | 2016-08-18 | 18.7 | 0 | 0.7 | 1.13 | 0.84
2025-08-18 | 12.4 | 5.6 | 0 | 2024-08-18 | 20.7 | 0 | 2.7 | 2023-08-18 | 19.1 | 0 | 1.1 | 2022-08-18 | 16.8 | 1.2 | 0 | 2021-08-18 | 20.9 | 0 | 2.9 | 2020-08-18 | 13.8 | 4.2 | 0 | 2019-08-18 | 17.7 | 0.3 | 0 | 2018-08-18 | 16.5 | 1.5 | 0 | 2017-08-18 | 16.6 | 1.4 | 0 | 2016-08-18 | 18.8 | 0 | 0.8 | 1.42 | 0.75
2025-08-18 | 11.8 | 6.2 | 0 | 2024-08-18 | 20.5 | 0 | 2.5 | 2023-08-18 | 19.8 | 0 | 1.8 | 2022-08-18 | 16.5 | 1.5 | 0 | 2021-08-18 | 20.9 | 0 | 2.9 | 2020-08-18 | 13.8 | 4.2 | 0 | 2019-08-18 | 17.1 | 0.9 | 0 | 2018-08-18 | 16.4 | 1.6 | 0 | 2017-08-18 | 16.2 | 1.8 | 0 | 2016-08-18 | 19 | 0 | 1 | 1.62 | 0.82
2025-08-18 | 10.3 | 7.7 | 0 | 2024-08-18 | 19.3 | 0 | 1.3 | 2023-08-18 | 19.3 | 0 | 1.3 | 2022-08-18 | 16.4 | 1.6 | 0 | 2021-08-18 | 20.8 | 0 | 2.8 | 2020-08-18 | 13.4 | 4.6 | 0 | 2019-08-18 | 17.6 | 0.4 | 0 | 2018-08-18 | 16.5 | 1.5 | 0 | 2017-08-18 | 16.2 | 1.8 | 0 | 2016-08-18 | 18.1 | 0 | 0.1 | 1.76 | 0.55
2025-08-18 | 10.2 | 7.8 | 0 | 2024-08-18 | 19.2 | 0 | 1.2 | 2023-08-18 | 18.5 | 0 | 0.5 | 2022-08-18 | 17 | 1 | 0 | 2021-08-18 | 20.8 | 0 | 2.8 | 2020-08-18 | 13.1 | 4.9 | 0 | 2019-08-18 | 17.1 | 0.9 | 0 | 2018-08-18 | 16.3 | 1.7 | 0 | 2017-08-18 | 16.6 | 1.4 | 0 | 2016-08-18 | 17.4 | 0.6 | 0 | 1.83 | 0.45
2025-08-18 | 11.4 | 6.6 | 0 | 2024-08-18 | 19.4 | 0 | 1.4 | 2023-08-18 | 18 | 0 | 0 | 2022-08-18 | 17.4 | 0.6 | 0 | 2021-08-18 | 20.9 | 0 | 2.9 | 2020-08-18 | 14.3 | 3.7 | 0 | 2019-08-18 | 17.7 | 0.3 | 0 | 2018-08-18 | 16.3 | 1.7 | 0 | 2017-08-18 | 16.9 | 1.1 | 0 | 2016-08-18 | 19 | 0 | 1 | 1.4 | 0.53
2025-08-18 | 12.9 | 5.1 | 0 | 2024-08-18 | 19.7 | 0 | 1.7 | 2023-08-18 | 17.9 | 0.1 | 0 | 2022-08-18 | 18.4 | 0 | 0.4 | 2021-08-18 | 21.2 | 0 | 3.2 | 2020-08-18 | 14.8 | 3.2 | 0 | 2019-08-18 | 18.3 | 0 | 0.3 | 2018-08-18 | 17.1 | 0.9 | 0 | 2017-08-18 | 17.1 | 0.9 | 0 | 2016-08-18 | 19.9 | 0 | 1.9 | 1.02 | 0.75
2025-08-18 | 14.4 | 3.6 | 0 | 2024-08-18 | 19.9 | 0 | 1.9 | 2023-08-18 | 18.2 | 0 | 0.2 | 2022-08-18 | 18.9 | 0 | 0.9 | 2021-08-18 | 21.7 | 0 | 3.7 | 2020-08-18 | 17.1 | 0.9 | 0 | 2019-08-18 | 18.6 | 0 | 0.6 | 2018-08-18 | 18.1 | 0 | 0.1 | 2017-08-18 | 17.2 | 0.8 | 0 | 2016-08-18 | 21.5 | 0 | 3.5 | 0.53 | 1.09
2025-08-18 | 16.5 | 1.5 | 0 | 2024-08-18 | 20.7 | 0 | 2.7 | 2023-08-18 | 19.4 | 0 | 1.4 | 2022-08-18 | 19.9 | 0 | 1.9 | 2021-08-18 | 22.5 | 0 | 4.5 | 2020-08-18 | 19.1 | 0 | 1.1 | 2019-08-18 | 19.4 | 0 | 1.4 | 2018-08-18 | 19.8 | 0 | 1.8 | 2017-08-18 | 17.3 | 0.7 | 0 | 2016-08-18 | 22.5 | 0 | 4.5 | 0.22 | 1.93
2025-08-18 | 17.2 | 0.8 | 0 | 2024-08-18 | 21.4 | 0 | 3.4 | 2023-08-18 | 19 | 0 | 1 | 2022-08-18 | 22.4 | 0 | 4.4 | 2021-08-18 | 24.4 | 0 | 6.4 | 2020-08-18 | 19.9 | 0 | 1.9 | 2019-08-18 | 20.6 | 0 | 2.6 | 2018-08-18 | 20.8 | 0 | 2.8 | 2017-08-18 | 17.6 | 0.4 | 0 | 2016-08-18 | 22.9 | 0 | 4.9 | 0.12 | 2.74
2025-08-18 | 19.1 | 0 | 1.1 | 2024-08-18 | 22.6 | 0 | 4.6 | 2023-08-18 | 20.9 | 0 | 2.9 | 2022-08-18 | 23.2 | 0 | 5.2 | 2021-08-18 | 25.3 | 0 | 7.3 | 2020-08-18 | 21.4 | 0 | 3.4 | 2019-08-18 | 22.5 | 0 | 4.5 | 2018-08-18 | 21.8 | 0 | 3.8 | 2017-08-18 | 18.6 | 0 | 0.6 | 2016-08-18 | 24.4 | 0 | 6.4 | 0 | 3.98
2025-08-18 | 19.7 | 0 | 1.7 | 2024-08-18 | 24.5 | 0 | 6.5 | 2023-08-18 | 20.7 | 0 | 2.7 | 2022-08-18 | 25 | 0 | 7 | 2021-08-18 | 27.3 | 0 | 9.3 | 2020-08-18 | 21.8 | 0 | 3.8 | 2019-08-18 | 23.9 | 0 | 5.9 | 2018-08-18 | 22.5 | 0 | 4.5 | 2017-08-18 | 20.3 | 0 | 2.3 | 2016-08-18 | 24.6 | 0 | 6.6 | 0 | 5.03
2025-08-18 | 20.3 | 0 | 2.3 | 2024-08-18 | 25.5 | 0 | 7.5 | 2023-08-18 | 21.7 | 0 | 3.7 | 2022-08-18 | 24.4 | 0 | 6.4 | 2021-08-18 | 27.8 | 0 | 9.8 | 2020-08-18 | 21.4 | 0 | 3.4 | 2019-08-18 | 24.9 | 0 | 6.9 | 2018-08-18 | 23.9 | 0 | 5.9 | 2017-08-18 | 21.8 | 0 | 3.8 | 2016-08-18 | 25.8 | 0 | 7.8 | 0 | 5.75
2025-08-18 | 20.2 | 0 | 2.2 | 2024-08-18 | 25.3 | 0 | 7.3 | 2023-08-18 | 20.2 | 0 | 2.2 | 2022-08-18 | 26.1 | 0 | 8.1 | 2021-08-18 | 28.5 | 0 | 10.5 | 2020-08-18 | 20.6 | 0 | 2.6 | 2019-08-18 | 25.5 | 0 | 7.5 | 2018-08-18 | 24.2 | 0 | 6.2 | 2017-08-18 | 21.8 | 0 | 3.8 | 2016-08-18 | 26.7 | 0 | 8.7 | 0 | 5.91
2025-08-18 | 20.8 | 0 | 2.8 | 2024-08-18 | 25.7 | 0 | 7.7 | 2023-08-18 | 20.7 | 0 | 2.7 | 2022-08-18 | 26.5 | 0 | 8.5 | 2021-08-18 | 28.2 | 0 | 10.2 | 2020-08-18 | 22.2 | 0 | 4.2 | 2019-08-18 | 24.4 | 0 | 6.4 | 2018-08-18 | 25 | 0 | 7 | 2017-08-18 | 23.8 | 0 | 5.8 | 2016-08-18 | 26.3 | 0 | 8.3 | 0 | 6.36
2025-08-18 | 21.5 | 0 | 3.5 | 2024-08-18 | 24.9 | 0 | 6.9 | 2023-08-18 | 21.3 | 0 | 3.3 | 2022-08-18 | 26 | 0 | 8 | 2021-08-18 | 27.8 | 0 | 9.8 | 2020-08-18 | 22.4 | 0 | 4.4 | 2019-08-18 | 21.6 | 0 | 3.6 | 2018-08-18 | 24.6 | 0 | 6.6 | 2017-08-18 | 23.2 | 0 | 5.2 | 2016-08-18 | 23.9 | 0 | 5.9 | 0 | 5.72
2025-08-18 | 20.6 | 0 | 2.6 | 2024-08-18 | 23.4 | 0 | 5.4 | 2023-08-18 | 18.2 | 0 | 0.2 | 2022-08-18 | 25.5 | 0 | 7.5 | 2021-08-18 | 27.4 | 0 | 9.4 | 2020-08-18 | 20.9 | 0 | 2.9 | 2019-08-18 | 21.6 | 0 | 3.6 | 2018-08-18 | 24.2 | 0 | 6.2 | 2017-08-18 | 23.6 | 0 | 5.6 | 2016-08-18 | 26.2 | 0 | 8.2 | 0 | 5.16
2025-08-18 | 19.8 | 0 | 1.8 | 2024-08-18 | 22.5 | 0 | 4.5 | 2023-08-18 | 16.7 | 1.3 | 0 | 2022-08-18 | 24.1 | 0 | 6.1 | 2021-08-18 | 26.4 | 0 | 8.4 | 2020-08-18 | 20.2 | 0 | 2.2 | 2019-08-18 | 22.1 | 0 | 4.1 | 2018-08-18 | 24 | 0 | 6 | 2017-08-18 | 23.7 | 0 | 5.7 | 2016-08-18 | 26.3 | 0 | 8.3 | 0.13 | 4.71
2025-08-18 | 17.6 | 0.4 | 0 | 2024-08-18 | 21.6 | 0 | 3.6 | 2023-08-18 | 16.5 | 1.5 | 0 | 2022-08-18 | 22.5 | 0 | 4.5 | 2021-08-18 | 24.8 | 0 | 6.8 | 2020-08-18 | 18.7 | 0 | 0.7 | 2019-08-18 | 21.2 | 0 | 3.2 | 2018-08-18 | 22.5 | 0 | 4.5 | 2017-08-18 | 24.8 | 0 | 6.8 | 2016-08-18 | 24.6 | 0 | 6.6 | 0.19 | 3.67
2025-08-18 | 16.6 | 1.4 | 0 | 2024-08-18 | 21 | 0 | 3 | 2023-08-18 | 15.4 | 2.6 | 0 | 2022-08-18 | 21 | 0 | 3 | 2021-08-18 | 23.4 | 0 | 5.4 | 2020-08-18 | 17.7 | 0.3 | 0 | 2019-08-18 | 20.4 | 0 | 2.4 | 2018-08-18 | 21.4 | 0 | 3.4 | 2017-08-18 | 23.1 | 0 | 5.1 | 2016-08-18 | 22.2 | 0 | 4.2 | 0.43 | 2.65
2025-08-18 | 13.6 | 4.4 | 0 | 2024-08-18 | 21 | 0 | 3 | 2023-08-18 | 14.9 | 3.1 | 0 | 2022-08-18 | 18.9 | 0 | 0.9 | 2021-08-18 | 22.6 | 0 | 4.6 | 2020-08-18 | 15.5 | 2.5 | 0 | 2019-08-18 | 20.4 | 0 | 2.4 | 2018-08-18 | 19.5 | 0 | 1.5 | 2017-08-18 | 21.9 | 0 | 3.9 | 2016-08-18 | 20.4 | 0 | 2.4 | 1 | 1.87
2025-08-18 | 13.7 | 4.3 | 0 | 2024-08-18 | 20.4 | 0 | 2.4 | 2023-08-18 | 14.5 | 3.5 | 0 | 2022-08-18 | 18.1 | 0 | 0.1 | 2021-08-18 | 21.9 | 0 | 3.9 | 2020-08-18 | 14.6 | 3.4 | 0 | 2019-08-18 | 20.3 | 0 | 2.3 | 2018-08-18 | 19.4 | 0 | 1.4 | 2017-08-18 | 20 | 0 | 2 | 2016-08-18 | 17.8 | 0.2 | 0 | 1.14 | 1.21
2025-08-18 | 13.4 | 4.6 | 0 | 2024-08-18 | 19.4 | 0 | 1.4 | 2023-08-18 | 14 | 4 | 0 | 2022-08-18 | 17.3 | 0.7 | 0 | 2021-08-18 | 21.5 | 0 | 3.5 | 2020-08-18 | 14.4 | 3.6 | 0 | 2019-08-18 | 19.4 | 0 | 1.4 | 2018-08-18 | 18.1 | 0 | 0.1 | 2017-08-18 | 21 | 0 | 3 | 2016-08-18 | 17.6 | 0.4 | 0 | 1.33 | 0.94
2025-08-19 | 12.9 | 5.1 | 0 | 2024-08-19 | 20 | 0 | 2 | 2023-08-19 | 13.7 | 4.3 | 0 | 2022-08-19 | 16.2 | 1.8 | 0 | 2021-08-19 | 20.1 | 0 | 2.1 | 2020-08-19 | 12.7 | 5.3 | 0 | 2019-08-19 | 19.9 | 0 | 1.9 | 2018-08-19 | 18.4 | 0 | 0.4 | 2017-08-19 | 20.7 | 0 | 2.7 | 2016-08-19 | 15.9 | 2.1 | 0 | 1.86 | 0.91
2025-08-19 | 14.1 | 3.9 | 0 | 2024-08-19 | 20.1 | 0 | 2.1 | 2023-08-19 | 13.7 | 4.3 | 0 | 2022-08-19 | 15.3 | 2.7 | 0 | 2021-08-19 | 19.7 | 0 | 1.7 | 2020-08-19 | 13.8 | 4.2 | 0 | 2019-08-19 | 19.7 | 0 | 1.7 | 2018-08-19 | 16.2 | 1.8 | 0 | 2017-08-19 | 20.7 | 0 | 2.7 | 2016-08-19 | 15.8 | 2.2 | 0 | 1.91 | 0.82
2025-08-19 | 12.5 | 5.5 | 0 | 2024-08-19 | 18.6 | 0 | 0.6 | 2023-08-19 | 13.6 | 4.4 | 0 | 2022-08-19 | 14.9 | 3.1 | 0 | 2021-08-19 | 20.2 | 0 | 2.2 | 2020-08-19 | 12.9 | 5.1 | 0 | 2019-08-19 | 19.7 | 0 | 1.7 | 2018-08-19 | 15.3 | 2.7 | 0 | 2017-08-19 | 20.1 | 0 | 2.1 | 2016-08-19 | 14.5 | 3.5 | 0 | 2.43 | 0.66
2025-08-19 | 11.4 | 6.6 | 0 | 2024-08-19 | 17.3 | 0.7 | 0 | 2023-08-19 | 13.6 | 4.4 | 0 | 2022-08-19 | 14.2 | 3.8 | 0 | 2021-08-19 | 19.4 | 0 | 1.4 | 2020-08-19 | 13.9 | 4.1 | 0 | 2019-08-19 | 20.2 | 0 | 2.2 | 2018-08-19 | 14.5 | 3.5 | 0 | 2017-08-19 | 19.5 | 0 | 1.5 | 2016-08-19 | 14.9 | 3.1 | 0 | 2.62 | 0.51
2025-08-19 | 12.1 | 5.9 | 0 | 2024-08-19 | 17.3 | 0.7 | 0 | 2023-08-19 | 13.4 | 4.6 | 0 | 2022-08-19 | 15.6 | 2.4 | 0 | 2021-08-19 | 19.6 | 0 | 1.6 | 2020-08-19 | 11.7 | 6.3 | 0 | 2019-08-19 | 20.4 | 0 | 2.4 | 2018-08-19 | 14.5 | 3.5 | 0 | 2017-08-19 | 19.8 | 0 | 1.8 | 2016-08-19 | 15.2 | 2.8 | 0 | 2.62 | 0.58
2025-08-19 | 11.2 | 6.8 | 0 | 2024-08-19 | 16.9 | 1.1 | 0 | 2023-08-19 | 13.5 | 4.5 | 0 | 2022-08-19 | 15.4 | 2.6 | 0 | 2021-08-19 | 20 | 0 | 2 | 2020-08-19 | 12.4 | 5.6 | 0 | 2019-08-19 | 20.6 | 0 | 2.6 | 2018-08-19 | 14.6 | 3.4 | 0 | 2017-08-19 | 19.3 | 0 | 1.3 | 2016-08-19 | 13.2 | 4.8 | 0 | 2.88 | 0.59
2025-08-19 | 11.8 | 6.2 | 0 | 2024-08-19 | 16.8 | 1.2 | 0 | 2023-08-19 | 13.5 | 4.5 | 0 | 2022-08-19 | 15.9 | 2.1 | 0 | 2021-08-19 | 20.3 | 0 | 2.3 | 2020-08-19 | 12.8 | 5.2 | 0 | 2019-08-19 | 20.8 | 0 | 2.8 | 2018-08-19 | 15.8 | 2.2 | 0 | 2017-08-19 | 19.8 | 0 | 1.8 | 2016-08-19 | 15.5 | 2.5 | 0 | 2.39 | 0.69
2025-08-19 | 13 | 5 | 0 | 2024-08-19 | 17 | 1 | 0 | 2023-08-19 | 13.6 | 4.4 | 0 | 2022-08-19 | 18.9 | 0 | 0.9 | 2021-08-19 | 20.6 | 0 | 2.6 | 2020-08-19 | 14.6 | 3.4 | 0 | 2019-08-19 | 21.4 | 0 | 3.4 | 2018-08-19 | 18 | 0 | 0 | 2017-08-19 | 20.2 | 0 | 2.2 | 2016-08-19 | 18.9 | 0 | 0.9 | 1.38 | 1
2025-08-19 | 14.6 | 3.4 | 0 | 2024-08-19 | 15.9 | 2.1 | 0 | 2023-08-19 | 13.1 | 4.9 | 0 | 2022-08-19 | 21.5 | 0 | 3.5 | 2021-08-19 | 21 | 0 | 3 | 2020-08-19 | 16 | 2 | 0 | 2019-08-19 | 22.4 | 0 | 4.4 | 2018-08-19 | 19.5 | 0 | 1.5 | 2017-08-19 | 20.8 | 0 | 2.8 | 2016-08-19 | 21.7 | 0 | 3.7 | 1.24 | 1.89
2025-08-19 | 16.9 | 1.1 | 0 | 2024-08-19 | 16.2 | 1.8 | 0 | 2023-08-19 | 13.1 | 4.9 | 0 | 2022-08-19 | 23.1 | 0 | 5.1 | 2021-08-19 | 22.2 | 0 | 4.2 | 2020-08-19 | 17.9 | 0.1 | 0 | 2019-08-19 | 24.3 | 0 | 6.3 | 2018-08-19 | 21.2 | 0 | 3.2 | 2017-08-19 | 21.3 | 0 | 3.3 | 2016-08-19 | 23.3 | 0 | 5.3 | 0.79 | 2.74
2025-08-19 | 19.4 | 0 | 1.4 | 2024-08-19 | 15.6 | 2.4 | 0 | 2023-08-19 | 14.4 | 3.6 | 0 | 2022-08-19 | 25.3 | 0 | 7.3 | 2021-08-19 | 23.6 | 0 | 5.6 | 2020-08-19 | 17.2 | 0.8 | 0 | 2019-08-19 | 26 | 0 | 8 | 2018-08-19 | 23.2 | 0 | 5.2 | 2017-08-19 | 21.8 | 0 | 3.8 | 2016-08-19 | 25.2 | 0 | 7.2 | 0.68 | 3.85
2025-08-19 | 21.1 | 0 | 3.1 | 2024-08-19 | 14.9 | 3.1 | 0 | 2023-08-19 | 15.5 | 2.5 | 0 | 2022-08-19 | 27.1 | 0 | 9.1 | 2021-08-19 | 24.8 | 0 | 6.8 | 2020-08-19 | 17.9 | 0.1 | 0 | 2019-08-19 | 26.8 | 0 | 8.8 | 2018-08-19 | 24.8 | 0 | 6.8 | 2017-08-19 | 23.2 | 0 | 5.2 | 2016-08-19 | 26.6 | 0 | 8.6 | 0.57 | 4.84
2025-08-19 | 21.4 | 0 | 3.4 | 2024-08-19 | 15.1 | 2.9 | 0 | 2023-08-19 | 17.4 | 0.6 | 0 | 2022-08-19 | 27.9 | 0 | 9.9 | 2021-08-19 | 26.2 | 0 | 8.2 | 2020-08-19 | 19.5 | 0 | 1.5 | 2019-08-19 | 27.6 | 0 | 9.6 | 2018-08-19 | 25.7 | 0 | 7.7 | 2017-08-19 | 23.2 | 0 | 5.2 | 2016-08-19 | 27.1 | 0 | 9.1 | 0.35 | 5.46
2025-08-19 | 21.7 | 0 | 3.7 | 2024-08-19 | 14.6 | 3.4 | 0 | 2023-08-19 | 18.1 | 0 | 0.1 | 2022-08-19 | 27.6 | 0 | 9.6 | 2021-08-19 | 26.2 | 0 | 8.2 | 2020-08-19 | 19.8 | 0 | 1.8 | 2019-08-19 | 29.3 | 0 | 11.3 | 2018-08-19 | 26.5 | 0 | 8.5 | 2017-08-19 | 22.1 | 0 | 4.1 | 2016-08-19 | 28.3 | 0 | 10.3 | 0.34 | 5.76
2025-08-19 | 21.2 | 0 | 3.2 | 2024-08-19 | 14.7 | 3.3 | 0 | 2023-08-19 | 20.2 | 0 | 2.2 | 2022-08-19 | 28.7 | 0 | 10.7 | 2021-08-19 | 26.4 | 0 | 8.4 | 2020-08-19 | 21.3 | 0 | 3.3 | 2019-08-19 | 29.9 | 0 | 11.9 | 2018-08-19 | 26.8 | 0 | 8.8 | 2017-08-19 | 22.6 | 0 | 4.6 | 2016-08-19 | 28.9 | 0 | 10.9 | 0.33 | 6.4
2025-08-19 | 20.3 | 0 | 2.3 | 2024-08-19 | 14.8 | 3.2 | 0 | 2023-08-19 | 22.5 | 0 | 4.5 | 2022-08-19 | 29.3 | 0 | 11.3 | 2021-08-19 | 26.9 | 0 | 8.9 | 2020-08-19 | 21 | 0 | 3 | 2019-08-19 | 30 | 0 | 12 | 2018-08-19 | 26.9 | 0 | 8.9 | 2017-08-19 | 23.4 | 0 | 5.4 | 2016-08-19 | 28.5 | 0 | 10.5 | 0.32 | 6.68
2025-08-19 | 19.1 | 0 | 1.1 | 2024-08-19 | 14.6 | 3.4 | 0 | 2023-08-19 | 23.2 | 0 | 5.2 | 2022-08-19 | 29.2 | 0 | 11.2 | 2021-08-19 | 27.1 | 0 | 9.1 | 2020-08-19 | 20.4 | 0 | 2.4 | 2019-08-19 | 29.4 | 0 | 11.4 | 2018-08-19 | 26.3 | 0 | 8.3 | 2017-08-19 | 23.2 | 0 | 5.2 | 2016-08-19 | 29.3 | 0 | 11.3 | 0.34 | 6.52
2025-08-19 | 18.7 | 0 | 0.7 | 2024-08-19 | 15.6 | 2.4 | 0 | 2023-08-19 | 23.2 | 0 | 5.2 | 2022-08-19 | 28.5 | 0 | 10.5 | 2021-08-19 | 28.7 | 0 | 10.7 | 2020-08-19 | 19.9 | 0 | 1.9 | 2019-08-19 | 28.3 | 0 | 10.3 | 2018-08-19 | 25.8 | 0 | 7.8 | 2017-08-19 | 23.3 | 0 | 5.3 | 2016-08-19 | 28.1 | 0 | 10.1 | 0.24 | 6.25
2025-08-19 | 18.1 | 0 | 0.1 | 2024-08-19 | 15.6 | 2.4 | 0 | 2023-08-19 | 21.7 | 0 | 3.7 | 2022-08-19 | 27.2 | 0 | 9.2 | 2021-08-19 | 26.3 | 0 | 8.3 | 2020-08-19 | 18.8 | 0 | 0.8 | 2019-08-19 | 27 | 0 | 9 | 2018-08-19 | 24.5 | 0 | 6.5 | 2017-08-19 | 22.5 | 0 | 4.5 | 2016-08-19 | 26.5 | 0 | 8.5 | 0.24 | 5.06
2025-08-19 | 17 | 1 | 0 | 2024-08-19 | 13.8 | 4.2 | 0 | 2023-08-19 | 18.9 | 0 | 0.9 | 2022-08-19 | 24.7 | 0 | 6.7 | 2021-08-19 | 24.9 | 0 | 6.9 | 2020-08-19 | 16.9 | 1.1 | 0 | 2019-08-19 | 24.3 | 0 | 6.3 | 2018-08-19 | 22.2 | 0 | 4.2 | 2017-08-19 | 21 | 0 | 3 | 2016-08-19 | 23.9 | 0 | 5.9 | 0.63 | 3.39
2025-08-19 | 16.3 | 1.7 | 0 | 2024-08-19 | 13.2 | 4.8 | 0 | 2023-08-19 | 18.3 | 0 | 0.3 | 2022-08-19 | 23.7 | 0 | 5.7 | 2021-08-19 | 23.8 | 0 | 5.8 | 2020-08-19 | 15.2 | 2.8 | 0 | 2019-08-19 | 20.8 | 0 | 2.8 | 2018-08-19 | 19.4 | 0 | 1.4 | 2017-08-19 | 20.2 | 0 | 2.2 | 2016-08-19 | 21.3 | 0 | 3.3 | 0.93 | 2.15
2025-08-19 | 16.8 | 1.2 | 0 | 2024-08-19 | 14.5 | 3.5 | 0 | 2023-08-19 | 16.2 | 1.8 | 0 | 2022-08-19 | 21.9 | 0 | 3.9 | 2021-08-19 | 21.8 | 0 | 3.8 | 2020-08-19 | 15.2 | 2.8 | 0 | 2019-08-19 | 18.9 | 0 | 0.9 | 2018-08-19 | 19.9 | 0 | 1.9 | 2017-08-19 | 18.9 | 0 | 0.9 | 2016-08-19 | 20.5 | 0 | 2.5 | 0.93 | 1.39
2025-08-19 | 17 | 1 | 0 | 2024-08-19 | 12.8 | 5.2 | 0 | 2023-08-19 | 16.7 | 1.3 | 0 | 2022-08-19 | 20.9 | 0 | 2.9 | 2021-08-19 | 21.9 | 0 | 3.9 | 2020-08-19 | 13.9 | 4.1 | 0 | 2019-08-19 | 15.6 | 2.4 | 0 | 2018-08-19 | 17.2 | 0.8 | 0 | 2017-08-19 | 17.6 | 0.4 | 0 | 2016-08-19 | 19.9 | 0 | 1.9 | 1.52 | 0.87
2025-08-19 | 16.8 | 1.2 | 0 | 2024-08-19 | 11.8 | 6.2 | 0 | 2023-08-19 | 14.7 | 3.3 | 0 | 2022-08-19 | 19.4 | 0 | 1.4 | 2021-08-19 | 21.9 | 0 | 3.9 | 2020-08-19 | 10.7 | 7.3 | 0 | 2019-08-19 | 14.8 | 3.2 | 0 | 2018-08-19 | 16.8 | 1.2 | 0 | 2017-08-19 | 17.6 | 0.4 | 0 | 2016-08-19 | 19.4 | 0 | 1.4 | 2.28 | 0.67
2025-08-20 | 16.4 | 1.6 | 0 | 2024-08-20 | 9.8 | 8.2 | 0 | 2023-08-20 | 14.5 | 3.5 | 0 | 2022-08-20 | 19.3 | 0 | 1.3 | 2021-08-20 | 19.8 | 0 | 1.8 | 2020-08-20 | 10.3 | 7.7 | 0 | 2019-08-20 | 15.8 | 2.2 | 0 | 2018-08-20 | 16.5 | 1.5 | 0 | 2017-08-20 | 17.4 | 0.6 | 0 | 2016-08-20 | 18.8 | 0 | 0.8 | 2.53 | 0.39
2025-08-20 | 16.2 | 1.8 | 0 | 2024-08-20 | 10.9 | 7.1 | 0 | 2023-08-20 | 15 | 3 | 0 | 2022-08-20 | 18.8 | 0 | 0.8 | 2021-08-20 | 20.3 | 0 | 2.3 | 2020-08-20 | 10.3 | 7.7 | 0 | 2019-08-20 | 15.8 | 2.2 | 0 | 2018-08-20 | 16 | 2 | 0 | 2017-08-20 | 16.6 | 1.4 | 0 | 2016-08-20 | 18.5 | 0 | 0.5 | 2.52 | 0.36
2025-08-20 | 16.1 | 1.9 | 0 | 2024-08-20 | 10.8 | 7.2 | 0 | 2023-08-20 | 15.1 | 2.9 | 0 | 2022-08-20 | 18.5 | 0 | 0.5 | 2021-08-20 | 20.1 | 0 | 2.1 | 2020-08-20 | 10 | 8 | 0 | 2019-08-20 | 14.8 | 3.2 | 0 | 2018-08-20 | 15.6 | 2.4 | 0 | 2017-08-20 | 15.7 | 2.3 | 0 | 2016-08-20 | 17.9 | 0.1 | 0 | 2.8 | 0.26
2025-08-20 | 16.2 | 1.8 | 0 | 2024-08-20 | 10.7 | 7.3 | 0 | 2023-08-20 | 14.3 | 3.7 | 0 | 2022-08-20 | 18 | 0 | 0 | 2021-08-20 | 20.4 | 0 | 2.4 | 2020-08-20 | 10.4 | 7.6 | 0 | 2019-08-20 | 13.2 | 4.8 | 0 | 2018-08-20 | 14.9 | 3.1 | 0 | 2017-08-20 | 15.2 | 2.8 | 0 | 2016-08-20 | 17.2 | 0.8 | 0 | 3.19 | 0.24
2025-08-20 | 15.6 | 2.4 | 0 | 2024-08-20 | 11.7 | 6.3 | 0 | 2023-08-20 | 14.7 | 3.3 | 0 | 2022-08-20 | 17.4 | 0.6 | 0 | 2021-08-20 | 19.1 | 0 | 1.1 | 2020-08-20 | 10 | 8 | 0 | 2019-08-20 | 13.6 | 4.4 | 0 | 2018-08-20 | 14.4 | 3.6 | 0 | 2017-08-20 | 14.2 | 3.8 | 0 | 2016-08-20 | 16.4 | 1.6 | 0 | 3.4 | 0.11
2025-08-20 | 16.1 | 1.9 | 0 | 2024-08-20 | 12.1 | 5.9 | 0 | 2023-08-20 | 14.6 | 3.4 | 0 | 2022-08-20 | 17.3 | 0.7 | 0 | 2021-08-20 | 17.9 | 0.1 | 0 | 2020-08-20 | 10.1 | 7.9 | 0 | 2019-08-20 | 13.3 | 4.7 | 0 | 2018-08-20 | 14.1 | 3.9 | 0 | 2017-08-20 | 13.9 | 4.1 | 0 | 2016-08-20 | 16.9 | 1.1 | 0 | 3.37 | 0
2025-08-20 | 15.9 | 2.1 | 0 | 2024-08-20 | 12.5 | 5.5 | 0 | 2023-08-20 | 15.3 | 2.7 | 0 | 2022-08-20 | 18 | 0 | 0 | 2021-08-20 | 18.7 | 0 | 0.7 | 2020-08-20 | 11.6 | 6.4 | 0 | 2019-08-20 | 14.7 | 3.3 | 0 | 2018-08-20 | 15 | 3 | 0 | 2017-08-20 | 14 | 4 | 0 | 2016-08-20 | 18.1 | 0 | 0.1 | 2.7 | 0.08
2025-08-20 | 15.2 | 2.8 | 0 | 2024-08-20 | 13 | 5 | 0 | 2023-08-20 | 17.3 | 0.7 | 0 | 2022-08-20 | 20.2 | 0 | 2.2 | 2021-08-20 | 20.1 | 0 | 2.1 | 2020-08-20 | 13.4 | 4.6 | 0 | 2019-08-20 | 17.6 | 0.4 | 0 | 2018-08-20 | 16.2 | 1.8 | 0 | 2017-08-20 | 16.3 | 1.7 | 0 | 2016-08-20 | 19.7 | 0 | 1.7 | 1.7 | 0.6
2025-08-20 | 15.5 | 2.5 | 0 | 2024-08-20 | 13.5 | 4.5 | 0 | 2023-08-20 | 18.9 | 0 | 0.9 | 2022-08-20 | 22.7 | 0 | 4.7 | 2021-08-20 | 22.4 | 0 | 4.4 | 2020-08-20 | 14.6 | 3.4 | 0 | 2019-08-20 | 20.1 | 0 | 2.1 | 2018-08-20 | 18.3 | 0 | 0.3 | 2017-08-20 | 18.3 | 0 | 0.3 | 2016-08-20 | 21.6 | 0 | 3.6 | 1.04 | 1.63
2025-08-20 | 15.1 | 2.9 | 0 | 2024-08-20 | 15.5 | 2.5 | 0 | 2023-08-20 | 20.9 | 0 | 2.9 | 2022-08-20 | 25.1 | 0 | 7.1 | 2021-08-20 | 24.8 | 0 | 6.8 | 2020-08-20 | 18.4 | 0 | 0.4 | 2019-08-20 | 21.9 | 0 | 3.9 | 2018-08-20 | 22 | 0 | 4 | 2017-08-20 | 20.1 | 0 | 2.1 | 2016-08-20 | 24.1 | 0 | 6.1 | 0.54 | 3.33
2025-08-20 | 16.3 | 1.7 | 0 | 2024-08-20 | 16.1 | 1.9 | 0 | 2023-08-20 | 21.1 | 0 | 3.1 | 2022-08-20 | 26.8 | 0 | 8.8 | 2021-08-20 | 27.8 | 0 | 9.8 | 2020-08-20 | 18.3 | 0 | 0.3 | 2019-08-20 | 23.9 | 0 | 5.9 | 2018-08-20 | 24.1 | 0 | 6.1 | 2017-08-20 | 21.6 | 0 | 3.6 | 2016-08-20 | 26.5 | 0 | 8.5 | 0.36 | 4.61
2025-08-20 | 17.9 | 0.1 | 0 | 2024-08-20 | 16.9 | 1.1 | 0 | 2023-08-20 | 21.9 | 0 | 3.9 | 2022-08-20 | 27.9 | 0 | 9.9 | 2021-08-20 | 29.2 | 0 | 11.2 | 2020-08-20 | 18.4 | 0 | 0.4 | 2019-08-20 | 25.1 | 0 | 7.1 | 2018-08-20 | 25.6 | 0 | 7.6 | 2017-08-20 | 22.2 | 0 | 4.2 | 2016-08-20 | 27.8 | 0 | 9.8 | 0.12 | 5.41
2025-08-20 | 20.4 | 0 | 2.4 | 2024-08-20 | 17.1 | 0.9 | 0 | 2023-08-20 | 22.5 | 0 | 4.5 | 2022-08-20 | 27.6 | 0 | 9.6 | 2021-08-20 | 31.1 | 0 | 13.1 | 2020-08-20 | 19 | 0 | 1 | 2019-08-20 | 25.9 | 0 | 7.9 | 2018-08-20 | 25.9 | 0 | 7.9 | 2017-08-20 | 22.9 | 0 | 4.9 | 2016-08-20 | 29.1 | 0 | 11.1 | 0.09 | 6.24
2025-08-20 | 21.1 | 0 | 3.1 | 2024-08-20 | 17.7 | 0.3 | 0 | 2023-08-20 | 24.9 | 0 | 6.9 | 2022-08-20 | 28.7 | 0 | 10.7 | 2021-08-20 | 31.7 | 0 | 13.7 | 2020-08-20 | 19.4 | 0 | 1.4 | 2019-08-20 | 27 | 0 | 9 | 2018-08-20 | 27 | 0 | 9 | 2017-08-20 | 24.4 | 0 | 6.4 | 2016-08-20 | 29.6 | 0 | 11.6 | 0.03 | 7.18
2025-08-20 | 22.1 | 0 | 4.1 | 2024-08-20 | 18.4 | 0 | 0.4 | 2023-08-20 | 26.5 | 0 | 8.5 | 2022-08-20 | 29.4 | 0 | 11.4 | 2021-08-20 | 32.1 | 0 | 14.1 | 2020-08-20 | 19.4 | 0 | 1.4 | 2019-08-20 | 27.6 | 0 | 9.6 | 2018-08-20 | 27.2 | 0 | 9.2 | 2017-08-20 | 25.6 | 0 | 7.6 | 2016-08-20 | 30.4 | 0 | 12.4 | 0 | 7.87
2025-08-20 | 22.4 | 0 | 4.4 | 2024-08-20 | 18.7 | 0 | 0.7 | 2023-08-20 | 25.7 | 0 | 7.7 | 2022-08-20 | 29.8 | 0 | 11.8 | 2021-08-20 | 31.4 | 0 | 13.4 | 2020-08-20 | 18.9 | 0 | 0.9 | 2019-08-20 | 28.3 | 0 | 10.3 | 2018-08-20 | 27.2 | 0 | 9.2 | 2017-08-20 | 26.1 | 0 | 8.1 | 2016-08-20 | 30.3 | 0 | 12.3 | 0 | 7.88
2025-08-20 | 23.7 | 0 | 5.7 | 2024-08-20 | 18.2 | 0 | 0.2 | 2023-08-20 | 26.5 | 0 | 8.5 | 2022-08-20 | 29.5 | 0 | 11.5 | 2021-08-20 | 31.1 | 0 | 13.1 | 2020-08-20 | 19.5 | 0 | 1.5 | 2019-08-20 | 28.4 | 0 | 10.4 | 2018-08-20 | 26.8 | 0 | 8.8 | 2017-08-20 | 26.1 | 0 | 8.1 | 2016-08-20 | 30.2 | 0 | 12.2 | 0 | 8
2025-08-20 | 23.1 | 0 | 5.1 | 2024-08-20 | 16.6 | 1.4 | 0 | 2023-08-20 | 25.1 | 0 | 7.1 | 2022-08-20 | 28.9 | 0 | 10.9 | 2021-08-20 | 31 | 0 | 13 | 2020-08-20 | 18.9 | 0 | 0.9 | 2019-08-20 | 27.8 | 0 | 9.8 | 2018-08-20 | 26.1 | 0 | 8.1 | 2017-08-20 | 25.5 | 0 | 7.5 | 2016-08-20 | 29.4 | 0 | 11.4 | 0.14 | 7.38
2025-08-20 | 22.7 | 0 | 4.7 | 2024-08-20 | 16.1 | 1.9 | 0 | 2023-08-20 | 24.6 | 0 | 6.6 | 2022-08-20 | 26.1 | 0 | 8.1 | 2021-08-20 | 29 | 0 | 11 | 2020-08-20 | 18.2 | 0 | 0.2 | 2019-08-20 | 25.9 | 0 | 7.9 | 2018-08-20 | 23.8 | 0 | 5.8 | 2017-08-20 | 24.1 | 0 | 6.1 | 2016-08-20 | 27.7 | 0 | 9.7 | 0.19 | 6.01
2025-08-20 | 21.3 | 0 | 3.3 | 2024-08-20 | 15.5 | 2.5 | 0 | 2023-08-20 | 23.6 | 0 | 5.6 | 2022-08-20 | 24.1 | 0 | 6.1 | 2021-08-20 | 28.6 | 0 | 10.6 | 2020-08-20 | 18.6 | 0 | 0.6 | 2019-08-20 | 23.3 | 0 | 5.3 | 2018-08-20 | 22.5 | 0 | 4.5 | 2017-08-20 | 22.1 | 0 | 4.1 | 2016-08-20 | 25.5 | 0 | 7.5 | 0.25 | 4.76
2025-08-20 | 19 | 0 | 1 | 2024-08-20 | 15.4 | 2.6 | 0 | 2023-08-20 | 22.9 | 0 | 4.9 | 2022-08-20 | 22.5 | 0 | 4.5 | 2021-08-20 | 26.2 | 0 | 8.2 | 2020-08-20 | 17.9 | 0.1 | 0 | 2019-08-20 | 20.1 | 0 | 2.1 | 2018-08-20 | 20.5 | 0 | 2.5 | 2017-08-20 | 20.9 | 0 | 2.9 | 2016-08-20 | 23.1 | 0 | 5.1 | 0.27 | 3.12
2025-08-20 | 16.6 | 1.4 | 0 | 2024-08-20 | 15.1 | 2.9 | 0 | 2023-08-20 | 22.1 | 0 | 4.1 | 2022-08-20 | 22.1 | 0 | 4.1 | 2021-08-20 | 26 | 0 | 8 | 2020-08-20 | 17.8 | 0.2 | 0 | 2019-08-20 | 19.3 | 0 | 1.3 | 2018-08-20 | 19.9 | 0 | 1.9 | 2017-08-20 | 20.3 | 0 | 2.3 | 2016-08-20 | 23.1 | 0 | 5.1 | 0.45 | 2.68
2025-08-20 | 15.8 | 2.2 | 0 | 2024-08-20 | 14.8 | 3.2 | 0 | 2023-08-20 | 22 | 0 | 4 | 2022-08-20 | 22.2 | 0 | 4.2 | 2021-08-20 | 23.6 | 0 | 5.6 | 2020-08-20 | 18.4 | 0 | 0.4 | 2019-08-20 | 18.6 | 0 | 0.6 | 2018-08-20 | 19.3 | 0 | 1.3 | 2017-08-20 | 20.1 | 0 | 2.1 | 2016-08-20 | 22.8 | 0 | 4.8 | 0.54 | 2.3
2025-08-20 | 14.8 | 3.2 | 0 | 2024-08-20 | 14.2 | 3.8 | 0 | 2023-08-20 | 20.7 | 0 | 2.7 | 2022-08-20 | 19.9 | 0 | 1.9 | 2021-08-20 | 23.1 | 0 | 5.1 | 2020-08-20 | 19 | 0 | 1 | 2019-08-20 | 18.6 | 0 | 0.6 | 2018-08-20 | 19.1 | 0 | 1.1 | 2017-08-20 | 19.2 | 0 | 1.2 | 2016-08-20 | 23.1 | 0 | 5.1 | 0.7 | 1.87
2025-08-21 | 12.5 | 5.5 | 0 | 2024-08-21 | 13.6 | 4.4 | 0 | 2023-08-21 | 20.3 | 0 | 2.3 | 2022-08-21 | 20.7 | 0 | 2.7 | 2021-08-21 | 22.9 | 0 | 4.9 | 2020-08-21 | 18.6 | 0 | 0.6 | 2019-08-21 | 17.7 | 0.3 | 0 | 2018-08-21 | 18.9 | 0 | 0.9 | 2017-08-21 | 19.2 | 0 | 1.2 | 2016-08-21 | 22.9 | 0 | 4.9 | 1.02 | 1.75
2025-08-21 | 12.4 | 5.6 | 0 | 2024-08-21 | 13.3 | 4.7 | 0 | 2023-08-21 | 20.5 | 0 | 2.5 | 2022-08-21 | 20.3 | 0 | 2.3 | 2021-08-21 | 22.7 | 0 | 4.7 | 2020-08-21 | 17.8 | 0.2 | 0 | 2019-08-21 | 18.4 | 0 | 0.4 | 2018-08-21 | 18 | 0 | 0 | 2017-08-21 | 18.1 | 0 | 0.1 | 2016-08-21 | 22.8 | 0 | 4.8 | 1.05 | 1.48
2025-08-21 | 11.2 | 6.8 | 0 | 2024-08-21 | 12.6 | 5.4 | 0 | 2023-08-21 | 21.2 | 0 | 3.2 | 2022-08-21 | 18.4 | 0 | 0.4 | 2021-08-21 | 24.2 | 0 | 6.2 | 2020-08-21 | 17.2 | 0.8 | 0 | 2019-08-21 | 18.9 | 0 | 0.9 | 2018-08-21 | 17.4 | 0.6 | 0 | 2017-08-21 | 17.9 | 0.1 | 0 | 2016-08-21 | 22.9 | 0 | 4.9 | 1.37 | 1.56
2025-08-21 | 11.9 | 6.1 | 0 | 2024-08-21 | 13.9 | 4.1 | 0 | 2023-08-21 | 19.8 | 0 | 1.8 | 2022-08-21 | 19.2 | 0 | 1.2 | 2021-08-21 | 20.4 | 0 | 2.4 | 2020-08-21 | 17.2 | 0.8 | 0 | 2019-08-21 | 17.9 | 0.1 | 0 | 2018-08-21 | 16.5 | 1.5 | 0 | 2017-08-21 | 17.5 | 0.5 | 0 | 2016-08-21 | 23 | 0 | 5 | 1.31 | 1.04
2025-08-21 | 11.8 | 6.2 | 0 | 2024-08-21 | 14 | 4 | 0 | 2023-08-21 | 17.5 | 0.5 | 0 | 2022-08-21 | 19.1 | 0 | 1.1 | 2021-08-21 | 20.9 | 0 | 2.9 | 2020-08-21 | 17.2 | 0.8 | 0 | 2019-08-21 | 18.4 | 0 | 0.4 | 2018-08-21 | 15.7 | 2.3 | 0 | 2017-08-21 | 17.1 | 0.9 | 0 | 2016-08-21 | 22.9 | 0 | 4.9 | 1.47 | 0.93
2025-08-21 | 11.1 | 6.9 | 0 | 2024-08-21 | 13.4 | 4.6 | 0 | 2023-08-21 | 16.4 | 1.6 | 0 | 2022-08-21 | 19.4 | 0 | 1.4 | 2021-08-21 | 21 | 0 | 3 | 2020-08-21 | 17.1 | 0.9 | 0 | 2019-08-21 | 17.1 | 0.9 | 0 | 2018-08-21 | 16 | 2 | 0 | 2017-08-21 | 16.3 | 1.7 | 0 | 2016-08-21 | 22.9 | 0 | 4.9 | 1.86 | 0.93
2025-08-21 | 12 | 6 | 0 | 2024-08-21 | 13.2 | 4.8 | 0 | 2023-08-21 | 15.6 | 2.4 | 0 | 2022-08-21 | 19.5 | 0 | 1.5 | 2021-08-21 | 20.5 | 0 | 2.5 | 2020-08-21 | 17.6 | 0.4 | 0 | 2019-08-21 | 16.9 | 1.1 | 0 | 2018-08-21 | 16.9 | 1.1 | 0 | 2017-08-21 | 16.9 | 1.1 | 0 | 2016-08-21 | 23.2 | 0 | 5.2 | 1.69 | 0.92
2025-08-21 | 14.9 | 3.1 | 0 | 2024-08-21 | 12.8 | 5.2 | 0 | 2023-08-21 | 15.9 | 2.1 | 0 | 2022-08-21 | 20.1 | 0 | 2.1 | 2021-08-21 | 23.1 | 0 | 5.1 | 2020-08-21 | 17.9 | 0.1 | 0 | 2019-08-21 | 18.4 | 0 | 0.4 | 2018-08-21 | 18.1 | 0 | 0.1 | 2017-08-21 | 18.7 | 0 | 0.7 | 2016-08-21 | 21.7 | 0 | 3.7 | 1.05 | 1.21
2025-08-21 | 18.3 | 0 | 0.3 | 2024-08-21 | 12.9 | 5.1 | 0 | 2023-08-21 | 16.3 | 1.7 | 0 | 2022-08-21 | 22.2 | 0 | 4.2 | 2021-08-21 | 25.6 | 0 | 7.6 | 2020-08-21 | 18.5 | 0 | 0.5 | 2019-08-21 | 18.8 | 0 | 0.8 | 2018-08-21 | 19.6 | 0 | 1.6 | 2017-08-21 | 21.1 | 0 | 3.1 | 2016-08-21 | 20.8 | 0 | 2.8 | 0.68 | 2.09
2025-08-21 | 20.5 | 0 | 2.5 | 2024-08-21 | 13 | 5 | 0 | 2023-08-21 | 17.6 | 0.4 | 0 | 2022-08-21 | 24.6 | 0 | 6.6 | 2021-08-21 | 27.3 | 0 | 9.3 | 2020-08-21 | 19.2 | 0 | 1.2 | 2019-08-21 | 19.4 | 0 | 1.4 | 2018-08-21 | 20.5 | 0 | 2.5 | 2017-08-21 | 23.9 | 0 | 5.9 | 2016-08-21 | 20.9 | 0 | 2.9 | 0.54 | 3.23
2025-08-21 | 22.9 | 0 | 4.9 | 2024-08-21 | 14.7 | 3.3 | 0 | 2023-08-21 | 18.9 | 0 | 0.9 | 2022-08-21 | 25.5 | 0 | 7.5 | 2021-08-21 | 29.1 | 0 | 11.1 | 2020-08-21 | 20.4 | 0 | 2.4 | 2019-08-21 | 21.1 | 0 | 3.1 | 2018-08-21 | 22.1 | 0 | 4.1 | 2017-08-21 | 25.7 | 0 | 7.7 | 2016-08-21 | 21.3 | 0 | 3.3 | 0.33 | 4.5
2025-08-21 | 24.3 | 0 | 6.3 | 2024-08-21 | 17.1 | 0.9 | 0 | 2023-08-21 | 20.4 | 0 | 2.4 | 2022-08-21 | 24.8 | 0 | 6.8 | 2021-08-21 | 30.1 | 0 | 12.1 | 2020-08-21 | 21 | 0 | 3 | 2019-08-21 | 24.7 | 0 | 6.7 | 2018-08-21 | 23.3 | 0 | 5.3 | 2017-08-21 | 26.7 | 0 | 8.7 | 2016-08-21 | 22 | 0 | 4 | 0.09 | 5.53
2025-08-21 | 24.8 | 0 | 6.8 | 2024-08-21 | 18 | 0 | 0 | 2023-08-21 | 20.5 | 0 | 2.5 | 2022-08-21 | 23.9 | 0 | 5.9 | 2021-08-21 | 31.1 | 0 | 13.1 | 2020-08-21 | 21.5 | 0 | 3.5 | 2019-08-21 | 27.1 | 0 | 9.1 | 2018-08-21 | 23.6 | 0 | 5.6 | 2017-08-21 | 27.5 | 0 | 9.5 | 2016-08-21 | 22.2 | 0 | 4.2 | 0 | 6.02
2025-08-21 | 25.9 | 0 | 7.9 | 2024-08-21 | 18.7 | 0 | 0.7 | 2023-08-21 | 21.4 | 0 | 3.4 | 2022-08-21 | 22.2 | 0 | 4.2 | 2021-08-21 | 32.5 | 0 | 14.5 | 2020-08-21 | 22.2 | 0 | 4.2 | 2019-08-21 | 26.1 | 0 | 8.1 | 2018-08-21 | 23 | 0 | 5 | 2017-08-21 | 27.2 | 0 | 9.2 | 2016-08-21 | 21.7 | 0 | 3.7 | 0 | 6.09
2025-08-21 | 25.8 | 0 | 7.8 | 2024-08-21 | 18.1 | 0 | 0.1 | 2023-08-21 | 22.1 | 0 | 4.1 | 2022-08-21 | 21.9 | 0 | 3.9 | 2021-08-21 | 32.5 | 0 | 14.5 | 2020-08-21 | 22.6 | 0 | 4.6 | 2019-08-21 | 26.4 | 0 | 8.4 | 2018-08-21 | 23.1 | 0 | 5.1 | 2017-08-21 | 26.8 | 0 | 8.8 | 2016-08-21 | 22.4 | 0 | 4.4 | 0 | 6.17
2025-08-21 | 25.8 | 0 | 7.8 | 2024-08-21 | 16.8 | 1.2 | 0 | 2023-08-21 | 21.2 | 0 | 3.2 | 2022-08-21 | 22.7 | 0 | 4.7 | 2021-08-21 | 32.5 | 0 | 14.5 | 2020-08-21 | 22.3 | 0 | 4.3 | 2019-08-21 | 27.3 | 0 | 9.3 | 2018-08-21 | 22.2 | 0 | 4.2 | 2017-08-21 | 27.9 | 0 | 9.9 | 2016-08-21 | 22.1 | 0 | 4.1 | 0.12 | 6.2
2025-08-21 | 26 | 0 | 8 | 2024-08-21 | 13.7 | 4.3 | 0 | 2023-08-21 | 21.6 | 0 | 3.6 | 2022-08-21 | 22.7 | 0 | 4.7 | 2021-08-21 | 31.9 | 0 | 13.9 | 2020-08-21 | 22.6 | 0 | 4.6 | 2019-08-21 | 26.8 | 0 | 8.8 | 2018-08-21 | 20.3 | 0 | 2.3 | 2017-08-21 | 27.9 | 0 | 9.9 | 2016-08-21 | 22.8 | 0 | 4.8 | 0.43 | 6.06
2025-08-21 | 26.4 | 0 | 8.4 | 2024-08-21 | 14.2 | 3.8 | 0 | 2023-08-21 | 20.4 | 0 | 2.4 | 2022-08-21 | 23.1 | 0 | 5.1 | 2021-08-21 | 31.2 | 0 | 13.2 | 2020-08-21 | 22.7 | 0 | 4.7 | 2019-08-21 | 25 | 0 | 7 | 2018-08-21 | 19.8 | 0 | 1.8 | 2017-08-21 | 27.6 | 0 | 9.6 | 2016-08-21 | 23.2 | 0 | 5.2 | 0.38 | 5.74
2025-08-21 | 25.4 | 0 | 7.4 | 2024-08-21 | 14.2 | 3.8 | 0 | 2023-08-21 | 19.6 | 0 | 1.6 | 2022-08-21 | 22.4 | 0 | 4.4 | 2021-08-21 | 29.5 | 0 | 11.5 | 2020-08-21 | 22.2 | 0 | 4.2 | 2019-08-21 | 23 | 0 | 5 | 2018-08-21 | 19.9 | 0 | 1.9 | 2017-08-21 | 26.1 | 0 | 8.1 | 2016-08-21 | 22.1 | 0 | 4.1 | 0.38 | 4.82
2025-08-21 | 21.3 | 0 | 3.3 | 2024-08-21 | 15 | 3 | 0 | 2023-08-21 | 19.2 | 0 | 1.2 | 2022-08-21 | 21.6 | 0 | 3.6 | 2021-08-21 | 26.9 | 0 | 8.9 | 2020-08-21 | 19.5 | 0 | 1.5 | 2019-08-21 | 21.8 | 0 | 3.8 | 2018-08-21 | 19.7 | 0 | 1.7 | 2017-08-21 | 24.3 | 0 | 6.3 | 2016-08-21 | 21.8 | 0 | 3.8 | 0.3 | 3.41
2025-08-21 | 20 | 0 | 2 | 2024-08-21 | 13.8 | 4.2 | 0 | 2023-08-21 | 18.4 | 0 | 0.4 | 2022-08-21 | 19.8 | 0 | 1.8 | 2021-08-21 | 25.3 | 0 | 7.3 | 2020-08-21 | 17.1 | 0.9 | 0 | 2019-08-21 | 21.6 | 0 | 3.6 | 2018-08-21 | 19.7 | 0 | 1.7 | 2017-08-21 | 23 | 0 | 5 | 2016-08-21 | 20.8 | 0 | 2.8 | 0.51 | 2.46
2025-08-21 | 17.1 | 0.9 | 0 | 2024-08-21 | 13.5 | 4.5 | 0 | 2023-08-21 | 16.8 | 1.2 | 0 | 2022-08-21 | 20.4 | 0 | 2.4 | 2021-08-21 | 25.7 | 0 | 7.7 | 2020-08-21 | 17.4 | 0.6 | 0 | 2019-08-21 | 20.9 | 0 | 2.9 | 2018-08-21 | 19.9 | 0 | 1.9 | 2017-08-21 | 22.1 | 0 | 4.1 | 2016-08-21 | 20.3 | 0 | 2.3 | 0.72 | 2.13
2025-08-21 | 17.7 | 0.3 | 0 | 2024-08-21 | 13.6 | 4.4 | 0 | 2023-08-21 | 15.8 | 2.2 | 0 | 2022-08-21 | 19.7 | 0 | 1.7 | 2021-08-21 | 22.6 | 0 | 4.6 | 2020-08-21 | 16.2 | 1.8 | 0 | 2019-08-21 | 21.1 | 0 | 3.1 | 2018-08-21 | 19.7 | 0 | 1.7 | 2017-08-21 | 21.4 | 0 | 3.4 | 2016-08-21 | 18.4 | 0 | 0.4 | 0.87 | 1.49
2025-08-21 | 17.1 | 0.9 | 0 | 2024-08-21 | 13.9 | 4.1 | 0 | 2023-08-21 | 15.4 | 2.6 | 0 | 2022-08-21 | 18.6 | 0 | 0.6 | 2021-08-21 | 22.5 | 0 | 4.5 | 2020-08-21 | 16.5 | 1.5 | 0 | 2019-08-21 | 20.7 | 0 | 2.7 | 2018-08-21 | 19.9 | 0 | 1.9 | 2017-08-21 | 20.9 | 0 | 2.9 | 2016-08-21 | 16.9 | 1.1 | 0 | 1.02 | 1.26
2025-08-22 | 16.3 | 1.7 | 0 | 2024-08-22 | 13.9 | 4.1 | 0 | 2023-08-22 | 15.3 | 2.7 | 0 | 2022-08-22 | 19.5 | 0 | 1.5 | 2021-08-22 | 22.4 | 0 | 4.4 | 2020-08-22 | 15.2 | 2.8 | 0 | 2019-08-22 | 20.5 | 0 | 2.5 | 2018-08-22 | 20.1 | 0 | 2.1 | 2017-08-22 | 20.1 | 0 | 2.1 | 2016-08-22 | 15.9 | 2.1 | 0 | 1.34 | 1.26
2025-08-22 | 15.3 | 2.7 | 0 | 2024-08-22 | 13.8 | 4.2 | 0 | 2023-08-22 | 14.3 | 3.7 | 0 | 2022-08-22 | 18.6 | 0 | 0.6 | 2021-08-22 | 20.7 | 0 | 2.7 | 2020-08-22 | 15.9 | 2.1 | 0 | 2019-08-22 | 20.1 | 0 | 2.1 | 2018-08-22 | 20.7 | 0 | 2.7 | 2017-08-22 | 19.6 | 0 | 1.6 | 2016-08-22 | 13.8 | 4.2 | 0 | 1.69 | 0.97
2025-08-22 | 14.6 | 3.4 | 0 | 2024-08-22 | 14.1 | 3.9 | 0 | 2023-08-22 | 11.7 | 6.3 | 0 | 2022-08-22 | 18.8 | 0 | 0.8 | 2021-08-22 | 21.1 | 0 | 3.1 | 2020-08-22 | 15.4 | 2.6 | 0 | 2019-08-22 | 20 | 0 | 2 | 2018-08-22 | 20.9 | 0 | 2.9 | 2017-08-22 | 19 | 0 | 1 | 2016-08-22 | 12.9 | 5.1 | 0 | 2.13 | 0.98
2025-08-22 | 15.7 | 2.3 | 0 | 2024-08-22 | 14.3 | 3.7 | 0 | 2023-08-22 | 11 | 7 | 0 | 2022-08-22 | 18.5 | 0 | 0.5 | 2021-08-22 | 20.4 | 0 | 2.4 | 2020-08-22 | 15.8 | 2.2 | 0 | 2019-08-22 | 19 | 0 | 1 | 2018-08-22 | 20.5 | 0 | 2.5 | 2017-08-22 | 19.1 | 0 | 1.1 | 2016-08-22 | 12.8 | 5.2 | 0 | 2.04 | 0.75
2025-08-22 | 12.7 | 5.3 | 0 | 2024-08-22 | 13.4 | 4.6 | 0 | 2023-08-22 | 11.6 | 6.4 | 0 | 2022-08-22 | 18.5 | 0 | 0.5 | 2021-08-22 | 21.1 | 0 | 3.1 | 2020-08-22 | 16.2 | 1.8 | 0 | 2019-08-22 | 18.6 | 0 | 0.6 | 2018-08-22 | 20.3 | 0 | 2.3 | 2017-08-22 | 19 | 0 | 1 | 2016-08-22 | 12.3 | 5.7 | 0 | 2.38 | 0.75
2025-08-22 | 12.6 | 5.4 | 0 | 2024-08-22 | 12.3 | 5.7 | 0 | 2023-08-22 | 10.9 | 7.1 | 0 | 2022-08-22 | 18 | 0 | 0 | 2021-08-22 | 21 | 0 | 3 | 2020-08-22 | 15.9 | 2.1 | 0 | 2019-08-22 | 17.7 | 0.3 | 0 | 2018-08-22 | 20.4 | 0 | 2.4 | 2017-08-22 | 19.1 | 0 | 1.1 | 2016-08-22 | 11.7 | 6.3 | 0 | 2.69 | 0.65
2025-08-22 | 13.6 | 4.4 | 0 | 2024-08-22 | 13.3 | 4.7 | 0 | 2023-08-22 | 12.6 | 5.4 | 0 | 2022-08-22 | 18.8 | 0 | 0.8 | 2021-08-22 | 20.8 | 0 | 2.8 | 2020-08-22 | 15.7 | 2.3 | 0 | 2019-08-22 | 18.7 | 0 | 0.7 | 2018-08-22 | 18.6 | 0 | 0.6 | 2017-08-22 | 19.8 | 0 | 1.8 | 2016-08-22 | 12 | 6 | 0 | 2.28 | 0.67
2025-08-22 | 17.1 | 0.9 | 0 | 2024-08-22 | 14.5 | 3.5 | 0 | 2023-08-22 | 14.6 | 3.4 | 0 | 2022-08-22 | 19.3 | 0 | 1.3 | 2021-08-22 | 22.7 | 0 | 4.7 | 2020-08-22 | 18.4 | 0 | 0.4 | 2019-08-22 | 19.3 | 0 | 1.3 | 2018-08-22 | 18.2 | 0 | 0.2 | 2017-08-22 | 20.2 | 0 | 2.2 | 2016-08-22 | 13.8 | 4.2 | 0 | 1.2 | 1.01
2025-08-22 | 20.3 | 0 | 2.3 | 2024-08-22 | 15 | 3 | 0 | 2023-08-22 | 17.8 | 0.2 | 0 | 2022-08-22 | 20.5 | 0 | 2.5 | 2021-08-22 | 25.2 | 0 | 7.2 | 2020-08-22 | 20 | 0 | 2 | 2019-08-22 | 19.8 | 0 | 1.8 | 2018-08-22 | 19.1 | 0 | 1.1 | 2017-08-22 | 20.5 | 0 | 2.5 | 2016-08-22 | 14.8 | 3.2 | 0 | 0.64 | 1.94
2025-08-22 | 23.9 | 0 | 5.9 | 2024-08-22 | 16 | 2 | 0 | 2023-08-22 | 19.4 | 0 | 1.4 | 2022-08-22 | 23 | 0 | 5 | 2021-08-22 | 27.5 | 0 | 9.5 | 2020-08-22 | 21.4 | 0 | 3.4 | 2019-08-22 | 21.6 | 0 | 3.6 | 2018-08-22 | 19.6 | 0 | 1.6 | 2017-08-22 | 21.4 | 0 | 3.4 | 2016-08-22 | 16.3 | 1.7 | 0 | 0.37 | 3.38
2025-08-22 | 25 | 0 | 7 | 2024-08-22 | 17.5 | 0.5 | 0 | 2023-08-22 | 21.2 | 0 | 3.2 | 2022-08-22 | 23 | 0 | 5 | 2021-08-22 | 28.7 | 0 | 10.7 | 2020-08-22 | 22.4 | 0 | 4.4 | 2019-08-22 | 22.2 | 0 | 4.2 | 2018-08-22 | 19.7 | 0 | 1.7 | 2017-08-22 | 23.4 | 0 | 5.4 | 2016-08-22 | 17.6 | 0.4 | 0 | 0.09 | 4.16
2025-08-22 | 26.7 | 0 | 8.7 | 2024-08-22 | 18.8 | 0 | 0.8 | 2023-08-22 | 22.7 | 0 | 4.7 | 2022-08-22 | 23.8 | 0 | 5.8 | 2021-08-22 | 29.3 | 0 | 11.3 | 2020-08-22 | 23.6 | 0 | 5.6 | 2019-08-22 | 22.7 | 0 | 4.7 | 2018-08-22 | 19.7 | 0 | 1.7 | 2017-08-22 | 24.3 | 0 | 6.3 | 2016-08-22 | 19.4 | 0 | 1.4 | 0 | 5.1
2025-08-22 | 27.4 | 0 | 9.4 | 2024-08-22 | 21.1 | 0 | 3.1 | 2023-08-22 | 23.7 | 0 | 5.7 | 2022-08-22 | 24.6 | 0 | 6.6 | 2021-08-22 | 30.8 | 0 | 12.8 | 2020-08-22 | 24.5 | 0 | 6.5 | 2019-08-22 | 24.1 | 0 | 6.1 | 2018-08-22 | 19.9 | 0 | 1.9 | 2017-08-22 | 24.7 | 0 | 6.7 | 2016-08-22 | 20.8 | 0 | 2.8 | 0 | 6.16
2025-08-22 | 28.5 | 0 | 10.5 | 2024-08-22 | 22.9 | 0 | 4.9 | 2023-08-22 | 23.2 | 0 | 5.2 | 2022-08-22 | 24.5 | 0 | 6.5 | 2021-08-22 | 31 | 0 | 13 | 2020-08-22 | 26 | 0 | 8 | 2019-08-22 | 22.2 | 0 | 4.2 | 2018-08-22 | 19.6 | 0 | 1.6 | 2017-08-22 | 23.7 | 0 | 5.7 | 2016-08-22 | 20.5 | 0 | 2.5 | 0 | 6.21
2025-08-22 | 28.6 | 0 | 10.6 | 2024-08-22 | 21.8 | 0 | 3.8 | 2023-08-22 | 24.8 | 0 | 6.8 | 2022-08-22 | 24.4 | 0 | 6.4 | 2021-08-22 | 32 | 0 | 14 | 2020-08-22 | 26.2 | 0 | 8.2 | 2019-08-22 | 24 | 0 | 6 | 2018-08-22 | 19.5 | 0 | 1.5 | 2017-08-22 | 24.7 | 0 | 6.7 | 2016-08-22 | 22 | 0 | 4 | 0 | 6.8
2025-08-22 | 28.4 | 0 | 10.4 | 2024-08-22 | 23.7 | 0 | 5.7 | 2023-08-22 | 24.6 | 0 | 6.6 | 2022-08-22 | 20.9 | 0 | 2.9 | 2021-08-22 | 31.9 | 0 | 13.9 | 2020-08-22 | 26.6 | 0 | 8.6 | 2019-08-22 | 23.8 | 0 | 5.8 | 2018-08-22 | 19.6 | 0 | 1.6 | 2017-08-22 | 25.2 | 0 | 7.2 | 2016-08-22 | 21.7 | 0 | 3.7 | 0 | 6.64
2025-08-22 | 29.9 | 0 | 11.9 | 2024-08-22 | 20.1 | 0 | 2.1 | 2023-08-22 | 24.6 | 0 | 6.6 | 2022-08-22 | 21.4 | 0 | 3.4 | 2021-08-22 | 31.6 | 0 | 13.6 | 2020-08-22 | 26.9 | 0 | 8.9 | 2019-08-22 | 23.3 | 0 | 5.3 | 2018-08-22 | 19.6 | 0 | 1.6 | 2017-08-22 | 19.5 | 0 | 1.5 | 2016-08-22 | 22.3 | 0 | 4.3 | 0 | 5.92
2025-08-22 | 27.4 | 0 | 9.4 | 2024-08-22 | 22.3 | 0 | 4.3 | 2023-08-22 | 23.6 | 0 | 5.6 | 2022-08-22 | 20.6 | 0 | 2.6 | 2021-08-22 | 30.1 | 0 | 12.1 | 2020-08-22 | 26.4 | 0 | 8.4 | 2019-08-22 | 22.7 | 0 | 4.7 | 2018-08-22 | 19.1 | 0 | 1.1 | 2017-08-22 | 20.9 | 0 | 2.9 | 2016-08-22 | 21.9 | 0 | 3.9 | 0 | 5.5
2025-08-22 | 26.7 | 0 | 8.7 | 2024-08-22 | 21.4 | 0 | 3.4 | 2023-08-22 | 22.1 | 0 | 4.1 | 2022-08-22 | 20.7 | 0 | 2.7 | 2021-08-22 | 29.7 | 0 | 11.7 | 2020-08-22 | 23.6 | 0 | 5.6 | 2019-08-22 | 21.4 | 0 | 3.4 | 2018-08-22 | 18.5 | 0 | 0.5 | 2017-08-22 | 21.4 | 0 | 3.4 | 2016-08-22 | 20.6 | 0 | 2.6 | 0 | 4.61
2025-08-22 | 25.4 | 0 | 7.4 | 2024-08-22 | 18.4 | 0 | 0.4 | 2023-08-22 | 20.2 | 0 | 2.2 | 2022-08-22 | 20.4 | 0 | 2.4 | 2021-08-22 | 27.7 | 0 | 9.7 | 2020-08-22 | 21.1 | 0 | 3.1 | 2019-08-22 | 19.3 | 0 | 1.3 | 2018-08-22 | 17 | 1 | 0 | 2017-08-22 | 21.1 | 0 | 3.1 | 2016-08-22 | 17.6 | 0.4 | 0 | 0.14 | 2.96
2025-08-22 | 24.1 | 0 | 6.1 | 2024-08-22 | 17.9 | 0.1 | 0 | 2023-08-22 | 18.9 | 0 | 0.9 | 2022-08-22 | 20.3 | 0 | 2.3 | 2021-08-22 | 26.4 | 0 | 8.4 | 2020-08-22 | 20.9 | 0 | 2.9 | 2019-08-22 | 17.9 | 0.1 | 0 | 2018-08-22 | 16.2 | 1.8 | 0 | 2017-08-22 | 20 | 0 | 2 | 2016-08-22 | 17.4 | 0.6 | 0 | 0.26 | 2.26
2025-08-22 | 22.7 | 0 | 4.7 | 2024-08-22 | 15.8 | 2.2 | 0 | 2023-08-22 | 19 | 0 | 1 | 2022-08-22 | 20.2 | 0 | 2.2 | 2021-08-22 | 25.5 | 0 | 7.5 | 2020-08-22 | 20.9 | 0 | 2.9 | 2019-08-22 | 16.1 | 1.9 | 0 | 2018-08-22 | 14.8 | 3.2 | 0 | 2017-08-22 | 20.2 | 0 | 2.2 | 2016-08-22 | 15.1 | 2.9 | 0 | 1.02 | 2.05
2025-08-22 | 22.5 | 0 | 4.5 | 2024-08-22 | 17.1 | 0.9 | 0 | 2023-08-22 | 15.2 | 2.8 | 0 | 2022-08-22 | 19.8 | 0 | 1.8 | 2021-08-22 | 25.7 | 0 | 7.7 | 2020-08-22 | 20.2 | 0 | 2.2 | 2019-08-22 | 16.6 | 1.4 | 0 | 2018-08-22 | 12.7 | 5.3 | 0 | 2017-08-22 | 20 | 0 | 2 | 2016-08-22 | 14.6 | 3.4 | 0 | 1.38 | 1.82
2025-08-22 | 21.7 | 0 | 3.7 | 2024-08-22 | 14.4 | 3.6 | 0 | 2023-08-22 | 15.3 | 2.7 | 0 | 2022-08-22 | 19.7 | 0 | 1.7 | 2021-08-22 | 24.5 | 0 | 6.5 | 2020-08-22 | 19.6 | 0 | 1.6 | 2019-08-22 | 16.8 | 1.2 | 0 | 2018-08-22 | 11.5 | 6.5 | 0 | 2017-08-22 | 18.8 | 0 | 0.8 | 2016-08-22 | 13.8 | 4.2 | 0 | 1.82 | 1.43
2025-08-23 | 20.6 | 0 | 2.6 | 2024-08-23 | 14.2 | 3.8 | 0 | 2023-08-23 | 15.6 | 2.4 | 0 | 2022-08-23 | 19.6 | 0 | 1.6 | 2021-08-23 | 23.1 | 0 | 5.1 | 2020-08-23 | 18.9 | 0 | 0.9 | 2019-08-23 | 14.8 | 3.2 | 0 | 2018-08-23 | 11.2 | 6.8 | 0 | 2017-08-23 | 17.2 | 0.8 | 0 | 2016-08-23 | 10.4 | 7.6 | 0 | 2.46 | 1.02
2025-08-23 | 19.3 | 0 | 1.3 | 2024-08-23 | 14.6 | 3.4 | 0 | 2023-08-23 | 15.1 | 2.9 | 0 | 2022-08-23 | 19.4 | 0 | 1.4 | 2021-08-23 | 22.4 | 0 | 4.4 | 2020-08-23 | 19.9 | 0 | 1.9 | 2019-08-23 | 13 | 5 | 0 | 2018-08-23 | 11.3 | 6.7 | 0 | 2017-08-23 | 16.4 | 1.6 | 0 | 2016-08-23 | 11.8 | 6.2 | 0 | 2.58 | 0.9
2025-08-23 | 18.7 | 0 | 0.7 | 2024-08-23 | 13.5 | 4.5 | 0 | 2023-08-23 | 13.4 | 4.6 | 0 | 2022-08-23 | 19.1 | 0 | 1.1 | 2021-08-23 | 21.8 | 0 | 3.8 | 2020-08-23 | 19.5 | 0 | 1.5 | 2019-08-23 | 12.7 | 5.3 | 0 | 2018-08-23 | 10.7 | 7.3 | 0 | 2017-08-23 | 15.9 | 2.1 | 0 | 2016-08-23 | 12 | 6 | 0 | 2.98 | 0.71
2025-08-23 | 17 | 1 | 0 | 2024-08-23 | 11.5 | 6.5 | 0 | 2023-08-23 | 14 | 4 | 0 | 2022-08-23 | 18.7 | 0 | 0.7 | 2021-08-23 | 21.4 | 0 | 3.4 | 2020-08-23 | 19.8 | 0 | 1.8 | 2019-08-23 | 12.9 | 5.1 | 0 | 2018-08-23 | 10.3 | 7.7 | 0 | 2017-08-23 | 15.7 | 2.3 | 0 | 2016-08-23 | 10.4 | 7.6 | 0 | 3.42 | 0.59
2025-08-23 | 16.2 | 1.8 | 0 | 2024-08-23 | 12.9 | 5.1 | 0 | 2023-08-23 | 13.4 | 4.6 | 0 | 2022-08-23 | 18.7 | 0 | 0.7 | 2021-08-23 | 21.4 | 0 | 3.4 | 2020-08-23 | 19.9 | 0 | 1.9 | 2019-08-23 | 12.4 | 5.6 | 0 | 2018-08-23 | 10.8 | 7.2 | 0 | 2017-08-23 | 15.1 | 2.9 | 0 | 2016-08-23 | 10.2 | 7.8 | 0 | 3.5 | 0.6
2025-08-23 | 15.3 | 2.7 | 0 | 2024-08-23 | 11.1 | 6.9 | 0 | 2023-08-23 | 14.2 | 3.8 | 0 | 2022-08-23 | 18.5 | 0 | 0.5 | 2021-08-23 | 21.2 | 0 | 3.2 | 2020-08-23 | 19.7 | 0 | 1.7 | 2019-08-23 | 11.2 | 6.8 | 0 | 2018-08-23 | 10.2 | 7.8 | 0 | 2017-08-23 | 14.3 | 3.7 | 0 | 2016-08-23 | 10 | 8 | 0 | 3.97 | 0.54
2025-08-23 | 16.7 | 1.3 | 0 | 2024-08-23 | 12 | 6 | 0 | 2023-08-23 | 13 | 5 | 0 | 2022-08-23 | 18.6 | 0 | 0.6 | 2021-08-23 | 21.4 | 0 | 3.4 | 2020-08-23 | 19.3 | 0 | 1.3 | 2019-08-23 | 13 | 5 | 0 | 2018-08-23 | 11 | 7 | 0 | 2017-08-23 | 14.1 | 3.9 | 0 | 2016-08-23 | 11.2 | 6.8 | 0 | 3.5 | 0.53
2025-08-23 | 19 | 0 | 1 | 2024-08-23 | 14.2 | 3.8 | 0 | 2023-08-23 | 17.1 | 0.9 | 0 | 2022-08-23 | 18.9 | 0 | 0.9 | 2021-08-23 | 23.1 | 0 | 5.1 | 2020-08-23 | 19.7 | 0 | 1.7 | 2019-08-23 | 15.1 | 2.9 | 0 | 2018-08-23 | 13.4 | 4.6 | 0 | 2017-08-23 | 15.2 | 2.8 | 0 | 2016-08-23 | 14.4 | 3.6 | 0 | 1.86 | 0.87
2025-08-23 | 20.9 | 0 | 2.9 | 2024-08-23 | 16.9 | 1.1 | 0 | 2023-08-23 | 19.9 | 0 | 1.9 | 2022-08-23 | 19.5 | 0 | 1.5 | 2021-08-23 | 23.6 | 0 | 5.6 | 2020-08-23 | 21.7 | 0 | 3.7 | 2019-08-23 | 16.5 | 1.5 | 0 | 2018-08-23 | 16.1 | 1.9 | 0 | 2017-08-23 | 16.8 | 1.2 | 0 | 2016-08-23 | 17.1 | 0.9 | 0 | 0.66 | 1.56
2025-08-23 | 21.4 | 0 | 3.4 | 2024-08-23 | 19.8 | 0 | 1.8 | 2023-08-23 | 21.8 | 0 | 3.8 | 2022-08-23 | 20.2 | 0 | 2.2 | 2021-08-23 | 25 | 0 | 7 | 2020-08-23 | 23.3 | 0 | 5.3 | 2019-08-23 | 18.6 | 0 | 0.6 | 2018-08-23 | 18.2 | 0 | 0.2 | 2017-08-23 | 18.1 | 0 | 0.1 | 2016-08-23 | 20.5 | 0 | 2.5 | 0 | 2.69
2025-08-23 | 22.6 | 0 | 4.6 | 2024-08-23 | 21.5 | 0 | 3.5 | 2023-08-23 | 23.6 | 0 | 5.6 | 2022-08-23 | 20.9 | 0 | 2.9 | 2021-08-23 | 26.5 | 0 | 8.5 | 2020-08-23 | 24.2 | 0 | 6.2 | 2019-08-23 | 19.8 | 0 | 1.8 | 2018-08-23 | 20.4 | 0 | 2.4 | 2017-08-23 | 19 | 0 | 1 | 2016-08-23 | 22.8 | 0 | 4.8 | 0 | 4.13
2025-08-23 | 25.9 | 0 | 7.9 | 2024-08-23 | 22.8 | 0 | 4.8 | 2023-08-23 | 24.3 | 0 | 6.3 | 2022-08-23 | 22.2 | 0 | 4.2 | 2021-08-23 | 26.8 | 0 | 8.8 | 2020-08-23 | 25.9 | 0 | 7.9 | 2019-08-23 | 21.2 | 0 | 3.2 | 2018-08-23 | 21.9 | 0 | 3.9 | 2017-08-23 | 19.6 | 0 | 1.6 | 2016-08-23 | 24.1 | 0 | 6.1 | 0 | 5.47
2025-08-23 | 26.3 | 0 | 8.3 | 2024-08-23 | 24.1 | 0 | 6.1 | 2023-08-23 | 25.3 | 0 | 7.3 | 2022-08-23 | 20.4 | 0 | 2.4 | 2021-08-23 | 27 | 0 | 9 | 2020-08-23 | 27.3 | 0 | 9.3 | 2019-08-23 | 20.5 | 0 | 2.5 | 2018-08-23 | 23.7 | 0 | 5.7 | 2017-08-23 | 21.5 | 0 | 3.5 | 2016-08-23 | 25.6 | 0 | 7.6 | 0 | 6.17
2025-08-23 | 27.9 | 0 | 9.9 | 2024-08-23 | 23.3 | 0 | 5.3 | 2023-08-23 | 25.4 | 0 | 7.4 | 2022-08-23 | 21.1 | 0 | 3.1 | 2021-08-23 | 26.1 | 0 | 8.1 | 2020-08-23 | 26.9 | 0 | 8.9 | 2019-08-23 | 20.3 | 0 | 2.3 | 2018-08-23 | 24.6 | 0 | 6.6 | 2017-08-23 | 21.5 | 0 | 3.5 | 2016-08-23 | 26.7 | 0 | 8.7 | 0 | 6.38
2025-08-23 | 27.3 | 0 | 9.3 | 2024-08-23 | 24.9 | 0 | 6.9 | 2023-08-23 | 25.8 | 0 | 7.8 | 2022-08-23 | 21.9 | 0 | 3.9 | 2021-08-23 | 26.1 | 0 | 8.1 | 2020-08-23 | 27.6 | 0 | 9.6 | 2019-08-23 | 20.4 | 0 | 2.4 | 2018-08-23 | 25.1 | 0 | 7.1 | 2017-08-23 | 21.3 | 0 | 3.3 | 2016-08-23 | 26.2 | 0 | 8.2 | 0 | 6.66
2025-08-23 | 26.8 | 0 | 8.8 | 2024-08-23 | 25.1 | 0 | 7.1 | 2023-08-23 | 22 | 0 | 4 | 2022-08-23 | 21 | 0 | 3 | 2021-08-23 | 26.8 | 0 | 8.8 | 2020-08-23 | 28 | 0 | 10 | 2019-08-23 | 21.2 | 0 | 3.2 | 2018-08-23 | 25.2 | 0 | 7.2 | 2017-08-23 | 21 | 0 | 3 | 2016-08-23 | 26.8 | 0 | 8.8 | 0 | 6.39
2025-08-23 | 26 | 0 | 8 | 2024-08-23 | 24.9 | 0 | 6.9 | 2023-08-23 | 21.7 | 0 | 3.7 | 2022-08-23 | 21.9 | 0 | 3.9 | 2021-08-23 | 28.1 | 0 | 10.1 | 2020-08-23 | 27.6 | 0 | 9.6 | 2019-08-23 | 19.4 | 0 | 1.4 | 2018-08-23 | 25.3 | 0 | 7.3 | 2017-08-23 | 21.1 | 0 | 3.1 | 2016-08-23 | 26.9 | 0 | 8.9 | 0 | 6.29
2025-08-23 | 25.6 | 0 | 7.6 | 2024-08-23 | 23.8 | 0 | 5.8 | 2023-08-23 | 22.3 | 0 | 4.3 | 2022-08-23 | 22.5 | 0 | 4.5 | 2021-08-23 | 27.1 | 0 | 9.1 | 2020-08-23 | 27.6 | 0 | 9.6 | 2019-08-23 | 20.4 | 0 | 2.4 | 2018-08-23 | 24.8 | 0 | 6.8 | 2017-08-23 | 20.7 | 0 | 2.7 | 2016-08-23 | 26.4 | 0 | 8.4 | 0 | 6.12
2025-08-23 | 25 | 0 | 7 | 2024-08-23 | 22.7 | 0 | 4.7 | 2023-08-23 | 21.4 | 0 | 3.4 | 2022-08-23 | 22.2 | 0 | 4.2 | 2021-08-23 | 26.1 | 0 | 8.1 | 2020-08-23 | 24.2 | 0 | 6.2 | 2019-08-23 | 18.8 | 0 | 0.8 | 2018-08-23 | 22.9 | 0 | 4.9 | 2017-08-23 | 20.6 | 0 | 2.6 | 2016-08-23 | 25.4 | 0 | 7.4 | 0 | 4.93
2025-08-23 | 24.3 | 0 | 6.3 | 2024-08-23 | 20.5 | 0 | 2.5 | 2023-08-23 | 20.4 | 0 | 2.4 | 2022-08-23 | 21.8 | 0 | 3.8 | 2021-08-23 | 24.6 | 0 | 6.6 | 2020-08-23 | 22.5 | 0 | 4.5 | 2019-08-23 | 18.1 | 0 | 0.1 | 2018-08-23 | 21 | 0 | 3 | 2017-08-23 | 18.6 | 0 | 0.6 | 2016-08-23 | 23.2 | 0 | 5.2 | 0 | 3.5
2025-08-23 | 23.3 | 0 | 5.3 | 2024-08-23 | 18.7 | 0 | 0.7 | 2023-08-23 | 18.4 | 0 | 0.4 | 2022-08-23 | 21.2 | 0 | 3.2 | 2021-08-23 | 22.7 | 0 | 4.7 | 2020-08-23 | 20.2 | 0 | 2.2 | 2019-08-23 | 18.1 | 0 | 0.1 | 2018-08-23 | 19.6 | 0 | 1.6 | 2017-08-23 | 17.3 | 0.7 | 0 | 2016-08-23 | 21.3 | 0 | 3.3 | 0.07 | 2.15
2025-08-23 | 22.7 | 0 | 4.7 | 2024-08-23 | 17.8 | 0.2 | 0 | 2023-08-23 | 20 | 0 | 2 | 2022-08-23 | 21.1 | 0 | 3.1 | 2021-08-23 | 22 | 0 | 4 | 2020-08-23 | 18.7 | 0 | 0.7 | 2019-08-23 | 17.4 | 0.6 | 0 | 2018-08-23 | 19.5 | 0 | 1.5 | 2017-08-23 | 15.7 | 2.3 | 0 | 2016-08-23 | 19.9 | 0 | 1.9 | 0.31 | 1.79
2025-08-23 | 22 | 0 | 4 | 2024-08-23 | 17.6 | 0.4 | 0 | 2023-08-23 | 18.7 | 0 | 0.7 | 2022-08-23 | 20.4 | 0 | 2.4 | 2021-08-23 | 23.3 | 0 | 5.3 | 2020-08-23 | 18.5 | 0 | 0.5 | 2019-08-23 | 16.3 | 1.7 | 0 | 2018-08-23 | 18.4 | 0 | 0.4 | 2017-08-23 | 13.1 | 4.9 | 0 | 2016-08-23 | 20 | 0 | 2 | 0.7 | 1.53
2025-08-23 | 21.1 | 0 | 3.1 | 2024-08-23 | 16.8 | 1.2 | 0 | 2023-08-23 | 16.7 | 1.3 | 0 | 2022-08-23 | 20.3 | 0 | 2.3 | 2021-08-23 | 23.1 | 0 | 5.1 | 2020-08-23 | 18.2 | 0 | 0.2 | 2019-08-23 | 14 | 4 | 0 | 2018-08-23 | 17.3 | 0.7 | 0 | 2017-08-23 | 13.1 | 4.9 | 0 | 2016-08-23 | 17.4 | 0.6 | 0 | 1.27 | 1.07
2025-08-24 | 21.2 | 0 | 3.2 | 2024-08-24 | 15.3 | 2.7 | 0 | 2023-08-24 | 15.3 | 2.7 | 0 | 2022-08-24 | 19.4 | 0 | 1.4 | 2021-08-24 | 22.8 | 0 | 4.8 | 2020-08-24 | 18.4 | 0 | 0.4 | 2019-08-24 | 15.1 | 2.9 | 0 | 2018-08-24 | 16.8 | 1.2 | 0 | 2017-08-24 | 12.6 | 5.4 | 0 | 2016-08-24 | 17.5 | 0.5 | 0 | 1.54 | 0.98
2025-08-24 | 20.6 | 0 | 2.6 | 2024-08-24 | 14.8 | 3.2 | 0 | 2023-08-24 | 15.4 | 2.6 | 0 | 2022-08-24 | 18.8 | 0 | 0.8 | 2021-08-24 | 21.4 | 0 | 3.4 | 2020-08-24 | 19.1 | 0 | 1.1 | 2019-08-24 | 15.7 | 2.3 | 0 | 2018-08-24 | 16 | 2 | 0 | 2017-08-24 | 12.1 | 5.9 | 0 | 2016-08-24 | 17.4 | 0.6 | 0 | 1.66 | 0.79
2025-08-24 | 20.9 | 0 | 2.9 | 2024-08-24 | 15.4 | 2.6 | 0 | 2023-08-24 | 13.7 | 4.3 | 0 | 2022-08-24 | 17.1 | 0.9 | 0 | 2021-08-24 | 20.8 | 0 | 2.8 | 2020-08-24 | 18.4 | 0 | 0.4 | 2019-08-24 | 14.8 | 3.2 | 0 | 2018-08-24 | 15.9 | 2.1 | 0 | 2017-08-24 | 12.7 | 5.3 | 0 | 2016-08-24 | 16.9 | 1.1 | 0 | 1.95 | 0.61
2025-08-24 | 20.8 | 0 | 2.8 | 2024-08-24 | 13.7 | 4.3 | 0 | 2023-08-24 | 13.7 | 4.3 | 0 | 2022-08-24 | 16.4 | 1.6 | 0 | 2021-08-24 | 20.9 | 0 | 2.9 | 2020-08-24 | 18.2 | 0 | 0.2 | 2019-08-24 | 13.1 | 4.9 | 0 | 2018-08-24 | 15.3 | 2.7 | 0 | 2017-08-24 | 13.7 | 4.3 | 0 | 2016-08-24 | 17.3 | 0.7 | 0 | 2.28 | 0.59
2025-08-24 | 20.4 | 0 | 2.4 | 2024-08-24 | 13.9 | 4.1 | 0 | 2023-08-24 | 13.4 | 4.6 | 0 | 2022-08-24 | 16.2 | 1.8 | 0 | 2021-08-24 | 21.3 | 0 | 3.3 | 2020-08-24 | 18 | 0 | 0 | 2019-08-24 | 13.9 | 4.1 | 0 | 2018-08-24 | 14.6 | 3.4 | 0 | 2017-08-24 | 13.3 | 4.7 | 0 | 2016-08-24 | 16.8 | 1.2 | 0 | 2.39 | 0.57
2025-08-24 | 19.3 | 0 | 1.3 | 2024-08-24 | 12.7 | 5.3 | 0 | 2023-08-24 | 13.4 | 4.6 | 0 | 2022-08-24 | 16.2 | 1.8 | 0 | 2021-08-24 | 20.9 | 0 | 2.9 | 2020-08-24 | 18 | 0 | 0 | 2019-08-24 | 15.2 | 2.8 | 0 | 2018-08-24 | 13.9 | 4.1 | 0 | 2017-08-24 | 12.6 | 5.4 | 0 | 2016-08-24 | 16.2 | 1.8 | 0 | 2.58 | 0.42
2025-08-24 | 19.4 | 0 | 1.4 | 2024-08-24 | 13.6 | 4.4 | 0 | 2023-08-24 | 13.8 | 4.2 | 0 | 2022-08-24 | 17.1 | 0.9 | 0 | 2021-08-24 | 20.6 | 0 | 2.6 | 2020-08-24 | 18.1 | 0 | 0.1 | 2019-08-24 | 14.9 | 3.1 | 0 | 2018-08-24 | 14.3 | 3.7 | 0 | 2017-08-24 | 13.1 | 4.9 | 0 | 2016-08-24 | 16.4 | 1.6 | 0 | 2.28 | 0.41
2025-08-24 | 19.3 | 0 | 1.3 | 2024-08-24 | 15.8 | 2.2 | 0 | 2023-08-24 | 16.3 | 1.7 | 0 | 2022-08-24 | 18.5 | 0 | 0.5 | 2021-08-24 | 21.8 | 0 | 3.8 | 2020-08-24 | 18.7 | 0 | 0.7 | 2019-08-24 | 16.2 | 1.8 | 0 | 2018-08-24 | 15.5 | 2.5 | 0 | 2017-08-24 | 14.9 | 3.1 | 0 | 2016-08-24 | 18.5 | 0 | 0.5 | 1.13 | 0.68
2025-08-24 | 20.1 | 0 | 2.1 | 2024-08-24 | 18.5 | 0 | 0.5 | 2023-08-24 | 18.9 | 0 | 0.9 | 2022-08-24 | 19.3 | 0 | 1.3 | 2021-08-24 | 23.4 | 0 | 5.4 | 2020-08-24 | 20.5 | 0 | 2.5 | 2019-08-24 | 17.6 | 0.4 | 0 | 2018-08-24 | 18.1 | 0 | 0.1 | 2017-08-24 | 16 | 2 | 0 | 2016-08-24 | 20.8 | 0 | 2.8 | 0.24 | 1.56
2025-08-24 | 22.3 | 0 | 4.3 | 2024-08-24 | 19.5 | 0 | 1.5 | 2023-08-24 | 20.9 | 0 | 2.9 | 2022-08-24 | 22.3 | 0 | 4.3 | 2021-08-24 | 25.2 | 0 | 7.2 | 2020-08-24 | 21.8 | 0 | 3.8 | 2019-08-24 | 18.2 | 0 | 0.2 | 2018-08-24 | 20.5 | 0 | 2.5 | 2017-08-24 | 17.2 | 0.8 | 0 | 2016-08-24 | 23.6 | 0 | 5.6 | 0.08 | 3.23
2025-08-24 | 23.4 | 0 | 5.4 | 2024-08-24 | 22 | 0 | 4 | 2023-08-24 | 22.9 | 0 | 4.9 | 2022-08-24 | 23.7 | 0 | 5.7 | 2021-08-24 | 26.7 | 0 | 8.7 | 2020-08-24 | 23.2 | 0 | 5.2 | 2019-08-24 | 19.1 | 0 | 1.1 | 2018-08-24 | 22.6 | 0 | 4.6 | 2017-08-24 | 17.8 | 0.2 | 0 | 2016-08-24 | 25.3 | 0 | 7.3 | 0.02 | 4.69
2025-08-24 | 25 | 0 | 7 | 2024-08-24 | 23.5 | 0 | 5.5 | 2023-08-24 | 23.3 | 0 | 5.3 | 2022-08-24 | 25.1 | 0 | 7.1 | 2021-08-24 | 29.2 | 0 | 11.2 | 2020-08-24 | 25.2 | 0 | 7.2 | 2019-08-24 | 19.9 | 0 | 1.9 | 2018-08-24 | 24.6 | 0 | 6.6 | 2017-08-24 | 18.1 | 0 | 0.1 | 2016-08-24 | 26.8 | 0 | 8.8 | 0 | 6.07
2025-08-24 | 24.8 | 0 | 6.8 | 2024-08-24 | 24.5 | 0 | 6.5 | 2023-08-24 | 22.6 | 0 | 4.6 | 2022-08-24 | 26.4 | 0 | 8.4 | 2021-08-24 | 30.5 | 0 | 12.5 | 2020-08-24 | 25.7 | 0 | 7.7 | 2019-08-24 | 21.6 | 0 | 3.6 | 2018-08-24 | 26.6 | 0 | 8.6 | 2017-08-24 | 19 | 0 | 1 | 2016-08-24 | 27.8 | 0 | 9.8 | 0 | 6.95
2025-08-24 | 27.8 | 0 | 9.8 | 2024-08-24 | 24.9 | 0 | 6.9 | 2023-08-24 | 20.6 | 0 | 2.6 | 2022-08-24 | 27.7 | 0 | 9.7 | 2021-08-24 | 31 | 0 | 13 | 2020-08-24 | 26.1 | 0 | 8.1 | 2019-08-24 | 23.1 | 0 | 5.1 | 2018-08-24 | 27.8 | 0 | 9.8 | 2017-08-24 | 19.7 | 0 | 1.7 | 2016-08-24 | 28.5 | 0 | 10.5 | 0 | 7.72
2025-08-24 | 27.6 | 0 | 9.6 | 2024-08-24 | 25.1 | 0 | 7.1 | 2023-08-24 | 20.8 | 0 | 2.8 | 2022-08-24 | 28.4 | 0 | 10.4 | 2021-08-24 | 31.3 | 0 | 13.3 | 2020-08-24 | 28.4 | 0 | 10.4 | 2019-08-24 | 23.8 | 0 | 5.8 | 2018-08-24 | 28 | 0 | 10 | 2017-08-24 | 19.8 | 0 | 1.8 | 2016-08-24 | 28.7 | 0 | 10.7 | 0 | 8.19
2025-08-24 | 27.5 | 0 | 9.5 | 2024-08-24 | 25.2 | 0 | 7.2 | 2023-08-24 | 19.9 | 0 | 1.9 | 2022-08-24 | 28.2 | 0 | 10.2 | 2021-08-24 | 30.9 | 0 | 12.9 | 2020-08-24 | 27.4 | 0 | 9.4 | 2019-08-24 | 24.5 | 0 | 6.5 | 2018-08-24 | 27.8 | 0 | 9.8 | 2017-08-24 | 20.3 | 0 | 2.3 | 2016-08-24 | 29.1 | 0 | 11.1 | 0 | 8.08
2025-08-24 | 26.5 | 0 | 8.5 | 2024-08-24 | 24.2 | 0 | 6.2 | 2023-08-24 | 18.2 | 0 | 0.2 | 2022-08-24 | 28 | 0 | 10 | 2021-08-24 | 30.6 | 0 | 12.6 | 2020-08-24 | 24.4 | 0 | 6.4 | 2019-08-24 | 24.2 | 0 | 6.2 | 2018-08-24 | 27.2 | 0 | 9.2 | 2017-08-24 | 20.1 | 0 | 2.1 | 2016-08-24 | 27.9 | 0 | 9.9 | 0 | 7.13
2025-08-24 | 27.3 | 0 | 9.3 | 2024-08-24 | 23.7 | 0 | 5.7 | 2023-08-24 | 17.2 | 0.8 | 0 | 2022-08-24 | 26.5 | 0 | 8.5 | 2021-08-24 | 29.5 | 0 | 11.5 | 2020-08-24 | 23.2 | 0 | 5.2 | 2019-08-24 | 23.8 | 0 | 5.8 | 2018-08-24 | 25.9 | 0 | 7.9 | 2017-08-24 | 19.7 | 0 | 1.7 | 2016-08-24 | 27.2 | 0 | 9.2 | 0.08 | 6.48
2025-08-24 | 24 | 0 | 6 | 2024-08-24 | 23.1 | 0 | 5.1 | 2023-08-24 | 16.8 | 1.2 | 0 | 2022-08-24 | 25.3 | 0 | 7.3 | 2021-08-24 | 28.1 | 0 | 10.1 | 2020-08-24 | 23 | 0 | 5 | 2019-08-24 | 22.7 | 0 | 4.7 | 2018-08-24 | 24.9 | 0 | 6.9 | 2017-08-24 | 18.6 | 0 | 0.6 | 2016-08-24 | 24.8 | 0 | 6.8 | 0.12 | 5.25
2025-08-24 | 23 | 0 | 5 | 2024-08-24 | 20.6 | 0 | 2.6 | 2023-08-24 | 16.4 | 1.6 | 0 | 2022-08-24 | 24.4 | 0 | 6.4 | 2021-08-24 | 27 | 0 | 9 | 2020-08-24 | 21.7 | 0 | 3.7 | 2019-08-24 | 18.7 | 0 | 0.7 | 2018-08-24 | 22.8 | 0 | 4.8 | 2017-08-24 | 16.4 | 1.6 | 0 | 2016-08-24 | 23.7 | 0 | 5.7 | 0.32 | 3.79
2025-08-24 | 21.6 | 0 | 3.6 | 2024-08-24 | 20.7 | 0 | 2.7 | 2023-08-24 | 16.4 | 1.6 | 0 | 2022-08-24 | 21.9 | 0 | 3.9 | 2021-08-24 | 22.8 | 0 | 4.8 | 2020-08-24 | 21.1 | 0 | 3.1 | 2019-08-24 | 17.3 | 0.7 | 0 | 2018-08-24 | 21.7 | 0 | 3.7 | 2017-08-24 | 15.2 | 2.8 | 0 | 2016-08-24 | 22.5 | 0 | 4.5 | 0.51 | 2.63
2025-08-24 | 19.9 | 0 | 1.9 | 2024-08-24 | 20.8 | 0 | 2.8 | 2023-08-24 | 16.3 | 1.7 | 0 | 2022-08-24 | 21.6 | 0 | 3.6 | 2021-08-24 | 21.6 | 0 | 3.6 | 2020-08-24 | 20.2 | 0 | 2.2 | 2019-08-24 | 15.5 | 2.5 | 0 | 2018-08-24 | 20.6 | 0 | 2.6 | 2017-08-24 | 14.1 | 3.9 | 0 | 2016-08-24 | 21.5 | 0 | 3.5 | 0.81 | 2.02
2025-08-24 | 18.7 | 0 | 0.7 | 2024-08-24 | 19.9 | 0 | 1.9 | 2023-08-24 | 15.9 | 2.1 | 0 | 2022-08-24 | 21 | 0 | 3 | 2021-08-24 | 22.6 | 0 | 4.6 | 2020-08-24 | 20.1 | 0 | 2.1 | 2019-08-24 | 14.8 | 3.2 | 0 | 2018-08-24 | 19.4 | 0 | 1.4 | 2017-08-24 | 13.3 | 4.7 | 0 | 2016-08-24 | 20.7 | 0 | 2.7 | 1 | 1.64
2025-08-24 | 18.2 | 0 | 0.2 | 2024-08-24 | 19.4 | 0 | 1.4 | 2023-08-24 | 15.8 | 2.2 | 0 | 2022-08-24 | 20.8 | 0 | 2.8 | 2021-08-24 | 21 | 0 | 3 | 2020-08-24 | 20.5 | 0 | 2.5 | 2019-08-24 | 14.5 | 3.5 | 0 | 2018-08-24 | 18.7 | 0 | 0.7 | 2017-08-24 | 12.2 | 5.8 | 0 | 2016-08-24 | 21.1 | 0 | 3.1 | 1.15 | 1.37
2025-08-25 | 17.7 | 0.3 | 0 | 2024-08-25 | 18.9 | 0 | 0.9 | 2023-08-25 | 15.9 | 2.1 | 0 | 2022-08-25 | 19.9 | 0 | 1.9 | 2021-08-25 | 20.4 | 0 | 2.4 | 2020-08-25 | 21.1 | 0 | 3.1 | 2019-08-25 | 13.3 | 4.7 | 0 | 2018-08-25 | 17.4 | 0.6 | 0 | 2017-08-25 | 12.4 | 5.6 | 0 | 2016-08-25 | 20.8 | 0 | 2.8 | 1.33 | 1.11
2025-08-25 | 16.5 | 1.5 | 0 | 2024-08-25 | 18.2 | 0 | 0.2 | 2023-08-25 | 15.9 | 2.1 | 0 | 2022-08-25 | 18.9 | 0 | 0.9 | 2021-08-25 | 19.9 | 0 | 1.9 | 2020-08-25 | 21.3 | 0 | 3.3 | 2019-08-25 | 12.1 | 5.9 | 0 | 2018-08-25 | 17.3 | 0.7 | 0 | 2017-08-25 | 10.6 | 7.4 | 0 | 2016-08-25 | 20.9 | 0 | 2.9 | 1.76 | 0.92
2025-08-25 | 15.5 | 2.5 | 0 | 2024-08-25 | 17.8 | 0.2 | 0 | 2023-08-25 | 16 | 2 | 0 | 2022-08-25 | 18.5 | 0 | 0.5 | 2021-08-25 | 19.5 | 0 | 1.5 | 2020-08-25 | 21.4 | 0 | 3.4 | 2019-08-25 | 11.7 | 6.3 | 0 | 2018-08-25 | 17.4 | 0.6 | 0 | 2017-08-25 | 10.5 | 7.5 | 0 | 2016-08-25 | 20.8 | 0 | 2.8 | 1.91 | 0.82
2025-08-25 | 14.2 | 3.8 | 0 | 2024-08-25 | 17.8 | 0.2 | 0 | 2023-08-25 | 15.9 | 2.1 | 0 | 2022-08-25 | 18 | 0 | 0 | 2021-08-25 | 19.1 | 0 | 1.1 | 2020-08-25 | 20.4 | 0 | 2.4 | 2019-08-25 | 11.3 | 6.7 | 0 | 2018-08-25 | 15.9 | 2.1 | 0 | 2017-08-25 | 10.2 | 7.8 | 0 | 2016-08-25 | 20.4 | 0 | 2.4 | 2.27 | 0.59
2025-08-25 | 13.8 | 4.2 | 0 | 2024-08-25 | 17.4 | 0.6 | 0 | 2023-08-25 | 15.9 | 2.1 | 0 | 2022-08-25 | 17.5 | 0.5 | 0 | 2021-08-25 | 18.6 | 0 | 0.6 | 2020-08-25 | 19.8 | 0 | 1.8 | 2019-08-25 | 11 | 7 | 0 | 2018-08-25 | 15.6 | 2.4 | 0 | 2017-08-25 | 9.9 | 8.1 | 0 | 2016-08-25 | 20.3 | 0 | 2.3 | 2.49 | 0.47
2025-08-25 | 13.1 | 4.9 | 0 | 2024-08-25 | 16.9 | 1.1 | 0 | 2023-08-25 | 15.9 | 2.1 | 0 | 2022-08-25 | 17 | 1 | 0 | 2021-08-25 | 18.3 | 0 | 0.3 | 2020-08-25 | 20.3 | 0 | 2.3 | 2019-08-25 | 10.7 | 7.3 | 0 | 2018-08-25 | 15.8 | 2.2 | 0 | 2017-08-25 | 9.8 | 8.2 | 0 | 2016-08-25 | 20.7 | 0 | 2.7 | 2.68 | 0.53
2025-08-25 | 14.8 | 3.2 | 0 | 2024-08-25 | 17.5 | 0.5 | 0 | 2023-08-25 | 16 | 2 | 0 | 2022-08-25 | 16.5 | 1.5 | 0 | 2021-08-25 | 19 | 0 | 1 | 2020-08-25 | 20.4 | 0 | 2.4 | 2019-08-25 | 12.2 | 5.8 | 0 | 2018-08-25 | 16.3 | 1.7 | 0 | 2017-08-25 | 9 | 9 | 0 | 2016-08-25 | 21 | 0 | 3 | 2.37 | 0.64
2025-08-25 | 16.1 | 1.9 | 0 | 2024-08-25 | 19.1 | 0 | 1.1 | 2023-08-25 | 16.4 | 1.6 | 0 | 2022-08-25 | 17.6 | 0.4 | 0 | 2021-08-25 | 20.5 | 0 | 2.5 | 2020-08-25 | 20.7 | 0 | 2.7 | 2019-08-25 | 14.6 | 3.4 | 0 | 2018-08-25 | 17.6 | 0.4 | 0 | 2017-08-25 | 12.4 | 5.6 | 0 | 2016-08-25 | 21.4 | 0 | 3.4 | 1.33 | 0.97
2025-08-25 | 18.6 | 0 | 0.6 | 2024-08-25 | 20.9 | 0 | 2.9 | 2023-08-25 | 17 | 1 | 0 | 2022-08-25 | 19 | 0 | 1 | 2021-08-25 | 23.6 | 0 | 5.6 | 2020-08-25 | 21.4 | 0 | 3.4 | 2019-08-25 | 17 | 1 | 0 | 2018-08-25 | 20.7 | 0 | 2.7 | 2017-08-25 | 14.7 | 3.3 | 0 | 2016-08-25 | 22.4 | 0 | 4.4 | 0.53 | 2.06
2025-08-25 | 20.8 | 0 | 2.8 | 2024-08-25 | 23 | 0 | 5 | 2023-08-25 | 18.2 | 0 | 0.2 | 2022-08-25 | 20.5 | 0 | 2.5 | 2021-08-25 | 25.5 | 0 | 7.5 | 2020-08-25 | 22.6 | 0 | 4.6 | 2019-08-25 | 19.3 | 0 | 1.3 | 2018-08-25 | 22.4 | 0 | 4.4 | 2017-08-25 | 16.6 | 1.4 | 0 | 2016-08-25 | 22.7 | 0 | 4.7 | 0.14 | 3.3
2025-08-25 | 22.9 | 0 | 4.9 | 2024-08-25 | 23.9 | 0 | 5.9 | 2023-08-25 | 18.8 | 0 | 0.8 | 2022-08-25 | 21.5 | 0 | 3.5 | 2021-08-25 | 27.4 | 0 | 9.4 | 2020-08-25 | 22.3 | 0 | 4.3 | 2019-08-25 | 20.9 | 0 | 2.9 | 2018-08-25 | 24 | 0 | 6 | 2017-08-25 | 17.5 | 0.5 | 0 | 2016-08-25 | 23.7 | 0 | 5.7 | 0.05 | 4.34
2025-08-25 | 22.8 | 0 | 4.8 | 2024-08-25 | 25.4 | 0 | 7.4 | 2023-08-25 | 19.6 | 0 | 1.6 | 2022-08-25 | 22.2 | 0 | 4.2 | 2021-08-25 | 28.8 | 0 | 10.8 | 2020-08-25 | 22.7 | 0 | 4.7 | 2019-08-25 | 22.8 | 0 | 4.8 | 2018-08-25 | 24.9 | 0 | 6.9 | 2017-08-25 | 19.1 | 0 | 1.1 | 2016-08-25 | 24.7 | 0 | 6.7 | 0 | 5.3
2025-08-25 | 24.5 | 0 | 6.5 | 2024-08-25 | 26.2 | 0 | 8.2 | 2023-08-25 | 20.1 | 0 | 2.1 | 2022-08-25 | 22.3 | 0 | 4.3 | 2021-08-25 | 29.6 | 0 | 11.6 | 2020-08-25 | 22.8 | 0 | 4.8 | 2019-08-25 | 23.4 | 0 | 5.4 | 2018-08-25 | 25.2 | 0 | 7.2 | 2017-08-25 | 19.9 | 0 | 1.9 | 2016-08-25 | 27.8 | 0 | 9.8 | 0 | 6.18
2025-08-25 | 24.4 | 0 | 6.4 | 2024-08-25 | 26.2 | 0 | 8.2 | 2023-08-25 | 21.4 | 0 | 3.4 | 2022-08-25 | 23.6 | 0 | 5.6 | 2021-08-25 | 30.9 | 0 | 12.9 | 2020-08-25 | 22.8 | 0 | 4.8 | 2019-08-25 | 24.3 | 0 | 6.3 | 2018-08-25 | 26.5 | 0 | 8.5 | 2017-08-25 | 19.7 | 0 | 1.7 | 2016-08-25 | 28.6 | 0 | 10.6 | 0 | 6.84
2025-08-25 | 23.6 | 0 | 5.6 | 2024-08-25 | 26.1 | 0 | 8.1 | 2023-08-25 | 22.8 | 0 | 4.8 | 2022-08-25 | 22.8 | 0 | 4.8 | 2021-08-25 | 32.6 | 0 | 14.6 | 2020-08-25 | 21.8 | 0 | 3.8 | 2019-08-25 | 24.8 | 0 | 6.8 | 2018-08-25 | 26.9 | 0 | 8.9 | 2017-08-25 | 19.9 | 0 | 1.9 | 2016-08-25 | 29.6 | 0 | 11.6 | 0 | 7.09
2025-08-25 | 23.6 | 0 | 5.6 | 2024-08-25 | 27.1 | 0 | 9.1 | 2023-08-25 | 23.9 | 0 | 5.9 | 2022-08-25 | 22.6 | 0 | 4.6 | 2021-08-25 | 32.2 | 0 | 14.2 | 2020-08-25 | 21.5 | 0 | 3.5 | 2019-08-25 | 25.2 | 0 | 7.2 | 2018-08-25 | 26.9 | 0 | 8.9 | 2017-08-25 | 20.1 | 0 | 2.1 | 2016-08-25 | 28.5 | 0 | 10.5 | 0 | 7.16
2025-08-25 | 23.3 | 0 | 5.3 | 2024-08-25 | 27.2 | 0 | 9.2 | 2023-08-25 | 22.1 | 0 | 4.1 | 2022-08-25 | 21.7 | 0 | 3.7 | 2021-08-25 | 31.4 | 0 | 13.4 | 2020-08-25 | 20.8 | 0 | 2.8 | 2019-08-25 | 25.4 | 0 | 7.4 | 2018-08-25 | 25.7 | 0 | 7.7 | 2017-08-25 | 19.8 | 0 | 1.8 | 2016-08-25 | 29.4 | 0 | 11.4 | 0 | 6.68
2025-08-25 | 21.8 | 0 | 3.8 | 2024-08-25 | 25.5 | 0 | 7.5 | 2023-08-25 | 21.6 | 0 | 3.6 | 2022-08-25 | 21.2 | 0 | 3.2 | 2021-08-25 | 31.6 | 0 | 13.6 | 2020-08-25 | 19.7 | 0 | 1.7 | 2019-08-25 | 24.3 | 0 | 6.3 | 2018-08-25 | 24.9 | 0 | 6.9 | 2017-08-25 | 19.2 | 0 | 1.2 | 2016-08-25 | 27.4 | 0 | 9.4 | 0 | 5.72
2025-08-25 | 18.8 | 0 | 0.8 | 2024-08-25 | 24.4 | 0 | 6.4 | 2023-08-25 | 21.1 | 0 | 3.1 | 2022-08-25 | 20.2 | 0 | 2.2 | 2021-08-25 | 29.9 | 0 | 11.9 | 2020-08-25 | 18.5 | 0 | 0.5 | 2019-08-25 | 23.1 | 0 | 5.1 | 2018-08-25 | 24 | 0 | 6 | 2017-08-25 | 17.3 | 0.7 | 0 | 2016-08-25 | 27.2 | 0 | 9.2 | 0.07 | 4.52
2025-08-25 | 18.7 | 0 | 0.7 | 2024-08-25 | 24 | 0 | 6 | 2023-08-25 | 20.2 | 0 | 2.2 | 2022-08-25 | 19.5 | 0 | 1.5 | 2021-08-25 | 28.8 | 0 | 10.8 | 2020-08-25 | 17.5 | 0.5 | 0 | 2019-08-25 | 20.5 | 0 | 2.5 | 2018-08-25 | 22.7 | 0 | 4.7 | 2017-08-25 | 14.8 | 3.2 | 0 | 2016-08-25 | 25.8 | 0 | 7.8 | 0.37 | 3.62
2025-08-25 | 18 | 0 | 0 | 2024-08-25 | 19.3 | 0 | 1.3 | 2023-08-25 | 19.6 | 0 | 1.6 | 2022-08-25 | 19.5 | 0 | 1.5 | 2021-08-25 | 26.7 | 0 | 8.7 | 2020-08-25 | 16.7 | 1.3 | 0 | 2019-08-25 | 19.1 | 0 | 1.1 | 2018-08-25 | 22.5 | 0 | 4.5 | 2017-08-25 | 13.1 | 4.9 | 0 | 2016-08-25 | 24.6 | 0 | 6.6 | 0.62 | 2.53
2025-08-25 | 16 | 2 | 0 | 2024-08-25 | 19.8 | 0 | 1.8 | 2023-08-25 | 18.8 | 0 | 0.8 | 2022-08-25 | 19.2 | 0 | 1.2 | 2021-08-25 | 25.7 | 0 | 7.7 | 2020-08-25 | 15.6 | 2.4 | 0 | 2019-08-25 | 17.5 | 0.5 | 0 | 2018-08-25 | 22 | 0 | 4 | 2017-08-25 | 12.2 | 5.8 | 0 | 2016-08-25 | 23.7 | 0 | 5.7 | 1.07 | 2.12
2025-08-25 | 14.9 | 3.1 | 0 | 2024-08-25 | 19.1 | 0 | 1.1 | 2023-08-25 | 18.9 | 0 | 0.9 | 2022-08-25 | 17.9 | 0.1 | 0 | 2021-08-25 | 24.6 | 0 | 6.6 | 2020-08-25 | 15 | 3 | 0 | 2019-08-25 | 15.8 | 2.2 | 0 | 2018-08-25 | 20.8 | 0 | 2.8 | 2017-08-25 | 12.2 | 5.8 | 0 | 2016-08-25 | 22.9 | 0 | 4.9 | 1.42 | 1.63
2025-08-25 | 15.4 | 2.6 | 0 | 2024-08-25 | 18.9 | 0 | 0.9 | 2023-08-25 | 18.9 | 0 | 0.9 | 2022-08-25 | 17.8 | 0.2 | 0 | 2021-08-25 | 23.7 | 0 | 5.7 | 2020-08-25 | 14.2 | 3.8 | 0 | 2019-08-25 | 16.7 | 1.3 | 0 | 2018-08-25 | 20.3 | 0 | 2.3 | 2017-08-25 | 10 | 8 | 0 | 2016-08-25 | 22.4 | 0 | 4.4 | 1.59 | 1.42
2025-08-26 | 14.8 | 3.2 | 0 | 2024-08-26 | 18.3 | 0 | 0.3 | 2023-08-26 | 18.5 | 0 | 0.5 | 2022-08-26 | 17.3 | 0.7 | 0 | 2021-08-26 | 22.7 | 0 | 4.7 | 2020-08-26 | 12.6 | 5.4 | 0 | 2019-08-26 | 16.8 | 1.2 | 0 | 2018-08-26 | 20.1 | 0 | 2.1 | 2017-08-26 | 9.6 | 8.4 | 0 | 2016-08-26 | 22.1 | 0 | 4.1 | 1.89 | 1.17
2025-08-26 | 14.6 | 3.4 | 0 | 2024-08-26 | 18.4 | 0 | 0.4 | 2023-08-26 | 17.7 | 0.3 | 0 | 2022-08-26 | 17.4 | 0.6 | 0 | 2021-08-26 | 22.5 | 0 | 4.5 | 2020-08-26 | 11.9 | 6.1 | 0 | 2019-08-26 | 15.1 | 2.9 | 0 | 2018-08-26 | 20.2 | 0 | 2.2 | 2017-08-26 | 9.8 | 8.2 | 0 | 2016-08-26 | 21.6 | 0 | 3.6 | 2.15 | 1.07
2025-08-26 | 14.1 | 3.9 | 0 | 2024-08-26 | 17.2 | 0.8 | 0 | 2023-08-26 | 17.9 | 0.1 | 0 | 2022-08-26 | 16.4 | 1.6 | 0 | 2021-08-26 | 22.4 | 0 | 4.4 | 2020-08-26 | 9.9 | 8.1 | 0 | 2019-08-26 | 13.7 | 4.3 | 0 | 2018-08-26 | 19.9 | 0 | 1.9 | 2017-08-26 | 8.8 | 9.2 | 0 | 2016-08-26 | 21.3 | 0 | 3.3 | 2.8 | 0.96
2025-08-26 | 14.3 | 3.7 | 0 | 2024-08-26 | 17.3 | 0.7 | 0 | 2023-08-26 | 18 | 0 | 0 | 2022-08-26 | 16.3 | 1.7 | 0 | 2021-08-26 | 21.8 | 0 | 3.8 | 2020-08-26 | 10.6 | 7.4 | 0 | 2019-08-26 | 13.2 | 4.8 | 0 | 2018-08-26 | 19.3 | 0 | 1.3 | 2017-08-26 | 8.8 | 9.2 | 0 | 2016-08-26 | 20.7 | 0 | 2.7 | 2.75 | 0.78
2025-08-26 | 13.4 | 4.6 | 0 | 2024-08-26 | 16.8 | 1.2 | 0 | 2023-08-26 | 18.4 | 0 | 0.4 | 2022-08-26 | 16 | 2 | 0 | 2021-08-26 | 21.3 | 0 | 3.3 | 2020-08-26 | 9.8 | 8.2 | 0 | 2019-08-26 | 12.9 | 5.1 | 0 | 2018-08-26 | 18.9 | 0 | 0.9 | 2017-08-26 | 8.7 | 9.3 | 0 | 2016-08-26 | 20.2 | 0 | 2.2 | 3.04 | 0.68
2025-08-26 | 13.6 | 4.4 | 0 | 2024-08-26 | 16.6 | 1.4 | 0 | 2023-08-26 | 17.7 | 0.3 | 0 | 2022-08-26 | 16.1 | 1.9 | 0 | 2021-08-26 | 21.3 | 0 | 3.3 | 2020-08-26 | 9 | 9 | 0 | 2019-08-26 | 11.4 | 6.6 | 0 | 2018-08-26 | 18.5 | 0 | 0.5 | 2017-08-26 | 8.2 | 9.8 | 0 | 2016-08-26 | 19.7 | 0 | 1.7 | 3.34 | 0.55
2025-08-26 | 13.6 | 4.4 | 0 | 2024-08-26 | 16.2 | 1.8 | 0 | 2023-08-26 | 18 | 0 | 0 | 2022-08-26 | 15.5 | 2.5 | 0 | 2021-08-26 | 21.6 | 0 | 3.6 | 2020-08-26 | 9.5 | 8.5 | 0 | 2019-08-26 | 12.6 | 5.4 | 0 | 2018-08-26 | 18.5 | 0 | 0.5 | 2017-08-26 | 7.9 | 10.1 | 0 | 2016-08-26 | 19.8 | 0 | 1.8 | 3.27 | 0.59
2025-08-26 | 14.1 | 3.9 | 0 | 2024-08-26 | 18.2 | 0 | 0.2 | 2023-08-26 | 18.6 | 0 | 0.6 | 2022-08-26 | 15.2 | 2.8 | 0 | 2021-08-26 | 23.4 | 0 | 5.4 | 2020-08-26 | 11.2 | 6.8 | 0 | 2019-08-26 | 15.2 | 2.8 | 0 | 2018-08-26 | 19.5 | 0 | 1.5 | 2017-08-26 | 11.6 | 6.4 | 0 | 2016-08-26 | 20.6 | 0 | 2.6 | 2.27 | 1.03
2025-08-26 | 15.2 | 2.8 | 0 | 2024-08-26 | 21.4 | 0 | 3.4 | 2023-08-26 | 19 | 0 | 1 | 2022-08-26 | 15.6 | 2.4 | 0 | 2021-08-26 | 25.9 | 0 | 7.9 | 2020-08-26 | 11.7 | 6.3 | 0 | 2019-08-26 | 18.3 | 0 | 0.3 | 2018-08-26 | 20.1 | 0 | 2.1 | 2017-08-26 | 14.5 | 3.5 | 0 | 2016-08-26 | 21.8 | 0 | 3.8 | 1.5 | 1.85
2025-08-26 | 16.1 | 1.9 | 0 | 2024-08-26 | 23 | 0 | 5 | 2023-08-26 | 19.5 | 0 | 1.5 | 2022-08-26 | 15.7 | 2.3 | 0 | 2021-08-26 | 27.3 | 0 | 9.3 | 2020-08-26 | 12.8 | 5.2 | 0 | 2019-08-26 | 20.1 | 0 | 2.1 | 2018-08-26 | 22 | 0 | 4 | 2017-08-26 | 17.5 | 0.5 | 0 | 2016-08-26 | 23.4 | 0 | 5.4 | 0.99 | 2.73
2025-08-26 | 16.6 | 1.4 | 0 | 2024-08-26 | 24.9 | 0 | 6.9 | 2023-08-26 | 19.4 | 0 | 1.4 | 2022-08-26 | 16.4 | 1.6 | 0 | 2021-08-26 | 28.1 | 0 | 10.1 | 2020-08-26 | 14.7 | 3.3 | 0 | 2019-08-26 | 22.7 | 0 | 4.7 | 2018-08-26 | 20.8 | 0 | 2.8 | 2017-08-26 | 18.7 | 0 | 0.7 | 2016-08-26 | 24.8 | 0 | 6.8 | 0.63 | 3.34
2025-08-26 | 18.1 | 0 | 0.1 | 2024-08-26 | 25.9 | 0 | 7.9 | 2023-08-26 | 19 | 0 | 1 | 2022-08-26 | 16.6 | 1.4 | 0 | 2021-08-26 | 30.7 | 0 | 12.7 | 2020-08-26 | 15.6 | 2.4 | 0 | 2019-08-26 | 23.5 | 0 | 5.5 | 2018-08-26 | 21.8 | 0 | 3.8 | 2017-08-26 | 19.3 | 0 | 1.3 | 2016-08-26 | 26.2 | 0 | 8.2 | 0.38 | 4.05
2025-08-26 | 18.4 | 0 | 0.4 | 2024-08-26 | 27.3 | 0 | 9.3 | 2023-08-26 | 19.8 | 0 | 1.8 | 2022-08-26 | 17 | 1 | 0 | 2021-08-26 | 31.4 | 0 | 13.4 | 2020-08-26 | 16 | 2 | 0 | 2019-08-26 | 24.2 | 0 | 6.2 | 2018-08-26 | 25.4 | 0 | 7.4 | 2017-08-26 | 19.6 | 0 | 1.6 | 2016-08-26 | 26.5 | 0 | 8.5 | 0.3 | 4.86
2025-08-26 | 19.2 | 0 | 1.2 | 2024-08-26 | 28 | 0 | 10 | 2023-08-26 | 18.5 | 0 | 0.5 | 2022-08-26 | 18.1 | 0 | 0.1 | 2021-08-26 | 31.9 | 0 | 13.9 | 2020-08-26 | 17 | 1 | 0 | 2019-08-26 | 25.9 | 0 | 7.9 | 2018-08-26 | 25.5 | 0 | 7.5 | 2017-08-26 | 21 | 0 | 3 | 2016-08-26 | 27.2 | 0 | 9.2 | 0.1 | 5.33
2025-08-26 | 18.7 | 0 | 0.7 | 2024-08-26 | 28 | 0 | 10 | 2023-08-26 | 18.5 | 0 | 0.5 | 2022-08-26 | 20 | 0 | 2 | 2021-08-26 | 31.9 | 0 | 13.9 | 2020-08-26 | 17.7 | 0.3 | 0 | 2019-08-26 | 26.6 | 0 | 8.6 | 2018-08-26 | 26.2 | 0 | 8.2 | 2017-08-26 | 20.6 | 0 | 2.6 | 2016-08-26 | 28.1 | 0 | 10.1 | 0.03 | 5.66
2025-08-26 | 19.4 | 0 | 1.4 | 2024-08-26 | 28.4 | 0 | 10.4 | 2023-08-26 | 18.5 | 0 | 0.5 | 2022-08-26 | 20 | 0 | 2 | 2021-08-26 | 32.2 | 0 | 14.2 | 2020-08-26 | 18.3 | 0 | 0.3 | 2019-08-26 | 26.1 | 0 | 8.1 | 2018-08-26 | 25.6 | 0 | 7.6 | 2017-08-26 | 21.1 | 0 | 3.1 | 2016-08-26 | 28.1 | 0 | 10.1 | 0 | 5.77
2025-08-26 | 19.3 | 0 | 1.3 | 2024-08-26 | 28.4 | 0 | 10.4 | 2023-08-26 | 18.4 | 0 | 0.4 | 2022-08-26 | 19.7 | 0 | 1.7 | 2021-08-26 | 31.8 | 0 | 13.8 | 2020-08-26 | 18.2 | 0 | 0.2 | 2019-08-26 | 26.6 | 0 | 8.6 | 2018-08-26 | 26.2 | 0 | 8.2 | 2017-08-26 | 21.2 | 0 | 3.2 | 2016-08-26 | 28.3 | 0 | 10.3 | 0 | 5.81
2025-08-26 | 19.7 | 0 | 1.7 | 2024-08-26 | 28 | 0 | 10 | 2023-08-26 | 16.8 | 1.2 | 0 | 2022-08-26 | 19.1 | 0 | 1.1 | 2021-08-26 | 31.3 | 0 | 13.3 | 2020-08-26 | 17.6 | 0.4 | 0 | 2019-08-26 | 25.9 | 0 | 7.9 | 2018-08-26 | 25.3 | 0 | 7.3 | 2017-08-26 | 20.4 | 0 | 2.4 | 2016-08-26 | 27.7 | 0 | 9.7 | 0.16 | 5.34
2025-08-26 | 18.7 | 0 | 0.7 | 2024-08-26 | 25.7 | 0 | 7.7 | 2023-08-26 | 16.5 | 1.5 | 0 | 2022-08-26 | 18.9 | 0 | 0.9 | 2021-08-26 | 29.6 | 0 | 11.6 | 2020-08-26 | 16.5 | 1.5 | 0 | 2019-08-26 | 23.2 | 0 | 5.2 | 2018-08-26 | 25.3 | 0 | 7.3 | 2017-08-26 | 19.1 | 0 | 1.1 | 2016-08-26 | 26.3 | 0 | 8.3 | 0.3 | 4.28
2025-08-26 | 17.2 | 0.8 | 0 | 2024-08-26 | 23.2 | 0 | 5.2 | 2023-08-26 | 16.2 | 1.8 | 0 | 2022-08-26 | 18.2 | 0 | 0.2 | 2021-08-26 | 27.9 | 0 | 9.9 | 2020-08-26 | 14.2 | 3.8 | 0 | 2019-08-26 | 19.6 | 0 | 1.6 | 2018-08-26 | 23.2 | 0 | 5.2 | 2017-08-26 | 17.6 | 0.4 | 0 | 2016-08-26 | 25.1 | 0 | 7.1 | 0.68 | 2.92
2025-08-26 | 15 | 3 | 0 | 2024-08-26 | 20.6 | 0 | 2.6 | 2023-08-26 | 16.1 | 1.9 | 0 | 2022-08-26 | 17.3 | 0.7 | 0 | 2021-08-26 | 26.6 | 0 | 8.6 | 2020-08-26 | 14.5 | 3.5 | 0 | 2019-08-26 | 17.8 | 0.2 | 0 | 2018-08-26 | 20.2 | 0 | 2.2 | 2017-08-26 | 14.4 | 3.6 | 0 | 2016-08-26 | 23.8 | 0 | 5.8 | 1.29 | 1.92
2025-08-26 | 15.9 | 2.1 | 0 | 2024-08-26 | 21.8 | 0 | 3.8 | 2023-08-26 | 16 | 2 | 0 | 2022-08-26 | 16.5 | 1.5 | 0 | 2021-08-26 | 25.3 | 0 | 7.3 | 2020-08-26 | 12.3 | 5.7 | 0 | 2019-08-26 | 17.9 | 0.1 | 0 | 2018-08-26 | 20.5 | 0 | 2.5 | 2017-08-26 | 14.8 | 3.2 | 0 | 2016-08-26 | 20.6 | 0 | 2.6 | 1.46 | 1.62
2025-08-26 | 14.6 | 3.4 | 0 | 2024-08-26 | 20.6 | 0 | 2.6 | 2023-08-26 | 14.8 | 3.2 | 0 | 2022-08-26 | 17 | 1 | 0 | 2021-08-26 | 25.3 | 0 | 7.3 | 2020-08-26 | 12.2 | 5.8 | 0 | 2019-08-26 | 17.7 | 0.3 | 0 | 2018-08-26 | 20.2 | 0 | 2.2 | 2017-08-26 | 15.1 | 2.9 | 0 | 2016-08-26 | 21.1 | 0 | 3.1 | 1.66 | 1.52
2025-08-26 | 14.7 | 3.3 | 0 | 2024-08-26 | 19.4 | 0 | 1.4 | 2023-08-26 | 15.3 | 2.7 | 0 | 2022-08-26 | 17.1 | 0.9 | 0 | 2021-08-26 | 23.8 | 0 | 5.8 | 2020-08-26 | 11.8 | 6.2 | 0 | 2019-08-26 | 16.1 | 1.9 | 0 | 2018-08-26 | 19.5 | 0 | 1.5 | 2017-08-26 | 15.7 | 2.3 | 0 | 2016-08-26 | 21.5 | 0 | 3.5 | 1.73 | 1.22
2025-08-27 | 12.3 | 5.7 | 0 | 2024-08-27 | 19.4 | 0 | 1.4 | 2023-08-27 | 15.1 | 2.9 | 0 | 2022-08-27 | 16.4 | 1.6 | 0 | 2021-08-27 | 23.1 | 0 | 5.1 | 2020-08-27 | 11.4 | 6.6 | 0 | 2019-08-27 | 15.4 | 2.6 | 0 | 2018-08-27 | 19.3 | 0 | 1.3 | 2017-08-27 | 13.7 | 4.3 | 0 | 2016-08-27 | 21.3 | 0 | 3.3 | 2.37 | 1.11
2025-08-27 | 11.2 | 6.8 | 0 | 2024-08-27 | 18 | 0 | 0 | 2023-08-27 | 14 | 4 | 0 | 2022-08-27 | 15.5 | 2.5 | 0 | 2021-08-27 | 22 | 0 | 4 | 2020-08-27 | 10.1 | 7.9 | 0 | 2019-08-27 | 14.4 | 3.6 | 0 | 2018-08-27 | 17.7 | 0.3 | 0 | 2017-08-27 | 9.7 | 8.3 | 0 | 2016-08-27 | 20.1 | 0 | 2.1 | 3.34 | 0.61
2025-08-27 | 9.2 | 8.8 | 0 | 2024-08-27 | 18 | 0 | 0 | 2023-08-27 | 13 | 5 | 0 | 2022-08-27 | 15.3 | 2.7 | 0 | 2021-08-27 | 20.8 | 0 | 2.8 | 2020-08-27 | 10.9 | 7.1 | 0 | 2019-08-27 | 14.4 | 3.6 | 0 | 2018-08-27 | 17.7 | 0.3 | 0 | 2017-08-27 | 10.3 | 7.7 | 0 | 2016-08-27 | 19.2 | 0 | 1.2 | 3.52 | 0.4
2025-08-27 | 8.5 | 9.5 | 0 | 2024-08-27 | 17.1 | 0.9 | 0 | 2023-08-27 | 12.7 | 5.3 | 0 | 2022-08-27 | 15.3 | 2.7 | 0 | 2021-08-27 | 20 | 0 | 2 | 2020-08-27 | 9.2 | 8.8 | 0 | 2019-08-27 | 13 | 5 | 0 | 2018-08-27 | 17.6 | 0.4 | 0 | 2017-08-27 | 9.9 | 8.1 | 0 | 2016-08-27 | 18.7 | 0 | 0.7 | 4.07 | 0.27
2025-08-27 | 8.4 | 9.6 | 0 | 2024-08-27 | 17.8 | 0.2 | 0 | 2023-08-27 | 11.4 | 6.6 | 0 | 2022-08-27 | 15 | 3 | 0 | 2021-08-27 | 19.3 | 0 | 1.3 | 2020-08-27 | 10.3 | 7.7 | 0 | 2019-08-27 | 12.1 | 5.9 | 0 | 2018-08-27 | 17.4 | 0.6 | 0 | 2017-08-27 | 10.3 | 7.7 | 0 | 2016-08-27 | 18.1 | 0 | 0.1 | 4.13 | 0.14
2025-08-27 | 9.2 | 8.8 | 0 | 2024-08-27 | 16.9 | 1.1 | 0 | 2023-08-27 | 12.6 | 5.4 | 0 | 2022-08-27 | 14.7 | 3.3 | 0 | 2021-08-27 | 17.6 | 0.4 | 0 | 2020-08-27 | 10.5 | 7.5 | 0 | 2019-08-27 | 11.9 | 6.1 | 0 | 2018-08-27 | 17.2 | 0.8 | 0 | 2017-08-27 | 10.2 | 7.8 | 0 | 2016-08-27 | 17.2 | 0.8 | 0 | 4.2 | 0
2025-08-27 | 9.7 | 8.3 | 0 | 2024-08-27 | 17.2 | 0.8 | 0 | 2023-08-27 | 13.5 | 4.5 | 0 | 2022-08-27 | 14.5 | 3.5 | 0 | 2021-08-27 | 17.2 | 0.8 | 0 | 2020-08-27 | 11.1 | 6.9 | 0 | 2019-08-27 | 12.5 | 5.5 | 0 | 2018-08-27 | 16.5 | 1.5 | 0 | 2017-08-27 | 10.3 | 7.7 | 0 | 2016-08-27 | 18 | 0 | 0 | 3.95 | 0
2025-08-27 | 11 | 7 | 0 | 2024-08-27 | 18.8 | 0 | 0.8 | 2023-08-27 | 14.7 | 3.3 | 0 | 2022-08-27 | 14.7 | 3.3 | 0 | 2021-08-27 | 17.4 | 0.6 | 0 | 2020-08-27 | 10.9 | 7.1 | 0 | 2019-08-27 | 15.7 | 2.3 | 0 | 2018-08-27 | 18.5 | 0 | 0.5 | 2017-08-27 | 12.5 | 5.5 | 0 | 2016-08-27 | 19.2 | 0 | 1.2 | 2.91 | 0.25
2025-08-27 | 12.9 | 5.1 | 0 | 2024-08-27 | 21.6 | 0 | 3.6 | 2023-08-27 | 16.7 | 1.3 | 0 | 2022-08-27 | 15.4 | 2.6 | 0 | 2021-08-27 | 18.2 | 0 | 0.2 | 2020-08-27 | 10.9 | 7.1 | 0 | 2019-08-27 | 19.1 | 0 | 1.1 | 2018-08-27 | 20.8 | 0 | 2.8 | 2017-08-27 | 14.4 | 3.6 | 0 | 2016-08-27 | 20.5 | 0 | 2.5 | 1.97 | 1.02
2025-08-27 | 15.2 | 2.8 | 0 | 2024-08-27 | 24.2 | 0 | 6.2 | 2023-08-27 | 18.4 | 0 | 0.4 | 2022-08-27 | 16.1 | 1.9 | 0 | 2021-08-27 | 18.9 | 0 | 0.9 | 2020-08-27 | 10.7 | 7.3 | 0 | 2019-08-27 | 20.8 | 0 | 2.8 | 2018-08-27 | 22 | 0 | 4 | 2017-08-27 | 17.6 | 0.4 | 0 | 2016-08-27 | 21.7 | 0 | 3.7 | 1.24 | 1.8
2025-08-27 | 17.5 | 0.5 | 0 | 2024-08-27 | 25.9 | 0 | 7.9 | 2023-08-27 | 19.6 | 0 | 1.6 | 2022-08-27 | 17.5 | 0.5 | 0 | 2021-08-27 | 20.3 | 0 | 2.3 | 2020-08-27 | 11.2 | 6.8 | 0 | 2019-08-27 | 22.1 | 0 | 4.1 | 2018-08-27 | 22.2 | 0 | 4.2 | 2017-08-27 | 19.2 | 0 | 1.2 | 2016-08-27 | 23.4 | 0 | 5.4 | 0.78 | 2.67
2025-08-27 | 19.2 | 0 | 1.2 | 2024-08-27 | 27.4 | 0 | 9.4 | 2023-08-27 | 21.3 | 0 | 3.3 | 2022-08-27 | 18.7 | 0 | 0.7 | 2021-08-27 | 21.2 | 0 | 3.2 | 2020-08-27 | 12.3 | 5.7 | 0 | 2019-08-27 | 23.7 | 0 | 5.7 | 2018-08-27 | 22.5 | 0 | 4.5 | 2017-08-27 | 21.1 | 0 | 3.1 | 2016-08-27 | 24.2 | 0 | 6.2 | 0.57 | 3.73
2025-08-27 | 19.1 | 0 | 1.1 | 2024-08-27 | 28.3 | 0 | 10.3 | 2023-08-27 | 21.2 | 0 | 3.2 | 2022-08-27 | 19.4 | 0 | 1.4 | 2021-08-27 | 21.4 | 0 | 3.4 | 2020-08-27 | 12.6 | 5.4 | 0 | 2019-08-27 | 23.9 | 0 | 5.9 | 2018-08-27 | 22.9 | 0 | 4.9 | 2017-08-27 | 21.3 | 0 | 3.3 | 2016-08-27 | 25.3 | 0 | 7.3 | 0.54 | 4.08
2025-08-27 | 21.2 | 0 | 3.2 | 2024-08-27 | 27.5 | 0 | 9.5 | 2023-08-27 | 22.3 | 0 | 4.3 | 2022-08-27 | 21.1 | 0 | 3.1 | 2021-08-27 | 22.2 | 0 | 4.2 | 2020-08-27 | 13.4 | 4.6 | 0 | 2019-08-27 | 24.1 | 0 | 6.1 | 2018-08-27 | 23.2 | 0 | 5.2 | 2017-08-27 | 21.3 | 0 | 3.3 | 2016-08-27 | 26 | 0 | 8 | 0.46 | 4.69
2025-08-27 | 21.8 | 0 | 3.8 | 2024-08-27 | 28.8 | 0 | 10.8 | 2023-08-27 | 23.4 | 0 | 5.4 | 2022-08-27 | 21.4 | 0 | 3.4 | 2021-08-27 | 22.8 | 0 | 4.8 | 2020-08-27 | 14.3 | 3.7 | 0 | 2019-08-27 | 25.2 | 0 | 7.2 | 2018-08-27 | 24.7 | 0 | 6.7 | 2017-08-27 | 21.2 | 0 | 3.2 | 2016-08-27 | 26.8 | 0 | 8.8 | 0.37 | 5.41
2025-08-27 | 21.4 | 0 | 3.4 | 2024-08-27 | 28.1 | 0 | 10.1 | 2023-08-27 | 23.3 | 0 | 5.3 | 2022-08-27 | 21.9 | 0 | 3.9 | 2021-08-27 | 23.4 | 0 | 5.4 | 2020-08-27 | 15.7 | 2.3 | 0 | 2019-08-27 | 24.3 | 0 | 6.3 | 2018-08-27 | 24.2 | 0 | 6.2 | 2017-08-27 | 22.1 | 0 | 4.1 | 2016-08-27 | 26.7 | 0 | 8.7 | 0.23 | 5.34
2025-08-27 | 21.2 | 0 | 3.2 | 2024-08-27 | 27.4 | 0 | 9.4 | 2023-08-27 | 22.5 | 0 | 4.5 | 2022-08-27 | 22.1 | 0 | 4.1 | 2021-08-27 | 22.2 | 0 | 4.2 | 2020-08-27 | 15.7 | 2.3 | 0 | 2019-08-27 | 24.4 | 0 | 6.4 | 2018-08-27 | 24.7 | 0 | 6.7 | 2017-08-27 | 22.3 | 0 | 4.3 | 2016-08-27 | 26.1 | 0 | 8.1 | 0.23 | 5.09
2025-08-27 | 21.2 | 0 | 3.2 | 2024-08-27 | 26.2 | 0 | 8.2 | 2023-08-27 | 21 | 0 | 3 | 2022-08-27 | 21.8 | 0 | 3.8 | 2021-08-27 | 20.9 | 0 | 2.9 | 2020-08-27 | 15.7 | 2.3 | 0 | 2019-08-27 | 24.4 | 0 | 6.4 | 2018-08-27 | 24.4 | 0 | 6.4 | 2017-08-27 | 19.7 | 0 | 1.7 | 2016-08-27 | 25.7 | 0 | 7.7 | 0.23 | 4.33
2025-08-27 | 19.6 | 0 | 1.6 | 2024-08-27 | 24.7 | 0 | 6.7 | 2023-08-27 | 19.7 | 0 | 1.7 | 2022-08-27 | 19.8 | 0 | 1.8 | 2021-08-27 | 20.1 | 0 | 2.1 | 2020-08-27 | 15.6 | 2.4 | 0 | 2019-08-27 | 23 | 0 | 5 | 2018-08-27 | 24.2 | 0 | 6.2 | 2017-08-27 | 19.3 | 0 | 1.3 | 2016-08-27 | 23.5 | 0 | 5.5 | 0.24 | 3.19
2025-08-27 | 16.9 | 1.1 | 0 | 2024-08-27 | 24.8 | 0 | 6.8 | 2023-08-27 | 20.7 | 0 | 2.7 | 2022-08-27 | 18.6 | 0 | 0.6 | 2021-08-27 | 19.1 | 0 | 1.1 | 2020-08-27 | 14.5 | 3.5 | 0 | 2019-08-27 | 21.6 | 0 | 3.6 | 2018-08-27 | 23.2 | 0 | 5.2 | 2017-08-27 | 16.2 | 1.8 | 0 | 2016-08-27 | 21.8 | 0 | 3.8 | 0.64 | 2.38
2025-08-27 | 13.2 | 4.8 | 0 | 2024-08-27 | 22.4 | 0 | 4.4 | 2023-08-27 | 18.5 | 0 | 0.5 | 2022-08-27 | 17.3 | 0.7 | 0 | 2021-08-27 | 18.8 | 0 | 0.8 | 2020-08-27 | 14.8 | 3.2 | 0 | 2019-08-27 | 21.5 | 0 | 3.5 | 2018-08-27 | 22.9 | 0 | 4.9 | 2017-08-27 | 15.6 | 2.4 | 0 | 2016-08-27 | 21.3 | 0 | 3.3 | 1.11 | 1.74
2025-08-27 | 13.4 | 4.6 | 0 | 2024-08-27 | 22.1 | 0 | 4.1 | 2023-08-27 | 16.6 | 1.4 | 0 | 2022-08-27 | 14.3 | 3.7 | 0 | 2021-08-27 | 18.1 | 0 | 0.1 | 2020-08-27 | 14.3 | 3.7 | 0 | 2019-08-27 | 21.3 | 0 | 3.3 | 2018-08-27 | 22.9 | 0 | 4.9 | 2017-08-27 | 15.4 | 2.6 | 0 | 2016-08-27 | 20.8 | 0 | 2.8 | 1.6 | 1.52
2025-08-27 | 13.4 | 4.6 | 0 | 2024-08-27 | 21.6 | 0 | 3.6 | 2023-08-27 | 15.5 | 2.5 | 0 | 2022-08-27 | 12.6 | 5.4 | 0 | 2021-08-27 | 17.4 | 0.6 | 0 | 2020-08-27 | 14 | 4 | 0 | 2019-08-27 | 20.5 | 0 | 2.5 | 2018-08-27 | 22.6 | 0 | 4.6 | 2017-08-27 | 14.2 | 3.8 | 0 | 2016-08-27 | 21 | 0 | 3 | 2.09 | 1.37
2025-08-27 | 12.6 | 5.4 | 0 | 2024-08-27 | 21.5 | 0 | 3.5 | 2023-08-27 | 15.1 | 2.9 | 0 | 2022-08-27 | 11.7 | 6.3 | 0 | 2021-08-27 | 17.2 | 0.8 | 0 | 2020-08-27 | 13.9 | 4.1 | 0 | 2019-08-27 | 20.4 | 0 | 2.4 | 2018-08-27 | 22.9 | 0 | 4.9 | 2017-08-27 | 13.6 | 4.4 | 0 | 2016-08-27 | 20.6 | 0 | 2.6 | 2.39 | 1.34
2025-08-28 | 12.3 | 5.7 | 0 | 2024-08-28 | 22.1 | 0 | 4.1 | 2023-08-28 | 11.1 | 6.9 | 0 | 2022-08-28 | 11.9 | 6.1 | 0 | 2021-08-28 | 17.1 | 0.9 | 0 | 2020-08-28 | 14.1 | 3.9 | 0 | 2019-08-28 | 20.1 | 0 | 2.1 | 2018-08-28 | 22.7 | 0 | 4.7 | 2017-08-28 | 11.8 | 6.2 | 0 | 2016-08-28 | 20.6 | 0 | 2.6 | 2.97 | 1.35
2025-08-28 | 12.8 | 5.2 | 0 | 2024-08-28 | 21.2 | 0 | 3.2 | 2023-08-28 | 11.6 | 6.4 | 0 | 2022-08-28 | 13 | 5 | 0 | 2021-08-28 | 16.6 | 1.4 | 0 | 2020-08-28 | 13.9 | 4.1 | 0 | 2019-08-28 | 19.8 | 0 | 1.8 | 2018-08-28 | 22.1 | 0 | 4.1 | 2017-08-28 | 12.9 | 5.1 | 0 | 2016-08-28 | 19.6 | 0 | 1.6 | 2.72 | 1.07
2025-08-28 | 12.6 | 5.4 | 0 | 2024-08-28 | 19.4 | 0 | 1.4 | 2023-08-28 | 11.4 | 6.6 | 0 | 2022-08-28 | 13.4 | 4.6 | 0 | 2021-08-28 | 16.7 | 1.3 | 0 | 2020-08-28 | 13.7 | 4.3 | 0 | 2019-08-28 | 19.9 | 0 | 1.9 | 2018-08-28 | 21.9 | 0 | 3.9 | 2017-08-28 | 9.6 | 8.4 | 0 | 2016-08-28 | 19.7 | 0 | 1.7 | 3.06 | 0.89
2025-08-28 | 12.4 | 5.6 | 0 | 2024-08-28 | 18.1 | 0 | 0.1 | 2023-08-28 | 11.8 | 6.2 | 0 | 2022-08-28 | 12.3 | 5.7 | 0 | 2021-08-28 | 16.8 | 1.2 | 0 | 2020-08-28 | 12.9 | 5.1 | 0 | 2019-08-28 | 18.8 | 0 | 0.8 | 2018-08-28 | 21.9 | 0 | 3.9 | 2017-08-28 | 9.7 | 8.3 | 0 | 2016-08-28 | 19.1 | 0 | 1.1 | 3.21 | 0.59
2025-08-28 | 12.1 | 5.9 | 0 | 2024-08-28 | 16.9 | 1.1 | 0 | 2023-08-28 | 12.1 | 5.9 | 0 | 2022-08-28 | 11.6 | 6.4 | 0 | 2021-08-28 | 16.6 | 1.4 | 0 | 2020-08-28 | 11 | 7 | 0 | 2019-08-28 | 18.2 | 0 | 0.2 | 2018-08-28 | 21.8 | 0 | 3.8 | 2017-08-28 | 9.6 | 8.4 | 0 | 2016-08-28 | 18.9 | 0 | 0.9 | 3.61 | 0.49
2025-08-28 | 11.7 | 6.3 | 0 | 2024-08-28 | 16.6 | 1.4 | 0 | 2023-08-28 | 9.6 | 8.4 | 0 | 2022-08-28 | 11.3 | 6.7 | 0 | 2021-08-28 | 16 | 2 | 0 | 2020-08-28 | 11.1 | 6.9 | 0 | 2019-08-28 | 18.2 | 0 | 0.2 | 2018-08-28 | 21.5 | 0 | 3.5 | 2017-08-28 | 10.2 | 7.8 | 0 | 2016-08-28 | 17.9 | 0.1 | 0 | 3.96 | 0.37
2025-08-28 | 12.2 | 5.8 | 0 | 2024-08-28 | 15.9 | 2.1 | 0 | 2023-08-28 | 11.6 | 6.4 | 0 | 2022-08-28 | 11.9 | 6.1 | 0 | 2021-08-28 | 16.1 | 1.9 | 0 | 2020-08-28 | 11.8 | 6.2 | 0 | 2019-08-28 | 18.3 | 0 | 0.3 | 2018-08-28 | 21.7 | 0 | 3.7 | 2017-08-28 | 11.1 | 6.9 | 0 | 2016-08-28 | 18.3 | 0 | 0.3 | 3.54 | 0.43
2025-08-28 | 13.2 | 4.8 | 0 | 2024-08-28 | 15.5 | 2.5 | 0 | 2023-08-28 | 14.1 | 3.9 | 0 | 2022-08-28 | 14.1 | 3.9 | 0 | 2021-08-28 | 16.1 | 1.9 | 0 | 2020-08-28 | 13.2 | 4.8 | 0 | 2019-08-28 | 18.5 | 0 | 0.5 | 2018-08-28 | 22.7 | 0 | 4.7 | 2017-08-28 | 12.8 | 5.2 | 0 | 2016-08-28 | 19 | 0 | 1 | 2.7 | 0.62
2025-08-28 | 14.4 | 3.6 | 0 | 2024-08-28 | 15.3 | 2.7 | 0 | 2023-08-28 | 16.5 | 1.5 | 0 | 2022-08-28 | 16.8 | 1.2 | 0 | 2021-08-28 | 16.4 | 1.6 | 0 | 2020-08-28 | 15.5 | 2.5 | 0 | 2019-08-28 | 18.5 | 0 | 0.5 | 2018-08-28 | 24.5 | 0 | 6.5 | 2017-08-28 | 15.5 | 2.5 | 0 | 2016-08-28 | 21 | 0 | 3 | 1.56 | 1
2025-08-28 | 15.8 | 2.2 | 0 | 2024-08-28 | 15.8 | 2.2 | 0 | 2023-08-28 | 18.6 | 0 | 0.6 | 2022-08-28 | 19 | 0 | 1 | 2021-08-28 | 17.6 | 0.4 | 0 | 2020-08-28 | 16.6 | 1.4 | 0 | 2019-08-28 | 18.7 | 0 | 0.7 | 2018-08-28 | 25.9 | 0 | 7.9 | 2017-08-28 | 17.4 | 0.6 | 0 | 2016-08-28 | 22.3 | 0 | 4.3 | 0.68 | 1.45
2025-08-28 | 16.8 | 1.2 | 0 | 2024-08-28 | 16.4 | 1.6 | 0 | 2023-08-28 | 20.8 | 0 | 2.8 | 2022-08-28 | 21.4 | 0 | 3.4 | 2021-08-28 | 17 | 1 | 0 | 2020-08-28 | 17.6 | 0.4 | 0 | 2019-08-28 | 19.5 | 0 | 1.5 | 2018-08-28 | 27.9 | 0 | 9.9 | 2017-08-28 | 19.3 | 0 | 1.3 | 2016-08-28 | 23.4 | 0 | 5.4 | 0.42 | 2.43
2025-08-28 | 18.7 | 0 | 0.7 | 2024-08-28 | 18.1 | 0 | 0.1 | 2023-08-28 | 22.2 | 0 | 4.2 | 2022-08-28 | 22.5 | 0 | 4.5 | 2021-08-28 | 17.2 | 0.8 | 0 | 2020-08-28 | 18.8 | 0 | 0.8 | 2019-08-28 | 19.9 | 0 | 1.9 | 2018-08-28 | 29.6 | 0 | 11.6 | 2017-08-28 | 21.3 | 0 | 3.3 | 2016-08-28 | 24.4 | 0 | 6.4 | 0.08 | 3.35
2025-08-28 | 19.2 | 0 | 1.2 | 2024-08-28 | 18.7 | 0 | 0.7 | 2023-08-28 | 23.6 | 0 | 5.6 | 2022-08-28 | 24.1 | 0 | 6.1 | 2021-08-28 | 17.5 | 0.5 | 0 | 2020-08-28 | 20.2 | 0 | 2.2 | 2019-08-28 | 20 | 0 | 2 | 2018-08-28 | 28.1 | 0 | 10.1 | 2017-08-28 | 22.7 | 0 | 4.7 | 2016-08-28 | 27.2 | 0 | 9.2 | 0.05 | 4.18
2025-08-28 | 17.5 | 0.5 | 0 | 2024-08-28 | 18.9 | 0 | 0.9 | 2023-08-28 | 24 | 0 | 6 | 2022-08-28 | 24.9 | 0 | 6.9 | 2021-08-28 | 17.8 | 0.2 | 0 | 2020-08-28 | 21 | 0 | 3 | 2019-08-28 | 21.1 | 0 | 3.1 | 2018-08-28 | 29.5 | 0 | 11.5 | 2017-08-28 | 22.6 | 0 | 4.6 | 2016-08-28 | 28 | 0 | 10 | 0.07 | 4.6
2025-08-28 | 17.6 | 0.4 | 0 | 2024-08-28 | 19.6 | 0 | 1.6 | 2023-08-28 | 24.5 | 0 | 6.5 | 2022-08-28 | 25.1 | 0 | 7.1 | 2021-08-28 | 18.6 | 0 | 0.6 | 2020-08-28 | 21.5 | 0 | 3.5 | 2019-08-28 | 22.3 | 0 | 4.3 | 2018-08-28 | 28.9 | 0 | 10.9 | 2017-08-28 | 22.8 | 0 | 4.8 | 2016-08-28 | 28.1 | 0 | 10.1 | 0.04 | 4.94
2025-08-28 | 17.1 | 0.9 | 0 | 2024-08-28 | 19.6 | 0 | 1.6 | 2023-08-28 | 24.1 | 0 | 6.1 | 2022-08-28 | 25.8 | 0 | 7.8 | 2021-08-28 | 18.5 | 0 | 0.5 | 2020-08-28 | 20.8 | 0 | 2.8 | 2019-08-28 | 22.1 | 0 | 4.1 | 2018-08-28 | 30 | 0 | 12 | 2017-08-28 | 23.5 | 0 | 5.5 | 2016-08-28 | 28.6 | 0 | 10.6 | 0.09 | 5.1
2025-08-28 | 16.4 | 1.6 | 0 | 2024-08-28 | 18.5 | 0 | 0.5 | 2023-08-28 | 22.9 | 0 | 4.9 | 2022-08-28 | 26 | 0 | 8 | 2021-08-28 | 18.4 | 0 | 0.4 | 2020-08-28 | 21.6 | 0 | 3.6 | 2019-08-28 | 22.2 | 0 | 4.2 | 2018-08-28 | 29.1 | 0 | 11.1 | 2017-08-28 | 23.2 | 0 | 5.2 | 2016-08-28 | 26.6 | 0 | 8.6 | 0.16 | 4.65
2025-08-28 | 14 | 4 | 0 | 2024-08-28 | 18.6 | 0 | 0.6 | 2023-08-28 | 21.9 | 0 | 3.9 | 2022-08-28 | 25.8 | 0 | 7.8 | 2021-08-28 | 18 | 0 | 0 | 2020-08-28 | 20.7 | 0 | 2.7 | 2019-08-28 | 21.6 | 0 | 3.6 | 2018-08-28 | 29.7 | 0 | 11.7 | 2017-08-28 | 22.7 | 0 | 4.7 | 2016-08-28 | 28.1 | 0 | 10.1 | 0.4 | 4.51
2025-08-28 | 14.3 | 3.7 | 0 | 2024-08-28 | 17.8 | 0.2 | 0 | 2023-08-28 | 21.4 | 0 | 3.4 | 2022-08-28 | 23.8 | 0 | 5.8 | 2021-08-28 | 18 | 0 | 0 | 2020-08-28 | 19.3 | 0 | 1.3 | 2019-08-28 | 21.2 | 0 | 3.2 | 2018-08-28 | 27.7 | 0 | 9.7 | 2017-08-28 | 20.7 | 0 | 2.7 | 2016-08-28 | 27.7 | 0 | 9.7 | 0.39 | 3.58
2025-08-28 | 14.7 | 3.3 | 0 | 2024-08-28 | 16.5 | 1.5 | 0 | 2023-08-28 | 18.4 | 0 | 0.4 | 2022-08-28 | 19.8 | 0 | 1.8 | 2021-08-28 | 17.7 | 0.3 | 0 | 2020-08-28 | 18.5 | 0 | 0.5 | 2019-08-28 | 20.5 | 0 | 2.5 | 2018-08-28 | 25 | 0 | 7 | 2017-08-28 | 18.2 | 0 | 0.2 | 2016-08-28 | 25.6 | 0 | 7.6 | 0.51 | 2
2025-08-28 | 13.8 | 4.2 | 0 | 2024-08-28 | 15.8 | 2.2 | 0 | 2023-08-28 | 18.7 | 0 | 0.7 | 2022-08-28 | 19.5 | 0 | 1.5 | 2021-08-28 | 16.8 | 1.2 | 0 | 2020-08-28 | 16.5 | 1.5 | 0 | 2019-08-28 | 19.8 | 0 | 1.8 | 2018-08-28 | 23.8 | 0 | 5.8 | 2017-08-28 | 17.5 | 0.5 | 0 | 2016-08-28 | 23.9 | 0 | 5.9 | 0.96 | 1.57
2025-08-28 | 13.7 | 4.3 | 0 | 2024-08-28 | 14.6 | 3.4 | 0 | 2023-08-28 | 17.2 | 0.8 | 0 | 2022-08-28 | 18.7 | 0 | 0.7 | 2021-08-28 | 15.7 | 2.3 | 0 | 2020-08-28 | 16.6 | 1.4 | 0 | 2019-08-28 | 19.5 | 0 | 1.5 | 2018-08-28 | 23.5 | 0 | 5.5 | 2017-08-28 | 17.3 | 0.7 | 0 | 2016-08-28 | 24.3 | 0 | 6.3 | 1.29 | 1.4
2025-08-28 | 13.8 | 4.2 | 0 | 2024-08-28 | 14.1 | 3.9 | 0 | 2023-08-28 | 14.7 | 3.3 | 0 | 2022-08-28 | 19.3 | 0 | 1.3 | 2021-08-28 | 15.7 | 2.3 | 0 | 2020-08-28 | 15.3 | 2.7 | 0 | 2019-08-28 | 18.9 | 0 | 0.9 | 2018-08-28 | 22.6 | 0 | 4.6 | 2017-08-28 | 16.1 | 1.9 | 0 | 2016-08-28 | 23.4 | 0 | 5.4 | 1.83 | 1.22
2025-08-28 | 13.6 | 4.4 | 0 | 2024-08-28 | 13.9 | 4.1 | 0 | 2023-08-28 | 13.2 | 4.8 | 0 | 2022-08-28 | 19.5 | 0 | 1.5 | 2021-08-28 | 15.7 | 2.3 | 0 | 2020-08-28 | 15.9 | 2.1 | 0 | 2019-08-28 | 18 | 0 | 0 | 2018-08-28 | 21.7 | 0 | 3.7 | 2017-08-28 | 16.4 | 1.6 | 0 | 2016-08-28 | 21.7 | 0 | 3.7 | 1.93 | 0.89
2025-08-29 | 13.6 | 4.4 | 0 | 2024-08-29 | 13.2 | 4.8 | 0 | 2023-08-29 | 15.2 | 2.8 | 0 | 2022-08-29 | 18.9 | 0 | 0.9 | 2021-08-29 | 15.9 | 2.1 | 0 | 2020-08-29 | 16.5 | 1.5 | 0 | 2019-08-29 | 17.3 | 0.7 | 0 | 2018-08-29 | 21 | 0 | 3 | 2017-08-29 | 14.3 | 3.7 | 0 | 2016-08-29 | 21.1 | 0 | 3.1 | 2 | 0.7
2025-08-29 | 13.2 | 4.8 | 0 | 2024-08-29 | 11.4 | 6.6 | 0 | 2023-08-29 | 13.6 | 4.4 | 0 | 2022-08-29 | 19.6 | 0 | 1.6 | 2021-08-29 | 16 | 2 | 0 | 2020-08-29 | 16.4 | 1.6 | 0 | 2019-08-29 | 16.1 | 1.9 | 0 | 2018-08-29 | 20.2 | 0 | 2.2 | 2017-08-29 | 14.3 | 3.7 | 0 | 2016-08-29 | 19.9 | 0 | 1.9 | 2.5 | 0.57
2025-08-29 | 12.7 | 5.3 | 0 | 2024-08-29 | 12 | 6 | 0 | 2023-08-29 | 13.2 | 4.8 | 0 | 2022-08-29 | 19.3 | 0 | 1.3 | 2021-08-29 | 16.1 | 1.9 | 0 | 2020-08-29 | 15.7 | 2.3 | 0 | 2019-08-29 | 15.3 | 2.7 | 0 | 2018-08-29 | 19.8 | 0 | 1.8 | 2017-08-29 | 14.1 | 3.9 | 0 | 2016-08-29 | 18.9 | 0 | 0.9 | 2.69 | 0.4
2025-08-29 | 12.4 | 5.6 | 0 | 2024-08-29 | 10.1 | 7.9 | 0 | 2023-08-29 | 13 | 5 | 0 | 2022-08-29 | 17.7 | 0.3 | 0 | 2021-08-29 | 16.2 | 1.8 | 0 | 2020-08-29 | 14.9 | 3.1 | 0 | 2019-08-29 | 13.6 | 4.4 | 0 | 2018-08-29 | 19.5 | 0 | 1.5 | 2017-08-29 | 13.4 | 4.6 | 0 | 2016-08-29 | 17.6 | 0.4 | 0 | 3.31 | 0.15
2025-08-29 | 12 | 6 | 0 | 2024-08-29 | 9.8 | 8.2 | 0 | 2023-08-29 | 11.2 | 6.8 | 0 | 2022-08-29 | 17.5 | 0.5 | 0 | 2021-08-29 | 16.4 | 1.6 | 0 | 2020-08-29 | 14.6 | 3.4 | 0 | 2019-08-29 | 13.7 | 4.3 | 0 | 2018-08-29 | 19.6 | 0 | 1.6 | 2017-08-29 | 12.9 | 5.1 | 0 | 2016-08-29 | 15.9 | 2.1 | 0 | 3.8 | 0.16
2025-08-29 | 11.8 | 6.2 | 0 | 2024-08-29 | 9.6 | 8.4 | 0 | 2023-08-29 | 11.5 | 6.5 | 0 | 2022-08-29 | 17.7 | 0.3 | 0 | 2021-08-29 | 16.4 | 1.6 | 0 | 2020-08-29 | 14.4 | 3.6 | 0 | 2019-08-29 | 13.8 | 4.2 | 0 | 2018-08-29 | 19.8 | 0 | 1.8 | 2017-08-29 | 12.3 | 5.7 | 0 | 2016-08-29 | 16.3 | 1.7 | 0 | 3.82 | 0.18
2025-08-29 | 11.6 | 6.4 | 0 | 2024-08-29 | 10.2 | 7.8 | 0 | 2023-08-29 | 10.9 | 7.1 | 0 | 2022-08-29 | 17.6 | 0.4 | 0 | 2021-08-29 | 16.5 | 1.5 | 0 | 2020-08-29 | 14.3 | 3.7 | 0 | 2019-08-29 | 14.2 | 3.8 | 0 | 2018-08-29 | 20.8 | 0 | 2.8 | 2017-08-29 | 13.3 | 4.7 | 0 | 2016-08-29 | 16.7 | 1.3 | 0 | 3.67 | 0.28
2025-08-29 | 12.8 | 5.2 | 0 | 2024-08-29 | 12.8 | 5.2 | 0 | 2023-08-29 | 14.1 | 3.9 | 0 | 2022-08-29 | 19.7 | 0 | 1.7 | 2021-08-29 | 16.9 | 1.1 | 0 | 2020-08-29 | 14.2 | 3.8 | 0 | 2019-08-29 | 15.3 | 2.7 | 0 | 2018-08-29 | 21.8 | 0 | 3.8 | 2017-08-29 | 14.4 | 3.6 | 0 | 2016-08-29 | 17.6 | 0.4 | 0 | 2.59 | 0.55
2025-08-29 | 13.1 | 4.9 | 0 | 2024-08-29 | 14.3 | 3.7 | 0 | 2023-08-29 | 17.2 | 0.8 | 0 | 2022-08-29 | 23.1 | 0 | 5.1 | 2021-08-29 | 17.4 | 0.6 | 0 | 2020-08-29 | 14.3 | 3.7 | 0 | 2019-08-29 | 18.5 | 0 | 0.5 | 2018-08-29 | 23.6 | 0 | 5.6 | 2017-08-29 | 17.1 | 0.9 | 0 | 2016-08-29 | 18.6 | 0 | 0.6 | 1.46 | 1.18
2025-08-29 | 13.8 | 4.2 | 0 | 2024-08-29 | 15.4 | 2.6 | 0 | 2023-08-29 | 19.9 | 0 | 1.9 | 2022-08-29 | 23.8 | 0 | 5.8 | 2021-08-29 | 18.1 | 0 | 0.1 | 2020-08-29 | 14.4 | 3.6 | 0 | 2019-08-29 | 20.4 | 0 | 2.4 | 2018-08-29 | 26.7 | 0 | 8.7 | 2017-08-29 | 19 | 0 | 1 | 2016-08-29 | 19.6 | 0 | 1.6 | 1.04 | 2.15
2025-08-29 | 14.3 | 3.7 | 0 | 2024-08-29 | 16.8 | 1.2 | 0 | 2023-08-29 | 22.1 | 0 | 4.1 | 2022-08-29 | 25.9 | 0 | 7.9 | 2021-08-29 | 18.4 | 0 | 0.4 | 2020-08-29 | 14.4 | 3.6 | 0 | 2019-08-29 | 20.8 | 0 | 2.8 | 2018-08-29 | 27.8 | 0 | 9.8 | 2017-08-29 | 21.9 | 0 | 3.9 | 2016-08-29 | 20.8 | 0 | 2.8 | 0.85 | 3.17
2025-08-29 | 14.8 | 3.2 | 0 | 2024-08-29 | 17.8 | 0.2 | 0 | 2023-08-29 | 22.6 | 0 | 4.6 | 2022-08-29 | 28.5 | 0 | 10.5 | 2021-08-29 | 19.5 | 0 | 1.5 | 2020-08-29 | 14.6 | 3.4 | 0 | 2019-08-29 | 21.7 | 0 | 3.7 | 2018-08-29 | 29.6 | 0 | 11.6 | 2017-08-29 | 22.6 | 0 | 4.6 | 2016-08-29 | 22.4 | 0 | 4.4 | 0.68 | 4.09
2025-08-29 | 15.6 | 2.4 | 0 | 2024-08-29 | 19.4 | 0 | 1.4 | 2023-08-29 | 23.9 | 0 | 5.9 | 2022-08-29 | 28.8 | 0 | 10.8 | 2021-08-29 | 20.5 | 0 | 2.5 | 2020-08-29 | 15.6 | 2.4 | 0 | 2019-08-29 | 22.5 | 0 | 4.5 | 2018-08-29 | 27 | 0 | 9 | 2017-08-29 | 22.2 | 0 | 4.2 | 2016-08-29 | 23.5 | 0 | 5.5 | 0.48 | 4.38
2025-08-29 | 17.2 | 0.8 | 0 | 2024-08-29 | 20 | 0 | 2 | 2023-08-29 | 25.4 | 0 | 7.4 | 2022-08-29 | 30.4 | 0 | 12.4 | 2021-08-29 | 21.4 | 0 | 3.4 | 2020-08-29 | 15.8 | 2.2 | 0 | 2019-08-29 | 21.5 | 0 | 3.5 | 2018-08-29 | 22.6 | 0 | 4.6 | 2017-08-29 | 22.7 | 0 | 4.7 | 2016-08-29 | 23.9 | 0 | 5.9 | 0.3 | 4.39
2025-08-29 | 18.1 | 0 | 0.1 | 2024-08-29 | 20.8 | 0 | 2.8 | 2023-08-29 | 24.8 | 0 | 6.8 | 2022-08-29 | 28.2 | 0 | 10.2 | 2021-08-29 | 23 | 0 | 5 | 2020-08-29 | 15.9 | 2.1 | 0 | 2019-08-29 | 22 | 0 | 4 | 2018-08-29 | 26.1 | 0 | 8.1 | 2017-08-29 | 23.4 | 0 | 5.4 | 2016-08-29 | 24.1 | 0 | 6.1 | 0.21 | 4.85
2025-08-29 | 13.9 | 4.1 | 0 | 2024-08-29 | 21 | 0 | 3 | 2023-08-29 | 24.8 | 0 | 6.8 | 2022-08-29 | 30.6 | 0 | 12.6 | 2021-08-29 | 23.7 | 0 | 5.7 | 2020-08-29 | 15.6 | 2.4 | 0 | 2019-08-29 | 22.8 | 0 | 4.8 | 2018-08-29 | 26.1 | 0 | 8.1 | 2017-08-29 | 23.3 | 0 | 5.3 | 2016-08-29 | 24.9 | 0 | 6.9 | 0.65 | 5.32
2025-08-29 | 15.8 | 2.2 | 0 | 2024-08-29 | 21.1 | 0 | 3.1 | 2023-08-29 | 26.2 | 0 | 8.2 | 2022-08-29 | 30.5 | 0 | 12.5 | 2021-08-29 | 24.2 | 0 | 6.2 | 2020-08-29 | 15.3 | 2.7 | 0 | 2019-08-29 | 23 | 0 | 5 | 2018-08-29 | 27.7 | 0 | 9.7 | 2017-08-29 | 22.6 | 0 | 4.6 | 2016-08-29 | 24.8 | 0 | 6.8 | 0.49 | 5.61
2025-08-29 | 15.9 | 2.1 | 0 | 2024-08-29 | 20.7 | 0 | 2.7 | 2023-08-29 | 25 | 0 | 7 | 2022-08-29 | 28.3 | 0 | 10.3 | 2021-08-29 | 25.6 | 0 | 7.6 | 2020-08-29 | 15.5 | 2.5 | 0 | 2019-08-29 | 22.9 | 0 | 4.9 | 2018-08-29 | 26.4 | 0 | 8.4 | 2017-08-29 | 21.1 | 0 | 3.1 | 2016-08-29 | 24.2 | 0 | 6.2 | 0.46 | 5.02
2025-08-29 | 14.6 | 3.4 | 0 | 2024-08-29 | 18.6 | 0 | 0.6 | 2023-08-29 | 22.8 | 0 | 4.8 | 2022-08-29 | 22.7 | 0 | 4.7 | 2021-08-29 | 25.3 | 0 | 7.3 | 2020-08-29 | 15.6 | 2.4 | 0 | 2019-08-29 | 21.5 | 0 | 3.5 | 2018-08-29 | 26 | 0 | 8 | 2017-08-29 | 20 | 0 | 2 | 2016-08-29 | 22.6 | 0 | 4.6 | 0.58 | 3.55
2025-08-29 | 13.8 | 4.2 | 0 | 2024-08-29 | 15.8 | 2.2 | 0 | 2023-08-29 | 20 | 0 | 2 | 2022-08-29 | 23.1 | 0 | 5.1 | 2021-08-29 | 24 | 0 | 6 | 2020-08-29 | 15.5 | 2.5 | 0 | 2019-08-29 | 18.9 | 0 | 0.9 | 2018-08-29 | 24.6 | 0 | 6.6 | 2017-08-29 | 18.9 | 0 | 0.9 | 2016-08-29 | 21.5 | 0 | 3.5 | 0.89 | 2.5
2025-08-29 | 13.4 | 4.6 | 0 | 2024-08-29 | 15.8 | 2.2 | 0 | 2023-08-29 | 20.9 | 0 | 2.9 | 2022-08-29 | 22.9 | 0 | 4.9 | 2021-08-29 | 23.3 | 0 | 5.3 | 2020-08-29 | 14.7 | 3.3 | 0 | 2019-08-29 | 18.2 | 0 | 0.2 | 2018-08-29 | 22.7 | 0 | 4.7 | 2017-08-29 | 16.2 | 1.8 | 0 | 2016-08-29 | 18.2 | 0 | 0.2 | 1.19 | 1.82
2025-08-29 | 13.1 | 4.9 | 0 | 2024-08-29 | 14.8 | 3.2 | 0 | 2023-08-29 | 20.1 | 0 | 2.1 | 2022-08-29 | 22.7 | 0 | 4.7 | 2021-08-29 | 22.8 | 0 | 4.8 | 2020-08-29 | 14.5 | 3.5 | 0 | 2019-08-29 | 16.9 | 1.1 | 0 | 2018-08-29 | 21.5 | 0 | 3.5 | 2017-08-29 | 15.5 | 2.5 | 0 | 2016-08-29 | 18.9 | 0 | 0.9 | 1.52 | 1.6
2025-08-29 | 11.6 | 6.4 | 0 | 2024-08-29 | 13.8 | 4.2 | 0 | 2023-08-29 | 18.9 | 0 | 0.9 | 2022-08-29 | 22.4 | 0 | 4.4 | 2021-08-29 | 23.1 | 0 | 5.1 | 2020-08-29 | 14.4 | 3.6 | 0 | 2019-08-29 | 16.2 | 1.8 | 0 | 2018-08-29 | 20.3 | 0 | 2.3 | 2017-08-29 | 14 | 4 | 0 | 2016-08-29 | 17.2 | 0.8 | 0 | 2.08 | 1.27
2025-08-29 | 11.6 | 6.4 | 0 | 2024-08-29 | 13.8 | 4.2 | 0 | 2023-08-29 | 18.4 | 0 | 0.4 | 2022-08-29 | 22.5 | 0 | 4.5 | 2021-08-29 | 23.1 | 0 | 5.1 | 2020-08-29 | 14.3 | 3.7 | 0 | 2019-08-29 | 15.8 | 2.2 | 0 | 2018-08-29 | 19.4 | 0 | 1.4 | 2017-08-29 | 13 | 5 | 0 | 2016-08-29 | 14.9 | 3.1 | 0 | 2.46 | 1.14
2025-08-30 | 11.1 | 6.9 | 0 | 2024-08-30 | 13.3 | 4.7 | 0 | 2023-08-30 | 18.5 | 0 | 0.5 | 2022-08-30 | 22.2 | 0 | 4.2 | 2021-08-30 | 23 | 0 | 5 | 2020-08-30 | 14.2 | 3.8 | 0 | 2019-08-30 | 14.8 | 3.2 | 0 | 2018-08-30 | 17.7 | 0.3 | 0 | 2017-08-30 | 12.6 | 5.4 | 0 | 2016-08-30 | 14 | 4 | 0 | 2.83 | 0.97
2025-08-30 | 10.4 | 7.6 | 0 | 2024-08-30 | 12.5 | 5.5 | 0 | 2023-08-30 | 19 | 0 | 1 | 2022-08-30 | 22 | 0 | 4 | 2021-08-30 | 22.6 | 0 | 4.6 | 2020-08-30 | 14.3 | 3.7 | 0 | 2019-08-30 | 15.4 | 2.6 | 0 | 2018-08-30 | 16.2 | 1.8 | 0 | 2017-08-30 | 12.9 | 5.1 | 0 | 2016-08-30 | 12.6 | 5.4 | 0 | 3.17 | 0.96
2025-08-30 | 11.1 | 6.9 | 0 | 2024-08-30 | 11 | 7 | 0 | 2023-08-30 | 18.8 | 0 | 0.8 | 2022-08-30 | 21.3 | 0 | 3.3 | 2021-08-30 | 22.5 | 0 | 4.5 | 2020-08-30 | 13.1 | 4.9 | 0 | 2019-08-30 | 16.4 | 1.6 | 0 | 2018-08-30 | 15.4 | 2.6 | 0 | 2017-08-30 | 11.8 | 6.2 | 0 | 2016-08-30 | 13.5 | 4.5 | 0 | 3.37 | 0.86
2025-08-30 | 11.1 | 6.9 | 0 | 2024-08-30 | 10.6 | 7.4 | 0 | 2023-08-30 | 17.9 | 0.1 | 0 | 2022-08-30 | 21.5 | 0 | 3.5 | 2021-08-30 | 22.5 | 0 | 4.5 | 2020-08-30 | 12.7 | 5.3 | 0 | 2019-08-30 | 16.3 | 1.7 | 0 | 2018-08-30 | 14.4 | 3.6 | 0 | 2017-08-30 | 9.7 | 8.3 | 0 | 2016-08-30 | 15 | 3 | 0 | 3.63 | 0.8
2025-08-30 | 10.4 | 7.6 | 0 | 2024-08-30 | 11.4 | 6.6 | 0 | 2023-08-30 | 17.9 | 0.1 | 0 | 2022-08-30 | 21.8 | 0 | 3.8 | 2021-08-30 | 22.2 | 0 | 4.2 | 2020-08-30 | 12.8 | 5.2 | 0 | 2019-08-30 | 15.5 | 2.5 | 0 | 2018-08-30 | 13.5 | 4.5 | 0 | 2017-08-30 | 10.1 | 7.9 | 0 | 2016-08-30 | 13.6 | 4.4 | 0 | 3.88 | 0.8
2025-08-30 | 10.7 | 7.3 | 0 | 2024-08-30 | 10.6 | 7.4 | 0 | 2023-08-30 | 17 | 1 | 0 | 2022-08-30 | 21.6 | 0 | 3.6 | 2021-08-30 | 22.3 | 0 | 4.3 | 2020-08-30 | 12.4 | 5.6 | 0 | 2019-08-30 | 15.9 | 2.1 | 0 | 2018-08-30 | 12.9 | 5.1 | 0 | 2017-08-30 | 10.3 | 7.7 | 0 | 2016-08-30 | 13.8 | 4.2 | 0 | 4.04 | 0.79
2025-08-30 | 11.2 | 6.8 | 0 | 2024-08-30 | 11.4 | 6.6 | 0 | 2023-08-30 | 17.1 | 0.9 | 0 | 2022-08-30 | 21.5 | 0 | 3.5 | 2021-08-30 | 22 | 0 | 4 | 2020-08-30 | 12.5 | 5.5 | 0 | 2019-08-30 | 16.4 | 1.6 | 0 | 2018-08-30 | 13.2 | 4.8 | 0 | 2017-08-30 | 12.4 | 5.6 | 0 | 2016-08-30 | 14 | 4 | 0 | 3.58 | 0.75
2025-08-30 | 11.8 | 6.2 | 0 | 2024-08-30 | 13.4 | 4.6 | 0 | 2023-08-30 | 17.5 | 0.5 | 0 | 2022-08-30 | 22 | 0 | 4 | 2021-08-30 | 22.3 | 0 | 4.3 | 2020-08-30 | 13.4 | 4.6 | 0 | 2019-08-30 | 17.9 | 0.1 | 0 | 2018-08-30 | 13.9 | 4.1 | 0 | 2017-08-30 | 14.1 | 3.9 | 0 | 2016-08-30 | 16.3 | 1.7 | 0 | 2.57 | 0.83
2025-08-30 | 12.5 | 5.5 | 0 | 2024-08-30 | 15.4 | 2.6 | 0 | 2023-08-30 | 19.1 | 0 | 1.1 | 2022-08-30 | 22.9 | 0 | 4.9 | 2021-08-30 | 23.9 | 0 | 5.9 | 2020-08-30 | 14.6 | 3.4 | 0 | 2019-08-30 | 18.5 | 0 | 0.5 | 2018-08-30 | 14 | 4 | 0 | 2017-08-30 | 16.2 | 1.8 | 0 | 2016-08-30 | 19.8 | 0 | 1.8 | 1.73 | 1.42
2025-08-30 | 14 | 4 | 0 | 2024-08-30 | 18.3 | 0 | 0.3 | 2023-08-30 | 18.1 | 0 | 0.1 | 2022-08-30 | 24.2 | 0 | 6.2 | 2021-08-30 | 25 | 0 | 7 | 2020-08-30 | 15.7 | 2.3 | 0 | 2019-08-30 | 19 | 0 | 1 | 2018-08-30 | 14.5 | 3.5 | 0 | 2017-08-30 | 17.8 | 0.2 | 0 | 2016-08-30 | 21.9 | 0 | 3.9 | 1 | 1.85
2025-08-30 | 15.6 | 2.4 | 0 | 2024-08-30 | 19.4 | 0 | 1.4 | 2023-08-30 | 17.3 | 0.7 | 0 | 2022-08-30 | 24.9 | 0 | 6.9 | 2021-08-30 | 25.1 | 0 | 7.1 | 2020-08-30 | 17 | 1 | 0 | 2019-08-30 | 20.8 | 0 | 2.8 | 2018-08-30 | 15.8 | 2.2 | 0 | 2017-08-30 | 19.8 | 0 | 1.8 | 2016-08-30 | 23.6 | 0 | 5.6 | 0.63 | 2.56
2025-08-30 | 15.8 | 2.2 | 0 | 2024-08-30 | 19.6 | 0 | 1.6 | 2023-08-30 | 15.8 | 2.2 | 0 | 2022-08-30 | 25.3 | 0 | 7.3 | 2021-08-30 | 26.2 | 0 | 8.2 | 2020-08-30 | 17.9 | 0.1 | 0 | 2019-08-30 | 22.2 | 0 | 4.2 | 2018-08-30 | 17.4 | 0.6 | 0 | 2017-08-30 | 21.8 | 0 | 3.8 | 2016-08-30 | 25.3 | 0 | 7.3 | 0.51 | 3.24
2025-08-30 | 16.8 | 1.2 | 0 | 2024-08-30 | 21.3 | 0 | 3.3 | 2023-08-30 | 18.1 | 0 | 0.1 | 2022-08-30 | 24.9 | 0 | 6.9 | 2021-08-30 | 27 | 0 | 9 | 2020-08-30 | 19.1 | 0 | 1.1 | 2019-08-30 | 23.4 | 0 | 5.4 | 2018-08-30 | 18.5 | 0 | 0.5 | 2017-08-30 | 22.3 | 0 | 4.3 | 2016-08-30 | 25.3 | 0 | 7.3 | 0.12 | 3.79
2025-08-30 | 17.6 | 0.4 | 0 | 2024-08-30 | 21.8 | 0 | 3.8 | 2023-08-30 | 19.6 | 0 | 1.6 | 2022-08-30 | 23.9 | 0 | 5.9 | 2021-08-30 | 27.7 | 0 | 9.7 | 2020-08-30 | 18.8 | 0 | 0.8 | 2019-08-30 | 22.5 | 0 | 4.5 | 2018-08-30 | 19.2 | 0 | 1.2 | 2017-08-30 | 23 | 0 | 5 | 2016-08-30 | 24.3 | 0 | 6.3 | 0.04 | 3.88
2025-08-30 | 19.8 | 0 | 1.8 | 2024-08-30 | 22.1 | 0 | 4.1 | 2023-08-30 | 20.2 | 0 | 2.2 | 2022-08-30 | 22.9 | 0 | 4.9 | 2021-08-30 | 28 | 0 | 10 | 2020-08-30 | 19.9 | 0 | 1.9 | 2019-08-30 | 22.3 | 0 | 4.3 | 2018-08-30 | 20 | 0 | 2 | 2017-08-30 | 23.4 | 0 | 5.4 | 2016-08-30 | 24.7 | 0 | 6.7 | 0 | 4.33
2025-08-30 | 19.9 | 0 | 1.9 | 2024-08-30 | 22.1 | 0 | 4.1 | 2023-08-30 | 19.1 | 0 | 1.1 | 2022-08-30 | 20.4 | 0 | 2.4 | 2021-08-30 | 27.6 | 0 | 9.6 | 2020-08-30 | 19.9 | 0 | 1.9 | 2019-08-30 | 21.9 | 0 | 3.9 | 2018-08-30 | 20.6 | 0 | 2.6 | 2017-08-30 | 22.5 | 0 | 4.5 | 2016-08-30 | 24.7 | 0 | 6.7 | 0 | 3.87
2025-08-30 | 19.9 | 0 | 1.9 | 2024-08-30 | 22.8 | 0 | 4.8 | 2023-08-30 | 18.2 | 0 | 0.2 | 2022-08-30 | 19.5 | 0 | 1.5 | 2021-08-30 | 27.4 | 0 | 9.4 | 2020-08-30 | 20 | 0 | 2 | 2019-08-30 | 21.8 | 0 | 3.8 | 2018-08-30 | 20.6 | 0 | 2.6 | 2017-08-30 | 24 | 0 | 6 | 2016-08-30 | 24.2 | 0 | 6.2 | 0 | 3.84
2025-08-30 | 18.4 | 0 | 0.4 | 2024-08-30 | 22.4 | 0 | 4.4 | 2023-08-30 | 17.4 | 0.6 | 0 | 2022-08-30 | 19.1 | 0 | 1.1 | 2021-08-30 | 26.4 | 0 | 8.4 | 2020-08-30 | 18.8 | 0 | 0.8 | 2019-08-30 | 21.1 | 0 | 3.1 | 2018-08-30 | 20.4 | 0 | 2.4 | 2017-08-30 | 23.3 | 0 | 5.3 | 2016-08-30 | 23.5 | 0 | 5.5 | 0.06 | 3.14
2025-08-30 | 19.1 | 0 | 1.1 | 2024-08-30 | 21.8 | 0 | 3.8 | 2023-08-30 | 16.1 | 1.9 | 0 | 2022-08-30 | 19.1 | 0 | 1.1 | 2021-08-30 | 25.4 | 0 | 7.4 | 2020-08-30 | 15.8 | 2.2 | 0 | 2019-08-30 | 20 | 0 | 2 | 2018-08-30 | 19.2 | 0 | 1.2 | 2017-08-30 | 21.3 | 0 | 3.3 | 2016-08-30 | 22.6 | 0 | 4.6 | 0.41 | 2.45
2025-08-30 | 16.7 | 1.3 | 0 | 2024-08-30 | 21.3 | 0 | 3.3 | 2023-08-30 | 14.7 | 3.3 | 0 | 2022-08-30 | 18.7 | 0 | 0.7 | 2021-08-30 | 22.5 | 0 | 4.5 | 2020-08-30 | 15.6 | 2.4 | 0 | 2019-08-30 | 17.6 | 0.4 | 0 | 2018-08-30 | 17.6 | 0.4 | 0 | 2017-08-30 | 20.1 | 0 | 2.1 | 2016-08-30 | 21.1 | 0 | 3.1 | 0.78 | 1.37
2025-08-30 | 12.3 | 5.7 | 0 | 2024-08-30 | 20.9 | 0 | 2.9 | 2023-08-30 | 13.9 | 4.1 | 0 | 2022-08-30 | 19 | 0 | 1 | 2021-08-30 | 21.1 | 0 | 3.1 | 2020-08-30 | 15 | 3 | 0 | 2019-08-30 | 15.7 | 2.3 | 0 | 2018-08-30 | 16.3 | 1.7 | 0 | 2017-08-30 | 19.1 | 0 | 1.1 | 2016-08-30 | 20.6 | 0 | 2.6 | 1.68 | 1.07
2025-08-30 | 13.9 | 4.1 | 0 | 2024-08-30 | 20.4 | 0 | 2.4 | 2023-08-30 | 13 | 5 | 0 | 2022-08-30 | 19.1 | 0 | 1.1 | 2021-08-30 | 21.1 | 0 | 3.1 | 2020-08-30 | 13.4 | 4.6 | 0 | 2019-08-30 | 17.3 | 0.7 | 0 | 2018-08-30 | 14.5 | 3.5 | 0 | 2017-08-30 | 18.7 | 0 | 0.7 | 2016-08-30 | 20.3 | 0 | 2.3 | 1.79 | 0.96
2025-08-30 | 13 | 5 | 0 | 2024-08-30 | 19.9 | 0 | 1.9 | 2023-08-30 | 11.9 | 6.1 | 0 | 2022-08-30 | 19 | 0 | 1 | 2021-08-30 | 20.7 | 0 | 2.7 | 2020-08-30 | 12.2 | 5.8 | 0 | 2019-08-30 | 17.2 | 0.8 | 0 | 2018-08-30 | 14.4 | 3.6 | 0 | 2017-08-30 | 18 | 0 | 0 | 2016-08-30 | 20.4 | 0 | 2.4 | 2.13 | 0.8
2025-08-30 | 12 | 6 | 0 | 2024-08-30 | 18.9 | 0 | 0.9 | 2023-08-30 | 10.8 | 7.2 | 0 | 2022-08-30 | 18.9 | 0 | 0.9 | 2021-08-30 | 19.4 | 0 | 1.4 | 2020-08-30 | 12.4 | 5.6 | 0 | 2019-08-30 | 14.9 | 3.1 | 0 | 2018-08-30 | 12.1 | 5.9 | 0 | 2017-08-30 | 17 | 1 | 0 | 2016-08-30 | 20.2 | 0 | 2.2 | 2.88 | 0.54
2025-08-31 | 11.4 | 6.6 | 0 | 2024-08-31 | 18.5 | 0 | 0.5 | 2023-08-31 | 10.3 | 7.7 | 0 | 2022-08-31 | 18.8 | 0 | 0.8 | 2021-08-31 | 19.1 | 0 | 1.1 | 2020-08-31 | 13.4 | 4.6 | 0 | 2019-08-31 | 12.8 | 5.2 | 0 | 2018-08-31 | 12.2 | 5.8 | 0 | 2017-08-31 | 15.8 | 2.2 | 0 | 2016-08-31 | 19 | 0 | 1 | 3.21 | 0.34
2025-08-31 | 11.6 | 6.4 | 0 | 2024-08-31 | 18.5 | 0 | 0.5 | 2023-08-31 | 11.3 | 6.7 | 0 | 2022-08-31 | 18.5 | 0 | 0.5 | 2021-08-31 | 16.9 | 1.1 | 0 | 2020-08-31 | 12.4 | 5.6 | 0 | 2019-08-31 | 13.3 | 4.7 | 0 | 2018-08-31 | 11.6 | 6.4 | 0 | 2017-08-31 | 14.9 | 3.1 | 0 | 2016-08-31 | 18.9 | 0 | 0.9 | 3.4 | 0.19
2025-08-31 | 9.7 | 8.3 | 0 | 2024-08-31 | 17.8 | 0.2 | 0 | 2023-08-31 | 9.9 | 8.1 | 0 | 2022-08-31 | 17.7 | 0.3 | 0 | 2021-08-31 | 16.7 | 1.3 | 0 | 2020-08-31 | 10.7 | 7.3 | 0 | 2019-08-31 | 12.7 | 5.3 | 0 | 2018-08-31 | 12 | 6 | 0 | 2017-08-31 | 15 | 3 | 0 | 2016-08-31 | 19.4 | 0 | 1.4 | 3.98 | 0.14
2025-08-31 | 9.4 | 8.6 | 0 | 2024-08-31 | 17.7 | 0.3 | 0 | 2023-08-31 | 10.7 | 7.3 | 0 | 2022-08-31 | 16.9 | 1.1 | 0 | 2021-08-31 | 15.7 | 2.3 | 0 | 2020-08-31 | 9.7 | 8.3 | 0 | 2019-08-31 | 12 | 6 | 0 | 2018-08-31 | 10.7 | 7.3 | 0 | 2017-08-31 | 15 | 3 | 0 | 2016-08-31 | 18.6 | 0 | 0.6 | 4.42 | 0.06
2025-08-31 | 10.9 | 7.1 | 0 | 2024-08-31 | 17.6 | 0.4 | 0 | 2023-08-31 | 8.8 | 9.2 | 0 | 2022-08-31 | 16.4 | 1.6 | 0 | 2021-08-31 | 15.6 | 2.4 | 0 | 2020-08-31 | 10.5 | 7.5 | 0 | 2019-08-31 | 11.3 | 6.7 | 0 | 2018-08-31 | 10.4 | 7.6 | 0 | 2017-08-31 | 14.2 | 3.8 | 0 | 2016-08-31 | 17.8 | 0.2 | 0 | 4.65 | 0
2025-08-31 | 10.6 | 7.4 | 0 | 2024-08-31 | 18 | 0 | 0 | 2023-08-31 | 8.7 | 9.3 | 0 | 2022-08-31 | 15.4 | 2.6 | 0 | 2021-08-31 | 14.9 | 3.1 | 0 | 2020-08-31 | 10.1 | 7.9 | 0 | 2019-08-31 | 10.6 | 7.4 | 0 | 2018-08-31 | 10.2 | 7.8 | 0 | 2017-08-31 | 14.3 | 3.7 | 0 | 2016-08-31 | 17.4 | 0.6 | 0 | 4.98 | 0
2025-08-31 | 10.4 | 7.6 | 0 | 2024-08-31 | 18.2 | 0 | 0.2 | 2023-08-31 | 7.1 | 10.9 | 0 | 2022-08-31 | 14.7 | 3.3 | 0 | 2021-08-31 | 15.4 | 2.6 | 0 | 2020-08-31 | 10.3 | 7.7 | 0 | 2019-08-31 | 12.4 | 5.6 | 0 | 2018-08-31 | 10.1 | 7.9 | 0 | 2017-08-31 | 13.9 | 4.1 | 0 | 2016-08-31 | 18.3 | 0 | 0.3 | 4.97 | 0.05
2025-08-31 | 13.1 | 4.9 | 0 | 2024-08-31 | 18.7 | 0 | 0.7 | 2023-08-31 | 11.3 | 6.7 | 0 | 2022-08-31 | 15.8 | 2.2 | 0 | 2021-08-31 | 18.1 | 0 | 0.1 | 2020-08-31 | 12.3 | 5.7 | 0 | 2019-08-31 | 14.4 | 3.6 | 0 | 2018-08-31 | 11.7 | 6.3 | 0 | 2017-08-31 | 13.2 | 4.8 | 0 | 2016-08-31 | 19.2 | 0 | 1.2 | 3.42 | 0.2
2025-08-31 | 15.6 | 2.4 | 0 | 2024-08-31 | 19.4 | 0 | 1.4 | 2023-08-31 | 13.9 | 4.1 | 0 | 2022-08-31 | 16.7 | 1.3 | 0 | 2021-08-31 | 19.4 | 0 | 1.4 | 2020-08-31 | 15.2 | 2.8 | 0 | 2019-08-31 | 15.3 | 2.7 | 0 | 2018-08-31 | 14 | 4 | 0 | 2017-08-31 | 12.7 | 5.3 | 0 | 2016-08-31 | 20.9 | 0 | 2.9 | 2.26 | 0.57
2025-08-31 | 18 | 0 | 0 | 2024-08-31 | 20 | 0 | 2 | 2023-08-31 | 15.1 | 2.9 | 0 | 2022-08-31 | 18.4 | 0 | 0.4 | 2021-08-31 | 20.7 | 0 | 2.7 | 2020-08-31 | 16.9 | 1.1 | 0 | 2019-08-31 | 15.9 | 2.1 | 0 | 2018-08-31 | 16 | 2 | 0 | 2017-08-31 | 12.9 | 5.1 | 0 | 2016-08-31 | 21.6 | 0 | 3.6 | 1.32 | 0.87
2025-08-31 | 20.6 | 0 | 2.6 | 2024-08-31 | 20.8 | 0 | 2.8 | 2023-08-31 | 16.1 | 1.9 | 0 | 2022-08-31 | 19.8 | 0 | 1.8 | 2021-08-31 | 21.8 | 0 | 3.8 | 2020-08-31 | 18.4 | 0 | 0.4 | 2019-08-31 | 16.8 | 1.2 | 0 | 2018-08-31 | 18.1 | 0 | 0.1 | 2017-08-31 | 12.9 | 5.1 | 0 | 2016-08-31 | 22.4 | 0 | 4.4 | 0.82 | 1.59
2025-08-31 | 22.7 | 0 | 4.7 | 2024-08-31 | 20.9 | 0 | 2.9 | 2023-08-31 | 18.1 | 0 | 0.1 | 2022-08-31 | 20.6 | 0 | 2.6 | 2021-08-31 | 22.8 | 0 | 4.8 | 2020-08-31 | 19.1 | 0 | 1.1 | 2019-08-31 | 18.8 | 0 | 0.8 | 2018-08-31 | 19.3 | 0 | 1.3 | 2017-08-31 | 13 | 5 | 0 | 2016-08-31 | 24.1 | 0 | 6.1 | 0.5 | 2.44
2025-08-31 | 23.6 | 0 | 5.6 | 2024-08-31 | 21.1 | 0 | 3.1 | 2023-08-31 | 18.8 | 0 | 0.8 | 2022-08-31 | 21.4 | 0 | 3.4 | 2021-08-31 | 23.4 | 0 | 5.4 | 2020-08-31 | 20.5 | 0 | 2.5 | 2019-08-31 | 20.1 | 0 | 2.1 | 2018-08-31 | 20.6 | 0 | 2.6 | 2017-08-31 | 13.6 | 4.4 | 0 | 2016-08-31 | 25.6 | 0 | 7.6 | 0.44 | 3.31
2025-08-31 | 24.2 | 0 | 6.2 | 2024-08-31 | 22.4 | 0 | 4.4 | 2023-08-31 | 19.2 | 0 | 1.2 | 2022-08-31 | 22.3 | 0 | 4.3 | 2021-08-31 | 24.2 | 0 | 6.2 | 2020-08-31 | 20.4 | 0 | 2.4 | 2019-08-31 | 18.9 | 0 | 0.9 | 2018-08-31 | 21.9 | 0 | 3.9 | 2017-08-31 | 14.3 | 3.7 | 0 | 2016-08-31 | 25.6 | 0 | 7.6 | 0.37 | 3.71
2025-08-31 | 24.4 | 0 | 6.4 | 2024-08-31 | 22.6 | 0 | 4.6 | 2023-08-31 | 20.7 | 0 | 2.7 | 2022-08-31 | 19.9 | 0 | 1.9 | 2021-08-31 | 24.4 | 0 | 6.4 | 2020-08-31 | 20.9 | 0 | 2.9 | 2019-08-31 | 20.6 | 0 | 2.6 | 2018-08-31 | 23 | 0 | 5 | 2017-08-31 | 13.1 | 4.9 | 0 | 2016-08-31 | 27.1 | 0 | 9.1 | 0.49 | 4.16
2025-08-31 | 25.3 | 0 | 7.3 | 2024-08-31 | 23.9 | 0 | 5.9 | 2023-08-31 | 20.9 | 0 | 2.9 | 2022-08-31 | 20 | 0 | 2 | 2021-08-31 | 24.6 | 0 | 6.6 | 2020-08-31 | 21.5 | 0 | 3.5 | 2019-08-31 | 19.3 | 0 | 1.3 | 2018-08-31 | 22.5 | 0 | 4.5 | 2017-08-31 | 14.7 | 3.3 | 0 | 2016-08-31 | 25.3 | 0 | 7.3 | 0.33 | 4.13
2025-08-31 | 25.2 | 0 | 7.2 | 2024-08-31 | 22.9 | 0 | 4.9 | 2023-08-31 | 21.5 | 0 | 3.5 | 2022-08-31 | 21.3 | 0 | 3.3 | 2021-08-31 | 24.3 | 0 | 6.3 | 2020-08-31 | 20.8 | 0 | 2.8 | 2019-08-31 | 19.1 | 0 | 1.1 | 2018-08-31 | 22.7 | 0 | 4.7 | 2017-08-31 | 14.3 | 3.7 | 0 | 2016-08-31 | 25.4 | 0 | 7.4 | 0.37 | 4.12
2025-08-31 | 24.7 | 0 | 6.7 | 2024-08-31 | 22.6 | 0 | 4.6 | 2023-08-31 | 21.1 | 0 | 3.1 | 2022-08-31 | 16.5 | 1.5 | 0 | 2021-08-31 | 23.8 | 0 | 5.8 | 2020-08-31 | 20.5 | 0 | 2.5 | 2019-08-31 | 19.4 | 0 | 1.4 | 2018-08-31 | 22.3 | 0 | 4.3 | 2017-08-31 | 13.9 | 4.1 | 0 | 2016-08-31 | 24.6 | 0 | 6.6 | 0.56 | 3.5
2025-08-31 | 23.6 | 0 | 5.6 | 2024-08-31 | 22.6 | 0 | 4.6 | 2023-08-31 | 20.1 | 0 | 2.1 | 2022-08-31 | 16.1 | 1.9 | 0 | 2021-08-31 | 22.6 | 0 | 4.6 | 2020-08-31 | 18.2 | 0 | 0.2 | 2019-08-31 | 17.9 | 0.1 | 0 | 2018-08-31 | 20.6 | 0 | 2.6 | 2017-08-31 | 12.9 | 5.1 | 0 | 2016-08-31 | 23.6 | 0 | 5.6 | 0.71 | 2.53
2025-08-31 | 19.3 | 0 | 1.3 | 2024-08-31 | 21.5 | 0 | 3.5 | 2023-08-31 | 15 | 3 | 0 | 2022-08-31 | 15.8 | 2.2 | 0 | 2021-08-31 | 21.2 | 0 | 3.2 | 2020-08-31 | 16.7 | 1.3 | 0 | 2019-08-31 | 15.1 | 2.9 | 0 | 2018-08-31 | 19.3 | 0 | 1.3 | 2017-08-31 | 11.5 | 6.5 | 0 | 2016-08-31 | 22.1 | 0 | 4.1 | 1.59 | 1.34
2025-08-31 | 17.5 | 0.5 | 0 | 2024-08-31 | 19.8 | 0 | 1.8 | 2023-08-31 | 16.4 | 1.6 | 0 | 2022-08-31 | 15.6 | 2.4 | 0 | 2021-08-31 | 19.5 | 0 | 1.5 | 2020-08-31 | 14 | 4 | 0 | 2019-08-31 | 13.3 | 4.7 | 0 | 2018-08-31 | 19.1 | 0 | 1.1 | 2017-08-31 | 9.1 | 8.9 | 0 | 2016-08-31 | 21 | 0 | 3 | 2.21 | 0.74
2025-08-31 | 17.3 | 0.7 | 0 | 2024-08-31 | 19.1 | 0 | 1.1 | 2023-08-31 | 15.1 | 2.9 | 0 | 2022-08-31 | 14.4 | 3.6 | 0 | 2021-08-31 | 18.8 | 0 | 0.8 | 2020-08-31 | 14.8 | 3.2 | 0 | 2019-08-31 | 12.5 | 5.5 | 0 | 2018-08-31 | 18.1 | 0 | 0.1 | 2017-08-31 | 10.6 | 7.4 | 0 | 2016-08-31 | 20.6 | 0 | 2.6 | 2.33 | 0.46
2025-08-31 | 14.8 | 3.2 | 0 | 2024-08-31 | 18.2 | 0 | 0.2 | 2023-08-31 | 12.5 | 5.5 | 0 | 2022-08-31 | 13.7 | 4.3 | 0 | 2021-08-31 | 16.4 | 1.6 | 0 | 2020-08-31 | 14.5 | 3.5 | 0 | 2019-08-31 | 12.1 | 5.9 | 0 | 2018-08-31 | 17.2 | 0.8 | 0 | 2017-08-31 | 9.7 | 8.3 | 0 | 2016-08-31 | 18.5 | 0 | 0.5 | 3.31 | 0.07
2025-08-31 | 14.2 | 3.8 | 0 | 2024-08-31 | 17.8 | 0.2 | 0 | 2023-08-31 | 11.3 | 6.7 | 0 | 2022-08-31 | 15.3 | 2.7 | 0 | 2021-08-31 | 16.3 | 1.7 | 0 | 2020-08-31 | 15.3 | 2.7 | 0 | 2019-08-31 | 13 | 5 | 0 | 2018-08-31 | 16.5 | 1.5 | 0 | 2017-08-31 | 8.4 | 9.6 | 0 | 2016-08-31 | 17.4 | 0.6 | 0 | 3.45 | 0
2025-09-01 | 13.6 | 4.4 | 0 | 2024-09-01 | 17.4 | 0.6 | 0 | 2023-09-01 | 11.5 | 6.5 | 0 | 2022-09-01 | 13.4 | 4.6 | 0 | 2021-09-01 | 16.6 | 1.4 | 0 | 2020-09-01 | 14.7 | 3.3 | 0 | 2019-09-01 | 11.2 | 6.8 | 0 | 2018-09-01 | 17.9 | 0.1 | 0 | 2017-09-01 | 7.8 | 10.2 | 0 | 2016-09-01 | 15.8 | 2.2 | 0 | 4.01 | 0
2025-09-01 | 12.9 | 5.1 | 0 | 2024-09-01 | 16.5 | 1.5 | 0 | 2023-09-01 | 11.3 | 6.7 | 0 | 2022-09-01 | 13.1 | 4.9 | 0 | 2021-09-01 | 16.7 | 1.3 | 0 | 2020-09-01 | 13.8 | 4.2 | 0 | 2019-09-01 | 10.3 | 7.7 | 0 | 2018-09-01 | 18.4 | 0 | 0.4 | 2017-09-01 | 5.6 | 12.4 | 0 | 2016-09-01 | 14.6 | 3.4 | 0 | 4.72 | 0.04
2025-09-01 | 12.5 | 5.5 | 0 | 2024-09-01 | 15.8 | 2.2 | 0 | 2023-09-01 | 10 | 8 | 0 | 2022-09-01 | 13.1 | 4.9 | 0 | 2021-09-01 | 14.7 | 3.3 | 0 | 2020-09-01 | 12.7 | 5.3 | 0 | 2019-09-01 | 9.7 | 8.3 | 0 | 2018-09-01 | 18.6 | 0 | 0.6 | 2017-09-01 | 6.9 | 11.1 | 0 | 2016-09-01 | 14.9 | 3.1 | 0 | 5.17 | 0.06
2025-09-01 | 12.4 | 5.6 | 0 | 2024-09-01 | 15.3 | 2.7 | 0 | 2023-09-01 | 11.1 | 6.9 | 0 | 2022-09-01 | 12.3 | 5.7 | 0 | 2021-09-01 | 13.4 | 4.6 | 0 | 2020-09-01 | 12.7 | 5.3 | 0 | 2019-09-01 | 9 | 9 | 0 | 2018-09-01 | 18.7 | 0 | 0.7 | 2017-09-01 | 6.2 | 11.8 | 0 | 2016-09-01 | 13.7 | 4.3 | 0 | 5.59 | 0.07
2025-09-01 | 10.7 | 7.3 | 0 | 2024-09-01 | 14.4 | 3.6 | 0 | 2023-09-01 | 8.5 | 9.5 | 0 | 2022-09-01 | 11.5 | 6.5 | 0 | 2021-09-01 | 14.9 | 3.1 | 0 | 2020-09-01 | 12.7 | 5.3 | 0 | 2019-09-01 | 10.1 | 7.9 | 0 | 2018-09-01 | 18.7 | 0 | 0.7 | 2017-09-01 | 7 | 11 | 0 | 2016-09-01 | 13.5 | 4.5 | 0 | 5.87 | 0.07
2025-09-01 | 11.4 | 6.6 | 0 | 2024-09-01 | 14 | 4 | 0 | 2023-09-01 | 10.7 | 7.3 | 0 | 2022-09-01 | 10.9 | 7.1 | 0 | 2021-09-01 | 14.9 | 3.1 | 0 | 2020-09-01 | 13 | 5 | 0 | 2019-09-01 | 9.4 | 8.6 | 0 | 2018-09-01 | 18.3 | 0 | 0.3 | 2017-09-01 | 4.8 | 13.2 | 0 | 2016-09-01 | 12.4 | 5.6 | 0 | 6.05 | 0.03
2025-09-01 | 11.2 | 6.8 | 0 | 2024-09-01 | 14.1 | 3.9 | 0 | 2023-09-01 | 9.7 | 8.3 | 0 | 2022-09-01 | 11 | 7 | 0 | 2021-09-01 | 14.8 | 3.2 | 0 | 2020-09-01 | 13.4 | 4.6 | 0 | 2019-09-01 | 9.6 | 8.4 | 0 | 2018-09-01 | 18.2 | 0 | 0.2 | 2017-09-01 | 5.7 | 12.3 | 0 | 2016-09-01 | 12.8 | 5.2 | 0 | 5.97 | 0.02
2025-09-01 | 16 | 2 | 0 | 2024-09-01 | 16.2 | 1.8 | 0 | 2023-09-01 | 13.7 | 4.3 | 0 | 2022-09-01 | 10.4 | 7.6 | 0 | 2021-09-01 | 16 | 2 | 0 | 2020-09-01 | 15.3 | 2.7 | 0 | 2019-09-01 | 11.9 | 6.1 | 0 | 2018-09-01 | 19.4 | 0 | 1.4 | 2017-09-01 | 8 | 10 | 0 | 2016-09-01 | 15.8 | 2.2 | 0 | 3.87 | 0.14
2025-09-01 | 18.8 | 0 | 0.8 | 2024-09-01 | 18.5 | 0 | 0.5 | 2023-09-01 | 16.6 | 1.4 | 0 | 2022-09-01 | 11.8 | 6.2 | 0 | 2021-09-01 | 17.1 | 0.9 | 0 | 2020-09-01 | 17.4 | 0.6 | 0 | 2019-09-01 | 14.4 | 3.6 | 0 | 2018-09-01 | 21.7 | 0 | 3.7 | 2017-09-01 | 9.5 | 8.5 | 0 | 2016-09-01 | 17 | 1 | 0 | 2.22 | 0.5
2025-09-01 | 21.5 | 0 | 3.5 | 2024-09-01 | 21.3 | 0 | 3.3 | 2023-09-01 | 18.9 | 0 | 0.9 | 2022-09-01 | 12.7 | 5.3 | 0 | 2021-09-01 | 17.5 | 0.5 | 0 | 2020-09-01 | 21.2 | 0 | 3.2 | 2019-09-01 | 16.8 | 1.2 | 0 | 2018-09-01 | 23.4 | 0 | 5.4 | 2017-09-01 | 11.2 | 6.8 | 0 | 2016-09-01 | 17.3 | 0.7 | 0 | 1.45 | 1.63
2025-09-01 | 23.8 | 0 | 5.8 | 2024-09-01 | 22.6 | 0 | 4.6 | 2023-09-01 | 20.2 | 0 | 2.2 | 2022-09-01 | 13.3 | 4.7 | 0 | 2021-09-01 | 18.4 | 0 | 0.4 | 2020-09-01 | 22.4 | 0 | 4.4 | 2019-09-01 | 19.5 | 0 | 1.5 | 2018-09-01 | 22.4 | 0 | 4.4 | 2017-09-01 | 11.9 | 6.1 | 0 | 2016-09-01 | 19.7 | 0 | 1.7 | 1.08 | 2.5
2025-09-01 | 25.1 | 0 | 7.1 | 2024-09-01 | 23.1 | 0 | 5.1 | 2023-09-01 | 21.6 | 0 | 3.6 | 2022-09-01 | 15.1 | 2.9 | 0 | 2021-09-01 | 20.2 | 0 | 2.2 | 2020-09-01 | 22.6 | 0 | 4.6 | 2019-09-01 | 20.8 | 0 | 2.8 | 2018-09-01 | 22.7 | 0 | 4.7 | 2017-09-01 | 14 | 4 | 0 | 2016-09-01 | 19.3 | 0 | 1.3 | 0.69 | 3.14
2025-09-01 | 26.2 | 0 | 8.2 | 2024-09-01 | 22.6 | 0 | 4.6 | 2023-09-01 | 22.2 | 0 | 4.2 | 2022-09-01 | 16.4 | 1.6 | 0 | 2021-09-01 | 21.8 | 0 | 3.8 | 2020-09-01 | 22.8 | 0 | 4.8 | 2019-09-01 | 21.6 | 0 | 3.6 | 2018-09-01 | 23 | 0 | 5 | 2017-09-01 | 13.4 | 4.6 | 0 | 2016-09-01 | 20.1 | 0 | 2.1 | 0.62 | 3.63
2025-09-01 | 25.1 | 0 | 7.1 | 2024-09-01 | 24 | 0 | 6 | 2023-09-01 | 23 | 0 | 5 | 2022-09-01 | 15.8 | 2.2 | 0 | 2021-09-01 | 21.4 | 0 | 3.4 | 2020-09-01 | 22.9 | 0 | 4.9 | 2019-09-01 | 22.5 | 0 | 4.5 | 2018-09-01 | 25.5 | 0 | 7.5 | 2017-09-01 | 15.1 | 2.9 | 0 | 2016-09-01 | 20.8 | 0 | 2.8 | 0.51 | 4.12
2025-09-01 | 27.5 | 0 | 9.5 | 2024-09-01 | 22.9 | 0 | 4.9 | 2023-09-01 | 23.8 | 0 | 5.8 | 2022-09-01 | 16.1 | 1.9 | 0 | 2021-09-01 | 22.2 | 0 | 4.2 | 2020-09-01 | 24 | 0 | 6 | 2019-09-01 | 22.6 | 0 | 4.6 | 2018-09-01 | 25 | 0 | 7 | 2017-09-01 | 16.1 | 1.9 | 0 | 2016-09-01 | 20.8 | 0 | 2.8 | 0.38 | 4.48
2025-09-01 | 26.6 | 0 | 8.6 | 2024-09-01 | 23.5 | 0 | 5.5 | 2023-09-01 | 23.8 | 0 | 5.8 | 2022-09-01 | 16.4 | 1.6 | 0 | 2021-09-01 | 22.6 | 0 | 4.6 | 2020-09-01 | 24.5 | 0 | 6.5 | 2019-09-01 | 23.2 | 0 | 5.2 | 2018-09-01 | 26.6 | 0 | 8.6 | 2017-09-01 | 16.8 | 1.2 | 0 | 2016-09-01 | 22.2 | 0 | 4.2 | 0.28 | 4.9
2025-09-01 | 26.6 | 0 | 8.6 | 2024-09-01 | 23.1 | 0 | 5.1 | 2023-09-01 | 23.2 | 0 | 5.2 | 2022-09-01 | 17.5 | 0.5 | 0 | 2021-09-01 | 22.4 | 0 | 4.4 | 2020-09-01 | 22.9 | 0 | 4.9 | 2019-09-01 | 24 | 0 | 6 | 2018-09-01 | 26.4 | 0 | 8.4 | 2017-09-01 | 16.7 | 1.3 | 0 | 2016-09-01 | 22 | 0 | 4 | 0.18 | 4.66
2025-09-01 | 25.2 | 0 | 7.2 | 2024-09-01 | 21.6 | 0 | 3.6 | 2023-09-01 | 22.5 | 0 | 4.5 | 2022-09-01 | 17.5 | 0.5 | 0 | 2021-09-01 | 22.5 | 0 | 4.5 | 2020-09-01 | 22.5 | 0 | 4.5 | 2019-09-01 | 22 | 0 | 4 | 2018-09-01 | 25.4 | 0 | 7.4 | 2017-09-01 | 16.4 | 1.6 | 0 | 2016-09-01 | 22.1 | 0 | 4.1 | 0.21 | 3.98
2025-09-01 | 23.2 | 0 | 5.2 | 2024-09-01 | 19.6 | 0 | 1.6 | 2023-09-01 | 20.6 | 0 | 2.6 | 2022-09-01 | 16.1 | 1.9 | 0 | 2021-09-01 | 21.5 | 0 | 3.5 | 2020-09-01 | 21.8 | 0 | 3.8 | 2019-09-01 | 20 | 0 | 2 | 2018-09-01 | 24.2 | 0 | 6.2 | 2017-09-01 | 15 | 3 | 0 | 2016-09-01 | 20.1 | 0 | 2.1 | 0.49 | 2.7
2025-09-01 | 20.1 | 0 | 2.1 | 2024-09-01 | 18.1 | 0 | 0.1 | 2023-09-01 | 18.7 | 0 | 0.7 | 2022-09-01 | 14.3 | 3.7 | 0 | 2021-09-01 | 18.9 | 0 | 0.9 | 2020-09-01 | 20.8 | 0 | 2.8 | 2019-09-01 | 18.9 | 0 | 0.9 | 2018-09-01 | 22 | 0 | 4 | 2017-09-01 | 12.5 | 5.5 | 0 | 2016-09-01 | 19.1 | 0 | 1.1 | 0.92 | 1.26
2025-09-01 | 19.8 | 0 | 1.8 | 2024-09-01 | 16.6 | 1.4 | 0 | 2023-09-01 | 17.7 | 0.3 | 0 | 2022-09-01 | 12.9 | 5.1 | 0 | 2021-09-01 | 17.5 | 0.5 | 0 | 2020-09-01 | 21 | 0 | 3 | 2019-09-01 | 17.6 | 0.4 | 0 | 2018-09-01 | 22 | 0 | 4 | 2017-09-01 | 11.1 | 6.9 | 0 | 2016-09-01 | 18.5 | 0 | 0.5 | 1.46 | 0.93
2025-09-01 | 19.4 | 0 | 1.4 | 2024-09-01 | 15.6 | 2.4 | 0 | 2023-09-01 | 16.5 | 1.5 | 0 | 2022-09-01 | 12.6 | 5.4 | 0 | 2021-09-01 | 18.1 | 0 | 0.1 | 2020-09-01 | 20.2 | 0 | 2.2 | 2019-09-01 | 17.5 | 0.5 | 0 | 2018-09-01 | 21.7 | 0 | 3.7 | 2017-09-01 | 10.1 | 7.9 | 0 | 2016-09-01 | 18.6 | 0 | 0.6 | 1.77 | 0.8
2025-09-01 | 18.7 | 0 | 0.7 | 2024-09-01 | 14.1 | 3.9 | 0 | 2023-09-01 | 16.1 | 1.9 | 0 | 2022-09-01 | 10.9 | 7.1 | 0 | 2021-09-01 | 16.7 | 1.3 | 0 | 2020-09-01 | 19.7 | 0 | 1.7 | 2019-09-01 | 17 | 1 | 0 | 2018-09-01 | 21.6 | 0 | 3.6 | 2017-09-01 | 8.9 | 9.1 | 0 | 2016-09-01 | 17.8 | 0.2 | 0 | 2.45 | 0.6
2025-09-01 | 17.2 | 0.8 | 0 | 2024-09-01 | 12.8 | 5.2 | 0 | 2023-09-01 | 15 | 3 | 0 | 2022-09-01 | 11.7 | 6.3 | 0 | 2021-09-01 | 15.7 | 2.3 | 0 | 2020-09-01 | 19.4 | 0 | 1.4 | 2019-09-01 | 16.5 | 1.5 | 0 | 2018-09-01 | 21.3 | 0 | 3.3 | 2017-09-01 | 7.5 | 10.5 | 0 | 2016-09-01 | 17.1 | 0.9 | 0 | 3.05 | 0.47
2025-09-02 | 18.7 | 0 | 0.7 | 2024-09-02 | 11.2 | 6.8 | 0 | 2023-09-02 | 14.3 | 3.7 | 0 | 2022-09-02 | 10.1 | 7.9 | 0 | 2021-09-02 | 14.7 | 3.3 | 0 | 2020-09-02 | 19.2 | 0 | 1.2 | 2019-09-02 | 15.8 | 2.2 | 0 | 2018-09-02 | 21.1 | 0 | 3.1 | 2017-09-02 | 5.9 | 12.1 | 0 | 2016-09-02 | 16.5 | 1.5 | 0 | 3.75 | 0.5
2025-09-02 | 16.5 | 1.5 | 0 | 2024-09-02 | 10.2 | 7.8 | 0 | 2023-09-02 | 14.2 | 3.8 | 0 | 2022-09-02 | 9.7 | 8.3 | 0 | 2021-09-02 | 13.6 | 4.4 | 0 | 2020-09-02 | 19.3 | 0 | 1.3 | 2019-09-02 | 15.9 | 2.1 | 0 | 2018-09-02 | 20.8 | 0 | 2.8 | 2017-09-02 | 7.6 | 10.4 | 0 | 2016-09-02 | 16.2 | 1.8 | 0 | 4.01 | 0.41
2025-09-02 | 13.8 | 4.2 | 0 | 2024-09-02 | 9.3 | 8.7 | 0 | 2023-09-02 | 14 | 4 | 0 | 2022-09-02 | 10.3 | 7.7 | 0 | 2021-09-02 | 12.8 | 5.2 | 0 | 2020-09-02 | 19.8 | 0 | 1.8 | 2019-09-02 | 15.9 | 2.1 | 0 | 2018-09-02 | 20.8 | 0 | 2.8 | 2017-09-02 | 6.7 | 11.3 | 0 | 2016-09-02 | 15 | 3 | 0 | 4.62 | 0.46
2025-09-02 | 13.9 | 4.1 | 0 | 2024-09-02 | 9.9 | 8.1 | 0 | 2023-09-02 | 13 | 5 | 0 | 2022-09-02 | 9.3 | 8.7 | 0 | 2021-09-02 | 12.5 | 5.5 | 0 | 2020-09-02 | 20.3 | 0 | 2.3 | 2019-09-02 | 15.9 | 2.1 | 0 | 2018-09-02 | 20.3 | 0 | 2.3 | 2017-09-02 | 6.2 | 11.8 | 0 | 2016-09-02 | 14.1 | 3.9 | 0 | 4.92 | 0.46
2025-09-02 | 15 | 3 | 0 | 2024-09-02 | 11.2 | 6.8 | 0 | 2023-09-02 | 11.8 | 6.2 | 0 | 2022-09-02 | 9.3 | 8.7 | 0 | 2021-09-02 | 11.9 | 6.1 | 0 | 2020-09-02 | 20.3 | 0 | 2.3 | 2019-09-02 | 16.2 | 1.8 | 0 | 2018-09-02 | 19.9 | 0 | 1.9 | 2017-09-02 | 4.4 | 13.6 | 0 | 2016-09-02 | 13.8 | 4.2 | 0 | 5.04 | 0.42
2025-09-02 | 14.4 | 3.6 | 0 | 2024-09-02 | 10.7 | 7.3 | 0 | 2023-09-02 | 12.6 | 5.4 | 0 | 2022-09-02 | 9.6 | 8.4 | 0 | 2021-09-02 | 11.7 | 6.3 | 0 | 2020-09-02 | 19.8 | 0 | 1.8 | 2019-09-02 | 16.1 | 1.9 | 0 | 2018-09-02 | 19.4 | 0 | 1.4 | 2017-09-02 | 5.7 | 12.3 | 0 | 2016-09-02 | 13.4 | 4.6 | 0 | 4.98 | 0.32
2025-09-02 | 13.3 | 4.7 | 0 | 2024-09-02 | 10.2 | 7.8 | 0 | 2023-09-02 | 12.8 | 5.2 | 0 | 2022-09-02 | 10 | 8 | 0 | 2021-09-02 | 11.9 | 6.1 | 0 | 2020-09-02 | 19.8 | 0 | 1.8 | 2019-09-02 | 16 | 2 | 0 | 2018-09-02 | 19.7 | 0 | 1.7 | 2017-09-02 | 6.3 | 11.7 | 0 | 2016-09-02 | 13.5 | 4.5 | 0 | 5 | 0.35
2025-09-02 | 15.3 | 2.7 | 0 | 2024-09-02 | 11.6 | 6.4 | 0 | 2023-09-02 | 14.7 | 3.3 | 0 | 2022-09-02 | 11.6 | 6.4 | 0 | 2021-09-02 | 12.9 | 5.1 | 0 | 2020-09-02 | 20.1 | 0 | 2.1 | 2019-09-02 | 16.1 | 1.9 | 0 | 2018-09-02 | 20.6 | 0 | 2.6 | 2017-09-02 | 7.1 | 10.9 | 0 | 2016-09-02 | 14.5 | 3.5 | 0 | 4.02 | 0.47
2025-09-02 | 16.7 | 1.3 | 0 | 2024-09-02 | 12.7 | 5.3 | 0 | 2023-09-02 | 17.1 | 0.9 | 0 | 2022-09-02 | 15.3 | 2.7 | 0 | 2021-09-02 | 13.4 | 4.6 | 0 | 2020-09-02 | 20.3 | 0 | 2.3 | 2019-09-02 | 16.5 | 1.5 | 0 | 2018-09-02 | 21.6 | 0 | 3.6 | 2017-09-02 | 12.1 | 5.9 | 0 | 2016-09-02 | 16 | 2 | 0 | 2.42 | 0.59
2025-09-02 | 19.4 | 0 | 1.4 | 2024-09-02 | 13.3 | 4.7 | 0 | 2023-09-02 | 19 | 0 | 1 | 2022-09-02 | 18.5 | 0 | 0.5 | 2021-09-02 | 14.4 | 3.6 | 0 | 2020-09-02 | 20.8 | 0 | 2.8 | 2019-09-02 | 17.4 | 0.6 | 0 | 2018-09-02 | 22.5 | 0 | 4.5 | 2017-09-02 | 14.7 | 3.3 | 0 | 2016-09-02 | 17.2 | 0.8 | 0 | 1.3 | 1.02
2025-09-02 | 21.9 | 0 | 3.9 | 2024-09-02 | 13.5 | 4.5 | 0 | 2023-09-02 | 20.3 | 0 | 2.3 | 2022-09-02 | 20.2 | 0 | 2.2 | 2021-09-02 | 15.6 | 2.4 | 0 | 2020-09-02 | 21.5 | 0 | 3.5 | 2019-09-02 | 18.4 | 0 | 0.4 | 2018-09-02 | 23.2 | 0 | 5.2 | 2017-09-02 | 15.6 | 2.4 | 0 | 2016-09-02 | 18.1 | 0 | 0.1 | 0.93 | 1.76
2025-09-02 | 23.6 | 0 | 5.6 | 2024-09-02 | 14.5 | 3.5 | 0 | 2023-09-02 | 22.4 | 0 | 4.4 | 2022-09-02 | 21.8 | 0 | 3.8 | 2021-09-02 | 16.6 | 1.4 | 0 | 2020-09-02 | 22.9 | 0 | 4.9 | 2019-09-02 | 19.8 | 0 | 1.8 | 2018-09-02 | 23.8 | 0 | 5.8 | 2017-09-02 | 16.9 | 1.1 | 0 | 2016-09-02 | 18.8 | 0 | 0.8 | 0.6 | 2.71
2025-09-02 | 24.6 | 0 | 6.6 | 2024-09-02 | 14.8 | 3.2 | 0 | 2023-09-02 | 22.6 | 0 | 4.6 | 2022-09-02 | 23.6 | 0 | 5.6 | 2021-09-02 | 15.7 | 2.3 | 0 | 2020-09-02 | 23.8 | 0 | 5.8 | 2019-09-02 | 21.3 | 0 | 3.3 | 2018-09-02 | 24.9 | 0 | 6.9 | 2017-09-02 | 18.4 | 0 | 0.4 | 2016-09-02 | 18.8 | 0 | 0.8 | 0.55 | 3.4
2025-09-02 | 25.3 | 0 | 7.3 | 2024-09-02 | 16.8 | 1.2 | 0 | 2023-09-02 | 24.5 | 0 | 6.5 | 2022-09-02 | 24.8 | 0 | 6.8 | 2021-09-02 | 16.3 | 1.7 | 0 | 2020-09-02 | 23.9 | 0 | 5.9 | 2019-09-02 | 22 | 0 | 4 | 2018-09-02 | 24.9 | 0 | 6.9 | 2017-09-02 | 19 | 0 | 1 | 2016-09-02 | 19.5 | 0 | 1.5 | 0.29 | 3.99
2025-09-02 | 24.9 | 0 | 6.9 | 2024-09-02 | 17.9 | 0.1 | 0 | 2023-09-02 | 24.3 | 0 | 6.3 | 2022-09-02 | 25.1 | 0 | 7.1 | 2021-09-02 | 16.8 | 1.2 | 0 | 2020-09-02 | 25.7 | 0 | 7.7 | 2019-09-02 | 22.8 | 0 | 4.8 | 2018-09-02 | 26.3 | 0 | 8.3 | 2017-09-02 | 19.8 | 0 | 1.8 | 2016-09-02 | 19.8 | 0 | 1.8 | 0.13 | 4.47
2025-09-02 | 25.8 | 0 | 7.8 | 2024-09-02 | 18.4 | 0 | 0.4 | 2023-09-02 | 24.2 | 0 | 6.2 | 2022-09-02 | 25.2 | 0 | 7.2 | 2021-09-02 | 16.9 | 1.1 | 0 | 2020-09-02 | 26.1 | 0 | 8.1 | 2019-09-02 | 24 | 0 | 6 | 2018-09-02 | 25.6 | 0 | 7.6 | 2017-09-02 | 20.1 | 0 | 2.1 | 2016-09-02 | 19.8 | 0 | 1.8 | 0.11 | 4.72
2025-09-02 | 25.6 | 0 | 7.6 | 2024-09-02 | 18.8 | 0 | 0.8 | 2023-09-02 | 23 | 0 | 5 | 2022-09-02 | 25 | 0 | 7 | 2021-09-02 | 17.4 | 0.6 | 0 | 2020-09-02 | 25 | 0 | 7 | 2019-09-02 | 23.3 | 0 | 5.3 | 2018-09-02 | 25.8 | 0 | 7.8 | 2017-09-02 | 19.6 | 0 | 1.6 | 2016-09-02 | 19.9 | 0 | 1.9 | 0.06 | 4.4
2025-09-02 | 23.5 | 0 | 5.5 | 2024-09-02 | 17.7 | 0.3 | 0 | 2023-09-02 | 23.4 | 0 | 5.4 | 2022-09-02 | 24.4 | 0 | 6.4 | 2021-09-02 | 17.1 | 0.9 | 0 | 2020-09-02 | 19.5 | 0 | 1.5 | 2019-09-02 | 22.4 | 0 | 4.4 | 2018-09-02 | 25.8 | 0 | 7.8 | 2017-09-02 | 19.1 | 0 | 1.1 | 2016-09-02 | 19.3 | 0 | 1.3 | 0.12 | 3.34
2025-09-02 | 22.8 | 0 | 4.8 | 2024-09-02 | 16.6 | 1.4 | 0 | 2023-09-02 | 21.9 | 0 | 3.9 | 2022-09-02 | 22.5 | 0 | 4.5 | 2021-09-02 | 17 | 1 | 0 | 2020-09-02 | 20.4 | 0 | 2.4 | 2019-09-02 | 20.8 | 0 | 2.8 | 2018-09-02 | 25.3 | 0 | 7.3 | 2017-09-02 | 16.4 | 1.6 | 0 | 2016-09-02 | 18 | 0 | 0 | 0.4 | 2.57
2025-09-02 | 17.8 | 0.2 | 0 | 2024-09-02 | 14.8 | 3.2 | 0 | 2023-09-02 | 21 | 0 | 3 | 2022-09-02 | 20.6 | 0 | 2.6 | 2021-09-02 | 17 | 1 | 0 | 2020-09-02 | 20.3 | 0 | 2.3 | 2019-09-02 | 18 | 0 | 0 | 2018-09-02 | 24.3 | 0 | 6.3 | 2017-09-02 | 14.6 | 3.4 | 0 | 2016-09-02 | 16.7 | 1.3 | 0 | 0.91 | 1.42
2025-09-02 | 18.7 | 0 | 0.7 | 2024-09-02 | 12.3 | 5.7 | 0 | 2023-09-02 | 20.3 | 0 | 2.3 | 2022-09-02 | 19.6 | 0 | 1.6 | 2021-09-02 | 16.4 | 1.6 | 0 | 2020-09-02 | 18.6 | 0 | 0.6 | 2019-09-02 | 17.3 | 0.7 | 0 | 2018-09-02 | 23.3 | 0 | 5.3 | 2017-09-02 | 13.6 | 4.4 | 0 | 2016-09-02 | 16 | 2 | 0 | 1.44 | 1.05
2025-09-02 | 15.5 | 2.5 | 0 | 2024-09-02 | 9.9 | 8.1 | 0 | 2023-09-02 | 19.6 | 0 | 1.6 | 2022-09-02 | 18.5 | 0 | 0.5 | 2021-09-02 | 16.2 | 1.8 | 0 | 2020-09-02 | 18.3 | 0 | 0.3 | 2019-09-02 | 16.9 | 1.1 | 0 | 2018-09-02 | 22.7 | 0 | 4.7 | 2017-09-02 | 13.2 | 4.8 | 0 | 2016-09-02 | 15.4 | 2.6 | 0 | 2.09 | 0.71
2025-09-02 | 17.5 | 0.5 | 0 | 2024-09-02 | 9.3 | 8.7 | 0 | 2023-09-02 | 19 | 0 | 1 | 2022-09-02 | 18.1 | 0 | 0.1 | 2021-09-02 | 15.3 | 2.7 | 0 | 2020-09-02 | 17.8 | 0.2 | 0 | 2019-09-02 | 15.9 | 2.1 | 0 | 2018-09-02 | 22.7 | 0 | 4.7 | 2017-09-02 | 12.7 | 5.3 | 0 | 2016-09-02 | 13.6 | 4.4 | 0 | 2.39 | 0.58
2025-09-02 | 16.4 | 1.6 | 0 | 2024-09-02 | 8.2 | 9.8 | 0 | 2023-09-02 | 18.9 | 0 | 0.9 | 2022-09-02 | 17.2 | 0.8 | 0 | 2021-09-02 | 15.3 | 2.7 | 0 | 2020-09-02 | 16.1 | 1.9 | 0 | 2019-09-02 | 15.4 | 2.6 | 0 | 2018-09-02 | 22.5 | 0 | 4.5 | 2017-09-02 | 11.4 | 6.6 | 0 | 2016-09-02 | 11 | 7 | 0 | 3.3 | 0.54
2025-09-03 | 15.1 | 2.9 | 0 | 2024-09-03 | 8.4 | 9.6 | 0 | 2023-09-03 | 18.9 | 0 | 0.9 | 2022-09-03 | 16.4 | 1.6 | 0 | 2021-09-03 | 15.2 | 2.8 | 0 | 2020-09-03 | 15.5 | 2.5 | 0 | 2019-09-03 | 14 | 4 | 0 | 2018-09-03 | 21.9 | 0 | 3.9 | 2017-09-03 | 10.5 | 7.5 | 0 | 2016-09-03 | 10.6 | 7.4 | 0 | 3.83 | 0.48
2025-09-03 | 14.1 | 3.9 | 0 | 2024-09-03 | 8.7 | 9.3 | 0 | 2023-09-03 | 18.3 | 0 | 0.3 | 2022-09-03 | 15.7 | 2.3 | 0 | 2021-09-03 | 14.7 | 3.3 | 0 | 2020-09-03 | 15.5 | 2.5 | 0 | 2019-09-03 | 13.5 | 4.5 | 0 | 2018-09-03 | 21.6 | 0 | 3.6 | 2017-09-03 | 11.2 | 6.8 | 0 | 2016-09-03 | 12.2 | 5.8 | 0 | 3.84 | 0.39
2025-09-03 | 13.6 | 4.4 | 0 | 2024-09-03 | 8.1 | 9.9 | 0 | 2023-09-03 | 17.9 | 0.1 | 0 | 2022-09-03 | 16.9 | 1.1 | 0 | 2021-09-03 | 14.4 | 3.6 | 0 | 2020-09-03 | 14.5 | 3.5 | 0 | 2019-09-03 | 12.9 | 5.1 | 0 | 2018-09-03 | 21.5 | 0 | 3.5 | 2017-09-03 | 10.9 | 7.1 | 0 | 2016-09-03 | 9.4 | 8.6 | 0 | 4.34 | 0.35
2025-09-03 | 13.5 | 4.5 | 0 | 2024-09-03 | 7.3 | 10.7 | 0 | 2023-09-03 | 17.5 | 0.5 | 0 | 2022-09-03 | 14.3 | 3.7 | 0 | 2021-09-03 | 12.2 | 5.8 | 0 | 2020-09-03 | 14 | 4 | 0 | 2019-09-03 | 11.3 | 6.7 | 0 | 2018-09-03 | 21.1 | 0 | 3.1 | 2017-09-03 | 10.4 | 7.6 | 0 | 2016-09-03 | 10.3 | 7.7 | 0 | 5.12 | 0.31
2025-09-03 | 13.1 | 4.9 | 0 | 2024-09-03 | 6 | 12 | 0 | 2023-09-03 | 17 | 1 | 0 | 2022-09-03 | 13.5 | 4.5 | 0 | 2021-09-03 | 12.2 | 5.8 | 0 | 2020-09-03 | 12.8 | 5.2 | 0 | 2019-09-03 | 11.8 | 6.2 | 0 | 2018-09-03 | 20.8 | 0 | 2.8 | 2017-09-03 | 10.5 | 7.5 | 0 | 2016-09-03 | 9.8 | 8.2 | 0 | 5.53 | 0.28
2025-09-03 | 12.8 | 5.2 | 0 | 2024-09-03 | 6.6 | 11.4 | 0 | 2023-09-03 | 16.8 | 1.2 | 0 | 2022-09-03 | 14.1 | 3.9 | 0 | 2021-09-03 | 11.9 | 6.1 | 0 | 2020-09-03 | 12.8 | 5.2 | 0 | 2019-09-03 | 11.4 | 6.6 | 0 | 2018-09-03 | 20.7 | 0 | 2.7 | 2017-09-03 | 10.6 | 7.4 | 0 | 2016-09-03 | 7.9 | 10.1 | 0 | 5.71 | 0.27
2025-09-03 | 13.2 | 4.8 | 0 | 2024-09-03 | 7 | 11 | 0 | 2023-09-03 | 16.9 | 1.1 | 0 | 2022-09-03 | 14.7 | 3.3 | 0 | 2021-09-03 | 12.6 | 5.4 | 0 | 2020-09-03 | 12.8 | 5.2 | 0 | 2019-09-03 | 11.2 | 6.8 | 0 | 2018-09-03 | 21.5 | 0 | 3.5 | 2017-09-03 | 10.3 | 7.7 | 0 | 2016-09-03 | 8.6 | 9.4 | 0 | 5.47 | 0.35
2025-09-03 | 15 | 3 | 0 | 2024-09-03 | 9.5 | 8.5 | 0 | 2023-09-03 | 18.2 | 0 | 0.2 | 2022-09-03 | 15.8 | 2.2 | 0 | 2021-09-03 | 14.9 | 3.1 | 0 | 2020-09-03 | 14.6 | 3.4 | 0 | 2019-09-03 | 12.5 | 5.5 | 0 | 2018-09-03 | 22.7 | 0 | 4.7 | 2017-09-03 | 10.3 | 7.7 | 0 | 2016-09-03 | 12.4 | 5.6 | 0 | 3.9 | 0.49
2025-09-03 | 18.6 | 0 | 0.6 | 2024-09-03 | 13.6 | 4.4 | 0 | 2023-09-03 | 20 | 0 | 2 | 2022-09-03 | 18.1 | 0 | 0.1 | 2021-09-03 | 17.5 | 0.5 | 0 | 2020-09-03 | 16.9 | 1.1 | 0 | 2019-09-03 | 13.8 | 4.2 | 0 | 2018-09-03 | 23.1 | 0 | 5.1 | 2017-09-03 | 10.8 | 7.2 | 0 | 2016-09-03 | 15.2 | 2.8 | 0 | 2.02 | 0.78
2025-09-03 | 21.6 | 0 | 3.6 | 2024-09-03 | 15.8 | 2.2 | 0 | 2023-09-03 | 22.2 | 0 | 4.2 | 2022-09-03 | 20.1 | 0 | 2.1 | 2021-09-03 | 17.8 | 0.2 | 0 | 2020-09-03 | 18.9 | 0 | 0.9 | 2019-09-03 | 15.6 | 2.4 | 0 | 2018-09-03 | 25.6 | 0 | 7.6 | 2017-09-03 | 11.1 | 6.9 | 0 | 2016-09-03 | 17.6 | 0.4 | 0 | 1.21 | 1.84
2025-09-03 | 23.4 | 0 | 5.4 | 2024-09-03 | 17.2 | 0.8 | 0 | 2023-09-03 | 23.9 | 0 | 5.9 | 2022-09-03 | 22.4 | 0 | 4.4 | 2021-09-03 | 18.9 | 0 | 0.9 | 2020-09-03 | 20.7 | 0 | 2.7 | 2019-09-03 | 17.4 | 0.6 | 0 | 2018-09-03 | 27.3 | 0 | 9.3 | 2017-09-03 | 11.5 | 6.5 | 0 | 2016-09-03 | 18.6 | 0 | 0.6 | 0.79 | 2.92
2025-09-03 | 24.5 | 0 | 6.5 | 2024-09-03 | 19.4 | 0 | 1.4 | 2023-09-03 | 25.4 | 0 | 7.4 | 2022-09-03 | 24.4 | 0 | 6.4 | 2021-09-03 | 19.4 | 0 | 1.4 | 2020-09-03 | 21.5 | 0 | 3.5 | 2019-09-03 | 17.9 | 0.1 | 0 | 2018-09-03 | 27.4 | 0 | 9.4 | 2017-09-03 | 11.8 | 6.2 | 0 | 2016-09-03 | 20.7 | 0 | 2.7 | 0.63 | 3.87
2025-09-03 | 25.2 | 0 | 7.2 | 2024-09-03 | 21.1 | 0 | 3.1 | 2023-09-03 | 26.9 | 0 | 8.9 | 2022-09-03 | 25.9 | 0 | 7.9 | 2021-09-03 | 20.5 | 0 | 2.5 | 2020-09-03 | 22.7 | 0 | 4.7 | 2019-09-03 | 18.6 | 0 | 0.6 | 2018-09-03 | 28.3 | 0 | 10.3 | 2017-09-03 | 12.6 | 5.4 | 0 | 2016-09-03 | 20.9 | 0 | 2.9 | 0.54 | 4.81
2025-09-03 | 26.1 | 0 | 8.1 | 2024-09-03 | 22 | 0 | 4 | 2023-09-03 | 28.2 | 0 | 10.2 | 2022-09-03 | 27.1 | 0 | 9.1 | 2021-09-03 | 21.7 | 0 | 3.7 | 2020-09-03 | 23.4 | 0 | 5.4 | 2019-09-03 | 19.9 | 0 | 1.9 | 2018-09-03 | 29 | 0 | 11 | 2017-09-03 | 12.9 | 5.1 | 0 | 2016-09-03 | 21.7 | 0 | 3.7 | 0.51 | 5.71
2025-09-03 | 25.9 | 0 | 7.9 | 2024-09-03 | 22.6 | 0 | 4.6 | 2023-09-03 | 28.9 | 0 | 10.9 | 2022-09-03 | 27.6 | 0 | 9.6 | 2021-09-03 | 22.6 | 0 | 4.6 | 2020-09-03 | 23.7 | 0 | 5.7 | 2019-09-03 | 19.2 | 0 | 1.2 | 2018-09-03 | 29.3 | 0 | 11.3 | 2017-09-03 | 13.3 | 4.7 | 0 | 2016-09-03 | 23 | 0 | 5 | 0.47 | 6.08
2025-09-03 | 26.9 | 0 | 8.9 | 2024-09-03 | 22.6 | 0 | 4.6 | 2023-09-03 | 29.4 | 0 | 11.4 | 2022-09-03 | 27.4 | 0 | 9.4 | 2021-09-03 | 21.4 | 0 | 3.4 | 2020-09-03 | 23.3 | 0 | 5.3 | 2019-09-03 | 19.3 | 0 | 1.3 | 2018-09-03 | 28.4 | 0 | 10.4 | 2017-09-03 | 13.4 | 4.6 | 0 | 2016-09-03 | 23.3 | 0 | 5.3 | 0.46 | 6
2025-09-03 | 26.1 | 0 | 8.1 | 2024-09-03 | 21.9 | 0 | 3.9 | 2023-09-03 | 29.1 | 0 | 11.1 | 2022-09-03 | 27.7 | 0 | 9.7 | 2021-09-03 | 21.1 | 0 | 3.1 | 2020-09-03 | 23.1 | 0 | 5.1 | 2019-09-03 | 18.1 | 0 | 0.1 | 2018-09-03 | 26.8 | 0 | 8.8 | 2017-09-03 | 13.8 | 4.2 | 0 | 2016-09-03 | 23.1 | 0 | 5.1 | 0.42 | 5.5
2025-09-03 | 25.5 | 0 | 7.5 | 2024-09-03 | 22.5 | 0 | 4.5 | 2023-09-03 | 27.4 | 0 | 9.4 | 2022-09-03 | 26.9 | 0 | 8.9 | 2021-09-03 | 20.5 | 0 | 2.5 | 2020-09-03 | 22.9 | 0 | 4.9 | 2019-09-03 | 17.6 | 0.4 | 0 | 2018-09-03 | 28 | 0 | 10 | 2017-09-03 | 13.6 | 4.4 | 0 | 2016-09-03 | 22.5 | 0 | 4.5 | 0.48 | 5.22
2025-09-03 | 23.3 | 0 | 5.3 | 2024-09-03 | 19.8 | 0 | 1.8 | 2023-09-03 | 25.6 | 0 | 7.6 | 2022-09-03 | 25.4 | 0 | 7.4 | 2021-09-03 | 20 | 0 | 2 | 2020-09-03 | 21.7 | 0 | 3.7 | 2019-09-03 | 16.6 | 1.4 | 0 | 2018-09-03 | 27 | 0 | 9 | 2017-09-03 | 13.5 | 4.5 | 0 | 2016-09-03 | 20.1 | 0 | 2.1 | 0.59 | 3.89
2025-09-03 | 20.2 | 0 | 2.2 | 2024-09-03 | 18.5 | 0 | 0.5 | 2023-09-03 | 23.6 | 0 | 5.6 | 2022-09-03 | 24 | 0 | 6 | 2021-09-03 | 17.3 | 0.7 | 0 | 2020-09-03 | 19.9 | 0 | 1.9 | 2019-09-03 | 16.2 | 1.8 | 0 | 2018-09-03 | 24.2 | 0 | 6.2 | 2017-09-03 | 13.3 | 4.7 | 0 | 2016-09-03 | 17.5 | 0.5 | 0 | 0.77 | 2.24
2025-09-03 | 18.2 | 0 | 0.2 | 2024-09-03 | 17.2 | 0.8 | 0 | 2023-09-03 | 22.1 | 0 | 4.1 | 2022-09-03 | 19.5 | 0 | 1.5 | 2021-09-03 | 17 | 1 | 0 | 2020-09-03 | 18.4 | 0 | 0.4 | 2019-09-03 | 15.9 | 2.1 | 0 | 2018-09-03 | 23.7 | 0 | 5.7 | 2017-09-03 | 13.4 | 4.6 | 0 | 2016-09-03 | 15.2 | 2.8 | 0 | 1.13 | 1.19
2025-09-03 | 17.1 | 0.9 | 0 | 2024-09-03 | 16.4 | 1.6 | 0 | 2023-09-03 | 22 | 0 | 4 | 2022-09-03 | 19.4 | 0 | 1.4 | 2021-09-03 | 15.1 | 2.9 | 0 | 2020-09-03 | 19.8 | 0 | 1.8 | 2019-09-03 | 15.5 | 2.5 | 0 | 2018-09-03 | 22.1 | 0 | 4.1 | 2017-09-03 | 13.1 | 4.9 | 0 | 2016-09-03 | 15.1 | 2.9 | 0 | 1.57 | 1.13
2025-09-03 | 16.5 | 1.5 | 0 | 2024-09-03 | 14.5 | 3.5 | 0 | 2023-09-03 | 22 | 0 | 4 | 2022-09-03 | 19.9 | 0 | 1.9 | 2021-09-03 | 13.9 | 4.1 | 0 | 2020-09-03 | 18.7 | 0 | 0.7 | 2019-09-03 | 15.9 | 2.1 | 0 | 2018-09-03 | 21.8 | 0 | 3.8 | 2017-09-03 | 12.9 | 5.1 | 0 | 2016-09-03 | 13.2 | 4.8 | 0 | 2.11 | 1.04
2025-09-03 | 17.1 | 0.9 | 0 | 2024-09-03 | 13.1 | 4.9 | 0 | 2023-09-03 | 22 | 0 | 4 | 2022-09-03 | 18.1 | 0 | 0.1 | 2021-09-03 | 13.3 | 4.7 | 0 | 2020-09-03 | 18.2 | 0 | 0.2 | 2019-09-03 | 15.4 | 2.6 | 0 | 2018-09-03 | 20.9 | 0 | 2.9 | 2017-09-03 | 12.4 | 5.6 | 0 | 2016-09-03 | 13.8 | 4.2 | 0 | 2.29 | 0.72
2025-09-04 | 16.6 | 1.4 | 0 | 2024-09-04 | 12.7 | 5.3 | 0 | 2023-09-04 | 22.2 | 0 | 4.2 | 2022-09-04 | 17.2 | 0.8 | 0 | 2021-09-04 | 14.4 | 3.6 | 0 | 2020-09-04 | 17.3 | 0.7 | 0 | 2019-09-04 | 15.8 | 2.2 | 0 | 2018-09-04 | 19.9 | 0 | 1.9 | 2017-09-04 | 11.9 | 6.1 | 0 | 2016-09-04 | 12.7 | 5.3 | 0 | 2.54 | 0.61
2025-09-04 | 16.5 | 1.5 | 0 | 2024-09-04 | 12.2 | 5.8 | 0 | 2023-09-04 | 20.9 | 0 | 2.9 | 2022-09-04 | 16.1 | 1.9 | 0 | 2021-09-04 | 14.3 | 3.7 | 0 | 2020-09-04 | 16.3 | 1.7 | 0 | 2019-09-04 | 16.4 | 1.6 | 0 | 2018-09-04 | 19.9 | 0 | 1.9 | 2017-09-04 | 10.5 | 7.5 | 0 | 2016-09-04 | 11.4 | 6.6 | 0 | 3.03 | 0.48
2025-09-04 | 15.7 | 2.3 | 0 | 2024-09-04 | 11.7 | 6.3 | 0 | 2023-09-04 | 20.1 | 0 | 2.1 | 2022-09-04 | 14.5 | 3.5 | 0 | 2021-09-04 | 13.2 | 4.8 | 0 | 2020-09-04 | 14.7 | 3.3 | 0 | 2019-09-04 | 17.8 | 0.2 | 0 | 2018-09-04 | 17.9 | 0.1 | 0 | 2017-09-04 | 11 | 7 | 0 | 2016-09-04 | 12 | 6 | 0 | 3.35 | 0.21
2025-09-04 | 15.6 | 2.4 | 0 | 2024-09-04 | 11.1 | 6.9 | 0 | 2023-09-04 | 19.1 | 0 | 1.1 | 2022-09-04 | 13.4 | 4.6 | 0 | 2021-09-04 | 11.7 | 6.3 | 0 | 2020-09-04 | 12.9 | 5.1 | 0 | 2019-09-04 | 18.9 | 0 | 0.9 | 2018-09-04 | 17.8 | 0.2 | 0 | 2017-09-04 | 10.9 | 7.1 | 0 | 2016-09-04 | 10.4 | 7.6 | 0 | 4.02 | 0.2
2025-09-04 | 16.3 | 1.7 | 0 | 2024-09-04 | 10.9 | 7.1 | 0 | 2023-09-04 | 18.9 | 0 | 0.9 | 2022-09-04 | 12.8 | 5.2 | 0 | 2021-09-04 | 11.4 | 6.6 | 0 | 2020-09-04 | 12.1 | 5.9 | 0 | 2019-09-04 | 19.2 | 0 | 1.2 | 2018-09-04 | 17.6 | 0.4 | 0 | 2017-09-04 | 10.5 | 7.5 | 0 | 2016-09-04 | 10.7 | 7.3 | 0 | 4.17 | 0.21
2025-09-04 | 16 | 2 | 0 | 2024-09-04 | 11 | 7 | 0 | 2023-09-04 | 18.7 | 0 | 0.7 | 2022-09-04 | 12.8 | 5.2 | 0 | 2021-09-04 | 10.9 | 7.1 | 0 | 2020-09-04 | 11.4 | 6.6 | 0 | 2019-09-04 | 19.2 | 0 | 1.2 | 2018-09-04 | 16.8 | 1.2 | 0 | 2017-09-04 | 10.7 | 7.3 | 0 | 2016-09-04 | 10.4 | 7.6 | 0 | 4.4 | 0.19
2025-09-04 | 16.7 | 1.3 | 0 | 2024-09-04 | 11 | 7 | 0 | 2023-09-04 | 18.6 | 0 | 0.6 | 2022-09-04 | 12.6 | 5.4 | 0 | 2021-09-04 | 10.3 | 7.7 | 0 | 2020-09-04 | 11.4 | 6.6 | 0 | 2019-09-04 | 19.3 | 0 | 1.3 | 2018-09-04 | 18.2 | 0 | 0.2 | 2017-09-04 | 11.8 | 6.2 | 0 | 2016-09-04 | 10.5 | 7.5 | 0 | 4.17 | 0.21
2025-09-04 | 16.1 | 1.9 | 0 | 2024-09-04 | 13.5 | 4.5 | 0 | 2023-09-04 | 20.4 | 0 | 2.4 | 2022-09-04 | 12.8 | 5.2 | 0 | 2021-09-04 | 13.5 | 4.5 | 0 | 2020-09-04 | 13.1 | 4.9 | 0 | 2019-09-04 | 19.6 | 0 | 1.6 | 2018-09-04 | 20 | 0 | 2 | 2017-09-04 | 12.7 | 5.3 | 0 | 2016-09-04 | 13.6 | 4.4 | 0 | 3.07 | 0.6
2025-09-04 | 18.6 | 0 | 0.6 | 2024-09-04 | 16.3 | 1.7 | 0 | 2023-09-04 | 22.6 | 0 | 4.6 | 2022-09-04 | 13 | 5 | 0 | 2021-09-04 | 16.3 | 1.7 | 0 | 2020-09-04 | 15.6 | 2.4 | 0 | 2019-09-04 | 21.2 | 0 | 3.2 | 2018-09-04 | 21 | 0 | 3 | 2017-09-04 | 13.9 | 4.1 | 0 | 2016-09-04 | 16.4 | 1.6 | 0 | 1.65 | 1.14
2025-09-04 | 21.8 | 0 | 3.8 | 2024-09-04 | 18.9 | 0 | 0.9 | 2023-09-04 | 24.4 | 0 | 6.4 | 2022-09-04 | 12.8 | 5.2 | 0 | 2021-09-04 | 18.6 | 0 | 0.6 | 2020-09-04 | 17.5 | 0.5 | 0 | 2019-09-04 | 22.4 | 0 | 4.4 | 2018-09-04 | 22.8 | 0 | 4.8 | 2017-09-04 | 15.9 | 2.1 | 0 | 2016-09-04 | 19.1 | 0 | 1.1 | 0.78 | 2.2
2025-09-04 | 22.9 | 0 | 4.9 | 2024-09-04 | 20.7 | 0 | 2.7 | 2023-09-04 | 25.9 | 0 | 7.9 | 2022-09-04 | 13.1 | 4.9 | 0 | 2021-09-04 | 19.9 | 0 | 1.9 | 2020-09-04 | 19 | 0 | 1 | 2019-09-04 | 21.2 | 0 | 3.2 | 2018-09-04 | 23.6 | 0 | 5.6 | 2017-09-04 | 16.1 | 1.9 | 0 | 2016-09-04 | 21.3 | 0 | 3.3 | 0.68 | 3.05
2025-09-04 | 25.9 | 0 | 7.9 | 2024-09-04 | 22.4 | 0 | 4.4 | 2023-09-04 | 26.2 | 0 | 8.2 | 2022-09-04 | 14 | 4 | 0 | 2021-09-04 | 20.1 | 0 | 2.1 | 2020-09-04 | 19.1 | 0 | 1.1 | 2019-09-04 | 20.5 | 0 | 2.5 | 2018-09-04 | 24.3 | 0 | 6.3 | 2017-09-04 | 17.8 | 0.2 | 0 | 2016-09-04 | 22.1 | 0 | 4.1 | 0.42 | 3.66
2025-09-04 | 25.9 | 0 | 7.9 | 2024-09-04 | 23.8 | 0 | 5.8 | 2023-09-04 | 27.7 | 0 | 9.7 | 2022-09-04 | 15.4 | 2.6 | 0 | 2021-09-04 | 21.4 | 0 | 3.4 | 2020-09-04 | 19.1 | 0 | 1.1 | 2019-09-04 | 21.3 | 0 | 3.3 | 2018-09-04 | 25.1 | 0 | 7.1 | 2017-09-04 | 19.1 | 0 | 1.1 | 2016-09-04 | 23.4 | 0 | 5.4 | 0.26 | 4.48
2025-09-04 | 20.6 | 0 | 2.6 | 2024-09-04 | 24.3 | 0 | 6.3 | 2023-09-04 | 29.2 | 0 | 11.2 | 2022-09-04 | 16.7 | 1.3 | 0 | 2021-09-04 | 21.9 | 0 | 3.9 | 2020-09-04 | 19 | 0 | 1 | 2019-09-04 | 19.4 | 0 | 1.4 | 2018-09-04 | 24.9 | 0 | 6.9 | 2017-09-04 | 21.1 | 0 | 3.1 | 2016-09-04 | 24.1 | 0 | 6.1 | 0.13 | 4.25
2025-09-04 | 19.3 | 0 | 1.3 | 2024-09-04 | 24.9 | 0 | 6.9 | 2023-09-04 | 29.4 | 0 | 11.4 | 2022-09-04 | 16.6 | 1.4 | 0 | 2021-09-04 | 23.4 | 0 | 5.4 | 2020-09-04 | 18.6 | 0 | 0.6 | 2019-09-04 | 20.2 | 0 | 2.2 | 2018-09-04 | 25.1 | 0 | 7.1 | 2017-09-04 | 22.6 | 0 | 4.6 | 2016-09-04 | 25.6 | 0 | 7.6 | 0.14 | 4.71
2025-09-04 | 15.4 | 2.6 | 0 | 2024-09-04 | 24.5 | 0 | 6.5 | 2023-09-04 | 29.8 | 0 | 11.8 | 2022-09-04 | 17.8 | 0.2 | 0 | 2021-09-04 | 23.4 | 0 | 5.4 | 2020-09-04 | 17.4 | 0.6 | 0 | 2019-09-04 | 17.7 | 0.3 | 0 | 2018-09-04 | 24.1 | 0 | 6.1 | 2017-09-04 | 21.6 | 0 | 3.6 | 2016-09-04 | 25.4 | 0 | 7.4 | 0.37 | 4.08
2025-09-04 | 15.7 | 2.3 | 0 | 2024-09-04 | 24 | 0 | 6 | 2023-09-04 | 29.7 | 0 | 11.7 | 2022-09-04 | 17.9 | 0.1 | 0 | 2021-09-04 | 23.7 | 0 | 5.7 | 2020-09-04 | 18.6 | 0 | 0.6 | 2019-09-04 | 17.2 | 0.8 | 0 | 2018-09-04 | 24.2 | 0 | 6.2 | 2017-09-04 | 20.6 | 0 | 2.6 | 2016-09-04 | 25.6 | 0 | 7.6 | 0.32 | 4.04
2025-09-04 | 14.8 | 3.2 | 0 | 2024-09-04 | 22.7 | 0 | 4.7 | 2023-09-04 | 29.3 | 0 | 11.3 | 2022-09-04 | 17.5 | 0.5 | 0 | 2021-09-04 | 23.7 | 0 | 5.7 | 2020-09-04 | 17.9 | 0.1 | 0 | 2019-09-04 | 17 | 1 | 0 | 2018-09-04 | 23.7 | 0 | 5.7 | 2017-09-04 | 19.4 | 0 | 1.4 | 2016-09-04 | 24.3 | 0 | 6.3 | 0.48 | 3.51
2025-09-04 | 14.2 | 3.8 | 0 | 2024-09-04 | 20.8 | 0 | 2.8 | 2023-09-04 | 26.9 | 0 | 8.9 | 2022-09-04 | 15.5 | 2.5 | 0 | 2021-09-04 | 19.7 | 0 | 1.7 | 2020-09-04 | 17.1 | 0.9 | 0 | 2019-09-04 | 16.4 | 1.6 | 0 | 2018-09-04 | 22.5 | 0 | 4.5 | 2017-09-04 | 18.5 | 0 | 0.5 | 2016-09-04 | 22.6 | 0 | 4.6 | 0.88 | 2.3
2025-09-04 | 13 | 5 | 0 | 2024-09-04 | 18.8 | 0 | 0.8 | 2023-09-04 | 24.4 | 0 | 6.4 | 2022-09-04 | 13.7 | 4.3 | 0 | 2021-09-04 | 18.9 | 0 | 0.9 | 2020-09-04 | 14.9 | 3.1 | 0 | 2019-09-04 | 15.8 | 2.2 | 0 | 2018-09-04 | 21.7 | 0 | 3.7 | 2017-09-04 | 18.3 | 0 | 0.3 | 2016-09-04 | 18.7 | 0 | 0.7 | 1.46 | 1.28
2025-09-04 | 13 | 5 | 0 | 2024-09-04 | 17.2 | 0.8 | 0 | 2023-09-04 | 23 | 0 | 5 | 2022-09-04 | 13.5 | 4.5 | 0 | 2021-09-04 | 19.1 | 0 | 1.1 | 2020-09-04 | 14.4 | 3.6 | 0 | 2019-09-04 | 15.9 | 2.1 | 0 | 2018-09-04 | 20.8 | 0 | 2.8 | 2017-09-04 | 18.3 | 0 | 0.3 | 2016-09-04 | 18.4 | 0 | 0.4 | 1.6 | 0.96
2025-09-04 | 11.4 | 6.6 | 0 | 2024-09-04 | 16 | 2 | 0 | 2023-09-04 | 22.9 | 0 | 4.9 | 2022-09-04 | 12.4 | 5.6 | 0 | 2021-09-04 | 18.3 | 0 | 0.3 | 2020-09-04 | 13.2 | 4.8 | 0 | 2019-09-04 | 13.8 | 4.2 | 0 | 2018-09-04 | 20.1 | 0 | 2.1 | 2017-09-04 | 18 | 0 | 0 | 2016-09-04 | 18.3 | 0 | 0.3 | 2.32 | 0.76
2025-09-04 | 10.8 | 7.2 | 0 | 2024-09-04 | 15.4 | 2.6 | 0 | 2023-09-04 | 22.9 | 0 | 4.9 | 2022-09-04 | 13.5 | 4.5 | 0 | 2021-09-04 | 18 | 0 | 0 | 2020-09-04 | 12.4 | 5.6 | 0 | 2019-09-04 | 12.2 | 5.8 | 0 | 2018-09-04 | 19.9 | 0 | 1.9 | 2017-09-04 | 18.2 | 0 | 0.2 | 2016-09-04 | 15.5 | 2.5 | 0 | 2.82 | 0.7
2025-09-04 | 9.1 | 8.9 | 0 | 2024-09-04 | 14.4 | 3.6 | 0 | 2023-09-04 | 21.9 | 0 | 3.9 | 2022-09-04 | 11.8 | 6.2 | 0 | 2021-09-04 | 17.4 | 0.6 | 0 | 2020-09-04 | 11.5 | 6.5 | 0 | 2019-09-04 | 11.7 | 6.3 | 0 | 2018-09-04 | 19.6 | 0 | 1.6 | 2017-09-04 | 18.1 | 0 | 0.1 | 2016-09-04 | 13.9 | 4.1 | 0 | 3.62 | 0.56
2025-09-05 | 8.6 | 9.4 | 0 | 2024-09-05 | 13.5 | 4.5 | 0 | 2023-09-05 | 20.7 | 0 | 2.7 | 2022-09-05 | 11.2 | 6.8 | 0 | 2021-09-05 | 16.6 | 1.4 | 0 | 2020-09-05 | 11.1 | 6.9 | 0 | 2019-09-05 | 10.7 | 7.3 | 0 | 2018-09-05 | 19.3 | 0 | 1.3 | 2017-09-05 | 18.4 | 0 | 0.4 | 2016-09-05 | 13.9 | 4.1 | 0 | 4.04 | 0.44
2025-09-05 | 8.4 | 9.6 | 0 | 2024-09-05 | 13.1 | 4.9 | 0 | 2023-09-05 | 21 | 0 | 3 | 2022-09-05 | 11.8 | 6.2 | 0 | 2021-09-05 | 16.4 | 1.6 | 0 | 2020-09-05 | 10.4 | 7.6 | 0 | 2019-09-05 | 8.3 | 9.7 | 0 | 2018-09-05 | 19.1 | 0 | 1.1 | 2017-09-05 | 18.2 | 0 | 0.2 | 2016-09-05 | 14 | 4 | 0 | 4.36 | 0.43
2025-09-05 | 8.8 | 9.2 | 0 | 2024-09-05 | 12 | 6 | 0 | 2023-09-05 | 19.3 | 0 | 1.3 | 2022-09-05 | 10.8 | 7.2 | 0 | 2021-09-05 | 16.2 | 1.8 | 0 | 2020-09-05 | 10.4 | 7.6 | 0 | 2019-09-05 | 8.3 | 9.7 | 0 | 2018-09-05 | 18.7 | 0 | 0.7 | 2017-09-05 | 17.1 | 0.9 | 0 | 2016-09-05 | 12.6 | 5.4 | 0 | 4.78 | 0.2
2025-09-05 | 9.9 | 8.1 | 0 | 2024-09-05 | 12 | 6 | 0 | 2023-09-05 | 18.5 | 0 | 0.5 | 2022-09-05 | 10 | 8 | 0 | 2021-09-05 | 15.8 | 2.2 | 0 | 2020-09-05 | 10.1 | 7.9 | 0 | 2019-09-05 | 8.8 | 9.2 | 0 | 2018-09-05 | 19 | 0 | 1 | 2017-09-05 | 16 | 2 | 0 | 2016-09-05 | 11.5 | 6.5 | 0 | 4.99 | 0.15
2025-09-05 | 10.4 | 7.6 | 0 | 2024-09-05 | 11.3 | 6.7 | 0 | 2023-09-05 | 19.4 | 0 | 1.4 | 2022-09-05 | 10 | 8 | 0 | 2021-09-05 | 15.4 | 2.6 | 0 | 2020-09-05 | 8.9 | 9.1 | 0 | 2019-09-05 | 8 | 10 | 0 | 2018-09-05 | 18 | 0 | 0 | 2017-09-05 | 15 | 3 | 0 | 2016-09-05 | 11.5 | 6.5 | 0 | 5.35 | 0.14
2025-09-05 | 10.9 | 7.1 | 0 | 2024-09-05 | 11.2 | 6.8 | 0 | 2023-09-05 | 19 | 0 | 1 | 2022-09-05 | 10 | 8 | 0 | 2021-09-05 | 15.7 | 2.3 | 0 | 2020-09-05 | 9.1 | 8.9 | 0 | 2019-09-05 | 6.6 | 11.4 | 0 | 2018-09-05 | 17.5 | 0.5 | 0 | 2017-09-05 | 13.8 | 4.2 | 0 | 2016-09-05 | 11.3 | 6.7 | 0 | 5.59 | 0.1
2025-09-05 | 11.4 | 6.6 | 0 | 2024-09-05 | 11 | 7 | 0 | 2023-09-05 | 19 | 0 | 1 | 2022-09-05 | 10.4 | 7.6 | 0 | 2021-09-05 | 15.1 | 2.9 | 0 | 2020-09-05 | 9.7 | 8.3 | 0 | 2019-09-05 | 7.9 | 10.1 | 0 | 2018-09-05 | 18.4 | 0 | 0.4 | 2017-09-05 | 13.4 | 4.6 | 0 | 2016-09-05 | 10.5 | 7.5 | 0 | 5.46 | 0.14
2025-09-05 | 12 | 6 | 0 | 2024-09-05 | 13.8 | 4.2 | 0 | 2023-09-05 | 20.4 | 0 | 2.4 | 2022-09-05 | 11.2 | 6.8 | 0 | 2021-09-05 | 15.8 | 2.2 | 0 | 2020-09-05 | 12.1 | 5.9 | 0 | 2019-09-05 | 9.7 | 8.3 | 0 | 2018-09-05 | 20 | 0 | 2 | 2017-09-05 | 14 | 4 | 0 | 2016-09-05 | 13.2 | 4.8 | 0 | 4.22 | 0.44
2025-09-05 | 14 | 4 | 0 | 2024-09-05 | 16.7 | 1.3 | 0 | 2023-09-05 | 22.7 | 0 | 4.7 | 2022-09-05 | 13.2 | 4.8 | 0 | 2021-09-05 | 17.1 | 0.9 | 0 | 2020-09-05 | 14.6 | 3.4 | 0 | 2019-09-05 | 13 | 5 | 0 | 2018-09-05 | 22.7 | 0 | 4.7 | 2017-09-05 | 15 | 3 | 0 | 2016-09-05 | 15.9 | 2.1 | 0 | 2.45 | 0.94
2025-09-05 | 16.4 | 1.6 | 0 | 2024-09-05 | 19.4 | 0 | 1.4 | 2023-09-05 | 26.1 | 0 | 8.1 | 2022-09-05 | 13.8 | 4.2 | 0 | 2021-09-05 | 18.2 | 0 | 0.2 | 2020-09-05 | 16.2 | 1.8 | 0 | 2019-09-05 | 15.8 | 2.2 | 0 | 2018-09-05 | 25.5 | 0 | 7.5 | 2017-09-05 | 15.4 | 2.6 | 0 | 2016-09-05 | 19.1 | 0 | 1.1 | 1.24 | 1.83
2025-09-05 | 18.5 | 0 | 0.5 | 2024-09-05 | 21.4 | 0 | 3.4 | 2023-09-05 | 28 | 0 | 10 | 2022-09-05 | 15.3 | 2.7 | 0 | 2021-09-05 | 19.6 | 0 | 1.6 | 2020-09-05 | 17.6 | 0.4 | 0 | 2019-09-05 | 17.7 | 0.3 | 0 | 2018-09-05 | 28.2 | 0 | 10.2 | 2017-09-05 | 16 | 2 | 0 | 2016-09-05 | 22.2 | 0 | 4.2 | 0.54 | 2.99
2025-09-05 | 20 | 0 | 2 | 2024-09-05 | 23.3 | 0 | 5.3 | 2023-09-05 | 29.2 | 0 | 11.2 | 2022-09-05 | 17.8 | 0.2 | 0 | 2021-09-05 | 19.2 | 0 | 1.2 | 2020-09-05 | 19.3 | 0 | 1.3 | 2019-09-05 | 19.3 | 0 | 1.3 | 2018-09-05 | 30.4 | 0 | 12.4 | 2017-09-05 | 16.9 | 1.1 | 0 | 2016-09-05 | 24.3 | 0 | 6.3 | 0.13 | 4.1
2025-09-05 | 21.4 | 0 | 3.4 | 2024-09-05 | 24.5 | 0 | 6.5 | 2023-09-05 | 30.6 | 0 | 12.6 | 2022-09-05 | 17.2 | 0.8 | 0 | 2021-09-05 | 18.6 | 0 | 0.6 | 2020-09-05 | 20 | 0 | 2 | 2019-09-05 | 19.9 | 0 | 1.9 | 2018-09-05 | 31.2 | 0 | 13.2 | 2017-09-05 | 18.1 | 0 | 0.1 | 2016-09-05 | 25.4 | 0 | 7.4 | 0.08 | 4.77
2025-09-05 | 22.9 | 0 | 4.9 | 2024-09-05 | 24.9 | 0 | 6.9 | 2023-09-05 | 31.4 | 0 | 13.4 | 2022-09-05 | 19 | 0 | 1 | 2021-09-05 | 19.2 | 0 | 1.2 | 2020-09-05 | 20.5 | 0 | 2.5 | 2019-09-05 | 20.5 | 0 | 2.5 | 2018-09-05 | 31.4 | 0 | 13.4 | 2017-09-05 | 19.3 | 0 | 1.3 | 2016-09-05 | 26.4 | 0 | 8.4 | 0 | 5.55
2025-09-05 | 22.9 | 0 | 4.9 | 2024-09-05 | 25 | 0 | 7 | 2023-09-05 | 32 | 0 | 14 | 2022-09-05 | 20 | 0 | 2 | 2021-09-05 | 21.7 | 0 | 3.7 | 2020-09-05 | 19.9 | 0 | 1.9 | 2019-09-05 | 21.6 | 0 | 3.6 | 2018-09-05 | 31.7 | 0 | 13.7 | 2017-09-05 | 19 | 0 | 1 | 2016-09-05 | 26.8 | 0 | 8.8 | 0 | 6.06
2025-09-05 | 22.3 | 0 | 4.3 | 2024-09-05 | 25.2 | 0 | 7.2 | 2023-09-05 | 30.8 | 0 | 12.8 | 2022-09-05 | 20.8 | 0 | 2.8 | 2021-09-05 | 23.1 | 0 | 5.1 | 2020-09-05 | 15.2 | 2.8 | 0 | 2019-09-05 | 21.3 | 0 | 3.3 | 2018-09-05 | 30 | 0 | 12 | 2017-09-05 | 19.6 | 0 | 1.6 | 2016-09-05 | 27.5 | 0 | 9.5 | 0.28 | 5.86
2025-09-05 | 21.9 | 0 | 3.9 | 2024-09-05 | 24.9 | 0 | 6.9 | 2023-09-05 | 31.6 | 0 | 13.6 | 2022-09-05 | 20.6 | 0 | 2.6 | 2021-09-05 | 22.9 | 0 | 4.9 | 2020-09-05 | 15.5 | 2.5 | 0 | 2019-09-05 | 21.7 | 0 | 3.7 | 2018-09-05 | 27.3 | 0 | 9.3 | 2017-09-05 | 19.8 | 0 | 1.8 | 2016-09-05 | 27.4 | 0 | 9.4 | 0.25 | 5.61
2025-09-05 | 22.4 | 0 | 4.4 | 2024-09-05 | 24 | 0 | 6 | 2023-09-05 | 31.4 | 0 | 13.4 | 2022-09-05 | 19.8 | 0 | 1.8 | 2021-09-05 | 23.7 | 0 | 5.7 | 2020-09-05 | 13.7 | 4.3 | 0 | 2019-09-05 | 21.5 | 0 | 3.5 | 2018-09-05 | 27.2 | 0 | 9.2 | 2017-09-05 | 19.5 | 0 | 1.5 | 2016-09-05 | 26.6 | 0 | 8.6 | 0.43 | 5.41
2025-09-05 | 21.1 | 0 | 3.1 | 2024-09-05 | 21.4 | 0 | 3.4 | 2023-09-05 | 28.9 | 0 | 10.9 | 2022-09-05 | 17.2 | 0.8 | 0 | 2021-09-05 | 21.2 | 0 | 3.2 | 2020-09-05 | 13.4 | 4.6 | 0 | 2019-09-05 | 19.3 | 0 | 1.3 | 2018-09-05 | 27.9 | 0 | 9.9 | 2017-09-05 | 19 | 0 | 1 | 2016-09-05 | 24.2 | 0 | 6.2 | 0.54 | 3.9
2025-09-05 | 20.8 | 0 | 2.8 | 2024-09-05 | 20.5 | 0 | 2.5 | 2023-09-05 | 26.7 | 0 | 8.7 | 2022-09-05 | 15.5 | 2.5 | 0 | 2021-09-05 | 19.6 | 0 | 1.6 | 2020-09-05 | 12 | 6 | 0 | 2019-09-05 | 17.2 | 0.8 | 0 | 2018-09-05 | 27.3 | 0 | 9.3 | 2017-09-05 | 16.5 | 1.5 | 0 | 2016-09-05 | 21.5 | 0 | 3.5 | 1.08 | 2.84
2025-09-05 | 16.3 | 1.7 | 0 | 2024-09-05 | 17.4 | 0.6 | 0 | 2023-09-05 | 25.7 | 0 | 7.7 | 2022-09-05 | 14.5 | 3.5 | 0 | 2021-09-05 | 19.8 | 0 | 1.8 | 2020-09-05 | 12.7 | 5.3 | 0 | 2019-09-05 | 16.3 | 1.7 | 0 | 2018-09-05 | 26.8 | 0 | 8.8 | 2017-09-05 | 16.9 | 1.1 | 0 | 2016-09-05 | 18.1 | 0 | 0.1 | 1.39 | 1.84
2025-09-05 | 15.9 | 2.1 | 0 | 2024-09-05 | 15.9 | 2.1 | 0 | 2023-09-05 | 24.9 | 0 | 6.9 | 2022-09-05 | 14.3 | 3.7 | 0 | 2021-09-05 | 18.4 | 0 | 0.4 | 2020-09-05 | 12 | 6 | 0 | 2019-09-05 | 13.6 | 4.4 | 0 | 2018-09-05 | 26.5 | 0 | 8.5 | 2017-09-05 | 16 | 2 | 0 | 2016-09-05 | 18.6 | 0 | 0.6 | 2.03 | 1.64
2025-09-05 | 15 | 3 | 0 | 2024-09-05 | 14.9 | 3.1 | 0 | 2023-09-05 | 24 | 0 | 6 | 2022-09-05 | 13.5 | 4.5 | 0 | 2021-09-05 | 16.4 | 1.6 | 0 | 2020-09-05 | 12.1 | 5.9 | 0 | 2019-09-05 | 14.1 | 3.9 | 0 | 2018-09-05 | 26.4 | 0 | 8.4 | 2017-09-05 | 14.2 | 3.8 | 0 | 2016-09-05 | 19 | 0 | 1 | 2.58 | 1.54
2025-09-05 | 13 | 5 | 0 | 2024-09-05 | 13.1 | 4.9 | 0 | 2023-09-05 | 23.1 | 0 | 5.1 | 2022-09-05 | 13.3 | 4.7 | 0 | 2021-09-05 | 15.5 | 2.5 | 0 | 2020-09-05 | 11.3 | 6.7 | 0 | 2019-09-05 | 14.1 | 3.9 | 0 | 2018-09-05 | 25.9 | 0 | 7.9 | 2017-09-05 | 14.1 | 3.9 | 0 | 2016-09-05 | 15.3 | 2.7 | 0 | 3.43 | 1.3
2025-09-06 | 12.6 | 5.4 | 0 | 2024-09-06 | 14.5 | 3.5 | 0 | 2023-09-06 | 21.8 | 0 | 3.8 | 2022-09-06 | 12.7 | 5.3 | 0 | 2021-09-06 | 14.9 | 3.1 | 0 | 2020-09-06 | 10.4 | 7.6 | 0 | 2019-09-06 | 14.4 | 3.6 | 0 | 2018-09-06 | 24.7 | 0 | 6.7 | 2017-09-06 | 13.2 | 4.8 | 0 | 2016-09-06 | 15.7 | 2.3 | 0 | 3.56 | 1.05
2025-09-06 | 12.3 | 5.7 | 0 | 2024-09-06 | 13.6 | 4.4 | 0 | 2023-09-06 | 21.3 | 0 | 3.3 | 2022-09-06 | 12.2 | 5.8 | 0 | 2021-09-06 | 14.5 | 3.5 | 0 | 2020-09-06 | 10.3 | 7.7 | 0 | 2019-09-06 | 12.6 | 5.4 | 0 | 2018-09-06 | 23.9 | 0 | 5.9 | 2017-09-06 | 13 | 5 | 0 | 2016-09-06 | 13.7 | 4.3 | 0 | 4.18 | 0.92
2025-09-06 | 11.2 | 6.8 | 0 | 2024-09-06 | 13.6 | 4.4 | 0 | 2023-09-06 | 20.7 | 0 | 2.7 | 2022-09-06 | 12.9 | 5.1 | 0 | 2021-09-06 | 15 | 3 | 0 | 2020-09-06 | 9.2 | 8.8 | 0 | 2019-09-06 | 13.3 | 4.7 | 0 | 2018-09-06 | 23.2 | 0 | 5.2 | 2017-09-06 | 12.4 | 5.6 | 0 | 2016-09-06 | 13.8 | 4.2 | 0 | 4.26 | 0.79
2025-09-06 | 11 | 7 | 0 | 2024-09-06 | 13 | 5 | 0 | 2023-09-06 | 20.5 | 0 | 2.5 | 2022-09-06 | 12.3 | 5.7 | 0 | 2021-09-06 | 14.1 | 3.9 | 0 | 2020-09-06 | 9 | 9 | 0 | 2019-09-06 | 12.3 | 5.7 | 0 | 2018-09-06 | 22.2 | 0 | 4.2 | 2017-09-06 | 12.5 | 5.5 | 0 | 2016-09-06 | 13.4 | 4.6 | 0 | 4.64 | 0.67
2025-09-06 | 10.4 | 7.6 | 0 | 2024-09-06 | 13.2 | 4.8 | 0 | 2023-09-06 | 20.2 | 0 | 2.2 | 2022-09-06 | 12.2 | 5.8 | 0 | 2021-09-06 | 15 | 3 | 0 | 2020-09-06 | 8.8 | 9.2 | 0 | 2019-09-06 | 12.7 | 5.3 | 0 | 2018-09-06 | 20.9 | 0 | 2.9 | 2017-09-06 | 12.5 | 5.5 | 0 | 2016-09-06 | 13.1 | 4.9 | 0 | 4.61 | 0.51
2025-09-06 | 9.8 | 8.2 | 0 | 2024-09-06 | 13.2 | 4.8 | 0 | 2023-09-06 | 19.9 | 0 | 1.9 | 2022-09-06 | 11.8 | 6.2 | 0 | 2021-09-06 | 14.3 | 3.7 | 0 | 2020-09-06 | 7.8 | 10.2 | 0 | 2019-09-06 | 11.9 | 6.1 | 0 | 2018-09-06 | 20.3 | 0 | 2.3 | 2017-09-06 | 12.7 | 5.3 | 0 | 2016-09-06 | 13.7 | 4.3 | 0 | 4.88 | 0.42
2025-09-06 | 10.4 | 7.6 | 0 | 2024-09-06 | 13.8 | 4.2 | 0 | 2023-09-06 | 19 | 0 | 1 | 2022-09-06 | 11.8 | 6.2 | 0 | 2021-09-06 | 13.6 | 4.4 | 0 | 2020-09-06 | 8.3 | 9.7 | 0 | 2019-09-06 | 11.2 | 6.8 | 0 | 2018-09-06 | 19.9 | 0 | 1.9 | 2017-09-06 | 12.5 | 5.5 | 0 | 2016-09-06 | 11.3 | 6.7 | 0 | 5.11 | 0.29
2025-09-06 | 11.5 | 6.5 | 0 | 2024-09-06 | 15.5 | 2.5 | 0 | 2023-09-06 | 22 | 0 | 4 | 2022-09-06 | 12.6 | 5.4 | 0 | 2021-09-06 | 15.8 | 2.2 | 0 | 2020-09-06 | 11 | 7 | 0 | 2019-09-06 | 12.9 | 5.1 | 0 | 2018-09-06 | 19.6 | 0 | 1.6 | 2017-09-06 | 12.6 | 5.4 | 0 | 2016-09-06 | 15.7 | 2.3 | 0 | 3.64 | 0.56
2025-09-06 | 12.3 | 5.7 | 0 | 2024-09-06 | 17.6 | 0.4 | 0 | 2023-09-06 | 24.6 | 0 | 6.6 | 2022-09-06 | 14.2 | 3.8 | 0 | 2021-09-06 | 16.7 | 1.3 | 0 | 2020-09-06 | 12.7 | 5.3 | 0 | 2019-09-06 | 15.1 | 2.9 | 0 | 2018-09-06 | 20 | 0 | 2 | 2017-09-06 | 12.7 | 5.3 | 0 | 2016-09-06 | 18.2 | 0 | 0.2 | 2.47 | 0.88
2025-09-06 | 12.8 | 5.2 | 0 | 2024-09-06 | 19.7 | 0 | 1.7 | 2023-09-06 | 27.1 | 0 | 9.1 | 2022-09-06 | 15.4 | 2.6 | 0 | 2021-09-06 | 17.6 | 0.4 | 0 | 2020-09-06 | 14.4 | 3.6 | 0 | 2019-09-06 | 16.3 | 1.7 | 0 | 2018-09-06 | 20.5 | 0 | 2.5 | 2017-09-06 | 13.1 | 4.9 | 0 | 2016-09-06 | 20.9 | 0 | 2.9 | 1.84 | 1.62
2025-09-06 | 12.9 | 5.1 | 0 | 2024-09-06 | 22.2 | 0 | 4.2 | 2023-09-06 | 28.6 | 0 | 10.6 | 2022-09-06 | 16.5 | 1.5 | 0 | 2021-09-06 | 18.7 | 0 | 0.7 | 2020-09-06 | 16 | 2 | 0 | 2019-09-06 | 17.5 | 0.5 | 0 | 2018-09-06 | 20.7 | 0 | 2.7 | 2017-09-06 | 14.3 | 3.7 | 0 | 2016-09-06 | 24.2 | 0 | 6.2 | 1.28 | 2.44
2025-09-06 | 13.6 | 4.4 | 0 | 2024-09-06 | 21.8 | 0 | 3.8 | 2023-09-06 | 29.7 | 0 | 11.7 | 2022-09-06 | 18 | 0 | 0 | 2021-09-06 | 18.8 | 0 | 0.8 | 2020-09-06 | 18.3 | 0 | 0.3 | 2019-09-06 | 18.5 | 0 | 0.5 | 2018-09-06 | 21.3 | 0 | 3.3 | 2017-09-06 | 16.4 | 1.6 | 0 | 2016-09-06 | 26.5 | 0 | 8.5 | 0.6 | 2.89
2025-09-06 | 16.1 | 1.9 | 0 | 2024-09-06 | 21.4 | 0 | 3.4 | 2023-09-06 | 30.9 | 0 | 12.9 | 2022-09-06 | 19.1 | 0 | 1.1 | 2021-09-06 | 15.7 | 2.3 | 0 | 2020-09-06 | 18.6 | 0 | 0.6 | 2019-09-06 | 20.5 | 0 | 2.5 | 2018-09-06 | 22.3 | 0 | 4.3 | 2017-09-06 | 18.3 | 0 | 0.3 | 2016-09-06 | 27 | 0 | 9 | 0.42 | 3.41
2025-09-06 | 17.8 | 0.2 | 0 | 2024-09-06 | 20.8 | 0 | 2.8 | 2023-09-06 | 31.3 | 0 | 13.3 | 2022-09-06 | 20.4 | 0 | 2.4 | 2021-09-06 | 17.8 | 0.2 | 0 | 2020-09-06 | 19.1 | 0 | 1.1 | 2019-09-06 | 20.7 | 0 | 2.7 | 2018-09-06 | 22.7 | 0 | 4.7 | 2017-09-06 | 19 | 0 | 1 | 2016-09-06 | 28.1 | 0 | 10.1 | 0.04 | 3.81
2025-09-06 | 18.5 | 0 | 0.5 | 2024-09-06 | 20.9 | 0 | 2.9 | 2023-09-06 | 31.3 | 0 | 13.3 | 2022-09-06 | 21.5 | 0 | 3.5 | 2021-09-06 | 19 | 0 | 1 | 2020-09-06 | 19.7 | 0 | 1.7 | 2019-09-06 | 20.2 | 0 | 2.2 | 2018-09-06 | 23.2 | 0 | 5.2 | 2017-09-06 | 18.8 | 0 | 0.8 | 2016-09-06 | 28.7 | 0 | 10.7 | 0 | 4.18
2025-09-06 | 19.3 | 0 | 1.3 | 2024-09-06 | 21.5 | 0 | 3.5 | 2023-09-06 | 31.1 | 0 | 13.1 | 2022-09-06 | 21.4 | 0 | 3.4 | 2021-09-06 | 20.9 | 0 | 2.9 | 2020-09-06 | 19.5 | 0 | 1.5 | 2019-09-06 | 19.4 | 0 | 1.4 | 2018-09-06 | 22.3 | 0 | 4.3 | 2017-09-06 | 19.1 | 0 | 1.1 | 2016-09-06 | 29.2 | 0 | 11.2 | 0 | 4.37
2025-09-06 | 20.3 | 0 | 2.3 | 2024-09-06 | 20.6 | 0 | 2.6 | 2023-09-06 | 31.9 | 0 | 13.9 | 2022-09-06 | 21 | 0 | 3 | 2021-09-06 | 20.7 | 0 | 2.7 | 2020-09-06 | 19.4 | 0 | 1.4 | 2019-09-06 | 18.9 | 0 | 0.9 | 2018-09-06 | 22.2 | 0 | 4.2 | 2017-09-06 | 19 | 0 | 1 | 2016-09-06 | 29.2 | 0 | 11.2 | 0 | 4.32
2025-09-06 | 18.8 | 0 | 0.8 | 2024-09-06 | 19.9 | 0 | 1.9 | 2023-09-06 | 30.8 | 0 | 12.8 | 2022-09-06 | 20.1 | 0 | 2.1 | 2021-09-06 | 20.2 | 0 | 2.2 | 2020-09-06 | 18.3 | 0 | 0.3 | 2019-09-06 | 17.9 | 0.1 | 0 | 2018-09-06 | 20.8 | 0 | 2.8 | 2017-09-06 | 18.1 | 0 | 0.1 | 2016-09-06 | 28.6 | 0 | 10.6 | 0.01 | 3.36
2025-09-06 | 18.3 | 0 | 0.3 | 2024-09-06 | 19.8 | 0 | 1.8 | 2023-09-06 | 28.7 | 0 | 10.7 | 2022-09-06 | 19.4 | 0 | 1.4 | 2021-09-06 | 18.7 | 0 | 0.7 | 2020-09-06 | 16 | 2 | 0 | 2019-09-06 | 17.1 | 0.9 | 0 | 2018-09-06 | 19.3 | 0 | 1.3 | 2017-09-06 | 16.4 | 1.6 | 0 | 2016-09-06 | 25 | 0 | 7 | 0.45 | 2.32
2025-09-06 | 17 | 1 | 0 | 2024-09-06 | 17.8 | 0.2 | 0 | 2023-09-06 | 26.8 | 0 | 8.8 | 2022-09-06 | 18.9 | 0 | 0.9 | 2021-09-06 | 15.5 | 2.5 | 0 | 2020-09-06 | 13.5 | 4.5 | 0 | 2019-09-06 | 16.5 | 1.5 | 0 | 2018-09-06 | 18.1 | 0 | 0.1 | 2017-09-06 | 15.4 | 2.6 | 0 | 2016-09-06 | 22.6 | 0 | 4.6 | 1.23 | 1.44
2025-09-06 | 16.3 | 1.7 | 0 | 2024-09-06 | 17.4 | 0.6 | 0 | 2023-09-06 | 25.4 | 0 | 7.4 | 2022-09-06 | 18.4 | 0 | 0.4 | 2021-09-06 | 15.9 | 2.1 | 0 | 2020-09-06 | 12.8 | 5.2 | 0 | 2019-09-06 | 15.7 | 2.3 | 0 | 2018-09-06 | 15.9 | 2.1 | 0 | 2017-09-06 | 14.6 | 3.4 | 0 | 2016-09-06 | 21.4 | 0 | 3.4 | 1.74 | 1.12
2025-09-06 | 14.6 | 3.4 | 0 | 2024-09-06 | 17.1 | 0.9 | 0 | 2023-09-06 | 24 | 0 | 6 | 2022-09-06 | 18.1 | 0 | 0.1 | 2021-09-06 | 14.4 | 3.6 | 0 | 2020-09-06 | 12 | 6 | 0 | 2019-09-06 | 14.9 | 3.1 | 0 | 2018-09-06 | 13.7 | 4.3 | 0 | 2017-09-06 | 14.6 | 3.4 | 0 | 2016-09-06 | 21.3 | 0 | 3.3 | 2.47 | 0.94
2025-09-06 | 14.5 | 3.5 | 0 | 2024-09-06 | 16.9 | 1.1 | 0 | 2023-09-06 | 23 | 0 | 5 | 2022-09-06 | 17.6 | 0.4 | 0 | 2021-09-06 | 13.7 | 4.3 | 0 | 2020-09-06 | 12.1 | 5.9 | 0 | 2019-09-06 | 14.1 | 3.9 | 0 | 2018-09-06 | 14.5 | 3.5 | 0 | 2017-09-06 | 14.7 | 3.3 | 0 | 2016-09-06 | 20.3 | 0 | 2.3 | 2.59 | 0.73
2025-09-06 | 13.5 | 4.5 | 0 | 2024-09-06 | 16.7 | 1.3 | 0 | 2023-09-06 | 22.4 | 0 | 4.4 | 2022-09-06 | 17.6 | 0.4 | 0 | 2021-09-06 | 12.9 | 5.1 | 0 | 2020-09-06 | 12.3 | 5.7 | 0 | 2019-09-06 | 13.7 | 4.3 | 0 | 2018-09-06 | 14.5 | 3.5 | 0 | 2017-09-06 | 13.3 | 4.7 | 0 | 2016-09-06 | 20.3 | 0 | 2.3 | 2.95 | 0.67
2025-09-07 | 13.5 | 4.5 | 0 | 2024-09-07 | 17.1 | 0.9 | 0 | 2023-09-07 | 21.9 | 0 | 3.9 | 2022-09-07 | 17.1 | 0.9 | 0 | 2021-09-07 | 13.3 | 4.7 | 0 | 2020-09-07 | 11.5 | 6.5 | 0 | 2019-09-07 | 13.2 | 4.8 | 0 | 2018-09-07 | 13.5 | 4.5 | 0 | 2017-09-07 | 13.9 | 4.1 | 0 | 2016-09-07 | 19.5 | 0 | 1.5 | 3.09 | 0.54
2025-09-07 | 12.5 | 5.5 | 0 | 2024-09-07 | 17 | 1 | 0 | 2023-09-07 | 22.1 | 0 | 4.1 | 2022-09-07 | 16.5 | 1.5 | 0 | 2021-09-07 | 12.5 | 5.5 | 0 | 2020-09-07 | 11.9 | 6.1 | 0 | 2019-09-07 | 12.9 | 5.1 | 0 | 2018-09-07 | 13.7 | 4.3 | 0 | 2017-09-07 | 13.4 | 4.6 | 0 | 2016-09-07 | 16.4 | 1.6 | 0 | 3.52 | 0.41
2025-09-07 | 12.8 | 5.2 | 0 | 2024-09-07 | 16.9 | 1.1 | 0 | 2023-09-07 | 21.7 | 0 | 3.7 | 2022-09-07 | 16.6 | 1.4 | 0 | 2021-09-07 | 12.3 | 5.7 | 0 | 2020-09-07 | 11.8 | 6.2 | 0 | 2019-09-07 | 13 | 5 | 0 | 2018-09-07 | 10.5 | 7.5 | 0 | 2017-09-07 | 13.5 | 4.5 | 0 | 2016-09-07 | 16.6 | 1.4 | 0 | 3.8 | 0.37
2025-09-07 | 12.2 | 5.8 | 0 | 2024-09-07 | 16.7 | 1.3 | 0 | 2023-09-07 | 22.1 | 0 | 4.1 | 2022-09-07 | 16.4 | 1.6 | 0 | 2021-09-07 | 11.9 | 6.1 | 0 | 2020-09-07 | 12.1 | 5.9 | 0 | 2019-09-07 | 13.1 | 4.9 | 0 | 2018-09-07 | 10.9 | 7.1 | 0 | 2017-09-07 | 13.7 | 4.3 | 0 | 2016-09-07 | 17.7 | 0.3 | 0 | 3.73 | 0.41
2025-09-07 | 12 | 6 | 0 | 2024-09-07 | 16.5 | 1.5 | 0 | 2023-09-07 | 21.5 | 0 | 3.5 | 2022-09-07 | 16.3 | 1.7 | 0 | 2021-09-07 | 10.8 | 7.2 | 0 | 2020-09-07 | 13.2 | 4.8 | 0 | 2019-09-07 | 13 | 5 | 0 | 2018-09-07 | 10.9 | 7.1 | 0 | 2017-09-07 | 13.7 | 4.3 | 0 | 2016-09-07 | 17.3 | 0.7 | 0 | 3.83 | 0.35
2025-09-07 | 11.4 | 6.6 | 0 | 2024-09-07 | 16.3 | 1.7 | 0 | 2023-09-07 | 21.4 | 0 | 3.4 | 2022-09-07 | 16.3 | 1.7 | 0 | 2021-09-07 | 11.2 | 6.8 | 0 | 2020-09-07 | 13.8 | 4.2 | 0 | 2019-09-07 | 13.1 | 4.9 | 0 | 2018-09-07 | 10.6 | 7.4 | 0 | 2017-09-07 | 13.9 | 4.1 | 0 | 2016-09-07 | 17.1 | 0.9 | 0 | 3.83 | 0.34
2025-09-07 | 11.7 | 6.3 | 0 | 2024-09-07 | 16.2 | 1.8 | 0 | 2023-09-07 | 21.4 | 0 | 3.4 | 2022-09-07 | 16.6 | 1.4 | 0 | 2021-09-07 | 12.2 | 5.8 | 0 | 2020-09-07 | 15.3 | 2.7 | 0 | 2019-09-07 | 13.1 | 4.9 | 0 | 2018-09-07 | 11.2 | 6.8 | 0 | 2017-09-07 | 13.5 | 4.5 | 0 | 2016-09-07 | 17 | 1 | 0 | 3.52 | 0.34
2025-09-07 | 12.8 | 5.2 | 0 | 2024-09-07 | 16.3 | 1.7 | 0 | 2023-09-07 | 21.9 | 0 | 3.9 | 2022-09-07 | 17.3 | 0.7 | 0 | 2021-09-07 | 13.2 | 4.8 | 0 | 2020-09-07 | 17.9 | 0.1 | 0 | 2019-09-07 | 13.3 | 4.7 | 0 | 2018-09-07 | 13.9 | 4.1 | 0 | 2017-09-07 | 13.6 | 4.4 | 0 | 2016-09-07 | 19.1 | 0 | 1.1 | 2.57 | 0.5
2025-09-07 | 14.4 | 3.6 | 0 | 2024-09-07 | 13.2 | 4.8 | 0 | 2023-09-07 | 23.2 | 0 | 5.2 | 2022-09-07 | 17.9 | 0.1 | 0 | 2021-09-07 | 15.1 | 2.9 | 0 | 2020-09-07 | 17.9 | 0.1 | 0 | 2019-09-07 | 13.5 | 4.5 | 0 | 2018-09-07 | 16.4 | 1.6 | 0 | 2017-09-07 | 14.3 | 3.7 | 0 | 2016-09-07 | 22.1 | 0 | 4.1 | 2.13 | 0.93
2025-09-07 | 16.3 | 1.7 | 0 | 2024-09-07 | 12.9 | 5.1 | 0 | 2023-09-07 | 24.2 | 0 | 6.2 | 2022-09-07 | 18.7 | 0 | 0.7 | 2021-09-07 | 16.5 | 1.5 | 0 | 2020-09-07 | 18.1 | 0 | 0.1 | 2019-09-07 | 13.2 | 4.8 | 0 | 2018-09-07 | 18.4 | 0 | 0.4 | 2017-09-07 | 15 | 3 | 0 | 2016-09-07 | 23.2 | 0 | 5.2 | 1.61 | 1.26
2025-09-07 | 16.5 | 1.5 | 0 | 2024-09-07 | 13.1 | 4.9 | 0 | 2023-09-07 | 26 | 0 | 8 | 2022-09-07 | 21.1 | 0 | 3.1 | 2021-09-07 | 17.8 | 0.2 | 0 | 2020-09-07 | 21.4 | 0 | 3.4 | 2019-09-07 | 14 | 4 | 0 | 2018-09-07 | 19.4 | 0 | 1.4 | 2017-09-07 | 16.8 | 1.2 | 0 | 2016-09-07 | 23.8 | 0 | 5.8 | 1.18 | 2.17
2025-09-07 | 15.9 | 2.1 | 0 | 2024-09-07 | 13.5 | 4.5 | 0 | 2023-09-07 | 25.9 | 0 | 7.9 | 2022-09-07 | 21.4 | 0 | 3.4 | 2021-09-07 | 19.2 | 0 | 1.2 | 2020-09-07 | 23.8 | 0 | 5.8 | 2019-09-07 | 14.8 | 3.2 | 0 | 2018-09-07 | 20.2 | 0 | 2.2 | 2017-09-07 | 18.4 | 0 | 0.4 | 2016-09-07 | 25.7 | 0 | 7.7 | 0.98 | 2.86
2025-09-07 | 15.4 | 2.6 | 0 | 2024-09-07 | 13.7 | 4.3 | 0 | 2023-09-07 | 26.4 | 0 | 8.4 | 2022-09-07 | 21.9 | 0 | 3.9 | 2021-09-07 | 20.9 | 0 | 2.9 | 2020-09-07 | 24.2 | 0 | 6.2 | 2019-09-07 | 16.4 | 1.6 | 0 | 2018-09-07 | 20.6 | 0 | 2.6 | 2017-09-07 | 20.3 | 0 | 2.3 | 2016-09-07 | 26.7 | 0 | 8.7 | 0.85 | 3.5
2025-09-07 | 16.4 | 1.6 | 0 | 2024-09-07 | 13.8 | 4.2 | 0 | 2023-09-07 | 29 | 0 | 11 | 2022-09-07 | 22.5 | 0 | 4.5 | 2021-09-07 | 20.5 | 0 | 2.5 | 2020-09-07 | 24.8 | 0 | 6.8 | 2019-09-07 | 16.8 | 1.2 | 0 | 2018-09-07 | 21.5 | 0 | 3.5 | 2017-09-07 | 13.6 | 4.4 | 0 | 2016-09-07 | 27.6 | 0 | 9.6 | 1.14 | 3.79
2025-09-07 | 19.3 | 0 | 1.3 | 2024-09-07 | 13.1 | 4.9 | 0 | 2023-09-07 | 27.9 | 0 | 9.9 | 2022-09-07 | 22.9 | 0 | 4.9 | 2021-09-07 | 21.5 | 0 | 3.5 | 2020-09-07 | 23 | 0 | 5 | 2019-09-07 | 17.6 | 0.4 | 0 | 2018-09-07 | 21.9 | 0 | 3.9 | 2017-09-07 | 13.4 | 4.6 | 0 | 2016-09-07 | 27.5 | 0 | 9.5 | 0.99 | 3.8
2025-09-07 | 19.1 | 0 | 1.1 | 2024-09-07 | 13 | 5 | 0 | 2023-09-07 | 29.9 | 0 | 11.9 | 2022-09-07 | 23.1 | 0 | 5.1 | 2021-09-07 | 22.5 | 0 | 4.5 | 2020-09-07 | 22.2 | 0 | 4.2 | 2019-09-07 | 16.6 | 1.4 | 0 | 2018-09-07 | 21.7 | 0 | 3.7 | 2017-09-07 | 15.7 | 2.3 | 0 | 2016-09-07 | 28.1 | 0 | 10.1 | 0.87 | 4.06
2025-09-07 | 18.2 | 0 | 0.2 | 2024-09-07 | 14.9 | 3.1 | 0 | 2023-09-07 | 26.1 | 0 | 8.1 | 2022-09-07 | 23.2 | 0 | 5.2 | 2021-09-07 | 22.2 | 0 | 4.2 | 2020-09-07 | 21.5 | 0 | 3.5 | 2019-09-07 | 16.6 | 1.4 | 0 | 2018-09-07 | 21.6 | 0 | 3.6 | 2017-09-07 | 16.4 | 1.6 | 0 | 2016-09-07 | 27.1 | 0 | 9.1 | 0.61 | 3.39
2025-09-07 | 17.7 | 0.3 | 0 | 2024-09-07 | 13.9 | 4.1 | 0 | 2023-09-07 | 25.6 | 0 | 7.6 | 2022-09-07 | 21.8 | 0 | 3.8 | 2021-09-07 | 22 | 0 | 4 | 2020-09-07 | 21.7 | 0 | 3.7 | 2019-09-07 | 16 | 2 | 0 | 2018-09-07 | 21.2 | 0 | 3.2 | 2017-09-07 | 15.8 | 2.2 | 0 | 2016-09-07 | 26.6 | 0 | 8.6 | 0.86 | 3.09
2025-09-07 | 14.8 | 3.2 | 0 | 2024-09-07 | 12.2 | 5.8 | 0 | 2023-09-07 | 23.8 | 0 | 5.8 | 2022-09-07 | 20.3 | 0 | 2.3 | 2021-09-07 | 20.6 | 0 | 2.6 | 2020-09-07 | 19.4 | 0 | 1.4 | 2019-09-07 | 15.8 | 2.2 | 0 | 2018-09-07 | 19.3 | 0 | 1.3 | 2017-09-07 | 13.6 | 4.4 | 0 | 2016-09-07 | 25.4 | 0 | 7.4 | 1.56 | 2.08
2025-09-07 | 13.6 | 4.4 | 0 | 2024-09-07 | 11.1 | 6.9 | 0 | 2023-09-07 | 21.6 | 0 | 3.6 | 2022-09-07 | 19.3 | 0 | 1.3 | 2021-09-07 | 18.6 | 0 | 0.6 | 2020-09-07 | 19.2 | 0 | 1.2 | 2019-09-07 | 14.5 | 3.5 | 0 | 2018-09-07 | 16.9 | 1.1 | 0 | 2017-09-07 | 13.6 | 4.4 | 0 | 2016-09-07 | 24.2 | 0 | 6.2 | 2.03 | 1.29
2025-09-07 | 14.3 | 3.7 | 0 | 2024-09-07 | 9.8 | 8.2 | 0 | 2023-09-07 | 22.7 | 0 | 4.7 | 2022-09-07 | 17.4 | 0.6 | 0 | 2021-09-07 | 16.6 | 1.4 | 0 | 2020-09-07 | 18.7 | 0 | 0.7 | 2019-09-07 | 13.6 | 4.4 | 0 | 2018-09-07 | 16.2 | 1.8 | 0 | 2017-09-07 | 11.9 | 6.1 | 0 | 2016-09-07 | 23.7 | 0 | 5.7 | 2.62 | 1.11
2025-09-07 | 13.6 | 4.4 | 0 | 2024-09-07 | 8.4 | 9.6 | 0 | 2023-09-07 | 22.3 | 0 | 4.3 | 2022-09-07 | 18.1 | 0 | 0.1 | 2021-09-07 | 16.3 | 1.7 | 0 | 2020-09-07 | 18.3 | 0 | 0.3 | 2019-09-07 | 13.2 | 4.8 | 0 | 2018-09-07 | 16.5 | 1.5 | 0 | 2017-09-07 | 10.9 | 7.1 | 0 | 2016-09-07 | 22.2 | 0 | 4.2 | 2.91 | 0.89
2025-09-07 | 10.9 | 7.1 | 0 | 2024-09-07 | 7.7 | 10.3 | 0 | 2023-09-07 | 20.9 | 0 | 2.9 | 2022-09-07 | 17.1 | 0.9 | 0 | 2021-09-07 | 17.4 | 0.6 | 0 | 2020-09-07 | 17.8 | 0.2 | 0 | 2019-09-07 | 12.5 | 5.5 | 0 | 2018-09-07 | 15.3 | 2.7 | 0 | 2017-09-07 | 10.2 | 7.8 | 0 | 2016-09-07 | 21.6 | 0 | 3.6 | 3.51 | 0.65
2025-09-07 | 9.9 | 8.1 | 0 | 2024-09-07 | 6.4 | 11.6 | 0 | 2023-09-07 | 20.3 | 0 | 2.3 | 2022-09-07 | 16.5 | 1.5 | 0 | 2021-09-07 | 17.9 | 0.1 | 0 | 2020-09-07 | 17.5 | 0.5 | 0 | 2019-09-07 | 11.7 | 6.3 | 0 | 2018-09-07 | 16.1 | 1.9 | 0 | 2017-09-07 | 10.7 | 7.3 | 0 | 2016-09-07 | 21.4 | 0 | 3.4 | 3.73 | 0.57
2025-09-08 | 9 | 9 | 0 | 2024-09-08 | 5.5 | 12.5 | 0 | 2023-09-08 | 19.5 | 0 | 1.5 | 2022-09-08 | 15.4 | 2.6 | 0 | 2021-09-08 | 17.6 | 0.4 | 0 | 2020-09-08 | 16.4 | 1.6 | 0 | 2019-09-08 | 12 | 6 | 0 | 2018-09-08 | 14.6 | 3.4 | 0 | 2017-09-08 | 10.5 | 7.5 | 0 | 2016-09-08 | 21.1 | 0 | 3.1 | 4.3 | 0.46
2025-09-08 | 8.1 | 9.9 | 0 | 2024-09-08 | 5 | 13 | 0 | 2023-09-08 | 19.3 | 0 | 1.3 | 2022-09-08 | 15.8 | 2.2 | 0 | 2021-09-08 | 15.7 | 2.3 | 0 | 2020-09-08 | 13.7 | 4.3 | 0 | 2019-09-08 | 11.8 | 6.2 | 0 | 2018-09-08 | 13.6 | 4.4 | 0 | 2017-09-08 | 10.1 | 7.9 | 0 | 2016-09-08 | 20.6 | 0 | 2.6 | 5.02 | 0.39
2025-09-08 | 6.8 | 11.2 | 0 | 2024-09-08 | 5.5 | 12.5 | 0 | 2023-09-08 | 19.6 | 0 | 1.6 | 2022-09-08 | 14.8 | 3.2 | 0 | 2021-09-08 | 16 | 2 | 0 | 2020-09-08 | 13.5 | 4.5 | 0 | 2019-09-08 | 11.9 | 6.1 | 0 | 2018-09-08 | 12.6 | 5.4 | 0 | 2017-09-08 | 10.5 | 7.5 | 0 | 2016-09-08 | 20.5 | 0 | 2.5 | 5.24 | 0.41
2025-09-08 | 6.7 | 11.3 | 0 | 2024-09-08 | 5.9 | 12.1 | 0 | 2023-09-08 | 19.2 | 0 | 1.2 | 2022-09-08 | 13.8 | 4.2 | 0 | 2021-09-08 | 16.1 | 1.9 | 0 | 2020-09-08 | 11.8 | 6.2 | 0 | 2019-09-08 | 11.2 | 6.8 | 0 | 2018-09-08 | 11.6 | 6.4 | 0 | 2017-09-08 | 11.6 | 6.4 | 0 | 2016-09-08 | 20.6 | 0 | 2.6 | 5.53 | 0.38
2025-09-08 | 6.4 | 11.6 | 0 | 2024-09-08 | 5.1 | 12.9 | 0 | 2023-09-08 | 18.6 | 0 | 0.6 | 2022-09-08 | 14 | 4 | 0 | 2021-09-08 | 16.4 | 1.6 | 0 | 2020-09-08 | 10.4 | 7.6 | 0 | 2019-09-08 | 11.1 | 6.9 | 0 | 2018-09-08 | 10.4 | 7.6 | 0 | 2017-09-08 | 11 | 7 | 0 | 2016-09-08 | 20.7 | 0 | 2.7 | 5.92 | 0.33
2025-09-08 | 6 | 12 | 0 | 2024-09-08 | 5.7 | 12.3 | 0 | 2023-09-08 | 18.2 | 0 | 0.2 | 2022-09-08 | 13.8 | 4.2 | 0 | 2021-09-08 | 16.3 | 1.7 | 0 | 2020-09-08 | 10.7 | 7.3 | 0 | 2019-09-08 | 11.1 | 6.9 | 0 | 2018-09-08 | 9.4 | 8.6 | 0 | 2017-09-08 | 9.8 | 8.2 | 0 | 2016-09-08 | 20.6 | 0 | 2.6 | 6.12 | 0.28
2025-09-08 | 5.6 | 12.4 | 0 | 2024-09-08 | 6.1 | 11.9 | 0 | 2023-09-08 | 17.9 | 0.1 | 0 | 2022-09-08 | 13.2 | 4.8 | 0 | 2021-09-08 | 16.3 | 1.7 | 0 | 2020-09-08 | 9.4 | 8.6 | 0 | 2019-09-08 | 10.5 | 7.5 | 0 | 2018-09-08 | 9 | 9 | 0 | 2017-09-08 | 8.6 | 9.4 | 0 | 2016-09-08 | 20.6 | 0 | 2.6 | 6.54 | 0.26
2025-09-08 | 8.5 | 9.5 | 0 | 2024-09-08 | 7.6 | 10.4 | 0 | 2023-09-08 | 17.1 | 0.9 | 0 | 2022-09-08 | 14.2 | 3.8 | 0 | 2021-09-08 | 16.4 | 1.6 | 0 | 2020-09-08 | 11.6 | 6.4 | 0 | 2019-09-08 | 11.8 | 6.2 | 0 | 2018-09-08 | 10.3 | 7.7 | 0 | 2017-09-08 | 10.6 | 7.4 | 0 | 2016-09-08 | 20.7 | 0 | 2.7 | 5.39 | 0.27
2025-09-08 | 11.2 | 6.8 | 0 | 2024-09-08 | 8.5 | 9.5 | 0 | 2023-09-08 | 16.8 | 1.2 | 0 | 2022-09-08 | 15.8 | 2.2 | 0 | 2021-09-08 | 16.3 | 1.7 | 0 | 2020-09-08 | 14 | 4 | 0 | 2019-09-08 | 13.2 | 4.8 | 0 | 2018-09-08 | 11.3 | 6.7 | 0 | 2017-09-08 | 11.4 | 6.6 | 0 | 2016-09-08 | 20.9 | 0 | 2.9 | 4.35 | 0.29
2025-09-08 | 13.7 | 4.3 | 0 | 2024-09-08 | 9.1 | 8.9 | 0 | 2023-09-08 | 18 | 0 | 0 | 2022-09-08 | 18.9 | 0 | 0.9 | 2021-09-08 | 16.9 | 1.1 | 0 | 2020-09-08 | 14.9 | 3.1 | 0 | 2019-09-08 | 15.3 | 2.7 | 0 | 2018-09-08 | 12.4 | 5.6 | 0 | 2017-09-08 | 11.9 | 6.1 | 0 | 2016-09-08 | 21 | 0 | 3 | 3.18 | 0.39
2025-09-08 | 15.2 | 2.8 | 0 | 2024-09-08 | 9.4 | 8.6 | 0 | 2023-09-08 | 18.4 | 0 | 0.4 | 2022-09-08 | 22 | 0 | 4 | 2021-09-08 | 16.9 | 1.1 | 0 | 2020-09-08 | 16.5 | 1.5 | 0 | 2019-09-08 | 15.5 | 2.5 | 0 | 2018-09-08 | 13.9 | 4.1 | 0 | 2017-09-08 | 12 | 6 | 0 | 2016-09-08 | 21.6 | 0 | 3.6 | 2.66 | 0.8
2025-09-08 | 17.1 | 0.9 | 0 | 2024-09-08 | 10.4 | 7.6 | 0 | 2023-09-08 | 19.2 | 0 | 1.2 | 2022-09-08 | 23.5 | 0 | 5.5 | 2021-09-08 | 18.8 | 0 | 0.8 | 2020-09-08 | 17.8 | 0.2 | 0 | 2019-09-08 | 16.4 | 1.6 | 0 | 2018-09-08 | 14.3 | 3.7 | 0 | 2017-09-08 | 14.1 | 3.9 | 0 | 2016-09-08 | 22.7 | 0 | 4.7 | 1.79 | 1.22
2025-09-08 | 16.4 | 1.6 | 0 | 2024-09-08 | 11.3 | 6.7 | 0 | 2023-09-08 | 19.1 | 0 | 1.1 | 2022-09-08 | 24.7 | 0 | 6.7 | 2021-09-08 | 20.4 | 0 | 2.4 | 2020-09-08 | 17.4 | 0.6 | 0 | 2019-09-08 | 17.1 | 0.9 | 0 | 2018-09-08 | 15.5 | 2.5 | 0 | 2017-09-08 | 13.9 | 4.1 | 0 | 2016-09-08 | 22.9 | 0 | 4.9 | 1.64 | 1.51
2025-09-08 | 17.1 | 0.9 | 0 | 2024-09-08 | 11.9 | 6.1 | 0 | 2023-09-08 | 19.2 | 0 | 1.2 | 2022-09-08 | 25.2 | 0 | 7.2 | 2021-09-08 | 21.2 | 0 | 3.2 | 2020-09-08 | 17.3 | 0.7 | 0 | 2019-09-08 | 16.1 | 1.9 | 0 | 2018-09-08 | 15.8 | 2.2 | 0 | 2017-09-08 | 15.1 | 2.9 | 0 | 2016-09-08 | 23.5 | 0 | 5.5 | 1.47 | 1.71
2025-09-08 | 18.5 | 0 | 0.5 | 2024-09-08 | 12 | 6 | 0 | 2023-09-08 | 19.4 | 0 | 1.4 | 2022-09-08 | 26 | 0 | 8 | 2021-09-08 | 22.2 | 0 | 4.2 | 2020-09-08 | 17.4 | 0.6 | 0 | 2019-09-08 | 14.7 | 3.3 | 0 | 2018-09-08 | 16.2 | 1.8 | 0 | 2017-09-08 | 14.1 | 3.9 | 0 | 2016-09-08 | 24.5 | 0 | 6.5 | 1.56 | 2.06
2025-09-08 | 17.6 | 0.4 | 0 | 2024-09-08 | 12.6 | 5.4 | 0 | 2023-09-08 | 19.9 | 0 | 1.9 | 2022-09-08 | 26.7 | 0 | 8.7 | 2021-09-08 | 24.4 | 0 | 6.4 | 2020-09-08 | 17 | 1 | 0 | 2019-09-08 | 15.7 | 2.3 | 0 | 2018-09-08 | 16.4 | 1.6 | 0 | 2017-09-08 | 15.4 | 2.6 | 0 | 2016-09-08 | 25.3 | 0 | 7.3 | 1.33 | 2.43
2025-09-08 | 17.7 | 0.3 | 0 | 2024-09-08 | 12.6 | 5.4 | 0 | 2023-09-08 | 20.1 | 0 | 2.1 | 2022-09-08 | 26.2 | 0 | 8.2 | 2021-09-08 | 24.1 | 0 | 6.1 | 2020-09-08 | 15.7 | 2.3 | 0 | 2019-09-08 | 14.8 | 3.2 | 0 | 2018-09-08 | 16.2 | 1.8 | 0 | 2017-09-08 | 14.6 | 3.4 | 0 | 2016-09-08 | 27.1 | 0 | 9.1 | 1.64 | 2.55
2025-09-08 | 17.4 | 0.6 | 0 | 2024-09-08 | 11.8 | 6.2 | 0 | 2023-09-08 | 18.9 | 0 | 0.9 | 2022-09-08 | 25.4 | 0 | 7.4 | 2021-09-08 | 23.5 | 0 | 5.5 | 2020-09-08 | 14.7 | 3.3 | 0 | 2019-09-08 | 15 | 3 | 0 | 2018-09-08 | 15.6 | 2.4 | 0 | 2017-09-08 | 13.2 | 4.8 | 0 | 2016-09-08 | 27.3 | 0 | 9.3 | 2.03 | 2.31
2025-09-08 | 15.9 | 2.1 | 0 | 2024-09-08 | 11 | 7 | 0 | 2023-09-08 | 18.4 | 0 | 0.4 | 2022-09-08 | 23.4 | 0 | 5.4 | 2021-09-08 | 21.7 | 0 | 3.7 | 2020-09-08 | 14.2 | 3.8 | 0 | 2019-09-08 | 13.7 | 4.3 | 0 | 2018-09-08 | 14.4 | 3.6 | 0 | 2017-09-08 | 12.2 | 5.8 | 0 | 2016-09-08 | 25.9 | 0 | 7.9 | 2.66 | 1.74
2025-09-08 | 14 | 4 | 0 | 2024-09-08 | 10.6 | 7.4 | 0 | 2023-09-08 | 17.7 | 0.3 | 0 | 2022-09-08 | 22.5 | 0 | 4.5 | 2021-09-08 | 19.9 | 0 | 1.9 | 2020-09-08 | 13.5 | 4.5 | 0 | 2019-09-08 | 12.2 | 5.8 | 0 | 2018-09-08 | 12.8 | 5.2 | 0 | 2017-09-08 | 11.8 | 6.2 | 0 | 2016-09-08 | 25 | 0 | 7 | 3.34 | 1.34
2025-09-08 | 13.7 | 4.3 | 0 | 2024-09-08 | 10 | 8 | 0 | 2023-09-08 | 16.9 | 1.1 | 0 | 2022-09-08 | 17.3 | 0.7 | 0 | 2021-09-08 | 19.1 | 0 | 1.1 | 2020-09-08 | 13.2 | 4.8 | 0 | 2019-09-08 | 12 | 6 | 0 | 2018-09-08 | 12.4 | 5.6 | 0 | 2017-09-08 | 11.4 | 6.6 | 0 | 2016-09-08 | 24.1 | 0 | 6.1 | 3.71 | 0.72
2025-09-08 | 9 | 9 | 0 | 2024-09-08 | 9.9 | 8.1 | 0 | 2023-09-08 | 16.1 | 1.9 | 0 | 2022-09-08 | 17.4 | 0.6 | 0 | 2021-09-08 | 17.1 | 0.9 | 0 | 2020-09-08 | 13 | 5 | 0 | 2019-09-08 | 11 | 7 | 0 | 2018-09-08 | 11.7 | 6.3 | 0 | 2017-09-08 | 11.4 | 6.6 | 0 | 2016-09-08 | 23.5 | 0 | 5.5 | 4.54 | 0.55
2025-09-08 | 8.4 | 9.6 | 0 | 2024-09-08 | 10.6 | 7.4 | 0 | 2023-09-08 | 15.5 | 2.5 | 0 | 2022-09-08 | 16.7 | 1.3 | 0 | 2021-09-08 | 17.6 | 0.4 | 0 | 2020-09-08 | 12.9 | 5.1 | 0 | 2019-09-08 | 10.2 | 7.8 | 0 | 2018-09-08 | 10.4 | 7.6 | 0 | 2017-09-08 | 11.2 | 6.8 | 0 | 2016-09-08 | 22.7 | 0 | 4.7 | 4.85 | 0.47
2025-09-08 | 9.5 | 8.5 | 0 | 2024-09-08 | 10.7 | 7.3 | 0 | 2023-09-08 | 15.1 | 2.9 | 0 | 2022-09-08 | 16.4 | 1.6 | 0 | 2021-09-08 | 17.1 | 0.9 | 0 | 2020-09-08 | 12.7 | 5.3 | 0 | 2019-09-08 | 9.4 | 8.6 | 0 | 2018-09-08 | 9.5 | 8.5 | 0 | 2017-09-08 | 11.2 | 6.8 | 0 | 2016-09-08 | 21.9 | 0 | 3.9 | 5.04 | 0.39
2025-09-09 | 7.7 | 10.3 | 0 | 2024-09-09 | 10.4 | 7.6 | 0 | 2023-09-09 | 14.8 | 3.2 | 0 | 2022-09-09 | 15.9 | 2.1 | 0 | 2021-09-09 | 16.2 | 1.8 | 0 | 2020-09-09 | 12.7 | 5.3 | 0 | 2019-09-09 | 8.6 | 9.4 | 0 | 2018-09-09 | 8.5 | 9.5 | 0 | 2017-09-09 | 11.2 | 6.8 | 0 | 2016-09-09 | 21.4 | 0 | 3.4 | 5.6 | 0.34
2025-09-09 | 7.8 | 10.2 | 0 | 2024-09-09 | 10.2 | 7.8 | 0 | 2023-09-09 | 13.1 | 4.9 | 0 | 2022-09-09 | 14.2 | 3.8 | 0 | 2021-09-09 | 15.4 | 2.6 | 0 | 2020-09-09 | 12.5 | 5.5 | 0 | 2019-09-09 | 8.6 | 9.4 | 0 | 2018-09-09 | 8 | 10 | 0 | 2017-09-09 | 11 | 7 | 0 | 2016-09-09 | 20.8 | 0 | 2.8 | 6.12 | 0.28
2025-09-09 | 7.7 | 10.3 | 0 | 2024-09-09 | 10.6 | 7.4 | 0 | 2023-09-09 | 12.8 | 5.2 | 0 | 2022-09-09 | 13.7 | 4.3 | 0 | 2021-09-09 | 14.3 | 3.7 | 0 | 2020-09-09 | 12.5 | 5.5 | 0 | 2019-09-09 | 7.2 | 10.8 | 0 | 2018-09-09 | 7 | 11 | 0 | 2017-09-09 | 10.7 | 7.3 | 0 | 2016-09-09 | 20.7 | 0 | 2.7 | 6.55 | 0.27
2025-09-09 | 6.4 | 11.6 | 0 | 2024-09-09 | 10.3 | 7.7 | 0 | 2023-09-09 | 11.6 | 6.4 | 0 | 2022-09-09 | 14.5 | 3.5 | 0 | 2021-09-09 | 14.2 | 3.8 | 0 | 2020-09-09 | 12.6 | 5.4 | 0 | 2019-09-09 | 5.6 | 12.4 | 0 | 2018-09-09 | 6.5 | 11.5 | 0 | 2017-09-09 | 10.6 | 7.4 | 0 | 2016-09-09 | 20.5 | 0 | 2.5 | 6.97 | 0.25
2025-09-09 | 5.8 | 12.2 | 0 | 2024-09-09 | 8.5 | 9.5 | 0 | 2023-09-09 | 11.3 | 6.7 | 0 | 2022-09-09 | 13.6 | 4.4 | 0 | 2021-09-09 | 13.8 | 4.2 | 0 | 2020-09-09 | 12.6 | 5.4 | 0 | 2019-09-09 | 4.5 | 13.5 | 0 | 2018-09-09 | 5.7 | 12.3 | 0 | 2017-09-09 | 10.5 | 7.5 | 0 | 2016-09-09 | 19.8 | 0 | 1.8 | 7.57 | 0.18
2025-09-09 | 5.4 | 12.6 | 0 | 2024-09-09 | 8 | 10 | 0 | 2023-09-09 | 10.7 | 7.3 | 0 | 2022-09-09 | 12.8 | 5.2 | 0 | 2021-09-09 | 13.2 | 4.8 | 0 | 2020-09-09 | 12.5 | 5.5 | 0 | 2019-09-09 | 5 | 13 | 0 | 2018-09-09 | 5.7 | 12.3 | 0 | 2017-09-09 | 10.5 | 7.5 | 0 | 2016-09-09 | 18.2 | 0 | 0.2 | 7.82 | 0.02
2025-09-09 | 4 | 14 | 0 | 2024-09-09 | 7.7 | 10.3 | 0 | 2023-09-09 | 9.7 | 8.3 | 0 | 2022-09-09 | 13.9 | 4.1 | 0 | 2021-09-09 | 12.4 | 5.6 | 0 | 2020-09-09 | 12.6 | 5.4 | 0 | 2019-09-09 | 6.1 | 11.9 | 0 | 2018-09-09 | 6.2 | 11.8 | 0 | 2017-09-09 | 10.6 | 7.4 | 0 | 2016-09-09 | 17.7 | 0.3 | 0 | 7.91 | 0
2025-09-09 | 7.2 | 10.8 | 0 | 2024-09-09 | 9.8 | 8.2 | 0 | 2023-09-09 | 11.6 | 6.4 | 0 | 2022-09-09 | 14.8 | 3.2 | 0 | 2021-09-09 | 14.3 | 3.7 | 0 | 2020-09-09 | 12.9 | 5.1 | 0 | 2019-09-09 | 8.7 | 9.3 | 0 | 2018-09-09 | 8.6 | 9.4 | 0 | 2017-09-09 | 10.9 | 7.1 | 0 | 2016-09-09 | 20.1 | 0 | 2.1 | 6.32 | 0.21
2025-09-09 | 8.2 | 9.8 | 0 | 2024-09-09 | 12.3 | 5.7 | 0 | 2023-09-09 | 15 | 3 | 0 | 2022-09-09 | 17 | 1 | 0 | 2021-09-09 | 17.2 | 0.8 | 0 | 2020-09-09 | 13.4 | 4.6 | 0 | 2019-09-09 | 11.2 | 6.8 | 0 | 2018-09-09 | 10.9 | 7.1 | 0 | 2017-09-09 | 11.9 | 6.1 | 0 | 2016-09-09 | 21.3 | 0 | 3.3 | 4.49 | 0.33
2025-09-09 | 11.4 | 6.6 | 0 | 2024-09-09 | 15.2 | 2.8 | 0 | 2023-09-09 | 17.3 | 0.7 | 0 | 2022-09-09 | 20 | 0 | 2 | 2021-09-09 | 19.2 | 0 | 1.2 | 2020-09-09 | 13.4 | 4.6 | 0 | 2019-09-09 | 12.5 | 5.5 | 0 | 2018-09-09 | 12.6 | 5.4 | 0 | 2017-09-09 | 14.4 | 3.6 | 0 | 2016-09-09 | 22.7 | 0 | 4.7 | 2.92 | 0.79
2025-09-09 | 15.3 | 2.7 | 0 | 2024-09-09 | 16.7 | 1.3 | 0 | 2023-09-09 | 18.7 | 0 | 0.7 | 2022-09-09 | 22.6 | 0 | 4.6 | 2021-09-09 | 19.9 | 0 | 1.9 | 2020-09-09 | 14 | 4 | 0 | 2019-09-09 | 13.9 | 4.1 | 0 | 2018-09-09 | 14 | 4 | 0 | 2017-09-09 | 16.1 | 1.9 | 0 | 2016-09-09 | 23.4 | 0 | 5.4 | 1.8 | 1.26
2025-09-09 | 17.9 | 0.1 | 0 | 2024-09-09 | 16.4 | 1.6 | 0 | 2023-09-09 | 20.1 | 0 | 2.1 | 2022-09-09 | 24.4 | 0 | 6.4 | 2021-09-09 | 21.3 | 0 | 3.3 | 2020-09-09 | 15 | 3 | 0 | 2019-09-09 | 15 | 3 | 0 | 2018-09-09 | 14.8 | 3.2 | 0 | 2017-09-09 | 17.5 | 0.5 | 0 | 2016-09-09 | 25.3 | 0 | 7.3 | 1.14 | 1.91
2025-09-09 | 19.4 | 0 | 1.4 | 2024-09-09 | 16.1 | 1.9 | 0 | 2023-09-09 | 21 | 0 | 3 | 2022-09-09 | 24.9 | 0 | 6.9 | 2021-09-09 | 20.6 | 0 | 2.6 | 2020-09-09 | 15.4 | 2.6 | 0 | 2019-09-09 | 15.2 | 2.8 | 0 | 2018-09-09 | 16 | 2 | 0 | 2017-09-09 | 18.6 | 0 | 0.6 | 2016-09-09 | 25.5 | 0 | 7.5 | 0.93 | 2.2
2025-09-09 | 20.5 | 0 | 2.5 | 2024-09-09 | 17.6 | 0.4 | 0 | 2023-09-09 | 21.7 | 0 | 3.7 | 2022-09-09 | 25.8 | 0 | 7.8 | 2021-09-09 | 21.2 | 0 | 3.2 | 2020-09-09 | 15.7 | 2.3 | 0 | 2019-09-09 | 16.4 | 1.6 | 0 | 2018-09-09 | 15.9 | 2.1 | 0 | 2017-09-09 | 19 | 0 | 1 | 2016-09-09 | 26.1 | 0 | 8.1 | 0.64 | 2.63
2025-09-09 | 21.1 | 0 | 3.1 | 2024-09-09 | 17.9 | 0.1 | 0 | 2023-09-09 | 21.5 | 0 | 3.5 | 2022-09-09 | 26.2 | 0 | 8.2 | 2021-09-09 | 22.8 | 0 | 4.8 | 2020-09-09 | 16 | 2 | 0 | 2019-09-09 | 16 | 2 | 0 | 2018-09-09 | 16.4 | 1.6 | 0 | 2017-09-09 | 18.9 | 0 | 0.9 | 2016-09-09 | 26.7 | 0 | 8.7 | 0.57 | 2.92
2025-09-09 | 21.5 | 0 | 3.5 | 2024-09-09 | 18.8 | 0 | 0.8 | 2023-09-09 | 21.8 | 0 | 3.8 | 2022-09-09 | 26.4 | 0 | 8.4 | 2021-09-09 | 22.5 | 0 | 4.5 | 2020-09-09 | 15.7 | 2.3 | 0 | 2019-09-09 | 16.5 | 1.5 | 0 | 2018-09-09 | 16.2 | 1.8 | 0 | 2017-09-09 | 18.4 | 0 | 0.4 | 2016-09-09 | 26.7 | 0 | 8.7 | 0.56 | 3.01
2025-09-09 | 21.5 | 0 | 3.5 | 2024-09-09 | 19 | 0 | 1 | 2023-09-09 | 22.2 | 0 | 4.2 | 2022-09-09 | 25.8 | 0 | 7.8 | 2021-09-09 | 18.8 | 0 | 0.8 | 2020-09-09 | 14.2 | 3.8 | 0 | 2019-09-09 | 17 | 1 | 0 | 2018-09-09 | 15.5 | 2.5 | 0 | 2017-09-09 | 18 | 0 | 0 | 2016-09-09 | 26.2 | 0 | 8.2 | 0.73 | 2.55
2025-09-09 | 20.4 | 0 | 2.4 | 2024-09-09 | 18.4 | 0 | 0.4 | 2023-09-09 | 22.3 | 0 | 4.3 | 2022-09-09 | 24.8 | 0 | 6.8 | 2021-09-09 | 18.6 | 0 | 0.6 | 2020-09-09 | 13.8 | 4.2 | 0 | 2019-09-09 | 16.5 | 1.5 | 0 | 2018-09-09 | 14.5 | 3.5 | 0 | 2017-09-09 | 17.2 | 0.8 | 0 | 2016-09-09 | 25.3 | 0 | 7.3 | 1 | 2.18
2025-09-09 | 17.7 | 0.3 | 0 | 2024-09-09 | 16.4 | 1.6 | 0 | 2023-09-09 | 19.3 | 0 | 1.3 | 2022-09-09 | 22.8 | 0 | 4.8 | 2021-09-09 | 17.2 | 0.8 | 0 | 2020-09-09 | 13.7 | 4.3 | 0 | 2019-09-09 | 15.1 | 2.9 | 0 | 2018-09-09 | 13.2 | 4.8 | 0 | 2017-09-09 | 16 | 2 | 0 | 2016-09-09 | 23.4 | 0 | 5.4 | 1.67 | 1.15
2025-09-09 | 14.5 | 3.5 | 0 | 2024-09-09 | 13.6 | 4.4 | 0 | 2023-09-09 | 17.4 | 0.6 | 0 | 2022-09-09 | 21 | 0 | 3 | 2021-09-09 | 16.5 | 1.5 | 0 | 2020-09-09 | 13.5 | 4.5 | 0 | 2019-09-09 | 13.8 | 4.2 | 0 | 2018-09-09 | 11.7 | 6.3 | 0 | 2017-09-09 | 14.3 | 3.7 | 0 | 2016-09-09 | 22.7 | 0 | 4.7 | 2.87 | 0.77
2025-09-09 | 16 | 2 | 0 | 2024-09-09 | 12.4 | 5.6 | 0 | 2023-09-09 | 17.4 | 0.6 | 0 | 2022-09-09 | 20 | 0 | 2 | 2021-09-09 | 15.4 | 2.6 | 0 | 2020-09-09 | 13.4 | 4.6 | 0 | 2019-09-09 | 9.4 | 8.6 | 0 | 2018-09-09 | 10.7 | 7.3 | 0 | 2017-09-09 | 13.6 | 4.4 | 0 | 2016-09-09 | 21.2 | 0 | 3.2 | 3.57 | 0.52
2025-09-09 | 13.7 | 4.3 | 0 | 2024-09-09 | 10.3 | 7.7 | 0 | 2023-09-09 | 16.3 | 1.7 | 0 | 2022-09-09 | 19.5 | 0 | 1.5 | 2021-09-09 | 15.2 | 2.8 | 0 | 2020-09-09 | 12.3 | 5.7 | 0 | 2019-09-09 | 11 | 7 | 0 | 2018-09-09 | 10.5 | 7.5 | 0 | 2017-09-09 | 12.3 | 5.7 | 0 | 2016-09-09 | 19.8 | 0 | 1.8 | 4.24 | 0.33
2025-09-09 | 13.4 | 4.6 | 0 | 2024-09-09 | 10.5 | 7.5 | 0 | 2023-09-09 | 17.2 | 0.8 | 0 | 2022-09-09 | 18.3 | 0 | 0.3 | 2021-09-09 | 15.4 | 2.6 | 0 | 2020-09-09 | 11.6 | 6.4 | 0 | 2019-09-09 | 8.2 | 9.8 | 0 | 2018-09-09 | 9.4 | 8.6 | 0 | 2017-09-09 | 11.2 | 6.8 | 0 | 2016-09-09 | 17.7 | 0.3 | 0 | 4.74 | 0.03
2025-09-09 | 12.2 | 5.8 | 0 | 2024-09-09 | 11 | 7 | 0 | 2023-09-09 | 16.7 | 1.3 | 0 | 2022-09-09 | 17.3 | 0.7 | 0 | 2021-09-09 | 14.8 | 3.2 | 0 | 2020-09-09 | 11.5 | 6.5 | 0 | 2019-09-09 | 8.7 | 9.3 | 0 | 2018-09-09 | 8 | 10 | 0 | 2017-09-09 | 9 | 9 | 0 | 2016-09-09 | 19.7 | 0 | 1.7 | 5.28 | 0.17
2025-09-10 | 12.3 | 5.7 | 0 | 2024-09-10 | 8.4 | 9.6 | 0 | 2023-09-10 | 16.4 | 1.6 | 0 | 2022-09-10 | 16.4 | 1.6 | 0 | 2021-09-10 | 14.2 | 3.8 | 0 | 2020-09-10 | 11.6 | 6.4 | 0 | 2019-09-10 | 8 | 10 | 0 | 2018-09-10 | 7.2 | 10.8 | 0 | 2017-09-10 | 7.9 | 10.1 | 0 | 2016-09-10 | 17.6 | 0.4 | 0 | 6 | 0
2025-09-10 | 11.9 | 6.1 | 0 | 2024-09-10 | 7.1 | 10.9 | 0 | 2023-09-10 | 15.8 | 2.2 | 0 | 2022-09-10 | 16.1 | 1.9 | 0 | 2021-09-10 | 13.6 | 4.4 | 0 | 2020-09-10 | 11.7 | 6.3 | 0 | 2019-09-10 | 7.2 | 10.8 | 0 | 2018-09-10 | 7 | 11 | 0 | 2017-09-10 | 8 | 10 | 0 | 2016-09-10 | 15.3 | 2.7 | 0 | 6.63 | 0
2025-09-10 | 10.5 | 7.5 | 0 | 2024-09-10 | 6.5 | 11.5 | 0 | 2023-09-10 | 15.2 | 2.8 | 0 | 2022-09-10 | 15.8 | 2.2 | 0 | 2021-09-10 | 13.6 | 4.4 | 0 | 2020-09-10 | 11.8 | 6.2 | 0 | 2019-09-10 | 5.7 | 12.3 | 0 | 2018-09-10 | 6.9 | 11.1 | 0 | 2017-09-10 | 6.9 | 11.1 | 0 | 2016-09-10 | 14.8 | 3.2 | 0 | 7.23 | 0
2025-09-10 | 10.8 | 7.2 | 0 | 2024-09-10 | 6.4 | 11.6 | 0 | 2023-09-10 | 14.9 | 3.1 | 0 | 2022-09-10 | 14.8 | 3.2 | 0 | 2021-09-10 | 13.5 | 4.5 | 0 | 2020-09-10 | 11.8 | 6.2 | 0 | 2019-09-10 | 6.1 | 11.9 | 0 | 2018-09-10 | 6.9 | 11.1 | 0 | 2017-09-10 | 6.8 | 11.2 | 0 | 2016-09-10 | 15.5 | 2.5 | 0 | 7.25 | 0
2025-09-10 | 8.7 | 9.3 | 0 | 2024-09-10 | 7 | 11 | 0 | 2023-09-10 | 15.2 | 2.8 | 0 | 2022-09-10 | 15.6 | 2.4 | 0 | 2021-09-10 | 13.8 | 4.2 | 0 | 2020-09-10 | 12 | 6 | 0 | 2019-09-10 | 4.4 | 13.6 | 0 | 2018-09-10 | 7.1 | 10.9 | 0 | 2017-09-10 | 7.8 | 10.2 | 0 | 2016-09-10 | 15 | 3 | 0 | 7.34 | 0
2025-09-10 | 8.3 | 9.7 | 0 | 2024-09-10 | 5.2 | 12.8 | 0 | 2023-09-10 | 14.8 | 3.2 | 0 | 2022-09-10 | 13.8 | 4.2 | 0 | 2021-09-10 | 11.9 | 6.1 | 0 | 2020-09-10 | 12 | 6 | 0 | 2019-09-10 | 5.5 | 12.5 | 0 | 2018-09-10 | 7.1 | 10.9 | 0 | 2017-09-10 | 7 | 11 | 0 | 2016-09-10 | 14.5 | 3.5 | 0 | 7.99 | 0
2025-09-10 | 8.7 | 9.3 | 0 | 2024-09-10 | 6 | 12 | 0 | 2023-09-10 | 14.9 | 3.1 | 0 | 2022-09-10 | 13.7 | 4.3 | 0 | 2021-09-10 | 11.5 | 6.5 | 0 | 2020-09-10 | 12.2 | 5.8 | 0 | 2019-09-10 | 5.8 | 12.2 | 0 | 2018-09-10 | 6.8 | 11.2 | 0 | 2017-09-10 | 7 | 11 | 0 | 2016-09-10 | 15.4 | 2.6 | 0 | 7.8 | 0
2025-09-10 | 10.4 | 7.6 | 0 | 2024-09-10 | 8.8 | 9.2 | 0 | 2023-09-10 | 15.8 | 2.2 | 0 | 2022-09-10 | 16.3 | 1.7 | 0 | 2021-09-10 | 13 | 5 | 0 | 2020-09-10 | 12.4 | 5.6 | 0 | 2019-09-10 | 8.1 | 9.9 | 0 | 2018-09-10 | 7.6 | 10.4 | 0 | 2017-09-10 | 8.8 | 9.2 | 0 | 2016-09-10 | 16.6 | 1.4 | 0 | 6.22 | 0
2025-09-10 | 13.1 | 4.9 | 0 | 2024-09-10 | 11.2 | 6.8 | 0 | 2023-09-10 | 16.1 | 1.9 | 0 | 2022-09-10 | 18.4 | 0 | 0.4 | 2021-09-10 | 13.6 | 4.4 | 0 | 2020-09-10 | 12.7 | 5.3 | 0 | 2019-09-10 | 10.6 | 7.4 | 0 | 2018-09-10 | 8.4 | 9.6 | 0 | 2017-09-10 | 11.4 | 6.6 | 0 | 2016-09-10 | 17.7 | 0.3 | 0 | 4.72 | 0.04
2025-09-10 | 16 | 2 | 0 | 2024-09-10 | 13.9 | 4.1 | 0 | 2023-09-10 | 17.2 | 0.8 | 0 | 2022-09-10 | 20.7 | 0 | 2.7 | 2021-09-10 | 14.8 | 3.2 | 0 | 2020-09-10 | 12.7 | 5.3 | 0 | 2019-09-10 | 11.9 | 6.1 | 0 | 2018-09-10 | 9.6 | 8.4 | 0 | 2017-09-10 | 13.9 | 4.1 | 0 | 2016-09-10 | 19.7 | 0 | 1.7 | 3.4 | 0.44
2025-09-10 | 17.2 | 0.8 | 0 | 2024-09-10 | 16.4 | 1.6 | 0 | 2023-09-10 | 17.8 | 0.2 | 0 | 2022-09-10 | 22.9 | 0 | 4.9 | 2021-09-10 | 15.8 | 2.2 | 0 | 2020-09-10 | 13.2 | 4.8 | 0 | 2019-09-10 | 13.8 | 4.2 | 0 | 2018-09-10 | 11.3 | 6.7 | 0 | 2017-09-10 | 15.9 | 2.1 | 0 | 2016-09-10 | 22.9 | 0 | 4.9 | 2.26 | 0.98
2025-09-10 | 18.8 | 0 | 0.8 | 2024-09-10 | 18.4 | 0 | 0.4 | 2023-09-10 | 18.2 | 0 | 0.2 | 2022-09-10 | 24.8 | 0 | 6.8 | 2021-09-10 | 17.4 | 0.6 | 0 | 2020-09-10 | 13.7 | 4.3 | 0 | 2019-09-10 | 15.3 | 2.7 | 0 | 2018-09-10 | 13.8 | 4.2 | 0 | 2017-09-10 | 17.9 | 0.1 | 0 | 2016-09-10 | 24.2 | 0 | 6.2 | 1.19 | 1.44
2025-09-10 | 21.5 | 0 | 3.5 | 2024-09-10 | 19.4 | 0 | 1.4 | 2023-09-10 | 19.6 | 0 | 1.6 | 2022-09-10 | 26.1 | 0 | 8.1 | 2021-09-10 | 18.4 | 0 | 0.4 | 2020-09-10 | 14.2 | 3.8 | 0 | 2019-09-10 | 15.8 | 2.2 | 0 | 2018-09-10 | 15.3 | 2.7 | 0 | 2017-09-10 | 18 | 0 | 0 | 2016-09-10 | 24.4 | 0 | 6.4 | 0.87 | 2.14
2025-09-10 | 22.6 | 0 | 4.6 | 2024-09-10 | 19.8 | 0 | 1.8 | 2023-09-10 | 19.4 | 0 | 1.4 | 2022-09-10 | 26.9 | 0 | 8.9 | 2021-09-10 | 19.5 | 0 | 1.5 | 2020-09-10 | 14.9 | 3.1 | 0 | 2019-09-10 | 16.3 | 1.7 | 0 | 2018-09-10 | 15.2 | 2.8 | 0 | 2017-09-10 | 19.3 | 0 | 1.3 | 2016-09-10 | 23.7 | 0 | 5.7 | 0.76 | 2.52
2025-09-10 | 23.7 | 0 | 5.7 | 2024-09-10 | 20.5 | 0 | 2.5 | 2023-09-10 | 19.9 | 0 | 1.9 | 2022-09-10 | 28.6 | 0 | 10.6 | 2021-09-10 | 18.8 | 0 | 0.8 | 2020-09-10 | 14.4 | 3.6 | 0 | 2019-09-10 | 16.5 | 1.5 | 0 | 2018-09-10 | 15.2 | 2.8 | 0 | 2017-09-10 | 19.7 | 0 | 1.7 | 2016-09-10 | 23.3 | 0 | 5.3 | 0.79 | 2.85
2025-09-10 | 23.9 | 0 | 5.9 | 2024-09-10 | 20.7 | 0 | 2.7 | 2023-09-10 | 21.1 | 0 | 3.1 | 2022-09-10 | 28.6 | 0 | 10.6 | 2021-09-10 | 20.9 | 0 | 2.9 | 2020-09-10 | 13.8 | 4.2 | 0 | 2019-09-10 | 16.2 | 1.8 | 0 | 2018-09-10 | 13.6 | 4.4 | 0 | 2017-09-10 | 19.9 | 0 | 1.9 | 2016-09-10 | 23.8 | 0 | 5.8 | 1.04 | 3.29
2025-09-10 | 23.4 | 0 | 5.4 | 2024-09-10 | 20.7 | 0 | 2.7 | 2023-09-10 | 20.4 | 0 | 2.4 | 2022-09-10 | 27.4 | 0 | 9.4 | 2021-09-10 | 19.7 | 0 | 1.7 | 2020-09-10 | 13.5 | 4.5 | 0 | 2019-09-10 | 15.1 | 2.9 | 0 | 2018-09-10 | 11.7 | 6.3 | 0 | 2017-09-10 | 19.9 | 0 | 1.9 | 2016-09-10 | 24.5 | 0 | 6.5 | 1.37 | 3
2025-09-10 | 23.4 | 0 | 5.4 | 2024-09-10 | 20.5 | 0 | 2.5 | 2023-09-10 | 20.1 | 0 | 2.1 | 2022-09-10 | 25.5 | 0 | 7.5 | 2021-09-10 | 18.2 | 0 | 0.2 | 2020-09-10 | 12.7 | 5.3 | 0 | 2019-09-10 | 15.4 | 2.6 | 0 | 2018-09-10 | 11.8 | 6.2 | 0 | 2017-09-10 | 19.6 | 0 | 1.6 | 2016-09-10 | 25.3 | 0 | 7.3 | 1.41 | 2.66
2025-09-10 | 20.6 | 0 | 2.6 | 2024-09-10 | 19.3 | 0 | 1.3 | 2023-09-10 | 18.2 | 0 | 0.2 | 2022-09-10 | 23.6 | 0 | 5.6 | 2021-09-10 | 17.4 | 0.6 | 0 | 2020-09-10 | 12.6 | 5.4 | 0 | 2019-09-10 | 15.2 | 2.8 | 0 | 2018-09-10 | 11.9 | 6.1 | 0 | 2017-09-10 | 16.6 | 1.4 | 0 | 2016-09-10 | 25.3 | 0 | 7.3 | 1.63 | 1.7
2025-09-10 | 20.1 | 0 | 2.1 | 2024-09-10 | 13.6 | 4.4 | 0 | 2023-09-10 | 15.9 | 2.1 | 0 | 2022-09-10 | 21.9 | 0 | 3.9 | 2021-09-10 | 16.1 | 1.9 | 0 | 2020-09-10 | 12.4 | 5.6 | 0 | 2019-09-10 | 14.7 | 3.3 | 0 | 2018-09-10 | 11.9 | 6.1 | 0 | 2017-09-10 | 14.2 | 3.8 | 0 | 2016-09-10 | 23.6 | 0 | 5.6 | 2.72 | 1.16
2025-09-10 | 15.8 | 2.2 | 0 | 2024-09-10 | 12.5 | 5.5 | 0 | 2023-09-10 | 15.3 | 2.7 | 0 | 2022-09-10 | 19.4 | 0 | 1.4 | 2021-09-10 | 14.7 | 3.3 | 0 | 2020-09-10 | 12.3 | 5.7 | 0 | 2019-09-10 | 14.8 | 3.2 | 0 | 2018-09-10 | 12 | 6 | 0 | 2017-09-10 | 12.6 | 5.4 | 0 | 2016-09-10 | 23.6 | 0 | 5.6 | 3.4 | 0.7
2025-09-10 | 14.8 | 3.2 | 0 | 2024-09-10 | 14.4 | 3.6 | 0 | 2023-09-10 | 15 | 3 | 0 | 2022-09-10 | 19 | 0 | 1 | 2021-09-10 | 13.1 | 4.9 | 0 | 2020-09-10 | 11.7 | 6.3 | 0 | 2019-09-10 | 14.9 | 3.1 | 0 | 2018-09-10 | 12.1 | 5.9 | 0 | 2017-09-10 | 12.1 | 5.9 | 0 | 2016-09-10 | 23.4 | 0 | 5.4 | 3.59 | 0.64
2025-09-10 | 15.3 | 2.7 | 0 | 2024-09-10 | 13.4 | 4.6 | 0 | 2023-09-10 | 13.3 | 4.7 | 0 | 2022-09-10 | 18.6 | 0 | 0.6 | 2021-09-10 | 13.8 | 4.2 | 0 | 2020-09-10 | 11.3 | 6.7 | 0 | 2019-09-10 | 14.8 | 3.2 | 0 | 2018-09-10 | 12.3 | 5.7 | 0 | 2017-09-10 | 10.8 | 7.2 | 0 | 2016-09-10 | 21.4 | 0 | 3.4 | 3.9 | 0.4
2025-09-10 | 12.7 | 5.3 | 0 | 2024-09-10 | 12.6 | 5.4 | 0 | 2023-09-10 | 14.2 | 3.8 | 0 | 2022-09-10 | 16.5 | 1.5 | 0 | 2021-09-10 | 13.8 | 4.2 | 0 | 2020-09-10 | 10.7 | 7.3 | 0 | 2019-09-10 | 14.8 | 3.2 | 0 | 2018-09-10 | 12.4 | 5.6 | 0 | 2017-09-10 | 10 | 8 | 0 | 2016-09-10 | 21 | 0 | 3 | 4.43 | 0.3
2025-09-11 | 13.5 | 4.5 | 0 | 2024-09-11 | 11.5 | 6.5 | 0 | 2023-09-11 | 13.4 | 4.6 | 0 | 2022-09-11 | 15.5 | 2.5 | 0 | 2021-09-11 | 14.2 | 3.8 | 0 | 2020-09-11 | 10.6 | 7.4 | 0 | 2019-09-11 | 15 | 3 | 0 | 2018-09-11 | 12.5 | 5.5 | 0 | 2017-09-11 | 10 | 8 | 0 | 2016-09-11 | 21 | 0 | 3 | 4.58 | 0.3
2025-09-11 | 12.8 | 5.2 | 0 | 2024-09-11 | 10.4 | 7.6 | 0 | 2023-09-11 | 13.5 | 4.5 | 0 | 2022-09-11 | 13.4 | 4.6 | 0 | 2021-09-11 | 13.1 | 4.9 | 0 | 2020-09-11 | 10.4 | 7.6 | 0 | 2019-09-11 | 15.1 | 2.9 | 0 | 2018-09-11 | 12.6 | 5.4 | 0 | 2017-09-11 | 9.1 | 8.9 | 0 | 2016-09-11 | 21.4 | 0 | 3.4 | 5.16 | 0.34
2025-09-11 | 12.5 | 5.5 | 0 | 2024-09-11 | 10.4 | 7.6 | 0 | 2023-09-11 | 12.6 | 5.4 | 0 | 2022-09-11 | 12.7 | 5.3 | 0 | 2021-09-11 | 12.4 | 5.6 | 0 | 2020-09-11 | 10.2 | 7.8 | 0 | 2019-09-11 | 16.1 | 1.9 | 0 | 2018-09-11 | 12.7 | 5.3 | 0 | 2017-09-11 | 7.6 | 10.4 | 0 | 2016-09-11 | 20.4 | 0 | 2.4 | 5.48 | 0.24
2025-09-11 | 12.1 | 5.9 | 0 | 2024-09-11 | 10 | 8 | 0 | 2023-09-11 | 12.9 | 5.1 | 0 | 2022-09-11 | 15.1 | 2.9 | 0 | 2021-09-11 | 10.7 | 7.3 | 0 | 2020-09-11 | 10 | 8 | 0 | 2019-09-11 | 16.3 | 1.7 | 0 | 2018-09-11 | 12.9 | 5.1 | 0 | 2017-09-11 | 8.1 | 9.9 | 0 | 2016-09-11 | 17.8 | 0.2 | 0 | 5.41 | 0
2025-09-11 | 13.2 | 4.8 | 0 | 2024-09-11 | 9.6 | 8.4 | 0 | 2023-09-11 | 12.4 | 5.6 | 0 | 2022-09-11 | 15 | 3 | 0 | 2021-09-11 | 10.8 | 7.2 | 0 | 2020-09-11 | 10 | 8 | 0 | 2019-09-11 | 16.7 | 1.3 | 0 | 2018-09-11 | 13.1 | 4.9 | 0 | 2017-09-11 | 8 | 10 | 0 | 2016-09-11 | 17.8 | 0.2 | 0 | 5.34 | 0
2025-09-11 | 11.7 | 6.3 | 0 | 2024-09-11 | 9.8 | 8.2 | 0 | 2023-09-11 | 12.6 | 5.4 | 0 | 2022-09-11 | 13.4 | 4.6 | 0 | 2021-09-11 | 9.6 | 8.4 | 0 | 2020-09-11 | 9.6 | 8.4 | 0 | 2019-09-11 | 17.2 | 0.8 | 0 | 2018-09-11 | 13.2 | 4.8 | 0 | 2017-09-11 | 8.2 | 9.8 | 0 | 2016-09-11 | 17.7 | 0.3 | 0 | 5.7 | 0
2025-09-11 | 13.7 | 4.3 | 0 | 2024-09-11 | 9.2 | 8.8 | 0 | 2023-09-11 | 13.4 | 4.6 | 0 | 2022-09-11 | 14.4 | 3.6 | 0 | 2021-09-11 | 9.9 | 8.1 | 0 | 2020-09-11 | 8.9 | 9.1 | 0 | 2019-09-11 | 17.6 | 0.4 | 0 | 2018-09-11 | 13.3 | 4.7 | 0 | 2017-09-11 | 8 | 10 | 0 | 2016-09-11 | 16.2 | 1.8 | 0 | 5.54 | 0
2025-09-11 | 16.1 | 1.9 | 0 | 2024-09-11 | 11.2 | 6.8 | 0 | 2023-09-11 | 14.1 | 3.9 | 0 | 2022-09-11 | 15.3 | 2.7 | 0 | 2021-09-11 | 12.4 | 5.6 | 0 | 2020-09-11 | 9.6 | 8.4 | 0 | 2019-09-11 | 18.4 | 0 | 0.4 | 2018-09-11 | 13.8 | 4.2 | 0 | 2017-09-11 | 10 | 8 | 0 | 2016-09-11 | 14.5 | 3.5 | 0 | 4.5 | 0.04
2025-09-11 | 16.5 | 1.5 | 0 | 2024-09-11 | 14 | 4 | 0 | 2023-09-11 | 15.6 | 2.4 | 0 | 2022-09-11 | 18.4 | 0 | 0.4 | 2021-09-11 | 15.3 | 2.7 | 0 | 2020-09-11 | 11.3 | 6.7 | 0 | 2019-09-11 | 19.9 | 0 | 1.9 | 2018-09-11 | 14.2 | 3.8 | 0 | 2017-09-11 | 12.8 | 5.2 | 0 | 2016-09-11 | 14.3 | 3.7 | 0 | 3 | 0.23
2025-09-11 | 17.4 | 0.6 | 0 | 2024-09-11 | 16.6 | 1.4 | 0 | 2023-09-11 | 17.6 | 0.4 | 0 | 2022-09-11 | 21.1 | 0 | 3.1 | 2021-09-11 | 17.9 | 0.1 | 0 | 2020-09-11 | 12.9 | 5.1 | 0 | 2019-09-11 | 23 | 0 | 5 | 2018-09-11 | 15 | 3 | 0 | 2017-09-11 | 15.5 | 2.5 | 0 | 2016-09-11 | 15.6 | 2.4 | 0 | 1.55 | 0.81
2025-09-11 | 19.6 | 0 | 1.6 | 2024-09-11 | 18.6 | 0 | 0.6 | 2023-09-11 | 20.3 | 0 | 2.3 | 2022-09-11 | 23.1 | 0 | 5.1 | 2021-09-11 | 19.7 | 0 | 1.7 | 2020-09-11 | 13.4 | 4.6 | 0 | 2019-09-11 | 23.3 | 0 | 5.3 | 2018-09-11 | 15.6 | 2.4 | 0 | 2017-09-11 | 18.1 | 0 | 0.1 | 2016-09-11 | 15.9 | 2.1 | 0 | 0.91 | 1.67
2025-09-11 | 20.9 | 0 | 2.9 | 2024-09-11 | 21.1 | 0 | 3.1 | 2023-09-11 | 20.9 | 0 | 2.9 | 2022-09-11 | 24.2 | 0 | 6.2 | 2021-09-11 | 19.8 | 0 | 1.8 | 2020-09-11 | 13.7 | 4.3 | 0 | 2019-09-11 | 24.4 | 0 | 6.4 | 2018-09-11 | 16.4 | 1.6 | 0 | 2017-09-11 | 20 | 0 | 2 | 2016-09-11 | 16.2 | 1.8 | 0 | 0.77 | 2.53
2025-09-11 | 21.5 | 0 | 3.5 | 2024-09-11 | 22.6 | 0 | 4.6 | 2023-09-11 | 22.4 | 0 | 4.4 | 2022-09-11 | 24.9 | 0 | 6.9 | 2021-09-11 | 19 | 0 | 1 | 2020-09-11 | 14.4 | 3.6 | 0 | 2019-09-11 | 25.1 | 0 | 7.1 | 2018-09-11 | 17.2 | 0.8 | 0 | 2017-09-11 | 20.9 | 0 | 2.9 | 2016-09-11 | 17.4 | 0.6 | 0 | 0.5 | 3.04
2025-09-11 | 22 | 0 | 4 | 2024-09-11 | 23.6 | 0 | 5.6 | 2023-09-11 | 23.9 | 0 | 5.9 | 2022-09-11 | 25.4 | 0 | 7.4 | 2021-09-11 | 21.3 | 0 | 3.3 | 2020-09-11 | 15.3 | 2.7 | 0 | 2019-09-11 | 25.4 | 0 | 7.4 | 2018-09-11 | 17.6 | 0.4 | 0 | 2017-09-11 | 21.9 | 0 | 3.9 | 2016-09-11 | 18 | 0 | 0 | 0.31 | 3.75
2025-09-11 | 23.2 | 0 | 5.2 | 2024-09-11 | 24.1 | 0 | 6.1 | 2023-09-11 | 23.9 | 0 | 5.9 | 2022-09-11 | 25.2 | 0 | 7.2 | 2021-09-11 | 22.7 | 0 | 4.7 | 2020-09-11 | 16.1 | 1.9 | 0 | 2019-09-11 | 25.2 | 0 | 7.2 | 2018-09-11 | 18.2 | 0 | 0.2 | 2017-09-11 | 22.1 | 0 | 4.1 | 2016-09-11 | 19.1 | 0 | 1.1 | 0.19 | 4.17
2025-09-11 | 22.3 | 0 | 4.3 | 2024-09-11 | 24.3 | 0 | 6.3 | 2023-09-11 | 23.6 | 0 | 5.6 | 2022-09-11 | 24.2 | 0 | 6.2 | 2021-09-11 | 23.4 | 0 | 5.4 | 2020-09-11 | 16.2 | 1.8 | 0 | 2019-09-11 | 23.4 | 0 | 5.4 | 2018-09-11 | 18.4 | 0 | 0.4 | 2017-09-11 | 22.4 | 0 | 4.4 | 2016-09-11 | 19.2 | 0 | 1.2 | 0.18 | 3.92
2025-09-11 | 21.7 | 0 | 3.7 | 2024-09-11 | 22.9 | 0 | 4.9 | 2023-09-11 | 23.8 | 0 | 5.8 | 2022-09-11 | 23.4 | 0 | 5.4 | 2021-09-11 | 23.6 | 0 | 5.6 | 2020-09-11 | 17 | 1 | 0 | 2019-09-11 | 21.5 | 0 | 3.5 | 2018-09-11 | 18.5 | 0 | 0.5 | 2017-09-11 | 22.6 | 0 | 4.6 | 2016-09-11 | 18.9 | 0 | 0.9 | 0.1 | 3.49
2025-09-11 | 21.4 | 0 | 3.4 | 2024-09-11 | 22.7 | 0 | 4.7 | 2023-09-11 | 22 | 0 | 4 | 2022-09-11 | 22.2 | 0 | 4.2 | 2021-09-11 | 22.4 | 0 | 4.4 | 2020-09-11 | 16.3 | 1.7 | 0 | 2019-09-11 | 19.3 | 0 | 1.3 | 2018-09-11 | 18.4 | 0 | 0.4 | 2017-09-11 | 21.6 | 0 | 3.6 | 2016-09-11 | 18.6 | 0 | 0.6 | 0.17 | 2.66
2025-09-11 | 18.8 | 0 | 0.8 | 2024-09-11 | 20.4 | 0 | 2.4 | 2023-09-11 | 19.9 | 0 | 1.9 | 2022-09-11 | 21.2 | 0 | 3.2 | 2021-09-11 | 21.8 | 0 | 3.8 | 2020-09-11 | 14.3 | 3.7 | 0 | 2019-09-11 | 16.7 | 1.3 | 0 | 2018-09-11 | 18.1 | 0 | 0.1 | 2017-09-11 | 18.6 | 0 | 0.6 | 2016-09-11 | 16.8 | 1.2 | 0 | 0.62 | 1.28
2025-09-11 | 16.6 | 1.4 | 0 | 2024-09-11 | 18.7 | 0 | 0.7 | 2023-09-11 | 17.7 | 0.3 | 0 | 2022-09-11 | 20.3 | 0 | 2.3 | 2021-09-11 | 21.5 | 0 | 3.5 | 2020-09-11 | 13.8 | 4.2 | 0 | 2019-09-11 | 16 | 2 | 0 | 2018-09-11 | 17.7 | 0.3 | 0 | 2017-09-11 | 17.5 | 0.5 | 0 | 2016-09-11 | 14.2 | 3.8 | 0 | 1.25 | 0.65
2025-09-11 | 15.3 | 2.7 | 0 | 2024-09-11 | 18.6 | 0 | 0.6 | 2023-09-11 | 17.7 | 0.3 | 0 | 2022-09-11 | 19.1 | 0 | 1.1 | 2021-09-11 | 20.6 | 0 | 2.6 | 2020-09-11 | 10.6 | 7.4 | 0 | 2019-09-11 | 15.2 | 2.8 | 0 | 2018-09-11 | 17.6 | 0.4 | 0 | 2017-09-11 | 16.6 | 1.4 | 0 | 2016-09-11 | 12.8 | 5.2 | 0 | 2.02 | 0.43
2025-09-11 | 13.7 | 4.3 | 0 | 2024-09-11 | 17.2 | 0.8 | 0 | 2023-09-11 | 15.9 | 2.1 | 0 | 2022-09-11 | 18.5 | 0 | 0.5 | 2021-09-11 | 20.3 | 0 | 2.3 | 2020-09-11 | 8.5 | 9.5 | 0 | 2019-09-11 | 14.6 | 3.4 | 0 | 2018-09-11 | 17.1 | 0.9 | 0 | 2017-09-11 | 15.3 | 2.7 | 0 | 2016-09-11 | 12.1 | 5.9 | 0 | 2.96 | 0.28
2025-09-11 | 12.1 | 5.9 | 0 | 2024-09-11 | 16.6 | 1.4 | 0 | 2023-09-11 | 15.8 | 2.2 | 0 | 2022-09-11 | 17.8 | 0.2 | 0 | 2021-09-11 | 20.1 | 0 | 2.1 | 2020-09-11 | 8.9 | 9.1 | 0 | 2019-09-11 | 14.1 | 3.9 | 0 | 2018-09-11 | 17.1 | 0.9 | 0 | 2017-09-11 | 13.8 | 4.2 | 0 | 2016-09-11 | 10.5 | 7.5 | 0 | 3.53 | 0.21
2025-09-11 | 11.9 | 6.1 | 0 | 2024-09-11 | 15.5 | 2.5 | 0 | 2023-09-11 | 14.2 | 3.8 | 0 | 2022-09-11 | 17.9 | 0.1 | 0 | 2021-09-11 | 19.8 | 0 | 1.8 | 2020-09-11 | 5.6 | 12.4 | 0 | 2019-09-11 | 13.6 | 4.4 | 0 | 2018-09-11 | 16.9 | 1.1 | 0 | 2017-09-11 | 13.6 | 4.4 | 0 | 2016-09-11 | 10.9 | 7.1 | 0 | 4.19 | 0.18
2025-09-12 | 10.9 | 7.1 | 0 | 2024-09-12 | 15.2 | 2.8 | 0 | 2023-09-12 | 14.7 | 3.3 | 0 | 2022-09-12 | 17.1 | 0.9 | 0 | 2021-09-12 | 19.9 | 0 | 1.9 | 2020-09-12 | 7.9 | 10.1 | 0 | 2019-09-12 | 13.4 | 4.6 | 0 | 2018-09-12 | 15.5 | 2.5 | 0 | 2017-09-12 | 12.8 | 5.2 | 0 | 2016-09-12 | 11 | 7 | 0 | 4.35 | 0.19
2025-09-12 | 10.5 | 7.5 | 0 | 2024-09-12 | 14.9 | 3.1 | 0 | 2023-09-12 | 14.2 | 3.8 | 0 | 2022-09-12 | 16.7 | 1.3 | 0 | 2021-09-12 | 21.4 | 0 | 3.4 | 2020-09-12 | 5.6 | 12.4 | 0 | 2019-09-12 | 13.3 | 4.7 | 0 | 2018-09-12 | 14.5 | 3.5 | 0 | 2017-09-12 | 11.7 | 6.3 | 0 | 2016-09-12 | 10.2 | 7.8 | 0 | 5.04 | 0.34
2025-09-12 | 10.2 | 7.8 | 0 | 2024-09-12 | 14.5 | 3.5 | 0 | 2023-09-12 | 13.6 | 4.4 | 0 | 2022-09-12 | 15.9 | 2.1 | 0 | 2021-09-12 | 18.3 | 0 | 0.3 | 2020-09-12 | 5 | 13 | 0 | 2019-09-12 | 13 | 5 | 0 | 2018-09-12 | 14.9 | 3.1 | 0 | 2017-09-12 | 11.5 | 6.5 | 0 | 2016-09-12 | 9.5 | 8.5 | 0 | 5.39 | 0.03
2025-09-12 | 9.8 | 8.2 | 0 | 2024-09-12 | 13.7 | 4.3 | 0 | 2023-09-12 | 13 | 5 | 0 | 2022-09-12 | 15.3 | 2.7 | 0 | 2021-09-12 | 17.7 | 0.3 | 0 | 2020-09-12 | 5.2 | 12.8 | 0 | 2019-09-12 | 12.8 | 5.2 | 0 | 2018-09-12 | 13.8 | 4.2 | 0 | 2017-09-12 | 11.4 | 6.6 | 0 | 2016-09-12 | 10.5 | 7.5 | 0 | 5.68 | 0
2025-09-12 | 8.1 | 9.9 | 0 | 2024-09-12 | 13.9 | 4.1 | 0 | 2023-09-12 | 12.9 | 5.1 | 0 | 2022-09-12 | 15.7 | 2.3 | 0 | 2021-09-12 | 17.8 | 0.2 | 0 | 2020-09-12 | 5.3 | 12.7 | 0 | 2019-09-12 | 11.7 | 6.3 | 0 | 2018-09-12 | 13.5 | 4.5 | 0 | 2017-09-12 | 10.4 | 7.6 | 0 | 2016-09-12 | 9 | 9 | 0 | 6.17 | 0
2025-09-12 | 9.2 | 8.8 | 0 | 2024-09-12 | 14.2 | 3.8 | 0 | 2023-09-12 | 13.7 | 4.3 | 0 | 2022-09-12 | 14.4 | 3.6 | 0 | 2021-09-12 | 18 | 0 | 0 | 2020-09-12 | 5.4 | 12.6 | 0 | 2019-09-12 | 11.1 | 6.9 | 0 | 2018-09-12 | 13.5 | 4.5 | 0 | 2017-09-12 | 9.9 | 8.1 | 0 | 2016-09-12 | 7.5 | 10.5 | 0 | 6.31 | 0
2025-09-12 | 6.8 | 11.2 | 0 | 2024-09-12 | 14.4 | 3.6 | 0 | 2023-09-12 | 13.8 | 4.2 | 0 | 2022-09-12 | 13.9 | 4.1 | 0 | 2021-09-12 | 17.8 | 0.2 | 0 | 2020-09-12 | 4.7 | 13.3 | 0 | 2019-09-12 | 10.9 | 7.1 | 0 | 2018-09-12 | 13.2 | 4.8 | 0 | 2017-09-12 | 9.8 | 8.2 | 0 | 2016-09-12 | 8.6 | 9.4 | 0 | 6.61 | 0
2025-09-12 | 10.3 | 7.7 | 0 | 2024-09-12 | 15.6 | 2.4 | 0 | 2023-09-12 | 14.3 | 3.7 | 0 | 2022-09-12 | 15.8 | 2.2 | 0 | 2021-09-12 | 17.9 | 0.1 | 0 | 2020-09-12 | 7.2 | 10.8 | 0 | 2019-09-12 | 12 | 6 | 0 | 2018-09-12 | 14.9 | 3.1 | 0 | 2017-09-12 | 11.4 | 6.6 | 0 | 2016-09-12 | 11 | 7 | 0 | 4.96 | 0
2025-09-12 | 12.3 | 5.7 | 0 | 2024-09-12 | 16.4 | 1.6 | 0 | 2023-09-12 | 15.5 | 2.5 | 0 | 2022-09-12 | 18.2 | 0 | 0.2 | 2021-09-12 | 18 | 0 | 0 | 2020-09-12 | 9.7 | 8.3 | 0 | 2019-09-12 | 13.7 | 4.3 | 0 | 2018-09-12 | 16.2 | 1.8 | 0 | 2017-09-12 | 14.1 | 3.9 | 0 | 2016-09-12 | 14.7 | 3.3 | 0 | 3.14 | 0.02
2025-09-12 | 13.9 | 4.1 | 0 | 2024-09-12 | 19.5 | 0 | 1.5 | 2023-09-12 | 16.6 | 1.4 | 0 | 2022-09-12 | 20.8 | 0 | 2.8 | 2021-09-12 | 18 | 0 | 0 | 2020-09-12 | 13.3 | 4.7 | 0 | 2019-09-12 | 15 | 3 | 0 | 2018-09-12 | 17.9 | 0.1 | 0 | 2017-09-12 | 17 | 1 | 0 | 2016-09-12 | 17.6 | 0.4 | 0 | 1.47 | 0.43
2025-09-12 | 15.8 | 2.2 | 0 | 2024-09-12 | 21.5 | 0 | 3.5 | 2023-09-12 | 17.8 | 0.2 | 0 | 2022-09-12 | 21.3 | 0 | 3.3 | 2021-09-12 | 18.6 | 0 | 0.6 | 2020-09-12 | 15.7 | 2.3 | 0 | 2019-09-12 | 16.8 | 1.2 | 0 | 2018-09-12 | 19.3 | 0 | 1.3 | 2017-09-12 | 19.3 | 0 | 1.3 | 2016-09-12 | 19.6 | 0 | 1.6 | 0.59 | 1.16
2025-09-12 | 17.6 | 0.4 | 0 | 2024-09-12 | 22.8 | 0 | 4.8 | 2023-09-12 | 18.3 | 0 | 0.3 | 2022-09-12 | 23.1 | 0 | 5.1 | 2021-09-12 | 19.7 | 0 | 1.7 | 2020-09-12 | 17 | 1 | 0 | 2019-09-12 | 17.4 | 0.6 | 0 | 2018-09-12 | 20.3 | 0 | 2.3 | 2017-09-12 | 21.5 | 0 | 3.5 | 2016-09-12 | 21.4 | 0 | 3.4 | 0.2 | 2.11
2025-09-12 | 19.2 | 0 | 1.2 | 2024-09-12 | 23.1 | 0 | 5.1 | 2023-09-12 | 19.3 | 0 | 1.3 | 2022-09-12 | 23.1 | 0 | 5.1 | 2021-09-12 | 20 | 0 | 2 | 2020-09-12 | 17.9 | 0.1 | 0 | 2019-09-12 | 19.1 | 0 | 1.1 | 2018-09-12 | 20.8 | 0 | 2.8 | 2017-09-12 | 22.9 | 0 | 4.9 | 2016-09-12 | 22.3 | 0 | 4.3 | 0.01 | 2.78
2025-09-12 | 20.1 | 0 | 2.1 | 2024-09-12 | 24.4 | 0 | 6.4 | 2023-09-12 | 19.1 | 0 | 1.1 | 2022-09-12 | 24.1 | 0 | 6.1 | 2021-09-12 | 22.1 | 0 | 4.1 | 2020-09-12 | 18.9 | 0 | 0.9 | 2019-09-12 | 18.8 | 0 | 0.8 | 2018-09-12 | 22.5 | 0 | 4.5 | 2017-09-12 | 23.9 | 0 | 5.9 | 2016-09-12 | 23 | 0 | 5 | 0 | 3.69
2025-09-12 | 20.6 | 0 | 2.6 | 2024-09-12 | 24.9 | 0 | 6.9 | 2023-09-12 | 19.3 | 0 | 1.3 | 2022-09-12 | 24.1 | 0 | 6.1 | 2021-09-12 | 21.5 | 0 | 3.5 | 2020-09-12 | 19.8 | 0 | 1.8 | 2019-09-12 | 19.3 | 0 | 1.3 | 2018-09-12 | 22 | 0 | 4 | 2017-09-12 | 24.4 | 0 | 6.4 | 2016-09-12 | 23.3 | 0 | 5.3 | 0 | 3.92
2025-09-12 | 21.4 | 0 | 3.4 | 2024-09-12 | 25.3 | 0 | 7.3 | 2023-09-12 | 19.2 | 0 | 1.2 | 2022-09-12 | 23.8 | 0 | 5.8 | 2021-09-12 | 21.2 | 0 | 3.2 | 2020-09-12 | 20.3 | 0 | 2.3 | 2019-09-12 | 19.5 | 0 | 1.5 | 2018-09-12 | 21.9 | 0 | 3.9 | 2017-09-12 | 25.4 | 0 | 7.4 | 2016-09-12 | 23.4 | 0 | 5.4 | 0 | 4.14
2025-09-12 | 20.9 | 0 | 2.9 | 2024-09-12 | 24.5 | 0 | 6.5 | 2023-09-12 | 19 | 0 | 1 | 2022-09-12 | 23.6 | 0 | 5.6 | 2021-09-12 | 21.6 | 0 | 3.6 | 2020-09-12 | 19.9 | 0 | 1.9 | 2019-09-12 | 19.6 | 0 | 1.6 | 2018-09-12 | 23.1 | 0 | 5.1 | 2017-09-12 | 25.1 | 0 | 7.1 | 2016-09-12 | 23.6 | 0 | 5.6 | 0 | 4.09
2025-09-12 | 19.8 | 0 | 1.8 | 2024-09-12 | 23.3 | 0 | 5.3 | 2023-09-12 | 19.2 | 0 | 1.2 | 2022-09-12 | 23.5 | 0 | 5.5 | 2021-09-12 | 21.2 | 0 | 3.2 | 2020-09-12 | 18.7 | 0 | 0.7 | 2019-09-12 | 18.9 | 0 | 0.9 | 2018-09-12 | 22.4 | 0 | 4.4 | 2017-09-12 | 24.2 | 0 | 6.2 | 2016-09-12 | 22.7 | 0 | 4.7 | 0 | 3.39
2025-09-12 | 18.3 | 0 | 0.3 | 2024-09-12 | 21.4 | 0 | 3.4 | 2023-09-12 | 18.4 | 0 | 0.4 | 2022-09-12 | 23.2 | 0 | 5.2 | 2021-09-12 | 18.4 | 0 | 0.4 | 2020-09-12 | 16.5 | 1.5 | 0 | 2019-09-12 | 17.1 | 0.9 | 0 | 2018-09-12 | 20.4 | 0 | 2.4 | 2017-09-12 | 21.6 | 0 | 3.6 | 2016-09-12 | 20.5 | 0 | 2.5 | 0.24 | 1.82
2025-09-12 | 15.9 | 2.1 | 0 | 2024-09-12 | 17.4 | 0.6 | 0 | 2023-09-12 | 18.4 | 0 | 0.4 | 2022-09-12 | 22.3 | 0 | 4.3 | 2021-09-12 | 16.8 | 1.2 | 0 | 2020-09-12 | 15.2 | 2.8 | 0 | 2019-09-12 | 15.1 | 2.9 | 0 | 2018-09-12 | 18.5 | 0 | 0.5 | 2017-09-12 | 19.4 | 0 | 1.4 | 2016-09-12 | 18.1 | 0 | 0.1 | 0.96 | 0.67
2025-09-12 | 14.6 | 3.4 | 0 | 2024-09-12 | 17.9 | 0.1 | 0 | 2023-09-12 | 18.6 | 0 | 0.6 | 2022-09-12 | 20.4 | 0 | 2.4 | 2021-09-12 | 15 | 3 | 0 | 2020-09-12 | 14.3 | 3.7 | 0 | 2019-09-12 | 14.2 | 3.8 | 0 | 2018-09-12 | 15.8 | 2.2 | 0 | 2017-09-12 | 17.7 | 0.3 | 0 | 2016-09-12 | 17.1 | 0.9 | 0 | 1.74 | 0.3
2025-09-12 | 13.2 | 4.8 | 0 | 2024-09-12 | 18.5 | 0 | 0.5 | 2023-09-12 | 19.1 | 0 | 1.1 | 2022-09-12 | 20.3 | 0 | 2.3 | 2021-09-12 | 15.5 | 2.5 | 0 | 2020-09-12 | 14.7 | 3.3 | 0 | 2019-09-12 | 13.3 | 4.7 | 0 | 2018-09-12 | 17.1 | 0.9 | 0 | 2017-09-12 | 17.1 | 0.9 | 0 | 2016-09-12 | 16.2 | 1.8 | 0 | 1.89 | 0.39
2025-09-12 | 12 | 6 | 0 | 2024-09-12 | 17.4 | 0.6 | 0 | 2023-09-12 | 19.2 | 0 | 1.2 | 2022-09-12 | 20.2 | 0 | 2.2 | 2021-09-12 | 16.6 | 1.4 | 0 | 2020-09-12 | 14.4 | 3.6 | 0 | 2019-09-12 | 10.9 | 7.1 | 0 | 2018-09-12 | 15.3 | 2.7 | 0 | 2017-09-12 | 16.4 | 1.6 | 0 | 2016-09-12 | 14.5 | 3.5 | 0 | 2.65 | 0.34
2025-09-12 | 14 | 4 | 0 | 2024-09-12 | 16 | 2 | 0 | 2023-09-12 | 18.8 | 0 | 0.8 | 2022-09-12 | 20 | 0 | 2 | 2021-09-12 | 16.6 | 1.4 | 0 | 2020-09-12 | 14.1 | 3.9 | 0 | 2019-09-12 | 10 | 8 | 0 | 2018-09-12 | 15.6 | 2.4 | 0 | 2017-09-12 | 15.2 | 2.8 | 0 | 2016-09-12 | 13.1 | 4.9 | 0 | 2.94 | 0.28
2025-09-13 | 13.1 | 4.9 | 0 | 2024-09-13 | 16.3 | 1.7 | 0 | 2023-09-13 | 18.4 | 0 | 0.4 | 2022-09-13 | 19.7 | 0 | 1.7 | 2021-09-13 | 15.3 | 2.7 | 0 | 2020-09-13 | 14.9 | 3.1 | 0 | 2019-09-13 | 9.2 | 8.8 | 0 | 2018-09-13 | 15.1 | 2.9 | 0 | 2017-09-13 | 15 | 3 | 0 | 2016-09-13 | 12.3 | 5.7 | 0 | 3.28 | 0.21
2025-09-13 | 12.6 | 5.4 | 0 | 2024-09-13 | 14.4 | 3.6 | 0 | 2023-09-13 | 17.9 | 0.1 | 0 | 2022-09-13 | 19.4 | 0 | 1.4 | 2021-09-13 | 16.3 | 1.7 | 0 | 2020-09-13 | 15.8 | 2.2 | 0 | 2019-09-13 | 7.9 | 10.1 | 0 | 2018-09-13 | 13.8 | 4.2 | 0 | 2017-09-13 | 14.1 | 3.9 | 0 | 2016-09-13 | 12.1 | 5.9 | 0 | 3.71 | 0.14
2025-09-13 | 12.7 | 5.3 | 0 | 2024-09-13 | 14.4 | 3.6 | 0 | 2023-09-13 | 18 | 0 | 0 | 2022-09-13 | 18.8 | 0 | 0.8 | 2021-09-13 | 14.7 | 3.3 | 0 | 2020-09-13 | 16.1 | 1.9 | 0 | 2019-09-13 | 7.5 | 10.5 | 0 | 2018-09-13 | 13.4 | 4.6 | 0 | 2017-09-13 | 12.8 | 5.2 | 0 | 2016-09-13 | 11.5 | 6.5 | 0 | 4.09 | 0.08
2025-09-13 | 12.2 | 5.8 | 0 | 2024-09-13 | 14.3 | 3.7 | 0 | 2023-09-13 | 17.7 | 0.3 | 0 | 2022-09-13 | 17.9 | 0.1 | 0 | 2021-09-13 | 14.2 | 3.8 | 0 | 2020-09-13 | 16.1 | 1.9 | 0 | 2019-09-13 | 8.2 | 9.8 | 0 | 2018-09-13 | 13.7 | 4.3 | 0 | 2017-09-13 | 12.6 | 5.4 | 0 | 2016-09-13 | 11.4 | 6.6 | 0 | 4.17 | 0
2025-09-13 | 11.8 | 6.2 | 0 | 2024-09-13 | 14.1 | 3.9 | 0 | 2023-09-13 | 17.1 | 0.9 | 0 | 2022-09-13 | 18.1 | 0 | 0.1 | 2021-09-13 | 11.7 | 6.3 | 0 | 2020-09-13 | 14.8 | 3.2 | 0 | 2019-09-13 | 7.2 | 10.8 | 0 | 2018-09-13 | 13.7 | 4.3 | 0 | 2017-09-13 | 12.1 | 5.9 | 0 | 2016-09-13 | 11.2 | 6.8 | 0 | 4.83 | 0.01
2025-09-13 | 11.6 | 6.4 | 0 | 2024-09-13 | 13.1 | 4.9 | 0 | 2023-09-13 | 16.3 | 1.7 | 0 | 2022-09-13 | 17 | 1 | 0 | 2021-09-13 | 11.1 | 6.9 | 0 | 2020-09-13 | 14.9 | 3.1 | 0 | 2019-09-13 | 6.6 | 11.4 | 0 | 2018-09-13 | 12.2 | 5.8 | 0 | 2017-09-13 | 11.7 | 6.3 | 0 | 2016-09-13 | 10.4 | 7.6 | 0 | 5.51 | 0
2025-09-13 | 11.2 | 6.8 | 0 | 2024-09-13 | 14.2 | 3.8 | 0 | 2023-09-13 | 14.6 | 3.4 | 0 | 2022-09-13 | 15.8 | 2.2 | 0 | 2021-09-13 | 11.6 | 6.4 | 0 | 2020-09-13 | 15 | 3 | 0 | 2019-09-13 | 6.6 | 11.4 | 0 | 2018-09-13 | 12.7 | 5.3 | 0 | 2017-09-13 | 10.9 | 7.1 | 0 | 2016-09-13 | 10.1 | 7.9 | 0 | 5.73 | 0
2025-09-13 | 11.7 | 6.3 | 0 | 2024-09-13 | 15.3 | 2.7 | 0 | 2023-09-13 | 15.4 | 2.6 | 0 | 2022-09-13 | 17.1 | 0.9 | 0 | 2021-09-13 | 14 | 4 | 0 | 2020-09-13 | 14 | 4 | 0 | 2019-09-13 | 8.7 | 9.3 | 0 | 2018-09-13 | 14.9 | 3.1 | 0 | 2017-09-13 | 13.3 | 4.7 | 0 | 2016-09-13 | 12.2 | 5.8 | 0 | 4.34 | 0
2025-09-13 | 14.5 | 3.5 | 0 | 2024-09-13 | 17.5 | 0.5 | 0 | 2023-09-13 | 17.3 | 0.7 | 0 | 2022-09-13 | 19.2 | 0 | 1.2 | 2021-09-13 | 15.7 | 2.3 | 0 | 2020-09-13 | 14.9 | 3.1 | 0 | 2019-09-13 | 11 | 7 | 0 | 2018-09-13 | 17.4 | 0.6 | 0 | 2017-09-13 | 16.3 | 1.7 | 0 | 2016-09-13 | 16.2 | 1.8 | 0 | 2.12 | 0.12
2025-09-13 | 16.1 | 1.9 | 0 | 2024-09-13 | 19.6 | 0 | 1.6 | 2023-09-13 | 18.9 | 0 | 0.9 | 2022-09-13 | 20.3 | 0 | 2.3 | 2021-09-13 | 17.4 | 0.6 | 0 | 2020-09-13 | 15.4 | 2.6 | 0 | 2019-09-13 | 13.9 | 4.1 | 0 | 2018-09-13 | 19.8 | 0 | 1.8 | 2017-09-13 | 19 | 0 | 1 | 2016-09-13 | 19.5 | 0 | 1.5 | 0.92 | 0.91
2025-09-13 | 18.1 | 0 | 0.1 | 2024-09-13 | 22.4 | 0 | 4.4 | 2023-09-13 | 21 | 0 | 3 | 2022-09-13 | 21.2 | 0 | 3.2 | 2021-09-13 | 18.8 | 0 | 0.8 | 2020-09-13 | 15.4 | 2.6 | 0 | 2019-09-13 | 16.3 | 1.7 | 0 | 2018-09-13 | 21.9 | 0 | 3.9 | 2017-09-13 | 21.3 | 0 | 3.3 | 2016-09-13 | 22.5 | 0 | 4.5 | 0.43 | 2.32
2025-09-13 | 19.6 | 0 | 1.6 | 2024-09-13 | 24.1 | 0 | 6.1 | 2023-09-13 | 20.1 | 0 | 2.1 | 2022-09-13 | 20.9 | 0 | 2.9 | 2021-09-13 | 19.5 | 0 | 1.5 | 2020-09-13 | 15.5 | 2.5 | 0 | 2019-09-13 | 17.7 | 0.3 | 0 | 2018-09-13 | 23.2 | 0 | 5.2 | 2017-09-13 | 23.6 | 0 | 5.6 | 2016-09-13 | 24.4 | 0 | 6.4 | 0.28 | 3.14
2025-09-13 | 20.1 | 0 | 2.1 | 2024-09-13 | 25.7 | 0 | 7.7 | 2023-09-13 | 20.2 | 0 | 2.2 | 2022-09-13 | 19 | 0 | 1 | 2021-09-13 | 19.4 | 0 | 1.4 | 2020-09-13 | 15.6 | 2.4 | 0 | 2019-09-13 | 19.9 | 0 | 1.9 | 2018-09-13 | 24.3 | 0 | 6.3 | 2017-09-13 | 24.1 | 0 | 6.1 | 2016-09-13 | 25.2 | 0 | 7.2 | 0.24 | 3.59
2025-09-13 | 20.8 | 0 | 2.8 | 2024-09-13 | 26.5 | 0 | 8.5 | 2023-09-13 | 20.3 | 0 | 2.3 | 2022-09-13 | 18 | 0 | 0 | 2021-09-13 | 21.1 | 0 | 3.1 | 2020-09-13 | 16.3 | 1.7 | 0 | 2019-09-13 | 19.6 | 0 | 1.6 | 2018-09-13 | 25.1 | 0 | 7.1 | 2017-09-13 | 26.2 | 0 | 8.2 | 2016-09-13 | 26.5 | 0 | 8.5 | 0.17 | 4.21
2025-09-13 | 21.2 | 0 | 3.2 | 2024-09-13 | 27.5 | 0 | 9.5 | 2023-09-13 | 20.9 | 0 | 2.9 | 2022-09-13 | 17.7 | 0.3 | 0 | 2021-09-13 | 21.1 | 0 | 3.1 | 2020-09-13 | 17.6 | 0.4 | 0 | 2019-09-13 | 20.1 | 0 | 2.1 | 2018-09-13 | 25.6 | 0 | 7.6 | 2017-09-13 | 26.3 | 0 | 8.3 | 2016-09-13 | 26.9 | 0 | 8.9 | 0.07 | 4.56
2025-09-13 | 22.5 | 0 | 4.5 | 2024-09-13 | 27.3 | 0 | 9.3 | 2023-09-13 | 19.6 | 0 | 1.6 | 2022-09-13 | 18.2 | 0 | 0.2 | 2021-09-13 | 21.6 | 0 | 3.6 | 2020-09-13 | 19.1 | 0 | 1.1 | 2019-09-13 | 19 | 0 | 1 | 2018-09-13 | 26.2 | 0 | 8.2 | 2017-09-13 | 26.5 | 0 | 8.5 | 2016-09-13 | 26.4 | 0 | 8.4 | 0 | 4.64
2025-09-13 | 21.5 | 0 | 3.5 | 2024-09-13 | 27.1 | 0 | 9.1 | 2023-09-13 | 20.1 | 0 | 2.1 | 2022-09-13 | 18.5 | 0 | 0.5 | 2021-09-13 | 20.6 | 0 | 2.6 | 2020-09-13 | 20.5 | 0 | 2.5 | 2019-09-13 | 20.2 | 0 | 2.2 | 2018-09-13 | 25.9 | 0 | 7.9 | 2017-09-13 | 25.5 | 0 | 7.5 | 2016-09-13 | 25.3 | 0 | 7.3 | 0 | 4.52
2025-09-13 | 21.5 | 0 | 3.5 | 2024-09-13 | 26 | 0 | 8 | 2023-09-13 | 18.5 | 0 | 0.5 | 2022-09-13 | 18.4 | 0 | 0.4 | 2021-09-13 | 19.7 | 0 | 1.7 | 2020-09-13 | 21.3 | 0 | 3.3 | 2019-09-13 | 19.2 | 0 | 1.2 | 2018-09-13 | 25.1 | 0 | 7.1 | 2017-09-13 | 23.7 | 0 | 5.7 | 2016-09-13 | 24.9 | 0 | 6.9 | 0 | 3.83
2025-09-13 | 19.3 | 0 | 1.3 | 2024-09-13 | 23.5 | 0 | 5.5 | 2023-09-13 | 18 | 0 | 0 | 2022-09-13 | 17.4 | 0.6 | 0 | 2021-09-13 | 18.2 | 0 | 0.2 | 2020-09-13 | 20.6 | 0 | 2.6 | 2019-09-13 | 18.2 | 0 | 0.2 | 2018-09-13 | 22.8 | 0 | 4.8 | 2017-09-13 | 22 | 0 | 4 | 2016-09-13 | 23.3 | 0 | 5.3 | 0.06 | 2.39
2025-09-13 | 18.3 | 0 | 0.3 | 2024-09-13 | 22.3 | 0 | 4.3 | 2023-09-13 | 17.2 | 0.8 | 0 | 2022-09-13 | 17.2 | 0.8 | 0 | 2021-09-13 | 16.7 | 1.3 | 0 | 2020-09-13 | 18.7 | 0 | 0.7 | 2019-09-13 | 18.2 | 0 | 0.2 | 2018-09-13 | 20.5 | 0 | 2.5 | 2017-09-13 | 20.6 | 0 | 2.6 | 2016-09-13 | 22.1 | 0 | 4.1 | 0.29 | 1.47
2025-09-13 | 17.4 | 0.6 | 0 | 2024-09-13 | 20.4 | 0 | 2.4 | 2023-09-13 | 16.5 | 1.5 | 0 | 2022-09-13 | 16.9 | 1.1 | 0 | 2021-09-13 | 15 | 3 | 0 | 2020-09-13 | 18.5 | 0 | 0.5 | 2019-09-13 | 18.7 | 0 | 0.7 | 2018-09-13 | 19.6 | 0 | 1.6 | 2017-09-13 | 19.5 | 0 | 1.5 | 2016-09-13 | 21 | 0 | 3 | 0.62 | 0.97
2025-09-13 | 16.9 | 1.1 | 0 | 2024-09-13 | 18.8 | 0 | 0.8 | 2023-09-13 | 15.2 | 2.8 | 0 | 2022-09-13 | 16.3 | 1.7 | 0 | 2021-09-13 | 13.8 | 4.2 | 0 | 2020-09-13 | 16.9 | 1.1 | 0 | 2019-09-13 | 18.7 | 0 | 0.7 | 2018-09-13 | 18.3 | 0 | 0.3 | 2017-09-13 | 17.6 | 0.4 | 0 | 2016-09-13 | 20.4 | 0 | 2.4 | 1.13 | 0.42
2025-09-13 | 15.9 | 2.1 | 0 | 2024-09-13 | 18.5 | 0 | 0.5 | 2023-09-13 | 14 | 4 | 0 | 2022-09-13 | 16.2 | 1.8 | 0 | 2021-09-13 | 11.8 | 6.2 | 0 | 2020-09-13 | 16.9 | 1.1 | 0 | 2019-09-13 | 18.5 | 0 | 0.5 | 2018-09-13 | 18.2 | 0 | 0.2 | 2017-09-13 | 16.6 | 1.4 | 0 | 2016-09-13 | 19.8 | 0 | 1.8 | 1.66 | 0.3
2025-09-13 | 14.8 | 3.2 | 0 | 2024-09-13 | 17.4 | 0.6 | 0 | 2023-09-13 | 11.7 | 6.3 | 0 | 2022-09-13 | 16.1 | 1.9 | 0 | 2021-09-13 | 12.9 | 5.1 | 0 | 2020-09-13 | 15.6 | 2.4 | 0 | 2019-09-13 | 18.3 | 0 | 0.3 | 2018-09-13 | 17.2 | 0.8 | 0 | 2017-09-13 | 15 | 3 | 0 | 2016-09-13 | 19.4 | 0 | 1.4 | 2.33 | 0.17
2025-09-14 | 13.6 | 4.4 | 0 | 2024-09-14 | 17.1 | 0.9 | 0 | 2023-09-14 | 11.4 | 6.6 | 0 | 2022-09-14 | 16.3 | 1.7 | 0 | 2021-09-14 | 12.7 | 5.3 | 0 | 2020-09-14 | 14.8 | 3.2 | 0 | 2019-09-14 | 17.5 | 0.5 | 0 | 2018-09-14 | 15.8 | 2.2 | 0 | 2017-09-14 | 15.8 | 2.2 | 0 | 2016-09-14 | 19.9 | 0 | 1.9 | 2.7 | 0.19
2025-09-14 | 13 | 5 | 0 | 2024-09-14 | 17 | 1 | 0 | 2023-09-14 | 10.3 | 7.7 | 0 | 2022-09-14 | 16.4 | 1.6 | 0 | 2021-09-14 | 13.2 | 4.8 | 0 | 2020-09-14 | 13.7 | 4.3 | 0 | 2019-09-14 | 14.7 | 3.3 | 0 | 2018-09-14 | 15.7 | 2.3 | 0 | 2017-09-14 | 15.6 | 2.4 | 0 | 2016-09-14 | 19.6 | 0 | 1.6 | 3.24 | 0.16
2025-09-14 | 12.2 | 5.8 | 0 | 2024-09-14 | 16 | 2 | 0 | 2023-09-14 | 9.8 | 8.2 | 0 | 2022-09-14 | 16.4 | 1.6 | 0 | 2021-09-14 | 13.1 | 4.9 | 0 | 2020-09-14 | 13.9 | 4.1 | 0 | 2019-09-14 | 15 | 3 | 0 | 2018-09-14 | 15.2 | 2.8 | 0 | 2017-09-14 | 14.7 | 3.3 | 0 | 2016-09-14 | 19.7 | 0 | 1.7 | 3.57 | 0.17
2025-09-14 | 13.2 | 4.8 | 0 | 2024-09-14 | 16.6 | 1.4 | 0 | 2023-09-14 | 10.5 | 7.5 | 0 | 2022-09-14 | 16.4 | 1.6 | 0 | 2021-09-14 | 12.1 | 5.9 | 0 | 2020-09-14 | 14.2 | 3.8 | 0 | 2019-09-14 | 15.4 | 2.6 | 0 | 2018-09-14 | 14.9 | 3.1 | 0 | 2017-09-14 | 13.5 | 4.5 | 0 | 2016-09-14 | 19.1 | 0 | 1.1 | 3.52 | 0.11
2025-09-14 | 12.4 | 5.6 | 0 | 2024-09-14 | 15.1 | 2.9 | 0 | 2023-09-14 | 10.9 | 7.1 | 0 | 2022-09-14 | 16.9 | 1.1 | 0 | 2021-09-14 | 10.3 | 7.7 | 0 | 2020-09-14 | 13.2 | 4.8 | 0 | 2019-09-14 | 15 | 3 | 0 | 2018-09-14 | 15.1 | 2.9 | 0 | 2017-09-14 | 14.2 | 3.8 | 0 | 2016-09-14 | 18.9 | 0 | 0.9 | 3.89 | 0.09
2025-09-14 | 11.2 | 6.8 | 0 | 2024-09-14 | 15.3 | 2.7 | 0 | 2023-09-14 | 11.4 | 6.6 | 0 | 2022-09-14 | 17.1 | 0.9 | 0 | 2021-09-14 | 9.9 | 8.1 | 0 | 2020-09-14 | 10.8 | 7.2 | 0 | 2019-09-14 | 15.1 | 2.9 | 0 | 2018-09-14 | 14.2 | 3.8 | 0 | 2017-09-14 | 13.1 | 4.9 | 0 | 2016-09-14 | 19.4 | 0 | 1.4 | 4.39 | 0.14
2025-09-14 | 13.6 | 4.4 | 0 | 2024-09-14 | 15.3 | 2.7 | 0 | 2023-09-14 | 11.4 | 6.6 | 0 | 2022-09-14 | 16.8 | 1.2 | 0 | 2021-09-14 | 10.1 | 7.9 | 0 | 2020-09-14 | 9.5 | 8.5 | 0 | 2019-09-14 | 15.1 | 2.9 | 0 | 2018-09-14 | 13.3 | 4.7 | 0 | 2017-09-14 | 11.9 | 6.1 | 0 | 2016-09-14 | 17.7 | 0.3 | 0 | 4.53 | 0
2025-09-14 | 13.8 | 4.2 | 0 | 2024-09-14 | 18 | 0 | 0 | 2023-09-14 | 12.2 | 5.8 | 0 | 2022-09-14 | 17.1 | 0.9 | 0 | 2021-09-14 | 11 | 7 | 0 | 2020-09-14 | 10.2 | 7.8 | 0 | 2019-09-14 | 15.6 | 2.4 | 0 | 2018-09-14 | 16.2 | 1.8 | 0 | 2017-09-14 | 14.9 | 3.1 | 0 | 2016-09-14 | 16 | 2 | 0 | 3.5 | 0
2025-09-14 | 17.3 | 0.7 | 0 | 2024-09-14 | 20.2 | 0 | 2.2 | 2023-09-14 | 13.1 | 4.9 | 0 | 2022-09-14 | 17.9 | 0.1 | 0 | 2021-09-14 | 13.4 | 4.6 | 0 | 2020-09-14 | 10.9 | 7.1 | 0 | 2019-09-14 | 16.2 | 1.8 | 0 | 2018-09-14 | 18.4 | 0 | 0.4 | 2017-09-14 | 18 | 0 | 0 | 2016-09-14 | 16 | 2 | 0 | 2.12 | 0.26
2025-09-14 | 18.9 | 0 | 0.9 | 2024-09-14 | 22.5 | 0 | 4.5 | 2023-09-14 | 14 | 4 | 0 | 2022-09-14 | 18.8 | 0 | 0.8 | 2021-09-14 | 15.2 | 2.8 | 0 | 2020-09-14 | 11.7 | 6.3 | 0 | 2019-09-14 | 17.5 | 0.5 | 0 | 2018-09-14 | 20.8 | 0 | 2.8 | 2017-09-14 | 20.4 | 0 | 2.4 | 2016-09-14 | 16.1 | 1.9 | 0 | 1.55 | 1.14
2025-09-14 | 20.8 | 0 | 2.8 | 2024-09-14 | 23.9 | 0 | 5.9 | 2023-09-14 | 14.1 | 3.9 | 0 | 2022-09-14 | 19.9 | 0 | 1.9 | 2021-09-14 | 18 | 0 | 0 | 2020-09-14 | 12.4 | 5.6 | 0 | 2019-09-14 | 19.6 | 0 | 1.6 | 2018-09-14 | 22.8 | 0 | 4.8 | 2017-09-14 | 22.5 | 0 | 4.5 | 2016-09-14 | 16.2 | 1.8 | 0 | 1.13 | 2.15
2025-09-14 | 21.5 | 0 | 3.5 | 2024-09-14 | 25.2 | 0 | 7.2 | 2023-09-14 | 13.4 | 4.6 | 0 | 2022-09-14 | 20.3 | 0 | 2.3 | 2021-09-14 | 18.7 | 0 | 0.7 | 2020-09-14 | 13 | 5 | 0 | 2019-09-14 | 19.9 | 0 | 1.9 | 2018-09-14 | 24.6 | 0 | 6.6 | 2017-09-14 | 23.9 | 0 | 5.9 | 2016-09-14 | 16.7 | 1.3 | 0 | 1.09 | 2.81
2025-09-14 | 22 | 0 | 4 | 2024-09-14 | 26.6 | 0 | 8.6 | 2023-09-14 | 13.5 | 4.5 | 0 | 2022-09-14 | 20 | 0 | 2 | 2021-09-14 | 18.9 | 0 | 0.9 | 2020-09-14 | 13.3 | 4.7 | 0 | 2019-09-14 | 23.4 | 0 | 5.4 | 2018-09-14 | 26.4 | 0 | 8.4 | 2017-09-14 | 25.4 | 0 | 7.4 | 2016-09-14 | 17.1 | 0.9 | 0 | 1.01 | 3.67
2025-09-14 | 23 | 0 | 5 | 2024-09-14 | 27.6 | 0 | 9.6 | 2023-09-14 | 15.2 | 2.8 | 0 | 2022-09-14 | 18.1 | 0 | 0.1 | 2021-09-14 | 19.4 | 0 | 1.4 | 2020-09-14 | 13.7 | 4.3 | 0 | 2019-09-14 | 21.5 | 0 | 3.5 | 2018-09-14 | 26.6 | 0 | 8.6 | 2017-09-14 | 26.4 | 0 | 8.4 | 2016-09-14 | 17.4 | 0.6 | 0 | 0.77 | 3.66
2025-09-14 | 23.4 | 0 | 5.4 | 2024-09-14 | 27.2 | 0 | 9.2 | 2023-09-14 | 15.4 | 2.6 | 0 | 2022-09-14 | 18.2 | 0 | 0.2 | 2021-09-14 | 20.6 | 0 | 2.6 | 2020-09-14 | 14.2 | 3.8 | 0 | 2019-09-14 | 21.1 | 0 | 3.1 | 2018-09-14 | 28 | 0 | 10 | 2017-09-14 | 26.5 | 0 | 8.5 | 2016-09-14 | 17.8 | 0.2 | 0 | 0.66 | 3.9
2025-09-14 | 23.4 | 0 | 5.4 | 2024-09-14 | 27.6 | 0 | 9.6 | 2023-09-14 | 15.2 | 2.8 | 0 | 2022-09-14 | 17.6 | 0.4 | 0 | 2021-09-14 | 19.5 | 0 | 1.5 | 2020-09-14 | 13.5 | 4.5 | 0 | 2019-09-14 | 20.3 | 0 | 2.3 | 2018-09-14 | 27.8 | 0 | 9.8 | 2017-09-14 | 27.3 | 0 | 9.3 | 2016-09-14 | 17.6 | 0.4 | 0 | 0.81 | 3.79
2025-09-14 | 23.2 | 0 | 5.2 | 2024-09-14 | 27.3 | 0 | 9.3 | 2023-09-14 | 15.4 | 2.6 | 0 | 2022-09-14 | 17.6 | 0.4 | 0 | 2021-09-14 | 19.6 | 0 | 1.6 | 2020-09-14 | 14.2 | 3.8 | 0 | 2019-09-14 | 19.9 | 0 | 1.9 | 2018-09-14 | 27.9 | 0 | 9.9 | 2017-09-14 | 26.6 | 0 | 8.6 | 2016-09-14 | 17 | 1 | 0 | 0.78 | 3.65
2025-09-14 | 21.9 | 0 | 3.9 | 2024-09-14 | 26.8 | 0 | 8.8 | 2023-09-14 | 15.5 | 2.5 | 0 | 2022-09-14 | 16 | 2 | 0 | 2021-09-14 | 18.8 | 0 | 0.8 | 2020-09-14 | 12.9 | 5.1 | 0 | 2019-09-14 | 19.5 | 0 | 1.5 | 2018-09-14 | 26.9 | 0 | 8.9 | 2017-09-14 | 25.5 | 0 | 7.5 | 2016-09-14 | 17.2 | 0.8 | 0 | 1.04 | 3.14
2025-09-14 | 20 | 0 | 2 | 2024-09-14 | 24.5 | 0 | 6.5 | 2023-09-14 | 15.6 | 2.4 | 0 | 2022-09-14 | 14.9 | 3.1 | 0 | 2021-09-14 | 18.5 | 0 | 0.5 | 2020-09-14 | 11.2 | 6.8 | 0 | 2019-09-14 | 18.7 | 0 | 0.7 | 2018-09-14 | 25.2 | 0 | 7.2 | 2017-09-14 | 23.3 | 0 | 5.3 | 2016-09-14 | 15.6 | 2.4 | 0 | 1.47 | 2.22
2025-09-14 | 18.5 | 0 | 0.5 | 2024-09-14 | 20.3 | 0 | 2.3 | 2023-09-14 | 12 | 6 | 0 | 2022-09-14 | 13.1 | 4.9 | 0 | 2021-09-14 | 16.8 | 1.2 | 0 | 2020-09-14 | 8.4 | 9.6 | 0 | 2019-09-14 | 17.9 | 0.1 | 0 | 2018-09-14 | 23.1 | 0 | 5.1 | 2017-09-14 | 21.2 | 0 | 3.2 | 2016-09-14 | 14.4 | 3.6 | 0 | 2.54 | 1.11
2025-09-14 | 17.6 | 0.4 | 0 | 2024-09-14 | 19.2 | 0 | 1.2 | 2023-09-14 | 10.3 | 7.7 | 0 | 2022-09-14 | 11.5 | 6.5 | 0 | 2021-09-14 | 17.6 | 0.4 | 0 | 2020-09-14 | 8.7 | 9.3 | 0 | 2019-09-14 | 17.6 | 0.4 | 0 | 2018-09-14 | 21.4 | 0 | 3.4 | 2017-09-14 | 18 | 0 | 0 | 2016-09-14 | 13.1 | 4.9 | 0 | 2.96 | 0.46
2025-09-14 | 16 | 2 | 0 | 2024-09-14 | 19.7 | 0 | 1.7 | 2023-09-14 | 11.7 | 6.3 | 0 | 2022-09-14 | 10 | 8 | 0 | 2021-09-14 | 17.9 | 0.1 | 0 | 2020-09-14 | 8.1 | 9.9 | 0 | 2019-09-14 | 16.3 | 1.7 | 0 | 2018-09-14 | 22.4 | 0 | 4.4 | 2017-09-14 | 18.1 | 0 | 0.1 | 2016-09-14 | 12.2 | 5.8 | 0 | 3.38 | 0.62
2025-09-14 | 15.1 | 2.9 | 0 | 2024-09-14 | 18.2 | 0 | 0.2 | 2023-09-14 | 10 | 8 | 0 | 2022-09-14 | 10 | 8 | 0 | 2021-09-14 | 18.7 | 0 | 0.7 | 2020-09-14 | 5.2 | 12.8 | 0 | 2019-09-14 | 14.7 | 3.3 | 0 | 2018-09-14 | 21 | 0 | 3 | 2017-09-14 | 18.6 | 0 | 0.6 | 2016-09-14 | 11.3 | 6.7 | 0 | 4.17 | 0.45
2025-09-14 | 14 | 4 | 0 | 2024-09-14 | 19.5 | 0 | 1.5 | 2023-09-14 | 10 | 8 | 0 | 2022-09-14 | 8.2 | 9.8 | 0 | 2021-09-14 | 22.6 | 0 | 4.6 | 2020-09-14 | 4.3 | 13.7 | 0 | 2019-09-14 | 13.7 | 4.3 | 0 | 2018-09-14 | 20.1 | 0 | 2.1 | 2017-09-14 | 17.9 | 0.1 | 0 | 2016-09-14 | 9.8 | 8.2 | 0 | 4.81 | 0.82
2025-09-15 | 13.5 | 4.5 | 0 | 2024-09-15 | 16.9 | 1.1 | 0 | 2023-09-15 | 7.8 | 10.2 | 0 | 2022-09-15 | 7 | 11 | 0 | 2021-09-15 | 20.1 | 0 | 2.1 | 2020-09-15 | 5 | 13 | 0 | 2019-09-15 | 12.7 | 5.3 | 0 | 2018-09-15 | 19.3 | 0 | 1.3 | 2017-09-15 | 15.5 | 2.5 | 0 | 2016-09-15 | 9.7 | 8.3 | 0 | 5.59 | 0.34
2025-09-15 | 12.5 | 5.5 | 0 | 2024-09-15 | 16.4 | 1.6 | 0 | 2023-09-15 | 8.2 | 9.8 | 0 | 2022-09-15 | 8.6 | 9.4 | 0 | 2021-09-15 | 19.7 | 0 | 1.7 | 2020-09-15 | 4.8 | 13.2 | 0 | 2019-09-15 | 12.2 | 5.8 | 0 | 2018-09-15 | 19.8 | 0 | 1.8 | 2017-09-15 | 13.8 | 4.2 | 0 | 2016-09-15 | 8.1 | 9.9 | 0 | 5.94 | 0.35
2025-09-15 | 12.1 | 5.9 | 0 | 2024-09-15 | 16.2 | 1.8 | 0 | 2023-09-15 | 8.6 | 9.4 | 0 | 2022-09-15 | 7.6 | 10.4 | 0 | 2021-09-15 | 18.8 | 0 | 0.8 | 2020-09-15 | 5 | 13 | 0 | 2019-09-15 | 11.4 | 6.6 | 0 | 2018-09-15 | 19.4 | 0 | 1.4 | 2017-09-15 | 14.8 | 3.2 | 0 | 2016-09-15 | 7.4 | 10.6 | 0 | 6.09 | 0.22
2025-09-15 | 10.6 | 7.4 | 0 | 2024-09-15 | 15.7 | 2.3 | 0 | 2023-09-15 | 8 | 10 | 0 | 2022-09-15 | 7.9 | 10.1 | 0 | 2021-09-15 | 18.9 | 0 | 0.9 | 2020-09-15 | 4.8 | 13.2 | 0 | 2019-09-15 | 11.7 | 6.3 | 0 | 2018-09-15 | 19.5 | 0 | 1.5 | 2017-09-15 | 14.2 | 3.8 | 0 | 2016-09-15 | 6.9 | 11.1 | 0 | 6.42 | 0.24
2025-09-15 | 10.9 | 7.1 | 0 | 2024-09-15 | 15.1 | 2.9 | 0 | 2023-09-15 | 7.5 | 10.5 | 0 | 2022-09-15 | 7.7 | 10.3 | 0 | 2021-09-15 | 18.9 | 0 | 0.9 | 2020-09-15 | 4.8 | 13.2 | 0 | 2019-09-15 | 9.8 | 8.2 | 0 | 2018-09-15 | 18.9 | 0 | 0.9 | 2017-09-15 | 15.4 | 2.6 | 0 | 2016-09-15 | 6.1 | 11.9 | 0 | 6.67 | 0.18
2025-09-15 | 10.6 | 7.4 | 0 | 2024-09-15 | 14.6 | 3.4 | 0 | 2023-09-15 | 8.4 | 9.6 | 0 | 2022-09-15 | 6.7 | 11.3 | 0 | 2021-09-15 | 18.9 | 0 | 0.9 | 2020-09-15 | 3.6 | 14.4 | 0 | 2019-09-15 | 8.9 | 9.1 | 0 | 2018-09-15 | 18.8 | 0 | 0.8 | 2017-09-15 | 14.8 | 3.2 | 0 | 2016-09-15 | 6 | 12 | 0 | 7.04 | 0.17
2025-09-15 | 10.5 | 7.5 | 0 | 2024-09-15 | 14.9 | 3.1 | 0 | 2023-09-15 | 9.3 | 8.7 | 0 | 2022-09-15 | 7.4 | 10.6 | 0 | 2021-09-15 | 18.5 | 0 | 0.5 | 2020-09-15 | 3 | 15 | 0 | 2019-09-15 | 9.8 | 8.2 | 0 | 2018-09-15 | 18.7 | 0 | 0.7 | 2017-09-15 | 14.6 | 3.4 | 0 | 2016-09-15 | 5.7 | 12.3 | 0 | 6.88 | 0.12
2025-09-15 | 12.4 | 5.6 | 0 | 2024-09-15 | 16.9 | 1.1 | 0 | 2023-09-15 | 9.8 | 8.2 | 0 | 2022-09-15 | 8.3 | 9.7 | 0 | 2021-09-15 | 17.8 | 0.2 | 0 | 2020-09-15 | 3 | 15 | 0 | 2019-09-15 | 11.2 | 6.8 | 0 | 2018-09-15 | 20.1 | 0 | 2.1 | 2017-09-15 | 16.6 | 1.4 | 0 | 2016-09-15 | 9.4 | 8.6 | 0 | 5.66 | 0.21
2025-09-15 | 14.8 | 3.2 | 0 | 2024-09-15 | 18.9 | 0 | 0.9 | 2023-09-15 | 12.4 | 5.6 | 0 | 2022-09-15 | 9.4 | 8.6 | 0 | 2021-09-15 | 18 | 0 | 0 | 2020-09-15 | 6.4 | 11.6 | 0 | 2019-09-15 | 13.8 | 4.2 | 0 | 2018-09-15 | 23 | 0 | 5 | 2017-09-15 | 17.6 | 0.4 | 0 | 2016-09-15 | 11.3 | 6.7 | 0 | 4.03 | 0.59
2025-09-15 | 16.5 | 1.5 | 0 | 2024-09-15 | 21 | 0 | 3 | 2023-09-15 | 15.9 | 2.1 | 0 | 2022-09-15 | 10.6 | 7.4 | 0 | 2021-09-15 | 17.8 | 0.2 | 0 | 2020-09-15 | 8.7 | 9.3 | 0 | 2019-09-15 | 14.7 | 3.3 | 0 | 2018-09-15 | 24.1 | 0 | 6.1 | 2017-09-15 | 19.7 | 0 | 1.7 | 2016-09-15 | 12.4 | 5.6 | 0 | 2.94 | 1.08
2025-09-15 | 18.1 | 0 | 0.1 | 2024-09-15 | 23.8 | 0 | 5.8 | 2023-09-15 | 18.9 | 0 | 0.9 | 2022-09-15 | 12.5 | 5.5 | 0 | 2021-09-15 | 16.6 | 1.4 | 0 | 2020-09-15 | 11.1 | 6.9 | 0 | 2019-09-15 | 15 | 3 | 0 | 2018-09-15 | 26.1 | 0 | 8.1 | 2017-09-15 | 21.8 | 0 | 3.8 | 2016-09-15 | 13.7 | 4.3 | 0 | 2.11 | 1.87
2025-09-15 | 19.5 | 0 | 1.5 | 2024-09-15 | 24.6 | 0 | 6.6 | 2023-09-15 | 19.2 | 0 | 1.2 | 2022-09-15 | 13.2 | 4.8 | 0 | 2021-09-15 | 17.3 | 0.7 | 0 | 2020-09-15 | 12.4 | 5.6 | 0 | 2019-09-15 | 15.8 | 2.2 | 0 | 2018-09-15 | 27.2 | 0 | 9.2 | 2017-09-15 | 24.2 | 0 | 6.2 | 2016-09-15 | 14.5 | 3.5 | 0 | 1.68 | 2.47
2025-09-15 | 20.8 | 0 | 2.8 | 2024-09-15 | 26.7 | 0 | 8.7 | 2023-09-15 | 20.4 | 0 | 2.4 | 2022-09-15 | 13.8 | 4.2 | 0 | 2021-09-15 | 18.3 | 0 | 0.3 | 2020-09-15 | 13.8 | 4.2 | 0 | 2019-09-15 | 15.3 | 2.7 | 0 | 2018-09-15 | 27.9 | 0 | 9.9 | 2017-09-15 | 25.2 | 0 | 7.2 | 2016-09-15 | 15.1 | 2.9 | 0 | 1.4 | 3.13
2025-09-15 | 21.9 | 0 | 3.9 | 2024-09-15 | 27.6 | 0 | 9.6 | 2023-09-15 | 21 | 0 | 3 | 2022-09-15 | 14.6 | 3.4 | 0 | 2021-09-15 | 18.6 | 0 | 0.6 | 2020-09-15 | 13.9 | 4.1 | 0 | 2019-09-15 | 14.3 | 3.7 | 0 | 2018-09-15 | 28.5 | 0 | 10.5 | 2017-09-15 | 25.9 | 0 | 7.9 | 2016-09-15 | 16.4 | 1.6 | 0 | 1.28 | 3.55
2025-09-15 | 22.9 | 0 | 4.9 | 2024-09-15 | 28.2 | 0 | 10.2 | 2023-09-15 | 21.2 | 0 | 3.2 | 2022-09-15 | 15.8 | 2.2 | 0 | 2021-09-15 | 17.7 | 0.3 | 0 | 2020-09-15 | 13.8 | 4.2 | 0 | 2019-09-15 | 15 | 3 | 0 | 2018-09-15 | 29.2 | 0 | 11.2 | 2017-09-15 | 27 | 0 | 9 | 2016-09-15 | 17.3 | 0.7 | 0 | 1.04 | 3.85
2025-09-15 | 22.5 | 0 | 4.5 | 2024-09-15 | 28.7 | 0 | 10.7 | 2023-09-15 | 21 | 0 | 3 | 2022-09-15 | 16.1 | 1.9 | 0 | 2021-09-15 | 18.4 | 0 | 0.4 | 2020-09-15 | 13.5 | 4.5 | 0 | 2019-09-15 | 16.3 | 1.7 | 0 | 2018-09-15 | 29.5 | 0 | 11.5 | 2017-09-15 | 27 | 0 | 9 | 2016-09-15 | 17.3 | 0.7 | 0 | 0.88 | 3.91
2025-09-15 | 22.9 | 0 | 4.9 | 2024-09-15 | 28.5 | 0 | 10.5 | 2023-09-15 | 21.1 | 0 | 3.1 | 2022-09-15 | 15.9 | 2.1 | 0 | 2021-09-15 | 18.2 | 0 | 0.2 | 2020-09-15 | 13.8 | 4.2 | 0 | 2019-09-15 | 16.5 | 1.5 | 0 | 2018-09-15 | 29.3 | 0 | 11.3 | 2017-09-15 | 26.3 | 0 | 8.3 | 2016-09-15 | 17.3 | 0.7 | 0 | 0.85 | 3.83
2025-09-15 | 22.7 | 0 | 4.7 | 2024-09-15 | 27.1 | 0 | 9.1 | 2023-09-15 | 20.3 | 0 | 2.3 | 2022-09-15 | 14.8 | 3.2 | 0 | 2021-09-15 | 17.8 | 0.2 | 0 | 2020-09-15 | 13.2 | 4.8 | 0 | 2019-09-15 | 16.2 | 1.8 | 0 | 2018-09-15 | 28.3 | 0 | 10.3 | 2017-09-15 | 25.3 | 0 | 7.3 | 2016-09-15 | 17.1 | 0.9 | 0 | 1.09 | 3.37
2025-09-15 | 20.4 | 0 | 2.4 | 2024-09-15 | 24.9 | 0 | 6.9 | 2023-09-15 | 17.4 | 0.6 | 0 | 2022-09-15 | 11.8 | 6.2 | 0 | 2021-09-15 | 16.6 | 1.4 | 0 | 2020-09-15 | 12.7 | 5.3 | 0 | 2019-09-15 | 14.4 | 3.6 | 0 | 2018-09-15 | 27.1 | 0 | 9.1 | 2017-09-15 | 24.1 | 0 | 6.1 | 2016-09-15 | 15.3 | 2.7 | 0 | 1.98 | 2.45
2025-09-15 | 17.4 | 0.6 | 0 | 2024-09-15 | 23.4 | 0 | 5.4 | 2023-09-15 | 16 | 2 | 0 | 2022-09-15 | 10.6 | 7.4 | 0 | 2021-09-15 | 13.3 | 4.7 | 0 | 2020-09-15 | 12.1 | 5.9 | 0 | 2019-09-15 | 14 | 4 | 0 | 2018-09-15 | 26.4 | 0 | 8.4 | 2017-09-15 | 22.4 | 0 | 4.4 | 2016-09-15 | 13.6 | 4.4 | 0 | 2.9 | 1.82
2025-09-15 | 15 | 3 | 0 | 2024-09-15 | 22.2 | 0 | 4.2 | 2023-09-15 | 13.8 | 4.2 | 0 | 2022-09-15 | 10.7 | 7.3 | 0 | 2021-09-15 | 12.4 | 5.6 | 0 | 2020-09-15 | 12.1 | 5.9 | 0 | 2019-09-15 | 13.2 | 4.8 | 0 | 2018-09-15 | 23.6 | 0 | 5.6 | 2017-09-15 | 20.7 | 0 | 2.7 | 2016-09-15 | 12.9 | 5.1 | 0 | 3.59 | 1.25
2025-09-15 | 14.3 | 3.7 | 0 | 2024-09-15 | 20.6 | 0 | 2.6 | 2023-09-15 | 12.8 | 5.2 | 0 | 2022-09-15 | 11.2 | 6.8 | 0 | 2021-09-15 | 13.2 | 4.8 | 0 | 2020-09-15 | 11.6 | 6.4 | 0 | 2019-09-15 | 13 | 5 | 0 | 2018-09-15 | 23.9 | 0 | 5.9 | 2017-09-15 | 19.9 | 0 | 1.9 | 2016-09-15 | 9.1 | 8.9 | 0 | 4.08 | 1.04
2025-09-15 | 17.1 | 0.9 | 0 | 2024-09-15 | 19.4 | 0 | 1.4 | 2023-09-15 | 12.6 | 5.4 | 0 | 2022-09-15 | 10.7 | 7.3 | 0 | 2021-09-15 | 12.5 | 5.5 | 0 | 2020-09-15 | 11.1 | 6.9 | 0 | 2019-09-15 | 8.7 | 9.3 | 0 | 2018-09-15 | 23.4 | 0 | 5.4 | 2017-09-15 | 17.4 | 0.6 | 0 | 2016-09-15 | 9.2 | 8.8 | 0 | 4.47 | 0.68
2025-09-15 | 13.3 | 4.7 | 0 | 2024-09-15 | 18.6 | 0 | 0.6 | 2023-09-15 | 12.8 | 5.2 | 0 | 2022-09-15 | 10.5 | 7.5 | 0 | 2021-09-15 | 11.9 | 6.1 | 0 | 2020-09-15 | 10.9 | 7.1 | 0 | 2019-09-15 | 8.7 | 9.3 | 0 | 2018-09-15 | 22.6 | 0 | 4.6 | 2017-09-15 | 17.3 | 0.7 | 0 | 2016-09-15 | 7.7 | 10.3 | 0 | 5.09 | 0.52
2025-09-16 | 11.8 | 6.2 | 0 | 2024-09-16 | 16.2 | 1.8 | 0 | 2023-09-16 | 12.7 | 5.3 | 0 | 2022-09-16 | 10.6 | 7.4 | 0 | 2021-09-16 | 11.3 | 6.7 | 0 | 2020-09-16 | 11.2 | 6.8 | 0 | 2019-09-16 | 10 | 8 | 0 | 2018-09-16 | 23 | 0 | 5 | 2017-09-16 | 18.1 | 0 | 0.1 | 2016-09-16 | 8.4 | 9.6 | 0 | 5.18 | 0.51
2025-09-16 | 12.7 | 5.3 | 0 | 2024-09-16 | 15.9 | 2.1 | 0 | 2023-09-16 | 9.2 | 8.8 | 0 | 2022-09-16 | 10.7 | 7.3 | 0 | 2021-09-16 | 10.8 | 7.2 | 0 | 2020-09-16 | 11.2 | 6.8 | 0 | 2019-09-16 | 8.6 | 9.4 | 0 | 2018-09-16 | 21.1 | 0 | 3.1 | 2017-09-16 | 17.3 | 0.7 | 0 | 2016-09-16 | 6.6 | 11.4 | 0 | 5.9 | 0.31
2025-09-16 | 11.4 | 6.6 | 0 | 2024-09-16 | 15.5 | 2.5 | 0 | 2023-09-16 | 10.3 | 7.7 | 0 | 2022-09-16 | 10.8 | 7.2 | 0 | 2021-09-16 | 9.7 | 8.3 | 0 | 2020-09-16 | 10.2 | 7.8 | 0 | 2019-09-16 | 8.8 | 9.2 | 0 | 2018-09-16 | 20.9 | 0 | 2.9 | 2017-09-16 | 16.1 | 1.9 | 0 | 2016-09-16 | 7 | 11 | 0 | 6.22 | 0.29
2025-09-16 | 10.2 | 7.8 | 0 | 2024-09-16 | 16.5 | 1.5 | 0 | 2023-09-16 | 9.6 | 8.4 | 0 | 2022-09-16 | 11.1 | 6.9 | 0 | 2021-09-16 | 9.7 | 8.3 | 0 | 2020-09-16 | 10.7 | 7.3 | 0 | 2019-09-16 | 8.6 | 9.4 | 0 | 2018-09-16 | 20.6 | 0 | 2.6 | 2017-09-16 | 16.5 | 1.5 | 0 | 2016-09-16 | 6.3 | 11.7 | 0 | 6.28 | 0.26
2025-09-16 | 10.1 | 7.9 | 0 | 2024-09-16 | 15.3 | 2.7 | 0 | 2023-09-16 | 9.1 | 8.9 | 0 | 2022-09-16 | 11.4 | 6.6 | 0 | 2021-09-16 | 10.3 | 7.7 | 0 | 2020-09-16 | 12.3 | 5.7 | 0 | 2019-09-16 | 6.7 | 11.3 | 0 | 2018-09-16 | 20.4 | 0 | 2.4 | 2017-09-16 | 14.8 | 3.2 | 0 | 2016-09-16 | 6.8 | 11.2 | 0 | 6.52 | 0.24
2025-09-16 | 10.5 | 7.5 | 0 | 2024-09-16 | 15.4 | 2.6 | 0 | 2023-09-16 | 7.9 | 10.1 | 0 | 2022-09-16 | 10.9 | 7.1 | 0 | 2021-09-16 | 9 | 9 | 0 | 2020-09-16 | 13.4 | 4.6 | 0 | 2019-09-16 | 6.3 | 11.7 | 0 | 2018-09-16 | 19.3 | 0 | 1.3 | 2017-09-16 | 15.4 | 2.6 | 0 | 2016-09-16 | 6.4 | 11.6 | 0 | 6.68 | 0.13
2025-09-16 | 10.5 | 7.5 | 0 | 2024-09-16 | 15.3 | 2.7 | 0 | 2023-09-16 | 9.1 | 8.9 | 0 | 2022-09-16 | 10.9 | 7.1 | 0 | 2021-09-16 | 8.6 | 9.4 | 0 | 2020-09-16 | 14.3 | 3.7 | 0 | 2019-09-16 | 5.1 | 12.9 | 0 | 2018-09-16 | 17.9 | 0.1 | 0 | 2017-09-16 | 15.3 | 2.7 | 0 | 2016-09-16 | 6.1 | 11.9 | 0 | 6.69 | 0
2025-09-16 | 13.3 | 4.7 | 0 | 2024-09-16 | 16.9 | 1.1 | 0 | 2023-09-16 | 10.1 | 7.9 | 0 | 2022-09-16 | 11.8 | 6.2 | 0 | 2021-09-16 | 12.7 | 5.3 | 0 | 2020-09-16 | 15 | 3 | 0 | 2019-09-16 | 8.7 | 9.3 | 0 | 2018-09-16 | 20.4 | 0 | 2.4 | 2017-09-16 | 15.5 | 2.5 | 0 | 2016-09-16 | 8.8 | 9.2 | 0 | 4.92 | 0.24
2025-09-16 | 15.3 | 2.7 | 0 | 2024-09-16 | 19.2 | 0 | 1.2 | 2023-09-16 | 12 | 6 | 0 | 2022-09-16 | 13.7 | 4.3 | 0 | 2021-09-16 | 14.9 | 3.1 | 0 | 2020-09-16 | 16.8 | 1.2 | 0 | 2019-09-16 | 11.5 | 6.5 | 0 | 2018-09-16 | 22.4 | 0 | 4.4 | 2017-09-16 | 18.3 | 0 | 0.3 | 2016-09-16 | 11.4 | 6.6 | 0 | 3.04 | 0.59
2025-09-16 | 17.9 | 0.1 | 0 | 2024-09-16 | 22 | 0 | 4 | 2023-09-16 | 15.6 | 2.4 | 0 | 2022-09-16 | 14.2 | 3.8 | 0 | 2021-09-16 | 18.2 | 0 | 0.2 | 2020-09-16 | 18.3 | 0 | 0.3 | 2019-09-16 | 14.7 | 3.3 | 0 | 2018-09-16 | 24.2 | 0 | 6.2 | 2017-09-16 | 21.2 | 0 | 3.2 | 2016-09-16 | 14.5 | 3.5 | 0 | 1.31 | 1.39
2025-09-16 | 20.4 | 0 | 2.4 | 2024-09-16 | 25 | 0 | 7 | 2023-09-16 | 18.5 | 0 | 0.5 | 2022-09-16 | 15 | 3 | 0 | 2021-09-16 | 19.8 | 0 | 1.8 | 2020-09-16 | 19.6 | 0 | 1.6 | 2019-09-16 | 16.2 | 1.8 | 0 | 2018-09-16 | 25.5 | 0 | 7.5 | 2017-09-16 | 23.4 | 0 | 5.4 | 2016-09-16 | 17.5 | 0.5 | 0 | 0.53 | 2.62
2025-09-16 | 22.2 | 0 | 4.2 | 2024-09-16 | 26.5 | 0 | 8.5 | 2023-09-16 | 20.1 | 0 | 2.1 | 2022-09-16 | 15.8 | 2.2 | 0 | 2021-09-16 | 21 | 0 | 3 | 2020-09-16 | 21.1 | 0 | 3.1 | 2019-09-16 | 17.9 | 0.1 | 0 | 2018-09-16 | 27.3 | 0 | 9.3 | 2017-09-16 | 24.5 | 0 | 6.5 | 2016-09-16 | 19.4 | 0 | 1.4 | 0.23 | 3.81
2025-09-16 | 23 | 0 | 5 | 2024-09-16 | 27.4 | 0 | 9.4 | 2023-09-16 | 21.2 | 0 | 3.2 | 2022-09-16 | 16.3 | 1.7 | 0 | 2021-09-16 | 20.6 | 0 | 2.6 | 2020-09-16 | 21.4 | 0 | 3.4 | 2019-09-16 | 18.4 | 0 | 0.4 | 2018-09-16 | 28 | 0 | 10 | 2017-09-16 | 25.7 | 0 | 7.7 | 2016-09-16 | 19.9 | 0 | 1.9 | 0.17 | 4.36
2025-09-16 | 24.7 | 0 | 6.7 | 2024-09-16 | 27.7 | 0 | 9.7 | 2023-09-16 | 21.8 | 0 | 3.8 | 2022-09-16 | 16.9 | 1.1 | 0 | 2021-09-16 | 22.9 | 0 | 4.9 | 2020-09-16 | 21.6 | 0 | 3.6 | 2019-09-16 | 19.9 | 0 | 1.9 | 2018-09-16 | 28.4 | 0 | 10.4 | 2017-09-16 | 26.9 | 0 | 8.9 | 2016-09-16 | 20.6 | 0 | 2.6 | 0.11 | 5.25
2025-09-16 | 24.9 | 0 | 6.9 | 2024-09-16 | 27.4 | 0 | 9.4 | 2023-09-16 | 22.5 | 0 | 4.5 | 2022-09-16 | 17.8 | 0.2 | 0 | 2021-09-16 | 23 | 0 | 5 | 2020-09-16 | 21.7 | 0 | 3.7 | 2019-09-16 | 20.2 | 0 | 2.2 | 2018-09-16 | 29 | 0 | 11 | 2017-09-16 | 26.4 | 0 | 8.4 | 2016-09-16 | 21.5 | 0 | 3.5 | 0.02 | 5.46
2025-09-16 | 25 | 0 | 7 | 2024-09-16 | 28.8 | 0 | 10.8 | 2023-09-16 | 22.7 | 0 | 4.7 | 2022-09-16 | 17.9 | 0.1 | 0 | 2021-09-16 | 23.3 | 0 | 5.3 | 2020-09-16 | 21.3 | 0 | 3.3 | 2019-09-16 | 20.6 | 0 | 2.6 | 2018-09-16 | 29.1 | 0 | 11.1 | 2017-09-16 | 26.7 | 0 | 8.7 | 2016-09-16 | 21.7 | 0 | 3.7 | 0.01 | 5.72
2025-09-16 | 24.8 | 0 | 6.8 | 2024-09-16 | 26.7 | 0 | 8.7 | 2023-09-16 | 22.6 | 0 | 4.6 | 2022-09-16 | 17.3 | 0.7 | 0 | 2021-09-16 | 22.5 | 0 | 4.5 | 2020-09-16 | 21.2 | 0 | 3.2 | 2019-09-16 | 20.8 | 0 | 2.8 | 2018-09-16 | 27.5 | 0 | 9.5 | 2017-09-16 | 26.6 | 0 | 8.6 | 2016-09-16 | 21.8 | 0 | 3.8 | 0.07 | 5.25
2025-09-16 | 23.8 | 0 | 5.8 | 2024-09-16 | 27.1 | 0 | 9.1 | 2023-09-16 | 21.3 | 0 | 3.3 | 2022-09-16 | 16.1 | 1.9 | 0 | 2021-09-16 | 21.6 | 0 | 3.6 | 2020-09-16 | 20 | 0 | 2 | 2019-09-16 | 20.2 | 0 | 2.2 | 2018-09-16 | 27.1 | 0 | 9.1 | 2017-09-16 | 26 | 0 | 8 | 2016-09-16 | 21.3 | 0 | 3.3 | 0.19 | 4.64
2025-09-16 | 21.1 | 0 | 3.1 | 2024-09-16 | 24.7 | 0 | 6.7 | 2023-09-16 | 17.9 | 0.1 | 0 | 2022-09-16 | 14.5 | 3.5 | 0 | 2021-09-16 | 18.5 | 0 | 0.5 | 2020-09-16 | 19 | 0 | 1 | 2019-09-16 | 16.7 | 1.3 | 0 | 2018-09-16 | 26.2 | 0 | 8.2 | 2017-09-16 | 23.5 | 0 | 5.5 | 2016-09-16 | 17.6 | 0.4 | 0 | 0.53 | 2.5
2025-09-16 | 18.2 | 0 | 0.2 | 2024-09-16 | 23 | 0 | 5 | 2023-09-16 | 16.8 | 1.2 | 0 | 2022-09-16 | 13.1 | 4.9 | 0 | 2021-09-16 | 16.1 | 1.9 | 0 | 2020-09-16 | 18.8 | 0 | 0.8 | 2019-09-16 | 15.6 | 2.4 | 0 | 2018-09-16 | 24.3 | 0 | 6.3 | 2017-09-16 | 21.7 | 0 | 3.7 | 2016-09-16 | 16.3 | 1.7 | 0 | 1.21 | 1.6
2025-09-16 | 17.2 | 0.8 | 0 | 2024-09-16 | 22.2 | 0 | 4.2 | 2023-09-16 | 14.4 | 3.6 | 0 | 2022-09-16 | 12.5 | 5.5 | 0 | 2021-09-16 | 15.8 | 2.2 | 0 | 2020-09-16 | 19.2 | 0 | 1.2 | 2019-09-16 | 13.6 | 4.4 | 0 | 2018-09-16 | 22 | 0 | 4 | 2017-09-16 | 21.1 | 0 | 3.1 | 2016-09-16 | 13.9 | 4.1 | 0 | 2.06 | 1.25
2025-09-16 | 17.1 | 0.9 | 0 | 2024-09-16 | 20.7 | 0 | 2.7 | 2023-09-16 | 13.3 | 4.7 | 0 | 2022-09-16 | 10.9 | 7.1 | 0 | 2021-09-16 | 13.8 | 4.2 | 0 | 2020-09-16 | 19.2 | 0 | 1.2 | 2019-09-16 | 12.9 | 5.1 | 0 | 2018-09-16 | 21.2 | 0 | 3.2 | 2017-09-16 | 20.1 | 0 | 2.1 | 2016-09-16 | 14.3 | 3.7 | 0 | 2.57 | 0.92
2025-09-16 | 14.6 | 3.4 | 0 | 2024-09-16 | 19.9 | 0 | 1.9 | 2023-09-16 | 12.5 | 5.5 | 0 | 2022-09-16 | 9.1 | 8.9 | 0 | 2021-09-16 | 13.1 | 4.9 | 0 | 2020-09-16 | 15.3 | 2.7 | 0 | 2019-09-16 | 11.9 | 6.1 | 0 | 2018-09-16 | 20.4 | 0 | 2.4 | 2017-09-16 | 19.4 | 0 | 1.4 | 2016-09-16 | 13.5 | 4.5 | 0 | 3.6 | 0.57
2025-09-16 | 13.1 | 4.9 | 0 | 2024-09-16 | 19.2 | 0 | 1.2 | 2023-09-16 | 11.4 | 6.6 | 0 | 2022-09-16 | 9.2 | 8.8 | 0 | 2021-09-16 | 13.2 | 4.8 | 0 | 2020-09-16 | 14.9 | 3.1 | 0 | 2019-09-16 | 11.4 | 6.6 | 0 | 2018-09-16 | 19.9 | 0 | 1.9 | 2017-09-16 | 19.3 | 0 | 1.3 | 2016-09-16 | 13.2 | 4.8 | 0 | 3.96 | 0.44
2025-09-17 | 13.2 | 4.8 | 0 | 2024-09-17 | 19.3 | 0 | 1.3 | 2023-09-17 | 12.1 | 5.9 | 0 | 2022-09-17 | 8.4 | 9.6 | 0 | 2021-09-17 | 13.2 | 4.8 | 0 | 2020-09-17 | 14.6 | 3.4 | 0 | 2019-09-17 | 8.4 | 9.6 | 0 | 2018-09-17 | 19.6 | 0 | 1.6 | 2017-09-17 | 18.5 | 0 | 0.5 | 2016-09-17 | 12.8 | 5.2 | 0 | 4.33 | 0.34
2025-09-17 | 12.2 | 5.8 | 0 | 2024-09-17 | 17.3 | 0.7 | 0 | 2023-09-17 | 11.2 | 6.8 | 0 | 2022-09-17 | 7.1 | 10.9 | 0 | 2021-09-17 | 12 | 6 | 0 | 2020-09-17 | 14.4 | 3.6 | 0 | 2019-09-17 | 10.2 | 7.8 | 0 | 2018-09-17 | 16.9 | 1.1 | 0 | 2017-09-17 | 17.7 | 0.3 | 0 | 2016-09-17 | 11.9 | 6.1 | 0 | 4.91 | 0
2025-09-17 | 11.9 | 6.1 | 0 | 2024-09-17 | 15.8 | 2.2 | 0 | 2023-09-17 | 10.5 | 7.5 | 0 | 2022-09-17 | 8 | 10 | 0 | 2021-09-17 | 11.1 | 6.9 | 0 | 2020-09-17 | 14.3 | 3.7 | 0 | 2019-09-17 | 9.8 | 8.2 | 0 | 2018-09-17 | 18.2 | 0 | 0.2 | 2017-09-17 | 17.3 | 0.7 | 0 | 2016-09-17 | 11.6 | 6.4 | 0 | 5.17 | 0.02
2025-09-17 | 12.2 | 5.8 | 0 | 2024-09-17 | 15.2 | 2.8 | 0 | 2023-09-17 | 9.9 | 8.1 | 0 | 2022-09-17 | 8.2 | 9.8 | 0 | 2021-09-17 | 10.2 | 7.8 | 0 | 2020-09-17 | 14.1 | 3.9 | 0 | 2019-09-17 | 8.4 | 9.6 | 0 | 2018-09-17 | 18.5 | 0 | 0.5 | 2017-09-17 | 16.7 | 1.3 | 0 | 2016-09-17 | 10.9 | 7.1 | 0 | 5.62 | 0.05
2025-09-17 | 12.1 | 5.9 | 0 | 2024-09-17 | 15.4 | 2.6 | 0 | 2023-09-17 | 11.7 | 6.3 | 0 | 2022-09-17 | 8.1 | 9.9 | 0 | 2021-09-17 | 9.7 | 8.3 | 0 | 2020-09-17 | 13.2 | 4.8 | 0 | 2019-09-17 | 8.5 | 9.5 | 0 | 2018-09-17 | 17.5 | 0.5 | 0 | 2017-09-17 | 16.5 | 1.5 | 0 | 2016-09-17 | 10.4 | 7.6 | 0 | 5.69 | 0
2025-09-17 | 10.9 | 7.1 | 0 | 2024-09-17 | 14.9 | 3.1 | 0 | 2023-09-17 | 12.8 | 5.2 | 0 | 2022-09-17 | 8.2 | 9.8 | 0 | 2021-09-17 | 9.5 | 8.5 | 0 | 2020-09-17 | 12.7 | 5.3 | 0 | 2019-09-17 | 9 | 9 | 0 | 2018-09-17 | 17.7 | 0.3 | 0 | 2017-09-17 | 16.1 | 1.9 | 0 | 2016-09-17 | 10 | 8 | 0 | 5.82 | 0
2025-09-17 | 10.7 | 7.3 | 0 | 2024-09-17 | 14 | 4 | 0 | 2023-09-17 | 13 | 5 | 0 | 2022-09-17 | 8.3 | 9.7 | 0 | 2021-09-17 | 9.5 | 8.5 | 0 | 2020-09-17 | 11.2 | 6.8 | 0 | 2019-09-17 | 9.6 | 8.4 | 0 | 2018-09-17 | 17.4 | 0.6 | 0 | 2017-09-17 | 15.7 | 2.3 | 0 | 2016-09-17 | 10.3 | 7.7 | 0 | 6.03 | 0
2025-09-17 | 12.9 | 5.1 | 0 | 2024-09-17 | 14.8 | 3.2 | 0 | 2023-09-17 | 13.5 | 4.5 | 0 | 2022-09-17 | 9.2 | 8.8 | 0 | 2021-09-17 | 11.6 | 6.4 | 0 | 2020-09-17 | 11.3 | 6.7 | 0 | 2019-09-17 | 11.3 | 6.7 | 0 | 2018-09-17 | 19.2 | 0 | 1.2 | 2017-09-17 | 17 | 1 | 0 | 2016-09-17 | 13 | 5 | 0 | 4.74 | 0.12
2025-09-17 | 15.6 | 2.4 | 0 | 2024-09-17 | 17.8 | 0.2 | 0 | 2023-09-17 | 15 | 3 | 0 | 2022-09-17 | 10.2 | 7.8 | 0 | 2021-09-17 | 15.2 | 2.8 | 0 | 2020-09-17 | 11 | 7 | 0 | 2019-09-17 | 13.9 | 4.1 | 0 | 2018-09-17 | 22 | 0 | 4 | 2017-09-17 | 19 | 0 | 1 | 2016-09-17 | 17.8 | 0.2 | 0 | 2.75 | 0.5
2025-09-17 | 17.7 | 0.3 | 0 | 2024-09-17 | 21.2 | 0 | 3.2 | 2023-09-17 | 17.1 | 0.9 | 0 | 2022-09-17 | 12.3 | 5.7 | 0 | 2021-09-17 | 18.9 | 0 | 0.9 | 2020-09-17 | 12.3 | 5.7 | 0 | 2019-09-17 | 15.7 | 2.3 | 0 | 2018-09-17 | 24.2 | 0 | 6.2 | 2017-09-17 | 21.8 | 0 | 3.8 | 2016-09-17 | 18.9 | 0 | 0.9 | 1.49 | 1.5
2025-09-17 | 20.3 | 0 | 2.3 | 2024-09-17 | 24.2 | 0 | 6.2 | 2023-09-17 | 18 | 0 | 0 | 2022-09-17 | 13.7 | 4.3 | 0 | 2021-09-17 | 20.5 | 0 | 2.5 | 2020-09-17 | 12.8 | 5.2 | 0 | 2019-09-17 | 17.6 | 0.4 | 0 | 2018-09-17 | 26.5 | 0 | 8.5 | 2017-09-17 | 24.3 | 0 | 6.3 | 2016-09-17 | 20.4 | 0 | 2.4 | 0.99 | 2.82
2025-09-17 | 21.3 | 0 | 3.3 | 2024-09-17 | 26.2 | 0 | 8.2 | 2023-09-17 | 20.2 | 0 | 2.2 | 2022-09-17 | 15.5 | 2.5 | 0 | 2021-09-17 | 22.1 | 0 | 4.1 | 2020-09-17 | 14 | 4 | 0 | 2019-09-17 | 18.2 | 0 | 0.2 | 2018-09-17 | 27.6 | 0 | 9.6 | 2017-09-17 | 26.8 | 0 | 8.8 | 2016-09-17 | 20.8 | 0 | 2.8 | 0.65 | 3.92
2025-09-17 | 22.6 | 0 | 4.6 | 2024-09-17 | 27.2 | 0 | 9.2 | 2023-09-17 | 22.3 | 0 | 4.3 | 2022-09-17 | 16.3 | 1.7 | 0 | 2021-09-17 | 23.5 | 0 | 5.5 | 2020-09-17 | 13.3 | 4.7 | 0 | 2019-09-17 | 20.1 | 0 | 2.1 | 2018-09-17 | 28.3 | 0 | 10.3 | 2017-09-17 | 27.5 | 0 | 9.5 | 2016-09-17 | 18.7 | 0 | 0.7 | 0.64 | 4.62
2025-09-17 | 24.4 | 0 | 6.4 | 2024-09-17 | 28 | 0 | 10 | 2023-09-17 | 23.7 | 0 | 5.7 | 2022-09-17 | 16.8 | 1.2 | 0 | 2021-09-17 | 25.7 | 0 | 7.7 | 2020-09-17 | 12.9 | 5.1 | 0 | 2019-09-17 | 21.1 | 0 | 3.1 | 2018-09-17 | 28.5 | 0 | 10.5 | 2017-09-17 | 27.7 | 0 | 9.7 | 2016-09-17 | 18 | 0 | 0 | 0.63 | 5.31
2025-09-17 | 25 | 0 | 7 | 2024-09-17 | 28.7 | 0 | 10.7 | 2023-09-17 | 22.7 | 0 | 4.7 | 2022-09-17 | 17.2 | 0.8 | 0 | 2021-09-17 | 26 | 0 | 8 | 2020-09-17 | 13.8 | 4.2 | 0 | 2019-09-17 | 21.2 | 0 | 3.2 | 2018-09-17 | 28.9 | 0 | 10.9 | 2017-09-17 | 28.3 | 0 | 10.3 | 2016-09-17 | 18.2 | 0 | 0.2 | 0.5 | 5.5
2025-09-17 | 25.6 | 0 | 7.6 | 2024-09-17 | 28.3 | 0 | 10.3 | 2023-09-17 | 22.4 | 0 | 4.4 | 2022-09-17 | 18.7 | 0 | 0.7 | 2021-09-17 | 24.5 | 0 | 6.5 | 2020-09-17 | 14 | 4 | 0 | 2019-09-17 | 22.2 | 0 | 4.2 | 2018-09-17 | 28.9 | 0 | 10.9 | 2017-09-17 | 27.4 | 0 | 9.4 | 2016-09-17 | 18.7 | 0 | 0.7 | 0.4 | 5.47
2025-09-17 | 25.4 | 0 | 7.4 | 2024-09-17 | 27.9 | 0 | 9.9 | 2023-09-17 | 23.8 | 0 | 5.8 | 2022-09-17 | 18.8 | 0 | 0.8 | 2021-09-17 | 24.6 | 0 | 6.6 | 2020-09-17 | 13.8 | 4.2 | 0 | 2019-09-17 | 21.9 | 0 | 3.9 | 2018-09-17 | 28.2 | 0 | 10.2 | 2017-09-17 | 26.9 | 0 | 8.9 | 2016-09-17 | 19.3 | 0 | 1.3 | 0.42 | 5.48
2025-09-17 | 25 | 0 | 7 | 2024-09-17 | 26.5 | 0 | 8.5 | 2023-09-17 | 22.2 | 0 | 4.2 | 2022-09-17 | 18.8 | 0 | 0.8 | 2021-09-17 | 24.7 | 0 | 6.7 | 2020-09-17 | 13.2 | 4.8 | 0 | 2019-09-17 | 20.9 | 0 | 2.9 | 2018-09-17 | 26.4 | 0 | 8.4 | 2017-09-17 | 26 | 0 | 8 | 2016-09-17 | 19.4 | 0 | 1.4 | 0.48 | 4.79
2025-09-17 | 21.6 | 0 | 3.6 | 2024-09-17 | 23.4 | 0 | 5.4 | 2023-09-17 | 20.2 | 0 | 2.2 | 2022-09-17 | 14.7 | 3.3 | 0 | 2021-09-17 | 22.7 | 0 | 4.7 | 2020-09-17 | 11.6 | 6.4 | 0 | 2019-09-17 | 18 | 0 | 0 | 2018-09-17 | 24.1 | 0 | 6.1 | 2017-09-17 | 22.9 | 0 | 4.9 | 2016-09-17 | 19.6 | 0 | 1.6 | 0.97 | 2.85
2025-09-17 | 19.8 | 0 | 1.8 | 2024-09-17 | 20.8 | 0 | 2.8 | 2023-09-17 | 18.2 | 0 | 0.2 | 2022-09-17 | 14.5 | 3.5 | 0 | 2021-09-17 | 21.4 | 0 | 3.4 | 2020-09-17 | 9.1 | 8.9 | 0 | 2019-09-17 | 14.7 | 3.3 | 0 | 2018-09-17 | 22.7 | 0 | 4.7 | 2017-09-17 | 21.8 | 0 | 3.8 | 2016-09-17 | 19.7 | 0 | 1.7 | 1.57 | 1.84
2025-09-17 | 19.1 | 0 | 1.1 | 2024-09-17 | 19.8 | 0 | 1.8 | 2023-09-17 | 17.4 | 0.6 | 0 | 2022-09-17 | 13.9 | 4.1 | 0 | 2021-09-17 | 20.7 | 0 | 2.7 | 2020-09-17 | 8.9 | 9.1 | 0 | 2019-09-17 | 14 | 4 | 0 | 2018-09-17 | 22 | 0 | 4 | 2017-09-17 | 20.6 | 0 | 2.6 | 2016-09-17 | 19.6 | 0 | 1.6 | 1.78 | 1.38
2025-09-17 | 16.4 | 1.6 | 0 | 2024-09-17 | 18.4 | 0 | 0.4 | 2023-09-17 | 17.6 | 0.4 | 0 | 2022-09-17 | 15 | 3 | 0 | 2021-09-17 | 20.3 | 0 | 2.3 | 2020-09-17 | 6.5 | 11.5 | 0 | 2019-09-17 | 11.5 | 6.5 | 0 | 2018-09-17 | 21.3 | 0 | 3.3 | 2017-09-17 | 20.2 | 0 | 2.2 | 2016-09-17 | 19.9 | 0 | 1.9 | 2.3 | 1.01
2025-09-17 | 16.2 | 1.8 | 0 | 2024-09-17 | 17.6 | 0.4 | 0 | 2023-09-17 | 17.1 | 0.9 | 0 | 2022-09-17 | 14.1 | 3.9 | 0 | 2021-09-17 | 20 | 0 | 2 | 2020-09-17 | 4.6 | 13.4 | 0 | 2019-09-17 | 12.1 | 5.9 | 0 | 2018-09-17 | 20.9 | 0 | 2.9 | 2017-09-17 | 18.9 | 0 | 0.9 | 2016-09-17 | 19.9 | 0 | 1.9 | 2.63 | 0.77
2025-09-17 | 16.2 | 1.8 | 0 | 2024-09-17 | 18.1 | 0 | 0.1 | 2023-09-17 | 16.1 | 1.9 | 0 | 2022-09-17 | 14.3 | 3.7 | 0 | 2021-09-17 | 19.7 | 0 | 1.7 | 2020-09-17 | 4.8 | 13.2 | 0 | 2019-09-17 | 12.2 | 5.8 | 0 | 2018-09-17 | 20.2 | 0 | 2.2 | 2017-09-17 | 18.4 | 0 | 0.4 | 2016-09-17 | 20 | 0 | 2 | 2.64 | 0.64
2025-09-18 | 15.9 | 2.1 | 0 | 2024-09-18 | 14.2 | 3.8 | 0 | 2023-09-18 | 15.2 | 2.8 | 0 | 2022-09-18 | 13.8 | 4.2 | 0 | 2021-09-18 | 19.6 | 0 | 1.6 | 2020-09-18 | 4.4 | 13.6 | 0 | 2019-09-18 | 8 | 10 | 0 | 2018-09-18 | 19.5 | 0 | 1.5 | 2017-09-18 | 18.7 | 0 | 0.7 | 2016-09-18 | 19.8 | 0 | 1.8 | 3.65 | 0.56
2025-09-18 | 15.2 | 2.8 | 0 | 2024-09-18 | 14 | 4 | 0 | 2023-09-18 | 14.3 | 3.7 | 0 | 2022-09-18 | 13.6 | 4.4 | 0 | 2021-09-18 | 19.2 | 0 | 1.2 | 2020-09-18 | 4 | 14 | 0 | 2019-09-18 | 8.6 | 9.4 | 0 | 2018-09-18 | 19.5 | 0 | 1.5 | 2017-09-18 | 14.7 | 3.3 | 0 | 2016-09-18 | 19.4 | 0 | 1.4 | 4.16 | 0.41
2025-09-18 | 14.7 | 3.3 | 0 | 2024-09-18 | 14.7 | 3.3 | 0 | 2023-09-18 | 14.1 | 3.9 | 0 | 2022-09-18 | 13.8 | 4.2 | 0 | 2021-09-18 | 19.1 | 0 | 1.1 | 2020-09-18 | 4.6 | 13.4 | 0 | 2019-09-18 | 9.1 | 8.9 | 0 | 2018-09-18 | 19.3 | 0 | 1.3 | 2017-09-18 | 15.7 | 2.3 | 0 | 2016-09-18 | 19 | 0 | 1 | 3.93 | 0.34
2025-09-18 | 13.9 | 4.1 | 0 | 2024-09-18 | 15 | 3 | 0 | 2023-09-18 | 14.8 | 3.2 | 0 | 2022-09-18 | 13.8 | 4.2 | 0 | 2021-09-18 | 18.4 | 0 | 0.4 | 2020-09-18 | 3.9 | 14.1 | 0 | 2019-09-18 | 9.2 | 8.8 | 0 | 2018-09-18 | 18.6 | 0 | 0.6 | 2017-09-18 | 13.7 | 4.3 | 0 | 2016-09-18 | 18.9 | 0 | 0.9 | 4.17 | 0.19
2025-09-18 | 13.6 | 4.4 | 0 | 2024-09-18 | 13.8 | 4.2 | 0 | 2023-09-18 | 13.1 | 4.9 | 0 | 2022-09-18 | 14.5 | 3.5 | 0 | 2021-09-18 | 18.5 | 0 | 0.5 | 2020-09-18 | 3.7 | 14.3 | 0 | 2019-09-18 | 9.7 | 8.3 | 0 | 2018-09-18 | 18.5 | 0 | 0.5 | 2017-09-18 | 14.9 | 3.1 | 0 | 2016-09-18 | 18.1 | 0 | 0.1 | 4.27 | 0.11
2025-09-18 | 12.7 | 5.3 | 0 | 2024-09-18 | 14.4 | 3.6 | 0 | 2023-09-18 | 12.9 | 5.1 | 0 | 2022-09-18 | 15.2 | 2.8 | 0 | 2021-09-18 | 17.6 | 0.4 | 0 | 2020-09-18 | 2.9 | 15.1 | 0 | 2019-09-18 | 9.7 | 8.3 | 0 | 2018-09-18 | 17.8 | 0.2 | 0 | 2017-09-18 | 15.1 | 2.9 | 0 | 2016-09-18 | 17.1 | 0.9 | 0 | 4.46 | 0
2025-09-18 | 11.8 | 6.2 | 0 | 2024-09-18 | 14.5 | 3.5 | 0 | 2023-09-18 | 10.8 | 7.2 | 0 | 2022-09-18 | 16 | 2 | 0 | 2021-09-18 | 17.8 | 0.2 | 0 | 2020-09-18 | 4.7 | 13.3 | 0 | 2019-09-18 | 9.9 | 8.1 | 0 | 2018-09-18 | 17.9 | 0.1 | 0 | 2017-09-18 | 14 | 4 | 0 | 2016-09-18 | 16.9 | 1.1 | 0 | 4.57 | 0
2025-09-18 | 14.2 | 3.8 | 0 | 2024-09-18 | 15.9 | 2.1 | 0 | 2023-09-18 | 13.4 | 4.6 | 0 | 2022-09-18 | 17.3 | 0.7 | 0 | 2021-09-18 | 16.7 | 1.3 | 0 | 2020-09-18 | 5.8 | 12.2 | 0 | 2019-09-18 | 11.2 | 6.8 | 0 | 2018-09-18 | 19 | 0 | 1 | 2017-09-18 | 16.5 | 1.5 | 0 | 2016-09-18 | 18.2 | 0 | 0.2 | 3.3 | 0.12
2025-09-18 | 17.4 | 0.6 | 0 | 2024-09-18 | 17.2 | 0.8 | 0 | 2023-09-18 | 16.5 | 1.5 | 0 | 2022-09-18 | 18.3 | 0 | 0.3 | 2021-09-18 | 17.8 | 0.2 | 0 | 2020-09-18 | 7.3 | 10.7 | 0 | 2019-09-18 | 11.7 | 6.3 | 0 | 2018-09-18 | 20.6 | 0 | 2.6 | 2017-09-18 | 18.2 | 0 | 0.2 | 2016-09-18 | 19 | 0 | 1 | 2.01 | 0.41
2025-09-18 | 20.1 | 0 | 2.1 | 2024-09-18 | 20.6 | 0 | 2.6 | 2023-09-18 | 18.2 | 0 | 0.2 | 2022-09-18 | 20.4 | 0 | 2.4 | 2021-09-18 | 18.1 | 0 | 0.1 | 2020-09-18 | 10.3 | 7.7 | 0 | 2019-09-18 | 15.2 | 2.8 | 0 | 2018-09-18 | 21 | 0 | 3 | 2017-09-18 | 21.4 | 0 | 3.4 | 2016-09-18 | 21.8 | 0 | 3.8 | 1.05 | 1.76
2025-09-18 | 22.1 | 0 | 4.1 | 2024-09-18 | 23 | 0 | 5 | 2023-09-18 | 19.6 | 0 | 1.6 | 2022-09-18 | 18.6 | 0 | 0.6 | 2021-09-18 | 18.9 | 0 | 0.9 | 2020-09-18 | 11.8 | 6.2 | 0 | 2019-09-18 | 17.1 | 0.9 | 0 | 2018-09-18 | 20.9 | 0 | 2.9 | 2017-09-18 | 22.6 | 0 | 4.6 | 2016-09-18 | 21 | 0 | 3 | 0.71 | 2.27
2025-09-18 | 24.4 | 0 | 6.4 | 2024-09-18 | 24.2 | 0 | 6.2 | 2023-09-18 | 20.2 | 0 | 2.2 | 2022-09-18 | 18.7 | 0 | 0.7 | 2021-09-18 | 20.4 | 0 | 2.4 | 2020-09-18 | 13.3 | 4.7 | 0 | 2019-09-18 | 18.6 | 0 | 0.6 | 2018-09-18 | 21.3 | 0 | 3.3 | 2017-09-18 | 24.9 | 0 | 6.9 | 2016-09-18 | 23.3 | 0 | 5.3 | 0.47 | 3.4
2025-09-18 | 24.4 | 0 | 6.4 | 2024-09-18 | 25.9 | 0 | 7.9 | 2023-09-18 | 20.4 | 0 | 2.4 | 2022-09-18 | 20 | 0 | 2 | 2021-09-18 | 21.6 | 0 | 3.6 | 2020-09-18 | 12.5 | 5.5 | 0 | 2019-09-18 | 19 | 0 | 1 | 2018-09-18 | 20.6 | 0 | 2.6 | 2017-09-18 | 25.8 | 0 | 7.8 | 2016-09-18 | 24 | 0 | 6 | 0.55 | 3.97
2025-09-18 | 25.2 | 0 | 7.2 | 2024-09-18 | 26.2 | 0 | 8.2 | 2023-09-18 | 20.1 | 0 | 2.1 | 2022-09-18 | 15 | 3 | 0 | 2021-09-18 | 22.2 | 0 | 4.2 | 2020-09-18 | 11.6 | 6.4 | 0 | 2019-09-18 | 19.8 | 0 | 1.8 | 2018-09-18 | 21.4 | 0 | 3.4 | 2017-09-18 | 26.9 | 0 | 8.9 | 2016-09-18 | 25.1 | 0 | 7.1 | 0.94 | 4.29
2025-09-18 | 25.3 | 0 | 7.3 | 2024-09-18 | 27 | 0 | 9 | 2023-09-18 | 21.2 | 0 | 3.2 | 2022-09-18 | 12.8 | 5.2 | 0 | 2021-09-18 | 22.1 | 0 | 4.1 | 2020-09-18 | 11.9 | 6.1 | 0 | 2019-09-18 | 20 | 0 | 2 | 2018-09-18 | 22 | 0 | 4 | 2017-09-18 | 27.3 | 0 | 9.3 | 2016-09-18 | 26 | 0 | 8 | 1.13 | 4.69
2025-09-18 | 24.3 | 0 | 6.3 | 2024-09-18 | 27.3 | 0 | 9.3 | 2023-09-18 | 20.3 | 0 | 2.3 | 2022-09-18 | 12.3 | 5.7 | 0 | 2021-09-18 | 21.5 | 0 | 3.5 | 2020-09-18 | 11.7 | 6.3 | 0 | 2019-09-18 | 20.4 | 0 | 2.4 | 2018-09-18 | 22.8 | 0 | 4.8 | 2017-09-18 | 27.8 | 0 | 9.8 | 2016-09-18 | 26.3 | 0 | 8.3 | 1.2 | 4.67
2025-09-18 | 23.7 | 0 | 5.7 | 2024-09-18 | 26.6 | 0 | 8.6 | 2023-09-18 | 19.9 | 0 | 1.9 | 2022-09-18 | 12.1 | 5.9 | 0 | 2021-09-18 | 20.9 | 0 | 2.9 | 2020-09-18 | 12.3 | 5.7 | 0 | 2019-09-18 | 19.9 | 0 | 1.9 | 2018-09-18 | 22.5 | 0 | 4.5 | 2017-09-18 | 26.7 | 0 | 8.7 | 2016-09-18 | 25.9 | 0 | 7.9 | 1.16 | 4.21
2025-09-18 | 23.8 | 0 | 5.8 | 2024-09-18 | 24.2 | 0 | 6.2 | 2023-09-18 | 19.5 | 0 | 1.5 | 2022-09-18 | 11.8 | 6.2 | 0 | 2021-09-18 | 20.1 | 0 | 2.1 | 2020-09-18 | 11.3 | 6.7 | 0 | 2019-09-18 | 19.1 | 0 | 1.1 | 2018-09-18 | 21.1 | 0 | 3.1 | 2017-09-18 | 25.8 | 0 | 7.8 | 2016-09-18 | 23.5 | 0 | 5.5 | 1.29 | 3.31
2025-09-18 | 22.2 | 0 | 4.2 | 2024-09-18 | 22.5 | 0 | 4.5 | 2023-09-18 | 16.7 | 1.3 | 0 | 2022-09-18 | 11.8 | 6.2 | 0 | 2021-09-18 | 18.4 | 0 | 0.4 | 2020-09-18 | 9.6 | 8.4 | 0 | 2019-09-18 | 15.6 | 2.4 | 0 | 2018-09-18 | 19.4 | 0 | 1.4 | 2017-09-18 | 23.8 | 0 | 5.8 | 2016-09-18 | 21 | 0 | 3 | 1.83 | 1.93
2025-09-18 | 21.2 | 0 | 3.2 | 2024-09-18 | 20.9 | 0 | 2.9 | 2023-09-18 | 15.5 | 2.5 | 0 | 2022-09-18 | 11.8 | 6.2 | 0 | 2021-09-18 | 16.9 | 1.1 | 0 | 2020-09-18 | 8.4 | 9.6 | 0 | 2019-09-18 | 12.6 | 5.4 | 0 | 2018-09-18 | 18.1 | 0 | 0.1 | 2017-09-18 | 22.1 | 0 | 4.1 | 2016-09-18 | 19.7 | 0 | 1.7 | 2.48 | 1.2
2025-09-18 | 19.3 | 0 | 1.3 | 2024-09-18 | 20.8 | 0 | 2.8 | 2023-09-18 | 15.1 | 2.9 | 0 | 2022-09-18 | 11.8 | 6.2 | 0 | 2021-09-18 | 15.8 | 2.2 | 0 | 2020-09-18 | 7.4 | 10.6 | 0 | 2019-09-18 | 12.6 | 5.4 | 0 | 2018-09-18 | 16.2 | 1.8 | 0 | 2017-09-18 | 21.9 | 0 | 3.9 | 2016-09-18 | 19.2 | 0 | 1.2 | 2.91 | 0.92
2025-09-18 | 17.1 | 0.9 | 0 | 2024-09-18 | 19.9 | 0 | 1.9 | 2023-09-18 | 15 | 3 | 0 | 2022-09-18 | 11.9 | 6.1 | 0 | 2021-09-18 | 15.1 | 2.9 | 0 | 2020-09-18 | 7.1 | 10.9 | 0 | 2019-09-18 | 11.3 | 6.7 | 0 | 2018-09-18 | 16.1 | 1.9 | 0 | 2017-09-18 | 20.3 | 0 | 2.3 | 2016-09-18 | 18.2 | 0 | 0.2 | 3.24 | 0.44
2025-09-18 | 16 | 2 | 0 | 2024-09-18 | 19 | 0 | 1 | 2023-09-18 | 14.9 | 3.1 | 0 | 2022-09-18 | 11.9 | 6.1 | 0 | 2021-09-18 | 14.2 | 3.8 | 0 | 2020-09-18 | 6 | 12 | 0 | 2019-09-18 | 10.6 | 7.4 | 0 | 2018-09-18 | 15.8 | 2.2 | 0 | 2017-09-18 | 19 | 0 | 1 | 2016-09-18 | 18 | 0 | 0 | 3.66 | 0.2
2025-09-18 | 14.6 | 3.4 | 0 | 2024-09-18 | 19.1 | 0 | 1.1 | 2023-09-18 | 14.8 | 3.2 | 0 | 2022-09-18 | 11.9 | 6.1 | 0 | 2021-09-18 | 13.2 | 4.8 | 0 | 2020-09-18 | 5.8 | 12.2 | 0 | 2019-09-18 | 11.1 | 6.9 | 0 | 2018-09-18 | 15.6 | 2.4 | 0 | 2017-09-18 | 20.3 | 0 | 2.3 | 2016-09-18 | 17.8 | 0.2 | 0 | 3.92 | 0.34
2025-09-19 | 13.2 | 4.8 | 0 | 2024-09-19 | 19.2 | 0 | 1.2 | 2023-09-19 | 14.6 | 3.4 | 0 | 2022-09-19 | 11.8 | 6.2 | 0 | 2021-09-19 | 13.1 | 4.9 | 0 | 2020-09-19 | 5.7 | 12.3 | 0 | 2019-09-19 | 9.7 | 8.3 | 0 | 2018-09-19 | 14.5 | 3.5 | 0 | 2017-09-19 | 18 | 0 | 0 | 2016-09-19 | 17.2 | 0.8 | 0 | 4.42 | 0.12
2025-09-19 | 11.8 | 6.2 | 0 | 2024-09-19 | 17.7 | 0.3 | 0 | 2023-09-19 | 14.3 | 3.7 | 0 | 2022-09-19 | 11.8 | 6.2 | 0 | 2021-09-19 | 12.5 | 5.5 | 0 | 2020-09-19 | 2.8 | 15.2 | 0 | 2019-09-19 | 9.1 | 8.9 | 0 | 2018-09-19 | 12.3 | 5.7 | 0 | 2017-09-19 | 17.9 | 0.1 | 0 | 2016-09-19 | 16.9 | 1.1 | 0 | 5.29 | 0
2025-09-19 | 11.6 | 6.4 | 0 | 2024-09-19 | 15.4 | 2.6 | 0 | 2023-09-19 | 14.3 | 3.7 | 0 | 2022-09-19 | 11.9 | 6.1 | 0 | 2021-09-19 | 11.5 | 6.5 | 0 | 2020-09-19 | 3.2 | 14.8 | 0 | 2019-09-19 | 9.4 | 8.6 | 0 | 2018-09-19 | 13.2 | 4.8 | 0 | 2017-09-19 | 17.1 | 0.9 | 0 | 2016-09-19 | 16.2 | 1.8 | 0 | 5.62 | 0
2025-09-19 | 9.2 | 8.8 | 0 | 2024-09-19 | 16.6 | 1.4 | 0 | 2023-09-19 | 14.4 | 3.6 | 0 | 2022-09-19 | 11.8 | 6.2 | 0 | 2021-09-19 | 10.6 | 7.4 | 0 | 2020-09-19 | 1 | 17 | 0 | 2019-09-19 | 8.6 | 9.4 | 0 | 2018-09-19 | 13.6 | 4.4 | 0 | 2017-09-19 | 18 | 0 | 0 | 2016-09-19 | 16.4 | 1.6 | 0 | 5.98 | 0
2025-09-19 | 8.3 | 9.7 | 0 | 2024-09-19 | 16.5 | 1.5 | 0 | 2023-09-19 | 14.2 | 3.8 | 0 | 2022-09-19 | 11.7 | 6.3 | 0 | 2021-09-19 | 10.8 | 7.2 | 0 | 2020-09-19 | 0.4 | 17.6 | 0 | 2019-09-19 | 8.2 | 9.8 | 0 | 2018-09-19 | 13.2 | 4.8 | 0 | 2017-09-19 | 16 | 2 | 0 | 2016-09-19 | 15.8 | 2.2 | 0 | 6.49 | 0
2025-09-19 | 8.7 | 9.3 | 0 | 2024-09-19 | 15.3 | 2.7 | 0 | 2023-09-19 | 14 | 4 | 0 | 2022-09-19 | 11.4 | 6.6 | 0 | 2021-09-19 | 10.2 | 7.8 | 0 | 2020-09-19 | 0.6 | 17.4 | 0 | 2019-09-19 | 6.3 | 11.7 | 0 | 2018-09-19 | 12.6 | 5.4 | 0 | 2017-09-19 | 15.2 | 2.8 | 0 | 2016-09-19 | 14 | 4 | 0 | 7.17 | 0
2025-09-19 | 9.1 | 8.9 | 0 | 2024-09-19 | 12.7 | 5.3 | 0 | 2023-09-19 | 13.9 | 4.1 | 0 | 2022-09-19 | 10.9 | 7.1 | 0 | 2021-09-19 | 9.8 | 8.2 | 0 | 2020-09-19 | 0.3 | 17.7 | 0 | 2019-09-19 | 6.5 | 11.5 | 0 | 2018-09-19 | 12.3 | 5.7 | 0 | 2017-09-19 | 15.7 | 2.3 | 0 | 2016-09-19 | 14.4 | 3.6 | 0 | 7.44 | 0
2025-09-19 | 10.2 | 7.8 | 0 | 2024-09-19 | 16.4 | 1.6 | 0 | 2023-09-19 | 13.8 | 4.2 | 0 | 2022-09-19 | 10.6 | 7.4 | 0 | 2021-09-19 | 11.5 | 6.5 | 0 | 2020-09-19 | 2.7 | 15.3 | 0 | 2019-09-19 | 9.2 | 8.8 | 0 | 2018-09-19 | 12.4 | 5.6 | 0 | 2017-09-19 | 18 | 0 | 0 | 2016-09-19 | 15 | 3 | 0 | 6.02 | 0
2025-09-19 | 12.1 | 5.9 | 0 | 2024-09-19 | 20 | 0 | 2 | 2023-09-19 | 14 | 4 | 0 | 2022-09-19 | 10.7 | 7.3 | 0 | 2021-09-19 | 13.4 | 4.6 | 0 | 2020-09-19 | 6.2 | 11.8 | 0 | 2019-09-19 | 11.1 | 6.9 | 0 | 2018-09-19 | 13 | 5 | 0 | 2017-09-19 | 19.7 | 0 | 1.7 | 2016-09-19 | 16.3 | 1.7 | 0 | 4.72 | 0.37
2025-09-19 | 13 | 5 | 0 | 2024-09-19 | 22 | 0 | 4 | 2023-09-19 | 14.2 | 3.8 | 0 | 2022-09-19 | 10.8 | 7.2 | 0 | 2021-09-19 | 15.3 | 2.7 | 0 | 2020-09-19 | 8.3 | 9.7 | 0 | 2019-09-19 | 14.6 | 3.4 | 0 | 2018-09-19 | 13.6 | 4.4 | 0 | 2017-09-19 | 21.7 | 0 | 3.7 | 2016-09-19 | 17.7 | 0.3 | 0 | 3.65 | 0.77
2025-09-19 | 14.6 | 3.4 | 0 | 2024-09-19 | 24.1 | 0 | 6.1 | 2023-09-19 | 15.2 | 2.8 | 0 | 2022-09-19 | 11.2 | 6.8 | 0 | 2021-09-19 | 16.6 | 1.4 | 0 | 2020-09-19 | 9.7 | 8.3 | 0 | 2019-09-19 | 17 | 1 | 0 | 2018-09-19 | 13.8 | 4.2 | 0 | 2017-09-19 | 23.2 | 0 | 5.2 | 2016-09-19 | 19.2 | 0 | 1.2 | 2.79 | 1.25
2025-09-19 | 15.6 | 2.4 | 0 | 2024-09-19 | 25.5 | 0 | 7.5 | 2023-09-19 | 15.5 | 2.5 | 0 | 2022-09-19 | 11.2 | 6.8 | 0 | 2021-09-19 | 16.9 | 1.1 | 0 | 2020-09-19 | 10.4 | 7.6 | 0 | 2019-09-19 | 19.6 | 0 | 1.6 | 2018-09-19 | 14.5 | 3.5 | 0 | 2017-09-19 | 24.6 | 0 | 6.6 | 2016-09-19 | 20.8 | 0 | 2.8 | 2.39 | 1.85
2025-09-19 | 16.2 | 1.8 | 0 | 2024-09-19 | 27 | 0 | 9 | 2023-09-19 | 16.4 | 1.6 | 0 | 2022-09-19 | 11.3 | 6.7 | 0 | 2021-09-19 | 18.3 | 0 | 0.3 | 2020-09-19 | 11.7 | 6.3 | 0 | 2019-09-19 | 20.5 | 0 | 2.5 | 2018-09-19 | 14.9 | 3.1 | 0 | 2017-09-19 | 25.8 | 0 | 7.8 | 2016-09-19 | 22.7 | 0 | 4.7 | 1.95 | 2.43
2025-09-19 | 17.6 | 0.4 | 0 | 2024-09-19 | 27.5 | 0 | 9.5 | 2023-09-19 | 17.9 | 0.1 | 0 | 2022-09-19 | 11.9 | 6.1 | 0 | 2021-09-19 | 19.2 | 0 | 1.2 | 2020-09-19 | 12.3 | 5.7 | 0 | 2019-09-19 | 22 | 0 | 4 | 2018-09-19 | 16.4 | 1.6 | 0 | 2017-09-19 | 27 | 0 | 9 | 2016-09-19 | 24.2 | 0 | 6.2 | 1.39 | 2.99
2025-09-19 | 18.9 | 0 | 0.9 | 2024-09-19 | 27.4 | 0 | 9.4 | 2023-09-19 | 19 | 0 | 1 | 2022-09-19 | 12.3 | 5.7 | 0 | 2021-09-19 | 19.9 | 0 | 1.9 | 2020-09-19 | 12.8 | 5.2 | 0 | 2019-09-19 | 23.4 | 0 | 5.4 | 2018-09-19 | 16.3 | 1.7 | 0 | 2017-09-19 | 27 | 0 | 9 | 2016-09-19 | 24.9 | 0 | 6.9 | 1.26 | 3.45
2025-09-19 | 18.3 | 0 | 0.3 | 2024-09-19 | 27.6 | 0 | 9.6 | 2023-09-19 | 18.3 | 0 | 0.3 | 2022-09-19 | 13.2 | 4.8 | 0 | 2021-09-19 | 20 | 0 | 2 | 2020-09-19 | 13.5 | 4.5 | 0 | 2019-09-19 | 23.5 | 0 | 5.5 | 2018-09-19 | 16.5 | 1.5 | 0 | 2017-09-19 | 27.2 | 0 | 9.2 | 2016-09-19 | 23.8 | 0 | 5.8 | 1.08 | 3.27
2025-09-19 | 18.3 | 0 | 0.3 | 2024-09-19 | 27.3 | 0 | 9.3 | 2023-09-19 | 18.4 | 0 | 0.4 | 2022-09-19 | 12.8 | 5.2 | 0 | 2021-09-19 | 20.3 | 0 | 2.3 | 2020-09-19 | 13.1 | 4.9 | 0 | 2019-09-19 | 23.4 | 0 | 5.4 | 2018-09-19 | 16.5 | 1.5 | 0 | 2017-09-19 | 26.8 | 0 | 8.8 | 2016-09-19 | 24.4 | 0 | 6.4 | 1.16 | 3.29
2025-09-19 | 17.3 | 0.7 | 0 | 2024-09-19 | 26 | 0 | 8 | 2023-09-19 | 17.9 | 0.1 | 0 | 2022-09-19 | 12.4 | 5.6 | 0 | 2021-09-19 | 19.5 | 0 | 1.5 | 2020-09-19 | 12.3 | 5.7 | 0 | 2019-09-19 | 22.2 | 0 | 4.2 | 2018-09-19 | 16.5 | 1.5 | 0 | 2017-09-19 | 25.3 | 0 | 7.3 | 2016-09-19 | 24.1 | 0 | 6.1 | 1.36 | 2.71
2025-09-19 | 15.3 | 2.7 | 0 | 2024-09-19 | 23.2 | 0 | 5.2 | 2023-09-19 | 16.1 | 1.9 | 0 | 2022-09-19 | 11.9 | 6.1 | 0 | 2021-09-19 | 17.7 | 0.3 | 0 | 2020-09-19 | 9.5 | 8.5 | 0 | 2019-09-19 | 19.4 | 0 | 1.4 | 2018-09-19 | 15.4 | 2.6 | 0 | 2017-09-19 | 24.5 | 0 | 6.5 | 2016-09-19 | 20.5 | 0 | 2.5 | 2.21 | 1.56
2025-09-19 | 14.3 | 3.7 | 0 | 2024-09-19 | 20.7 | 0 | 2.7 | 2023-09-19 | 14.2 | 3.8 | 0 | 2022-09-19 | 11.8 | 6.2 | 0 | 2021-09-19 | 13.8 | 4.2 | 0 | 2020-09-19 | 8.6 | 9.4 | 0 | 2019-09-19 | 17.8 | 0.2 | 0 | 2018-09-19 | 15.6 | 2.4 | 0 | 2017-09-19 | 23.7 | 0 | 5.7 | 2016-09-19 | 20.4 | 0 | 2.4 | 2.99 | 1.08
2025-09-19 | 12.5 | 5.5 | 0 | 2024-09-19 | 20.8 | 0 | 2.8 | 2023-09-19 | 12.3 | 5.7 | 0 | 2022-09-19 | 11.8 | 6.2 | 0 | 2021-09-19 | 12.6 | 5.4 | 0 | 2020-09-19 | 4.7 | 13.3 | 0 | 2019-09-19 | 16.4 | 1.6 | 0 | 2018-09-19 | 14.6 | 3.4 | 0 | 2017-09-19 | 22.8 | 0 | 4.8 | 2016-09-19 | 19.5 | 0 | 1.5 | 4.11 | 0.91
2025-09-19 | 11.3 | 6.7 | 0 | 2024-09-19 | 17.8 | 0.2 | 0 | 2023-09-19 | 12 | 6 | 0 | 2022-09-19 | 11.7 | 6.3 | 0 | 2021-09-19 | 11.1 | 6.9 | 0 | 2020-09-19 | 7.2 | 10.8 | 0 | 2019-09-19 | 14.9 | 3.1 | 0 | 2018-09-19 | 12 | 6 | 0 | 2017-09-19 | 22.1 | 0 | 4.1 | 2016-09-19 | 18.3 | 0 | 0.3 | 4.6 | 0.44
2025-09-19 | 10.5 | 7.5 | 0 | 2024-09-19 | 18.6 | 0 | 0.6 | 2023-09-19 | 11.7 | 6.3 | 0 | 2022-09-19 | 11.5 | 6.5 | 0 | 2021-09-19 | 11.6 | 6.4 | 0 | 2020-09-19 | 5.7 | 12.3 | 0 | 2019-09-19 | 14.5 | 3.5 | 0 | 2018-09-19 | 10.9 | 7.1 | 0 | 2017-09-19 | 21.5 | 0 | 3.5 | 2016-09-19 | 17.5 | 0.5 | 0 | 5.01 | 0.41
2025-09-19 | 9.5 | 8.5 | 0 | 2024-09-19 | 17.5 | 0.5 | 0 | 2023-09-19 | 11.6 | 6.4 | 0 | 2022-09-19 | 11.6 | 6.4 | 0 | 2021-09-19 | 11.3 | 6.7 | 0 | 2020-09-19 | 3.7 | 14.3 | 0 | 2019-09-19 | 14.1 | 3.9 | 0 | 2018-09-19 | 9.8 | 8.2 | 0 | 2017-09-19 | 20.8 | 0 | 2.8 | 2016-09-19 | 16.7 | 1.3 | 0 | 5.62 | 0.28
2025-09-20 | 8.7 | 9.3 | 0 | 2024-09-20 | 17.7 | 0.3 | 0 | 2023-09-20 | 8.9 | 9.1 | 0 | 2022-09-20 | 11.6 | 6.4 | 0 | 2021-09-20 | 9.9 | 8.1 | 0 | 2020-09-20 | 7.9 | 10.1 | 0 | 2019-09-20 | 13.2 | 4.8 | 0 | 2018-09-20 | 10 | 8 | 0 | 2017-09-20 | 20.3 | 0 | 2.3 | 2016-09-20 | 16.3 | 1.7 | 0 | 5.78 | 0.23
2025-09-20 | 8 | 10 | 0 | 2024-09-20 | 16.9 | 1.1 | 0 | 2023-09-20 | 8.8 | 9.2 | 0 | 2022-09-20 | 11.6 | 6.4 | 0 | 2021-09-20 | 10.5 | 7.5 | 0 | 2020-09-20 | 6.7 | 11.3 | 0 | 2019-09-20 | 11.4 | 6.6 | 0 | 2018-09-20 | 8.7 | 9.3 | 0 | 2017-09-20 | 19.8 | 0 | 1.8 | 2016-09-20 | 16.1 | 1.9 | 0 | 6.33 | 0.18
2025-09-20 | 5.1 | 12.9 | 0 | 2024-09-20 | 17 | 1 | 0 | 2023-09-20 | 7.1 | 10.9 | 0 | 2022-09-20 | 11.7 | 6.3 | 0 | 2021-09-20 | 8.2 | 9.8 | 0 | 2020-09-20 | 6.4 | 11.6 | 0 | 2019-09-20 | 11.5 | 6.5 | 0 | 2018-09-20 | 8.6 | 9.4 | 0 | 2017-09-20 | 19.2 | 0 | 1.2 | 2016-09-20 | 16.1 | 1.9 | 0 | 7.03 | 0.12
2025-09-20 | 6.3 | 11.7 | 0 | 2024-09-20 | 16.2 | 1.8 | 0 | 2023-09-20 | 6.6 | 11.4 | 0 | 2022-09-20 | 11.8 | 6.2 | 0 | 2021-09-20 | 8 | 10 | 0 | 2020-09-20 | 6 | 12 | 0 | 2019-09-20 | 11.5 | 6.5 | 0 | 2018-09-20 | 9.2 | 8.8 | 0 | 2017-09-20 | 18.6 | 0 | 0.6 | 2016-09-20 | 15.9 | 2.1 | 0 | 7.05 | 0.06
2025-09-20 | 5.7 | 12.3 | 0 | 2024-09-20 | 15.6 | 2.4 | 0 | 2023-09-20 | 7.3 | 10.7 | 0 | 2022-09-20 | 11.9 | 6.1 | 0 | 2021-09-20 | 7.1 | 10.9 | 0 | 2020-09-20 | 4.8 | 13.2 | 0 | 2019-09-20 | 10.1 | 7.9 | 0 | 2018-09-20 | 10.9 | 7.1 | 0 | 2017-09-20 | 18.3 | 0 | 0.3 | 2016-09-20 | 17.2 | 0.8 | 0 | 7.14 | 0.03
2025-09-20 | 4.6 | 13.4 | 0 | 2024-09-20 | 14.9 | 3.1 | 0 | 2023-09-20 | 7.1 | 10.9 | 0 | 2022-09-20 | 11.8 | 6.2 | 0 | 2021-09-20 | 6 | 12 | 0 | 2020-09-20 | 4.9 | 13.1 | 0 | 2019-09-20 | 10.2 | 7.8 | 0 | 2018-09-20 | 11 | 7 | 0 | 2017-09-20 | 18.3 | 0 | 0.3 | 2016-09-20 | 16.6 | 1.4 | 0 | 7.49 | 0.03
2025-09-20 | 4.3 | 13.7 | 0 | 2024-09-20 | 14.8 | 3.2 | 0 | 2023-09-20 | 7.2 | 10.8 | 0 | 2022-09-20 | 11.7 | 6.3 | 0 | 2021-09-20 | 6.3 | 11.7 | 0 | 2020-09-20 | 3.3 | 14.7 | 0 | 2019-09-20 | 10 | 8 | 0 | 2018-09-20 | 11.1 | 6.9 | 0 | 2017-09-20 | 17.9 | 0.1 | 0 | 2016-09-20 | 16.5 | 1.5 | 0 | 7.69 | 0
2025-09-20 | 6.9 | 11.1 | 0 | 2024-09-20 | 15.9 | 2.1 | 0 | 2023-09-20 | 8.4 | 9.6 | 0 | 2022-09-20 | 12.1 | 5.9 | 0 | 2021-09-20 | 9.7 | 8.3 | 0 | 2020-09-20 | 6.3 | 11.7 | 0 | 2019-09-20 | 11.2 | 6.8 | 0 | 2018-09-20 | 10.9 | 7.1 | 0 | 2017-09-20 | 18.7 | 0 | 0.7 | 2016-09-20 | 17.5 | 0.5 | 0 | 6.31 | 0.07
2025-09-20 | 9.5 | 8.5 | 0 | 2024-09-20 | 17 | 1 | 0 | 2023-09-20 | 10 | 8 | 0 | 2022-09-20 | 11.9 | 6.1 | 0 | 2021-09-20 | 11.8 | 6.2 | 0 | 2020-09-20 | 8.5 | 9.5 | 0 | 2019-09-20 | 14.3 | 3.7 | 0 | 2018-09-20 | 11 | 7 | 0 | 2017-09-20 | 21 | 0 | 3 | 2016-09-20 | 19.5 | 0 | 1.5 | 5 | 0.45
2025-09-20 | 11.8 | 6.2 | 0 | 2024-09-20 | 18.8 | 0 | 0.8 | 2023-09-20 | 12 | 6 | 0 | 2022-09-20 | 12.3 | 5.7 | 0 | 2021-09-20 | 14.7 | 3.3 | 0 | 2020-09-20 | 10.5 | 7.5 | 0 | 2019-09-20 | 17.7 | 0.3 | 0 | 2018-09-20 | 12.1 | 5.9 | 0 | 2017-09-20 | 22.3 | 0 | 4.3 | 2016-09-20 | 20.4 | 0 | 2.4 | 3.49 | 0.75
2025-09-20 | 11.9 | 6.1 | 0 | 2024-09-20 | 20.2 | 0 | 2.2 | 2023-09-20 | 13.9 | 4.1 | 0 | 2022-09-20 | 12.9 | 5.1 | 0 | 2021-09-20 | 17.2 | 0.8 | 0 | 2020-09-20 | 11.4 | 6.6 | 0 | 2019-09-20 | 20 | 0 | 2 | 2018-09-20 | 13.2 | 4.8 | 0 | 2017-09-20 | 24 | 0 | 6 | 2016-09-20 | 23 | 0 | 5 | 2.75 | 1.52
2025-09-20 | 13.6 | 4.4 | 0 | 2024-09-20 | 21.9 | 0 | 3.9 | 2023-09-20 | 16.4 | 1.6 | 0 | 2022-09-20 | 13.3 | 4.7 | 0 | 2021-09-20 | 19.8 | 0 | 1.8 | 2020-09-20 | 12.7 | 5.3 | 0 | 2019-09-20 | 22 | 0 | 4 | 2018-09-20 | 13.8 | 4.2 | 0 | 2017-09-20 | 24.1 | 0 | 6.1 | 2016-09-20 | 24 | 0 | 6 | 2.02 | 2.18
2025-09-20 | 14.8 | 3.2 | 0 | 2024-09-20 | 23.9 | 0 | 5.9 | 2023-09-20 | 16.6 | 1.4 | 0 | 2022-09-20 | 14.7 | 3.3 | 0 | 2021-09-20 | 21.7 | 0 | 3.7 | 2020-09-20 | 13.4 | 4.6 | 0 | 2019-09-20 | 23.3 | 0 | 5.3 | 2018-09-20 | 15.3 | 2.7 | 0 | 2017-09-20 | 26.7 | 0 | 8.7 | 2016-09-20 | 25.6 | 0 | 7.6 | 1.52 | 3.12
2025-09-20 | 16.9 | 1.1 | 0 | 2024-09-20 | 25 | 0 | 7 | 2023-09-20 | 18 | 0 | 0 | 2022-09-20 | 14.6 | 3.4 | 0 | 2021-09-20 | 22.5 | 0 | 4.5 | 2020-09-20 | 14.3 | 3.7 | 0 | 2019-09-20 | 24.8 | 0 | 6.8 | 2018-09-20 | 16 | 2 | 0 | 2017-09-20 | 26.4 | 0 | 8.4 | 2016-09-20 | 26.4 | 0 | 8.4 | 1.02 | 3.51
2025-09-20 | 17.2 | 0.8 | 0 | 2024-09-20 | 25.7 | 0 | 7.7 | 2023-09-20 | 18.4 | 0 | 0.4 | 2022-09-20 | 14.9 | 3.1 | 0 | 2021-09-20 | 23.6 | 0 | 5.6 | 2020-09-20 | 14.8 | 3.2 | 0 | 2019-09-20 | 25.2 | 0 | 7.2 | 2018-09-20 | 16.3 | 1.7 | 0 | 2017-09-20 | 25.9 | 0 | 7.9 | 2016-09-20 | 26.6 | 0 | 8.6 | 0.88 | 3.74
2025-09-20 | 18.1 | 0 | 0.1 | 2024-09-20 | 26.1 | 0 | 8.1 | 2023-09-20 | 17.9 | 0.1 | 0 | 2022-09-20 | 14.6 | 3.4 | 0 | 2021-09-20 | 24 | 0 | 6 | 2020-09-20 | 14.6 | 3.4 | 0 | 2019-09-20 | 26.1 | 0 | 8.1 | 2018-09-20 | 16.3 | 1.7 | 0 | 2017-09-20 | 26.3 | 0 | 8.3 | 2016-09-20 | 26.6 | 0 | 8.6 | 0.86 | 3.92
2025-09-20 | 17.6 | 0.4 | 0 | 2024-09-20 | 25.7 | 0 | 7.7 | 2023-09-20 | 17.3 | 0.7 | 0 | 2022-09-20 | 15 | 3 | 0 | 2021-09-20 | 22.9 | 0 | 4.9 | 2020-09-20 | 14.3 | 3.7 | 0 | 2019-09-20 | 25.9 | 0 | 7.9 | 2018-09-20 | 16 | 2 | 0 | 2017-09-20 | 26.2 | 0 | 8.2 | 2016-09-20 | 25.6 | 0 | 7.6 | 0.98 | 3.63
2025-09-20 | 17.1 | 0.9 | 0 | 2024-09-20 | 24.5 | 0 | 6.5 | 2023-09-20 | 17.3 | 0.7 | 0 | 2022-09-20 | 14.3 | 3.7 | 0 | 2021-09-20 | 21.1 | 0 | 3.1 | 2020-09-20 | 13.5 | 4.5 | 0 | 2019-09-20 | 24.6 | 0 | 6.6 | 2018-09-20 | 15.3 | 2.7 | 0 | 2017-09-20 | 24.9 | 0 | 6.9 | 2016-09-20 | 24.3 | 0 | 6.3 | 1.25 | 2.94
2025-09-20 | 14.6 | 3.4 | 0 | 2024-09-20 | 22.3 | 0 | 4.3 | 2023-09-20 | 15 | 3 | 0 | 2022-09-20 | 14 | 4 | 0 | 2021-09-20 | 16.7 | 1.3 | 0 | 2020-09-20 | 11.9 | 6.1 | 0 | 2019-09-20 | 22.9 | 0 | 4.9 | 2018-09-20 | 14.5 | 3.5 | 0 | 2017-09-20 | 23.5 | 0 | 5.5 | 2016-09-20 | 20.3 | 0 | 2.3 | 2.13 | 1.7
2025-09-20 | 10.9 | 7.1 | 0 | 2024-09-20 | 20.9 | 0 | 2.9 | 2023-09-20 | 13 | 5 | 0 | 2022-09-20 | 13.6 | 4.4 | 0 | 2021-09-20 | 17.2 | 0.8 | 0 | 2020-09-20 | 8.4 | 9.6 | 0 | 2019-09-20 | 19.7 | 0 | 1.7 | 2018-09-20 | 14 | 4 | 0 | 2017-09-20 | 23.3 | 0 | 5.3 | 2016-09-20 | 18.9 | 0 | 0.9 | 3.09 | 1.08
2025-09-20 | 8.8 | 9.2 | 0 | 2024-09-20 | 20.2 | 0 | 2.2 | 2023-09-20 | 11.6 | 6.4 | 0 | 2022-09-20 | 13.4 | 4.6 | 0 | 2021-09-20 | 15.6 | 2.4 | 0 | 2020-09-20 | 5.6 | 12.4 | 0 | 2019-09-20 | 18.4 | 0 | 0.4 | 2018-09-20 | 13.6 | 4.4 | 0 | 2017-09-20 | 21.6 | 0 | 3.6 | 2016-09-20 | 17.9 | 0.1 | 0 | 3.95 | 0.62
2025-09-20 | 7.8 | 10.2 | 0 | 2024-09-20 | 19.4 | 0 | 1.4 | 2023-09-20 | 11.1 | 6.9 | 0 | 2022-09-20 | 13.2 | 4.8 | 0 | 2021-09-20 | 15.7 | 2.3 | 0 | 2020-09-20 | 7.9 | 10.1 | 0 | 2019-09-20 | 17.9 | 0.1 | 0 | 2018-09-20 | 13.3 | 4.7 | 0 | 2017-09-20 | 21 | 0 | 3 | 2016-09-20 | 16.9 | 1.1 | 0 | 4.02 | 0.44
2025-09-20 | 7.5 | 10.5 | 0 | 2024-09-20 | 18.5 | 0 | 0.5 | 2023-09-20 | 9.5 | 8.5 | 0 | 2022-09-20 | 12.8 | 5.2 | 0 | 2021-09-20 | 16.1 | 1.9 | 0 | 2020-09-20 | 6.3 | 11.7 | 0 | 2019-09-20 | 17.5 | 0.5 | 0 | 2018-09-20 | 13.3 | 4.7 | 0 | 2017-09-20 | 19.1 | 0 | 1.1 | 2016-09-20 | 16.3 | 1.7 | 0 | 4.47 | 0.16
2025-09-20 | 7.1 | 10.9 | 0 | 2024-09-20 | 17.6 | 0.4 | 0 | 2023-09-20 | 10 | 8 | 0 | 2022-09-20 | 12.8 | 5.2 | 0 | 2021-09-20 | 16.2 | 1.8 | 0 | 2020-09-20 | 4.8 | 13.2 | 0 | 2019-09-20 | 15.9 | 2.1 | 0 | 2018-09-20 | 13.1 | 4.9 | 0 | 2017-09-20 | 18.3 | 0 | 0.3 | 2016-09-20 | 14.4 | 3.6 | 0 | 5.01 | 0.03
2025-09-21 | 5.1 | 12.9 | 0 | 2024-09-21 | 16.8 | 1.2 | 0 | 2023-09-21 | 9.3 | 8.7 | 0 | 2022-09-21 | 12.7 | 5.3 | 0 | 2021-09-21 | 16.1 | 1.9 | 0 | 2020-09-21 | 5 | 13 | 0 | 2019-09-21 | 15.5 | 2.5 | 0 | 2018-09-21 | 13 | 5 | 0 | 2017-09-21 | 18.4 | 0 | 0.4 | 2016-09-21 | 13.1 | 4.9 | 0 | 5.54 | 0.04
2025-09-21 | 3.8 | 14.2 | 0 | 2024-09-21 | 16.4 | 1.6 | 0 | 2023-09-21 | 8.6 | 9.4 | 0 | 2022-09-21 | 12.2 | 5.8 | 0 | 2021-09-21 | 16 | 2 | 0 | 2020-09-21 | 2.6 | 15.4 | 0 | 2019-09-21 | 14.7 | 3.3 | 0 | 2018-09-21 | 13.1 | 4.9 | 0 | 2017-09-21 | 17.6 | 0.4 | 0 | 2016-09-21 | 12 | 6 | 0 | 6.3 | 0
2025-09-21 | 3.3 | 14.7 | 0 | 2024-09-21 | 15.8 | 2.2 | 0 | 2023-09-21 | 6.5 | 11.5 | 0 | 2022-09-21 | 12 | 6 | 0 | 2021-09-21 | 15.2 | 2.8 | 0 | 2020-09-21 | 2.3 | 15.7 | 0 | 2019-09-21 | 14.3 | 3.7 | 0 | 2018-09-21 | 12.9 | 5.1 | 0 | 2017-09-21 | 16.9 | 1.1 | 0 | 2016-09-21 | 12.2 | 5.8 | 0 | 6.86 | 0
2025-09-21 | 2.2 | 15.8 | 0 | 2024-09-21 | 15.4 | 2.6 | 0 | 2023-09-21 | 7.8 | 10.2 | 0 | 2022-09-21 | 11.4 | 6.6 | 0 | 2021-09-21 | 14.9 | 3.1 | 0 | 2020-09-21 | 0.8 | 17.2 | 0 | 2019-09-21 | 13 | 5 | 0 | 2018-09-21 | 13.3 | 4.7 | 0 | 2017-09-21 | 16.7 | 1.3 | 0 | 2016-09-21 | 11.3 | 6.7 | 0 | 7.32 | 0
2025-09-21 | 2.6 | 15.4 | 0 | 2024-09-21 | 14.9 | 3.1 | 0 | 2023-09-21 | 7.8 | 10.2 | 0 | 2022-09-21 | 11.7 | 6.3 | 0 | 2021-09-21 | 14 | 4 | 0 | 2020-09-21 | 1.8 | 16.2 | 0 | 2019-09-21 | 12.7 | 5.3 | 0 | 2018-09-21 | 12.9 | 5.1 | 0 | 2017-09-21 | 15.8 | 2.2 | 0 | 2016-09-21 | 11.3 | 6.7 | 0 | 7.45 | 0
2025-09-21 | 3.2 | 14.8 | 0 | 2024-09-21 | 14.7 | 3.3 | 0 | 2023-09-21 | 6.7 | 11.3 | 0 | 2022-09-21 | 11.6 | 6.4 | 0 | 2021-09-21 | 13.3 | 4.7 | 0 | 2020-09-21 | 1.2 | 16.8 | 0 | 2019-09-21 | 12.7 | 5.3 | 0 | 2018-09-21 | 13.3 | 4.7 | 0 | 2017-09-21 | 15.9 | 2.1 | 0 | 2016-09-21 | 10.9 | 7.1 | 0 | 7.65 | 0
2025-09-21 | 3.2 | 14.8 | 0 | 2024-09-21 | 14.2 | 3.8 | 0 | 2023-09-21 | 6.5 | 11.5 | 0 | 2022-09-21 | 11.6 | 6.4 | 0 | 2021-09-21 | 14.1 | 3.9 | 0 | 2020-09-21 | 0.2 | 17.8 | 0 | 2019-09-21 | 12.4 | 5.6 | 0 | 2018-09-21 | 14.7 | 3.3 | 0 | 2017-09-21 | 14.6 | 3.4 | 0 | 2016-09-21 | 11.1 | 6.9 | 0 | 7.74 | 0
2025-09-21 | 5.7 | 12.3 | 0 | 2024-09-21 | 15 | 3 | 0 | 2023-09-21 | 9.2 | 8.8 | 0 | 2022-09-21 | 12.2 | 5.8 | 0 | 2021-09-21 | 16.5 | 1.5 | 0 | 2020-09-21 | 1.8 | 16.2 | 0 | 2019-09-21 | 14.7 | 3.3 | 0 | 2018-09-21 | 15.8 | 2.2 | 0 | 2017-09-21 | 17 | 1 | 0 | 2016-09-21 | 12.4 | 5.6 | 0 | 5.97 | 0
2025-09-21 | 8.5 | 9.5 | 0 | 2024-09-21 | 15.5 | 2.5 | 0 | 2023-09-21 | 11.8 | 6.2 | 0 | 2022-09-21 | 13.9 | 4.1 | 0 | 2021-09-21 | 17.9 | 0.1 | 0 | 2020-09-21 | 6.4 | 11.6 | 0 | 2019-09-21 | 17.6 | 0.4 | 0 | 2018-09-21 | 18.4 | 0 | 0.4 | 2017-09-21 | 18.9 | 0 | 0.9 | 2016-09-21 | 16.2 | 1.8 | 0 | 3.62 | 0.13
2025-09-21 | 11.8 | 6.2 | 0 | 2024-09-21 | 18.2 | 0 | 0.2 | 2023-09-21 | 15.1 | 2.9 | 0 | 2022-09-21 | 15 | 3 | 0 | 2021-09-21 | 18.9 | 0 | 0.9 | 2020-09-21 | 9.7 | 8.3 | 0 | 2019-09-21 | 19.1 | 0 | 1.1 | 2018-09-21 | 19.1 | 0 | 1.1 | 2017-09-21 | 20.1 | 0 | 2.1 | 2016-09-21 | 19.4 | 0 | 1.4 | 2.04 | 0.68
2025-09-21 | 15 | 3 | 0 | 2024-09-21 | 20.7 | 0 | 2.7 | 2023-09-21 | 17.5 | 0.5 | 0 | 2022-09-21 | 15.5 | 2.5 | 0 | 2021-09-21 | 20.8 | 0 | 2.8 | 2020-09-21 | 12.7 | 5.3 | 0 | 2019-09-21 | 22.3 | 0 | 4.3 | 2018-09-21 | 20.1 | 0 | 2.1 | 2017-09-21 | 21.2 | 0 | 3.2 | 2016-09-21 | 21.6 | 0 | 3.6 | 1.13 | 1.87
2025-09-21 | 17.8 | 0.2 | 0 | 2024-09-21 | 21.3 | 0 | 3.3 | 2023-09-21 | 19.1 | 0 | 1.1 | 2022-09-21 | 17.1 | 0.9 | 0 | 2021-09-21 | 21.6 | 0 | 3.6 | 2020-09-21 | 14.2 | 3.8 | 0 | 2019-09-21 | 24.2 | 0 | 6.2 | 2018-09-21 | 23.4 | 0 | 5.4 | 2017-09-21 | 22.9 | 0 | 4.9 | 2016-09-21 | 23.5 | 0 | 5.5 | 0.49 | 3
2025-09-21 | 19.8 | 0 | 1.8 | 2024-09-21 | 23 | 0 | 5 | 2023-09-21 | 19.5 | 0 | 1.5 | 2022-09-21 | 19.6 | 0 | 1.6 | 2021-09-21 | 23.1 | 0 | 5.1 | 2020-09-21 | 15.4 | 2.6 | 0 | 2019-09-21 | 25.3 | 0 | 7.3 | 2018-09-21 | 24.9 | 0 | 6.9 | 2017-09-21 | 24.4 | 0 | 6.4 | 2016-09-21 | 25.4 | 0 | 7.4 | 0.26 | 4.3
2025-09-21 | 22.1 | 0 | 4.1 | 2024-09-21 | 24.2 | 0 | 6.2 | 2023-09-21 | 20.9 | 0 | 2.9 | 2022-09-21 | 20.8 | 0 | 2.8 | 2021-09-21 | 21.5 | 0 | 3.5 | 2020-09-21 | 16.2 | 1.8 | 0 | 2019-09-21 | 26.1 | 0 | 8.1 | 2018-09-21 | 25.9 | 0 | 7.9 | 2017-09-21 | 25.4 | 0 | 7.4 | 2016-09-21 | 25.8 | 0 | 7.8 | 0.18 | 5.07
2025-09-21 | 23.5 | 0 | 5.5 | 2024-09-21 | 24.1 | 0 | 6.1 | 2023-09-21 | 20.6 | 0 | 2.6 | 2022-09-21 | 21.7 | 0 | 3.7 | 2021-09-21 | 19.9 | 0 | 1.9 | 2020-09-21 | 17.6 | 0.4 | 0 | 2019-09-21 | 27.3 | 0 | 9.3 | 2018-09-21 | 27.3 | 0 | 9.3 | 2017-09-21 | 25.6 | 0 | 7.6 | 2016-09-21 | 26.8 | 0 | 8.8 | 0.04 | 5.48
2025-09-21 | 24 | 0 | 6 | 2024-09-21 | 24.3 | 0 | 6.3 | 2023-09-21 | 21 | 0 | 3 | 2022-09-21 | 19.9 | 0 | 1.9 | 2021-09-21 | 20.5 | 0 | 2.5 | 2020-09-21 | 17.2 | 0.8 | 0 | 2019-09-21 | 27 | 0 | 9 | 2018-09-21 | 28.1 | 0 | 10.1 | 2017-09-21 | 25.7 | 0 | 7.7 | 2016-09-21 | 26.4 | 0 | 8.4 | 0.08 | 5.49
2025-09-21 | 24.6 | 0 | 6.6 | 2024-09-21 | 23.7 | 0 | 5.7 | 2023-09-21 | 20.8 | 0 | 2.8 | 2022-09-21 | 19.6 | 0 | 1.6 | 2021-09-21 | 21.2 | 0 | 3.2 | 2020-09-21 | 17.1 | 0.9 | 0 | 2019-09-21 | 27.3 | 0 | 9.3 | 2018-09-21 | 27.2 | 0 | 9.2 | 2017-09-21 | 25.5 | 0 | 7.5 | 2016-09-21 | 25.6 | 0 | 7.6 | 0.09 | 5.35
2025-09-21 | 24 | 0 | 6 | 2024-09-21 | 22.9 | 0 | 4.9 | 2023-09-21 | 20.1 | 0 | 2.1 | 2022-09-21 | 21 | 0 | 3 | 2021-09-21 | 20.4 | 0 | 2.4 | 2020-09-21 | 15.9 | 2.1 | 0 | 2019-09-21 | 25.8 | 0 | 7.8 | 2018-09-21 | 24.7 | 0 | 6.7 | 2017-09-21 | 24.4 | 0 | 6.4 | 2016-09-21 | 23.4 | 0 | 5.4 | 0.21 | 4.47
2025-09-21 | 19.8 | 0 | 1.8 | 2024-09-21 | 20.4 | 0 | 2.4 | 2023-09-21 | 17.4 | 0.6 | 0 | 2022-09-21 | 19.3 | 0 | 1.3 | 2021-09-21 | 19.1 | 0 | 1.1 | 2020-09-21 | 12.1 | 5.9 | 0 | 2019-09-21 | 23.6 | 0 | 5.6 | 2018-09-21 | 22.4 | 0 | 4.4 | 2017-09-21 | 19.4 | 0 | 1.4 | 2016-09-21 | 21.9 | 0 | 3.9 | 0.65 | 2.19
2025-09-21 | 18.5 | 0 | 0.5 | 2024-09-21 | 19.5 | 0 | 1.5 | 2023-09-21 | 14.2 | 3.8 | 0 | 2022-09-21 | 18.9 | 0 | 0.9 | 2021-09-21 | 18.5 | 0 | 0.5 | 2020-09-21 | 9.3 | 8.7 | 0 | 2019-09-21 | 21.2 | 0 | 3.2 | 2018-09-21 | 21.9 | 0 | 3.9 | 2017-09-21 | 21 | 0 | 3 | 2016-09-21 | 20 | 0 | 2 | 1.25 | 1.55
2025-09-21 | 18 | 0 | 0 | 2024-09-21 | 18.2 | 0 | 0.2 | 2023-09-21 | 12.9 | 5.1 | 0 | 2022-09-21 | 19.4 | 0 | 1.4 | 2021-09-21 | 18.4 | 0 | 0.4 | 2020-09-21 | 8.2 | 9.8 | 0 | 2019-09-21 | 20.4 | 0 | 2.4 | 2018-09-21 | 21 | 0 | 3 | 2017-09-21 | 18.1 | 0 | 0.1 | 2016-09-21 | 19.3 | 0 | 1.3 | 1.49 | 0.88
2025-09-21 | 14.9 | 3.1 | 0 | 2024-09-21 | 16.7 | 1.3 | 0 | 2023-09-21 | 13.2 | 4.8 | 0 | 2022-09-21 | 20 | 0 | 2 | 2021-09-21 | 17.8 | 0.2 | 0 | 2020-09-21 | 7.9 | 10.1 | 0 | 2019-09-21 | 19.7 | 0 | 1.7 | 2018-09-21 | 20.8 | 0 | 2.8 | 2017-09-21 | 17.6 | 0.4 | 0 | 2016-09-21 | 19.4 | 0 | 1.4 | 1.99 | 0.79
2025-09-21 | 14.4 | 3.6 | 0 | 2024-09-21 | 15.8 | 2.2 | 0 | 2023-09-21 | 10.5 | 7.5 | 0 | 2022-09-21 | 19.7 | 0 | 1.7 | 2021-09-21 | 18 | 0 | 0 | 2020-09-21 | 8 | 10 | 0 | 2019-09-21 | 19.3 | 0 | 1.3 | 2018-09-21 | 19.2 | 0 | 1.2 | 2017-09-21 | 17.8 | 0.2 | 0 | 2016-09-21 | 19.1 | 0 | 1.1 | 2.35 | 0.53
2025-09-21 | 15.4 | 2.6 | 0 | 2024-09-21 | 14.7 | 3.3 | 0 | 2023-09-21 | 9.7 | 8.3 | 0 | 2022-09-21 | 19.6 | 0 | 1.6 | 2021-09-21 | 18.5 | 0 | 0.5 | 2020-09-21 | 7.1 | 10.9 | 0 | 2019-09-21 | 18.4 | 0 | 0.4 | 2018-09-21 | 17.8 | 0.2 | 0 | 2017-09-21 | 16.2 | 1.8 | 0 | 2016-09-21 | 18.1 | 0 | 0.1 | 2.71 | 0.26
2025-09-22 | 15.2 | 2.8 | 0 | 2024-09-22 | 14.6 | 3.4 | 0 | 2023-09-22 | 10.5 | 7.5 | 0 | 2022-09-22 | 19 | 0 | 1 | 2021-09-22 | 18.4 | 0 | 0.4 | 2020-09-22 | 6 | 12 | 0 | 2019-09-22 | 17.6 | 0.4 | 0 | 2018-09-22 | 16.6 | 1.4 | 0 | 2017-09-22 | 15.2 | 2.8 | 0 | 2016-09-22 | 16.6 | 1.4 | 0 | 3.17 | 0.14
2025-09-22 | 14.9 | 3.1 | 0 | 2024-09-22 | 14.1 | 3.9 | 0 | 2023-09-22 | 8.2 | 9.8 | 0 | 2022-09-22 | 17.5 | 0.5 | 0 | 2021-09-22 | 18.3 | 0 | 0.3 | 2020-09-22 | 3.1 | 14.9 | 0 | 2019-09-22 | 17.1 | 0.9 | 0 | 2018-09-22 | 15.1 | 2.9 | 0 | 2017-09-22 | 13.9 | 4.1 | 0 | 2016-09-22 | 16.5 | 1.5 | 0 | 4.16 | 0.03
2025-09-22 | 14.8 | 3.2 | 0 | 2024-09-22 | 13.2 | 4.8 | 0 | 2023-09-22 | 8.5 | 9.5 | 0 | 2022-09-22 | 15.9 | 2.1 | 0 | 2021-09-22 | 17.3 | 0.7 | 0 | 2020-09-22 | 4.2 | 13.8 | 0 | 2019-09-22 | 16.1 | 1.9 | 0 | 2018-09-22 | 12.3 | 5.7 | 0 | 2017-09-22 | 14.1 | 3.9 | 0 | 2016-09-22 | 16.6 | 1.4 | 0 | 4.7 | 0
2025-09-22 | 14.8 | 3.2 | 0 | 2024-09-22 | 11.8 | 6.2 | 0 | 2023-09-22 | 7.7 | 10.3 | 0 | 2022-09-22 | 14.5 | 3.5 | 0 | 2021-09-22 | 17.4 | 0.6 | 0 | 2020-09-22 | 4.4 | 13.6 | 0 | 2019-09-22 | 16 | 2 | 0 | 2018-09-22 | 11.1 | 6.9 | 0 | 2017-09-22 | 14.4 | 3.6 | 0 | 2016-09-22 | 16 | 2 | 0 | 5.19 | 0
2025-09-22 | 14 | 4 | 0 | 2024-09-22 | 12.2 | 5.8 | 0 | 2023-09-22 | 7.4 | 10.6 | 0 | 2022-09-22 | 13.6 | 4.4 | 0 | 2021-09-22 | 16.9 | 1.1 | 0 | 2020-09-22 | 3.1 | 14.9 | 0 | 2019-09-22 | 15.6 | 2.4 | 0 | 2018-09-22 | 10.1 | 7.9 | 0 | 2017-09-22 | 13.6 | 4.4 | 0 | 2016-09-22 | 16.2 | 1.8 | 0 | 5.73 | 0
2025-09-22 | 13.6 | 4.4 | 0 | 2024-09-22 | 12 | 6 | 0 | 2023-09-22 | 5.7 | 12.3 | 0 | 2022-09-22 | 12.6 | 5.4 | 0 | 2021-09-22 | 16.8 | 1.2 | 0 | 2020-09-22 | 2.8 | 15.2 | 0 | 2019-09-22 | 15.8 | 2.2 | 0 | 2018-09-22 | 8.6 | 9.4 | 0 | 2017-09-22 | 12.8 | 5.2 | 0 | 2016-09-22 | 15.5 | 2.5 | 0 | 6.38 | 0
2025-09-22 | 13.6 | 4.4 | 0 | 2024-09-22 | 12.3 | 5.7 | 0 | 2023-09-22 | 7.5 | 10.5 | 0 | 2022-09-22 | 11.3 | 6.7 | 0 | 2021-09-22 | 17 | 1 | 0 | 2020-09-22 | 2.8 | 15.2 | 0 | 2019-09-22 | 15.8 | 2.2 | 0 | 2018-09-22 | 8.3 | 9.7 | 0 | 2017-09-22 | 14.2 | 3.8 | 0 | 2016-09-22 | 15 | 3 | 0 | 6.22 | 0
2025-09-22 | 15 | 3 | 0 | 2024-09-22 | 13.4 | 4.6 | 0 | 2023-09-22 | 8.9 | 9.1 | 0 | 2022-09-22 | 12.8 | 5.2 | 0 | 2021-09-22 | 17.1 | 0.9 | 0 | 2020-09-22 | 4.8 | 13.2 | 0 | 2019-09-22 | 17.3 | 0.7 | 0 | 2018-09-22 | 8.7 | 9.3 | 0 | 2017-09-22 | 16.4 | 1.6 | 0 | 2016-09-22 | 16.7 | 1.3 | 0 | 4.89 | 0
2025-09-22 | 15.7 | 2.3 | 0 | 2024-09-22 | 15 | 3 | 0 | 2023-09-22 | 12.1 | 5.9 | 0 | 2022-09-22 | 14 | 4 | 0 | 2021-09-22 | 17.5 | 0.5 | 0 | 2020-09-22 | 8.3 | 9.7 | 0 | 2019-09-22 | 19.4 | 0 | 1.4 | 2018-09-22 | 9.9 | 8.1 | 0 | 2017-09-22 | 18.6 | 0 | 0.6 | 2016-09-22 | 18.5 | 0 | 0.5 | 3.35 | 0.25
2025-09-22 | 17.5 | 0.5 | 0 | 2024-09-22 | 17.1 | 0.9 | 0 | 2023-09-22 | 15.4 | 2.6 | 0 | 2022-09-22 | 14.8 | 3.2 | 0 | 2021-09-22 | 18.5 | 0 | 0.5 | 2020-09-22 | 11.3 | 6.7 | 0 | 2019-09-22 | 20.3 | 0 | 2.3 | 2018-09-22 | 11.2 | 6.8 | 0 | 2017-09-22 | 20.3 | 0 | 2.3 | 2016-09-22 | 19.9 | 0 | 1.9 | 2.07 | 0.7
2025-09-22 | 18.9 | 0 | 0.9 | 2024-09-22 | 18.4 | 0 | 0.4 | 2023-09-22 | 17.7 | 0.3 | 0 | 2022-09-22 | 14.3 | 3.7 | 0 | 2021-09-22 | 19 | 0 | 1 | 2020-09-22 | 13.8 | 4.2 | 0 | 2019-09-22 | 22.2 | 0 | 4.2 | 2018-09-22 | 11.3 | 6.7 | 0 | 2017-09-22 | 22 | 0 | 4 | 2016-09-22 | 21.5 | 0 | 3.5 | 1.49 | 1.4
2025-09-22 | 19.2 | 0 | 1.2 | 2024-09-22 | 20.8 | 0 | 2.8 | 2023-09-22 | 19.6 | 0 | 1.6 | 2022-09-22 | 14.9 | 3.1 | 0 | 2021-09-22 | 18.9 | 0 | 0.9 | 2020-09-22 | 15.7 | 2.3 | 0 | 2019-09-22 | 23.3 | 0 | 5.3 | 2018-09-22 | 12.1 | 5.9 | 0 | 2017-09-22 | 23.6 | 0 | 5.6 | 2016-09-22 | 21.6 | 0 | 3.6 | 1.13 | 2.1
2025-09-22 | 19.9 | 0 | 1.9 | 2024-09-22 | 21.8 | 0 | 3.8 | 2023-09-22 | 21.1 | 0 | 3.1 | 2022-09-22 | 13.4 | 4.6 | 0 | 2021-09-22 | 19.3 | 0 | 1.3 | 2020-09-22 | 17.2 | 0.8 | 0 | 2019-09-22 | 24.6 | 0 | 6.6 | 2018-09-22 | 13.2 | 4.8 | 0 | 2017-09-22 | 25 | 0 | 7 | 2016-09-22 | 23.4 | 0 | 5.4 | 1.02 | 2.91
2025-09-22 | 18.1 | 0 | 0.1 | 2024-09-22 | 22.2 | 0 | 4.2 | 2023-09-22 | 21.8 | 0 | 3.8 | 2022-09-22 | 15.1 | 2.9 | 0 | 2021-09-22 | 19.3 | 0 | 1.3 | 2020-09-22 | 17.9 | 0.1 | 0 | 2019-09-22 | 24 | 0 | 6 | 2018-09-22 | 14.2 | 3.8 | 0 | 2017-09-22 | 25.8 | 0 | 7.8 | 2016-09-22 | 24.6 | 0 | 6.6 | 0.68 | 2.98
2025-09-22 | 17.6 | 0.4 | 0 | 2024-09-22 | 23.4 | 0 | 5.4 | 2023-09-22 | 22.6 | 0 | 4.6 | 2022-09-22 | 14.7 | 3.3 | 0 | 2021-09-22 | 19.4 | 0 | 1.4 | 2020-09-22 | 18.8 | 0 | 0.8 | 2019-09-22 | 24.6 | 0 | 6.6 | 2018-09-22 | 14.2 | 3.8 | 0 | 2017-09-22 | 26.6 | 0 | 8.6 | 2016-09-22 | 24.4 | 0 | 6.4 | 0.75 | 3.38
2025-09-22 | 17.4 | 0.6 | 0 | 2024-09-22 | 22.6 | 0 | 4.6 | 2023-09-22 | 22.6 | 0 | 4.6 | 2022-09-22 | 13.9 | 4.1 | 0 | 2021-09-22 | 19.7 | 0 | 1.7 | 2020-09-22 | 18.9 | 0 | 0.9 | 2019-09-22 | 26.5 | 0 | 8.5 | 2018-09-22 | 14.2 | 3.8 | 0 | 2017-09-22 | 26.9 | 0 | 8.9 | 2016-09-22 | 21.8 | 0 | 3.8 | 0.85 | 3.3
2025-09-22 | 18 | 0 | 0 | 2024-09-22 | 22.6 | 0 | 4.6 | 2023-09-22 | 22.2 | 0 | 4.2 | 2022-09-22 | 13 | 5 | 0 | 2021-09-22 | 20 | 0 | 2 | 2020-09-22 | 18.9 | 0 | 0.9 | 2019-09-22 | 27.4 | 0 | 9.4 | 2018-09-22 | 14.2 | 3.8 | 0 | 2017-09-22 | 26.4 | 0 | 8.4 | 2016-09-22 | 20.1 | 0 | 2.1 | 0.88 | 3.16
2025-09-22 | 18.1 | 0 | 0.1 | 2024-09-22 | 21 | 0 | 3 | 2023-09-22 | 20.9 | 0 | 2.9 | 2022-09-22 | 11.1 | 6.9 | 0 | 2021-09-22 | 20 | 0 | 2 | 2020-09-22 | 17.6 | 0.4 | 0 | 2019-09-22 | 26.8 | 0 | 8.8 | 2018-09-22 | 13.7 | 4.3 | 0 | 2017-09-22 | 24.9 | 0 | 6.9 | 2016-09-22 | 18.8 | 0 | 0.8 | 1.16 | 2.45
2025-09-22 | 17.7 | 0.3 | 0 | 2024-09-22 | 19.6 | 0 | 1.6 | 2023-09-22 | 16.2 | 1.8 | 0 | 2022-09-22 | 10.5 | 7.5 | 0 | 2021-09-22 | 19.7 | 0 | 1.7 | 2020-09-22 | 15.6 | 2.4 | 0 | 2019-09-22 | 25.2 | 0 | 7.2 | 2018-09-22 | 11.6 | 6.4 | 0 | 2017-09-22 | 22 | 0 | 4 | 2016-09-22 | 17.9 | 0.1 | 0 | 1.85 | 1.45
2025-09-22 | 16.5 | 1.5 | 0 | 2024-09-22 | 17.4 | 0.6 | 0 | 2023-09-22 | 15.4 | 2.6 | 0 | 2022-09-22 | 9.9 | 8.1 | 0 | 2021-09-22 | 19.7 | 0 | 1.7 | 2020-09-22 | 14 | 4 | 0 | 2019-09-22 | 24.5 | 0 | 6.5 | 2018-09-22 | 6.7 | 11.3 | 0 | 2017-09-22 | 20.3 | 0 | 2.3 | 2016-09-22 | 14.8 | 3.2 | 0 | 3.13 | 1.05
2025-09-22 | 16.9 | 1.1 | 0 | 2024-09-22 | 16.4 | 1.6 | 0 | 2023-09-22 | 15.7 | 2.3 | 0 | 2022-09-22 | 9.1 | 8.9 | 0 | 2021-09-22 | 19.9 | 0 | 1.9 | 2020-09-22 | 12.8 | 5.2 | 0 | 2019-09-22 | 24.4 | 0 | 6.4 | 2018-09-22 | 6.9 | 11.1 | 0 | 2017-09-22 | 18.9 | 0 | 0.9 | 2016-09-22 | 13.8 | 4.2 | 0 | 3.44 | 0.92
2025-09-22 | 16.4 | 1.6 | 0 | 2024-09-22 | 16.5 | 1.5 | 0 | 2023-09-22 | 13 | 5 | 0 | 2022-09-22 | 8.7 | 9.3 | 0 | 2021-09-22 | 15.8 | 2.2 | 0 | 2020-09-22 | 13.3 | 4.7 | 0 | 2019-09-22 | 24.7 | 0 | 6.7 | 2018-09-22 | 7.1 | 10.9 | 0 | 2017-09-22 | 17.6 | 0.4 | 0 | 2016-09-22 | 13.2 | 4.8 | 0 | 4.04 | 0.67
2025-09-22 | 16.1 | 1.9 | 0 | 2024-09-22 | 16.1 | 1.9 | 0 | 2023-09-22 | 12.2 | 5.8 | 0 | 2022-09-22 | 8.3 | 9.7 | 0 | 2021-09-22 | 15.1 | 2.9 | 0 | 2020-09-22 | 11.7 | 6.3 | 0 | 2019-09-22 | 24.8 | 0 | 6.8 | 2018-09-22 | 7.6 | 10.4 | 0 | 2017-09-22 | 18 | 0 | 0 | 2016-09-22 | 12.9 | 5.1 | 0 | 4.4 | 0.68
2025-09-22 | 16.1 | 1.9 | 0 | 2024-09-22 | 15.8 | 2.2 | 0 | 2023-09-22 | 13.1 | 4.9 | 0 | 2022-09-22 | 7.5 | 10.5 | 0 | 2021-09-22 | 15.4 | 2.6 | 0 | 2020-09-22 | 10.3 | 7.7 | 0 | 2019-09-22 | 25.3 | 0 | 7.3 | 2018-09-22 | 7.3 | 10.7 | 0 | 2017-09-22 | 17.7 | 0.3 | 0 | 2016-09-22 | 12.5 | 5.5 | 0 | 4.63 | 0.73
2025-09-23 | 16.2 | 1.8 | 0 | 2024-09-23 | 15.1 | 2.9 | 0 | 2023-09-23 | 11.9 | 6.1 | 0 | 2022-09-23 | 7.2 | 10.8 | 0 | 2021-09-23 | 16.2 | 1.8 | 0 | 2020-09-23 | 10.6 | 7.4 | 0 | 2019-09-23 | 24.9 | 0 | 6.9 | 2018-09-23 | 6.9 | 11.1 | 0 | 2017-09-23 | 17.2 | 0.8 | 0 | 2016-09-23 | 12.7 | 5.3 | 0 | 4.8 | 0.69
2025-09-23 | 16.3 | 1.7 | 0 | 2024-09-23 | 15.1 | 2.9 | 0 | 2023-09-23 | 10.2 | 7.8 | 0 | 2022-09-23 | 6.6 | 11.4 | 0 | 2021-09-23 | 17.7 | 0.3 | 0 | 2020-09-23 | 10.5 | 7.5 | 0 | 2019-09-23 | 22.9 | 0 | 4.9 | 2018-09-23 | 6.7 | 11.3 | 0 | 2017-09-23 | 16.7 | 1.3 | 0 | 2016-09-23 | 12.7 | 5.3 | 0 | 4.95 | 0.49
2025-09-23 | 16.2 | 1.8 | 0 | 2024-09-23 | 15.2 | 2.8 | 0 | 2023-09-23 | 10.9 | 7.1 | 0 | 2022-09-23 | 6.2 | 11.8 | 0 | 2021-09-23 | 17.3 | 0.7 | 0 | 2020-09-23 | 9.3 | 8.7 | 0 | 2019-09-23 | 21 | 0 | 3 | 2018-09-23 | 5.4 | 12.6 | 0 | 2017-09-23 | 16.2 | 1.8 | 0 | 2016-09-23 | 12.6 | 5.4 | 0 | 5.27 | 0.3
2025-09-23 | 16.2 | 1.8 | 0 | 2024-09-23 | 15.3 | 2.7 | 0 | 2023-09-23 | 10.7 | 7.3 | 0 | 2022-09-23 | 5.8 | 12.2 | 0 | 2021-09-23 | 18.7 | 0 | 0.7 | 2020-09-23 | 8.9 | 9.1 | 0 | 2019-09-23 | 21.1 | 0 | 3.1 | 2018-09-23 | 5.5 | 12.5 | 0 | 2017-09-23 | 16.3 | 1.7 | 0 | 2016-09-23 | 12.4 | 5.6 | 0 | 5.29 | 0.38
2025-09-23 | 16.1 | 1.9 | 0 | 2024-09-23 | 15.2 | 2.8 | 0 | 2023-09-23 | 9.8 | 8.2 | 0 | 2022-09-23 | 4.8 | 13.2 | 0 | 2021-09-23 | 19.1 | 0 | 1.1 | 2020-09-23 | 10 | 8 | 0 | 2019-09-23 | 20.8 | 0 | 2.8 | 2018-09-23 | 5.5 | 12.5 | 0 | 2017-09-23 | 15.5 | 2.5 | 0 | 2016-09-23 | 12.4 | 5.6 | 0 | 5.47 | 0.39
2025-09-23 | 16.1 | 1.9 | 0 | 2024-09-23 | 14.9 | 3.1 | 0 | 2023-09-23 | 9.2 | 8.8 | 0 | 2022-09-23 | 4.4 | 13.6 | 0 | 2021-09-23 | 19.3 | 0 | 1.3 | 2020-09-23 | 11.5 | 6.5 | 0 | 2019-09-23 | 18.7 | 0 | 0.7 | 2018-09-23 | 5.1 | 12.9 | 0 | 2017-09-23 | 15.6 | 2.4 | 0 | 2016-09-23 | 12 | 6 | 0 | 5.52 | 0.2
2025-09-23 | 16 | 2 | 0 | 2024-09-23 | 14.3 | 3.7 | 0 | 2023-09-23 | 9.4 | 8.6 | 0 | 2022-09-23 | 4.7 | 13.3 | 0 | 2021-09-23 | 19.3 | 0 | 1.3 | 2020-09-23 | 11.8 | 6.2 | 0 | 2019-09-23 | 18.7 | 0 | 0.7 | 2018-09-23 | 4.9 | 13.1 | 0 | 2017-09-23 | 15.5 | 2.5 | 0 | 2016-09-23 | 11.5 | 6.5 | 0 | 5.59 | 0.2
2025-09-23 | 16.3 | 1.7 | 0 | 2024-09-23 | 14.4 | 3.6 | 0 | 2023-09-23 | 10.5 | 7.5 | 0 | 2022-09-23 | 5.4 | 12.6 | 0 | 2021-09-23 | 19.2 | 0 | 1.2 | 2020-09-23 | 12.6 | 5.4 | 0 | 2019-09-23 | 18.5 | 0 | 0.5 | 2018-09-23 | 6.3 | 11.7 | 0 | 2017-09-23 | 16.4 | 1.6 | 0 | 2016-09-23 | 11.1 | 6.9 | 0 | 5.1 | 0.17
2025-09-23 | 16.5 | 1.5 | 0 | 2024-09-23 | 14.7 | 3.3 | 0 | 2023-09-23 | 12.4 | 5.6 | 0 | 2022-09-23 | 6 | 12 | 0 | 2021-09-23 | 19.8 | 0 | 1.8 | 2020-09-23 | 14 | 4 | 0 | 2019-09-23 | 18.7 | 0 | 0.7 | 2018-09-23 | 8.3 | 9.7 | 0 | 2017-09-23 | 19.6 | 0 | 1.6 | 2016-09-23 | 11.2 | 6.8 | 0 | 4.29 | 0.41
2025-09-23 | 16.9 | 1.1 | 0 | 2024-09-23 | 15.1 | 2.9 | 0 | 2023-09-23 | 13.9 | 4.1 | 0 | 2022-09-23 | 6.6 | 11.4 | 0 | 2021-09-23 | 20.6 | 0 | 2.6 | 2020-09-23 | 16.3 | 1.7 | 0 | 2019-09-23 | 20 | 0 | 2 | 2018-09-23 | 10.3 | 7.7 | 0 | 2017-09-23 | 23.1 | 0 | 5.1 | 2016-09-23 | 12.7 | 5.3 | 0 | 3.42 | 0.97
2025-09-23 | 17.5 | 0.5 | 0 | 2024-09-23 | 16.7 | 1.3 | 0 | 2023-09-23 | 15.7 | 2.3 | 0 | 2022-09-23 | 7.8 | 10.2 | 0 | 2021-09-23 | 21.7 | 0 | 3.7 | 2020-09-23 | 18.4 | 0 | 0.4 | 2019-09-23 | 20.9 | 0 | 2.9 | 2018-09-23 | 11.2 | 6.8 | 0 | 2017-09-23 | 25.2 | 0 | 7.2 | 2016-09-23 | 14.4 | 3.6 | 0 | 2.47 | 1.42
2025-09-23 | 18.6 | 0 | 0.6 | 2024-09-23 | 17 | 1 | 0 | 2023-09-23 | 18.2 | 0 | 0.2 | 2022-09-23 | 9.1 | 8.9 | 0 | 2021-09-23 | 22.7 | 0 | 4.7 | 2020-09-23 | 20.1 | 0 | 2.1 | 2019-09-23 | 22.1 | 0 | 4.1 | 2018-09-23 | 12.3 | 5.7 | 0 | 2017-09-23 | 27.4 | 0 | 9.4 | 2016-09-23 | 14.7 | 3.3 | 0 | 1.89 | 2.11
2025-09-23 | 20.2 | 0 | 2.2 | 2024-09-23 | 17.4 | 0.6 | 0 | 2023-09-23 | 20.4 | 0 | 2.4 | 2022-09-23 | 10.9 | 7.1 | 0 | 2021-09-23 | 20.8 | 0 | 2.8 | 2020-09-23 | 21.7 | 0 | 3.7 | 2019-09-23 | 22.4 | 0 | 4.4 | 2018-09-23 | 13.4 | 4.6 | 0 | 2017-09-23 | 28.2 | 0 | 10.2 | 2016-09-23 | 15.1 | 2.9 | 0 | 1.52 | 2.57
2025-09-23 | 21.1 | 0 | 3.1 | 2024-09-23 | 18.1 | 0 | 0.1 | 2023-09-23 | 21.2 | 0 | 3.2 | 2022-09-23 | 11.8 | 6.2 | 0 | 2021-09-23 | 20.8 | 0 | 2.8 | 2020-09-23 | 22.6 | 0 | 4.6 | 2019-09-23 | 23 | 0 | 5 | 2018-09-23 | 14.4 | 3.6 | 0 | 2017-09-23 | 28.9 | 0 | 10.9 | 2016-09-23 | 17 | 1 | 0 | 1.08 | 2.97
2025-09-23 | 21.6 | 0 | 3.6 | 2024-09-23 | 17.9 | 0.1 | 0 | 2023-09-23 | 21.6 | 0 | 3.6 | 2022-09-23 | 12.4 | 5.6 | 0 | 2021-09-23 | 21 | 0 | 3 | 2020-09-23 | 22.7 | 0 | 4.7 | 2019-09-23 | 23.6 | 0 | 5.6 | 2018-09-23 | 15.7 | 2.3 | 0 | 2017-09-23 | 28.8 | 0 | 10.8 | 2016-09-23 | 16.3 | 1.7 | 0 | 0.97 | 3.13
2025-09-23 | 21.8 | 0 | 3.8 | 2024-09-23 | 17.9 | 0.1 | 0 | 2023-09-23 | 21.2 | 0 | 3.2 | 2022-09-23 | 12.5 | 5.5 | 0 | 2021-09-23 | 20.9 | 0 | 2.9 | 2020-09-23 | 22.4 | 0 | 4.4 | 2019-09-23 | 23.9 | 0 | 5.9 | 2018-09-23 | 15.4 | 2.6 | 0 | 2017-09-23 | 28.6 | 0 | 10.6 | 2016-09-23 | 16.2 | 1.8 | 0 | 1 | 3.08
2025-09-23 | 21.9 | 0 | 3.9 | 2024-09-23 | 17.1 | 0.9 | 0 | 2023-09-23 | 20.5 | 0 | 2.5 | 2022-09-23 | 12.8 | 5.2 | 0 | 2021-09-23 | 21.1 | 0 | 3.1 | 2020-09-23 | 22.8 | 0 | 4.8 | 2019-09-23 | 22.4 | 0 | 4.4 | 2018-09-23 | 13.8 | 4.2 | 0 | 2017-09-23 | 28.4 | 0 | 10.4 | 2016-09-23 | 15.8 | 2.2 | 0 | 1.25 | 2.91
2025-09-23 | 20.9 | 0 | 2.9 | 2024-09-23 | 16.9 | 1.1 | 0 | 2023-09-23 | 19.6 | 0 | 1.6 | 2022-09-23 | 12.2 | 5.8 | 0 | 2021-09-23 | 21.1 | 0 | 3.1 | 2020-09-23 | 21.5 | 0 | 3.5 | 2019-09-23 | 21.3 | 0 | 3.3 | 2018-09-23 | 10.8 | 7.2 | 0 | 2017-09-23 | 27.7 | 0 | 9.7 | 2016-09-23 | 16.5 | 1.5 | 0 | 1.56 | 2.41
2025-09-23 | 19.5 | 0 | 1.5 | 2024-09-23 | 16.3 | 1.7 | 0 | 2023-09-23 | 17.8 | 0.2 | 0 | 2022-09-23 | 10.5 | 7.5 | 0 | 2021-09-23 | 20.5 | 0 | 2.5 | 2020-09-23 | 18.1 | 0 | 0.1 | 2019-09-23 | 19.2 | 0 | 1.2 | 2018-09-23 | 9.8 | 8.2 | 0 | 2017-09-23 | 25.5 | 0 | 7.5 | 2016-09-23 | 14 | 4 | 0 | 2.16 | 1.28
2025-09-23 | 18.4 | 0 | 0.4 | 2024-09-23 | 15.9 | 2.1 | 0 | 2023-09-23 | 15.3 | 2.7 | 0 | 2022-09-23 | 8.4 | 9.6 | 0 | 2021-09-23 | 20.5 | 0 | 2.5 | 2020-09-23 | 17.3 | 0.7 | 0 | 2019-09-23 | 17.7 | 0.3 | 0 | 2018-09-23 | 8.9 | 9.1 | 0 | 2017-09-23 | 24.6 | 0 | 6.6 | 2016-09-23 | 13.1 | 4.9 | 0 | 2.94 | 0.95
2025-09-23 | 17.7 | 0.3 | 0 | 2024-09-23 | 15.2 | 2.8 | 0 | 2023-09-23 | 15.6 | 2.4 | 0 | 2022-09-23 | 7.3 | 10.7 | 0 | 2021-09-23 | 20.2 | 0 | 2.2 | 2020-09-23 | 17.2 | 0.8 | 0 | 2019-09-23 | 17 | 1 | 0 | 2018-09-23 | 8.4 | 9.6 | 0 | 2017-09-23 | 21.2 | 0 | 3.2 | 2016-09-23 | 12.5 | 5.5 | 0 | 3.31 | 0.54
2025-09-23 | 17.5 | 0.5 | 0 | 2024-09-23 | 15 | 3 | 0 | 2023-09-23 | 14.9 | 3.1 | 0 | 2022-09-23 | 7.7 | 10.3 | 0 | 2021-09-23 | 16.9 | 1.1 | 0 | 2020-09-23 | 15 | 3 | 0 | 2019-09-23 | 17.2 | 0.8 | 0 | 2018-09-23 | 8.2 | 9.8 | 0 | 2017-09-23 | 21.9 | 0 | 3.9 | 2016-09-23 | 10 | 8 | 0 | 3.96 | 0.39
2025-09-23 | 16.5 | 1.5 | 0 | 2024-09-23 | 14.8 | 3.2 | 0 | 2023-09-23 | 13 | 5 | 0 | 2022-09-23 | 8.3 | 9.7 | 0 | 2021-09-23 | 16.4 | 1.6 | 0 | 2020-09-23 | 13.5 | 4.5 | 0 | 2019-09-23 | 15.5 | 2.5 | 0 | 2018-09-23 | 7.9 | 10.1 | 0 | 2017-09-23 | 20.8 | 0 | 2.8 | 2016-09-23 | 9.1 | 8.9 | 0 | 4.7 | 0.28
2025-09-23 | 16.7 | 1.3 | 0 | 2024-09-23 | 14.6 | 3.4 | 0 | 2023-09-23 | 12.9 | 5.1 | 0 | 2022-09-23 | 7 | 11 | 0 | 2021-09-23 | 16.4 | 1.6 | 0 | 2020-09-23 | 12.3 | 5.7 | 0 | 2019-09-23 | 14.5 | 3.5 | 0 | 2018-09-23 | 7.8 | 10.2 | 0 | 2017-09-23 | 20.4 | 0 | 2.4 | 2016-09-23 | 8.1 | 9.9 | 0 | 5.17 | 0.24
2025-09-24 | 16.8 | 1.2 | 0 | 2024-09-24 | 14 | 4 | 0 | 2023-09-24 | 11.8 | 6.2 | 0 | 2022-09-24 | 4.9 | 13.1 | 0 | 2021-09-24 | 16 | 2 | 0 | 2020-09-24 | 12.1 | 5.9 | 0 | 2019-09-24 | 13.6 | 4.4 | 0 | 2018-09-24 | 7.6 | 10.4 | 0 | 2017-09-24 | 19.8 | 0 | 1.8 | 2016-09-24 | 7.9 | 10.1 | 0 | 5.73 | 0.18
2025-09-24 | 16.1 | 1.9 | 0 | 2024-09-24 | 13.6 | 4.4 | 0 | 2023-09-24 | 11.8 | 6.2 | 0 | 2022-09-24 | 4.2 | 13.8 | 0 | 2021-09-24 | 15.5 | 2.5 | 0 | 2020-09-24 | 11.5 | 6.5 | 0 | 2019-09-24 | 13.8 | 4.2 | 0 | 2018-09-24 | 7.8 | 10.2 | 0 | 2017-09-24 | 19.2 | 0 | 1.2 | 2016-09-24 | 7.3 | 10.7 | 0 | 6.04 | 0.12
2025-09-24 | 16 | 2 | 0 | 2024-09-24 | 13.1 | 4.9 | 0 | 2023-09-24 | 11.4 | 6.6 | 0 | 2022-09-24 | 4.4 | 13.6 | 0 | 2021-09-24 | 15.2 | 2.8 | 0 | 2020-09-24 | 11.2 | 6.8 | 0 | 2019-09-24 | 13.8 | 4.2 | 0 | 2018-09-24 | 7.5 | 10.5 | 0 | 2017-09-24 | 18.7 | 0 | 0.7 | 2016-09-24 | 5.9 | 12.1 | 0 | 6.35 | 0.07
2025-09-24 | 15.7 | 2.3 | 0 | 2024-09-24 | 12.7 | 5.3 | 0 | 2023-09-24 | 11.2 | 6.8 | 0 | 2022-09-24 | 4 | 14 | 0 | 2021-09-24 | 15 | 3 | 0 | 2020-09-24 | 10.7 | 7.3 | 0 | 2019-09-24 | 13.4 | 4.6 | 0 | 2018-09-24 | 6.9 | 11.1 | 0 | 2017-09-24 | 19.1 | 0 | 1.1 | 2016-09-24 | 6.7 | 11.3 | 0 | 6.57 | 0.11
2025-09-24 | 15.7 | 2.3 | 0 | 2024-09-24 | 12.3 | 5.7 | 0 | 2023-09-24 | 10.3 | 7.7 | 0 | 2022-09-24 | 4.5 | 13.5 | 0 | 2021-09-24 | 14.6 | 3.4 | 0 | 2020-09-24 | 10.3 | 7.7 | 0 | 2019-09-24 | 13.2 | 4.8 | 0 | 2018-09-24 | 6.5 | 11.5 | 0 | 2017-09-24 | 19.2 | 0 | 1.2 | 2016-09-24 | 7.6 | 10.4 | 0 | 6.7 | 0.12
2025-09-24 | 15.6 | 2.4 | 0 | 2024-09-24 | 12.6 | 5.4 | 0 | 2023-09-24 | 10.1 | 7.9 | 0 | 2022-09-24 | 4.2 | 13.8 | 0 | 2021-09-24 | 12.7 | 5.3 | 0 | 2020-09-24 | 10.6 | 7.4 | 0 | 2019-09-24 | 12.8 | 5.2 | 0 | 2018-09-24 | 5.8 | 12.2 | 0 | 2017-09-24 | 19.8 | 0 | 1.8 | 2016-09-24 | 5.5 | 12.5 | 0 | 7.21 | 0.18
2025-09-24 | 15.8 | 2.2 | 0 | 2024-09-24 | 12.2 | 5.8 | 0 | 2023-09-24 | 11.1 | 6.9 | 0 | 2022-09-24 | 3.9 | 14.1 | 0 | 2021-09-24 | 12.4 | 5.6 | 0 | 2020-09-24 | 10.8 | 7.2 | 0 | 2019-09-24 | 12.6 | 5.4 | 0 | 2018-09-24 | 5.1 | 12.9 | 0 | 2017-09-24 | 19.5 | 0 | 1.5 | 2016-09-24 | 4.8 | 13.2 | 0 | 7.33 | 0.15
2025-09-24 | 15.3 | 2.7 | 0 | 2024-09-24 | 12.7 | 5.3 | 0 | 2023-09-24 | 12 | 6 | 0 | 2022-09-24 | 6.8 | 11.2 | 0 | 2021-09-24 | 12.2 | 5.8 | 0 | 2020-09-24 | 11.6 | 6.4 | 0 | 2019-09-24 | 12.8 | 5.2 | 0 | 2018-09-24 | 5.5 | 12.5 | 0 | 2017-09-24 | 20.2 | 0 | 2.2 | 2016-09-24 | 7.6 | 10.4 | 0 | 6.55 | 0.22
2025-09-24 | 16 | 2 | 0 | 2024-09-24 | 15.7 | 2.3 | 0 | 2023-09-24 | 14.9 | 3.1 | 0 | 2022-09-24 | 9.1 | 8.9 | 0 | 2021-09-24 | 14.1 | 3.9 | 0 | 2020-09-24 | 12.9 | 5.1 | 0 | 2019-09-24 | 13.4 | 4.6 | 0 | 2018-09-24 | 6.6 | 11.4 | 0 | 2017-09-24 | 22.9 | 0 | 4.9 | 2016-09-24 | 9.7 | 8.3 | 0 | 4.96 | 0.49
2025-09-24 | 18.2 | 0 | 0.2 | 2024-09-24 | 16.5 | 1.5 | 0 | 2023-09-24 | 17.6 | 0.4 | 0 | 2022-09-24 | 11.7 | 6.3 | 0 | 2021-09-24 | 15.3 | 2.7 | 0 | 2020-09-24 | 15.3 | 2.7 | 0 | 2019-09-24 | 14.5 | 3.5 | 0 | 2018-09-24 | 8.6 | 9.4 | 0 | 2017-09-24 | 25 | 0 | 7 | 2016-09-24 | 12 | 6 | 0 | 3.25 | 0.72
2025-09-24 | 19.9 | 0 | 1.9 | 2024-09-24 | 17.6 | 0.4 | 0 | 2023-09-24 | 19.4 | 0 | 1.4 | 2022-09-24 | 13.3 | 4.7 | 0 | 2021-09-24 | 16.3 | 1.7 | 0 | 2020-09-24 | 15.9 | 2.1 | 0 | 2019-09-24 | 14.1 | 3.9 | 0 | 2018-09-24 | 9.7 | 8.3 | 0 | 2017-09-24 | 26.6 | 0 | 8.6 | 2016-09-24 | 14.2 | 3.8 | 0 | 2.49 | 1.19
2025-09-24 | 21.8 | 0 | 3.8 | 2024-09-24 | 18.6 | 0 | 0.6 | 2023-09-24 | 21.2 | 0 | 3.2 | 2022-09-24 | 15.7 | 2.3 | 0 | 2021-09-24 | 16.8 | 1.2 | 0 | 2020-09-24 | 17.4 | 0.6 | 0 | 2019-09-24 | 15.6 | 2.4 | 0 | 2018-09-24 | 10.8 | 7.2 | 0 | 2017-09-24 | 27.5 | 0 | 9.5 | 2016-09-24 | 15.5 | 2.5 | 0 | 1.62 | 1.71
2025-09-24 | 22.7 | 0 | 4.7 | 2024-09-24 | 19.4 | 0 | 1.4 | 2023-09-24 | 22.6 | 0 | 4.6 | 2022-09-24 | 16.8 | 1.2 | 0 | 2021-09-24 | 16.6 | 1.4 | 0 | 2020-09-24 | 16.8 | 1.2 | 0 | 2019-09-24 | 16.4 | 1.6 | 0 | 2018-09-24 | 12.2 | 5.8 | 0 | 2017-09-24 | 28.9 | 0 | 10.9 | 2016-09-24 | 15 | 3 | 0 | 1.42 | 2.16
2025-09-24 | 23.3 | 0 | 5.3 | 2024-09-24 | 19.4 | 0 | 1.4 | 2023-09-24 | 23.2 | 0 | 5.2 | 2022-09-24 | 17.8 | 0.2 | 0 | 2021-09-24 | 17.1 | 0.9 | 0 | 2020-09-24 | 16.7 | 1.3 | 0 | 2019-09-24 | 16.5 | 1.5 | 0 | 2018-09-24 | 13.4 | 4.6 | 0 | 2017-09-24 | 30.5 | 0 | 12.5 | 2016-09-24 | 15.3 | 2.7 | 0 | 1.12 | 2.44
2025-09-24 | 23.2 | 0 | 5.2 | 2024-09-24 | 19.7 | 0 | 1.7 | 2023-09-24 | 23.8 | 0 | 5.8 | 2022-09-24 | 18.1 | 0 | 0.1 | 2021-09-24 | 16.6 | 1.4 | 0 | 2020-09-24 | 15 | 3 | 0 | 2019-09-24 | 16.4 | 1.6 | 0 | 2018-09-24 | 14.1 | 3.9 | 0 | 2017-09-24 | 31.4 | 0 | 13.4 | 2016-09-24 | 17.3 | 0.7 | 0 | 1.06 | 2.62
2025-09-24 | 23.9 | 0 | 5.9 | 2024-09-24 | 20.3 | 0 | 2.3 | 2023-09-24 | 24.1 | 0 | 6.1 | 2022-09-24 | 18.6 | 0 | 0.6 | 2021-09-24 | 16.1 | 1.9 | 0 | 2020-09-24 | 15.4 | 2.6 | 0 | 2019-09-24 | 15.8 | 2.2 | 0 | 2018-09-24 | 13.9 | 4.1 | 0 | 2017-09-24 | 31.3 | 0 | 13.3 | 2016-09-24 | 16.8 | 1.2 | 0 | 1.2 | 2.82
2025-09-24 | 22.9 | 0 | 4.9 | 2024-09-24 | 19.6 | 0 | 1.6 | 2023-09-24 | 23.7 | 0 | 5.7 | 2022-09-24 | 18.2 | 0 | 0.2 | 2021-09-24 | 16.4 | 1.6 | 0 | 2020-09-24 | 16.1 | 1.9 | 0 | 2019-09-24 | 15.7 | 2.3 | 0 | 2018-09-24 | 13.7 | 4.3 | 0 | 2017-09-24 | 30.7 | 0 | 12.7 | 2016-09-24 | 16.2 | 1.8 | 0 | 1.19 | 2.51
2025-09-24 | 21.7 | 0 | 3.7 | 2024-09-24 | 18 | 0 | 0 | 2023-09-24 | 22.5 | 0 | 4.5 | 2022-09-24 | 17.2 | 0.8 | 0 | 2021-09-24 | 15.9 | 2.1 | 0 | 2020-09-24 | 15.7 | 2.3 | 0 | 2019-09-24 | 15 | 3 | 0 | 2018-09-24 | 12.7 | 5.3 | 0 | 2017-09-24 | 29.9 | 0 | 11.9 | 2016-09-24 | 14.7 | 3.3 | 0 | 1.68 | 2.01
2025-09-24 | 19.5 | 0 | 1.5 | 2024-09-24 | 17.2 | 0.8 | 0 | 2023-09-24 | 19.4 | 0 | 1.4 | 2022-09-24 | 14.4 | 3.6 | 0 | 2021-09-24 | 15.2 | 2.8 | 0 | 2020-09-24 | 14.6 | 3.4 | 0 | 2019-09-24 | 14.9 | 3.1 | 0 | 2018-09-24 | 10.8 | 7.2 | 0 | 2017-09-24 | 27.3 | 0 | 9.3 | 2016-09-24 | 13.5 | 4.5 | 0 | 2.54 | 1.22
2025-09-24 | 18.7 | 0 | 0.7 | 2024-09-24 | 16.7 | 1.3 | 0 | 2023-09-24 | 16.8 | 1.2 | 0 | 2022-09-24 | 13.8 | 4.2 | 0 | 2021-09-24 | 14.9 | 3.1 | 0 | 2020-09-24 | 14 | 4 | 0 | 2019-09-24 | 13.9 | 4.1 | 0 | 2018-09-24 | 9.6 | 8.4 | 0 | 2017-09-24 | 26.5 | 0 | 8.5 | 2016-09-24 | 12.3 | 5.7 | 0 | 3.2 | 0.92
2025-09-24 | 17.5 | 0.5 | 0 | 2024-09-24 | 16.3 | 1.7 | 0 | 2023-09-24 | 17.9 | 0.1 | 0 | 2022-09-24 | 11.3 | 6.7 | 0 | 2021-09-24 | 13.7 | 4.3 | 0 | 2020-09-24 | 14.1 | 3.9 | 0 | 2019-09-24 | 13.7 | 4.3 | 0 | 2018-09-24 | 9 | 9 | 0 | 2017-09-24 | 23.7 | 0 | 5.7 | 2016-09-24 | 11.1 | 6.9 | 0 | 3.74 | 0.57
2025-09-24 | 16.6 | 1.4 | 0 | 2024-09-24 | 15.6 | 2.4 | 0 | 2023-09-24 | 15.1 | 2.9 | 0 | 2022-09-24 | 10.9 | 7.1 | 0 | 2021-09-24 | 12.9 | 5.1 | 0 | 2020-09-24 | 13.3 | 4.7 | 0 | 2019-09-24 | 13.4 | 4.6 | 0 | 2018-09-24 | 8.4 | 9.6 | 0 | 2017-09-24 | 22.6 | 0 | 4.6 | 2016-09-24 | 8.9 | 9.1 | 0 | 4.69 | 0.46
2025-09-24 | 16.2 | 1.8 | 0 | 2024-09-24 | 15.6 | 2.4 | 0 | 2023-09-24 | 15.1 | 2.9 | 0 | 2022-09-24 | 10.7 | 7.3 | 0 | 2021-09-24 | 12.6 | 5.4 | 0 | 2020-09-24 | 13.2 | 4.8 | 0 | 2019-09-24 | 12.6 | 5.4 | 0 | 2018-09-24 | 8.1 | 9.9 | 0 | 2017-09-24 | 22.4 | 0 | 4.4 | 2016-09-24 | 9.1 | 8.9 | 0 | 4.88 | 0.44
2025-09-24 | 16.4 | 1.6 | 0 | 2024-09-24 | 14.4 | 3.6 | 0 | 2023-09-24 | 15.9 | 2.1 | 0 | 2022-09-24 | 10.6 | 7.4 | 0 | 2021-09-24 | 11.9 | 6.1 | 0 | 2020-09-24 | 11.8 | 6.2 | 0 | 2019-09-24 | 10.9 | 7.1 | 0 | 2018-09-24 | 7.6 | 10.4 | 0 | 2017-09-24 | 21.5 | 0 | 3.5 | 2016-09-24 | 8.1 | 9.9 | 0 | 5.44 | 0.35
2025-09-25 | 15.5 | 2.5 | 0 | 2024-09-25 | 14.2 | 3.8 | 0 | 2023-09-25 | 15.1 | 2.9 | 0 | 2022-09-25 | 10.2 | 7.8 | 0 | 2021-09-25 | 10.9 | 7.1 | 0 | 2020-09-25 | 11.3 | 6.7 | 0 | 2019-09-25 | 10.2 | 7.8 | 0 | 2018-09-25 | 7.4 | 10.6 | 0 | 2017-09-25 | 19.7 | 0 | 1.7 | 2016-09-25 | 7.7 | 10.3 | 0 | 5.95 | 0.17
2025-09-25 | 15.4 | 2.6 | 0 | 2024-09-25 | 13.6 | 4.4 | 0 | 2023-09-25 | 12.3 | 5.7 | 0 | 2022-09-25 | 10.7 | 7.3 | 0 | 2021-09-25 | 10.4 | 7.6 | 0 | 2020-09-25 | 11.4 | 6.6 | 0 | 2019-09-25 | 8.3 | 9.7 | 0 | 2018-09-25 | 7.4 | 10.6 | 0 | 2017-09-25 | 20.1 | 0 | 2.1 | 2016-09-25 | 7 | 11 | 0 | 6.55 | 0.21
2025-09-25 | 15.3 | 2.7 | 0 | 2024-09-25 | 13 | 5 | 0 | 2023-09-25 | 12 | 6 | 0 | 2022-09-25 | 10.7 | 7.3 | 0 | 2021-09-25 | 10.4 | 7.6 | 0 | 2020-09-25 | 10.9 | 7.1 | 0 | 2019-09-25 | 7.4 | 10.6 | 0 | 2018-09-25 | 7.4 | 10.6 | 0 | 2017-09-25 | 19.2 | 0 | 1.2 | 2016-09-25 | 7.3 | 10.7 | 0 | 6.76 | 0.12
2025-09-25 | 15.3 | 2.7 | 0 | 2024-09-25 | 12.9 | 5.1 | 0 | 2023-09-25 | 10.9 | 7.1 | 0 | 2022-09-25 | 9.9 | 8.1 | 0 | 2021-09-25 | 9.3 | 8.7 | 0 | 2020-09-25 | 11.1 | 6.9 | 0 | 2019-09-25 | 8.2 | 9.8 | 0 | 2018-09-25 | 7.8 | 10.2 | 0 | 2017-09-25 | 18.7 | 0 | 0.7 | 2016-09-25 | 3.8 | 14.2 | 0 | 7.28 | 0.07
2025-09-25 | 15.2 | 2.8 | 0 | 2024-09-25 | 12.9 | 5.1 | 0 | 2023-09-25 | 10.6 | 7.4 | 0 | 2022-09-25 | 9.9 | 8.1 | 0 | 2021-09-25 | 8 | 10 | 0 | 2020-09-25 | 10.7 | 7.3 | 0 | 2019-09-25 | 7 | 11 | 0 | 2018-09-25 | 8.1 | 9.9 | 0 | 2017-09-25 | 19 | 0 | 1 | 2016-09-25 | 4.2 | 13.8 | 0 | 7.54 | 0.1
2025-09-25 | 14.6 | 3.4 | 0 | 2024-09-25 | 12.7 | 5.3 | 0 | 2023-09-25 | 11.2 | 6.8 | 0 | 2022-09-25 | 9.7 | 8.3 | 0 | 2021-09-25 | 7.8 | 10.2 | 0 | 2020-09-25 | 10.6 | 7.4 | 0 | 2019-09-25 | 7.1 | 10.9 | 0 | 2018-09-25 | 8.5 | 9.5 | 0 | 2017-09-25 | 18.1 | 0 | 0.1 | 2016-09-25 | 4.7 | 13.3 | 0 | 7.51 | 0.01
2025-09-25 | 14.1 | 3.9 | 0 | 2024-09-25 | 12.8 | 5.2 | 0 | 2023-09-25 | 11.2 | 6.8 | 0 | 2022-09-25 | 9.7 | 8.3 | 0 | 2021-09-25 | 8.3 | 9.7 | 0 | 2020-09-25 | 9.5 | 8.5 | 0 | 2019-09-25 | 5.9 | 12.1 | 0 | 2018-09-25 | 8.9 | 9.1 | 0 | 2017-09-25 | 17 | 1 | 0 | 2016-09-25 | 4.5 | 13.5 | 0 | 7.81 | 0
2025-09-25 | 14.2 | 3.8 | 0 | 2024-09-25 | 12.9 | 5.1 | 0 | 2023-09-25 | 11.8 | 6.2 | 0 | 2022-09-25 | 10.1 | 7.9 | 0 | 2021-09-25 | 9.5 | 8.5 | 0 | 2020-09-25 | 10.2 | 7.8 | 0 | 2019-09-25 | 7.9 | 10.1 | 0 | 2018-09-25 | 8.6 | 9.4 | 0 | 2017-09-25 | 19.2 | 0 | 1.2 | 2016-09-25 | 6.1 | 11.9 | 0 | 7.07 | 0.12
2025-09-25 | 14.5 | 3.5 | 0 | 2024-09-25 | 12.9 | 5.1 | 0 | 2023-09-25 | 14.1 | 3.9 | 0 | 2022-09-25 | 11.3 | 6.7 | 0 | 2021-09-25 | 11.9 | 6.1 | 0 | 2020-09-25 | 10.9 | 7.1 | 0 | 2019-09-25 | 10.9 | 7.1 | 0 | 2018-09-25 | 9.2 | 8.8 | 0 | 2017-09-25 | 21.4 | 0 | 3.4 | 2016-09-25 | 8.3 | 9.7 | 0 | 5.8 | 0.34
2025-09-25 | 14.8 | 3.2 | 0 | 2024-09-25 | 13.1 | 4.9 | 0 | 2023-09-25 | 15.8 | 2.2 | 0 | 2022-09-25 | 13.6 | 4.4 | 0 | 2021-09-25 | 15.1 | 2.9 | 0 | 2020-09-25 | 11.9 | 6.1 | 0 | 2019-09-25 | 14.3 | 3.7 | 0 | 2018-09-25 | 9.7 | 8.3 | 0 | 2017-09-25 | 25.6 | 0 | 7.6 | 2016-09-25 | 10.6 | 7.4 | 0 | 4.31 | 0.76
2025-09-25 | 15.2 | 2.8 | 0 | 2024-09-25 | 13.6 | 4.4 | 0 | 2023-09-25 | 17.6 | 0.4 | 0 | 2022-09-25 | 15.4 | 2.6 | 0 | 2021-09-25 | 17.8 | 0.2 | 0 | 2020-09-25 | 12.9 | 5.1 | 0 | 2019-09-25 | 16.4 | 1.6 | 0 | 2018-09-25 | 10.6 | 7.4 | 0 | 2017-09-25 | 27.9 | 0 | 9.9 | 2016-09-25 | 12.9 | 5.1 | 0 | 2.96 | 0.99
2025-09-25 | 15.8 | 2.2 | 0 | 2024-09-25 | 14.2 | 3.8 | 0 | 2023-09-25 | 18.8 | 0 | 0.8 | 2022-09-25 | 16.3 | 1.7 | 0 | 2021-09-25 | 18.8 | 0 | 0.8 | 2020-09-25 | 15.1 | 2.9 | 0 | 2019-09-25 | 18.2 | 0 | 0.2 | 2018-09-25 | 11.2 | 6.8 | 0 | 2017-09-25 | 30.1 | 0 | 12.1 | 2016-09-25 | 14.5 | 3.5 | 0 | 2.09 | 1.39
2025-09-25 | 16.1 | 1.9 | 0 | 2024-09-25 | 15 | 3 | 0 | 2023-09-25 | 19.7 | 0 | 1.7 | 2022-09-25 | 16.6 | 1.4 | 0 | 2021-09-25 | 19.6 | 0 | 1.6 | 2020-09-25 | 16.6 | 1.4 | 0 | 2019-09-25 | 19.6 | 0 | 1.6 | 2018-09-25 | 12 | 6 | 0 | 2017-09-25 | 31.4 | 0 | 13.4 | 2016-09-25 | 15.1 | 2.9 | 0 | 1.66 | 1.83
2025-09-25 | 16.6 | 1.4 | 0 | 2024-09-25 | 15.6 | 2.4 | 0 | 2023-09-25 | 20.3 | 0 | 2.3 | 2022-09-25 | 16.5 | 1.5 | 0 | 2021-09-25 | 21.1 | 0 | 3.1 | 2020-09-25 | 16.4 | 1.6 | 0 | 2019-09-25 | 21.8 | 0 | 3.8 | 2018-09-25 | 13.3 | 4.7 | 0 | 2017-09-25 | 32.3 | 0 | 14.3 | 2016-09-25 | 15.7 | 2.3 | 0 | 1.39 | 2.35
2025-09-25 | 17.1 | 0.9 | 0 | 2024-09-25 | 15.9 | 2.1 | 0 | 2023-09-25 | 20.9 | 0 | 2.9 | 2022-09-25 | 16.5 | 1.5 | 0 | 2021-09-25 | 21.6 | 0 | 3.6 | 2020-09-25 | 16.9 | 1.1 | 0 | 2019-09-25 | 21.7 | 0 | 3.7 | 2018-09-25 | 14.3 | 3.7 | 0 | 2017-09-25 | 33 | 0 | 15 | 2016-09-25 | 16.1 | 1.9 | 0 | 1.12 | 2.52
2025-09-25 | 16.9 | 1.1 | 0 | 2024-09-25 | 16 | 2 | 0 | 2023-09-25 | 20.5 | 0 | 2.5 | 2022-09-25 | 15.6 | 2.4 | 0 | 2021-09-25 | 21.6 | 0 | 3.6 | 2020-09-25 | 18 | 0 | 0 | 2019-09-25 | 22.5 | 0 | 4.5 | 2018-09-25 | 15.1 | 2.9 | 0 | 2017-09-25 | 32.8 | 0 | 14.8 | 2016-09-25 | 16.5 | 1.5 | 0 | 0.99 | 2.54
2025-09-25 | 16.7 | 1.3 | 0 | 2024-09-25 | 16.3 | 1.7 | 0 | 2023-09-25 | 19.8 | 0 | 1.8 | 2022-09-25 | 14.7 | 3.3 | 0 | 2021-09-25 | 21.4 | 0 | 3.4 | 2020-09-25 | 17.9 | 0.1 | 0 | 2019-09-25 | 22.5 | 0 | 4.5 | 2018-09-25 | 15.5 | 2.5 | 0 | 2017-09-25 | 31.8 | 0 | 13.8 | 2016-09-25 | 16.5 | 1.5 | 0 | 1.04 | 2.35
2025-09-25 | 16.8 | 1.2 | 0 | 2024-09-25 | 16.4 | 1.6 | 0 | 2023-09-25 | 18.3 | 0 | 0.3 | 2022-09-25 | 14.1 | 3.9 | 0 | 2021-09-25 | 19.4 | 0 | 1.4 | 2020-09-25 | 16.8 | 1.2 | 0 | 2019-09-25 | 20.8 | 0 | 2.8 | 2018-09-25 | 15.7 | 2.3 | 0 | 2017-09-25 | 29.7 | 0 | 11.7 | 2016-09-25 | 15.3 | 2.7 | 0 | 1.29 | 1.62
2025-09-25 | 16.8 | 1.2 | 0 | 2024-09-25 | 15.8 | 2.2 | 0 | 2023-09-25 | 16.1 | 1.9 | 0 | 2022-09-25 | 13.5 | 4.5 | 0 | 2021-09-25 | 17 | 1 | 0 | 2020-09-25 | 13.8 | 4.2 | 0 | 2019-09-25 | 19.9 | 0 | 1.9 | 2018-09-25 | 15.4 | 2.6 | 0 | 2017-09-25 | 26.9 | 0 | 8.9 | 2016-09-25 | 11.9 | 6.1 | 0 | 2.37 | 1.08
2025-09-25 | 16.8 | 1.2 | 0 | 2024-09-25 | 15.6 | 2.4 | 0 | 2023-09-25 | 14.6 | 3.4 | 0 | 2022-09-25 | 12.9 | 5.1 | 0 | 2021-09-25 | 15.6 | 2.4 | 0 | 2020-09-25 | 13.6 | 4.4 | 0 | 2019-09-25 | 19.7 | 0 | 1.7 | 2018-09-25 | 15.5 | 2.5 | 0 | 2017-09-25 | 25.9 | 0 | 7.9 | 2016-09-25 | 11.5 | 6.5 | 0 | 2.79 | 0.96
2025-09-25 | 16.7 | 1.3 | 0 | 2024-09-25 | 15.3 | 2.7 | 0 | 2023-09-25 | 14.1 | 3.9 | 0 | 2022-09-25 | 12.7 | 5.3 | 0 | 2021-09-25 | 16.6 | 1.4 | 0 | 2020-09-25 | 12.4 | 5.6 | 0 | 2019-09-25 | 19.4 | 0 | 1.4 | 2018-09-25 | 15.6 | 2.4 | 0 | 2017-09-25 | 24.6 | 0 | 6.6 | 2016-09-25 | 10.8 | 7.2 | 0 | 2.98 | 0.8
2025-09-25 | 16.1 | 1.9 | 0 | 2024-09-25 | 15.2 | 2.8 | 0 | 2023-09-25 | 12.5 | 5.5 | 0 | 2022-09-25 | 12.3 | 5.7 | 0 | 2021-09-25 | 16.3 | 1.7 | 0 | 2020-09-25 | 11.9 | 6.1 | 0 | 2019-09-25 | 19.7 | 0 | 1.7 | 2018-09-25 | 15.9 | 2.1 | 0 | 2017-09-25 | 23.5 | 0 | 5.5 | 2016-09-25 | 8.6 | 9.4 | 0 | 3.52 | 0.72
2025-09-25 | 16.1 | 1.9 | 0 | 2024-09-25 | 15.2 | 2.8 | 0 | 2023-09-25 | 11.8 | 6.2 | 0 | 2022-09-25 | 12.4 | 5.6 | 0 | 2021-09-25 | 15.8 | 2.2 | 0 | 2020-09-25 | 10.2 | 7.8 | 0 | 2019-09-25 | 20.7 | 0 | 2.7 | 2018-09-25 | 16.2 | 1.8 | 0 | 2017-09-25 | 23.1 | 0 | 5.1 | 2016-09-25 | 7.9 | 10.1 | 0 | 3.84 | 0.78
2025-09-25 | 15.8 | 2.2 | 0 | 2024-09-25 | 15.2 | 2.8 | 0 | 2023-09-25 | 11.6 | 6.4 | 0 | 2022-09-25 | 12.4 | 5.6 | 0 | 2021-09-25 | 15.6 | 2.4 | 0 | 2020-09-25 | 9.8 | 8.2 | 0 | 2019-09-25 | 21 | 0 | 3 | 2018-09-25 | 16.8 | 1.2 | 0 | 2017-09-25 | 22.5 | 0 | 4.5 | 2016-09-25 | 6.8 | 11.2 | 0 | 4 | 0.75
2025-09-26 | 15.8 | 2.2 | 0 | 2024-09-26 | 15.4 | 2.6 | 0 | 2023-09-26 | 11.2 | 6.8 | 0 | 2022-09-26 | 12.2 | 5.8 | 0 | 2021-09-26 | 14.7 | 3.3 | 0 | 2020-09-26 | 8.5 | 9.5 | 0 | 2019-09-26 | 20.1 | 0 | 2.1 | 2018-09-26 | 17.3 | 0.7 | 0 | 2017-09-26 | 21 | 0 | 3 | 2016-09-26 | 6.6 | 11.4 | 0 | 4.23 | 0.51
2025-09-26 | 15.4 | 2.6 | 0 | 2024-09-26 | 15.4 | 2.6 | 0 | 2023-09-26 | 10.6 | 7.4 | 0 | 2022-09-26 | 11.9 | 6.1 | 0 | 2021-09-26 | 13.8 | 4.2 | 0 | 2020-09-26 | 8.2 | 9.8 | 0 | 2019-09-26 | 19.8 | 0 | 1.8 | 2018-09-26 | 17.5 | 0.5 | 0 | 2017-09-26 | 20.4 | 0 | 2.4 | 2016-09-26 | 4.5 | 13.5 | 0 | 4.67 | 0.42
2025-09-26 | 14.2 | 3.8 | 0 | 2024-09-26 | 15.5 | 2.5 | 0 | 2023-09-26 | 10 | 8 | 0 | 2022-09-26 | 11.4 | 6.6 | 0 | 2021-09-26 | 12.9 | 5.1 | 0 | 2020-09-26 | 8 | 10 | 0 | 2019-09-26 | 19.2 | 0 | 1.2 | 2018-09-26 | 17.8 | 0.2 | 0 | 2017-09-26 | 19.2 | 0 | 1.2 | 2016-09-26 | 5.3 | 12.7 | 0 | 4.89 | 0.24
2025-09-26 | 14.6 | 3.4 | 0 | 2024-09-26 | 15.4 | 2.6 | 0 | 2023-09-26 | 9.6 | 8.4 | 0 | 2022-09-26 | 11.5 | 6.5 | 0 | 2021-09-26 | 12.2 | 5.8 | 0 | 2020-09-26 | 8.1 | 9.9 | 0 | 2019-09-26 | 18.7 | 0 | 0.7 | 2018-09-26 | 18.1 | 0 | 0.1 | 2017-09-26 | 19.7 | 0 | 1.7 | 2016-09-26 | 3.7 | 14.3 | 0 | 5.09 | 0.25
2025-09-26 | 14.9 | 3.1 | 0 | 2024-09-26 | 15.7 | 2.3 | 0 | 2023-09-26 | 9.2 | 8.8 | 0 | 2022-09-26 | 11.2 | 6.8 | 0 | 2021-09-26 | 11.5 | 6.5 | 0 | 2020-09-26 | 8.2 | 9.8 | 0 | 2019-09-26 | 17.9 | 0.1 | 0 | 2018-09-26 | 18.9 | 0 | 0.9 | 2017-09-26 | 18.9 | 0 | 0.9 | 2016-09-26 | 3.5 | 14.5 | 0 | 5.19 | 0.18
2025-09-26 | 15.3 | 2.7 | 0 | 2024-09-26 | 16.1 | 1.9 | 0 | 2023-09-26 | 9 | 9 | 0 | 2022-09-26 | 11.4 | 6.6 | 0 | 2021-09-26 | 10.6 | 7.4 | 0 | 2020-09-26 | 8 | 10 | 0 | 2019-09-26 | 16.6 | 1.4 | 0 | 2018-09-26 | 19.3 | 0 | 1.3 | 2017-09-26 | 18.2 | 0 | 0.2 | 2016-09-26 | 3.3 | 14.7 | 0 | 5.37 | 0.15
2025-09-26 | 15.2 | 2.8 | 0 | 2024-09-26 | 16.4 | 1.6 | 0 | 2023-09-26 | 8.9 | 9.1 | 0 | 2022-09-26 | 11.5 | 6.5 | 0 | 2021-09-26 | 9.9 | 8.1 | 0 | 2020-09-26 | 7 | 11 | 0 | 2019-09-26 | 17.5 | 0.5 | 0 | 2018-09-26 | 19.7 | 0 | 1.7 | 2017-09-26 | 17.8 | 0.2 | 0 | 2016-09-26 | 3.1 | 14.9 | 0 | 5.47 | 0.17
2025-09-26 | 15.3 | 2.7 | 0 | 2024-09-26 | 16.5 | 1.5 | 0 | 2023-09-26 | 9.8 | 8.2 | 0 | 2022-09-26 | 11.4 | 6.6 | 0 | 2021-09-26 | 10.6 | 7.4 | 0 | 2020-09-26 | 8.9 | 9.1 | 0 | 2019-09-26 | 15.8 | 2.2 | 0 | 2018-09-26 | 20.2 | 0 | 2.2 | 2017-09-26 | 18.9 | 0 | 0.9 | 2016-09-26 | 5.5 | 12.5 | 0 | 5.02 | 0.31
2025-09-26 | 16.1 | 1.9 | 0 | 2024-09-26 | 17.7 | 0.3 | 0 | 2023-09-26 | 11 | 7 | 0 | 2022-09-26 | 12 | 6 | 0 | 2021-09-26 | 12.5 | 5.5 | 0 | 2020-09-26 | 11.6 | 6.4 | 0 | 2019-09-26 | 15.4 | 2.6 | 0 | 2018-09-26 | 21 | 0 | 3 | 2017-09-26 | 20.7 | 0 | 2.7 | 2016-09-26 | 8.4 | 9.6 | 0 | 3.93 | 0.57
2025-09-26 | 16.9 | 1.1 | 0 | 2024-09-26 | 17.5 | 0.5 | 0 | 2023-09-26 | 12.3 | 5.7 | 0 | 2022-09-26 | 13.4 | 4.6 | 0 | 2021-09-26 | 14.5 | 3.5 | 0 | 2020-09-26 | 16.5 | 1.5 | 0 | 2019-09-26 | 15.1 | 2.9 | 0 | 2018-09-26 | 21 | 0 | 3 | 2017-09-26 | 24 | 0 | 6 | 2016-09-26 | 10.3 | 7.7 | 0 | 2.75 | 0.9
2025-09-26 | 18.6 | 0 | 0.6 | 2024-09-26 | 18.1 | 0 | 0.1 | 2023-09-26 | 13.7 | 4.3 | 0 | 2022-09-26 | 16.2 | 1.8 | 0 | 2021-09-26 | 16.3 | 1.7 | 0 | 2020-09-26 | 20.9 | 0 | 2.9 | 2019-09-26 | 14 | 4 | 0 | 2018-09-26 | 20.7 | 0 | 2.7 | 2017-09-26 | 26.9 | 0 | 8.9 | 2016-09-26 | 13.8 | 4.2 | 0 | 1.6 | 1.52
2025-09-26 | 20.3 | 0 | 2.3 | 2024-09-26 | 19.6 | 0 | 1.6 | 2023-09-26 | 15.5 | 2.5 | 0 | 2022-09-26 | 17.7 | 0.3 | 0 | 2021-09-26 | 16.4 | 1.6 | 0 | 2020-09-26 | 22.2 | 0 | 4.2 | 2019-09-26 | 14 | 4 | 0 | 2018-09-26 | 22.5 | 0 | 4.5 | 2017-09-26 | 27.2 | 0 | 9.2 | 2016-09-26 | 14.6 | 3.4 | 0 | 1.18 | 2.18
2025-09-26 | 20.1 | 0 | 2.1 | 2024-09-26 | 20.6 | 0 | 2.6 | 2023-09-26 | 16.9 | 1.1 | 0 | 2022-09-26 | 17.7 | 0.3 | 0 | 2021-09-26 | 18.8 | 0 | 0.8 | 2020-09-26 | 25 | 0 | 7 | 2019-09-26 | 14.3 | 3.7 | 0 | 2018-09-26 | 23.1 | 0 | 5.1 | 2017-09-26 | 28.4 | 0 | 10.4 | 2016-09-26 | 15.3 | 2.7 | 0 | 0.78 | 2.8
2025-09-26 | 21.4 | 0 | 3.4 | 2024-09-26 | 20.3 | 0 | 2.3 | 2023-09-26 | 17.6 | 0.4 | 0 | 2022-09-26 | 18.4 | 0 | 0.4 | 2021-09-26 | 18.6 | 0 | 0.6 | 2020-09-26 | 25 | 0 | 7 | 2019-09-26 | 16.5 | 1.5 | 0 | 2018-09-26 | 19.3 | 0 | 1.3 | 2017-09-26 | 29.6 | 0 | 11.6 | 2016-09-26 | 15.9 | 2.1 | 0 | 0.4 | 2.66
2025-09-26 | 21.9 | 0 | 3.9 | 2024-09-26 | 20.6 | 0 | 2.6 | 2023-09-26 | 18.2 | 0 | 0.2 | 2022-09-26 | 17.1 | 0.9 | 0 | 2021-09-26 | 16.4 | 1.6 | 0 | 2020-09-26 | 25.6 | 0 | 7.6 | 2019-09-26 | 18.5 | 0 | 0.5 | 2018-09-26 | 20.2 | 0 | 2.2 | 2017-09-26 | 29.4 | 0 | 11.4 | 2016-09-26 | 16.6 | 1.4 | 0 | 0.39 | 2.84
2025-09-26 | 20.7 | 0 | 2.7 | 2024-09-26 | 21.9 | 0 | 3.9 | 2023-09-26 | 17.8 | 0.2 | 0 | 2022-09-26 | 16.1 | 1.9 | 0 | 2021-09-26 | 18.1 | 0 | 0.1 | 2020-09-26 | 24.7 | 0 | 6.7 | 2019-09-26 | 18.7 | 0 | 0.7 | 2018-09-26 | 22.1 | 0 | 4.1 | 2017-09-26 | 30.3 | 0 | 12.3 | 2016-09-26 | 16.5 | 1.5 | 0 | 0.36 | 3.05
2025-09-26 | 18.9 | 0 | 0.9 | 2024-09-26 | 21.6 | 0 | 3.6 | 2023-09-26 | 16.6 | 1.4 | 0 | 2022-09-26 | 15.2 | 2.8 | 0 | 2021-09-26 | 15.4 | 2.6 | 0 | 2020-09-26 | 23.7 | 0 | 5.7 | 2019-09-26 | 17.1 | 0.9 | 0 | 2018-09-26 | 21.2 | 0 | 3.2 | 2017-09-26 | 29.2 | 0 | 11.2 | 2016-09-26 | 15.9 | 2.1 | 0 | 0.98 | 2.46
2025-09-26 | 18.9 | 0 | 0.9 | 2024-09-26 | 20.1 | 0 | 2.1 | 2023-09-26 | 16.2 | 1.8 | 0 | 2022-09-26 | 14.8 | 3.2 | 0 | 2021-09-26 | 15.5 | 2.5 | 0 | 2020-09-26 | 22.5 | 0 | 4.5 | 2019-09-26 | 15 | 3 | 0 | 2018-09-26 | 19.7 | 0 | 1.7 | 2017-09-26 | 27.2 | 0 | 9.2 | 2016-09-26 | 15.4 | 2.6 | 0 | 1.31 | 1.84
2025-09-26 | 18.2 | 0 | 0.2 | 2024-09-26 | 17.1 | 0.9 | 0 | 2023-09-26 | 13.4 | 4.6 | 0 | 2022-09-26 | 13.7 | 4.3 | 0 | 2021-09-26 | 13.1 | 4.9 | 0 | 2020-09-26 | 21.2 | 0 | 3.2 | 2019-09-26 | 13.2 | 4.8 | 0 | 2018-09-26 | 16.8 | 1.2 | 0 | 2017-09-26 | 25.1 | 0 | 7.1 | 2016-09-26 | 14.5 | 3.5 | 0 | 2.42 | 1.05
2025-09-26 | 17.6 | 0.4 | 0 | 2024-09-26 | 16.1 | 1.9 | 0 | 2023-09-26 | 12.6 | 5.4 | 0 | 2022-09-26 | 12.5 | 5.5 | 0 | 2021-09-26 | 12.8 | 5.2 | 0 | 2020-09-26 | 19.8 | 0 | 1.8 | 2019-09-26 | 12.1 | 5.9 | 0 | 2018-09-26 | 15.5 | 2.5 | 0 | 2017-09-26 | 24.3 | 0 | 6.3 | 2016-09-26 | 14.1 | 3.9 | 0 | 3.07 | 0.81
2025-09-26 | 16.5 | 1.5 | 0 | 2024-09-26 | 16.6 | 1.4 | 0 | 2023-09-26 | 12.8 | 5.2 | 0 | 2022-09-26 | 11.4 | 6.6 | 0 | 2021-09-26 | 12.9 | 5.1 | 0 | 2020-09-26 | 18.8 | 0 | 0.8 | 2019-09-26 | 10.6 | 7.4 | 0 | 2018-09-26 | 15.1 | 2.9 | 0 | 2017-09-26 | 23 | 0 | 5 | 2016-09-26 | 13.9 | 4.1 | 0 | 3.42 | 0.58
2025-09-26 | 15.5 | 2.5 | 0 | 2024-09-26 | 13.7 | 4.3 | 0 | 2023-09-26 | 11.4 | 6.6 | 0 | 2022-09-26 | 10.5 | 7.5 | 0 | 2021-09-26 | 11.7 | 6.3 | 0 | 2020-09-26 | 17.6 | 0.4 | 0 | 2019-09-26 | 10.9 | 7.1 | 0 | 2018-09-26 | 14 | 4 | 0 | 2017-09-26 | 22.6 | 0 | 4.6 | 2016-09-26 | 13.5 | 4.5 | 0 | 4.32 | 0.46
2025-09-26 | 14.5 | 3.5 | 0 | 2024-09-26 | 13.5 | 4.5 | 0 | 2023-09-26 | 11 | 7 | 0 | 2022-09-26 | 9.3 | 8.7 | 0 | 2021-09-26 | 10.9 | 7.1 | 0 | 2020-09-26 | 17.2 | 0.8 | 0 | 2019-09-26 | 10.7 | 7.3 | 0 | 2018-09-26 | 11.9 | 6.1 | 0 | 2017-09-26 | 22.2 | 0 | 4.2 | 2016-09-26 | 13.7 | 4.3 | 0 | 4.93 | 0.42
2025-09-26 | 13.6 | 4.4 | 0 | 2024-09-26 | 11 | 7 | 0 | 2023-09-26 | 8.1 | 9.9 | 0 | 2022-09-26 | 9.5 | 8.5 | 0 | 2021-09-26 | 10.4 | 7.6 | 0 | 2020-09-26 | 17.6 | 0.4 | 0 | 2019-09-26 | 10.1 | 7.9 | 0 | 2018-09-26 | 10.1 | 7.9 | 0 | 2017-09-26 | 21.8 | 0 | 3.8 | 2016-09-26 | 15.1 | 2.9 | 0 | 5.65 | 0.38
2025-09-27 | 13.5 | 4.5 | 0 | 2024-09-27 | 12.3 | 5.7 | 0 | 2023-09-27 | 7.6 | 10.4 | 0 | 2022-09-27 | 9.6 | 8.4 | 0 | 2021-09-27 | 9.9 | 8.1 | 0 | 2020-09-27 | 17.4 | 0.6 | 0 | 2019-09-27 | 9.1 | 8.9 | 0 | 2018-09-27 | 9.3 | 8.7 | 0 | 2017-09-27 | 20.9 | 0 | 2.9 | 2016-09-27 | 15.1 | 2.9 | 0 | 5.82 | 0.29
2025-09-27 | 13.8 | 4.2 | 0 | 2024-09-27 | 11.4 | 6.6 | 0 | 2023-09-27 | 7.7 | 10.3 | 0 | 2022-09-27 | 10.4 | 7.6 | 0 | 2021-09-27 | 10.6 | 7.4 | 0 | 2020-09-27 | 16.9 | 1.1 | 0 | 2019-09-27 | 7.2 | 10.8 | 0 | 2018-09-27 | 8.3 | 9.7 | 0 | 2017-09-27 | 20.3 | 0 | 2.3 | 2016-09-27 | 14.9 | 3.1 | 0 | 6.08 | 0.23
2025-09-27 | 13.6 | 4.4 | 0 | 2024-09-27 | 11.5 | 6.5 | 0 | 2023-09-27 | 6.8 | 11.2 | 0 | 2022-09-27 | 11.1 | 6.9 | 0 | 2021-09-27 | 10.4 | 7.6 | 0 | 2020-09-27 | 17.1 | 0.9 | 0 | 2019-09-27 | 8.3 | 9.7 | 0 | 2018-09-27 | 7.8 | 10.2 | 0 | 2017-09-27 | 19.8 | 0 | 1.8 | 2016-09-27 | 13.3 | 4.7 | 0 | 6.21 | 0.18
2025-09-27 | 13.2 | 4.8 | 0 | 2024-09-27 | 11.1 | 6.9 | 0 | 2023-09-27 | 6.8 | 11.2 | 0 | 2022-09-27 | 11 | 7 | 0 | 2021-09-27 | 10.3 | 7.7 | 0 | 2020-09-27 | 17.2 | 0.8 | 0 | 2019-09-27 | 7.1 | 10.9 | 0 | 2018-09-27 | 7.7 | 10.3 | 0 | 2017-09-27 | 19.2 | 0 | 1.2 | 2016-09-27 | 12.4 | 5.6 | 0 | 6.52 | 0.12
2025-09-27 | 13.1 | 4.9 | 0 | 2024-09-27 | 10.3 | 7.7 | 0 | 2023-09-27 | 6.3 | 11.7 | 0 | 2022-09-27 | 10.9 | 7.1 | 0 | 2021-09-27 | 9.7 | 8.3 | 0 | 2020-09-27 | 17.1 | 0.9 | 0 | 2019-09-27 | 8 | 10 | 0 | 2018-09-27 | 6 | 12 | 0 | 2017-09-27 | 18.8 | 0 | 0.8 | 2016-09-27 | 11.6 | 6.4 | 0 | 6.9 | 0.08
2025-09-27 | 12.9 | 5.1 | 0 | 2024-09-27 | 11 | 7 | 0 | 2023-09-27 | 5.5 | 12.5 | 0 | 2022-09-27 | 10.8 | 7.2 | 0 | 2021-09-27 | 9.6 | 8.4 | 0 | 2020-09-27 | 17.1 | 0.9 | 0 | 2019-09-27 | 7.1 | 10.9 | 0 | 2018-09-27 | 7.2 | 10.8 | 0 | 2017-09-27 | 18.9 | 0 | 0.9 | 2016-09-27 | 10.6 | 7.4 | 0 | 7.02 | 0.09
2025-09-27 | 12.9 | 5.1 | 0 | 2024-09-27 | 10.8 | 7.2 | 0 | 2023-09-27 | 5.3 | 12.7 | 0 | 2022-09-27 | 11 | 7 | 0 | 2021-09-27 | 9.9 | 8.1 | 0 | 2020-09-27 | 16.8 | 1.2 | 0 | 2019-09-27 | 6.8 | 11.2 | 0 | 2018-09-27 | 5.2 | 12.8 | 0 | 2017-09-27 | 18.4 | 0 | 0.4 | 2016-09-27 | 10.4 | 7.6 | 0 | 7.29 | 0.04
2025-09-27 | 12.7 | 5.3 | 0 | 2024-09-27 | 11.1 | 6.9 | 0 | 2023-09-27 | 8 | 10 | 0 | 2022-09-27 | 11.2 | 6.8 | 0 | 2021-09-27 | 11.3 | 6.7 | 0 | 2020-09-27 | 17.7 | 0.3 | 0 | 2019-09-27 | 8.2 | 9.8 | 0 | 2018-09-27 | 7 | 11 | 0 | 2017-09-27 | 19.1 | 0 | 1.1 | 2016-09-27 | 11.4 | 6.6 | 0 | 6.34 | 0.11
2025-09-27 | 14.2 | 3.8 | 0 | 2024-09-27 | 14.4 | 3.6 | 0 | 2023-09-27 | 10.2 | 7.8 | 0 | 2022-09-27 | 12 | 6 | 0 | 2021-09-27 | 12.2 | 5.8 | 0 | 2020-09-27 | 19 | 0 | 1 | 2019-09-27 | 11.2 | 6.8 | 0 | 2018-09-27 | 9.6 | 8.4 | 0 | 2017-09-27 | 21.4 | 0 | 3.4 | 2016-09-27 | 13.6 | 4.4 | 0 | 4.66 | 0.44
2025-09-27 | 16.1 | 1.9 | 0 | 2024-09-27 | 17.4 | 0.6 | 0 | 2023-09-27 | 12.9 | 5.1 | 0 | 2022-09-27 | 12.7 | 5.3 | 0 | 2021-09-27 | 12.8 | 5.2 | 0 | 2020-09-27 | 20.7 | 0 | 2.7 | 2019-09-27 | 13.7 | 4.3 | 0 | 2018-09-27 | 11.7 | 6.3 | 0 | 2017-09-27 | 24.2 | 0 | 6.2 | 2016-09-27 | 15.7 | 2.3 | 0 | 3.1 | 0.89
2025-09-27 | 17.8 | 0.2 | 0 | 2024-09-27 | 19.2 | 0 | 1.2 | 2023-09-27 | 14.8 | 3.2 | 0 | 2022-09-27 | 13.2 | 4.8 | 0 | 2021-09-27 | 13.4 | 4.6 | 0 | 2020-09-27 | 21.2 | 0 | 3.2 | 2019-09-27 | 16 | 2 | 0 | 2018-09-27 | 14 | 4 | 0 | 2017-09-27 | 27 | 0 | 9 | 2016-09-27 | 17.7 | 0.3 | 0 | 1.91 | 1.34
2025-09-27 | 18.6 | 0 | 0.6 | 2024-09-27 | 19.5 | 0 | 1.5 | 2023-09-27 | 16.7 | 1.3 | 0 | 2022-09-27 | 13.7 | 4.3 | 0 | 2021-09-27 | 14.2 | 3.8 | 0 | 2020-09-27 | 22.3 | 0 | 4.3 | 2019-09-27 | 17.9 | 0.1 | 0 | 2018-09-27 | 15 | 3 | 0 | 2017-09-27 | 29.6 | 0 | 11.6 | 2016-09-27 | 19.1 | 0 | 1.1 | 1.25 | 1.91
2025-09-27 | 20.1 | 0 | 2.1 | 2024-09-27 | 20.5 | 0 | 2.5 | 2023-09-27 | 17.5 | 0.5 | 0 | 2022-09-27 | 13.9 | 4.1 | 0 | 2021-09-27 | 14.4 | 3.6 | 0 | 2020-09-27 | 23.8 | 0 | 5.8 | 2019-09-27 | 19.4 | 0 | 1.4 | 2018-09-27 | 15 | 3 | 0 | 2017-09-27 | 29.5 | 0 | 11.5 | 2016-09-27 | 19.7 | 0 | 1.7 | 1.12 | 2.5
2025-09-27 | 20.6 | 0 | 2.6 | 2024-09-27 | 20.8 | 0 | 2.8 | 2023-09-27 | 18.6 | 0 | 0.6 | 2022-09-27 | 14.1 | 3.9 | 0 | 2021-09-27 | 15.3 | 2.7 | 0 | 2020-09-27 | 24.5 | 0 | 6.5 | 2019-09-27 | 19.9 | 0 | 1.9 | 2018-09-27 | 16.7 | 1.3 | 0 | 2017-09-27 | 28.9 | 0 | 10.9 | 2016-09-27 | 19.1 | 0 | 1.1 | 0.79 | 2.64
2025-09-27 | 20.2 | 0 | 2.2 | 2024-09-27 | 21.1 | 0 | 3.1 | 2023-09-27 | 18.7 | 0 | 0.7 | 2022-09-27 | 14.6 | 3.4 | 0 | 2021-09-27 | 16.1 | 1.9 | 0 | 2020-09-27 | 25.4 | 0 | 7.4 | 2019-09-27 | 19.9 | 0 | 1.9 | 2018-09-27 | 17.2 | 0.8 | 0 | 2017-09-27 | 29.2 | 0 | 11.2 | 2016-09-27 | 20.2 | 0 | 2.2 | 0.61 | 2.87
2025-09-27 | 19.9 | 0 | 1.9 | 2024-09-27 | 21.5 | 0 | 3.5 | 2023-09-27 | 18.9 | 0 | 0.9 | 2022-09-27 | 15.3 | 2.7 | 0 | 2021-09-27 | 15.8 | 2.2 | 0 | 2020-09-27 | 25.9 | 0 | 7.9 | 2019-09-27 | 19 | 0 | 1 | 2018-09-27 | 16.4 | 1.6 | 0 | 2017-09-27 | 22.4 | 0 | 4.4 | 2016-09-27 | 20.1 | 0 | 2.1 | 0.65 | 2.17
2025-09-27 | 20.4 | 0 | 2.4 | 2024-09-27 | 21.5 | 0 | 3.5 | 2023-09-27 | 18.5 | 0 | 0.5 | 2022-09-27 | 15.6 | 2.4 | 0 | 2021-09-27 | 15.8 | 2.2 | 0 | 2020-09-27 | 25.5 | 0 | 7.5 | 2019-09-27 | 18.1 | 0 | 0.1 | 2018-09-27 | 16.1 | 1.9 | 0 | 2017-09-27 | 22.9 | 0 | 4.9 | 2016-09-27 | 19 | 0 | 1 | 0.65 | 1.99
2025-09-27 | 20.1 | 0 | 2.1 | 2024-09-27 | 20.4 | 0 | 2.4 | 2023-09-27 | 17.1 | 0.9 | 0 | 2022-09-27 | 14.8 | 3.2 | 0 | 2021-09-27 | 15.4 | 2.6 | 0 | 2020-09-27 | 24.6 | 0 | 6.6 | 2019-09-27 | 16.9 | 1.1 | 0 | 2018-09-27 | 14.1 | 3.9 | 0 | 2017-09-27 | 23.7 | 0 | 5.7 | 2016-09-27 | 18 | 0 | 0 | 1.17 | 1.68
2025-09-27 | 17.5 | 0.5 | 0 | 2024-09-27 | 17 | 1 | 0 | 2023-09-27 | 13.6 | 4.4 | 0 | 2022-09-27 | 14.2 | 3.8 | 0 | 2021-09-27 | 14.9 | 3.1 | 0 | 2020-09-27 | 22.6 | 0 | 4.6 | 2019-09-27 | 16.4 | 1.6 | 0 | 2018-09-27 | 12.1 | 5.9 | 0 | 2017-09-27 | 22.3 | 0 | 4.3 | 2016-09-27 | 16.6 | 1.4 | 0 | 2.17 | 0.89
2025-09-27 | 17.3 | 0.7 | 0 | 2024-09-27 | 15.9 | 2.1 | 0 | 2023-09-27 | 14.3 | 3.7 | 0 | 2022-09-27 | 12.5 | 5.5 | 0 | 2021-09-27 | 14 | 4 | 0 | 2020-09-27 | 21.1 | 0 | 3.1 | 2019-09-27 | 16.1 | 1.9 | 0 | 2018-09-27 | 12 | 6 | 0 | 2017-09-27 | 21.1 | 0 | 3.1 | 2016-09-27 | 14.9 | 3.1 | 0 | 2.7 | 0.62
2025-09-27 | 17.7 | 0.3 | 0 | 2024-09-27 | 14.9 | 3.1 | 0 | 2023-09-27 | 12.3 | 5.7 | 0 | 2022-09-27 | 12.7 | 5.3 | 0 | 2021-09-27 | 12.9 | 5.1 | 0 | 2020-09-27 | 19.9 | 0 | 1.9 | 2019-09-27 | 16 | 2 | 0 | 2018-09-27 | 11.7 | 6.3 | 0 | 2017-09-27 | 19.8 | 0 | 1.8 | 2016-09-27 | 14.7 | 3.3 | 0 | 3.11 | 0.37
2025-09-27 | 18.1 | 0 | 0.1 | 2024-09-27 | 13.5 | 4.5 | 0 | 2023-09-27 | 11.2 | 6.8 | 0 | 2022-09-27 | 12.5 | 5.5 | 0 | 2021-09-27 | 11.6 | 6.4 | 0 | 2020-09-27 | 20 | 0 | 2 | 2019-09-27 | 16.4 | 1.6 | 0 | 2018-09-27 | 11.8 | 6.2 | 0 | 2017-09-27 | 18.5 | 0 | 0.5 | 2016-09-27 | 13.7 | 4.3 | 0 | 3.53 | 0.26
2025-09-27 | 17.7 | 0.3 | 0 | 2024-09-27 | 13 | 5 | 0 | 2023-09-27 | 10 | 8 | 0 | 2022-09-27 | 10.7 | 7.3 | 0 | 2021-09-27 | 12.8 | 5.2 | 0 | 2020-09-27 | 18.2 | 0 | 0.2 | 2019-09-27 | 14.9 | 3.1 | 0 | 2018-09-27 | 10.6 | 7.4 | 0 | 2017-09-27 | 17.6 | 0.4 | 0 | 2016-09-27 | 13.6 | 4.4 | 0 | 4.11 | 0.02
2025-09-27 | 17.4 | 0.6 | 0 | 2024-09-27 | 12.2 | 5.8 | 0 | 2023-09-27 | 9.4 | 8.6 | 0 | 2022-09-27 | 10.9 | 7.1 | 0 | 2021-09-27 | 11.4 | 6.6 | 0 | 2020-09-27 | 18 | 0 | 0 | 2019-09-27 | 14.3 | 3.7 | 0 | 2018-09-27 | 11.2 | 6.8 | 0 | 2017-09-27 | 15.9 | 2.1 | 0 | 2016-09-27 | 13.4 | 4.6 | 0 | 4.59 | 0
2025-09-28 | 16.7 | 1.3 | 0 | 2024-09-28 | 11.7 | 6.3 | 0 | 2023-09-28 | 8.7 | 9.3 | 0 | 2022-09-28 | 10.9 | 7.1 | 0 | 2021-09-28 | 10.5 | 7.5 | 0 | 2020-09-28 | 17.8 | 0.2 | 0 | 2019-09-28 | 13.9 | 4.1 | 0 | 2018-09-28 | 11.1 | 6.9 | 0 | 2017-09-28 | 15.5 | 2.5 | 0 | 2016-09-28 | 10 | 8 | 0 | 5.32 | 0
2025-09-28 | 15.9 | 2.1 | 0 | 2024-09-28 | 12.2 | 5.8 | 0 | 2023-09-28 | 8.1 | 9.9 | 0 | 2022-09-28 | 11.6 | 6.4 | 0 | 2021-09-28 | 9.1 | 8.9 | 0 | 2020-09-28 | 17.5 | 0.5 | 0 | 2019-09-28 | 13.8 | 4.2 | 0 | 2018-09-28 | 10.8 | 7.2 | 0 | 2017-09-28 | 15.1 | 2.9 | 0 | 2016-09-28 | 11.1 | 6.9 | 0 | 5.48 | 0
2025-09-28 | 15.5 | 2.5 | 0 | 2024-09-28 | 10.9 | 7.1 | 0 | 2023-09-28 | 8.4 | 9.6 | 0 | 2022-09-28 | 12.1 | 5.9 | 0 | 2021-09-28 | 8.9 | 9.1 | 0 | 2020-09-28 | 17.8 | 0.2 | 0 | 2019-09-28 | 14.2 | 3.8 | 0 | 2018-09-28 | 10.4 | 7.6 | 0 | 2017-09-28 | 13.3 | 4.7 | 0 | 2016-09-28 | 11 | 7 | 0 | 5.75 | 0
2025-09-28 | 15.4 | 2.6 | 0 | 2024-09-28 | 10.3 | 7.7 | 0 | 2023-09-28 | 8 | 10 | 0 | 2022-09-28 | 12.2 | 5.8 | 0 | 2021-09-28 | 7.4 | 10.6 | 0 | 2020-09-28 | 17.1 | 0.9 | 0 | 2019-09-28 | 13.4 | 4.6 | 0 | 2018-09-28 | 10.7 | 7.3 | 0 | 2017-09-28 | 12.8 | 5.2 | 0 | 2016-09-28 | 10.6 | 7.4 | 0 | 6.21 | 0
2025-09-28 | 15.3 | 2.7 | 0 | 2024-09-28 | 9.8 | 8.2 | 0 | 2023-09-28 | 7 | 11 | 0 | 2022-09-28 | 11.9 | 6.1 | 0 | 2021-09-28 | 5.9 | 12.1 | 0 | 2020-09-28 | 16.9 | 1.1 | 0 | 2019-09-28 | 15.3 | 2.7 | 0 | 2018-09-28 | 8.3 | 9.7 | 0 | 2017-09-28 | 11.6 | 6.4 | 0 | 2016-09-28 | 10.6 | 7.4 | 0 | 6.74 | 0
2025-09-28 | 15.3 | 2.7 | 0 | 2024-09-28 | 10.6 | 7.4 | 0 | 2023-09-28 | 6.8 | 11.2 | 0 | 2022-09-28 | 11.6 | 6.4 | 0 | 2021-09-28 | 5.7 | 12.3 | 0 | 2020-09-28 | 16.7 | 1.3 | 0 | 2019-09-28 | 16.4 | 1.6 | 0 | 2018-09-28 | 8.2 | 9.8 | 0 | 2017-09-28 | 10.2 | 7.8 | 0 | 2016-09-28 | 10 | 8 | 0 | 6.85 | 0
2025-09-28 | 14.3 | 3.7 | 0 | 2024-09-28 | 10.9 | 7.1 | 0 | 2023-09-28 | 7.9 | 10.1 | 0 | 2022-09-28 | 11.3 | 6.7 | 0 | 2021-09-28 | 5.6 | 12.4 | 0 | 2020-09-28 | 14.9 | 3.1 | 0 | 2019-09-28 | 15.7 | 2.3 | 0 | 2018-09-28 | 9.2 | 8.8 | 0 | 2017-09-28 | 9.8 | 8.2 | 0 | 2016-09-28 | 10.1 | 7.9 | 0 | 7.03 | 0
2025-09-28 | 15 | 3 | 0 | 2024-09-28 | 11.8 | 6.2 | 0 | 2023-09-28 | 8.6 | 9.4 | 0 | 2022-09-28 | 11.3 | 6.7 | 0 | 2021-09-28 | 7.1 | 10.9 | 0 | 2020-09-28 | 15.7 | 2.3 | 0 | 2019-09-28 | 15.2 | 2.8 | 0 | 2018-09-28 | 11 | 7 | 0 | 2017-09-28 | 10.6 | 7.4 | 0 | 2016-09-28 | 10.3 | 7.7 | 0 | 6.34 | 0
2025-09-28 | 16.8 | 1.2 | 0 | 2024-09-28 | 13.8 | 4.2 | 0 | 2023-09-28 | 11.4 | 6.6 | 0 | 2022-09-28 | 12.5 | 5.5 | 0 | 2021-09-28 | 9.7 | 8.3 | 0 | 2020-09-28 | 17.5 | 0.5 | 0 | 2019-09-28 | 15.6 | 2.4 | 0 | 2018-09-28 | 13.1 | 4.9 | 0 | 2017-09-28 | 11.7 | 6.3 | 0 | 2016-09-28 | 10.8 | 7.2 | 0 | 4.71 | 0
2025-09-28 | 18.9 | 0 | 0.9 | 2024-09-28 | 16.2 | 1.8 | 0 | 2023-09-28 | 14.2 | 3.8 | 0 | 2022-09-28 | 12.1 | 5.9 | 0 | 2021-09-28 | 11 | 7 | 0 | 2020-09-28 | 19.2 | 0 | 1.2 | 2019-09-28 | 16.3 | 1.7 | 0 | 2018-09-28 | 14.8 | 3.2 | 0 | 2017-09-28 | 12.6 | 5.4 | 0 | 2016-09-28 | 11.5 | 6.5 | 0 | 3.53 | 0.21
2025-09-28 | 20.5 | 0 | 2.5 | 2024-09-28 | 18.4 | 0 | 0.4 | 2023-09-28 | 16.4 | 1.6 | 0 | 2022-09-28 | 12.5 | 5.5 | 0 | 2021-09-28 | 11.7 | 6.3 | 0 | 2020-09-28 | 20.3 | 0 | 2.3 | 2019-09-28 | 17.5 | 0.5 | 0 | 2018-09-28 | 16.5 | 1.5 | 0 | 2017-09-28 | 13.2 | 4.8 | 0 | 2016-09-28 | 12.9 | 5.1 | 0 | 2.53 | 0.52
2025-09-28 | 21.5 | 0 | 3.5 | 2024-09-28 | 19.6 | 0 | 1.6 | 2023-09-28 | 17.8 | 0.2 | 0 | 2022-09-28 | 12.8 | 5.2 | 0 | 2021-09-28 | 11.5 | 6.5 | 0 | 2020-09-28 | 23.6 | 0 | 5.6 | 2019-09-28 | 17.7 | 0.3 | 0 | 2018-09-28 | 18 | 0 | 0 | 2017-09-28 | 13.6 | 4.4 | 0 | 2016-09-28 | 13.9 | 4.1 | 0 | 2.07 | 1.07
2025-09-28 | 22.4 | 0 | 4.4 | 2024-09-28 | 20.6 | 0 | 2.6 | 2023-09-28 | 18.6 | 0 | 0.6 | 2022-09-28 | 13.1 | 4.9 | 0 | 2021-09-28 | 13.5 | 4.5 | 0 | 2020-09-28 | 24.6 | 0 | 6.6 | 2019-09-28 | 18.3 | 0 | 0.3 | 2018-09-28 | 18.7 | 0 | 0.7 | 2017-09-28 | 14.1 | 3.9 | 0 | 2016-09-28 | 17 | 1 | 0 | 1.43 | 1.52
2025-09-28 | 22.9 | 0 | 4.9 | 2024-09-28 | 21.1 | 0 | 3.1 | 2023-09-28 | 20.8 | 0 | 2.8 | 2022-09-28 | 13 | 5 | 0 | 2021-09-28 | 13.5 | 4.5 | 0 | 2020-09-28 | 25.9 | 0 | 7.9 | 2019-09-28 | 16.9 | 1.1 | 0 | 2018-09-28 | 19.3 | 0 | 1.3 | 2017-09-28 | 14.9 | 3.1 | 0 | 2016-09-28 | 18.3 | 0 | 0.3 | 1.37 | 2.03
2025-09-28 | 23.5 | 0 | 5.5 | 2024-09-28 | 21.5 | 0 | 3.5 | 2023-09-28 | 21.5 | 0 | 3.5 | 2022-09-28 | 13.5 | 4.5 | 0 | 2021-09-28 | 14.9 | 3.1 | 0 | 2020-09-28 | 25.7 | 0 | 7.7 | 2019-09-28 | 17.1 | 0.9 | 0 | 2018-09-28 | 20.2 | 0 | 2.2 | 2017-09-28 | 14.3 | 3.7 | 0 | 2016-09-28 | 19.2 | 0 | 1.2 | 1.22 | 2.36
2025-09-28 | 23.7 | 0 | 5.7 | 2024-09-28 | 21.8 | 0 | 3.8 | 2023-09-28 | 20.9 | 0 | 2.9 | 2022-09-28 | 14 | 4 | 0 | 2021-09-28 | 15.9 | 2.1 | 0 | 2020-09-28 | 25.6 | 0 | 7.6 | 2019-09-28 | 17.4 | 0.6 | 0 | 2018-09-28 | 19.3 | 0 | 1.3 | 2017-09-28 | 13.9 | 4.1 | 0 | 2016-09-28 | 18.7 | 0 | 0.7 | 1.08 | 2.2
2025-09-28 | 23.2 | 0 | 5.2 | 2024-09-28 | 21.2 | 0 | 3.2 | 2023-09-28 | 21.3 | 0 | 3.3 | 2022-09-28 | 13.5 | 4.5 | 0 | 2021-09-28 | 15.3 | 2.7 | 0 | 2020-09-28 | 26.1 | 0 | 8.1 | 2019-09-28 | 17.8 | 0.2 | 0 | 2018-09-28 | 19.2 | 0 | 1.2 | 2017-09-28 | 13.6 | 4.4 | 0 | 2016-09-28 | 18.4 | 0 | 0.4 | 1.18 | 2.14
2025-09-28 | 21.7 | 0 | 3.7 | 2024-09-28 | 19.6 | 0 | 1.6 | 2023-09-28 | 19.4 | 0 | 1.4 | 2022-09-28 | 12.5 | 5.5 | 0 | 2021-09-28 | 13.9 | 4.1 | 0 | 2020-09-28 | 24.5 | 0 | 6.5 | 2019-09-28 | 17.4 | 0.6 | 0 | 2018-09-28 | 18.2 | 0 | 0.2 | 2017-09-28 | 13 | 5 | 0 | 2016-09-28 | 17.2 | 0.8 | 0 | 1.6 | 1.34
2025-09-28 | 18.6 | 0 | 0.6 | 2024-09-28 | 17.4 | 0.6 | 0 | 2023-09-28 | 16.7 | 1.3 | 0 | 2022-09-28 | 11.7 | 6.3 | 0 | 2021-09-28 | 12.7 | 5.3 | 0 | 2020-09-28 | 22.6 | 0 | 4.6 | 2019-09-28 | 16 | 2 | 0 | 2018-09-28 | 17.4 | 0.6 | 0 | 2017-09-28 | 12.4 | 5.6 | 0 | 2016-09-28 | 15.7 | 2.3 | 0 | 2.4 | 0.52
2025-09-28 | 18.5 | 0 | 0.5 | 2024-09-28 | 16.6 | 1.4 | 0 | 2023-09-28 | 15.5 | 2.5 | 0 | 2022-09-28 | 11.2 | 6.8 | 0 | 2021-09-28 | 12.7 | 5.3 | 0 | 2020-09-28 | 20.7 | 0 | 2.7 | 2019-09-28 | 15.9 | 2.1 | 0 | 2018-09-28 | 12.1 | 5.9 | 0 | 2017-09-28 | 11.6 | 6.4 | 0 | 2016-09-28 | 14.8 | 3.2 | 0 | 3.36 | 0.32
2025-09-28 | 16.5 | 1.5 | 0 | 2024-09-28 | 16.1 | 1.9 | 0 | 2023-09-28 | 14.8 | 3.2 | 0 | 2022-09-28 | 10.9 | 7.1 | 0 | 2021-09-28 | 11.3 | 6.7 | 0 | 2020-09-28 | 20.6 | 0 | 2.6 | 2019-09-28 | 14.8 | 3.2 | 0 | 2018-09-28 | 12 | 6 | 0 | 2017-09-28 | 11.8 | 6.2 | 0 | 2016-09-28 | 13.8 | 4.2 | 0 | 4 | 0.26
2025-09-28 | 13.6 | 4.4 | 0 | 2024-09-28 | 14.9 | 3.1 | 0 | 2023-09-28 | 13.9 | 4.1 | 0 | 2022-09-28 | 10.3 | 7.7 | 0 | 2021-09-28 | 9.4 | 8.6 | 0 | 2020-09-28 | 21 | 0 | 3 | 2019-09-28 | 13.7 | 4.3 | 0 | 2018-09-28 | 11.1 | 6.9 | 0 | 2017-09-28 | 11 | 7 | 0 | 2016-09-28 | 13 | 5 | 0 | 5.11 | 0.3
2025-09-28 | 11 | 7 | 0 | 2024-09-28 | 13.1 | 4.9 | 0 | 2023-09-28 | 13.2 | 4.8 | 0 | 2022-09-28 | 9.6 | 8.4 | 0 | 2021-09-28 | 9.2 | 8.8 | 0 | 2020-09-28 | 21 | 0 | 3 | 2019-09-28 | 12.5 | 5.5 | 0 | 2018-09-28 | 10.9 | 7.1 | 0 | 2017-09-28 | 8.8 | 9.2 | 0 | 2016-09-28 | 12.2 | 5.8 | 0 | 6.15 | 0.3
2025-09-28 | 10.9 | 7.1 | 0 | 2024-09-28 | 12.3 | 5.7 | 0 | 2023-09-28 | 12 | 6 | 0 | 2022-09-28 | 9.4 | 8.6 | 0 | 2021-09-28 | 8.1 | 9.9 | 0 | 2020-09-28 | 21.8 | 0 | 3.8 | 2019-09-28 | 10.8 | 7.2 | 0 | 2018-09-28 | 10.4 | 7.6 | 0 | 2017-09-28 | 8.2 | 9.8 | 0 | 2016-09-28 | 11.4 | 6.6 | 0 | 6.85 | 0.38
2025-09-29 | 12.7 | 5.3 | 0 | 2024-09-29 | 12.9 | 5.1 | 0 | 2023-09-29 | 11.4 | 6.6 | 0 | 2022-09-29 | 9.2 | 8.8 | 0 | 2021-09-29 | 8.1 | 9.9 | 0 | 2020-09-29 | 20.8 | 0 | 2.8 | 2019-09-29 | 9.5 | 8.5 | 0 | 2018-09-29 | 10.6 | 7.4 | 0 | 2017-09-29 | 7.5 | 10.5 | 0 | 2016-09-29 | 10.9 | 7.1 | 0 | 6.92 | 0.28
2025-09-29 | 12.6 | 5.4 | 0 | 2024-09-29 | 12.7 | 5.3 | 0 | 2023-09-29 | 10.1 | 7.9 | 0 | 2022-09-29 | 8.9 | 9.1 | 0 | 2021-09-29 | 8.7 | 9.3 | 0 | 2020-09-29 | 20.5 | 0 | 2.5 | 2019-09-29 | 8.6 | 9.4 | 0 | 2018-09-29 | 10.1 | 7.9 | 0 | 2017-09-29 | 6.5 | 11.5 | 0 | 2016-09-29 | 10.4 | 7.6 | 0 | 7.34 | 0.25
2025-09-29 | 12.3 | 5.7 | 0 | 2024-09-29 | 12.6 | 5.4 | 0 | 2023-09-29 | 9.8 | 8.2 | 0 | 2022-09-29 | 8.6 | 9.4 | 0 | 2021-09-29 | 8.8 | 9.2 | 0 | 2020-09-29 | 19.8 | 0 | 1.8 | 2019-09-29 | 8.6 | 9.4 | 0 | 2018-09-29 | 9.8 | 8.2 | 0 | 2017-09-29 | 6.9 | 11.1 | 0 | 2016-09-29 | 9.8 | 8.2 | 0 | 7.48 | 0.18
2025-09-29 | 12.6 | 5.4 | 0 | 2024-09-29 | 10.8 | 7.2 | 0 | 2023-09-29 | 9.7 | 8.3 | 0 | 2022-09-29 | 8.2 | 9.8 | 0 | 2021-09-29 | 6.8 | 11.2 | 0 | 2020-09-29 | 20.3 | 0 | 2.3 | 2019-09-29 | 6.6 | 11.4 | 0 | 2018-09-29 | 9.8 | 8.2 | 0 | 2017-09-29 | 5 | 13 | 0 | 2016-09-29 | 9.9 | 8.1 | 0 | 8.26 | 0.23
2025-09-29 | 11.9 | 6.1 | 0 | 2024-09-29 | 10.8 | 7.2 | 0 | 2023-09-29 | 10.2 | 7.8 | 0 | 2022-09-29 | 8 | 10 | 0 | 2021-09-29 | 8.4 | 9.6 | 0 | 2020-09-29 | 20.7 | 0 | 2.7 | 2019-09-29 | 5.8 | 12.2 | 0 | 2018-09-29 | 9.6 | 8.4 | 0 | 2017-09-29 | 4.5 | 13.5 | 0 | 2016-09-29 | 9.1 | 8.9 | 0 | 8.37 | 0.27
2025-09-29 | 11.3 | 6.7 | 0 | 2024-09-29 | 10.3 | 7.7 | 0 | 2023-09-29 | 10.7 | 7.3 | 0 | 2022-09-29 | 7.6 | 10.4 | 0 | 2021-09-29 | 7.7 | 10.3 | 0 | 2020-09-29 | 19.8 | 0 | 1.8 | 2019-09-29 | 6.3 | 11.7 | 0 | 2018-09-29 | 9.1 | 8.9 | 0 | 2017-09-29 | 4.8 | 13.2 | 0 | 2016-09-29 | 8.6 | 9.4 | 0 | 8.56 | 0.18
2025-09-29 | 8.7 | 9.3 | 0 | 2024-09-29 | 11.7 | 6.3 | 0 | 2023-09-29 | 10.8 | 7.2 | 0 | 2022-09-29 | 7.2 | 10.8 | 0 | 2021-09-29 | 7.8 | 10.2 | 0 | 2020-09-29 | 18.6 | 0 | 0.6 | 2019-09-29 | 6 | 12 | 0 | 2018-09-29 | 8.8 | 9.2 | 0 | 2017-09-29 | 5 | 13 | 0 | 2016-09-29 | 8.1 | 9.9 | 0 | 8.79 | 0.06
2025-09-29 | 10.6 | 7.4 | 0 | 2024-09-29 | 12.4 | 5.6 | 0 | 2023-09-29 | 11.2 | 6.8 | 0 | 2022-09-29 | 7 | 11 | 0 | 2021-09-29 | 8.2 | 9.8 | 0 | 2020-09-29 | 17.1 | 0.9 | 0 | 2019-09-29 | 7.2 | 10.8 | 0 | 2018-09-29 | 9.2 | 8.8 | 0 | 2017-09-29 | 7.5 | 10.5 | 0 | 2016-09-29 | 9 | 9 | 0 | 8.06 | 0
2025-09-29 | 15 | 3 | 0 | 2024-09-29 | 14 | 4 | 0 | 2023-09-29 | 12.8 | 5.2 | 0 | 2022-09-29 | 8.3 | 9.7 | 0 | 2021-09-29 | 10.2 | 7.8 | 0 | 2020-09-29 | 16.1 | 1.9 | 0 | 2019-09-29 | 8.9 | 9.1 | 0 | 2018-09-29 | 10.2 | 7.8 | 0 | 2017-09-29 | 9.6 | 8.4 | 0 | 2016-09-29 | 10.3 | 7.7 | 0 | 6.46 | 0
2025-09-29 | 17.4 | 0.6 | 0 | 2024-09-29 | 15.6 | 2.4 | 0 | 2023-09-29 | 15.9 | 2.1 | 0 | 2022-09-29 | 9.1 | 8.9 | 0 | 2021-09-29 | 10.8 | 7.2 | 0 | 2020-09-29 | 15.8 | 2.2 | 0 | 2019-09-29 | 10.6 | 7.4 | 0 | 2018-09-29 | 11.2 | 6.8 | 0 | 2017-09-29 | 11.1 | 6.9 | 0 | 2016-09-29 | 12.1 | 5.9 | 0 | 5.04 | 0
2025-09-29 | 19.4 | 0 | 1.4 | 2024-09-29 | 17.5 | 0.5 | 0 | 2023-09-29 | 18.1 | 0 | 0.1 | 2022-09-29 | 9.8 | 8.2 | 0 | 2021-09-29 | 11.9 | 6.1 | 0 | 2020-09-29 | 17 | 1 | 0 | 2019-09-29 | 11.7 | 6.3 | 0 | 2018-09-29 | 12 | 6 | 0 | 2017-09-29 | 12.6 | 5.4 | 0 | 2016-09-29 | 13.7 | 4.3 | 0 | 3.78 | 0.15
2025-09-29 | 22.4 | 0 | 4.4 | 2024-09-29 | 19.2 | 0 | 1.2 | 2023-09-29 | 19.5 | 0 | 1.5 | 2022-09-29 | 10.3 | 7.7 | 0 | 2021-09-29 | 12.5 | 5.5 | 0 | 2020-09-29 | 17.1 | 0.9 | 0 | 2019-09-29 | 12.2 | 5.8 | 0 | 2018-09-29 | 13.1 | 4.9 | 0 | 2017-09-29 | 13.5 | 4.5 | 0 | 2016-09-29 | 15.7 | 2.3 | 0 | 3.16 | 0.71
2025-09-29 | 25 | 0 | 7 | 2024-09-29 | 21.2 | 0 | 3.2 | 2023-09-29 | 19.7 | 0 | 1.7 | 2022-09-29 | 11.1 | 6.9 | 0 | 2021-09-29 | 13.3 | 4.7 | 0 | 2020-09-29 | 17.8 | 0.2 | 0 | 2019-09-29 | 12.8 | 5.2 | 0 | 2018-09-29 | 12.3 | 5.7 | 0 | 2017-09-29 | 13.8 | 4.2 | 0 | 2016-09-29 | 17.4 | 0.6 | 0 | 2.75 | 1.19
2025-09-29 | 26.5 | 0 | 8.5 | 2024-09-29 | 22.1 | 0 | 4.1 | 2023-09-29 | 20 | 0 | 2 | 2022-09-29 | 12 | 6 | 0 | 2021-09-29 | 12.8 | 5.2 | 0 | 2020-09-29 | 17.4 | 0.6 | 0 | 2019-09-29 | 14.3 | 3.7 | 0 | 2018-09-29 | 13.6 | 4.4 | 0 | 2017-09-29 | 14.6 | 3.4 | 0 | 2016-09-29 | 17.2 | 0.8 | 0 | 2.41 | 1.46
2025-09-29 | 26.9 | 0 | 8.9 | 2024-09-29 | 23.1 | 0 | 5.1 | 2023-09-29 | 20.6 | 0 | 2.6 | 2022-09-29 | 12.9 | 5.1 | 0 | 2021-09-29 | 12.8 | 5.2 | 0 | 2020-09-29 | 17.3 | 0.7 | 0 | 2019-09-29 | 14.5 | 3.5 | 0 | 2018-09-29 | 13.8 | 4.2 | 0 | 2017-09-29 | 14.1 | 3.9 | 0 | 2016-09-29 | 18 | 0 | 0 | 2.26 | 1.66
2025-09-29 | 26.1 | 0 | 8.1 | 2024-09-29 | 23.1 | 0 | 5.1 | 2023-09-29 | 21.7 | 0 | 3.7 | 2022-09-29 | 13.4 | 4.6 | 0 | 2021-09-29 | 13.3 | 4.7 | 0 | 2020-09-29 | 16.9 | 1.1 | 0 | 2019-09-29 | 14.1 | 3.9 | 0 | 2018-09-29 | 13.4 | 4.6 | 0 | 2017-09-29 | 13.9 | 4.1 | 0 | 2016-09-29 | 17.6 | 0.4 | 0 | 2.34 | 1.69
2025-09-29 | 26.1 | 0 | 8.1 | 2024-09-29 | 23.2 | 0 | 5.2 | 2023-09-29 | 20.1 | 0 | 2.1 | 2022-09-29 | 13.2 | 4.8 | 0 | 2021-09-29 | 13.4 | 4.6 | 0 | 2020-09-29 | 16.3 | 1.7 | 0 | 2019-09-29 | 13.3 | 4.7 | 0 | 2018-09-29 | 13.4 | 4.6 | 0 | 2017-09-29 | 13.2 | 4.8 | 0 | 2016-09-29 | 17.7 | 0.3 | 0 | 2.55 | 1.54
2025-09-29 | 24.6 | 0 | 6.6 | 2024-09-29 | 21.7 | 0 | 3.7 | 2023-09-29 | 19.1 | 0 | 1.1 | 2022-09-29 | 12.2 | 5.8 | 0 | 2021-09-29 | 13.1 | 4.9 | 0 | 2020-09-29 | 15.8 | 2.2 | 0 | 2019-09-29 | 12.4 | 5.6 | 0 | 2018-09-29 | 13 | 5 | 0 | 2017-09-29 | 12.7 | 5.3 | 0 | 2016-09-29 | 15.7 | 2.3 | 0 | 3.11 | 1.14
2025-09-29 | 22.1 | 0 | 4.1 | 2024-09-29 | 18.9 | 0 | 0.9 | 2023-09-29 | 16.4 | 1.6 | 0 | 2022-09-29 | 9.8 | 8.2 | 0 | 2021-09-29 | 11.3 | 6.7 | 0 | 2020-09-29 | 15.5 | 2.5 | 0 | 2019-09-29 | 11.3 | 6.7 | 0 | 2018-09-29 | 10.5 | 7.5 | 0 | 2017-09-29 | 11.5 | 6.5 | 0 | 2016-09-29 | 14.9 | 3.1 | 0 | 4.28 | 0.5
2025-09-29 | 20 | 0 | 2 | 2024-09-29 | 15.8 | 2.2 | 0 | 2023-09-29 | 15.9 | 2.1 | 0 | 2022-09-29 | 8.6 | 9.4 | 0 | 2021-09-29 | 10.4 | 7.6 | 0 | 2020-09-29 | 15.1 | 2.9 | 0 | 2019-09-29 | 10.5 | 7.5 | 0 | 2018-09-29 | 10.7 | 7.3 | 0 | 2017-09-29 | 10.3 | 7.7 | 0 | 2016-09-29 | 14.4 | 3.6 | 0 | 5.03 | 0.2
2025-09-29 | 18.8 | 0 | 0.8 | 2024-09-29 | 16.5 | 1.5 | 0 | 2023-09-29 | 15.9 | 2.1 | 0 | 2022-09-29 | 7.1 | 10.9 | 0 | 2021-09-29 | 10.5 | 7.5 | 0 | 2020-09-29 | 14.3 | 3.7 | 0 | 2019-09-29 | 9.9 | 8.1 | 0 | 2018-09-29 | 10.4 | 7.6 | 0 | 2017-09-29 | 9.6 | 8.4 | 0 | 2016-09-29 | 13.8 | 4.2 | 0 | 5.4 | 0.08
2025-09-29 | 16.7 | 1.3 | 0 | 2024-09-29 | 15.5 | 2.5 | 0 | 2023-09-29 | 15.7 | 2.3 | 0 | 2022-09-29 | 5.6 | 12.4 | 0 | 2021-09-29 | 10.9 | 7.1 | 0 | 2020-09-29 | 13.4 | 4.6 | 0 | 2019-09-29 | 9.2 | 8.8 | 0 | 2018-09-29 | 9.6 | 8.4 | 0 | 2017-09-29 | 9 | 9 | 0 | 2016-09-29 | 13.3 | 4.7 | 0 | 6.11 | 0
2025-09-29 | 15.4 | 2.6 | 0 | 2024-09-29 | 14.3 | 3.7 | 0 | 2023-09-29 | 15 | 3 | 0 | 2022-09-29 | 5.7 | 12.3 | 0 | 2021-09-29 | 10.8 | 7.2 | 0 | 2020-09-29 | 12.8 | 5.2 | 0 | 2019-09-29 | 8.7 | 9.3 | 0 | 2018-09-29 | 7.6 | 10.4 | 0 | 2017-09-29 | 8.9 | 9.1 | 0 | 2016-09-29 | 12.5 | 5.5 | 0 | 6.83 | 0
2025-09-29 | 15.1 | 2.9 | 0 | 2024-09-29 | 14.7 | 3.3 | 0 | 2023-09-29 | 14.4 | 3.6 | 0 | 2022-09-29 | 4.4 | 13.6 | 0 | 2021-09-29 | 10.5 | 7.5 | 0 | 2020-09-29 | 12.7 | 5.3 | 0 | 2019-09-29 | 8.6 | 9.4 | 0 | 2018-09-29 | 6.8 | 11.2 | 0 | 2017-09-29 | 8.9 | 9.1 | 0 | 2016-09-29 | 12.2 | 5.8 | 0 | 7.17 | 0
2025-09-30 | 14.2 | 3.8 | 0 | 2024-09-30 | 15.8 | 2.2 | 0 | 2023-09-30 | 12.2 | 5.8 | 0 | 2022-09-30 | 4 | 14 | 0 | 2021-09-30 | 10 | 8 | 0 | 2020-09-30 | 12.7 | 5.3 | 0 | 2019-09-30 | 8.5 | 9.5 | 0 | 2018-09-30 | 5.7 | 12.3 | 0 | 2017-09-30 | 8.7 | 9.3 | 0 | 2016-09-30 | 12.1 | 5.9 | 0 | 7.61 | 0
2025-09-30 | 14.9 | 3.1 | 0 | 2024-09-30 | 15.2 | 2.8 | 0 | 2023-09-30 | 12 | 6 | 0 | 2022-09-30 | 5.1 | 12.9 | 0 | 2021-09-30 | 9.9 | 8.1 | 0 | 2020-09-30 | 12.5 | 5.5 | 0 | 2019-09-30 | 7.5 | 10.5 | 0 | 2018-09-30 | 6 | 12 | 0 | 2017-09-30 | 8.9 | 9.1 | 0 | 2016-09-30 | 11.8 | 6.2 | 0 | 7.62 | 0
2025-09-30 | 15 | 3 | 0 | 2024-09-30 | 14.7 | 3.3 | 0 | 2023-09-30 | 12.6 | 5.4 | 0 | 2022-09-30 | 4.2 | 13.8 | 0 | 2021-09-30 | 8.9 | 9.1 | 0 | 2020-09-30 | 12.4 | 5.6 | 0 | 2019-09-30 | 7.6 | 10.4 | 0 | 2018-09-30 | 6.2 | 11.8 | 0 | 2017-09-30 | 8.8 | 9.2 | 0 | 2016-09-30 | 11.5 | 6.5 | 0 | 7.81 | 0
2025-09-30 | 15 | 3 | 0 | 2024-09-30 | 14.1 | 3.9 | 0 | 2023-09-30 | 12.8 | 5.2 | 0 | 2022-09-30 | 3.3 | 14.7 | 0 | 2021-09-30 | 8.1 | 9.9 | 0 | 2020-09-30 | 12 | 6 | 0 | 2019-09-30 | 7.1 | 10.9 | 0 | 2018-09-30 | 6.1 | 11.9 | 0 | 2017-09-30 | 8.6 | 9.4 | 0 | 2016-09-30 | 11 | 7 | 0 | 8.19 | 0
2025-09-30 | 14.7 | 3.3 | 0 | 2024-09-30 | 13.3 | 4.7 | 0 | 2023-09-30 | 13.1 | 4.9 | 0 | 2022-09-30 | 3.7 | 14.3 | 0 | 2021-09-30 | 7 | 11 | 0 | 2020-09-30 | 11.7 | 6.3 | 0 | 2019-09-30 | 6.4 | 11.6 | 0 | 2018-09-30 | 5.9 | 12.1 | 0 | 2017-09-30 | 8.6 | 9.4 | 0 | 2016-09-30 | 10.8 | 7.2 | 0 | 8.48 | 0
2025-09-30 | 14 | 4 | 0 | 2024-09-30 | 12.4 | 5.6 | 0 | 2023-09-30 | 12.7 | 5.3 | 0 | 2022-09-30 | 2.2 | 15.8 | 0 | 2021-09-30 | 7.1 | 10.9 | 0 | 2020-09-30 | 11.6 | 6.4 | 0 | 2019-09-30 | 5.9 | 12.1 | 0 | 2018-09-30 | 4.8 | 13.2 | 0 | 2017-09-30 | 8.4 | 9.6 | 0 | 2016-09-30 | 10.5 | 7.5 | 0 | 9.04 | 0
2025-09-30 | 13.1 | 4.9 | 0 | 2024-09-30 | 11.9 | 6.1 | 0 | 2023-09-30 | 13.5 | 4.5 | 0 | 2022-09-30 | 3.3 | 14.7 | 0 | 2021-09-30 | 7.2 | 10.8 | 0 | 2020-09-30 | 11.4 | 6.6 | 0 | 2019-09-30 | 5.8 | 12.2 | 0 | 2018-09-30 | 5.5 | 12.5 | 0 | 2017-09-30 | 8.1 | 9.9 | 0 | 2016-09-30 | 10.4 | 7.6 | 0 | 8.98 | 0
2025-09-30 | 13.4 | 4.6 | 0 | 2024-09-30 | 13 | 5 | 0 | 2023-09-30 | 13.8 | 4.2 | 0 | 2022-09-30 | 4.2 | 13.8 | 0 | 2021-09-30 | 8.8 | 9.2 | 0 | 2020-09-30 | 10.7 | 7.3 | 0 | 2019-09-30 | 5.9 | 12.1 | 0 | 2018-09-30 | 6.3 | 11.7 | 0 | 2017-09-30 | 8 | 10 | 0 | 2016-09-30 | 10.4 | 7.6 | 0 | 8.55 | 0
2025-09-30 | 16.3 | 1.7 | 0 | 2024-09-30 | 14.7 | 3.3 | 0 | 2023-09-30 | 16.4 | 1.6 | 0 | 2022-09-30 | 8 | 10 | 0 | 2021-09-30 | 10.3 | 7.7 | 0 | 2020-09-30 | 11.2 | 6.8 | 0 | 2019-09-30 | 6.8 | 11.2 | 0 | 2018-09-30 | 7 | 11 | 0 | 2017-09-30 | 9.4 | 8.6 | 0 | 2016-09-30 | 11 | 7 | 0 | 6.89 | 0
2025-09-30 | 17.6 | 0.4 | 0 | 2024-09-30 | 16.5 | 1.5 | 0 | 2023-09-30 | 18.3 | 0 | 0.3 | 2022-09-30 | 10.7 | 7.3 | 0 | 2021-09-30 | 11.8 | 6.2 | 0 | 2020-09-30 | 11.2 | 6.8 | 0 | 2019-09-30 | 8.1 | 9.9 | 0 | 2018-09-30 | 7.6 | 10.4 | 0 | 2017-09-30 | 11 | 7 | 0 | 2016-09-30 | 12.3 | 5.7 | 0 | 5.52 | 0.03
2025-09-30 | 18.6 | 0 | 0.6 | 2024-09-30 | 18.2 | 0 | 0.2 | 2023-09-30 | 20.3 | 0 | 2.3 | 2022-09-30 | 13.2 | 4.8 | 0 | 2021-09-30 | 13.2 | 4.8 | 0 | 2020-09-30 | 11.6 | 6.4 | 0 | 2019-09-30 | 9.7 | 8.3 | 0 | 2018-09-30 | 8.7 | 9.3 | 0 | 2017-09-30 | 12.1 | 5.9 | 0 | 2016-09-30 | 14 | 4 | 0 | 4.35 | 0.31
2025-09-30 | 18.9 | 0 | 0.9 | 2024-09-30 | 19.6 | 0 | 1.6 | 2023-09-30 | 20.8 | 0 | 2.8 | 2022-09-30 | 14.4 | 3.6 | 0 | 2021-09-30 | 14.3 | 3.7 | 0 | 2020-09-30 | 12.5 | 5.5 | 0 | 2019-09-30 | 11.5 | 6.5 | 0 | 2018-09-30 | 9.8 | 8.2 | 0 | 2017-09-30 | 13.8 | 4.2 | 0 | 2016-09-30 | 15.1 | 2.9 | 0 | 3.46 | 0.53
2025-09-30 | 20.3 | 0 | 2.3 | 2024-09-30 | 21.2 | 0 | 3.2 | 2023-09-30 | 22 | 0 | 4 | 2022-09-30 | 16 | 2 | 0 | 2021-09-30 | 15.3 | 2.7 | 0 | 2020-09-30 | 14.8 | 3.2 | 0 | 2019-09-30 | 13 | 5 | 0 | 2018-09-30 | 10.3 | 7.7 | 0 | 2017-09-30 | 12.8 | 5.2 | 0 | 2016-09-30 | 17.4 | 0.6 | 0 | 2.64 | 0.95
2025-09-30 | 20.2 | 0 | 2.2 | 2024-09-30 | 22.7 | 0 | 4.7 | 2023-09-30 | 22.6 | 0 | 4.6 | 2022-09-30 | 16.5 | 1.5 | 0 | 2021-09-30 | 16.2 | 1.8 | 0 | 2020-09-30 | 15.8 | 2.2 | 0 | 2019-09-30 | 14.2 | 3.8 | 0 | 2018-09-30 | 10.9 | 7.1 | 0 | 2017-09-30 | 13.6 | 4.4 | 0 | 2016-09-30 | 18.4 | 0 | 0.4 | 2.08 | 1.19
2025-09-30 | 20.2 | 0 | 2.2 | 2024-09-30 | 22.5 | 0 | 4.5 | 2023-09-30 | 23.9 | 0 | 5.9 | 2022-09-30 | 17.8 | 0.2 | 0 | 2021-09-30 | 15.2 | 2.8 | 0 | 2020-09-30 | 13 | 5 | 0 | 2019-09-30 | 14.5 | 3.5 | 0 | 2018-09-30 | 10.9 | 7.1 | 0 | 2017-09-30 | 14.3 | 3.7 | 0 | 2016-09-30 | 17.1 | 0.9 | 0 | 2.32 | 1.26
2025-09-30 | 19.4 | 0 | 1.4 | 2024-09-30 | 23 | 0 | 5 | 2023-09-30 | 23.6 | 0 | 5.6 | 2022-09-30 | 18.3 | 0 | 0.3 | 2021-09-30 | 15.1 | 2.9 | 0 | 2020-09-30 | 15.7 | 2.3 | 0 | 2019-09-30 | 14.9 | 3.1 | 0 | 2018-09-30 | 10.3 | 7.7 | 0 | 2017-09-30 | 13.9 | 4.1 | 0 | 2016-09-30 | 16.4 | 1.6 | 0 | 2.17 | 1.23
2025-09-30 | 18.7 | 0 | 0.7 | 2024-09-30 | 22.6 | 0 | 4.6 | 2023-09-30 | 23.4 | 0 | 5.4 | 2022-09-30 | 17.5 | 0.5 | 0 | 2021-09-30 | 15.7 | 2.3 | 0 | 2020-09-30 | 15.4 | 2.6 | 0 | 2019-09-30 | 14.5 | 3.5 | 0 | 2018-09-30 | 9.9 | 8.1 | 0 | 2017-09-30 | 14 | 4 | 0 | 2016-09-30 | 15.9 | 2.1 | 0 | 2.31 | 1.07
2025-09-30 | 17.3 | 0.7 | 0 | 2024-09-30 | 21.2 | 0 | 3.2 | 2023-09-30 | 22.3 | 0 | 4.3 | 2022-09-30 | 16.4 | 1.6 | 0 | 2021-09-30 | 14.5 | 3.5 | 0 | 2020-09-30 | 13.4 | 4.6 | 0 | 2019-09-30 | 13.9 | 4.1 | 0 | 2018-09-30 | 9.5 | 8.5 | 0 | 2017-09-30 | 12.9 | 5.1 | 0 | 2016-09-30 | 15.5 | 2.5 | 0 | 3.06 | 0.75
2025-09-30 | 15.7 | 2.3 | 0 | 2024-09-30 | 18.8 | 0 | 0.8 | 2023-09-30 | 19.1 | 0 | 1.1 | 2022-09-30 | 13.4 | 4.6 | 0 | 2021-09-30 | 11.1 | 6.9 | 0 | 2020-09-30 | 10.9 | 7.1 | 0 | 2019-09-30 | 12.7 | 5.3 | 0 | 2018-09-30 | 8.9 | 9.1 | 0 | 2017-09-30 | 11 | 7 | 0 | 2016-09-30 | 14.7 | 3.3 | 0 | 4.56 | 0.19
2025-09-30 | 14.5 | 3.5 | 0 | 2024-09-30 | 15.5 | 2.5 | 0 | 2023-09-30 | 16.8 | 1.2 | 0 | 2022-09-30 | 10.8 | 7.2 | 0 | 2021-09-30 | 10.3 | 7.7 | 0 | 2020-09-30 | 10.2 | 7.8 | 0 | 2019-09-30 | 11.8 | 6.2 | 0 | 2018-09-30 | 8.5 | 9.5 | 0 | 2017-09-30 | 8.8 | 9.2 | 0 | 2016-09-30 | 13.6 | 4.4 | 0 | 5.92 | 0
2025-09-30 | 13.6 | 4.4 | 0 | 2024-09-30 | 16.5 | 1.5 | 0 | 2023-09-30 | 14.2 | 3.8 | 0 | 2022-09-30 | 9.9 | 8.1 | 0 | 2021-09-30 | 10.1 | 7.9 | 0 | 2020-09-30 | 11.7 | 6.3 | 0 | 2019-09-30 | 11.3 | 6.7 | 0 | 2018-09-30 | 8.5 | 9.5 | 0 | 2017-09-30 | 7.5 | 10.5 | 0 | 2016-09-30 | 13.2 | 4.8 | 0 | 6.35 | 0
2025-09-30 | 12.2 | 5.8 | 0 | 2024-09-30 | 16.2 | 1.8 | 0 | 2023-09-30 | 14.9 | 3.1 | 0 | 2022-09-30 | 9.3 | 8.7 | 0 | 2021-09-30 | 10.3 | 7.7 | 0 | 2020-09-30 | 11.2 | 6.8 | 0 | 2019-09-30 | 10.8 | 7.2 | 0 | 2018-09-30 | 8.3 | 9.7 | 0 | 2017-09-30 | 6.7 | 11.3 | 0 | 2016-09-30 | 13.3 | 4.7 | 0 | 6.68 | 0
2025-09-30 | 10.8 | 7.2 | 0 | 2024-09-30 | 14.5 | 3.5 | 0 | 2023-09-30 | 13.9 | 4.1 | 0 | 2022-09-30 | 10.7 | 7.3 | 0 | 2021-09-30 | 7 | 11 | 0 | 2020-09-30 | 10.9 | 7.1 | 0 | 2019-09-30 | 9.2 | 8.8 | 0 | 2018-09-30 | 7.8 | 10.2 | 0 | 2017-09-30 | 5.2 | 12.8 | 0 | 2016-09-30 | 13.2 | 4.8 | 0 | 7.68 | 0
2025-09-30 | 9.7 | 8.3 | 0 | 2024-09-30 | 14.5 | 3.5 | 0 | 2023-09-30 | 14 | 4 | 0 | 2022-09-30 | 9.1 | 8.9 | 0 | 2021-09-30 | 8.9 | 9.1 | 0 | 2020-09-30 | 11.3 | 6.7 | 0 | 2019-09-30 | 8.4 | 9.6 | 0 | 2018-09-30 | 7.4 | 10.6 | 0 | 2017-09-30 | 4.6 | 13.4 | 0 | 2016-09-30 | 12.7 | 5.3 | 0 | 7.94 | 0
2025-10-01 | 7.3 | 10.7 | 0 | 2024-10-01 | 13.4 | 4.6 | 0 | 2023-10-01 | 12.7 | 5.3 | 0 | 2022-10-01 | 8.8 | 9.2 | 0 | 2021-10-01 | 7.3 | 10.7 | 0 | 2020-10-01 | 10.9 | 7.1 | 0 | 2019-10-01 | 8 | 10 | 0 | 2018-10-01 | 7.2 | 10.8 | 0 | 2017-10-01 | 3.7 | 14.3 | 0 | 2016-10-01 | 12.6 | 5.4 | 0 | 8.81 | 0
2025-10-01 | 9 | 9 | 0 | 2024-10-01 | 13 | 5 | 0 | 2023-10-01 | 12.4 | 5.6 | 0 | 2022-10-01 | 7.9 | 10.1 | 0 | 2021-10-01 | 7.2 | 10.8 | 0 | 2020-10-01 | 10.8 | 7.2 | 0 | 2019-10-01 | 8.1 | 9.9 | 0 | 2018-10-01 | 7.2 | 10.8 | 0 | 2017-10-01 | 3.9 | 14.1 | 0 | 2016-10-01 | 12.3 | 5.7 | 0 | 8.82 | 0
2025-10-01 | 8.5 | 9.5 | 0 | 2024-10-01 | 12.3 | 5.7 | 0 | 2023-10-01 | 13 | 5 | 0 | 2022-10-01 | 8 | 10 | 0 | 2021-10-01 | 6 | 12 | 0 | 2020-10-01 | 9.9 | 8.1 | 0 | 2019-10-01 | 8.2 | 9.8 | 0 | 2018-10-01 | 6.8 | 11.2 | 0 | 2017-10-01 | 2.4 | 15.6 | 0 | 2016-10-01 | 12.3 | 5.7 | 0 | 9.26 | 0
2025-10-01 | 7.7 | 10.3 | 0 | 2024-10-01 | 12.4 | 5.6 | 0 | 2023-10-01 | 11.6 | 6.4 | 0 | 2022-10-01 | 6.2 | 11.8 | 0 | 2021-10-01 | 5.1 | 12.9 | 0 | 2020-10-01 | 10.1 | 7.9 | 0 | 2019-10-01 | 8.2 | 9.8 | 0 | 2018-10-01 | 6.7 | 11.3 | 0 | 2017-10-01 | 2.8 | 15.2 | 0 | 2016-10-01 | 11.6 | 6.4 | 0 | 9.76 | 0
2025-10-01 | 6.7 | 11.3 | 0 | 2024-10-01 | 12.1 | 5.9 | 0 | 2023-10-01 | 12.3 | 5.7 | 0 | 2022-10-01 | 6.9 | 11.1 | 0 | 2021-10-01 | 5.7 | 12.3 | 0 | 2020-10-01 | 10 | 8 | 0 | 2019-10-01 | 8.2 | 9.8 | 0 | 2018-10-01 | 6.9 | 11.1 | 0 | 2017-10-01 | 3.4 | 14.6 | 0 | 2016-10-01 | 11.6 | 6.4 | 0 | 9.62 | 0
2025-10-01 | 6.1 | 11.9 | 0 | 2024-10-01 | 11.4 | 6.6 | 0 | 2023-10-01 | 11.9 | 6.1 | 0 | 2022-10-01 | 6.7 | 11.3 | 0 | 2021-10-01 | 5.4 | 12.6 | 0 | 2020-10-01 | 9.6 | 8.4 | 0 | 2019-10-01 | 8.2 | 9.8 | 0 | 2018-10-01 | 7 | 11 | 0 | 2017-10-01 | 3.2 | 14.8 | 0 | 2016-10-01 | 11 | 7 | 0 | 9.95 | 0
2025-10-01 | 6.2 | 11.8 | 0 | 2024-10-01 | 10.8 | 7.2 | 0 | 2023-10-01 | 13.2 | 4.8 | 0 | 2022-10-01 | 7.2 | 10.8 | 0 | 2021-10-01 | 7 | 11 | 0 | 2020-10-01 | 9.7 | 8.3 | 0 | 2019-10-01 | 8.5 | 9.5 | 0 | 2018-10-01 | 6.7 | 11.3 | 0 | 2017-10-01 | 3.1 | 14.9 | 0 | 2016-10-01 | 10.9 | 7.1 | 0 | 9.67 | 0
2025-10-01 | 7.2 | 10.8 | 0 | 2024-10-01 | 11.6 | 6.4 | 0 | 2023-10-01 | 13.3 | 4.7 | 0 | 2022-10-01 | 6.2 | 11.8 | 0 | 2021-10-01 | 7.2 | 10.8 | 0 | 2020-10-01 | 9.9 | 8.1 | 0 | 2019-10-01 | 8.3 | 9.7 | 0 | 2018-10-01 | 6.9 | 11.1 | 0 | 2017-10-01 | 3.5 | 14.5 | 0 | 2016-10-01 | 11.5 | 6.5 | 0 | 9.44 | 0
2025-10-01 | 9.2 | 8.8 | 0 | 2024-10-01 | 12.5 | 5.5 | 0 | 2023-10-01 | 16.5 | 1.5 | 0 | 2022-10-01 | 9.4 | 8.6 | 0 | 2021-10-01 | 8.4 | 9.6 | 0 | 2020-10-01 | 10.7 | 7.3 | 0 | 2019-10-01 | 8.8 | 9.2 | 0 | 2018-10-01 | 7.5 | 10.5 | 0 | 2017-10-01 | 8.3 | 9.7 | 0 | 2016-10-01 | 12.4 | 5.6 | 0 | 7.63 | 0
2025-10-01 | 10.4 | 7.6 | 0 | 2024-10-01 | 16.2 | 1.8 | 0 | 2023-10-01 | 19.7 | 0 | 1.7 | 2022-10-01 | 11.6 | 6.4 | 0 | 2021-10-01 | 8.1 | 9.9 | 0 | 2020-10-01 | 11.9 | 6.1 | 0 | 2019-10-01 | 9.3 | 8.7 | 0 | 2018-10-01 | 8 | 10 | 0 | 2017-10-01 | 11 | 7 | 0 | 2016-10-01 | 13.1 | 4.9 | 0 | 6.24 | 0.17
2025-10-01 | 12.1 | 5.9 | 0 | 2024-10-01 | 18.3 | 0 | 0.3 | 2023-10-01 | 21.6 | 0 | 3.6 | 2022-10-01 | 13.6 | 4.4 | 0 | 2021-10-01 | 11.1 | 6.9 | 0 | 2020-10-01 | 14.4 | 3.6 | 0 | 2019-10-01 | 10.1 | 7.9 | 0 | 2018-10-01 | 8.1 | 9.9 | 0 | 2017-10-01 | 13.1 | 4.9 | 0 | 2016-10-01 | 14.3 | 3.7 | 0 | 4.72 | 0.39
2025-10-01 | 12.8 | 5.2 | 0 | 2024-10-01 | 20.7 | 0 | 2.7 | 2023-10-01 | 23 | 0 | 5 | 2022-10-01 | 16 | 2 | 0 | 2021-10-01 | 14.3 | 3.7 | 0 | 2020-10-01 | 15.3 | 2.7 | 0 | 2019-10-01 | 10.5 | 7.5 | 0 | 2018-10-01 | 9.5 | 8.5 | 0 | 2017-10-01 | 14.8 | 3.2 | 0 | 2016-10-01 | 15.5 | 2.5 | 0 | 3.53 | 0.77
2025-10-01 | 15.4 | 2.6 | 0 | 2024-10-01 | 21.8 | 0 | 3.8 | 2023-10-01 | 24.3 | 0 | 6.3 | 2022-10-01 | 17.6 | 0.4 | 0 | 2021-10-01 | 15.4 | 2.6 | 0 | 2020-10-01 | 15.2 | 2.8 | 0 | 2019-10-01 | 11.9 | 6.1 | 0 | 2018-10-01 | 10.8 | 7.2 | 0 | 2017-10-01 | 16.2 | 1.8 | 0 | 2016-10-01 | 16.4 | 1.6 | 0 | 2.51 | 1.01
2025-10-01 | 15.6 | 2.4 | 0 | 2024-10-01 | 22.4 | 0 | 4.4 | 2023-10-01 | 24.6 | 0 | 6.6 | 2022-10-01 | 18.4 | 0 | 0.4 | 2021-10-01 | 15.6 | 2.4 | 0 | 2020-10-01 | 15.7 | 2.3 | 0 | 2019-10-01 | 13.2 | 4.8 | 0 | 2018-10-01 | 11.7 | 6.3 | 0 | 2017-10-01 | 17.1 | 0.9 | 0 | 2016-10-01 | 16.7 | 1.3 | 0 | 2.04 | 1.14
2025-10-01 | 17.5 | 0.5 | 0 | 2024-10-01 | 22 | 0 | 4 | 2023-10-01 | 25 | 0 | 7 | 2022-10-01 | 17.8 | 0.2 | 0 | 2021-10-01 | 16.1 | 1.9 | 0 | 2020-10-01 | 17.2 | 0.8 | 0 | 2019-10-01 | 13.2 | 4.8 | 0 | 2018-10-01 | 12.5 | 5.5 | 0 | 2017-10-01 | 17.3 | 0.7 | 0 | 2016-10-01 | 17.3 | 0.7 | 0 | 1.51 | 1.1
2025-10-01 | 17.4 | 0.6 | 0 | 2024-10-01 | 22.1 | 0 | 4.1 | 2023-10-01 | 24 | 0 | 6 | 2022-10-01 | 17.4 | 0.6 | 0 | 2021-10-01 | 15.9 | 2.1 | 0 | 2020-10-01 | 14.1 | 3.9 | 0 | 2019-10-01 | 12.9 | 5.1 | 0 | 2018-10-01 | 12.5 | 5.5 | 0 | 2017-10-01 | 17.9 | 0.1 | 0 | 2016-10-01 | 16.5 | 1.5 | 0 | 1.94 | 1.01
2025-10-01 | 16.8 | 1.2 | 0 | 2024-10-01 | 21.6 | 0 | 3.6 | 2023-10-01 | 23.1 | 0 | 5.1 | 2022-10-01 | 16.4 | 1.6 | 0 | 2021-10-01 | 14.9 | 3.1 | 0 | 2020-10-01 | 16.2 | 1.8 | 0 | 2019-10-01 | 13.2 | 4.8 | 0 | 2018-10-01 | 12.3 | 5.7 | 0 | 2017-10-01 | 17.6 | 0.4 | 0 | 2016-10-01 | 15.9 | 2.1 | 0 | 2.07 | 0.87
2025-10-01 | 15.7 | 2.3 | 0 | 2024-10-01 | 21.1 | 0 | 3.1 | 2023-10-01 | 21.5 | 0 | 3.5 | 2022-10-01 | 15 | 3 | 0 | 2021-10-01 | 14.9 | 3.1 | 0 | 2020-10-01 | 14.6 | 3.4 | 0 | 2019-10-01 | 13.6 | 4.4 | 0 | 2018-10-01 | 11.2 | 6.8 | 0 | 2017-10-01 | 16.4 | 1.6 | 0 | 2016-10-01 | 15.6 | 2.4 | 0 | 2.7 | 0.66
2025-10-01 | 13.6 | 4.4 | 0 | 2024-10-01 | 17.5 | 0.5 | 0 | 2023-10-01 | 20.7 | 0 | 2.7 | 2022-10-01 | 13 | 5 | 0 | 2021-10-01 | 14.1 | 3.9 | 0 | 2020-10-01 | 11.6 | 6.4 | 0 | 2019-10-01 | 14.3 | 3.7 | 0 | 2018-10-01 | 10.4 | 7.6 | 0 | 2017-10-01 | 13.5 | 4.5 | 0 | 2016-10-01 | 15.1 | 2.9 | 0 | 3.89 | 0.27
2025-10-01 | 12 | 6 | 0 | 2024-10-01 | 16.9 | 1.1 | 0 | 2023-10-01 | 20.1 | 0 | 2.1 | 2022-10-01 | 12.1 | 5.9 | 0 | 2021-10-01 | 10.3 | 7.7 | 0 | 2020-10-01 | 11.6 | 6.4 | 0 | 2019-10-01 | 14.8 | 3.2 | 0 | 2018-10-01 | 9.6 | 8.4 | 0 | 2017-10-01 | 10.3 | 7.7 | 0 | 2016-10-01 | 15 | 3 | 0 | 4.94 | 0.21
2025-10-01 | 11.5 | 6.5 | 0 | 2024-10-01 | 15 | 3 | 0 | 2023-10-01 | 18.6 | 0 | 0.6 | 2022-10-01 | 12.1 | 5.9 | 0 | 2021-10-01 | 11.2 | 6.8 | 0 | 2020-10-01 | 9.6 | 8.4 | 0 | 2019-10-01 | 15 | 3 | 0 | 2018-10-01 | 9.3 | 8.7 | 0 | 2017-10-01 | 8.6 | 9.4 | 0 | 2016-10-01 | 14.6 | 3.4 | 0 | 5.51 | 0.06
2025-10-01 | 11 | 7 | 0 | 2024-10-01 | 14.9 | 3.1 | 0 | 2023-10-01 | 17.6 | 0.4 | 0 | 2022-10-01 | 11.8 | 6.2 | 0 | 2021-10-01 | 11.4 | 6.6 | 0 | 2020-10-01 | 9.7 | 8.3 | 0 | 2019-10-01 | 15.5 | 2.5 | 0 | 2018-10-01 | 9.7 | 8.3 | 0 | 2017-10-01 | 7.4 | 10.6 | 0 | 2016-10-01 | 14 | 4 | 0 | 5.7 | 0
2025-10-01 | 9.8 | 8.2 | 0 | 2024-10-01 | 15.2 | 2.8 | 0 | 2023-10-01 | 16.8 | 1.2 | 0 | 2022-10-01 | 10.3 | 7.7 | 0 | 2021-10-01 | 11 | 7 | 0 | 2020-10-01 | 8.8 | 9.2 | 0 | 2019-10-01 | 17.3 | 0.7 | 0 | 2018-10-01 | 9.4 | 8.6 | 0 | 2017-10-01 | 8.5 | 9.5 | 0 | 2016-10-01 | 13.5 | 4.5 | 0 | 5.94 | 0
2025-10-01 | 6 | 12 | 0 | 2024-10-01 | 15.1 | 2.9 | 0 | 2023-10-01 | 16.3 | 1.7 | 0 | 2022-10-01 | 8.9 | 9.1 | 0 | 2021-10-01 | 10.6 | 7.4 | 0 | 2020-10-01 | 9 | 9 | 0 | 2019-10-01 | 16.7 | 1.3 | 0 | 2018-10-01 | 9.2 | 8.8 | 0 | 2017-10-01 | 7.5 | 10.5 | 0 | 2016-10-01 | 13.3 | 4.7 | 0 | 6.74 | 0
2025-10-02 | 6.4 | 11.6 | 0 | 2024-10-02 | 15.9 | 2.1 | 0 | 2023-10-02 | 15.3 | 2.7 | 0 | 2022-10-02 | 7.5 | 10.5 | 0 | 2021-10-02 | 10.5 | 7.5 | 0 | 2020-10-02 | 9.2 | 8.8 | 0 | 2019-10-02 | 16.9 | 1.1 | 0 | 2018-10-02 | 8.1 | 9.9 | 0 | 2017-10-02 | 7.6 | 10.4 | 0 | 2016-10-02 | 13.1 | 4.9 | 0 | 6.95 | 0
2025-10-02 | 4.8 | 13.2 | 0 | 2024-10-02 | 16 | 2 | 0 | 2023-10-02 | 13.9 | 4.1 | 0 | 2022-10-02 | 6.6 | 11.4 | 0 | 2021-10-02 | 10.8 | 7.2 | 0 | 2020-10-02 | 8.9 | 9.1 | 0 | 2019-10-02 | 16.9 | 1.1 | 0 | 2018-10-02 | 7.5 | 10.5 | 0 | 2017-10-02 | 5.9 | 12.1 | 0 | 2016-10-02 | 12.7 | 5.3 | 0 | 7.6 | 0
2025-10-02 | 2.7 | 15.3 | 0 | 2024-10-02 | 15.6 | 2.4 | 0 | 2023-10-02 | 12.6 | 5.4 | 0 | 2022-10-02 | 5.6 | 12.4 | 0 | 2021-10-02 | 11 | 7 | 0 | 2020-10-02 | 9.3 | 8.7 | 0 | 2019-10-02 | 15.1 | 2.9 | 0 | 2018-10-02 | 7.2 | 10.8 | 0 | 2017-10-02 | 4.2 | 13.8 | 0 | 2016-10-02 | 12.2 | 5.8 | 0 | 8.45 | 0
2025-10-02 | 3.1 | 14.9 | 0 | 2024-10-02 | 15.1 | 2.9 | 0 | 2023-10-02 | 11.3 | 6.7 | 0 | 2022-10-02 | 5 | 13 | 0 | 2021-10-02 | 11.2 | 6.8 | 0 | 2020-10-02 | 8.9 | 9.1 | 0 | 2019-10-02 | 14.4 | 3.6 | 0 | 2018-10-02 | 7.3 | 10.7 | 0 | 2017-10-02 | 5.9 | 12.1 | 0 | 2016-10-02 | 11.9 | 6.1 | 0 | 8.59 | 0
2025-10-02 | 3.2 | 14.8 | 0 | 2024-10-02 | 15.5 | 2.5 | 0 | 2023-10-02 | 11.2 | 6.8 | 0 | 2022-10-02 | 4.2 | 13.8 | 0 | 2021-10-02 | 11.5 | 6.5 | 0 | 2020-10-02 | 8.2 | 9.8 | 0 | 2019-10-02 | 13.4 | 4.6 | 0 | 2018-10-02 | 7 | 11 | 0 | 2017-10-02 | 4.7 | 13.3 | 0 | 2016-10-02 | 11.8 | 6.2 | 0 | 8.93 | 0
2025-10-02 | 2.7 | 15.3 | 0 | 2024-10-02 | 15.4 | 2.6 | 0 | 2023-10-02 | 10.6 | 7.4 | 0 | 2022-10-02 | 3.7 | 14.3 | 0 | 2021-10-02 | 12.1 | 5.9 | 0 | 2020-10-02 | 8 | 10 | 0 | 2019-10-02 | 11.7 | 6.3 | 0 | 2018-10-02 | 6.9 | 11.1 | 0 | 2017-10-02 | 4.6 | 13.4 | 0 | 2016-10-02 | 11.7 | 6.3 | 0 | 9.26 | 0
2025-10-02 | 2.9 | 15.1 | 0 | 2024-10-02 | 14.4 | 3.6 | 0 | 2023-10-02 | 11.4 | 6.6 | 0 | 2022-10-02 | 3.2 | 14.8 | 0 | 2021-10-02 | 11.8 | 6.2 | 0 | 2020-10-02 | 8.7 | 9.3 | 0 | 2019-10-02 | 11 | 7 | 0 | 2018-10-02 | 6.7 | 11.3 | 0 | 2017-10-02 | 6.4 | 11.6 | 0 | 2016-10-02 | 11.8 | 6.2 | 0 | 9.17 | 0
2025-10-02 | 4.8 | 13.2 | 0 | 2024-10-02 | 13.8 | 4.2 | 0 | 2023-10-02 | 11.7 | 6.3 | 0 | 2022-10-02 | 4 | 14 | 0 | 2021-10-02 | 12.3 | 5.7 | 0 | 2020-10-02 | 9.3 | 8.7 | 0 | 2019-10-02 | 10.6 | 7.4 | 0 | 2018-10-02 | 6.9 | 11.1 | 0 | 2017-10-02 | 5.6 | 12.4 | 0 | 2016-10-02 | 12.3 | 5.7 | 0 | 8.87 | 0
2025-10-02 | 7.9 | 10.1 | 0 | 2024-10-02 | 13.3 | 4.7 | 0 | 2023-10-02 | 14.7 | 3.3 | 0 | 2022-10-02 | 5.5 | 12.5 | 0 | 2021-10-02 | 13 | 5 | 0 | 2020-10-02 | 9.9 | 8.1 | 0 | 2019-10-02 | 10.4 | 7.6 | 0 | 2018-10-02 | 7.5 | 10.5 | 0 | 2017-10-02 | 8.6 | 9.4 | 0 | 2016-10-02 | 12.7 | 5.3 | 0 | 7.65 | 0
2025-10-02 | 10.2 | 7.8 | 0 | 2024-10-02 | 12.7 | 5.3 | 0 | 2023-10-02 | 17.7 | 0.3 | 0 | 2022-10-02 | 7.9 | 10.1 | 0 | 2021-10-02 | 13.9 | 4.1 | 0 | 2020-10-02 | 9.7 | 8.3 | 0 | 2019-10-02 | 9.9 | 8.1 | 0 | 2018-10-02 | 7.6 | 10.4 | 0 | 2017-10-02 | 13.7 | 4.3 | 0 | 2016-10-02 | 13.1 | 4.9 | 0 | 6.36 | 0
2025-10-02 | 12.6 | 5.4 | 0 | 2024-10-02 | 12.9 | 5.1 | 0 | 2023-10-02 | 20.2 | 0 | 2.2 | 2022-10-02 | 9.2 | 8.8 | 0 | 2021-10-02 | 14.3 | 3.7 | 0 | 2020-10-02 | 9.3 | 8.7 | 0 | 2019-10-02 | 9.9 | 8.1 | 0 | 2018-10-02 | 8 | 10 | 0 | 2017-10-02 | 16.1 | 1.9 | 0 | 2016-10-02 | 13.8 | 4.2 | 0 | 5.59 | 0.22
2025-10-02 | 14.6 | 3.4 | 0 | 2024-10-02 | 14.2 | 3.8 | 0 | 2023-10-02 | 22.3 | 0 | 4.3 | 2022-10-02 | 10.4 | 7.6 | 0 | 2021-10-02 | 15.2 | 2.8 | 0 | 2020-10-02 | 9.5 | 8.5 | 0 | 2019-10-02 | 11.8 | 6.2 | 0 | 2018-10-02 | 9 | 9 | 0 | 2017-10-02 | 18.6 | 0 | 0.6 | 2016-10-02 | 14.2 | 3.8 | 0 | 4.51 | 0.49
2025-10-02 | 15.8 | 2.2 | 0 | 2024-10-02 | 14 | 4 | 0 | 2023-10-02 | 23.2 | 0 | 5.2 | 2022-10-02 | 11.1 | 6.9 | 0 | 2021-10-02 | 15.4 | 2.6 | 0 | 2020-10-02 | 9.4 | 8.6 | 0 | 2019-10-02 | 11.8 | 6.2 | 0 | 2018-10-02 | 9.2 | 8.8 | 0 | 2017-10-02 | 19 | 0 | 1 | 2016-10-02 | 14.7 | 3.3 | 0 | 4.26 | 0.62
2025-10-02 | 17.2 | 0.8 | 0 | 2024-10-02 | 14.6 | 3.4 | 0 | 2023-10-02 | 23.9 | 0 | 5.9 | 2022-10-02 | 12.6 | 5.4 | 0 | 2021-10-02 | 12.8 | 5.2 | 0 | 2020-10-02 | 10.1 | 7.9 | 0 | 2019-10-02 | 11.8 | 6.2 | 0 | 2018-10-02 | 9.5 | 8.5 | 0 | 2017-10-02 | 19.5 | 0 | 1.5 | 2016-10-02 | 15 | 3 | 0 | 4.04 | 0.74
2025-10-02 | 17.9 | 0.1 | 0 | 2024-10-02 | 14.6 | 3.4 | 0 | 2023-10-02 | 24.6 | 0 | 6.6 | 2022-10-02 | 13.1 | 4.9 | 0 | 2021-10-02 | 12.7 | 5.3 | 0 | 2020-10-02 | 11.1 | 6.9 | 0 | 2019-10-02 | 12.4 | 5.6 | 0 | 2018-10-02 | 9.7 | 8.3 | 0 | 2017-10-02 | 19.6 | 0 | 1.6 | 2016-10-02 | 15.5 | 2.5 | 0 | 3.7 | 0.82
2025-10-02 | 18.2 | 0 | 0.2 | 2024-10-02 | 15.6 | 2.4 | 0 | 2023-10-02 | 24.7 | 0 | 6.7 | 2022-10-02 | 13.2 | 4.8 | 0 | 2021-10-02 | 12.4 | 5.6 | 0 | 2020-10-02 | 11.1 | 6.9 | 0 | 2019-10-02 | 11.1 | 6.9 | 0 | 2018-10-02 | 10 | 8 | 0 | 2017-10-02 | 19.8 | 0 | 1.8 | 2016-10-02 | 15.7 | 2.3 | 0 | 3.69 | 0.87
2025-10-02 | 18.1 | 0 | 0.1 | 2024-10-02 | 15.3 | 2.7 | 0 | 2023-10-02 | 24.5 | 0 | 6.5 | 2022-10-02 | 13 | 5 | 0 | 2021-10-02 | 12.1 | 5.9 | 0 | 2020-10-02 | 10.8 | 7.2 | 0 | 2019-10-02 | 10.5 | 7.5 | 0 | 2018-10-02 | 10 | 8 | 0 | 2017-10-02 | 19.4 | 0 | 1.4 | 2016-10-02 | 14.6 | 3.4 | 0 | 3.97 | 0.8
2025-10-02 | 16.7 | 1.3 | 0 | 2024-10-02 | 15 | 3 | 0 | 2023-10-02 | 22.5 | 0 | 4.5 | 2022-10-02 | 11.4 | 6.6 | 0 | 2021-10-02 | 11.8 | 6.2 | 0 | 2020-10-02 | 10.4 | 7.6 | 0 | 2019-10-02 | 10 | 8 | 0 | 2018-10-02 | 9.9 | 8.1 | 0 | 2017-10-02 | 18 | 0 | 0 | 2016-10-02 | 14.3 | 3.7 | 0 | 4.45 | 0.45
2025-10-02 | 12.8 | 5.2 | 0 | 2024-10-02 | 12.6 | 5.4 | 0 | 2023-10-02 | 20 | 0 | 2 | 2022-10-02 | 10.4 | 7.6 | 0 | 2021-10-02 | 11.6 | 6.4 | 0 | 2020-10-02 | 9.3 | 8.7 | 0 | 2019-10-02 | 8.8 | 9.2 | 0 | 2018-10-02 | 9.7 | 8.3 | 0 | 2017-10-02 | 15.4 | 2.6 | 0 | 2016-10-02 | 14.2 | 3.8 | 0 | 5.72 | 0.2
2025-10-02 | 12.3 | 5.7 | 0 | 2024-10-02 | 11.6 | 6.4 | 0 | 2023-10-02 | 19.6 | 0 | 1.6 | 2022-10-02 | 9.2 | 8.8 | 0 | 2021-10-02 | 11.5 | 6.5 | 0 | 2020-10-02 | 8.9 | 9.1 | 0 | 2019-10-02 | 8.2 | 9.8 | 0 | 2018-10-02 | 9.5 | 8.5 | 0 | 2017-10-02 | 13.4 | 4.6 | 0 | 2016-10-02 | 14.1 | 3.9 | 0 | 6.33 | 0.16
2025-10-02 | 12.4 | 5.6 | 0 | 2024-10-02 | 11.1 | 6.9 | 0 | 2023-10-02 | 18.9 | 0 | 0.9 | 2022-10-02 | 8 | 10 | 0 | 2021-10-02 | 11.3 | 6.7 | 0 | 2020-10-02 | 9.1 | 8.9 | 0 | 2019-10-02 | 7.6 | 10.4 | 0 | 2018-10-02 | 9.3 | 8.7 | 0 | 2017-10-02 | 12 | 6 | 0 | 2016-10-02 | 14.1 | 3.9 | 0 | 6.71 | 0.09
2025-10-02 | 11.1 | 6.9 | 0 | 2024-10-02 | 7.8 | 10.2 | 0 | 2023-10-02 | 18.9 | 0 | 0.9 | 2022-10-02 | 6.5 | 11.5 | 0 | 2021-10-02 | 11.2 | 6.8 | 0 | 2020-10-02 | 7.6 | 10.4 | 0 | 2019-10-02 | 7.3 | 10.7 | 0 | 2018-10-02 | 9.3 | 8.7 | 0 | 2017-10-02 | 10.9 | 7.1 | 0 | 2016-10-02 | 13.8 | 4.2 | 0 | 7.65 | 0.09
2025-10-02 | 10.7 | 7.3 | 0 | 2024-10-02 | 9.4 | 8.6 | 0 | 2023-10-02 | 18.6 | 0 | 0.6 | 2022-10-02 | 5.3 | 12.7 | 0 | 2021-10-02 | 11.2 | 6.8 | 0 | 2020-10-02 | 6.2 | 11.8 | 0 | 2019-10-02 | 6.8 | 11.2 | 0 | 2018-10-02 | 9.5 | 8.5 | 0 | 2017-10-02 | 11.7 | 6.3 | 0 | 2016-10-02 | 13.6 | 4.4 | 0 | 7.76 | 0.06
2025-10-02 | 8.9 | 9.1 | 0 | 2024-10-02 | 8.3 | 9.7 | 0 | 2023-10-02 | 18.6 | 0 | 0.6 | 2022-10-02 | 2.5 | 15.5 | 0 | 2021-10-02 | 11.1 | 6.9 | 0 | 2020-10-02 | 6.6 | 11.4 | 0 | 2019-10-02 | 5.5 | 12.5 | 0 | 2018-10-02 | 9.3 | 8.7 | 0 | 2017-10-02 | 8.9 | 9.1 | 0 | 2016-10-02 | 13.5 | 4.5 | 0 | 8.74 | 0.06
2025-10-03 | 8.9 | 9.1 | 0 | 2024-10-03 | 7.3 | 10.7 | 0 | 2023-10-03 | 17.4 | 0.6 | 0 | 2022-10-03 | 4.3 | 13.7 | 0 | 2021-10-03 | 11 | 7 | 0 | 2020-10-03 | 4.9 | 13.1 | 0 | 2019-10-03 | 5 | 13 | 0 | 2018-10-03 | 9.4 | 8.6 | 0 | 2017-10-03 | 8.6 | 9.4 | 0 | 2016-10-03 | 13.4 | 4.6 | 0 | 8.98 | 0
2025-10-03 | 6.2 | 11.8 | 0 | 2024-10-03 | 5.9 | 12.1 | 0 | 2023-10-03 | 16.2 | 1.8 | 0 | 2022-10-03 | 1.6 | 16.4 | 0 | 2021-10-03 | 11.1 | 6.9 | 0 | 2020-10-03 | 4.9 | 13.1 | 0 | 2019-10-03 | 3.3 | 14.7 | 0 | 2018-10-03 | 9.7 | 8.3 | 0 | 2017-10-03 | 8.6 | 9.4 | 0 | 2016-10-03 | 13.4 | 4.6 | 0 | 9.91 | 0
2025-10-03 | 6.4 | 11.6 | 0 | 2024-10-03 | 7.5 | 10.5 | 0 | 2023-10-03 | 16.2 | 1.8 | 0 | 2022-10-03 | 1.4 | 16.6 | 0 | 2021-10-03 | 11 | 7 | 0 | 2020-10-03 | 4.8 | 13.2 | 0 | 2019-10-03 | 2.9 | 15.1 | 0 | 2018-10-03 | 9.2 | 8.8 | 0 | 2017-10-03 | 7.5 | 10.5 | 0 | 2016-10-03 | 13.6 | 4.4 | 0 | 9.95 | 0
2025-10-03 | 6.7 | 11.3 | 0 | 2024-10-03 | 7.8 | 10.2 | 0 | 2023-10-03 | 15.6 | 2.4 | 0 | 2022-10-03 | 2.5 | 15.5 | 0 | 2021-10-03 | 11 | 7 | 0 | 2020-10-03 | 5 | 13 | 0 | 2019-10-03 | 2.3 | 15.7 | 0 | 2018-10-03 | 9.5 | 8.5 | 0 | 2017-10-03 | 6.4 | 11.6 | 0 | 2016-10-03 | 13.7 | 4.3 | 0 | 9.95 | 0
2025-10-03 | 6.4 | 11.6 | 0 | 2024-10-03 | 7.3 | 10.7 | 0 | 2023-10-03 | 15.7 | 2.3 | 0 | 2022-10-03 | 2 | 16 | 0 | 2021-10-03 | 10.9 | 7.1 | 0 | 2020-10-03 | 5.5 | 12.5 | 0 | 2019-10-03 | 3.1 | 14.9 | 0 | 2018-10-03 | 9.4 | 8.6 | 0 | 2017-10-03 | 6 | 12 | 0 | 2016-10-03 | 13.8 | 4.2 | 0 | 9.99 | 0
2025-10-03 | 6.3 | 11.7 | 0 | 2024-10-03 | 6.6 | 11.4 | 0 | 2023-10-03 | 15.6 | 2.4 | 0 | 2022-10-03 | 1.6 | 16.4 | 0 | 2021-10-03 | 10.9 | 7.1 | 0 | 2020-10-03 | 5 | 13 | 0 | 2019-10-03 | 3.5 | 14.5 | 0 | 2018-10-03 | 9.9 | 8.1 | 0 | 2017-10-03 | 5.8 | 12.2 | 0 | 2016-10-03 | 13.7 | 4.3 | 0 | 10.11 | 0
2025-10-03 | 5 | 13 | 0 | 2024-10-03 | 6.9 | 11.1 | 0 | 2023-10-03 | 15.2 | 2.8 | 0 | 2022-10-03 | 2.3 | 15.7 | 0 | 2021-10-03 | 10.8 | 7.2 | 0 | 2020-10-03 | 4.7 | 13.3 | 0 | 2019-10-03 | 3.4 | 14.6 | 0 | 2018-10-03 | 9.6 | 8.4 | 0 | 2017-10-03 | 5.8 | 12.2 | 0 | 2016-10-03 | 13.6 | 4.4 | 0 | 10.27 | 0
2025-10-03 | 6.8 | 11.2 | 0 | 2024-10-03 | 8 | 10 | 0 | 2023-10-03 | 15.8 | 2.2 | 0 | 2022-10-03 | 3 | 15 | 0 | 2021-10-03 | 10.6 | 7.4 | 0 | 2020-10-03 | 4.7 | 13.3 | 0 | 2019-10-03 | 3.8 | 14.2 | 0 | 2018-10-03 | 10.1 | 7.9 | 0 | 2017-10-03 | 7.1 | 10.9 | 0 | 2016-10-03 | 13.5 | 4.5 | 0 | 9.66 | 0
2025-10-03 | 10.2 | 7.8 | 0 | 2024-10-03 | 11 | 7 | 0 | 2023-10-03 | 17.8 | 0.2 | 0 | 2022-10-03 | 5.8 | 12.2 | 0 | 2021-10-03 | 10.4 | 7.6 | 0 | 2020-10-03 | 6.4 | 11.6 | 0 | 2019-10-03 | 4.7 | 13.3 | 0 | 2018-10-03 | 10.5 | 7.5 | 0 | 2017-10-03 | 10.3 | 7.7 | 0 | 2016-10-03 | 14.3 | 3.7 | 0 | 7.86 | 0
2025-10-03 | 14 | 4 | 0 | 2024-10-03 | 14.2 | 3.8 | 0 | 2023-10-03 | 19.8 | 0 | 1.8 | 2022-10-03 | 8.3 | 9.7 | 0 | 2021-10-03 | 10.3 | 7.7 | 0 | 2020-10-03 | 7.3 | 10.7 | 0 | 2019-10-03 | 6.3 | 11.7 | 0 | 2018-10-03 | 10.8 | 7.2 | 0 | 2017-10-03 | 13.6 | 4.4 | 0 | 2016-10-03 | 14.5 | 3.5 | 0 | 6.27 | 0.18
2025-10-03 | 17.1 | 0.9 | 0 | 2024-10-03 | 16.6 | 1.4 | 0 | 2023-10-03 | 21.1 | 0 | 3.1 | 2022-10-03 | 11.2 | 6.8 | 0 | 2021-10-03 | 10.3 | 7.7 | 0 | 2020-10-03 | 8 | 10 | 0 | 2019-10-03 | 7.5 | 10.5 | 0 | 2018-10-03 | 11.3 | 6.7 | 0 | 2017-10-03 | 16.5 | 1.5 | 0 | 2016-10-03 | 15.7 | 2.3 | 0 | 4.78 | 0.31
2025-10-03 | 19.4 | 0 | 1.4 | 2024-10-03 | 18.2 | 0 | 0.2 | 2023-10-03 | 24.9 | 0 | 6.9 | 2022-10-03 | 11.8 | 6.2 | 0 | 2021-10-03 | 10.5 | 7.5 | 0 | 2020-10-03 | 8.6 | 9.4 | 0 | 2019-10-03 | 8.6 | 9.4 | 0 | 2018-10-03 | 11.5 | 6.5 | 0 | 2017-10-03 | 18.6 | 0 | 0.6 | 2016-10-03 | 16.2 | 1.8 | 0 | 4.08 | 0.91
2025-10-03 | 22 | 0 | 4 | 2024-10-03 | 19.2 | 0 | 1.2 | 2023-10-03 | 27.3 | 0 | 9.3 | 2022-10-03 | 12.8 | 5.2 | 0 | 2021-10-03 | 10.6 | 7.4 | 0 | 2020-10-03 | 9.8 | 8.2 | 0 | 2019-10-03 | 9.4 | 8.6 | 0 | 2018-10-03 | 12 | 6 | 0 | 2017-10-03 | 20.9 | 0 | 2.9 | 2016-10-03 | 16.8 | 1.2 | 0 | 3.66 | 1.74
2025-10-03 | 23.4 | 0 | 5.4 | 2024-10-03 | 20.1 | 0 | 2.1 | 2023-10-03 | 28.6 | 0 | 10.6 | 2022-10-03 | 13.4 | 4.6 | 0 | 2021-10-03 | 10.8 | 7.2 | 0 | 2020-10-03 | 10.8 | 7.2 | 0 | 2019-10-03 | 9.2 | 8.8 | 0 | 2018-10-03 | 12.4 | 5.6 | 0 | 2017-10-03 | 21.9 | 0 | 3.9 | 2016-10-03 | 18 | 0 | 0 | 3.34 | 2.2
2025-10-03 | 24.6 | 0 | 6.6 | 2024-10-03 | 19.9 | 0 | 1.9 | 2023-10-03 | 29.6 | 0 | 11.6 | 2022-10-03 | 14.6 | 3.4 | 0 | 2021-10-03 | 11.3 | 6.7 | 0 | 2020-10-03 | 11.5 | 6.5 | 0 | 2019-10-03 | 8.8 | 9.2 | 0 | 2018-10-03 | 12.6 | 5.4 | 0 | 2017-10-03 | 22.7 | 0 | 4.7 | 2016-10-03 | 18.8 | 0 | 0.8 | 3.12 | 2.56
2025-10-03 | 25 | 0 | 7 | 2024-10-03 | 20.1 | 0 | 2.1 | 2023-10-03 | 30.6 | 0 | 12.6 | 2022-10-03 | 14.9 | 3.1 | 0 | 2021-10-03 | 12.3 | 5.7 | 0 | 2020-10-03 | 11.6 | 6.4 | 0 | 2019-10-03 | 8.5 | 9.5 | 0 | 2018-10-03 | 12.3 | 5.7 | 0 | 2017-10-03 | 22.7 | 0 | 4.7 | 2016-10-03 | 19.8 | 0 | 1.8 | 3.04 | 2.82
2025-10-03 | 24.4 | 0 | 6.4 | 2024-10-03 | 19.6 | 0 | 1.6 | 2023-10-03 | 30.5 | 0 | 12.5 | 2022-10-03 | 14.9 | 3.1 | 0 | 2021-10-03 | 12.1 | 5.9 | 0 | 2020-10-03 | 10.7 | 7.3 | 0 | 2019-10-03 | 8.4 | 9.6 | 0 | 2018-10-03 | 12.5 | 5.5 | 0 | 2017-10-03 | 21.6 | 0 | 3.6 | 2016-10-03 | 19.3 | 0 | 1.3 | 3.14 | 2.54
2025-10-03 | 23 | 0 | 5 | 2024-10-03 | 18.1 | 0 | 0.1 | 2023-10-03 | 28.7 | 0 | 10.7 | 2022-10-03 | 13.2 | 4.8 | 0 | 2021-10-03 | 12 | 6 | 0 | 2020-10-03 | 10.2 | 7.8 | 0 | 2019-10-03 | 8.2 | 9.8 | 0 | 2018-10-03 | 12 | 6 | 0 | 2017-10-03 | 20.2 | 0 | 2.2 | 2016-10-03 | 18.1 | 0 | 0.1 | 3.44 | 1.81
2025-10-03 | 20.5 | 0 | 2.5 | 2024-10-03 | 16.2 | 1.8 | 0 | 2023-10-03 | 25.5 | 0 | 7.5 | 2022-10-03 | 12.5 | 5.5 | 0 | 2021-10-03 | 11.8 | 6.2 | 0 | 2020-10-03 | 8.4 | 9.6 | 0 | 2019-10-03 | 7.6 | 10.4 | 0 | 2018-10-03 | 11.8 | 6.2 | 0 | 2017-10-03 | 17 | 1 | 0 | 2016-10-03 | 15.2 | 2.8 | 0 | 4.35 | 1
2025-10-03 | 19.2 | 0 | 1.2 | 2024-10-03 | 14.7 | 3.3 | 0 | 2023-10-03 | 23.1 | 0 | 5.1 | 2022-10-03 | 7.3 | 10.7 | 0 | 2021-10-03 | 12 | 6 | 0 | 2020-10-03 | 7.5 | 10.5 | 0 | 2019-10-03 | 6.8 | 11.2 | 0 | 2018-10-03 | 11.7 | 6.3 | 0 | 2017-10-03 | 16.1 | 1.9 | 0 | 2016-10-03 | 14 | 4 | 0 | 5.39 | 0.63
2025-10-03 | 17.3 | 0.7 | 0 | 2024-10-03 | 13.9 | 4.1 | 0 | 2023-10-03 | 21.6 | 0 | 3.6 | 2022-10-03 | 6.3 | 11.7 | 0 | 2021-10-03 | 12.1 | 5.9 | 0 | 2020-10-03 | 5.9 | 12.1 | 0 | 2019-10-03 | 5.1 | 12.9 | 0 | 2018-10-03 | 11.6 | 6.4 | 0 | 2017-10-03 | 14.8 | 3.2 | 0 | 2016-10-03 | 13.5 | 4.5 | 0 | 6.15 | 0.36
2025-10-03 | 15.9 | 2.1 | 0 | 2024-10-03 | 13.6 | 4.4 | 0 | 2023-10-03 | 20.3 | 0 | 2.3 | 2022-10-03 | 6.3 | 11.7 | 0 | 2021-10-03 | 12.2 | 5.8 | 0 | 2020-10-03 | 5.3 | 12.7 | 0 | 2019-10-03 | 4.7 | 13.3 | 0 | 2018-10-03 | 11.3 | 6.7 | 0 | 2017-10-03 | 13 | 5 | 0 | 2016-10-03 | 12.3 | 5.7 | 0 | 6.74 | 0.23
2025-10-03 | 15.6 | 2.4 | 0 | 2024-10-03 | 13.2 | 4.8 | 0 | 2023-10-03 | 19.9 | 0 | 1.9 | 2022-10-03 | 3.5 | 14.5 | 0 | 2021-10-03 | 12.4 | 5.6 | 0 | 2020-10-03 | 3.8 | 14.2 | 0 | 2019-10-03 | 5.1 | 12.9 | 0 | 2018-10-03 | 11.5 | 6.5 | 0 | 2017-10-03 | 12.1 | 5.9 | 0 | 2016-10-03 | 11.1 | 6.9 | 0 | 7.37 | 0.19
2025-10-03 | 14.4 | 3.6 | 0 | 2024-10-03 | 12.1 | 5.9 | 0 | 2023-10-03 | 18.6 | 0 | 0.6 | 2022-10-03 | 4.5 | 13.5 | 0 | 2021-10-03 | 12.3 | 5.7 | 0 | 2020-10-03 | 3.8 | 14.2 | 0 | 2019-10-03 | 5 | 13 | 0 | 2018-10-03 | 11.6 | 6.4 | 0 | 2017-10-03 | 12.7 | 5.3 | 0 | 2016-10-03 | 11.8 | 6.2 | 0 | 7.38 | 0.06
2025-10-04 | 13.7 | 4.3 | 0 | 2024-10-04 | 11.4 | 6.6 | 0 | 2023-10-04 | 15.8 | 2.2 | 0 | 2022-10-04 | 7.2 | 10.8 | 0 | 2021-10-04 | 11.8 | 6.2 | 0 | 2020-10-04 | 4.9 | 13.1 | 0 | 2019-10-04 | 5.2 | 12.8 | 0 | 2018-10-04 | 11.8 | 6.2 | 0 | 2017-10-04 | 13.6 | 4.4 | 0 | 2016-10-04 | 9.8 | 8.2 | 0 | 7.48 | 0
2025-10-04 | 13.5 | 4.5 | 0 | 2024-10-04 | 10.4 | 7.6 | 0 | 2023-10-04 | 16.4 | 1.6 | 0 | 2022-10-04 | 5.8 | 12.2 | 0 | 2021-10-04 | 11 | 7 | 0 | 2020-10-04 | 5.2 | 12.8 | 0 | 2019-10-04 | 5.2 | 12.8 | 0 | 2018-10-04 | 11.9 | 6.1 | 0 | 2017-10-04 | 14.3 | 3.7 | 0 | 2016-10-04 | 9.3 | 8.7 | 0 | 7.7 | 0
2025-10-04 | 13.8 | 4.2 | 0 | 2024-10-04 | 10.8 | 7.2 | 0 | 2023-10-04 | 15.4 | 2.6 | 0 | 2022-10-04 | 3.8 | 14.2 | 0 | 2021-10-04 | 10.3 | 7.7 | 0 | 2020-10-04 | 5.6 | 12.4 | 0 | 2019-10-04 | 5.3 | 12.7 | 0 | 2018-10-04 | 12.1 | 5.9 | 0 | 2017-10-04 | 14.5 | 3.5 | 0 | 2016-10-04 | 8.6 | 9.4 | 0 | 7.98 | 0
2025-10-04 | 13.2 | 4.8 | 0 | 2024-10-04 | 9.7 | 8.3 | 0 | 2023-10-04 | 15.1 | 2.9 | 0 | 2022-10-04 | 3 | 15 | 0 | 2021-10-04 | 9.7 | 8.3 | 0 | 2020-10-04 | 5.3 | 12.7 | 0 | 2019-10-04 | 5.4 | 12.6 | 0 | 2018-10-04 | 12.3 | 5.7 | 0 | 2017-10-04 | 14.8 | 3.2 | 0 | 2016-10-04 | 8.3 | 9.7 | 0 | 8.32 | 0
2025-10-04 | 12.9 | 5.1 | 0 | 2024-10-04 | 8.6 | 9.4 | 0 | 2023-10-04 | 14.4 | 3.6 | 0 | 2022-10-04 | 0.4 | 17.6 | 0 | 2021-10-04 | 9.2 | 8.8 | 0 | 2020-10-04 | 4.7 | 13.3 | 0 | 2019-10-04 | 5.4 | 12.6 | 0 | 2018-10-04 | 13 | 5 | 0 | 2017-10-04 | 15.4 | 2.6 | 0 | 2016-10-04 | 7 | 11 | 0 | 8.9 | 0
2025-10-04 | 12.2 | 5.8 | 0 | 2024-10-04 | 8.8 | 9.2 | 0 | 2023-10-04 | 14.6 | 3.4 | 0 | 2022-10-04 | 1.1 | 16.9 | 0 | 2021-10-04 | 9.2 | 8.8 | 0 | 2020-10-04 | 5.3 | 12.7 | 0 | 2019-10-04 | 5.5 | 12.5 | 0 | 2018-10-04 | 14.4 | 3.6 | 0 | 2017-10-04 | 15 | 3 | 0 | 2016-10-04 | 7.9 | 10.1 | 0 | 8.6 | 0
2025-10-04 | 10.9 | 7.1 | 0 | 2024-10-04 | 7.1 | 10.9 | 0 | 2023-10-04 | 14.2 | 3.8 | 0 | 2022-10-04 | 1.4 | 16.6 | 0 | 2021-10-04 | 8.3 | 9.7 | 0 | 2020-10-04 | 5.2 | 12.8 | 0 | 2019-10-04 | 5.1 | 12.9 | 0 | 2018-10-04 | 15.5 | 2.5 | 0 | 2017-10-04 | 15.9 | 2.1 | 0 | 2016-10-04 | 7.7 | 10.3 | 0 | 8.87 | 0
2025-10-04 | 12.8 | 5.2 | 0 | 2024-10-04 | 9.3 | 8.7 | 0 | 2023-10-04 | 15.3 | 2.7 | 0 | 2022-10-04 | 3.4 | 14.6 | 0 | 2021-10-04 | 8.1 | 9.9 | 0 | 2020-10-04 | 6.1 | 11.9 | 0 | 2019-10-04 | 5.2 | 12.8 | 0 | 2018-10-04 | 15.9 | 2.1 | 0 | 2017-10-04 | 17.3 | 0.7 | 0 | 2016-10-04 | 7.9 | 10.1 | 0 | 7.87 | 0
2025-10-04 | 15.7 | 2.3 | 0 | 2024-10-04 | 11.9 | 6.1 | 0 | 2023-10-04 | 17.8 | 0.2 | 0 | 2022-10-04 | 6.7 | 11.3 | 0 | 2021-10-04 | 9.4 | 8.6 | 0 | 2020-10-04 | 7.5 | 10.5 | 0 | 2019-10-04 | 6.7 | 11.3 | 0 | 2018-10-04 | 17.8 | 0.2 | 0 | 2017-10-04 | 17.7 | 0.3 | 0 | 2016-10-04 | 9.5 | 8.5 | 0 | 5.93 | 0
2025-10-04 | 19.3 | 0 | 1.3 | 2024-10-04 | 14.7 | 3.3 | 0 | 2023-10-04 | 21.7 | 0 | 3.7 | 2022-10-04 | 9.2 | 8.8 | 0 | 2021-10-04 | 11.3 | 6.7 | 0 | 2020-10-04 | 9.6 | 8.4 | 0 | 2019-10-04 | 6.3 | 11.7 | 0 | 2018-10-04 | 19.4 | 0 | 1.4 | 2017-10-04 | 19.1 | 0 | 1.1 | 2016-10-04 | 11.4 | 6.6 | 0 | 4.55 | 0.75
2025-10-04 | 21.8 | 0 | 3.8 | 2024-10-04 | 17.1 | 0.9 | 0 | 2023-10-04 | 24.7 | 0 | 6.7 | 2022-10-04 | 12.1 | 5.9 | 0 | 2021-10-04 | 12.6 | 5.4 | 0 | 2020-10-04 | 11.1 | 6.9 | 0 | 2019-10-04 | 7.2 | 10.8 | 0 | 2018-10-04 | 20.2 | 0 | 2.2 | 2017-10-04 | 19.4 | 0 | 1.4 | 2016-10-04 | 13.4 | 4.6 | 0 | 3.45 | 1.41
2025-10-04 | 23.3 | 0 | 5.3 | 2024-10-04 | 18.7 | 0 | 0.7 | 2023-10-04 | 26.9 | 0 | 8.9 | 2022-10-04 | 14.8 | 3.2 | 0 | 2021-10-04 | 15.2 | 2.8 | 0 | 2020-10-04 | 12.6 | 5.4 | 0 | 2019-10-04 | 8.1 | 9.9 | 0 | 2018-10-04 | 22.6 | 0 | 4.6 | 2017-10-04 | 19.7 | 0 | 1.7 | 2016-10-04 | 16 | 2 | 0 | 2.33 | 2.12
2025-10-04 | 24.9 | 0 | 6.9 | 2024-10-04 | 20 | 0 | 2 | 2023-10-04 | 28.5 | 0 | 10.5 | 2022-10-04 | 16 | 2 | 0 | 2021-10-04 | 14.9 | 3.1 | 0 | 2020-10-04 | 13.7 | 4.3 | 0 | 2019-10-04 | 8.3 | 9.7 | 0 | 2018-10-04 | 23.8 | 0 | 5.8 | 2017-10-04 | 21.6 | 0 | 3.6 | 2016-10-04 | 17.8 | 0.2 | 0 | 1.93 | 2.88
2025-10-04 | 26.4 | 0 | 8.4 | 2024-10-04 | 20.5 | 0 | 2.5 | 2023-10-04 | 28.9 | 0 | 10.9 | 2022-10-04 | 15.4 | 2.6 | 0 | 2021-10-04 | 15.1 | 2.9 | 0 | 2020-10-04 | 13.7 | 4.3 | 0 | 2019-10-04 | 9.6 | 8.4 | 0 | 2018-10-04 | 22.4 | 0 | 4.4 | 2017-10-04 | 22.8 | 0 | 4.8 | 2016-10-04 | 19.1 | 0 | 1.1 | 1.82 | 3.21
2025-10-04 | 26.7 | 0 | 8.7 | 2024-10-04 | 20.1 | 0 | 2.1 | 2023-10-04 | 29.4 | 0 | 11.4 | 2022-10-04 | 17.2 | 0.8 | 0 | 2021-10-04 | 16 | 2 | 0 | 2020-10-04 | 14 | 4 | 0 | 2019-10-04 | 10.2 | 7.8 | 0 | 2018-10-04 | 21.2 | 0 | 3.2 | 2017-10-04 | 23 | 0 | 5 | 2016-10-04 | 19.8 | 0 | 1.8 | 1.46 | 3.22
2025-10-04 | 27.1 | 0 | 9.1 | 2024-10-04 | 19.7 | 0 | 1.7 | 2023-10-04 | 29.6 | 0 | 11.6 | 2022-10-04 | 17 | 1 | 0 | 2021-10-04 | 16.6 | 1.4 | 0 | 2020-10-04 | 10.6 | 7.4 | 0 | 2019-10-04 | 10.3 | 7.7 | 0 | 2018-10-04 | 20.2 | 0 | 2.2 | 2017-10-04 | 22.8 | 0 | 4.8 | 2016-10-04 | 19.5 | 0 | 1.5 | 1.75 | 3.09
2025-10-04 | 25.9 | 0 | 7.9 | 2024-10-04 | 18.6 | 0 | 0.6 | 2023-10-04 | 29.1 | 0 | 11.1 | 2022-10-04 | 16.9 | 1.1 | 0 | 2021-10-04 | 16.1 | 1.9 | 0 | 2020-10-04 | 11.2 | 6.8 | 0 | 2019-10-04 | 9.6 | 8.4 | 0 | 2018-10-04 | 18.9 | 0 | 0.9 | 2017-10-04 | 22.5 | 0 | 4.5 | 2016-10-04 | 19.3 | 0 | 1.3 | 1.82 | 2.63
2025-10-04 | 24.9 | 0 | 6.9 | 2024-10-04 | 17.4 | 0.6 | 0 | 2023-10-04 | 26.8 | 0 | 8.8 | 2022-10-04 | 16 | 2 | 0 | 2021-10-04 | 15.4 | 2.6 | 0 | 2020-10-04 | 11 | 7 | 0 | 2019-10-04 | 8.6 | 9.4 | 0 | 2018-10-04 | 16.6 | 1.4 | 0 | 2017-10-04 | 22.2 | 0 | 4.2 | 2016-10-04 | 17.7 | 0.3 | 0 | 2.33 | 1.99
2025-10-04 | 23.1 | 0 | 5.1 | 2024-10-04 | 16 | 2 | 0 | 2023-10-04 | 24.2 | 0 | 6.2 | 2022-10-04 | 12.3 | 5.7 | 0 | 2021-10-04 | 14.4 | 3.6 | 0 | 2020-10-04 | 10.4 | 7.6 | 0 | 2019-10-04 | 7.4 | 10.6 | 0 | 2018-10-04 | 13.9 | 4.1 | 0 | 2017-10-04 | 20.1 | 0 | 2.1 | 2016-10-04 | 14.8 | 3.2 | 0 | 3.68 | 1.34
2025-10-04 | 21.3 | 0 | 3.3 | 2024-10-04 | 14.9 | 3.1 | 0 | 2023-10-04 | 23.4 | 0 | 5.4 | 2022-10-04 | 10.7 | 7.3 | 0 | 2021-10-04 | 14.3 | 3.7 | 0 | 2020-10-04 | 9.8 | 8.2 | 0 | 2019-10-04 | 6.6 | 11.4 | 0 | 2018-10-04 | 12 | 6 | 0 | 2017-10-04 | 19.3 | 0 | 1.3 | 2016-10-04 | 13.3 | 4.7 | 0 | 4.44 | 1
2025-10-04 | 19.8 | 0 | 1.8 | 2024-10-04 | 14.7 | 3.3 | 0 | 2023-10-04 | 20.9 | 0 | 2.9 | 2022-10-04 | 8 | 10 | 0 | 2021-10-04 | 14.2 | 3.8 | 0 | 2020-10-04 | 9.5 | 8.5 | 0 | 2019-10-04 | 5.7 | 12.3 | 0 | 2018-10-04 | 10.4 | 7.6 | 0 | 2017-10-04 | 18 | 0 | 0 | 2016-10-04 | 13.2 | 4.8 | 0 | 5.03 | 0.47
2025-10-04 | 18.8 | 0 | 0.8 | 2024-10-04 | 14.5 | 3.5 | 0 | 2023-10-04 | 20.4 | 0 | 2.4 | 2022-10-04 | 9.2 | 8.8 | 0 | 2021-10-04 | 14.1 | 3.9 | 0 | 2020-10-04 | 9.3 | 8.7 | 0 | 2019-10-04 | 4.2 | 13.8 | 0 | 2018-10-04 | 9.2 | 8.8 | 0 | 2017-10-04 | 16.8 | 1.2 | 0 | 2016-10-04 | 12.2 | 5.8 | 0 | 5.45 | 0.32
2025-10-04 | 18.2 | 0 | 0.2 | 2024-10-04 | 13.5 | 4.5 | 0 | 2023-10-04 | 19.9 | 0 | 1.9 | 2022-10-04 | 7.6 | 10.4 | 0 | 2021-10-04 | 14.3 | 3.7 | 0 | 2020-10-04 | 9.2 | 8.8 | 0 | 2019-10-04 | 3 | 15 | 0 | 2018-10-04 | 8.3 | 9.7 | 0 | 2017-10-04 | 15.9 | 2.1 | 0 | 2016-10-04 | 10.4 | 7.6 | 0 | 6.18 | 0.21
2025-10-04 | 17.6 | 0.4 | 0 | 2024-10-04 | 11.8 | 6.2 | 0 | 2023-10-04 | 19.4 | 0 | 1.4 | 2022-10-04 | 7 | 11 | 0 | 2021-10-04 | 14 | 4 | 0 | 2020-10-04 | 9.5 | 8.5 | 0 | 2019-10-04 | 3.3 | 14.7 | 0 | 2018-10-04 | 7.1 | 10.9 | 0 | 2017-10-04 | 14.7 | 3.3 | 0 | 2016-10-04 | 11.6 | 6.4 | 0 | 6.54 | 0.14
2025-10-05 | 16.7 | 1.3 | 0 | 2024-10-05 | 11.9 | 6.1 | 0 | 2023-10-05 | 19.1 | 0 | 1.1 | 2022-10-05 | 3.9 | 14.1 | 0 | 2021-10-05 | 13.7 | 4.3 | 0 | 2020-10-05 | 8.9 | 9.1 | 0 | 2019-10-05 | 2.4 | 15.6 | 0 | 2018-10-05 | 5.1 | 12.9 | 0 | 2017-10-05 | 13.9 | 4.1 | 0 | 2016-10-05 | 8.4 | 9.6 | 0 | 7.71 | 0.11
2025-10-05 | 16.1 | 1.9 | 0 | 2024-10-05 | 9.7 | 8.3 | 0 | 2023-10-05 | 18.9 | 0 | 0.9 | 2022-10-05 | 5.2 | 12.8 | 0 | 2021-10-05 | 13.5 | 4.5 | 0 | 2020-10-05 | 8.6 | 9.4 | 0 | 2019-10-05 | 3.1 | 14.9 | 0 | 2018-10-05 | 5 | 13 | 0 | 2017-10-05 | 12.6 | 5.4 | 0 | 2016-10-05 | 8.2 | 9.8 | 0 | 8 | 0.09
2025-10-05 | 15.6 | 2.4 | 0 | 2024-10-05 | 9.1 | 8.9 | 0 | 2023-10-05 | 18 | 0 | 0 | 2022-10-05 | 4.8 | 13.2 | 0 | 2021-10-05 | 13.3 | 4.7 | 0 | 2020-10-05 | 8.7 | 9.3 | 0 | 2019-10-05 | 0.4 | 17.6 | 0 | 2018-10-05 | 3.6 | 14.4 | 0 | 2017-10-05 | 11.1 | 6.9 | 0 | 2016-10-05 | 10.2 | 7.8 | 0 | 8.52 | 0
2025-10-05 | 15.3 | 2.7 | 0 | 2024-10-05 | 8.5 | 9.5 | 0 | 2023-10-05 | 17.3 | 0.7 | 0 | 2022-10-05 | 3.4 | 14.6 | 0 | 2021-10-05 | 13 | 5 | 0 | 2020-10-05 | 8.6 | 9.4 | 0 | 2019-10-05 | -0.6 | 18.6 | 0 | 2018-10-05 | 2.3 | 15.7 | 0 | 2017-10-05 | 10.3 | 7.7 | 0 | 2016-10-05 | 10.3 | 7.7 | 0 | 9.16 | 0
2025-10-05 | 14.9 | 3.1 | 0 | 2024-10-05 | 8.8 | 9.2 | 0 | 2023-10-05 | 17 | 1 | 0 | 2022-10-05 | 4.1 | 13.9 | 0 | 2021-10-05 | 12 | 6 | 0 | 2020-10-05 | 8.7 | 9.3 | 0 | 2019-10-05 | 0.3 | 17.7 | 0 | 2018-10-05 | 3.3 | 14.7 | 0 | 2017-10-05 | 9.9 | 8.1 | 0 | 2016-10-05 | 8 | 10 | 0 | 9.3 | 0
2025-10-05 | 13.6 | 4.4 | 0 | 2024-10-05 | 6.8 | 11.2 | 0 | 2023-10-05 | 16.5 | 1.5 | 0 | 2022-10-05 | 5.2 | 12.8 | 0 | 2021-10-05 | 10.6 | 7.4 | 0 | 2020-10-05 | 8.8 | 9.2 | 0 | 2019-10-05 | 0.2 | 17.8 | 0 | 2018-10-05 | 3.2 | 14.8 | 0 | 2017-10-05 | 9.3 | 8.7 | 0 | 2016-10-05 | 7.8 | 10.2 | 0 | 9.8 | 0
2025-10-05 | 13.8 | 4.2 | 0 | 2024-10-05 | 7.1 | 10.9 | 0 | 2023-10-05 | 16.5 | 1.5 | 0 | 2022-10-05 | 1.9 | 16.1 | 0 | 2021-10-05 | 10.9 | 7.1 | 0 | 2020-10-05 | 8.9 | 9.1 | 0 | 2019-10-05 | -1.6 | 19.6 | 0 | 2018-10-05 | 2.6 | 15.4 | 0 | 2017-10-05 | 9.6 | 8.4 | 0 | 2016-10-05 | 8.7 | 9.3 | 0 | 10.16 | 0
2025-10-05 | 14.8 | 3.2 | 0 | 2024-10-05 | 8.5 | 9.5 | 0 | 2023-10-05 | 17.9 | 0.1 | 0 | 2022-10-05 | 5.1 | 12.9 | 0 | 2021-10-05 | 12 | 6 | 0 | 2020-10-05 | 9 | 9 | 0 | 2019-10-05 | -1 | 19 | 0 | 2018-10-05 | 3.9 | 14.1 | 0 | 2017-10-05 | 10.1 | 7.9 | 0 | 2016-10-05 | 9.6 | 8.4 | 0 | 9.01 | 0
2025-10-05 | 18.5 | 0 | 0.5 | 2024-10-05 | 11 | 7 | 0 | 2023-10-05 | 19.7 | 0 | 1.7 | 2022-10-05 | 9.5 | 8.5 | 0 | 2021-10-05 | 12.9 | 5.1 | 0 | 2020-10-05 | 9.4 | 8.6 | 0 | 2019-10-05 | 2.8 | 15.2 | 0 | 2018-10-05 | 5.7 | 12.3 | 0 | 2017-10-05 | 12.1 | 5.9 | 0 | 2016-10-05 | 11.9 | 6.1 | 0 | 6.87 | 0.22
2025-10-05 | 21.4 | 0 | 3.4 | 2024-10-05 | 12.8 | 5.2 | 0 | 2023-10-05 | 21.3 | 0 | 3.3 | 2022-10-05 | 12.3 | 5.7 | 0 | 2021-10-05 | 14.2 | 3.8 | 0 | 2020-10-05 | 10.1 | 7.9 | 0 | 2019-10-05 | 6.8 | 11.2 | 0 | 2018-10-05 | 7 | 11 | 0 | 2017-10-05 | 13.7 | 4.3 | 0 | 2016-10-05 | 13.4 | 4.6 | 0 | 5.37 | 0.67
2025-10-05 | 24.1 | 0 | 6.1 | 2024-10-05 | 15 | 3 | 0 | 2023-10-05 | 22.9 | 0 | 4.9 | 2022-10-05 | 15.3 | 2.7 | 0 | 2021-10-05 | 16.2 | 1.8 | 0 | 2020-10-05 | 11 | 7 | 0 | 2019-10-05 | 8.7 | 9.3 | 0 | 2018-10-05 | 7.7 | 10.3 | 0 | 2017-10-05 | 15.7 | 2.3 | 0 | 2016-10-05 | 16.4 | 1.6 | 0 | 3.8 | 1.1
2025-10-05 | 26.6 | 0 | 8.6 | 2024-10-05 | 16.2 | 1.8 | 0 | 2023-10-05 | 25 | 0 | 7 | 2022-10-05 | 17.6 | 0.4 | 0 | 2021-10-05 | 17.8 | 0.2 | 0 | 2020-10-05 | 11.5 | 6.5 | 0 | 2019-10-05 | 9.9 | 8.1 | 0 | 2018-10-05 | 8.7 | 9.3 | 0 | 2017-10-05 | 17.9 | 0.1 | 0 | 2016-10-05 | 18.3 | 0 | 0.3 | 2.64 | 1.59
2025-10-05 | 28.5 | 0 | 10.5 | 2024-10-05 | 16 | 2 | 0 | 2023-10-05 | 26 | 0 | 8 | 2022-10-05 | 18.9 | 0 | 0.9 | 2021-10-05 | 18.9 | 0 | 0.9 | 2020-10-05 | 11.4 | 6.6 | 0 | 2019-10-05 | 10.9 | 7.1 | 0 | 2018-10-05 | 9 | 9 | 0 | 2017-10-05 | 18.5 | 0 | 0.5 | 2016-10-05 | 19.2 | 0 | 1.2 | 2.47 | 2.2
2025-10-05 | 29.4 | 0 | 11.4 | 2024-10-05 | 16 | 2 | 0 | 2023-10-05 | 26.4 | 0 | 8.4 | 2022-10-05 | 20 | 0 | 2 | 2021-10-05 | 19.2 | 0 | 1.2 | 2020-10-05 | 11.3 | 6.7 | 0 | 2019-10-05 | 11.7 | 6.3 | 0 | 2018-10-05 | 10.1 | 7.9 | 0 | 2017-10-05 | 19.4 | 0 | 1.4 | 2016-10-05 | 19.4 | 0 | 1.4 | 2.29 | 2.58
2025-10-05 | 29.7 | 0 | 11.7 | 2024-10-05 | 16.6 | 1.4 | 0 | 2023-10-05 | 26.2 | 0 | 8.2 | 2022-10-05 | 21 | 0 | 3 | 2021-10-05 | 18.9 | 0 | 0.9 | 2020-10-05 | 11.6 | 6.4 | 0 | 2019-10-05 | 12.2 | 5.8 | 0 | 2018-10-05 | 10.5 | 7.5 | 0 | 2017-10-05 | 19.7 | 0 | 1.7 | 2016-10-05 | 20.8 | 0 | 2.8 | 2.11 | 2.83
2025-10-05 | 29.6 | 0 | 11.6 | 2024-10-05 | 16.7 | 1.3 | 0 | 2023-10-05 | 26.4 | 0 | 8.4 | 2022-10-05 | 21.4 | 0 | 3.4 | 2021-10-05 | 18.9 | 0 | 0.9 | 2020-10-05 | 11.1 | 6.9 | 0 | 2019-10-05 | 12.6 | 5.4 | 0 | 2018-10-05 | 9.7 | 8.3 | 0 | 2017-10-05 | 18.3 | 0 | 0.3 | 2016-10-05 | 20.7 | 0 | 2.7 | 2.19 | 2.73
2025-10-05 | 28.2 | 0 | 10.2 | 2024-10-05 | 16.4 | 1.6 | 0 | 2023-10-05 | 25.6 | 0 | 7.6 | 2022-10-05 | 21.4 | 0 | 3.4 | 2021-10-05 | 19.1 | 0 | 1.1 | 2020-10-05 | 11 | 7 | 0 | 2019-10-05 | 12.5 | 5.5 | 0 | 2018-10-05 | 8.9 | 9.1 | 0 | 2017-10-05 | 18.2 | 0 | 0.2 | 2016-10-05 | 18.1 | 0 | 0.1 | 2.32 | 2.26
2025-10-05 | 26.7 | 0 | 8.7 | 2024-10-05 | 14.8 | 3.2 | 0 | 2023-10-05 | 23.8 | 0 | 5.8 | 2022-10-05 | 19.4 | 0 | 1.4 | 2021-10-05 | 17.3 | 0.7 | 0 | 2020-10-05 | 10.5 | 7.5 | 0 | 2019-10-05 | 9.6 | 8.4 | 0 | 2018-10-05 | 8.6 | 9.4 | 0 | 2017-10-05 | 16.6 | 1.4 | 0 | 2016-10-05 | 18.1 | 0 | 0.1 | 3.06 | 1.6
2025-10-05 | 24.2 | 0 | 6.2 | 2024-10-05 | 12.7 | 5.3 | 0 | 2023-10-05 | 22.5 | 0 | 4.5 | 2022-10-05 | 16.9 | 1.1 | 0 | 2021-10-05 | 14 | 4 | 0 | 2020-10-05 | 8.7 | 9.3 | 0 | 2019-10-05 | 8.5 | 9.5 | 0 | 2018-10-05 | 8.1 | 9.9 | 0 | 2017-10-05 | 14.9 | 3.1 | 0 | 2016-10-05 | 15 | 3 | 0 | 4.52 | 1.07
2025-10-05 | 22.1 | 0 | 4.1 | 2024-10-05 | 11.3 | 6.7 | 0 | 2023-10-05 | 21.3 | 0 | 3.3 | 2022-10-05 | 16.8 | 1.2 | 0 | 2021-10-05 | 13.2 | 4.8 | 0 | 2020-10-05 | 7.5 | 10.5 | 0 | 2019-10-05 | 7.2 | 10.8 | 0 | 2018-10-05 | 6.8 | 11.2 | 0 | 2017-10-05 | 13.8 | 4.2 | 0 | 2016-10-05 | 13.9 | 4.1 | 0 | 5.35 | 0.74
2025-10-05 | 20.8 | 0 | 2.8 | 2024-10-05 | 9.3 | 8.7 | 0 | 2023-10-05 | 21.4 | 0 | 3.4 | 2022-10-05 | 14.9 | 3.1 | 0 | 2021-10-05 | 11.9 | 6.1 | 0 | 2020-10-05 | 7.5 | 10.5 | 0 | 2019-10-05 | 6.2 | 11.8 | 0 | 2018-10-05 | 7.1 | 10.9 | 0 | 2017-10-05 | 13.4 | 4.6 | 0 | 2016-10-05 | 13.7 | 4.3 | 0 | 6 | 0.62
2025-10-05 | 19.2 | 0 | 1.2 | 2024-10-05 | 6.9 | 11.1 | 0 | 2023-10-05 | 21.3 | 0 | 3.3 | 2022-10-05 | 14.6 | 3.4 | 0 | 2021-10-05 | 13.1 | 4.9 | 0 | 2020-10-05 | 7.8 | 10.2 | 0 | 2019-10-05 | 6.4 | 11.6 | 0 | 2018-10-05 | 6.9 | 11.1 | 0 | 2017-10-05 | 12 | 6 | 0 | 2016-10-05 | 12.7 | 5.3 | 0 | 6.36 | 0.45
2025-10-05 | 17.9 | 0.1 | 0 | 2024-10-05 | 7.6 | 10.4 | 0 | 2023-10-05 | 22 | 0 | 4 | 2022-10-05 | 13.1 | 4.9 | 0 | 2021-10-05 | 10.7 | 7.3 | 0 | 2020-10-05 | 7.2 | 10.8 | 0 | 2019-10-05 | 6.9 | 11.1 | 0 | 2018-10-05 | 6.6 | 11.4 | 0 | 2017-10-05 | 10.9 | 7.1 | 0 | 2016-10-05 | 13.2 | 4.8 | 0 | 6.79 | 0.4
2025-10-05 | 16.5 | 1.5 | 0 | 2024-10-05 | 5.2 | 12.8 | 0 | 2023-10-05 | 21.4 | 0 | 3.4 | 2022-10-05 | 12.6 | 5.4 | 0 | 2021-10-05 | 11.6 | 6.4 | 0 | 2020-10-05 | 6.6 | 11.4 | 0 | 2019-10-05 | 6 | 12 | 0 | 2018-10-05 | 5.8 | 12.2 | 0 | 2017-10-05 | 11.4 | 6.6 | 0 | 2016-10-05 | 12.2 | 5.8 | 0 | 7.41 | 0.34
2025-10-06 | 16.3 | 1.7 | 0 | 2024-10-06 | 4.7 | 13.3 | 0 | 2023-10-06 | 20.5 | 0 | 2.5 | 2022-10-06 | 11.8 | 6.2 | 0 | 2021-10-06 | 10.2 | 7.8 | 0 | 2020-10-06 | 6.7 | 11.3 | 0 | 2019-10-06 | 5.3 | 12.7 | 0 | 2018-10-06 | 6.4 | 11.6 | 0 | 2017-10-06 | 9.8 | 8.2 | 0 | 2016-10-06 | 12.1 | 5.9 | 0 | 7.87 | 0.25
2025-10-06 | 15.5 | 2.5 | 0 | 2024-10-06 | 5.1 | 12.9 | 0 | 2023-10-06 | 20 | 0 | 2 | 2022-10-06 | 9.6 | 8.4 | 0 | 2021-10-06 | 9.1 | 8.9 | 0 | 2020-10-06 | 6.9 | 11.1 | 0 | 2019-10-06 | 5.9 | 12.1 | 0 | 2018-10-06 | 6.5 | 11.5 | 0 | 2017-10-06 | 10.3 | 7.7 | 0 | 2016-10-06 | 11.1 | 6.9 | 0 | 8.2 | 0.2
2025-10-06 | 15 | 3 | 0 | 2024-10-06 | 4.8 | 13.2 | 0 | 2023-10-06 | 19.9 | 0 | 1.9 | 2022-10-06 | 10.5 | 7.5 | 0 | 2021-10-06 | 8.2 | 9.8 | 0 | 2020-10-06 | 6.5 | 11.5 | 0 | 2019-10-06 | 5.4 | 12.6 | 0 | 2018-10-06 | 6.4 | 11.6 | 0 | 2017-10-06 | 10.3 | 7.7 | 0 | 2016-10-06 | 11.1 | 6.9 | 0 | 8.38 | 0.19
2025-10-06 | 13.3 | 4.7 | 0 | 2024-10-06 | 3.9 | 14.1 | 0 | 2023-10-06 | 19.7 | 0 | 1.7 | 2022-10-06 | 10.3 | 7.7 | 0 | 2021-10-06 | 7.5 | 10.5 | 0 | 2020-10-06 | 5.8 | 12.2 | 0 | 2019-10-06 | 6.1 | 11.9 | 0 | 2018-10-06 | 6.2 | 11.8 | 0 | 2017-10-06 | 10.6 | 7.4 | 0 | 2016-10-06 | 10.1 | 7.9 | 0 | 8.82 | 0.17
2025-10-06 | 14.1 | 3.9 | 0 | 2024-10-06 | 4.1 | 13.9 | 0 | 2023-10-06 | 19.1 | 0 | 1.1 | 2022-10-06 | 9.8 | 8.2 | 0 | 2021-10-06 | 7.8 | 10.2 | 0 | 2020-10-06 | 7.2 | 10.8 | 0 | 2019-10-06 | 6 | 12 | 0 | 2018-10-06 | 6.1 | 11.9 | 0 | 2017-10-06 | 10.4 | 7.6 | 0 | 2016-10-06 | 9.9 | 8.1 | 0 | 8.66 | 0.11
2025-10-06 | 13.6 | 4.4 | 0 | 2024-10-06 | 2.6 | 15.4 | 0 | 2023-10-06 | 19.5 | 0 | 1.5 | 2022-10-06 | 9.1 | 8.9 | 0 | 2021-10-06 | 7.1 | 10.9 | 0 | 2020-10-06 | 6.8 | 11.2 | 0 | 2019-10-06 | 6.2 | 11.8 | 0 | 2018-10-06 | 5.8 | 12.2 | 0 | 2017-10-06 | 10.8 | 7.2 | 0 | 2016-10-06 | 8 | 10 | 0 | 9.2 | 0.15
2025-10-06 | 13 | 5 | 0 | 2024-10-06 | 2.5 | 15.5 | 0 | 2023-10-06 | 18.5 | 0 | 0.5 | 2022-10-06 | 9.7 | 8.3 | 0 | 2021-10-06 | 6.8 | 11.2 | 0 | 2020-10-06 | 7.4 | 10.6 | 0 | 2019-10-06 | 5.8 | 12.2 | 0 | 2018-10-06 | 5.9 | 12.1 | 0 | 2017-10-06 | 10.9 | 7.1 | 0 | 2016-10-06 | 7.7 | 10.3 | 0 | 9.23 | 0.05
2025-10-06 | 14.1 | 3.9 | 0 | 2024-10-06 | 4.7 | 13.3 | 0 | 2023-10-06 | 18.8 | 0 | 0.8 | 2022-10-06 | 10.3 | 7.7 | 0 | 2021-10-06 | 7.1 | 10.9 | 0 | 2020-10-06 | 8.2 | 9.8 | 0 | 2019-10-06 | 7.6 | 10.4 | 0 | 2018-10-06 | 5.9 | 12.1 | 0 | 2017-10-06 | 11.3 | 6.7 | 0 | 2016-10-06 | 9.1 | 8.9 | 0 | 8.37 | 0.08
2025-10-06 | 16.3 | 1.7 | 0 | 2024-10-06 | 7.4 | 10.6 | 0 | 2023-10-06 | 19.6 | 0 | 1.6 | 2022-10-06 | 13.3 | 4.7 | 0 | 2021-10-06 | 10.5 | 7.5 | 0 | 2020-10-06 | 10.4 | 7.6 | 0 | 2019-10-06 | 8.1 | 9.9 | 0 | 2018-10-06 | 6.8 | 11.2 | 0 | 2017-10-06 | 12.2 | 5.8 | 0 | 2016-10-06 | 13.2 | 4.8 | 0 | 6.38 | 0.16
2025-10-06 | 20.2 | 0 | 2.2 | 2024-10-06 | 10.1 | 7.9 | 0 | 2023-10-06 | 19.4 | 0 | 1.4 | 2022-10-06 | 14.7 | 3.3 | 0 | 2021-10-06 | 12.7 | 5.3 | 0 | 2020-10-06 | 11.3 | 6.7 | 0 | 2019-10-06 | 9.3 | 8.7 | 0 | 2018-10-06 | 7.5 | 10.5 | 0 | 2017-10-06 | 14.5 | 3.5 | 0 | 2016-10-06 | 15.9 | 2.1 | 0 | 4.8 | 0.36
2025-10-06 | 23.2 | 0 | 5.2 | 2024-10-06 | 12.4 | 5.6 | 0 | 2023-10-06 | 20.2 | 0 | 2.2 | 2022-10-06 | 17.7 | 0.3 | 0 | 2021-10-06 | 16.2 | 1.8 | 0 | 2020-10-06 | 12.6 | 5.4 | 0 | 2019-10-06 | 10.6 | 7.4 | 0 | 2018-10-06 | 7.6 | 10.4 | 0 | 2017-10-06 | 15.4 | 2.6 | 0 | 2016-10-06 | 18.1 | 0 | 0.1 | 3.35 | 0.75
2025-10-06 | 26.2 | 0 | 8.2 | 2024-10-06 | 14.5 | 3.5 | 0 | 2023-10-06 | 19.1 | 0 | 1.1 | 2022-10-06 | 20 | 0 | 2 | 2021-10-06 | 18.4 | 0 | 0.4 | 2020-10-06 | 13.5 | 4.5 | 0 | 2019-10-06 | 12.1 | 5.9 | 0 | 2018-10-06 | 8.3 | 9.7 | 0 | 2017-10-06 | 16.2 | 1.8 | 0 | 2016-10-06 | 18.8 | 0 | 0.8 | 2.54 | 1.25
2025-10-06 | 28.2 | 0 | 10.2 | 2024-10-06 | 16.4 | 1.6 | 0 | 2023-10-06 | 18.1 | 0 | 0.1 | 2022-10-06 | 22.2 | 0 | 4.2 | 2021-10-06 | 20.2 | 0 | 2.2 | 2020-10-06 | 15.2 | 2.8 | 0 | 2019-10-06 | 15 | 3 | 0 | 2018-10-06 | 8.6 | 9.4 | 0 | 2017-10-06 | 17.1 | 0.9 | 0 | 2016-10-06 | 20.3 | 0 | 2.3 | 1.77 | 1.9
2025-10-06 | 28.5 | 0 | 10.5 | 2024-10-06 | 18.7 | 0 | 0.7 | 2023-10-06 | 18.9 | 0 | 0.9 | 2022-10-06 | 21 | 0 | 3 | 2021-10-06 | 20.4 | 0 | 2.4 | 2020-10-06 | 15.3 | 2.7 | 0 | 2019-10-06 | 16.2 | 1.8 | 0 | 2018-10-06 | 9.1 | 8.9 | 0 | 2017-10-06 | 18.4 | 0 | 0.4 | 2016-10-06 | 21.2 | 0 | 3.2 | 1.34 | 2.11
2025-10-06 | 28.8 | 0 | 10.8 | 2024-10-06 | 19.2 | 0 | 1.2 | 2023-10-06 | 19.3 | 0 | 1.3 | 2022-10-06 | 20.5 | 0 | 2.5 | 2021-10-06 | 20.9 | 0 | 2.9 | 2020-10-06 | 15.3 | 2.7 | 0 | 2019-10-06 | 16.9 | 1.1 | 0 | 2018-10-06 | 8.9 | 9.1 | 0 | 2017-10-06 | 18 | 0 | 0 | 2016-10-06 | 21.5 | 0 | 3.5 | 1.29 | 2.22
2025-10-06 | 28.2 | 0 | 10.2 | 2024-10-06 | 20.8 | 0 | 2.8 | 2023-10-06 | 20.3 | 0 | 2.3 | 2022-10-06 | 20.3 | 0 | 2.3 | 2021-10-06 | 21.1 | 0 | 3.1 | 2020-10-06 | 15.9 | 2.1 | 0 | 2019-10-06 | 18 | 0 | 0 | 2018-10-06 | 8.1 | 9.9 | 0 | 2017-10-06 | 17.4 | 0.6 | 0 | 2016-10-06 | 22 | 0 | 4 | 1.26 | 2.47
2025-10-06 | 27.1 | 0 | 9.1 | 2024-10-06 | 19.1 | 0 | 1.1 | 2023-10-06 | 21 | 0 | 3 | 2022-10-06 | 19.2 | 0 | 1.2 | 2021-10-06 | 20.9 | 0 | 2.9 | 2020-10-06 | 15.1 | 2.9 | 0 | 2019-10-06 | 17.2 | 0.8 | 0 | 2018-10-06 | 7.8 | 10.2 | 0 | 2017-10-06 | 18 | 0 | 0 | 2016-10-06 | 21.7 | 0 | 3.7 | 1.39 | 2.1
2025-10-06 | 25.3 | 0 | 7.3 | 2024-10-06 | 15.4 | 2.6 | 0 | 2023-10-06 | 19.6 | 0 | 1.6 | 2022-10-06 | 18.2 | 0 | 0.2 | 2021-10-06 | 19 | 0 | 1 | 2020-10-06 | 14.6 | 3.4 | 0 | 2019-10-06 | 16.9 | 1.1 | 0 | 2018-10-06 | 7.9 | 10.1 | 0 | 2017-10-06 | 16.9 | 1.1 | 0 | 2016-10-06 | 20.3 | 0 | 2.3 | 1.83 | 1.24
2025-10-06 | 23.5 | 0 | 5.5 | 2024-10-06 | 12.9 | 5.1 | 0 | 2023-10-06 | 18.6 | 0 | 0.6 | 2022-10-06 | 17.3 | 0.7 | 0 | 2021-10-06 | 15.4 | 2.6 | 0 | 2020-10-06 | 14.2 | 3.8 | 0 | 2019-10-06 | 16.4 | 1.6 | 0 | 2018-10-06 | 8 | 10 | 0 | 2017-10-06 | 14.3 | 3.7 | 0 | 2016-10-06 | 17.4 | 0.6 | 0 | 2.81 | 0.61
2025-10-06 | 21.8 | 0 | 3.8 | 2024-10-06 | 12.5 | 5.5 | 0 | 2023-10-06 | 17.8 | 0.2 | 0 | 2022-10-06 | 16.2 | 1.8 | 0 | 2021-10-06 | 13.6 | 4.4 | 0 | 2020-10-06 | 14.3 | 3.7 | 0 | 2019-10-06 | 16.1 | 1.9 | 0 | 2018-10-06 | 8 | 10 | 0 | 2017-10-06 | 13 | 5 | 0 | 2016-10-06 | 15.9 | 2.1 | 0 | 3.46 | 0.38
2025-10-06 | 20.5 | 0 | 2.5 | 2024-10-06 | 12.1 | 5.9 | 0 | 2023-10-06 | 17.5 | 0.5 | 0 | 2022-10-06 | 16 | 2 | 0 | 2021-10-06 | 13.3 | 4.7 | 0 | 2020-10-06 | 14.1 | 3.9 | 0 | 2019-10-06 | 15.6 | 2.4 | 0 | 2018-10-06 | 8.1 | 9.9 | 0 | 2017-10-06 | 11.1 | 6.9 | 0 | 2016-10-06 | 16.5 | 1.5 | 0 | 3.77 | 0.25
2025-10-06 | 20.1 | 0 | 2.1 | 2024-10-06 | 11.1 | 6.9 | 0 | 2023-10-06 | 17.1 | 0.9 | 0 | 2022-10-06 | 15.3 | 2.7 | 0 | 2021-10-06 | 11.7 | 6.3 | 0 | 2020-10-06 | 14.1 | 3.9 | 0 | 2019-10-06 | 15.1 | 2.9 | 0 | 2018-10-06 | 8.4 | 9.6 | 0 | 2017-10-06 | 11.2 | 6.8 | 0 | 2016-10-06 | 16 | 2 | 0 | 4.2 | 0.21
2025-10-06 | 19.6 | 0 | 1.6 | 2024-10-06 | 9.2 | 8.8 | 0 | 2023-10-06 | 16.6 | 1.4 | 0 | 2022-10-06 | 14.8 | 3.2 | 0 | 2021-10-06 | 11.8 | 6.2 | 0 | 2020-10-06 | 14.5 | 3.5 | 0 | 2019-10-06 | 15.4 | 2.6 | 0 | 2018-10-06 | 8.7 | 9.3 | 0 | 2017-10-06 | 11.2 | 6.8 | 0 | 2016-10-06 | 12.9 | 5.1 | 0 | 4.69 | 0.16
2025-10-06 | 18.9 | 0 | 0.9 | 2024-10-06 | 9.9 | 8.1 | 0 | 2023-10-06 | 16.3 | 1.7 | 0 | 2022-10-06 | 14.4 | 3.6 | 0 | 2021-10-06 | 10.1 | 7.9 | 0 | 2020-10-06 | 14.6 | 3.4 | 0 | 2019-10-06 | 15.2 | 2.8 | 0 | 2018-10-06 | 8.3 | 9.7 | 0 | 2017-10-06 | 10.7 | 7.3 | 0 | 2016-10-06 | 12.3 | 5.7 | 0 | 5.02 | 0.09
2025-10-07 | 17.6 | 0.4 | 0 | 2024-10-07 | 8.5 | 9.5 | 0 | 2023-10-07 | 15.8 | 2.2 | 0 | 2022-10-07 | 14.1 | 3.9 | 0 | 2021-10-07 | 10.3 | 7.7 | 0 | 2020-10-07 | 13.7 | 4.3 | 0 | 2019-10-07 | 14.3 | 3.7 | 0 | 2018-10-07 | 8.7 | 9.3 | 0 | 2017-10-07 | 10.6 | 7.4 | 0 | 2016-10-07 | 9.8 | 8.2 | 0 | 5.66 | 0
2025-10-07 | 18 | 0 | 0 | 2024-10-07 | 8.4 | 9.6 | 0 | 2023-10-07 | 16.7 | 1.3 | 0 | 2022-10-07 | 14.4 | 3.6 | 0 | 2021-10-07 | 8.9 | 9.1 | 0 | 2020-10-07 | 12.1 | 5.9 | 0 | 2019-10-07 | 12.5 | 5.5 | 0 | 2018-10-07 | 9.2 | 8.8 | 0 | 2017-10-07 | 10.4 | 7.6 | 0 | 2016-10-07 | 10 | 8 | 0 | 5.94 | 0
2025-10-07 | 16.7 | 1.3 | 0 | 2024-10-07 | 7.6 | 10.4 | 0 | 2023-10-07 | 16.5 | 1.5 | 0 | 2022-10-07 | 14.1 | 3.9 | 0 | 2021-10-07 | 8.2 | 9.8 | 0 | 2020-10-07 | 9.6 | 8.4 | 0 | 2019-10-07 | 13 | 5 | 0 | 2018-10-07 | 9.2 | 8.8 | 0 | 2017-10-07 | 7.8 | 10.2 | 0 | 2016-10-07 | 9.3 | 8.7 | 0 | 6.8 | 0
2025-10-07 | 15.9 | 2.1 | 0 | 2024-10-07 | 9.5 | 8.5 | 0 | 2023-10-07 | 15.7 | 2.3 | 0 | 2022-10-07 | 12.6 | 5.4 | 0 | 2021-10-07 | 7.6 | 10.4 | 0 | 2020-10-07 | 10.6 | 7.4 | 0 | 2019-10-07 | 12.6 | 5.4 | 0 | 2018-10-07 | 9.5 | 8.5 | 0 | 2017-10-07 | 8.8 | 9.2 | 0 | 2016-10-07 | 11 | 7 | 0 | 6.62 | 0
2025-10-07 | 15.7 | 2.3 | 0 | 2024-10-07 | 10 | 8 | 0 | 2023-10-07 | 14.7 | 3.3 | 0 | 2022-10-07 | 12.6 | 5.4 | 0 | 2021-10-07 | 8.6 | 9.4 | 0 | 2020-10-07 | 11.9 | 6.1 | 0 | 2019-10-07 | 12.1 | 5.9 | 0 | 2018-10-07 | 9.3 | 8.7 | 0 | 2017-10-07 | 9.7 | 8.3 | 0 | 2016-10-07 | 10.4 | 7.6 | 0 | 6.5 | 0
2025-10-07 | 16 | 2 | 0 | 2024-10-07 | 10.1 | 7.9 | 0 | 2023-10-07 | 14.4 | 3.6 | 0 | 2022-10-07 | 12.3 | 5.7 | 0 | 2021-10-07 | 8 | 10 | 0 | 2020-10-07 | 11.9 | 6.1 | 0 | 2019-10-07 | 12.1 | 5.9 | 0 | 2018-10-07 | 9.1 | 8.9 | 0 | 2017-10-07 | 10 | 8 | 0 | 2016-10-07 | 7.6 | 10.4 | 0 | 6.85 | 0
2025-10-07 | 16.9 | 1.1 | 0 | 2024-10-07 | 9.6 | 8.4 | 0 | 2023-10-07 | 13.7 | 4.3 | 0 | 2022-10-07 | 10.8 | 7.2 | 0 | 2021-10-07 | 7.7 | 10.3 | 0 | 2020-10-07 | 12.6 | 5.4 | 0 | 2019-10-07 | 12 | 6 | 0 | 2018-10-07 | 8.3 | 9.7 | 0 | 2017-10-07 | 10.7 | 7.3 | 0 | 2016-10-07 | 8.7 | 9.3 | 0 | 6.9 | 0
2025-10-07 | 17.7 | 0.3 | 0 | 2024-10-07 | 9.6 | 8.4 | 0 | 2023-10-07 | 13.8 | 4.2 | 0 | 2022-10-07 | 9.8 | 8.2 | 0 | 2021-10-07 | 9.4 | 8.6 | 0 | 2020-10-07 | 12.3 | 5.7 | 0 | 2019-10-07 | 11.9 | 6.1 | 0 | 2018-10-07 | 8.2 | 9.8 | 0 | 2017-10-07 | 11.5 | 6.5 | 0 | 2016-10-07 | 9.5 | 8.5 | 0 | 6.63 | 0
2025-10-07 | 18.9 | 0 | 0.9 | 2024-10-07 | 10.8 | 7.2 | 0 | 2023-10-07 | 13.9 | 4.1 | 0 | 2022-10-07 | 9.3 | 8.7 | 0 | 2021-10-07 | 11.4 | 6.6 | 0 | 2020-10-07 | 12.9 | 5.1 | 0 | 2019-10-07 | 11.8 | 6.2 | 0 | 2018-10-07 | 8.5 | 9.5 | 0 | 2017-10-07 | 12.3 | 5.7 | 0 | 2016-10-07 | 11.6 | 6.4 | 0 | 5.95 | 0.09
2025-10-07 | 16.4 | 1.6 | 0 | 2024-10-07 | 12.3 | 5.7 | 0 | 2023-10-07 | 14.4 | 3.6 | 0 | 2022-10-07 | 9.6 | 8.4 | 0 | 2021-10-07 | 12.6 | 5.4 | 0 | 2020-10-07 | 13.3 | 4.7 | 0 | 2019-10-07 | 12.6 | 5.4 | 0 | 2018-10-07 | 8.3 | 9.7 | 0 | 2017-10-07 | 12.8 | 5.2 | 0 | 2016-10-07 | 15 | 3 | 0 | 5.27 | 0
2025-10-07 | 17.4 | 0.6 | 0 | 2024-10-07 | 12.4 | 5.6 | 0 | 2023-10-07 | 14.6 | 3.4 | 0 | 2022-10-07 | 9.2 | 8.8 | 0 | 2021-10-07 | 14.4 | 3.6 | 0 | 2020-10-07 | 14.3 | 3.7 | 0 | 2019-10-07 | 14.7 | 3.3 | 0 | 2018-10-07 | 9.2 | 8.8 | 0 | 2017-10-07 | 13.8 | 4.2 | 0 | 2016-10-07 | 18.6 | 0 | 0.6 | 4.2 | 0.06
2025-10-07 | 18.1 | 0 | 0.1 | 2024-10-07 | 12.5 | 5.5 | 0 | 2023-10-07 | 15 | 3 | 0 | 2022-10-07 | 9.2 | 8.8 | 0 | 2021-10-07 | 16.7 | 1.3 | 0 | 2020-10-07 | 14.4 | 3.6 | 0 | 2019-10-07 | 17.3 | 0.7 | 0 | 2018-10-07 | 9.4 | 8.6 | 0 | 2017-10-07 | 15.2 | 2.8 | 0 | 2016-10-07 | 21.1 | 0 | 3.1 | 3.43 | 0.32
2025-10-07 | 19.1 | 0 | 1.1 | 2024-10-07 | 12.7 | 5.3 | 0 | 2023-10-07 | 15.9 | 2.1 | 0 | 2022-10-07 | 9.7 | 8.3 | 0 | 2021-10-07 | 18.4 | 0 | 0.4 | 2020-10-07 | 16.1 | 1.9 | 0 | 2019-10-07 | 16.9 | 1.1 | 0 | 2018-10-07 | 10.3 | 7.7 | 0 | 2017-10-07 | 16.9 | 1.1 | 0 | 2016-10-07 | 22.5 | 0 | 4.5 | 2.75 | 0.6
2025-10-07 | 18.5 | 0 | 0.5 | 2024-10-07 | 13.2 | 4.8 | 0 | 2023-10-07 | 14 | 4 | 0 | 2022-10-07 | 8.5 | 9.5 | 0 | 2021-10-07 | 19.5 | 0 | 1.5 | 2020-10-07 | 13.2 | 4.8 | 0 | 2019-10-07 | 16.6 | 1.4 | 0 | 2018-10-07 | 10.8 | 7.2 | 0 | 2017-10-07 | 19.5 | 0 | 1.5 | 2016-10-07 | 23.7 | 0 | 5.7 | 3.17 | 0.92
2025-10-07 | 18.7 | 0 | 0.7 | 2024-10-07 | 12.8 | 5.2 | 0 | 2023-10-07 | 13.2 | 4.8 | 0 | 2022-10-07 | 7.7 | 10.3 | 0 | 2021-10-07 | 19 | 0 | 1 | 2020-10-07 | 15.3 | 2.7 | 0 | 2019-10-07 | 17.1 | 0.9 | 0 | 2018-10-07 | 11.2 | 6.8 | 0 | 2017-10-07 | 21.1 | 0 | 3.1 | 2016-10-07 | 24.2 | 0 | 6.2 | 3.07 | 1.1
2025-10-07 | 18.5 | 0 | 0.5 | 2024-10-07 | 12.6 | 5.4 | 0 | 2023-10-07 | 11.3 | 6.7 | 0 | 2022-10-07 | 8.7 | 9.3 | 0 | 2021-10-07 | 19.8 | 0 | 1.8 | 2020-10-07 | 13.6 | 4.4 | 0 | 2019-10-07 | 16.9 | 1.1 | 0 | 2018-10-07 | 11 | 7 | 0 | 2017-10-07 | 19.8 | 0 | 1.8 | 2016-10-07 | 24 | 0 | 6 | 3.39 | 1.01
2025-10-07 | 18.3 | 0 | 0.3 | 2024-10-07 | 11.6 | 6.4 | 0 | 2023-10-07 | 10.6 | 7.4 | 0 | 2022-10-07 | 8.1 | 9.9 | 0 | 2021-10-07 | 18.1 | 0 | 0.1 | 2020-10-07 | 12.1 | 5.9 | 0 | 2019-10-07 | 16.2 | 1.8 | 0 | 2018-10-07 | 10.6 | 7.4 | 0 | 2017-10-07 | 19.7 | 0 | 1.7 | 2016-10-07 | 23.1 | 0 | 5.1 | 3.88 | 0.72
2025-10-07 | 16.1 | 1.9 | 0 | 2024-10-07 | 10.7 | 7.3 | 0 | 2023-10-07 | 9.8 | 8.2 | 0 | 2022-10-07 | 7.9 | 10.1 | 0 | 2021-10-07 | 17.6 | 0.4 | 0 | 2020-10-07 | 10.2 | 7.8 | 0 | 2019-10-07 | 15.2 | 2.8 | 0 | 2018-10-07 | 10.1 | 7.9 | 0 | 2017-10-07 | 19.4 | 0 | 1.4 | 2016-10-07 | 21.2 | 0 | 3.2 | 4.64 | 0.46
2025-10-07 | 15.4 | 2.6 | 0 | 2024-10-07 | 7.8 | 10.2 | 0 | 2023-10-07 | 9.4 | 8.6 | 0 | 2022-10-07 | 7.2 | 10.8 | 0 | 2021-10-07 | 15.9 | 2.1 | 0 | 2020-10-07 | 10.5 | 7.5 | 0 | 2019-10-07 | 14.8 | 3.2 | 0 | 2018-10-07 | 9.6 | 8.4 | 0 | 2017-10-07 | 19.1 | 0 | 1.1 | 2016-10-07 | 18.5 | 0 | 0.5 | 5.34 | 0.16
2025-10-07 | 14.7 | 3.3 | 0 | 2024-10-07 | 8.1 | 9.9 | 0 | 2023-10-07 | 9.2 | 8.8 | 0 | 2022-10-07 | 5.9 | 12.1 | 0 | 2021-10-07 | 14.2 | 3.8 | 0 | 2020-10-07 | 10.9 | 7.1 | 0 | 2019-10-07 | 14.1 | 3.9 | 0 | 2018-10-07 | 9.1 | 8.9 | 0 | 2017-10-07 | 18.9 | 0 | 0.9 | 2016-10-07 | 17.3 | 0.7 | 0 | 5.85 | 0.09
2025-10-07 | 13.6 | 4.4 | 0 | 2024-10-07 | 4.9 | 13.1 | 0 | 2023-10-07 | 9.2 | 8.8 | 0 | 2022-10-07 | 4.5 | 13.5 | 0 | 2021-10-07 | 13.2 | 4.8 | 0 | 2020-10-07 | 10.1 | 7.9 | 0 | 2019-10-07 | 13.4 | 4.6 | 0 | 2018-10-07 | 8.7 | 9.3 | 0 | 2017-10-07 | 18.7 | 0 | 0.7 | 2016-10-07 | 15.1 | 2.9 | 0 | 6.93 | 0.07
2025-10-07 | 13.7 | 4.3 | 0 | 2024-10-07 | 5.1 | 12.9 | 0 | 2023-10-07 | 9.1 | 8.9 | 0 | 2022-10-07 | 3.8 | 14.2 | 0 | 2021-10-07 | 12.1 | 5.9 | 0 | 2020-10-07 | 9.4 | 8.6 | 0 | 2019-10-07 | 11.1 | 6.9 | 0 | 2018-10-07 | 8.2 | 9.8 | 0 | 2017-10-07 | 18.7 | 0 | 0.7 | 2016-10-07 | 15.3 | 2.7 | 0 | 7.42 | 0.07
2025-10-07 | 12.5 | 5.5 | 0 | 2024-10-07 | 5 | 13 | 0 | 2023-10-07 | 9.5 | 8.5 | 0 | 2022-10-07 | 3.2 | 14.8 | 0 | 2021-10-07 | 11.2 | 6.8 | 0 | 2020-10-07 | 8.7 | 9.3 | 0 | 2019-10-07 | 9.8 | 8.2 | 0 | 2018-10-07 | 7.7 | 10.3 | 0 | 2017-10-07 | 18.4 | 0 | 0.4 | 2016-10-07 | 16.6 | 1.4 | 0 | 7.78 | 0.04
2025-10-07 | 12.6 | 5.4 | 0 | 2024-10-07 | 4.3 | 13.7 | 0 | 2023-10-07 | 9.5 | 8.5 | 0 | 2022-10-07 | 2.4 | 15.6 | 0 | 2021-10-07 | 10 | 8 | 0 | 2020-10-07 | 7.3 | 10.7 | 0 | 2019-10-07 | 8.6 | 9.4 | 0 | 2018-10-07 | 7.5 | 10.5 | 0 | 2017-10-07 | 18.4 | 0 | 0.4 | 2016-10-07 | 16 | 2 | 0 | 8.38 | 0.04
2025-10-08 | 12.5 | 5.5 | 0 | 2024-10-08 | 3.9 | 14.1 | 0 | 2023-10-08 | 9.5 | 8.5 | 0 | 2022-10-08 | 1.6 | 16.4 | 0 | 2021-10-08 | 10.3 | 7.7 | 0 | 2020-10-08 | 7.3 | 10.7 | 0 | 2019-10-08 | 8.1 | 9.9 | 0 | 2018-10-08 | 7.4 | 10.6 | 0 | 2017-10-08 | 18.4 | 0 | 0.4 | 2016-10-08 | 15.6 | 2.4 | 0 | 8.58 | 0.04
2025-10-08 | 11 | 7 | 0 | 2024-10-08 | 2.8 | 15.2 | 0 | 2023-10-08 | 9.3 | 8.7 | 0 | 2022-10-08 | 0 | 18 | 0 | 2021-10-08 | 8.9 | 9.1 | 0 | 2020-10-08 | 6.3 | 11.7 | 0 | 2019-10-08 | 7.3 | 10.7 | 0 | 2018-10-08 | 7.3 | 10.7 | 0 | 2017-10-08 | 18.7 | 0 | 0.7 | 2016-10-08 | 15 | 3 | 0 | 9.41 | 0.07
2025-10-08 | 11 | 7 | 0 | 2024-10-08 | 2.9 | 15.1 | 0 | 2023-10-08 | 8.9 | 9.1 | 0 | 2022-10-08 | -0.9 | 18.9 | 0 | 2021-10-08 | 9.6 | 8.4 | 0 | 2020-10-08 | 5.7 | 12.3 | 0 | 2019-10-08 | 6.4 | 11.6 | 0 | 2018-10-08 | 7.1 | 10.9 | 0 | 2017-10-08 | 20.5 | 0 | 2.5 | 2016-10-08 | 14.5 | 3.5 | 0 | 9.68 | 0.25
2025-10-08 | 10.8 | 7.2 | 0 | 2024-10-08 | 3 | 15 | 0 | 2023-10-08 | 8.2 | 9.8 | 0 | 2022-10-08 | -1.8 | 19.8 | 0 | 2021-10-08 | 8.2 | 9.8 | 0 | 2020-10-08 | 5.3 | 12.7 | 0 | 2019-10-08 | 5.2 | 12.8 | 0 | 2018-10-08 | 6.9 | 11.1 | 0 | 2017-10-08 | 19.3 | 0 | 1.3 | 2016-10-08 | 15.8 | 2.2 | 0 | 10.04 | 0.13
2025-10-08 | 8.8 | 9.2 | 0 | 2024-10-08 | 1.8 | 16.2 | 0 | 2023-10-08 | 7.4 | 10.6 | 0 | 2022-10-08 | -1.5 | 19.5 | 0 | 2021-10-08 | 7.8 | 10.2 | 0 | 2020-10-08 | 4.3 | 13.7 | 0 | 2019-10-08 | 4.8 | 13.2 | 0 | 2018-10-08 | 6.1 | 11.9 | 0 | 2017-10-08 | 19.7 | 0 | 1.7 | 2016-10-08 | 16.2 | 1.8 | 0 | 10.63 | 0.17
2025-10-08 | 8.3 | 9.7 | 0 | 2024-10-08 | 2 | 16 | 0 | 2023-10-08 | 7.1 | 10.9 | 0 | 2022-10-08 | -1.3 | 19.3 | 0 | 2021-10-08 | 6.4 | 11.6 | 0 | 2020-10-08 | 4.3 | 13.7 | 0 | 2019-10-08 | 3.8 | 14.2 | 0 | 2018-10-08 | 6 | 12 | 0 | 2017-10-08 | 18.6 | 0 | 0.6 | 2016-10-08 | 16.6 | 1.4 | 0 | 10.88 | 0.06
2025-10-08 | 8.6 | 9.4 | 0 | 2024-10-08 | 2.4 | 15.6 | 0 | 2023-10-08 | 7 | 11 | 0 | 2022-10-08 | -1.8 | 19.8 | 0 | 2021-10-08 | 7 | 11 | 0 | 2020-10-08 | 4.6 | 13.4 | 0 | 2019-10-08 | 4.5 | 13.5 | 0 | 2018-10-08 | 6.1 | 11.9 | 0 | 2017-10-08 | 20.2 | 0 | 2.2 | 2016-10-08 | 16.7 | 1.3 | 0 | 10.69 | 0.22
2025-10-08 | 8.9 | 9.1 | 0 | 2024-10-08 | 2.6 | 15.4 | 0 | 2023-10-08 | 7.3 | 10.7 | 0 | 2022-10-08 | -0.8 | 18.8 | 0 | 2021-10-08 | 7.6 | 10.4 | 0 | 2020-10-08 | 4.9 | 13.1 | 0 | 2019-10-08 | 4.9 | 13.1 | 0 | 2018-10-08 | 6.3 | 11.7 | 0 | 2017-10-08 | 20.6 | 0 | 2.6 | 2016-10-08 | 16.7 | 1.3 | 0 | 10.36 | 0.26
2025-10-08 | 11.9 | 6.1 | 0 | 2024-10-08 | 4.8 | 13.2 | 0 | 2023-10-08 | 8.1 | 9.9 | 0 | 2022-10-08 | 2.1 | 15.9 | 0 | 2021-10-08 | 11.5 | 6.5 | 0 | 2020-10-08 | 5.6 | 12.4 | 0 | 2019-10-08 | 7.9 | 10.1 | 0 | 2018-10-08 | 7 | 11 | 0 | 2017-10-08 | 21.2 | 0 | 3.2 | 2016-10-08 | 16.4 | 1.6 | 0 | 8.67 | 0.32
2025-10-08 | 12.3 | 5.7 | 0 | 2024-10-08 | 6.5 | 11.5 | 0 | 2023-10-08 | 9.5 | 8.5 | 0 | 2022-10-08 | 5.2 | 12.8 | 0 | 2021-10-08 | 15.2 | 2.8 | 0 | 2020-10-08 | 5.9 | 12.1 | 0 | 2019-10-08 | 10.5 | 7.5 | 0 | 2018-10-08 | 7.5 | 10.5 | 0 | 2017-10-08 | 21.2 | 0 | 3.2 | 2016-10-08 | 16.2 | 1.8 | 0 | 7.32 | 0.32
2025-10-08 | 12.2 | 5.8 | 0 | 2024-10-08 | 8.7 | 9.3 | 0 | 2023-10-08 | 10.6 | 7.4 | 0 | 2022-10-08 | 4.9 | 13.1 | 0 | 2021-10-08 | 17.7 | 0.3 | 0 | 2020-10-08 | 6.6 | 11.4 | 0 | 2019-10-08 | 12.8 | 5.2 | 0 | 2018-10-08 | 8.3 | 9.7 | 0 | 2017-10-08 | 20.8 | 0 | 2.8 | 2016-10-08 | 15.8 | 2.2 | 0 | 6.44 | 0.28
2025-10-08 | 12.3 | 5.7 | 0 | 2024-10-08 | 10.8 | 7.2 | 0 | 2023-10-08 | 11.7 | 6.3 | 0 | 2022-10-08 | 4.8 | 13.2 | 0 | 2021-10-08 | 19.3 | 0 | 1.3 | 2020-10-08 | 6.9 | 11.1 | 0 | 2019-10-08 | 14.4 | 3.6 | 0 | 2018-10-08 | 8.9 | 9.1 | 0 | 2017-10-08 | 21.3 | 0 | 3.3 | 2016-10-08 | 15.7 | 2.3 | 0 | 5.85 | 0.46
2025-10-08 | 13.1 | 4.9 | 0 | 2024-10-08 | 12.7 | 5.3 | 0 | 2023-10-08 | 11.4 | 6.6 | 0 | 2022-10-08 | 6.2 | 11.8 | 0 | 2021-10-08 | 21.2 | 0 | 3.2 | 2020-10-08 | 7.5 | 10.5 | 0 | 2019-10-08 | 15.1 | 2.9 | 0 | 2018-10-08 | 9.4 | 8.6 | 0 | 2017-10-08 | 21.8 | 0 | 3.8 | 2016-10-08 | 11.5 | 6.5 | 0 | 5.71 | 0.7
2025-10-08 | 12.7 | 5.3 | 0 | 2024-10-08 | 13.8 | 4.2 | 0 | 2023-10-08 | 11 | 7 | 0 | 2022-10-08 | 7.4 | 10.6 | 0 | 2021-10-08 | 22 | 0 | 4 | 2020-10-08 | 8.1 | 9.9 | 0 | 2019-10-08 | 15.8 | 2.2 | 0 | 2018-10-08 | 8.5 | 9.5 | 0 | 2017-10-08 | 22 | 0 | 4 | 2016-10-08 | 11 | 7 | 0 | 5.57 | 0.8
2025-10-08 | 11.3 | 6.7 | 0 | 2024-10-08 | 14.3 | 3.7 | 0 | 2023-10-08 | 12.1 | 5.9 | 0 | 2022-10-08 | 9.3 | 8.7 | 0 | 2021-10-08 | 22.6 | 0 | 4.6 | 2020-10-08 | 9.3 | 8.7 | 0 | 2019-10-08 | 16.7 | 1.3 | 0 | 2018-10-08 | 8.2 | 9.8 | 0 | 2017-10-08 | 22.5 | 0 | 4.5 | 2016-10-08 | 12.2 | 5.8 | 0 | 5.06 | 0.91
2025-10-08 | 11.4 | 6.6 | 0 | 2024-10-08 | 12.6 | 5.4 | 0 | 2023-10-08 | 10.4 | 7.6 | 0 | 2022-10-08 | 8.6 | 9.4 | 0 | 2021-10-08 | 22.4 | 0 | 4.4 | 2020-10-08 | 9.2 | 8.8 | 0 | 2019-10-08 | 16.3 | 1.7 | 0 | 2018-10-08 | 8.1 | 9.9 | 0 | 2017-10-08 | 21.3 | 0 | 3.3 | 2016-10-08 | 15 | 3 | 0 | 5.24 | 0.77
2025-10-08 | 11.2 | 6.8 | 0 | 2024-10-08 | 13 | 5 | 0 | 2023-10-08 | 8.6 | 9.4 | 0 | 2022-10-08 | 8.5 | 9.5 | 0 | 2021-10-08 | 21.9 | 0 | 3.9 | 2020-10-08 | 9.1 | 8.9 | 0 | 2019-10-08 | 16.2 | 1.8 | 0 | 2018-10-08 | 8 | 10 | 0 | 2017-10-08 | 21.3 | 0 | 3.3 | 2016-10-08 | 14.9 | 3.1 | 0 | 5.45 | 0.72
2025-10-08 | 11.1 | 6.9 | 0 | 2024-10-08 | 10.4 | 7.6 | 0 | 2023-10-08 | 9.2 | 8.8 | 0 | 2022-10-08 | 8.3 | 9.7 | 0 | 2021-10-08 | 19.7 | 0 | 1.7 | 2020-10-08 | 7.6 | 10.4 | 0 | 2019-10-08 | 14.8 | 3.2 | 0 | 2018-10-08 | 7.6 | 10.4 | 0 | 2017-10-08 | 20.2 | 0 | 2.2 | 2016-10-08 | 13.3 | 4.7 | 0 | 6.17 | 0.39
2025-10-08 | 8.8 | 9.2 | 0 | 2024-10-08 | 8.5 | 9.5 | 0 | 2023-10-08 | 6.2 | 11.8 | 0 | 2022-10-08 | 7.9 | 10.1 | 0 | 2021-10-08 | 16.4 | 1.6 | 0 | 2020-10-08 | 6.6 | 11.4 | 0 | 2019-10-08 | 12.6 | 5.4 | 0 | 2018-10-08 | 7.4 | 10.6 | 0 | 2017-10-08 | 18 | 0 | 0 | 2016-10-08 | 12.8 | 5.2 | 0 | 7.48 | 0
2025-10-08 | 8.1 | 9.9 | 0 | 2024-10-08 | 8.4 | 9.6 | 0 | 2023-10-08 | 4.4 | 13.6 | 0 | 2022-10-08 | 7.7 | 10.3 | 0 | 2021-10-08 | 16.3 | 1.7 | 0 | 2020-10-08 | 4.7 | 13.3 | 0 | 2019-10-08 | 6.8 | 11.2 | 0 | 2018-10-08 | 7.3 | 10.7 | 0 | 2017-10-08 | 17.3 | 0.7 | 0 | 2016-10-08 | 12.2 | 5.8 | 0 | 8.68 | 0
2025-10-08 | 6.9 | 11.1 | 0 | 2024-10-08 | 6.7 | 11.3 | 0 | 2023-10-08 | 4.6 | 13.4 | 0 | 2022-10-08 | 7.9 | 10.1 | 0 | 2021-10-08 | 15.6 | 2.4 | 0 | 2020-10-08 | 4.2 | 13.8 | 0 | 2019-10-08 | 8.7 | 9.3 | 0 | 2018-10-08 | 7.4 | 10.6 | 0 | 2017-10-08 | 16.4 | 1.6 | 0 | 2016-10-08 | 12.1 | 5.9 | 0 | 8.95 | 0
2025-10-08 | 6.4 | 11.6 | 0 | 2024-10-08 | 6.5 | 11.5 | 0 | 2023-10-08 | 4.3 | 13.7 | 0 | 2022-10-08 | 7.5 | 10.5 | 0 | 2021-10-08 | 15.4 | 2.6 | 0 | 2020-10-08 | 3.9 | 14.1 | 0 | 2019-10-08 | 7.7 | 10.3 | 0 | 2018-10-08 | 7.5 | 10.5 | 0 | 2017-10-08 | 15.8 | 2.2 | 0 | 2016-10-08 | 11.7 | 6.3 | 0 | 9.33 | 0
2025-10-08 | 6.1 | 11.9 | 0 | 2024-10-08 | 4.8 | 13.2 | 0 | 2023-10-08 | 4.4 | 13.6 | 0 | 2022-10-08 | 6.8 | 11.2 | 0 | 2021-10-08 | 14.6 | 3.4 | 0 | 2020-10-08 | 3.4 | 14.6 | 0 | 2019-10-08 | 6.6 | 11.4 | 0 | 2018-10-08 | 7.8 | 10.2 | 0 | 2017-10-08 | 15.2 | 2.8 | 0 | 2016-10-08 | 10.8 | 7.2 | 0 | 9.95 | 0
2025-10-08 | 4.2 | 13.8 | 0 | 2024-10-08 | 3.9 | 14.1 | 0 | 2023-10-08 | 4.6 | 13.4 | 0 | 2022-10-08 | 6.8 | 11.2 | 0 | 2021-10-08 | 14.1 | 3.9 | 0 | 2020-10-08 | 2.1 | 15.9 | 0 | 2019-10-08 | 4.9 | 13.1 | 0 | 2018-10-08 | 7.8 | 10.2 | 0 | 2017-10-08 | 14.6 | 3.4 | 0 | 2016-10-08 | 9.3 | 8.7 | 0 | 10.77 | 0
2025-10-09 | 4.5 | 13.5 | 0 | 2024-10-09 | 4.8 | 13.2 | 0 | 2023-10-09 | 4.9 | 13.1 | 0 | 2022-10-09 | 7 | 11 | 0 | 2021-10-09 | 13.3 | 4.7 | 0 | 2020-10-09 | 1.4 | 16.6 | 0 | 2019-10-09 | 5.2 | 12.8 | 0 | 2018-10-09 | 8.1 | 9.9 | 0 | 2017-10-09 | 14.4 | 3.6 | 0 | 2016-10-09 | 8.5 | 9.5 | 0 | 10.79 | 0
2025-10-09 | 4.3 | 13.7 | 0 | 2024-10-09 | 2.8 | 15.2 | 0 | 2023-10-09 | 5.3 | 12.7 | 0 | 2022-10-09 | 7.4 | 10.6 | 0 | 2021-10-09 | 12.8 | 5.2 | 0 | 2020-10-09 | 1.6 | 16.4 | 0 | 2019-10-09 | 3.9 | 14.1 | 0 | 2018-10-09 | 8.3 | 9.7 | 0 | 2017-10-09 | 13.3 | 4.7 | 0 | 2016-10-09 | 7.3 | 10.7 | 0 | 11.3 | 0
2025-10-09 | 4.2 | 13.8 | 0 | 2024-10-09 | 2.4 | 15.6 | 0 | 2023-10-09 | 5.4 | 12.6 | 0 | 2022-10-09 | 7.9 | 10.1 | 0 | 2021-10-09 | 12.3 | 5.7 | 0 | 2020-10-09 | 1.7 | 16.3 | 0 | 2019-10-09 | 2.8 | 15.2 | 0 | 2018-10-09 | 8.5 | 9.5 | 0 | 2017-10-09 | 13.5 | 4.5 | 0 | 2016-10-09 | 5.5 | 12.5 | 0 | 11.58 | 0
2025-10-09 | 3.9 | 14.1 | 0 | 2024-10-09 | 2.5 | 15.5 | 0 | 2023-10-09 | 5.1 | 12.9 | 0 | 2022-10-09 | 8.1 | 9.9 | 0 | 2021-10-09 | 11.8 | 6.2 | 0 | 2020-10-09 | 1.5 | 16.5 | 0 | 2019-10-09 | 4.1 | 13.9 | 0 | 2018-10-09 | 8.7 | 9.3 | 0 | 2017-10-09 | 13.8 | 4.2 | 0 | 2016-10-09 | 5.2 | 12.8 | 0 | 11.53 | 0
2025-10-09 | 3.6 | 14.4 | 0 | 2024-10-09 | 2.1 | 15.9 | 0 | 2023-10-09 | 4.9 | 13.1 | 0 | 2022-10-09 | 8.3 | 9.7 | 0 | 2021-10-09 | 11.2 | 6.8 | 0 | 2020-10-09 | 0.6 | 17.4 | 0 | 2019-10-09 | 2.6 | 15.4 | 0 | 2018-10-09 | 8.9 | 9.1 | 0 | 2017-10-09 | 13.5 | 4.5 | 0 | 2016-10-09 | 6.7 | 11.3 | 0 | 11.76 | 0
2025-10-09 | 2.9 | 15.1 | 0 | 2024-10-09 | 3.6 | 14.4 | 0 | 2023-10-09 | 5.1 | 12.9 | 0 | 2022-10-09 | 8.3 | 9.7 | 0 | 2021-10-09 | 10.7 | 7.3 | 0 | 2020-10-09 | -0.5 | 18.5 | 0 | 2019-10-09 | 2.7 | 15.3 | 0 | 2018-10-09 | 9.2 | 8.8 | 0 | 2017-10-09 | 13.2 | 4.8 | 0 | 2016-10-09 | 5.3 | 12.7 | 0 | 11.95 | 0
2025-10-09 | 2.4 | 15.6 | 0 | 2024-10-09 | 2.8 | 15.2 | 0 | 2023-10-09 | 5.4 | 12.6 | 0 | 2022-10-09 | 8.5 | 9.5 | 0 | 2021-10-09 | 10.2 | 7.8 | 0 | 2020-10-09 | -0.1 | 18.1 | 0 | 2019-10-09 | 2.7 | 15.3 | 0 | 2018-10-09 | 9.4 | 8.6 | 0 | 2017-10-09 | 13.4 | 4.6 | 0 | 2016-10-09 | 4.5 | 13.5 | 0 | 12.08 | 0
2025-10-09 | 3.5 | 14.5 | 0 | 2024-10-09 | 4.4 | 13.6 | 0 | 2023-10-09 | 5.8 | 12.2 | 0 | 2022-10-09 | 7.4 | 10.6 | 0 | 2021-10-09 | 10.6 | 7.4 | 0 | 2020-10-09 | 0.3 | 17.7 | 0 | 2019-10-09 | 3.8 | 14.2 | 0 | 2018-10-09 | 10.2 | 7.8 | 0 | 2017-10-09 | 13.7 | 4.3 | 0 | 2016-10-09 | 4.6 | 13.4 | 0 | 11.57 | 0
2025-10-09 | 4.8 | 13.2 | 0 | 2024-10-09 | 6 | 12 | 0 | 2023-10-09 | 7.1 | 10.9 | 0 | 2022-10-09 | 7 | 11 | 0 | 2021-10-09 | 11.9 | 6.1 | 0 | 2020-10-09 | 4.2 | 13.8 | 0 | 2019-10-09 | 7.3 | 10.7 | 0 | 2018-10-09 | 11.4 | 6.6 | 0 | 2017-10-09 | 14.2 | 3.8 | 0 | 2016-10-09 | 7.5 | 10.5 | 0 | 9.86 | 0
2025-10-09 | 6.3 | 11.7 | 0 | 2024-10-09 | 7.3 | 10.7 | 0 | 2023-10-09 | 7.5 | 10.5 | 0 | 2022-10-09 | 7.1 | 10.9 | 0 | 2021-10-09 | 13.4 | 4.6 | 0 | 2020-10-09 | 7.9 | 10.1 | 0 | 2019-10-09 | 9.5 | 8.5 | 0 | 2018-10-09 | 19.4 | 0 | 1.4 | 2017-10-09 | 14.8 | 3.2 | 0 | 2016-10-09 | 9.2 | 8.8 | 0 | 7.9 | 0.14
2025-10-09 | 7.8 | 10.2 | 0 | 2024-10-09 | 8.8 | 9.2 | 0 | 2023-10-09 | 8 | 10 | 0 | 2022-10-09 | 9.1 | 8.9 | 0 | 2021-10-09 | 15.7 | 2.3 | 0 | 2020-10-09 | 10.7 | 7.3 | 0 | 2019-10-09 | 11.4 | 6.6 | 0 | 2018-10-09 | 21.3 | 0 | 3.3 | 2017-10-09 | 15.2 | 2.8 | 0 | 2016-10-09 | 9.9 | 8.1 | 0 | 6.54 | 0.33
2025-10-09 | 8.6 | 9.4 | 0 | 2024-10-09 | 9.1 | 8.9 | 0 | 2023-10-09 | 8.7 | 9.3 | 0 | 2022-10-09 | 10.1 | 7.9 | 0 | 2021-10-09 | 18.1 | 0 | 0.1 | 2020-10-09 | 12.5 | 5.5 | 0 | 2019-10-09 | 13.4 | 4.6 | 0 | 2018-10-09 | 23.9 | 0 | 5.9 | 2017-10-09 | 15.5 | 2.5 | 0 | 2016-10-09 | 9.9 | 8.1 | 0 | 5.62 | 0.6
2025-10-09 | 9.8 | 8.2 | 0 | 2024-10-09 | 9.4 | 8.6 | 0 | 2023-10-09 | 9.5 | 8.5 | 0 | 2022-10-09 | 11.2 | 6.8 | 0 | 2021-10-09 | 18 | 0 | 0 | 2020-10-09 | 14 | 4 | 0 | 2019-10-09 | 13.6 | 4.4 | 0 | 2018-10-09 | 25.2 | 0 | 7.2 | 2017-10-09 | 15.6 | 2.4 | 0 | 2016-10-09 | 11.1 | 6.9 | 0 | 4.98 | 0.72
2025-10-09 | 10.2 | 7.8 | 0 | 2024-10-09 | 9.2 | 8.8 | 0 | 2023-10-09 | 9.2 | 8.8 | 0 | 2022-10-09 | 10.1 | 7.9 | 0 | 2021-10-09 | 18.9 | 0 | 0.9 | 2020-10-09 | 14.3 | 3.7 | 0 | 2019-10-09 | 15.7 | 2.3 | 0 | 2018-10-09 | 26.4 | 0 | 8.4 | 2017-10-09 | 16.2 | 1.8 | 0 | 2016-10-09 | 11.3 | 6.7 | 0 | 4.78 | 0.93
2025-10-09 | 10.5 | 7.5 | 0 | 2024-10-09 | 9 | 9 | 0 | 2023-10-09 | 9.2 | 8.8 | 0 | 2022-10-09 | 10.7 | 7.3 | 0 | 2021-10-09 | 19.3 | 0 | 1.3 | 2020-10-09 | 13.5 | 4.5 | 0 | 2019-10-09 | 14.9 | 3.1 | 0 | 2018-10-09 | 27.1 | 0 | 9.1 | 2017-10-09 | 16.5 | 1.5 | 0 | 2016-10-09 | 10.9 | 7.1 | 0 | 4.88 | 1.04
2025-10-09 | 10.8 | 7.2 | 0 | 2024-10-09 | 8.9 | 9.1 | 0 | 2023-10-09 | 8.7 | 9.3 | 0 | 2022-10-09 | 10.6 | 7.4 | 0 | 2021-10-09 | 19.7 | 0 | 1.7 | 2020-10-09 | 14.1 | 3.9 | 0 | 2019-10-09 | 15.1 | 2.9 | 0 | 2018-10-09 | 26.7 | 0 | 8.7 | 2017-10-09 | 16.5 | 1.5 | 0 | 2016-10-09 | 9.8 | 8.2 | 0 | 4.95 | 1.04
2025-10-09 | 10.6 | 7.4 | 0 | 2024-10-09 | 7.7 | 10.3 | 0 | 2023-10-09 | 8.6 | 9.4 | 0 | 2022-10-09 | 10 | 8 | 0 | 2021-10-09 | 19.7 | 0 | 1.7 | 2020-10-09 | 13.5 | 4.5 | 0 | 2019-10-09 | 15.5 | 2.5 | 0 | 2018-10-09 | 25.9 | 0 | 7.9 | 2017-10-09 | 16.8 | 1.2 | 0 | 2016-10-09 | 9.7 | 8.3 | 0 | 5.16 | 0.96
2025-10-09 | 9.2 | 8.8 | 0 | 2024-10-09 | 7 | 11 | 0 | 2023-10-09 | 8.3 | 9.7 | 0 | 2022-10-09 | 8.5 | 9.5 | 0 | 2021-10-09 | 18.5 | 0 | 0.5 | 2020-10-09 | 13.1 | 4.9 | 0 | 2019-10-09 | 13.5 | 4.5 | 0 | 2018-10-09 | 25.1 | 0 | 7.1 | 2017-10-09 | 17.1 | 0.9 | 0 | 2016-10-09 | 9.2 | 8.8 | 0 | 5.81 | 0.76
2025-10-09 | 8.2 | 9.8 | 0 | 2024-10-09 | 6 | 12 | 0 | 2023-10-09 | 8 | 10 | 0 | 2022-10-09 | 7 | 11 | 0 | 2021-10-09 | 17.3 | 0.7 | 0 | 2020-10-09 | 11.9 | 6.1 | 0 | 2019-10-09 | 11.3 | 6.7 | 0 | 2018-10-09 | 23.8 | 0 | 5.8 | 2017-10-09 | 16.7 | 1.3 | 0 | 2016-10-09 | 9.1 | 8.9 | 0 | 6.65 | 0.58
2025-10-09 | 3.9 | 14.1 | 0 | 2024-10-09 | 5.6 | 12.4 | 0 | 2023-10-09 | 7.7 | 10.3 | 0 | 2022-10-09 | 5.7 | 12.3 | 0 | 2021-10-09 | 16.8 | 1.2 | 0 | 2020-10-09 | 11.3 | 6.7 | 0 | 2019-10-09 | 9.7 | 8.3 | 0 | 2018-10-09 | 23 | 0 | 5 | 2017-10-09 | 15 | 3 | 0 | 2016-10-09 | 7.6 | 10.4 | 0 | 7.87 | 0.5
2025-10-09 | 2.5 | 15.5 | 0 | 2024-10-09 | 5.3 | 12.7 | 0 | 2023-10-09 | 7.4 | 10.6 | 0 | 2022-10-09 | 4.4 | 13.6 | 0 | 2021-10-09 | 16 | 2 | 0 | 2020-10-09 | 11.1 | 6.9 | 0 | 2019-10-09 | 8.9 | 9.1 | 0 | 2018-10-09 | 22.9 | 0 | 4.9 | 2017-10-09 | 14.2 | 3.8 | 0 | 2016-10-09 | 6.2 | 11.8 | 0 | 8.6 | 0.49
2025-10-09 | 3 | 15 | 0 | 2024-10-09 | 5.4 | 12.6 | 0 | 2023-10-09 | 7.6 | 10.4 | 0 | 2022-10-09 | 3.3 | 14.7 | 0 | 2021-10-09 | 15.9 | 2.1 | 0 | 2020-10-09 | 10.5 | 7.5 | 0 | 2019-10-09 | 6.7 | 11.3 | 0 | 2018-10-09 | 23.1 | 0 | 5.1 | 2017-10-09 | 14.3 | 3.7 | 0 | 2016-10-09 | 5.8 | 12.2 | 0 | 8.95 | 0.51
2025-10-09 | 2 | 16 | 0 | 2024-10-09 | 5.1 | 12.9 | 0 | 2023-10-09 | 7 | 11 | 0 | 2022-10-09 | 3.6 | 14.4 | 0 | 2021-10-09 | 15 | 3 | 0 | 2020-10-09 | 10.4 | 7.6 | 0 | 2019-10-09 | 5.8 | 12.2 | 0 | 2018-10-09 | 22.5 | 0 | 4.5 | 2017-10-09 | 13.9 | 4.1 | 0 | 2016-10-09 | 5.1 | 12.9 | 0 | 9.41 | 0.45
2025-10-09 | 0.6 | 17.4 | 0 | 2024-10-09 | 4.3 | 13.7 | 0 | 2023-10-09 | 7 | 11 | 0 | 2022-10-09 | 2.9 | 15.1 | 0 | 2021-10-09 | 14 | 4 | 0 | 2020-10-09 | 10.6 | 7.4 | 0 | 2019-10-09 | 5.5 | 12.5 | 0 | 2018-10-09 | 21.4 | 0 | 3.4 | 2017-10-09 | 13.2 | 4.8 | 0 | 2016-10-09 | 2.2 | 15.8 | 0 | 10.17 | 0.34
2025-10-10 | 2 | 16 | 0 | 2024-10-10 | 4.2 | 13.8 | 0 | 2023-10-10 | 6.9 | 11.1 | 0 | 2022-10-10 | 1.8 | 16.2 | 0 | 2021-10-10 | 13.9 | 4.1 | 0 | 2020-10-10 | 12.8 | 5.2 | 0 | 2019-10-10 | 6.6 | 11.4 | 0 | 2018-10-10 | 20.4 | 0 | 2.4 | 2017-10-10 | 12.7 | 5.3 | 0 | 2016-10-10 | 4 | 14 | 0 | 9.71 | 0.24
2025-10-10 | 1.6 | 16.4 | 0 | 2024-10-10 | 4.5 | 13.5 | 0 | 2023-10-10 | 7.1 | 10.9 | 0 | 2022-10-10 | 2.9 | 15.1 | 0 | 2021-10-10 | 13.6 | 4.4 | 0 | 2020-10-10 | 14.2 | 3.8 | 0 | 2019-10-10 | 4 | 14 | 0 | 2018-10-10 | 19.7 | 0 | 1.7 | 2017-10-10 | 12.1 | 5.9 | 0 | 2016-10-10 | 2.3 | 15.7 | 0 | 9.97 | 0.17
2025-10-10 | 1.4 | 16.6 | 0 | 2024-10-10 | 4.4 | 13.6 | 0 | 2023-10-10 | 7.3 | 10.7 | 0 | 2022-10-10 | 4.2 | 13.8 | 0 | 2021-10-10 | 13.1 | 4.9 | 0 | 2020-10-10 | 16.2 | 1.8 | 0 | 2019-10-10 | 3.6 | 14.4 | 0 | 2018-10-10 | 19.2 | 0 | 1.2 | 2017-10-10 | 11.6 | 6.4 | 0 | 2016-10-10 | 1 | 17 | 0 | 9.92 | 0.12
2025-10-10 | 0.5 | 17.5 | 0 | 2024-10-10 | 3.8 | 14.2 | 0 | 2023-10-10 | 6.9 | 11.1 | 0 | 2022-10-10 | 3.6 | 14.4 | 0 | 2021-10-10 | 12.6 | 5.4 | 0 | 2020-10-10 | 17.1 | 0.9 | 0 | 2019-10-10 | 3.4 | 14.6 | 0 | 2018-10-10 | 19.2 | 0 | 1.2 | 2017-10-10 | 11.4 | 6.6 | 0 | 2016-10-10 | 2 | 16 | 0 | 10.07 | 0.12
2025-10-10 | 0.2 | 17.8 | 0 | 2024-10-10 | 3.9 | 14.1 | 0 | 2023-10-10 | 6.8 | 11.2 | 0 | 2022-10-10 | 3.1 | 14.9 | 0 | 2021-10-10 | 12.6 | 5.4 | 0 | 2020-10-10 | 16.9 | 1.1 | 0 | 2019-10-10 | 3.3 | 14.7 | 0 | 2018-10-10 | 19.4 | 0 | 1.4 | 2017-10-10 | 12.3 | 5.7 | 0 | 2016-10-10 | 0.3 | 17.7 | 0 | 10.26 | 0.14
2025-10-10 | -0.5 | 18.5 | 0 | 2024-10-10 | 4.7 | 13.3 | 0 | 2023-10-10 | 6.9 | 11.1 | 0 | 2022-10-10 | 1.7 | 16.3 | 0 | 2021-10-10 | 12.7 | 5.3 | 0 | 2020-10-10 | 16.4 | 1.6 | 0 | 2019-10-10 | 3.4 | 14.6 | 0 | 2018-10-10 | 18.7 | 0 | 0.7 | 2017-10-10 | 11.9 | 6.1 | 0 | 2016-10-10 | 0.7 | 17.3 | 0 | 10.41 | 0.07
2025-10-10 | -1.4 | 19.4 | 0 | 2024-10-10 | 4.2 | 13.8 | 0 | 2023-10-10 | 7 | 11 | 0 | 2022-10-10 | 2.8 | 15.2 | 0 | 2021-10-10 | 12.5 | 5.5 | 0 | 2020-10-10 | 15.8 | 2.2 | 0 | 2019-10-10 | 3.4 | 14.6 | 0 | 2018-10-10 | 18.9 | 0 | 0.9 | 2017-10-10 | 11.6 | 6.4 | 0 | 2016-10-10 | 0.6 | 17.4 | 0 | 10.55 | 0.09
2025-10-10 | -0.6 | 18.6 | 0 | 2024-10-10 | 4.1 | 13.9 | 0 | 2023-10-10 | 7.5 | 10.5 | 0 | 2022-10-10 | 4 | 14 | 0 | 2021-10-10 | 12.8 | 5.2 | 0 | 2020-10-10 | 16.5 | 1.5 | 0 | 2019-10-10 | 3.5 | 14.5 | 0 | 2018-10-10 | 18.8 | 0 | 0.8 | 2017-10-10 | 11.7 | 6.3 | 0 | 2016-10-10 | 1.1 | 16.9 | 0 | 10.14 | 0.08
2025-10-10 | 2.9 | 15.1 | 0 | 2024-10-10 | 5.1 | 12.9 | 0 | 2023-10-10 | 7.7 | 10.3 | 0 | 2022-10-10 | 5.1 | 12.9 | 0 | 2021-10-10 | 13.2 | 4.8 | 0 | 2020-10-10 | 17.1 | 0.9 | 0 | 2019-10-10 | 7.7 | 10.3 | 0 | 2018-10-10 | 19.5 | 0 | 1.5 | 2017-10-10 | 12.3 | 5.7 | 0 | 2016-10-10 | 3.8 | 14.2 | 0 | 8.71 | 0.15
2025-10-10 | 5.2 | 12.8 | 0 | 2024-10-10 | 6.4 | 11.6 | 0 | 2023-10-10 | 8 | 10 | 0 | 2022-10-10 | 6.2 | 11.8 | 0 | 2021-10-10 | 13.4 | 4.6 | 0 | 2020-10-10 | 19.1 | 0 | 1.1 | 2019-10-10 | 10.4 | 7.6 | 0 | 2018-10-10 | 21.3 | 0 | 3.3 | 2017-10-10 | 14.9 | 3.1 | 0 | 2016-10-10 | 5.7 | 12.3 | 0 | 7.38 | 0.44
2025-10-10 | 8.5 | 9.5 | 0 | 2024-10-10 | 7.3 | 10.7 | 0 | 2023-10-10 | 8.6 | 9.4 | 0 | 2022-10-10 | 9.1 | 8.9 | 0 | 2021-10-10 | 14.2 | 3.8 | 0 | 2020-10-10 | 20.6 | 0 | 2.6 | 2019-10-10 | 12.3 | 5.7 | 0 | 2018-10-10 | 23.3 | 0 | 5.3 | 2017-10-10 | 17.1 | 0.9 | 0 | 2016-10-10 | 6.1 | 11.9 | 0 | 6.08 | 0.79
2025-10-10 | 11.5 | 6.5 | 0 | 2024-10-10 | 8.2 | 9.8 | 0 | 2023-10-10 | 9.1 | 8.9 | 0 | 2022-10-10 | 9.2 | 8.8 | 0 | 2021-10-10 | 16.2 | 1.8 | 0 | 2020-10-10 | 21.5 | 0 | 3.5 | 2019-10-10 | 13.8 | 4.2 | 0 | 2018-10-10 | 25 | 0 | 7 | 2017-10-10 | 17.3 | 0.7 | 0 | 2016-10-10 | 7.4 | 10.6 | 0 | 5.13 | 1.05
2025-10-10 | 12.7 | 5.3 | 0 | 2024-10-10 | 9.7 | 8.3 | 0 | 2023-10-10 | 9.9 | 8.1 | 0 | 2022-10-10 | 10.3 | 7.7 | 0 | 2021-10-10 | 17 | 1 | 0 | 2020-10-10 | 21.4 | 0 | 3.4 | 2019-10-10 | 15.9 | 2.1 | 0 | 2018-10-10 | 25.6 | 0 | 7.6 | 2017-10-10 | 16.4 | 1.6 | 0 | 2016-10-10 | 8.9 | 9.1 | 0 | 4.32 | 1.1
2025-10-10 | 14.3 | 3.7 | 0 | 2024-10-10 | 10.4 | 7.6 | 0 | 2023-10-10 | 10.4 | 7.6 | 0 | 2022-10-10 | 10.3 | 7.7 | 0 | 2021-10-10 | 17.3 | 0.7 | 0 | 2020-10-10 | 20.8 | 0 | 2.8 | 2019-10-10 | 16.7 | 1.3 | 0 | 2018-10-10 | 26.2 | 0 | 8.2 | 2017-10-10 | 15.9 | 2.1 | 0 | 2016-10-10 | 10.2 | 7.8 | 0 | 3.85 | 1.1
2025-10-10 | 14.8 | 3.2 | 0 | 2024-10-10 | 11.1 | 6.9 | 0 | 2023-10-10 | 11.2 | 6.8 | 0 | 2022-10-10 | 10.8 | 7.2 | 0 | 2021-10-10 | 18.1 | 0 | 0.1 | 2020-10-10 | 22.5 | 0 | 4.5 | 2019-10-10 | 17.5 | 0.5 | 0 | 2018-10-10 | 26.1 | 0 | 8.1 | 2017-10-10 | 18.3 | 0 | 0.3 | 2016-10-10 | 11 | 7 | 0 | 3.16 | 1.3
2025-10-10 | 14.9 | 3.1 | 0 | 2024-10-10 | 10.7 | 7.3 | 0 | 2023-10-10 | 11.2 | 6.8 | 0 | 2022-10-10 | 10.9 | 7.1 | 0 | 2021-10-10 | 18.8 | 0 | 0.8 | 2020-10-10 | 21.9 | 0 | 3.9 | 2019-10-10 | 18.4 | 0 | 0.4 | 2018-10-10 | 20.4 | 0 | 2.4 | 2017-10-10 | 19.1 | 0 | 1.1 | 2016-10-10 | 11.4 | 6.6 | 0 | 3.09 | 0.86
2025-10-10 | 14.7 | 3.3 | 0 | 2024-10-10 | 10.7 | 7.3 | 0 | 2023-10-10 | 11.2 | 6.8 | 0 | 2022-10-10 | 10.3 | 7.7 | 0 | 2021-10-10 | 19.1 | 0 | 1.1 | 2020-10-10 | 21 | 0 | 3 | 2019-10-10 | 18.2 | 0 | 0.2 | 2018-10-10 | 19.7 | 0 | 1.7 | 2017-10-10 | 19.4 | 0 | 1.4 | 2016-10-10 | 11.1 | 6.9 | 0 | 3.2 | 0.74
2025-10-10 | 13.6 | 4.4 | 0 | 2024-10-10 | 9.9 | 8.1 | 0 | 2023-10-10 | 9.9 | 8.1 | 0 | 2022-10-10 | 8.6 | 9.4 | 0 | 2021-10-10 | 17.9 | 0.1 | 0 | 2020-10-10 | 18.2 | 0 | 0.2 | 2019-10-10 | 15.7 | 2.3 | 0 | 2018-10-10 | 17.3 | 0.7 | 0 | 2017-10-10 | 17.8 | 0.2 | 0 | 2016-10-10 | 9.2 | 8.8 | 0 | 4.21 | 0.02
2025-10-10 | 11.2 | 6.8 | 0 | 2024-10-10 | 7.2 | 10.8 | 0 | 2023-10-10 | 8.4 | 9.6 | 0 | 2022-10-10 | 6.9 | 11.1 | 0 | 2021-10-10 | 16.9 | 1.1 | 0 | 2020-10-10 | 16.1 | 1.9 | 0 | 2019-10-10 | 13.8 | 4.2 | 0 | 2018-10-10 | 14.5 | 3.5 | 0 | 2017-10-10 | 16.1 | 1.9 | 0 | 2016-10-10 | 7.5 | 10.5 | 0 | 6.14 | 0
2025-10-10 | 9.8 | 8.2 | 0 | 2024-10-10 | 7.1 | 10.9 | 0 | 2023-10-10 | 7.5 | 10.5 | 0 | 2022-10-10 | 2.1 | 15.9 | 0 | 2021-10-10 | 17.1 | 0.9 | 0 | 2020-10-10 | 13.1 | 4.9 | 0 | 2019-10-10 | 12 | 6 | 0 | 2018-10-10 | 12.9 | 5.1 | 0 | 2017-10-10 | 13.2 | 4.8 | 0 | 2016-10-10 | 7.1 | 10.9 | 0 | 7.81 | 0
2025-10-10 | 9 | 9 | 0 | 2024-10-10 | 5.2 | 12.8 | 0 | 2023-10-10 | 6.5 | 11.5 | 0 | 2022-10-10 | 1.8 | 16.2 | 0 | 2021-10-10 | 17 | 1 | 0 | 2020-10-10 | 11.1 | 6.9 | 0 | 2019-10-10 | 11.5 | 6.5 | 0 | 2018-10-10 | 12 | 6 | 0 | 2017-10-10 | 13.5 | 4.5 | 0 | 2016-10-10 | 6.6 | 11.4 | 0 | 8.58 | 0
2025-10-10 | 7.1 | 10.9 | 0 | 2024-10-10 | 4.8 | 13.2 | 0 | 2023-10-10 | 6.2 | 11.8 | 0 | 2022-10-10 | 4.3 | 13.7 | 0 | 2021-10-10 | 16.8 | 1.2 | 0 | 2020-10-10 | 9.6 | 8.4 | 0 | 2019-10-10 | 10.8 | 7.2 | 0 | 2018-10-10 | 11.4 | 6.6 | 0 | 2017-10-10 | 14.9 | 3.1 | 0 | 2016-10-10 | 2.5 | 15.5 | 0 | 9.16 | 0
2025-10-10 | 7.4 | 10.6 | 0 | 2024-10-10 | 4.1 | 13.9 | 0 | 2023-10-10 | 6.7 | 11.3 | 0 | 2022-10-10 | 3.5 | 14.5 | 0 | 2021-10-10 | 16.6 | 1.4 | 0 | 2020-10-10 | 8.6 | 9.4 | 0 | 2019-10-10 | 9.9 | 8.1 | 0 | 2018-10-10 | 11 | 7 | 0 | 2017-10-10 | 13.5 | 4.5 | 0 | 2016-10-10 | 2.2 | 15.8 | 0 | 9.65 | 0
2025-10-10 | 7.7 | 10.3 | 0 | 2024-10-10 | 3.6 | 14.4 | 0 | 2023-10-10 | 7.2 | 10.8 | 0 | 2022-10-10 | 2.4 | 15.6 | 0 | 2021-10-10 | 15.6 | 2.4 | 0 | 2020-10-10 | 8 | 10 | 0 | 2019-10-10 | 6.8 | 11.2 | 0 | 2018-10-10 | 10.6 | 7.4 | 0 | 2017-10-10 | 12.7 | 5.3 | 0 | 2016-10-10 | 3.8 | 14.2 | 0 | 10.16 | 0
2025-10-11 | 8.6 | 9.4 | 0 | 2024-10-11 | 3.6 | 14.4 | 0 | 2023-10-11 | 8 | 10 | 0 | 2022-10-11 | 3.1 | 14.9 | 0 | 2021-10-11 | 15.3 | 2.7 | 0 | 2020-10-11 | 6.9 | 11.1 | 0 | 2019-10-11 | 8.4 | 9.6 | 0 | 2018-10-11 | 10.3 | 7.7 | 0 | 2017-10-11 | 11.5 | 6.5 | 0 | 2016-10-11 | 3.5 | 14.5 | 0 | 10.08 | 0
2025-10-11 | 8.5 | 9.5 | 0 | 2024-10-11 | 3.2 | 14.8 | 0 | 2023-10-11 | 8.1 | 9.9 | 0 | 2022-10-11 | 2.8 | 15.2 | 0 | 2021-10-11 | 14.4 | 3.6 | 0 | 2020-10-11 | 6.3 | 11.7 | 0 | 2019-10-11 | 7.3 | 10.7 | 0 | 2018-10-11 | 9.8 | 8.2 | 0 | 2017-10-11 | 10.5 | 7.5 | 0 | 2016-10-11 | 2.5 | 15.5 | 0 | 10.66 | 0
2025-10-11 | 7.8 | 10.2 | 0 | 2024-10-11 | 3 | 15 | 0 | 2023-10-11 | 7.9 | 10.1 | 0 | 2022-10-11 | 2.5 | 15.5 | 0 | 2021-10-11 | 14.7 | 3.3 | 0 | 2020-10-11 | 5.1 | 12.9 | 0 | 2019-10-11 | 7.4 | 10.6 | 0 | 2018-10-11 | 9.2 | 8.8 | 0 | 2017-10-11 | 9.4 | 8.6 | 0 | 2016-10-11 | 2.2 | 15.8 | 0 | 11.08 | 0
2025-10-11 | 7.7 | 10.3 | 0 | 2024-10-11 | 3.2 | 14.8 | 0 | 2023-10-11 | 7.8 | 10.2 | 0 | 2022-10-11 | 2.1 | 15.9 | 0 | 2021-10-11 | 15.7 | 2.3 | 0 | 2020-10-11 | 4.8 | 13.2 | 0 | 2019-10-11 | 6.8 | 11.2 | 0 | 2018-10-11 | 8.9 | 9.1 | 0 | 2017-10-11 | 8.8 | 9.2 | 0 | 2016-10-11 | 1.6 | 16.4 | 0 | 11.26 | 0
2025-10-11 | 6.6 | 11.4 | 0 | 2024-10-11 | 2.5 | 15.5 | 0 | 2023-10-11 | 7.7 | 10.3 | 0 | 2022-10-11 | 2.3 | 15.7 | 0 | 2021-10-11 | 15.5 | 2.5 | 0 | 2020-10-11 | 3.9 | 14.1 | 0 | 2019-10-11 | 5 | 13 | 0 | 2018-10-11 | 8.7 | 9.3 | 0 | 2017-10-11 | 8.5 | 9.5 | 0 | 2016-10-11 | 0.6 | 17.4 | 0 | 11.87 | 0
2025-10-11 | 6.7 | 11.3 | 0 | 2024-10-11 | 2.2 | 15.8 | 0 | 2023-10-11 | 7.8 | 10.2 | 0 | 2022-10-11 | 1.4 | 16.6 | 0 | 2021-10-11 | 14 | 4 | 0 | 2020-10-11 | 3.4 | 14.6 | 0 | 2019-10-11 | 4.2 | 13.8 | 0 | 2018-10-11 | 8.6 | 9.4 | 0 | 2017-10-11 | 7.6 | 10.4 | 0 | 2016-10-11 | 0.6 | 17.4 | 0 | 12.35 | 0
2025-10-11 | 6.8 | 11.2 | 0 | 2024-10-11 | 2.4 | 15.6 | 0 | 2023-10-11 | 7.9 | 10.1 | 0 | 2022-10-11 | 2.2 | 15.8 | 0 | 2021-10-11 | 14.6 | 3.4 | 0 | 2020-10-11 | 1.9 | 16.1 | 0 | 2019-10-11 | 3.1 | 14.9 | 0 | 2018-10-11 | 8.5 | 9.5 | 0 | 2017-10-11 | 7.5 | 10.5 | 0 | 2016-10-11 | 0.4 | 17.6 | 0 | 12.47 | 0
2025-10-11 | 7.1 | 10.9 | 0 | 2024-10-11 | 2.5 | 15.5 | 0 | 2023-10-11 | 8.1 | 9.9 | 0 | 2022-10-11 | 1.8 | 16.2 | 0 | 2021-10-11 | 15.1 | 2.9 | 0 | 2020-10-11 | 2.9 | 15.1 | 0 | 2019-10-11 | 5.6 | 12.4 | 0 | 2018-10-11 | 8.6 | 9.4 | 0 | 2017-10-11 | 7.6 | 10.4 | 0 | 2016-10-11 | 1.6 | 16.4 | 0 | 11.91 | 0
2025-10-11 | 8.7 | 9.3 | 0 | 2024-10-11 | 5.3 | 12.7 | 0 | 2023-10-11 | 8.4 | 9.6 | 0 | 2022-10-11 | 4.3 | 13.7 | 0 | 2021-10-11 | 16.6 | 1.4 | 0 | 2020-10-11 | 4.7 | 13.3 | 0 | 2019-10-11 | 8.2 | 9.8 | 0 | 2018-10-11 | 8.8 | 9.2 | 0 | 2017-10-11 | 8.3 | 9.7 | 0 | 2016-10-11 | 4.9 | 13.1 | 0 | 10.18 | 0
2025-10-11 | 12.4 | 5.6 | 0 | 2024-10-11 | 9 | 9 | 0 | 2023-10-11 | 8.9 | 9.1 | 0 | 2022-10-11 | 8.2 | 9.8 | 0 | 2021-10-11 | 17.2 | 0.8 | 0 | 2020-10-11 | 5.7 | 12.3 | 0 | 2019-10-11 | 10.8 | 7.2 | 0 | 2018-10-11 | 9 | 9 | 0 | 2017-10-11 | 8.6 | 9.4 | 0 | 2016-10-11 | 9.1 | 8.9 | 0 | 8.11 | 0
2025-10-11 | 14.3 | 3.7 | 0 | 2024-10-11 | 11.5 | 6.5 | 0 | 2023-10-11 | 10 | 8 | 0 | 2022-10-11 | 10.6 | 7.4 | 0 | 2021-10-11 | 17.9 | 0.1 | 0 | 2020-10-11 | 7 | 11 | 0 | 2019-10-11 | 14 | 4 | 0 | 2018-10-11 | 9.3 | 8.7 | 0 | 2017-10-11 | 8.8 | 9.2 | 0 | 2016-10-11 | 11.7 | 6.3 | 0 | 6.49 | 0
2025-10-11 | 15.9 | 2.1 | 0 | 2024-10-11 | 13.4 | 4.6 | 0 | 2023-10-11 | 10.9 | 7.1 | 0 | 2022-10-11 | 12.2 | 5.8 | 0 | 2021-10-11 | 17.8 | 0.2 | 0 | 2020-10-11 | 7.7 | 10.3 | 0 | 2019-10-11 | 16.1 | 1.9 | 0 | 2018-10-11 | 9.9 | 8.1 | 0 | 2017-10-11 | 9.2 | 8.8 | 0 | 2016-10-11 | 13.3 | 4.7 | 0 | 5.36 | 0
2025-10-11 | 16.3 | 1.7 | 0 | 2024-10-11 | 14.9 | 3.1 | 0 | 2023-10-11 | 11.6 | 6.4 | 0 | 2022-10-11 | 14.1 | 3.9 | 0 | 2021-10-11 | 19.7 | 0 | 1.7 | 2020-10-11 | 8.7 | 9.3 | 0 | 2019-10-11 | 18.1 | 0 | 0.1 | 2018-10-11 | 10.8 | 7.2 | 0 | 2017-10-11 | 9.2 | 8.8 | 0 | 2016-10-11 | 15 | 3 | 0 | 4.34 | 0.18
2025-10-11 | 16.5 | 1.5 | 0 | 2024-10-11 | 16.3 | 1.7 | 0 | 2023-10-11 | 12.9 | 5.1 | 0 | 2022-10-11 | 15.8 | 2.2 | 0 | 2021-10-11 | 21.5 | 0 | 3.5 | 2020-10-11 | 10.1 | 7.9 | 0 | 2019-10-11 | 19.1 | 0 | 1.1 | 2018-10-11 | 11.4 | 6.6 | 0 | 2017-10-11 | 9.6 | 8.4 | 0 | 2016-10-11 | 16.6 | 1.4 | 0 | 3.48 | 0.46
2025-10-11 | 16.9 | 1.1 | 0 | 2024-10-11 | 17.1 | 0.9 | 0 | 2023-10-11 | 11.9 | 6.1 | 0 | 2022-10-11 | 16.9 | 1.1 | 0 | 2021-10-11 | 22.6 | 0 | 4.6 | 2020-10-11 | 10 | 8 | 0 | 2019-10-11 | 20 | 0 | 2 | 2018-10-11 | 11.7 | 6.3 | 0 | 2017-10-11 | 9.6 | 8.4 | 0 | 2016-10-11 | 17.7 | 0.3 | 0 | 3.22 | 0.66
2025-10-11 | 17.4 | 0.6 | 0 | 2024-10-11 | 17.3 | 0.7 | 0 | 2023-10-11 | 12.5 | 5.5 | 0 | 2022-10-11 | 17.5 | 0.5 | 0 | 2021-10-11 | 22.4 | 0 | 4.4 | 2020-10-11 | 10.1 | 7.9 | 0 | 2019-10-11 | 19.7 | 0 | 1.7 | 2018-10-11 | 11.2 | 6.8 | 0 | 2017-10-11 | 9.4 | 8.6 | 0 | 2016-10-11 | 18.2 | 0 | 0.2 | 3.06 | 0.63
2025-10-11 | 17.2 | 0.8 | 0 | 2024-10-11 | 16.7 | 1.3 | 0 | 2023-10-11 | 12.9 | 5.1 | 0 | 2022-10-11 | 17.3 | 0.7 | 0 | 2021-10-11 | 22.7 | 0 | 4.7 | 2020-10-11 | 10.1 | 7.9 | 0 | 2019-10-11 | 18.9 | 0 | 0.9 | 2018-10-11 | 10.7 | 7.3 | 0 | 2017-10-11 | 9.2 | 8.8 | 0 | 2016-10-11 | 16.3 | 1.7 | 0 | 3.36 | 0.56
2025-10-11 | 15.1 | 2.9 | 0 | 2024-10-11 | 15.9 | 2.1 | 0 | 2023-10-11 | 11.6 | 6.4 | 0 | 2022-10-11 | 15.5 | 2.5 | 0 | 2021-10-11 | 20.1 | 0 | 2.1 | 2020-10-11 | 8.6 | 9.4 | 0 | 2019-10-11 | 16.6 | 1.4 | 0 | 2018-10-11 | 10.5 | 7.5 | 0 | 2017-10-11 | 8.2 | 9.8 | 0 | 2016-10-11 | 14.1 | 3.9 | 0 | 4.59 | 0.21
2025-10-11 | 12.7 | 5.3 | 0 | 2024-10-11 | 14.9 | 3.1 | 0 | 2023-10-11 | 8.8 | 9.2 | 0 | 2022-10-11 | 13.4 | 4.6 | 0 | 2021-10-11 | 18.2 | 0 | 0.2 | 2020-10-11 | 4.8 | 13.2 | 0 | 2019-10-11 | 13.7 | 4.3 | 0 | 2018-10-11 | 10.3 | 7.7 | 0 | 2017-10-11 | 8 | 10 | 0 | 2016-10-11 | 12.8 | 5.2 | 0 | 6.26 | 0.02
2025-10-11 | 12.3 | 5.7 | 0 | 2024-10-11 | 14.9 | 3.1 | 0 | 2023-10-11 | 9 | 9 | 0 | 2022-10-11 | 11.8 | 6.2 | 0 | 2021-10-11 | 18.6 | 0 | 0.6 | 2020-10-11 | 5.2 | 12.8 | 0 | 2019-10-11 | 12.8 | 5.2 | 0 | 2018-10-11 | 10.7 | 7.3 | 0 | 2017-10-11 | 7.6 | 10.4 | 0 | 2016-10-11 | 11.5 | 6.5 | 0 | 6.62 | 0.06
2025-10-11 | 9.7 | 8.3 | 0 | 2024-10-11 | 14.3 | 3.7 | 0 | 2023-10-11 | 8.7 | 9.3 | 0 | 2022-10-11 | 12 | 6 | 0 | 2021-10-11 | 16.6 | 1.4 | 0 | 2020-10-11 | 4.6 | 13.4 | 0 | 2019-10-11 | 12.5 | 5.5 | 0 | 2018-10-11 | 10.4 | 7.6 | 0 | 2017-10-11 | 7.2 | 10.8 | 0 | 2016-10-11 | 11.4 | 6.6 | 0 | 7.26 | 0
2025-10-11 | 9 | 9 | 0 | 2024-10-11 | 13 | 5 | 0 | 2023-10-11 | 8.6 | 9.4 | 0 | 2022-10-11 | 10.5 | 7.5 | 0 | 2021-10-11 | 16.2 | 1.8 | 0 | 2020-10-11 | 3.9 | 14.1 | 0 | 2019-10-11 | 12.2 | 5.8 | 0 | 2018-10-11 | 10.1 | 7.9 | 0 | 2017-10-11 | 6.3 | 11.7 | 0 | 2016-10-11 | 11.3 | 6.7 | 0 | 7.89 | 0
2025-10-11 | 8.5 | 9.5 | 0 | 2024-10-11 | 13.7 | 4.3 | 0 | 2023-10-11 | 8.7 | 9.3 | 0 | 2022-10-11 | 9.7 | 8.3 | 0 | 2021-10-11 | 15.7 | 2.3 | 0 | 2020-10-11 | 2.8 | 15.2 | 0 | 2019-10-11 | 10.9 | 7.1 | 0 | 2018-10-11 | 11 | 7 | 0 | 2017-10-11 | 5.3 | 12.7 | 0 | 2016-10-11 | 9.3 | 8.7 | 0 | 8.44 | 0
2025-10-11 | 8.9 | 9.1 | 0 | 2024-10-11 | 14.1 | 3.9 | 0 | 2023-10-11 | 8.5 | 9.5 | 0 | 2022-10-11 | 9 | 9 | 0 | 2021-10-11 | 14.5 | 3.5 | 0 | 2020-10-11 | 2.4 | 15.6 | 0 | 2019-10-11 | 10 | 8 | 0 | 2018-10-11 | 11 | 7 | 0 | 2017-10-11 | 4.9 | 13.1 | 0 | 2016-10-11 | 10.3 | 7.7 | 0 | 8.64 | 0
2025-10-12 | 9.2 | 8.8 | 0 | 2024-10-12 | 14.8 | 3.2 | 0 | 2023-10-12 | 7.6 | 10.4 | 0 | 2022-10-12 | 7.9 | 10.1 | 0 | 2021-10-12 | 15 | 3 | 0 | 2020-10-12 | 2.1 | 15.9 | 0 | 2019-10-12 | 9.3 | 8.7 | 0 | 2018-10-12 | 10.8 | 7.2 | 0 | 2017-10-12 | 4.8 | 13.2 | 0 | 2016-10-12 | 11.4 | 6.6 | 0 | 8.71 | 0
2025-10-12 | 7.3 | 10.7 | 0 | 2024-10-12 | 14.7 | 3.3 | 0 | 2023-10-12 | 6.9 | 11.1 | 0 | 2022-10-12 | 5.9 | 12.1 | 0 | 2021-10-12 | 14.4 | 3.6 | 0 | 2020-10-12 | 2 | 16 | 0 | 2019-10-12 | 7.7 | 10.3 | 0 | 2018-10-12 | 10.7 | 7.3 | 0 | 2017-10-12 | 4.5 | 13.5 | 0 | 2016-10-12 | 10.8 | 7.2 | 0 | 9.51 | 0
2025-10-12 | 8.7 | 9.3 | 0 | 2024-10-12 | 13.2 | 4.8 | 0 | 2023-10-12 | 7.3 | 10.7 | 0 | 2022-10-12 | 5.6 | 12.4 | 0 | 2021-10-12 | 14.3 | 3.7 | 0 | 2020-10-12 | 1.6 | 16.4 | 0 | 2019-10-12 | 8 | 10 | 0 | 2018-10-12 | 9.2 | 8.8 | 0 | 2017-10-12 | 3 | 15 | 0 | 2016-10-12 | 8.4 | 9.6 | 0 | 10.07 | 0
2025-10-12 | 6.5 | 11.5 | 0 | 2024-10-12 | 10.8 | 7.2 | 0 | 2023-10-12 | 7.4 | 10.6 | 0 | 2022-10-12 | 7.3 | 10.7 | 0 | 2021-10-12 | 14.3 | 3.7 | 0 | 2020-10-12 | 1.4 | 16.6 | 0 | 2019-10-12 | 7.8 | 10.2 | 0 | 2018-10-12 | 9.6 | 8.4 | 0 | 2017-10-12 | 2.4 | 15.6 | 0 | 2016-10-12 | 8 | 10 | 0 | 10.45 | 0
2025-10-12 | 7.6 | 10.4 | 0 | 2024-10-12 | 8.6 | 9.4 | 0 | 2023-10-12 | 7.6 | 10.4 | 0 | 2022-10-12 | 4.9 | 13.1 | 0 | 2021-10-12 | 13.9 | 4.1 | 0 | 2020-10-12 | 1 | 17 | 0 | 2019-10-12 | 6.7 | 11.3 | 0 | 2018-10-12 | 8.6 | 9.4 | 0 | 2017-10-12 | 2.1 | 15.9 | 0 | 2016-10-12 | 7.5 | 10.5 | 0 | 11.15 | 0
2025-10-12 | 7.5 | 10.5 | 0 | 2024-10-12 | 7.8 | 10.2 | 0 | 2023-10-12 | 7.6 | 10.4 | 0 | 2022-10-12 | 4.8 | 13.2 | 0 | 2021-10-12 | 12.4 | 5.6 | 0 | 2020-10-12 | 1.1 | 16.9 | 0 | 2019-10-12 | 6 | 12 | 0 | 2018-10-12 | 7.4 | 10.6 | 0 | 2017-10-12 | 1.1 | 16.9 | 0 | 2016-10-12 | 7.2 | 10.8 | 0 | 11.71 | 0
2025-10-12 | 7.7 | 10.3 | 0 | 2024-10-12 | 7.4 | 10.6 | 0 | 2023-10-12 | 7.6 | 10.4 | 0 | 2022-10-12 | 8 | 10 | 0 | 2021-10-12 | 11.9 | 6.1 | 0 | 2020-10-12 | 0.8 | 17.2 | 0 | 2019-10-12 | 6.2 | 11.8 | 0 | 2018-10-12 | 7.4 | 10.6 | 0 | 2017-10-12 | 1.4 | 16.6 | 0 | 2016-10-12 | 5 | 13 | 0 | 11.66 | 0
2025-10-12 | 6.7 | 11.3 | 0 | 2024-10-12 | 6.9 | 11.1 | 0 | 2023-10-12 | 7.2 | 10.8 | 0 | 2022-10-12 | 8.4 | 9.6 | 0 | 2021-10-12 | 12.6 | 5.4 | 0 | 2020-10-12 | 1.7 | 16.3 | 0 | 2019-10-12 | 7.2 | 10.8 | 0 | 2018-10-12 | 6.3 | 11.7 | 0 | 2017-10-12 | 2.6 | 15.4 | 0 | 2016-10-12 | 5.2 | 12.8 | 0 | 11.52 | 0
2025-10-12 | 10 | 8 | 0 | 2024-10-12 | 7.2 | 10.8 | 0 | 2023-10-12 | 8.1 | 9.9 | 0 | 2022-10-12 | 11.1 | 6.9 | 0 | 2021-10-12 | 13.4 | 4.6 | 0 | 2020-10-12 | 3.7 | 14.3 | 0 | 2019-10-12 | 9.5 | 8.5 | 0 | 2018-10-12 | 7.4 | 10.6 | 0 | 2017-10-12 | 6.3 | 11.7 | 0 | 2016-10-12 | 9.8 | 8.2 | 0 | 9.35 | 0
2025-10-12 | 12.2 | 5.8 | 0 | 2024-10-12 | 8.6 | 9.4 | 0 | 2023-10-12 | 8.9 | 9.1 | 0 | 2022-10-12 | 13.7 | 4.3 | 0 | 2021-10-12 | 16.3 | 1.7 | 0 | 2020-10-12 | 5.5 | 12.5 | 0 | 2019-10-12 | 10.1 | 7.9 | 0 | 2018-10-12 | 8 | 10 | 0 | 2017-10-12 | 9.2 | 8.8 | 0 | 2016-10-12 | 13.5 | 4.5 | 0 | 7.4 | 0
2025-10-12 | 14.2 | 3.8 | 0 | 2024-10-12 | 9.6 | 8.4 | 0 | 2023-10-12 | 9.4 | 8.6 | 0 | 2022-10-12 | 15.4 | 2.6 | 0 | 2021-10-12 | 18.8 | 0 | 0.8 | 2020-10-12 | 7.2 | 10.8 | 0 | 2019-10-12 | 12.6 | 5.4 | 0 | 2018-10-12 | 8.3 | 9.7 | 0 | 2017-10-12 | 11.8 | 6.2 | 0 | 2016-10-12 | 15.9 | 2.1 | 0 | 5.76 | 0.08
2025-10-12 | 17 | 1 | 0 | 2024-10-12 | 10.5 | 7.5 | 0 | 2023-10-12 | 11.3 | 6.7 | 0 | 2022-10-12 | 15.5 | 2.5 | 0 | 2021-10-12 | 20.1 | 0 | 2.1 | 2020-10-12 | 8.8 | 9.2 | 0 | 2019-10-12 | 13.4 | 4.6 | 0 | 2018-10-12 | 10.1 | 7.9 | 0 | 2017-10-12 | 13.1 | 4.9 | 0 | 2016-10-12 | 17.6 | 0.4 | 0 | 4.47 | 0.21
2025-10-12 | 18.2 | 0 | 0.2 | 2024-10-12 | 10.7 | 7.3 | 0 | 2023-10-12 | 11 | 7 | 0 | 2022-10-12 | 17 | 1 | 0 | 2021-10-12 | 21.6 | 0 | 3.6 | 2020-10-12 | 10.4 | 7.6 | 0 | 2019-10-12 | 13.8 | 4.2 | 0 | 2018-10-12 | 9.8 | 8.2 | 0 | 2017-10-12 | 14.2 | 3.8 | 0 | 2016-10-12 | 18.4 | 0 | 0.4 | 3.91 | 0.42
2025-10-12 | 19.4 | 0 | 1.4 | 2024-10-12 | 11.6 | 6.4 | 0 | 2023-10-12 | 10.8 | 7.2 | 0 | 2022-10-12 | 18.4 | 0 | 0.4 | 2021-10-12 | 23 | 0 | 5 | 2020-10-12 | 11.1 | 6.9 | 0 | 2019-10-12 | 13.7 | 4.3 | 0 | 2018-10-12 | 9.3 | 8.7 | 0 | 2017-10-12 | 15 | 3 | 0 | 2016-10-12 | 18.8 | 0 | 0.8 | 3.65 | 0.76
2025-10-12 | 19.7 | 0 | 1.7 | 2024-10-12 | 12 | 6 | 0 | 2023-10-12 | 12 | 6 | 0 | 2022-10-12 | 18.6 | 0 | 0.6 | 2021-10-12 | 23.9 | 0 | 5.9 | 2020-10-12 | 11.6 | 6.4 | 0 | 2019-10-12 | 12.7 | 5.3 | 0 | 2018-10-12 | 10.8 | 7.2 | 0 | 2017-10-12 | 15.3 | 2.7 | 0 | 2016-10-12 | 19.8 | 0 | 1.8 | 3.36 | 1
2025-10-12 | 19.1 | 0 | 1.1 | 2024-10-12 | 12.1 | 5.9 | 0 | 2023-10-12 | 11.2 | 6.8 | 0 | 2022-10-12 | 19.1 | 0 | 1.1 | 2021-10-12 | 24.3 | 0 | 6.3 | 2020-10-12 | 12.6 | 5.4 | 0 | 2019-10-12 | 12.2 | 5.8 | 0 | 2018-10-12 | 10.1 | 7.9 | 0 | 2017-10-12 | 15.2 | 2.8 | 0 | 2016-10-12 | 19.8 | 0 | 1.8 | 3.46 | 1.03
2025-10-12 | 18 | 0 | 0 | 2024-10-12 | 11.9 | 6.1 | 0 | 2023-10-12 | 10.2 | 7.8 | 0 | 2022-10-12 | 18.1 | 0 | 0.1 | 2021-10-12 | 23.7 | 0 | 5.7 | 2020-10-12 | 13.6 | 4.4 | 0 | 2019-10-12 | 11.2 | 6.8 | 0 | 2018-10-12 | 10.2 | 7.8 | 0 | 2017-10-12 | 14.5 | 3.5 | 0 | 2016-10-12 | 19.6 | 0 | 1.6 | 3.64 | 0.74
2025-10-12 | 16.4 | 1.6 | 0 | 2024-10-12 | 10.3 | 7.7 | 0 | 2023-10-12 | 9.4 | 8.6 | 0 | 2022-10-12 | 18 | 0 | 0 | 2021-10-12 | 21.2 | 0 | 3.2 | 2020-10-12 | 13.2 | 4.8 | 0 | 2019-10-12 | 11.2 | 6.8 | 0 | 2018-10-12 | 7.9 | 10.1 | 0 | 2017-10-12 | 12.5 | 5.5 | 0 | 2016-10-12 | 17.8 | 0.2 | 0 | 4.53 | 0.32
2025-10-12 | 14.3 | 3.7 | 0 | 2024-10-12 | 7.4 | 10.6 | 0 | 2023-10-12 | 7.7 | 10.3 | 0 | 2022-10-12 | 16.1 | 1.9 | 0 | 2021-10-12 | 18.3 | 0 | 0.3 | 2020-10-12 | 11.8 | 6.2 | 0 | 2019-10-12 | 11.4 | 6.6 | 0 | 2018-10-12 | 7.5 | 10.5 | 0 | 2017-10-12 | 10 | 8 | 0 | 2016-10-12 | 15.9 | 2.1 | 0 | 5.99 | 0.03
2025-10-12 | 13.1 | 4.9 | 0 | 2024-10-12 | 7.5 | 10.5 | 0 | 2023-10-12 | 5.9 | 12.1 | 0 | 2022-10-12 | 15.7 | 2.3 | 0 | 2021-10-12 | 19.1 | 0 | 1.1 | 2020-10-12 | 11.2 | 6.8 | 0 | 2019-10-12 | 11.6 | 6.4 | 0 | 2018-10-12 | 8.1 | 9.9 | 0 | 2017-10-12 | 9 | 9 | 0 | 2016-10-12 | 13.2 | 4.8 | 0 | 6.67 | 0.11
2025-10-12 | 12.8 | 5.2 | 0 | 2024-10-12 | 6 | 12 | 0 | 2023-10-12 | 4.6 | 13.4 | 0 | 2022-10-12 | 16.3 | 1.7 | 0 | 2021-10-12 | 16.9 | 1.1 | 0 | 2020-10-12 | 11.5 | 6.5 | 0 | 2019-10-12 | 11.3 | 6.7 | 0 | 2018-10-12 | 7.2 | 10.8 | 0 | 2017-10-12 | 8.9 | 9.1 | 0 | 2016-10-12 | 13.3 | 4.7 | 0 | 7.12 | 0
2025-10-12 | 12.3 | 5.7 | 0 | 2024-10-12 | 4.2 | 13.8 | 0 | 2023-10-12 | 5.3 | 12.7 | 0 | 2022-10-12 | 15.7 | 2.3 | 0 | 2021-10-12 | 14.6 | 3.4 | 0 | 2020-10-12 | 11.4 | 6.6 | 0 | 2019-10-12 | 10.2 | 7.8 | 0 | 2018-10-12 | 6.7 | 11.3 | 0 | 2017-10-12 | 7.9 | 10.1 | 0 | 2016-10-12 | 14 | 4 | 0 | 7.77 | 0
2025-10-12 | 11.6 | 6.4 | 0 | 2024-10-12 | 3.8 | 14.2 | 0 | 2023-10-12 | 6.4 | 11.6 | 0 | 2022-10-12 | 15.5 | 2.5 | 0 | 2021-10-12 | 13.7 | 4.3 | 0 | 2020-10-12 | 11.1 | 6.9 | 0 | 2019-10-12 | 7.6 | 10.4 | 0 | 2018-10-12 | 6.2 | 11.8 | 0 | 2017-10-12 | 7.5 | 10.5 | 0 | 2016-10-12 | 15 | 3 | 0 | 8.16 | 0
2025-10-12 | 10.7 | 7.3 | 0 | 2024-10-12 | 6.1 | 11.9 | 0 | 2023-10-12 | 5 | 13 | 0 | 2022-10-12 | 15 | 3 | 0 | 2021-10-12 | 14.4 | 3.6 | 0 | 2020-10-12 | 10.9 | 7.1 | 0 | 2019-10-12 | 5.8 | 12.2 | 0 | 2018-10-12 | 5.9 | 12.1 | 0 | 2017-10-12 | 7.1 | 10.9 | 0 | 2016-10-12 | 15.4 | 2.6 | 0 | 8.37 | 0
2025-10-13 | 9.5 | 8.5 | 0 | 2024-10-13 | 5.6 | 12.4 | 0 | 2023-10-13 | 4.2 | 13.8 | 0 | 2022-10-13 | 14.8 | 3.2 | 0 | 2021-10-13 | 13.2 | 4.8 | 0 | 2020-10-13 | 10.5 | 7.5 | 0 | 2019-10-13 | 5.2 | 12.8 | 0 | 2018-10-13 | 5 | 13 | 0 | 2017-10-13 | 6.7 | 11.3 | 0 | 2016-10-13 | 14.7 | 3.3 | 0 | 9.06 | 0
2025-10-13 | 8.2 | 9.8 | 0 | 2024-10-13 | 4.1 | 13.9 | 0 | 2023-10-13 | 4.1 | 13.9 | 0 | 2022-10-13 | 12.1 | 5.9 | 0 | 2021-10-13 | 13.3 | 4.7 | 0 | 2020-10-13 | 9 | 9 | 0 | 2019-10-13 | 4.7 | 13.3 | 0 | 2018-10-13 | 5 | 13 | 0 | 2017-10-13 | 5.5 | 12.5 | 0 | 2016-10-13 | 13.9 | 4.1 | 0 | 10.01 | 0
2025-10-13 | 8.8 | 9.2 | 0 | 2024-10-13 | 4 | 14 | 0 | 2023-10-13 | 5.1 | 12.9 | 0 | 2022-10-13 | 13.4 | 4.6 | 0 | 2021-10-13 | 16.1 | 1.9 | 0 | 2020-10-13 | 8.2 | 9.8 | 0 | 2019-10-13 | 3.6 | 14.4 | 0 | 2018-10-13 | 2.3 | 15.7 | 0 | 2017-10-13 | 5.5 | 12.5 | 0 | 2016-10-13 | 13.6 | 4.4 | 0 | 9.94 | 0
2025-10-13 | 6.9 | 11.1 | 0 | 2024-10-13 | 4.6 | 13.4 | 0 | 2023-10-13 | 4.3 | 13.7 | 0 | 2022-10-13 | 13.6 | 4.4 | 0 | 2021-10-13 | 15.5 | 2.5 | 0 | 2020-10-13 | 7.5 | 10.5 | 0 | 2019-10-13 | 3.9 | 14.1 | 0 | 2018-10-13 | 3.8 | 14.2 | 0 | 2017-10-13 | 5.4 | 12.6 | 0 | 2016-10-13 | 13.8 | 4.2 | 0 | 10.07 | 0
2025-10-13 | 8.2 | 9.8 | 0 | 2024-10-13 | 4.7 | 13.3 | 0 | 2023-10-13 | 5.7 | 12.3 | 0 | 2022-10-13 | 14.2 | 3.8 | 0 | 2021-10-13 | 15 | 3 | 0 | 2020-10-13 | 7.4 | 10.6 | 0 | 2019-10-13 | 1.8 | 16.2 | 0 | 2018-10-13 | 4.1 | 13.9 | 0 | 2017-10-13 | 5 | 13 | 0 | 2016-10-13 | 13.5 | 4.5 | 0 | 10.04 | 0
2025-10-13 | 8.6 | 9.4 | 0 | 2024-10-13 | 4.4 | 13.6 | 0 | 2023-10-13 | 4.8 | 13.2 | 0 | 2022-10-13 | 14.3 | 3.7 | 0 | 2021-10-13 | 14.7 | 3.3 | 0 | 2020-10-13 | 7.5 | 10.5 | 0 | 2019-10-13 | 2.1 | 15.9 | 0 | 2018-10-13 | 4.1 | 13.9 | 0 | 2017-10-13 | 3.8 | 14.2 | 0 | 2016-10-13 | 13.5 | 4.5 | 0 | 10.22 | 0
2025-10-13 | 7.9 | 10.1 | 0 | 2024-10-13 | 4 | 14 | 0 | 2023-10-13 | 5.9 | 12.1 | 0 | 2022-10-13 | 13.4 | 4.6 | 0 | 2021-10-13 | 14.5 | 3.5 | 0 | 2020-10-13 | 7.5 | 10.5 | 0 | 2019-10-13 | 1.6 | 16.4 | 0 | 2018-10-13 | 2.7 | 15.3 | 0 | 2017-10-13 | 4.3 | 13.7 | 0 | 2016-10-13 | 12.9 | 5.1 | 0 | 10.53 | 0
2025-10-13 | 8.1 | 9.9 | 0 | 2024-10-13 | 4.5 | 13.5 | 0 | 2023-10-13 | 6.4 | 11.6 | 0 | 2022-10-13 | 13.9 | 4.1 | 0 | 2021-10-13 | 14.7 | 3.3 | 0 | 2020-10-13 | 7.8 | 10.2 | 0 | 2019-10-13 | 3 | 15 | 0 | 2018-10-13 | 2 | 16 | 0 | 2017-10-13 | 6.1 | 11.9 | 0 | 2016-10-13 | 12.6 | 5.4 | 0 | 10.09 | 0
2025-10-13 | 10.4 | 7.6 | 0 | 2024-10-13 | 5.4 | 12.6 | 0 | 2023-10-13 | 8.6 | 9.4 | 0 | 2022-10-13 | 14.3 | 3.7 | 0 | 2021-10-13 | 15.3 | 2.7 | 0 | 2020-10-13 | 8.3 | 9.7 | 0 | 2019-10-13 | 3.9 | 14.1 | 0 | 2018-10-13 | 4.7 | 13.3 | 0 | 2017-10-13 | 9 | 9 | 0 | 2016-10-13 | 12.9 | 5.1 | 0 | 8.72 | 0
2025-10-13 | 11.8 | 6.2 | 0 | 2024-10-13 | 6.2 | 11.8 | 0 | 2023-10-13 | 9.7 | 8.3 | 0 | 2022-10-13 | 14.6 | 3.4 | 0 | 2021-10-13 | 16.3 | 1.7 | 0 | 2020-10-13 | 8.8 | 9.2 | 0 | 2019-10-13 | 8 | 10 | 0 | 2018-10-13 | 6.6 | 11.4 | 0 | 2017-10-13 | 11 | 7 | 0 | 2016-10-13 | 13.2 | 4.8 | 0 | 7.38 | 0
2025-10-13 | 12.6 | 5.4 | 0 | 2024-10-13 | 7.2 | 10.8 | 0 | 2023-10-13 | 11.9 | 6.1 | 0 | 2022-10-13 | 14.8 | 3.2 | 0 | 2021-10-13 | 17.1 | 0.9 | 0 | 2020-10-13 | 9.5 | 8.5 | 0 | 2019-10-13 | 11 | 7 | 0 | 2018-10-13 | 6.8 | 11.2 | 0 | 2017-10-13 | 12.9 | 5.1 | 0 | 2016-10-13 | 9.7 | 8.3 | 0 | 6.65 | 0
2025-10-13 | 15 | 3 | 0 | 2024-10-13 | 7.8 | 10.2 | 0 | 2023-10-13 | 13.6 | 4.4 | 0 | 2022-10-13 | 15.6 | 2.4 | 0 | 2021-10-13 | 18.2 | 0 | 0.2 | 2020-10-13 | 9.8 | 8.2 | 0 | 2019-10-13 | 12.4 | 5.6 | 0 | 2018-10-13 | 7.1 | 10.9 | 0 | 2017-10-13 | 15.4 | 2.6 | 0 | 2016-10-13 | 9.5 | 8.5 | 0 | 5.58 | 0.02
2025-10-13 | 15.1 | 2.9 | 0 | 2024-10-13 | 8.6 | 9.4 | 0 | 2023-10-13 | 13.6 | 4.4 | 0 | 2022-10-13 | 16.3 | 1.7 | 0 | 2021-10-13 | 20 | 0 | 2 | 2020-10-13 | 10.6 | 7.4 | 0 | 2019-10-13 | 13.7 | 4.3 | 0 | 2018-10-13 | 7.2 | 10.8 | 0 | 2017-10-13 | 15.1 | 2.9 | 0 | 2016-10-13 | 9.8 | 8.2 | 0 | 5.2 | 0.2
2025-10-13 | 15.4 | 2.6 | 0 | 2024-10-13 | 9.6 | 8.4 | 0 | 2023-10-13 | 13.6 | 4.4 | 0 | 2022-10-13 | 16.4 | 1.6 | 0 | 2021-10-13 | 20.4 | 0 | 2.4 | 2020-10-13 | 11.5 | 6.5 | 0 | 2019-10-13 | 14.8 | 3.2 | 0 | 2018-10-13 | 8.2 | 9.8 | 0 | 2017-10-13 | 14.9 | 3.1 | 0 | 2016-10-13 | 10.1 | 7.9 | 0 | 4.75 | 0.24
2025-10-13 | 15.4 | 2.6 | 0 | 2024-10-13 | 11.1 | 6.9 | 0 | 2023-10-13 | 14.6 | 3.4 | 0 | 2022-10-13 | 13.6 | 4.4 | 0 | 2021-10-13 | 21 | 0 | 3 | 2020-10-13 | 12.2 | 5.8 | 0 | 2019-10-13 | 15.1 | 2.9 | 0 | 2018-10-13 | 8.4 | 9.6 | 0 | 2017-10-13 | 14.7 | 3.3 | 0 | 2016-10-13 | 9.4 | 8.6 | 0 | 4.75 | 0.3
2025-10-13 | 15 | 3 | 0 | 2024-10-13 | 10.7 | 7.3 | 0 | 2023-10-13 | 13.6 | 4.4 | 0 | 2022-10-13 | 13.2 | 4.8 | 0 | 2021-10-13 | 21.1 | 0 | 3.1 | 2020-10-13 | 11.2 | 6.8 | 0 | 2019-10-13 | 15.6 | 2.4 | 0 | 2018-10-13 | 8.7 | 9.3 | 0 | 2017-10-13 | 14.7 | 3.3 | 0 | 2016-10-13 | 9.3 | 8.7 | 0 | 5 | 0.31
2025-10-13 | 14.4 | 3.6 | 0 | 2024-10-13 | 9.7 | 8.3 | 0 | 2023-10-13 | 12.9 | 5.1 | 0 | 2022-10-13 | 12.5 | 5.5 | 0 | 2021-10-13 | 19.7 | 0 | 1.7 | 2020-10-13 | 11.7 | 6.3 | 0 | 2019-10-13 | 15.3 | 2.7 | 0 | 2018-10-13 | 8.4 | 9.6 | 0 | 2017-10-13 | 14.6 | 3.4 | 0 | 2016-10-13 | 8.9 | 9.1 | 0 | 5.36 | 0.17
2025-10-13 | 13.4 | 4.6 | 0 | 2024-10-13 | 8 | 10 | 0 | 2023-10-13 | 12.5 | 5.5 | 0 | 2022-10-13 | 12.1 | 5.9 | 0 | 2021-10-13 | 18.8 | 0 | 0.8 | 2020-10-13 | 10.6 | 7.4 | 0 | 2019-10-13 | 12.8 | 5.2 | 0 | 2018-10-13 | 6.3 | 11.7 | 0 | 2017-10-13 | 14.5 | 3.5 | 0 | 2016-10-13 | 8.2 | 9.8 | 0 | 6.36 | 0.08
2025-10-13 | 12 | 6 | 0 | 2024-10-13 | 5.8 | 12.2 | 0 | 2023-10-13 | 11 | 7 | 0 | 2022-10-13 | 12.3 | 5.7 | 0 | 2021-10-13 | 18.4 | 0 | 0.4 | 2020-10-13 | 10.1 | 7.9 | 0 | 2019-10-13 | 9 | 9 | 0 | 2018-10-13 | 5.6 | 12.4 | 0 | 2017-10-13 | 14.2 | 3.8 | 0 | 2016-10-13 | 6.4 | 11.6 | 0 | 7.56 | 0.04
2025-10-13 | 12.6 | 5.4 | 0 | 2024-10-13 | 5.6 | 12.4 | 0 | 2023-10-13 | 11 | 7 | 0 | 2022-10-13 | 11.8 | 6.2 | 0 | 2021-10-13 | 18.2 | 0 | 0.2 | 2020-10-13 | 9.6 | 8.4 | 0 | 2019-10-13 | 8.1 | 9.9 | 0 | 2018-10-13 | 6.2 | 11.8 | 0 | 2017-10-13 | 13.9 | 4.1 | 0 | 2016-10-13 | 6 | 12 | 0 | 7.72 | 0.02
2025-10-13 | 12.8 | 5.2 | 0 | 2024-10-13 | 5.4 | 12.6 | 0 | 2023-10-13 | 9.2 | 8.8 | 0 | 2022-10-13 | 11.5 | 6.5 | 0 | 2021-10-13 | 17.6 | 0.4 | 0 | 2020-10-13 | 9 | 9 | 0 | 2019-10-13 | 8.1 | 9.9 | 0 | 2018-10-13 | 6 | 12 | 0 | 2017-10-13 | 13.9 | 4.1 | 0 | 2016-10-13 | 4 | 14 | 0 | 8.25 | 0
2025-10-13 | 12.7 | 5.3 | 0 | 2024-10-13 | 4.9 | 13.1 | 0 | 2023-10-13 | 9.5 | 8.5 | 0 | 2022-10-13 | 11 | 7 | 0 | 2021-10-13 | 17 | 1 | 0 | 2020-10-13 | 8.4 | 9.6 | 0 | 2019-10-13 | 6.5 | 11.5 | 0 | 2018-10-13 | 5.7 | 12.3 | 0 | 2017-10-13 | 14 | 4 | 0 | 2016-10-13 | 4.5 | 13.5 | 0 | 8.58 | 0
2025-10-13 | 12.1 | 5.9 | 0 | 2024-10-13 | 5.5 | 12.5 | 0 | 2023-10-13 | 9 | 9 | 0 | 2022-10-13 | 10.5 | 7.5 | 0 | 2021-10-13 | 16.7 | 1.3 | 0 | 2020-10-13 | 7.8 | 10.2 | 0 | 2019-10-13 | 8.7 | 9.3 | 0 | 2018-10-13 | 5.3 | 12.7 | 0 | 2017-10-13 | 14.4 | 3.6 | 0 | 2016-10-13 | 5.3 | 12.7 | 0 | 8.47 | 0
2025-10-13 | 10.9 | 7.1 | 0 | 2024-10-13 | 5.5 | 12.5 | 0 | 2023-10-13 | 8.4 | 9.6 | 0 | 2022-10-13 | 10.5 | 7.5 | 0 | 2021-10-13 | 16.1 | 1.9 | 0 | 2020-10-13 | 6.6 | 11.4 | 0 | 2019-10-13 | 7.7 | 10.3 | 0 | 2018-10-13 | 4.1 | 13.9 | 0 | 2017-10-13 | 15.2 | 2.8 | 0 | 2016-10-13 | 3.2 | 14.8 | 0 | 9.18 | 0
2025-10-14 | 10.7 | 7.3 | 0 | 2024-10-14 | 5.2 | 12.8 | 0 | 2023-10-14 | 7.3 | 10.7 | 0 | 2022-10-14 | 10.5 | 7.5 | 0 | 2021-10-14 | 15.7 | 2.3 | 0 | 2020-10-14 | 7.3 | 10.7 | 0 | 2019-10-14 | 7.3 | 10.7 | 0 | 2018-10-14 | 4.1 | 13.9 | 0 | 2017-10-14 | 14.6 | 3.4 | 0 | 2016-10-14 | 2.9 | 15.1 | 0 | 9.44 | 0
2025-10-14 | 10.1 | 7.9 | 0 | 2024-10-14 | 4.9 | 13.1 | 0 | 2023-10-14 | 7.5 | 10.5 | 0 | 2022-10-14 | 9.4 | 8.6 | 0 | 2021-10-14 | 14.8 | 3.2 | 0 | 2020-10-14 | 7.1 | 10.9 | 0 | 2019-10-14 | 7.3 | 10.7 | 0 | 2018-10-14 | 4.1 | 13.9 | 0 | 2017-10-14 | 13.8 | 4.2 | 0 | 2016-10-14 | 2.5 | 15.5 | 0 | 9.85 | 0
2025-10-14 | 9.9 | 8.1 | 0 | 2024-10-14 | 4.7 | 13.3 | 0 | 2023-10-14 | 7.8 | 10.2 | 0 | 2022-10-14 | 8.9 | 9.1 | 0 | 2021-10-14 | 15.1 | 2.9 | 0 | 2020-10-14 | 5.5 | 12.5 | 0 | 2019-10-14 | 8.5 | 9.5 | 0 | 2018-10-14 | 2.8 | 15.2 | 0 | 2017-10-14 | 13 | 5 | 0 | 2016-10-14 | 0.8 | 17.2 | 0 | 10.3 | 0
2025-10-14 | 9.7 | 8.3 | 0 | 2024-10-14 | 4.4 | 13.6 | 0 | 2023-10-14 | 7.3 | 10.7 | 0 | 2022-10-14 | 8.8 | 9.2 | 0 | 2021-10-14 | 15.1 | 2.9 | 0 | 2020-10-14 | 6.1 | 11.9 | 0 | 2019-10-14 | 9.5 | 8.5 | 0 | 2018-10-14 | 1.7 | 16.3 | 0 | 2017-10-14 | 14 | 4 | 0 | 2016-10-14 | -2.4 | 20.4 | 0 | 10.58 | 0
2025-10-14 | 9.9 | 8.1 | 0 | 2024-10-14 | 4 | 14 | 0 | 2023-10-14 | 5.7 | 12.3 | 0 | 2022-10-14 | 9.6 | 8.4 | 0 | 2021-10-14 | 15.2 | 2.8 | 0 | 2020-10-14 | 5 | 13 | 0 | 2019-10-14 | 9.2 | 8.8 | 0 | 2018-10-14 | 2.2 | 15.8 | 0 | 2017-10-14 | 14.3 | 3.7 | 0 | 2016-10-14 | -1.2 | 19.2 | 0 | 10.61 | 0
2025-10-14 | 10.1 | 7.9 | 0 | 2024-10-14 | 3.9 | 14.1 | 0 | 2023-10-14 | 7.8 | 10.2 | 0 | 2022-10-14 | 7.4 | 10.6 | 0 | 2021-10-14 | 15.6 | 2.4 | 0 | 2020-10-14 | 5 | 13 | 0 | 2019-10-14 | 9.5 | 8.5 | 0 | 2018-10-14 | 1.2 | 16.8 | 0 | 2017-10-14 | 14 | 4 | 0 | 2016-10-14 | -0.5 | 18.5 | 0 | 10.6 | 0
2025-10-14 | 10 | 8 | 0 | 2024-10-14 | 3.3 | 14.7 | 0 | 2023-10-14 | 8.2 | 9.8 | 0 | 2022-10-14 | 6.8 | 11.2 | 0 | 2021-10-14 | 15.3 | 2.7 | 0 | 2020-10-14 | 3.6 | 14.4 | 0 | 2019-10-14 | 8.5 | 9.5 | 0 | 2018-10-14 | 0.5 | 17.5 | 0 | 2017-10-14 | 13.9 | 4.1 | 0 | 2016-10-14 | -4 | 22 | 0 | 11.39 | 0
2025-10-14 | 10.6 | 7.4 | 0 | 2024-10-14 | 3.7 | 14.3 | 0 | 2023-10-14 | 8.4 | 9.6 | 0 | 2022-10-14 | 7.1 | 10.9 | 0 | 2021-10-14 | 15.4 | 2.6 | 0 | 2020-10-14 | 4.6 | 13.4 | 0 | 2019-10-14 | 8.9 | 9.1 | 0 | 2018-10-14 | 1.2 | 16.8 | 0 | 2017-10-14 | 14.1 | 3.9 | 0 | 2016-10-14 | -2.2 | 20.2 | 0 | 10.82 | 0
2025-10-14 | 11.2 | 6.8 | 0 | 2024-10-14 | 5.1 | 12.9 | 0 | 2023-10-14 | 9 | 9 | 0 | 2022-10-14 | 9.3 | 8.7 | 0 | 2021-10-14 | 15.6 | 2.4 | 0 | 2020-10-14 | 7.4 | 10.6 | 0 | 2019-10-14 | 8.1 | 9.9 | 0 | 2018-10-14 | 3.6 | 14.4 | 0 | 2017-10-14 | 14.6 | 3.4 | 0 | 2016-10-14 | 2.9 | 15.1 | 0 | 9.32 | 0
2025-10-14 | 12.2 | 5.8 | 0 | 2024-10-14 | 6.5 | 11.5 | 0 | 2023-10-14 | 11.6 | 6.4 | 0 | 2022-10-14 | 11.7 | 6.3 | 0 | 2021-10-14 | 16.1 | 1.9 | 0 | 2020-10-14 | 10.4 | 7.6 | 0 | 2019-10-14 | 8.6 | 9.4 | 0 | 2018-10-14 | 6.8 | 11.2 | 0 | 2017-10-14 | 14.6 | 3.4 | 0 | 2016-10-14 | 5.1 | 12.9 | 0 | 7.64 | 0
2025-10-14 | 13.1 | 4.9 | 0 | 2024-10-14 | 6.4 | 11.6 | 0 | 2023-10-14 | 12.8 | 5.2 | 0 | 2022-10-14 | 13.2 | 4.8 | 0 | 2021-10-14 | 16.6 | 1.4 | 0 | 2020-10-14 | 11.5 | 6.5 | 0 | 2019-10-14 | 8.2 | 9.8 | 0 | 2018-10-14 | 9.8 | 8.2 | 0 | 2017-10-14 | 15.2 | 2.8 | 0 | 2016-10-14 | 7.8 | 10.2 | 0 | 6.54 | 0
2025-10-14 | 15.5 | 2.5 | 0 | 2024-10-14 | 6.9 | 11.1 | 0 | 2023-10-14 | 13.3 | 4.7 | 0 | 2022-10-14 | 14.5 | 3.5 | 0 | 2021-10-14 | 17.6 | 0.4 | 0 | 2020-10-14 | 12.7 | 5.3 | 0 | 2019-10-14 | 9.4 | 8.6 | 0 | 2018-10-14 | 11.2 | 6.8 | 0 | 2017-10-14 | 15.6 | 2.4 | 0 | 2016-10-14 | 8.9 | 9.1 | 0 | 5.44 | 0
2025-10-14 | 16.6 | 1.4 | 0 | 2024-10-14 | 8.2 | 9.8 | 0 | 2023-10-14 | 13.6 | 4.4 | 0 | 2022-10-14 | 15.7 | 2.3 | 0 | 2021-10-14 | 18.8 | 0 | 0.8 | 2020-10-14 | 13.9 | 4.1 | 0 | 2019-10-14 | 10.4 | 7.6 | 0 | 2018-10-14 | 11.9 | 6.1 | 0 | 2017-10-14 | 16.1 | 1.9 | 0 | 2016-10-14 | 10.5 | 7.5 | 0 | 4.51 | 0.08
2025-10-14 | 17.4 | 0.6 | 0 | 2024-10-14 | 9.3 | 8.7 | 0 | 2023-10-14 | 13.1 | 4.9 | 0 | 2022-10-14 | 16.6 | 1.4 | 0 | 2021-10-14 | 19.9 | 0 | 1.9 | 2020-10-14 | 15 | 3 | 0 | 2019-10-14 | 10.5 | 7.5 | 0 | 2018-10-14 | 13.3 | 4.7 | 0 | 2017-10-14 | 16.2 | 1.8 | 0 | 2016-10-14 | 11.6 | 6.4 | 0 | 3.9 | 0.19
2025-10-14 | 18.7 | 0 | 0.7 | 2024-10-14 | 9.9 | 8.1 | 0 | 2023-10-14 | 14 | 4 | 0 | 2022-10-14 | 15.5 | 2.5 | 0 | 2021-10-14 | 20.4 | 0 | 2.4 | 2020-10-14 | 15.6 | 2.4 | 0 | 2019-10-14 | 10.5 | 7.5 | 0 | 2018-10-14 | 13.4 | 4.6 | 0 | 2017-10-14 | 16.3 | 1.7 | 0 | 2016-10-14 | 11.8 | 6.2 | 0 | 3.7 | 0.31
2025-10-14 | 19 | 0 | 1 | 2024-10-14 | 10.8 | 7.2 | 0 | 2023-10-14 | 13.6 | 4.4 | 0 | 2022-10-14 | 16.4 | 1.6 | 0 | 2021-10-14 | 21.2 | 0 | 3.2 | 2020-10-14 | 14.4 | 3.6 | 0 | 2019-10-14 | 11.1 | 6.9 | 0 | 2018-10-14 | 12.8 | 5.2 | 0 | 2017-10-14 | 16.6 | 1.4 | 0 | 2016-10-14 | 11.6 | 6.4 | 0 | 3.67 | 0.42
2025-10-14 | 19 | 0 | 1 | 2024-10-14 | 10.1 | 7.9 | 0 | 2023-10-14 | 13.3 | 4.7 | 0 | 2022-10-14 | 14.9 | 3.1 | 0 | 2021-10-14 | 20.8 | 0 | 2.8 | 2020-10-14 | 14.8 | 3.2 | 0 | 2019-10-14 | 10.5 | 7.5 | 0 | 2018-10-14 | 12.8 | 5.2 | 0 | 2017-10-14 | 16.6 | 1.4 | 0 | 2016-10-14 | 11.4 | 6.6 | 0 | 3.96 | 0.38
2025-10-14 | 17 | 1 | 0 | 2024-10-14 | 9 | 9 | 0 | 2023-10-14 | 11.9 | 6.1 | 0 | 2022-10-14 | 11.1 | 6.9 | 0 | 2021-10-14 | 18.8 | 0 | 0.8 | 2020-10-14 | 12.3 | 5.7 | 0 | 2019-10-14 | 7.9 | 10.1 | 0 | 2018-10-14 | 10.7 | 7.3 | 0 | 2017-10-14 | 15.8 | 2.2 | 0 | 2016-10-14 | 8.7 | 9.3 | 0 | 5.76 | 0.08
2025-10-14 | 15.4 | 2.6 | 0 | 2024-10-14 | 7.8 | 10.2 | 0 | 2023-10-14 | 9.3 | 8.7 | 0 | 2022-10-14 | 10 | 8 | 0 | 2021-10-14 | 18.9 | 0 | 0.9 | 2020-10-14 | 10 | 8 | 0 | 2019-10-14 | 8 | 10 | 0 | 2018-10-14 | 8.9 | 9.1 | 0 | 2017-10-14 | 14.6 | 3.4 | 0 | 2016-10-14 | 9.3 | 8.7 | 0 | 6.87 | 0.09
2025-10-14 | 14.3 | 3.7 | 0 | 2024-10-14 | 6.1 | 11.9 | 0 | 2023-10-14 | 9.8 | 8.2 | 0 | 2022-10-14 | 6.8 | 11.2 | 0 | 2021-10-14 | 16.7 | 1.3 | 0 | 2020-10-14 | 10.2 | 7.8 | 0 | 2019-10-14 | 7.2 | 10.8 | 0 | 2018-10-14 | 7.9 | 10.1 | 0 | 2017-10-14 | 14.3 | 3.7 | 0 | 2016-10-14 | 8.7 | 9.3 | 0 | 7.8 | 0
2025-10-14 | 11.4 | 6.6 | 0 | 2024-10-14 | 6.3 | 11.7 | 0 | 2023-10-14 | 9.3 | 8.7 | 0 | 2022-10-14 | 6.2 | 11.8 | 0 | 2021-10-14 | 17.4 | 0.6 | 0 | 2020-10-14 | 8 | 10 | 0 | 2019-10-14 | 6 | 12 | 0 | 2018-10-14 | 7.1 | 10.9 | 0 | 2017-10-14 | 14.3 | 3.7 | 0 | 2016-10-14 | 8.7 | 9.3 | 0 | 8.53 | 0
2025-10-14 | 11.8 | 6.2 | 0 | 2024-10-14 | 5.2 | 12.8 | 0 | 2023-10-14 | 8.8 | 9.2 | 0 | 2022-10-14 | 5 | 13 | 0 | 2021-10-14 | 16.8 | 1.2 | 0 | 2020-10-14 | 8.2 | 9.8 | 0 | 2019-10-14 | 5.8 | 12.2 | 0 | 2018-10-14 | 7.2 | 10.8 | 0 | 2017-10-14 | 14.2 | 3.8 | 0 | 2016-10-14 | 6.9 | 11.1 | 0 | 9.01 | 0
2025-10-14 | 14.6 | 3.4 | 0 | 2024-10-14 | 4.7 | 13.3 | 0 | 2023-10-14 | 8.2 | 9.8 | 0 | 2022-10-14 | 3.8 | 14.2 | 0 | 2021-10-14 | 16.5 | 1.5 | 0 | 2020-10-14 | 8.6 | 9.4 | 0 | 2019-10-14 | 6.8 | 11.2 | 0 | 2018-10-14 | 7 | 11 | 0 | 2017-10-14 | 14.2 | 3.8 | 0 | 2016-10-14 | 5.9 | 12.1 | 0 | 8.97 | 0
2025-10-14 | 12.8 | 5.2 | 0 | 2024-10-14 | 4.2 | 13.8 | 0 | 2023-10-14 | 7.9 | 10.1 | 0 | 2022-10-14 | 4.1 | 13.9 | 0 | 2021-10-14 | 16.5 | 1.5 | 0 | 2020-10-14 | 9 | 9 | 0 | 2019-10-14 | 5.1 | 12.9 | 0 | 2018-10-14 | 6.5 | 11.5 | 0 | 2017-10-14 | 13.7 | 4.3 | 0 | 2016-10-14 | 4.3 | 13.7 | 0 | 9.59 | 0
2025-10-15 | 11.1 | 6.9 | 0 | 2024-10-15 | 4 | 14 | 0 | 2023-10-15 | 6.8 | 11.2 | 0 | 2022-10-15 | 4.1 | 13.9 | 0 | 2021-10-15 | 15.9 | 2.1 | 0 | 2020-10-15 | 8.3 | 9.7 | 0 | 2019-10-15 | 3.7 | 14.3 | 0 | 2018-10-15 | 6 | 12 | 0 | 2017-10-15 | 14 | 4 | 0 | 2016-10-15 | 2 | 16 | 0 | 10.41 | 0
2025-10-15 | 10.7 | 7.3 | 0 | 2024-10-15 | 4.7 | 13.3 | 0 | 2023-10-15 | 5.9 | 12.1 | 0 | 2022-10-15 | 4.9 | 13.1 | 0 | 2021-10-15 | 16 | 2 | 0 | 2020-10-15 | 8.4 | 9.6 | 0 | 2019-10-15 | 3 | 15 | 0 | 2018-10-15 | 5.3 | 12.7 | 0 | 2017-10-15 | 14.3 | 3.7 | 0 | 2016-10-15 | 2 | 16 | 0 | 10.48 | 0
2025-10-15 | 9.9 | 8.1 | 0 | 2024-10-15 | 5 | 13 | 0 | 2023-10-15 | 6 | 12 | 0 | 2022-10-15 | 4.3 | 13.7 | 0 | 2021-10-15 | 16.4 | 1.6 | 0 | 2020-10-15 | 8.4 | 9.6 | 0 | 2019-10-15 | 2.7 | 15.3 | 0 | 2018-10-15 | 4.6 | 13.4 | 0 | 2017-10-15 | 14.4 | 3.6 | 0 | 2016-10-15 | 2.4 | 15.6 | 0 | 10.59 | 0
2025-10-15 | 9 | 9 | 0 | 2024-10-15 | 5.3 | 12.7 | 0 | 2023-10-15 | 4.7 | 13.3 | 0 | 2022-10-15 | 2.5 | 15.5 | 0 | 2021-10-15 | 16.1 | 1.9 | 0 | 2020-10-15 | 8.2 | 9.8 | 0 | 2019-10-15 | 2.7 | 15.3 | 0 | 2018-10-15 | 2.4 | 15.6 | 0 | 2017-10-15 | 14.6 | 3.4 | 0 | 2016-10-15 | 0.9 | 17.1 | 0 | 11.36 | 0
2025-10-15 | 8.2 | 9.8 | 0 | 2024-10-15 | 5.4 | 12.6 | 0 | 2023-10-15 | 6 | 12 | 0 | 2022-10-15 | 4.4 | 13.6 | 0 | 2021-10-15 | 16.1 | 1.9 | 0 | 2020-10-15 | 8 | 10 | 0 | 2019-10-15 | 2.9 | 15.1 | 0 | 2018-10-15 | 4.1 | 13.9 | 0 | 2017-10-15 | 14.6 | 3.4 | 0 | 2016-10-15 | 1.2 | 16.8 | 0 | 10.91 | 0
2025-10-15 | 7.8 | 10.2 | 0 | 2024-10-15 | 5.6 | 12.4 | 0 | 2023-10-15 | 5.6 | 12.4 | 0 | 2022-10-15 | 4.5 | 13.5 | 0 | 2021-10-15 | 16.2 | 1.8 | 0 | 2020-10-15 | 8.4 | 9.6 | 0 | 2019-10-15 | 2.2 | 15.8 | 0 | 2018-10-15 | 4.1 | 13.9 | 0 | 2017-10-15 | 14.7 | 3.3 | 0 | 2016-10-15 | 1.9 | 16.1 | 0 | 10.9 | 0
2025-10-15 | 7.6 | 10.4 | 0 | 2024-10-15 | 5.4 | 12.6 | 0 | 2023-10-15 | 7.3 | 10.7 | 0 | 2022-10-15 | 4.5 | 13.5 | 0 | 2021-10-15 | 15.7 | 2.3 | 0 | 2020-10-15 | 8.8 | 9.2 | 0 | 2019-10-15 | 1.8 | 16.2 | 0 | 2018-10-15 | 3.6 | 14.4 | 0 | 2017-10-15 | 14.6 | 3.4 | 0 | 2016-10-15 | 1.1 | 16.9 | 0 | 10.96 | 0
2025-10-15 | 6.9 | 11.1 | 0 | 2024-10-15 | 5 | 13 | 0 | 2023-10-15 | 7.8 | 10.2 | 0 | 2022-10-15 | 5.1 | 12.9 | 0 | 2021-10-15 | 15.7 | 2.3 | 0 | 2020-10-15 | 10.1 | 7.9 | 0 | 2019-10-15 | 1.1 | 16.9 | 0 | 2018-10-15 | 5.2 | 12.8 | 0 | 2017-10-15 | 14.7 | 3.3 | 0 | 2016-10-15 | 1.2 | 16.8 | 0 | 10.72 | 0
2025-10-15 | 7.1 | 10.9 | 0 | 2024-10-15 | 6 | 12 | 0 | 2023-10-15 | 8.6 | 9.4 | 0 | 2022-10-15 | 8.4 | 9.6 | 0 | 2021-10-15 | 15.8 | 2.2 | 0 | 2020-10-15 | 12.7 | 5.3 | 0 | 2019-10-15 | 4.4 | 13.6 | 0 | 2018-10-15 | 5.9 | 12.1 | 0 | 2017-10-15 | 14.8 | 3.2 | 0 | 2016-10-15 | 3.5 | 14.5 | 0 | 9.28 | 0
2025-10-15 | 8.9 | 9.1 | 0 | 2024-10-15 | 6.3 | 11.7 | 0 | 2023-10-15 | 9.1 | 8.9 | 0 | 2022-10-15 | 11.1 | 6.9 | 0 | 2021-10-15 | 16.2 | 1.8 | 0 | 2020-10-15 | 15.3 | 2.7 | 0 | 2019-10-15 | 7.5 | 10.5 | 0 | 2018-10-15 | 7.7 | 10.3 | 0 | 2017-10-15 | 15.1 | 2.9 | 0 | 2016-10-15 | 7.1 | 10.9 | 0 | 7.57 | 0
2025-10-15 | 9.7 | 8.3 | 0 | 2024-10-15 | 7.6 | 10.4 | 0 | 2023-10-15 | 9.6 | 8.4 | 0 | 2022-10-15 | 13.9 | 4.1 | 0 | 2021-10-15 | 17.2 | 0.8 | 0 | 2020-10-15 | 17 | 1 | 0 | 2019-10-15 | 10.2 | 7.8 | 0 | 2018-10-15 | 7.9 | 10.1 | 0 | 2017-10-15 | 17.3 | 0.7 | 0 | 2016-10-15 | 10.5 | 7.5 | 0 | 5.91 | 0
2025-10-15 | 10.7 | 7.3 | 0 | 2024-10-15 | 8.3 | 9.7 | 0 | 2023-10-15 | 10.5 | 7.5 | 0 | 2022-10-15 | 16.9 | 1.1 | 0 | 2021-10-15 | 18 | 0 | 0 | 2020-10-15 | 18.9 | 0 | 0.9 | 2019-10-15 | 11.7 | 6.3 | 0 | 2018-10-15 | 7.8 | 10.2 | 0 | 2017-10-15 | 18.3 | 0 | 0.3 | 2016-10-15 | 13.1 | 4.9 | 0 | 4.7 | 0.12
2025-10-15 | 12 | 6 | 0 | 2024-10-15 | 8.4 | 9.6 | 0 | 2023-10-15 | 10.1 | 7.9 | 0 | 2022-10-15 | 17.3 | 0.7 | 0 | 2021-10-15 | 18.7 | 0 | 0.7 | 2020-10-15 | 18.5 | 0 | 0.5 | 2019-10-15 | 11 | 7 | 0 | 2018-10-15 | 8.1 | 9.9 | 0 | 2017-10-15 | 19.6 | 0 | 1.6 | 2016-10-15 | 15.1 | 2.9 | 0 | 4.4 | 0.28
2025-10-15 | 12.8 | 5.2 | 0 | 2024-10-15 | 7.7 | 10.3 | 0 | 2023-10-15 | 10.2 | 7.8 | 0 | 2022-10-15 | 17 | 1 | 0 | 2021-10-15 | 19 | 0 | 1 | 2020-10-15 | 14.6 | 3.4 | 0 | 2019-10-15 | 12.7 | 5.3 | 0 | 2018-10-15 | 8.4 | 9.6 | 0 | 2017-10-15 | 20.3 | 0 | 2.3 | 2016-10-15 | 16.4 | 1.6 | 0 | 4.42 | 0.33
2025-10-15 | 13 | 5 | 0 | 2024-10-15 | 7.6 | 10.4 | 0 | 2023-10-15 | 9.8 | 8.2 | 0 | 2022-10-15 | 13.6 | 4.4 | 0 | 2021-10-15 | 19.6 | 0 | 1.6 | 2020-10-15 | 13.8 | 4.2 | 0 | 2019-10-15 | 12.8 | 5.2 | 0 | 2018-10-15 | 9.1 | 8.9 | 0 | 2017-10-15 | 19 | 0 | 1 | 2016-10-15 | 17.5 | 0.5 | 0 | 4.68 | 0.26
2025-10-15 | 11.9 | 6.1 | 0 | 2024-10-15 | 5.4 | 12.6 | 0 | 2023-10-15 | 11.1 | 6.9 | 0 | 2022-10-15 | 12.9 | 5.1 | 0 | 2021-10-15 | 20.6 | 0 | 2.6 | 2020-10-15 | 12.6 | 5.4 | 0 | 2019-10-15 | 12.8 | 5.2 | 0 | 2018-10-15 | 9.7 | 8.3 | 0 | 2017-10-15 | 20.8 | 0 | 2.8 | 2016-10-15 | 17.9 | 0.1 | 0 | 4.97 | 0.54
2025-10-15 | 11.4 | 6.6 | 0 | 2024-10-15 | 5 | 13 | 0 | 2023-10-15 | 9.9 | 8.1 | 0 | 2022-10-15 | 12.3 | 5.7 | 0 | 2021-10-15 | 19.9 | 0 | 1.9 | 2020-10-15 | 11.2 | 6.8 | 0 | 2019-10-15 | 12.8 | 5.2 | 0 | 2018-10-15 | 11.1 | 6.9 | 0 | 2017-10-15 | 21.6 | 0 | 3.6 | 2016-10-15 | 17 | 1 | 0 | 5.33 | 0.55
2025-10-15 | 10.3 | 7.7 | 0 | 2024-10-15 | 5 | 13 | 0 | 2023-10-15 | 10.6 | 7.4 | 0 | 2022-10-15 | 12.1 | 5.9 | 0 | 2021-10-15 | 19 | 0 | 1 | 2020-10-15 | 10.7 | 7.3 | 0 | 2019-10-15 | 11.6 | 6.4 | 0 | 2018-10-15 | 11.7 | 6.3 | 0 | 2017-10-15 | 21.4 | 0 | 3.4 | 2016-10-15 | 15.2 | 2.8 | 0 | 5.68 | 0.44
2025-10-15 | 8.8 | 9.2 | 0 | 2024-10-15 | 5.5 | 12.5 | 0 | 2023-10-15 | 9.8 | 8.2 | 0 | 2022-10-15 | 10.6 | 7.4 | 0 | 2021-10-15 | 18.4 | 0 | 0.4 | 2020-10-15 | 10.7 | 7.3 | 0 | 2019-10-15 | 10.5 | 7.5 | 0 | 2018-10-15 | 10.5 | 7.5 | 0 | 2017-10-15 | 16.8 | 1.2 | 0 | 2016-10-15 | 13.2 | 4.8 | 0 | 6.56 | 0.04
2025-10-15 | 7.1 | 10.9 | 0 | 2024-10-15 | 5.1 | 12.9 | 0 | 2023-10-15 | 10.3 | 7.7 | 0 | 2022-10-15 | 8.8 | 9.2 | 0 | 2021-10-15 | 17.9 | 0.1 | 0 | 2020-10-15 | 10.5 | 7.5 | 0 | 2019-10-15 | 9.3 | 8.7 | 0 | 2018-10-15 | 9.2 | 8.8 | 0 | 2017-10-15 | 16.6 | 1.4 | 0 | 2016-10-15 | 12.5 | 5.5 | 0 | 7.27 | 0
2025-10-15 | 6 | 12 | 0 | 2024-10-15 | 4.9 | 13.1 | 0 | 2023-10-15 | 10.4 | 7.6 | 0 | 2022-10-15 | 8.8 | 9.2 | 0 | 2021-10-15 | 17.7 | 0.3 | 0 | 2020-10-15 | 10.3 | 7.7 | 0 | 2019-10-15 | 8.7 | 9.3 | 0 | 2018-10-15 | 7.3 | 10.7 | 0 | 2017-10-15 | 11.4 | 6.6 | 0 | 2016-10-15 | 9.9 | 8.1 | 0 | 8.46 | 0
2025-10-15 | 4.8 | 13.2 | 0 | 2024-10-15 | 5 | 13 | 0 | 2023-10-15 | 10.2 | 7.8 | 0 | 2022-10-15 | 8 | 10 | 0 | 2021-10-15 | 17.4 | 0.6 | 0 | 2020-10-15 | 10 | 8 | 0 | 2019-10-15 | 8 | 10 | 0 | 2018-10-15 | 6.8 | 11.2 | 0 | 2017-10-15 | 9.1 | 8.9 | 0 | 2016-10-15 | 9.9 | 8.1 | 0 | 9.08 | 0
2025-10-15 | 5.5 | 12.5 | 0 | 2024-10-15 | 4.9 | 13.1 | 0 | 2023-10-15 | 10 | 8 | 0 | 2022-10-15 | 6.3 | 11.7 | 0 | 2021-10-15 | 17.2 | 0.8 | 0 | 2020-10-15 | 9.8 | 8.2 | 0 | 2019-10-15 | 6.3 | 11.7 | 0 | 2018-10-15 | 4.5 | 13.5 | 0 | 2017-10-15 | 7.7 | 10.3 | 0 | 2016-10-15 | 11.4 | 6.6 | 0 | 9.64 | 0
2025-10-15 | 4.4 | 13.6 | 0 | 2024-10-15 | 5.1 | 12.9 | 0 | 2023-10-15 | 10.2 | 7.8 | 0 | 2022-10-15 | 5.8 | 12.2 | 0 | 2021-10-15 | 17 | 1 | 0 | 2020-10-15 | 9.8 | 8.2 | 0 | 2019-10-15 | 7.4 | 10.6 | 0 | 2018-10-15 | 4.2 | 13.8 | 0 | 2017-10-15 | 7.1 | 10.9 | 0 | 2016-10-15 | 12.9 | 5.1 | 0 | 9.61 | 0
2025-10-16 | 5.4 | 12.6 | 0 | 2024-10-16 | 5.2 | 12.8 | 0 | 2023-10-16 | 10.3 | 7.7 | 0 | 2022-10-16 | 4.8 | 13.2 | 0 | 2021-10-16 | 16.8 | 1.2 | 0 | 2020-10-16 | 9.5 | 8.5 | 0 | 2019-10-16 | 6.7 | 11.3 | 0 | 2018-10-16 | 3.6 | 14.4 | 0 | 2017-10-16 | 6.8 | 11.2 | 0 | 2016-10-16 | 13.3 | 4.7 | 0 | 9.76 | 0
2025-10-16 | 5.8 | 12.2 | 0 | 2024-10-16 | 5.1 | 12.9 | 0 | 2023-10-16 | 10.4 | 7.6 | 0 | 2022-10-16 | 4.8 | 13.2 | 0 | 2021-10-16 | 16.6 | 1.4 | 0 | 2020-10-16 | 9.5 | 8.5 | 0 | 2019-10-16 | 7.5 | 10.5 | 0 | 2018-10-16 | 4 | 14 | 0 | 2017-10-16 | 5.9 | 12.1 | 0 | 2016-10-16 | 13.8 | 4.2 | 0 | 9.66 | 0
2025-10-16 | 5.4 | 12.6 | 0 | 2024-10-16 | 4.3 | 13.7 | 0 | 2023-10-16 | 10.4 | 7.6 | 0 | 2022-10-16 | 4.2 | 13.8 | 0 | 2021-10-16 | 16.5 | 1.5 | 0 | 2020-10-16 | 9.2 | 8.8 | 0 | 2019-10-16 | 7.2 | 10.8 | 0 | 2018-10-16 | 4 | 14 | 0 | 2017-10-16 | 6.2 | 11.8 | 0 | 2016-10-16 | 13.8 | 4.2 | 0 | 9.88 | 0
2025-10-16 | 2.9 | 15.1 | 0 | 2024-10-16 | 2.5 | 15.5 | 0 | 2023-10-16 | 10.3 | 7.7 | 0 | 2022-10-16 | 3.6 | 14.4 | 0 | 2021-10-16 | 16.5 | 1.5 | 0 | 2020-10-16 | 8.8 | 9.2 | 0 | 2019-10-16 | 6.5 | 11.5 | 0 | 2018-10-16 | 3.8 | 14.2 | 0 | 2017-10-16 | 5.7 | 12.3 | 0 | 2016-10-16 | 14.2 | 3.8 | 0 | 10.52 | 0
2025-10-16 | 2.4 | 15.6 | 0 | 2024-10-16 | 2.2 | 15.8 | 0 | 2023-10-16 | 10.2 | 7.8 | 0 | 2022-10-16 | 3.6 | 14.4 | 0 | 2021-10-16 | 17.1 | 0.9 | 0 | 2020-10-16 | 9.4 | 8.6 | 0 | 2019-10-16 | 6.1 | 11.9 | 0 | 2018-10-16 | 3.6 | 14.4 | 0 | 2017-10-16 | 4.9 | 13.1 | 0 | 2016-10-16 | 14 | 4 | 0 | 10.65 | 0
2025-10-16 | 1 | 17 | 0 | 2024-10-16 | 2 | 16 | 0 | 2023-10-16 | 9.7 | 8.3 | 0 | 2022-10-16 | 3.3 | 14.7 | 0 | 2021-10-16 | 17.5 | 0.5 | 0 | 2020-10-16 | 9.3 | 8.7 | 0 | 2019-10-16 | 6.3 | 11.7 | 0 | 2018-10-16 | 3 | 15 | 0 | 2017-10-16 | 4.6 | 13.4 | 0 | 2016-10-16 | 13.1 | 4.9 | 0 | 11.02 | 0
2025-10-16 | 0.8 | 17.2 | 0 | 2024-10-16 | 2.8 | 15.2 | 0 | 2023-10-16 | 10.4 | 7.6 | 0 | 2022-10-16 | 3.5 | 14.5 | 0 | 2021-10-16 | 17.7 | 0.3 | 0 | 2020-10-16 | 9 | 9 | 0 | 2019-10-16 | 6.2 | 11.8 | 0 | 2018-10-16 | 2.3 | 15.7 | 0 | 2017-10-16 | 4.2 | 13.8 | 0 | 2016-10-16 | 13.7 | 4.3 | 0 | 10.94 | 0
2025-10-16 | 2.6 | 15.4 | 0 | 2024-10-16 | 4.1 | 13.9 | 0 | 2023-10-16 | 10.5 | 7.5 | 0 | 2022-10-16 | 5.5 | 12.5 | 0 | 2021-10-16 | 18.3 | 0 | 0.3 | 2020-10-16 | 8.8 | 9.2 | 0 | 2019-10-16 | 7 | 11 | 0 | 2018-10-16 | 1.7 | 16.3 | 0 | 2017-10-16 | 4 | 14 | 0 | 2016-10-16 | 14.8 | 3.2 | 0 | 10.3 | 0.03
2025-10-16 | 5.2 | 12.8 | 0 | 2024-10-16 | 5.9 | 12.1 | 0 | 2023-10-16 | 11.6 | 6.4 | 0 | 2022-10-16 | 7.5 | 10.5 | 0 | 2021-10-16 | 18.3 | 0 | 0.3 | 2020-10-16 | 8.7 | 9.3 | 0 | 2019-10-16 | 7.4 | 10.6 | 0 | 2018-10-16 | 3.5 | 14.5 | 0 | 2017-10-16 | 5.2 | 12.8 | 0 | 2016-10-16 | 15.6 | 2.4 | 0 | 9.14 | 0.03
2025-10-16 | 7.4 | 10.6 | 0 | 2024-10-16 | 5.6 | 12.4 | 0 | 2023-10-16 | 12.3 | 5.7 | 0 | 2022-10-16 | 8.8 | 9.2 | 0 | 2021-10-16 | 18.5 | 0 | 0.5 | 2020-10-16 | 9.1 | 8.9 | 0 | 2019-10-16 | 8.7 | 9.3 | 0 | 2018-10-16 | 5.1 | 12.9 | 0 | 2017-10-16 | 5.8 | 12.2 | 0 | 2016-10-16 | 16.4 | 1.6 | 0 | 8.28 | 0.05
2025-10-16 | 8.4 | 9.6 | 0 | 2024-10-16 | 7.1 | 10.9 | 0 | 2023-10-16 | 11.7 | 6.3 | 0 | 2022-10-16 | 10.3 | 7.7 | 0 | 2021-10-16 | 18 | 0 | 0 | 2020-10-16 | 9.6 | 8.4 | 0 | 2019-10-16 | 9.9 | 8.1 | 0 | 2018-10-16 | 6.8 | 11.2 | 0 | 2017-10-16 | 6.4 | 11.6 | 0 | 2016-10-16 | 15.3 | 2.7 | 0 | 7.65 | 0
2025-10-16 | 10.1 | 7.9 | 0 | 2024-10-16 | 7.3 | 10.7 | 0 | 2023-10-16 | 14 | 4 | 0 | 2022-10-16 | 11.4 | 6.6 | 0 | 2021-10-16 | 16.7 | 1.3 | 0 | 2020-10-16 | 9.6 | 8.4 | 0 | 2019-10-16 | 9.7 | 8.3 | 0 | 2018-10-16 | 7.1 | 10.9 | 0 | 2017-10-16 | 6.6 | 11.4 | 0 | 2016-10-16 | 16.7 | 1.3 | 0 | 7.08 | 0
2025-10-16 | 11.8 | 6.2 | 0 | 2024-10-16 | 9.2 | 8.8 | 0 | 2023-10-16 | 12.5 | 5.5 | 0 | 2022-10-16 | 12.2 | 5.8 | 0 | 2021-10-16 | 16.3 | 1.7 | 0 | 2020-10-16 | 10.1 | 7.9 | 0 | 2019-10-16 | 10.3 | 7.7 | 0 | 2018-10-16 | 7.1 | 10.9 | 0 | 2017-10-16 | 5.9 | 12.1 | 0 | 2016-10-16 | 17.7 | 0.3 | 0 | 6.69 | 0
2025-10-16 | 12.6 | 5.4 | 0 | 2024-10-16 | 10.1 | 7.9 | 0 | 2023-10-16 | 13.3 | 4.7 | 0 | 2022-10-16 | 12.7 | 5.3 | 0 | 2021-10-16 | 15.5 | 2.5 | 0 | 2020-10-16 | 9.9 | 8.1 | 0 | 2019-10-16 | 11.7 | 6.3 | 0 | 2018-10-16 | 7.8 | 10.2 | 0 | 2017-10-16 | 7.3 | 10.7 | 0 | 2016-10-16 | 18 | 0 | 0 | 6.11 | 0
2025-10-16 | 13 | 5 | 0 | 2024-10-16 | 10.2 | 7.8 | 0 | 2023-10-16 | 13.8 | 4.2 | 0 | 2022-10-16 | 12.8 | 5.2 | 0 | 2021-10-16 | 15.4 | 2.6 | 0 | 2020-10-16 | 9.2 | 8.8 | 0 | 2019-10-16 | 12.9 | 5.1 | 0 | 2018-10-16 | 8 | 10 | 0 | 2017-10-16 | 6.8 | 11.2 | 0 | 2016-10-16 | 18.5 | 0 | 0.5 | 5.99 | 0.05
2025-10-16 | 13.2 | 4.8 | 0 | 2024-10-16 | 10.2 | 7.8 | 0 | 2023-10-16 | 14.4 | 3.6 | 0 | 2022-10-16 | 12.8 | 5.2 | 0 | 2021-10-16 | 15.7 | 2.3 | 0 | 2020-10-16 | 9.2 | 8.8 | 0 | 2019-10-16 | 14.5 | 3.5 | 0 | 2018-10-16 | 8.7 | 9.3 | 0 | 2017-10-16 | 6.9 | 11.1 | 0 | 2016-10-16 | 18.5 | 0 | 0.5 | 5.64 | 0.05
2025-10-16 | 12.9 | 5.1 | 0 | 2024-10-16 | 10.1 | 7.9 | 0 | 2023-10-16 | 12.5 | 5.5 | 0 | 2022-10-16 | 12.6 | 5.4 | 0 | 2021-10-16 | 15.3 | 2.7 | 0 | 2020-10-16 | 7.4 | 10.6 | 0 | 2019-10-16 | 13.6 | 4.4 | 0 | 2018-10-16 | 8.6 | 9.4 | 0 | 2017-10-16 | 6.9 | 11.1 | 0 | 2016-10-16 | 18.5 | 0 | 0.5 | 6.21 | 0.05
2025-10-16 | 11.6 | 6.4 | 0 | 2024-10-16 | 8.3 | 9.7 | 0 | 2023-10-16 | 11.5 | 6.5 | 0 | 2022-10-16 | 11.7 | 6.3 | 0 | 2021-10-16 | 13.5 | 4.5 | 0 | 2020-10-16 | 7.6 | 10.4 | 0 | 2019-10-16 | 11.4 | 6.6 | 0 | 2018-10-16 | 7.5 | 10.5 | 0 | 2017-10-16 | 6.7 | 11.3 | 0 | 2016-10-16 | 17.8 | 0.2 | 0 | 7.24 | 0
2025-10-16 | 10.7 | 7.3 | 0 | 2024-10-16 | 5 | 13 | 0 | 2023-10-16 | 10.5 | 7.5 | 0 | 2022-10-16 | 10.3 | 7.7 | 0 | 2021-10-16 | 13.4 | 4.6 | 0 | 2020-10-16 | 6.2 | 11.8 | 0 | 2019-10-16 | 11.8 | 6.2 | 0 | 2018-10-16 | 6.5 | 11.5 | 0 | 2017-10-16 | 4.5 | 13.5 | 0 | 2016-10-16 | 17.5 | 0.5 | 0 | 8.36 | 0
2025-10-16 | 9.6 | 8.4 | 0 | 2024-10-16 | 4.2 | 13.8 | 0 | 2023-10-16 | 9.7 | 8.3 | 0 | 2022-10-16 | 10.2 | 7.8 | 0 | 2021-10-16 | 11.8 | 6.2 | 0 | 2020-10-16 | 5.8 | 12.2 | 0 | 2019-10-16 | 11.5 | 6.5 | 0 | 2018-10-16 | 6.3 | 11.7 | 0 | 2017-10-16 | 2.4 | 15.6 | 0 | 2016-10-16 | 17 | 1 | 0 | 9.15 | 0
2025-10-16 | 8.7 | 9.3 | 0 | 2024-10-16 | 3.9 | 14.1 | 0 | 2023-10-16 | 9 | 9 | 0 | 2022-10-16 | 9.8 | 8.2 | 0 | 2021-10-16 | 10.9 | 7.1 | 0 | 2020-10-16 | 4.1 | 13.9 | 0 | 2019-10-16 | 11 | 7 | 0 | 2018-10-16 | 6.1 | 11.9 | 0 | 2017-10-16 | 1.8 | 16.2 | 0 | 2016-10-16 | 16.3 | 1.7 | 0 | 9.84 | 0
2025-10-16 | 7.8 | 10.2 | 0 | 2024-10-16 | 3.2 | 14.8 | 0 | 2023-10-16 | 6.8 | 11.2 | 0 | 2022-10-16 | 8.6 | 9.4 | 0 | 2021-10-16 | 10.4 | 7.6 | 0 | 2020-10-16 | 4.7 | 13.3 | 0 | 2019-10-16 | 10 | 8 | 0 | 2018-10-16 | 6.2 | 11.8 | 0 | 2017-10-16 | 1.5 | 16.5 | 0 | 2016-10-16 | 15.5 | 2.5 | 0 | 10.53 | 0
2025-10-16 | 6.9 | 11.1 | 0 | 2024-10-16 | 1.8 | 16.2 | 0 | 2023-10-16 | 5.5 | 12.5 | 0 | 2022-10-16 | 9.2 | 8.8 | 0 | 2021-10-16 | 10.2 | 7.8 | 0 | 2020-10-16 | 3.4 | 14.6 | 0 | 2019-10-16 | 9.7 | 8.3 | 0 | 2018-10-16 | 6 | 12 | 0 | 2017-10-16 | 0.5 | 17.5 | 0 | 2016-10-16 | 14.6 | 3.4 | 0 | 11.22 | 0
2025-10-16 | 6 | 12 | 0 | 2024-10-16 | 2.6 | 15.4 | 0 | 2023-10-16 | 5.7 | 12.3 | 0 | 2022-10-16 | 8.5 | 9.5 | 0 | 2021-10-16 | 9.6 | 8.4 | 0 | 2020-10-16 | 2.9 | 15.1 | 0 | 2019-10-16 | 9.4 | 8.6 | 0 | 2018-10-16 | 5.6 | 12.4 | 0 | 2017-10-16 | 0.2 | 17.8 | 0 | 2016-10-16 | 14.8 | 3.2 | 0 | 11.47 | 0
2025-10-17 | 5.1 | 12.9 | 0 | 2024-10-17 | 1.3 | 16.7 | 0 | 2023-10-17 | 6.7 | 11.3 | 0 | 2022-10-17 | 8.3 | 9.7 | 0 | 2021-10-17 | 7.8 | 10.2 | 0 | 2020-10-17 | 0.6 | 17.4 | 0 | 2019-10-17 | 9.3 | 8.7 | 0 | 2018-10-17 | 5.2 | 12.8 | 0 | 2017-10-17 | -0.3 | 18.3 | 0 | 2016-10-17 | 15 | 3 | 0 | 12.1 | 0
2025-10-17 | 4.6 | 13.4 | 0 | 2024-10-17 | 1.5 | 16.5 | 0 | 2023-10-17 | 4.9 | 13.1 | 0 | 2022-10-17 | 9 | 9 | 0 | 2021-10-17 | 6.7 | 11.3 | 0 | 2020-10-17 | 1.5 | 16.5 | 0 | 2019-10-17 | 9 | 9 | 0 | 2018-10-17 | 5.9 | 12.1 | 0 | 2017-10-17 | -0.2 | 18.2 | 0 | 2016-10-17 | 13.4 | 4.6 | 0 | 12.37 | 0
2025-10-17 | 3.5 | 14.5 | 0 | 2024-10-17 | 0.3 | 17.7 | 0 | 2023-10-17 | 4.4 | 13.6 | 0 | 2022-10-17 | 8.7 | 9.3 | 0 | 2021-10-17 | 6 | 12 | 0 | 2020-10-17 | 1.2 | 16.8 | 0 | 2019-10-17 | 8.8 | 9.2 | 0 | 2018-10-17 | 6.4 | 11.6 | 0 | 2017-10-17 | -0.9 | 18.9 | 0 | 2016-10-17 | 11.9 | 6.1 | 0 | 12.97 | 0
2025-10-17 | 2.2 | 15.8 | 0 | 2024-10-17 | -0.2 | 18.2 | 0 | 2023-10-17 | 4.3 | 13.7 | 0 | 2022-10-17 | 8.1 | 9.9 | 0 | 2021-10-17 | 6 | 12 | 0 | 2020-10-17 | 0.4 | 17.6 | 0 | 2019-10-17 | 8.7 | 9.3 | 0 | 2018-10-17 | 7.8 | 10.2 | 0 | 2017-10-17 | -0.6 | 18.6 | 0 | 2016-10-17 | 10.8 | 7.2 | 0 | 13.25 | 0
2025-10-17 | 0.1 | 17.9 | 0 | 2024-10-17 | 1.4 | 16.6 | 0 | 2023-10-17 | 4.8 | 13.2 | 0 | 2022-10-17 | 8.1 | 9.9 | 0 | 2021-10-17 | 5.8 | 12.2 | 0 | 2020-10-17 | -0.2 | 18.2 | 0 | 2019-10-17 | 8.3 | 9.7 | 0 | 2018-10-17 | 7.4 | 10.6 | 0 | 2017-10-17 | -0.5 | 18.5 | 0 | 2016-10-17 | 9.1 | 8.9 | 0 | 13.57 | 0
2025-10-17 | 0.5 | 17.5 | 0 | 2024-10-17 | -0.6 | 18.6 | 0 | 2023-10-17 | 4.1 | 13.9 | 0 | 2022-10-17 | 7.8 | 10.2 | 0 | 2021-10-17 | 5.1 | 12.9 | 0 | 2020-10-17 | 0.1 | 17.9 | 0 | 2019-10-17 | 8.2 | 9.8 | 0 | 2018-10-17 | 7 | 11 | 0 | 2017-10-17 | 0.6 | 17.4 | 0 | 2016-10-17 | 8.7 | 9.3 | 0 | 13.85 | 0
2025-10-17 | 1.1 | 16.9 | 0 | 2024-10-17 | -0.7 | 18.7 | 0 | 2023-10-17 | 4.6 | 13.4 | 0 | 2022-10-17 | 7.3 | 10.7 | 0 | 2021-10-17 | 4.8 | 13.2 | 0 | 2020-10-17 | 0 | 18 | 0 | 2019-10-17 | 8.4 | 9.6 | 0 | 2018-10-17 | 6.7 | 11.3 | 0 | 2017-10-17 | 1.5 | 16.5 | 0 | 2016-10-17 | 8.2 | 9.8 | 0 | 13.81 | 0
2025-10-17 | 0.3 | 17.7 | 0 | 2024-10-17 | -0.6 | 18.6 | 0 | 2023-10-17 | 5.5 | 12.5 | 0 | 2022-10-17 | 7 | 11 | 0 | 2021-10-17 | 5.3 | 12.7 | 0 | 2020-10-17 | 0 | 18 | 0 | 2019-10-17 | 8.4 | 9.6 | 0 | 2018-10-17 | 6.6 | 11.4 | 0 | 2017-10-17 | 2.5 | 15.5 | 0 | 2016-10-17 | 7.8 | 10.2 | 0 | 13.72 | 0
2025-10-17 | 4.4 | 13.6 | 0 | 2024-10-17 | 2.4 | 15.6 | 0 | 2023-10-17 | 8 | 10 | 0 | 2022-10-17 | 7.1 | 10.9 | 0 | 2021-10-17 | 8.3 | 9.7 | 0 | 2020-10-17 | 2.3 | 15.7 | 0 | 2019-10-17 | 8.7 | 9.3 | 0 | 2018-10-17 | 6.3 | 11.7 | 0 | 2017-10-17 | 4.1 | 13.9 | 0 | 2016-10-17 | 8.8 | 9.2 | 0 | 11.96 | 0
2025-10-17 | 6.6 | 11.4 | 0 | 2024-10-17 | 6 | 12 | 0 | 2023-10-17 | 8.9 | 9.1 | 0 | 2022-10-17 | 7.2 | 10.8 | 0 | 2021-10-17 | 9.1 | 8.9 | 0 | 2020-10-17 | 6 | 12 | 0 | 2019-10-17 | 8.6 | 9.4 | 0 | 2018-10-17 | 7.7 | 10.3 | 0 | 2017-10-17 | 5.9 | 12.1 | 0 | 2016-10-17 | 9.5 | 8.5 | 0 | 10.45 | 0
2025-10-17 | 9.2 | 8.8 | 0 | 2024-10-17 | 9.3 | 8.7 | 0 | 2023-10-17 | 9.6 | 8.4 | 0 | 2022-10-17 | 7.6 | 10.4 | 0 | 2021-10-17 | 9.6 | 8.4 | 0 | 2020-10-17 | 9.5 | 8.5 | 0 | 2019-10-17 | 8.7 | 9.3 | 0 | 2018-10-17 | 7 | 11 | 0 | 2017-10-17 | 9.7 | 8.3 | 0 | 2016-10-17 | 10.8 | 7.2 | 0 | 8.9 | 0
2025-10-17 | 9.8 | 8.2 | 0 | 2024-10-17 | 10.6 | 7.4 | 0 | 2023-10-17 | 10.3 | 7.7 | 0 | 2022-10-17 | 7.8 | 10.2 | 0 | 2021-10-17 | 10.8 | 7.2 | 0 | 2020-10-17 | 11.1 | 6.9 | 0 | 2019-10-17 | 8.8 | 9.2 | 0 | 2018-10-17 | 7.1 | 10.9 | 0 | 2017-10-17 | 12.6 | 5.4 | 0 | 2016-10-17 | 12.1 | 5.9 | 0 | 7.9 | 0
2025-10-17 | 10.4 | 7.6 | 0 | 2024-10-17 | 12.5 | 5.5 | 0 | 2023-10-17 | 11.8 | 6.2 | 0 | 2022-10-17 | 7.9 | 10.1 | 0 | 2021-10-17 | 11 | 7 | 0 | 2020-10-17 | 12.1 | 5.9 | 0 | 2019-10-17 | 8.6 | 9.4 | 0 | 2018-10-17 | 8.2 | 9.8 | 0 | 2017-10-17 | 13 | 5 | 0 | 2016-10-17 | 13.2 | 4.8 | 0 | 7.13 | 0
2025-10-17 | 11 | 7 | 0 | 2024-10-17 | 13.7 | 4.3 | 0 | 2023-10-17 | 12.1 | 5.9 | 0 | 2022-10-17 | 8.5 | 9.5 | 0 | 2021-10-17 | 12.1 | 5.9 | 0 | 2020-10-17 | 13.3 | 4.7 | 0 | 2019-10-17 | 8.4 | 9.6 | 0 | 2018-10-17 | 6.9 | 11.1 | 0 | 2017-10-17 | 12.1 | 5.9 | 0 | 2016-10-17 | 14.1 | 3.9 | 0 | 6.78 | 0
2025-10-17 | 11.2 | 6.8 | 0 | 2024-10-17 | 14.4 | 3.6 | 0 | 2023-10-17 | 12.7 | 5.3 | 0 | 2022-10-17 | 8.7 | 9.3 | 0 | 2021-10-17 | 11.8 | 6.2 | 0 | 2020-10-17 | 12.7 | 5.3 | 0 | 2019-10-17 | 8.8 | 9.2 | 0 | 2018-10-17 | 5.1 | 12.9 | 0 | 2017-10-17 | 12.7 | 5.3 | 0 | 2016-10-17 | 15.3 | 2.7 | 0 | 6.66 | 0
2025-10-17 | 11.8 | 6.2 | 0 | 2024-10-17 | 15 | 3 | 0 | 2023-10-17 | 13.7 | 4.3 | 0 | 2022-10-17 | 8.9 | 9.1 | 0 | 2021-10-17 | 11.3 | 6.7 | 0 | 2020-10-17 | 13.3 | 4.7 | 0 | 2019-10-17 | 9.2 | 8.8 | 0 | 2018-10-17 | 4.4 | 13.6 | 0 | 2017-10-17 | 15.3 | 2.7 | 0 | 2016-10-17 | 14.5 | 3.5 | 0 | 6.26 | 0
2025-10-17 | 11.3 | 6.7 | 0 | 2024-10-17 | 14.4 | 3.6 | 0 | 2023-10-17 | 13.1 | 4.9 | 0 | 2022-10-17 | 8.8 | 9.2 | 0 | 2021-10-17 | 10.1 | 7.9 | 0 | 2020-10-17 | 11.6 | 6.4 | 0 | 2019-10-17 | 9.4 | 8.6 | 0 | 2018-10-17 | 3.7 | 14.3 | 0 | 2017-10-17 | 14.9 | 3.1 | 0 | 2016-10-17 | 14.2 | 3.8 | 0 | 6.85 | 0
2025-10-17 | 9.9 | 8.1 | 0 | 2024-10-17 | 12.8 | 5.2 | 0 | 2023-10-17 | 10.4 | 7.6 | 0 | 2022-10-17 | 7.8 | 10.2 | 0 | 2021-10-17 | 9.3 | 8.7 | 0 | 2020-10-17 | 11.1 | 6.9 | 0 | 2019-10-17 | 9.7 | 8.3 | 0 | 2018-10-17 | 4.7 | 13.3 | 0 | 2017-10-17 | 14.2 | 3.8 | 0 | 2016-10-17 | 12.4 | 5.6 | 0 | 7.77 | 0
2025-10-17 | 8.7 | 9.3 | 0 | 2024-10-17 | 10.7 | 7.3 | 0 | 2023-10-17 | 10.1 | 7.9 | 0 | 2022-10-17 | 7.3 | 10.7 | 0 | 2021-10-17 | 8.7 | 9.3 | 0 | 2020-10-17 | 8.5 | 9.5 | 0 | 2019-10-17 | 8.3 | 9.7 | 0 | 2018-10-17 | 3.7 | 14.3 | 0 | 2017-10-17 | 13.3 | 4.7 | 0 | 2016-10-17 | 12.2 | 5.8 | 0 | 8.85 | 0
2025-10-17 | 7.2 | 10.8 | 0 | 2024-10-17 | 9.3 | 8.7 | 0 | 2023-10-17 | 8.8 | 9.2 | 0 | 2022-10-17 | 6.9 | 11.1 | 0 | 2021-10-17 | 8.5 | 9.5 | 0 | 2020-10-17 | 7.6 | 10.4 | 0 | 2019-10-17 | 8 | 10 | 0 | 2018-10-17 | 3 | 15 | 0 | 2017-10-17 | 12.8 | 5.2 | 0 | 2016-10-17 | 11.2 | 6.8 | 0 | 9.67 | 0
2025-10-17 | 8.3 | 9.7 | 0 | 2024-10-17 | 7.3 | 10.7 | 0 | 2023-10-17 | 7.8 | 10.2 | 0 | 2022-10-17 | 7.1 | 10.9 | 0 | 2021-10-17 | 8.4 | 9.6 | 0 | 2020-10-17 | 6.5 | 11.5 | 0 | 2019-10-17 | 8.1 | 9.9 | 0 | 2018-10-17 | 2.2 | 15.8 | 0 | 2017-10-17 | 13.7 | 4.3 | 0 | 2016-10-17 | 10.9 | 7.1 | 0 | 9.97 | 0
2025-10-17 | 8.6 | 9.4 | 0 | 2024-10-17 | 6.1 | 11.9 | 0 | 2023-10-17 | 6.9 | 11.1 | 0 | 2022-10-17 | 7 | 11 | 0 | 2021-10-17 | 7.4 | 10.6 | 0 | 2020-10-17 | 5.8 | 12.2 | 0 | 2019-10-17 | 7.7 | 10.3 | 0 | 2018-10-17 | 1.4 | 16.6 | 0 | 2017-10-17 | 13.5 | 4.5 | 0 | 2016-10-17 | 10.2 | 7.8 | 0 | 10.54 | 0
2025-10-17 | 8.6 | 9.4 | 0 | 2024-10-17 | 5.3 | 12.7 | 0 | 2023-10-17 | 6.2 | 11.8 | 0 | 2022-10-17 | 7 | 11 | 0 | 2021-10-17 | 6.5 | 11.5 | 0 | 2020-10-17 | 4.9 | 13.1 | 0 | 2019-10-17 | 7.5 | 10.5 | 0 | 2018-10-17 | 0.5 | 17.5 | 0 | 2017-10-17 | 12.8 | 5.2 | 0 | 2016-10-17 | 10.5 | 7.5 | 0 | 11.02 | 0
2025-10-17 | 8.6 | 9.4 | 0 | 2024-10-17 | 3.8 | 14.2 | 0 | 2023-10-17 | 6.2 | 11.8 | 0 | 2022-10-17 | 6.7 | 11.3 | 0 | 2021-10-17 | 5.9 | 12.1 | 0 | 2020-10-17 | 4.7 | 13.3 | 0 | 2019-10-17 | 7.3 | 10.7 | 0 | 2018-10-17 | 0.3 | 17.7 | 0 | 2017-10-17 | 11.6 | 6.4 | 0 | 2016-10-17 | 10.5 | 7.5 | 0 | 11.44 | 0
2025-10-18 | 7.7 | 10.3 | 0 | 2024-10-18 | 5 | 13 | 0 | 2023-10-18 | 5.9 | 12.1 | 0 | 2022-10-18 | 6.5 | 11.5 | 0 | 2021-10-18 | 4.5 | 13.5 | 0 | 2020-10-18 | 3.2 | 14.8 | 0 | 2019-10-18 | 7.2 | 10.8 | 0 | 2018-10-18 | 0.1 | 17.9 | 0 | 2017-10-18 | 11 | 7 | 0 | 2016-10-18 | 10.3 | 7.7 | 0 | 11.86 | 0
2025-10-18 | 7.9 | 10.1 | 0 | 2024-10-18 | 2.3 | 15.7 | 0 | 2023-10-18 | 6.3 | 11.7 | 0 | 2022-10-18 | 6.2 | 11.8 | 0 | 2021-10-18 | 6.1 | 11.9 | 0 | 2020-10-18 | 3 | 15 | 0 | 2019-10-18 | 7 | 11 | 0 | 2018-10-18 | -0.2 | 18.2 | 0 | 2017-10-18 | 10.3 | 7.7 | 0 | 2016-10-18 | 8.3 | 9.7 | 0 | 12.28 | 0
2025-10-18 | 7.8 | 10.2 | 0 | 2024-10-18 | 1.7 | 16.3 | 0 | 2023-10-18 | 6.2 | 11.8 | 0 | 2022-10-18 | 5.8 | 12.2 | 0 | 2021-10-18 | 6.5 | 11.5 | 0 | 2020-10-18 | 4.9 | 13.1 | 0 | 2019-10-18 | 6.6 | 11.4 | 0 | 2018-10-18 | -0.6 | 18.6 | 0 | 2017-10-18 | 9.6 | 8.4 | 0 | 2016-10-18 | 8.1 | 9.9 | 0 | 12.34 | 0
2025-10-18 | 8.1 | 9.9 | 0 | 2024-10-18 | 1.9 | 16.1 | 0 | 2023-10-18 | 6 | 12 | 0 | 2022-10-18 | 5.1 | 12.9 | 0 | 2021-10-18 | 6.9 | 11.1 | 0 | 2020-10-18 | 4.7 | 13.3 | 0 | 2019-10-18 | 6.5 | 11.5 | 0 | 2018-10-18 | -0.5 | 18.5 | 0 | 2017-10-18 | 8.1 | 9.9 | 0 | 2016-10-18 | 8.2 | 9.8 | 0 | 12.5 | 0
2025-10-18 | 8.3 | 9.7 | 0 | 2024-10-18 | 2 | 16 | 0 | 2023-10-18 | 6.1 | 11.9 | 0 | 2022-10-18 | 5.2 | 12.8 | 0 | 2021-10-18 | 6.9 | 11.1 | 0 | 2020-10-18 | 5 | 13 | 0 | 2019-10-18 | 6.3 | 11.7 | 0 | 2018-10-18 | -0.5 | 18.5 | 0 | 2017-10-18 | 8.6 | 9.4 | 0 | 2016-10-18 | 8.4 | 9.6 | 0 | 12.37 | 0
2025-10-18 | 8.4 | 9.6 | 0 | 2024-10-18 | 0.5 | 17.5 | 0 | 2023-10-18 | 6 | 12 | 0 | 2022-10-18 | 4.9 | 13.1 | 0 | 2021-10-18 | 6.7 | 11.3 | 0 | 2020-10-18 | 5.3 | 12.7 | 0 | 2019-10-18 | 6.2 | 11.8 | 0 | 2018-10-18 | -1 | 19 | 0 | 2017-10-18 | 7.8 | 10.2 | 0 | 2016-10-18 | 8.4 | 9.6 | 0 | 12.68 | 0
2025-10-18 | 8.5 | 9.5 | 0 | 2024-10-18 | 0.4 | 17.6 | 0 | 2023-10-18 | 5.2 | 12.8 | 0 | 2022-10-18 | 4.2 | 13.8 | 0 | 2021-10-18 | 6.7 | 11.3 | 0 | 2020-10-18 | 5.4 | 12.6 | 0 | 2019-10-18 | 6.2 | 11.8 | 0 | 2018-10-18 | -1.1 | 19.1 | 0 | 2017-10-18 | 5.5 | 12.5 | 0 | 2016-10-18 | 8.5 | 9.5 | 0 | 13.05 | 0
2025-10-18 | 8.9 | 9.1 | 0 | 2024-10-18 | -0.2 | 18.2 | 0 | 2023-10-18 | 5.4 | 12.6 | 0 | 2022-10-18 | 3.8 | 14.2 | 0 | 2021-10-18 | 6.5 | 11.5 | 0 | 2020-10-18 | 6.9 | 11.1 | 0 | 2019-10-18 | 6.1 | 11.9 | 0 | 2018-10-18 | -1.2 | 19.2 | 0 | 2017-10-18 | 6.7 | 11.3 | 0 | 2016-10-18 | 8.6 | 9.4 | 0 | 12.85 | 0
2025-10-18 | 9.4 | 8.6 | 0 | 2024-10-18 | 3.7 | 14.3 | 0 | 2023-10-18 | 6.8 | 11.2 | 0 | 2022-10-18 | 5.7 | 12.3 | 0 | 2021-10-18 | 6.9 | 11.1 | 0 | 2020-10-18 | 8.4 | 9.6 | 0 | 2019-10-18 | 6.1 | 11.9 | 0 | 2018-10-18 | -0.1 | 18.1 | 0 | 2017-10-18 | 9.6 | 8.4 | 0 | 2016-10-18 | 10.5 | 7.5 | 0 | 11.3 | 0
2025-10-18 | 10.7 | 7.3 | 0 | 2024-10-18 | 8.2 | 9.8 | 0 | 2023-10-18 | 8.1 | 9.9 | 0 | 2022-10-18 | 7.8 | 10.2 | 0 | 2021-10-18 | 7.4 | 10.6 | 0 | 2020-10-18 | 9.2 | 8.8 | 0 | 2019-10-18 | 6.1 | 11.9 | 0 | 2018-10-18 | 0.8 | 17.2 | 0 | 2017-10-18 | 12.3 | 5.7 | 0 | 2016-10-18 | 14.9 | 3.1 | 0 | 9.45 | 0
2025-10-18 | 11.6 | 6.4 | 0 | 2024-10-18 | 10.9 | 7.1 | 0 | 2023-10-18 | 9.3 | 8.7 | 0 | 2022-10-18 | 8.6 | 9.4 | 0 | 2021-10-18 | 7.8 | 10.2 | 0 | 2020-10-18 | 10.7 | 7.3 | 0 | 2019-10-18 | 6.5 | 11.5 | 0 | 2018-10-18 | 1.4 | 16.6 | 0 | 2017-10-18 | 14.6 | 3.4 | 0 | 2016-10-18 | 18.4 | 0 | 0.4 | 8.06 | 0.04
2025-10-18 | 14.1 | 3.9 | 0 | 2024-10-18 | 13 | 5 | 0 | 2023-10-18 | 10.3 | 7.7 | 0 | 2022-10-18 | 9.6 | 8.4 | 0 | 2021-10-18 | 9 | 9 | 0 | 2020-10-18 | 11.6 | 6.4 | 0 | 2019-10-18 | 6.7 | 11.3 | 0 | 2018-10-18 | 2.7 | 15.3 | 0 | 2017-10-18 | 16.6 | 1.4 | 0 | 2016-10-18 | 22.7 | 0 | 4.7 | 6.84 | 0.47
2025-10-18 | 16 | 2 | 0 | 2024-10-18 | 15.2 | 2.8 | 0 | 2023-10-18 | 11.7 | 6.3 | 0 | 2022-10-18 | 9.6 | 8.4 | 0 | 2021-10-18 | 10.4 | 7.6 | 0 | 2020-10-18 | 13.6 | 4.4 | 0 | 2019-10-18 | 7 | 11 | 0 | 2018-10-18 | 2.8 | 15.2 | 0 | 2017-10-18 | 18 | 0 | 0 | 2016-10-18 | 24 | 0 | 6 | 5.77 | 0.6
2025-10-18 | 16.9 | 1.1 | 0 | 2024-10-18 | 16.7 | 1.3 | 0 | 2023-10-18 | 13.7 | 4.3 | 0 | 2022-10-18 | 9.7 | 8.3 | 0 | 2021-10-18 | 9.6 | 8.4 | 0 | 2020-10-18 | 13.7 | 4.3 | 0 | 2019-10-18 | 7.4 | 10.6 | 0 | 2018-10-18 | 3.6 | 14.4 | 0 | 2017-10-18 | 19.2 | 0 | 1.2 | 2016-10-18 | 23.4 | 0 | 5.4 | 5.27 | 0.66
2025-10-18 | 17.2 | 0.8 | 0 | 2024-10-18 | 17.2 | 0.8 | 0 | 2023-10-18 | 13.9 | 4.1 | 0 | 2022-10-18 | 8.9 | 9.1 | 0 | 2021-10-18 | 11.2 | 6.8 | 0 | 2020-10-18 | 13.1 | 4.9 | 0 | 2019-10-18 | 7.7 | 10.3 | 0 | 2018-10-18 | 4 | 14 | 0 | 2017-10-18 | 20 | 0 | 2 | 2016-10-18 | 23.4 | 0 | 5.4 | 5.08 | 0.74
2025-10-18 | 16.7 | 1.3 | 0 | 2024-10-18 | 17.5 | 0.5 | 0 | 2023-10-18 | 14.1 | 3.9 | 0 | 2022-10-18 | 8.8 | 9.2 | 0 | 2021-10-18 | 8.9 | 9.1 | 0 | 2020-10-18 | 12.8 | 5.2 | 0 | 2019-10-18 | 9.2 | 8.8 | 0 | 2018-10-18 | 4.6 | 13.4 | 0 | 2017-10-18 | 20.4 | 0 | 2.4 | 2016-10-18 | 22.9 | 0 | 4.9 | 5.14 | 0.73
2025-10-18 | 16.9 | 1.1 | 0 | 2024-10-18 | 16.9 | 1.1 | 0 | 2023-10-18 | 13.6 | 4.4 | 0 | 2022-10-18 | 8.3 | 9.7 | 0 | 2021-10-18 | 9.1 | 8.9 | 0 | 2020-10-18 | 11.9 | 6.1 | 0 | 2019-10-18 | 8.3 | 9.7 | 0 | 2018-10-18 | 4.4 | 13.6 | 0 | 2017-10-18 | 19.3 | 0 | 1.3 | 2016-10-18 | 23 | 0 | 5 | 5.46 | 0.63
2025-10-18 | 16.1 | 1.9 | 0 | 2024-10-18 | 15.4 | 2.6 | 0 | 2023-10-18 | 12.8 | 5.2 | 0 | 2022-10-18 | 6.9 | 11.1 | 0 | 2021-10-18 | 8.9 | 9.1 | 0 | 2020-10-18 | 12.1 | 5.9 | 0 | 2019-10-18 | 7.5 | 10.5 | 0 | 2018-10-18 | 3.7 | 14.3 | 0 | 2017-10-18 | 17.1 | 0.9 | 0 | 2016-10-18 | 22.8 | 0 | 4.8 | 6.15 | 0.48
2025-10-18 | 13.8 | 4.2 | 0 | 2024-10-18 | 12.4 | 5.6 | 0 | 2023-10-18 | 12 | 6 | 0 | 2022-10-18 | 4.6 | 13.4 | 0 | 2021-10-18 | 7.2 | 10.8 | 0 | 2020-10-18 | 11.8 | 6.2 | 0 | 2019-10-18 | 6.5 | 11.5 | 0 | 2018-10-18 | 3.6 | 14.4 | 0 | 2017-10-18 | 15.2 | 2.8 | 0 | 2016-10-18 | 21.6 | 0 | 3.6 | 7.49 | 0.36
2025-10-18 | 13.5 | 4.5 | 0 | 2024-10-18 | 11.2 | 6.8 | 0 | 2023-10-18 | 11.7 | 6.3 | 0 | 2022-10-18 | 3.9 | 14.1 | 0 | 2021-10-18 | 8.1 | 9.9 | 0 | 2020-10-18 | 11.5 | 6.5 | 0 | 2019-10-18 | 5.4 | 12.6 | 0 | 2018-10-18 | 3.5 | 14.5 | 0 | 2017-10-18 | 13.3 | 4.7 | 0 | 2016-10-18 | 19.8 | 0 | 1.8 | 7.99 | 0.18
2025-10-18 | 11.8 | 6.2 | 0 | 2024-10-18 | 9.7 | 8.3 | 0 | 2023-10-18 | 10.9 | 7.1 | 0 | 2022-10-18 | 3.9 | 14.1 | 0 | 2021-10-18 | 7.8 | 10.2 | 0 | 2020-10-18 | 12.2 | 5.8 | 0 | 2019-10-18 | 5 | 13 | 0 | 2018-10-18 | 2.6 | 15.4 | 0 | 2017-10-18 | 12.6 | 5.4 | 0 | 2016-10-18 | 19.6 | 0 | 1.6 | 8.55 | 0.16
2025-10-18 | 11.2 | 6.8 | 0 | 2024-10-18 | 8.7 | 9.3 | 0 | 2023-10-18 | 10.6 | 7.4 | 0 | 2022-10-18 | 3.7 | 14.3 | 0 | 2021-10-18 | 6.9 | 11.1 | 0 | 2020-10-18 | 12.4 | 5.6 | 0 | 2019-10-18 | 5.2 | 12.8 | 0 | 2018-10-18 | 2.5 | 15.5 | 0 | 2017-10-18 | 11.7 | 6.3 | 0 | 2016-10-18 | 18.7 | 0 | 0.7 | 8.91 | 0.07
2025-10-18 | 11.4 | 6.6 | 0 | 2024-10-18 | 8.4 | 9.6 | 0 | 2023-10-18 | 10.5 | 7.5 | 0 | 2022-10-18 | 2.2 | 15.8 | 0 | 2021-10-18 | 7.4 | 10.6 | 0 | 2020-10-18 | 13.3 | 4.7 | 0 | 2019-10-18 | 4.8 | 13.2 | 0 | 2018-10-18 | 2.5 | 15.5 | 0 | 2017-10-18 | 9.8 | 8.2 | 0 | 2016-10-18 | 16.1 | 1.9 | 0 | 9.36 | 0
2025-10-18 | 10.2 | 7.8 | 0 | 2024-10-18 | 7.5 | 10.5 | 0 | 2023-10-18 | 10.3 | 7.7 | 0 | 2022-10-18 | 2.4 | 15.6 | 0 | 2021-10-18 | 7.9 | 10.1 | 0 | 2020-10-18 | 13.1 | 4.9 | 0 | 2019-10-18 | 3.4 | 14.6 | 0 | 2018-10-18 | 2.5 | 15.5 | 0 | 2017-10-18 | 10.8 | 7.2 | 0 | 2016-10-18 | 13.7 | 4.3 | 0 | 9.82 | 0
2025-10-19 | 9.9 | 8.1 | 0 | 2024-10-19 | 6.5 | 11.5 | 0 | 2023-10-19 | 9.8 | 8.2 | 0 | 2022-10-19 | 1.9 | 16.1 | 0 | 2021-10-19 | 7.3 | 10.7 | 0 | 2020-10-19 | 13.3 | 4.7 | 0 | 2019-10-19 | 2.2 | 15.8 | 0 | 2018-10-19 | 2.7 | 15.3 | 0 | 2017-10-19 | 10.8 | 7.2 | 0 | 2016-10-19 | 12.3 | 5.7 | 0 | 10.33 | 0
2025-10-19 | 9.6 | 8.4 | 0 | 2024-10-19 | 5 | 13 | 0 | 2023-10-19 | 10.1 | 7.9 | 0 | 2022-10-19 | 1.9 | 16.1 | 0 | 2021-10-19 | 5.7 | 12.3 | 0 | 2020-10-19 | 13.4 | 4.6 | 0 | 2019-10-19 | 2.2 | 15.8 | 0 | 2018-10-19 | 2.8 | 15.2 | 0 | 2017-10-19 | 11 | 7 | 0 | 2016-10-19 | 11.7 | 6.3 | 0 | 10.66 | 0
2025-10-19 | 9.1 | 8.9 | 0 | 2024-10-19 | 4.1 | 13.9 | 0 | 2023-10-19 | 10.2 | 7.8 | 0 | 2022-10-19 | 2.5 | 15.5 | 0 | 2021-10-19 | 3.3 | 14.7 | 0 | 2020-10-19 | 13.2 | 4.8 | 0 | 2019-10-19 | 1.1 | 16.9 | 0 | 2018-10-19 | 3.4 | 14.6 | 0 | 2017-10-19 | 11.5 | 6.5 | 0 | 2016-10-19 | 10.9 | 7.1 | 0 | 11.07 | 0
2025-10-19 | 8.3 | 9.7 | 0 | 2024-10-19 | 4.1 | 13.9 | 0 | 2023-10-19 | 10.2 | 7.8 | 0 | 2022-10-19 | 0.2 | 17.8 | 0 | 2021-10-19 | 2.7 | 15.3 | 0 | 2020-10-19 | 7.7 | 10.3 | 0 | 2019-10-19 | -0.3 | 18.3 | 0 | 2018-10-19 | 3.2 | 14.8 | 0 | 2017-10-19 | 10.7 | 7.3 | 0 | 2016-10-19 | 9.7 | 8.3 | 0 | 12.35 | 0
2025-10-19 | 8 | 10 | 0 | 2024-10-19 | 3.7 | 14.3 | 0 | 2023-10-19 | 10 | 8 | 0 | 2022-10-19 | -0.5 | 18.5 | 0 | 2021-10-19 | 2.4 | 15.6 | 0 | 2020-10-19 | 7.5 | 10.5 | 0 | 2019-10-19 | -0.4 | 18.4 | 0 | 2018-10-19 | 3 | 15 | 0 | 2017-10-19 | 10.6 | 7.4 | 0 | 2016-10-19 | 10.6 | 7.4 | 0 | 12.51 | 0
2025-10-19 | 7.9 | 10.1 | 0 | 2024-10-19 | 2.9 | 15.1 | 0 | 2023-10-19 | 9.4 | 8.6 | 0 | 2022-10-19 | -0.5 | 18.5 | 0 | 2021-10-19 | 2.5 | 15.5 | 0 | 2020-10-19 | 6.7 | 11.3 | 0 | 2019-10-19 | -0.4 | 18.4 | 0 | 2018-10-19 | 2.7 | 15.3 | 0 | 2017-10-19 | 11.2 | 6.8 | 0 | 2016-10-19 | 11.1 | 6.9 | 0 | 12.65 | 0
2025-10-19 | 7.7 | 10.3 | 0 | 2024-10-19 | 3.5 | 14.5 | 0 | 2023-10-19 | 8.8 | 9.2 | 0 | 2022-10-19 | -1 | 19 | 0 | 2021-10-19 | 3.3 | 14.7 | 0 | 2020-10-19 | 6.4 | 11.6 | 0 | 2019-10-19 | -1.1 | 19.1 | 0 | 2018-10-19 | 2.2 | 15.8 | 0 | 2017-10-19 | 11 | 7 | 0 | 2016-10-19 | 11.8 | 6.2 | 0 | 12.74 | 0
2025-10-19 | 8.5 | 9.5 | 0 | 2024-10-19 | 2.8 | 15.2 | 0 | 2023-10-19 | 9 | 9 | 0 | 2022-10-19 | -1.6 | 19.6 | 0 | 2021-10-19 | 3.8 | 14.2 | 0 | 2020-10-19 | 6.1 | 11.9 | 0 | 2019-10-19 | 0.3 | 17.7 | 0 | 2018-10-19 | 2.8 | 15.2 | 0 | 2017-10-19 | 11 | 7 | 0 | 2016-10-19 | 11.9 | 6.1 | 0 | 12.54 | 0
2025-10-19 | 10.1 | 7.9 | 0 | 2024-10-19 | 4.8 | 13.2 | 0 | 2023-10-19 | 10.2 | 7.8 | 0 | 2022-10-19 | -0.3 | 18.3 | 0 | 2021-10-19 | 5.1 | 12.9 | 0 | 2020-10-19 | 6.1 | 11.9 | 0 | 2019-10-19 | 1.8 | 16.2 | 0 | 2018-10-19 | 4.9 | 13.1 | 0 | 2017-10-19 | 13.5 | 4.5 | 0 | 2016-10-19 | 12.4 | 5.6 | 0 | 11.14 | 0
2025-10-19 | 13.2 | 4.8 | 0 | 2024-10-19 | 8.5 | 9.5 | 0 | 2023-10-19 | 11.7 | 6.3 | 0 | 2022-10-19 | 4.6 | 13.4 | 0 | 2021-10-19 | 6.5 | 11.5 | 0 | 2020-10-19 | 6.4 | 11.6 | 0 | 2019-10-19 | 5 | 13 | 0 | 2018-10-19 | 8.2 | 9.8 | 0 | 2017-10-19 | 15.2 | 2.8 | 0 | 2016-10-19 | 12.7 | 5.3 | 0 | 8.8 | 0
2025-10-19 | 16.7 | 1.3 | 0 | 2024-10-19 | 11.8 | 6.2 | 0 | 2023-10-19 | 13.9 | 4.1 | 0 | 2022-10-19 | 6.7 | 11.3 | 0 | 2021-10-19 | 7.6 | 10.4 | 0 | 2020-10-19 | 6.3 | 11.7 | 0 | 2019-10-19 | 6.9 | 11.1 | 0 | 2018-10-19 | 11 | 7 | 0 | 2017-10-19 | 17.5 | 0.5 | 0 | 2016-10-19 | 13.9 | 4.1 | 0 | 6.77 | 0
2025-10-19 | 20.2 | 0 | 2.2 | 2024-10-19 | 15.1 | 2.9 | 0 | 2023-10-19 | 14.8 | 3.2 | 0 | 2022-10-19 | 8.3 | 9.7 | 0 | 2021-10-19 | 8.6 | 9.4 | 0 | 2020-10-19 | 6.4 | 11.6 | 0 | 2019-10-19 | 8.2 | 9.8 | 0 | 2018-10-19 | 12.9 | 5.1 | 0 | 2017-10-19 | 18.5 | 0 | 0.5 | 2016-10-19 | 14.4 | 3.6 | 0 | 5.53 | 0.27
2025-10-19 | 22.9 | 0 | 4.9 | 2024-10-19 | 18.1 | 0 | 0.1 | 2023-10-19 | 16.1 | 1.9 | 0 | 2022-10-19 | 8.7 | 9.3 | 0 | 2021-10-19 | 10.1 | 7.9 | 0 | 2020-10-19 | 6.6 | 11.4 | 0 | 2019-10-19 | 8.1 | 9.9 | 0 | 2018-10-19 | 15.1 | 2.9 | 0 | 2017-10-19 | 18.7 | 0 | 0.7 | 2016-10-19 | 15.3 | 2.7 | 0 | 4.6 | 0.57
2025-10-19 | 24.6 | 0 | 6.6 | 2024-10-19 | 18.7 | 0 | 0.7 | 2023-10-19 | 16.4 | 1.6 | 0 | 2022-10-19 | 8.7 | 9.3 | 0 | 2021-10-19 | 12.8 | 5.2 | 0 | 2020-10-19 | 6.5 | 11.5 | 0 | 2019-10-19 | 9.1 | 8.9 | 0 | 2018-10-19 | 16.3 | 1.7 | 0 | 2017-10-19 | 19.2 | 0 | 1.2 | 2016-10-19 | 16.3 | 1.7 | 0 | 3.99 | 0.85
2025-10-19 | 25.9 | 0 | 7.9 | 2024-10-19 | 19.3 | 0 | 1.3 | 2023-10-19 | 16 | 2 | 0 | 2022-10-19 | 8 | 10 | 0 | 2021-10-19 | 16.4 | 1.6 | 0 | 2020-10-19 | 6.6 | 11.4 | 0 | 2019-10-19 | 9.8 | 8.2 | 0 | 2018-10-19 | 16.2 | 1.8 | 0 | 2017-10-19 | 19.7 | 0 | 1.7 | 2016-10-19 | 16.5 | 1.5 | 0 | 3.65 | 1.09
2025-10-19 | 25.1 | 0 | 7.1 | 2024-10-19 | 18.8 | 0 | 0.8 | 2023-10-19 | 15.6 | 2.4 | 0 | 2022-10-19 | 7.3 | 10.7 | 0 | 2021-10-19 | 17 | 1 | 0 | 2020-10-19 | 6.5 | 11.5 | 0 | 2019-10-19 | 10.1 | 7.9 | 0 | 2018-10-19 | 14.5 | 3.5 | 0 | 2017-10-19 | 18.6 | 0 | 0.6 | 2016-10-19 | 16.4 | 1.6 | 0 | 3.86 | 0.85
2025-10-19 | 24.6 | 0 | 6.6 | 2024-10-19 | 17.5 | 0.5 | 0 | 2023-10-19 | 14.4 | 3.6 | 0 | 2022-10-19 | 5.4 | 12.6 | 0 | 2021-10-19 | 17.1 | 0.9 | 0 | 2020-10-19 | 6.6 | 11.4 | 0 | 2019-10-19 | 8.9 | 9.1 | 0 | 2018-10-19 | 13.9 | 4.1 | 0 | 2017-10-19 | 18.9 | 0 | 0.9 | 2016-10-19 | 16.1 | 1.9 | 0 | 4.41 | 0.75
2025-10-19 | 23.5 | 0 | 5.5 | 2024-10-19 | 15.6 | 2.4 | 0 | 2023-10-19 | 13.3 | 4.7 | 0 | 2022-10-19 | 4.7 | 13.3 | 0 | 2021-10-19 | 14.2 | 3.8 | 0 | 2020-10-19 | 6.4 | 11.6 | 0 | 2019-10-19 | 8.1 | 9.9 | 0 | 2018-10-19 | 13.3 | 4.7 | 0 | 2017-10-19 | 17.3 | 0.7 | 0 | 2016-10-19 | 14.4 | 3.6 | 0 | 5.47 | 0.55
2025-10-19 | 22.5 | 0 | 4.5 | 2024-10-19 | 13.4 | 4.6 | 0 | 2023-10-19 | 11.6 | 6.4 | 0 | 2022-10-19 | 4.4 | 13.6 | 0 | 2021-10-19 | 13.5 | 4.5 | 0 | 2020-10-19 | 6.2 | 11.8 | 0 | 2019-10-19 | 4.3 | 13.7 | 0 | 2018-10-19 | 12.4 | 5.6 | 0 | 2017-10-19 | 15.6 | 2.4 | 0 | 2016-10-19 | 11.4 | 6.6 | 0 | 6.92 | 0.45
2025-10-19 | 20.4 | 0 | 2.4 | 2024-10-19 | 12.3 | 5.7 | 0 | 2023-10-19 | 11.3 | 6.7 | 0 | 2022-10-19 | 4.3 | 13.7 | 0 | 2021-10-19 | 8.5 | 9.5 | 0 | 2020-10-19 | 6.1 | 11.9 | 0 | 2019-10-19 | 3.1 | 14.9 | 0 | 2018-10-19 | 12.2 | 5.8 | 0 | 2017-10-19 | 14.4 | 3.6 | 0 | 2016-10-19 | 10.8 | 7.2 | 0 | 7.9 | 0.24
2025-10-19 | 21 | 0 | 3 | 2024-10-19 | 11.2 | 6.8 | 0 | 2023-10-19 | 10.8 | 7.2 | 0 | 2022-10-19 | 3.9 | 14.1 | 0 | 2021-10-19 | 11.4 | 6.6 | 0 | 2020-10-19 | 5.9 | 12.1 | 0 | 2019-10-19 | 4 | 14 | 0 | 2018-10-19 | 11.8 | 6.2 | 0 | 2017-10-19 | 13.1 | 4.9 | 0 | 2016-10-19 | 10.1 | 7.9 | 0 | 7.98 | 0.3
2025-10-19 | 21.1 | 0 | 3.1 | 2024-10-19 | 10.1 | 7.9 | 0 | 2023-10-19 | 11.4 | 6.6 | 0 | 2022-10-19 | 3.7 | 14.3 | 0 | 2021-10-19 | 9.3 | 8.7 | 0 | 2020-10-19 | 5.7 | 12.3 | 0 | 2019-10-19 | 4.6 | 13.4 | 0 | 2018-10-19 | 11.5 | 6.5 | 0 | 2017-10-19 | 13.4 | 4.6 | 0 | 2016-10-19 | 10.6 | 7.4 | 0 | 8.17 | 0.31
2025-10-19 | 20.7 | 0 | 2.7 | 2024-10-19 | 9.5 | 8.5 | 0 | 2023-10-19 | 11.4 | 6.6 | 0 | 2022-10-19 | 3.6 | 14.4 | 0 | 2021-10-19 | 9 | 9 | 0 | 2020-10-19 | 5.7 | 12.3 | 0 | 2019-10-19 | 4.6 | 13.4 | 0 | 2018-10-19 | 11.2 | 6.8 | 0 | 2017-10-19 | 10.5 | 7.5 | 0 | 2016-10-19 | 9.5 | 8.5 | 0 | 8.7 | 0.27
2025-10-19 | 20.3 | 0 | 2.3 | 2024-10-19 | 7.8 | 10.2 | 0 | 2023-10-19 | 11.1 | 6.9 | 0 | 2022-10-19 | 4 | 14 | 0 | 2021-10-19 | 9.3 | 8.7 | 0 | 2020-10-19 | 5.6 | 12.4 | 0 | 2019-10-19 | 3.2 | 14.8 | 0 | 2018-10-19 | 11.4 | 6.6 | 0 | 2017-10-19 | 9.7 | 8.3 | 0 | 2016-10-19 | 9.6 | 8.4 | 0 | 9.03 | 0.23
2025-10-20 | 20 | 0 | 2 | 2024-10-20 | 5.2 | 12.8 | 0 | 2023-10-20 | 10.9 | 7.1 | 0 | 2022-10-20 | 3.9 | 14.1 | 0 | 2021-10-20 | 8.9 | 9.1 | 0 | 2020-10-20 | 5.2 | 12.8 | 0 | 2019-10-20 | 1.7 | 16.3 | 0 | 2018-10-20 | 10.6 | 7.4 | 0 | 2017-10-20 | 9.4 | 8.6 | 0 | 2016-10-20 | 8.2 | 9.8 | 0 | 9.8 | 0.2
2025-10-20 | 18.3 | 0 | 0.3 | 2024-10-20 | 6.8 | 11.2 | 0 | 2023-10-20 | 11.7 | 6.3 | 0 | 2022-10-20 | 4.3 | 13.7 | 0 | 2021-10-20 | 8.6 | 9.4 | 0 | 2020-10-20 | 4.5 | 13.5 | 0 | 2019-10-20 | 0.4 | 17.6 | 0 | 2018-10-20 | 10.2 | 7.8 | 0 | 2017-10-20 | 10.9 | 7.1 | 0 | 2016-10-20 | 9.1 | 8.9 | 0 | 9.55 | 0.03
2025-10-20 | 17.2 | 0.8 | 0 | 2024-10-20 | 7.3 | 10.7 | 0 | 2023-10-20 | 11.9 | 6.1 | 0 | 2022-10-20 | 4.4 | 13.6 | 0 | 2021-10-20 | 7.5 | 10.5 | 0 | 2020-10-20 | 4.2 | 13.8 | 0 | 2019-10-20 | 0.1 | 17.9 | 0 | 2018-10-20 | 9.6 | 8.4 | 0 | 2017-10-20 | 10 | 8 | 0 | 2016-10-20 | 7.5 | 10.5 | 0 | 10.03 | 0
2025-10-20 | 16.1 | 1.9 | 0 | 2024-10-20 | 7.2 | 10.8 | 0 | 2023-10-20 | 11.5 | 6.5 | 0 | 2022-10-20 | 3.7 | 14.3 | 0 | 2021-10-20 | 6.9 | 11.1 | 0 | 2020-10-20 | 4.2 | 13.8 | 0 | 2019-10-20 | 1.1 | 16.9 | 0 | 2018-10-20 | 8.7 | 9.3 | 0 | 2017-10-20 | 8.9 | 9.1 | 0 | 2016-10-20 | 7.9 | 10.1 | 0 | 10.38 | 0
2025-10-20 | 14.9 | 3.1 | 0 | 2024-10-20 | 6.4 | 11.6 | 0 | 2023-10-20 | 11.5 | 6.5 | 0 | 2022-10-20 | 3.4 | 14.6 | 0 | 2021-10-20 | 7.8 | 10.2 | 0 | 2020-10-20 | 4.2 | 13.8 | 0 | 2019-10-20 | 1 | 17 | 0 | 2018-10-20 | 8.5 | 9.5 | 0 | 2017-10-20 | 6.4 | 11.6 | 0 | 2016-10-20 | 8.8 | 9.2 | 0 | 10.71 | 0
2025-10-20 | 14.5 | 3.5 | 0 | 2024-10-20 | 6.7 | 11.3 | 0 | 2023-10-20 | 10.8 | 7.2 | 0 | 2022-10-20 | 3.2 | 14.8 | 0 | 2021-10-20 | 8.4 | 9.6 | 0 | 2020-10-20 | 4.1 | 13.9 | 0 | 2019-10-20 | 0.2 | 17.8 | 0 | 2018-10-20 | 8.8 | 9.2 | 0 | 2017-10-20 | 5.7 | 12.3 | 0 | 2016-10-20 | 7.3 | 10.7 | 0 | 11.03 | 0
2025-10-20 | 14.3 | 3.7 | 0 | 2024-10-20 | 6.4 | 11.6 | 0 | 2023-10-20 | 11.1 | 6.9 | 0 | 2022-10-20 | 3.2 | 14.8 | 0 | 2021-10-20 | 9.4 | 8.6 | 0 | 2020-10-20 | 4.2 | 13.8 | 0 | 2019-10-20 | 1.2 | 16.8 | 0 | 2018-10-20 | 8.9 | 9.1 | 0 | 2017-10-20 | 5.4 | 12.6 | 0 | 2016-10-20 | 7.3 | 10.7 | 0 | 10.86 | 0
2025-10-20 | 14.2 | 3.8 | 0 | 2024-10-20 | 6.6 | 11.4 | 0 | 2023-10-20 | 10.9 | 7.1 | 0 | 2022-10-20 | 3.2 | 14.8 | 0 | 2021-10-20 | 10.2 | 7.8 | 0 | 2020-10-20 | 4.5 | 13.5 | 0 | 2019-10-20 | 1.1 | 16.9 | 0 | 2018-10-20 | 8.7 | 9.3 | 0 | 2017-10-20 | 6.5 | 11.5 | 0 | 2016-10-20 | 7.7 | 10.3 | 0 | 10.64 | 0
2025-10-20 | 14.6 | 3.4 | 0 | 2024-10-20 | 7.8 | 10.2 | 0 | 2023-10-20 | 12.9 | 5.1 | 0 | 2022-10-20 | 4.1 | 13.9 | 0 | 2021-10-20 | 11.9 | 6.1 | 0 | 2020-10-20 | 5 | 13 | 0 | 2019-10-20 | 3 | 15 | 0 | 2018-10-20 | 9.5 | 8.5 | 0 | 2017-10-20 | 9.6 | 8.4 | 0 | 2016-10-20 | 8.4 | 9.6 | 0 | 9.32 | 0
2025-10-20 | 15.4 | 2.6 | 0 | 2024-10-20 | 10.3 | 7.7 | 0 | 2023-10-20 | 14.1 | 3.9 | 0 | 2022-10-20 | 4.8 | 13.2 | 0 | 2021-10-20 | 13.9 | 4.1 | 0 | 2020-10-20 | 5.4 | 12.6 | 0 | 2019-10-20 | 5.5 | 12.5 | 0 | 2018-10-20 | 10.5 | 7.5 | 0 | 2017-10-20 | 11.1 | 6.9 | 0 | 2016-10-20 | 9.1 | 8.9 | 0 | 7.99 | 0
2025-10-20 | 15.5 | 2.5 | 0 | 2024-10-20 | 13.8 | 4.2 | 0 | 2023-10-20 | 15.4 | 2.6 | 0 | 2022-10-20 | 6.4 | 11.6 | 0 | 2021-10-20 | 15.5 | 2.5 | 0 | 2020-10-20 | 6.5 | 11.5 | 0 | 2019-10-20 | 8.3 | 9.7 | 0 | 2018-10-20 | 10.8 | 7.2 | 0 | 2017-10-20 | 12.8 | 5.2 | 0 | 2016-10-20 | 9.2 | 8.8 | 0 | 6.58 | 0
2025-10-20 | 12.3 | 5.7 | 0 | 2024-10-20 | 16.9 | 1.1 | 0 | 2023-10-20 | 18 | 0 | 0 | 2022-10-20 | 7.3 | 10.7 | 0 | 2021-10-20 | 16.7 | 1.3 | 0 | 2020-10-20 | 8 | 10 | 0 | 2019-10-20 | 10.4 | 7.6 | 0 | 2018-10-20 | 11.6 | 6.4 | 0 | 2017-10-20 | 14.7 | 3.3 | 0 | 2016-10-20 | 10.4 | 7.6 | 0 | 5.37 | 0
2025-10-20 | 11.4 | 6.6 | 0 | 2024-10-20 | 18.6 | 0 | 0.6 | 2023-10-20 | 18.8 | 0 | 0.8 | 2022-10-20 | 8.5 | 9.5 | 0 | 2021-10-20 | 18 | 0 | 0 | 2020-10-20 | 9 | 9 | 0 | 2019-10-20 | 12.3 | 5.7 | 0 | 2018-10-20 | 10.5 | 7.5 | 0 | 2017-10-20 | 15.9 | 2.1 | 0 | 2016-10-20 | 11 | 7 | 0 | 4.74 | 0.14
2025-10-20 | 11 | 7 | 0 | 2024-10-20 | 19.7 | 0 | 1.7 | 2023-10-20 | 18 | 0 | 0 | 2022-10-20 | 7.9 | 10.1 | 0 | 2021-10-20 | 19.1 | 0 | 1.1 | 2020-10-20 | 8.9 | 9.1 | 0 | 2019-10-20 | 13.2 | 4.8 | 0 | 2018-10-20 | 10.8 | 7.2 | 0 | 2017-10-20 | 16.9 | 1.1 | 0 | 2016-10-20 | 11.7 | 6.3 | 0 | 4.56 | 0.28
2025-10-20 | 11.4 | 6.6 | 0 | 2024-10-20 | 20.2 | 0 | 2.2 | 2023-10-20 | 18.2 | 0 | 0.2 | 2022-10-20 | 7.4 | 10.6 | 0 | 2021-10-20 | 19 | 0 | 1 | 2020-10-20 | 8.9 | 9.1 | 0 | 2019-10-20 | 14.4 | 3.6 | 0 | 2018-10-20 | 10.2 | 7.8 | 0 | 2017-10-20 | 18.1 | 0 | 0.1 | 2016-10-20 | 11.5 | 6.5 | 0 | 4.42 | 0.35
2025-10-20 | 11.2 | 6.8 | 0 | 2024-10-20 | 20.6 | 0 | 2.6 | 2023-10-20 | 17.5 | 0.5 | 0 | 2022-10-20 | 6.9 | 11.1 | 0 | 2021-10-20 | 19.8 | 0 | 1.8 | 2020-10-20 | 8.6 | 9.4 | 0 | 2019-10-20 | 14 | 4 | 0 | 2018-10-20 | 10.7 | 7.3 | 0 | 2017-10-20 | 18.8 | 0 | 0.8 | 2016-10-20 | 11.6 | 6.4 | 0 | 4.55 | 0.52
2025-10-20 | 11 | 7 | 0 | 2024-10-20 | 20.3 | 0 | 2.3 | 2023-10-20 | 16.6 | 1.4 | 0 | 2022-10-20 | 6.6 | 11.4 | 0 | 2021-10-20 | 18.4 | 0 | 0.4 | 2020-10-20 | 8.2 | 9.8 | 0 | 2019-10-20 | 14.8 | 3.2 | 0 | 2018-10-20 | 9.4 | 8.6 | 0 | 2017-10-20 | 18.5 | 0 | 0.5 | 2016-10-20 | 11.2 | 6.8 | 0 | 4.82 | 0.32
2025-10-20 | 10.7 | 7.3 | 0 | 2024-10-20 | 18.3 | 0 | 0.3 | 2023-10-20 | 15.2 | 2.8 | 0 | 2022-10-20 | 5.8 | 12.2 | 0 | 2021-10-20 | 17.3 | 0.7 | 0 | 2020-10-20 | 6.9 | 11.1 | 0 | 2019-10-20 | 12.8 | 5.2 | 0 | 2018-10-20 | 8.2 | 9.8 | 0 | 2017-10-20 | 16 | 2 | 0 | 2016-10-20 | 10.6 | 7.4 | 0 | 5.85 | 0.03
2025-10-20 | 10.4 | 7.6 | 0 | 2024-10-20 | 16.7 | 1.3 | 0 | 2023-10-20 | 14.2 | 3.8 | 0 | 2022-10-20 | 5.5 | 12.5 | 0 | 2021-10-20 | 16.5 | 1.5 | 0 | 2020-10-20 | 5.6 | 12.4 | 0 | 2019-10-20 | 10.7 | 7.3 | 0 | 2018-10-20 | 6.3 | 11.7 | 0 | 2017-10-20 | 14.2 | 3.8 | 0 | 2016-10-20 | 10.1 | 7.9 | 0 | 6.98 | 0
2025-10-20 | 10.2 | 7.8 | 0 | 2024-10-20 | 16.1 | 1.9 | 0 | 2023-10-20 | 13.5 | 4.5 | 0 | 2022-10-20 | 5.1 | 12.9 | 0 | 2021-10-20 | 14.9 | 3.1 | 0 | 2020-10-20 | 3.9 | 14.1 | 0 | 2019-10-20 | 9.1 | 8.9 | 0 | 2018-10-20 | 4.4 | 13.6 | 0 | 2017-10-20 | 13.1 | 4.9 | 0 | 2016-10-20 | 9.7 | 8.3 | 0 | 8 | 0
2025-10-20 | 10.2 | 7.8 | 0 | 2024-10-20 | 16.6 | 1.4 | 0 | 2023-10-20 | 12.5 | 5.5 | 0 | 2022-10-20 | 4.7 | 13.3 | 0 | 2021-10-20 | 14.3 | 3.7 | 0 | 2020-10-20 | 3.5 | 14.5 | 0 | 2019-10-20 | 7.5 | 10.5 | 0 | 2018-10-20 | 3.9 | 14.1 | 0 | 2017-10-20 | 12 | 6 | 0 | 2016-10-20 | 9.5 | 8.5 | 0 | 8.53 | 0
2025-10-20 | 10.1 | 7.9 | 0 | 2024-10-20 | 16.8 | 1.2 | 0 | 2023-10-20 | 12.6 | 5.4 | 0 | 2022-10-20 | 5.3 | 12.7 | 0 | 2021-10-20 | 13.5 | 4.5 | 0 | 2020-10-20 | 2.7 | 15.3 | 0 | 2019-10-20 | 6 | 12 | 0 | 2018-10-20 | 2.8 | 15.2 | 0 | 2017-10-20 | 11.9 | 6.1 | 0 | 2016-10-20 | 9.6 | 8.4 | 0 | 8.87 | 0
2025-10-20 | 9.8 | 8.2 | 0 | 2024-10-20 | 15.5 | 2.5 | 0 | 2023-10-20 | 12.3 | 5.7 | 0 | 2022-10-20 | 3.6 | 14.4 | 0 | 2021-10-20 | 13 | 5 | 0 | 2020-10-20 | 2.8 | 15.2 | 0 | 2019-10-20 | 5.4 | 12.6 | 0 | 2018-10-20 | 1.7 | 16.3 | 0 | 2017-10-20 | 10.4 | 7.6 | 0 | 2016-10-20 | 9.7 | 8.3 | 0 | 9.58 | 0
2025-10-20 | 9.2 | 8.8 | 0 | 2024-10-20 | 15.2 | 2.8 | 0 | 2023-10-20 | 11.6 | 6.4 | 0 | 2022-10-20 | 3.2 | 14.8 | 0 | 2021-10-20 | 11.4 | 6.6 | 0 | 2020-10-20 | 3.2 | 14.8 | 0 | 2019-10-20 | 4.6 | 13.4 | 0 | 2018-10-20 | 2 | 16 | 0 | 2017-10-20 | 10 | 8 | 0 | 2016-10-20 | 9.6 | 8.4 | 0 | 10 | 0
2025-10-21 | 9 | 9 | 0 | 2024-10-21 | 14.5 | 3.5 | 0 | 2023-10-21 | 11.8 | 6.2 | 0 | 2022-10-21 | 3 | 15 | 0 | 2021-10-21 | 10.9 | 7.1 | 0 | 2020-10-21 | 2.4 | 15.6 | 0 | 2019-10-21 | 3.7 | 14.3 | 0 | 2018-10-21 | 0.6 | 17.4 | 0 | 2017-10-21 | 9.4 | 8.6 | 0 | 2016-10-21 | 9.5 | 8.5 | 0 | 10.52 | 0
2025-10-21 | 9.1 | 8.9 | 0 | 2024-10-21 | 13.4 | 4.6 | 0 | 2023-10-21 | 11.7 | 6.3 | 0 | 2022-10-21 | 2.8 | 15.2 | 0 | 2021-10-21 | 10.6 | 7.4 | 0 | 2020-10-21 | 3.4 | 14.6 | 0 | 2019-10-21 | 3.5 | 14.5 | 0 | 2018-10-21 | 0.7 | 17.3 | 0 | 2017-10-21 | 9.4 | 8.6 | 0 | 2016-10-21 | 9.4 | 8.6 | 0 | 10.6 | 0
2025-10-21 | 9.1 | 8.9 | 0 | 2024-10-21 | 13.6 | 4.4 | 0 | 2023-10-21 | 11.6 | 6.4 | 0 | 2022-10-21 | 2 | 16 | 0 | 2021-10-21 | 11.3 | 6.7 | 0 | 2020-10-21 | 4.7 | 13.3 | 0 | 2019-10-21 | 2.7 | 15.3 | 0 | 2018-10-21 | 0.3 | 17.7 | 0 | 2017-10-21 | 9.2 | 8.8 | 0 | 2016-10-21 | 9.3 | 8.7 | 0 | 10.62 | 0
2025-10-21 | 8.8 | 9.2 | 0 | 2024-10-21 | 13 | 5 | 0 | 2023-10-21 | 11.6 | 6.4 | 0 | 2022-10-21 | 2.1 | 15.9 | 0 | 2021-10-21 | 10.7 | 7.3 | 0 | 2020-10-21 | 4.7 | 13.3 | 0 | 2019-10-21 | 2.4 | 15.6 | 0 | 2018-10-21 | 0.6 | 17.4 | 0 | 2017-10-21 | 9.4 | 8.6 | 0 | 2016-10-21 | 9.4 | 8.6 | 0 | 10.73 | 0
2025-10-21 | 8 | 10 | 0 | 2024-10-21 | 12.2 | 5.8 | 0 | 2023-10-21 | 11.7 | 6.3 | 0 | 2022-10-21 | 1.2 | 16.8 | 0 | 2021-10-21 | 11.1 | 6.9 | 0 | 2020-10-21 | 4.8 | 13.2 | 0 | 2019-10-21 | 2 | 16 | 0 | 2018-10-21 | 0.2 | 17.8 | 0 | 2017-10-21 | 9.5 | 8.5 | 0 | 2016-10-21 | 9.4 | 8.6 | 0 | 10.99 | 0
2025-10-21 | 8.1 | 9.9 | 0 | 2024-10-21 | 11 | 7 | 0 | 2023-10-21 | 11.8 | 6.2 | 0 | 2022-10-21 | 0.9 | 17.1 | 0 | 2021-10-21 | 10.7 | 7.3 | 0 | 2020-10-21 | 4.4 | 13.6 | 0 | 2019-10-21 | 3.1 | 14.9 | 0 | 2018-10-21 | -0.4 | 18.4 | 0 | 2017-10-21 | 9.1 | 8.9 | 0 | 2016-10-21 | 9.3 | 8.7 | 0 | 11.2 | 0
2025-10-21 | 7.6 | 10.4 | 0 | 2024-10-21 | 10.5 | 7.5 | 0 | 2023-10-21 | 11.7 | 6.3 | 0 | 2022-10-21 | 0.9 | 17.1 | 0 | 2021-10-21 | 9.5 | 8.5 | 0 | 2020-10-21 | 4 | 14 | 0 | 2019-10-21 | 2.8 | 15.2 | 0 | 2018-10-21 | -0.8 | 18.8 | 0 | 2017-10-21 | 8 | 10 | 0 | 2016-10-21 | 9.3 | 8.7 | 0 | 11.65 | 0
2025-10-21 | 7.5 | 10.5 | 0 | 2024-10-21 | 11.1 | 6.9 | 0 | 2023-10-21 | 11.7 | 6.3 | 0 | 2022-10-21 | 2 | 16 | 0 | 2021-10-21 | 9.3 | 8.7 | 0 | 2020-10-21 | 4.2 | 13.8 | 0 | 2019-10-21 | 1.9 | 16.1 | 0 | 2018-10-21 | 0 | 18 | 0 | 2017-10-21 | 8.6 | 9.4 | 0 | 2016-10-21 | 9.3 | 8.7 | 0 | 11.44 | 0
2025-10-21 | 8.3 | 9.7 | 0 | 2024-10-21 | 13.4 | 4.6 | 0 | 2023-10-21 | 11.8 | 6.2 | 0 | 2022-10-21 | 4.1 | 13.9 | 0 | 2021-10-21 | 9.8 | 8.2 | 0 | 2020-10-21 | 4.7 | 13.3 | 0 | 2019-10-21 | 5.7 | 12.3 | 0 | 2018-10-21 | 0.2 | 17.8 | 0 | 2017-10-21 | 11.3 | 6.7 | 0 | 2016-10-21 | 9.1 | 8.9 | 0 | 10.16 | 0
2025-10-21 | 9.5 | 8.5 | 0 | 2024-10-21 | 16.2 | 1.8 | 0 | 2023-10-21 | 12.2 | 5.8 | 0 | 2022-10-21 | 7.2 | 10.8 | 0 | 2021-10-21 | 9.6 | 8.4 | 0 | 2020-10-21 | 5.8 | 12.2 | 0 | 2019-10-21 | 8.2 | 9.8 | 0 | 2018-10-21 | 1.4 | 16.6 | 0 | 2017-10-21 | 13.8 | 4.2 | 0 | 2016-10-21 | 9.2 | 8.8 | 0 | 8.69 | 0
2025-10-21 | 11.4 | 6.6 | 0 | 2024-10-21 | 18.6 | 0 | 0.6 | 2023-10-21 | 12.2 | 5.8 | 0 | 2022-10-21 | 8.6 | 9.4 | 0 | 2021-10-21 | 10.1 | 7.9 | 0 | 2020-10-21 | 7.1 | 10.9 | 0 | 2019-10-21 | 10.6 | 7.4 | 0 | 2018-10-21 | 1.5 | 16.5 | 0 | 2017-10-21 | 16.2 | 1.8 | 0 | 2016-10-21 | 9.3 | 8.7 | 0 | 7.5 | 0.06
2025-10-21 | 12 | 6 | 0 | 2024-10-21 | 20.3 | 0 | 2.3 | 2023-10-21 | 12.6 | 5.4 | 0 | 2022-10-21 | 9.9 | 8.1 | 0 | 2021-10-21 | 11.1 | 6.9 | 0 | 2020-10-21 | 10 | 8 | 0 | 2019-10-21 | 12.4 | 5.6 | 0 | 2018-10-21 | 2.3 | 15.7 | 0 | 2017-10-21 | 18.9 | 0 | 0.9 | 2016-10-21 | 9.4 | 8.6 | 0 | 6.43 | 0.32
2025-10-21 | 13.9 | 4.1 | 0 | 2024-10-21 | 22 | 0 | 4 | 2023-10-21 | 12.7 | 5.3 | 0 | 2022-10-21 | 11.3 | 6.7 | 0 | 2021-10-21 | 13.5 | 4.5 | 0 | 2020-10-21 | 15.4 | 2.6 | 0 | 2019-10-21 | 14.6 | 3.4 | 0 | 2018-10-21 | 2.5 | 15.5 | 0 | 2017-10-21 | 20.8 | 0 | 2.8 | 2016-10-21 | 9.4 | 8.6 | 0 | 5.07 | 0.68
2025-10-21 | 13.7 | 4.3 | 0 | 2024-10-21 | 23.1 | 0 | 5.1 | 2023-10-21 | 13.1 | 4.9 | 0 | 2022-10-21 | 13.4 | 4.6 | 0 | 2021-10-21 | 14.8 | 3.2 | 0 | 2020-10-21 | 11.9 | 6.1 | 0 | 2019-10-21 | 15.1 | 2.9 | 0 | 2018-10-21 | 2.6 | 15.4 | 0 | 2017-10-21 | 21.5 | 0 | 3.5 | 2016-10-21 | 9.5 | 8.5 | 0 | 4.99 | 0.86
2025-10-21 | 13.1 | 4.9 | 0 | 2024-10-21 | 24.4 | 0 | 6.4 | 2023-10-21 | 11 | 7 | 0 | 2022-10-21 | 13.7 | 4.3 | 0 | 2021-10-21 | 15.4 | 2.6 | 0 | 2020-10-21 | 13.6 | 4.4 | 0 | 2019-10-21 | 15.8 | 2.2 | 0 | 2018-10-21 | 3 | 15 | 0 | 2017-10-21 | 22.1 | 0 | 4.1 | 2016-10-21 | 9.4 | 8.6 | 0 | 4.9 | 1.05
2025-10-21 | 12.4 | 5.6 | 0 | 2024-10-21 | 24.5 | 0 | 6.5 | 2023-10-21 | 10 | 8 | 0 | 2022-10-21 | 13.8 | 4.2 | 0 | 2021-10-21 | 16 | 2 | 0 | 2020-10-21 | 13.7 | 4.3 | 0 | 2019-10-21 | 16 | 2 | 0 | 2018-10-21 | 2.7 | 15.3 | 0 | 2017-10-21 | 21 | 0 | 3 | 2016-10-21 | 9 | 9 | 0 | 5.04 | 0.95
2025-10-21 | 12 | 6 | 0 | 2024-10-21 | 23.5 | 0 | 5.5 | 2023-10-21 | 9.4 | 8.6 | 0 | 2022-10-21 | 13.8 | 4.2 | 0 | 2021-10-21 | 15.7 | 2.3 | 0 | 2020-10-21 | 14.8 | 3.2 | 0 | 2019-10-21 | 15.2 | 2.8 | 0 | 2018-10-21 | 2.4 | 15.6 | 0 | 2017-10-21 | 20.9 | 0 | 2.9 | 2016-10-21 | 8.4 | 9.6 | 0 | 5.23 | 0.84
2025-10-21 | 11.2 | 6.8 | 0 | 2024-10-21 | 21.6 | 0 | 3.6 | 2023-10-21 | 9.2 | 8.8 | 0 | 2022-10-21 | 12.1 | 5.9 | 0 | 2021-10-21 | 14.9 | 3.1 | 0 | 2020-10-21 | 13.2 | 4.8 | 0 | 2019-10-21 | 12.7 | 5.3 | 0 | 2018-10-21 | 2.3 | 15.7 | 0 | 2017-10-21 | 18.1 | 0 | 0.1 | 2016-10-21 | 7.9 | 10.1 | 0 | 6.05 | 0.37
2025-10-21 | 11.2 | 6.8 | 0 | 2024-10-21 | 19.3 | 0 | 1.3 | 2023-10-21 | 8.7 | 9.3 | 0 | 2022-10-21 | 11.1 | 6.9 | 0 | 2021-10-21 | 14.6 | 3.4 | 0 | 2020-10-21 | 10.8 | 7.2 | 0 | 2019-10-21 | 11.7 | 6.3 | 0 | 2018-10-21 | 1.7 | 16.3 | 0 | 2017-10-21 | 16.5 | 1.5 | 0 | 2016-10-21 | 7.5 | 10.5 | 0 | 6.82 | 0.13
2025-10-21 | 11.1 | 6.9 | 0 | 2024-10-21 | 18.7 | 0 | 0.7 | 2023-10-21 | 8.2 | 9.8 | 0 | 2022-10-21 | 10.2 | 7.8 | 0 | 2021-10-21 | 14.6 | 3.4 | 0 | 2020-10-21 | 10 | 8 | 0 | 2019-10-21 | 10.9 | 7.1 | 0 | 2018-10-21 | 1 | 17 | 0 | 2017-10-21 | 15.3 | 2.7 | 0 | 2016-10-21 | 6.7 | 11.3 | 0 | 7.4 | 0.07
2025-10-21 | 11.3 | 6.7 | 0 | 2024-10-21 | 17.3 | 0.7 | 0 | 2023-10-21 | 7.8 | 10.2 | 0 | 2022-10-21 | 9.8 | 8.2 | 0 | 2021-10-21 | 14.4 | 3.6 | 0 | 2020-10-21 | 9.2 | 8.8 | 0 | 2019-10-21 | 10.6 | 7.4 | 0 | 2018-10-21 | 0.1 | 17.9 | 0 | 2017-10-21 | 14.7 | 3.3 | 0 | 2016-10-21 | 6.2 | 11.8 | 0 | 7.86 | 0
2025-10-21 | 10.3 | 7.7 | 0 | 2024-10-21 | 16.3 | 1.7 | 0 | 2023-10-21 | 7.7 | 10.3 | 0 | 2022-10-21 | 10 | 8 | 0 | 2021-10-21 | 14 | 4 | 0 | 2020-10-21 | 8.1 | 9.9 | 0 | 2019-10-21 | 10 | 8 | 0 | 2018-10-21 | 0.4 | 17.6 | 0 | 2017-10-21 | 14.2 | 3.8 | 0 | 2016-10-21 | 6.3 | 11.7 | 0 | 8.27 | 0
2025-10-21 | 8.6 | 9.4 | 0 | 2024-10-21 | 14.7 | 3.3 | 0 | 2023-10-21 | 7.2 | 10.8 | 0 | 2022-10-21 | 11.1 | 6.9 | 0 | 2021-10-21 | 14.4 | 3.6 | 0 | 2020-10-21 | 7.2 | 10.8 | 0 | 2019-10-21 | 9.8 | 8.2 | 0 | 2018-10-21 | 0.3 | 17.7 | 0 | 2017-10-21 | 13.8 | 4.2 | 0 | 2016-10-21 | 5.9 | 12.1 | 0 | 8.7 | 0
2025-10-21 | 9.6 | 8.4 | 0 | 2024-10-21 | 13.2 | 4.8 | 0 | 2023-10-21 | 7.1 | 10.9 | 0 | 2022-10-21 | 10.8 | 7.2 | 0 | 2021-10-21 | 14.2 | 3.8 | 0 | 2020-10-21 | 6.2 | 11.8 | 0 | 2019-10-21 | 9.7 | 8.3 | 0 | 2018-10-21 | -0.5 | 18.5 | 0 | 2017-10-21 | 12.7 | 5.3 | 0 | 2016-10-21 | 5.6 | 12.4 | 0 | 9.14 | 0
2025-10-22 | 8.3 | 9.7 | 0 | 2024-10-22 | 13.2 | 4.8 | 0 | 2023-10-22 | 6.6 | 11.4 | 0 | 2022-10-22 | 10 | 8 | 0 | 2021-10-22 | 14 | 4 | 0 | 2020-10-22 | 6.8 | 11.2 | 0 | 2019-10-22 | 10 | 8 | 0 | 2018-10-22 | -0.5 | 18.5 | 0 | 2017-10-22 | 12.3 | 5.7 | 0 | 2016-10-22 | 5.4 | 12.6 | 0 | 9.39 | 0
2025-10-22 | 8.5 | 9.5 | 0 | 2024-10-22 | 11.1 | 6.9 | 0 | 2023-10-22 | 6.2 | 11.8 | 0 | 2022-10-22 | 9.7 | 8.3 | 0 | 2021-10-22 | 12.1 | 5.9 | 0 | 2020-10-22 | 4.5 | 13.5 | 0 | 2019-10-22 | 10 | 8 | 0 | 2018-10-22 | -0.6 | 18.6 | 0 | 2017-10-22 | 10.7 | 7.3 | 0 | 2016-10-22 | 5.1 | 12.9 | 0 | 10.27 | 0
2025-10-22 | 7.7 | 10.3 | 0 | 2024-10-22 | 11.7 | 6.3 | 0 | 2023-10-22 | 5.7 | 12.3 | 0 | 2022-10-22 | 8.8 | 9.2 | 0 | 2021-10-22 | 10.4 | 7.6 | 0 | 2020-10-22 | 4.5 | 13.5 | 0 | 2019-10-22 | 9.7 | 8.3 | 0 | 2018-10-22 | -1.2 | 19.2 | 0 | 2017-10-22 | 7.9 | 10.1 | 0 | 2016-10-22 | 5 | 13 | 0 | 10.98 | 0
2025-10-22 | 6.7 | 11.3 | 0 | 2024-10-22 | 9.9 | 8.1 | 0 | 2023-10-22 | 5.4 | 12.6 | 0 | 2022-10-22 | 8.9 | 9.1 | 0 | 2021-10-22 | 9.2 | 8.8 | 0 | 2020-10-22 | 6.1 | 11.9 | 0 | 2019-10-22 | 9.3 | 8.7 | 0 | 2018-10-22 | -0.8 | 18.8 | 0 | 2017-10-22 | 8.4 | 9.6 | 0 | 2016-10-22 | 4.7 | 13.3 | 0 | 11.22 | 0
2025-10-22 | 7.3 | 10.7 | 0 | 2024-10-22 | 9.6 | 8.4 | 0 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 8.6 | 9.4 | 0 | 2021-10-22 | 7.8 | 10.2 | 0 | 2020-10-22 | 6.1 | 11.9 | 0 | 2019-10-22 | 9.2 | 8.8 | 0 | 2018-10-22 | -0.7 | 18.7 | 0 | 2017-10-22 | 8.2 | 9.8 | 0 | 2016-10-22 | 4.6 | 13.4 | 0 | 11.46 | 0
2025-10-22 | 6.1 | 11.9 | 0 | 2024-10-22 | 9 | 9 | 0 | 2023-10-22 | 4.4 | 13.6 | 0 | 2022-10-22 | 8 | 10 | 0 | 2021-10-22 | 6.2 | 11.8 | 0 | 2020-10-22 | 6.3 | 11.7 | 0 | 2019-10-22 | 9.1 | 8.9 | 0 | 2018-10-22 | -0.8 | 18.8 | 0 | 2017-10-22 | 8.6 | 9.4 | 0 | 2016-10-22 | 4.4 | 13.6 | 0 | 11.87 | 0
2025-10-22 | 6.2 | 11.8 | 0 | 2024-10-22 | 9.3 | 8.7 | 0 | 2023-10-22 | 4.2 | 13.8 | 0 | 2022-10-22 | 8.4 | 9.6 | 0 | 2021-10-22 | 5 | 13 | 0 | 2020-10-22 | 6.5 | 11.5 | 0 | 2019-10-22 | 8.7 | 9.3 | 0 | 2018-10-22 | -1 | 19 | 0 | 2017-10-22 | 8.1 | 9.9 | 0 | 2016-10-22 | 4.5 | 13.5 | 0 | 12.01 | 0
2025-10-22 | 6.5 | 11.5 | 0 | 2024-10-22 | 9.7 | 8.3 | 0 | 2023-10-22 | 4.1 | 13.9 | 0 | 2022-10-22 | 8.9 | 9.1 | 0 | 2021-10-22 | 4.2 | 13.8 | 0 | 2020-10-22 | 6.5 | 11.5 | 0 | 2019-10-22 | 8.8 | 9.2 | 0 | 2018-10-22 | -0.8 | 18.8 | 0 | 2017-10-22 | 8.3 | 9.7 | 0 | 2016-10-22 | 4.4 | 13.6 | 0 | 11.94 | 0
2025-10-22 | 8.2 | 9.8 | 0 | 2024-10-22 | 10.6 | 7.4 | 0 | 2023-10-22 | 4.2 | 13.8 | 0 | 2022-10-22 | 10.8 | 7.2 | 0 | 2021-10-22 | 4.1 | 13.9 | 0 | 2020-10-22 | 7.5 | 10.5 | 0 | 2019-10-22 | 9.5 | 8.5 | 0 | 2018-10-22 | 0.3 | 17.7 | 0 | 2017-10-22 | 11.6 | 6.4 | 0 | 2016-10-22 | 4.4 | 13.6 | 0 | 10.88 | 0
2025-10-22 | 9.1 | 8.9 | 0 | 2024-10-22 | 12.7 | 5.3 | 0 | 2023-10-22 | 4.3 | 13.7 | 0 | 2022-10-22 | 13.4 | 4.6 | 0 | 2021-10-22 | 4.1 | 13.9 | 0 | 2020-10-22 | 8.6 | 9.4 | 0 | 2019-10-22 | 9.6 | 8.4 | 0 | 2018-10-22 | 1.3 | 16.7 | 0 | 2017-10-22 | 14.5 | 3.5 | 0 | 2016-10-22 | 4.6 | 13.4 | 0 | 9.78 | 0
2025-10-22 | 9.1 | 8.9 | 0 | 2024-10-22 | 15.9 | 2.1 | 0 | 2023-10-22 | 4.5 | 13.5 | 0 | 2022-10-22 | 15.9 | 2.1 | 0 | 2021-10-22 | 4.4 | 13.6 | 0 | 2020-10-22 | 9.4 | 8.6 | 0 | 2019-10-22 | 10.5 | 7.5 | 0 | 2018-10-22 | 2.5 | 15.5 | 0 | 2017-10-22 | 16.8 | 1.2 | 0 | 2016-10-22 | 4.6 | 13.4 | 0 | 8.64 | 0
2025-10-22 | 8.9 | 9.1 | 0 | 2024-10-22 | 18.3 | 0 | 0.3 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 17.7 | 0.3 | 0 | 2021-10-22 | 5.4 | 12.6 | 0 | 2020-10-22 | 10.1 | 7.9 | 0 | 2019-10-22 | 11.7 | 6.3 | 0 | 2018-10-22 | 3.4 | 14.6 | 0 | 2017-10-22 | 18.6 | 0 | 0.6 | 2016-10-22 | 4.9 | 13.1 | 0 | 7.72 | 0.09
2025-10-22 | 9.9 | 8.1 | 0 | 2024-10-22 | 20.4 | 0 | 2.4 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 18.9 | 0 | 0.9 | 2021-10-22 | 5.2 | 12.8 | 0 | 2020-10-22 | 11.1 | 6.9 | 0 | 2019-10-22 | 11.3 | 6.7 | 0 | 2018-10-22 | 4.3 | 13.7 | 0 | 2017-10-22 | 20.4 | 0 | 2.4 | 2016-10-22 | 5 | 13 | 0 | 7.45 | 0.57
2025-10-22 | 10.3 | 7.7 | 0 | 2024-10-22 | 22.2 | 0 | 4.2 | 2023-10-22 | 4.4 | 13.6 | 0 | 2022-10-22 | 20.1 | 0 | 2.1 | 2021-10-22 | 5.8 | 12.2 | 0 | 2020-10-22 | 11.1 | 6.9 | 0 | 2019-10-22 | 10.8 | 7.2 | 0 | 2018-10-22 | 4.5 | 13.5 | 0 | 2017-10-22 | 21.1 | 0 | 3.1 | 2016-10-22 | 4.7 | 13.3 | 0 | 7.44 | 0.94
2025-10-22 | 9.7 | 8.3 | 0 | 2024-10-22 | 24.1 | 0 | 6.1 | 2023-10-22 | 4.5 | 13.5 | 0 | 2022-10-22 | 20.6 | 0 | 2.6 | 2021-10-22 | 5.9 | 12.1 | 0 | 2020-10-22 | 11.1 | 6.9 | 0 | 2019-10-22 | 10.8 | 7.2 | 0 | 2018-10-22 | 4.4 | 13.6 | 0 | 2017-10-22 | 21.8 | 0 | 3.8 | 2016-10-22 | 4.5 | 13.5 | 0 | 7.51 | 1.25
2025-10-22 | 11.1 | 6.9 | 0 | 2024-10-22 | 24.2 | 0 | 6.2 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 20.4 | 0 | 2.4 | 2021-10-22 | 6.3 | 11.7 | 0 | 2020-10-22 | 11.2 | 6.8 | 0 | 2019-10-22 | 10.9 | 7.1 | 0 | 2018-10-22 | 4.4 | 13.6 | 0 | 2017-10-22 | 21.3 | 0 | 3.3 | 2016-10-22 | 4.1 | 13.9 | 0 | 7.33 | 1.19
2025-10-22 | 11.8 | 6.2 | 0 | 2024-10-22 | 22.7 | 0 | 4.7 | 2023-10-22 | 4.8 | 13.2 | 0 | 2022-10-22 | 19.4 | 0 | 1.4 | 2021-10-22 | 5.7 | 12.3 | 0 | 2020-10-22 | 11.1 | 6.9 | 0 | 2019-10-22 | 11.4 | 6.6 | 0 | 2018-10-22 | 4 | 14 | 0 | 2017-10-22 | 19 | 0 | 1 | 2016-10-22 | 3.7 | 14.3 | 0 | 7.35 | 0.71
2025-10-22 | 9.8 | 8.2 | 0 | 2024-10-22 | 20.5 | 0 | 2.5 | 2023-10-22 | 4.8 | 13.2 | 0 | 2022-10-22 | 16.6 | 1.4 | 0 | 2021-10-22 | 4.2 | 13.8 | 0 | 2020-10-22 | 10.6 | 7.4 | 0 | 2019-10-22 | 11.4 | 6.6 | 0 | 2018-10-22 | 3.8 | 14.2 | 0 | 2017-10-22 | 18 | 0 | 0 | 2016-10-22 | 3.6 | 14.4 | 0 | 7.92 | 0.25
2025-10-22 | 8.6 | 9.4 | 0 | 2024-10-22 | 17.6 | 0.4 | 0 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 14.8 | 3.2 | 0 | 2021-10-22 | 1.9 | 16.1 | 0 | 2020-10-22 | 9.6 | 8.4 | 0 | 2019-10-22 | 11.7 | 6.3 | 0 | 2018-10-22 | 3.1 | 14.9 | 0 | 2017-10-22 | 16.2 | 1.8 | 0 | 2016-10-22 | 3.5 | 14.5 | 0 | 8.83 | 0
2025-10-22 | 7.9 | 10.1 | 0 | 2024-10-22 | 17 | 1 | 0 | 2023-10-22 | 4.5 | 13.5 | 0 | 2022-10-22 | 13.4 | 4.6 | 0 | 2021-10-22 | 1.8 | 16.2 | 0 | 2020-10-22 | 9.7 | 8.3 | 0 | 2019-10-22 | 12 | 6 | 0 | 2018-10-22 | 2.5 | 15.5 | 0 | 2017-10-22 | 13.7 | 4.3 | 0 | 2016-10-22 | 3.3 | 14.7 | 0 | 9.42 | 0
2025-10-22 | 6.9 | 11.1 | 0 | 2024-10-22 | 15.5 | 2.5 | 0 | 2023-10-22 | 4.4 | 13.6 | 0 | 2022-10-22 | 15.3 | 2.7 | 0 | 2021-10-22 | 0.8 | 17.2 | 0 | 2020-10-22 | 9.4 | 8.6 | 0 | 2019-10-22 | 12.4 | 5.6 | 0 | 2018-10-22 | 2.2 | 15.8 | 0 | 2017-10-22 | 13.1 | 4.9 | 0 | 2016-10-22 | 3.4 | 14.6 | 0 | 9.66 | 0
2025-10-22 | 7.3 | 10.7 | 0 | 2024-10-22 | 14.7 | 3.3 | 0 | 2023-10-22 | 4.5 | 13.5 | 0 | 2022-10-22 | 12.4 | 5.6 | 0 | 2021-10-22 | 1.4 | 16.6 | 0 | 2020-10-22 | 9.6 | 8.4 | 0 | 2019-10-22 | 12.4 | 5.6 | 0 | 2018-10-22 | 1.9 | 16.1 | 0 | 2017-10-22 | 14 | 4 | 0 | 2016-10-22 | 3.9 | 14.1 | 0 | 9.79 | 0
2025-10-22 | 5.9 | 12.1 | 0 | 2024-10-22 | 13.8 | 4.2 | 0 | 2023-10-22 | 4.7 | 13.3 | 0 | 2022-10-22 | 12 | 6 | 0 | 2021-10-22 | 1.9 | 16.1 | 0 | 2020-10-22 | 9.8 | 8.2 | 0 | 2019-10-22 | 12.4 | 5.6 | 0 | 2018-10-22 | 0 | 18 | 0 | 2017-10-22 | 11.9 | 6.1 | 0 | 2016-10-22 | 4.8 | 13.2 | 0 | 10.28 | 0
2025-10-22 | 6 | 12 | 0 | 2024-10-22 | 13.5 | 4.5 | 0 | 2023-10-22 | 5 | 13 | 0 | 2022-10-22 | 10.8 | 7.2 | 0 | 2021-10-22 | 1.1 | 16.9 | 0 | 2020-10-22 | 9.6 | 8.4 | 0 | 2019-10-22 | 12.2 | 5.8 | 0 | 2018-10-22 | 0.3 | 17.7 | 0 | 2017-10-22 | 11.2 | 6.8 | 0 | 2016-10-22 | 4.7 | 13.3 | 0 | 10.56 | 0
2025-10-23 | 6.3 | 11.7 | 0 | 2024-10-23 | 13.7 | 4.3 | 0 | 2023-10-23 | 4.8 | 13.2 | 0 | 2022-10-23 | 11 | 7 | 0 | 2021-10-23 | 0.3 | 17.7 | 0 | 2020-10-23 | 9.6 | 8.4 | 0 | 2019-10-23 | 12.3 | 5.7 | 0 | 2018-10-23 | 0.5 | 17.5 | 0 | 2017-10-23 | 10.7 | 7.3 | 0 | 2016-10-23 | 4.6 | 13.4 | 0 | 10.62 | 0
2025-10-23 | 6.1 | 11.9 | 0 | 2024-10-23 | 11.5 | 6.5 | 0 | 2023-10-23 | 4.1 | 13.9 | 0 | 2022-10-23 | 10.4 | 7.6 | 0 | 2021-10-23 | -0.1 | 18.1 | 0 | 2020-10-23 | 9.7 | 8.3 | 0 | 2019-10-23 | 11 | 7 | 0 | 2018-10-23 | 0.8 | 17.2 | 0 | 2017-10-23 | 9.1 | 8.9 | 0 | 2016-10-23 | 4.6 | 13.4 | 0 | 11.28 | 0
2025-10-23 | 6.4 | 11.6 | 0 | 2024-10-23 | 13.7 | 4.3 | 0 | 2023-10-23 | 4.2 | 13.8 | 0 | 2022-10-23 | 10.2 | 7.8 | 0 | 2021-10-23 | 1 | 17 | 0 | 2020-10-23 | 9.8 | 8.2 | 0 | 2019-10-23 | 10.8 | 7.2 | 0 | 2018-10-23 | 0.9 | 17.1 | 0 | 2017-10-23 | 8.8 | 9.2 | 0 | 2016-10-23 | 4.1 | 13.9 | 0 | 11.01 | 0
2025-10-23 | 6.4 | 11.6 | 0 | 2024-10-23 | 13.8 | 4.2 | 0 | 2023-10-23 | 2.8 | 15.2 | 0 | 2022-10-23 | 7.8 | 10.2 | 0 | 2021-10-23 | 0.9 | 17.1 | 0 | 2020-10-23 | 10 | 8 | 0 | 2019-10-23 | 9.6 | 8.4 | 0 | 2018-10-23 | 1.1 | 16.9 | 0 | 2017-10-23 | 9.7 | 8.3 | 0 | 2016-10-23 | 4 | 14 | 0 | 11.39 | 0
2025-10-23 | 6.5 | 11.5 | 0 | 2024-10-23 | 14.4 | 3.6 | 0 | 2023-10-23 | 1.8 | 16.2 | 0 | 2022-10-23 | 8.1 | 9.9 | 0 | 2021-10-23 | 0.6 | 17.4 | 0 | 2020-10-23 | 10.1 | 7.9 | 0 | 2019-10-23 | 9.3 | 8.7 | 0 | 2018-10-23 | 1 | 17 | 0 | 2017-10-23 | 11.4 | 6.6 | 0 | 2016-10-23 | 3.2 | 14.8 | 0 | 11.36 | 0
2025-10-23 | 6 | 12 | 0 | 2024-10-23 | 13.8 | 4.2 | 0 | 2023-10-23 | 1.2 | 16.8 | 0 | 2022-10-23 | 5.2 | 12.8 | 0 | 2021-10-23 | 0.6 | 17.4 | 0 | 2020-10-23 | 9.6 | 8.4 | 0 | 2019-10-23 | 8.3 | 9.7 | 0 | 2018-10-23 | 0.6 | 17.4 | 0 | 2017-10-23 | 8.1 | 9.9 | 0 | 2016-10-23 | 2.4 | 15.6 | 0 | 12.42 | 0
2025-10-23 | 6.2 | 11.8 | 0 | 2024-10-23 | 13.8 | 4.2 | 0 | 2023-10-23 | 0.3 | 17.7 | 0 | 2022-10-23 | 4.7 | 13.3 | 0 | 2021-10-23 | 0.6 | 17.4 | 0 | 2020-10-23 | 9 | 9 | 0 | 2019-10-23 | 7.3 | 10.7 | 0 | 2018-10-23 | 0.8 | 17.2 | 0 | 2017-10-23 | 7.3 | 10.7 | 0 | 2016-10-23 | 2.5 | 15.5 | 0 | 12.75 | 0
2025-10-23 | 6.6 | 11.4 | 0 | 2024-10-23 | 15.2 | 2.8 | 0 | 2023-10-23 | 0.8 | 17.2 | 0 | 2022-10-23 | 4.7 | 13.3 | 0 | 2021-10-23 | 0.8 | 17.2 | 0 | 2020-10-23 | 9.3 | 8.7 | 0 | 2019-10-23 | 6.7 | 11.3 | 0 | 2018-10-23 | 1 | 17 | 0 | 2017-10-23 | 7.5 | 10.5 | 0 | 2016-10-23 | 1.5 | 16.5 | 0 | 12.59 | 0
2025-10-23 | 7 | 11 | 0 | 2024-10-23 | 16.8 | 1.2 | 0 | 2023-10-23 | 2.8 | 15.2 | 0 | 2022-10-23 | 9.6 | 8.4 | 0 | 2021-10-23 | 1.8 | 16.2 | 0 | 2020-10-23 | 10.2 | 7.8 | 0 | 2019-10-23 | 8.7 | 9.3 | 0 | 2018-10-23 | 1.7 | 16.3 | 0 | 2017-10-23 | 11.5 | 6.5 | 0 | 2016-10-23 | 1.7 | 16.3 | 0 | 10.82 | 0
2025-10-23 | 7.6 | 10.4 | 0 | 2024-10-23 | 17.8 | 0.2 | 0 | 2023-10-23 | 4.5 | 13.5 | 0 | 2022-10-23 | 13.2 | 4.8 | 0 | 2021-10-23 | 3.6 | 14.4 | 0 | 2020-10-23 | 12.2 | 5.8 | 0 | 2019-10-23 | 10.6 | 7.4 | 0 | 2018-10-23 | 2.9 | 15.1 | 0 | 2017-10-23 | 16.8 | 1.2 | 0 | 2016-10-23 | 3.4 | 14.6 | 0 | 8.74 | 0
2025-10-23 | 7.6 | 10.4 | 0 | 2024-10-23 | 17.4 | 0.6 | 0 | 2023-10-23 | 6 | 12 | 0 | 2022-10-23 | 15.3 | 2.7 | 0 | 2021-10-23 | 4.8 | 13.2 | 0 | 2020-10-23 | 15.8 | 2.2 | 0 | 2019-10-23 | 11.6 | 6.4 | 0 | 2018-10-23 | 4.2 | 13.8 | 0 | 2017-10-23 | 18 | 0 | 0 | 2016-10-23 | 4.8 | 13.2 | 0 | 7.45 | 0
2025-10-23 | 7.3 | 10.7 | 0 | 2024-10-23 | 19.3 | 0 | 1.3 | 2023-10-23 | 7.1 | 10.9 | 0 | 2022-10-23 | 17.3 | 0.7 | 0 | 2021-10-23 | 5.2 | 12.8 | 0 | 2020-10-23 | 19.7 | 0 | 1.7 | 2019-10-23 | 13 | 5 | 0 | 2018-10-23 | 6.7 | 11.3 | 0 | 2017-10-23 | 18.7 | 0 | 0.7 | 2016-10-23 | 6.8 | 11.2 | 0 | 6.26 | 0.37
2025-10-23 | 8.7 | 9.3 | 0 | 2024-10-23 | 20.8 | 0 | 2.8 | 2023-10-23 | 8.6 | 9.4 | 0 | 2022-10-23 | 19.4 | 0 | 1.4 | 2021-10-23 | 6.6 | 11.4 | 0 | 2020-10-23 | 22.7 | 0 | 4.7 | 2019-10-23 | 13.3 | 4.7 | 0 | 2018-10-23 | 8.5 | 9.5 | 0 | 2017-10-23 | 19.7 | 0 | 1.7 | 2016-10-23 | 8.4 | 9.6 | 0 | 5.39 | 1.06
2025-10-23 | 9.4 | 8.6 | 0 | 2024-10-23 | 20.2 | 0 | 2.2 | 2023-10-23 | 10.1 | 7.9 | 0 | 2022-10-23 | 20.7 | 0 | 2.7 | 2021-10-23 | 6.9 | 11.1 | 0 | 2020-10-23 | 22.9 | 0 | 4.9 | 2019-10-23 | 13.2 | 4.8 | 0 | 2018-10-23 | 9.1 | 8.9 | 0 | 2017-10-23 | 20.7 | 0 | 2.7 | 2016-10-23 | 10 | 8 | 0 | 4.93 | 1.25
2025-10-23 | 9.1 | 8.9 | 0 | 2024-10-23 | 20.4 | 0 | 2.4 | 2023-10-23 | 10 | 8 | 0 | 2022-10-23 | 21.1 | 0 | 3.1 | 2021-10-23 | 8.4 | 9.6 | 0 | 2020-10-23 | 23.9 | 0 | 5.9 | 2019-10-23 | 12.8 | 5.2 | 0 | 2018-10-23 | 9.3 | 8.7 | 0 | 2017-10-23 | 21 | 0 | 3 | 2016-10-23 | 11.1 | 6.9 | 0 | 4.73 | 1.44
2025-10-23 | 9.2 | 8.8 | 0 | 2024-10-23 | 20.3 | 0 | 2.3 | 2023-10-23 | 10.2 | 7.8 | 0 | 2022-10-23 | 20.9 | 0 | 2.9 | 2021-10-23 | 8.2 | 9.8 | 0 | 2020-10-23 | 24.4 | 0 | 6.4 | 2019-10-23 | 12.8 | 5.2 | 0 | 2018-10-23 | 9.4 | 8.6 | 0 | 2017-10-23 | 20.3 | 0 | 2.3 | 2016-10-23 | 10.9 | 7.1 | 0 | 4.73 | 1.39
2025-10-23 | 9.3 | 8.7 | 0 | 2024-10-23 | 19.2 | 0 | 1.2 | 2023-10-23 | 9.3 | 8.7 | 0 | 2022-10-23 | 18.7 | 0 | 0.7 | 2021-10-23 | 7.2 | 10.8 | 0 | 2020-10-23 | 23.4 | 0 | 5.4 | 2019-10-23 | 12.2 | 5.8 | 0 | 2018-10-23 | 8 | 10 | 0 | 2017-10-23 | 19.8 | 0 | 1.8 | 2016-10-23 | 10.2 | 7.8 | 0 | 5.18 | 0.91
2025-10-23 | 7.3 | 10.7 | 0 | 2024-10-23 | 18.2 | 0 | 0.2 | 2023-10-23 | 7.8 | 10.2 | 0 | 2022-10-23 | 16.7 | 1.3 | 0 | 2021-10-23 | 5.8 | 12.2 | 0 | 2020-10-23 | 22.3 | 0 | 4.3 | 2019-10-23 | 11.7 | 6.3 | 0 | 2018-10-23 | 6.6 | 11.4 | 0 | 2017-10-23 | 18.6 | 0 | 0.6 | 2016-10-23 | 8 | 10 | 0 | 6.21 | 0.51
2025-10-23 | 8 | 10 | 0 | 2024-10-23 | 17.3 | 0.7 | 0 | 2023-10-23 | 6.3 | 11.7 | 0 | 2022-10-23 | 14.7 | 3.3 | 0 | 2021-10-23 | 4.6 | 13.4 | 0 | 2020-10-23 | 21.2 | 0 | 3.2 | 2019-10-23 | 10.5 | 7.5 | 0 | 2018-10-23 | 4.8 | 13.2 | 0 | 2017-10-23 | 18.5 | 0 | 0.5 | 2016-10-23 | 7 | 11 | 0 | 7.08 | 0.37
2025-10-23 | 6.4 | 11.6 | 0 | 2024-10-23 | 17.1 | 0.9 | 0 | 2023-10-23 | 1.7 | 16.3 | 0 | 2022-10-23 | 13.2 | 4.8 | 0 | 2021-10-23 | 3.9 | 14.1 | 0 | 2020-10-23 | 20.8 | 0 | 2.8 | 2019-10-23 | 10 | 8 | 0 | 2018-10-23 | 4.2 | 13.8 | 0 | 2017-10-23 | 16.9 | 1.1 | 0 | 2016-10-23 | 7.5 | 10.5 | 0 | 8.11 | 0.28
2025-10-23 | 5.8 | 12.2 | 0 | 2024-10-23 | 14.6 | 3.4 | 0 | 2023-10-23 | 1.9 | 16.1 | 0 | 2022-10-23 | 12.5 | 5.5 | 0 | 2021-10-23 | 4.1 | 13.9 | 0 | 2020-10-23 | 19.6 | 0 | 1.6 | 2019-10-23 | 10.1 | 7.9 | 0 | 2018-10-23 | 5 | 13 | 0 | 2017-10-23 | 16.5 | 1.5 | 0 | 2016-10-23 | 7 | 11 | 0 | 8.45 | 0.16
2025-10-23 | 3.6 | 14.4 | 0 | 2024-10-23 | 11.3 | 6.7 | 0 | 2023-10-23 | 2.5 | 15.5 | 0 | 2022-10-23 | 10.7 | 7.3 | 0 | 2021-10-23 | 3.6 | 14.4 | 0 | 2020-10-23 | 20.8 | 0 | 2.8 | 2019-10-23 | 9.9 | 8.1 | 0 | 2018-10-23 | 5 | 13 | 0 | 2017-10-23 | 16.3 | 1.7 | 0 | 2016-10-23 | 7 | 11 | 0 | 9.21 | 0.28
2025-10-23 | 4.3 | 13.7 | 0 | 2024-10-23 | 9.6 | 8.4 | 0 | 2023-10-23 | 3.7 | 14.3 | 0 | 2022-10-23 | 9.5 | 8.5 | 0 | 2021-10-23 | 3.5 | 14.5 | 0 | 2020-10-23 | 20.8 | 0 | 2.8 | 2019-10-23 | 9.7 | 8.3 | 0 | 2018-10-23 | 5 | 13 | 0 | 2017-10-23 | 16.8 | 1.2 | 0 | 2016-10-23 | 6.6 | 11.4 | 0 | 9.33 | 0.28
2025-10-23 | 4.1 | 13.9 | 0 | 2024-10-23 | 8.2 | 9.8 | 0 | 2023-10-23 | 3.3 | 14.7 | 0 | 2022-10-23 | 7.5 | 10.5 | 0 | 2021-10-23 | 3.5 | 14.5 | 0 | 2020-10-23 | 19.1 | 0 | 1.1 | 2019-10-23 | 9 | 9 | 0 | 2018-10-23 | 4.8 | 13.2 | 0 | 2017-10-23 | 16.4 | 1.6 | 0 | 2016-10-23 | 6.6 | 11.4 | 0 | 9.86 | 0.11
2025-10-24 | 4 | 14 | 0 | 2024-10-24 | 6.9 | 11.1 | 0 | 2023-10-24 | 3.7 | 14.3 | 0 | 2022-10-24 | 8.2 | 9.8 | 0 | 2021-10-24 | 3.4 | 14.6 | 0 | 2020-10-24 | 19 | 0 | 1 | 2019-10-24 | 8.9 | 9.1 | 0 | 2018-10-24 | 1.9 | 16.1 | 0 | 2017-10-24 | 16.3 | 1.7 | 0 | 2016-10-24 | 5.6 | 12.4 | 0 | 10.31 | 0.1
2025-10-24 | 3.5 | 14.5 | 0 | 2024-10-24 | 6.6 | 11.4 | 0 | 2023-10-24 | 3.9 | 14.1 | 0 | 2022-10-24 | 6.8 | 11.2 | 0 | 2021-10-24 | 3.6 | 14.4 | 0 | 2020-10-24 | 18.4 | 0 | 0.4 | 2019-10-24 | 8.3 | 9.7 | 0 | 2018-10-24 | 2 | 16 | 0 | 2017-10-24 | 15.7 | 2.3 | 0 | 2016-10-24 | 4.3 | 13.7 | 0 | 10.73 | 0.04
2025-10-24 | 4.1 | 13.9 | 0 | 2024-10-24 | 5.8 | 12.2 | 0 | 2023-10-24 | 4.3 | 13.7 | 0 | 2022-10-24 | 7.3 | 10.7 | 0 | 2021-10-24 | 2.9 | 15.1 | 0 | 2020-10-24 | 18 | 0 | 0 | 2019-10-24 | 6.8 | 11.2 | 0 | 2018-10-24 | 2.5 | 15.5 | 0 | 2017-10-24 | 16 | 2 | 0 | 2016-10-24 | 4.2 | 13.8 | 0 | 10.81 | 0
2025-10-24 | 3 | 15 | 0 | 2024-10-24 | 5.7 | 12.3 | 0 | 2023-10-24 | 4.5 | 13.5 | 0 | 2022-10-24 | 6.5 | 11.5 | 0 | 2021-10-24 | 3.4 | 14.6 | 0 | 2020-10-24 | 13.9 | 4.1 | 0 | 2019-10-24 | 5.7 | 12.3 | 0 | 2018-10-24 | 3.2 | 14.8 | 0 | 2017-10-24 | 16.2 | 1.8 | 0 | 2016-10-24 | 3.1 | 14.9 | 0 | 11.48 | 0
2025-10-24 | 3.6 | 14.4 | 0 | 2024-10-24 | 4.6 | 13.4 | 0 | 2023-10-24 | 4.9 | 13.1 | 0 | 2022-10-24 | 6.2 | 11.8 | 0 | 2021-10-24 | 3.3 | 14.7 | 0 | 2020-10-24 | 7 | 11 | 0 | 2019-10-24 | 5.8 | 12.2 | 0 | 2018-10-24 | 3.4 | 14.6 | 0 | 2017-10-24 | 16.3 | 1.7 | 0 | 2016-10-24 | 1.4 | 16.6 | 0 | 12.35 | 0
2025-10-24 | 3.7 | 14.3 | 0 | 2024-10-24 | 3.9 | 14.1 | 0 | 2023-10-24 | 5.1 | 12.9 | 0 | 2022-10-24 | 6.7 | 11.3 | 0 | 2021-10-24 | 2.4 | 15.6 | 0 | 2020-10-24 | 5.6 | 12.4 | 0 | 2019-10-24 | 6.2 | 11.8 | 0 | 2018-10-24 | 3.6 | 14.4 | 0 | 2017-10-24 | 16.4 | 1.6 | 0 | 2016-10-24 | 1.7 | 16.3 | 0 | 12.47 | 0
2025-10-24 | 3.7 | 14.3 | 0 | 2024-10-24 | 3.9 | 14.1 | 0 | 2023-10-24 | 5.3 | 12.7 | 0 | 2022-10-24 | 5.9 | 12.1 | 0 | 2021-10-24 | 1.8 | 16.2 | 0 | 2020-10-24 | 4.8 | 13.2 | 0 | 2019-10-24 | 6.6 | 11.4 | 0 | 2018-10-24 | 3.9 | 14.1 | 0 | 2017-10-24 | 16.6 | 1.4 | 0 | 2016-10-24 | 1.3 | 16.7 | 0 | 12.62 | 0
2025-10-24 | 4.1 | 13.9 | 0 | 2024-10-24 | 3.8 | 14.2 | 0 | 2023-10-24 | 5.5 | 12.5 | 0 | 2022-10-24 | 6.1 | 11.9 | 0 | 2021-10-24 | 1.3 | 16.7 | 0 | 2020-10-24 | 4 | 14 | 0 | 2019-10-24 | 7.7 | 10.3 | 0 | 2018-10-24 | 3.7 | 14.3 | 0 | 2017-10-24 | 15.9 | 2.1 | 0 | 2016-10-24 | 2.2 | 15.8 | 0 | 12.57 | 0
2025-10-24 | 4.7 | 13.3 | 0 | 2024-10-24 | 4.3 | 13.7 | 0 | 2023-10-24 | 6.3 | 11.7 | 0 | 2022-10-24 | 10.1 | 7.9 | 0 | 2021-10-24 | 3.8 | 14.2 | 0 | 2020-10-24 | 4.5 | 13.5 | 0 | 2019-10-24 | 8.7 | 9.3 | 0 | 2018-10-24 | 4.6 | 13.4 | 0 | 2017-10-24 | 15.1 | 2.9 | 0 | 2016-10-24 | 4 | 14 | 0 | 11.39 | 0
2025-10-24 | 5.6 | 12.4 | 0 | 2024-10-24 | 4.9 | 13.1 | 0 | 2023-10-24 | 7.5 | 10.5 | 0 | 2022-10-24 | 11.3 | 6.7 | 0 | 2021-10-24 | 6.9 | 11.1 | 0 | 2020-10-24 | 4.9 | 13.1 | 0 | 2019-10-24 | 9.6 | 8.4 | 0 | 2018-10-24 | 5.4 | 12.6 | 0 | 2017-10-24 | 14.2 | 3.8 | 0 | 2016-10-24 | 4.6 | 13.4 | 0 | 10.51 | 0
2025-10-24 | 6.3 | 11.7 | 0 | 2024-10-24 | 6.1 | 11.9 | 0 | 2023-10-24 | 8.5 | 9.5 | 0 | 2022-10-24 | 14.8 | 3.2 | 0 | 2021-10-24 | 8.8 | 9.2 | 0 | 2020-10-24 | 6.1 | 11.9 | 0 | 2019-10-24 | 9.8 | 8.2 | 0 | 2018-10-24 | 7 | 11 | 0 | 2017-10-24 | 14.5 | 3.5 | 0 | 2016-10-24 | 5.2 | 12.8 | 0 | 9.29 | 0
2025-10-24 | 7 | 11 | 0 | 2024-10-24 | 7.2 | 10.8 | 0 | 2023-10-24 | 9.5 | 8.5 | 0 | 2022-10-24 | 17.3 | 0.7 | 0 | 2021-10-24 | 10.4 | 7.6 | 0 | 2020-10-24 | 6.2 | 11.8 | 0 | 2019-10-24 | 11.3 | 6.7 | 0 | 2018-10-24 | 7.8 | 10.2 | 0 | 2017-10-24 | 15.3 | 2.7 | 0 | 2016-10-24 | 5.7 | 12.3 | 0 | 8.23 | 0
2025-10-24 | 6.8 | 11.2 | 0 | 2024-10-24 | 9.1 | 8.9 | 0 | 2023-10-24 | 10.3 | 7.7 | 0 | 2022-10-24 | 18.8 | 0 | 0.8 | 2021-10-24 | 11.1 | 6.9 | 0 | 2020-10-24 | 6.7 | 11.3 | 0 | 2019-10-24 | 12.1 | 5.9 | 0 | 2018-10-24 | 7.7 | 10.3 | 0 | 2017-10-24 | 16.9 | 1.1 | 0 | 2016-10-24 | 6 | 12 | 0 | 7.53 | 0.08
2025-10-24 | 8.3 | 9.7 | 0 | 2024-10-24 | 8.9 | 9.1 | 0 | 2023-10-24 | 11.3 | 6.7 | 0 | 2022-10-24 | 20.2 | 0 | 2.2 | 2021-10-24 | 11.9 | 6.1 | 0 | 2020-10-24 | 7.1 | 10.9 | 0 | 2019-10-24 | 9.8 | 8.2 | 0 | 2018-10-24 | 8.5 | 9.5 | 0 | 2017-10-24 | 18.4 | 0 | 0.4 | 2016-10-24 | 6.7 | 11.3 | 0 | 7.15 | 0.26
2025-10-24 | 7.8 | 10.2 | 0 | 2024-10-24 | 9.8 | 8.2 | 0 | 2023-10-24 | 11.3 | 6.7 | 0 | 2022-10-24 | 20.9 | 0 | 2.9 | 2021-10-24 | 11.4 | 6.6 | 0 | 2020-10-24 | 6.6 | 11.4 | 0 | 2019-10-24 | 10.1 | 7.9 | 0 | 2018-10-24 | 7.3 | 10.7 | 0 | 2017-10-24 | 18.8 | 0 | 0.8 | 2016-10-24 | 6.8 | 11.2 | 0 | 7.29 | 0.37
2025-10-24 | 7.7 | 10.3 | 0 | 2024-10-24 | 9.2 | 8.8 | 0 | 2023-10-24 | 11.7 | 6.3 | 0 | 2022-10-24 | 21 | 0 | 3 | 2021-10-24 | 12 | 6 | 0 | 2020-10-24 | 6.3 | 11.7 | 0 | 2019-10-24 | 10.7 | 7.3 | 0 | 2018-10-24 | 6.2 | 11.8 | 0 | 2017-10-24 | 18.2 | 0 | 0.2 | 2016-10-24 | 7.3 | 10.7 | 0 | 7.29 | 0.32
2025-10-24 | 7.7 | 10.3 | 0 | 2024-10-24 | 8.4 | 9.6 | 0 | 2023-10-24 | 11.5 | 6.5 | 0 | 2022-10-24 | 20.2 | 0 | 2.2 | 2021-10-24 | 11.6 | 6.4 | 0 | 2020-10-24 | 6.1 | 11.9 | 0 | 2019-10-24 | 11.5 | 6.5 | 0 | 2018-10-24 | 5.3 | 12.7 | 0 | 2017-10-24 | 17.6 | 0.4 | 0 | 2016-10-24 | 6.4 | 11.6 | 0 | 7.59 | 0.22
2025-10-24 | 7.2 | 10.8 | 0 | 2024-10-24 | 6.2 | 11.8 | 0 | 2023-10-24 | 10.8 | 7.2 | 0 | 2022-10-24 | 17.4 | 0.6 | 0 | 2021-10-24 | 8.8 | 9.2 | 0 | 2020-10-24 | 5.1 | 12.9 | 0 | 2019-10-24 | 9.4 | 8.6 | 0 | 2018-10-24 | 4.5 | 13.5 | 0 | 2017-10-24 | 16.6 | 1.4 | 0 | 2016-10-24 | 5 | 13 | 0 | 8.9 | 0
2025-10-24 | 6.7 | 11.3 | 0 | 2024-10-24 | 4.5 | 13.5 | 0 | 2023-10-24 | 10 | 8 | 0 | 2022-10-24 | 15.5 | 2.5 | 0 | 2021-10-24 | 7.8 | 10.2 | 0 | 2020-10-24 | 4.7 | 13.3 | 0 | 2019-10-24 | 8.6 | 9.4 | 0 | 2018-10-24 | 4 | 14 | 0 | 2017-10-24 | 13.8 | 4.2 | 0 | 2016-10-24 | 3.5 | 14.5 | 0 | 10.09 | 0
2025-10-24 | 6.6 | 11.4 | 0 | 2024-10-24 | 4.7 | 13.3 | 0 | 2023-10-24 | 9.8 | 8.2 | 0 | 2022-10-24 | 14.8 | 3.2 | 0 | 2021-10-24 | 5.9 | 12.1 | 0 | 2020-10-24 | 4.3 | 13.7 | 0 | 2019-10-24 | 8.9 | 9.1 | 0 | 2018-10-24 | 4.1 | 13.9 | 0 | 2017-10-24 | 13.5 | 4.5 | 0 | 2016-10-24 | 1.8 | 16.2 | 0 | 10.56 | 0
2025-10-24 | 6.6 | 11.4 | 0 | 2024-10-24 | 3.8 | 14.2 | 0 | 2023-10-24 | 9.5 | 8.5 | 0 | 2022-10-24 | 13.8 | 4.2 | 0 | 2021-10-24 | 5.5 | 12.5 | 0 | 2020-10-24 | 3.7 | 14.3 | 0 | 2019-10-24 | 6.8 | 11.2 | 0 | 2018-10-24 | 3.8 | 14.2 | 0 | 2017-10-24 | 14.1 | 3.9 | 0 | 2016-10-24 | 1.9 | 16.1 | 0 | 11.05 | 0
2025-10-24 | 6 | 12 | 0 | 2024-10-24 | 2 | 16 | 0 | 2023-10-24 | 8.9 | 9.1 | 0 | 2022-10-24 | 13.4 | 4.6 | 0 | 2021-10-24 | 3.5 | 14.5 | 0 | 2020-10-24 | 3.1 | 14.9 | 0 | 2019-10-24 | 5.9 | 12.1 | 0 | 2018-10-24 | 3.3 | 14.7 | 0 | 2017-10-24 | 13 | 5 | 0 | 2016-10-24 | 2.9 | 15.1 | 0 | 11.8 | 0
2025-10-24 | 6.3 | 11.7 | 0 | 2024-10-24 | 1.6 | 16.4 | 0 | 2023-10-24 | 8.8 | 9.2 | 0 | 2022-10-24 | 13 | 5 | 0 | 2021-10-24 | 4.6 | 13.4 | 0 | 2020-10-24 | 2.9 | 15.1 | 0 | 2019-10-24 | 5.6 | 12.4 | 0 | 2018-10-24 | 2.6 | 15.4 | 0 | 2017-10-24 | 11.5 | 6.5 | 0 | 2016-10-24 | 1.1 | 16.9 | 0 | 12.2 | 0
2025-10-24 | 5.6 | 12.4 | 0 | 2024-10-24 | -0.8 | 18.8 | 0 | 2023-10-24 | 8.4 | 9.6 | 0 | 2022-10-24 | 12.2 | 5.8 | 0 | 2021-10-24 | 4.3 | 13.7 | 0 | 2020-10-24 | 2.6 | 15.4 | 0 | 2019-10-24 | 5.2 | 12.8 | 0 | 2018-10-24 | 1.9 | 16.1 | 0 | 2017-10-24 | 12.3 | 5.7 | 0 | 2016-10-24 | 0.3 | 17.7 | 0 | 12.8 | 0
2025-10-25 | 6 | 12 | 0 | 2024-10-25 | 0.3 | 17.7 | 0 | 2023-10-25 | 7.9 | 10.1 | 0 | 2022-10-25 | 11 | 7 | 0 | 2021-10-25 | 3 | 15 | 0 | 2020-10-25 | 1.9 | 16.1 | 0 | 2019-10-25 | 4.5 | 13.5 | 0 | 2018-10-25 | 1.3 | 16.7 | 0 | 2017-10-25 | 12.6 | 5.4 | 0 | 2016-10-25 | 1.6 | 16.4 | 0 | 12.99 | 0
2025-10-25 | 5.8 | 12.2 | 0 | 2024-10-25 | 1.2 | 16.8 | 0 | 2023-10-25 | 8.6 | 9.4 | 0 | 2022-10-25 | 10.5 | 7.5 | 0 | 2021-10-25 | 2.8 | 15.2 | 0 | 2020-10-25 | 1.3 | 16.7 | 0 | 2019-10-25 | 3.7 | 14.3 | 0 | 2018-10-25 | 1.1 | 16.9 | 0 | 2017-10-25 | 11.9 | 6.1 | 0 | 2016-10-25 | 1.1 | 16.9 | 0 | 13.2 | 0
2025-10-25 | 5.4 | 12.6 | 0 | 2024-10-25 | 0.3 | 17.7 | 0 | 2023-10-25 | 9.1 | 8.9 | 0 | 2022-10-25 | 10.8 | 7.2 | 0 | 2021-10-25 | 3.1 | 14.9 | 0 | 2020-10-25 | 1.2 | 16.8 | 0 | 2019-10-25 | 3.9 | 14.1 | 0 | 2018-10-25 | 0.6 | 17.4 | 0 | 2017-10-25 | 11.6 | 6.4 | 0 | 2016-10-25 | 0.9 | 17.1 | 0 | 13.31 | 0
2025-10-25 | 3.2 | 14.8 | 0 | 2024-10-25 | -1 | 19 | 0 | 2023-10-25 | 8.7 | 9.3 | 0 | 2022-10-25 | 10.6 | 7.4 | 0 | 2021-10-25 | 3.6 | 14.4 | 0 | 2020-10-25 | 0.9 | 17.1 | 0 | 2019-10-25 | 4.1 | 13.9 | 0 | 2018-10-25 | 0.5 | 17.5 | 0 | 2017-10-25 | 11.3 | 6.7 | 0 | 2016-10-25 | 0.3 | 17.7 | 0 | 13.78 | 0
2025-10-25 | 3.2 | 14.8 | 0 | 2024-10-25 | -1.9 | 19.9 | 0 | 2023-10-25 | 8.8 | 9.2 | 0 | 2022-10-25 | 10.3 | 7.7 | 0 | 2021-10-25 | 4.3 | 13.7 | 0 | 2020-10-25 | 0 | 18 | 0 | 2019-10-25 | 3.7 | 14.3 | 0 | 2018-10-25 | 0.2 | 17.8 | 0 | 2017-10-25 | 9.9 | 8.1 | 0 | 2016-10-25 | 0.9 | 17.1 | 0 | 14.06 | 0
2025-10-25 | 2.3 | 15.7 | 0 | 2024-10-25 | -1 | 19 | 0 | 2023-10-25 | 10.9 | 7.1 | 0 | 2022-10-25 | 9.6 | 8.4 | 0 | 2021-10-25 | 4.7 | 13.3 | 0 | 2020-10-25 | -0.3 | 18.3 | 0 | 2019-10-25 | 3.6 | 14.4 | 0 | 2018-10-25 | 0.1 | 17.9 | 0 | 2017-10-25 | 10.1 | 7.9 | 0 | 2016-10-25 | 0 | 18 | 0 | 14 | 0
2025-10-25 | 0.2 | 17.8 | 0 | 2024-10-25 | -2.6 | 20.6 | 0 | 2023-10-25 | 12.4 | 5.6 | 0 | 2022-10-25 | 11.3 | 6.7 | 0 | 2021-10-25 | 5.1 | 12.9 | 0 | 2020-10-25 | -1.2 | 19.2 | 0 | 2019-10-25 | 2.9 | 15.1 | 0 | 2018-10-25 | -0.1 | 18.1 | 0 | 2017-10-25 | 8.4 | 9.6 | 0 | 2016-10-25 | 0.2 | 17.8 | 0 | 14.34 | 0
2025-10-25 | 1.4 | 16.6 | 0 | 2024-10-25 | -0.1 | 18.1 | 0 | 2023-10-25 | 11.9 | 6.1 | 0 | 2022-10-25 | 11.6 | 6.4 | 0 | 2021-10-25 | 5.6 | 12.4 | 0 | 2020-10-25 | -0.9 | 18.9 | 0 | 2019-10-25 | 3.3 | 14.7 | 0 | 2018-10-25 | -0.2 | 18.2 | 0 | 2017-10-25 | 8.9 | 9.1 | 0 | 2016-10-25 | 1.3 | 16.7 | 0 | 13.72 | 0
2025-10-25 | 4.1 | 13.9 | 0 | 2024-10-25 | 2.8 | 15.2 | 0 | 2023-10-25 | 12.5 | 5.5 | 0 | 2022-10-25 | 12.6 | 5.4 | 0 | 2021-10-25 | 5.7 | 12.3 | 0 | 2020-10-25 | 0.7 | 17.3 | 0 | 2019-10-25 | 4.3 | 13.7 | 0 | 2018-10-25 | 0.1 | 17.9 | 0 | 2017-10-25 | 9.4 | 8.6 | 0 | 2016-10-25 | 1.8 | 16.2 | 0 | 12.6 | 0
2025-10-25 | 4.7 | 13.3 | 0 | 2024-10-25 | 5 | 13 | 0 | 2023-10-25 | 13.4 | 4.6 | 0 | 2022-10-25 | 13.9 | 4.1 | 0 | 2021-10-25 | 6.1 | 11.9 | 0 | 2020-10-25 | 2.1 | 15.9 | 0 | 2019-10-25 | 5.5 | 12.5 | 0 | 2018-10-25 | 0.5 | 17.5 | 0 | 2017-10-25 | 10.7 | 7.3 | 0 | 2016-10-25 | 2.8 | 15.2 | 0 | 11.53 | 0
2025-10-25 | 6.5 | 11.5 | 0 | 2024-10-25 | 7.3 | 10.7 | 0 | 2023-10-25 | 15.2 | 2.8 | 0 | 2022-10-25 | 15.3 | 2.7 | 0 | 2021-10-25 | 6 | 12 | 0 | 2020-10-25 | 3.1 | 14.9 | 0 | 2019-10-25 | 6.7 | 11.3 | 0 | 2018-10-25 | 0.5 | 17.5 | 0 | 2017-10-25 | 12.1 | 5.9 | 0 | 2016-10-25 | 3.5 | 14.5 | 0 | 10.38 | 0
2025-10-25 | 6.7 | 11.3 | 0 | 2024-10-25 | 9.2 | 8.8 | 0 | 2023-10-25 | 15.4 | 2.6 | 0 | 2022-10-25 | 17 | 1 | 0 | 2021-10-25 | 5.7 | 12.3 | 0 | 2020-10-25 | 4 | 14 | 0 | 2019-10-25 | 8.3 | 9.7 | 0 | 2018-10-25 | 0.8 | 17.2 | 0 | 2017-10-25 | 12.9 | 5.1 | 0 | 2016-10-25 | 4.2 | 13.8 | 0 | 9.58 | 0
2025-10-25 | 8.2 | 9.8 | 0 | 2024-10-25 | 9.3 | 8.7 | 0 | 2023-10-25 | 15.4 | 2.6 | 0 | 2022-10-25 | 18.1 | 0 | 0.1 | 2021-10-25 | 6.1 | 11.9 | 0 | 2020-10-25 | 4.1 | 13.9 | 0 | 2019-10-25 | 9 | 9 | 0 | 2018-10-25 | 1.8 | 16.2 | 0 | 2017-10-25 | 13.9 | 4.1 | 0 | 2016-10-25 | 5.4 | 12.6 | 0 | 8.88 | 0.01
2025-10-25 | 8.6 | 9.4 | 0 | 2024-10-25 | 9.5 | 8.5 | 0 | 2023-10-25 | 16 | 2 | 0 | 2022-10-25 | 19.8 | 0 | 1.8 | 2021-10-25 | 6.5 | 11.5 | 0 | 2020-10-25 | 4.2 | 13.8 | 0 | 2019-10-25 | 9.2 | 8.8 | 0 | 2018-10-25 | 2.5 | 15.5 | 0 | 2017-10-25 | 13.5 | 4.5 | 0 | 2016-10-25 | 5.5 | 12.5 | 0 | 8.65 | 0.18
2025-10-25 | 8.9 | 9.1 | 0 | 2024-10-25 | 9.5 | 8.5 | 0 | 2023-10-25 | 17.4 | 0.6 | 0 | 2022-10-25 | 19.6 | 0 | 1.6 | 2021-10-25 | 6.8 | 11.2 | 0 | 2020-10-25 | 5.2 | 12.8 | 0 | 2019-10-25 | 9.2 | 8.8 | 0 | 2018-10-25 | 3.6 | 14.4 | 0 | 2017-10-25 | 13.2 | 4.8 | 0 | 2016-10-25 | 5.6 | 12.4 | 0 | 8.26 | 0.16
2025-10-25 | 9 | 9 | 0 | 2024-10-25 | 9.8 | 8.2 | 0 | 2023-10-25 | 17.4 | 0.6 | 0 | 2022-10-25 | 20.1 | 0 | 2.1 | 2021-10-25 | 6.8 | 11.2 | 0 | 2020-10-25 | 4.9 | 13.1 | 0 | 2019-10-25 | 9 | 9 | 0 | 2018-10-25 | 3.5 | 14.5 | 0 | 2017-10-25 | 13 | 5 | 0 | 2016-10-25 | 5.2 | 12.8 | 0 | 8.34 | 0.21
2025-10-25 | 8 | 10 | 0 | 2024-10-25 | 9.4 | 8.6 | 0 | 2023-10-25 | 17.4 | 0.6 | 0 | 2022-10-25 | 19.8 | 0 | 1.8 | 2021-10-25 | 6.6 | 11.4 | 0 | 2020-10-25 | 4.4 | 13.6 | 0 | 2019-10-25 | 8.2 | 9.8 | 0 | 2018-10-25 | 2.7 | 15.3 | 0 | 2017-10-25 | 13.3 | 4.7 | 0 | 2016-10-25 | 5 | 13 | 0 | 8.7 | 0.18
2025-10-25 | 7.2 | 10.8 | 0 | 2024-10-25 | 9.1 | 8.9 | 0 | 2023-10-25 | 17.1 | 0.9 | 0 | 2022-10-25 | 17.4 | 0.6 | 0 | 2021-10-25 | 5.9 | 12.1 | 0 | 2020-10-25 | 2.7 | 15.3 | 0 | 2019-10-25 | 6.9 | 11.1 | 0 | 2018-10-25 | 1.7 | 16.3 | 0 | 2017-10-25 | 11.8 | 6.2 | 0 | 2016-10-25 | 4.5 | 13.5 | 0 | 9.57 | 0
2025-10-25 | 5.4 | 12.6 | 0 | 2024-10-25 | 8.7 | 9.3 | 0 | 2023-10-25 | 16.8 | 1.2 | 0 | 2022-10-25 | 16.6 | 1.4 | 0 | 2021-10-25 | 5.8 | 12.2 | 0 | 2020-10-25 | 1.8 | 16.2 | 0 | 2019-10-25 | 6 | 12 | 0 | 2018-10-25 | 1.9 | 16.1 | 0 | 2017-10-25 | 9.9 | 8.1 | 0 | 2016-10-25 | 2.7 | 15.3 | 0 | 10.44 | 0
2025-10-25 | 3.8 | 14.2 | 0 | 2024-10-25 | 8.1 | 9.9 | 0 | 2023-10-25 | 16.6 | 1.4 | 0 | 2022-10-25 | 16.4 | 1.6 | 0 | 2021-10-25 | 4.9 | 13.1 | 0 | 2020-10-25 | 0.2 | 17.8 | 0 | 2019-10-25 | 5.7 | 12.3 | 0 | 2018-10-25 | 1.8 | 16.2 | 0 | 2017-10-25 | 9.1 | 8.9 | 0 | 2016-10-25 | 3.4 | 14.6 | 0 | 11 | 0
2025-10-25 | 3.7 | 14.3 | 0 | 2024-10-25 | 8.2 | 9.8 | 0 | 2023-10-25 | 16.5 | 1.5 | 0 | 2022-10-25 | 15 | 3 | 0 | 2021-10-25 | 5.1 | 12.9 | 0 | 2020-10-25 | 1.7 | 16.3 | 0 | 2019-10-25 | 4.5 | 13.5 | 0 | 2018-10-25 | 1.8 | 16.2 | 0 | 2017-10-25 | 7.7 | 10.3 | 0 | 2016-10-25 | 1.8 | 16.2 | 0 | 11.4 | 0
2025-10-25 | 3.1 | 14.9 | 0 | 2024-10-25 | 8.6 | 9.4 | 0 | 2023-10-25 | 16.4 | 1.6 | 0 | 2022-10-25 | 16.1 | 1.9 | 0 | 2021-10-25 | 5 | 13 | 0 | 2020-10-25 | 1.9 | 16.1 | 0 | 2019-10-25 | 3.9 | 14.1 | 0 | 2018-10-25 | 1.6 | 16.4 | 0 | 2017-10-25 | 6.9 | 11.1 | 0 | 2016-10-25 | -0.1 | 18.1 | 0 | 11.66 | 0
2025-10-25 | 1.3 | 16.7 | 0 | 2024-10-25 | 9 | 9 | 0 | 2023-10-25 | 16.2 | 1.8 | 0 | 2022-10-25 | 16.4 | 1.6 | 0 | 2021-10-25 | 5.3 | 12.7 | 0 | 2020-10-25 | 1.7 | 16.3 | 0 | 2019-10-25 | 4.3 | 13.7 | 0 | 2018-10-25 | 1.4 | 16.6 | 0 | 2017-10-25 | 5.3 | 12.7 | 0 | 2016-10-25 | 0.2 | 17.8 | 0 | 11.89 | 0
2025-10-25 | 0.1 | 17.9 | 0 | 2024-10-25 | 8.8 | 9.2 | 0 | 2023-10-25 | 15.9 | 2.1 | 0 | 2022-10-25 | 17 | 1 | 0 | 2021-10-25 | 5.4 | 12.6 | 0 | 2020-10-25 | 1.6 | 16.4 | 0 | 2019-10-25 | 4.7 | 13.3 | 0 | 2018-10-25 | 1.2 | 16.8 | 0 | 2017-10-25 | 5.4 | 12.6 | 0 | 2016-10-25 | -0.1 | 18.1 | 0 | 12 | 0
2025-10-26 | -0.1 | 18.1 | 0 | 2024-10-26 | 8.4 | 9.6 | 0 | 2023-10-26 | 16.5 | 1.5 | 0 | 2022-10-26 | 17.4 | 0.6 | 0 | 2021-10-26 | 5.2 | 12.8 | 0 | 2020-10-26 | 2.3 | 15.7 | 0 | 2019-10-26 | 4.6 | 13.4 | 0 | 2018-10-26 | -0.2 | 18.2 | 0 | 2017-10-26 | 5.7 | 12.3 | 0 | 2016-10-26 | -0.8 | 18.8 | 0 | 12.1 | 0
2025-10-26 | 0.3 | 17.7 | 0 | 2024-10-26 | 8.5 | 9.5 | 0 | 2023-10-26 | 16.5 | 1.5 | 0 | 2022-10-26 | 16.9 | 1.1 | 0 | 2021-10-26 | 5.2 | 12.8 | 0 | 2020-10-26 | 2.4 | 15.6 | 0 | 2019-10-26 | 5.6 | 12.4 | 0 | 2018-10-26 | -2.3 | 20.3 | 0 | 2017-10-26 | 5.6 | 12.4 | 0 | 2016-10-26 | -1.5 | 19.5 | 0 | 12.28 | 0
2025-10-26 | -0.4 | 18.4 | 0 | 2024-10-26 | 8 | 10 | 0 | 2023-10-26 | 16.1 | 1.9 | 0 | 2022-10-26 | 14.4 | 3.6 | 0 | 2021-10-26 | 5.3 | 12.7 | 0 | 2020-10-26 | 2 | 16 | 0 | 2019-10-26 | 5.7 | 12.3 | 0 | 2018-10-26 | -2.2 | 20.2 | 0 | 2017-10-26 | 5 | 13 | 0 | 2016-10-26 | -1.9 | 19.9 | 0 | 12.8 | 0
2025-10-26 | -0.2 | 18.2 | 0 | 2024-10-26 | 9.2 | 8.8 | 0 | 2023-10-26 | 15.3 | 2.7 | 0 | 2022-10-26 | 15.3 | 2.7 | 0 | 2021-10-26 | 5.5 | 12.5 | 0 | 2020-10-26 | 2.2 | 15.8 | 0 | 2019-10-26 | 3.1 | 14.9 | 0 | 2018-10-26 | -2.2 | 20.2 | 0 | 2017-10-26 | 5.1 | 12.9 | 0 | 2016-10-26 | -2.1 | 20.1 | 0 | 12.88 | 0
2025-10-26 | 0.4 | 17.6 | 0 | 2024-10-26 | 8 | 10 | 0 | 2023-10-26 | 14.7 | 3.3 | 0 | 2022-10-26 | 13.3 | 4.7 | 0 | 2021-10-26 | 5.8 | 12.2 | 0 | 2020-10-26 | 2.1 | 15.9 | 0 | 2019-10-26 | 2.6 | 15.4 | 0 | 2018-10-26 | -1.7 | 19.7 | 0 | 2017-10-26 | 5 | 13 | 0 | 2016-10-26 | -2.8 | 20.8 | 0 | 13.26 | 0
2025-10-26 | 0.6 | 17.4 | 0 | 2024-10-26 | 6.5 | 11.5 | 0 | 2023-10-26 | 15 | 3 | 0 | 2022-10-26 | 14.3 | 3.7 | 0 | 2021-10-26 | 6 | 12 | 0 | 2020-10-26 | 2 | 16 | 0 | 2019-10-26 | 1.2 | 16.8 | 0 | 2018-10-26 | -3.5 | 21.5 | 0 | 2017-10-26 | 3.5 | 14.5 | 0 | 2016-10-26 | -1.8 | 19.8 | 0 | 13.62 | 0
2025-10-26 | 1.8 | 16.2 | 0 | 2024-10-26 | 5 | 13 | 0 | 2023-10-26 | 15 | 3 | 0 | 2022-10-26 | 14.2 | 3.8 | 0 | 2021-10-26 | 6.1 | 11.9 | 0 | 2020-10-26 | 1.4 | 16.6 | 0 | 2019-10-26 | 1.8 | 16.2 | 0 | 2018-10-26 | -4.5 | 22.5 | 0 | 2017-10-26 | 2.8 | 15.2 | 0 | 2016-10-26 | -1.2 | 19.2 | 0 | 13.76 | 0
2025-10-26 | 0.9 | 17.1 | 0 | 2024-10-26 | 4.4 | 13.6 | 0 | 2023-10-26 | 15.2 | 2.8 | 0 | 2022-10-26 | 14.3 | 3.7 | 0 | 2021-10-26 | 6.3 | 11.7 | 0 | 2020-10-26 | 0.5 | 17.5 | 0 | 2019-10-26 | 1.1 | 16.9 | 0 | 2018-10-26 | -3.4 | 21.4 | 0 | 2017-10-26 | 2.7 | 15.3 | 0 | 2016-10-26 | -0.4 | 18.4 | 0 | 13.84 | 0
2025-10-26 | 2.8 | 15.2 | 0 | 2024-10-26 | 5.1 | 12.9 | 0 | 2023-10-26 | 15.2 | 2.8 | 0 | 2022-10-26 | 16.9 | 1.1 | 0 | 2021-10-26 | 6.7 | 11.3 | 0 | 2020-10-26 | 0.4 | 17.6 | 0 | 2019-10-26 | 3.6 | 14.4 | 0 | 2018-10-26 | -1.7 | 19.7 | 0 | 2017-10-26 | 5.4 | 12.6 | 0 | 2016-10-26 | -0.1 | 18.1 | 0 | 12.57 | 0
2025-10-26 | 3.4 | 14.6 | 0 | 2024-10-26 | 5.2 | 12.8 | 0 | 2023-10-26 | 15.4 | 2.6 | 0 | 2022-10-26 | 20 | 0 | 2 | 2021-10-26 | 7 | 11 | 0 | 2020-10-26 | 0.4 | 17.6 | 0 | 2019-10-26 | 6.1 | 11.9 | 0 | 2018-10-26 | 1.1 | 16.9 | 0 | 2017-10-26 | 6.4 | 11.6 | 0 | 2016-10-26 | 0.5 | 17.5 | 0 | 11.65 | 0.2
2025-10-26 | 4.3 | 13.7 | 0 | 2024-10-26 | 6 | 12 | 0 | 2023-10-26 | 16.2 | 1.8 | 0 | 2022-10-26 | 20.1 | 0 | 2.1 | 2021-10-26 | 7.3 | 10.7 | 0 | 2020-10-26 | 0.8 | 17.2 | 0 | 2019-10-26 | 7.7 | 10.3 | 0 | 2018-10-26 | 2.2 | 15.8 | 0 | 2017-10-26 | 7.3 | 10.7 | 0 | 2016-10-26 | 1.3 | 16.7 | 0 | 10.89 | 0.21
2025-10-26 | 5.5 | 12.5 | 0 | 2024-10-26 | 6.8 | 11.2 | 0 | 2023-10-26 | 16.2 | 1.8 | 0 | 2022-10-26 | 21.5 | 0 | 3.5 | 2021-10-26 | 7.4 | 10.6 | 0 | 2020-10-26 | 0.9 | 17.1 | 0 | 2019-10-26 | 8.8 | 9.2 | 0 | 2018-10-26 | 3.3 | 14.7 | 0 | 2017-10-26 | 8.9 | 9.1 | 0 | 2016-10-26 | 2.1 | 15.9 | 0 | 10.21 | 0.35
2025-10-26 | 6 | 12 | 0 | 2024-10-26 | 8.6 | 9.4 | 0 | 2023-10-26 | 16.5 | 1.5 | 0 | 2022-10-26 | 23.4 | 0 | 5.4 | 2021-10-26 | 7.6 | 10.4 | 0 | 2020-10-26 | 1.5 | 16.5 | 0 | 2019-10-26 | 9.6 | 8.4 | 0 | 2018-10-26 | 4.1 | 13.9 | 0 | 2017-10-26 | 9.9 | 8.1 | 0 | 2016-10-26 | 2.6 | 15.4 | 0 | 9.56 | 0.54
2025-10-26 | 7.1 | 10.9 | 0 | 2024-10-26 | 9.7 | 8.3 | 0 | 2023-10-26 | 16.4 | 1.6 | 0 | 2022-10-26 | 23.2 | 0 | 5.2 | 2021-10-26 | 7.9 | 10.1 | 0 | 2020-10-26 | 2.1 | 15.9 | 0 | 2019-10-26 | 10.8 | 7.2 | 0 | 2018-10-26 | 4.6 | 13.4 | 0 | 2017-10-26 | 10.5 | 7.5 | 0 | 2016-10-26 | 2.3 | 15.7 | 0 | 9.06 | 0.52
2025-10-26 | 6.5 | 11.5 | 0 | 2024-10-26 | 10.3 | 7.7 | 0 | 2023-10-26 | 16.5 | 1.5 | 0 | 2022-10-26 | 22.6 | 0 | 4.6 | 2021-10-26 | 8.1 | 9.9 | 0 | 2020-10-26 | 2.3 | 15.7 | 0 | 2019-10-26 | 11 | 7 | 0 | 2018-10-26 | 4.2 | 13.8 | 0 | 2017-10-26 | 11.7 | 6.3 | 0 | 2016-10-26 | 2.2 | 15.8 | 0 | 8.92 | 0.46
2025-10-26 | 7 | 11 | 0 | 2024-10-26 | 6.1 | 11.9 | 0 | 2023-10-26 | 16.4 | 1.6 | 0 | 2022-10-26 | 22.8 | 0 | 4.8 | 2021-10-26 | 8.6 | 9.4 | 0 | 2020-10-26 | 2.6 | 15.4 | 0 | 2019-10-26 | 11.5 | 6.5 | 0 | 2018-10-26 | 3.9 | 14.1 | 0 | 2017-10-26 | 10.4 | 7.6 | 0 | 2016-10-26 | 2.4 | 15.6 | 0 | 9.31 | 0.48
2025-10-26 | 7.1 | 10.9 | 0 | 2024-10-26 | 6.1 | 11.9 | 0 | 2023-10-26 | 16 | 2 | 0 | 2022-10-26 | 20 | 0 | 2 | 2021-10-26 | 9.1 | 8.9 | 0 | 2020-10-26 | 2.7 | 15.3 | 0 | 2019-10-26 | 10.9 | 7.1 | 0 | 2018-10-26 | 3.6 | 14.4 | 0 | 2017-10-26 | 9.6 | 8.4 | 0 | 2016-10-26 | 1.9 | 16.1 | 0 | 9.5 | 0.2
2025-10-26 | 5.6 | 12.4 | 0 | 2024-10-26 | 5.2 | 12.8 | 0 | 2023-10-26 | 15.2 | 2.8 | 0 | 2022-10-26 | 18.2 | 0 | 0.2 | 2021-10-26 | 9.3 | 8.7 | 0 | 2020-10-26 | 2.4 | 15.6 | 0 | 2019-10-26 | 8.3 | 9.7 | 0 | 2018-10-26 | 2.5 | 15.5 | 0 | 2017-10-26 | 8.4 | 9.6 | 0 | 2016-10-26 | 1.5 | 16.5 | 0 | 10.36 | 0.02
2025-10-26 | 4.3 | 13.7 | 0 | 2024-10-26 | 4.6 | 13.4 | 0 | 2023-10-26 | 14.7 | 3.3 | 0 | 2022-10-26 | 17.2 | 0.8 | 0 | 2021-10-26 | 9.5 | 8.5 | 0 | 2020-10-26 | 2.8 | 15.2 | 0 | 2019-10-26 | 7.1 | 10.9 | 0 | 2018-10-26 | 1.3 | 16.7 | 0 | 2017-10-26 | 8.1 | 9.9 | 0 | 2016-10-26 | 1.6 | 16.4 | 0 | 10.88 | 0
2025-10-26 | 4.1 | 13.9 | 0 | 2024-10-26 | 4.4 | 13.6 | 0 | 2023-10-26 | 14.8 | 3.2 | 0 | 2022-10-26 | 17.1 | 0.9 | 0 | 2021-10-26 | 9.7 | 8.3 | 0 | 2020-10-26 | 2.8 | 15.2 | 0 | 2019-10-26 | 5.8 | 12.2 | 0 | 2018-10-26 | 0.3 | 17.7 | 0 | 2017-10-26 | 7.4 | 10.6 | 0 | 2016-10-26 | 1.6 | 16.4 | 0 | 11.2 | 0
2025-10-26 | 2.6 | 15.4 | 0 | 2024-10-26 | 3.9 | 14.1 | 0 | 2023-10-26 | 15 | 3 | 0 | 2022-10-26 | 16.2 | 1.8 | 0 | 2021-10-26 | 9.6 | 8.4 | 0 | 2020-10-26 | 2.4 | 15.6 | 0 | 2019-10-26 | 5.7 | 12.3 | 0 | 2018-10-26 | -1.4 | 19.4 | 0 | 2017-10-26 | 6.6 | 11.4 | 0 | 2016-10-26 | 0.9 | 17.1 | 0 | 11.85 | 0
2025-10-26 | 2.3 | 15.7 | 0 | 2024-10-26 | 3 | 15 | 0 | 2023-10-26 | 14.9 | 3.1 | 0 | 2022-10-26 | 15.9 | 2.1 | 0 | 2021-10-26 | 9.4 | 8.6 | 0 | 2020-10-26 | 2 | 16 | 0 | 2019-10-26 | 5.9 | 12.1 | 0 | 2018-10-26 | -1.1 | 19.1 | 0 | 2017-10-26 | 7.2 | 10.8 | 0 | 2016-10-26 | -0.6 | 18.6 | 0 | 12.11 | 0
2025-10-26 | 0.8 | 17.2 | 0 | 2024-10-26 | 2.7 | 15.3 | 0 | 2023-10-26 | 15.1 | 2.9 | 0 | 2022-10-26 | 15.2 | 2.8 | 0 | 2021-10-26 | 8.9 | 9.1 | 0 | 2020-10-26 | 2 | 16 | 0 | 2019-10-26 | 5.5 | 12.5 | 0 | 2018-10-26 | -1.3 | 19.3 | 0 | 2017-10-26 | 7.3 | 10.7 | 0 | 2016-10-26 | -0.1 | 18.1 | 0 | 12.39 | 0
2025-10-26 | 0.8 | 17.2 | 0 | 2024-10-26 | 0 | 18 | 0 | 2023-10-26 | 15 | 3 | 0 | 2022-10-26 | 14.4 | 3.6 | 0 | 2021-10-26 | 8.2 | 9.8 | 0 | 2020-10-26 | 2 | 16 | 0 | 2019-10-26 | 5.3 | 12.7 | 0 | 2018-10-26 | -1.2 | 19.2 | 0 | 2017-10-26 | 6.1 | 11.9 | 0 | 2016-10-26 | -0.8 | 18.8 | 0 | 13.02 | 0
2025-10-27 | -0.1 | 18.1 | 0 | 2024-10-27 | -1.2 | 19.2 | 0 | 2023-10-27 | 14.5 | 3.5 | 0 | 2022-10-27 | 13 | 5 | 0 | 2021-10-27 | 7.7 | 10.3 | 0 | 2020-10-27 | 1.7 | 16.3 | 0 | 2019-10-27 | 5.7 | 12.3 | 0 | 2018-10-27 | -1.4 | 19.4 | 0 | 2017-10-27 | 5 | 13 | 0 | 2016-10-27 | -1.8 | 19.8 | 0 | 13.69 | 0
2025-10-27 | 0.6 | 17.4 | 0 | 2024-10-27 | -1.4 | 19.4 | 0 | 2023-10-27 | 14.9 | 3.1 | 0 | 2022-10-27 | 8.8 | 9.2 | 0 | 2021-10-27 | 7.5 | 10.5 | 0 | 2020-10-27 | 1.7 | 16.3 | 0 | 2019-10-27 | 5.7 | 12.3 | 0 | 2018-10-27 | -1.1 | 19.1 | 0 | 2017-10-27 | 4.6 | 13.4 | 0 | 2016-10-27 | -2.3 | 20.3 | 0 | 14.1 | 0
2025-10-27 | -0.3 | 18.3 | 0 | 2024-10-27 | -1.3 | 19.3 | 0 | 2023-10-27 | 15.3 | 2.7 | 0 | 2022-10-27 | 8.2 | 9.8 | 0 | 2021-10-27 | 7.4 | 10.6 | 0 | 2020-10-27 | 1.6 | 16.4 | 0 | 2019-10-27 | 6 | 12 | 0 | 2018-10-27 | -0.7 | 18.7 | 0 | 2017-10-27 | 4 | 14 | 0 | 2016-10-27 | -2.6 | 20.6 | 0 | 14.24 | 0
2025-10-27 | -1.2 | 19.2 | 0 | 2024-10-27 | -0.8 | 18.8 | 0 | 2023-10-27 | 15.7 | 2.3 | 0 | 2022-10-27 | 6.8 | 11.2 | 0 | 2021-10-27 | 7.2 | 10.8 | 0 | 2020-10-27 | 0.9 | 17.1 | 0 | 2019-10-27 | 5.6 | 12.4 | 0 | 2018-10-27 | -1.2 | 19.2 | 0 | 2017-10-27 | 3.9 | 14.1 | 0 | 2016-10-27 | -2 | 20 | 0 | 14.51 | 0
2025-10-27 | 0.4 | 17.6 | 0 | 2024-10-27 | -2.1 | 20.1 | 0 | 2023-10-27 | 15.8 | 2.2 | 0 | 2022-10-27 | 5.8 | 12.2 | 0 | 2021-10-27 | 6.6 | 11.4 | 0 | 2020-10-27 | -0.2 | 18.2 | 0 | 2019-10-27 | 4.8 | 13.2 | 0 | 2018-10-27 | -0.9 | 18.9 | 0 | 2017-10-27 | 3.8 | 14.2 | 0 | 2016-10-27 | -1.9 | 19.9 | 0 | 14.79 | 0
2025-10-27 | -1.2 | 19.2 | 0 | 2024-10-27 | -1.9 | 19.9 | 0 | 2023-10-27 | 15.4 | 2.6 | 0 | 2022-10-27 | 5.5 | 12.5 | 0 | 2021-10-27 | 6 | 12 | 0 | 2020-10-27 | -0.8 | 18.8 | 0 | 2019-10-27 | 4.7 | 13.3 | 0 | 2018-10-27 | -0.8 | 18.8 | 0 | 2017-10-27 | 3.2 | 14.8 | 0 | 2016-10-27 | -1.9 | 19.9 | 0 | 15.18 | 0
2025-10-27 | 0.2 | 17.8 | 0 | 2024-10-27 | -2.1 | 20.1 | 0 | 2023-10-27 | 15.1 | 2.9 | 0 | 2022-10-27 | 5.2 | 12.8 | 0 | 2021-10-27 | 5.7 | 12.3 | 0 | 2020-10-27 | -1.4 | 19.4 | 0 | 2019-10-27 | 4.7 | 13.3 | 0 | 2018-10-27 | -0.5 | 18.5 | 0 | 2017-10-27 | 4.3 | 13.7 | 0 | 2016-10-27 | -1.2 | 19.2 | 0 | 15 | 0
2025-10-27 | -0.8 | 18.8 | 0 | 2024-10-27 | -1.4 | 19.4 | 0 | 2023-10-27 | 15 | 3 | 0 | 2022-10-27 | 4.5 | 13.5 | 0 | 2021-10-27 | 5.5 | 12.5 | 0 | 2020-10-27 | -2.1 | 20.1 | 0 | 2019-10-27 | 5 | 13 | 0 | 2018-10-27 | -0.7 | 18.7 | 0 | 2017-10-27 | 5.3 | 12.7 | 0 | 2016-10-27 | -0.8 | 18.8 | 0 | 15.05 | 0
2025-10-27 | 2.3 | 15.7 | 0 | 2024-10-27 | 1.1 | 16.9 | 0 | 2023-10-27 | 15.2 | 2.8 | 0 | 2022-10-27 | 4.7 | 13.3 | 0 | 2021-10-27 | 6.9 | 11.1 | 0 | 2020-10-27 | -1.1 | 19.1 | 0 | 2019-10-27 | 4.8 | 13.2 | 0 | 2018-10-27 | -0.1 | 18.1 | 0 | 2017-10-27 | 5.6 | 12.4 | 0 | 2016-10-27 | -0.4 | 18.4 | 0 | 14.1 | 0
2025-10-27 | 4.5 | 13.5 | 0 | 2024-10-27 | 2.7 | 15.3 | 0 | 2023-10-27 | 16 | 2 | 0 | 2022-10-27 | 5.4 | 12.6 | 0 | 2021-10-27 | 7.8 | 10.2 | 0 | 2020-10-27 | -0.3 | 18.3 | 0 | 2019-10-27 | 5 | 13 | 0 | 2018-10-27 | 1.5 | 16.5 | 0 | 2017-10-27 | 6.1 | 11.9 | 0 | 2016-10-27 | 0.6 | 17.4 | 0 | 13.07 | 0
2025-10-27 | 6 | 12 | 0 | 2024-10-27 | 4.1 | 13.9 | 0 | 2023-10-27 | 17.1 | 0.9 | 0 | 2022-10-27 | 5.8 | 12.2 | 0 | 2021-10-27 | 9.3 | 8.7 | 0 | 2020-10-27 | 0 | 18 | 0 | 2019-10-27 | 6.4 | 11.6 | 0 | 2018-10-27 | 2.5 | 15.5 | 0 | 2017-10-27 | 6.2 | 11.8 | 0 | 2016-10-27 | 1.4 | 16.6 | 0 | 12.12 | 0
2025-10-27 | 7.6 | 10.4 | 0 | 2024-10-27 | 5.4 | 12.6 | 0 | 2023-10-27 | 17.5 | 0.5 | 0 | 2022-10-27 | 6.6 | 11.4 | 0 | 2021-10-27 | 10.9 | 7.1 | 0 | 2020-10-27 | 1.5 | 16.5 | 0 | 2019-10-27 | 7 | 11 | 0 | 2018-10-27 | 3.5 | 14.5 | 0 | 2017-10-27 | 7.3 | 10.7 | 0 | 2016-10-27 | 1.4 | 16.6 | 0 | 11.13 | 0
2025-10-27 | 9 | 9 | 0 | 2024-10-27 | 5.5 | 12.5 | 0 | 2023-10-27 | 16.9 | 1.1 | 0 | 2022-10-27 | 7.3 | 10.7 | 0 | 2021-10-27 | 11.6 | 6.4 | 0 | 2020-10-27 | 1.7 | 16.3 | 0 | 2019-10-27 | 7.2 | 10.8 | 0 | 2018-10-27 | 4 | 14 | 0 | 2017-10-27 | 8.8 | 9.2 | 0 | 2016-10-27 | 1.8 | 16.2 | 0 | 10.62 | 0
2025-10-27 | 9.9 | 8.1 | 0 | 2024-10-27 | 5.5 | 12.5 | 0 | 2023-10-27 | 17.8 | 0.2 | 0 | 2022-10-27 | 7.8 | 10.2 | 0 | 2021-10-27 | 12.4 | 5.6 | 0 | 2020-10-27 | 2 | 16 | 0 | 2019-10-27 | 7.3 | 10.7 | 0 | 2018-10-27 | 4.5 | 13.5 | 0 | 2017-10-27 | 9.3 | 8.7 | 0 | 2016-10-27 | 2.1 | 15.9 | 0 | 10.14 | 0
2025-10-27 | 10.1 | 7.9 | 0 | 2024-10-27 | 5.9 | 12.1 | 0 | 2023-10-27 | 18.9 | 0 | 0.9 | 2022-10-27 | 7.9 | 10.1 | 0 | 2021-10-27 | 13.3 | 4.7 | 0 | 2020-10-27 | 2.6 | 15.4 | 0 | 2019-10-27 | 7.7 | 10.3 | 0 | 2018-10-27 | 4.5 | 13.5 | 0 | 2017-10-27 | 10.8 | 7.2 | 0 | 2016-10-27 | 2.6 | 15.4 | 0 | 9.66 | 0.09
2025-10-27 | 10.9 | 7.1 | 0 | 2024-10-27 | 5.7 | 12.3 | 0 | 2023-10-27 | 20.2 | 0 | 2.2 | 2022-10-27 | 8 | 10 | 0 | 2021-10-27 | 13.8 | 4.2 | 0 | 2020-10-27 | 2 | 16 | 0 | 2019-10-27 | 8 | 10 | 0 | 2018-10-27 | 4.5 | 13.5 | 0 | 2017-10-27 | 10.7 | 7.3 | 0 | 2016-10-27 | 1.8 | 16.2 | 0 | 9.66 | 0.22
2025-10-27 | 10.5 | 7.5 | 0 | 2024-10-27 | 5 | 13 | 0 | 2023-10-27 | 20.2 | 0 | 2.2 | 2022-10-27 | 7.5 | 10.5 | 0 | 2021-10-27 | 12.2 | 5.8 | 0 | 2020-10-27 | 1.5 | 16.5 | 0 | 2019-10-27 | 8.2 | 9.8 | 0 | 2018-10-27 | 3.6 | 14.4 | 0 | 2017-10-27 | 9.9 | 8.1 | 0 | 2016-10-27 | 0.7 | 17.3 | 0 | 10.29 | 0.22
2025-10-27 | 8.6 | 9.4 | 0 | 2024-10-27 | 4.6 | 13.4 | 0 | 2023-10-27 | 19.5 | 0 | 1.5 | 2022-10-27 | 5.1 | 12.9 | 0 | 2021-10-27 | 9.8 | 8.2 | 0 | 2020-10-27 | 0 | 18 | 0 | 2019-10-27 | 9.3 | 8.7 | 0 | 2018-10-27 | 3.5 | 14.5 | 0 | 2017-10-27 | 9.1 | 8.9 | 0 | 2016-10-27 | 0.2 | 17.8 | 0 | 11.18 | 0.15
2025-10-27 | 7.8 | 10.2 | 0 | 2024-10-27 | 4.1 | 13.9 | 0 | 2023-10-27 | 19.1 | 0 | 1.1 | 2022-10-27 | 4.8 | 13.2 | 0 | 2021-10-27 | 9.7 | 8.3 | 0 | 2020-10-27 | -0.1 | 18.1 | 0 | 2019-10-27 | 10.6 | 7.4 | 0 | 2018-10-27 | 0.5 | 17.5 | 0 | 2017-10-27 | 7 | 11 | 0 | 2016-10-27 | 0.3 | 17.7 | 0 | 11.73 | 0.11
2025-10-27 | 5.4 | 12.6 | 0 | 2024-10-27 | 3.4 | 14.6 | 0 | 2023-10-27 | 18.5 | 0 | 0.5 | 2022-10-27 | 2.4 | 15.6 | 0 | 2021-10-27 | 9.8 | 8.2 | 0 | 2020-10-27 | -1.2 | 19.2 | 0 | 2019-10-27 | 10.9 | 7.1 | 0 | 2018-10-27 | 0.3 | 17.7 | 0 | 2017-10-27 | 7.5 | 10.5 | 0 | 2016-10-27 | 0.4 | 17.6 | 0 | 12.31 | 0.05
2025-10-27 | 2.6 | 15.4 | 0 | 2024-10-27 | 2.6 | 15.4 | 0 | 2023-10-27 | 18.3 | 0 | 0.3 | 2022-10-27 | 3.4 | 14.6 | 0 | 2021-10-27 | 9.2 | 8.8 | 0 | 2020-10-27 | -0.9 | 18.9 | 0 | 2019-10-27 | 10.5 | 7.5 | 0 | 2018-10-27 | 0.2 | 17.8 | 0 | 2017-10-27 | 6.4 | 11.6 | 0 | 2016-10-27 | 0.4 | 17.6 | 0 | 12.76 | 0.03
2025-10-27 | 1.2 | 16.8 | 0 | 2024-10-27 | 2.1 | 15.9 | 0 | 2023-10-27 | 17.9 | 0.1 | 0 | 2022-10-27 | 2.8 | 15.2 | 0 | 2021-10-27 | 8.6 | 9.4 | 0 | 2020-10-27 | -0.8 | 18.8 | 0 | 2019-10-27 | 10.6 | 7.4 | 0 | 2018-10-27 | 0.2 | 17.8 | 0 | 2017-10-27 | 5.9 | 12.1 | 0 | 2016-10-27 | 0.3 | 17.7 | 0 | 13.12 | 0
2025-10-27 | 3 | 15 | 0 | 2024-10-27 | 2.3 | 15.7 | 0 | 2023-10-27 | 17.3 | 0.7 | 0 | 2022-10-27 | 0.7 | 17.3 | 0 | 2021-10-27 | 7.7 | 10.3 | 0 | 2020-10-27 | -0.9 | 18.9 | 0 | 2019-10-27 | 10.9 | 7.1 | 0 | 2018-10-27 | 0.3 | 17.7 | 0 | 2017-10-27 | 5.4 | 12.6 | 0 | 2016-10-27 | 0.4 | 17.6 | 0 | 13.29 | 0
2025-10-27 | 2.5 | 15.5 | 0 | 2024-10-27 | 2.4 | 15.6 | 0 | 2023-10-27 | 16.8 | 1.2 | 0 | 2022-10-27 | 0.1 | 17.9 | 0 | 2021-10-27 | 7.2 | 10.8 | 0 | 2020-10-27 | -0.9 | 18.9 | 0 | 2019-10-27 | 11.3 | 6.7 | 0 | 2018-10-27 | 0.3 | 17.7 | 0 | 2017-10-27 | 4.7 | 13.3 | 0 | 2016-10-27 | 0.4 | 17.6 | 0 | 13.52 | 0
2025-10-28 | 1 | 17 | 0 | 2024-10-28 | 1.4 | 16.6 | 0 | 2023-10-28 | 16.3 | 1.7 | 0 | 2022-10-28 | -0.3 | 18.3 | 0 | 2021-10-28 | 6.8 | 11.2 | 0 | 2020-10-28 | -0.6 | 18.6 | 0 | 2019-10-28 | 11.4 | 6.6 | 0 | 2018-10-28 | 0.4 | 17.6 | 0 | 2017-10-28 | 4.3 | 13.7 | 0 | 2016-10-28 | 0.3 | 17.7 | 0 | 13.9 | 0
2025-10-28 | 0.5 | 17.5 | 0 | 2024-10-28 | 0.9 | 17.1 | 0 | 2023-10-28 | 16.2 | 1.8 | 0 | 2022-10-28 | -1.4 | 19.4 | 0 | 2021-10-28 | 6.9 | 11.1 | 0 | 2020-10-28 | -0.6 | 18.6 | 0 | 2019-10-28 | 10.5 | 7.5 | 0 | 2018-10-28 | 0.3 | 17.7 | 0 | 2017-10-28 | 4.3 | 13.7 | 0 | 2016-10-28 | 0.4 | 17.6 | 0 | 14.2 | 0
2025-10-28 | 0.8 | 17.2 | 0 | 2024-10-28 | 0.6 | 17.4 | 0 | 2023-10-28 | 17.6 | 0.4 | 0 | 2022-10-28 | -1.4 | 19.4 | 0 | 2021-10-28 | 5.7 | 12.3 | 0 | 2020-10-28 | -0.5 | 18.5 | 0 | 2019-10-28 | 9.9 | 8.1 | 0 | 2018-10-28 | 0.3 | 17.7 | 0 | 2017-10-28 | 4 | 14 | 0 | 2016-10-28 | 0.4 | 17.6 | 0 | 14.26 | 0
2025-10-28 | 0.2 | 17.8 | 0 | 2024-10-28 | 0.5 | 17.5 | 0 | 2023-10-28 | 18.1 | 0 | 0.1 | 2022-10-28 | -1.7 | 19.7 | 0 | 2021-10-28 | 4.1 | 13.9 | 0 | 2020-10-28 | -0.4 | 18.4 | 0 | 2019-10-28 | 9.4 | 8.6 | 0 | 2018-10-28 | 0.3 | 17.7 | 0 | 2017-10-28 | 4.1 | 13.9 | 0 | 2016-10-28 | 0.6 | 17.4 | 0 | 14.49 | 0.01
2025-10-28 | 1 | 17 | 0 | 2024-10-28 | -0.1 | 18.1 | 0 | 2023-10-28 | 17.9 | 0.1 | 0 | 2022-10-28 | -1.8 | 19.8 | 0 | 2021-10-28 | 3.8 | 14.2 | 0 | 2020-10-28 | -0.6 | 18.6 | 0 | 2019-10-28 | 9 | 9 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 4.2 | 13.8 | 0 | 2016-10-28 | 0.7 | 17.3 | 0 | 14.57 | 0
2025-10-28 | 0.9 | 17.1 | 0 | 2024-10-28 | -1.6 | 19.6 | 0 | 2023-10-28 | 18 | 0 | 0 | 2022-10-28 | -2.2 | 20.2 | 0 | 2021-10-28 | 3.2 | 14.8 | 0 | 2020-10-28 | -0.8 | 18.8 | 0 | 2019-10-28 | 9.1 | 8.9 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 4 | 14 | 0 | 2016-10-28 | 1 | 17 | 0 | 14.82 | 0
2025-10-28 | 1.1 | 16.9 | 0 | 2024-10-28 | -1.9 | 19.9 | 0 | 2023-10-28 | 17.9 | 0.1 | 0 | 2022-10-28 | -1.3 | 19.3 | 0 | 2021-10-28 | 2.1 | 15.9 | 0 | 2020-10-28 | -1 | 19 | 0 | 2019-10-28 | 9.2 | 8.8 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 4.1 | 13.9 | 0 | 2016-10-28 | 1 | 17 | 0 | 14.86 | 0
2025-10-28 | 0.7 | 17.3 | 0 | 2024-10-28 | -1.6 | 19.6 | 0 | 2023-10-28 | 16.1 | 1.9 | 0 | 2022-10-28 | -2.5 | 20.5 | 0 | 2021-10-28 | 1.9 | 16.1 | 0 | 2020-10-28 | -0.9 | 18.9 | 0 | 2019-10-28 | 8.9 | 9.1 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 4.8 | 13.2 | 0 | 2016-10-28 | 1.3 | 16.7 | 0 | 15.11 | 0
2025-10-28 | 3.3 | 14.7 | 0 | 2024-10-28 | -0.8 | 18.8 | 0 | 2023-10-28 | 13.8 | 4.2 | 0 | 2022-10-28 | 0.5 | 17.5 | 0 | 2021-10-28 | 4.6 | 13.4 | 0 | 2020-10-28 | -0.7 | 18.7 | 0 | 2019-10-28 | 9.5 | 8.5 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 6.8 | 11.2 | 0 | 2016-10-28 | 1.6 | 16.4 | 0 | 14.12 | 0
2025-10-28 | 6.1 | 11.9 | 0 | 2024-10-28 | 1.7 | 16.3 | 0 | 2023-10-28 | 13.6 | 4.4 | 0 | 2022-10-28 | 3.2 | 14.8 | 0 | 2021-10-28 | 5.8 | 12.2 | 0 | 2020-10-28 | -0.1 | 18.1 | 0 | 2019-10-28 | 9.6 | 8.4 | 0 | 2018-10-28 | 0.2 | 17.8 | 0 | 2017-10-28 | 10.8 | 7.2 | 0 | 2016-10-28 | 1.7 | 16.3 | 0 | 12.74 | 0
2025-10-28 | 8.3 | 9.7 | 0 | 2024-10-28 | 3 | 15 | 0 | 2023-10-28 | 14.4 | 3.6 | 0 | 2022-10-28 | 4.4 | 13.6 | 0 | 2021-10-28 | 6.8 | 11.2 | 0 | 2020-10-28 | 1.5 | 16.5 | 0 | 2019-10-28 | 10 | 8 | 0 | 2018-10-28 | 0.5 | 17.5 | 0 | 2017-10-28 | 14 | 4 | 0 | 2016-10-28 | 2.1 | 15.9 | 0 | 11.5 | 0
2025-10-28 | 9.7 | 8.3 | 0 | 2024-10-28 | 4 | 14 | 0 | 2023-10-28 | 13 | 5 | 0 | 2022-10-28 | 6.5 | 11.5 | 0 | 2021-10-28 | 7.1 | 10.9 | 0 | 2020-10-28 | 4.4 | 13.6 | 0 | 2019-10-28 | 10.7 | 7.3 | 0 | 2018-10-28 | 0.8 | 17.2 | 0 | 2017-10-28 | 16 | 2 | 0 | 2016-10-28 | 2.4 | 15.6 | 0 | 10.54 | 0
2025-10-28 | 10.8 | 7.2 | 0 | 2024-10-28 | 4.9 | 13.1 | 0 | 2023-10-28 | 12 | 6 | 0 | 2022-10-28 | 7.5 | 10.5 | 0 | 2021-10-28 | 7.5 | 10.5 | 0 | 2020-10-28 | 6.7 | 11.3 | 0 | 2019-10-28 | 11.6 | 6.4 | 0 | 2018-10-28 | 1.1 | 16.9 | 0 | 2017-10-28 | 18 | 0 | 0 | 2016-10-28 | 2.6 | 15.4 | 0 | 9.73 | 0
2025-10-28 | 11.7 | 6.3 | 0 | 2024-10-28 | 5.4 | 12.6 | 0 | 2023-10-28 | 12.4 | 5.6 | 0 | 2022-10-28 | 8 | 10 | 0 | 2021-10-28 | 8.9 | 9.1 | 0 | 2020-10-28 | 8 | 10 | 0 | 2019-10-28 | 13.2 | 4.8 | 0 | 2018-10-28 | 1.5 | 16.5 | 0 | 2017-10-28 | 18.3 | 0 | 0.3 | 2016-10-28 | 2.9 | 15.1 | 0 | 9 | 0.03
2025-10-28 | 12.3 | 5.7 | 0 | 2024-10-28 | 5.5 | 12.5 | 0 | 2023-10-28 | 12 | 6 | 0 | 2022-10-28 | 8 | 10 | 0 | 2021-10-28 | 9.2 | 8.8 | 0 | 2020-10-28 | 8.8 | 9.2 | 0 | 2019-10-28 | 13.3 | 4.7 | 0 | 2018-10-28 | 1.6 | 16.4 | 0 | 2017-10-28 | 17.4 | 0.6 | 0 | 2016-10-28 | 3.5 | 14.5 | 0 | 8.84 | 0
2025-10-28 | 12.3 | 5.7 | 0 | 2024-10-28 | 5.7 | 12.3 | 0 | 2023-10-28 | 11.6 | 6.4 | 0 | 2022-10-28 | 8.7 | 9.3 | 0 | 2021-10-28 | 9.6 | 8.4 | 0 | 2020-10-28 | 8.5 | 9.5 | 0 | 2019-10-28 | 14.4 | 3.6 | 0 | 2018-10-28 | 1.7 | 16.3 | 0 | 2017-10-28 | 15.7 | 2.3 | 0 | 2016-10-28 | 3.8 | 14.2 | 0 | 8.8 | 0
2025-10-28 | 11.7 | 6.3 | 0 | 2024-10-28 | 5 | 13 | 0 | 2023-10-28 | 10.6 | 7.4 | 0 | 2022-10-28 | 7.7 | 10.3 | 0 | 2021-10-28 | 9.2 | 8.8 | 0 | 2020-10-28 | 8.5 | 9.5 | 0 | 2019-10-28 | 14.5 | 3.5 | 0 | 2018-10-28 | 1.6 | 16.4 | 0 | 2017-10-28 | 13.1 | 4.9 | 0 | 2016-10-28 | 3 | 15 | 0 | 9.51 | 0
2025-10-28 | 9.3 | 8.7 | 0 | 2024-10-28 | 3.3 | 14.7 | 0 | 2023-10-28 | 8.6 | 9.4 | 0 | 2022-10-28 | 6.4 | 11.6 | 0 | 2021-10-28 | 6.9 | 11.1 | 0 | 2020-10-28 | 7.7 | 10.3 | 0 | 2019-10-28 | 10.4 | 7.6 | 0 | 2018-10-28 | 1.4 | 16.6 | 0 | 2017-10-28 | 12.3 | 5.7 | 0 | 2016-10-28 | 2.7 | 15.3 | 0 | 11.1 | 0
2025-10-28 | 7 | 11 | 0 | 2024-10-28 | 0.4 | 17.6 | 0 | 2023-10-28 | 8.1 | 9.9 | 0 | 2022-10-28 | 4.8 | 13.2 | 0 | 2021-10-28 | 5.1 | 12.9 | 0 | 2020-10-28 | 7.3 | 10.7 | 0 | 2019-10-28 | 10.6 | 7.4 | 0 | 2018-10-28 | 1.1 | 16.9 | 0 | 2017-10-28 | 12.2 | 5.8 | 0 | 2016-10-28 | 2.4 | 15.6 | 0 | 12.1 | 0
2025-10-28 | 6.8 | 11.2 | 0 | 2024-10-28 | 0.5 | 17.5 | 0 | 2023-10-28 | 7.3 | 10.7 | 0 | 2022-10-28 | 2.7 | 15.3 | 0 | 2021-10-28 | 4.7 | 13.3 | 0 | 2020-10-28 | 7.3 | 10.7 | 0 | 2019-10-28 | 9.2 | 8.8 | 0 | 2018-10-28 | 1.1 | 16.9 | 0 | 2017-10-28 | 12 | 6 | 0 | 2016-10-28 | 2.2 | 15.8 | 0 | 12.62 | 0
2025-10-28 | 6.1 | 11.9 | 0 | 2024-10-28 | 2.1 | 15.9 | 0 | 2023-10-28 | 6.3 | 11.7 | 0 | 2022-10-28 | 3.8 | 14.2 | 0 | 2021-10-28 | 5.4 | 12.6 | 0 | 2020-10-28 | 7 | 11 | 0 | 2019-10-28 | 6.8 | 11.2 | 0 | 2018-10-28 | 1 | 17 | 0 | 2017-10-28 | 12 | 6 | 0 | 2016-10-28 | 2 | 16 | 0 | 12.75 | 0
2025-10-28 | 3.4 | 14.6 | 0 | 2024-10-28 | 2 | 16 | 0 | 2023-10-28 | 6.1 | 11.9 | 0 | 2022-10-28 | 2.2 | 15.8 | 0 | 2021-10-28 | 5.1 | 12.9 | 0 | 2020-10-28 | 7 | 11 | 0 | 2019-10-28 | 6.7 | 11.3 | 0 | 2018-10-28 | 1.1 | 16.9 | 0 | 2017-10-28 | 9.9 | 8.1 | 0 | 2016-10-28 | 0.8 | 17.2 | 0 | 13.57 | 0
2025-10-28 | 3.7 | 14.3 | 0 | 2024-10-28 | 1.6 | 16.4 | 0 | 2023-10-28 | 5.7 | 12.3 | 0 | 2022-10-28 | 0.7 | 17.3 | 0 | 2021-10-28 | 3.6 | 14.4 | 0 | 2020-10-28 | 7 | 11 | 0 | 2019-10-28 | 6.5 | 11.5 | 0 | 2018-10-28 | 1 | 17 | 0 | 2017-10-28 | 9 | 9 | 0 | 2016-10-28 | 0.7 | 17.3 | 0 | 14.05 | 0
2025-10-28 | 3.8 | 14.2 | 0 | 2024-10-28 | 0.9 | 17.1 | 0 | 2023-10-28 | 4.9 | 13.1 | 0 | 2022-10-28 | 1.1 | 16.9 | 0 | 2021-10-28 | 3.6 | 14.4 | 0 | 2020-10-28 | 7.2 | 10.8 | 0 | 2019-10-28 | 5.7 | 12.3 | 0 | 2018-10-28 | 0.7 | 17.3 | 0 | 2017-10-28 | 8.1 | 9.9 | 0 | 2016-10-28 | 1.1 | 16.9 | 0 | 14.29 | 0
2025-10-29 | 2.3 | 15.7 | 0 | 2024-10-29 | 0.8 | 17.2 | 0 | 2023-10-29 | 4.4 | 13.6 | 0 | 2022-10-29 | 0.8 | 17.2 | 0 | 2021-10-29 | 3.6 | 14.4 | 0 | 2020-10-29 | 6.6 | 11.4 | 0 | 2019-10-29 | 5.6 | 12.4 | 0 | 2018-10-29 | 0.9 | 17.1 | 0 | 2017-10-29 | 7.5 | 10.5 | 0 | 2016-10-29 | 1 | 17 | 0 | 14.65 | 0
2025-10-29 | 1.6 | 16.4 | 0 | 2024-10-29 | -0.2 | 18.2 | 0 | 2023-10-29 | 4.1 | 13.9 | 0 | 2022-10-29 | -1.2 | 19.2 | 0 | 2021-10-29 | 2.7 | 15.3 | 0 | 2020-10-29 | 5.9 | 12.1 | 0 | 2019-10-29 | 6 | 12 | 0 | 2018-10-29 | 0.9 | 17.1 | 0 | 2017-10-29 | 6.9 | 11.1 | 0 | 2016-10-29 | 0.9 | 17.1 | 0 | 15.24 | 0
2025-10-29 | 1.6 | 16.4 | 0 | 2024-10-29 | 0.1 | 17.9 | 0 | 2023-10-29 | 3.6 | 14.4 | 0 | 2022-10-29 | -2.4 | 20.4 | 0 | 2021-10-29 | 2.3 | 15.7 | 0 | 2020-10-29 | 5.9 | 12.1 | 0 | 2019-10-29 | 5 | 13 | 0 | 2018-10-29 | 1.2 | 16.8 | 0 | 2017-10-29 | 6.7 | 11.3 | 0 | 2016-10-29 | 1.4 | 16.6 | 0 | 15.46 | 0
2025-10-29 | 1.1 | 16.9 | 0 | 2024-10-29 | 0.2 | 17.8 | 0 | 2023-10-29 | 3.3 | 14.7 | 0 | 2022-10-29 | -1.6 | 19.6 | 0 | 2021-10-29 | 2.3 | 15.7 | 0 | 2020-10-29 | 4.7 | 13.3 | 0 | 2019-10-29 | 4.7 | 13.3 | 0 | 2018-10-29 | 1.2 | 16.8 | 0 | 2017-10-29 | 6.5 | 11.5 | 0 | 2016-10-29 | 1.8 | 16.2 | 0 | 15.58 | 0
2025-10-29 | -0.2 | 18.2 | 0 | 2024-10-29 | -0.3 | 18.3 | 0 | 2023-10-29 | 3.4 | 14.6 | 0 | 2022-10-29 | -0.9 | 18.9 | 0 | 2021-10-29 | 2.1 | 15.9 | 0 | 2020-10-29 | 4.6 | 13.4 | 0 | 2019-10-29 | 4.6 | 13.4 | 0 | 2018-10-29 | 1 | 17 | 0 | 2017-10-29 | 6.5 | 11.5 | 0 | 2016-10-29 | 2.2 | 15.8 | 0 | 15.7 | 0
2025-10-29 | 1.1 | 16.9 | 0 | 2024-10-29 | -0.9 | 18.9 | 0 | 2023-10-29 | 3.3 | 14.7 | 0 | 2022-10-29 | -0.9 | 18.9 | 0 | 2021-10-29 | 1.5 | 16.5 | 0 | 2020-10-29 | 5 | 13 | 0 | 2019-10-29 | 4.7 | 13.3 | 0 | 2018-10-29 | 1.1 | 16.9 | 0 | 2017-10-29 | 6.4 | 11.6 | 0 | 2016-10-29 | 2.5 | 15.5 | 0 | 15.62 | 0
2025-10-29 | 1.1 | 16.9 | 0 | 2024-10-29 | -0.9 | 18.9 | 0 | 2023-10-29 | 3 | 15 | 0 | 2022-10-29 | -1.6 | 19.6 | 0 | 2021-10-29 | 1 | 17 | 0 | 2020-10-29 | 5.1 | 12.9 | 0 | 2019-10-29 | 4.7 | 13.3 | 0 | 2018-10-29 | 1.5 | 16.5 | 0 | 2017-10-29 | 6.4 | 11.6 | 0 | 2016-10-29 | 2.7 | 15.3 | 0 | 15.7 | 0
2025-10-29 | 1.5 | 16.5 | 0 | 2024-10-29 | -0.4 | 18.4 | 0 | 2023-10-29 | 2.6 | 15.4 | 0 | 2022-10-29 | -2.2 | 20.2 | 0 | 2021-10-29 | 1.3 | 16.7 | 0 | 2020-10-29 | 4.5 | 13.5 | 0 | 2019-10-29 | 4.7 | 13.3 | 0 | 2018-10-29 | 1.8 | 16.2 | 0 | 2017-10-29 | 6.4 | 11.6 | 0 | 2016-10-29 | 2.8 | 15.2 | 0 | 15.7 | 0
2025-10-29 | 3.6 | 14.4 | 0 | 2024-10-29 | 0.7 | 17.3 | 0 | 2023-10-29 | 2.5 | 15.5 | 0 | 2022-10-29 | 0.7 | 17.3 | 0 | 2021-10-29 | 3.1 | 14.9 | 0 | 2020-10-29 | 5 | 13 | 0 | 2019-10-29 | 6.9 | 11.1 | 0 | 2018-10-29 | 2.3 | 15.7 | 0 | 2017-10-29 | 6.9 | 11.1 | 0 | 2016-10-29 | 2.8 | 15.2 | 0 | 14.55 | 0
2025-10-29 | 5.7 | 12.3 | 0 | 2024-10-29 | 2.9 | 15.1 | 0 | 2023-10-29 | 2.6 | 15.4 | 0 | 2022-10-29 | 3.9 | 14.1 | 0 | 2021-10-29 | 5.1 | 12.9 | 0 | 2020-10-29 | 5.4 | 12.6 | 0 | 2019-10-29 | 9.9 | 8.1 | 0 | 2018-10-29 | 2.9 | 15.1 | 0 | 2017-10-29 | 6.8 | 11.2 | 0 | 2016-10-29 | 3 | 15 | 0 | 13.18 | 0
2025-10-29 | 8 | 10 | 0 | 2024-10-29 | 4.1 | 13.9 | 0 | 2023-10-29 | 3.2 | 14.8 | 0 | 2022-10-29 | 7.4 | 10.6 | 0 | 2021-10-29 | 7.2 | 10.8 | 0 | 2020-10-29 | 5.4 | 12.6 | 0 | 2019-10-29 | 13 | 5 | 0 | 2018-10-29 | 3.5 | 14.5 | 0 | 2017-10-29 | 6.8 | 11.2 | 0 | 2016-10-29 | 3.5 | 14.5 | 0 | 11.79 | 0
2025-10-29 | 9.2 | 8.8 | 0 | 2024-10-29 | 5.8 | 12.2 | 0 | 2023-10-29 | 3.2 | 14.8 | 0 | 2022-10-29 | 10.5 | 7.5 | 0 | 2021-10-29 | 8.9 | 9.1 | 0 | 2020-10-29 | 5.4 | 12.6 | 0 | 2019-10-29 | 15.9 | 2.1 | 0 | 2018-10-29 | 2.8 | 15.2 | 0 | 2017-10-29 | 7.1 | 10.9 | 0 | 2016-10-29 | 3.8 | 14.2 | 0 | 10.74 | 0
2025-10-29 | 10.5 | 7.5 | 0 | 2024-10-29 | 8 | 10 | 0 | 2023-10-29 | 3.7 | 14.3 | 0 | 2022-10-29 | 12.1 | 5.9 | 0 | 2021-10-29 | 10.7 | 7.3 | 0 | 2020-10-29 | 5.4 | 12.6 | 0 | 2019-10-29 | 16.6 | 1.4 | 0 | 2018-10-29 | 3.3 | 14.7 | 0 | 2017-10-29 | 7.5 | 10.5 | 0 | 2016-10-29 | 4 | 14 | 0 | 9.82 | 0
2025-10-29 | 11.2 | 6.8 | 0 | 2024-10-29 | 10.1 | 7.9 | 0 | 2023-10-29 | 4.1 | 13.9 | 0 | 2022-10-29 | 13.6 | 4.4 | 0 | 2021-10-29 | 11.8 | 6.2 | 0 | 2020-10-29 | 5.2 | 12.8 | 0 | 2019-10-29 | 17 | 1 | 0 | 2018-10-29 | 4.1 | 13.9 | 0 | 2017-10-29 | 7.9 | 10.1 | 0 | 2016-10-29 | 4.4 | 13.6 | 0 | 9.06 | 0
2025-10-29 | 11.2 | 6.8 | 0 | 2024-10-29 | 11 | 7 | 0 | 2023-10-29 | 4.5 | 13.5 | 0 | 2022-10-29 | 15 | 3 | 0 | 2021-10-29 | 13.1 | 4.9 | 0 | 2020-10-29 | 4.8 | 13.2 | 0 | 2019-10-29 | 17.5 | 0.5 | 0 | 2018-10-29 | 4.3 | 13.7 | 0 | 2017-10-29 | 8.2 | 9.8 | 0 | 2016-10-29 | 5 | 13 | 0 | 8.54 | 0
2025-10-29 | 11.4 | 6.6 | 0 | 2024-10-29 | 11.1 | 6.9 | 0 | 2023-10-29 | 4.6 | 13.4 | 0 | 2022-10-29 | 15.2 | 2.8 | 0 | 2021-10-29 | 12.4 | 5.6 | 0 | 2020-10-29 | 4.5 | 13.5 | 0 | 2019-10-29 | 17.8 | 0.2 | 0 | 2018-10-29 | 3.6 | 14.4 | 0 | 2017-10-29 | 8.2 | 9.8 | 0 | 2016-10-29 | 5.6 | 12.4 | 0 | 8.56 | 0
2025-10-29 | 10.6 | 7.4 | 0 | 2024-10-29 | 10.4 | 7.6 | 0 | 2023-10-29 | 3.9 | 14.1 | 0 | 2022-10-29 | 15 | 3 | 0 | 2021-10-29 | 11.7 | 6.3 | 0 | 2020-10-29 | 4.4 | 13.6 | 0 | 2019-10-29 | 17.4 | 0.6 | 0 | 2018-10-29 | 3.3 | 14.7 | 0 | 2017-10-29 | 7.9 | 10.1 | 0 | 2016-10-29 | 6.1 | 11.9 | 0 | 8.93 | 0
2025-10-29 | 8.3 | 9.7 | 0 | 2024-10-29 | 8 | 10 | 0 | 2023-10-29 | 3.6 | 14.4 | 0 | 2022-10-29 | 12.9 | 5.1 | 0 | 2021-10-29 | 9.6 | 8.4 | 0 | 2020-10-29 | 3.3 | 14.7 | 0 | 2019-10-29 | 16.4 | 1.6 | 0 | 2018-10-29 | 2.6 | 15.4 | 0 | 2017-10-29 | 7.8 | 10.2 | 0 | 2016-10-29 | 6.3 | 11.7 | 0 | 10.12 | 0
2025-10-29 | 6.1 | 11.9 | 0 | 2024-10-29 | 7.7 | 10.3 | 0 | 2023-10-29 | 3.6 | 14.4 | 0 | 2022-10-29 | 11.1 | 6.9 | 0 | 2021-10-29 | 7.4 | 10.6 | 0 | 2020-10-29 | 2.7 | 15.3 | 0 | 2019-10-29 | 14.9 | 3.1 | 0 | 2018-10-29 | 2.2 | 15.8 | 0 | 2017-10-29 | 8 | 10 | 0 | 2016-10-29 | 7.6 | 10.4 | 0 | 10.87 | 0
2025-10-29 | 5.8 | 12.2 | 0 | 2024-10-29 | 7.5 | 10.5 | 0 | 2023-10-29 | 3.5 | 14.5 | 0 | 2022-10-29 | 9.4 | 8.6 | 0 | 2021-10-29 | 8 | 10 | 0 | 2020-10-29 | 2.2 | 15.8 | 0 | 2019-10-29 | 15.3 | 2.7 | 0 | 2018-10-29 | 2.2 | 15.8 | 0 | 2017-10-29 | 8.3 | 9.7 | 0 | 2016-10-29 | 8.6 | 9.4 | 0 | 10.92 | 0
2025-10-29 | 4.6 | 13.4 | 0 | 2024-10-29 | 8.5 | 9.5 | 0 | 2023-10-29 | 3.5 | 14.5 | 0 | 2022-10-29 | 7.8 | 10.2 | 0 | 2021-10-29 | 7.5 | 10.5 | 0 | 2020-10-29 | 1.6 | 16.4 | 0 | 2019-10-29 | 16 | 2 | 0 | 2018-10-29 | 2.3 | 15.7 | 0 | 2017-10-29 | 8.3 | 9.7 | 0 | 2016-10-29 | 8.3 | 9.7 | 0 | 11.16 | 0
2025-10-29 | 4.4 | 13.6 | 0 | 2024-10-29 | 10.9 | 7.1 | 0 | 2023-10-29 | 3.4 | 14.6 | 0 | 2022-10-29 | 6.6 | 11.4 | 0 | 2021-10-29 | 7.1 | 10.9 | 0 | 2020-10-29 | 0.8 | 17.2 | 0 | 2019-10-29 | 15.5 | 2.5 | 0 | 2018-10-29 | 1.8 | 16.2 | 0 | 2017-10-29 | 8.7 | 9.3 | 0 | 2016-10-29 | 7.9 | 10.1 | 0 | 11.29 | 0
2025-10-29 | 4.1 | 13.9 | 0 | 2024-10-29 | 10.6 | 7.4 | 0 | 2023-10-29 | 3.4 | 14.6 | 0 | 2022-10-29 | 6.2 | 11.8 | 0 | 2021-10-29 | 7.1 | 10.9 | 0 | 2020-10-29 | 0.2 | 17.8 | 0 | 2019-10-29 | 14.5 | 3.5 | 0 | 2018-10-29 | 1.4 | 16.6 | 0 | 2017-10-29 | 9.1 | 8.9 | 0 | 2016-10-29 | 7.6 | 10.4 | 0 | 11.58 | 0
2025-10-29 | 3.7 | 14.3 | 0 | 2024-10-29 | 8.4 | 9.6 | 0 | 2023-10-29 | 3.2 | 14.8 | 0 | 2022-10-29 | 5.6 | 12.4 | 0 | 2021-10-29 | 7.4 | 10.6 | 0 | 2020-10-29 | -0.2 | 18.2 | 0 | 2019-10-29 | 14.2 | 3.8 | 0 | 2018-10-29 | 0.9 | 17.1 | 0 | 2017-10-29 | 9.5 | 8.5 | 0 | 2016-10-29 | 6.9 | 11.1 | 0 | 12.04 | 0
2025-10-30 | 2.5 | 15.5 | 0 | 2024-10-30 | 8.3 | 9.7 | 0 | 2023-10-30 | 3.5 | 14.5 | 0 | 2022-10-30 | 4.8 | 13.2 | 0 | 2021-10-30 | 6.7 | 11.3 | 0 | 2020-10-30 | -0.7 | 18.7 | 0 | 2019-10-30 | 13.1 | 4.9 | 0 | 2018-10-30 | 0.9 | 17.1 | 0 | 2017-10-30 | 9.8 | 8.2 | 0 | 2016-10-30 | 6.3 | 11.7 | 0 | 12.48 | 0
2025-10-30 | 2.7 | 15.3 | 0 | 2024-10-30 | 8.5 | 9.5 | 0 | 2023-10-30 | 3.5 | 14.5 | 0 | 2022-10-30 | 4 | 14 | 0 | 2021-10-30 | 7.2 | 10.8 | 0 | 2020-10-30 | -1.3 | 19.3 | 0 | 2019-10-30 | 12.6 | 5.4 | 0 | 2018-10-30 | 0.9 | 17.1 | 0 | 2017-10-30 | 10 | 8 | 0 | 2016-10-30 | 5.8 | 12.2 | 0 | 12.61 | 0
2025-10-30 | 2.2 | 15.8 | 0 | 2024-10-30 | 8.5 | 9.5 | 0 | 2023-10-30 | 0.9 | 17.1 | 0 | 2022-10-30 | 4.1 | 13.9 | 0 | 2021-10-30 | 6.6 | 11.4 | 0 | 2020-10-30 | -1.9 | 19.9 | 0 | 2019-10-30 | 10.9 | 7.1 | 0 | 2018-10-30 | 1 | 17 | 0 | 2017-10-30 | 9.8 | 8.2 | 0 | 2016-10-30 | 5.5 | 12.5 | 0 | 13.24 | 0
2025-10-30 | 2.1 | 15.9 | 0 | 2024-10-30 | 8.8 | 9.2 | 0 | 2023-10-30 | 0.1 | 17.9 | 0 | 2022-10-30 | 2 | 16 | 0 | 2021-10-30 | 6.1 | 11.9 | 0 | 2020-10-30 | -3.1 | 21.1 | 0 | 2019-10-30 | 11.5 | 6.5 | 0 | 2018-10-30 | 1.3 | 16.7 | 0 | 2017-10-30 | 9.5 | 8.5 | 0 | 2016-10-30 | 5.1 | 12.9 | 0 | 13.66 | 0
2025-10-30 | 2.6 | 15.4 | 0 | 2024-10-30 | 9.1 | 8.9 | 0 | 2023-10-30 | 0.1 | 17.9 | 0 | 2022-10-30 | 1.6 | 16.4 | 0 | 2021-10-30 | 6.1 | 11.9 | 0 | 2020-10-30 | -4 | 22 | 0 | 2019-10-30 | 11.1 | 6.9 | 0 | 2018-10-30 | 1.1 | 16.9 | 0 | 2017-10-30 | 10.2 | 7.8 | 0 | 2016-10-30 | 4.6 | 13.4 | 0 | 13.75 | 0
2025-10-30 | 2 | 16 | 0 | 2024-10-30 | 8.7 | 9.3 | 0 | 2023-10-30 | -0.1 | 18.1 | 0 | 2022-10-30 | 1 | 17 | 0 | 2021-10-30 | 5.8 | 12.2 | 0 | 2020-10-30 | -4.5 | 22.5 | 0 | 2019-10-30 | 11.4 | 6.6 | 0 | 2018-10-30 | 0.2 | 17.8 | 0 | 2017-10-30 | 9.6 | 8.4 | 0 | 2016-10-30 | 4.5 | 13.5 | 0 | 14.14 | 0
2025-10-30 | 2 | 16 | 0 | 2024-10-30 | 8 | 10 | 0 | 2023-10-30 | 0 | 18 | 0 | 2022-10-30 | 0.3 | 17.7 | 0 | 2021-10-30 | 5.6 | 12.4 | 0 | 2020-10-30 | -4.7 | 22.7 | 0 | 2019-10-30 | 10.8 | 7.2 | 0 | 2018-10-30 | 0.4 | 17.6 | 0 | 2017-10-30 | 7.6 | 10.4 | 0 | 2016-10-30 | 4.2 | 13.8 | 0 | 14.58 | 0
2025-10-30 | 2.7 | 15.3 | 0 | 2024-10-30 | 7.6 | 10.4 | 0 | 2023-10-30 | 0 | 18 | 0 | 2022-10-30 | 0.1 | 17.9 | 0 | 2021-10-30 | 5.5 | 12.5 | 0 | 2020-10-30 | -4.8 | 22.8 | 0 | 2019-10-30 | 10.3 | 7.7 | 0 | 2018-10-30 | 0.5 | 17.5 | 0 | 2017-10-30 | 6.2 | 11.8 | 0 | 2016-10-30 | 3.9 | 14.1 | 0 | 14.8 | 0
2025-10-30 | 3.3 | 14.7 | 0 | 2024-10-30 | 11 | 7 | 0 | 2023-10-30 | 0.1 | 17.9 | 0 | 2022-10-30 | 3.2 | 14.8 | 0 | 2021-10-30 | 5.2 | 12.8 | 0 | 2020-10-30 | -4.2 | 22.2 | 0 | 2019-10-30 | 9.7 | 8.3 | 0 | 2018-10-30 | 0.9 | 17.1 | 0 | 2017-10-30 | 5.8 | 12.2 | 0 | 2016-10-30 | 3.7 | 14.3 | 0 | 14.13 | 0
2025-10-30 | 3.4 | 14.6 | 0 | 2024-10-30 | 15.3 | 2.7 | 0 | 2023-10-30 | 0.5 | 17.5 | 0 | 2022-10-30 | 6 | 12 | 0 | 2021-10-30 | 6.8 | 11.2 | 0 | 2020-10-30 | -2.9 | 20.9 | 0 | 2019-10-30 | 10.2 | 7.8 | 0 | 2018-10-30 | 1.7 | 16.3 | 0 | 2017-10-30 | 5.6 | 12.4 | 0 | 2016-10-30 | 4.4 | 13.6 | 0 | 12.9 | 0
2025-10-30 | 3.5 | 14.5 | 0 | 2024-10-30 | 17.3 | 0.7 | 0 | 2023-10-30 | 0.9 | 17.1 | 0 | 2022-10-30 | 10 | 8 | 0 | 2021-10-30 | 7.1 | 10.9 | 0 | 2020-10-30 | -0.4 | 18.4 | 0 | 2019-10-30 | 10.7 | 7.3 | 0 | 2018-10-30 | 2 | 16 | 0 | 2017-10-30 | 5.8 | 12.2 | 0 | 2016-10-30 | 4.7 | 13.3 | 0 | 11.84 | 0
2025-10-30 | 3.5 | 14.5 | 0 | 2024-10-30 | 18.9 | 0 | 0.9 | 2023-10-30 | 1.6 | 16.4 | 0 | 2022-10-30 | 12.7 | 5.3 | 0 | 2021-10-30 | 7 | 11 | 0 | 2020-10-30 | 0.9 | 17.1 | 0 | 2019-10-30 | 10.2 | 7.8 | 0 | 2018-10-30 | 2.5 | 15.5 | 0 | 2017-10-30 | 5.9 | 12.1 | 0 | 2016-10-30 | 5 | 13 | 0 | 11.27 | 0.09
2025-10-30 | 3.6 | 14.4 | 0 | 2024-10-30 | 20.8 | 0 | 2.8 | 2023-10-30 | 2 | 16 | 0 | 2022-10-30 | 14.2 | 3.8 | 0 | 2021-10-30 | 6.9 | 11.1 | 0 | 2020-10-30 | 2.2 | 15.8 | 0 | 2019-10-30 | 9.2 | 8.8 | 0 | 2018-10-30 | 3.4 | 14.6 | 0 | 2017-10-30 | 6.7 | 11.3 | 0 | 2016-10-30 | 4.8 | 13.2 | 0 | 10.9 | 0.28
2025-10-30 | 4.2 | 13.8 | 0 | 2024-10-30 | 21.4 | 0 | 3.4 | 2023-10-30 | 2.9 | 15.1 | 0 | 2022-10-30 | 15.6 | 2.4 | 0 | 2021-10-30 | 7.2 | 10.8 | 0 | 2020-10-30 | 3.2 | 14.8 | 0 | 2019-10-30 | 9.3 | 8.7 | 0 | 2018-10-30 | 5.5 | 12.5 | 0 | 2017-10-30 | 8.8 | 9.2 | 0 | 2016-10-30 | 5 | 13 | 0 | 10.03 | 0.34
2025-10-30 | 4.5 | 13.5 | 0 | 2024-10-30 | 22 | 0 | 4 | 2023-10-30 | 3.5 | 14.5 | 0 | 2022-10-30 | 16.2 | 1.8 | 0 | 2021-10-30 | 8.1 | 9.9 | 0 | 2020-10-30 | 3.4 | 14.6 | 0 | 2019-10-30 | 8.9 | 9.1 | 0 | 2018-10-30 | 6 | 12 | 0 | 2017-10-30 | 9.7 | 8.3 | 0 | 2016-10-30 | 5.2 | 12.8 | 0 | 9.65 | 0.4
2025-10-30 | 4.7 | 13.3 | 0 | 2024-10-30 | 21.8 | 0 | 3.8 | 2023-10-30 | 4 | 14 | 0 | 2022-10-30 | 17.1 | 0.9 | 0 | 2021-10-30 | 8.6 | 9.4 | 0 | 2020-10-30 | 3.8 | 14.2 | 0 | 2019-10-30 | 8.7 | 9.3 | 0 | 2018-10-30 | 6.7 | 11.3 | 0 | 2017-10-30 | 9.9 | 8.1 | 0 | 2016-10-30 | 5.2 | 12.8 | 0 | 9.33 | 0.38
2025-10-30 | 4.6 | 13.4 | 0 | 2024-10-30 | 20.6 | 0 | 2.6 | 2023-10-30 | 3.9 | 14.1 | 0 | 2022-10-30 | 15.6 | 2.4 | 0 | 2021-10-30 | 8.4 | 9.6 | 0 | 2020-10-30 | 2.9 | 15.1 | 0 | 2019-10-30 | 8.5 | 9.5 | 0 | 2018-10-30 | 6.2 | 11.8 | 0 | 2017-10-30 | 9.1 | 8.9 | 0 | 2016-10-30 | 5.2 | 12.8 | 0 | 9.76 | 0.26
2025-10-30 | 4.5 | 13.5 | 0 | 2024-10-30 | 20.3 | 0 | 2.3 | 2023-10-30 | 3.3 | 14.7 | 0 | 2022-10-30 | 13 | 5 | 0 | 2021-10-30 | 8.6 | 9.4 | 0 | 2020-10-30 | 0.2 | 17.8 | 0 | 2019-10-30 | 8.1 | 9.9 | 0 | 2018-10-30 | 4.5 | 13.5 | 0 | 2017-10-30 | 7.4 | 10.6 | 0 | 2016-10-30 | 4.7 | 13.3 | 0 | 10.77 | 0.23
2025-10-30 | 4.5 | 13.5 | 0 | 2024-10-30 | 20 | 0 | 2 | 2023-10-30 | 1.9 | 16.1 | 0 | 2022-10-30 | 11.9 | 6.1 | 0 | 2021-10-30 | 8.8 | 9.2 | 0 | 2020-10-30 | -0.1 | 18.1 | 0 | 2019-10-30 | 7.9 | 10.1 | 0 | 2018-10-30 | 3.3 | 14.7 | 0 | 2017-10-30 | 7.7 | 10.3 | 0 | 2016-10-30 | 4 | 14 | 0 | 11.21 | 0.2
2025-10-30 | 4.8 | 13.2 | 0 | 2024-10-30 | 19.3 | 0 | 1.3 | 2023-10-30 | 1.1 | 16.9 | 0 | 2022-10-30 | 11.8 | 6.2 | 0 | 2021-10-30 | 8.7 | 9.3 | 0 | 2020-10-30 | -1.4 | 19.4 | 0 | 2019-10-30 | 7.5 | 10.5 | 0 | 2018-10-30 | 2.6 | 15.4 | 0 | 2017-10-30 | 7.2 | 10.8 | 0 | 2016-10-30 | 3.8 | 14.2 | 0 | 11.59 | 0.13
2025-10-30 | 5.4 | 12.6 | 0 | 2024-10-30 | 19.2 | 0 | 1.2 | 2023-10-30 | -0.1 | 18.1 | 0 | 2022-10-30 | 9.3 | 8.7 | 0 | 2021-10-30 | 8.5 | 9.5 | 0 | 2020-10-30 | -2.4 | 20.4 | 0 | 2019-10-30 | 7.2 | 10.8 | 0 | 2018-10-30 | 2.7 | 15.3 | 0 | 2017-10-30 | 6.2 | 11.8 | 0 | 2016-10-30 | 3.8 | 14.2 | 0 | 12.14 | 0.12
2025-10-30 | 5.7 | 12.3 | 0 | 2024-10-30 | 18.6 | 0 | 0.6 | 2023-10-30 | -0.5 | 18.5 | 0 | 2022-10-30 | 8.5 | 9.5 | 0 | 2021-10-30 | 8.9 | 9.1 | 0 | 2020-10-30 | -3.7 | 21.7 | 0 | 2019-10-30 | 7.3 | 10.7 | 0 | 2018-10-30 | 0.5 | 17.5 | 0 | 2017-10-30 | 6.6 | 11.4 | 0 | 2016-10-30 | 3.9 | 14.1 | 0 | 12.48 | 0.06
2025-10-30 | 6 | 12 | 0 | 2024-10-30 | 18.6 | 0 | 0.6 | 2023-10-30 | 0.1 | 17.9 | 0 | 2022-10-30 | 6.7 | 11.3 | 0 | 2021-10-30 | 8.8 | 9.2 | 0 | 2020-10-30 | -3.6 | 21.6 | 0 | 2019-10-30 | 7.3 | 10.7 | 0 | 2018-10-30 | 0.4 | 17.6 | 0 | 2017-10-30 | 6.2 | 11.8 | 0 | 2016-10-30 | 3.7 | 14.3 | 0 | 12.64 | 0.06
2025-10-30 | 6.3 | 11.7 | 0 | 2024-10-30 | 19.2 | 0 | 1.2 | 2023-10-30 | -1 | 19 | 0 | 2022-10-30 | 9.7 | 8.3 | 0 | 2021-10-30 | 8.9 | 9.1 | 0 | 2020-10-30 | -3.5 | 21.5 | 0 | 2019-10-30 | 7.3 | 10.7 | 0 | 2018-10-30 | 0.3 | 17.7 | 0 | 2017-10-30 | 6.2 | 11.8 | 0 | 2016-10-30 | 2.4 | 15.6 | 0 | 12.54 | 0.12
2025-10-31 | 6.3 | 11.7 | 0 | 2024-10-31 | 19.2 | 0 | 1.2 | 2023-10-31 | -1.5 | 19.5 | 0 | 2022-10-31 | 8 | 10 | 0 | 2021-10-31 | 9.1 | 8.9 | 0 | 2020-10-31 | -3.5 | 21.5 | 0 | 2019-10-31 | 7.3 | 10.7 | 0 | 2018-10-31 | 0.5 | 17.5 | 0 | 2017-10-31 | 5.6 | 12.4 | 0 | 2016-10-31 | 0.8 | 17.2 | 0 | 12.94 | 0.12
2025-10-31 | 6.7 | 11.3 | 0 | 2024-10-31 | 19.3 | 0 | 1.3 | 2023-10-31 | -1.5 | 19.5 | 0 | 2022-10-31 | 6.9 | 11.1 | 0 | 2021-10-31 | 8.9 | 9.1 | 0 | 2020-10-31 | -4.1 | 22.1 | 0 | 2019-10-31 | 7.4 | 10.6 | 0 | 2018-10-31 | 0.6 | 17.4 | 0 | 2017-10-31 | 5.1 | 12.9 | 0 | 2016-10-31 | 0.5 | 17.5 | 0 | 13.15 | 0.13
2025-10-31 | 7.1 | 10.9 | 0 | 2024-10-31 | 18.8 | 0 | 0.8 | 2023-10-31 | -2.8 | 20.8 | 0 | 2022-10-31 | 7.2 | 10.8 | 0 | 2021-10-31 | 8.8 | 9.2 | 0 | 2020-10-31 | -5.7 | 23.7 | 0 | 2019-10-31 | 7.8 | 10.2 | 0 | 2018-10-31 | 0.6 | 17.4 | 0 | 2017-10-31 | 5.2 | 12.8 | 0 | 2016-10-31 | 0.7 | 17.3 | 0 | 13.31 | 0.08
2025-10-31 | 7.2 | 10.8 | 0 | 2024-10-31 | 18.4 | 0 | 0.4 | 2023-10-31 | -2.2 | 20.2 | 0 | 2022-10-31 | 4.6 | 13.4 | 0 | 2021-10-31 | 8.8 | 9.2 | 0 | 2020-10-31 | -5.5 | 23.5 | 0 | 2019-10-31 | 8.3 | 9.7 | 0 | 2018-10-31 | 0.4 | 17.6 | 0 | 2017-10-31 | 5.9 | 12.1 | 0 | 2016-10-31 | -0.9 | 18.9 | 0 | 13.54 | 0.04
2025-10-31 | 7.3 | 10.7 | 0 | 2024-10-31 | 16.5 | 1.5 | 0 | 2023-10-31 | -2.6 | 20.6 | 0 | 2022-10-31 | 5.6 | 12.4 | 0 | 2021-10-31 | 8.7 | 9.3 | 0 | 2020-10-31 | -6 | 24 | 0 | 2019-10-31 | 8.8 | 9.2 | 0 | 2018-10-31 | 0.6 | 17.4 | 0 | 2017-10-31 | 5.7 | 12.3 | 0 | 2016-10-31 | -1.3 | 19.3 | 0 | 13.67 | 0
2025-10-31 | 6.8 | 11.2 | 0 | 2024-10-31 | 15.6 | 2.4 | 0 | 2023-10-31 | -3.6 | 21.6 | 0 | 2022-10-31 | 6.5 | 11.5 | 0 | 2021-10-31 | 8.6 | 9.4 | 0 | 2020-10-31 | -6.7 | 24.7 | 0 | 2019-10-31 | 8.6 | 9.4 | 0 | 2018-10-31 | 1.1 | 16.9 | 0 | 2017-10-31 | 5.5 | 12.5 | 0 | 2016-10-31 | 0.8 | 17.2 | 0 | 13.68 | 0
2025-10-31 | 6.6 | 11.4 | 0 | 2024-10-31 | 14.7 | 3.3 | 0 | 2023-10-31 | -3.4 | 21.4 | 0 | 2022-10-31 | 6.7 | 11.3 | 0 | 2021-10-31 | 8.4 | 9.6 | 0 | 2020-10-31 | -6.8 | 24.8 | 0 | 2019-10-31 | 8.3 | 9.7 | 0 | 2018-10-31 | 0.6 | 17.4 | 0 | 2017-10-31 | 4.8 | 13.2 | 0 | 2016-10-31 | 1.1 | 16.9 | 0 | 13.9 | 0
2025-10-31 | 6.3 | 11.7 | 0 | 2024-10-31 | 14.6 | 3.4 | 0 | 2023-10-31 | -4.3 | 22.3 | 0 | 2022-10-31 | 4.7 | 13.3 | 0 | 2021-10-31 | 8.4 | 9.6 | 0 | 2020-10-31 | -6.3 | 24.3 | 0 | 2019-10-31 | 8.4 | 9.6 | 0 | 2018-10-31 | 0.8 | 17.2 | 0 | 2017-10-31 | 4.6 | 13.4 | 0 | 2016-10-31 | 1.6 | 16.4 | 0 | 14.12 | 0
2025-10-31 | 6.5 | 11.5 | 0 | 2024-10-31 | 16.4 | 1.6 | 0 | 2023-10-31 | -1.6 | 19.6 | 0 | 2022-10-31 | 6.8 | 11.2 | 0 | 2021-10-31 | 8.7 | 9.3 | 0 | 2020-10-31 | -4.1 | 22.1 | 0 | 2019-10-31 | 8.8 | 9.2 | 0 | 2018-10-31 | 0.9 | 17.1 | 0 | 2017-10-31 | 5.7 | 12.3 | 0 | 2016-10-31 | 2.1 | 15.9 | 0 | 12.98 | 0
2025-10-31 | 6.5 | 11.5 | 0 | 2024-10-31 | 18.3 | 0 | 0.3 | 2023-10-31 | -0.4 | 18.4 | 0 | 2022-10-31 | 9 | 9 | 0 | 2021-10-31 | 9.1 | 8.9 | 0 | 2020-10-31 | -1.6 | 19.6 | 0 | 2019-10-31 | 8.9 | 9.1 | 0 | 2018-10-31 | 1.4 | 16.6 | 0 | 2017-10-31 | 6 | 12 | 0 | 2016-10-31 | 2.4 | 15.6 | 0 | 12.07 | 0.03
2025-10-31 | 6.2 | 11.8 | 0 | 2024-10-31 | 19.9 | 0 | 1.9 | 2023-10-31 | 0.8 | 17.2 | 0 | 2022-10-31 | 11 | 7 | 0 | 2021-10-31 | 9.6 | 8.4 | 0 | 2020-10-31 | 0.5 | 17.5 | 0 | 2019-10-31 | 9 | 9 | 0 | 2018-10-31 | 1.7 | 16.3 | 0 | 2017-10-31 | 7 | 11 | 0 | 2016-10-31 | 2.6 | 15.4 | 0 | 11.36 | 0.19
2025-10-31 | 6.2 | 11.8 | 0 | 2024-10-31 | 20.9 | 0 | 2.9 | 2023-10-31 | 1.9 | 16.1 | 0 | 2022-10-31 | 11.9 | 6.1 | 0 | 2021-10-31 | 9.8 | 8.2 | 0 | 2020-10-31 | 2.4 | 15.6 | 0 | 2019-10-31 | 9.3 | 8.7 | 0 | 2018-10-31 | 2.1 | 15.9 | 0 | 2017-10-31 | 8 | 10 | 0 | 2016-10-31 | 2.8 | 15.2 | 0 | 10.76 | 0.29
2025-10-31 | 5.9 | 12.1 | 0 | 2024-10-31 | 22.6 | 0 | 4.6 | 2023-10-31 | 1.9 | 16.1 | 0 | 2022-10-31 | 13.3 | 4.7 | 0 | 2021-10-31 | 10.2 | 7.8 | 0 | 2020-10-31 | 3.4 | 14.6 | 0 | 2019-10-31 | 9.4 | 8.6 | 0 | 2018-10-31 | 2.2 | 15.8 | 0 | 2017-10-31 | 8 | 10 | 0 | 2016-10-31 | 3 | 15 | 0 | 10.47 | 0.46
2025-10-31 | 5 | 13 | 0 | 2024-10-31 | 23.5 | 0 | 5.5 | 2023-10-31 | 2.1 | 15.9 | 0 | 2022-10-31 | 14 | 4 | 0 | 2021-10-31 | 10.4 | 7.6 | 0 | 2020-10-31 | 4.8 | 13.2 | 0 | 2019-10-31 | 8.8 | 9.2 | 0 | 2018-10-31 | 2.6 | 15.4 | 0 | 2017-10-31 | 8.6 | 9.4 | 0 | 2016-10-31 | 3.1 | 14.9 | 0 | 10.26 | 0.55
2025-10-31 | 3.8 | 14.2 | 0 | 2024-10-31 | 22.2 | 0 | 4.2 | 2023-10-31 | 3.6 | 14.4 | 0 | 2022-10-31 | 14.2 | 3.8 | 0 | 2021-10-31 | 10.6 | 7.4 | 0 | 2020-10-31 | 5.7 | 12.3 | 0 | 2019-10-31 | 8.5 | 9.5 | 0 | 2018-10-31 | 2.8 | 15.2 | 0 | 2017-10-31 | 9.2 | 8.8 | 0 | 2016-10-31 | 3.4 | 14.6 | 0 | 10.02 | 0.42
2025-10-31 | 3 | 15 | 0 | 2024-10-31 | 21.8 | 0 | 3.8 | 2023-10-31 | 2.8 | 15.2 | 0 | 2022-10-31 | 14.2 | 3.8 | 0 | 2021-10-31 | 10.3 | 7.7 | 0 | 2020-10-31 | 5.9 | 12.1 | 0 | 2019-10-31 | 8.1 | 9.9 | 0 | 2018-10-31 | 3 | 15 | 0 | 2017-10-31 | 8.9 | 9.1 | 0 | 2016-10-31 | 3 | 15 | 0 | 10.28 | 0.38
2025-10-31 | 2.9 | 15.1 | 0 | 2024-10-31 | 21.6 | 0 | 3.6 | 2023-10-31 | 1.8 | 16.2 | 0 | 2022-10-31 | 13.2 | 4.8 | 0 | 2021-10-31 | 10.4 | 7.6 | 0 | 2020-10-31 | 5.3 | 12.7 | 0 | 2019-10-31 | 7.9 | 10.1 | 0 | 2018-10-31 | 3.1 | 14.9 | 0 | 2017-10-31 | 7.4 | 10.6 | 0 | 2016-10-31 | 2.6 | 15.4 | 0 | 10.74 | 0.36
2025-10-31 | 3.2 | 14.8 | 0 | 2024-10-31 | 21.4 | 0 | 3.4 | 2023-10-31 | 1.4 | 16.6 | 0 | 2022-10-31 | 12.1 | 5.9 | 0 | 2021-10-31 | 10.4 | 7.6 | 0 | 2020-10-31 | 3 | 15 | 0 | 2019-10-31 | 7.3 | 10.7 | 0 | 2018-10-31 | 3 | 15 | 0 | 2017-10-31 | 5.7 | 12.3 | 0 | 2016-10-31 | 1.9 | 16.1 | 0 | 11.4 | 0.34
2025-10-31 | 3.8 | 14.2 | 0 | 2024-10-31 | 21.7 | 0 | 3.7 | 2023-10-31 | 0.8 | 17.2 | 0 | 2022-10-31 | 12.1 | 5.9 | 0 | 2021-10-31 | 10.8 | 7.2 | 0 | 2020-10-31 | 1.8 | 16.2 | 0 | 2019-10-31 | 7.2 | 10.8 | 0 | 2018-10-31 | 3.1 | 14.9 | 0 | 2017-10-31 | 4.2 | 13.8 | 0 | 2016-10-31 | 0.4 | 17.6 | 0 | 11.78 | 0.37
2025-10-31 | 4.2 | 13.8 | 0 | 2024-10-31 | 21 | 0 | 3 | 2023-10-31 | 0.7 | 17.3 | 0 | 2022-10-31 | 12.1 | 5.9 | 0 | 2021-10-31 | 10 | 8 | 0 | 2020-10-31 | 3.4 | 14.6 | 0 | 2019-10-31 | 7.9 | 10.1 | 0 | 2018-10-31 | 3 | 15 | 0 | 2017-10-31 | 2.9 | 15.1 | 0 | 2016-10-31 | 0.5 | 17.5 | 0 | 11.73 | 0.3
2025-10-31 | 4.4 | 13.6 | 0 | 2024-10-31 | 18 | 0 | 0 | 2023-10-31 | 0.6 | 17.4 | 0 | 2022-10-31 | 11.9 | 6.1 | 0 | 2021-10-31 | 9.5 | 8.5 | 0 | 2020-10-31 | 2.2 | 15.8 | 0 | 2019-10-31 | 7.6 | 10.4 | 0 | 2018-10-31 | 3 | 15 | 0 | 2017-10-31 | 1.8 | 16.2 | 0 | 2016-10-31 | -2.5 | 20.5 | 0 | 12.35 | 0
2025-10-31 | 4.6 | 13.4 | 0 | 2024-10-31 | 17.7 | 0.3 | 0 | 2023-10-31 | 0.4 | 17.6 | 0 | 2022-10-31 | 10.6 | 7.4 | 0 | 2021-10-31 | 8.8 | 9.2 | 0 | 2020-10-31 | 0.8 | 17.2 | 0 | 2019-10-31 | 8.3 | 9.7 | 0 | 2018-10-31 | 3.3 | 14.7 | 0 | 2017-10-31 | 1.5 | 16.5 | 0 | 2016-10-31 | -1 | 19 | 0 | 12.5 | 0
2025-10-31 | 4.5 | 13.5 | 0 | 2024-10-31 | 17.4 | 0.6 | 0 | 2023-10-31 | 0.7 | 17.3 | 0 | 2022-10-31 | 9.9 | 8.1 | 0 | 2021-10-31 | 8.1 | 9.9 | 0 | 2020-10-31 | 1.6 | 16.4 | 0 | 2019-10-31 | 9.1 | 8.9 | 0 | 2018-10-31 | 3.5 | 14.5 | 0 | 2017-10-31 | 1.8 | 16.2 | 0 | 2016-10-31 | -2.8 | 20.8 | 0 | 12.62 | 0
2025-10-31 | 4.5 | 13.5 | 0 | 2024-10-31 | 17.8 | 0.2 | 0 | 2023-10-31 | 0.7 | 17.3 | 0 | 2022-10-31 | 9.8 | 8.2 | 0 | 2021-10-31 | 7.6 | 10.4 | 0 | 2020-10-31 | -0.2 | 18.2 | 0 | 2019-10-31 | 8.5 | 9.5 | 0 | 2018-10-31 | 3.5 | 14.5 | 0 | 2017-10-31 | 1.1 | 16.9 | 0 | 2016-10-31 | -1.8 | 19.8 | 0 | 12.85 | 0
2025-11-01 | 4.8 | 13.2 | 0 | 2024-11-01 | 17.3 | 0.7 | 0 | 2023-11-01 | -0.2 | 18.2 | 0 | 2022-11-01 | 9.8 | 8.2 | 0 | 2021-11-01 | 7.4 | 10.6 | 0 | 2020-11-01 | -1 | 19 | 0 | 2019-11-01 | 7 | 11 | 0 | 2018-11-01 | 3.6 | 14.4 | 0 | 2017-11-01 | 1.1 | 16.9 | 0 | 2016-11-01 | -1.8 | 19.8 | 0 | 13.2 | 0
2025-11-01 | 4.9 | 13.1 | 0 | 2024-11-01 | 16.5 | 1.5 | 0 | 2023-11-01 | -1.2 | 19.2 | 0 | 2022-11-01 | 9.8 | 8.2 | 0 | 2021-11-01 | 7.7 | 10.3 | 0 | 2020-11-01 | 0.1 | 17.9 | 0 | 2019-11-01 | 8.4 | 9.6 | 0 | 2018-11-01 | 2.4 | 15.6 | 0 | 2017-11-01 | 0.7 | 17.3 | 0 | 2016-11-01 | -3.6 | 21.6 | 0 | 13.43 | 0
2025-11-01 | 4.9 | 13.1 | 0 | 2024-11-01 | 16.3 | 1.7 | 0 | 2023-11-01 | -1.4 | 19.4 | 0 | 2022-11-01 | 9.6 | 8.4 | 0 | 2021-11-01 | 8.3 | 9.7 | 0 | 2020-11-01 | 0.8 | 17.2 | 0 | 2019-11-01 | 7.9 | 10.1 | 0 | 2018-11-01 | 3.1 | 14.9 | 0 | 2017-11-01 | -0.5 | 18.5 | 0 | 2016-11-01 | -1.4 | 19.4 | 0 | 13.24 | 0
2025-11-01 | 4.4 | 13.6 | 0 | 2024-11-01 | 15.6 | 2.4 | 0 | 2023-11-01 | -1.1 | 19.1 | 0 | 2022-11-01 | 9.5 | 8.5 | 0 | 2021-11-01 | 8.5 | 9.5 | 0 | 2020-11-01 | 1.4 | 16.6 | 0 | 2019-11-01 | 6.6 | 11.4 | 0 | 2018-11-01 | 3.6 | 14.4 | 0 | 2017-11-01 | -1.7 | 19.7 | 0 | 2016-11-01 | -2.4 | 20.4 | 0 | 13.56 | 0
2025-11-01 | 3.3 | 14.7 | 0 | 2024-11-01 | 14.6 | 3.4 | 0 | 2023-11-01 | -1.5 | 19.5 | 0 | 2022-11-01 | 9.5 | 8.5 | 0 | 2021-11-01 | 6.1 | 11.9 | 0 | 2020-11-01 | 1.3 | 16.7 | 0 | 2019-11-01 | 6 | 12 | 0 | 2018-11-01 | 3.9 | 14.1 | 0 | 2017-11-01 | -0.9 | 18.9 | 0 | 2016-11-01 | -2 | 20 | 0 | 13.97 | 0
2025-11-01 | 3.3 | 14.7 | 0 | 2024-11-01 | 14.7 | 3.3 | 0 | 2023-11-01 | -1.8 | 19.8 | 0 | 2022-11-01 | 9.6 | 8.4 | 0 | 2021-11-01 | 5.2 | 12.8 | 0 | 2020-11-01 | 1.9 | 16.1 | 0 | 2019-11-01 | 5.6 | 12.4 | 0 | 2018-11-01 | 3.5 | 14.5 | 0 | 2017-11-01 | -0.5 | 18.5 | 0 | 2016-11-01 | -1.9 | 19.9 | 0 | 14.04 | 0
2025-11-01 | 2.9 | 15.1 | 0 | 2024-11-01 | 14.3 | 3.7 | 0 | 2023-11-01 | -1.8 | 19.8 | 0 | 2022-11-01 | 9.9 | 8.1 | 0 | 2021-11-01 | 4.4 | 13.6 | 0 | 2020-11-01 | 2.2 | 15.8 | 0 | 2019-11-01 | 3.8 | 14.2 | 0 | 2018-11-01 | 3.4 | 14.6 | 0 | 2017-11-01 | 0.9 | 17.1 | 0 | 2016-11-01 | -1.9 | 19.9 | 0 | 14.19 | 0
2025-11-01 | 2.7 | 15.3 | 0 | 2024-11-01 | 13.8 | 4.2 | 0 | 2023-11-01 | -2 | 20 | 0 | 2022-11-01 | 10 | 8 | 0 | 2021-11-01 | 3.8 | 14.2 | 0 | 2020-11-01 | 2.8 | 15.2 | 0 | 2019-11-01 | 2.8 | 15.2 | 0 | 2018-11-01 | 2.6 | 15.4 | 0 | 2017-11-01 | 1.4 | 16.6 | 0 | 2016-11-01 | -1.1 | 19.1 | 0 | 14.32 | 0
2025-11-01 | 3.5 | 14.5 | 0 | 2024-11-01 | 12.8 | 5.2 | 0 | 2023-11-01 | -1.8 | 19.8 | 0 | 2022-11-01 | 10.6 | 7.4 | 0 | 2021-11-01 | 5 | 13 | 0 | 2020-11-01 | 3.7 | 14.3 | 0 | 2019-11-01 | 2.4 | 15.6 | 0 | 2018-11-01 | 3.5 | 14.5 | 0 | 2017-11-01 | 2.5 | 15.5 | 0 | 2016-11-01 | -0.4 | 18.4 | 0 | 13.82 | 0
2025-11-01 | 4.5 | 13.5 | 0 | 2024-11-01 | 11.2 | 6.8 | 0 | 2023-11-01 | -0.8 | 18.8 | 0 | 2022-11-01 | 11.5 | 6.5 | 0 | 2021-11-01 | 6.5 | 11.5 | 0 | 2020-11-01 | 4.3 | 13.7 | 0 | 2019-11-01 | 2.3 | 15.7 | 0 | 2018-11-01 | 3.9 | 14.1 | 0 | 2017-11-01 | 2.9 | 15.1 | 0 | 2016-11-01 | 1.8 | 16.2 | 0 | 13.19 | 0
2025-11-01 | 4.4 | 13.6 | 0 | 2024-11-01 | 10.3 | 7.7 | 0 | 2023-11-01 | -0.6 | 18.6 | 0 | 2022-11-01 | 12 | 6 | 0 | 2021-11-01 | 8 | 10 | 0 | 2020-11-01 | 6.7 | 11.3 | 0 | 2019-11-01 | 3.1 | 14.9 | 0 | 2018-11-01 | 5 | 13 | 0 | 2017-11-01 | 3.1 | 14.9 | 0 | 2016-11-01 | 3.8 | 14.2 | 0 | 12.42 | 0
2025-11-01 | 4.6 | 13.4 | 0 | 2024-11-01 | 12 | 6 | 0 | 2023-11-01 | 0 | 18 | 0 | 2022-11-01 | 12.8 | 5.2 | 0 | 2021-11-01 | 9.6 | 8.4 | 0 | 2020-11-01 | 7.8 | 10.2 | 0 | 2019-11-01 | 3.5 | 14.5 | 0 | 2018-11-01 | 5.7 | 12.3 | 0 | 2017-11-01 | 4.3 | 13.7 | 0 | 2016-11-01 | 6 | 12 | 0 | 11.37 | 0
2025-11-01 | 5.4 | 12.6 | 0 | 2024-11-01 | 11.2 | 6.8 | 0 | 2023-11-01 | 0.4 | 17.6 | 0 | 2022-11-01 | 15.2 | 2.8 | 0 | 2021-11-01 | 10.1 | 7.9 | 0 | 2020-11-01 | 6.5 | 11.5 | 0 | 2019-11-01 | 3.8 | 14.2 | 0 | 2018-11-01 | 6.4 | 11.6 | 0 | 2017-11-01 | 4.7 | 13.3 | 0 | 2016-11-01 | 7.3 | 10.7 | 0 | 10.9 | 0
2025-11-01 | 5.2 | 12.8 | 0 | 2024-11-01 | 11.2 | 6.8 | 0 | 2023-11-01 | 0.6 | 17.4 | 0 | 2022-11-01 | 15.2 | 2.8 | 0 | 2021-11-01 | 10.6 | 7.4 | 0 | 2020-11-01 | 6.7 | 11.3 | 0 | 2019-11-01 | 3.3 | 14.7 | 0 | 2018-11-01 | 7 | 11 | 0 | 2017-11-01 | 5 | 13 | 0 | 2016-11-01 | 7.8 | 10.2 | 0 | 10.74 | 0
2025-11-01 | 5.6 | 12.4 | 0 | 2024-11-01 | 11.2 | 6.8 | 0 | 2023-11-01 | 0.6 | 17.4 | 0 | 2022-11-01 | 15.1 | 2.9 | 0 | 2021-11-01 | 11.1 | 6.9 | 0 | 2020-11-01 | 7.1 | 10.9 | 0 | 2019-11-01 | 3.1 | 14.9 | 0 | 2018-11-01 | 7.3 | 10.7 | 0 | 2017-11-01 | 5.8 | 12.2 | 0 | 2016-11-01 | 8.7 | 9.3 | 0 | 10.44 | 0
2025-11-01 | 5.6 | 12.4 | 0 | 2024-11-01 | 10 | 8 | 0 | 2023-11-01 | 1 | 17 | 0 | 2022-11-01 | 15.7 | 2.3 | 0 | 2021-11-01 | 9.6 | 8.4 | 0 | 2020-11-01 | 7.2 | 10.8 | 0 | 2019-11-01 | 2.7 | 15.3 | 0 | 2018-11-01 | 7.3 | 10.7 | 0 | 2017-11-01 | 6.1 | 11.9 | 0 | 2016-11-01 | 8.2 | 9.8 | 0 | 10.66 | 0
2025-11-01 | 5.5 | 12.5 | 0 | 2024-11-01 | 8.6 | 9.4 | 0 | 2023-11-01 | 1 | 17 | 0 | 2022-11-01 | 15.2 | 2.8 | 0 | 2021-11-01 | 9 | 9 | 0 | 2020-11-01 | 7.5 | 10.5 | 0 | 2019-11-01 | 2.3 | 15.7 | 0 | 2018-11-01 | 6.9 | 11.1 | 0 | 2017-11-01 | 5.6 | 12.4 | 0 | 2016-11-01 | 8.4 | 9.6 | 0 | 11 | 0
2025-11-01 | 4.3 | 13.7 | 0 | 2024-11-01 | 7.6 | 10.4 | 0 | 2023-11-01 | 0.8 | 17.2 | 0 | 2022-11-01 | 12 | 6 | 0 | 2021-11-01 | 6.7 | 11.3 | 0 | 2020-11-01 | 6.8 | 11.2 | 0 | 2019-11-01 | 1.8 | 16.2 | 0 | 2018-11-01 | 6.6 | 11.4 | 0 | 2017-11-01 | 5.2 | 12.8 | 0 | 2016-11-01 | 7.9 | 10.1 | 0 | 12.03 | 0
2025-11-01 | 2.9 | 15.1 | 0 | 2024-11-01 | 6.7 | 11.3 | 0 | 2023-11-01 | 0.5 | 17.5 | 0 | 2022-11-01 | 10.2 | 7.8 | 0 | 2021-11-01 | 5.5 | 12.5 | 0 | 2020-11-01 | 6.1 | 11.9 | 0 | 2019-11-01 | 1.6 | 16.4 | 0 | 2018-11-01 | 5.8 | 12.2 | 0 | 2017-11-01 | 4.4 | 13.6 | 0 | 2016-11-01 | 7.7 | 10.3 | 0 | 12.86 | 0
2025-11-01 | 3 | 15 | 0 | 2024-11-01 | 5.8 | 12.2 | 0 | 2023-11-01 | 0 | 18 | 0 | 2022-11-01 | 10.6 | 7.4 | 0 | 2021-11-01 | 4.6 | 13.4 | 0 | 2020-11-01 | 4.2 | 13.8 | 0 | 2019-11-01 | 1.1 | 16.9 | 0 | 2018-11-01 | 5.8 | 12.2 | 0 | 2017-11-01 | 4.2 | 13.8 | 0 | 2016-11-01 | 7.8 | 10.2 | 0 | 13.29 | 0
2025-11-01 | 2.8 | 15.2 | 0 | 2024-11-01 | 5.7 | 12.3 | 0 | 2023-11-01 | 0.1 | 17.9 | 0 | 2022-11-01 | 11.2 | 6.8 | 0 | 2021-11-01 | 3.9 | 14.1 | 0 | 2020-11-01 | 3.4 | 14.6 | 0 | 2019-11-01 | 0.3 | 17.7 | 0 | 2018-11-01 | 5.5 | 12.5 | 0 | 2017-11-01 | 4.1 | 13.9 | 0 | 2016-11-01 | 7.7 | 10.3 | 0 | 13.53 | 0
2025-11-01 | 3.3 | 14.7 | 0 | 2024-11-01 | 5.2 | 12.8 | 0 | 2023-11-01 | -0.4 | 18.4 | 0 | 2022-11-01 | 8.1 | 9.9 | 0 | 2021-11-01 | 3.3 | 14.7 | 0 | 2020-11-01 | 2.7 | 15.3 | 0 | 2019-11-01 | -1.9 | 19.9 | 0 | 2018-11-01 | 5.2 | 12.8 | 0 | 2017-11-01 | 4.1 | 13.9 | 0 | 2016-11-01 | 6.4 | 11.6 | 0 | 14.4 | 0
2025-11-01 | 3.4 | 14.6 | 0 | 2024-11-01 | 4.7 | 13.3 | 0 | 2023-11-01 | -1.2 | 19.2 | 0 | 2022-11-01 | 7.2 | 10.8 | 0 | 2021-11-01 | 2.5 | 15.5 | 0 | 2020-11-01 | 1.9 | 16.1 | 0 | 2019-11-01 | -1.4 | 19.4 | 0 | 2018-11-01 | 5 | 13 | 0 | 2017-11-01 | 4.1 | 13.9 | 0 | 2016-11-01 | 9.3 | 8.7 | 0 | 14.45 | 0
2025-11-01 | 3.5 | 14.5 | 0 | 2024-11-01 | 3.8 | 14.2 | 0 | 2023-11-01 | -1.6 | 19.6 | 0 | 2022-11-01 | 8.3 | 9.7 | 0 | 2021-11-01 | 1.7 | 16.3 | 0 | 2020-11-01 | 1.6 | 16.4 | 0 | 2019-11-01 | -3.1 | 21.1 | 0 | 2018-11-01 | 4.8 | 13.2 | 0 | 2017-11-01 | 4 | 14 | 0 | 2016-11-01 | 8.3 | 9.7 | 0 | 14.87 | 0
2025-11-02 | 3.4 | 14.6 | 0 | 2024-11-02 | 3.6 | 14.4 | 0 | 2023-11-02 | -2.1 | 20.1 | 0 | 2022-11-02 | 8 | 10 | 0 | 2021-11-02 | 1.6 | 16.4 | 0 | 2020-11-02 | 1.7 | 16.3 | 0 | 2019-11-02 | -2.8 | 20.8 | 0 | 2018-11-02 | 4.7 | 13.3 | 0 | 2017-11-02 | 4.1 | 13.9 | 0 | 2016-11-02 | 7 | 11 | 0 | 15.08 | 0
2025-11-02 | 3.1 | 14.9 | 0 | 2024-11-02 | 3.4 | 14.6 | 0 | 2023-11-02 | -2.8 | 20.8 | 0 | 2022-11-02 | 6.8 | 11.2 | 0 | 2021-11-02 | 1.1 | 16.9 | 0 | 2020-11-02 | 2 | 16 | 0 | 2019-11-02 | -3.2 | 21.2 | 0 | 2018-11-02 | 4.2 | 13.8 | 0 | 2017-11-02 | 4.2 | 13.8 | 0 | 2016-11-02 | 6.6 | 11.4 | 0 | 15.46 | 0
2025-11-02 | 3.3 | 14.7 | 0 | 2024-11-02 | 2.8 | 15.2 | 0 | 2023-11-02 | -3.4 | 21.4 | 0 | 2022-11-02 | 7.8 | 10.2 | 0 | 2021-11-02 | -1 | 19 | 0 | 2020-11-02 | 1 | 17 | 0 | 2019-11-02 | -2.5 | 20.5 | 0 | 2018-11-02 | 3.3 | 14.7 | 0 | 2017-11-02 | 4.3 | 13.7 | 0 | 2016-11-02 | 7.4 | 10.6 | 0 | 15.7 | 0
2025-11-02 | 3 | 15 | 0 | 2024-11-02 | 2.3 | 15.7 | 0 | 2023-11-02 | -2.9 | 20.9 | 0 | 2022-11-02 | 6.4 | 11.6 | 0 | 2021-11-02 | 0.1 | 17.9 | 0 | 2020-11-02 | 0.1 | 17.9 | 0 | 2019-11-02 | -2 | 20 | 0 | 2018-11-02 | 3 | 15 | 0 | 2017-11-02 | 4.5 | 13.5 | 0 | 2016-11-02 | 7.9 | 10.1 | 0 | 15.76 | 0
2025-11-02 | 3.6 | 14.4 | 0 | 2024-11-02 | 1.3 | 16.7 | 0 | 2023-11-02 | -2 | 20 | 0 | 2022-11-02 | 4.8 | 13.2 | 0 | 2021-11-02 | 0.7 | 17.3 | 0 | 2020-11-02 | -0.9 | 18.9 | 0 | 2019-11-02 | -1.2 | 19.2 | 0 | 2018-11-02 | 3 | 15 | 0 | 2017-11-02 | 4.8 | 13.2 | 0 | 2016-11-02 | 6.1 | 11.9 | 0 | 15.98 | 0
2025-11-02 | 2.8 | 15.2 | 0 | 2024-11-02 | 0.9 | 17.1 | 0 | 2023-11-02 | -1.8 | 19.8 | 0 | 2022-11-02 | 4.4 | 13.6 | 0 | 2021-11-02 | 0.5 | 17.5 | 0 | 2020-11-02 | -1.1 | 19.1 | 0 | 2019-11-02 | -1.3 | 19.3 | 0 | 2018-11-02 | 2.2 | 15.8 | 0 | 2017-11-02 | 5 | 13 | 0 | 2016-11-02 | 6.5 | 11.5 | 0 | 16.19 | 0
2025-11-02 | 2.8 | 15.2 | 0 | 2024-11-02 | 1.4 | 16.6 | 0 | 2023-11-02 | -1.8 | 19.8 | 0 | 2022-11-02 | 5 | 13 | 0 | 2021-11-02 | -0.1 | 18.1 | 0 | 2020-11-02 | -1.1 | 19.1 | 0 | 2019-11-02 | -0.8 | 18.8 | 0 | 2018-11-02 | 2.2 | 15.8 | 0 | 2017-11-02 | 5.3 | 12.7 | 0 | 2016-11-02 | 7.3 | 10.7 | 0 | 15.98 | 0
2025-11-02 | 2.6 | 15.4 | 0 | 2024-11-02 | 1.3 | 16.7 | 0 | 2023-11-02 | -1.4 | 19.4 | 0 | 2022-11-02 | 4.2 | 13.8 | 0 | 2021-11-02 | -0.2 | 18.2 | 0 | 2020-11-02 | -1.6 | 19.6 | 0 | 2019-11-02 | -1.1 | 19.1 | 0 | 2018-11-02 | 2.8 | 15.2 | 0 | 2017-11-02 | 5.5 | 12.5 | 0 | 2016-11-02 | 7.6 | 10.4 | 0 | 16.03 | 0
2025-11-02 | 3.1 | 14.9 | 0 | 2024-11-02 | 1.6 | 16.4 | 0 | 2023-11-02 | -0.2 | 18.2 | 0 | 2022-11-02 | 6.4 | 11.6 | 0 | 2021-11-02 | 1.1 | 16.9 | 0 | 2020-11-02 | -1.9 | 19.9 | 0 | 2019-11-02 | 0 | 18 | 0 | 2018-11-02 | 3 | 15 | 0 | 2017-11-02 | 5.7 | 12.3 | 0 | 2016-11-02 | 9.5 | 8.5 | 0 | 15.17 | 0
2025-11-02 | 4.1 | 13.9 | 0 | 2024-11-02 | 2.3 | 15.7 | 0 | 2023-11-02 | 1.3 | 16.7 | 0 | 2022-11-02 | 10.3 | 7.7 | 0 | 2021-11-02 | 3.4 | 14.6 | 0 | 2020-11-02 | -1.5 | 19.5 | 0 | 2019-11-02 | 0.7 | 17.3 | 0 | 2018-11-02 | 3.1 | 14.9 | 0 | 2017-11-02 | 5.8 | 12.2 | 0 | 2016-11-02 | 11.6 | 6.4 | 0 | 13.89 | 0
2025-11-02 | 5.2 | 12.8 | 0 | 2024-11-02 | 3.5 | 14.5 | 0 | 2023-11-02 | 3.5 | 14.5 | 0 | 2022-11-02 | 12 | 6 | 0 | 2021-11-02 | 4.1 | 13.9 | 0 | 2020-11-02 | -1.3 | 19.3 | 0 | 2019-11-02 | 1.6 | 16.4 | 0 | 2018-11-02 | 3.5 | 14.5 | 0 | 2017-11-02 | 6.3 | 11.7 | 0 | 2016-11-02 | 12.8 | 5.2 | 0 | 12.88 | 0
2025-11-02 | 6 | 12 | 0 | 2024-11-02 | 3.1 | 14.9 | 0 | 2023-11-02 | 5.4 | 12.6 | 0 | 2022-11-02 | 13.1 | 4.9 | 0 | 2021-11-02 | 5.6 | 12.4 | 0 | 2020-11-02 | -1.8 | 19.8 | 0 | 2019-11-02 | 2.6 | 15.4 | 0 | 2018-11-02 | 3.8 | 14.2 | 0 | 2017-11-02 | 7.2 | 10.8 | 0 | 2016-11-02 | 13.9 | 4.1 | 0 | 12.11 | 0
2025-11-02 | 6.1 | 11.9 | 0 | 2024-11-02 | 3.1 | 14.9 | 0 | 2023-11-02 | 6.9 | 11.1 | 0 | 2022-11-02 | 14.2 | 3.8 | 0 | 2021-11-02 | 7.9 | 10.1 | 0 | 2020-11-02 | -1.3 | 19.3 | 0 | 2019-11-02 | 3.4 | 14.6 | 0 | 2018-11-02 | 4.1 | 13.9 | 0 | 2017-11-02 | 7.4 | 10.6 | 0 | 2016-11-02 | 14.2 | 3.8 | 0 | 11.4 | 0
2025-11-02 | 6 | 12 | 0 | 2024-11-02 | 3.5 | 14.5 | 0 | 2023-11-02 | 7.4 | 10.6 | 0 | 2022-11-02 | 14.4 | 3.6 | 0 | 2021-11-02 | 9.2 | 8.8 | 0 | 2020-11-02 | -0.3 | 18.3 | 0 | 2019-11-02 | 3.3 | 14.7 | 0 | 2018-11-02 | 4.3 | 13.7 | 0 | 2017-11-02 | 10.9 | 7.1 | 0 | 2016-11-02 | 15.6 | 2.4 | 0 | 10.57 | 0
2025-11-02 | 7 | 11 | 0 | 2024-11-02 | 3.2 | 14.8 | 0 | 2023-11-02 | 7.5 | 10.5 | 0 | 2022-11-02 | 15.2 | 2.8 | 0 | 2021-11-02 | 6.8 | 11.2 | 0 | 2020-11-02 | 0 | 18 | 0 | 2019-11-02 | 3.4 | 14.6 | 0 | 2018-11-02 | 4.4 | 13.6 | 0 | 2017-11-02 | 12.9 | 5.1 | 0 | 2016-11-02 | 15.8 | 2.2 | 0 | 10.38 | 0
2025-11-02 | 7.1 | 10.9 | 0 | 2024-11-02 | 4.5 | 13.5 | 0 | 2023-11-02 | 7.4 | 10.6 | 0 | 2022-11-02 | 15.1 | 2.9 | 0 | 2021-11-02 | 7.5 | 10.5 | 0 | 2020-11-02 | -0.4 | 18.4 | 0 | 2019-11-02 | 3.5 | 14.5 | 0 | 2018-11-02 | 4.4 | 13.6 | 0 | 2017-11-02 | 13 | 5 | 0 | 2016-11-02 | 15 | 3 | 0 | 10.29 | 0
2025-11-02 | 6.9 | 11.1 | 0 | 2024-11-02 | 3.8 | 14.2 | 0 | 2023-11-02 | 6.8 | 11.2 | 0 | 2022-11-02 | 14.7 | 3.3 | 0 | 2021-11-02 | 6.1 | 11.9 | 0 | 2020-11-02 | -0.2 | 18.2 | 0 | 2019-11-02 | 3.4 | 14.6 | 0 | 2018-11-02 | 4.2 | 13.8 | 0 | 2017-11-02 | 12.8 | 5.2 | 0 | 2016-11-02 | 14.8 | 3.2 | 0 | 10.67 | 0
2025-11-02 | 5.8 | 12.2 | 0 | 2024-11-02 | 1.9 | 16.1 | 0 | 2023-11-02 | 6 | 12 | 0 | 2022-11-02 | 12.1 | 5.9 | 0 | 2021-11-02 | 3.3 | 14.7 | 0 | 2020-11-02 | -1.5 | 19.5 | 0 | 2019-11-02 | 3.2 | 14.8 | 0 | 2018-11-02 | 4.1 | 13.9 | 0 | 2017-11-02 | 13 | 5 | 0 | 2016-11-02 | 12.7 | 5.3 | 0 | 11.94 | 0
2025-11-02 | 5.4 | 12.6 | 0 | 2024-11-02 | 0.6 | 17.4 | 0 | 2023-11-02 | 5.8 | 12.2 | 0 | 2022-11-02 | 6.8 | 11.2 | 0 | 2021-11-02 | 3.3 | 14.7 | 0 | 2020-11-02 | -2.4 | 20.4 | 0 | 2019-11-02 | 3.2 | 14.8 | 0 | 2018-11-02 | 3.9 | 14.1 | 0 | 2017-11-02 | 13.1 | 4.9 | 0 | 2016-11-02 | 11.6 | 6.4 | 0 | 12.87 | 0
2025-11-02 | 5 | 13 | 0 | 2024-11-02 | 0.9 | 17.1 | 0 | 2023-11-02 | 6 | 12 | 0 | 2022-11-02 | 7.3 | 10.7 | 0 | 2021-11-02 | 3.1 | 14.9 | 0 | 2020-11-02 | -2.5 | 20.5 | 0 | 2019-11-02 | 3.4 | 14.6 | 0 | 2018-11-02 | 3.9 | 14.1 | 0 | 2017-11-02 | 13 | 5 | 0 | 2016-11-02 | 12.2 | 5.8 | 0 | 12.77 | 0
2025-11-02 | 4.4 | 13.6 | 0 | 2024-11-02 | 0.4 | 17.6 | 0 | 2023-11-02 | 5.5 | 12.5 | 0 | 2022-11-02 | 7.6 | 10.4 | 0 | 2021-11-02 | 1.8 | 16.2 | 0 | 2020-11-02 | -2.4 | 20.4 | 0 | 2019-11-02 | 3.4 | 14.6 | 0 | 2018-11-02 | 3.9 | 14.1 | 0 | 2017-11-02 | 13.3 | 4.7 | 0 | 2016-11-02 | 10.4 | 7.6 | 0 | 13.17 | 0
2025-11-02 | 2.9 | 15.1 | 0 | 2024-11-02 | -1.1 | 19.1 | 0 | 2023-11-02 | 4.5 | 13.5 | 0 | 2022-11-02 | 8.3 | 9.7 | 0 | 2021-11-02 | 1.2 | 16.8 | 0 | 2020-11-02 | -2 | 20 | 0 | 2019-11-02 | 3.3 | 14.7 | 0 | 2018-11-02 | 3.8 | 14.2 | 0 | 2017-11-02 | 13.1 | 4.9 | 0 | 2016-11-02 | 9.9 | 8.1 | 0 | 13.61 | 0
2025-11-02 | 1.9 | 16.1 | 0 | 2024-11-02 | -1 | 19 | 0 | 2023-11-02 | 4 | 14 | 0 | 2022-11-02 | 7.7 | 10.3 | 0 | 2021-11-02 | 1.4 | 16.6 | 0 | 2020-11-02 | -0.2 | 18.2 | 0 | 2019-11-02 | 2.8 | 15.2 | 0 | 2018-11-02 | 3.8 | 14.2 | 0 | 2017-11-02 | 13.5 | 4.5 | 0 | 2016-11-02 | 9.5 | 8.5 | 0 | 13.66 | 0
2025-11-02 | 2.9 | 15.1 | 0 | 2024-11-02 | -0.3 | 18.3 | 0 | 2023-11-02 | 3.4 | 14.6 | 0 | 2022-11-02 | 7.5 | 10.5 | 0 | 2021-11-02 | 0.9 | 17.1 | 0 | 2020-11-02 | 0.5 | 17.5 | 0 | 2019-11-02 | 2.8 | 15.2 | 0 | 2018-11-02 | 3.8 | 14.2 | 0 | 2017-11-02 | 13.7 | 4.3 | 0 | 2016-11-02 | 8.9 | 9.1 | 0 | 13.59 | 0
2025-11-03 | 2.5 | 15.5 | 0 | 2024-11-03 | -1.9 | 19.9 | 0 | 2023-11-03 | 3.3 | 14.7 | 0 | 2022-11-03 | 5.2 | 12.8 | 0 | 2021-11-03 | 0.8 | 17.2 | 0 | 2020-11-03 | 0.2 | 17.8 | 0 | 2019-11-03 | 2.6 | 15.4 | 0 | 2018-11-03 | 3.8 | 14.2 | 0 | 2017-11-03 | 13.7 | 4.3 | 0 | 2016-11-03 | 8.2 | 9.8 | 0 | 14.16 | 0
2025-11-03 | 2.4 | 15.6 | 0 | 2024-11-03 | -2 | 20 | 0 | 2023-11-03 | 4.1 | 13.9 | 0 | 2022-11-03 | 2.4 | 15.6 | 0 | 2021-11-03 | 0.9 | 17.1 | 0 | 2020-11-03 | -0.4 | 18.4 | 0 | 2019-11-03 | 1.8 | 16.2 | 0 | 2018-11-03 | 3.8 | 14.2 | 0 | 2017-11-03 | 13.5 | 4.5 | 0 | 2016-11-03 | 8 | 10 | 0 | 14.55 | 0
2025-11-03 | 1.8 | 16.2 | 0 | 2024-11-03 | -2.4 | 20.4 | 0 | 2023-11-03 | 4.5 | 13.5 | 0 | 2022-11-03 | 2.6 | 15.4 | 0 | 2021-11-03 | 1.1 | 16.9 | 0 | 2020-11-03 | -0.5 | 18.5 | 0 | 2019-11-03 | 1 | 17 | 0 | 2018-11-03 | 3.8 | 14.2 | 0 | 2017-11-03 | 11.2 | 6.8 | 0 | 2016-11-03 | 7.4 | 10.6 | 0 | 14.95 | 0
2025-11-03 | 1.9 | 16.1 | 0 | 2024-11-03 | -4.1 | 22.1 | 0 | 2023-11-03 | 4.7 | 13.3 | 0 | 2022-11-03 | 1.8 | 16.2 | 0 | 2021-11-03 | 1.3 | 16.7 | 0 | 2020-11-03 | -1.2 | 19.2 | 0 | 2019-11-03 | 0.5 | 17.5 | 0 | 2018-11-03 | 3.8 | 14.2 | 0 | 2017-11-03 | 10.9 | 7.1 | 0 | 2016-11-03 | 7.3 | 10.7 | 0 | 15.31 | 0
2025-11-03 | 2.6 | 15.4 | 0 | 2024-11-03 | -3.5 | 21.5 | 0 | 2023-11-03 | 5 | 13 | 0 | 2022-11-03 | 1 | 17 | 0 | 2021-11-03 | 1 | 17 | 0 | 2020-11-03 | -2 | 20 | 0 | 2019-11-03 | -0.2 | 18.2 | 0 | 2018-11-03 | 3.8 | 14.2 | 0 | 2017-11-03 | 10.1 | 7.9 | 0 | 2016-11-03 | 7.8 | 10.2 | 0 | 15.44 | 0
2025-11-03 | 3.5 | 14.5 | 0 | 2024-11-03 | -3.5 | 21.5 | 0 | 2023-11-03 | 5.2 | 12.8 | 0 | 2022-11-03 | 0.1 | 17.9 | 0 | 2021-11-03 | 1 | 17 | 0 | 2020-11-03 | -2.9 | 20.9 | 0 | 2019-11-03 | 0.6 | 17.4 | 0 | 2018-11-03 | 3.7 | 14.3 | 0 | 2017-11-03 | 9.8 | 8.2 | 0 | 2016-11-03 | 7.9 | 10.1 | 0 | 15.46 | 0
2025-11-03 | 4.1 | 13.9 | 0 | 2024-11-03 | -3.1 | 21.1 | 0 | 2023-11-03 | 5.2 | 12.8 | 0 | 2022-11-03 | 1 | 17 | 0 | 2021-11-03 | 1.3 | 16.7 | 0 | 2020-11-03 | -3.1 | 21.1 | 0 | 2019-11-03 | 1.1 | 16.9 | 0 | 2018-11-03 | 3.4 | 14.6 | 0 | 2017-11-03 | 9.1 | 8.9 | 0 | 2016-11-03 | 7.9 | 10.1 | 0 | 15.31 | 0
2025-11-03 | 5.2 | 12.8 | 0 | 2024-11-03 | -3.5 | 21.5 | 0 | 2023-11-03 | 5.6 | 12.4 | 0 | 2022-11-03 | 0.9 | 17.1 | 0 | 2021-11-03 | 1.1 | 16.9 | 0 | 2020-11-03 | -3.8 | 21.8 | 0 | 2019-11-03 | 1.5 | 16.5 | 0 | 2018-11-03 | 3.3 | 14.7 | 0 | 2017-11-03 | 9.5 | 8.5 | 0 | 2016-11-03 | 7.6 | 10.4 | 0 | 15.26 | 0
2025-11-03 | 6.7 | 11.3 | 0 | 2024-11-03 | -1.7 | 19.7 | 0 | 2023-11-03 | 5.9 | 12.1 | 0 | 2022-11-03 | 3.2 | 14.8 | 0 | 2021-11-03 | 1.6 | 16.4 | 0 | 2020-11-03 | -3 | 21 | 0 | 2019-11-03 | 1.9 | 16.1 | 0 | 2018-11-03 | 3.5 | 14.5 | 0 | 2017-11-03 | 9.3 | 8.7 | 0 | 2016-11-03 | 8 | 10 | 0 | 14.46 | 0
2025-11-03 | 8.1 | 9.9 | 0 | 2024-11-03 | 0.3 | 17.7 | 0 | 2023-11-03 | 6.6 | 11.4 | 0 | 2022-11-03 | 6.8 | 11.2 | 0 | 2021-11-03 | 2.2 | 15.8 | 0 | 2020-11-03 | -3.6 | 21.6 | 0 | 2019-11-03 | 2.6 | 15.4 | 0 | 2018-11-03 | 3.5 | 14.5 | 0 | 2017-11-03 | 10.1 | 7.9 | 0 | 2016-11-03 | 7.9 | 10.1 | 0 | 13.55 | 0
2025-11-03 | 9.3 | 8.7 | 0 | 2024-11-03 | 1.2 | 16.8 | 0 | 2023-11-03 | 9.2 | 8.8 | 0 | 2022-11-03 | 9.4 | 8.6 | 0 | 2021-11-03 | 2.8 | 15.2 | 0 | 2020-11-03 | -3 | 21 | 0 | 2019-11-03 | 4.6 | 13.4 | 0 | 2018-11-03 | 3.5 | 14.5 | 0 | 2017-11-03 | 10.1 | 7.9 | 0 | 2016-11-03 | 8.3 | 9.7 | 0 | 12.46 | 0
2025-11-03 | 8.8 | 9.2 | 0 | 2024-11-03 | 2.7 | 15.3 | 0 | 2023-11-03 | 10.4 | 7.6 | 0 | 2022-11-03 | 12 | 6 | 0 | 2021-11-03 | 3.2 | 14.8 | 0 | 2020-11-03 | -2.1 | 20.1 | 0 | 2019-11-03 | 5.1 | 12.9 | 0 | 2018-11-03 | 2.8 | 15.2 | 0 | 2017-11-03 | 9.2 | 8.8 | 0 | 2016-11-03 | 8.6 | 9.4 | 0 | 11.93 | 0
2025-11-03 | 10 | 8 | 0 | 2024-11-03 | 3.5 | 14.5 | 0 | 2023-11-03 | 11.1 | 6.9 | 0 | 2022-11-03 | 14.5 | 3.5 | 0 | 2021-11-03 | 4.1 | 13.9 | 0 | 2020-11-03 | -1.9 | 19.9 | 0 | 2019-11-03 | 5.1 | 12.9 | 0 | 2018-11-03 | 3.1 | 14.9 | 0 | 2017-11-03 | 10.1 | 7.9 | 0 | 2016-11-03 | 8.8 | 9.2 | 0 | 11.16 | 0
2025-11-03 | 10 | 8 | 0 | 2024-11-03 | 4.8 | 13.2 | 0 | 2023-11-03 | 11.1 | 6.9 | 0 | 2022-11-03 | 15.3 | 2.7 | 0 | 2021-11-03 | 4.9 | 13.1 | 0 | 2020-11-03 | -1.9 | 19.9 | 0 | 2019-11-03 | 7.5 | 10.5 | 0 | 2018-11-03 | 3 | 15 | 0 | 2017-11-03 | 10.8 | 7.2 | 0 | 2016-11-03 | 9.6 | 8.4 | 0 | 10.49 | 0
2025-11-03 | 8 | 10 | 0 | 2024-11-03 | 5.3 | 12.7 | 0 | 2023-11-03 | 11.2 | 6.8 | 0 | 2022-11-03 | 16.4 | 1.6 | 0 | 2021-11-03 | 5.2 | 12.8 | 0 | 2020-11-03 | -1.8 | 19.8 | 0 | 2019-11-03 | 7.5 | 10.5 | 0 | 2018-11-03 | 4.5 | 13.5 | 0 | 2017-11-03 | 9.8 | 8.2 | 0 | 2016-11-03 | 10 | 8 | 0 | 10.39 | 0
2025-11-03 | 7.5 | 10.5 | 0 | 2024-11-03 | 5.5 | 12.5 | 0 | 2023-11-03 | 11 | 7 | 0 | 2022-11-03 | 16.9 | 1.1 | 0 | 2021-11-03 | 4.8 | 13.2 | 0 | 2020-11-03 | -1.6 | 19.6 | 0 | 2019-11-03 | 6.1 | 11.9 | 0 | 2018-11-03 | 3.6 | 14.4 | 0 | 2017-11-03 | 10.4 | 7.6 | 0 | 2016-11-03 | 10.6 | 7.4 | 0 | 10.52 | 0
2025-11-03 | 7 | 11 | 0 | 2024-11-03 | 5 | 13 | 0 | 2023-11-03 | 11.2 | 6.8 | 0 | 2022-11-03 | 16.5 | 1.5 | 0 | 2021-11-03 | 4.4 | 13.6 | 0 | 2020-11-03 | -2.1 | 20.1 | 0 | 2019-11-03 | 2.8 | 15.2 | 0 | 2018-11-03 | 3.2 | 14.8 | 0 | 2017-11-03 | 8 | 10 | 0 | 2016-11-03 | 10.2 | 7.8 | 0 | 11.38 | 0
2025-11-03 | 6.5 | 11.5 | 0 | 2024-11-03 | 3.2 | 14.8 | 0 | 2023-11-03 | 11.5 | 6.5 | 0 | 2022-11-03 | 14.7 | 3.3 | 0 | 2021-11-03 | 0.7 | 17.3 | 0 | 2020-11-03 | -2.6 | 20.6 | 0 | 2019-11-03 | 2.8 | 15.2 | 0 | 2018-11-03 | 2.9 | 15.1 | 0 | 2017-11-03 | 6.9 | 11.1 | 0 | 2016-11-03 | 9.3 | 8.7 | 0 | 12.41 | 0
2025-11-03 | 6.1 | 11.9 | 0 | 2024-11-03 | 2.4 | 15.6 | 0 | 2023-11-03 | 11.2 | 6.8 | 0 | 2022-11-03 | 12.9 | 5.1 | 0 | 2021-11-03 | 0.5 | 17.5 | 0 | 2020-11-03 | -2.4 | 20.4 | 0 | 2019-11-03 | 2.8 | 15.2 | 0 | 2018-11-03 | 3 | 15 | 0 | 2017-11-03 | 6.1 | 11.9 | 0 | 2016-11-03 | 9.4 | 8.6 | 0 | 12.8 | 0
2025-11-03 | 6 | 12 | 0 | 2024-11-03 | 1.5 | 16.5 | 0 | 2023-11-03 | 11.4 | 6.6 | 0 | 2022-11-03 | 11.5 | 6.5 | 0 | 2021-11-03 | -0.1 | 18.1 | 0 | 2020-11-03 | -2.4 | 20.4 | 0 | 2019-11-03 | 2.6 | 15.4 | 0 | 2018-11-03 | 2.3 | 15.7 | 0 | 2017-11-03 | 5.3 | 12.7 | 0 | 2016-11-03 | 9.1 | 8.9 | 0 | 13.28 | 0
2025-11-03 | 6.2 | 11.8 | 0 | 2024-11-03 | 1.2 | 16.8 | 0 | 2023-11-03 | 11.5 | 6.5 | 0 | 2022-11-03 | 10.2 | 7.8 | 0 | 2021-11-03 | -0.9 | 18.9 | 0 | 2020-11-03 | -2.3 | 20.3 | 0 | 2019-11-03 | 1.9 | 16.1 | 0 | 2018-11-03 | 2.7 | 15.3 | 0 | 2017-11-03 | 4.8 | 13.2 | 0 | 2016-11-03 | 8.4 | 9.6 | 0 | 13.63 | 0
2025-11-03 | 6.8 | 11.2 | 0 | 2024-11-03 | 0.1 | 17.9 | 0 | 2023-11-03 | 12.4 | 5.6 | 0 | 2022-11-03 | 8.9 | 9.1 | 0 | 2021-11-03 | -3 | 21 | 0 | 2020-11-03 | -2.3 | 20.3 | 0 | 2019-11-03 | 1.2 | 16.8 | 0 | 2018-11-03 | 2.6 | 15.4 | 0 | 2017-11-03 | 3.9 | 14.1 | 0 | 2016-11-03 | 7.2 | 10.8 | 0 | 14.22 | 0
2025-11-03 | 6.7 | 11.3 | 0 | 2024-11-03 | -0.9 | 18.9 | 0 | 2023-11-03 | 9 | 9 | 0 | 2022-11-03 | 8.3 | 9.7 | 0 | 2021-11-03 | -1.6 | 19.6 | 0 | 2020-11-03 | -2.3 | 20.3 | 0 | 2019-11-03 | 0.8 | 17.2 | 0 | 2018-11-03 | 2.6 | 15.4 | 0 | 2017-11-03 | 3.2 | 14.8 | 0 | 2016-11-03 | 6.2 | 11.8 | 0 | 14.8 | 0
2025-11-03 | 6.8 | 11.2 | 0 | 2024-11-03 | -0.1 | 18.1 | 0 | 2023-11-03 | 8.2 | 9.8 | 0 | 2022-11-03 | 7.4 | 10.6 | 0 | 2021-11-03 | -2 | 20 | 0 | 2020-11-03 | -2.5 | 20.5 | 0 | 2019-11-03 | 0.5 | 17.5 | 0 | 2018-11-03 | 2.2 | 15.8 | 0 | 2017-11-03 | 2.6 | 15.4 | 0 | 2016-11-03 | 5.8 | 12.2 | 0 | 15.11 | 0
2025-11-04 | 6.8 | 11.2 | 0 | 2024-11-04 | 0.1 | 17.9 | 0 | 2023-11-04 | 8.3 | 9.7 | 0 | 2022-11-04 | 7 | 11 | 0 | 2021-11-04 | -2.7 | 20.7 | 0 | 2020-11-04 | -2.5 | 20.5 | 0 | 2019-11-04 | -0.4 | 18.4 | 0 | 2018-11-04 | 1.9 | 16.1 | 0 | 2017-11-04 | 1.2 | 16.8 | 0 | 2016-11-04 | 5.1 | 12.9 | 0 | 15.52 | 0
2025-11-04 | 6.5 | 11.5 | 0 | 2024-11-04 | 0.2 | 17.8 | 0 | 2023-11-04 | 8.5 | 9.5 | 0 | 2022-11-04 | 7.5 | 10.5 | 0 | 2021-11-04 | -3.5 | 21.5 | 0 | 2020-11-04 | -2.1 | 20.1 | 0 | 2019-11-04 | -1.2 | 19.2 | 0 | 2018-11-04 | 1 | 17 | 0 | 2017-11-04 | 0.3 | 17.7 | 0 | 2016-11-04 | 4.6 | 13.4 | 0 | 15.82 | 0
2025-11-04 | 6.3 | 11.7 | 0 | 2024-11-04 | 0.3 | 17.7 | 0 | 2023-11-04 | 8.7 | 9.3 | 0 | 2022-11-04 | 6.7 | 11.3 | 0 | 2021-11-04 | -2.7 | 20.7 | 0 | 2020-11-04 | -2 | 20 | 0 | 2019-11-04 | -1.6 | 19.6 | 0 | 2018-11-04 | 1.3 | 16.7 | 0 | 2017-11-04 | 1.3 | 16.7 | 0 | 2016-11-04 | 4.3 | 13.7 | 0 | 15.74 | 0
2025-11-04 | 6.1 | 11.9 | 0 | 2024-11-04 | 0.6 | 17.4 | 0 | 2023-11-04 | 7.8 | 10.2 | 0 | 2022-11-04 | 6.6 | 11.4 | 0 | 2021-11-04 | -3.1 | 21.1 | 0 | 2020-11-04 | -2.8 | 20.8 | 0 | 2019-11-04 | -1.6 | 19.6 | 0 | 2018-11-04 | 1.7 | 16.3 | 0 | 2017-11-04 | -0.4 | 18.4 | 0 | 2016-11-04 | 2.7 | 15.3 | 0 | 16.24 | 0
2025-11-04 | 5.1 | 12.9 | 0 | 2024-11-04 | 0.9 | 17.1 | 0 | 2023-11-04 | 6.6 | 11.4 | 0 | 2022-11-04 | 6.8 | 11.2 | 0 | 2021-11-04 | -2.3 | 20.3 | 0 | 2020-11-04 | -2 | 20 | 0 | 2019-11-04 | -2 | 20 | 0 | 2018-11-04 | 1.8 | 16.2 | 0 | 2017-11-04 | -1.2 | 19.2 | 0 | 2016-11-04 | 1.6 | 16.4 | 0 | 16.47 | 0
2025-11-04 | 4.4 | 13.6 | 0 | 2024-11-04 | 0.5 | 17.5 | 0 | 2023-11-04 | 5.6 | 12.4 | 0 | 2022-11-04 | 7 | 11 | 0 | 2021-11-04 | -1.3 | 19.3 | 0 | 2020-11-04 | -1.7 | 19.7 | 0 | 2019-11-04 | -2.9 | 20.9 | 0 | 2018-11-04 | 1.7 | 16.3 | 0 | 2017-11-04 | -0.6 | 18.6 | 0 | 2016-11-04 | 0.6 | 17.4 | 0 | 16.67 | 0
2025-11-04 | 3.7 | 14.3 | 0 | 2024-11-04 | 0.4 | 17.6 | 0 | 2023-11-04 | 4.9 | 13.1 | 0 | 2022-11-04 | 5.9 | 12.1 | 0 | 2021-11-04 | -3 | 21 | 0 | 2020-11-04 | -1.8 | 19.8 | 0 | 2019-11-04 | -2.9 | 20.9 | 0 | 2018-11-04 | 0.2 | 17.8 | 0 | 2017-11-04 | 0 | 18 | 0 | 2016-11-04 | 0.3 | 17.7 | 0 | 17.23 | 0
2025-11-04 | 3.5 | 14.5 | 0 | 2024-11-04 | 0.9 | 17.1 | 0 | 2023-11-04 | 4.3 | 13.7 | 0 | 2022-11-04 | 6 | 12 | 0 | 2021-11-04 | -3 | 21 | 0 | 2020-11-04 | -2.2 | 20.2 | 0 | 2019-11-04 | -3.5 | 21.5 | 0 | 2018-11-04 | -1.1 | 19.1 | 0 | 2017-11-04 | -1.9 | 19.9 | 0 | 2016-11-04 | 0.1 | 17.9 | 0 | 17.69 | 0
2025-11-04 | 4.8 | 13.2 | 0 | 2024-11-04 | 1.5 | 16.5 | 0 | 2023-11-04 | 3.8 | 14.2 | 0 | 2022-11-04 | 8.4 | 9.6 | 0 | 2021-11-04 | -0.9 | 18.9 | 0 | 2020-11-04 | -1.4 | 19.4 | 0 | 2019-11-04 | -1.6 | 19.6 | 0 | 2018-11-04 | 0.8 | 17.2 | 0 | 2017-11-04 | -0.3 | 18.3 | 0 | 2016-11-04 | 0.3 | 17.7 | 0 | 16.46 | 0
2025-11-04 | 6.5 | 11.5 | 0 | 2024-11-04 | 2.4 | 15.6 | 0 | 2023-11-04 | 5 | 13 | 0 | 2022-11-04 | 11.1 | 6.9 | 0 | 2021-11-04 | 0.9 | 17.1 | 0 | 2020-11-04 | -0.5 | 18.5 | 0 | 2019-11-04 | 0 | 18 | 0 | 2018-11-04 | 2.7 | 15.3 | 0 | 2017-11-04 | 3 | 15 | 0 | 2016-11-04 | 0.4 | 17.6 | 0 | 14.85 | 0
2025-11-04 | 8.1 | 9.9 | 0 | 2024-11-04 | 3.3 | 14.7 | 0 | 2023-11-04 | 5.3 | 12.7 | 0 | 2022-11-04 | 14.1 | 3.9 | 0 | 2021-11-04 | 2.7 | 15.3 | 0 | 2020-11-04 | 0.4 | 17.6 | 0 | 2019-11-04 | 1.6 | 16.4 | 0 | 2018-11-04 | 3.7 | 14.3 | 0 | 2017-11-04 | 3.7 | 14.3 | 0 | 2016-11-04 | 1.3 | 16.7 | 0 | 13.58 | 0
2025-11-04 | 9.8 | 8.2 | 0 | 2024-11-04 | 4.9 | 13.1 | 0 | 2023-11-04 | 6.3 | 11.7 | 0 | 2022-11-04 | 17.4 | 0.6 | 0 | 2021-11-04 | 4.2 | 13.8 | 0 | 2020-11-04 | 3 | 15 | 0 | 2019-11-04 | 2.4 | 15.6 | 0 | 2018-11-04 | 4 | 14 | 0 | 2017-11-04 | 4.1 | 13.9 | 0 | 2016-11-04 | 2.7 | 15.3 | 0 | 12.12 | 0
2025-11-04 | 10.6 | 7.4 | 0 | 2024-11-04 | 5.3 | 12.7 | 0 | 2023-11-04 | 7.7 | 10.3 | 0 | 2022-11-04 | 19.4 | 0 | 1.4 | 2021-11-04 | 3.7 | 14.3 | 0 | 2020-11-04 | 5.5 | 12.5 | 0 | 2019-11-04 | 3.4 | 14.6 | 0 | 2018-11-04 | 4.8 | 13.2 | 0 | 2017-11-04 | 3.9 | 14.1 | 0 | 2016-11-04 | 3.1 | 14.9 | 0 | 11.4 | 0.14
2025-11-04 | 11.9 | 6.1 | 0 | 2024-11-04 | 4.9 | 13.1 | 0 | 2023-11-04 | 8.7 | 9.3 | 0 | 2022-11-04 | 20.2 | 0 | 2.2 | 2021-11-04 | 4.8 | 13.2 | 0 | 2020-11-04 | 8.5 | 9.5 | 0 | 2019-11-04 | 4.7 | 13.3 | 0 | 2018-11-04 | 5.3 | 12.7 | 0 | 2017-11-04 | 4 | 14 | 0 | 2016-11-04 | 4.4 | 13.6 | 0 | 10.48 | 0.22
2025-11-04 | 10.6 | 7.4 | 0 | 2024-11-04 | 5 | 13 | 0 | 2023-11-04 | 9.6 | 8.4 | 0 | 2022-11-04 | 20 | 0 | 2 | 2021-11-04 | 3.9 | 14.1 | 0 | 2020-11-04 | 10.4 | 7.6 | 0 | 2019-11-04 | 6 | 12 | 0 | 2018-11-04 | 5.8 | 12.2 | 0 | 2017-11-04 | 4.1 | 13.9 | 0 | 2016-11-04 | 4.3 | 13.7 | 0 | 10.23 | 0.2
2025-11-04 | 10.1 | 7.9 | 0 | 2024-11-04 | 4.8 | 13.2 | 0 | 2023-11-04 | 8.8 | 9.2 | 0 | 2022-11-04 | 20.3 | 0 | 2.3 | 2021-11-04 | 5.2 | 12.8 | 0 | 2020-11-04 | 12.9 | 5.1 | 0 | 2019-11-04 | 6.4 | 11.6 | 0 | 2018-11-04 | 6.4 | 11.6 | 0 | 2017-11-04 | 4 | 14 | 0 | 2016-11-04 | 4.6 | 13.4 | 0 | 9.88 | 0.23
2025-11-04 | 9.6 | 8.4 | 0 | 2024-11-04 | 4.7 | 13.3 | 0 | 2023-11-04 | 7.6 | 10.4 | 0 | 2022-11-04 | 19 | 0 | 1 | 2021-11-04 | 4.3 | 13.7 | 0 | 2020-11-04 | 11.7 | 6.3 | 0 | 2019-11-04 | 7.7 | 10.3 | 0 | 2018-11-04 | 4.3 | 13.7 | 0 | 2017-11-04 | 2.5 | 15.5 | 0 | 2016-11-04 | 4.4 | 13.6 | 0 | 10.52 | 0.1
2025-11-04 | 8.5 | 9.5 | 0 | 2024-11-04 | 4.8 | 13.2 | 0 | 2023-11-04 | 5.2 | 12.8 | 0 | 2022-11-04 | 17.4 | 0.6 | 0 | 2021-11-04 | 2.2 | 15.8 | 0 | 2020-11-04 | 12.1 | 5.9 | 0 | 2019-11-04 | 6.2 | 11.8 | 0 | 2018-11-04 | 3.4 | 14.6 | 0 | 2017-11-04 | 1.2 | 16.8 | 0 | 2016-11-04 | 2.9 | 15.1 | 0 | 11.61 | 0
2025-11-04 | 7.5 | 10.5 | 0 | 2024-11-04 | 4.8 | 13.2 | 0 | 2023-11-04 | 4.2 | 13.8 | 0 | 2022-11-04 | 15.9 | 2.1 | 0 | 2021-11-04 | 2.6 | 15.4 | 0 | 2020-11-04 | 5.8 | 12.2 | 0 | 2019-11-04 | 6.3 | 11.7 | 0 | 2018-11-04 | 1.8 | 16.2 | 0 | 2017-11-04 | 1.2 | 16.8 | 0 | 2016-11-04 | 2.2 | 15.8 | 0 | 12.77 | 0
2025-11-04 | 5.7 | 12.3 | 0 | 2024-11-04 | 4.7 | 13.3 | 0 | 2023-11-04 | 5.3 | 12.7 | 0 | 2022-11-04 | 15.4 | 2.6 | 0 | 2021-11-04 | -0.9 | 18.9 | 0 | 2020-11-04 | 5.1 | 12.9 | 0 | 2019-11-04 | 6.4 | 11.6 | 0 | 2018-11-04 | 1.9 | 16.1 | 0 | 2017-11-04 | 1.3 | 16.7 | 0 | 2016-11-04 | -0.9 | 18.9 | 0 | 13.6 | 0
2025-11-04 | 5.4 | 12.6 | 0 | 2024-11-04 | 4.6 | 13.4 | 0 | 2023-11-04 | 4.5 | 13.5 | 0 | 2022-11-04 | 16.7 | 1.3 | 0 | 2021-11-04 | -2 | 20 | 0 | 2020-11-04 | 4.7 | 13.3 | 0 | 2019-11-04 | 6.8 | 11.2 | 0 | 2018-11-04 | 1 | 17 | 0 | 2017-11-04 | 1.4 | 16.6 | 0 | 2016-11-04 | -2.6 | 20.6 | 0 | 13.95 | 0
2025-11-04 | 4.1 | 13.9 | 0 | 2024-11-04 | 4.6 | 13.4 | 0 | 2023-11-04 | 5 | 13 | 0 | 2022-11-04 | 16.7 | 1.3 | 0 | 2021-11-04 | -2.5 | 20.5 | 0 | 2020-11-04 | 2.9 | 15.1 | 0 | 2019-11-04 | 7.8 | 10.2 | 0 | 2018-11-04 | 1 | 17 | 0 | 2017-11-04 | 2.1 | 15.9 | 0 | 2016-11-04 | 0.7 | 17.3 | 0 | 13.76 | 0
2025-11-04 | 2.9 | 15.1 | 0 | 2024-11-04 | 4.7 | 13.3 | 0 | 2023-11-04 | 4.3 | 13.7 | 0 | 2022-11-04 | 15.8 | 2.2 | 0 | 2021-11-04 | -1.7 | 19.7 | 0 | 2020-11-04 | 1.4 | 16.6 | 0 | 2019-11-04 | 8.8 | 9.2 | 0 | 2018-11-04 | 1.4 | 16.6 | 0 | 2017-11-04 | 2.5 | 15.5 | 0 | 2016-11-04 | -0.2 | 18.2 | 0 | 14.01 | 0
2025-11-04 | 3.8 | 14.2 | 0 | 2024-11-04 | 5.2 | 12.8 | 0 | 2023-11-04 | 0.1 | 17.9 | 0 | 2022-11-04 | 14.7 | 3.3 | 0 | 2021-11-04 | -2.4 | 20.4 | 0 | 2020-11-04 | 1.4 | 16.6 | 0 | 2019-11-04 | 9.4 | 8.6 | 0 | 2018-11-04 | 1.7 | 16.3 | 0 | 2017-11-04 | 2.9 | 15.1 | 0 | 2016-11-04 | -0.3 | 18.3 | 0 | 14.35 | 0
2025-11-05 | 2.3 | 15.7 | 0 | 2024-11-05 | 6.9 | 11.1 | 0 | 2023-11-05 | 1.4 | 16.6 | 0 | 2022-11-05 | 15.2 | 2.8 | 0 | 2021-11-05 | -2.2 | 20.2 | 0 | 2020-11-05 | 0.5 | 17.5 | 0 | 2019-11-05 | 9.5 | 8.5 | 0 | 2018-11-05 | 1.8 | 16.2 | 0 | 2017-11-05 | 3.1 | 14.9 | 0 | 2016-11-05 | 0.5 | 17.5 | 0 | 14.1 | 0
2025-11-05 | 1.9 | 16.1 | 0 | 2024-11-05 | 7.4 | 10.6 | 0 | 2023-11-05 | 2 | 16 | 0 | 2022-11-05 | 15.9 | 2.1 | 0 | 2021-11-05 | -1.5 | 19.5 | 0 | 2020-11-05 | -0.4 | 18.4 | 0 | 2019-11-05 | 9 | 9 | 0 | 2018-11-05 | 2 | 16 | 0 | 2017-11-05 | 2.8 | 15.2 | 0 | 2016-11-05 | 2.5 | 15.5 | 0 | 13.84 | 0
2025-11-05 | 0.4 | 17.6 | 0 | 2024-11-05 | 6.8 | 11.2 | 0 | 2023-11-05 | 2.8 | 15.2 | 0 | 2022-11-05 | 16.1 | 1.9 | 0 | 2021-11-05 | -1.8 | 19.8 | 0 | 2020-11-05 | -0.2 | 18.2 | 0 | 2019-11-05 | 9 | 9 | 0 | 2018-11-05 | 2 | 16 | 0 | 2017-11-05 | 2.5 | 15.5 | 0 | 2016-11-05 | 2.3 | 15.7 | 0 | 14.01 | 0
2025-11-05 | 0.9 | 17.1 | 0 | 2024-11-05 | 7.2 | 10.8 | 0 | 2023-11-05 | 3.2 | 14.8 | 0 | 2022-11-05 | 15.8 | 2.2 | 0 | 2021-11-05 | -1.9 | 19.9 | 0 | 2020-11-05 | -0.8 | 18.8 | 0 | 2019-11-05 | 9.3 | 8.7 | 0 | 2018-11-05 | 2.2 | 15.8 | 0 | 2017-11-05 | 2.2 | 15.8 | 0 | 2016-11-05 | 3 | 15 | 0 | 13.89 | 0
2025-11-05 | 0.7 | 17.3 | 0 | 2024-11-05 | 10.5 | 7.5 | 0 | 2023-11-05 | 1.3 | 16.7 | 0 | 2022-11-05 | 15.5 | 2.5 | 0 | 2021-11-05 | -1.7 | 19.7 | 0 | 2020-11-05 | -0.8 | 18.8 | 0 | 2019-11-05 | 9.5 | 8.5 | 0 | 2018-11-05 | 2.2 | 15.8 | 0 | 2017-11-05 | 2.1 | 15.9 | 0 | 2016-11-05 | 3.3 | 14.7 | 0 | 13.74 | 0
2025-11-05 | 1 | 17 | 0 | 2024-11-05 | 11.3 | 6.7 | 0 | 2023-11-05 | 1.9 | 16.1 | 0 | 2022-11-05 | 15.4 | 2.6 | 0 | 2021-11-05 | -3 | 21 | 0 | 2020-11-05 | -0.9 | 18.9 | 0 | 2019-11-05 | 8.3 | 9.7 | 0 | 2018-11-05 | 1.9 | 16.1 | 0 | 2017-11-05 | 2.3 | 15.7 | 0 | 2016-11-05 | 4 | 14 | 0 | 13.78 | 0
2025-11-05 | 0.9 | 17.1 | 0 | 2024-11-05 | 11.2 | 6.8 | 0 | 2023-11-05 | 2 | 16 | 0 | 2022-11-05 | 15 | 3 | 0 | 2021-11-05 | -2.1 | 20.1 | 0 | 2020-11-05 | -0.3 | 18.3 | 0 | 2019-11-05 | 7.4 | 10.6 | 0 | 2018-11-05 | 1.9 | 16.1 | 0 | 2017-11-05 | 2.8 | 15.2 | 0 | 2016-11-05 | 3.7 | 14.3 | 0 | 13.75 | 0
2025-11-05 | 2.1 | 15.9 | 0 | 2024-11-05 | 11.5 | 6.5 | 0 | 2023-11-05 | -0.1 | 18.1 | 0 | 2022-11-05 | 15 | 3 | 0 | 2021-11-05 | -4.2 | 22.2 | 0 | 2020-11-05 | 7.5 | 10.5 | 0 | 2019-11-05 | 7.3 | 10.7 | 0 | 2018-11-05 | 1.8 | 16.2 | 0 | 2017-11-05 | 3.3 | 14.7 | 0 | 2016-11-05 | 3.9 | 14.1 | 0 | 13.19 | 0
2025-11-05 | 3.6 | 14.4 | 0 | 2024-11-05 | 12.3 | 5.7 | 0 | 2023-11-05 | 2.1 | 15.9 | 0 | 2022-11-05 | 16.1 | 1.9 | 0 | 2021-11-05 | -1.1 | 19.1 | 0 | 2020-11-05 | 10.7 | 7.3 | 0 | 2019-11-05 | 7.5 | 10.5 | 0 | 2018-11-05 | 1.7 | 16.3 | 0 | 2017-11-05 | 3.8 | 14.2 | 0 | 2016-11-05 | 5.4 | 12.6 | 0 | 11.79 | 0
2025-11-05 | 4.3 | 13.7 | 0 | 2024-11-05 | 13.2 | 4.8 | 0 | 2023-11-05 | 2.6 | 15.4 | 0 | 2022-11-05 | 17.8 | 0.2 | 0 | 2021-11-05 | 1.6 | 16.4 | 0 | 2020-11-05 | 13.8 | 4.2 | 0 | 2019-11-05 | 7.7 | 10.3 | 0 | 2018-11-05 | 1.9 | 16.1 | 0 | 2017-11-05 | 4.2 | 13.8 | 0 | 2016-11-05 | 6.3 | 11.7 | 0 | 10.66 | 0
2025-11-05 | 4.4 | 13.6 | 0 | 2024-11-05 | 14.3 | 3.7 | 0 | 2023-11-05 | 3.1 | 14.9 | 0 | 2022-11-05 | 18.9 | 0 | 0.9 | 2021-11-05 | 3.6 | 14.4 | 0 | 2020-11-05 | 15.9 | 2.1 | 0 | 2019-11-05 | 8.2 | 9.8 | 0 | 2018-11-05 | 2.3 | 15.7 | 0 | 2017-11-05 | 5 | 13 | 0 | 2016-11-05 | 7.3 | 10.7 | 0 | 9.79 | 0.09
2025-11-05 | 4.6 | 13.4 | 0 | 2024-11-05 | 15.6 | 2.4 | 0 | 2023-11-05 | 5.4 | 12.6 | 0 | 2022-11-05 | 21.8 | 0 | 3.8 | 2021-11-05 | 5.8 | 12.2 | 0 | 2020-11-05 | 17.2 | 0.8 | 0 | 2019-11-05 | 8.6 | 9.4 | 0 | 2018-11-05 | 2.5 | 15.5 | 0 | 2017-11-05 | 6.2 | 11.8 | 0 | 2016-11-05 | 8.7 | 9.3 | 0 | 8.74 | 0.38
2025-11-05 | 4.7 | 13.3 | 0 | 2024-11-05 | 16.6 | 1.4 | 0 | 2023-11-05 | 6.2 | 11.8 | 0 | 2022-11-05 | 20.8 | 0 | 2.8 | 2021-11-05 | 6.9 | 11.1 | 0 | 2020-11-05 | 18.1 | 0 | 0.1 | 2019-11-05 | 8.9 | 9.1 | 0 | 2018-11-05 | 2.9 | 15.1 | 0 | 2017-11-05 | 6.8 | 11.2 | 0 | 2016-11-05 | 9.7 | 8.3 | 0 | 8.13 | 0.29
2025-11-05 | 4.6 | 13.4 | 0 | 2024-11-05 | 17.7 | 0.3 | 0 | 2023-11-05 | 6 | 12 | 0 | 2022-11-05 | 22 | 0 | 4 | 2021-11-05 | 7.9 | 10.1 | 0 | 2020-11-05 | 19 | 0 | 1 | 2019-11-05 | 9.4 | 8.6 | 0 | 2018-11-05 | 2.5 | 15.5 | 0 | 2017-11-05 | 7.8 | 10.2 | 0 | 2016-11-05 | 9.6 | 8.4 | 0 | 7.85 | 0.5
2025-11-05 | 4.4 | 13.6 | 0 | 2024-11-05 | 18.8 | 0 | 0.8 | 2023-11-05 | 6 | 12 | 0 | 2022-11-05 | 23.2 | 0 | 5.2 | 2021-11-05 | 8.5 | 9.5 | 0 | 2020-11-05 | 18.6 | 0 | 0.6 | 2019-11-05 | 9.6 | 8.4 | 0 | 2018-11-05 | 3.3 | 14.7 | 0 | 2017-11-05 | 9.6 | 8.4 | 0 | 2016-11-05 | 9.7 | 8.3 | 0 | 7.49 | 0.66
2025-11-05 | 4.2 | 13.8 | 0 | 2024-11-05 | 19.1 | 0 | 1.1 | 2023-11-05 | 5.3 | 12.7 | 0 | 2022-11-05 | 23.2 | 0 | 5.2 | 2021-11-05 | 8.3 | 9.7 | 0 | 2020-11-05 | 17.3 | 0.7 | 0 | 2019-11-05 | 9.4 | 8.6 | 0 | 2018-11-05 | 3.2 | 14.8 | 0 | 2017-11-05 | 10.4 | 7.6 | 0 | 2016-11-05 | 10.4 | 7.6 | 0 | 7.55 | 0.63
2025-11-05 | 3.8 | 14.2 | 0 | 2024-11-05 | 19.5 | 0 | 1.5 | 2023-11-05 | 4.2 | 13.8 | 0 | 2022-11-05 | 22.6 | 0 | 4.6 | 2021-11-05 | 6.9 | 11.1 | 0 | 2020-11-05 | 16.2 | 1.8 | 0 | 2019-11-05 | 7.9 | 10.1 | 0 | 2018-11-05 | 3.4 | 14.6 | 0 | 2017-11-05 | 10.6 | 7.4 | 0 | 2016-11-05 | 9.2 | 8.8 | 0 | 8.18 | 0.61
2025-11-05 | 3.1 | 14.9 | 0 | 2024-11-05 | 19.5 | 0 | 1.5 | 2023-11-05 | 2.5 | 15.5 | 0 | 2022-11-05 | 21.6 | 0 | 3.6 | 2021-11-05 | 4.9 | 13.1 | 0 | 2020-11-05 | 14.8 | 3.2 | 0 | 2019-11-05 | 7.1 | 10.9 | 0 | 2018-11-05 | 3.4 | 14.6 | 0 | 2017-11-05 | 10.8 | 7.2 | 0 | 2016-11-05 | 8.6 | 9.4 | 0 | 8.88 | 0.51
2025-11-05 | 2.3 | 15.7 | 0 | 2024-11-05 | 18.8 | 0 | 0.8 | 2023-11-05 | 1.5 | 16.5 | 0 | 2022-11-05 | 20.9 | 0 | 2.9 | 2021-11-05 | 6 | 12 | 0 | 2020-11-05 | 13.8 | 4.2 | 0 | 2019-11-05 | 5.1 | 12.9 | 0 | 2018-11-05 | 3.5 | 14.5 | 0 | 2017-11-05 | 10.9 | 7.1 | 0 | 2016-11-05 | 8.3 | 9.7 | 0 | 9.26 | 0.37
2025-11-05 | 2.1 | 15.9 | 0 | 2024-11-05 | 18 | 0 | 0 | 2023-11-05 | 0.8 | 17.2 | 0 | 2022-11-05 | 21.1 | 0 | 3.1 | 2021-11-05 | 4.3 | 13.7 | 0 | 2020-11-05 | 13 | 5 | 0 | 2019-11-05 | 4.8 | 13.2 | 0 | 2018-11-05 | 3.6 | 14.4 | 0 | 2017-11-05 | 11.3 | 6.7 | 0 | 2016-11-05 | 7.7 | 10.3 | 0 | 9.64 | 0.31
2025-11-05 | 2.4 | 15.6 | 0 | 2024-11-05 | 17.6 | 0.4 | 0 | 2023-11-05 | -0.9 | 18.9 | 0 | 2022-11-05 | 21 | 0 | 3 | 2021-11-05 | 3.3 | 14.7 | 0 | 2020-11-05 | 12.6 | 5.4 | 0 | 2019-11-05 | 4.1 | 13.9 | 0 | 2018-11-05 | 4 | 14 | 0 | 2017-11-05 | 11.5 | 6.5 | 0 | 2016-11-05 | 7.7 | 10.3 | 0 | 9.97 | 0.3
2025-11-05 | 2.8 | 15.2 | 0 | 2024-11-05 | 18.9 | 0 | 0.9 | 2023-11-05 | -1 | 19 | 0 | 2022-11-05 | 20.9 | 0 | 2.9 | 2021-11-05 | 2.9 | 15.1 | 0 | 2020-11-05 | 12.7 | 5.3 | 0 | 2019-11-05 | 2.1 | 15.9 | 0 | 2018-11-05 | 4.2 | 13.8 | 0 | 2017-11-05 | 12.1 | 5.9 | 0 | 2016-11-05 | 7.2 | 10.8 | 0 | 10.1 | 0.38
2025-11-05 | 3 | 15 | 0 | 2024-11-05 | 18.7 | 0 | 0.7 | 2023-11-05 | -1.6 | 19.6 | 0 | 2022-11-05 | 20.9 | 0 | 2.9 | 2021-11-05 | 2.2 | 15.8 | 0 | 2020-11-05 | 12.3 | 5.7 | 0 | 2019-11-05 | 2.9 | 15.1 | 0 | 2018-11-05 | 4.5 | 13.5 | 0 | 2017-11-05 | 12.4 | 5.6 | 0 | 2016-11-05 | 7.6 | 10.4 | 0 | 10.07 | 0.36
2025-11-05 | 2.9 | 15.1 | 0 | 2024-11-05 | 18.7 | 0 | 0.7 | 2023-11-05 | -2.9 | 20.9 | 0 | 2022-11-05 | 21 | 0 | 3 | 2021-11-05 | 1.7 | 16.3 | 0 | 2020-11-05 | 12.1 | 5.9 | 0 | 2019-11-05 | 1.2 | 16.8 | 0 | 2018-11-05 | 4.9 | 13.1 | 0 | 2017-11-05 | 12.7 | 5.3 | 0 | 2016-11-05 | 7.4 | 10.6 | 0 | 10.4 | 0.37
2025-11-06 | 3.1 | 14.9 | 0 | 2024-11-06 | 18.3 | 0 | 0.3 | 2023-11-06 | -2.7 | 20.7 | 0 | 2022-11-06 | 21.3 | 0 | 3.3 | 2021-11-06 | 1.2 | 16.8 | 0 | 2020-11-06 | 12.2 | 5.8 | 0 | 2019-11-06 | 1.5 | 16.5 | 0 | 2018-11-06 | 5.1 | 12.9 | 0 | 2017-11-06 | 13.1 | 4.9 | 0 | 2016-11-06 | 6.9 | 11.1 | 0 | 10.36 | 0.36
2025-11-06 | 3.2 | 14.8 | 0 | 2024-11-06 | 17.9 | 0.1 | 0 | 2023-11-06 | -3.5 | 21.5 | 0 | 2022-11-06 | 21.2 | 0 | 3.2 | 2021-11-06 | 0.5 | 17.5 | 0 | 2020-11-06 | 11.7 | 6.3 | 0 | 2019-11-06 | 1.5 | 16.5 | 0 | 2018-11-06 | 5.1 | 12.9 | 0 | 2017-11-06 | 13.7 | 4.3 | 0 | 2016-11-06 | 5.9 | 12.1 | 0 | 10.6 | 0.32
2025-11-06 | 3.1 | 14.9 | 0 | 2024-11-06 | 17.8 | 0.2 | 0 | 2023-11-06 | -3.5 | 21.5 | 0 | 2022-11-06 | 21.4 | 0 | 3.4 | 2021-11-06 | -0.7 | 18.7 | 0 | 2020-11-06 | 11.1 | 6.9 | 0 | 2019-11-06 | 1.1 | 16.9 | 0 | 2018-11-06 | 5 | 13 | 0 | 2017-11-06 | 14 | 4 | 0 | 2016-11-06 | 4.2 | 13.8 | 0 | 10.99 | 0.34
2025-11-06 | 3.4 | 14.6 | 0 | 2024-11-06 | 17.9 | 0.1 | 0 | 2023-11-06 | -4.1 | 22.1 | 0 | 2022-11-06 | 21.1 | 0 | 3.1 | 2021-11-06 | -0.3 | 18.3 | 0 | 2020-11-06 | 11.3 | 6.7 | 0 | 2019-11-06 | 1 | 17 | 0 | 2018-11-06 | 4.7 | 13.3 | 0 | 2017-11-06 | 14 | 4 | 0 | 2016-11-06 | 3.6 | 14.4 | 0 | 11.05 | 0.31
2025-11-06 | 3.1 | 14.9 | 0 | 2024-11-06 | 18 | 0 | 0 | 2023-11-06 | -3.1 | 21.1 | 0 | 2022-11-06 | 17.7 | 0.3 | 0 | 2021-11-06 | -0.5 | 18.5 | 0 | 2020-11-06 | 9.9 | 8.1 | 0 | 2019-11-06 | 0.8 | 17.2 | 0 | 2018-11-06 | 4.9 | 13.1 | 0 | 2017-11-06 | 13.9 | 4.1 | 0 | 2016-11-06 | 3.2 | 14.8 | 0 | 11.21 | 0
2025-11-06 | 2.6 | 15.4 | 0 | 2024-11-06 | 18.6 | 0 | 0.6 | 2023-11-06 | -2.7 | 20.7 | 0 | 2022-11-06 | 16.8 | 1.2 | 0 | 2021-11-06 | -1.2 | 19.2 | 0 | 2020-11-06 | 9 | 9 | 0 | 2019-11-06 | 0.6 | 17.4 | 0 | 2018-11-06 | 5.1 | 12.9 | 0 | 2017-11-06 | 12.4 | 5.6 | 0 | 2016-11-06 | 2.4 | 15.6 | 0 | 11.7 | 0.06
2025-11-06 | 2.7 | 15.3 | 0 | 2024-11-06 | 18.8 | 0 | 0.8 | 2023-11-06 | -2.6 | 20.6 | 0 | 2022-11-06 | 16.6 | 1.4 | 0 | 2021-11-06 | -1.2 | 19.2 | 0 | 2020-11-06 | 8.3 | 9.7 | 0 | 2019-11-06 | 0 | 18 | 0 | 2018-11-06 | 5.2 | 12.8 | 0 | 2017-11-06 | 11.1 | 6.9 | 0 | 2016-11-06 | 1.4 | 16.6 | 0 | 12.05 | 0.08
2025-11-06 | 2.6 | 15.4 | 0 | 2024-11-06 | 18.5 | 0 | 0.5 | 2023-11-06 | -2.4 | 20.4 | 0 | 2022-11-06 | 16.4 | 1.6 | 0 | 2021-11-06 | -1.2 | 19.2 | 0 | 2020-11-06 | 8 | 10 | 0 | 2019-11-06 | -1.1 | 19.1 | 0 | 2018-11-06 | 5.3 | 12.7 | 0 | 2017-11-06 | 10.9 | 7.1 | 0 | 2016-11-06 | 2.4 | 15.6 | 0 | 12.11 | 0.05
2025-11-06 | 2.2 | 15.8 | 0 | 2024-11-06 | 18.5 | 0 | 0.5 | 2023-11-06 | -1.9 | 19.9 | 0 | 2022-11-06 | 16 | 2 | 0 | 2021-11-06 | 0.7 | 17.3 | 0 | 2020-11-06 | 10 | 8 | 0 | 2019-11-06 | -0.5 | 18.5 | 0 | 2018-11-06 | 5.7 | 12.3 | 0 | 2017-11-06 | 10.6 | 7.4 | 0 | 2016-11-06 | 3.2 | 14.8 | 0 | 11.6 | 0.05
2025-11-06 | 2.8 | 15.2 | 0 | 2024-11-06 | 18.8 | 0 | 0.8 | 2023-11-06 | -1.1 | 19.1 | 0 | 2022-11-06 | 16.4 | 1.6 | 0 | 2021-11-06 | 3.8 | 14.2 | 0 | 2020-11-06 | 12 | 6 | 0 | 2019-11-06 | 1 | 17 | 0 | 2018-11-06 | 5.6 | 12.4 | 0 | 2017-11-06 | 9.8 | 8.2 | 0 | 2016-11-06 | 4.8 | 13.2 | 0 | 10.69 | 0.08
2025-11-06 | 2.6 | 15.4 | 0 | 2024-11-06 | 19.9 | 0 | 1.9 | 2023-11-06 | 0 | 18 | 0 | 2022-11-06 | 17.7 | 0.3 | 0 | 2021-11-06 | 6.7 | 11.3 | 0 | 2020-11-06 | 13.4 | 4.6 | 0 | 2019-11-06 | 1.9 | 16.1 | 0 | 2018-11-06 | 5.5 | 12.5 | 0 | 2017-11-06 | 9.9 | 8.1 | 0 | 2016-11-06 | 5.8 | 12.2 | 0 | 9.85 | 0.19
2025-11-06 | 3.2 | 14.8 | 0 | 2024-11-06 | 20 | 0 | 2 | 2023-11-06 | 0.2 | 17.8 | 0 | 2022-11-06 | 19.4 | 0 | 1.4 | 2021-11-06 | 8.6 | 9.4 | 0 | 2020-11-06 | 15.3 | 2.7 | 0 | 2019-11-06 | 3.1 | 14.9 | 0 | 2018-11-06 | 6 | 12 | 0 | 2017-11-06 | 9.3 | 8.7 | 0 | 2016-11-06 | 6.5 | 11.5 | 0 | 9.18 | 0.34
2025-11-06 | 2.7 | 15.3 | 0 | 2024-11-06 | 20.2 | 0 | 2.2 | 2023-11-06 | 0.7 | 17.3 | 0 | 2022-11-06 | 19.9 | 0 | 1.9 | 2021-11-06 | 9.5 | 8.5 | 0 | 2020-11-06 | 15.4 | 2.6 | 0 | 2019-11-06 | 3.3 | 14.7 | 0 | 2018-11-06 | 7.2 | 10.8 | 0 | 2017-11-06 | 7.2 | 10.8 | 0 | 2016-11-06 | 7.3 | 10.7 | 0 | 9.07 | 0.41
2025-11-06 | 2.4 | 15.6 | 0 | 2024-11-06 | 19.3 | 0 | 1.3 | 2023-11-06 | 1.2 | 16.8 | 0 | 2022-11-06 | 19.6 | 0 | 1.6 | 2021-11-06 | 9.8 | 8.2 | 0 | 2020-11-06 | 16.6 | 1.4 | 0 | 2019-11-06 | 3.7 | 14.3 | 0 | 2018-11-06 | 7.9 | 10.1 | 0 | 2017-11-06 | 8.2 | 9.8 | 0 | 2016-11-06 | 8.3 | 9.7 | 0 | 8.59 | 0.29
2025-11-06 | 2 | 16 | 0 | 2024-11-06 | 18.9 | 0 | 0.9 | 2023-11-06 | 1.9 | 16.1 | 0 | 2022-11-06 | 19.2 | 0 | 1.2 | 2021-11-06 | 10.2 | 7.8 | 0 | 2020-11-06 | 17.6 | 0.4 | 0 | 2019-11-06 | 3.9 | 14.1 | 0 | 2018-11-06 | 9.2 | 8.8 | 0 | 2017-11-06 | 7.1 | 10.9 | 0 | 2016-11-06 | 8.3 | 9.7 | 0 | 8.38 | 0.21
2025-11-06 | 2.7 | 15.3 | 0 | 2024-11-06 | 18.5 | 0 | 0.5 | 2023-11-06 | 1.5 | 16.5 | 0 | 2022-11-06 | 18.4 | 0 | 0.4 | 2021-11-06 | 9.7 | 8.3 | 0 | 2020-11-06 | 18.1 | 0 | 0.1 | 2019-11-06 | 3.7 | 14.3 | 0 | 2018-11-06 | 10.9 | 7.1 | 0 | 2017-11-06 | 6 | 12 | 0 | 2016-11-06 | 8.1 | 9.9 | 0 | 8.34 | 0.1
2025-11-06 | 2.2 | 15.8 | 0 | 2024-11-06 | 17.1 | 0.9 | 0 | 2023-11-06 | 1.3 | 16.7 | 0 | 2022-11-06 | 17.6 | 0.4 | 0 | 2021-11-06 | 8.8 | 9.2 | 0 | 2020-11-06 | 16.5 | 1.5 | 0 | 2019-11-06 | 3.5 | 14.5 | 0 | 2018-11-06 | 12.3 | 5.7 | 0 | 2017-11-06 | 5.2 | 12.8 | 0 | 2016-11-06 | 7.3 | 10.7 | 0 | 8.82 | 0
2025-11-06 | 0.2 | 17.8 | 0 | 2024-11-06 | 16.2 | 1.8 | 0 | 2023-11-06 | 1.2 | 16.8 | 0 | 2022-11-06 | 16.9 | 1.1 | 0 | 2021-11-06 | 6.7 | 11.3 | 0 | 2020-11-06 | 15.7 | 2.3 | 0 | 2019-11-06 | 2.8 | 15.2 | 0 | 2018-11-06 | 12.4 | 5.6 | 0 | 2017-11-06 | 4.2 | 13.8 | 0 | 2016-11-06 | 6.1 | 11.9 | 0 | 9.76 | 0
2025-11-06 | -0.6 | 18.6 | 0 | 2024-11-06 | 15.4 | 2.6 | 0 | 2023-11-06 | 1.7 | 16.3 | 0 | 2022-11-06 | 15.9 | 2.1 | 0 | 2021-11-06 | 5.1 | 12.9 | 0 | 2020-11-06 | 14.4 | 3.6 | 0 | 2019-11-06 | 2.5 | 15.5 | 0 | 2018-11-06 | 11.8 | 6.2 | 0 | 2017-11-06 | 3.6 | 14.4 | 0 | 2016-11-06 | 4.5 | 13.5 | 0 | 10.57 | 0
2025-11-06 | -1.1 | 19.1 | 0 | 2024-11-06 | 14.7 | 3.3 | 0 | 2023-11-06 | 2.3 | 15.7 | 0 | 2022-11-06 | 14.8 | 3.2 | 0 | 2021-11-06 | 4.9 | 13.1 | 0 | 2020-11-06 | 13.7 | 4.3 | 0 | 2019-11-06 | 2.9 | 15.1 | 0 | 2018-11-06 | 10.8 | 7.2 | 0 | 2017-11-06 | 2 | 16 | 0 | 2016-11-06 | 0.3 | 17.7 | 0 | 11.47 | 0
2025-11-06 | -3.6 | 21.6 | 0 | 2024-11-06 | 13.5 | 4.5 | 0 | 2023-11-06 | 2.3 | 15.7 | 0 | 2022-11-06 | 14.6 | 3.4 | 0 | 2021-11-06 | 3.8 | 14.2 | 0 | 2020-11-06 | 12.9 | 5.1 | 0 | 2019-11-06 | 2.5 | 15.5 | 0 | 2018-11-06 | 10.8 | 7.2 | 0 | 2017-11-06 | 2.1 | 15.9 | 0 | 2016-11-06 | 1.8 | 16.2 | 0 | 11.93 | 0
2025-11-06 | -1.7 | 19.7 | 0 | 2024-11-06 | 12.6 | 5.4 | 0 | 2023-11-06 | 3.7 | 14.3 | 0 | 2022-11-06 | 14.1 | 3.9 | 0 | 2021-11-06 | 2.8 | 15.2 | 0 | 2020-11-06 | 12.3 | 5.7 | 0 | 2019-11-06 | 2.5 | 15.5 | 0 | 2018-11-06 | 10.2 | 7.8 | 0 | 2017-11-06 | 2.1 | 15.9 | 0 | 2016-11-06 | 0.4 | 17.6 | 0 | 12.1 | 0
2025-11-06 | -2.8 | 20.8 | 0 | 2024-11-06 | 11.5 | 6.5 | 0 | 2023-11-06 | 5.6 | 12.4 | 0 | 2022-11-06 | 13.3 | 4.7 | 0 | 2021-11-06 | 2.4 | 15.6 | 0 | 2020-11-06 | 12 | 6 | 0 | 2019-11-06 | 2.4 | 15.6 | 0 | 2018-11-06 | 10.3 | 7.7 | 0 | 2017-11-06 | 1.9 | 16.1 | 0 | 2016-11-06 | 0.8 | 17.2 | 0 | 12.26 | 0
2025-11-06 | -3.2 | 21.2 | 0 | 2024-11-06 | 10.1 | 7.9 | 0 | 2023-11-06 | 7.6 | 10.4 | 0 | 2022-11-06 | 13.3 | 4.7 | 0 | 2021-11-06 | 2.5 | 15.5 | 0 | 2020-11-06 | 11.7 | 6.3 | 0 | 2019-11-06 | 2 | 16 | 0 | 2018-11-06 | 10.4 | 7.6 | 0 | 2017-11-06 | 1.6 | 16.4 | 0 | 2016-11-06 | 0.6 | 17.4 | 0 | 12.34 | 0
2025-11-07 | -3.3 | 21.3 | 0 | 2024-11-07 | 9.5 | 8.5 | 0 | 2023-11-07 | 8.2 | 9.8 | 0 | 2022-11-07 | 13.2 | 4.8 | 0 | 2021-11-07 | 1.8 | 16.2 | 0 | 2020-11-07 | 11.4 | 6.6 | 0 | 2019-11-07 | 1 | 17 | 0 | 2018-11-07 | 10.4 | 7.6 | 0 | 2017-11-07 | 1.2 | 16.8 | 0 | 2016-11-07 | 0.2 | 17.8 | 0 | 12.64 | 0
2025-11-07 | -3 | 21 | 0 | 2024-11-07 | 9.1 | 8.9 | 0 | 2023-11-07 | 9.1 | 8.9 | 0 | 2022-11-07 | 13.1 | 4.9 | 0 | 2021-11-07 | 0.9 | 17.1 | 0 | 2020-11-07 | 10.9 | 7.1 | 0 | 2019-11-07 | 0.9 | 17.1 | 0 | 2018-11-07 | 10.3 | 7.7 | 0 | 2017-11-07 | 1.1 | 16.9 | 0 | 2016-11-07 | 0.3 | 17.7 | 0 | 12.73 | 0
2025-11-07 | -3.9 | 21.9 | 0 | 2024-11-07 | 8.4 | 9.6 | 0 | 2023-11-07 | 10.3 | 7.7 | 0 | 2022-11-07 | 11.9 | 6.1 | 0 | 2021-11-07 | -1 | 19 | 0 | 2020-11-07 | 10.3 | 7.7 | 0 | 2019-11-07 | 0.7 | 17.3 | 0 | 2018-11-07 | 10.1 | 7.9 | 0 | 2017-11-07 | 0.5 | 17.5 | 0 | 2016-11-07 | -1.2 | 19.2 | 0 | 13.39 | 0
2025-11-07 | -3.5 | 21.5 | 0 | 2024-11-07 | 7.9 | 10.1 | 0 | 2023-11-07 | 10.5 | 7.5 | 0 | 2022-11-07 | 12 | 6 | 0 | 2021-11-07 | -2.7 | 20.7 | 0 | 2020-11-07 | 9.7 | 8.3 | 0 | 2019-11-07 | 0.7 | 17.3 | 0 | 2018-11-07 | 9.6 | 8.4 | 0 | 2017-11-07 | -0.5 | 18.5 | 0 | 2016-11-07 | -2.2 | 20.2 | 0 | 13.85 | 0
2025-11-07 | -3.2 | 21.2 | 0 | 2024-11-07 | 6 | 12 | 0 | 2023-11-07 | 9.4 | 8.6 | 0 | 2022-11-07 | 11 | 7 | 0 | 2021-11-07 | 0.8 | 17.2 | 0 | 2020-11-07 | 9 | 9 | 0 | 2019-11-07 | 0 | 18 | 0 | 2018-11-07 | 9.1 | 8.9 | 0 | 2017-11-07 | -1.9 | 19.9 | 0 | 2016-11-07 | -1.9 | 19.9 | 0 | 14.17 | 0
2025-11-07 | -2.4 | 20.4 | 0 | 2024-11-07 | 6.5 | 11.5 | 0 | 2023-11-07 | 9.4 | 8.6 | 0 | 2022-11-07 | 10.6 | 7.4 | 0 | 2021-11-07 | 1.2 | 16.8 | 0 | 2020-11-07 | 8.8 | 9.2 | 0 | 2019-11-07 | -0.2 | 18.2 | 0 | 2018-11-07 | 8.6 | 9.4 | 0 | 2017-11-07 | -1.9 | 19.9 | 0 | 2016-11-07 | -3.3 | 21.3 | 0 | 14.27 | 0
2025-11-07 | -1.8 | 19.8 | 0 | 2024-11-07 | 4.6 | 13.4 | 0 | 2023-11-07 | 9.6 | 8.4 | 0 | 2022-11-07 | 10.5 | 7.5 | 0 | 2021-11-07 | 0.9 | 17.1 | 0 | 2020-11-07 | 8.7 | 9.3 | 0 | 2019-11-07 | -0.8 | 18.8 | 0 | 2018-11-07 | 8.5 | 9.5 | 0 | 2017-11-07 | -4.5 | 22.5 | 0 | 2016-11-07 | -4.4 | 22.4 | 0 | 14.87 | 0
2025-11-07 | -1.7 | 19.7 | 0 | 2024-11-07 | 4 | 14 | 0 | 2023-11-07 | 9.9 | 8.1 | 0 | 2022-11-07 | 10.2 | 7.8 | 0 | 2021-11-07 | -0.4 | 18.4 | 0 | 2020-11-07 | 8.9 | 9.1 | 0 | 2019-11-07 | -1.6 | 19.6 | 0 | 2018-11-07 | 8.1 | 9.9 | 0 | 2017-11-07 | -4.5 | 22.5 | 0 | 2016-11-07 | -2.3 | 20.3 | 0 | 14.94 | 0
2025-11-07 | -1.2 | 19.2 | 0 | 2024-11-07 | 5.5 | 12.5 | 0 | 2023-11-07 | 10.1 | 7.9 | 0 | 2022-11-07 | 11.1 | 6.9 | 0 | 2021-11-07 | 2 | 16 | 0 | 2020-11-07 | 9.9 | 8.1 | 0 | 2019-11-07 | -2 | 20 | 0 | 2018-11-07 | 8.5 | 9.5 | 0 | 2017-11-07 | -1.4 | 19.4 | 0 | 2016-11-07 | 0.1 | 17.9 | 0 | 13.74 | 0
2025-11-07 | -0.1 | 18.1 | 0 | 2024-11-07 | 5.9 | 12.1 | 0 | 2023-11-07 | 9.3 | 8.7 | 0 | 2022-11-07 | 12.4 | 5.6 | 0 | 2021-11-07 | 5.4 | 12.6 | 0 | 2020-11-07 | 12.3 | 5.7 | 0 | 2019-11-07 | -1.9 | 19.9 | 0 | 2018-11-07 | 9.2 | 8.8 | 0 | 2017-11-07 | 0.5 | 17.5 | 0 | 2016-11-07 | 2.7 | 15.3 | 0 | 12.43 | 0
2025-11-07 | 1.9 | 16.1 | 0 | 2024-11-07 | 7.6 | 10.4 | 0 | 2023-11-07 | 8.3 | 9.7 | 0 | 2022-11-07 | 12.3 | 5.7 | 0 | 2021-11-07 | 8.2 | 9.8 | 0 | 2020-11-07 | 14.6 | 3.4 | 0 | 2019-11-07 | -1.5 | 19.5 | 0 | 2018-11-07 | 10.1 | 7.9 | 0 | 2017-11-07 | 0.9 | 17.1 | 0 | 2016-11-07 | 6.8 | 11.2 | 0 | 11.08 | 0
2025-11-07 | 3 | 15 | 0 | 2024-11-07 | 8.6 | 9.4 | 0 | 2023-11-07 | 6.4 | 11.6 | 0 | 2022-11-07 | 12.5 | 5.5 | 0 | 2021-11-07 | 10.9 | 7.1 | 0 | 2020-11-07 | 17 | 1 | 0 | 2019-11-07 | -0.7 | 18.7 | 0 | 2018-11-07 | 10.4 | 7.6 | 0 | 2017-11-07 | 3.1 | 14.9 | 0 | 2016-11-07 | 8.3 | 9.7 | 0 | 10.05 | 0
2025-11-07 | 3.1 | 14.9 | 0 | 2024-11-07 | 9.2 | 8.8 | 0 | 2023-11-07 | 5.6 | 12.4 | 0 | 2022-11-07 | 12.2 | 5.8 | 0 | 2021-11-07 | 12.4 | 5.6 | 0 | 2020-11-07 | 18.4 | 0 | 0.4 | 2019-11-07 | -0.8 | 18.8 | 0 | 2018-11-07 | 9.3 | 8.7 | 0 | 2017-11-07 | 4.2 | 13.8 | 0 | 2016-11-07 | 10.9 | 7.1 | 0 | 9.59 | 0.04
2025-11-07 | 3.2 | 14.8 | 0 | 2024-11-07 | 9.9 | 8.1 | 0 | 2023-11-07 | 5.2 | 12.8 | 0 | 2022-11-07 | 12.8 | 5.2 | 0 | 2021-11-07 | 13 | 5 | 0 | 2020-11-07 | 20.2 | 0 | 2.2 | 2019-11-07 | -0.9 | 18.9 | 0 | 2018-11-07 | 9.2 | 8.8 | 0 | 2017-11-07 | 4.9 | 13.1 | 0 | 2016-11-07 | 12.8 | 5.2 | 0 | 9.19 | 0.22
2025-11-07 | 3.7 | 14.3 | 0 | 2024-11-07 | 10.7 | 7.3 | 0 | 2023-11-07 | 4.8 | 13.2 | 0 | 2022-11-07 | 12.8 | 5.2 | 0 | 2021-11-07 | 13.4 | 4.6 | 0 | 2020-11-07 | 20.3 | 0 | 2.3 | 2019-11-07 | -1 | 19 | 0 | 2018-11-07 | 7.2 | 10.8 | 0 | 2017-11-07 | 5.8 | 12.2 | 0 | 2016-11-07 | 13.3 | 4.7 | 0 | 9.13 | 0.23
2025-11-07 | 4.1 | 13.9 | 0 | 2024-11-07 | 11 | 7 | 0 | 2023-11-07 | 3.4 | 14.6 | 0 | 2022-11-07 | 11.1 | 6.9 | 0 | 2021-11-07 | 13.6 | 4.4 | 0 | 2020-11-07 | 19.9 | 0 | 1.9 | 2019-11-07 | -0.9 | 18.9 | 0 | 2018-11-07 | 7.8 | 10.2 | 0 | 2017-11-07 | 5 | 13 | 0 | 2016-11-07 | 13.6 | 4.4 | 0 | 9.33 | 0.19
2025-11-07 | 2.7 | 15.3 | 0 | 2024-11-07 | 10.5 | 7.5 | 0 | 2023-11-07 | 2.3 | 15.7 | 0 | 2022-11-07 | 10.7 | 7.3 | 0 | 2021-11-07 | 12.5 | 5.5 | 0 | 2020-11-07 | 18.6 | 0 | 0.6 | 2019-11-07 | -1.2 | 19.2 | 0 | 2018-11-07 | 6.9 | 11.1 | 0 | 2017-11-07 | 4.1 | 13.9 | 0 | 2016-11-07 | 12.7 | 5.3 | 0 | 10.08 | 0.06
2025-11-07 | 2.7 | 15.3 | 0 | 2024-11-07 | 7.7 | 10.3 | 0 | 2023-11-07 | 0.6 | 17.4 | 0 | 2022-11-07 | 10.2 | 7.8 | 0 | 2021-11-07 | 10.6 | 7.4 | 0 | 2020-11-07 | 16.8 | 1.2 | 0 | 2019-11-07 | -1.9 | 19.9 | 0 | 2018-11-07 | 6.6 | 11.4 | 0 | 2017-11-07 | 1.4 | 16.6 | 0 | 2016-11-07 | 10.1 | 7.9 | 0 | 11.52 | 0
2025-11-07 | 3.5 | 14.5 | 0 | 2024-11-07 | 7.5 | 10.5 | 0 | 2023-11-07 | 0.3 | 17.7 | 0 | 2022-11-07 | 9.5 | 8.5 | 0 | 2021-11-07 | 9.7 | 8.3 | 0 | 2020-11-07 | 15.3 | 2.7 | 0 | 2019-11-07 | -2.1 | 20.1 | 0 | 2018-11-07 | 6.4 | 11.6 | 0 | 2017-11-07 | 1.3 | 16.7 | 0 | 2016-11-07 | 8.4 | 9.6 | 0 | 12.02 | 0
2025-11-07 | 3.7 | 14.3 | 0 | 2024-11-07 | 7.3 | 10.7 | 0 | 2023-11-07 | 0.1 | 17.9 | 0 | 2022-11-07 | 8.2 | 9.8 | 0 | 2021-11-07 | 8.8 | 9.2 | 0 | 2020-11-07 | 14.3 | 3.7 | 0 | 2019-11-07 | -2.4 | 20.4 | 0 | 2018-11-07 | 6.5 | 11.5 | 0 | 2017-11-07 | -0.2 | 18.2 | 0 | 2016-11-07 | 7.3 | 10.7 | 0 | 12.64 | 0
2025-11-07 | 3.9 | 14.1 | 0 | 2024-11-07 | 7.8 | 10.2 | 0 | 2023-11-07 | -0.3 | 18.3 | 0 | 2022-11-07 | 7 | 11 | 0 | 2021-11-07 | 7.4 | 10.6 | 0 | 2020-11-07 | 14.4 | 3.6 | 0 | 2019-11-07 | -3 | 21 | 0 | 2018-11-07 | 6.2 | 11.8 | 0 | 2017-11-07 | 0.8 | 17.2 | 0 | 2016-11-07 | 6 | 12 | 0 | 12.98 | 0
2025-11-07 | 3.8 | 14.2 | 0 | 2024-11-07 | 7.4 | 10.6 | 0 | 2023-11-07 | -0.5 | 18.5 | 0 | 2022-11-07 | 7 | 11 | 0 | 2021-11-07 | 7.3 | 10.7 | 0 | 2020-11-07 | 13.6 | 4.4 | 0 | 2019-11-07 | -3.5 | 21.5 | 0 | 2018-11-07 | 5.8 | 12.2 | 0 | 2017-11-07 | 1.1 | 16.9 | 0 | 2016-11-07 | 4.9 | 13.1 | 0 | 13.31 | 0
2025-11-07 | 7.4 | 10.6 | 0 | 2024-11-07 | 6.8 | 11.2 | 0 | 2023-11-07 | -0.8 | 18.8 | 0 | 2022-11-07 | 5.8 | 12.2 | 0 | 2021-11-07 | 7.4 | 10.6 | 0 | 2020-11-07 | 12.8 | 5.2 | 0 | 2019-11-07 | -3.8 | 21.8 | 0 | 2018-11-07 | 5.5 | 12.5 | 0 | 2017-11-07 | 1.6 | 16.4 | 0 | 2016-11-07 | 4.7 | 13.3 | 0 | 13.26 | 0
2025-11-07 | 8.6 | 9.4 | 0 | 2024-11-07 | 6.5 | 11.5 | 0 | 2023-11-07 | -1.1 | 19.1 | 0 | 2022-11-07 | 5.3 | 12.7 | 0 | 2021-11-07 | 7.3 | 10.7 | 0 | 2020-11-07 | 12.4 | 5.6 | 0 | 2019-11-07 | -4.4 | 22.4 | 0 | 2018-11-07 | 4.7 | 13.3 | 0 | 2017-11-07 | 1.7 | 16.3 | 0 | 2016-11-07 | 4 | 14 | 0 | 13.5 | 0
2025-11-08 | 9.1 | 8.9 | 0 | 2024-11-08 | 6.3 | 11.7 | 0 | 2023-11-08 | -1.2 | 19.2 | 0 | 2022-11-08 | 5 | 13 | 0 | 2021-11-08 | 7.4 | 10.6 | 0 | 2020-11-08 | 11.6 | 6.4 | 0 | 2019-11-08 | -4.5 | 22.5 | 0 | 2018-11-08 | 4.5 | 13.5 | 0 | 2017-11-08 | 1.6 | 16.4 | 0 | 2016-11-08 | 3.7 | 14.3 | 0 | 13.65 | 0
2025-11-08 | 9.3 | 8.7 | 0 | 2024-11-08 | 6.9 | 11.1 | 0 | 2023-11-08 | -1.7 | 19.7 | 0 | 2022-11-08 | 3.6 | 14.4 | 0 | 2021-11-08 | 6.8 | 11.2 | 0 | 2020-11-08 | 11 | 7 | 0 | 2019-11-08 | -4.6 | 22.6 | 0 | 2018-11-08 | 3.8 | 14.2 | 0 | 2017-11-08 | 1.4 | 16.6 | 0 | 2016-11-08 | 4.7 | 13.3 | 0 | 13.88 | 0
2025-11-08 | 9 | 9 | 0 | 2024-11-08 | 6.7 | 11.3 | 0 | 2023-11-08 | -1.6 | 19.6 | 0 | 2022-11-08 | 1.9 | 16.1 | 0 | 2021-11-08 | 7 | 11 | 0 | 2020-11-08 | 10.1 | 7.9 | 0 | 2019-11-08 | -4.3 | 22.3 | 0 | 2018-11-08 | 2.6 | 15.4 | 0 | 2017-11-08 | 1.4 | 16.6 | 0 | 2016-11-08 | 3.6 | 14.4 | 0 | 14.36 | 0
2025-11-08 | 7.6 | 10.4 | 0 | 2024-11-08 | 6.6 | 11.4 | 0 | 2023-11-08 | -1.7 | 19.7 | 0 | 2022-11-08 | 4 | 14 | 0 | 2021-11-08 | 5.6 | 12.4 | 0 | 2020-11-08 | 9.5 | 8.5 | 0 | 2019-11-08 | -4.8 | 22.8 | 0 | 2018-11-08 | 2.9 | 15.1 | 0 | 2017-11-08 | 1.3 | 16.7 | 0 | 2016-11-08 | 3 | 15 | 0 | 14.6 | 0
2025-11-08 | 5.3 | 12.7 | 0 | 2024-11-08 | 6.7 | 11.3 | 0 | 2023-11-08 | -1.9 | 19.9 | 0 | 2022-11-08 | 3.1 | 14.9 | 0 | 2021-11-08 | 5.1 | 12.9 | 0 | 2020-11-08 | 8.4 | 9.6 | 0 | 2019-11-08 | -5.1 | 23.1 | 0 | 2018-11-08 | 2.6 | 15.4 | 0 | 2017-11-08 | 1.3 | 16.7 | 0 | 2016-11-08 | 2.6 | 15.4 | 0 | 15.19 | 0
2025-11-08 | 3.5 | 14.5 | 0 | 2024-11-08 | 6.7 | 11.3 | 0 | 2023-11-08 | -1.9 | 19.9 | 0 | 2022-11-08 | 2 | 16 | 0 | 2021-11-08 | 4.5 | 13.5 | 0 | 2020-11-08 | 7.3 | 10.7 | 0 | 2019-11-08 | -5.3 | 23.3 | 0 | 2018-11-08 | 2.4 | 15.6 | 0 | 2017-11-08 | 1.4 | 16.6 | 0 | 2016-11-08 | 2.1 | 15.9 | 0 | 15.73 | 0
2025-11-08 | 2.6 | 15.4 | 0 | 2024-11-08 | 6.9 | 11.1 | 0 | 2023-11-08 | -2 | 20 | 0 | 2022-11-08 | 1 | 17 | 0 | 2021-11-08 | 2 | 16 | 0 | 2020-11-08 | 6.7 | 11.3 | 0 | 2019-11-08 | -5.7 | 23.7 | 0 | 2018-11-08 | 2 | 16 | 0 | 2017-11-08 | 1.6 | 16.4 | 0 | 2016-11-08 | 2.7 | 15.3 | 0 | 16.22 | 0
2025-11-08 | 1.6 | 16.4 | 0 | 2024-11-08 | 7.9 | 10.1 | 0 | 2023-11-08 | -3 | 21 | 0 | 2022-11-08 | 0.4 | 17.6 | 0 | 2021-11-08 | 1.7 | 16.3 | 0 | 2020-11-08 | 6.6 | 11.4 | 0 | 2019-11-08 | -6.2 | 24.2 | 0 | 2018-11-08 | 1.3 | 16.7 | 0 | 2017-11-08 | 1.4 | 16.6 | 0 | 2016-11-08 | 2.3 | 15.7 | 0 | 16.6 | 0
2025-11-08 | 1.6 | 16.4 | 0 | 2024-11-08 | 8.5 | 9.5 | 0 | 2023-11-08 | -2 | 20 | 0 | 2022-11-08 | 1 | 17 | 0 | 2021-11-08 | 3.8 | 14.2 | 0 | 2020-11-08 | 7.9 | 10.1 | 0 | 2019-11-08 | -5.9 | 23.9 | 0 | 2018-11-08 | 3 | 15 | 0 | 2017-11-08 | 1.8 | 16.2 | 0 | 2016-11-08 | 3.7 | 14.3 | 0 | 15.66 | 0
2025-11-08 | 1.5 | 16.5 | 0 | 2024-11-08 | 8.8 | 9.2 | 0 | 2023-11-08 | -0.6 | 18.6 | 0 | 2022-11-08 | 2.1 | 15.9 | 0 | 2021-11-08 | 7.3 | 10.7 | 0 | 2020-11-08 | 10.8 | 7.2 | 0 | 2019-11-08 | -5.3 | 23.3 | 0 | 2018-11-08 | 3.9 | 14.1 | 0 | 2017-11-08 | 3.2 | 14.8 | 0 | 2016-11-08 | 5.8 | 12.2 | 0 | 14.25 | 0
2025-11-08 | 1.3 | 16.7 | 0 | 2024-11-08 | 8.9 | 9.1 | 0 | 2023-11-08 | -0.4 | 18.4 | 0 | 2022-11-08 | 3 | 15 | 0 | 2021-11-08 | 10.7 | 7.3 | 0 | 2020-11-08 | 13.9 | 4.1 | 0 | 2019-11-08 | -3.5 | 21.5 | 0 | 2018-11-08 | 5.4 | 12.6 | 0 | 2017-11-08 | 4.6 | 13.4 | 0 | 2016-11-08 | 10 | 8 | 0 | 12.61 | 0
2025-11-08 | 1.1 | 16.9 | 0 | 2024-11-08 | 10.9 | 7.1 | 0 | 2023-11-08 | 0.7 | 17.3 | 0 | 2022-11-08 | 4.2 | 13.8 | 0 | 2021-11-08 | 12.8 | 5.2 | 0 | 2020-11-08 | 16.9 | 1.1 | 0 | 2019-11-08 | -3.1 | 21.1 | 0 | 2018-11-08 | 7.3 | 10.7 | 0 | 2017-11-08 | 5.9 | 12.1 | 0 | 2016-11-08 | 11.9 | 6.1 | 0 | 11.14 | 0
2025-11-08 | 0.8 | 17.2 | 0 | 2024-11-08 | 10.7 | 7.3 | 0 | 2023-11-08 | 1.2 | 16.8 | 0 | 2022-11-08 | 4.7 | 13.3 | 0 | 2021-11-08 | 13.8 | 4.2 | 0 | 2020-11-08 | 18.7 | 0 | 0.7 | 2019-11-08 | -2.4 | 20.4 | 0 | 2018-11-08 | 6.2 | 11.8 | 0 | 2017-11-08 | 6.1 | 11.9 | 0 | 2016-11-08 | 14.2 | 3.8 | 0 | 10.67 | 0.07
2025-11-08 | 0.9 | 17.1 | 0 | 2024-11-08 | 11.7 | 6.3 | 0 | 2023-11-08 | 2.1 | 15.9 | 0 | 2022-11-08 | 5.4 | 12.6 | 0 | 2021-11-08 | 14.3 | 3.7 | 0 | 2020-11-08 | 20.2 | 0 | 2.2 | 2019-11-08 | -1.7 | 19.7 | 0 | 2018-11-08 | 5.7 | 12.3 | 0 | 2017-11-08 | 6.8 | 11.2 | 0 | 2016-11-08 | 15.3 | 2.7 | 0 | 10.15 | 0.22
2025-11-08 | 0.9 | 17.1 | 0 | 2024-11-08 | 5.9 | 12.1 | 0 | 2023-11-08 | 1.9 | 16.1 | 0 | 2022-11-08 | 5.7 | 12.3 | 0 | 2021-11-08 | 14 | 4 | 0 | 2020-11-08 | 21.3 | 0 | 3.3 | 2019-11-08 | -1.4 | 19.4 | 0 | 2018-11-08 | 6.3 | 11.7 | 0 | 2017-11-08 | 7 | 11 | 0 | 2016-11-08 | 16.4 | 1.6 | 0 | 10.53 | 0.33
2025-11-08 | 0.9 | 17.1 | 0 | 2024-11-08 | 8.2 | 9.8 | 0 | 2023-11-08 | 1.9 | 16.1 | 0 | 2022-11-08 | 5.8 | 12.2 | 0 | 2021-11-08 | 13.6 | 4.4 | 0 | 2020-11-08 | 21.1 | 0 | 3.1 | 2019-11-08 | -1.2 | 19.2 | 0 | 2018-11-08 | 6.1 | 11.9 | 0 | 2017-11-08 | 7.2 | 10.8 | 0 | 2016-11-08 | 16 | 2 | 0 | 10.35 | 0.31
2025-11-08 | 0.4 | 17.6 | 0 | 2024-11-08 | 7.8 | 10.2 | 0 | 2023-11-08 | 0.8 | 17.2 | 0 | 2022-11-08 | 5 | 13 | 0 | 2021-11-08 | 12.7 | 5.3 | 0 | 2020-11-08 | 19.1 | 0 | 1.1 | 2019-11-08 | -1.8 | 19.8 | 0 | 2018-11-08 | 5.2 | 12.8 | 0 | 2017-11-08 | 5.8 | 12.2 | 0 | 2016-11-08 | 14 | 4 | 0 | 11.21 | 0.11
2025-11-08 | -0.7 | 18.7 | 0 | 2024-11-08 | 6.9 | 11.1 | 0 | 2023-11-08 | 0.6 | 17.4 | 0 | 2022-11-08 | 3.9 | 14.1 | 0 | 2021-11-08 | 11.3 | 6.7 | 0 | 2020-11-08 | 16.8 | 1.2 | 0 | 2019-11-08 | -3.5 | 21.5 | 0 | 2018-11-08 | 4.7 | 13.3 | 0 | 2017-11-08 | 5.2 | 12.8 | 0 | 2016-11-08 | 11.8 | 6.2 | 0 | 12.3 | 0
2025-11-08 | -2.2 | 20.2 | 0 | 2024-11-08 | 6.2 | 11.8 | 0 | 2023-11-08 | -0.8 | 18.8 | 0 | 2022-11-08 | 3 | 15 | 0 | 2021-11-08 | 10.1 | 7.9 | 0 | 2020-11-08 | 14.9 | 3.1 | 0 | 2019-11-08 | -4.4 | 22.4 | 0 | 2018-11-08 | 3.5 | 14.5 | 0 | 2017-11-08 | 4.2 | 13.8 | 0 | 2016-11-08 | 10.4 | 7.6 | 0 | 13.51 | 0
2025-11-08 | -1.8 | 19.8 | 0 | 2024-11-08 | 5.6 | 12.4 | 0 | 2023-11-08 | -0.8 | 18.8 | 0 | 2022-11-08 | 2.8 | 15.2 | 0 | 2021-11-08 | 9.1 | 8.9 | 0 | 2020-11-08 | 13.2 | 4.8 | 0 | 2019-11-08 | -4.3 | 22.3 | 0 | 2018-11-08 | 3.7 | 14.3 | 0 | 2017-11-08 | 2.6 | 15.4 | 0 | 2016-11-08 | 10.5 | 7.5 | 0 | 13.94 | 0
2025-11-08 | -1.8 | 19.8 | 0 | 2024-11-08 | 4 | 14 | 0 | 2023-11-08 | -0.9 | 18.9 | 0 | 2022-11-08 | 1.7 | 16.3 | 0 | 2021-11-08 | 8.4 | 9.6 | 0 | 2020-11-08 | 11.6 | 6.4 | 0 | 2019-11-08 | -5.7 | 23.7 | 0 | 2018-11-08 | 1.1 | 16.9 | 0 | 2017-11-08 | 1.8 | 16.2 | 0 | 2016-11-08 | 9.6 | 8.4 | 0 | 15.02 | 0
2025-11-08 | -2.4 | 20.4 | 0 | 2024-11-08 | 3.5 | 14.5 | 0 | 2023-11-08 | -0.2 | 18.2 | 0 | 2022-11-08 | 1.3 | 16.7 | 0 | 2021-11-08 | 7.2 | 10.8 | 0 | 2020-11-08 | 10.7 | 7.3 | 0 | 2019-11-08 | -5.2 | 23.2 | 0 | 2018-11-08 | 0.9 | 17.1 | 0 | 2017-11-08 | 1.1 | 16.9 | 0 | 2016-11-08 | 10.1 | 7.9 | 0 | 15.3 | 0
2025-11-08 | -2.6 | 20.6 | 0 | 2024-11-08 | 3.1 | 14.9 | 0 | 2023-11-08 | -0.1 | 18.1 | 0 | 2022-11-08 | -0.3 | 18.3 | 0 | 2021-11-08 | 7.7 | 10.3 | 0 | 2020-11-08 | 10.2 | 7.8 | 0 | 2019-11-08 | -5.7 | 23.7 | 0 | 2018-11-08 | 1.8 | 16.2 | 0 | 2017-11-08 | 0.4 | 17.6 | 0 | 2016-11-08 | 9.5 | 8.5 | 0 | 15.6 | 0
2025-11-08 | -3 | 21 | 0 | 2024-11-08 | 2.6 | 15.4 | 0 | 2023-11-08 | 0 | 18 | 0 | 2022-11-08 | -0.5 | 18.5 | 0 | 2021-11-08 | 7 | 11 | 0 | 2020-11-08 | 8.8 | 9.2 | 0 | 2019-11-08 | -6.7 | 24.7 | 0 | 2018-11-08 | 0.8 | 17.2 | 0 | 2017-11-08 | -0.1 | 18.1 | 0 | 2016-11-08 | 9.6 | 8.4 | 0 | 16.15 | 0
2025-11-09 | -2.5 | 20.5 | 0 | 2024-11-09 | 2.3 | 15.7 | 0 | 2023-11-09 | -0.2 | 18.2 | 0 | 2022-11-09 | -2.3 | 20.3 | 0 | 2021-11-09 | 6.6 | 11.4 | 0 | 2020-11-09 | 7.6 | 10.4 | 0 | 2019-11-09 | -6.7 | 24.7 | 0 | 2018-11-09 | -1.7 | 19.7 | 0 | 2017-11-09 | -0.6 | 18.6 | 0 | 2016-11-09 | 9.1 | 8.9 | 0 | 16.84 | 0
2025-11-09 | -2.2 | 20.2 | 0 | 2024-11-09 | 2.3 | 15.7 | 0 | 2023-11-09 | -0.2 | 18.2 | 0 | 2022-11-09 | -2.5 | 20.5 | 0 | 2021-11-09 | 6.3 | 11.7 | 0 | 2020-11-09 | 7.8 | 10.2 | 0 | 2019-11-09 | -8.2 | 26.2 | 0 | 2018-11-09 | -2 | 20 | 0 | 2017-11-09 | -1 | 19 | 0 | 2016-11-09 | 9.7 | 8.3 | 0 | 17 | 0
2025-11-09 | -2.5 | 20.5 | 0 | 2024-11-09 | 1.5 | 16.5 | 0 | 2023-11-09 | -0.2 | 18.2 | 0 | 2022-11-09 | -2.2 | 20.2 | 0 | 2021-11-09 | 5.6 | 12.4 | 0 | 2020-11-09 | 8.4 | 9.6 | 0 | 2019-11-09 | -8.5 | 26.5 | 0 | 2018-11-09 | -1.8 | 19.8 | 0 | 2017-11-09 | -1.2 | 19.2 | 0 | 2016-11-09 | 9.4 | 8.6 | 0 | 17.15 | 0
2025-11-09 | -2.5 | 20.5 | 0 | 2024-11-09 | 1.2 | 16.8 | 0 | 2023-11-09 | -0.7 | 18.7 | 0 | 2022-11-09 | -3.2 | 21.2 | 0 | 2021-11-09 | 6.2 | 11.8 | 0 | 2020-11-09 | 7.2 | 10.8 | 0 | 2019-11-09 | -9.5 | 27.5 | 0 | 2018-11-09 | -1 | 19 | 0 | 2017-11-09 | -1 | 19 | 0 | 2016-11-09 | 9.1 | 8.9 | 0 | 17.42 | 0
2025-11-09 | -2.6 | 20.6 | 0 | 2024-11-09 | 1.2 | 16.8 | 0 | 2023-11-09 | -1.7 | 19.7 | 0 | 2022-11-09 | -4.4 | 22.4 | 0 | 2021-11-09 | 6.9 | 11.1 | 0 | 2020-11-09 | 6.3 | 11.7 | 0 | 2019-11-09 | -8.4 | 26.4 | 0 | 2018-11-09 | -3.3 | 21.3 | 0 | 2017-11-09 | -1.1 | 19.1 | 0 | 2016-11-09 | 7.5 | 10.5 | 0 | 17.96 | 0
2025-11-09 | -3 | 21 | 0 | 2024-11-09 | 0.9 | 17.1 | 0 | 2023-11-09 | -1.8 | 19.8 | 0 | 2022-11-09 | -4.3 | 22.3 | 0 | 2021-11-09 | 7.4 | 10.6 | 0 | 2020-11-09 | 7.3 | 10.7 | 0 | 2019-11-09 | -8.7 | 26.7 | 0 | 2018-11-09 | -3.5 | 21.5 | 0 | 2017-11-09 | -0.9 | 18.9 | 0 | 2016-11-09 | 6.3 | 11.7 | 0 | 18.03 | 0
2025-11-09 | -3.1 | 21.1 | 0 | 2024-11-09 | -0.1 | 18.1 | 0 | 2023-11-09 | -1.7 | 19.7 | 0 | 2022-11-09 | -4.9 | 22.9 | 0 | 2021-11-09 | 8.4 | 9.6 | 0 | 2020-11-09 | 8.2 | 9.8 | 0 | 2019-11-09 | -8.9 | 26.9 | 0 | 2018-11-09 | -3.3 | 21.3 | 0 | 2017-11-09 | -0.8 | 18.8 | 0 | 2016-11-09 | 5.8 | 12.2 | 0 | 18.04 | 0
2025-11-09 | -2.8 | 20.8 | 0 | 2024-11-09 | -0.2 | 18.2 | 0 | 2023-11-09 | -1.9 | 19.9 | 0 | 2022-11-09 | -3.4 | 21.4 | 0 | 2021-11-09 | 7.6 | 10.4 | 0 | 2020-11-09 | 8.3 | 9.7 | 0 | 2019-11-09 | -7.6 | 25.6 | 0 | 2018-11-09 | -2.3 | 20.3 | 0 | 2017-11-09 | -0.8 | 18.8 | 0 | 2016-11-09 | 5.3 | 12.7 | 0 | 17.78 | 0
2025-11-09 | -2.4 | 20.4 | 0 | 2024-11-09 | 0.8 | 17.2 | 0 | 2023-11-09 | -1.5 | 19.5 | 0 | 2022-11-09 | -1.8 | 19.8 | 0 | 2021-11-09 | 8.9 | 9.1 | 0 | 2020-11-09 | 8.8 | 9.2 | 0 | 2019-11-09 | -5.4 | 23.4 | 0 | 2018-11-09 | -1.3 | 19.3 | 0 | 2017-11-09 | 0.3 | 17.7 | 0 | 2016-11-09 | 4.5 | 13.5 | 0 | 16.91 | 0
2025-11-09 | -2 | 20 | 0 | 2024-11-09 | 2.9 | 15.1 | 0 | 2023-11-09 | -1.2 | 19.2 | 0 | 2022-11-09 | 0.7 | 17.3 | 0 | 2021-11-09 | 9.3 | 8.7 | 0 | 2020-11-09 | 11.2 | 6.8 | 0 | 2019-11-09 | -3.6 | 21.6 | 0 | 2018-11-09 | -0.7 | 18.7 | 0 | 2017-11-09 | 1.7 | 16.3 | 0 | 2016-11-09 | 4.5 | 13.5 | 0 | 15.72 | 0
2025-11-09 | -1.6 | 19.6 | 0 | 2024-11-09 | 3.7 | 14.3 | 0 | 2023-11-09 | -1.4 | 19.4 | 0 | 2022-11-09 | 3.2 | 14.8 | 0 | 2021-11-09 | 11.6 | 6.4 | 0 | 2020-11-09 | 14.3 | 3.7 | 0 | 2019-11-09 | -2 | 20 | 0 | 2018-11-09 | 0 | 18 | 0 | 2017-11-09 | 3.2 | 14.8 | 0 | 2016-11-09 | 4.9 | 13.1 | 0 | 14.41 | 0
2025-11-09 | -1.3 | 19.3 | 0 | 2024-11-09 | 4.6 | 13.4 | 0 | 2023-11-09 | -1.2 | 19.2 | 0 | 2022-11-09 | 4.9 | 13.1 | 0 | 2021-11-09 | 13.2 | 4.8 | 0 | 2020-11-09 | 18.3 | 0 | 0.3 | 2019-11-09 | -1.2 | 19.2 | 0 | 2018-11-09 | 0.4 | 17.6 | 0 | 2017-11-09 | 5.1 | 12.9 | 0 | 2016-11-09 | 4.8 | 13.2 | 0 | 13.27 | 0.03
2025-11-09 | -1.6 | 19.6 | 0 | 2024-11-09 | 5.3 | 12.7 | 0 | 2023-11-09 | -1.2 | 19.2 | 0 | 2022-11-09 | 6.9 | 11.1 | 0 | 2021-11-09 | 13.6 | 4.4 | 0 | 2020-11-09 | 20.4 | 0 | 2.4 | 2019-11-09 | -0.7 | 18.7 | 0 | 2018-11-09 | 0.9 | 17.1 | 0 | 2017-11-09 | 6.3 | 11.7 | 0 | 2016-11-09 | 5.1 | 12.9 | 0 | 12.74 | 0.24
2025-11-09 | -2.1 | 20.1 | 0 | 2024-11-09 | 5.7 | 12.3 | 0 | 2023-11-09 | -1.2 | 19.2 | 0 | 2022-11-09 | 8 | 10 | 0 | 2021-11-09 | 14 | 4 | 0 | 2020-11-09 | 20.5 | 0 | 2.5 | 2019-11-09 | -0.4 | 18.4 | 0 | 2018-11-09 | 1.3 | 16.7 | 0 | 2017-11-09 | 6.9 | 11.1 | 0 | 2016-11-09 | 4.8 | 13.2 | 0 | 12.5 | 0.25
2025-11-09 | -1.8 | 19.8 | 0 | 2024-11-09 | 6.3 | 11.7 | 0 | 2023-11-09 | -1 | 19 | 0 | 2022-11-09 | 9.4 | 8.6 | 0 | 2021-11-09 | 12.1 | 5.9 | 0 | 2020-11-09 | 22.1 | 0 | 4.1 | 2019-11-09 | -1 | 19 | 0 | 2018-11-09 | 0.4 | 17.6 | 0 | 2017-11-09 | 7.2 | 10.8 | 0 | 2016-11-09 | 4.5 | 13.5 | 0 | 12.59 | 0.41
2025-11-09 | -1.8 | 19.8 | 0 | 2024-11-09 | 6.2 | 11.8 | 0 | 2023-11-09 | -0.7 | 18.7 | 0 | 2022-11-09 | 10.2 | 7.8 | 0 | 2021-11-09 | 12.2 | 5.8 | 0 | 2020-11-09 | 21.2 | 0 | 3.2 | 2019-11-09 | -0.4 | 18.4 | 0 | 2018-11-09 | 0.3 | 17.7 | 0 | 2017-11-09 | 7.5 | 10.5 | 0 | 2016-11-09 | 4.6 | 13.4 | 0 | 12.39 | 0.32
2025-11-09 | -1.9 | 19.9 | 0 | 2024-11-09 | 5.4 | 12.6 | 0 | 2023-11-09 | -0.3 | 18.3 | 0 | 2022-11-09 | 10 | 8 | 0 | 2021-11-09 | 11 | 7 | 0 | 2020-11-09 | 19.7 | 0 | 1.7 | 2019-11-09 | -0.2 | 18.2 | 0 | 2018-11-09 | 0.1 | 17.9 | 0 | 2017-11-09 | 7.2 | 10.8 | 0 | 2016-11-09 | 4.1 | 13.9 | 0 | 12.66 | 0.17
2025-11-09 | -2 | 20 | 0 | 2024-11-09 | 2.9 | 15.1 | 0 | 2023-11-09 | -0.1 | 18.1 | 0 | 2022-11-09 | 6.7 | 11.3 | 0 | 2021-11-09 | 9.8 | 8.2 | 0 | 2020-11-09 | 17.3 | 0.7 | 0 | 2019-11-09 | -0.1 | 18.1 | 0 | 2018-11-09 | 0.1 | 17.9 | 0 | 2017-11-09 | 6.9 | 11.1 | 0 | 2016-11-09 | 2.9 | 15.1 | 0 | 13.56 | 0
2025-11-09 | -2.1 | 20.1 | 0 | 2024-11-09 | 3.2 | 14.8 | 0 | 2023-11-09 | 0.2 | 17.8 | 0 | 2022-11-09 | 7.9 | 10.1 | 0 | 2021-11-09 | 9.4 | 8.6 | 0 | 2020-11-09 | 17 | 1 | 0 | 2019-11-09 | 0.4 | 17.6 | 0 | 2018-11-09 | 0.1 | 17.9 | 0 | 2017-11-09 | 6.9 | 11.1 | 0 | 2016-11-09 | 2.2 | 15.8 | 0 | 13.48 | 0
2025-11-09 | -2.5 | 20.5 | 0 | 2024-11-09 | 1.1 | 16.9 | 0 | 2023-11-09 | 1.2 | 16.8 | 0 | 2022-11-09 | 7.8 | 10.2 | 0 | 2021-11-09 | 9 | 9 | 0 | 2020-11-09 | 15.5 | 2.5 | 0 | 2019-11-09 | 0.6 | 17.4 | 0 | 2018-11-09 | 0.2 | 17.8 | 0 | 2017-11-09 | 6.1 | 11.9 | 0 | 2016-11-09 | 1.4 | 16.6 | 0 | 13.96 | 0
2025-11-09 | -2.7 | 20.7 | 0 | 2024-11-09 | -0.4 | 18.4 | 0 | 2023-11-09 | 2.4 | 15.6 | 0 | 2022-11-09 | 6.4 | 11.6 | 0 | 2021-11-09 | 7 | 11 | 0 | 2020-11-09 | 14.9 | 3.1 | 0 | 2019-11-09 | 0.7 | 17.3 | 0 | 2018-11-09 | 0.3 | 17.7 | 0 | 2017-11-09 | 4.7 | 13.3 | 0 | 2016-11-09 | -0.9 | 18.9 | 0 | 14.76 | 0
2025-11-09 | -2.8 | 20.8 | 0 | 2024-11-09 | 1.5 | 16.5 | 0 | 2023-11-09 | 2.3 | 15.7 | 0 | 2022-11-09 | 6 | 12 | 0 | 2021-11-09 | 6 | 12 | 0 | 2020-11-09 | 13.8 | 4.2 | 0 | 2019-11-09 | 0.6 | 17.4 | 0 | 2018-11-09 | 0.3 | 17.7 | 0 | 2017-11-09 | 4.9 | 13.1 | 0 | 2016-11-09 | -1.1 | 19.1 | 0 | 14.85 | 0
2025-11-09 | -2.8 | 20.8 | 0 | 2024-11-09 | 0.7 | 17.3 | 0 | 2023-11-09 | 2.7 | 15.3 | 0 | 2022-11-09 | 5.5 | 12.5 | 0 | 2021-11-09 | 7 | 11 | 0 | 2020-11-09 | 12.6 | 5.4 | 0 | 2019-11-09 | 0.9 | 17.1 | 0 | 2018-11-09 | 0.4 | 17.6 | 0 | 2017-11-09 | 0.8 | 17.2 | 0 | 2016-11-09 | -0.2 | 18.2 | 0 | 15.24 | 0
2025-11-09 | -2.9 | 20.9 | 0 | 2024-11-09 | -0.1 | 18.1 | 0 | 2023-11-09 | 2.7 | 15.3 | 0 | 2022-11-09 | 6.7 | 11.3 | 0 | 2021-11-09 | 5.5 | 12.5 | 0 | 2020-11-09 | 11.7 | 6.3 | 0 | 2019-11-09 | 1 | 17 | 0 | 2018-11-09 | 0.3 | 17.7 | 0 | 2017-11-09 | -1.9 | 19.9 | 0 | 2016-11-09 | -1.8 | 19.8 | 0 | 15.88 | 0
2025-11-10 | -2.9 | 20.9 | 0 | 2024-11-10 | -0.1 | 18.1 | 0 | 2023-11-10 | 2.2 | 15.8 | 0 | 2022-11-10 | 7.7 | 10.3 | 0 | 2021-11-10 | 5.6 | 12.4 | 0 | 2020-11-10 | 11.9 | 6.1 | 0 | 2019-11-10 | 1.2 | 16.8 | 0 | 2018-11-10 | 0.7 | 17.3 | 0 | 2017-11-10 | -3.9 | 21.9 | 0 | 2016-11-10 | -2 | 20 | 0 | 15.96 | 0
2025-11-10 | -3 | 21 | 0 | 2024-11-10 | 0 | 18 | 0 | 2023-11-10 | 2 | 16 | 0 | 2022-11-10 | 9.4 | 8.6 | 0 | 2021-11-10 | 3.6 | 14.4 | 0 | 2020-11-10 | 11.9 | 6.1 | 0 | 2019-11-10 | 1.4 | 16.6 | 0 | 2018-11-10 | 1.2 | 16.8 | 0 | 2017-11-10 | -4.9 | 22.9 | 0 | 2016-11-10 | -2.1 | 20.1 | 0 | 16.05 | 0
2025-11-10 | -3 | 21 | 0 | 2024-11-10 | -0.4 | 18.4 | 0 | 2023-11-10 | 2.5 | 15.5 | 0 | 2022-11-10 | 10 | 8 | 0 | 2021-11-10 | 4.3 | 13.7 | 0 | 2020-11-10 | 11.4 | 6.6 | 0 | 2019-11-10 | 1.9 | 16.1 | 0 | 2018-11-10 | 1.8 | 16.2 | 0 | 2017-11-10 | -6.3 | 24.3 | 0 | 2016-11-10 | -1.6 | 19.6 | 0 | 15.94 | 0
2025-11-10 | -3.2 | 21.2 | 0 | 2024-11-10 | -0.6 | 18.6 | 0 | 2023-11-10 | 2.9 | 15.1 | 0 | 2022-11-10 | 10.3 | 7.7 | 0 | 2021-11-10 | 4.3 | 13.7 | 0 | 2020-11-10 | 10.3 | 7.7 | 0 | 2019-11-10 | 2 | 16 | 0 | 2018-11-10 | 2.5 | 15.5 | 0 | 2017-11-10 | -8.3 | 26.3 | 0 | 2016-11-10 | -2.7 | 20.7 | 0 | 16.25 | 0
2025-11-10 | -3 | 21 | 0 | 2024-11-10 | -1 | 19 | 0 | 2023-11-10 | 3.3 | 14.7 | 0 | 2022-11-10 | 10 | 8 | 0 | 2021-11-10 | 3 | 15 | 0 | 2020-11-10 | 9.8 | 8.2 | 0 | 2019-11-10 | 1.4 | 16.6 | 0 | 2018-11-10 | 2.9 | 15.1 | 0 | 2017-11-10 | -8.6 | 26.6 | 0 | 2016-11-10 | -2.7 | 20.7 | 0 | 16.49 | 0
2025-11-10 | -2.9 | 20.9 | 0 | 2024-11-10 | -0.6 | 18.6 | 0 | 2023-11-10 | 3.4 | 14.6 | 0 | 2022-11-10 | 9.5 | 8.5 | 0 | 2021-11-10 | 2.9 | 15.1 | 0 | 2020-11-10 | 9.3 | 8.7 | 0 | 2019-11-10 | 1.5 | 16.5 | 0 | 2018-11-10 | 2.3 | 15.7 | 0 | 2017-11-10 | -9.9 | 27.9 | 0 | 2016-11-10 | -2.7 | 20.7 | 0 | 16.72 | 0
2025-11-10 | -3.4 | 21.4 | 0 | 2024-11-10 | -2.2 | 20.2 | 0 | 2023-11-10 | 3.4 | 14.6 | 0 | 2022-11-10 | 8.7 | 9.3 | 0 | 2021-11-10 | 3.4 | 14.6 | 0 | 2020-11-10 | 9.3 | 8.7 | 0 | 2019-11-10 | 1.6 | 16.4 | 0 | 2018-11-10 | 2 | 16 | 0 | 2017-11-10 | -10.5 | 28.5 | 0 | 2016-11-10 | -2.3 | 20.3 | 0 | 17 | 0
2025-11-10 | -3.1 | 21.1 | 0 | 2024-11-10 | -2.5 | 20.5 | 0 | 2023-11-10 | 3.5 | 14.5 | 0 | 2022-11-10 | 9.5 | 8.5 | 0 | 2021-11-10 | 2.6 | 15.4 | 0 | 2020-11-10 | 9.7 | 8.3 | 0 | 2019-11-10 | 1.6 | 16.4 | 0 | 2018-11-10 | 1.6 | 16.4 | 0 | 2017-11-10 | -11.1 | 29.1 | 0 | 2016-11-10 | -1.8 | 19.8 | 0 | 17 | 0
2025-11-10 | -3.1 | 21.1 | 0 | 2024-11-10 | -1.3 | 19.3 | 0 | 2023-11-10 | 3.8 | 14.2 | 0 | 2022-11-10 | 10.6 | 7.4 | 0 | 2021-11-10 | 3.6 | 14.4 | 0 | 2020-11-10 | 11.7 | 6.3 | 0 | 2019-11-10 | 1.8 | 16.2 | 0 | 2018-11-10 | 1.3 | 16.7 | 0 | 2017-11-10 | -11 | 29 | 0 | 2016-11-10 | -0.4 | 18.4 | 0 | 16.3 | 0
2025-11-10 | -2.9 | 20.9 | 0 | 2024-11-10 | 1.9 | 16.1 | 0 | 2023-11-10 | 4.4 | 13.6 | 0 | 2022-11-10 | 11.4 | 6.6 | 0 | 2021-11-10 | 5.2 | 12.8 | 0 | 2020-11-10 | 14.5 | 3.5 | 0 | 2019-11-10 | 2.3 | 15.7 | 0 | 2018-11-10 | 1.4 | 16.6 | 0 | 2017-11-10 | -10.1 | 28.1 | 0 | 2016-11-10 | 2.2 | 15.8 | 0 | 14.97 | 0
2025-11-10 | -2.6 | 20.6 | 0 | 2024-11-10 | 2.8 | 15.2 | 0 | 2023-11-10 | 5.2 | 12.8 | 0 | 2022-11-10 | 13.1 | 4.9 | 0 | 2021-11-10 | 6.7 | 11.3 | 0 | 2020-11-10 | 16.1 | 1.9 | 0 | 2019-11-10 | 3.1 | 14.9 | 0 | 2018-11-10 | 1.4 | 16.6 | 0 | 2017-11-10 | -9.1 | 27.1 | 0 | 2016-11-10 | 4.4 | 13.6 | 0 | 13.89 | 0
2025-11-10 | -2.3 | 20.3 | 0 | 2024-11-10 | 3.6 | 14.4 | 0 | 2023-11-10 | 5.8 | 12.2 | 0 | 2022-11-10 | 15.7 | 2.3 | 0 | 2021-11-10 | 8 | 10 | 0 | 2020-11-10 | 19.9 | 0 | 1.9 | 2019-11-10 | 4.2 | 13.8 | 0 | 2018-11-10 | 1.7 | 16.3 | 0 | 2017-11-10 | -8 | 26 | 0 | 2016-11-10 | 8.1 | 9.9 | 0 | 12.52 | 0.19
2025-11-10 | -2.1 | 20.1 | 0 | 2024-11-10 | 3.9 | 14.1 | 0 | 2023-11-10 | 6.3 | 11.7 | 0 | 2022-11-10 | 15.8 | 2.2 | 0 | 2021-11-10 | 9.9 | 8.1 | 0 | 2020-11-10 | 21.8 | 0 | 3.8 | 2019-11-10 | 4.7 | 13.3 | 0 | 2018-11-10 | 0.4 | 17.6 | 0 | 2017-11-10 | -7.5 | 25.5 | 0 | 2016-11-10 | 10.2 | 7.8 | 0 | 12.04 | 0.38
2025-11-10 | -2.1 | 20.1 | 0 | 2024-11-10 | 3.9 | 14.1 | 0 | 2023-11-10 | 6.3 | 11.7 | 0 | 2022-11-10 | 16.1 | 1.9 | 0 | 2021-11-10 | 10.3 | 7.7 | 0 | 2020-11-10 | 23.1 | 0 | 5.1 | 2019-11-10 | 4.7 | 13.3 | 0 | 2018-11-10 | 0.1 | 17.9 | 0 | 2017-11-10 | -6.5 | 24.5 | 0 | 2016-11-10 | 12.2 | 5.8 | 0 | 11.7 | 0.51
2025-11-10 | -2.2 | 20.2 | 0 | 2024-11-10 | 4.6 | 13.4 | 0 | 2023-11-10 | 6.8 | 11.2 | 0 | 2022-11-10 | 16 | 2 | 0 | 2021-11-10 | 10.7 | 7.3 | 0 | 2020-11-10 | 22.6 | 0 | 4.6 | 2019-11-10 | 5.1 | 12.9 | 0 | 2018-11-10 | 0.9 | 17.1 | 0 | 2017-11-10 | -5.5 | 23.5 | 0 | 2016-11-10 | 11.9 | 6.1 | 0 | 11.37 | 0.46
2025-11-10 | -2.4 | 20.4 | 0 | 2024-11-10 | 4.5 | 13.5 | 0 | 2023-11-10 | 6.7 | 11.3 | 0 | 2022-11-10 | 16.3 | 1.7 | 0 | 2021-11-10 | 10.6 | 7.4 | 0 | 2020-11-10 | 21.4 | 0 | 3.4 | 2019-11-10 | 5 | 13 | 0 | 2018-11-10 | 0.1 | 17.9 | 0 | 2017-11-10 | -5.2 | 23.2 | 0 | 2016-11-10 | 12.2 | 5.8 | 0 | 11.42 | 0.34
2025-11-10 | -2.5 | 20.5 | 0 | 2024-11-10 | 4.7 | 13.3 | 0 | 2023-11-10 | 4 | 14 | 0 | 2022-11-10 | 16.4 | 1.6 | 0 | 2021-11-10 | 9.7 | 8.3 | 0 | 2020-11-10 | 20 | 0 | 2 | 2019-11-10 | 2.1 | 15.9 | 0 | 2018-11-10 | 0.3 | 17.7 | 0 | 2017-11-10 | -5.2 | 23.2 | 0 | 2016-11-10 | 11.8 | 6.2 | 0 | 12.07 | 0.2
2025-11-10 | -2.6 | 20.6 | 0 | 2024-11-10 | 3.8 | 14.2 | 0 | 2023-11-10 | 3.6 | 14.4 | 0 | 2022-11-10 | 15.1 | 2.9 | 0 | 2021-11-10 | 6.7 | 11.3 | 0 | 2020-11-10 | 19.1 | 0 | 1.1 | 2019-11-10 | 1 | 17 | 0 | 2018-11-10 | -0.6 | 18.6 | 0 | 2017-11-10 | -5.8 | 23.8 | 0 | 2016-11-10 | 11.1 | 6.9 | 0 | 12.97 | 0.11
2025-11-10 | -2.6 | 20.6 | 0 | 2024-11-10 | 4.4 | 13.6 | 0 | 2023-11-10 | 3.3 | 14.7 | 0 | 2022-11-10 | 15.9 | 2.1 | 0 | 2021-11-10 | 6.9 | 11.1 | 0 | 2020-11-10 | 17.8 | 0.2 | 0 | 2019-11-10 | 0.6 | 17.4 | 0 | 2018-11-10 | -1.2 | 19.2 | 0 | 2017-11-10 | -5.8 | 23.8 | 0 | 2016-11-10 | 10 | 8 | 0 | 13.07 | 0
2025-11-10 | -2.8 | 20.8 | 0 | 2024-11-10 | 4.5 | 13.5 | 0 | 2023-11-10 | 2.8 | 15.2 | 0 | 2022-11-10 | 16 | 2 | 0 | 2021-11-10 | 4.4 | 13.6 | 0 | 2020-11-10 | 16.5 | 1.5 | 0 | 2019-11-10 | -0.1 | 18.1 | 0 | 2018-11-10 | -1.2 | 19.2 | 0 | 2017-11-10 | -6.4 | 24.4 | 0 | 2016-11-10 | 11.1 | 6.9 | 0 | 13.52 | 0
2025-11-10 | -3.2 | 21.2 | 0 | 2024-11-10 | 4.1 | 13.9 | 0 | 2023-11-10 | 1.4 | 16.6 | 0 | 2022-11-10 | 15.4 | 2.6 | 0 | 2021-11-10 | 2.6 | 15.4 | 0 | 2020-11-10 | 15.9 | 2.1 | 0 | 2019-11-10 | -0.8 | 18.8 | 0 | 2018-11-10 | -1.6 | 19.6 | 0 | 2017-11-10 | -7.3 | 25.3 | 0 | 2016-11-10 | 10.6 | 7.4 | 0 | 14.29 | 0
2025-11-10 | -3.3 | 21.3 | 0 | 2024-11-10 | 3.9 | 14.1 | 0 | 2023-11-10 | 0.9 | 17.1 | 0 | 2022-11-10 | 15.5 | 2.5 | 0 | 2021-11-10 | 3.2 | 14.8 | 0 | 2020-11-10 | 16.1 | 1.9 | 0 | 2019-11-10 | -1.7 | 19.7 | 0 | 2018-11-10 | -1.8 | 19.8 | 0 | 2017-11-10 | -8.3 | 26.3 | 0 | 2016-11-10 | 10.4 | 7.6 | 0 | 14.51 | 0
2025-11-10 | -3.2 | 21.2 | 0 | 2024-11-10 | 4 | 14 | 0 | 2023-11-10 | -0.3 | 18.3 | 0 | 2022-11-10 | 14.9 | 3.1 | 0 | 2021-11-10 | 1.2 | 16.8 | 0 | 2020-11-10 | 16.8 | 1.2 | 0 | 2019-11-10 | -2.4 | 20.4 | 0 | 2018-11-10 | -2.1 | 20.1 | 0 | 2017-11-10 | -8.7 | 26.7 | 0 | 2016-11-10 | 10.5 | 7.5 | 0 | 14.93 | 0
2025-11-10 | -3.1 | 21.1 | 0 | 2024-11-10 | 4.4 | 13.6 | 0 | 2023-11-10 | -1.4 | 19.4 | 0 | 2022-11-10 | 13.7 | 4.3 | 0 | 2021-11-10 | 0.8 | 17.2 | 0 | 2020-11-10 | 16.9 | 1.1 | 0 | 2019-11-10 | -3.1 | 21.1 | 0 | 2018-11-10 | -2.5 | 20.5 | 0 | 2017-11-10 | -8.9 | 26.9 | 0 | 2016-11-10 | 10.4 | 7.6 | 0 | 15.28 | 0
2025-11-11 | -3.1 | 21.1 | 0 | 2024-11-11 | 5.1 | 12.9 | 0 | 2023-11-11 | -2.2 | 20.2 | 0 | 2022-11-11 | 13.1 | 4.9 | 0 | 2021-11-11 | -0.3 | 18.3 | 0 | 2020-11-11 | 17.4 | 0.6 | 0 | 2019-11-11 | -4.1 | 22.1 | 0 | 2018-11-11 | -2.9 | 20.9 | 0 | 2017-11-11 | -9.2 | 27.2 | 0 | 2016-11-11 | 10.5 | 7.5 | 0 | 15.57 | 0
2025-11-11 | -3.3 | 21.3 | 0 | 2024-11-11 | 6 | 12 | 0 | 2023-11-11 | -2.2 | 20.2 | 0 | 2022-11-11 | 13.2 | 4.8 | 0 | 2021-11-11 | -0.7 | 18.7 | 0 | 2020-11-11 | 17.2 | 0.8 | 0 | 2019-11-11 | -4.5 | 22.5 | 0 | 2018-11-11 | -3.3 | 21.3 | 0 | 2017-11-11 | -9.4 | 27.4 | 0 | 2016-11-11 | 10.3 | 7.7 | 0 | 15.67 | 0
2025-11-11 | -3.3 | 21.3 | 0 | 2024-11-11 | 6.3 | 11.7 | 0 | 2023-11-11 | -2.8 | 20.8 | 0 | 2022-11-11 | 11.5 | 6.5 | 0 | 2021-11-11 | 0.5 | 17.5 | 0 | 2020-11-11 | 17 | 1 | 0 | 2019-11-11 | -5.2 | 23.2 | 0 | 2018-11-11 | -4.4 | 22.4 | 0 | 2017-11-11 | -9.5 | 27.5 | 0 | 2016-11-11 | 10.6 | 7.4 | 0 | 15.93 | 0
2025-11-11 | -3.5 | 21.5 | 0 | 2024-11-11 | 7.3 | 10.7 | 0 | 2023-11-11 | -3.1 | 21.1 | 0 | 2022-11-11 | 11.2 | 6.8 | 0 | 2021-11-11 | 0.1 | 17.9 | 0 | 2020-11-11 | 17.1 | 0.9 | 0 | 2019-11-11 | -5.5 | 23.5 | 0 | 2018-11-11 | -4.2 | 22.2 | 0 | 2017-11-11 | -10 | 28 | 0 | 2016-11-11 | 8 | 10 | 0 | 16.26 | 0
2025-11-11 | -3.5 | 21.5 | 0 | 2024-11-11 | 8.2 | 9.8 | 0 | 2023-11-11 | -3.8 | 21.8 | 0 | 2022-11-11 | 10.8 | 7.2 | 0 | 2021-11-11 | -0.2 | 18.2 | 0 | 2020-11-11 | 17.1 | 0.9 | 0 | 2019-11-11 | -5.8 | 23.8 | 0 | 2018-11-11 | -4.9 | 22.9 | 0 | 2017-11-11 | -9.8 | 27.8 | 0 | 2016-11-11 | 6.9 | 11.1 | 0 | 16.5 | 0
2025-11-11 | -3.7 | 21.7 | 0 | 2024-11-11 | 8.7 | 9.3 | 0 | 2023-11-11 | -4.2 | 22.2 | 0 | 2022-11-11 | 10.6 | 7.4 | 0 | 2021-11-11 | -1.6 | 19.6 | 0 | 2020-11-11 | 16.9 | 1.1 | 0 | 2019-11-11 | -6 | 24 | 0 | 2018-11-11 | -6.3 | 24.3 | 0 | 2017-11-11 | -10.3 | 28.3 | 0 | 2016-11-11 | 5.1 | 12.9 | 0 | 17.08 | 0
2025-11-11 | -3.7 | 21.7 | 0 | 2024-11-11 | 8.8 | 9.2 | 0 | 2023-11-11 | -3.6 | 21.6 | 0 | 2022-11-11 | 10.3 | 7.7 | 0 | 2021-11-11 | -1.5 | 19.5 | 0 | 2020-11-11 | 16.6 | 1.4 | 0 | 2019-11-11 | -6.2 | 24.2 | 0 | 2018-11-11 | -6.4 | 24.4 | 0 | 2017-11-11 | -10.3 | 28.3 | 0 | 2016-11-11 | 4.1 | 13.9 | 0 | 17.19 | 0
2025-11-11 | -3.7 | 21.7 | 0 | 2024-11-11 | 9.6 | 8.4 | 0 | 2023-11-11 | -3.6 | 21.6 | 0 | 2022-11-11 | 10.7 | 7.3 | 0 | 2021-11-11 | -2.4 | 20.4 | 0 | 2020-11-11 | 16.8 | 1.2 | 0 | 2019-11-11 | -6.7 | 24.7 | 0 | 2018-11-11 | -6.4 | 24.4 | 0 | 2017-11-11 | -11.6 | 29.6 | 0 | 2016-11-11 | 2.8 | 15.2 | 0 | 17.45 | 0
2025-11-11 | -3.6 | 21.6 | 0 | 2024-11-11 | 10.1 | 7.9 | 0 | 2023-11-11 | -2.2 | 20.2 | 0 | 2022-11-11 | 10.6 | 7.4 | 0 | 2021-11-11 | -0.2 | 18.2 | 0 | 2020-11-11 | 15.9 | 2.1 | 0 | 2019-11-11 | -6.6 | 24.6 | 0 | 2018-11-11 | -5.9 | 23.9 | 0 | 2017-11-11 | -8.7 | 26.7 | 0 | 2016-11-11 | 3.4 | 14.6 | 0 | 16.72 | 0
2025-11-11 | -3.5 | 21.5 | 0 | 2024-11-11 | 10.9 | 7.1 | 0 | 2023-11-11 | -0.8 | 18.8 | 0 | 2022-11-11 | 12 | 6 | 0 | 2021-11-11 | 1.9 | 16.1 | 0 | 2020-11-11 | 16.2 | 1.8 | 0 | 2019-11-11 | -6.4 | 24.4 | 0 | 2018-11-11 | -4.7 | 22.7 | 0 | 2017-11-11 | -7.6 | 25.6 | 0 | 2016-11-11 | 3.2 | 14.8 | 0 | 15.88 | 0
2025-11-11 | -3.4 | 21.4 | 0 | 2024-11-11 | 10.9 | 7.1 | 0 | 2023-11-11 | 0.2 | 17.8 | 0 | 2022-11-11 | 13.7 | 4.3 | 0 | 2021-11-11 | 3.8 | 14.2 | 0 | 2020-11-11 | 16.3 | 1.7 | 0 | 2019-11-11 | -5.6 | 23.6 | 0 | 2018-11-11 | -4.2 | 22.2 | 0 | 2017-11-11 | -6.5 | 24.5 | 0 | 2016-11-11 | 3.2 | 14.8 | 0 | 15.16 | 0
2025-11-11 | -3 | 21 | 0 | 2024-11-11 | 11.7 | 6.3 | 0 | 2023-11-11 | 0.4 | 17.6 | 0 | 2022-11-11 | 14.7 | 3.3 | 0 | 2021-11-11 | 5.5 | 12.5 | 0 | 2020-11-11 | 17.1 | 0.9 | 0 | 2019-11-11 | -5.1 | 23.1 | 0 | 2018-11-11 | -3.2 | 21.2 | 0 | 2017-11-11 | -5 | 23 | 0 | 2016-11-11 | 3.6 | 14.4 | 0 | 14.33 | 0
2025-11-11 | -2.1 | 20.1 | 0 | 2024-11-11 | 11.6 | 6.4 | 0 | 2023-11-11 | 0.8 | 17.2 | 0 | 2022-11-11 | 16.1 | 1.9 | 0 | 2021-11-11 | 5.9 | 12.1 | 0 | 2020-11-11 | 17.9 | 0.1 | 0 | 2019-11-11 | -5.3 | 23.3 | 0 | 2018-11-11 | -2.4 | 20.4 | 0 | 2017-11-11 | -4.2 | 22.2 | 0 | 2016-11-11 | 4.1 | 13.9 | 0 | 13.76 | 0
2025-11-11 | -1 | 19 | 0 | 2024-11-11 | 12.1 | 5.9 | 0 | 2023-11-11 | 1.1 | 16.9 | 0 | 2022-11-11 | 16.8 | 1.2 | 0 | 2021-11-11 | 6.5 | 11.5 | 0 | 2020-11-11 | 18.1 | 0 | 0.1 | 2019-11-11 | -5 | 23 | 0 | 2018-11-11 | -1.3 | 19.3 | 0 | 2017-11-11 | -3.3 | 21.3 | 0 | 2016-11-11 | 5.2 | 12.8 | 0 | 13.09 | 0.01
2025-11-11 | -0.4 | 18.4 | 0 | 2024-11-11 | 11.8 | 6.2 | 0 | 2023-11-11 | 1.1 | 16.9 | 0 | 2022-11-11 | 17.1 | 0.9 | 0 | 2021-11-11 | 6.9 | 11.1 | 0 | 2020-11-11 | 18.9 | 0 | 0.9 | 2019-11-11 | -4.9 | 22.9 | 0 | 2018-11-11 | -0.7 | 18.7 | 0 | 2017-11-11 | -2.5 | 20.5 | 0 | 2016-11-11 | 5.1 | 12.9 | 0 | 12.85 | 0.09
2025-11-11 | -0.3 | 18.3 | 0 | 2024-11-11 | 10.4 | 7.6 | 0 | 2023-11-11 | 1.2 | 16.8 | 0 | 2022-11-11 | 16.8 | 1.2 | 0 | 2021-11-11 | 6.8 | 11.2 | 0 | 2020-11-11 | 19 | 0 | 1 | 2019-11-11 | -5.2 | 23.2 | 0 | 2018-11-11 | -0.7 | 18.7 | 0 | 2017-11-11 | -2.5 | 20.5 | 0 | 2016-11-11 | 4.9 | 13.1 | 0 | 13.06 | 0.1
2025-11-11 | -0.3 | 18.3 | 0 | 2024-11-11 | 10.4 | 7.6 | 0 | 2023-11-11 | 0.8 | 17.2 | 0 | 2022-11-11 | 15 | 3 | 0 | 2021-11-11 | 6.3 | 11.7 | 0 | 2020-11-11 | 17.6 | 0.4 | 0 | 2019-11-11 | -6.6 | 24.6 | 0 | 2018-11-11 | -1.1 | 19.1 | 0 | 2017-11-11 | -2.9 | 20.9 | 0 | 2016-11-11 | 4.2 | 13.8 | 0 | 13.66 | 0
2025-11-11 | -0.9 | 18.9 | 0 | 2024-11-11 | 10 | 8 | 0 | 2023-11-11 | 0.4 | 17.6 | 0 | 2022-11-11 | 13.9 | 4.1 | 0 | 2021-11-11 | 5.9 | 12.1 | 0 | 2020-11-11 | 16.3 | 1.7 | 0 | 2019-11-11 | -7 | 25 | 0 | 2018-11-11 | -2.6 | 20.6 | 0 | 2017-11-11 | -4.1 | 22.1 | 0 | 2016-11-11 | 3.6 | 14.4 | 0 | 14.45 | 0
2025-11-11 | -1.1 | 19.1 | 0 | 2024-11-11 | 9.8 | 8.2 | 0 | 2023-11-11 | 0.3 | 17.7 | 0 | 2022-11-11 | 14.1 | 3.9 | 0 | 2021-11-11 | 5.5 | 12.5 | 0 | 2020-11-11 | 14.8 | 3.2 | 0 | 2019-11-11 | -7 | 25 | 0 | 2018-11-11 | -3.2 | 21.2 | 0 | 2017-11-11 | -4.2 | 22.2 | 0 | 2016-11-11 | 2.7 | 15.3 | 0 | 14.83 | 0
2025-11-11 | -0.6 | 18.6 | 0 | 2024-11-11 | 9.4 | 8.6 | 0 | 2023-11-11 | 0.2 | 17.8 | 0 | 2022-11-11 | 14 | 4 | 0 | 2021-11-11 | 5.2 | 12.8 | 0 | 2020-11-11 | 11.9 | 6.1 | 0 | 2019-11-11 | -7.2 | 25.2 | 0 | 2018-11-11 | -5.1 | 23.1 | 0 | 2017-11-11 | -4.4 | 22.4 | 0 | 2016-11-11 | 2.3 | 15.7 | 0 | 15.43 | 0
2025-11-11 | -1.1 | 19.1 | 0 | 2024-11-11 | 9.3 | 8.7 | 0 | 2023-11-11 | 0 | 18 | 0 | 2022-11-11 | 14.1 | 3.9 | 0 | 2021-11-11 | 5.2 | 12.8 | 0 | 2020-11-11 | 9.1 | 8.9 | 0 | 2019-11-11 | -7.3 | 25.3 | 0 | 2018-11-11 | -3.5 | 21.5 | 0 | 2017-11-11 | -5 | 23 | 0 | 2016-11-11 | 1.7 | 16.3 | 0 | 15.75 | 0
2025-11-11 | -1.1 | 19.1 | 0 | 2024-11-11 | 7.2 | 10.8 | 0 | 2023-11-11 | -0.1 | 18.1 | 0 | 2022-11-11 | 14.3 | 3.7 | 0 | 2021-11-11 | 4.8 | 13.2 | 0 | 2020-11-11 | 7.4 | 10.6 | 0 | 2019-11-11 | -7.4 | 25.4 | 0 | 2018-11-11 | -5.1 | 23.1 | 0 | 2017-11-11 | -5.5 | 23.5 | 0 | 2016-11-11 | 2 | 16 | 0 | 16.35 | 0
2025-11-11 | -2.1 | 20.1 | 0 | 2024-11-11 | 5.5 | 12.5 | 0 | 2023-11-11 | -0.1 | 18.1 | 0 | 2022-11-11 | 14.2 | 3.8 | 0 | 2021-11-11 | 4.8 | 13.2 | 0 | 2020-11-11 | 6.5 | 11.5 | 0 | 2019-11-11 | -7.3 | 25.3 | 0 | 2018-11-11 | -4.3 | 22.3 | 0 | 2017-11-11 | -5.2 | 23.2 | 0 | 2016-11-11 | 1.5 | 16.5 | 0 | 16.65 | 0
2025-11-11 | -2.9 | 20.9 | 0 | 2024-11-11 | 5.1 | 12.9 | 0 | 2023-11-11 | -0.5 | 18.5 | 0 | 2022-11-11 | 13.8 | 4.2 | 0 | 2021-11-11 | 4.9 | 13.1 | 0 | 2020-11-11 | 4.4 | 13.6 | 0 | 2019-11-11 | -7.3 | 25.3 | 0 | 2018-11-11 | -3.6 | 21.6 | 0 | 2017-11-11 | -4.9 | 22.9 | 0 | 2016-11-11 | 1.4 | 16.6 | 0 | 16.96 | 0
2025-11-12 | -3.1 | 21.1 | 0 | 2024-11-12 | 4.2 | 13.8 | 0 | 2023-11-12 | -0.9 | 18.9 | 0 | 2022-11-12 | 13.4 | 4.6 | 0 | 2021-11-12 | 5 | 13 | 0 | 2020-11-12 | 2.7 | 15.3 | 0 | 2019-11-12 | -7.4 | 25.4 | 0 | 2018-11-12 | -4.3 | 22.3 | 0 | 2017-11-12 | -4.5 | 22.5 | 0 | 2016-11-12 | 1.4 | 16.6 | 0 | 17.35 | 0
2025-11-12 | -1.6 | 19.6 | 0 | 2024-11-12 | 3.4 | 14.6 | 0 | 2023-11-12 | -1.1 | 19.1 | 0 | 2022-11-12 | 13.4 | 4.6 | 0 | 2021-11-12 | 5.2 | 12.8 | 0 | 2020-11-12 | 2.4 | 15.6 | 0 | 2019-11-12 | -7.5 | 25.5 | 0 | 2018-11-12 | -4.7 | 22.7 | 0 | 2017-11-12 | -4.3 | 22.3 | 0 | 2016-11-12 | 0.9 | 17.1 | 0 | 17.39 | 0
2025-11-12 | -0.7 | 18.7 | 0 | 2024-11-12 | 2.8 | 15.2 | 0 | 2023-11-12 | -1 | 19 | 0 | 2022-11-12 | 13.3 | 4.7 | 0 | 2021-11-12 | 5.8 | 12.2 | 0 | 2020-11-12 | 1.6 | 16.4 | 0 | 2019-11-12 | -7.6 | 25.6 | 0 | 2018-11-12 | -4.7 | 22.7 | 0 | 2017-11-12 | -4.3 | 22.3 | 0 | 2016-11-12 | 0 | 18 | 0 | 17.48 | 0
2025-11-12 | -0.1 | 18.1 | 0 | 2024-11-12 | 2.2 | 15.8 | 0 | 2023-11-12 | -1.7 | 19.7 | 0 | 2022-11-12 | 13.2 | 4.8 | 0 | 2021-11-12 | 5.3 | 12.7 | 0 | 2020-11-12 | 1.8 | 16.2 | 0 | 2019-11-12 | -7.8 | 25.8 | 0 | 2018-11-12 | -3.7 | 21.7 | 0 | 2017-11-12 | -4.2 | 22.2 | 0 | 2016-11-12 | -0.4 | 18.4 | 0 | 17.54 | 0
2025-11-12 | -0.4 | 18.4 | 0 | 2024-11-12 | 2.3 | 15.7 | 0 | 2023-11-12 | -2.2 | 20.2 | 0 | 2022-11-12 | 13.4 | 4.6 | 0 | 2021-11-12 | 4.7 | 13.3 | 0 | 2020-11-12 | 2.2 | 15.8 | 0 | 2019-11-12 | -8 | 26 | 0 | 2018-11-12 | -3.2 | 21.2 | 0 | 2017-11-12 | -4.5 | 22.5 | 0 | 2016-11-12 | -2.2 | 20.2 | 0 | 17.79 | 0
2025-11-12 | -0.6 | 18.6 | 0 | 2024-11-12 | 2.1 | 15.9 | 0 | 2023-11-12 | -2.6 | 20.6 | 0 | 2022-11-12 | 13.5 | 4.5 | 0 | 2021-11-12 | 5.3 | 12.7 | 0 | 2020-11-12 | 1.1 | 16.9 | 0 | 2019-11-12 | -8.2 | 26.2 | 0 | 2018-11-12 | -2.4 | 20.4 | 0 | 2017-11-12 | -4.6 | 22.6 | 0 | 2016-11-12 | -3.2 | 21.2 | 0 | 17.96 | 0
2025-11-12 | -0.5 | 18.5 | 0 | 2024-11-12 | 1.1 | 16.9 | 0 | 2023-11-12 | -3.4 | 21.4 | 0 | 2022-11-12 | 13.2 | 4.8 | 0 | 2021-11-12 | 6.2 | 11.8 | 0 | 2020-11-12 | 0.2 | 17.8 | 0 | 2019-11-12 | -8.2 | 26.2 | 0 | 2018-11-12 | -2.7 | 20.7 | 0 | 2017-11-12 | -4.5 | 22.5 | 0 | 2016-11-12 | -4 | 22 | 0 | 18.26 | 0
2025-11-12 | -0.4 | 18.4 | 0 | 2024-11-12 | 0.7 | 17.3 | 0 | 2023-11-12 | -3.8 | 21.8 | 0 | 2022-11-12 | 12.6 | 5.4 | 0 | 2021-11-12 | 7.2 | 10.8 | 0 | 2020-11-12 | 2 | 16 | 0 | 2019-11-12 | -8.5 | 26.5 | 0 | 2018-11-12 | -2.9 | 20.9 | 0 | 2017-11-12 | -4.5 | 22.5 | 0 | 2016-11-12 | -4.5 | 22.5 | 0 | 18.21 | 0
2025-11-12 | -0.1 | 18.1 | 0 | 2024-11-12 | 1.3 | 16.7 | 0 | 2023-11-12 | -2.4 | 20.4 | 0 | 2022-11-12 | 12.4 | 5.6 | 0 | 2021-11-12 | 8.4 | 9.6 | 0 | 2020-11-12 | 2.6 | 15.4 | 0 | 2019-11-12 | -8.6 | 26.6 | 0 | 2018-11-12 | -2.5 | 20.5 | 0 | 2017-11-12 | -4.1 | 22.1 | 0 | 2016-11-12 | -2.6 | 20.6 | 0 | 17.56 | 0
2025-11-12 | 0 | 18 | 0 | 2024-11-12 | 2.4 | 15.6 | 0 | 2023-11-12 | -1 | 19 | 0 | 2022-11-12 | 12 | 6 | 0 | 2021-11-12 | 9.1 | 8.9 | 0 | 2020-11-12 | 4.2 | 13.8 | 0 | 2019-11-12 | -8.2 | 26.2 | 0 | 2018-11-12 | -1.3 | 19.3 | 0 | 2017-11-12 | -3.1 | 21.1 | 0 | 2016-11-12 | -0.5 | 18.5 | 0 | 16.64 | 0
2025-11-12 | 0.5 | 17.5 | 0 | 2024-11-12 | 3.7 | 14.3 | 0 | 2023-11-12 | -1.2 | 19.2 | 0 | 2022-11-12 | 11.6 | 6.4 | 0 | 2021-11-12 | 9.1 | 8.9 | 0 | 2020-11-12 | 5.3 | 12.7 | 0 | 2019-11-12 | -8.5 | 26.5 | 0 | 2018-11-12 | 0.5 | 17.5 | 0 | 2017-11-12 | -0.6 | 18.6 | 0 | 2016-11-12 | 1 | 17 | 0 | 15.86 | 0
2025-11-12 | 0.6 | 17.4 | 0 | 2024-11-12 | 4 | 14 | 0 | 2023-11-12 | 0.1 | 17.9 | 0 | 2022-11-12 | 10.5 | 7.5 | 0 | 2021-11-12 | 10.4 | 7.6 | 0 | 2020-11-12 | 5.8 | 12.2 | 0 | 2019-11-12 | -8.7 | 26.7 | 0 | 2018-11-12 | 2.6 | 15.4 | 0 | 2017-11-12 | 0.2 | 17.8 | 0 | 2016-11-12 | 2.6 | 15.4 | 0 | 15.19 | 0
2025-11-12 | 1.1 | 16.9 | 0 | 2024-11-12 | 4.4 | 13.6 | 0 | 2023-11-12 | 0.3 | 17.7 | 0 | 2022-11-12 | 10 | 8 | 0 | 2021-11-12 | 10.4 | 7.6 | 0 | 2020-11-12 | 5.9 | 12.1 | 0 | 2019-11-12 | -8.6 | 26.6 | 0 | 2018-11-12 | 4.2 | 13.8 | 0 | 2017-11-12 | 1.9 | 16.1 | 0 | 2016-11-12 | 3.6 | 14.4 | 0 | 14.68 | 0
2025-11-12 | 1.5 | 16.5 | 0 | 2024-11-12 | 4 | 14 | 0 | 2023-11-12 | 1.3 | 16.7 | 0 | 2022-11-12 | 9 | 9 | 0 | 2021-11-12 | 10.9 | 7.1 | 0 | 2020-11-12 | 7.5 | 10.5 | 0 | 2019-11-12 | -8.1 | 26.1 | 0 | 2018-11-12 | 4.8 | 13.2 | 0 | 2017-11-12 | 2.4 | 15.6 | 0 | 2016-11-12 | 3.6 | 14.4 | 0 | 14.31 | 0
2025-11-12 | 1.5 | 16.5 | 0 | 2024-11-12 | 4.7 | 13.3 | 0 | 2023-11-12 | 1.8 | 16.2 | 0 | 2022-11-12 | 9 | 9 | 0 | 2021-11-12 | 12.2 | 5.8 | 0 | 2020-11-12 | 7.1 | 10.9 | 0 | 2019-11-12 | -8 | 26 | 0 | 2018-11-12 | 4.8 | 13.2 | 0 | 2017-11-12 | 3.1 | 14.9 | 0 | 2016-11-12 | 4.3 | 13.7 | 0 | 13.95 | 0
2025-11-12 | 1.3 | 16.7 | 0 | 2024-11-12 | 4.4 | 13.6 | 0 | 2023-11-12 | 1.6 | 16.4 | 0 | 2022-11-12 | 8.3 | 9.7 | 0 | 2021-11-12 | 11.6 | 6.4 | 0 | 2020-11-12 | 7.2 | 10.8 | 0 | 2019-11-12 | -9 | 27 | 0 | 2018-11-12 | 4.8 | 13.2 | 0 | 2017-11-12 | 3 | 15 | 0 | 2016-11-12 | 4.8 | 13.2 | 0 | 14.2 | 0
2025-11-12 | 0.5 | 17.5 | 0 | 2024-11-12 | 3.5 | 14.5 | 0 | 2023-11-12 | 1 | 17 | 0 | 2022-11-12 | 7.5 | 10.5 | 0 | 2021-11-12 | 10.2 | 7.8 | 0 | 2020-11-12 | 6 | 12 | 0 | 2019-11-12 | -9.5 | 27.5 | 0 | 2018-11-12 | 3.9 | 14.1 | 0 | 2017-11-12 | 1.8 | 16.2 | 0 | 2016-11-12 | 4.8 | 13.2 | 0 | 15.03 | 0
2025-11-12 | 0.1 | 17.9 | 0 | 2024-11-12 | 2.7 | 15.3 | 0 | 2023-11-12 | -0.2 | 18.2 | 0 | 2022-11-12 | 7.3 | 10.7 | 0 | 2021-11-12 | 8.8 | 9.2 | 0 | 2020-11-12 | 4.5 | 13.5 | 0 | 2019-11-12 | -10.3 | 28.3 | 0 | 2018-11-12 | 3.5 | 14.5 | 0 | 2017-11-12 | -0.1 | 18.1 | 0 | 2016-11-12 | 4.9 | 13.1 | 0 | 15.88 | 0
2025-11-12 | 0.4 | 17.6 | 0 | 2024-11-12 | 2.2 | 15.8 | 0 | 2023-11-12 | -3 | 21 | 0 | 2022-11-12 | 7 | 11 | 0 | 2021-11-12 | 7.1 | 10.9 | 0 | 2020-11-12 | 2.4 | 15.6 | 0 | 2019-11-12 | -10.2 | 28.2 | 0 | 2018-11-12 | 1.9 | 16.1 | 0 | 2017-11-12 | -0.5 | 18.5 | 0 | 2016-11-12 | 5.3 | 12.7 | 0 | 16.74 | 0
2025-11-12 | 0.5 | 17.5 | 0 | 2024-11-12 | 1.3 | 16.7 | 0 | 2023-11-12 | -3 | 21 | 0 | 2022-11-12 | 6.7 | 11.3 | 0 | 2021-11-12 | 5.8 | 12.2 | 0 | 2020-11-12 | 1.5 | 16.5 | 0 | 2019-11-12 | -10.7 | 28.7 | 0 | 2018-11-12 | 2 | 16 | 0 | 2017-11-12 | -0.8 | 18.8 | 0 | 2016-11-12 | 5.5 | 12.5 | 0 | 17.12 | 0
2025-11-12 | 1 | 17 | 0 | 2024-11-12 | 0.5 | 17.5 | 0 | 2023-11-12 | -3 | 21 | 0 | 2022-11-12 | 6.2 | 11.8 | 0 | 2021-11-12 | 4.9 | 13.1 | 0 | 2020-11-12 | -0.6 | 18.6 | 0 | 2019-11-12 | -11.4 | 29.4 | 0 | 2018-11-12 | 1.7 | 16.3 | 0 | 2017-11-12 | -0.4 | 18.4 | 0 | 2016-11-12 | 5.7 | 12.3 | 0 | 17.54 | 0
2025-11-12 | 1.4 | 16.6 | 0 | 2024-11-12 | -0.1 | 18.1 | 0 | 2023-11-12 | -2.6 | 20.6 | 0 | 2022-11-12 | 6 | 12 | 0 | 2021-11-12 | 3.5 | 14.5 | 0 | 2020-11-12 | -0.5 | 18.5 | 0 | 2019-11-12 | -11.6 | 29.6 | 0 | 2018-11-12 | 1.1 | 16.9 | 0 | 2017-11-12 | -0.6 | 18.6 | 0 | 2016-11-12 | 6.3 | 11.7 | 0 | 17.71 | 0
2025-11-12 | 1.2 | 16.8 | 0 | 2024-11-12 | -0.6 | 18.6 | 0 | 2023-11-12 | -5.8 | 23.8 | 0 | 2022-11-12 | 5.1 | 12.9 | 0 | 2021-11-12 | 4 | 14 | 0 | 2020-11-12 | -0.7 | 18.7 | 0 | 2019-11-12 | -11.8 | 29.8 | 0 | 2018-11-12 | 0.7 | 17.3 | 0 | 2017-11-12 | -0.3 | 18.3 | 0 | 2016-11-12 | 6.5 | 11.5 | 0 | 18.17 | 0
2025-11-12 | 1.5 | 16.5 | 0 | 2024-11-12 | -1.3 | 19.3 | 0 | 2023-11-12 | -4.2 | 22.2 | 0 | 2022-11-12 | 4.5 | 13.5 | 0 | 2021-11-12 | 5 | 13 | 0 | 2020-11-12 | -1.9 | 19.9 | 0 | 2019-11-12 | -12.7 | 30.7 | 0 | 2018-11-12 | 0.7 | 17.3 | 0 | 2017-11-12 | -0.9 | 18.9 | 0 | 2016-11-12 | 6 | 12 | 0 | 18.33 | 0
2025-11-13 | 1.2 | 16.8 | 0 | 2024-11-13 | -1.5 | 19.5 | 0 | 2023-11-13 | -5.3 | 23.3 | 0 | 2022-11-13 | 4.3 | 13.7 | 0 | 2021-11-13 | 2 | 16 | 0 | 2020-11-13 | -0.2 | 18.2 | 0 | 2019-11-13 | -13 | 31 | 0 | 2018-11-13 | 1.2 | 16.8 | 0 | 2017-11-13 | -1.1 | 19.1 | 0 | 2016-11-13 | 5.9 | 12.1 | 0 | 18.65 | 0
2025-11-13 | 1.3 | 16.7 | 0 | 2024-11-13 | -3.2 | 21.2 | 0 | 2023-11-13 | -4.8 | 22.8 | 0 | 2022-11-13 | 3.4 | 14.6 | 0 | 2021-11-13 | 2.3 | 15.7 | 0 | 2020-11-13 | -2.2 | 20.2 | 0 | 2019-11-13 | -13.7 | 31.7 | 0 | 2018-11-13 | 1.4 | 16.6 | 0 | 2017-11-13 | -1.3 | 19.3 | 0 | 2016-11-13 | 5.6 | 12.4 | 0 | 19.12 | 0
2025-11-13 | 1.1 | 16.9 | 0 | 2024-11-13 | -2.1 | 20.1 | 0 | 2023-11-13 | -5.8 | 23.8 | 0 | 2022-11-13 | 2 | 16 | 0 | 2021-11-13 | 2.3 | 15.7 | 0 | 2020-11-13 | -2.4 | 20.4 | 0 | 2019-11-13 | -13.6 | 31.6 | 0 | 2018-11-13 | 1.1 | 16.9 | 0 | 2017-11-13 | -1.3 | 19.3 | 0 | 2016-11-13 | 5.8 | 12.2 | 0 | 19.29 | 0
2025-11-13 | 0.9 | 17.1 | 0 | 2024-11-13 | -2.5 | 20.5 | 0 | 2023-11-13 | -6.5 | 24.5 | 0 | 2022-11-13 | 2 | 16 | 0 | 2021-11-13 | 1.8 | 16.2 | 0 | 2020-11-13 | -1.9 | 19.9 | 0 | 2019-11-13 | -14.1 | 32.1 | 0 | 2018-11-13 | 0.2 | 17.8 | 0 | 2017-11-13 | -1.5 | 19.5 | 0 | 2016-11-13 | 5.7 | 12.3 | 0 | 19.59 | 0
2025-11-13 | 0.9 | 17.1 | 0 | 2024-11-13 | -3.4 | 21.4 | 0 | 2023-11-13 | -6.5 | 24.5 | 0 | 2022-11-13 | 1.9 | 16.1 | 0 | 2021-11-13 | 0.7 | 17.3 | 0 | 2020-11-13 | -1.2 | 19.2 | 0 | 2019-11-13 | -14.1 | 32.1 | 0 | 2018-11-13 | 0 | 18 | 0 | 2017-11-13 | -1.5 | 19.5 | 0 | 2016-11-13 | 5.6 | 12.4 | 0 | 19.76 | 0
2025-11-13 | 0.7 | 17.3 | 0 | 2024-11-13 | -3.5 | 21.5 | 0 | 2023-11-13 | -6.5 | 24.5 | 0 | 2022-11-13 | 1.6 | 16.4 | 0 | 2021-11-13 | 1.1 | 16.9 | 0 | 2020-11-13 | -1.2 | 19.2 | 0 | 2019-11-13 | -14.2 | 32.2 | 0 | 2018-11-13 | 0 | 18 | 0 | 2017-11-13 | -1.5 | 19.5 | 0 | 2016-11-13 | 5.4 | 12.6 | 0 | 19.81 | 0
2025-11-13 | 0.7 | 17.3 | 0 | 2024-11-13 | -4.7 | 22.7 | 0 | 2023-11-13 | -7.7 | 25.7 | 0 | 2022-11-13 | 1.3 | 16.7 | 0 | 2021-11-13 | 1.9 | 16.1 | 0 | 2020-11-13 | -1.3 | 19.3 | 0 | 2019-11-13 | -14 | 32 | 0 | 2018-11-13 | 0 | 18 | 0 | 2017-11-13 | -1.6 | 19.6 | 0 | 2016-11-13 | 4.5 | 13.5 | 0 | 20.09 | 0
2025-11-13 | 0.6 | 17.4 | 0 | 2024-11-13 | -5.2 | 23.2 | 0 | 2023-11-13 | -6.1 | 24.1 | 0 | 2022-11-13 | 0.9 | 17.1 | 0 | 2021-11-13 | 2.7 | 15.3 | 0 | 2020-11-13 | -0.8 | 18.8 | 0 | 2019-11-13 | -14.2 | 32.2 | 0 | 2018-11-13 | 0 | 18 | 0 | 2017-11-13 | -1.7 | 19.7 | 0 | 2016-11-13 | 3.3 | 14.7 | 0 | 20.05 | 0
2025-11-13 | 0.8 | 17.2 | 0 | 2024-11-13 | -2.6 | 20.6 | 0 | 2023-11-13 | -4.2 | 22.2 | 0 | 2022-11-13 | 0.5 | 17.5 | 0 | 2021-11-13 | 4 | 14 | 0 | 2020-11-13 | -0.1 | 18.1 | 0 | 2019-11-13 | -13.9 | 31.9 | 0 | 2018-11-13 | 0 | 18 | 0 | 2017-11-13 | -1.6 | 19.6 | 0 | 2016-11-13 | 4.2 | 13.8 | 0 | 19.29 | 0
2025-11-13 | 1.3 | 16.7 | 0 | 2024-11-13 | -0.6 | 18.6 | 0 | 2023-11-13 | -3.1 | 21.1 | 0 | 2022-11-13 | 0.3 | 17.7 | 0 | 2021-11-13 | 4.4 | 13.6 | 0 | 2020-11-13 | 1.1 | 16.9 | 0 | 2019-11-13 | -12.9 | 30.9 | 0 | 2018-11-13 | 0.2 | 17.8 | 0 | 2017-11-13 | -1.3 | 19.3 | 0 | 2016-11-13 | 6 | 12 | 0 | 18.46 | 0
2025-11-13 | 1.8 | 16.2 | 0 | 2024-11-13 | 0.8 | 17.2 | 0 | 2023-11-13 | -2.2 | 20.2 | 0 | 2022-11-13 | 0.5 | 17.5 | 0 | 2021-11-13 | 4.3 | 13.7 | 0 | 2020-11-13 | 2.3 | 15.7 | 0 | 2019-11-13 | -12.1 | 30.1 | 0 | 2018-11-13 | 0.3 | 17.7 | 0 | 2017-11-13 | -0.9 | 18.9 | 0 | 2016-11-13 | 8.2 | 9.8 | 0 | 17.7 | 0
2025-11-13 | 2.2 | 15.8 | 0 | 2024-11-13 | 1.6 | 16.4 | 0 | 2023-11-13 | -1.5 | 19.5 | 0 | 2022-11-13 | 0.5 | 17.5 | 0 | 2021-11-13 | 3.7 | 14.3 | 0 | 2020-11-13 | 4.1 | 13.9 | 0 | 2019-11-13 | -11.1 | 29.1 | 0 | 2018-11-13 | 0.6 | 17.4 | 0 | 2017-11-13 | -0.3 | 18.3 | 0 | 2016-11-13 | 9.4 | 8.6 | 0 | 17.08 | 0
2025-11-13 | 2.6 | 15.4 | 0 | 2024-11-13 | 2.6 | 15.4 | 0 | 2023-11-13 | -1.8 | 19.8 | 0 | 2022-11-13 | 0.8 | 17.2 | 0 | 2021-11-13 | 4.1 | 13.9 | 0 | 2020-11-13 | 5.4 | 12.6 | 0 | 2019-11-13 | -10.3 | 28.3 | 0 | 2018-11-13 | 0.5 | 17.5 | 0 | 2017-11-13 | 0.1 | 17.9 | 0 | 2016-11-13 | 10.9 | 7.1 | 0 | 16.51 | 0
2025-11-13 | 3.3 | 14.7 | 0 | 2024-11-13 | 3.2 | 14.8 | 0 | 2023-11-13 | -1.4 | 19.4 | 0 | 2022-11-13 | 1.2 | 16.8 | 0 | 2021-11-13 | 4.9 | 13.1 | 0 | 2020-11-13 | 4.9 | 13.1 | 0 | 2019-11-13 | -9.6 | 27.6 | 0 | 2018-11-13 | 0.2 | 17.8 | 0 | 2017-11-13 | 0.3 | 17.7 | 0 | 2016-11-13 | 11.6 | 6.4 | 0 | 16.14 | 0
2025-11-13 | 3.4 | 14.6 | 0 | 2024-11-13 | 3.5 | 14.5 | 0 | 2023-11-13 | -1.2 | 19.2 | 0 | 2022-11-13 | 0.9 | 17.1 | 0 | 2021-11-13 | 5.7 | 12.3 | 0 | 2020-11-13 | 5.9 | 12.1 | 0 | 2019-11-13 | -9.2 | 27.2 | 0 | 2018-11-13 | -1 | 19 | 0 | 2017-11-13 | 0.6 | 17.4 | 0 | 2016-11-13 | 11.9 | 6.1 | 0 | 15.95 | 0
2025-11-13 | 4.2 | 13.8 | 0 | 2024-11-13 | 3.6 | 14.4 | 0 | 2023-11-13 | -1 | 19 | 0 | 2022-11-13 | 0.3 | 17.7 | 0 | 2021-11-13 | 5.5 | 12.5 | 0 | 2020-11-13 | 5.7 | 12.3 | 0 | 2019-11-13 | -9.1 | 27.1 | 0 | 2018-11-13 | -2.4 | 20.4 | 0 | 2017-11-13 | 0.6 | 17.4 | 0 | 2016-11-13 | 11.3 | 6.7 | 0 | 16.13 | 0
2025-11-13 | 3.8 | 14.2 | 0 | 2024-11-13 | 2.1 | 15.9 | 0 | 2023-11-13 | -1.2 | 19.2 | 0 | 2022-11-13 | 0 | 18 | 0 | 2021-11-13 | 5.1 | 12.9 | 0 | 2020-11-13 | 4.7 | 13.3 | 0 | 2019-11-13 | -9.4 | 27.4 | 0 | 2018-11-13 | -2.8 | 20.8 | 0 | 2017-11-13 | 0.4 | 17.6 | 0 | 2016-11-13 | 10.4 | 7.6 | 0 | 16.69 | 0
2025-11-13 | 2.6 | 15.4 | 0 | 2024-11-13 | -0.4 | 18.4 | 0 | 2023-11-13 | -1.3 | 19.3 | 0 | 2022-11-13 | -0.1 | 18.1 | 0 | 2021-11-13 | 4.5 | 13.5 | 0 | 2020-11-13 | 3.1 | 14.9 | 0 | 2019-11-13 | -10.5 | 28.5 | 0 | 2018-11-13 | -3.3 | 21.3 | 0 | 2017-11-13 | -0.1 | 18.1 | 0 | 2016-11-13 | 8.6 | 9.4 | 0 | 17.69 | 0
2025-11-13 | 2.7 | 15.3 | 0 | 2024-11-13 | -1.3 | 19.3 | 0 | 2023-11-13 | -1.2 | 19.2 | 0 | 2022-11-13 | -0.3 | 18.3 | 0 | 2021-11-13 | 4.2 | 13.8 | 0 | 2020-11-13 | 2 | 16 | 0 | 2019-11-13 | -10.8 | 28.8 | 0 | 2018-11-13 | -5 | 23 | 0 | 2017-11-13 | -0.4 | 18.4 | 0 | 2016-11-13 | 7 | 11 | 0 | 18.31 | 0
2025-11-13 | 2.3 | 15.7 | 0 | 2024-11-13 | -2.1 | 20.1 | 0 | 2023-11-13 | -1.2 | 19.2 | 0 | 2022-11-13 | -0.9 | 18.9 | 0 | 2021-11-13 | 4.1 | 13.9 | 0 | 2020-11-13 | 2.3 | 15.7 | 0 | 2019-11-13 | -10.1 | 28.1 | 0 | 2018-11-13 | -6.2 | 24.2 | 0 | 2017-11-13 | -0.2 | 18.2 | 0 | 2016-11-13 | 6.6 | 11.4 | 0 | 18.54 | 0
2025-11-13 | 2.4 | 15.6 | 0 | 2024-11-13 | -2.2 | 20.2 | 0 | 2023-11-13 | -1.2 | 19.2 | 0 | 2022-11-13 | -1.2 | 19.2 | 0 | 2021-11-13 | 2.7 | 15.3 | 0 | 2020-11-13 | 1 | 17 | 0 | 2019-11-13 | -10.8 | 28.8 | 0 | 2018-11-13 | -6.8 | 24.8 | 0 | 2017-11-13 | -0.2 | 18.2 | 0 | 2016-11-13 | 5.6 | 12.4 | 0 | 19.07 | 0
2025-11-13 | 2.1 | 15.9 | 0 | 2024-11-13 | -2.3 | 20.3 | 0 | 2023-11-13 | -1.3 | 19.3 | 0 | 2022-11-13 | -1.4 | 19.4 | 0 | 2021-11-13 | 2.6 | 15.4 | 0 | 2020-11-13 | 1.5 | 16.5 | 0 | 2019-11-13 | -10.9 | 28.9 | 0 | 2018-11-13 | -7.3 | 25.3 | 0 | 2017-11-13 | -0.5 | 18.5 | 0 | 2016-11-13 | 5.1 | 12.9 | 0 | 19.24 | 0
2025-11-13 | 1.9 | 16.1 | 0 | 2024-11-13 | -3 | 21 | 0 | 2023-11-13 | -0.8 | 18.8 | 0 | 2022-11-13 | -1.3 | 19.3 | 0 | 2021-11-13 | 1.9 | 16.1 | 0 | 2020-11-13 | 2.2 | 15.8 | 0 | 2019-11-13 | -10.8 | 28.8 | 0 | 2018-11-13 | -7.3 | 25.3 | 0 | 2017-11-13 | -0.4 | 18.4 | 0 | 2016-11-13 | 5 | 13 | 0 | 19.26 | 0
2025-11-13 | 1 | 17 | 0 | 2024-11-13 | -3.7 | 21.7 | 0 | 2023-11-13 | -0.9 | 18.9 | 0 | 2022-11-13 | -1.5 | 19.5 | 0 | 2021-11-13 | 1.5 | 16.5 | 0 | 2020-11-13 | 2.2 | 15.8 | 0 | 2019-11-13 | -10.5 | 28.5 | 0 | 2018-11-13 | -7.4 | 25.4 | 0 | 2017-11-13 | -0.7 | 18.7 | 0 | 2016-11-13 | 5.6 | 12.4 | 0 | 19.44 | 0
2025-11-14 | 0.3 | 17.7 | 0 | 2024-11-14 | -3.8 | 21.8 | 0 | 2023-11-14 | -0.9 | 18.9 | 0 | 2022-11-14 | -1.7 | 19.7 | 0 | 2021-11-14 | 1.4 | 16.6 | 0 | 2020-11-14 | 2.8 | 15.2 | 0 | 2019-11-14 | -10.1 | 28.1 | 0 | 2018-11-14 | -8.2 | 26.2 | 0 | 2017-11-14 | -0.8 | 18.8 | 0 | 2016-11-14 | 5.7 | 12.3 | 0 | 19.53 | 0
2025-11-14 | -0.1 | 18.1 | 0 | 2024-11-14 | -3.7 | 21.7 | 0 | 2023-11-14 | -0.9 | 18.9 | 0 | 2022-11-14 | -1.8 | 19.8 | 0 | 2021-11-14 | 2.4 | 15.6 | 0 | 2020-11-14 | 2.4 | 15.6 | 0 | 2019-11-14 | -10 | 28 | 0 | 2018-11-14 | -8.9 | 26.9 | 0 | 2017-11-14 | -0.9 | 18.9 | 0 | 2016-11-14 | 5.6 | 12.4 | 0 | 19.59 | 0
2025-11-14 | -0.6 | 18.6 | 0 | 2024-11-14 | -3.9 | 21.9 | 0 | 2023-11-14 | -0.8 | 18.8 | 0 | 2022-11-14 | -1.6 | 19.6 | 0 | 2021-11-14 | 2.9 | 15.1 | 0 | 2020-11-14 | 3.2 | 14.8 | 0 | 2019-11-14 | -9.8 | 27.8 | 0 | 2018-11-14 | -8.7 | 26.7 | 0 | 2017-11-14 | -0.8 | 18.8 | 0 | 2016-11-14 | 5.6 | 12.4 | 0 | 19.45 | 0
2025-11-14 | -1.3 | 19.3 | 0 | 2024-11-14 | -4.3 | 22.3 | 0 | 2023-11-14 | -0.7 | 18.7 | 0 | 2022-11-14 | -1.6 | 19.6 | 0 | 2021-11-14 | 2.2 | 15.8 | 0 | 2020-11-14 | 2.8 | 15.2 | 0 | 2019-11-14 | -9.3 | 27.3 | 0 | 2018-11-14 | -8.8 | 26.8 | 0 | 2017-11-14 | -0.9 | 18.9 | 0 | 2016-11-14 | 5.6 | 12.4 | 0 | 19.63 | 0
2025-11-14 | -1.8 | 19.8 | 0 | 2024-11-14 | -4.2 | 22.2 | 0 | 2023-11-14 | -0.5 | 18.5 | 0 | 2022-11-14 | -1.9 | 19.9 | 0 | 2021-11-14 | 0.9 | 17.1 | 0 | 2020-11-14 | 2.7 | 15.3 | 0 | 2019-11-14 | -9.5 | 27.5 | 0 | 2018-11-14 | -8.8 | 26.8 | 0 | 2017-11-14 | -0.9 | 18.9 | 0 | 2016-11-14 | 5 | 13 | 0 | 19.9 | 0
2025-11-14 | -2.5 | 20.5 | 0 | 2024-11-14 | -5.2 | 23.2 | 0 | 2023-11-14 | -0.1 | 18.1 | 0 | 2022-11-14 | -2.2 | 20.2 | 0 | 2021-11-14 | 0.8 | 17.2 | 0 | 2020-11-14 | 2.2 | 15.8 | 0 | 2019-11-14 | -9.1 | 27.1 | 0 | 2018-11-14 | -9.6 | 27.6 | 0 | 2017-11-14 | -0.5 | 18.5 | 0 | 2016-11-14 | 5.2 | 12.8 | 0 | 20.1 | 0
2025-11-14 | -1.6 | 19.6 | 0 | 2024-11-14 | -4 | 22 | 0 | 2023-11-14 | 0.4 | 17.6 | 0 | 2022-11-14 | -2 | 20 | 0 | 2021-11-14 | -0.6 | 18.6 | 0 | 2020-11-14 | 2 | 16 | 0 | 2019-11-14 | -9.3 | 27.3 | 0 | 2018-11-14 | -10 | 28 | 0 | 2017-11-14 | -0.6 | 18.6 | 0 | 2016-11-14 | 3.9 | 14.1 | 0 | 20.18 | 0
2025-11-14 | -1.2 | 19.2 | 0 | 2024-11-14 | -4.2 | 22.2 | 0 | 2023-11-14 | 0.8 | 17.2 | 0 | 2022-11-14 | -2 | 20 | 0 | 2021-11-14 | -0.7 | 18.7 | 0 | 2020-11-14 | 2.1 | 15.9 | 0 | 2019-11-14 | -8.7 | 26.7 | 0 | 2018-11-14 | -10.3 | 28.3 | 0 | 2017-11-14 | -0.3 | 18.3 | 0 | 2016-11-14 | 3.9 | 14.1 | 0 | 20.06 | 0
2025-11-14 | -0.7 | 18.7 | 0 | 2024-11-14 | -3.4 | 21.4 | 0 | 2023-11-14 | 1.3 | 16.7 | 0 | 2022-11-14 | -1.8 | 19.8 | 0 | 2021-11-14 | 0.3 | 17.7 | 0 | 2020-11-14 | 2.3 | 15.7 | 0 | 2019-11-14 | -8.1 | 26.1 | 0 | 2018-11-14 | -10.7 | 28.7 | 0 | 2017-11-14 | -0.3 | 18.3 | 0 | 2016-11-14 | 5 | 13 | 0 | 19.61 | 0
2025-11-14 | -0.2 | 18.2 | 0 | 2024-11-14 | -2.2 | 20.2 | 0 | 2023-11-14 | 1.9 | 16.1 | 0 | 2022-11-14 | -0.8 | 18.8 | 0 | 2021-11-14 | 1.8 | 16.2 | 0 | 2020-11-14 | 2.6 | 15.4 | 0 | 2019-11-14 | -6.8 | 24.8 | 0 | 2018-11-14 | -10.3 | 28.3 | 0 | 2017-11-14 | 0 | 18 | 0 | 2016-11-14 | 6.5 | 11.5 | 0 | 18.75 | 0
2025-11-14 | 0.4 | 17.6 | 0 | 2024-11-14 | -0.4 | 18.4 | 0 | 2023-11-14 | 2.8 | 15.2 | 0 | 2022-11-14 | 0.1 | 17.9 | 0 | 2021-11-14 | 2 | 16 | 0 | 2020-11-14 | 2.6 | 15.4 | 0 | 2019-11-14 | -5.9 | 23.9 | 0 | 2018-11-14 | -9.8 | 27.8 | 0 | 2017-11-14 | 0.3 | 17.7 | 0 | 2016-11-14 | 8.8 | 9.2 | 0 | 17.91 | 0
2025-11-14 | 1 | 17 | 0 | 2024-11-14 | 0.8 | 17.2 | 0 | 2023-11-14 | 4.3 | 13.7 | 0 | 2022-11-14 | 0.3 | 17.7 | 0 | 2021-11-14 | 3.3 | 14.7 | 0 | 2020-11-14 | 3.4 | 14.6 | 0 | 2019-11-14 | -4.7 | 22.7 | 0 | 2018-11-14 | -8.7 | 26.7 | 0 | 2017-11-14 | 0.7 | 17.3 | 0 | 2016-11-14 | 10.5 | 7.5 | 0 | 16.91 | 0
2025-11-14 | 1.8 | 16.2 | 0 | 2024-11-14 | 1.8 | 16.2 | 0 | 2023-11-14 | 4 | 14 | 0 | 2022-11-14 | 0.7 | 17.3 | 0 | 2021-11-14 | 4.4 | 13.6 | 0 | 2020-11-14 | 4.1 | 13.9 | 0 | 2019-11-14 | -3.8 | 21.8 | 0 | 2018-11-14 | -8.6 | 26.6 | 0 | 2017-11-14 | 1.1 | 16.9 | 0 | 2016-11-14 | 11.4 | 6.6 | 0 | 16.31 | 0
2025-11-14 | 2.8 | 15.2 | 0 | 2024-11-14 | 3.4 | 14.6 | 0 | 2023-11-14 | 3.6 | 14.4 | 0 | 2022-11-14 | 1.8 | 16.2 | 0 | 2021-11-14 | 4.7 | 13.3 | 0 | 2020-11-14 | 4.3 | 13.7 | 0 | 2019-11-14 | -2.9 | 20.9 | 0 | 2018-11-14 | -7.7 | 25.7 | 0 | 2017-11-14 | 1.4 | 16.6 | 0 | 2016-11-14 | 12.3 | 5.7 | 0 | 15.63 | 0
2025-11-14 | 2.5 | 15.5 | 0 | 2024-11-14 | 3.2 | 14.8 | 0 | 2023-11-14 | 4.5 | 13.5 | 0 | 2022-11-14 | 2.2 | 15.8 | 0 | 2021-11-14 | 5.1 | 12.9 | 0 | 2020-11-14 | 4.3 | 13.7 | 0 | 2019-11-14 | -2.3 | 20.3 | 0 | 2018-11-14 | -7.8 | 25.8 | 0 | 2017-11-14 | 1.5 | 16.5 | 0 | 2016-11-14 | 12.9 | 5.1 | 0 | 15.39 | 0
2025-11-14 | 2.6 | 15.4 | 0 | 2024-11-14 | 2.6 | 15.4 | 0 | 2023-11-14 | 4.2 | 13.8 | 0 | 2022-11-14 | 1.6 | 16.4 | 0 | 2021-11-14 | 5.1 | 12.9 | 0 | 2020-11-14 | 4.3 | 13.7 | 0 | 2019-11-14 | -2 | 20 | 0 | 2018-11-14 | -7.4 | 25.4 | 0 | 2017-11-14 | 1.4 | 16.6 | 0 | 2016-11-14 | 13 | 5 | 0 | 15.46 | 0
2025-11-14 | 0.3 | 17.7 | 0 | 2024-11-14 | 2 | 16 | 0 | 2023-11-14 | 3.9 | 14.1 | 0 | 2022-11-14 | 0.6 | 17.4 | 0 | 2021-11-14 | 4.6 | 13.4 | 0 | 2020-11-14 | 3.4 | 14.6 | 0 | 2019-11-14 | -1.7 | 19.7 | 0 | 2018-11-14 | -8 | 26 | 0 | 2017-11-14 | 1 | 17 | 0 | 2016-11-14 | 11.7 | 6.3 | 0 | 16.22 | 0
2025-11-14 | 0.5 | 17.5 | 0 | 2024-11-14 | 1 | 17 | 0 | 2023-11-14 | 3.5 | 14.5 | 0 | 2022-11-14 | -0.4 | 18.4 | 0 | 2021-11-14 | 4.5 | 13.5 | 0 | 2020-11-14 | 1.3 | 16.7 | 0 | 2019-11-14 | -1.5 | 19.5 | 0 | 2018-11-14 | -8.7 | 26.7 | 0 | 2017-11-14 | 0.8 | 17.2 | 0 | 2016-11-14 | 9.8 | 8.2 | 0 | 16.92 | 0
2025-11-14 | 0.3 | 17.7 | 0 | 2024-11-14 | 1 | 17 | 0 | 2023-11-14 | 3.1 | 14.9 | 0 | 2022-11-14 | -1.4 | 19.4 | 0 | 2021-11-14 | 3.6 | 14.4 | 0 | 2020-11-14 | 1.4 | 16.6 | 0 | 2019-11-14 | -1 | 19 | 0 | 2018-11-14 | -9.1 | 27.1 | 0 | 2017-11-14 | 0.5 | 17.5 | 0 | 2016-11-14 | 8.9 | 9.1 | 0 | 17.27 | 0
2025-11-14 | 0.1 | 17.9 | 0 | 2024-11-14 | 0.5 | 17.5 | 0 | 2023-11-14 | 3 | 15 | 0 | 2022-11-14 | -2.6 | 20.6 | 0 | 2021-11-14 | 2.8 | 15.2 | 0 | 2020-11-14 | -1.6 | 19.6 | 0 | 2019-11-14 | -0.9 | 18.9 | 0 | 2018-11-14 | -9.6 | 27.6 | 0 | 2017-11-14 | 0.5 | 17.5 | 0 | 2016-11-14 | 7.9 | 10.1 | 0 | 17.99 | 0
2025-11-14 | -0.9 | 18.9 | 0 | 2024-11-14 | 0.1 | 17.9 | 0 | 2023-11-14 | 2.3 | 15.7 | 0 | 2022-11-14 | -2.6 | 20.6 | 0 | 2021-11-14 | 2.5 | 15.5 | 0 | 2020-11-14 | -2.4 | 20.4 | 0 | 2019-11-14 | -0.9 | 18.9 | 0 | 2018-11-14 | -9.9 | 27.9 | 0 | 2017-11-14 | -0.1 | 18.1 | 0 | 2016-11-14 | 5.9 | 12.1 | 0 | 18.6 | 0
2025-11-14 | -1.5 | 19.5 | 0 | 2024-11-14 | -0.1 | 18.1 | 0 | 2023-11-14 | 2 | 16 | 0 | 2022-11-14 | -2.2 | 20.2 | 0 | 2021-11-14 | 2.1 | 15.9 | 0 | 2020-11-14 | -3.5 | 21.5 | 0 | 2019-11-14 | -1 | 19 | 0 | 2018-11-14 | -10.5 | 28.5 | 0 | 2017-11-14 | -0.2 | 18.2 | 0 | 2016-11-14 | 5.9 | 12.1 | 0 | 18.9 | 0
2025-11-14 | -3 | 21 | 0 | 2024-11-14 | -0.2 | 18.2 | 0 | 2023-11-14 | 1.1 | 16.9 | 0 | 2022-11-14 | -2.9 | 20.9 | 0 | 2021-11-14 | 1.4 | 16.6 | 0 | 2020-11-14 | -4.3 | 22.3 | 0 | 2019-11-14 | -1.1 | 19.1 | 0 | 2018-11-14 | -10.2 | 28.2 | 0 | 2017-11-14 | -0.2 | 18.2 | 0 | 2016-11-14 | 3.4 | 14.6 | 0 | 19.6 | 0
2025-11-14 | -4.1 | 22.1 | 0 | 2024-11-14 | -0.6 | 18.6 | 0 | 2023-11-14 | 0.7 | 17.3 | 0 | 2022-11-14 | -2.9 | 20.9 | 0 | 2021-11-14 | 0.5 | 17.5 | 0 | 2020-11-14 | -3.8 | 21.8 | 0 | 2019-11-14 | -0.8 | 18.8 | 0 | 2018-11-14 | -10.8 | 28.8 | 0 | 2017-11-14 | -0.4 | 18.4 | 0 | 2016-11-14 | 3.8 | 14.2 | 0 | 19.84 | 0
2025-11-15 | -4.3 | 22.3 | 0 | 2024-11-15 | -0.6 | 18.6 | 0 | 2023-11-15 | -0.6 | 18.6 | 0 | 2022-11-15 | -4.6 | 22.6 | 0 | 2021-11-15 | 0.3 | 17.7 | 0 | 2020-11-15 | -3.8 | 21.8 | 0 | 2019-11-15 | -1 | 19 | 0 | 2018-11-15 | -11 | 29 | 0 | 2017-11-15 | -2.2 | 20.2 | 0 | 2016-11-15 | 2 | 16 | 0 | 20.58 | 0
2025-11-15 | -4 | 22 | 0 | 2024-11-15 | -0.6 | 18.6 | 0 | 2023-11-15 | -0.5 | 18.5 | 0 | 2022-11-15 | -4.9 | 22.9 | 0 | 2021-11-15 | 0.2 | 17.8 | 0 | 2020-11-15 | -4.3 | 22.3 | 0 | 2019-11-15 | -1.2 | 19.2 | 0 | 2018-11-15 | -11.9 | 29.9 | 0 | 2017-11-15 | -0.9 | 18.9 | 0 | 2016-11-15 | 1.4 | 16.6 | 0 | 20.67 | 0
2025-11-15 | -5.8 | 23.8 | 0 | 2024-11-15 | -0.5 | 18.5 | 0 | 2023-11-15 | -1.3 | 19.3 | 0 | 2022-11-15 | -5.2 | 23.2 | 0 | 2021-11-15 | 0.2 | 17.8 | 0 | 2020-11-15 | -4.5 | 22.5 | 0 | 2019-11-15 | -0.8 | 18.8 | 0 | 2018-11-15 | -11.7 | 29.7 | 0 | 2017-11-15 | -2.9 | 20.9 | 0 | 2016-11-15 | 1.1 | 16.9 | 0 | 21.14 | 0
2025-11-15 | -5 | 23 | 0 | 2024-11-15 | -0.7 | 18.7 | 0 | 2023-11-15 | -0.8 | 18.8 | 0 | 2022-11-15 | -3.7 | 21.7 | 0 | 2021-11-15 | 0 | 18 | 0 | 2020-11-15 | -4.1 | 22.1 | 0 | 2019-11-15 | -0.5 | 18.5 | 0 | 2018-11-15 | -11.7 | 29.7 | 0 | 2017-11-15 | -4 | 22 | 0 | 2016-11-15 | 1.9 | 16.1 | 0 | 20.86 | 0
2025-11-15 | -6.8 | 24.8 | 0 | 2024-11-15 | -0.5 | 18.5 | 0 | 2023-11-15 | -1 | 19 | 0 | 2022-11-15 | -3.9 | 21.9 | 0 | 2021-11-15 | 0 | 18 | 0 | 2020-11-15 | -4 | 22 | 0 | 2019-11-15 | -0.8 | 18.8 | 0 | 2018-11-15 | -11.7 | 29.7 | 0 | 2017-11-15 | -3.1 | 21.1 | 0 | 2016-11-15 | 0.3 | 17.7 | 0 | 21.15 | 0
2025-11-15 | -5 | 23 | 0 | 2024-11-15 | -0.4 | 18.4 | 0 | 2023-11-15 | -1.1 | 19.1 | 0 | 2022-11-15 | -4.3 | 22.3 | 0 | 2021-11-15 | 0 | 18 | 0 | 2020-11-15 | -3.2 | 21.2 | 0 | 2019-11-15 | -0.6 | 18.6 | 0 | 2018-11-15 | -11.7 | 29.7 | 0 | 2017-11-15 | -3.7 | 21.7 | 0 | 2016-11-15 | 1.1 | 16.9 | 0 | 20.89 | 0
2025-11-15 | -6.6 | 24.6 | 0 | 2024-11-15 | -1 | 19 | 0 | 2023-11-15 | 0.3 | 17.7 | 0 | 2022-11-15 | -4.2 | 22.2 | 0 | 2021-11-15 | 0 | 18 | 0 | 2020-11-15 | -2.9 | 20.9 | 0 | 2019-11-15 | -0.7 | 18.7 | 0 | 2018-11-15 | -11.9 | 29.9 | 0 | 2017-11-15 | -3.8 | 21.8 | 0 | 2016-11-15 | 2.1 | 15.9 | 0 | 20.87 | 0
2025-11-15 | -7 | 25 | 0 | 2024-11-15 | -1.6 | 19.6 | 0 | 2023-11-15 | -0.2 | 18.2 | 0 | 2022-11-15 | -4.7 | 22.7 | 0 | 2021-11-15 | 0.2 | 17.8 | 0 | 2020-11-15 | -2 | 20 | 0 | 2019-11-15 | -0.6 | 18.6 | 0 | 2018-11-15 | -11.6 | 29.6 | 0 | 2017-11-15 | -5 | 23 | 0 | 2016-11-15 | 2.2 | 15.8 | 0 | 21.03 | 0
2025-11-15 | -4.8 | 22.8 | 0 | 2024-11-15 | 0.4 | 17.6 | 0 | 2023-11-15 | 1 | 17 | 0 | 2022-11-15 | -3.2 | 21.2 | 0 | 2021-11-15 | 0.2 | 17.8 | 0 | 2020-11-15 | -1 | 19 | 0 | 2019-11-15 | 0 | 18 | 0 | 2018-11-15 | -10.9 | 28.9 | 0 | 2017-11-15 | -3.1 | 21.1 | 0 | 2016-11-15 | 2 | 16 | 0 | 19.94 | 0
2025-11-15 | -3 | 21 | 0 | 2024-11-15 | 0.9 | 17.1 | 0 | 2023-11-15 | 2.7 | 15.3 | 0 | 2022-11-15 | -1.6 | 19.6 | 0 | 2021-11-15 | 0.5 | 17.5 | 0 | 2020-11-15 | -1.1 | 19.1 | 0 | 2019-11-15 | 0.4 | 17.6 | 0 | 2018-11-15 | -9.8 | 27.8 | 0 | 2017-11-15 | 0 | 18 | 0 | 2016-11-15 | 3.3 | 14.7 | 0 | 18.77 | 0
2025-11-15 | -1.7 | 19.7 | 0 | 2024-11-15 | 4.2 | 13.8 | 0 | 2023-11-15 | 3.7 | 14.3 | 0 | 2022-11-15 | -0.8 | 18.8 | 0 | 2021-11-15 | 1.5 | 16.5 | 0 | 2020-11-15 | -0.2 | 18.2 | 0 | 2019-11-15 | 0.6 | 17.4 | 0 | 2018-11-15 | -8.7 | 26.7 | 0 | 2017-11-15 | 2 | 16 | 0 | 2016-11-15 | 6 | 12 | 0 | 17.34 | 0
2025-11-15 | -0.7 | 18.7 | 0 | 2024-11-15 | 5.3 | 12.7 | 0 | 2023-11-15 | 4.7 | 13.3 | 0 | 2022-11-15 | -0.3 | 18.3 | 0 | 2021-11-15 | 2.3 | 15.7 | 0 | 2020-11-15 | 0.9 | 17.1 | 0 | 2019-11-15 | 1 | 17 | 0 | 2018-11-15 | -7.8 | 25.8 | 0 | 2017-11-15 | 3.9 | 14.1 | 0 | 2016-11-15 | 8.2 | 9.8 | 0 | 16.25 | 0
2025-11-15 | -0.6 | 18.6 | 0 | 2024-11-15 | 7 | 11 | 0 | 2023-11-15 | 7.2 | 10.8 | 0 | 2022-11-15 | -0.5 | 18.5 | 0 | 2021-11-15 | 2.9 | 15.1 | 0 | 2020-11-15 | 2.3 | 15.7 | 0 | 2019-11-15 | 0.6 | 17.4 | 0 | 2018-11-15 | -7.1 | 25.1 | 0 | 2017-11-15 | 5.4 | 12.6 | 0 | 2016-11-15 | 9.8 | 8.2 | 0 | 15.3 | 0
2025-11-15 | -0.6 | 18.6 | 0 | 2024-11-15 | 8.1 | 9.9 | 0 | 2023-11-15 | 6.9 | 11.1 | 0 | 2022-11-15 | -0.4 | 18.4 | 0 | 2021-11-15 | 3.3 | 14.7 | 0 | 2020-11-15 | 2.9 | 15.1 | 0 | 2019-11-15 | 1.1 | 16.9 | 0 | 2018-11-15 | -6.6 | 24.6 | 0 | 2017-11-15 | 6 | 12 | 0 | 2016-11-15 | 11.3 | 6.7 | 0 | 14.8 | 0
2025-11-15 | -0.8 | 18.8 | 0 | 2024-11-15 | 9.2 | 8.8 | 0 | 2023-11-15 | 7.5 | 10.5 | 0 | 2022-11-15 | -0.2 | 18.2 | 0 | 2021-11-15 | 1.6 | 16.4 | 0 | 2020-11-15 | 3.2 | 14.8 | 0 | 2019-11-15 | -1.3 | 19.3 | 0 | 2018-11-15 | -6 | 24 | 0 | 2017-11-15 | 6.2 | 11.8 | 0 | 2016-11-15 | 11.1 | 6.9 | 0 | 14.95 | 0
2025-11-15 | -0.5 | 18.5 | 0 | 2024-11-15 | 9.2 | 8.8 | 0 | 2023-11-15 | 8.3 | 9.7 | 0 | 2022-11-15 | -0.1 | 18.1 | 0 | 2021-11-15 | 2.1 | 15.9 | 0 | 2020-11-15 | 2.9 | 15.1 | 0 | 2019-11-15 | -0.9 | 18.9 | 0 | 2018-11-15 | -5.9 | 23.9 | 0 | 2017-11-15 | 6 | 12 | 0 | 2016-11-15 | 11.5 | 6.5 | 0 | 14.74 | 0
2025-11-15 | -0.4 | 18.4 | 0 | 2024-11-15 | 7.3 | 10.7 | 0 | 2023-11-15 | 9.2 | 8.8 | 0 | 2022-11-15 | -0.8 | 18.8 | 0 | 2021-11-15 | 1.5 | 16.5 | 0 | 2020-11-15 | 3.3 | 14.7 | 0 | 2019-11-15 | -0.5 | 18.5 | 0 | 2018-11-15 | -6.1 | 24.1 | 0 | 2017-11-15 | 4.5 | 13.5 | 0 | 2016-11-15 | 10.3 | 7.7 | 0 | 15.17 | 0
2025-11-15 | -0.4 | 18.4 | 0 | 2024-11-15 | 5.8 | 12.2 | 0 | 2023-11-15 | 8.6 | 9.4 | 0 | 2022-11-15 | -1 | 19 | 0 | 2021-11-15 | 1.2 | 16.8 | 0 | 2020-11-15 | 3.7 | 14.3 | 0 | 2019-11-15 | -2.4 | 20.4 | 0 | 2018-11-15 | -6.5 | 24.5 | 0 | 2017-11-15 | 3.9 | 14.1 | 0 | 2016-11-15 | 7.8 | 10.2 | 0 | 15.93 | 0
2025-11-15 | -0.5 | 18.5 | 0 | 2024-11-15 | 5.5 | 12.5 | 0 | 2023-11-15 | 8.1 | 9.9 | 0 | 2022-11-15 | -1.1 | 19.1 | 0 | 2021-11-15 | 1.3 | 16.7 | 0 | 2020-11-15 | 8.2 | 9.8 | 0 | 2019-11-15 | -3 | 21 | 0 | 2018-11-15 | -6.5 | 24.5 | 0 | 2017-11-15 | 3.3 | 14.7 | 0 | 2016-11-15 | 6.7 | 11.3 | 0 | 15.8 | 0
2025-11-15 | -0.5 | 18.5 | 0 | 2024-11-15 | 5 | 13 | 0 | 2023-11-15 | 7.8 | 10.2 | 0 | 2022-11-15 | -1.1 | 19.1 | 0 | 2021-11-15 | 0.7 | 17.3 | 0 | 2020-11-15 | 7.6 | 10.4 | 0 | 2019-11-15 | -4.3 | 22.3 | 0 | 2018-11-15 | -6.5 | 24.5 | 0 | 2017-11-15 | 3.1 | 14.9 | 0 | 2016-11-15 | 3.8 | 14.2 | 0 | 16.44 | 0
2025-11-15 | -0.5 | 18.5 | 0 | 2024-11-15 | 4.5 | 13.5 | 0 | 2023-11-15 | 7.5 | 10.5 | 0 | 2022-11-15 | -1.3 | 19.3 | 0 | 2021-11-15 | 0.9 | 17.1 | 0 | 2020-11-15 | 7.5 | 10.5 | 0 | 2019-11-15 | -6.1 | 24.1 | 0 | 2018-11-15 | -6.5 | 24.5 | 0 | 2017-11-15 | 3.1 | 14.9 | 0 | 2016-11-15 | 3.3 | 14.7 | 0 | 16.76 | 0
2025-11-15 | -0.4 | 18.4 | 0 | 2024-11-15 | 4.1 | 13.9 | 0 | 2023-11-15 | 6.7 | 11.3 | 0 | 2022-11-15 | -1.7 | 19.7 | 0 | 2021-11-15 | 1.2 | 16.8 | 0 | 2020-11-15 | 7.8 | 10.2 | 0 | 2019-11-15 | -7.8 | 25.8 | 0 | 2018-11-15 | -6.5 | 24.5 | 0 | 2017-11-15 | 3.4 | 14.6 | 0 | 2016-11-15 | 4.4 | 13.6 | 0 | 16.88 | 0
2025-11-15 | -0.3 | 18.3 | 0 | 2024-11-15 | 2.6 | 15.4 | 0 | 2023-11-15 | 6.2 | 11.8 | 0 | 2022-11-15 | -1.8 | 19.8 | 0 | 2021-11-15 | 1.3 | 16.7 | 0 | 2020-11-15 | 6.7 | 11.3 | 0 | 2019-11-15 | -9.3 | 27.3 | 0 | 2018-11-15 | -6.4 | 24.4 | 0 | 2017-11-15 | 3.5 | 14.5 | 0 | 2016-11-15 | 4.9 | 13.1 | 0 | 17.26 | 0
2025-11-15 | -0.4 | 18.4 | 0 | 2024-11-15 | 3.9 | 14.1 | 0 | 2023-11-15 | 5.1 | 12.9 | 0 | 2022-11-15 | -1.4 | 19.4 | 0 | 2021-11-15 | 0.6 | 17.4 | 0 | 2020-11-15 | 6.6 | 11.4 | 0 | 2019-11-15 | -10.2 | 28.2 | 0 | 2018-11-15 | -6.6 | 24.6 | 0 | 2017-11-15 | 3.4 | 14.6 | 0 | 2016-11-15 | 4.5 | 13.5 | 0 | 17.45 | 0
2025-11-16 | -0.3 | 18.3 | 0 | 2024-11-16 | 4.5 | 13.5 | 0 | 2023-11-16 | 3.5 | 14.5 | 0 | 2022-11-16 | -1.4 | 19.4 | 0 | 2021-11-16 | 0.9 | 17.1 | 0 | 2020-11-16 | 6.1 | 11.9 | 0 | 2019-11-16 | -11 | 29 | 0 | 2018-11-16 | -7.1 | 25.1 | 0 | 2017-11-16 | 3.3 | 14.7 | 0 | 2016-11-16 | 5.7 | 12.3 | 0 | 17.58 | 0
2025-11-16 | -0.3 | 18.3 | 0 | 2024-11-16 | 4.3 | 13.7 | 0 | 2023-11-16 | 2.2 | 15.8 | 0 | 2022-11-16 | -1.6 | 19.6 | 0 | 2021-11-16 | 0.4 | 17.6 | 0 | 2020-11-16 | 5.7 | 12.3 | 0 | 2019-11-16 | -11.8 | 29.8 | 0 | 2018-11-16 | -7.3 | 25.3 | 0 | 2017-11-16 | 3.5 | 14.5 | 0 | 2016-11-16 | 5.4 | 12.6 | 0 | 17.95 | 0
2025-11-16 | -0.3 | 18.3 | 0 | 2024-11-16 | 3.9 | 14.1 | 0 | 2023-11-16 | 2.6 | 15.4 | 0 | 2022-11-16 | -1.9 | 19.9 | 0 | 2021-11-16 | 1.2 | 16.8 | 0 | 2020-11-16 | 4.7 | 13.3 | 0 | 2019-11-16 | -13.2 | 31.2 | 0 | 2018-11-16 | -7 | 25 | 0 | 2017-11-16 | 2.3 | 15.7 | 0 | 2016-11-16 | 5.2 | 12.8 | 0 | 18.25 | 0
2025-11-16 | -0.2 | 18.2 | 0 | 2024-11-16 | 3.9 | 14.1 | 0 | 2023-11-16 | 1.5 | 16.5 | 0 | 2022-11-16 | -2 | 20 | 0 | 2021-11-16 | 0.9 | 17.1 | 0 | 2020-11-16 | 5 | 13 | 0 | 2019-11-16 | -13.1 | 31.1 | 0 | 2018-11-16 | -6.7 | 24.7 | 0 | 2017-11-16 | 2.7 | 15.3 | 0 | 2016-11-16 | 5.1 | 12.9 | 0 | 18.29 | 0
2025-11-16 | -0.2 | 18.2 | 0 | 2024-11-16 | 4.1 | 13.9 | 0 | 2023-11-16 | 0.4 | 17.6 | 0 | 2022-11-16 | -2.2 | 20.2 | 0 | 2021-11-16 | 0.9 | 17.1 | 0 | 2020-11-16 | 5.1 | 12.9 | 0 | 2019-11-16 | -13.3 | 31.3 | 0 | 2018-11-16 | -6.8 | 24.8 | 0 | 2017-11-16 | 5.1 | 12.9 | 0 | 2016-11-16 | 5.2 | 12.8 | 0 | 18.17 | 0
2025-11-16 | 0.2 | 17.8 | 0 | 2024-11-16 | 3.2 | 14.8 | 0 | 2023-11-16 | -0.2 | 18.2 | 0 | 2022-11-16 | -2.4 | 20.4 | 0 | 2021-11-16 | 0.9 | 17.1 | 0 | 2020-11-16 | 5 | 13 | 0 | 2019-11-16 | -14 | 32 | 0 | 2018-11-16 | -6.5 | 24.5 | 0 | 2017-11-16 | 5.5 | 12.5 | 0 | 2016-11-16 | 5.2 | 12.8 | 0 | 18.31 | 0
2025-11-16 | 0.4 | 17.6 | 0 | 2024-11-16 | 3.2 | 14.8 | 0 | 2023-11-16 | -0.9 | 18.9 | 0 | 2022-11-16 | -2.5 | 20.5 | 0 | 2021-11-16 | 0.4 | 17.6 | 0 | 2020-11-16 | 4.9 | 13.1 | 0 | 2019-11-16 | -14 | 32 | 0 | 2018-11-16 | -6.4 | 24.4 | 0 | 2017-11-16 | 6.1 | 11.9 | 0 | 2016-11-16 | 5 | 13 | 0 | 18.38 | 0
2025-11-16 | 0.5 | 17.5 | 0 | 2024-11-16 | 2.8 | 15.2 | 0 | 2023-11-16 | -0.9 | 18.9 | 0 | 2022-11-16 | -2.5 | 20.5 | 0 | 2021-11-16 | 0.1 | 17.9 | 0 | 2020-11-16 | 4.6 | 13.4 | 0 | 2019-11-16 | -14.2 | 32.2 | 0 | 2018-11-16 | -6.1 | 24.1 | 0 | 2017-11-16 | 6.5 | 11.5 | 0 | 2016-11-16 | 5.3 | 12.7 | 0 | 18.39 | 0
2025-11-16 | 0.6 | 17.4 | 0 | 2024-11-16 | 3.6 | 14.4 | 0 | 2023-11-16 | -0.2 | 18.2 | 0 | 2022-11-16 | -2.3 | 20.3 | 0 | 2021-11-16 | 0.6 | 17.4 | 0 | 2020-11-16 | 4.4 | 13.6 | 0 | 2019-11-16 | -14.1 | 32.1 | 0 | 2018-11-16 | -5.6 | 23.6 | 0 | 2017-11-16 | 6.4 | 11.6 | 0 | 2016-11-16 | 5.5 | 12.5 | 0 | 18.11 | 0
2025-11-16 | 0.6 | 17.4 | 0 | 2024-11-16 | 5 | 13 | 0 | 2023-11-16 | 2.9 | 15.1 | 0 | 2022-11-16 | -1.9 | 19.9 | 0 | 2021-11-16 | 1.1 | 16.9 | 0 | 2020-11-16 | 4.7 | 13.3 | 0 | 2019-11-16 | -13.1 | 31.1 | 0 | 2018-11-16 | -5.1 | 23.1 | 0 | 2017-11-16 | 6.6 | 11.4 | 0 | 2016-11-16 | 5.6 | 12.4 | 0 | 17.36 | 0
2025-11-16 | 0.8 | 17.2 | 0 | 2024-11-16 | 6.8 | 11.2 | 0 | 2023-11-16 | 5.3 | 12.7 | 0 | 2022-11-16 | -1.4 | 19.4 | 0 | 2021-11-16 | 1.1 | 16.9 | 0 | 2020-11-16 | 5.6 | 12.4 | 0 | 2019-11-16 | -11.1 | 29.1 | 0 | 2018-11-16 | -4.4 | 22.4 | 0 | 2017-11-16 | 6.7 | 11.3 | 0 | 2016-11-16 | 5.6 | 12.4 | 0 | 16.5 | 0
2025-11-16 | 0.9 | 17.1 | 0 | 2024-11-16 | 8.8 | 9.2 | 0 | 2023-11-16 | 7.1 | 10.9 | 0 | 2022-11-16 | -1 | 19 | 0 | 2021-11-16 | 2.2 | 15.8 | 0 | 2020-11-16 | 6 | 12 | 0 | 2019-11-16 | -9.6 | 27.6 | 0 | 2018-11-16 | -3.8 | 21.8 | 0 | 2017-11-16 | 6.6 | 11.4 | 0 | 2016-11-16 | 6.7 | 11.3 | 0 | 15.61 | 0
2025-11-16 | 0.1 | 17.9 | 0 | 2024-11-16 | 10.9 | 7.1 | 0 | 2023-11-16 | 8.3 | 9.7 | 0 | 2022-11-16 | -0.7 | 18.7 | 0 | 2021-11-16 | 2.9 | 15.1 | 0 | 2020-11-16 | 6 | 12 | 0 | 2019-11-16 | -8.8 | 26.8 | 0 | 2018-11-16 | -3.4 | 21.4 | 0 | 2017-11-16 | 6.5 | 11.5 | 0 | 2016-11-16 | 7.2 | 10.8 | 0 | 15.1 | 0
2025-11-16 | 1.3 | 16.7 | 0 | 2024-11-16 | 11.9 | 6.1 | 0 | 2023-11-16 | 10.4 | 7.6 | 0 | 2022-11-16 | -0.3 | 18.3 | 0 | 2021-11-16 | 2.9 | 15.1 | 0 | 2020-11-16 | 5.8 | 12.2 | 0 | 2019-11-16 | -7.8 | 25.8 | 0 | 2018-11-16 | -3.5 | 21.5 | 0 | 2017-11-16 | 5.5 | 12.5 | 0 | 2016-11-16 | 7.9 | 10.1 | 0 | 14.59 | 0
2025-11-16 | 0.9 | 17.1 | 0 | 2024-11-16 | 12.5 | 5.5 | 0 | 2023-11-16 | 11.7 | 6.3 | 0 | 2022-11-16 | 0 | 18 | 0 | 2021-11-16 | 2.6 | 15.4 | 0 | 2020-11-16 | 7.5 | 10.5 | 0 | 2019-11-16 | -6.8 | 24.8 | 0 | 2018-11-16 | -3.7 | 21.7 | 0 | 2017-11-16 | 5.5 | 12.5 | 0 | 2016-11-16 | 8.7 | 9.3 | 0 | 14.11 | 0
2025-11-16 | 0.6 | 17.4 | 0 | 2024-11-16 | 11.8 | 6.2 | 0 | 2023-11-16 | 11.2 | 6.8 | 0 | 2022-11-16 | -0.1 | 18.1 | 0 | 2021-11-16 | 1.9 | 16.1 | 0 | 2020-11-16 | 6 | 12 | 0 | 2019-11-16 | -6.6 | 24.6 | 0 | 2018-11-16 | -3.7 | 21.7 | 0 | 2017-11-16 | 5.6 | 12.4 | 0 | 2016-11-16 | 8.8 | 9.2 | 0 | 14.45 | 0
2025-11-16 | -0.1 | 18.1 | 0 | 2024-11-16 | 10.2 | 7.8 | 0 | 2023-11-16 | 9.5 | 8.5 | 0 | 2022-11-16 | -0.2 | 18.2 | 0 | 2021-11-16 | 0.6 | 17.4 | 0 | 2020-11-16 | 5.2 | 12.8 | 0 | 2019-11-16 | -7 | 25 | 0 | 2018-11-16 | -3.8 | 21.8 | 0 | 2017-11-16 | 3.8 | 14.2 | 0 | 2016-11-16 | 7.7 | 10.3 | 0 | 15.41 | 0
2025-11-16 | -0.7 | 18.7 | 0 | 2024-11-16 | 7.6 | 10.4 | 0 | 2023-11-16 | 8.4 | 9.6 | 0 | 2022-11-16 | -0.3 | 18.3 | 0 | 2021-11-16 | -0.6 | 18.6 | 0 | 2020-11-16 | 4.4 | 13.6 | 0 | 2019-11-16 | -8.5 | 26.5 | 0 | 2018-11-16 | -3.8 | 21.8 | 0 | 2017-11-16 | 2.8 | 15.2 | 0 | 2016-11-16 | 6.2 | 11.8 | 0 | 16.45 | 0
2025-11-16 | -1 | 19 | 0 | 2024-11-16 | 7.6 | 10.4 | 0 | 2023-11-16 | 6.8 | 11.2 | 0 | 2022-11-16 | -0.5 | 18.5 | 0 | 2021-11-16 | -1.9 | 19.9 | 0 | 2020-11-16 | 3.5 | 14.5 | 0 | 2019-11-16 | -11.6 | 29.6 | 0 | 2018-11-16 | -4.3 | 22.3 | 0 | 2017-11-16 | 2.9 | 15.1 | 0 | 2016-11-16 | 3.9 | 14.1 | 0 | 17.46 | 0
2025-11-16 | -1.2 | 19.2 | 0 | 2024-11-16 | 5.6 | 12.4 | 0 | 2023-11-16 | 7.4 | 10.6 | 0 | 2022-11-16 | -0.7 | 18.7 | 0 | 2021-11-16 | -0.9 | 18.9 | 0 | 2020-11-16 | 2.4 | 15.6 | 0 | 2019-11-16 | -13.1 | 31.1 | 0 | 2018-11-16 | -3.9 | 21.9 | 0 | 2017-11-16 | 1.8 | 16.2 | 0 | 2016-11-16 | 4 | 14 | 0 | 17.86 | 0
2025-11-16 | -1.7 | 19.7 | 0 | 2024-11-16 | 5.1 | 12.9 | 0 | 2023-11-16 | 6.6 | 11.4 | 0 | 2022-11-16 | -1.1 | 19.1 | 0 | 2021-11-16 | -2.5 | 20.5 | 0 | 2020-11-16 | 2.1 | 15.9 | 0 | 2019-11-16 | -11.8 | 29.8 | 0 | 2018-11-16 | -3.8 | 21.8 | 0 | 2017-11-16 | 0.7 | 17.3 | 0 | 2016-11-16 | 3.9 | 14.1 | 0 | 18.25 | 0
2025-11-16 | -1.9 | 19.9 | 0 | 2024-11-16 | 3.2 | 14.8 | 0 | 2023-11-16 | 5.5 | 12.5 | 0 | 2022-11-16 | -1.7 | 19.7 | 0 | 2021-11-16 | -2.2 | 20.2 | 0 | 2020-11-16 | 2.1 | 15.9 | 0 | 2019-11-16 | -11.6 | 29.6 | 0 | 2018-11-16 | -3.7 | 21.7 | 0 | 2017-11-16 | 0 | 18 | 0 | 2016-11-16 | 3 | 15 | 0 | 18.73 | 0
2025-11-16 | -2.1 | 20.1 | 0 | 2024-11-16 | 2.5 | 15.5 | 0 | 2023-11-16 | 5 | 13 | 0 | 2022-11-16 | -2.6 | 20.6 | 0 | 2021-11-16 | -2.1 | 20.1 | 0 | 2020-11-16 | 2.1 | 15.9 | 0 | 2019-11-16 | -13.3 | 31.3 | 0 | 2018-11-16 | -3.4 | 21.4 | 0 | 2017-11-16 | -0.7 | 18.7 | 0 | 2016-11-16 | 3.6 | 14.4 | 0 | 19.1 | 0
2025-11-16 | -2.1 | 20.1 | 0 | 2024-11-16 | 0.4 | 17.6 | 0 | 2023-11-16 | 4 | 14 | 0 | 2022-11-16 | -2.2 | 20.2 | 0 | 2021-11-16 | -2.4 | 20.4 | 0 | 2020-11-16 | 2.2 | 15.8 | 0 | 2019-11-16 | -12.6 | 30.6 | 0 | 2018-11-16 | -2.4 | 20.4 | 0 | 2017-11-16 | -1.2 | 19.2 | 0 | 2016-11-16 | 5.2 | 12.8 | 0 | 19.11 | 0
2025-11-17 | -2.3 | 20.3 | 0 | 2024-11-17 | 1.4 | 16.6 | 0 | 2023-11-17 | 5.1 | 12.9 | 0 | 2022-11-17 | -2.2 | 20.2 | 0 | 2021-11-17 | -3.8 | 21.8 | 0 | 2020-11-17 | 1.9 | 16.1 | 0 | 2019-11-17 | -13 | 31 | 0 | 2018-11-17 | -1.7 | 19.7 | 0 | 2017-11-17 | -1.7 | 19.7 | 0 | 2016-11-17 | 4.7 | 13.3 | 0 | 19.16 | 0
2025-11-17 | -2.3 | 20.3 | 0 | 2024-11-17 | 0.3 | 17.7 | 0 | 2023-11-17 | 4.8 | 13.2 | 0 | 2022-11-17 | -2.1 | 20.1 | 0 | 2021-11-17 | -4.6 | 22.6 | 0 | 2020-11-17 | 1.1 | 16.9 | 0 | 2019-11-17 | -13.9 | 31.9 | 0 | 2018-11-17 | -1 | 19 | 0 | 2017-11-17 | -2.2 | 20.2 | 0 | 2016-11-17 | 3.3 | 14.7 | 0 | 19.66 | 0
2025-11-17 | -2.5 | 20.5 | 0 | 2024-11-17 | 0.6 | 17.4 | 0 | 2023-11-17 | 6.3 | 11.7 | 0 | 2022-11-17 | -2.1 | 20.1 | 0 | 2021-11-17 | -5.4 | 23.4 | 0 | 2020-11-17 | 0.7 | 17.3 | 0 | 2019-11-17 | -13.7 | 31.7 | 0 | 2018-11-17 | -1.2 | 19.2 | 0 | 2017-11-17 | -2.4 | 20.4 | 0 | 2016-11-17 | 5.3 | 12.7 | 0 | 19.44 | 0
2025-11-17 | -2.3 | 20.3 | 0 | 2024-11-17 | 0 | 18 | 0 | 2023-11-17 | 7 | 11 | 0 | 2022-11-17 | -2.4 | 20.4 | 0 | 2021-11-17 | -4.8 | 22.8 | 0 | 2020-11-17 | 0.7 | 17.3 | 0 | 2019-11-17 | -13.2 | 31.2 | 0 | 2018-11-17 | -1.5 | 19.5 | 0 | 2017-11-17 | -2.8 | 20.8 | 0 | 2016-11-17 | 4.2 | 13.8 | 0 | 19.51 | 0
2025-11-17 | -2.2 | 20.2 | 0 | 2024-11-17 | -1.2 | 19.2 | 0 | 2023-11-17 | 7.3 | 10.7 | 0 | 2022-11-17 | -2.3 | 20.3 | 0 | 2021-11-17 | -3.8 | 21.8 | 0 | 2020-11-17 | 0.5 | 17.5 | 0 | 2019-11-17 | -13.3 | 31.3 | 0 | 2018-11-17 | -1.1 | 19.1 | 0 | 2017-11-17 | -3.1 | 21.1 | 0 | 2016-11-17 | 6 | 12 | 0 | 19.32 | 0
2025-11-17 | -2.2 | 20.2 | 0 | 2024-11-17 | -0.6 | 18.6 | 0 | 2023-11-17 | 10.5 | 7.5 | 0 | 2022-11-17 | -2.5 | 20.5 | 0 | 2021-11-17 | -3.9 | 21.9 | 0 | 2020-11-17 | -0.4 | 18.4 | 0 | 2019-11-17 | -13.8 | 31.8 | 0 | 2018-11-17 | -1 | 19 | 0 | 2017-11-17 | -3.7 | 21.7 | 0 | 2016-11-17 | 5.3 | 12.7 | 0 | 19.23 | 0
2025-11-17 | -2.4 | 20.4 | 0 | 2024-11-17 | -2.3 | 20.3 | 0 | 2023-11-17 | 10.5 | 7.5 | 0 | 2022-11-17 | -2.5 | 20.5 | 0 | 2021-11-17 | -3.2 | 21.2 | 0 | 2020-11-17 | -2.2 | 20.2 | 0 | 2019-11-17 | -13.9 | 31.9 | 0 | 2018-11-17 | -1.2 | 19.2 | 0 | 2017-11-17 | -4.4 | 22.4 | 0 | 2016-11-17 | 4.8 | 13.2 | 0 | 19.68 | 0
2025-11-17 | -2.2 | 20.2 | 0 | 2024-11-17 | -1.4 | 19.4 | 0 | 2023-11-17 | 11.1 | 6.9 | 0 | 2022-11-17 | -3.7 | 21.7 | 0 | 2021-11-17 | -2.7 | 20.7 | 0 | 2020-11-17 | -2.8 | 20.8 | 0 | 2019-11-17 | -13.3 | 31.3 | 0 | 2018-11-17 | -0.8 | 18.8 | 0 | 2017-11-17 | -5.1 | 23.1 | 0 | 2016-11-17 | 5.2 | 12.8 | 0 | 19.57 | 0
2025-11-17 | -2.1 | 20.1 | 0 | 2024-11-17 | -0.6 | 18.6 | 0 | 2023-11-17 | 11.4 | 6.6 | 0 | 2022-11-17 | -3.5 | 21.5 | 0 | 2021-11-17 | -1.9 | 19.9 | 0 | 2020-11-17 | -1.3 | 19.3 | 0 | 2019-11-17 | -12.4 | 30.4 | 0 | 2018-11-17 | 0.3 | 17.7 | 0 | 2017-11-17 | -5.7 | 23.7 | 0 | 2016-11-17 | 5.9 | 12.1 | 0 | 18.99 | 0
2025-11-17 | -2 | 20 | 0 | 2024-11-17 | 2.1 | 15.9 | 0 | 2023-11-17 | 12.4 | 5.6 | 0 | 2022-11-17 | -3 | 21 | 0 | 2021-11-17 | -1.8 | 19.8 | 0 | 2020-11-17 | 0.2 | 17.8 | 0 | 2019-11-17 | -11.4 | 29.4 | 0 | 2018-11-17 | 0.2 | 17.8 | 0 | 2017-11-17 | -5.4 | 23.4 | 0 | 2016-11-17 | 7.2 | 10.8 | 0 | 18.15 | 0
2025-11-17 | -1.5 | 19.5 | 0 | 2024-11-17 | 3.8 | 14.2 | 0 | 2023-11-17 | 14.3 | 3.7 | 0 | 2022-11-17 | -2.5 | 20.5 | 0 | 2021-11-17 | -0.7 | 18.7 | 0 | 2020-11-17 | 0.6 | 17.4 | 0 | 2019-11-17 | -9.2 | 27.2 | 0 | 2018-11-17 | 0.2 | 17.8 | 0 | 2017-11-17 | -4.7 | 22.7 | 0 | 2016-11-17 | 7.8 | 10.2 | 0 | 17.19 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 5.1 | 12.9 | 0 | 2023-11-17 | 14.9 | 3.1 | 0 | 2022-11-17 | -2.3 | 20.3 | 0 | 2021-11-17 | 0 | 18 | 0 | 2020-11-17 | 1.7 | 16.3 | 0 | 2019-11-17 | -7.2 | 25.2 | 0 | 2018-11-17 | 0.7 | 17.3 | 0 | 2017-11-17 | -3.9 | 21.9 | 0 | 2016-11-17 | 8.4 | 9.6 | 0 | 16.38 | 0
2025-11-17 | -1.1 | 19.1 | 0 | 2024-11-17 | 6.8 | 11.2 | 0 | 2023-11-17 | 14.3 | 3.7 | 0 | 2022-11-17 | -2.1 | 20.1 | 0 | 2021-11-17 | 0.4 | 17.6 | 0 | 2020-11-17 | 2.2 | 15.8 | 0 | 2019-11-17 | -5.7 | 23.7 | 0 | 2018-11-17 | 0.8 | 17.2 | 0 | 2017-11-17 | -3.2 | 21.2 | 0 | 2016-11-17 | 8.6 | 9.4 | 0 | 15.9 | 0
2025-11-17 | -1 | 19 | 0 | 2024-11-17 | 7.2 | 10.8 | 0 | 2023-11-17 | 13 | 5 | 0 | 2022-11-17 | -2.7 | 20.7 | 0 | 2021-11-17 | 0.6 | 17.4 | 0 | 2020-11-17 | 0.2 | 17.8 | 0 | 2019-11-17 | -4.4 | 22.4 | 0 | 2018-11-17 | 0 | 18 | 0 | 2017-11-17 | -2 | 20 | 0 | 2016-11-17 | 8.7 | 9.3 | 0 | 16.04 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 7.9 | 10.1 | 0 | 2023-11-17 | 10.7 | 7.3 | 0 | 2022-11-17 | -2.9 | 20.9 | 0 | 2021-11-17 | 0.5 | 17.5 | 0 | 2020-11-17 | -1.1 | 19.1 | 0 | 2019-11-17 | -3.6 | 21.6 | 0 | 2018-11-17 | -0.6 | 18.6 | 0 | 2017-11-17 | -1.7 | 19.7 | 0 | 2016-11-17 | 9 | 9 | 0 | 16.3 | 0
2025-11-17 | -1 | 19 | 0 | 2024-11-17 | 7.8 | 10.2 | 0 | 2023-11-17 | 10.4 | 7.6 | 0 | 2022-11-17 | -3.4 | 21.4 | 0 | 2021-11-17 | 0.7 | 17.3 | 0 | 2020-11-17 | -1.1 | 19.1 | 0 | 2019-11-17 | -3.5 | 21.5 | 0 | 2018-11-17 | -0.9 | 18.9 | 0 | 2017-11-17 | -1.4 | 19.4 | 0 | 2016-11-17 | 9.7 | 8.3 | 0 | 16.27 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 7.3 | 10.7 | 0 | 2023-11-17 | 8 | 10 | 0 | 2022-11-17 | -3.7 | 21.7 | 0 | 2021-11-17 | 0.8 | 17.2 | 0 | 2020-11-17 | -2.2 | 20.2 | 0 | 2019-11-17 | -3.7 | 21.7 | 0 | 2018-11-17 | -1.7 | 19.7 | 0 | 2017-11-17 | -2.2 | 20.2 | 0 | 2016-11-17 | 8.7 | 9.3 | 0 | 16.99 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 5.9 | 12.1 | 0 | 2023-11-17 | 6.6 | 11.4 | 0 | 2022-11-17 | -4.3 | 22.3 | 0 | 2021-11-17 | 1 | 17 | 0 | 2020-11-17 | -2.8 | 20.8 | 0 | 2019-11-17 | -5.4 | 23.4 | 0 | 2018-11-17 | -2.5 | 20.5 | 0 | 2017-11-17 | -3.3 | 21.3 | 0 | 2016-11-17 | 8 | 10 | 0 | 17.8 | 0
2025-11-17 | -1.1 | 19.1 | 0 | 2024-11-17 | 6.1 | 11.9 | 0 | 2023-11-17 | 5.3 | 12.7 | 0 | 2022-11-17 | -4.9 | 22.9 | 0 | 2021-11-17 | 0.4 | 17.6 | 0 | 2020-11-17 | -4.2 | 22.2 | 0 | 2019-11-17 | -6.1 | 24.1 | 0 | 2018-11-17 | -3 | 21 | 0 | 2017-11-17 | -4.2 | 22.2 | 0 | 2016-11-17 | 8 | 10 | 0 | 18.37 | 0
2025-11-17 | -1 | 19 | 0 | 2024-11-17 | 3.7 | 14.3 | 0 | 2023-11-17 | 3.4 | 14.6 | 0 | 2022-11-17 | -6.9 | 24.9 | 0 | 2021-11-17 | 0.4 | 17.6 | 0 | 2020-11-17 | -5.6 | 23.6 | 0 | 2019-11-17 | -6.6 | 24.6 | 0 | 2018-11-17 | -4 | 22 | 0 | 2017-11-17 | -4.5 | 22.5 | 0 | 2016-11-17 | 5.1 | 12.9 | 0 | 19.6 | 0
2025-11-17 | -1 | 19 | 0 | 2024-11-17 | 2.7 | 15.3 | 0 | 2023-11-17 | 2 | 16 | 0 | 2022-11-17 | -7.2 | 25.2 | 0 | 2021-11-17 | 0 | 18 | 0 | 2020-11-17 | -7 | 25 | 0 | 2019-11-17 | -7.1 | 25.1 | 0 | 2018-11-17 | -7 | 25 | 0 | 2017-11-17 | -5 | 23 | 0 | 2016-11-17 | 3.6 | 14.4 | 0 | 20.6 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 4.1 | 13.9 | 0 | 2023-11-17 | 0.8 | 17.2 | 0 | 2022-11-17 | -6.8 | 24.8 | 0 | 2021-11-17 | -0.2 | 18.2 | 0 | 2020-11-17 | -7.6 | 25.6 | 0 | 2019-11-17 | -8.3 | 26.3 | 0 | 2018-11-17 | -7.3 | 25.3 | 0 | 2017-11-17 | -5.7 | 23.7 | 0 | 2016-11-17 | 4.1 | 13.9 | 0 | 20.81 | 0
2025-11-17 | -1.2 | 19.2 | 0 | 2024-11-17 | 4.8 | 13.2 | 0 | 2023-11-17 | 0.2 | 17.8 | 0 | 2022-11-17 | -7.7 | 25.7 | 0 | 2021-11-17 | 0 | 18 | 0 | 2020-11-17 | -7.9 | 25.9 | 0 | 2019-11-17 | -8.8 | 26.8 | 0 | 2018-11-17 | -7.8 | 25.8 | 0 | 2017-11-17 | -5.9 | 23.9 | 0 | 2016-11-17 | 2.9 | 15.1 | 0 | 21.14 | 0
2025-11-17 | -1.4 | 19.4 | 0 | 2024-11-17 | 4.5 | 13.5 | 0 | 2023-11-17 | -0.2 | 18.2 | 0 | 2022-11-17 | -8.5 | 26.5 | 0 | 2021-11-17 | 0.2 | 17.8 | 0 | 2020-11-17 | -8 | 26 | 0 | 2019-11-17 | -8.9 | 26.9 | 0 | 2018-11-17 | -8.7 | 26.7 | 0 | 2017-11-17 | -5.9 | 23.9 | 0 | 2016-11-17 | 2.6 | 15.4 | 0 | 21.43 | 0
2025-11-18 | -1.3 | 19.3 | 0 | 2024-11-18 | 5 | 13 | 0 | 2023-11-18 | -0.9 | 18.9 | 0 | 2022-11-18 | -9.2 | 27.2 | 0 | 2021-11-18 | 0.4 | 17.6 | 0 | 2020-11-18 | -8.1 | 26.1 | 0 | 2019-11-18 | -8.3 | 26.3 | 0 | 2018-11-18 | -10.4 | 28.4 | 0 | 2017-11-18 | -5.3 | 23.3 | 0 | 2016-11-18 | 0.8 | 17.2 | 0 | 21.73 | 0
2025-11-18 | -1.4 | 19.4 | 0 | 2024-11-18 | 4.7 | 13.3 | 0 | 2023-11-18 | -1 | 19 | 0 | 2022-11-18 | -10.5 | 28.5 | 0 | 2021-11-18 | 0.7 | 17.3 | 0 | 2020-11-18 | -7.6 | 25.6 | 0 | 2019-11-18 | -7.8 | 25.8 | 0 | 2018-11-18 | -9.8 | 27.8 | 0 | 2017-11-18 | -6 | 24 | 0 | 2016-11-18 | -0.1 | 18.1 | 0 | 21.88 | 0
2025-11-18 | -1.8 | 19.8 | 0 | 2024-11-18 | 4.7 | 13.3 | 0 | 2023-11-18 | -0.5 | 18.5 | 0 | 2022-11-18 | -8.9 | 26.9 | 0 | 2021-11-18 | 1.1 | 16.9 | 0 | 2020-11-18 | -6.8 | 24.8 | 0 | 2019-11-18 | -7.3 | 25.3 | 0 | 2018-11-18 | -11.3 | 29.3 | 0 | 2017-11-18 | -4.3 | 22.3 | 0 | 2016-11-18 | 0.2 | 17.8 | 0 | 21.49 | 0
2025-11-18 | -1.7 | 19.7 | 0 | 2024-11-18 | 4.8 | 13.2 | 0 | 2023-11-18 | -0.6 | 18.6 | 0 | 2022-11-18 | -7.5 | 25.5 | 0 | 2021-11-18 | 1.6 | 16.4 | 0 | 2020-11-18 | -6.8 | 24.8 | 0 | 2019-11-18 | -6.9 | 24.9 | 0 | 2018-11-18 | -12.9 | 30.9 | 0 | 2017-11-18 | -3.7 | 21.7 | 0 | 2016-11-18 | 0.1 | 17.9 | 0 | 21.36 | 0
2025-11-18 | -1.6 | 19.6 | 0 | 2024-11-18 | 4 | 14 | 0 | 2023-11-18 | -1.1 | 19.1 | 0 | 2022-11-18 | -7.3 | 25.3 | 0 | 2021-11-18 | 2.2 | 15.8 | 0 | 2020-11-18 | -7.6 | 25.6 | 0 | 2019-11-18 | -6.6 | 24.6 | 0 | 2018-11-18 | -13.4 | 31.4 | 0 | 2017-11-18 | -4.3 | 22.3 | 0 | 2016-11-18 | 0.4 | 17.6 | 0 | 21.53 | 0
2025-11-18 | -1.4 | 19.4 | 0 | 2024-11-18 | 4 | 14 | 0 | 2023-11-18 | -1.7 | 19.7 | 0 | 2022-11-18 | -6.8 | 24.8 | 0 | 2021-11-18 | 3.2 | 14.8 | 0 | 2020-11-18 | -7.7 | 25.7 | 0 | 2019-11-18 | -6.4 | 24.4 | 0 | 2018-11-18 | -12.7 | 30.7 | 0 | 2017-11-18 | -3.8 | 21.8 | 0 | 2016-11-18 | -0.5 | 18.5 | 0 | 21.38 | 0
2025-11-18 | -1.2 | 19.2 | 0 | 2024-11-18 | 2.7 | 15.3 | 0 | 2023-11-18 | -1.7 | 19.7 | 0 | 2022-11-18 | -6.2 | 24.2 | 0 | 2021-11-18 | 4.9 | 13.1 | 0 | 2020-11-18 | -8.6 | 26.6 | 0 | 2019-11-18 | -6.3 | 24.3 | 0 | 2018-11-18 | -12.4 | 30.4 | 0 | 2017-11-18 | -4.3 | 22.3 | 0 | 2016-11-18 | -0.1 | 18.1 | 0 | 21.32 | 0
2025-11-18 | -1.1 | 19.1 | 0 | 2024-11-18 | 2.8 | 15.2 | 0 | 2023-11-18 | -2.9 | 20.9 | 0 | 2022-11-18 | -6.2 | 24.2 | 0 | 2021-11-18 | 10.2 | 7.8 | 0 | 2020-11-18 | -8.3 | 26.3 | 0 | 2019-11-18 | -5.9 | 23.9 | 0 | 2018-11-18 | -13.6 | 31.6 | 0 | 2017-11-18 | -4 | 22 | 0 | 2016-11-18 | -0.4 | 18.4 | 0 | 20.94 | 0
2025-11-18 | -1.1 | 19.1 | 0 | 2024-11-18 | 3.7 | 14.3 | 0 | 2023-11-18 | -2.9 | 20.9 | 0 | 2022-11-18 | -5.8 | 23.8 | 0 | 2021-11-18 | 5.8 | 12.2 | 0 | 2020-11-18 | -7.9 | 25.9 | 0 | 2019-11-18 | -5.4 | 23.4 | 0 | 2018-11-18 | -12.6 | 30.6 | 0 | 2017-11-18 | -3.5 | 21.5 | 0 | 2016-11-18 | 0.1 | 17.9 | 0 | 20.96 | 0
2025-11-18 | -1.2 | 19.2 | 0 | 2024-11-18 | 6.6 | 11.4 | 0 | 2023-11-18 | -1 | 19 | 0 | 2022-11-18 | -5.8 | 23.8 | 0 | 2021-11-18 | 6.3 | 11.7 | 0 | 2020-11-18 | -6.7 | 24.7 | 0 | 2019-11-18 | -5 | 23 | 0 | 2018-11-18 | -10.4 | 28.4 | 0 | 2017-11-18 | -2.6 | 20.6 | 0 | 2016-11-18 | 1.5 | 16.5 | 0 | 19.83 | 0
2025-11-18 | -1.1 | 19.1 | 0 | 2024-11-18 | 8.5 | 9.5 | 0 | 2023-11-18 | 0.1 | 17.9 | 0 | 2022-11-18 | -5.4 | 23.4 | 0 | 2021-11-18 | 7.2 | 10.8 | 0 | 2020-11-18 | -5.4 | 23.4 | 0 | 2019-11-18 | -4 | 22 | 0 | 2018-11-18 | -9 | 27 | 0 | 2017-11-18 | -2.5 | 20.5 | 0 | 2016-11-18 | 3.2 | 14.8 | 0 | 18.84 | 0
2025-11-18 | -1.2 | 19.2 | 0 | 2024-11-18 | 9 | 9 | 0 | 2023-11-18 | 1 | 17 | 0 | 2022-11-18 | -5.3 | 23.3 | 0 | 2021-11-18 | 7.5 | 10.5 | 0 | 2020-11-18 | -4.4 | 22.4 | 0 | 2019-11-18 | -2.7 | 20.7 | 0 | 2018-11-18 | -7.2 | 25.2 | 0 | 2017-11-18 | -2 | 20 | 0 | 2016-11-18 | 6.2 | 11.8 | 0 | 17.91 | 0
2025-11-18 | -1 | 19 | 0 | 2024-11-18 | 8.5 | 9.5 | 0 | 2023-11-18 | 1.7 | 16.3 | 0 | 2022-11-18 | -4.8 | 22.8 | 0 | 2021-11-18 | 7.2 | 10.8 | 0 | 2020-11-18 | -5.2 | 23.2 | 0 | 2019-11-18 | -1.5 | 19.5 | 0 | 2018-11-18 | -4.5 | 22.5 | 0 | 2017-11-18 | -1.7 | 19.7 | 0 | 2016-11-18 | 9 | 9 | 0 | 17.23 | 0
2025-11-18 | -0.8 | 18.8 | 0 | 2024-11-18 | 9.8 | 8.2 | 0 | 2023-11-18 | 2.7 | 15.3 | 0 | 2022-11-18 | -4.4 | 22.4 | 0 | 2021-11-18 | 6.8 | 11.2 | 0 | 2020-11-18 | -3.9 | 21.9 | 0 | 2019-11-18 | 0.2 | 17.8 | 0 | 2018-11-18 | -3.9 | 21.9 | 0 | 2017-11-18 | -1.5 | 19.5 | 0 | 2016-11-18 | 9.8 | 8.2 | 0 | 16.52 | 0
2025-11-18 | -0.9 | 18.9 | 0 | 2024-11-18 | 9.9 | 8.1 | 0 | 2023-11-18 | 3.5 | 14.5 | 0 | 2022-11-18 | -3.9 | 21.9 | 0 | 2021-11-18 | 6.3 | 11.7 | 0 | 2020-11-18 | -3.9 | 21.9 | 0 | 2019-11-18 | 0.2 | 17.8 | 0 | 2018-11-18 | -3.1 | 21.1 | 0 | 2017-11-18 | -1 | 19 | 0 | 2016-11-18 | 9.4 | 8.6 | 0 | 16.35 | 0
2025-11-18 | -0.6 | 18.6 | 0 | 2024-11-18 | 9.2 | 8.8 | 0 | 2023-11-18 | 3.8 | 14.2 | 0 | 2022-11-18 | -3.6 | 21.6 | 0 | 2021-11-18 | 6.3 | 11.7 | 0 | 2020-11-18 | -4.1 | 22.1 | 0 | 2019-11-18 | -0.1 | 18.1 | 0 | 2018-11-18 | -3 | 21 | 0 | 2017-11-18 | -1.3 | 19.3 | 0 | 2016-11-18 | 9.8 | 8.2 | 0 | 16.36 | 0
2025-11-18 | -1.3 | 19.3 | 0 | 2024-11-18 | 8.9 | 9.1 | 0 | 2023-11-18 | 2.5 | 15.5 | 0 | 2022-11-18 | -3.7 | 21.7 | 0 | 2021-11-18 | 6.1 | 11.9 | 0 | 2020-11-18 | -5.2 | 23.2 | 0 | 2019-11-18 | -0.7 | 18.7 | 0 | 2018-11-18 | -3.2 | 21.2 | 0 | 2017-11-18 | -1.2 | 19.2 | 0 | 2016-11-18 | 8.8 | 9.2 | 0 | 16.9 | 0
2025-11-18 | -2.5 | 20.5 | 0 | 2024-11-18 | 8.6 | 9.4 | 0 | 2023-11-18 | 2.3 | 15.7 | 0 | 2022-11-18 | -4.7 | 22.7 | 0 | 2021-11-18 | 5.6 | 12.4 | 0 | 2020-11-18 | -6.2 | 24.2 | 0 | 2019-11-18 | -1.9 | 19.9 | 0 | 2018-11-18 | -3.1 | 21.1 | 0 | 2017-11-18 | -1.4 | 19.4 | 0 | 2016-11-18 | 7.3 | 10.7 | 0 | 17.6 | 0
2025-11-18 | -2.6 | 20.6 | 0 | 2024-11-18 | 7.4 | 10.6 | 0 | 2023-11-18 | 1.8 | 16.2 | 0 | 2022-11-18 | -4.8 | 22.8 | 0 | 2021-11-18 | 5.4 | 12.6 | 0 | 2020-11-18 | -6.5 | 24.5 | 0 | 2019-11-18 | -2.8 | 20.8 | 0 | 2018-11-18 | -3.3 | 21.3 | 0 | 2017-11-18 | -1.6 | 19.6 | 0 | 2016-11-18 | 7.3 | 10.7 | 0 | 17.97 | 0
2025-11-18 | -3 | 21 | 0 | 2024-11-18 | 6.3 | 11.7 | 0 | 2023-11-18 | 2.1 | 15.9 | 0 | 2022-11-18 | -5.2 | 23.2 | 0 | 2021-11-18 | 5.2 | 12.8 | 0 | 2020-11-18 | -8.3 | 26.3 | 0 | 2019-11-18 | -2.4 | 20.4 | 0 | 2018-11-18 | -3.6 | 21.6 | 0 | 2017-11-18 | -1.6 | 19.6 | 0 | 2016-11-18 | 6.1 | 11.9 | 0 | 18.44 | 0
2025-11-18 | -4 | 22 | 0 | 2024-11-18 | 4.5 | 13.5 | 0 | 2023-11-18 | 2.1 | 15.9 | 0 | 2022-11-18 | -5.1 | 23.1 | 0 | 2021-11-18 | 4.2 | 13.8 | 0 | 2020-11-18 | -8.1 | 26.1 | 0 | 2019-11-18 | -2.8 | 20.8 | 0 | 2018-11-18 | -3.5 | 21.5 | 0 | 2017-11-18 | -1.6 | 19.6 | 0 | 2016-11-18 | 4.9 | 13.1 | 0 | 18.94 | 0
2025-11-18 | -3.6 | 21.6 | 0 | 2024-11-18 | 6.2 | 11.8 | 0 | 2023-11-18 | 2 | 16 | 0 | 2022-11-18 | -5.6 | 23.6 | 0 | 2021-11-18 | 2.7 | 15.3 | 0 | 2020-11-18 | -8 | 26 | 0 | 2019-11-18 | -3.7 | 21.7 | 0 | 2018-11-18 | -3.4 | 21.4 | 0 | 2017-11-18 | -2 | 20 | 0 | 2016-11-18 | 3.8 | 14.2 | 0 | 19.16 | 0
2025-11-18 | -5.1 | 23.1 | 0 | 2024-11-18 | 6.5 | 11.5 | 0 | 2023-11-18 | 0.6 | 17.4 | 0 | 2022-11-18 | -4.9 | 22.9 | 0 | 2021-11-18 | 2.1 | 15.9 | 0 | 2020-11-18 | -7.3 | 25.3 | 0 | 2019-11-18 | -3.9 | 21.9 | 0 | 2018-11-18 | -3.5 | 21.5 | 0 | 2017-11-18 | -1.4 | 19.4 | 0 | 2016-11-18 | 3.6 | 14.4 | 0 | 19.33 | 0
2025-11-18 | -5.7 | 23.7 | 0 | 2024-11-18 | 3.9 | 14.1 | 0 | 2023-11-18 | 2 | 16 | 0 | 2022-11-18 | -5.2 | 23.2 | 0 | 2021-11-18 | 1.1 | 16.9 | 0 | 2020-11-18 | -6.6 | 24.6 | 0 | 2019-11-18 | -3.3 | 21.3 | 0 | 2018-11-18 | -3.3 | 21.3 | 0 | 2017-11-18 | -1.2 | 19.2 | 0 | 2016-11-18 | 4 | 14 | 0 | 19.43 | 0
2025-11-19 | -6.2 | 24.2 | 0 | 2024-11-19 | 3.8 | 14.2 | 0 | 2023-11-19 | 2 | 16 | 0 | 2022-11-19 | -5.8 | 23.8 | 0 | 2021-11-19 | 1 | 17 | 0 | 2020-11-19 | -5.8 | 23.8 | 0 | 2019-11-19 | -3.3 | 21.3 | 0 | 2018-11-19 | -3.6 | 21.6 | 0 | 2017-11-19 | -1.2 | 19.2 | 0 | 2016-11-19 | 4.3 | 13.7 | 0 | 19.48 | 0
2025-11-19 | -6.2 | 24.2 | 0 | 2024-11-19 | 3.3 | 14.7 | 0 | 2023-11-19 | 1.4 | 16.6 | 0 | 2022-11-19 | -5.7 | 23.7 | 0 | 2021-11-19 | 0.8 | 17.2 | 0 | 2020-11-19 | -5.2 | 23.2 | 0 | 2019-11-19 | -2.2 | 20.2 | 0 | 2018-11-19 | -3.5 | 21.5 | 0 | 2017-11-19 | -0.7 | 18.7 | 0 | 2016-11-19 | 4.3 | 13.7 | 0 | 19.37 | 0
2025-11-19 | -5.9 | 23.9 | 0 | 2024-11-19 | 2.2 | 15.8 | 0 | 2023-11-19 | 1.1 | 16.9 | 0 | 2022-11-19 | -6.3 | 24.3 | 0 | 2021-11-19 | 0.9 | 17.1 | 0 | 2020-11-19 | -5.2 | 23.2 | 0 | 2019-11-19 | -3.4 | 21.4 | 0 | 2018-11-19 | -3.5 | 21.5 | 0 | 2017-11-19 | -0.3 | 18.3 | 0 | 2016-11-19 | 4.1 | 13.9 | 0 | 19.63 | 0
2025-11-19 | -4.5 | 22.5 | 0 | 2024-11-19 | 5 | 13 | 0 | 2023-11-19 | 1.3 | 16.7 | 0 | 2022-11-19 | -6.6 | 24.6 | 0 | 2021-11-19 | 0.3 | 17.7 | 0 | 2020-11-19 | -5.7 | 23.7 | 0 | 2019-11-19 | -3.5 | 21.5 | 0 | 2018-11-19 | -4 | 22 | 0 | 2017-11-19 | -0.2 | 18.2 | 0 | 2016-11-19 | 3.9 | 14.1 | 0 | 19.4 | 0
2025-11-19 | -4.3 | 22.3 | 0 | 2024-11-19 | 4.9 | 13.1 | 0 | 2023-11-19 | 1 | 17 | 0 | 2022-11-19 | -7 | 25 | 0 | 2021-11-19 | -0.2 | 18.2 | 0 | 2020-11-19 | -4.8 | 22.8 | 0 | 2019-11-19 | -3.4 | 21.4 | 0 | 2018-11-19 | -4.2 | 22.2 | 0 | 2017-11-19 | -0.5 | 18.5 | 0 | 2016-11-19 | 3.9 | 14.1 | 0 | 19.46 | 0
2025-11-19 | -4.2 | 22.2 | 0 | 2024-11-19 | 4.3 | 13.7 | 0 | 2023-11-19 | 0.2 | 17.8 | 0 | 2022-11-19 | -6.1 | 24.1 | 0 | 2021-11-19 | 0.2 | 17.8 | 0 | 2020-11-19 | -4.5 | 22.5 | 0 | 2019-11-19 | -3.5 | 21.5 | 0 | 2018-11-19 | -4.2 | 22.2 | 0 | 2017-11-19 | -0.9 | 18.9 | 0 | 2016-11-19 | 3.8 | 14.2 | 0 | 19.49 | 0
2025-11-19 | -4.2 | 22.2 | 0 | 2024-11-19 | 2.7 | 15.3 | 0 | 2023-11-19 | -0.3 | 18.3 | 0 | 2022-11-19 | -6.3 | 24.3 | 0 | 2021-11-19 | 0.4 | 17.6 | 0 | 2020-11-19 | -4.3 | 22.3 | 0 | 2019-11-19 | -4.1 | 22.1 | 0 | 2018-11-19 | -4.3 | 22.3 | 0 | 2017-11-19 | -1.2 | 19.2 | 0 | 2016-11-19 | 3.6 | 14.4 | 0 | 19.8 | 0
2025-11-19 | -4.5 | 22.5 | 0 | 2024-11-19 | 2.4 | 15.6 | 0 | 2023-11-19 | -0.9 | 18.9 | 0 | 2022-11-19 | -6.4 | 24.4 | 0 | 2021-11-19 | 0.5 | 17.5 | 0 | 2020-11-19 | -4.3 | 22.3 | 0 | 2019-11-19 | -5.3 | 23.3 | 0 | 2018-11-19 | -4.1 | 22.1 | 0 | 2017-11-19 | -1.5 | 19.5 | 0 | 2016-11-19 | 3.3 | 14.7 | 0 | 20.08 | 0
2025-11-19 | -4.9 | 22.9 | 0 | 2024-11-19 | 4.3 | 13.7 | 0 | 2023-11-19 | -0.1 | 18.1 | 0 | 2022-11-19 | -6.2 | 24.2 | 0 | 2021-11-19 | 1 | 17 | 0 | 2020-11-19 | -2.8 | 20.8 | 0 | 2019-11-19 | -4.8 | 22.8 | 0 | 2018-11-19 | -4.5 | 22.5 | 0 | 2017-11-19 | -2 | 20 | 0 | 2016-11-19 | 3.2 | 14.8 | 0 | 19.68 | 0
2025-11-19 | -4.6 | 22.6 | 0 | 2024-11-19 | 6.7 | 11.3 | 0 | 2023-11-19 | 1 | 17 | 0 | 2022-11-19 | -3.8 | 21.8 | 0 | 2021-11-19 | 1.2 | 16.8 | 0 | 2020-11-19 | -0.5 | 18.5 | 0 | 2019-11-19 | -4.8 | 22.8 | 0 | 2018-11-19 | -4 | 22 | 0 | 2017-11-19 | -2.4 | 20.4 | 0 | 2016-11-19 | 3.6 | 14.4 | 0 | 18.76 | 0
2025-11-19 | -3.6 | 21.6 | 0 | 2024-11-19 | 7 | 11 | 0 | 2023-11-19 | 1.9 | 16.1 | 0 | 2022-11-19 | -2.2 | 20.2 | 0 | 2021-11-19 | 2.3 | 15.7 | 0 | 2020-11-19 | 1.3 | 16.7 | 0 | 2019-11-19 | -1.2 | 19.2 | 0 | 2018-11-19 | -2.3 | 20.3 | 0 | 2017-11-19 | -2.2 | 20.2 | 0 | 2016-11-19 | 4.1 | 13.9 | 0 | 17.49 | 0
2025-11-19 | -2.5 | 20.5 | 0 | 2024-11-19 | 8.2 | 9.8 | 0 | 2023-11-19 | 3.5 | 14.5 | 0 | 2022-11-19 | -1.1 | 19.1 | 0 | 2021-11-19 | 2.5 | 15.5 | 0 | 2020-11-19 | 2.2 | 15.8 | 0 | 2019-11-19 | -0.2 | 18.2 | 0 | 2018-11-19 | -1.1 | 19.1 | 0 | 2017-11-19 | -2.1 | 20.1 | 0 | 2016-11-19 | 4.5 | 13.5 | 0 | 16.61 | 0
2025-11-19 | -2.1 | 20.1 | 0 | 2024-11-19 | 8.9 | 9.1 | 0 | 2023-11-19 | 1 | 17 | 0 | 2022-11-19 | -0.3 | 18.3 | 0 | 2021-11-19 | 2.6 | 15.4 | 0 | 2020-11-19 | 3.6 | 14.4 | 0 | 2019-11-19 | 0.1 | 17.9 | 0 | 2018-11-19 | -0.3 | 18.3 | 0 | 2017-11-19 | -1.7 | 19.7 | 0 | 2016-11-19 | 5 | 13 | 0 | 16.32 | 0
2025-11-19 | -0.6 | 18.6 | 0 | 2024-11-19 | 9 | 9 | 0 | 2023-11-19 | 2.7 | 15.3 | 0 | 2022-11-19 | -0.7 | 18.7 | 0 | 2021-11-19 | 3.3 | 14.7 | 0 | 2020-11-19 | 5.2 | 12.8 | 0 | 2019-11-19 | 0.8 | 17.2 | 0 | 2018-11-19 | 0.1 | 17.9 | 0 | 2017-11-19 | -1.3 | 19.3 | 0 | 2016-11-19 | 5.9 | 12.1 | 0 | 15.56 | 0
2025-11-19 | -0.2 | 18.2 | 0 | 2024-11-19 | 9.5 | 8.5 | 0 | 2023-11-19 | 1.3 | 16.7 | 0 | 2022-11-19 | -0.8 | 18.8 | 0 | 2021-11-19 | 3.8 | 14.2 | 0 | 2020-11-19 | 7.4 | 10.6 | 0 | 2019-11-19 | 1.3 | 16.7 | 0 | 2018-11-19 | -0.2 | 18.2 | 0 | 2017-11-19 | -0.9 | 18.9 | 0 | 2016-11-19 | 7.9 | 10.1 | 0 | 15.09 | 0
2025-11-19 | 0.1 | 17.9 | 0 | 2024-11-19 | 9.2 | 8.8 | 0 | 2023-11-19 | 2.1 | 15.9 | 0 | 2022-11-19 | -1.9 | 19.9 | 0 | 2021-11-19 | 3.4 | 14.6 | 0 | 2020-11-19 | 7.8 | 10.2 | 0 | 2019-11-19 | 1.5 | 16.5 | 0 | 2018-11-19 | -0.1 | 18.1 | 0 | 2017-11-19 | -0.9 | 18.9 | 0 | 2016-11-19 | 8.3 | 9.7 | 0 | 15.05 | 0
2025-11-19 | -0.7 | 18.7 | 0 | 2024-11-19 | 8.2 | 9.8 | 0 | 2023-11-19 | 1.4 | 16.6 | 0 | 2022-11-19 | -2 | 20 | 0 | 2021-11-19 | 2.5 | 15.5 | 0 | 2020-11-19 | 7.1 | 10.9 | 0 | 2019-11-19 | 1.1 | 16.9 | 0 | 2018-11-19 | -0.5 | 18.5 | 0 | 2017-11-19 | -1.5 | 19.5 | 0 | 2016-11-19 | 7.2 | 10.8 | 0 | 15.72 | 0
2025-11-19 | -1.4 | 19.4 | 0 | 2024-11-19 | 5.5 | 12.5 | 0 | 2023-11-19 | 0.3 | 17.7 | 0 | 2022-11-19 | -2.1 | 20.1 | 0 | 2021-11-19 | 1.3 | 16.7 | 0 | 2020-11-19 | 7.2 | 10.8 | 0 | 2019-11-19 | 0.6 | 17.4 | 0 | 2018-11-19 | -2.2 | 20.2 | 0 | 2017-11-19 | -1.9 | 19.9 | 0 | 2016-11-19 | 6.6 | 11.4 | 0 | 16.61 | 0
2025-11-19 | -3.4 | 21.4 | 0 | 2024-11-19 | 5 | 13 | 0 | 2023-11-19 | -0.5 | 18.5 | 0 | 2022-11-19 | -2.2 | 20.2 | 0 | 2021-11-19 | 0.2 | 17.8 | 0 | 2020-11-19 | 7.2 | 10.8 | 0 | 2019-11-19 | 0.3 | 17.7 | 0 | 2018-11-19 | -3 | 21 | 0 | 2017-11-19 | -2.4 | 20.4 | 0 | 2016-11-19 | 6.6 | 11.4 | 0 | 17.22 | 0
2025-11-19 | -4 | 22 | 0 | 2024-11-19 | 3.8 | 14.2 | 0 | 2023-11-19 | -0.7 | 18.7 | 0 | 2022-11-19 | -2.8 | 20.8 | 0 | 2021-11-19 | -0.6 | 18.6 | 0 | 2020-11-19 | 7.8 | 10.2 | 0 | 2019-11-19 | 0.2 | 17.8 | 0 | 2018-11-19 | -3.2 | 21.2 | 0 | 2017-11-19 | -2.8 | 20.8 | 0 | 2016-11-19 | 7.8 | 10.2 | 0 | 17.45 | 0
2025-11-19 | -3.9 | 21.9 | 0 | 2024-11-19 | 4 | 14 | 0 | 2023-11-19 | -1.4 | 19.4 | 0 | 2022-11-19 | -3 | 21 | 0 | 2021-11-19 | -1.7 | 19.7 | 0 | 2020-11-19 | 8 | 10 | 0 | 2019-11-19 | 0.1 | 17.9 | 0 | 2018-11-19 | -3.7 | 21.7 | 0 | 2017-11-19 | -3.2 | 21.2 | 0 | 2016-11-19 | 8.5 | 9.5 | 0 | 17.63 | 0
2025-11-19 | -4.4 | 22.4 | 0 | 2024-11-19 | 3.3 | 14.7 | 0 | 2023-11-19 | -2.5 | 20.5 | 0 | 2022-11-19 | -3.2 | 21.2 | 0 | 2021-11-19 | -2 | 20 | 0 | 2020-11-19 | 7.4 | 10.6 | 0 | 2019-11-19 | 0.5 | 17.5 | 0 | 2018-11-19 | -4.1 | 22.1 | 0 | 2017-11-19 | -3.4 | 21.4 | 0 | 2016-11-19 | 7.2 | 10.8 | 0 | 18.12 | 0
2025-11-19 | -4.6 | 22.6 | 0 | 2024-11-19 | 3.3 | 14.7 | 0 | 2023-11-19 | -3.3 | 21.3 | 0 | 2022-11-19 | -2.7 | 20.7 | 0 | 2021-11-19 | -2 | 20 | 0 | 2020-11-19 | 7.1 | 10.9 | 0 | 2019-11-19 | -0.3 | 18.3 | 0 | 2018-11-19 | -4.3 | 22.3 | 0 | 2017-11-19 | -3.6 | 21.6 | 0 | 2016-11-19 | 5.9 | 12.1 | 0 | 18.45 | 0
2025-11-19 | -4.9 | 22.9 | 0 | 2024-11-19 | 3.4 | 14.6 | 0 | 2023-11-19 | -4.9 | 22.9 | 0 | 2022-11-19 | -2.7 | 20.7 | 0 | 2021-11-19 | -2 | 20 | 0 | 2020-11-19 | 6.7 | 11.3 | 0 | 2019-11-19 | -0.1 | 18.1 | 0 | 2018-11-19 | -4.5 | 22.5 | 0 | 2017-11-19 | -3.7 | 21.7 | 0 | 2016-11-19 | 5.1 | 12.9 | 0 | 18.76 | 0
2025-11-20 | -4.5 | 22.5 | 0 | 2024-11-20 | 3.5 | 14.5 | 0 | 2023-11-20 | -6.3 | 24.3 | 0 | 2022-11-20 | -3.6 | 21.6 | 0 | 2021-11-20 | -4.7 | 22.7 | 0 | 2020-11-20 | 7.2 | 10.8 | 0 | 2019-11-20 | 0.1 | 17.9 | 0 | 2018-11-20 | -4.7 | 22.7 | 0 | 2017-11-20 | -5.2 | 23.2 | 0 | 2016-11-20 | 4.4 | 13.6 | 0 | 19.38 | 0
2025-11-20 | -4.2 | 22.2 | 0 | 2024-11-20 | 3.6 | 14.4 | 0 | 2023-11-20 | -6.1 | 24.1 | 0 | 2022-11-20 | -3.5 | 21.5 | 0 | 2021-11-20 | -3.8 | 21.8 | 0 | 2020-11-20 | 7.7 | 10.3 | 0 | 2019-11-20 | 0.1 | 17.9 | 0 | 2018-11-20 | -4.7 | 22.7 | 0 | 2017-11-20 | -6.3 | 24.3 | 0 | 2016-11-20 | 3.1 | 14.9 | 0 | 19.41 | 0
2025-11-20 | -4.9 | 22.9 | 0 | 2024-11-20 | 2.7 | 15.3 | 0 | 2023-11-20 | -6 | 24 | 0 | 2022-11-20 | -4.2 | 22.2 | 0 | 2021-11-20 | -3.7 | 21.7 | 0 | 2020-11-20 | 8.2 | 9.8 | 0 | 2019-11-20 | -0.6 | 18.6 | 0 | 2018-11-20 | -4.7 | 22.7 | 0 | 2017-11-20 | -6.7 | 24.7 | 0 | 2016-11-20 | 3 | 15 | 0 | 19.69 | 0
2025-11-20 | -5.6 | 23.6 | 0 | 2024-11-20 | 3.3 | 14.7 | 0 | 2023-11-20 | -6.2 | 24.2 | 0 | 2022-11-20 | -4.6 | 22.6 | 0 | 2021-11-20 | -6.3 | 24.3 | 0 | 2020-11-20 | 8.9 | 9.1 | 0 | 2019-11-20 | -0.6 | 18.6 | 0 | 2018-11-20 | -4.7 | 22.7 | 0 | 2017-11-20 | -6.8 | 24.8 | 0 | 2016-11-20 | 2.5 | 15.5 | 0 | 20.01 | 0
2025-11-20 | -5.7 | 23.7 | 0 | 2024-11-20 | 2.9 | 15.1 | 0 | 2023-11-20 | -4.9 | 22.9 | 0 | 2022-11-20 | -4.3 | 22.3 | 0 | 2021-11-20 | -6 | 24 | 0 | 2020-11-20 | 7.9 | 10.1 | 0 | 2019-11-20 | -1.5 | 19.5 | 0 | 2018-11-20 | -4.8 | 22.8 | 0 | 2017-11-20 | -7.3 | 25.3 | 0 | 2016-11-20 | 1.9 | 16.1 | 0 | 20.18 | 0
2025-11-20 | -5.8 | 23.8 | 0 | 2024-11-20 | 2.7 | 15.3 | 0 | 2023-11-20 | -5.3 | 23.3 | 0 | 2022-11-20 | -5.3 | 23.3 | 0 | 2021-11-20 | -6.4 | 24.4 | 0 | 2020-11-20 | 8.3 | 9.7 | 0 | 2019-11-20 | -1.4 | 19.4 | 0 | 2018-11-20 | -4.8 | 22.8 | 0 | 2017-11-20 | -8 | 26 | 0 | 2016-11-20 | 1.7 | 16.3 | 0 | 20.43 | 0
2025-11-20 | -5.9 | 23.9 | 0 | 2024-11-20 | 2.6 | 15.4 | 0 | 2023-11-20 | -6.7 | 24.7 | 0 | 2022-11-20 | -5.3 | 23.3 | 0 | 2021-11-20 | -4.4 | 22.4 | 0 | 2020-11-20 | 8.3 | 9.7 | 0 | 2019-11-20 | -1.4 | 19.4 | 0 | 2018-11-20 | -4.8 | 22.8 | 0 | 2017-11-20 | -8.3 | 26.3 | 0 | 2016-11-20 | 1.1 | 16.9 | 0 | 20.48 | 0
2025-11-20 | -5.9 | 23.9 | 0 | 2024-11-20 | 1.8 | 16.2 | 0 | 2023-11-20 | -7.9 | 25.9 | 0 | 2022-11-20 | -5.3 | 23.3 | 0 | 2021-11-20 | -4.9 | 22.9 | 0 | 2020-11-20 | 8 | 10 | 0 | 2019-11-20 | -1.8 | 19.8 | 0 | 2018-11-20 | -4.9 | 22.9 | 0 | 2017-11-20 | -8.7 | 26.7 | 0 | 2016-11-20 | 1 | 17 | 0 | 20.86 | 0
2025-11-20 | -5.4 | 23.4 | 0 | 2024-11-20 | 1.8 | 16.2 | 0 | 2023-11-20 | -6.1 | 24.1 | 0 | 2022-11-20 | -5.9 | 23.9 | 0 | 2021-11-20 | -4 | 22 | 0 | 2020-11-20 | 8 | 10 | 0 | 2019-11-20 | -1.3 | 19.3 | 0 | 2018-11-20 | -4.9 | 22.9 | 0 | 2017-11-20 | -7.6 | 25.6 | 0 | 2016-11-20 | 1.4 | 16.6 | 0 | 20.4 | 0
2025-11-20 | -5.5 | 23.5 | 0 | 2024-11-20 | 2.3 | 15.7 | 0 | 2023-11-20 | -3.7 | 21.7 | 0 | 2022-11-20 | -4.8 | 22.8 | 0 | 2021-11-20 | -1.7 | 19.7 | 0 | 2020-11-20 | 9.8 | 8.2 | 0 | 2019-11-20 | -0.6 | 18.6 | 0 | 2018-11-20 | -5.2 | 23.2 | 0 | 2017-11-20 | -7.1 | 25.1 | 0 | 2016-11-20 | 1 | 17 | 0 | 19.55 | 0
2025-11-20 | -5.1 | 23.1 | 0 | 2024-11-20 | 2.7 | 15.3 | 0 | 2023-11-20 | -2.6 | 20.6 | 0 | 2022-11-20 | -4.2 | 22.2 | 0 | 2021-11-20 | -0.2 | 18.2 | 0 | 2020-11-20 | 11.7 | 6.3 | 0 | 2019-11-20 | 0.1 | 17.9 | 0 | 2018-11-20 | -5.9 | 23.9 | 0 | 2017-11-20 | -6.7 | 24.7 | 0 | 2016-11-20 | 0.1 | 17.9 | 0 | 19.01 | 0
2025-11-20 | -5 | 23 | 0 | 2024-11-20 | 3.2 | 14.8 | 0 | 2023-11-20 | -2.3 | 20.3 | 0 | 2022-11-20 | -3.7 | 21.7 | 0 | 2021-11-20 | 1.1 | 16.9 | 0 | 2020-11-20 | 12.8 | 5.2 | 0 | 2019-11-20 | 0.3 | 17.7 | 0 | 2018-11-20 | -6 | 24 | 0 | 2017-11-20 | -6.4 | 24.4 | 0 | 2016-11-20 | -0.6 | 18.6 | 0 | 18.66 | 0
2025-11-20 | -4.5 | 22.5 | 0 | 2024-11-20 | 3.4 | 14.6 | 0 | 2023-11-20 | -1.8 | 19.8 | 0 | 2022-11-20 | -4.6 | 22.6 | 0 | 2021-11-20 | 1.8 | 16.2 | 0 | 2020-11-20 | 13 | 5 | 0 | 2019-11-20 | 1.1 | 16.9 | 0 | 2018-11-20 | -6.1 | 24.1 | 0 | 2017-11-20 | -5.3 | 23.3 | 0 | 2016-11-20 | -1.2 | 19.2 | 0 | 18.42 | 0
2025-11-20 | -3.9 | 21.9 | 0 | 2024-11-20 | 3.4 | 14.6 | 0 | 2023-11-20 | -1.3 | 19.3 | 0 | 2022-11-20 | -5 | 23 | 0 | 2021-11-20 | 2.9 | 15.1 | 0 | 2020-11-20 | 13.5 | 4.5 | 0 | 2019-11-20 | 1.7 | 16.3 | 0 | 2018-11-20 | -6 | 24 | 0 | 2017-11-20 | -5.2 | 23.2 | 0 | 2016-11-20 | -1.4 | 19.4 | 0 | 18.13 | 0
2025-11-20 | -3.5 | 21.5 | 0 | 2024-11-20 | 3.5 | 14.5 | 0 | 2023-11-20 | -1.1 | 19.1 | 0 | 2022-11-20 | -5.3 | 23.3 | 0 | 2021-11-20 | 3 | 15 | 0 | 2020-11-20 | 15.1 | 2.9 | 0 | 2019-11-20 | 2.1 | 15.9 | 0 | 2018-11-20 | -5.3 | 23.3 | 0 | 2017-11-20 | -5.6 | 23.6 | 0 | 2016-11-20 | -1.6 | 19.6 | 0 | 17.87 | 0
2025-11-20 | -3.5 | 21.5 | 0 | 2024-11-20 | 3.8 | 14.2 | 0 | 2023-11-20 | -1.1 | 19.1 | 0 | 2022-11-20 | -5.9 | 23.9 | 0 | 2021-11-20 | 3.2 | 14.8 | 0 | 2020-11-20 | 14.4 | 3.6 | 0 | 2019-11-20 | 2.5 | 15.5 | 0 | 2018-11-20 | -5.3 | 23.3 | 0 | 2017-11-20 | -4.9 | 22.9 | 0 | 2016-11-20 | -1.7 | 19.7 | 0 | 17.85 | 0
2025-11-20 | -3.7 | 21.7 | 0 | 2024-11-20 | 4 | 14 | 0 | 2023-11-20 | -1.9 | 19.9 | 0 | 2022-11-20 | -6.5 | 24.5 | 0 | 2021-11-20 | 2.1 | 15.9 | 0 | 2020-11-20 | 13.6 | 4.4 | 0 | 2019-11-20 | 2.5 | 15.5 | 0 | 2018-11-20 | -5.6 | 23.6 | 0 | 2017-11-20 | -5.6 | 23.6 | 0 | 2016-11-20 | -1.9 | 19.9 | 0 | 18.3 | 0
2025-11-20 | -3.7 | 21.7 | 0 | 2024-11-20 | 4.5 | 13.5 | 0 | 2023-11-20 | -2.6 | 20.6 | 0 | 2022-11-20 | -7.4 | 25.4 | 0 | 2021-11-20 | 0.9 | 17.1 | 0 | 2020-11-20 | 12.9 | 5.1 | 0 | 2019-11-20 | 2.1 | 15.9 | 0 | 2018-11-20 | -6.5 | 24.5 | 0 | 2017-11-20 | -5.9 | 23.9 | 0 | 2016-11-20 | -2 | 20 | 0 | 18.77 | 0
2025-11-20 | -3.7 | 21.7 | 0 | 2024-11-20 | 5.3 | 12.7 | 0 | 2023-11-20 | -4.7 | 22.7 | 0 | 2022-11-20 | -8.1 | 26.1 | 0 | 2021-11-20 | 0.7 | 17.3 | 0 | 2020-11-20 | 11.2 | 6.8 | 0 | 2019-11-20 | 0.6 | 17.4 | 0 | 2018-11-20 | -6.9 | 24.9 | 0 | 2017-11-20 | -6.1 | 24.1 | 0 | 2016-11-20 | -2.2 | 20.2 | 0 | 19.39 | 0
2025-11-20 | -3.8 | 21.8 | 0 | 2024-11-20 | 5.7 | 12.3 | 0 | 2023-11-20 | -4.8 | 22.8 | 0 | 2022-11-20 | -8.4 | 26.4 | 0 | 2021-11-20 | 1.1 | 16.9 | 0 | 2020-11-20 | 11.3 | 6.7 | 0 | 2019-11-20 | -0.7 | 18.7 | 0 | 2018-11-20 | -7.4 | 25.4 | 0 | 2017-11-20 | -6.1 | 24.1 | 0 | 2016-11-20 | -2.7 | 20.7 | 0 | 19.58 | 0
2025-11-20 | -3.8 | 21.8 | 0 | 2024-11-20 | 5.5 | 12.5 | 0 | 2023-11-20 | -6 | 24 | 0 | 2022-11-20 | -9.3 | 27.3 | 0 | 2021-11-20 | 1.9 | 16.1 | 0 | 2020-11-20 | 10.5 | 7.5 | 0 | 2019-11-20 | -1 | 19 | 0 | 2018-11-20 | -8.9 | 26.9 | 0 | 2017-11-20 | -5.3 | 23.3 | 0 | 2016-11-20 | -2.9 | 20.9 | 0 | 19.93 | 0
2025-11-20 | -4 | 22 | 0 | 2024-11-20 | 5.9 | 12.1 | 0 | 2023-11-20 | -6 | 24 | 0 | 2022-11-20 | -11.4 | 29.4 | 0 | 2021-11-20 | 2.2 | 15.8 | 0 | 2020-11-20 | 9.5 | 8.5 | 0 | 2019-11-20 | -4.1 | 22.1 | 0 | 2018-11-20 | -9.9 | 27.9 | 0 | 2017-11-20 | -4.9 | 22.9 | 0 | 2016-11-20 | -3.2 | 21.2 | 0 | 20.59 | 0
2025-11-20 | -4.1 | 22.1 | 0 | 2024-11-20 | 6.1 | 11.9 | 0 | 2023-11-20 | -6.3 | 24.3 | 0 | 2022-11-20 | -12 | 30 | 0 | 2021-11-20 | 2.3 | 15.7 | 0 | 2020-11-20 | 7.9 | 10.1 | 0 | 2019-11-20 | -3.2 | 21.2 | 0 | 2018-11-20 | -8.8 | 26.8 | 0 | 2017-11-20 | -4.5 | 22.5 | 0 | 2016-11-20 | -3.2 | 21.2 | 0 | 20.58 | 0
2025-11-20 | -4 | 22 | 0 | 2024-11-20 | 6.2 | 11.8 | 0 | 2023-11-20 | -6.8 | 24.8 | 0 | 2022-11-20 | -11.7 | 29.7 | 0 | 2021-11-20 | 2.6 | 15.4 | 0 | 2020-11-20 | 7.6 | 10.4 | 0 | 2019-11-20 | -5.1 | 23.1 | 0 | 2018-11-20 | -8.8 | 26.8 | 0 | 2017-11-20 | -4.2 | 22.2 | 0 | 2016-11-20 | -3.3 | 21.3 | 0 | 20.75 | 0
2025-11-21 | -4 | 22 | 0 | 2024-11-21 | 6.3 | 11.7 | 0 | 2023-11-21 | -7.3 | 25.3 | 0 | 2022-11-21 | -11.9 | 29.9 | 0 | 2021-11-21 | 2.5 | 15.5 | 0 | 2020-11-21 | 6.5 | 11.5 | 0 | 2019-11-21 | -3.5 | 21.5 | 0 | 2018-11-21 | -9.1 | 27.1 | 0 | 2017-11-21 | -3.8 | 21.8 | 0 | 2016-11-21 | -3.4 | 21.4 | 0 | 20.77 | 0
2025-11-21 | -3.9 | 21.9 | 0 | 2024-11-21 | 6 | 12 | 0 | 2023-11-21 | -7.4 | 25.4 | 0 | 2022-11-21 | -12.4 | 30.4 | 0 | 2021-11-21 | 1.8 | 16.2 | 0 | 2020-11-21 | 7.2 | 10.8 | 0 | 2019-11-21 | -3 | 21 | 0 | 2018-11-21 | -9.1 | 27.1 | 0 | 2017-11-21 | -3.7 | 21.7 | 0 | 2016-11-21 | -3.2 | 21.2 | 0 | 20.77 | 0
2025-11-21 | -3.8 | 21.8 | 0 | 2024-11-21 | 5.6 | 12.4 | 0 | 2023-11-21 | -7.7 | 25.7 | 0 | 2022-11-21 | -10.1 | 28.1 | 0 | 2021-11-21 | 1.7 | 16.3 | 0 | 2020-11-21 | 6.1 | 11.9 | 0 | 2019-11-21 | -1.9 | 19.9 | 0 | 2018-11-21 | -9 | 27 | 0 | 2017-11-21 | -4.6 | 22.6 | 0 | 2016-11-21 | -3.1 | 21.1 | 0 | 20.68 | 0
2025-11-21 | -3.7 | 21.7 | 0 | 2024-11-21 | 5.3 | 12.7 | 0 | 2023-11-21 | -8.1 | 26.1 | 0 | 2022-11-21 | -9.5 | 27.5 | 0 | 2021-11-21 | 1.4 | 16.6 | 0 | 2020-11-21 | 6 | 12 | 0 | 2019-11-21 | -1.9 | 19.9 | 0 | 2018-11-21 | -9.2 | 27.2 | 0 | 2017-11-21 | -4.8 | 22.8 | 0 | 2016-11-21 | -3.2 | 21.2 | 0 | 20.77 | 0
2025-11-21 | -3.5 | 21.5 | 0 | 2024-11-21 | 5.1 | 12.9 | 0 | 2023-11-21 | -9.4 | 27.4 | 0 | 2022-11-21 | -9.8 | 27.8 | 0 | 2021-11-21 | 1.7 | 16.3 | 0 | 2020-11-21 | 5.1 | 12.9 | 0 | 2019-11-21 | -1.5 | 19.5 | 0 | 2018-11-21 | -7.9 | 25.9 | 0 | 2017-11-21 | -4.8 | 22.8 | 0 | 2016-11-21 | -3.6 | 21.6 | 0 | 20.86 | 0
2025-11-21 | -3.2 | 21.2 | 0 | 2024-11-21 | 5.1 | 12.9 | 0 | 2023-11-21 | -8.8 | 26.8 | 0 | 2022-11-21 | -9.1 | 27.1 | 0 | 2021-11-21 | 1.9 | 16.1 | 0 | 2020-11-21 | 4.4 | 13.6 | 0 | 2019-11-21 | -3.3 | 21.3 | 0 | 2018-11-21 | -7.1 | 25.1 | 0 | 2017-11-21 | -4.3 | 22.3 | 0 | 2016-11-21 | -3.9 | 21.9 | 0 | 20.83 | 0
2025-11-21 | -2.9 | 20.9 | 0 | 2024-11-21 | 5 | 13 | 0 | 2023-11-21 | -8.4 | 26.4 | 0 | 2022-11-21 | -9.2 | 27.2 | 0 | 2021-11-21 | 1.8 | 16.2 | 0 | 2020-11-21 | 3.6 | 14.4 | 0 | 2019-11-21 | -2 | 20 | 0 | 2018-11-21 | -5.9 | 23.9 | 0 | 2017-11-21 | -3.6 | 21.6 | 0 | 2016-11-21 | -4.3 | 22.3 | 0 | 20.59 | 0
2025-11-21 | -2.5 | 20.5 | 0 | 2024-11-21 | 5.1 | 12.9 | 0 | 2023-11-21 | -7.8 | 25.8 | 0 | 2022-11-21 | -8.1 | 26.1 | 0 | 2021-11-21 | 1.9 | 16.1 | 0 | 2020-11-21 | 3.5 | 14.5 | 0 | 2019-11-21 | -1.9 | 19.9 | 0 | 2018-11-21 | -5.1 | 23.1 | 0 | 2017-11-21 | -3.8 | 21.8 | 0 | 2016-11-21 | -4.4 | 22.4 | 0 | 20.31 | 0
2025-11-21 | -1.5 | 19.5 | 0 | 2024-11-21 | 5.2 | 12.8 | 0 | 2023-11-21 | -6.7 | 24.7 | 0 | 2022-11-21 | -6.7 | 24.7 | 0 | 2021-11-21 | 2.1 | 15.9 | 0 | 2020-11-21 | 2.7 | 15.3 | 0 | 2019-11-21 | -1.1 | 19.1 | 0 | 2018-11-21 | -4.1 | 22.1 | 0 | 2017-11-21 | -2.9 | 20.9 | 0 | 2016-11-21 | -4.3 | 22.3 | 0 | 19.73 | 0
2025-11-21 | -0.4 | 18.4 | 0 | 2024-11-21 | 5.3 | 12.7 | 0 | 2023-11-21 | -5.4 | 23.4 | 0 | 2022-11-21 | -5.5 | 23.5 | 0 | 2021-11-21 | 2.5 | 15.5 | 0 | 2020-11-21 | 3.1 | 14.9 | 0 | 2019-11-21 | -0.3 | 18.3 | 0 | 2018-11-21 | -3.2 | 21.2 | 0 | 2017-11-21 | 2.5 | 15.5 | 0 | 2016-11-21 | -4.2 | 22.2 | 0 | 18.56 | 0
2025-11-21 | 0 | 18 | 0 | 2024-11-21 | 5.4 | 12.6 | 0 | 2023-11-21 | -3.5 | 21.5 | 0 | 2022-11-21 | -4 | 22 | 0 | 2021-11-21 | 3.7 | 14.3 | 0 | 2020-11-21 | 4.1 | 13.9 | 0 | 2019-11-21 | 0.8 | 17.2 | 0 | 2018-11-21 | -4.7 | 22.7 | 0 | 2017-11-21 | 3 | 15 | 0 | 2016-11-21 | -4.2 | 22.2 | 0 | 17.94 | 0
2025-11-21 | 0.2 | 17.8 | 0 | 2024-11-21 | 4.8 | 13.2 | 0 | 2023-11-21 | -2.5 | 20.5 | 0 | 2022-11-21 | -2.8 | 20.8 | 0 | 2021-11-21 | 4.4 | 13.6 | 0 | 2020-11-21 | 3.2 | 14.8 | 0 | 2019-11-21 | 1.7 | 16.3 | 0 | 2018-11-21 | -5.8 | 23.8 | 0 | 2017-11-21 | 4.8 | 13.2 | 0 | 2016-11-21 | -3.5 | 21.5 | 0 | 17.55 | 0
2025-11-21 | 3 | 15 | 0 | 2024-11-21 | 4.7 | 13.3 | 0 | 2023-11-21 | -1.9 | 19.9 | 0 | 2022-11-21 | -1.2 | 19.2 | 0 | 2021-11-21 | 4.9 | 13.1 | 0 | 2020-11-21 | 4 | 14 | 0 | 2019-11-21 | 2.5 | 15.5 | 0 | 2018-11-21 | -7.6 | 25.6 | 0 | 2017-11-21 | 6.3 | 11.7 | 0 | 2016-11-21 | -3.4 | 21.4 | 0 | 16.87 | 0
2025-11-21 | 4.5 | 13.5 | 0 | 2024-11-21 | 4.6 | 13.4 | 0 | 2023-11-21 | -1.3 | 19.3 | 0 | 2022-11-21 | -0.8 | 18.8 | 0 | 2021-11-21 | 5.2 | 12.8 | 0 | 2020-11-21 | 2.6 | 15.4 | 0 | 2019-11-21 | 2.8 | 15.2 | 0 | 2018-11-21 | -8 | 26 | 0 | 2017-11-21 | 6.6 | 11.4 | 0 | 2016-11-21 | -3.3 | 21.3 | 0 | 16.71 | 0
2025-11-21 | 6.9 | 11.1 | 0 | 2024-11-21 | 4.9 | 13.1 | 0 | 2023-11-21 | -1.3 | 19.3 | 0 | 2022-11-21 | -0.5 | 18.5 | 0 | 2021-11-21 | 6.1 | 11.9 | 0 | 2020-11-21 | 3.4 | 14.6 | 0 | 2019-11-21 | 2.9 | 15.1 | 0 | 2018-11-21 | -8.8 | 26.8 | 0 | 2017-11-21 | 7.3 | 10.7 | 0 | 2016-11-21 | -3.2 | 21.2 | 0 | 16.23 | 0
2025-11-21 | 7.3 | 10.7 | 0 | 2024-11-21 | 5.2 | 12.8 | 0 | 2023-11-21 | -1.2 | 19.2 | 0 | 2022-11-21 | 2.2 | 15.8 | 0 | 2021-11-21 | 5.3 | 12.7 | 0 | 2020-11-21 | 2.7 | 15.3 | 0 | 2019-11-21 | 2.7 | 15.3 | 0 | 2018-11-21 | -10.1 | 28.1 | 0 | 2017-11-21 | 8.5 | 9.5 | 0 | 2016-11-21 | -2.9 | 20.9 | 0 | 16.03 | 0
2025-11-21 | 4.4 | 13.6 | 0 | 2024-11-21 | 5.1 | 12.9 | 0 | 2023-11-21 | -0.9 | 18.9 | 0 | 2022-11-21 | 2.8 | 15.2 | 0 | 2021-11-21 | 4.7 | 13.3 | 0 | 2020-11-21 | 2.3 | 15.7 | 0 | 2019-11-21 | 2.2 | 15.8 | 0 | 2018-11-21 | -10.3 | 28.3 | 0 | 2017-11-21 | 7.6 | 10.4 | 0 | 2016-11-21 | -3.1 | 21.1 | 0 | 16.52 | 0
2025-11-21 | 2.9 | 15.1 | 0 | 2024-11-21 | 5 | 13 | 0 | 2023-11-21 | -0.7 | 18.7 | 0 | 2022-11-21 | 2.9 | 15.1 | 0 | 2021-11-21 | 4.2 | 13.8 | 0 | 2020-11-21 | 1.9 | 16.1 | 0 | 2019-11-21 | 1.9 | 16.1 | 0 | 2018-11-21 | -11.9 | 29.9 | 0 | 2017-11-21 | 6.2 | 11.8 | 0 | 2016-11-21 | -3.4 | 21.4 | 0 | 17.1 | 0
2025-11-21 | 2.6 | 15.4 | 0 | 2024-11-21 | 4.9 | 13.1 | 0 | 2023-11-21 | -1 | 19 | 0 | 2022-11-21 | 3 | 15 | 0 | 2021-11-21 | 3.9 | 14.1 | 0 | 2020-11-21 | 1.6 | 16.4 | 0 | 2019-11-21 | 1.8 | 16.2 | 0 | 2018-11-21 | -13.1 | 31.1 | 0 | 2017-11-21 | 6.3 | 11.7 | 0 | 2016-11-21 | -3 | 21 | 0 | 17.3 | 0
2025-11-21 | 0.8 | 17.2 | 0 | 2024-11-21 | 4.8 | 13.2 | 0 | 2023-11-21 | -1.1 | 19.1 | 0 | 2022-11-21 | 3.4 | 14.6 | 0 | 2021-11-21 | 3.4 | 14.6 | 0 | 2020-11-21 | 0.6 | 17.4 | 0 | 2019-11-21 | 2 | 16 | 0 | 2018-11-21 | -14.2 | 32.2 | 0 | 2017-11-21 | 6.2 | 11.8 | 0 | 2016-11-21 | -2.9 | 20.9 | 0 | 17.7 | 0
2025-11-21 | 0.6 | 17.4 | 0 | 2024-11-21 | 4.3 | 13.7 | 0 | 2023-11-21 | -1 | 19 | 0 | 2022-11-21 | 3.1 | 14.9 | 0 | 2021-11-21 | 3.6 | 14.4 | 0 | 2020-11-21 | -1.7 | 19.7 | 0 | 2019-11-21 | 1.3 | 16.7 | 0 | 2018-11-21 | -15.1 | 33.1 | 0 | 2017-11-21 | 5.6 | 12.4 | 0 | 2016-11-21 | -3.1 | 21.1 | 0 | 18.24 | 0
2025-11-21 | -0.5 | 18.5 | 0 | 2024-11-21 | 4.2 | 13.8 | 0 | 2023-11-21 | -1.4 | 19.4 | 0 | 2022-11-21 | 2.4 | 15.6 | 0 | 2021-11-21 | 4 | 14 | 0 | 2020-11-21 | -2.2 | 20.2 | 0 | 2019-11-21 | 1 | 17 | 0 | 2018-11-21 | -15.5 | 33.5 | 0 | 2017-11-21 | 5.5 | 12.5 | 0 | 2016-11-21 | -3.1 | 21.1 | 0 | 18.56 | 0
2025-11-21 | -0.8 | 18.8 | 0 | 2024-11-21 | 4.4 | 13.6 | 0 | 2023-11-21 | -1.3 | 19.3 | 0 | 2022-11-21 | 2.2 | 15.8 | 0 | 2021-11-21 | 4.5 | 13.5 | 0 | 2020-11-21 | -4.6 | 22.6 | 0 | 2019-11-21 | 1 | 17 | 0 | 2018-11-21 | -15.8 | 33.8 | 0 | 2017-11-21 | 6.5 | 11.5 | 0 | 2016-11-21 | -3 | 21 | 0 | 18.69 | 0
2025-11-21 | -0.5 | 18.5 | 0 | 2024-11-21 | 4.5 | 13.5 | 0 | 2023-11-21 | -1.2 | 19.2 | 0 | 2022-11-21 | 0.2 | 17.8 | 0 | 2021-11-21 | 4.8 | 13.2 | 0 | 2020-11-21 | -4.2 | 22.2 | 0 | 2019-11-21 | 0.7 | 17.3 | 0 | 2018-11-21 | -16.2 | 34.2 | 0 | 2017-11-21 | 5.2 | 12.8 | 0 | 2016-11-21 | -3 | 21 | 0 | 18.97 | 0
2025-11-22 | -2.2 | 20.2 | 0 | 2024-11-22 | 4.8 | 13.2 | 0 | 2023-11-22 | -0.8 | 18.8 | 0 | 2022-11-22 | -1.3 | 19.3 | 0 | 2021-11-22 | 4.8 | 13.2 | 0 | 2020-11-22 | -4.7 | 22.7 | 0 | 2019-11-22 | 1.4 | 16.6 | 0 | 2018-11-22 | -16.3 | 34.3 | 0 | 2017-11-22 | 4.7 | 13.3 | 0 | 2016-11-22 | -2.4 | 20.4 | 0 | 19.2 | 0
2025-11-22 | -1.1 | 19.1 | 0 | 2024-11-22 | 5 | 13 | 0 | 2023-11-22 | -0.3 | 18.3 | 0 | 2022-11-22 | -2.1 | 20.1 | 0 | 2021-11-22 | 5 | 13 | 0 | 2020-11-22 | -4.5 | 22.5 | 0 | 2019-11-22 | 1.5 | 16.5 | 0 | 2018-11-22 | -17.9 | 35.9 | 0 | 2017-11-22 | 2.6 | 15.4 | 0 | 2016-11-22 | -2.3 | 20.3 | 0 | 19.41 | 0
2025-11-22 | -1 | 19 | 0 | 2024-11-22 | 5 | 13 | 0 | 2023-11-22 | 0 | 18 | 0 | 2022-11-22 | -3 | 21 | 0 | 2021-11-22 | 5.5 | 12.5 | 0 | 2020-11-22 | -5.7 | 23.7 | 0 | 2019-11-22 | 2 | 16 | 0 | 2018-11-22 | -17.9 | 35.9 | 0 | 2017-11-22 | 1.2 | 16.8 | 0 | 2016-11-22 | -2.2 | 20.2 | 0 | 19.61 | 0
2025-11-22 | -1 | 19 | 0 | 2024-11-22 | 5 | 13 | 0 | 2023-11-22 | 0.2 | 17.8 | 0 | 2022-11-22 | -4.1 | 22.1 | 0 | 2021-11-22 | 5.8 | 12.2 | 0 | 2020-11-22 | -4.4 | 22.4 | 0 | 2019-11-22 | 5 | 13 | 0 | 2018-11-22 | -15.9 | 33.9 | 0 | 2017-11-22 | 0.8 | 17.2 | 0 | 2016-11-22 | -2.2 | 20.2 | 0 | 19.08 | 0
2025-11-22 | -1.6 | 19.6 | 0 | 2024-11-22 | 5.1 | 12.9 | 0 | 2023-11-22 | 0.3 | 17.7 | 0 | 2022-11-22 | -4.8 | 22.8 | 0 | 2021-11-22 | 5.6 | 12.4 | 0 | 2020-11-22 | -4.6 | 22.6 | 0 | 2019-11-22 | 5.7 | 12.3 | 0 | 2018-11-22 | -16.2 | 34.2 | 0 | 2017-11-22 | 0.3 | 17.7 | 0 | 2016-11-22 | -2.1 | 20.1 | 0 | 19.23 | 0
2025-11-22 | -2.1 | 20.1 | 0 | 2024-11-22 | 4.8 | 13.2 | 0 | 2023-11-22 | 0.4 | 17.6 | 0 | 2022-11-22 | -5.7 | 23.7 | 0 | 2021-11-22 | 4.7 | 13.3 | 0 | 2020-11-22 | -4.3 | 22.3 | 0 | 2019-11-22 | 6.1 | 11.9 | 0 | 2018-11-22 | -14.8 | 32.8 | 0 | 2017-11-22 | 0.2 | 17.8 | 0 | 2016-11-22 | -2.1 | 20.1 | 0 | 19.28 | 0
2025-11-22 | -1.5 | 19.5 | 0 | 2024-11-22 | 4.5 | 13.5 | 0 | 2023-11-22 | 0.3 | 17.7 | 0 | 2022-11-22 | -7.6 | 25.6 | 0 | 2021-11-22 | 1.3 | 16.7 | 0 | 2020-11-22 | -4 | 22 | 0 | 2019-11-22 | 6.5 | 11.5 | 0 | 2018-11-22 | -15 | 33 | 0 | 2017-11-22 | 0.2 | 17.8 | 0 | 2016-11-22 | -2.4 | 20.4 | 0 | 19.77 | 0
2025-11-22 | -1.3 | 19.3 | 0 | 2024-11-22 | 4.4 | 13.6 | 0 | 2023-11-22 | 0.3 | 17.7 | 0 | 2022-11-22 | -7.5 | 25.5 | 0 | 2021-11-22 | 0.7 | 17.3 | 0 | 2020-11-22 | -3.9 | 21.9 | 0 | 2019-11-22 | 6.5 | 11.5 | 0 | 2018-11-22 | -15.1 | 33.1 | 0 | 2017-11-22 | 0.3 | 17.7 | 0 | 2016-11-22 | -2.3 | 20.3 | 0 | 19.79 | 0
2025-11-22 | -1.1 | 19.1 | 0 | 2024-11-22 | 4.7 | 13.3 | 0 | 2023-11-22 | 0.2 | 17.8 | 0 | 2022-11-22 | -7.7 | 25.7 | 0 | 2021-11-22 | 0 | 18 | 0 | 2020-11-22 | -3.5 | 21.5 | 0 | 2019-11-22 | 5.1 | 12.9 | 0 | 2018-11-22 | -15.1 | 33.1 | 0 | 2017-11-22 | 0.4 | 17.6 | 0 | 2016-11-22 | -2 | 20 | 0 | 19.9 | 0
2025-11-22 | -0.5 | 18.5 | 0 | 2024-11-22 | 4.8 | 13.2 | 0 | 2023-11-22 | 0.6 | 17.4 | 0 | 2022-11-22 | -4.8 | 22.8 | 0 | 2021-11-22 | 1 | 17 | 0 | 2020-11-22 | -2.9 | 20.9 | 0 | 2019-11-22 | 4.8 | 13.2 | 0 | 2018-11-22 | -14.3 | 32.3 | 0 | 2017-11-22 | 0.3 | 17.7 | 0 | 2016-11-22 | -1.6 | 19.6 | 0 | 19.26 | 0
2025-11-22 | 1.2 | 16.8 | 0 | 2024-11-22 | 5.1 | 12.9 | 0 | 2023-11-22 | 0.7 | 17.3 | 0 | 2022-11-22 | -3.9 | 21.9 | 0 | 2021-11-22 | 1.8 | 16.2 | 0 | 2020-11-22 | -2.2 | 20.2 | 0 | 2019-11-22 | 2.8 | 15.2 | 0 | 2018-11-22 | -13.3 | 31.3 | 0 | 2017-11-22 | 0.3 | 17.7 | 0 | 2016-11-22 | -2.1 | 20.1 | 0 | 18.96 | 0
2025-11-22 | 2 | 16 | 0 | 2024-11-22 | 5.3 | 12.7 | 0 | 2023-11-22 | 1 | 17 | 0 | 2022-11-22 | -2.9 | 20.9 | 0 | 2021-11-22 | 2.7 | 15.3 | 0 | 2020-11-22 | -1.5 | 19.5 | 0 | 2019-11-22 | 2.7 | 15.3 | 0 | 2018-11-22 | -12 | 30 | 0 | 2017-11-22 | -0.6 | 18.6 | 0 | 2016-11-22 | -1.9 | 19.9 | 0 | 18.52 | 0
2025-11-22 | 2.7 | 15.3 | 0 | 2024-11-22 | 5.4 | 12.6 | 0 | 2023-11-22 | 1 | 17 | 0 | 2022-11-22 | -2.4 | 20.4 | 0 | 2021-11-22 | 2.9 | 15.1 | 0 | 2020-11-22 | -1 | 19 | 0 | 2019-11-22 | 0.4 | 17.6 | 0 | 2018-11-22 | -11.2 | 29.2 | 0 | 2017-11-22 | -1.2 | 19.2 | 0 | 2016-11-22 | -1.4 | 19.4 | 0 | 18.48 | 0
2025-11-22 | 2.4 | 15.6 | 0 | 2024-11-22 | 6.1 | 11.9 | 0 | 2023-11-22 | 1.3 | 16.7 | 0 | 2022-11-22 | -1.7 | 19.7 | 0 | 2021-11-22 | 3.2 | 14.8 | 0 | 2020-11-22 | -0.7 | 18.7 | 0 | 2019-11-22 | 0 | 18 | 0 | 2018-11-22 | -10.5 | 28.5 | 0 | 2017-11-22 | -1.4 | 19.4 | 0 | 2016-11-22 | -0.6 | 18.6 | 0 | 18.19 | 0
2025-11-22 | 2.7 | 15.3 | 0 | 2024-11-22 | 7 | 11 | 0 | 2023-11-22 | 1.5 | 16.5 | 0 | 2022-11-22 | -1.3 | 19.3 | 0 | 2021-11-22 | 2.3 | 15.7 | 0 | 2020-11-22 | 0 | 18 | 0 | 2019-11-22 | -0.2 | 18.2 | 0 | 2018-11-22 | -10.4 | 28.4 | 0 | 2017-11-22 | -1 | 19 | 0 | 2016-11-22 | -0.6 | 18.6 | 0 | 18 | 0
2025-11-22 | 3.2 | 14.8 | 0 | 2024-11-22 | 6.7 | 11.3 | 0 | 2023-11-22 | 1.5 | 16.5 | 0 | 2022-11-22 | -1.3 | 19.3 | 0 | 2021-11-22 | 1.5 | 16.5 | 0 | 2020-11-22 | -0.5 | 18.5 | 0 | 2019-11-22 | -0.3 | 18.3 | 0 | 2018-11-22 | -10.8 | 28.8 | 0 | 2017-11-22 | -1.1 | 19.1 | 0 | 2016-11-22 | -0.7 | 18.7 | 0 | 18.18 | 0
2025-11-22 | 1.4 | 16.6 | 0 | 2024-11-22 | 6.5 | 11.5 | 0 | 2023-11-22 | 1.6 | 16.4 | 0 | 2022-11-22 | -1.1 | 19.1 | 0 | 2021-11-22 | 1.3 | 16.7 | 0 | 2020-11-22 | -1.7 | 19.7 | 0 | 2019-11-22 | -0.6 | 18.6 | 0 | 2018-11-22 | -11.5 | 29.5 | 0 | 2017-11-22 | -2.2 | 20.2 | 0 | 2016-11-22 | -1.2 | 19.2 | 0 | 18.75 | 0
2025-11-22 | -0.1 | 18.1 | 0 | 2024-11-22 | 6.4 | 11.6 | 0 | 2023-11-22 | 1.5 | 16.5 | 0 | 2022-11-22 | -1.4 | 19.4 | 0 | 2021-11-22 | -0.8 | 18.8 | 0 | 2020-11-22 | -2.1 | 20.1 | 0 | 2019-11-22 | -1.1 | 19.1 | 0 | 2018-11-22 | -12.9 | 30.9 | 0 | 2017-11-22 | -3.5 | 21.5 | 0 | 2016-11-22 | -1.4 | 19.4 | 0 | 19.54 | 0
2025-11-22 | -0.6 | 18.6 | 0 | 2024-11-22 | 5.8 | 12.2 | 0 | 2023-11-22 | 1.6 | 16.4 | 0 | 2022-11-22 | -1.7 | 19.7 | 0 | 2021-11-22 | -1 | 19 | 0 | 2020-11-22 | -2.2 | 20.2 | 0 | 2019-11-22 | -1.6 | 19.6 | 0 | 2018-11-22 | -14 | 32 | 0 | 2017-11-22 | -4.2 | 22.2 | 0 | 2016-11-22 | -1.4 | 19.4 | 0 | 19.93 | 0
2025-11-22 | -2.1 | 20.1 | 0 | 2024-11-22 | 5.8 | 12.2 | 0 | 2023-11-22 | 1.8 | 16.2 | 0 | 2022-11-22 | -1.9 | 19.9 | 0 | 2021-11-22 | -1.9 | 19.9 | 0 | 2020-11-22 | -2.2 | 20.2 | 0 | 2019-11-22 | -2.3 | 20.3 | 0 | 2018-11-22 | -15 | 33 | 0 | 2017-11-22 | -5.1 | 23.1 | 0 | 2016-11-22 | -1.7 | 19.7 | 0 | 20.46 | 0
2025-11-22 | -1.6 | 19.6 | 0 | 2024-11-22 | 5.6 | 12.4 | 0 | 2023-11-22 | 1.7 | 16.3 | 0 | 2022-11-22 | -1.9 | 19.9 | 0 | 2021-11-22 | -2.6 | 20.6 | 0 | 2020-11-22 | -2.2 | 20.2 | 0 | 2019-11-22 | -2.9 | 20.9 | 0 | 2018-11-22 | -13.1 | 31.1 | 0 | 2017-11-22 | -5.8 | 23.8 | 0 | 2016-11-22 | -1.9 | 19.9 | 0 | 20.47 | 0
2025-11-22 | -2.8 | 20.8 | 0 | 2024-11-22 | 5.5 | 12.5 | 0 | 2023-11-22 | 1.5 | 16.5 | 0 | 2022-11-22 | -2 | 20 | 0 | 2021-11-22 | -2.5 | 20.5 | 0 | 2020-11-22 | -1.9 | 19.9 | 0 | 2019-11-22 | -3.4 | 21.4 | 0 | 2018-11-22 | -15 | 33 | 0 | 2017-11-22 | -6.4 | 24.4 | 0 | 2016-11-22 | -2 | 20 | 0 | 20.9 | 0
2025-11-22 | -2.7 | 20.7 | 0 | 2024-11-22 | 5.5 | 12.5 | 0 | 2023-11-22 | 1.4 | 16.6 | 0 | 2022-11-22 | -2.5 | 20.5 | 0 | 2021-11-22 | -2.3 | 20.3 | 0 | 2020-11-22 | -1.8 | 19.8 | 0 | 2019-11-22 | -4.1 | 22.1 | 0 | 2018-11-22 | -14.7 | 32.7 | 0 | 2017-11-22 | -6.9 | 24.9 | 0 | 2016-11-22 | -2.5 | 20.5 | 0 | 21.06 | 0
2025-11-22 | -5 | 23 | 0 | 2024-11-22 | 5.2 | 12.8 | 0 | 2023-11-22 | 1.1 | 16.9 | 0 | 2022-11-22 | -2.5 | 20.5 | 0 | 2021-11-22 | -3.7 | 21.7 | 0 | 2020-11-22 | -1.8 | 19.8 | 0 | 2019-11-22 | -4.5 | 22.5 | 0 | 2018-11-22 | -16.7 | 34.7 | 0 | 2017-11-22 | -7.5 | 25.5 | 0 | 2016-11-22 | -3 | 21 | 0 | 21.84 | 0
2025-11-23 | -4.7 | 22.7 | 0 | 2024-11-23 | 5.1 | 12.9 | 0 | 2023-11-23 | 1 | 17 | 0 | 2022-11-23 | -2.4 | 20.4 | 0 | 2021-11-23 | -4.3 | 22.3 | 0 | 2020-11-23 | -0.8 | 18.8 | 0 | 2019-11-23 | -5 | 23 | 0 | 2018-11-23 | -17.8 | 35.8 | 0 | 2017-11-23 | -7.5 | 25.5 | 0 | 2016-11-23 | -3.6 | 21.6 | 0 | 22 | 0
2025-11-23 | -6.8 | 24.8 | 0 | 2024-11-23 | 5.2 | 12.8 | 0 | 2023-11-23 | 0.4 | 17.6 | 0 | 2022-11-23 | -2.7 | 20.7 | 0 | 2021-11-23 | -5.2 | 23.2 | 0 | 2020-11-23 | -0.2 | 18.2 | 0 | 2019-11-23 | -5.4 | 23.4 | 0 | 2018-11-23 | -17.9 | 35.9 | 0 | 2017-11-23 | -8.2 | 26.2 | 0 | 2016-11-23 | -3.8 | 21.8 | 0 | 22.46 | 0
2025-11-23 | -5.4 | 23.4 | 0 | 2024-11-23 | 5.2 | 12.8 | 0 | 2023-11-23 | 0.3 | 17.7 | 0 | 2022-11-23 | -2.9 | 20.9 | 0 | 2021-11-23 | -5.3 | 23.3 | 0 | 2020-11-23 | 0 | 18 | 0 | 2019-11-23 | -6.3 | 24.3 | 0 | 2018-11-23 | -17.9 | 35.9 | 0 | 2017-11-23 | -8 | 26 | 0 | 2016-11-23 | -4.4 | 22.4 | 0 | 22.47 | 0
2025-11-23 | -5 | 23 | 0 | 2024-11-23 | 5 | 13 | 0 | 2023-11-23 | -0.6 | 18.6 | 0 | 2022-11-23 | -3 | 21 | 0 | 2021-11-23 | -6.8 | 24.8 | 0 | 2020-11-23 | 0 | 18 | 0 | 2019-11-23 | -6.3 | 24.3 | 0 | 2018-11-23 | -19.7 | 37.7 | 0 | 2017-11-23 | -9.1 | 27.1 | 0 | 2016-11-23 | -4.7 | 22.7 | 0 | 23.02 | 0
2025-11-23 | -4.2 | 22.2 | 0 | 2024-11-23 | 4.9 | 13.1 | 0 | 2023-11-23 | -0.5 | 18.5 | 0 | 2022-11-23 | -3.1 | 21.1 | 0 | 2021-11-23 | -5.6 | 23.6 | 0 | 2020-11-23 | 0.1 | 17.9 | 0 | 2019-11-23 | -7.6 | 25.6 | 0 | 2018-11-23 | -18.8 | 36.8 | 0 | 2017-11-23 | -9 | 27 | 0 | 2016-11-23 | -5.2 | 23.2 | 0 | 22.9 | 0
2025-11-23 | -3.7 | 21.7 | 0 | 2024-11-23 | 4.8 | 13.2 | 0 | 2023-11-23 | -0.4 | 18.4 | 0 | 2022-11-23 | -2.8 | 20.8 | 0 | 2021-11-23 | -5.5 | 23.5 | 0 | 2020-11-23 | 0 | 18 | 0 | 2019-11-23 | -7.4 | 25.4 | 0 | 2018-11-23 | -20.8 | 38.8 | 0 | 2017-11-23 | -9 | 27 | 0 | 2016-11-23 | -5.8 | 23.8 | 0 | 23.06 | 0
2025-11-23 | -3.1 | 21.1 | 0 | 2024-11-23 | 4.4 | 13.6 | 0 | 2023-11-23 | -0.3 | 18.3 | 0 | 2022-11-23 | -2.2 | 20.2 | 0 | 2021-11-23 | -5.3 | 23.3 | 0 | 2020-11-23 | -0.7 | 18.7 | 0 | 2019-11-23 | -5.9 | 23.9 | 0 | 2018-11-23 | -18.5 | 36.5 | 0 | 2017-11-23 | -8.9 | 26.9 | 0 | 2016-11-23 | -5.3 | 23.3 | 0 | 22.58 | 0
2025-11-23 | -3 | 21 | 0 | 2024-11-23 | 4.1 | 13.9 | 0 | 2023-11-23 | 0 | 18 | 0 | 2022-11-23 | -2 | 20 | 0 | 2021-11-23 | -6.3 | 24.3 | 0 | 2020-11-23 | -1.2 | 19.2 | 0 | 2019-11-23 | -4.8 | 22.8 | 0 | 2018-11-23 | -17.9 | 35.9 | 0 | 2017-11-23 | -8.6 | 26.6 | 0 | 2016-11-23 | -5.3 | 23.3 | 0 | 22.5 | 0
2025-11-23 | -2.6 | 20.6 | 0 | 2024-11-23 | 3.9 | 14.1 | 0 | 2023-11-23 | 0 | 18 | 0 | 2022-11-23 | -1.5 | 19.5 | 0 | 2021-11-23 | -6.1 | 24.1 | 0 | 2020-11-23 | -1.6 | 19.6 | 0 | 2019-11-23 | -3.6 | 21.6 | 0 | 2018-11-23 | -17.7 | 35.7 | 0 | 2017-11-23 | -7.4 | 25.4 | 0 | 2016-11-23 | -4.8 | 22.8 | 0 | 22.14 | 0
2025-11-23 | -2.4 | 20.4 | 0 | 2024-11-23 | 4.2 | 13.8 | 0 | 2023-11-23 | 0.5 | 17.5 | 0 | 2022-11-23 | -0.6 | 18.6 | 0 | 2021-11-23 | -5.2 | 23.2 | 0 | 2020-11-23 | -1.5 | 19.5 | 0 | 2019-11-23 | -2.5 | 20.5 | 0 | 2018-11-23 | -14.7 | 32.7 | 0 | 2017-11-23 | -5.8 | 23.8 | 0 | 2016-11-23 | -4.2 | 22.2 | 0 | 21.22 | 0
2025-11-23 | -1.5 | 19.5 | 0 | 2024-11-23 | 4.3 | 13.7 | 0 | 2023-11-23 | 1.4 | 16.6 | 0 | 2022-11-23 | 0 | 18 | 0 | 2021-11-23 | -4.3 | 22.3 | 0 | 2020-11-23 | -1.1 | 19.1 | 0 | 2019-11-23 | -0.8 | 18.8 | 0 | 2018-11-23 | -10.8 | 28.8 | 0 | 2017-11-23 | -5.1 | 23.1 | 0 | 2016-11-23 | -3.6 | 21.6 | 0 | 20.15 | 0
2025-11-23 | -1 | 19 | 0 | 2024-11-23 | 5.2 | 12.8 | 0 | 2023-11-23 | 1.8 | 16.2 | 0 | 2022-11-23 | 0.9 | 17.1 | 0 | 2021-11-23 | -3.7 | 21.7 | 0 | 2020-11-23 | -1 | 19 | 0 | 2019-11-23 | 1 | 17 | 0 | 2018-11-23 | -9 | 27 | 0 | 2017-11-23 | -4 | 22 | 0 | 2016-11-23 | -2.9 | 20.9 | 0 | 19.27 | 0
2025-11-23 | -0.5 | 18.5 | 0 | 2024-11-23 | 6.3 | 11.7 | 0 | 2023-11-23 | 2.4 | 15.6 | 0 | 2022-11-23 | 1.2 | 16.8 | 0 | 2021-11-23 | -3.2 | 21.2 | 0 | 2020-11-23 | -0.7 | 18.7 | 0 | 2019-11-23 | 2.9 | 15.1 | 0 | 2018-11-23 | -7.9 | 25.9 | 0 | 2017-11-23 | -2.6 | 20.6 | 0 | 2016-11-23 | -2 | 20 | 0 | 18.41 | 0
2025-11-23 | -0.5 | 18.5 | 0 | 2024-11-23 | 6.3 | 11.7 | 0 | 2023-11-23 | 3.6 | 14.4 | 0 | 2022-11-23 | 1.5 | 16.5 | 0 | 2021-11-23 | -3.2 | 21.2 | 0 | 2020-11-23 | -0.4 | 18.4 | 0 | 2019-11-23 | 4.2 | 13.8 | 0 | 2018-11-23 | -6.4 | 24.4 | 0 | 2017-11-23 | -1.9 | 19.9 | 0 | 2016-11-23 | -1.6 | 19.6 | 0 | 17.84 | 0
2025-11-23 | -0.4 | 18.4 | 0 | 2024-11-23 | 5.8 | 12.2 | 0 | 2023-11-23 | 3.2 | 14.8 | 0 | 2022-11-23 | 1.9 | 16.1 | 0 | 2021-11-23 | -3 | 21 | 0 | 2020-11-23 | 0.1 | 17.9 | 0 | 2019-11-23 | 4 | 14 | 0 | 2018-11-23 | -5.9 | 23.9 | 0 | 2017-11-23 | -1 | 19 | 0 | 2016-11-23 | -1.6 | 19.6 | 0 | 17.69 | 0
2025-11-23 | -0.3 | 18.3 | 0 | 2024-11-23 | 5.9 | 12.1 | 0 | 2023-11-23 | 3.3 | 14.7 | 0 | 2022-11-23 | 1.8 | 16.2 | 0 | 2021-11-23 | -2.8 | 20.8 | 0 | 2020-11-23 | 0.5 | 17.5 | 0 | 2019-11-23 | 4.4 | 13.6 | 0 | 2018-11-23 | -5.5 | 23.5 | 0 | 2017-11-23 | -0.7 | 18.7 | 0 | 2016-11-23 | -2 | 20 | 0 | 17.54 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 5.8 | 12.2 | 0 | 2023-11-23 | 3.7 | 14.3 | 0 | 2022-11-23 | 1.5 | 16.5 | 0 | 2021-11-23 | -3.5 | 21.5 | 0 | 2020-11-23 | 0.3 | 17.7 | 0 | 2019-11-23 | 3.7 | 14.3 | 0 | 2018-11-23 | -5.2 | 23.2 | 0 | 2017-11-23 | -0.5 | 18.5 | 0 | 2016-11-23 | -3.5 | 21.5 | 0 | 17.79 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 5.5 | 12.5 | 0 | 2023-11-23 | 3.8 | 14.2 | 0 | 2022-11-23 | 0.8 | 17.2 | 0 | 2021-11-23 | -5.1 | 23.1 | 0 | 2020-11-23 | 0 | 18 | 0 | 2019-11-23 | 1.8 | 16.2 | 0 | 2018-11-23 | -5 | 23 | 0 | 2017-11-23 | -0.6 | 18.6 | 0 | 2016-11-23 | -4.1 | 22.1 | 0 | 18.31 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 5.1 | 12.9 | 0 | 2023-11-23 | 3.8 | 14.2 | 0 | 2022-11-23 | -0.6 | 18.6 | 0 | 2021-11-23 | -5.9 | 23.9 | 0 | 2020-11-23 | -0.8 | 18.8 | 0 | 2019-11-23 | 0.8 | 17.2 | 0 | 2018-11-23 | -4.4 | 22.4 | 0 | 2017-11-23 | -0.6 | 18.6 | 0 | 2016-11-23 | -3.8 | 21.8 | 0 | 18.66 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 4.9 | 13.1 | 0 | 2023-11-23 | 3.2 | 14.8 | 0 | 2022-11-23 | -2.9 | 20.9 | 0 | 2021-11-23 | -6 | 24 | 0 | 2020-11-23 | -0.1 | 18.1 | 0 | 2019-11-23 | 0.1 | 17.9 | 0 | 2018-11-23 | -4.1 | 22.1 | 0 | 2017-11-23 | -0.3 | 18.3 | 0 | 2016-11-23 | -5.3 | 23.3 | 0 | 19.07 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 5 | 13 | 0 | 2023-11-23 | 2.6 | 15.4 | 0 | 2022-11-23 | -3.8 | 21.8 | 0 | 2021-11-23 | -6.6 | 24.6 | 0 | 2020-11-23 | 0.6 | 17.4 | 0 | 2019-11-23 | -0.7 | 18.7 | 0 | 2018-11-23 | -4.4 | 22.4 | 0 | 2017-11-23 | 0.3 | 17.7 | 0 | 2016-11-23 | -4.8 | 22.8 | 0 | 19.2 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 4.2 | 13.8 | 0 | 2023-11-23 | 2.2 | 15.8 | 0 | 2022-11-23 | -2.9 | 20.9 | 0 | 2021-11-23 | -7.6 | 25.6 | 0 | 2020-11-23 | -0.5 | 18.5 | 0 | 2019-11-23 | -0.4 | 18.4 | 0 | 2018-11-23 | -5.2 | 23.2 | 0 | 2017-11-23 | 0.7 | 17.3 | 0 | 2016-11-23 | -4.9 | 22.9 | 0 | 19.46 | 0
2025-11-23 | -0.2 | 18.2 | 0 | 2024-11-23 | 3.6 | 14.4 | 0 | 2023-11-23 | 1.2 | 16.8 | 0 | 2022-11-23 | -3.3 | 21.3 | 0 | 2021-11-23 | -6.8 | 24.8 | 0 | 2020-11-23 | 0.3 | 17.7 | 0 | 2019-11-23 | -2.7 | 20.7 | 0 | 2018-11-23 | -6.4 | 24.4 | 0 | 2017-11-23 | 1.3 | 16.7 | 0 | 2016-11-23 | -5.2 | 23.2 | 0 | 19.82 | 0
2025-11-23 | -0.1 | 18.1 | 0 | 2024-11-23 | 3.3 | 14.7 | 0 | 2023-11-23 | 0.6 | 17.4 | 0 | 2022-11-23 | -5.4 | 23.4 | 0 | 2021-11-23 | -6.5 | 24.5 | 0 | 2020-11-23 | 0 | 18 | 0 | 2019-11-23 | -1.2 | 19.2 | 0 | 2018-11-23 | -7.5 | 25.5 | 0 | 2017-11-23 | 1.5 | 16.5 | 0 | 2016-11-23 | -4.1 | 22.1 | 0 | 19.94 | 0
2025-11-24 | -0.1 | 18.1 | 0 | 2024-11-24 | 2.3 | 15.7 | 0 | 2023-11-24 | -0.6 | 18.6 | 0 | 2022-11-24 | -5 | 23 | 0 | 2021-11-24 | -7 | 25 | 0 | 2020-11-24 | -0.7 | 18.7 | 0 | 2019-11-24 | -2.2 | 20.2 | 0 | 2018-11-24 | -7.6 | 25.6 | 0 | 2017-11-24 | 1.7 | 16.3 | 0 | 2016-11-24 | -4.4 | 22.4 | 0 | 20.36 | 0
2025-11-24 | 0.2 | 17.8 | 0 | 2024-11-24 | 1.7 | 16.3 | 0 | 2023-11-24 | -2.9 | 20.9 | 0 | 2022-11-24 | -2.4 | 20.4 | 0 | 2021-11-24 | -7.7 | 25.7 | 0 | 2020-11-24 | -1 | 19 | 0 | 2019-11-24 | -2.6 | 20.6 | 0 | 2018-11-24 | -10.7 | 28.7 | 0 | 2017-11-24 | 0.9 | 17.1 | 0 | 2016-11-24 | -4.2 | 22.2 | 0 | 20.87 | 0
2025-11-24 | 0.4 | 17.6 | 0 | 2024-11-24 | 1.5 | 16.5 | 0 | 2023-11-24 | -4 | 22 | 0 | 2022-11-24 | -2.8 | 20.8 | 0 | 2021-11-24 | -9.8 | 27.8 | 0 | 2020-11-24 | -1.7 | 19.7 | 0 | 2019-11-24 | -1.9 | 19.9 | 0 | 2018-11-24 | -9 | 27 | 0 | 2017-11-24 | 1.1 | 16.9 | 0 | 2016-11-24 | -4 | 22 | 0 | 21.02 | 0
2025-11-24 | 0.9 | 17.1 | 0 | 2024-11-24 | 1.5 | 16.5 | 0 | 2023-11-24 | -5.7 | 23.7 | 0 | 2022-11-24 | -2.7 | 20.7 | 0 | 2021-11-24 | -9.6 | 27.6 | 0 | 2020-11-24 | -1.8 | 19.8 | 0 | 2019-11-24 | -2.2 | 20.2 | 0 | 2018-11-24 | -9.4 | 27.4 | 0 | 2017-11-24 | 1.2 | 16.8 | 0 | 2016-11-24 | -4.1 | 22.1 | 0 | 21.19 | 0
2025-11-24 | 1 | 17 | 0 | 2024-11-24 | 1.1 | 16.9 | 0 | 2023-11-24 | -6.6 | 24.6 | 0 | 2022-11-24 | -2.9 | 20.9 | 0 | 2021-11-24 | -10.2 | 28.2 | 0 | 2020-11-24 | -3.6 | 21.6 | 0 | 2019-11-24 | -3.4 | 21.4 | 0 | 2018-11-24 | -8.8 | 26.8 | 0 | 2017-11-24 | 1.3 | 16.7 | 0 | 2016-11-24 | -3.9 | 21.9 | 0 | 21.6 | 0
2025-11-24 | 0.8 | 17.2 | 0 | 2024-11-24 | 0.2 | 17.8 | 0 | 2023-11-24 | -7.3 | 25.3 | 0 | 2022-11-24 | -3.2 | 21.2 | 0 | 2021-11-24 | -10.3 | 28.3 | 0 | 2020-11-24 | -5.8 | 23.8 | 0 | 2019-11-24 | -4 | 22 | 0 | 2018-11-24 | -8.8 | 26.8 | 0 | 2017-11-24 | 1.2 | 16.8 | 0 | 2016-11-24 | -3.6 | 21.6 | 0 | 22.08 | 0
2025-11-24 | 0 | 18 | 0 | 2024-11-24 | -0.2 | 18.2 | 0 | 2023-11-24 | -8.1 | 26.1 | 0 | 2022-11-24 | -3.2 | 21.2 | 0 | 2021-11-24 | -9.2 | 27.2 | 0 | 2020-11-24 | -6.6 | 24.6 | 0 | 2019-11-24 | -4.6 | 22.6 | 0 | 2018-11-24 | -8.2 | 26.2 | 0 | 2017-11-24 | 0.9 | 17.1 | 0 | 2016-11-24 | -3.4 | 21.4 | 0 | 22.26 | 0
2025-11-24 | 0 | 18 | 0 | 2024-11-24 | -0.2 | 18.2 | 0 | 2023-11-24 | -7.8 | 25.8 | 0 | 2022-11-24 | -2.8 | 20.8 | 0 | 2021-11-24 | -8.5 | 26.5 | 0 | 2020-11-24 | -6.2 | 24.2 | 0 | 2019-11-24 | -4.7 | 22.7 | 0 | 2018-11-24 | -7.5 | 25.5 | 0 | 2017-11-24 | 0.9 | 17.1 | 0 | 2016-11-24 | -3.1 | 21.1 | 0 | 21.99 | 0
2025-11-24 | 0.3 | 17.7 | 0 | 2024-11-24 | 0.5 | 17.5 | 0 | 2023-11-24 | -8 | 26 | 0 | 2022-11-24 | -2.6 | 20.6 | 0 | 2021-11-24 | -6.9 | 24.9 | 0 | 2020-11-24 | -6.5 | 24.5 | 0 | 2019-11-24 | -4.1 | 22.1 | 0 | 2018-11-24 | -7.4 | 25.4 | 0 | 2017-11-24 | 1 | 17 | 0 | 2016-11-24 | -2.6 | 20.6 | 0 | 21.63 | 0
2025-11-24 | 0.9 | 17.1 | 0 | 2024-11-24 | 1.7 | 16.3 | 0 | 2023-11-24 | -7.2 | 25.2 | 0 | 2022-11-24 | -2 | 20 | 0 | 2021-11-24 | -4 | 22 | 0 | 2020-11-24 | -6.2 | 24.2 | 0 | 2019-11-24 | -1.7 | 19.7 | 0 | 2018-11-24 | -6.2 | 24.2 | 0 | 2017-11-24 | 2.1 | 15.9 | 0 | 2016-11-24 | -2.2 | 20.2 | 0 | 20.48 | 0
2025-11-24 | 1.3 | 16.7 | 0 | 2024-11-24 | 2.4 | 15.6 | 0 | 2023-11-24 | -7.2 | 25.2 | 0 | 2022-11-24 | -0.9 | 18.9 | 0 | 2021-11-24 | -1.7 | 19.7 | 0 | 2020-11-24 | -5.7 | 23.7 | 0 | 2019-11-24 | 0.2 | 17.8 | 0 | 2018-11-24 | -4.9 | 22.9 | 0 | 2017-11-24 | 4 | 14 | 0 | 2016-11-24 | -2 | 20 | 0 | 19.45 | 0
2025-11-24 | 1.4 | 16.6 | 0 | 2024-11-24 | 3 | 15 | 0 | 2023-11-24 | -7.1 | 25.1 | 0 | 2022-11-24 | 0.2 | 17.8 | 0 | 2021-11-24 | 0.7 | 17.3 | 0 | 2020-11-24 | -5.3 | 23.3 | 0 | 2019-11-24 | 2 | 16 | 0 | 2018-11-24 | -3.1 | 21.1 | 0 | 2017-11-24 | 4.8 | 13.2 | 0 | 2016-11-24 | -1.8 | 19.8 | 0 | 18.52 | 0
2025-11-24 | 1.4 | 16.6 | 0 | 2024-11-24 | 3.5 | 14.5 | 0 | 2023-11-24 | -5.5 | 23.5 | 0 | 2022-11-24 | 1.4 | 16.6 | 0 | 2021-11-24 | 2.3 | 15.7 | 0 | 2020-11-24 | -5.1 | 23.1 | 0 | 2019-11-24 | 3.3 | 14.7 | 0 | 2018-11-24 | -2 | 20 | 0 | 2017-11-24 | 6.3 | 11.7 | 0 | 2016-11-24 | -1.4 | 19.4 | 0 | 17.58 | 0
2025-11-24 | 1.6 | 16.4 | 0 | 2024-11-24 | 2.6 | 15.4 | 0 | 2023-11-24 | -5.4 | 23.4 | 0 | 2022-11-24 | 2.5 | 15.5 | 0 | 2021-11-24 | 3.8 | 14.2 | 0 | 2020-11-24 | -4.7 | 22.7 | 0 | 2019-11-24 | 4.2 | 13.8 | 0 | 2018-11-24 | -0.7 | 18.7 | 0 | 2017-11-24 | 7.7 | 10.3 | 0 | 2016-11-24 | -1 | 19 | 0 | 16.94 | 0
2025-11-24 | 2.4 | 15.6 | 0 | 2024-11-24 | 2.6 | 15.4 | 0 | 2023-11-24 | -4.5 | 22.5 | 0 | 2022-11-24 | 2.4 | 15.6 | 0 | 2021-11-24 | 4.4 | 13.6 | 0 | 2020-11-24 | -4.4 | 22.4 | 0 | 2019-11-24 | 4.7 | 13.3 | 0 | 2018-11-24 | -0.7 | 18.7 | 0 | 2017-11-24 | 7.1 | 10.9 | 0 | 2016-11-24 | -1.1 | 19.1 | 0 | 16.71 | 0
2025-11-24 | 3.1 | 14.9 | 0 | 2024-11-24 | 2.5 | 15.5 | 0 | 2023-11-24 | -4.1 | 22.1 | 0 | 2022-11-24 | 2.5 | 15.5 | 0 | 2021-11-24 | 4.2 | 13.8 | 0 | 2020-11-24 | -5 | 23 | 0 | 2019-11-24 | 4.8 | 13.2 | 0 | 2018-11-24 | 0.1 | 17.9 | 0 | 2017-11-24 | 6.7 | 11.3 | 0 | 2016-11-24 | -1 | 19 | 0 | 16.62 | 0
2025-11-24 | 1.9 | 16.1 | 0 | 2024-11-24 | 1.6 | 16.4 | 0 | 2023-11-24 | -4.5 | 22.5 | 0 | 2022-11-24 | 2.3 | 15.7 | 0 | 2021-11-24 | 2.8 | 15.2 | 0 | 2020-11-24 | -5.4 | 23.4 | 0 | 2019-11-24 | 3.2 | 14.8 | 0 | 2018-11-24 | -0.2 | 18.2 | 0 | 2017-11-24 | 6.5 | 11.5 | 0 | 2016-11-24 | -1.1 | 19.1 | 0 | 17.29 | 0
2025-11-24 | 0.4 | 17.6 | 0 | 2024-11-24 | 0.5 | 17.5 | 0 | 2023-11-24 | -6 | 24 | 0 | 2022-11-24 | 1 | 17 | 0 | 2021-11-24 | 1.8 | 16.2 | 0 | 2020-11-24 | -5.8 | 23.8 | 0 | 2019-11-24 | 1.9 | 16.1 | 0 | 2018-11-24 | 0.3 | 17.7 | 0 | 2017-11-24 | 6.4 | 11.6 | 0 | 2016-11-24 | -1.1 | 19.1 | 0 | 18.06 | 0
2025-11-24 | 0.2 | 17.8 | 0 | 2024-11-24 | 0.3 | 17.7 | 0 | 2023-11-24 | -6.2 | 24.2 | 0 | 2022-11-24 | -0.1 | 18.1 | 0 | 2021-11-24 | 1.1 | 16.9 | 0 | 2020-11-24 | -7 | 25 | 0 | 2019-11-24 | -0.1 | 18.1 | 0 | 2018-11-24 | 0.4 | 17.6 | 0 | 2017-11-24 | 6 | 12 | 0 | 2016-11-24 | -1.2 | 19.2 | 0 | 18.66 | 0
2025-11-24 | 1.6 | 16.4 | 0 | 2024-11-24 | 0 | 18 | 0 | 2023-11-24 | -7 | 25 | 0 | 2022-11-24 | -0.4 | 18.4 | 0 | 2021-11-24 | 0.6 | 17.4 | 0 | 2020-11-24 | -8.2 | 26.2 | 0 | 2019-11-24 | 0.1 | 17.9 | 0 | 2018-11-24 | 0.2 | 17.8 | 0 | 2017-11-24 | 6.5 | 11.5 | 0 | 2016-11-24 | -1.2 | 19.2 | 0 | 18.78 | 0
2025-11-24 | 1.7 | 16.3 | 0 | 2024-11-24 | -0.6 | 18.6 | 0 | 2023-11-24 | -6.7 | 24.7 | 0 | 2022-11-24 | -0.8 | 18.8 | 0 | 2021-11-24 | -0.2 | 18.2 | 0 | 2020-11-24 | -8.1 | 26.1 | 0 | 2019-11-24 | -0.3 | 18.3 | 0 | 2018-11-24 | -0.4 | 18.4 | 0 | 2017-11-24 | 7.1 | 10.9 | 0 | 2016-11-24 | -1.3 | 19.3 | 0 | 18.96 | 0
2025-11-24 | 2.1 | 15.9 | 0 | 2024-11-24 | -1.1 | 19.1 | 0 | 2023-11-24 | -6.3 | 24.3 | 0 | 2022-11-24 | -1.6 | 19.6 | 0 | 2021-11-24 | -0.3 | 18.3 | 0 | 2020-11-24 | -7.4 | 25.4 | 0 | 2019-11-24 | -1.7 | 19.7 | 0 | 2018-11-24 | -0.6 | 18.6 | 0 | 2017-11-24 | 7.6 | 10.4 | 0 | 2016-11-24 | -1.2 | 19.2 | 0 | 19.05 | 0
2025-11-24 | 1.8 | 16.2 | 0 | 2024-11-24 | -1.2 | 19.2 | 0 | 2023-11-24 | -7.1 | 25.1 | 0 | 2022-11-24 | -2.4 | 20.4 | 0 | 2021-11-24 | 0.2 | 17.8 | 0 | 2020-11-24 | -6.9 | 24.9 | 0 | 2019-11-24 | -0.3 | 18.3 | 0 | 2018-11-24 | -0.2 | 18.2 | 0 | 2017-11-24 | 7.3 | 10.7 | 0 | 2016-11-24 | -1.2 | 19.2 | 0 | 19 | 0
2025-11-24 | 1.7 | 16.3 | 0 | 2024-11-24 | -1.7 | 19.7 | 0 | 2023-11-24 | -8 | 26 | 0 | 2022-11-24 | -2.4 | 20.4 | 0 | 2021-11-24 | -1.2 | 19.2 | 0 | 2020-11-24 | -6.7 | 24.7 | 0 | 2019-11-24 | -1.2 | 19.2 | 0 | 2018-11-24 | 0.1 | 17.9 | 0 | 2017-11-24 | 7.8 | 10.2 | 0 | 2016-11-24 | -1.1 | 19.1 | 0 | 19.27 | 0
2025-11-25 | 1.8 | 16.2 | 0 | 2024-11-25 | -1.6 | 19.6 | 0 | 2023-11-25 | -9.7 | 27.7 | 0 | 2022-11-25 | -2.1 | 20.1 | 0 | 2021-11-25 | -1.9 | 19.9 | 0 | 2020-11-25 | -6.5 | 24.5 | 0 | 2019-11-25 | 0.3 | 17.7 | 0 | 2018-11-25 | 0.3 | 17.7 | 0 | 2017-11-25 | 7.4 | 10.6 | 0 | 2016-11-25 | -1 | 19 | 0 | 19.3 | 0
2025-11-25 | 1.9 | 16.1 | 0 | 2024-11-25 | -2 | 20 | 0 | 2023-11-25 | -9.7 | 27.7 | 0 | 2022-11-25 | -2.1 | 20.1 | 0 | 2021-11-25 | -1.6 | 19.6 | 0 | 2020-11-25 | -6.5 | 24.5 | 0 | 2019-11-25 | 0.6 | 17.4 | 0 | 2018-11-25 | 0.4 | 17.6 | 0 | 2017-11-25 | 7 | 11 | 0 | 2016-11-25 | -0.9 | 18.9 | 0 | 19.29 | 0
2025-11-25 | 2.5 | 15.5 | 0 | 2024-11-25 | -2.7 | 20.7 | 0 | 2023-11-25 | -9.2 | 27.2 | 0 | 2022-11-25 | -1.9 | 19.9 | 0 | 2021-11-25 | -1.8 | 19.8 | 0 | 2020-11-25 | -6 | 24 | 0 | 2019-11-25 | 0.8 | 17.2 | 0 | 2018-11-25 | 0.6 | 17.4 | 0 | 2017-11-25 | 7 | 11 | 0 | 2016-11-25 | -0.9 | 18.9 | 0 | 19.16 | 0
2025-11-25 | 2.5 | 15.5 | 0 | 2024-11-25 | -3.1 | 21.1 | 0 | 2023-11-25 | -9.9 | 27.9 | 0 | 2022-11-25 | -2.1 | 20.1 | 0 | 2021-11-25 | -0.7 | 18.7 | 0 | 2020-11-25 | -5.7 | 23.7 | 0 | 2019-11-25 | 1.5 | 16.5 | 0 | 2018-11-25 | 0.7 | 17.3 | 0 | 2017-11-25 | 6.7 | 11.3 | 0 | 2016-11-25 | -0.9 | 18.9 | 0 | 19.1 | 0
2025-11-25 | 2.3 | 15.7 | 0 | 2024-11-25 | -2.8 | 20.8 | 0 | 2023-11-25 | -9.6 | 27.6 | 0 | 2022-11-25 | -1.8 | 19.8 | 0 | 2021-11-25 | -0.4 | 18.4 | 0 | 2020-11-25 | -5.8 | 23.8 | 0 | 2019-11-25 | 2.1 | 15.9 | 0 | 2018-11-25 | 0.7 | 17.3 | 0 | 2017-11-25 | 7.2 | 10.8 | 0 | 2016-11-25 | -0.8 | 18.8 | 0 | 18.89 | 0
2025-11-25 | 1.6 | 16.4 | 0 | 2024-11-25 | -4 | 22 | 0 | 2023-11-25 | -9.7 | 27.7 | 0 | 2022-11-25 | -1 | 19 | 0 | 2021-11-25 | -0.2 | 18.2 | 0 | 2020-11-25 | -5.8 | 23.8 | 0 | 2019-11-25 | 2 | 16 | 0 | 2018-11-25 | 1 | 17 | 0 | 2017-11-25 | 7.3 | 10.7 | 0 | 2016-11-25 | -0.8 | 18.8 | 0 | 18.96 | 0
2025-11-25 | 0.9 | 17.1 | 0 | 2024-11-25 | -3.4 | 21.4 | 0 | 2023-11-25 | -9.7 | 27.7 | 0 | 2022-11-25 | -0.6 | 18.6 | 0 | 2021-11-25 | -0.5 | 18.5 | 0 | 2020-11-25 | -5.7 | 23.7 | 0 | 2019-11-25 | 0.5 | 17.5 | 0 | 2018-11-25 | 1.1 | 16.9 | 0 | 2017-11-25 | 7.2 | 10.8 | 0 | 2016-11-25 | -0.7 | 18.7 | 0 | 19.09 | 0
2025-11-25 | 2.2 | 15.8 | 0 | 2024-11-25 | -3.7 | 21.7 | 0 | 2023-11-25 | -9.8 | 27.8 | 0 | 2022-11-25 | 1.1 | 16.9 | 0 | 2021-11-25 | 0 | 18 | 0 | 2020-11-25 | -5.5 | 23.5 | 0 | 2019-11-25 | 0.1 | 17.9 | 0 | 2018-11-25 | 1.4 | 16.6 | 0 | 2017-11-25 | 5.4 | 12.6 | 0 | 2016-11-25 | -0.7 | 18.7 | 0 | 18.95 | 0
2025-11-25 | 1.4 | 16.6 | 0 | 2024-11-25 | -2.9 | 20.9 | 0 | 2023-11-25 | -7.5 | 25.5 | 0 | 2022-11-25 | 3.1 | 14.9 | 0 | 2021-11-25 | 0.2 | 17.8 | 0 | 2020-11-25 | -5.2 | 23.2 | 0 | 2019-11-25 | 0.5 | 17.5 | 0 | 2018-11-25 | 1.5 | 16.5 | 0 | 2017-11-25 | 5 | 13 | 0 | 2016-11-25 | -0.6 | 18.6 | 0 | 18.45 | 0
2025-11-25 | 2.5 | 15.5 | 0 | 2024-11-25 | -1.3 | 19.3 | 0 | 2023-11-25 | -4 | 22 | 0 | 2022-11-25 | 4 | 14 | 0 | 2021-11-25 | 0.8 | 17.2 | 0 | 2020-11-25 | -5 | 23 | 0 | 2019-11-25 | 2.3 | 15.7 | 0 | 2018-11-25 | 2.7 | 15.3 | 0 | 2017-11-25 | 5.7 | 12.3 | 0 | 2016-11-25 | -0.4 | 18.4 | 0 | 17.27 | 0
2025-11-25 | 4.2 | 13.8 | 0 | 2024-11-25 | -0.2 | 18.2 | 0 | 2023-11-25 | -1.6 | 19.6 | 0 | 2022-11-25 | 4.4 | 13.6 | 0 | 2021-11-25 | 1.5 | 16.5 | 0 | 2020-11-25 | -5.1 | 23.1 | 0 | 2019-11-25 | 3.6 | 14.4 | 0 | 2018-11-25 | 3.8 | 14.2 | 0 | 2017-11-25 | 5.4 | 12.6 | 0 | 2016-11-25 | -0.1 | 18.1 | 0 | 16.41 | 0
2025-11-25 | 5.1 | 12.9 | 0 | 2024-11-25 | -0.1 | 18.1 | 0 | 2023-11-25 | 1.1 | 16.9 | 0 | 2022-11-25 | 4.8 | 13.2 | 0 | 2021-11-25 | 2 | 16 | 0 | 2020-11-25 | -4.5 | 22.5 | 0 | 2019-11-25 | 4.6 | 13.4 | 0 | 2018-11-25 | 3.9 | 14.1 | 0 | 2017-11-25 | 5.6 | 12.4 | 0 | 2016-11-25 | 0.1 | 17.9 | 0 | 15.74 | 0
2025-11-25 | 5.5 | 12.5 | 0 | 2024-11-25 | 1.5 | 16.5 | 0 | 2023-11-25 | 2.8 | 15.2 | 0 | 2022-11-25 | 4.1 | 13.9 | 0 | 2021-11-25 | 1.8 | 16.2 | 0 | 2020-11-25 | -4.1 | 22.1 | 0 | 2019-11-25 | 5.3 | 12.7 | 0 | 2018-11-25 | 3 | 15 | 0 | 2017-11-25 | 6.1 | 11.9 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 15.38 | 0
2025-11-25 | 5.6 | 12.4 | 0 | 2024-11-25 | 2.3 | 15.7 | 0 | 2023-11-25 | 3.2 | 14.8 | 0 | 2022-11-25 | 3.7 | 14.3 | 0 | 2021-11-25 | 1.8 | 16.2 | 0 | 2020-11-25 | -3.8 | 21.8 | 0 | 2019-11-25 | 6 | 12 | 0 | 2018-11-25 | 4.3 | 13.7 | 0 | 2017-11-25 | 6.6 | 11.4 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 15.01 | 0
2025-11-25 | 5.6 | 12.4 | 0 | 2024-11-25 | 2.8 | 15.2 | 0 | 2023-11-25 | 2.8 | 15.2 | 0 | 2022-11-25 | 3.9 | 14.1 | 0 | 2021-11-25 | 2.2 | 15.8 | 0 | 2020-11-25 | -3.5 | 21.5 | 0 | 2019-11-25 | 6.8 | 11.2 | 0 | 2018-11-25 | 4.7 | 13.3 | 0 | 2017-11-25 | 6.6 | 11.4 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 14.79 | 0
2025-11-25 | 5.5 | 12.5 | 0 | 2024-11-25 | 2.6 | 15.4 | 0 | 2023-11-25 | 2.5 | 15.5 | 0 | 2022-11-25 | 3.7 | 14.3 | 0 | 2021-11-25 | 2.5 | 15.5 | 0 | 2020-11-25 | -3.1 | 21.1 | 0 | 2019-11-25 | 6.7 | 11.3 | 0 | 2018-11-25 | 4.8 | 13.2 | 0 | 2017-11-25 | 6.6 | 11.4 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 14.8 | 0
2025-11-25 | 4.5 | 13.5 | 0 | 2024-11-25 | 1.8 | 16.2 | 0 | 2023-11-25 | 1.9 | 16.1 | 0 | 2022-11-25 | 3.4 | 14.6 | 0 | 2021-11-25 | 2.2 | 15.8 | 0 | 2020-11-25 | -3 | 21 | 0 | 2019-11-25 | 6.7 | 11.3 | 0 | 2018-11-25 | 4.7 | 13.3 | 0 | 2017-11-25 | 5.9 | 12.1 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 15.17 | 0
2025-11-25 | 3.6 | 14.4 | 0 | 2024-11-25 | 0.7 | 17.3 | 0 | 2023-11-25 | 1.3 | 16.7 | 0 | 2022-11-25 | 3.2 | 14.8 | 0 | 2021-11-25 | 1.7 | 16.3 | 0 | 2020-11-25 | -2.7 | 20.7 | 0 | 2019-11-25 | 5.5 | 12.5 | 0 | 2018-11-25 | 4.2 | 13.8 | 0 | 2017-11-25 | 4.3 | 13.7 | 0 | 2016-11-25 | 0.3 | 17.7 | 0 | 15.79 | 0
2025-11-25 | 2.8 | 15.2 | 0 | 2024-11-25 | 0.3 | 17.7 | 0 | 2023-11-25 | 0.9 | 17.1 | 0 | 2022-11-25 | 2.2 | 15.8 | 0 | 2021-11-25 | 1.4 | 16.6 | 0 | 2020-11-25 | -2.5 | 20.5 | 0 | 2019-11-25 | 3.8 | 14.2 | 0 | 2018-11-25 | 3.9 | 14.1 | 0 | 2017-11-25 | 4.3 | 13.7 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 16.27 | 0
2025-11-25 | 3.1 | 14.9 | 0 | 2024-11-25 | -0.7 | 18.7 | 0 | 2023-11-25 | -0.1 | 18.1 | 0 | 2022-11-25 | 2 | 16 | 0 | 2021-11-25 | 1.3 | 16.7 | 0 | 2020-11-25 | -2.3 | 20.3 | 0 | 2019-11-25 | 3.2 | 14.8 | 0 | 2018-11-25 | 3.8 | 14.2 | 0 | 2017-11-25 | 4.2 | 13.8 | 0 | 2016-11-25 | 0.1 | 17.9 | 0 | 16.54 | 0
2025-11-25 | 3.1 | 14.9 | 0 | 2024-11-25 | -1.5 | 19.5 | 0 | 2023-11-25 | -0.8 | 18.8 | 0 | 2022-11-25 | 1.8 | 16.2 | 0 | 2021-11-25 | 1.4 | 16.6 | 0 | 2020-11-25 | -2 | 20 | 0 | 2019-11-25 | 2.7 | 15.3 | 0 | 2018-11-25 | 3.8 | 14.2 | 0 | 2017-11-25 | 3.3 | 14.7 | 0 | 2016-11-25 | 0.2 | 17.8 | 0 | 16.8 | 0
2025-11-25 | 2.8 | 15.2 | 0 | 2024-11-25 | -1.6 | 19.6 | 0 | 2023-11-25 | -1.2 | 19.2 | 0 | 2022-11-25 | 1.8 | 16.2 | 0 | 2021-11-25 | 1.4 | 16.6 | 0 | 2020-11-25 | -1.8 | 19.8 | 0 | 2019-11-25 | 3.2 | 14.8 | 0 | 2018-11-25 | 3.2 | 14.8 | 0 | 2017-11-25 | 3 | 15 | 0 | 2016-11-25 | 0.1 | 17.9 | 0 | 16.91 | 0
2025-11-25 | 2.4 | 15.6 | 0 | 2024-11-25 | -0.7 | 18.7 | 0 | 2023-11-25 | -1.6 | 19.6 | 0 | 2022-11-25 | 1.2 | 16.8 | 0 | 2021-11-25 | 1.3 | 16.7 | 0 | 2020-11-25 | -1.5 | 19.5 | 0 | 2019-11-25 | 3.8 | 14.2 | 0 | 2018-11-25 | 2.9 | 15.1 | 0 | 2017-11-25 | 2.5 | 15.5 | 0 | 2016-11-25 | 0.3 | 17.7 | 0 | 16.94 | 0
2025-11-25 | 2.1 | 15.9 | 0 | 2024-11-25 | -0.2 | 18.2 | 0 | 2023-11-25 | -1.5 | 19.5 | 0 | 2022-11-25 | 0.9 | 17.1 | 0 | 2021-11-25 | 1.1 | 16.9 | 0 | 2020-11-25 | -1.2 | 19.2 | 0 | 2019-11-25 | 4.3 | 13.7 | 0 | 2018-11-25 | 3 | 15 | 0 | 2017-11-25 | 1.5 | 16.5 | 0 | 2016-11-25 | 0.4 | 17.6 | 0 | 16.96 | 0
2025-11-26 | 2.1 | 15.9 | 0 | 2024-11-26 | -0.2 | 18.2 | 0 | 2023-11-26 | -1.5 | 19.5 | 0 | 2022-11-26 | 1 | 17 | 0 | 2021-11-26 | 1.2 | 16.8 | 0 | 2020-11-26 | -0.8 | 18.8 | 0 | 2019-11-26 | 4.5 | 13.5 | 0 | 2018-11-26 | 2.6 | 15.4 | 0 | 2017-11-26 | 1.1 | 16.9 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 16.96 | 0
2025-11-26 | 2.2 | 15.8 | 0 | 2024-11-26 | 0.2 | 17.8 | 0 | 2023-11-26 | -1.7 | 19.7 | 0 | 2022-11-26 | 0.6 | 17.4 | 0 | 2021-11-26 | 1.2 | 16.8 | 0 | 2020-11-26 | -0.5 | 18.5 | 0 | 2019-11-26 | 4.1 | 13.9 | 0 | 2018-11-26 | 2.5 | 15.5 | 0 | 2017-11-26 | 0.6 | 17.4 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.04 | 0
2025-11-26 | 2.2 | 15.8 | 0 | 2024-11-26 | 0.2 | 17.8 | 0 | 2023-11-26 | -1.3 | 19.3 | 0 | 2022-11-26 | 0.7 | 17.3 | 0 | 2021-11-26 | 1.1 | 16.9 | 0 | 2020-11-26 | -0.2 | 18.2 | 0 | 2019-11-26 | 3 | 15 | 0 | 2018-11-26 | 2 | 16 | 0 | 2017-11-26 | -0.6 | 18.6 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.25 | 0
2025-11-26 | 2.2 | 15.8 | 0 | 2024-11-26 | 0.3 | 17.7 | 0 | 2023-11-26 | -2.5 | 20.5 | 0 | 2022-11-26 | 0.6 | 17.4 | 0 | 2021-11-26 | 0.9 | 17.1 | 0 | 2020-11-26 | 0 | 18 | 0 | 2019-11-26 | 3.4 | 14.6 | 0 | 2018-11-26 | 2 | 16 | 0 | 2017-11-26 | -1.4 | 19.4 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.41 | 0
2025-11-26 | 2.2 | 15.8 | 0 | 2024-11-26 | 0.4 | 17.6 | 0 | 2023-11-26 | -3.1 | 21.1 | 0 | 2022-11-26 | 0.6 | 17.4 | 0 | 2021-11-26 | 0.9 | 17.1 | 0 | 2020-11-26 | 0.2 | 17.8 | 0 | 2019-11-26 | 3.5 | 14.5 | 0 | 2018-11-26 | 2.1 | 15.9 | 0 | 2017-11-26 | -2 | 20 | 0 | 2016-11-26 | 0.2 | 17.8 | 0 | 17.5 | 0
2025-11-26 | 2.1 | 15.9 | 0 | 2024-11-26 | 0.3 | 17.7 | 0 | 2023-11-26 | -2.2 | 20.2 | 0 | 2022-11-26 | 1.1 | 16.9 | 0 | 2021-11-26 | 0.8 | 17.2 | 0 | 2020-11-26 | 0.3 | 17.7 | 0 | 2019-11-26 | 3.9 | 14.1 | 0 | 2018-11-26 | 1.5 | 16.5 | 0 | 2017-11-26 | -2.5 | 20.5 | 0 | 2016-11-26 | 0.3 | 17.7 | 0 | 17.44 | 0
2025-11-26 | 1.9 | 16.1 | 0 | 2024-11-26 | 0.4 | 17.6 | 0 | 2023-11-26 | -2.1 | 20.1 | 0 | 2022-11-26 | 1.3 | 16.7 | 0 | 2021-11-26 | 0.9 | 17.1 | 0 | 2020-11-26 | 0.3 | 17.7 | 0 | 2019-11-26 | 4.7 | 13.3 | 0 | 2018-11-26 | 1.3 | 16.7 | 0 | 2017-11-26 | -3 | 21 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.39 | 0
2025-11-26 | 2.1 | 15.9 | 0 | 2024-11-26 | 0.2 | 17.8 | 0 | 2023-11-26 | -1.7 | 19.7 | 0 | 2022-11-26 | 0.1 | 17.9 | 0 | 2021-11-26 | 1.1 | 16.9 | 0 | 2020-11-26 | 0.2 | 17.8 | 0 | 2019-11-26 | 4.2 | 13.8 | 0 | 2018-11-26 | 1.3 | 16.7 | 0 | 2017-11-26 | -4.2 | 22.2 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.63 | 0
2025-11-26 | 2.2 | 15.8 | 0 | 2024-11-26 | 0.1 | 17.9 | 0 | 2023-11-26 | -1.2 | 19.2 | 0 | 2022-11-26 | 0 | 18 | 0 | 2021-11-26 | 1.4 | 16.6 | 0 | 2020-11-26 | 0.2 | 17.8 | 0 | 2019-11-26 | 5 | 13 | 0 | 2018-11-26 | 0.9 | 17.1 | 0 | 2017-11-26 | -4.6 | 22.6 | 0 | 2016-11-26 | 0.4 | 17.6 | 0 | 17.56 | 0
2025-11-26 | 2.4 | 15.6 | 0 | 2024-11-26 | 0.1 | 17.9 | 0 | 2023-11-26 | -0.3 | 18.3 | 0 | 2022-11-26 | 2.4 | 15.6 | 0 | 2021-11-26 | 1.5 | 16.5 | 0 | 2020-11-26 | 0.3 | 17.7 | 0 | 2019-11-26 | 6 | 12 | 0 | 2018-11-26 | 1.1 | 16.9 | 0 | 2017-11-26 | -4.5 | 22.5 | 0 | 2016-11-26 | 0.6 | 17.4 | 0 | 17.04 | 0
2025-11-26 | 2.5 | 15.5 | 0 | 2024-11-26 | 0.2 | 17.8 | 0 | 2023-11-26 | 2.2 | 15.8 | 0 | 2022-11-26 | 3.9 | 14.1 | 0 | 2021-11-26 | 1.6 | 16.4 | 0 | 2020-11-26 | 0.6 | 17.4 | 0 | 2019-11-26 | 7.3 | 10.7 | 0 | 2018-11-26 | 1.3 | 16.7 | 0 | 2017-11-26 | -4.1 | 22.1 | 0 | 2016-11-26 | 0.9 | 17.1 | 0 | 16.36 | 0
2025-11-26 | 2.8 | 15.2 | 0 | 2024-11-26 | 0.3 | 17.7 | 0 | 2023-11-26 | 3.2 | 14.8 | 0 | 2022-11-26 | 5.7 | 12.3 | 0 | 2021-11-26 | 1.9 | 16.1 | 0 | 2020-11-26 | 0.8 | 17.2 | 0 | 2019-11-26 | 8.1 | 9.9 | 0 | 2018-11-26 | 1.4 | 16.6 | 0 | 2017-11-26 | -3.9 | 21.9 | 0 | 2016-11-26 | 1.3 | 16.7 | 0 | 15.84 | 0
2025-11-26 | 3.2 | 14.8 | 0 | 2024-11-26 | 0.9 | 17.1 | 0 | 2023-11-26 | 4.6 | 13.4 | 0 | 2022-11-26 | 7.2 | 10.8 | 0 | 2021-11-26 | 1.7 | 16.3 | 0 | 2020-11-26 | 1 | 17 | 0 | 2019-11-26 | 9.4 | 8.6 | 0 | 2018-11-26 | 1.6 | 16.4 | 0 | 2017-11-26 | -3.8 | 21.8 | 0 | 2016-11-26 | 1.4 | 16.6 | 0 | 15.28 | 0
2025-11-26 | 3.2 | 14.8 | 0 | 2024-11-26 | 1.3 | 16.7 | 0 | 2023-11-26 | 4.4 | 13.6 | 0 | 2022-11-26 | 8.8 | 9.2 | 0 | 2021-11-26 | 1.3 | 16.7 | 0 | 2020-11-26 | 1.1 | 16.9 | 0 | 2019-11-26 | 10 | 8 | 0 | 2018-11-26 | 1.8 | 16.2 | 0 | 2017-11-26 | -3.8 | 21.8 | 0 | 2016-11-26 | 1.4 | 16.6 | 0 | 15.05 | 0
2025-11-26 | 3.1 | 14.9 | 0 | 2024-11-26 | 2.4 | 15.6 | 0 | 2023-11-26 | 4.1 | 13.9 | 0 | 2022-11-26 | 9.9 | 8.1 | 0 | 2021-11-26 | 1 | 17 | 0 | 2020-11-26 | 1.4 | 16.6 | 0 | 2019-11-26 | 9.6 | 8.4 | 0 | 2018-11-26 | 1.5 | 16.5 | 0 | 2017-11-26 | -3.9 | 21.9 | 0 | 2016-11-26 | 1.5 | 16.5 | 0 | 14.94 | 0
2025-11-26 | 3.1 | 14.9 | 0 | 2024-11-26 | 4.4 | 13.6 | 0 | 2023-11-26 | 3.8 | 14.2 | 0 | 2022-11-26 | 10.3 | 7.7 | 0 | 2021-11-26 | 0.4 | 17.6 | 0 | 2020-11-26 | 1.5 | 16.5 | 0 | 2019-11-26 | 9.7 | 8.3 | 0 | 2018-11-26 | 1.5 | 16.5 | 0 | 2017-11-26 | -3.7 | 21.7 | 0 | 2016-11-26 | 1.4 | 16.6 | 0 | 14.76 | 0
2025-11-26 | 3.3 | 14.7 | 0 | 2024-11-26 | 4.5 | 13.5 | 0 | 2023-11-26 | 3.1 | 14.9 | 0 | 2022-11-26 | 8.9 | 9.1 | 0 | 2021-11-26 | -0.6 | 18.6 | 0 | 2020-11-26 | 1.3 | 16.7 | 0 | 2019-11-26 | 8.8 | 9.2 | 0 | 2018-11-26 | 1.7 | 16.3 | 0 | 2017-11-26 | -3.4 | 21.4 | 0 | 2016-11-26 | 1.4 | 16.6 | 0 | 15.1 | 0
2025-11-26 | 3.4 | 14.6 | 0 | 2024-11-26 | 4 | 14 | 0 | 2023-11-26 | 2.3 | 15.7 | 0 | 2022-11-26 | 7.3 | 10.7 | 0 | 2021-11-26 | -1.3 | 19.3 | 0 | 2020-11-26 | 1.2 | 16.8 | 0 | 2019-11-26 | 7.5 | 10.5 | 0 | 2018-11-26 | 2 | 16 | 0 | 2017-11-26 | -3.6 | 21.6 | 0 | 2016-11-26 | 1 | 17 | 0 | 15.62 | 0
2025-11-26 | 3.2 | 14.8 | 0 | 2024-11-26 | 1.9 | 16.1 | 0 | 2023-11-26 | 2.7 | 15.3 | 0 | 2022-11-26 | 6.1 | 11.9 | 0 | 2021-11-26 | -1.9 | 19.9 | 0 | 2020-11-26 | 1 | 17 | 0 | 2019-11-26 | 6.3 | 11.7 | 0 | 2018-11-26 | 2 | 16 | 0 | 2017-11-26 | -4 | 22 | 0 | 2016-11-26 | 0 | 18 | 0 | 16.27 | 0
2025-11-26 | 3.4 | 14.6 | 0 | 2024-11-26 | 2.1 | 15.9 | 0 | 2023-11-26 | 1.8 | 16.2 | 0 | 2022-11-26 | 6.4 | 11.6 | 0 | 2021-11-26 | -2.2 | 20.2 | 0 | 2020-11-26 | 0.9 | 17.1 | 0 | 2019-11-26 | 3.8 | 14.2 | 0 | 2018-11-26 | 2.4 | 15.6 | 0 | 2017-11-26 | -3.9 | 21.9 | 0 | 2016-11-26 | 0.2 | 17.8 | 0 | 16.51 | 0
2025-11-26 | 4.2 | 13.8 | 0 | 2024-11-26 | 1.4 | 16.6 | 0 | 2023-11-26 | 1.6 | 16.4 | 0 | 2022-11-26 | 5.9 | 12.1 | 0 | 2021-11-26 | -2.6 | 20.6 | 0 | 2020-11-26 | 1 | 17 | 0 | 2019-11-26 | 4.8 | 13.2 | 0 | 2018-11-26 | 2.1 | 15.9 | 0 | 2017-11-26 | -3.8 | 21.8 | 0 | 2016-11-26 | -0.3 | 18.3 | 0 | 16.57 | 0
2025-11-26 | 4.1 | 13.9 | 0 | 2024-11-26 | 2.1 | 15.9 | 0 | 2023-11-26 | 1.9 | 16.1 | 0 | 2022-11-26 | 4.9 | 13.1 | 0 | 2021-11-26 | -2.6 | 20.6 | 0 | 2020-11-26 | 1.1 | 16.9 | 0 | 2019-11-26 | 4.2 | 13.8 | 0 | 2018-11-26 | 2.2 | 15.8 | 0 | 2017-11-26 | -3.6 | 21.6 | 0 | 2016-11-26 | 0.1 | 17.9 | 0 | 16.56 | 0
2025-11-26 | 3.5 | 14.5 | 0 | 2024-11-26 | 2.5 | 15.5 | 0 | 2023-11-26 | 1.4 | 16.6 | 0 | 2022-11-26 | 4.9 | 13.1 | 0 | 2021-11-26 | -2.7 | 20.7 | 0 | 2020-11-26 | 1.1 | 16.9 | 0 | 2019-11-26 | 0.6 | 17.4 | 0 | 2018-11-26 | 2.1 | 15.9 | 0 | 2017-11-26 | -3.2 | 21.2 | 0 | 2016-11-26 | -0.2 | 18.2 | 0 | 17 | 0
2025-11-26 | 2.3 | 15.7 | 0 | 2024-11-26 | 2.8 | 15.2 | 0 | 2023-11-26 | 1.3 | 16.7 | 0 | 2022-11-26 | 4.4 | 13.6 | 0 | 2021-11-26 | -3.3 | 21.3 | 0 | 2020-11-26 | 1 | 17 | 0 | 2019-11-26 | -0.2 | 18.2 | 0 | 2018-11-26 | 1.9 | 16.1 | 0 | 2017-11-26 | -2.3 | 20.3 | 0 | 2016-11-26 | -0.4 | 18.4 | 0 | 17.25 | 0
2025-11-27 | 1.4 | 16.6 | 0 | 2024-11-27 | 2.4 | 15.6 | 0 | 2023-11-27 | 1.1 | 16.9 | 0 | 2022-11-27 | 4.1 | 13.9 | 0 | 2021-11-27 | -3.6 | 21.6 | 0 | 2020-11-27 | 1.3 | 16.7 | 0 | 2019-11-27 | -1.2 | 19.2 | 0 | 2018-11-27 | 1.3 | 16.7 | 0 | 2017-11-27 | -1.3 | 19.3 | 0 | 2016-11-27 | -0.1 | 18.1 | 0 | 17.46 | 0
2025-11-27 | 1.4 | 16.6 | 0 | 2024-11-27 | 2.2 | 15.8 | 0 | 2023-11-27 | 1.3 | 16.7 | 0 | 2022-11-27 | 4.1 | 13.9 | 0 | 2021-11-27 | -4 | 22 | 0 | 2020-11-27 | 1.6 | 16.4 | 0 | 2019-11-27 | -1.4 | 19.4 | 0 | 2018-11-27 | 1.3 | 16.7 | 0 | 2017-11-27 | -1 | 19 | 0 | 2016-11-27 | -0.2 | 18.2 | 0 | 17.47 | 0
2025-11-27 | 1.1 | 16.9 | 0 | 2024-11-27 | 1.9 | 16.1 | 0 | 2023-11-27 | 2.6 | 15.4 | 0 | 2022-11-27 | 2.8 | 15.2 | 0 | 2021-11-27 | -4.9 | 22.9 | 0 | 2020-11-27 | 2.3 | 15.7 | 0 | 2019-11-27 | -1.7 | 19.7 | 0 | 2018-11-27 | 0.7 | 17.3 | 0 | 2017-11-27 | -1.3 | 19.3 | 0 | 2016-11-27 | -0.5 | 18.5 | 0 | 17.7 | 0
2025-11-27 | 1.2 | 16.8 | 0 | 2024-11-27 | 1.5 | 16.5 | 0 | 2023-11-27 | 3.7 | 14.3 | 0 | 2022-11-27 | 3 | 15 | 0 | 2021-11-27 | -5.1 | 23.1 | 0 | 2020-11-27 | 1.8 | 16.2 | 0 | 2019-11-27 | -1.1 | 19.1 | 0 | 2018-11-27 | 0.3 | 17.7 | 0 | 2017-11-27 | -1.5 | 19.5 | 0 | 2016-11-27 | -0.3 | 18.3 | 0 | 17.65 | 0
2025-11-27 | 1.1 | 16.9 | 0 | 2024-11-27 | 1.2 | 16.8 | 0 | 2023-11-27 | 4.1 | 13.9 | 0 | 2022-11-27 | 2.4 | 15.6 | 0 | 2021-11-27 | -5.5 | 23.5 | 0 | 2020-11-27 | 2.2 | 15.8 | 0 | 2019-11-27 | -1.4 | 19.4 | 0 | 2018-11-27 | 0 | 18 | 0 | 2017-11-27 | -2.3 | 20.3 | 0 | 2016-11-27 | -0.4 | 18.4 | 0 | 17.86 | 0
2025-11-27 | 0.7 | 17.3 | 0 | 2024-11-27 | 0.6 | 17.4 | 0 | 2023-11-27 | 4.2 | 13.8 | 0 | 2022-11-27 | 1.8 | 16.2 | 0 | 2021-11-27 | -6.1 | 24.1 | 0 | 2020-11-27 | 2.1 | 15.9 | 0 | 2019-11-27 | -1.1 | 19.1 | 0 | 2018-11-27 | -0.3 | 18.3 | 0 | 2017-11-27 | -3.2 | 21.2 | 0 | 2016-11-27 | -0.5 | 18.5 | 0 | 18.18 | 0
2025-11-27 | 0.6 | 17.4 | 0 | 2024-11-27 | 0.1 | 17.9 | 0 | 2023-11-27 | 4 | 14 | 0 | 2022-11-27 | 2.1 | 15.9 | 0 | 2021-11-27 | -7 | 25 | 0 | 2020-11-27 | 2.5 | 15.5 | 0 | 2019-11-27 | 0.2 | 17.8 | 0 | 2018-11-27 | -0.6 | 18.6 | 0 | 2017-11-27 | -4.5 | 22.5 | 0 | 2016-11-27 | -0.4 | 18.4 | 0 | 18.3 | 0
2025-11-27 | 1.1 | 16.9 | 0 | 2024-11-27 | -0.6 | 18.6 | 0 | 2023-11-27 | 3.5 | 14.5 | 0 | 2022-11-27 | 1.9 | 16.1 | 0 | 2021-11-27 | -7.8 | 25.8 | 0 | 2020-11-27 | 2.4 | 15.6 | 0 | 2019-11-27 | 0.5 | 17.5 | 0 | 2018-11-27 | -0.7 | 18.7 | 0 | 2017-11-27 | -6.9 | 24.9 | 0 | 2016-11-27 | -0.4 | 18.4 | 0 | 18.7 | 0
2025-11-27 | 1.1 | 16.9 | 0 | 2024-11-27 | 0 | 18 | 0 | 2023-11-27 | 3 | 15 | 0 | 2022-11-27 | 2.1 | 15.9 | 0 | 2021-11-27 | -8.2 | 26.2 | 0 | 2020-11-27 | 2.4 | 15.6 | 0 | 2019-11-27 | 1 | 17 | 0 | 2018-11-27 | -0.7 | 18.7 | 0 | 2017-11-27 | -7.8 | 25.8 | 0 | 2016-11-27 | -0.4 | 18.4 | 0 | 18.75 | 0
2025-11-27 | 2.1 | 15.9 | 0 | 2024-11-27 | 1.1 | 16.9 | 0 | 2023-11-27 | 2.7 | 15.3 | 0 | 2022-11-27 | 4.6 | 13.4 | 0 | 2021-11-27 | -7.2 | 25.2 | 0 | 2020-11-27 | 2.8 | 15.2 | 0 | 2019-11-27 | 1 | 17 | 0 | 2018-11-27 | -0.6 | 18.6 | 0 | 2017-11-27 | -7.6 | 25.6 | 0 | 2016-11-27 | -0.2 | 18.2 | 0 | 18.13 | 0
2025-11-27 | 2.4 | 15.6 | 0 | 2024-11-27 | 2 | 16 | 0 | 2023-11-27 | 2.8 | 15.2 | 0 | 2022-11-27 | 6.2 | 11.8 | 0 | 2021-11-27 | -6.8 | 24.8 | 0 | 2020-11-27 | 3.1 | 14.9 | 0 | 2019-11-27 | 1.2 | 16.8 | 0 | 2018-11-27 | -0.3 | 18.3 | 0 | 2017-11-27 | -7.9 | 25.9 | 0 | 2016-11-27 | -0.1 | 18.1 | 0 | 17.74 | 0
2025-11-27 | 3.4 | 14.6 | 0 | 2024-11-27 | 4.3 | 13.7 | 0 | 2023-11-27 | 3.2 | 14.8 | 0 | 2022-11-27 | 7.2 | 10.8 | 0 | 2021-11-27 | -5.2 | 23.2 | 0 | 2020-11-27 | 3.5 | 14.5 | 0 | 2019-11-27 | 1.2 | 16.8 | 0 | 2018-11-27 | -0.4 | 18.4 | 0 | 2017-11-27 | -8 | 26 | 0 | 2016-11-27 | -0.5 | 18.5 | 0 | 17.13 | 0
2025-11-27 | 3.5 | 14.5 | 0 | 2024-11-27 | 4.3 | 13.7 | 0 | 2023-11-27 | 3.8 | 14.2 | 0 | 2022-11-27 | 7.7 | 10.3 | 0 | 2021-11-27 | -4.3 | 22.3 | 0 | 2020-11-27 | 3.8 | 14.2 | 0 | 2019-11-27 | 1.5 | 16.5 | 0 | 2018-11-27 | -0.1 | 18.1 | 0 | 2017-11-27 | -7.4 | 25.4 | 0 | 2016-11-27 | -0.2 | 18.2 | 0 | 16.74 | 0
2025-11-27 | 3.4 | 14.6 | 0 | 2024-11-27 | 5.1 | 12.9 | 0 | 2023-11-27 | 4.4 | 13.6 | 0 | 2022-11-27 | 8.7 | 9.3 | 0 | 2021-11-27 | -3.4 | 21.4 | 0 | 2020-11-27 | 4.1 | 13.9 | 0 | 2019-11-27 | 2.6 | 15.4 | 0 | 2018-11-27 | 0.2 | 17.8 | 0 | 2017-11-27 | -7.2 | 25.2 | 0 | 2016-11-27 | 0.2 | 17.8 | 0 | 16.19 | 0
2025-11-27 | 3.3 | 14.7 | 0 | 2024-11-27 | 4.2 | 13.8 | 0 | 2023-11-27 | 4.4 | 13.6 | 0 | 2022-11-27 | 8.8 | 9.2 | 0 | 2021-11-27 | -3.1 | 21.1 | 0 | 2020-11-27 | 4 | 14 | 0 | 2019-11-27 | 3.1 | 14.9 | 0 | 2018-11-27 | 0.4 | 17.6 | 0 | 2017-11-27 | -6.8 | 24.8 | 0 | 2016-11-27 | 0.2 | 17.8 | 0 | 16.15 | 0
2025-11-27 | 3 | 15 | 0 | 2024-11-27 | 4 | 14 | 0 | 2023-11-27 | 1.3 | 16.7 | 0 | 2022-11-27 | 8.1 | 9.9 | 0 | 2021-11-27 | -2.9 | 20.9 | 0 | 2020-11-27 | 4 | 14 | 0 | 2019-11-27 | 2.6 | 15.4 | 0 | 2018-11-27 | 0.4 | 17.6 | 0 | 2017-11-27 | -7.6 | 25.6 | 0 | 2016-11-27 | 0.2 | 17.8 | 0 | 16.69 | 0
2025-11-27 | 1.8 | 16.2 | 0 | 2024-11-27 | 3.7 | 14.3 | 0 | 2023-11-27 | 1.3 | 16.7 | 0 | 2022-11-27 | 7.1 | 10.9 | 0 | 2021-11-27 | -3.4 | 21.4 | 0 | 2020-11-27 | 3.9 | 14.1 | 0 | 2019-11-27 | 2.4 | 15.6 | 0 | 2018-11-27 | 0.5 | 17.5 | 0 | 2017-11-27 | -8.8 | 26.8 | 0 | 2016-11-27 | 0.1 | 17.9 | 0 | 17.14 | 0
2025-11-27 | 0.8 | 17.2 | 0 | 2024-11-27 | 3.3 | 14.7 | 0 | 2023-11-27 | 1.3 | 16.7 | 0 | 2022-11-27 | 6.2 | 11.8 | 0 | 2021-11-27 | -4 | 22 | 0 | 2020-11-27 | 3.8 | 14.2 | 0 | 2019-11-27 | 2.2 | 15.8 | 0 | 2018-11-27 | 0.3 | 17.7 | 0 | 2017-11-27 | -9 | 27 | 0 | 2016-11-27 | 0 | 18 | 0 | 17.51 | 0
2025-11-27 | 1.1 | 16.9 | 0 | 2024-11-27 | 3.1 | 14.9 | 0 | 2023-11-27 | 1 | 17 | 0 | 2022-11-27 | 5 | 13 | 0 | 2021-11-27 | -4.4 | 22.4 | 0 | 2020-11-27 | 2.7 | 15.3 | 0 | 2019-11-27 | 2.4 | 15.6 | 0 | 2018-11-27 | 0.1 | 17.9 | 0 | 2017-11-27 | -9.4 | 27.4 | 0 | 2016-11-27 | 0 | 18 | 0 | 17.84 | 0
2025-11-27 | 1 | 17 | 0 | 2024-11-27 | 1.6 | 16.4 | 0 | 2023-11-27 | 0.1 | 17.9 | 0 | 2022-11-27 | 4.7 | 13.3 | 0 | 2021-11-27 | -5 | 23 | 0 | 2020-11-27 | 3.4 | 14.6 | 0 | 2019-11-27 | 2.5 | 15.5 | 0 | 2018-11-27 | 0 | 18 | 0 | 2017-11-27 | -10.5 | 28.5 | 0 | 2016-11-27 | -0.1 | 18.1 | 0 | 18.23 | 0
2025-11-27 | 0.8 | 17.2 | 0 | 2024-11-27 | 0.4 | 17.6 | 0 | 2023-11-27 | -0.2 | 18.2 | 0 | 2022-11-27 | 4.1 | 13.9 | 0 | 2021-11-27 | -5.4 | 23.4 | 0 | 2020-11-27 | 3 | 15 | 0 | 2019-11-27 | 2.3 | 15.7 | 0 | 2018-11-27 | -0.1 | 18.1 | 0 | 2017-11-27 | -10.5 | 28.5 | 0 | 2016-11-27 | -0.2 | 18.2 | 0 | 18.58 | 0
2025-11-27 | 0.6 | 17.4 | 0 | 2024-11-27 | -0.3 | 18.3 | 0 | 2023-11-27 | -0.6 | 18.6 | 0 | 2022-11-27 | 4.4 | 13.6 | 0 | 2021-11-27 | -6 | 24 | 0 | 2020-11-27 | 2.7 | 15.3 | 0 | 2019-11-27 | 1.9 | 16.1 | 0 | 2018-11-27 | -0.1 | 18.1 | 0 | 2017-11-27 | -13.1 | 31.1 | 0 | 2016-11-27 | -0.2 | 18.2 | 0 | 19.07 | 0
2025-11-27 | -0.4 | 18.4 | 0 | 2024-11-27 | 0.9 | 17.1 | 0 | 2023-11-27 | -0.8 | 18.8 | 0 | 2022-11-27 | 3.9 | 14.1 | 0 | 2021-11-27 | -6.5 | 24.5 | 0 | 2020-11-27 | 2.7 | 15.3 | 0 | 2019-11-27 | 1.8 | 16.2 | 0 | 2018-11-27 | -0.1 | 18.1 | 0 | 2017-11-27 | -12.7 | 30.7 | 0 | 2016-11-27 | -0.3 | 18.3 | 0 | 19.15 | 0
2025-11-27 | -0.6 | 18.6 | 0 | 2024-11-27 | 0.3 | 17.7 | 0 | 2023-11-27 | -1.9 | 19.9 | 0 | 2022-11-27 | 3.8 | 14.2 | 0 | 2021-11-27 | -6.9 | 24.9 | 0 | 2020-11-27 | 2.4 | 15.6 | 0 | 2019-11-27 | 1.6 | 16.4 | 0 | 2018-11-27 | -0.1 | 18.1 | 0 | 2017-11-27 | -12.6 | 30.6 | 0 | 2016-11-27 | -0.8 | 18.8 | 0 | 19.48 | 0
2025-11-28 | -1.6 | 19.6 | 0 | 2024-11-28 | -0.8 | 18.8 | 0 | 2023-11-28 | -2.5 | 20.5 | 0 | 2022-11-28 | 3.5 | 14.5 | 0 | 2021-11-28 | -7.6 | 25.6 | 0 | 2020-11-28 | 2.2 | 15.8 | 0 | 2019-11-28 | 1 | 17 | 0 | 2018-11-28 | 0 | 18 | 0 | 2017-11-28 | -13.1 | 31.1 | 0 | 2016-11-28 | -2.8 | 20.8 | 0 | 20.17 | 0
2025-11-28 | -1.9 | 19.9 | 0 | 2024-11-28 | -1.9 | 19.9 | 0 | 2023-11-28 | -2.3 | 20.3 | 0 | 2022-11-28 | 3.5 | 14.5 | 0 | 2021-11-28 | -8 | 26 | 0 | 2020-11-28 | 2.4 | 15.6 | 0 | 2019-11-28 | 1.1 | 16.9 | 0 | 2018-11-28 | 0.1 | 17.9 | 0 | 2017-11-28 | -13.3 | 31.3 | 0 | 2016-11-28 | -4.2 | 22.2 | 0 | 20.45 | 0
2025-11-28 | -2.1 | 20.1 | 0 | 2024-11-28 | -1.4 | 19.4 | 0 | 2023-11-28 | -3 | 21 | 0 | 2022-11-28 | 3 | 15 | 0 | 2021-11-28 | -8.5 | 26.5 | 0 | 2020-11-28 | 1.8 | 16.2 | 0 | 2019-11-28 | 0.7 | 17.3 | 0 | 2018-11-28 | 0.1 | 17.9 | 0 | 2017-11-28 | -12.1 | 30.1 | 0 | 2016-11-28 | -3.2 | 21.2 | 0 | 20.47 | 0
2025-11-28 | -2.8 | 20.8 | 0 | 2024-11-28 | -1.3 | 19.3 | 0 | 2023-11-28 | -4.4 | 22.4 | 0 | 2022-11-28 | 2.7 | 15.3 | 0 | 2021-11-28 | -9.1 | 27.1 | 0 | 2020-11-28 | 1.8 | 16.2 | 0 | 2019-11-28 | 1.4 | 16.6 | 0 | 2018-11-28 | 0.1 | 17.9 | 0 | 2017-11-28 | -10.4 | 28.4 | 0 | 2016-11-28 | -2.8 | 20.8 | 0 | 20.48 | 0
2025-11-28 | -2.6 | 20.6 | 0 | 2024-11-28 | -1.9 | 19.9 | 0 | 2023-11-28 | -4.4 | 22.4 | 0 | 2022-11-28 | 2.2 | 15.8 | 0 | 2021-11-28 | -9.8 | 27.8 | 0 | 2020-11-28 | 2 | 16 | 0 | 2019-11-28 | 1.5 | 16.5 | 0 | 2018-11-28 | 0.1 | 17.9 | 0 | 2017-11-28 | -9.9 | 27.9 | 0 | 2016-11-28 | -2.2 | 20.2 | 0 | 20.5 | 0
2025-11-28 | -2.9 | 20.9 | 0 | 2024-11-28 | -2 | 20 | 0 | 2023-11-28 | -4.9 | 22.9 | 0 | 2022-11-28 | 2 | 16 | 0 | 2021-11-28 | -10.3 | 28.3 | 0 | 2020-11-28 | 1.8 | 16.2 | 0 | 2019-11-28 | 1.1 | 16.9 | 0 | 2018-11-28 | 0.2 | 17.8 | 0 | 2017-11-28 | -10.1 | 28.1 | 0 | 2016-11-28 | -1.5 | 19.5 | 0 | 20.66 | 0
2025-11-28 | -2.6 | 20.6 | 0 | 2024-11-28 | -1.6 | 19.6 | 0 | 2023-11-28 | -4.8 | 22.8 | 0 | 2022-11-28 | 1.3 | 16.7 | 0 | 2021-11-28 | -9.9 | 27.9 | 0 | 2020-11-28 | 1.7 | 16.3 | 0 | 2019-11-28 | 0.6 | 17.4 | 0 | 2018-11-28 | 0.1 | 17.9 | 0 | 2017-11-28 | -9.7 | 27.7 | 0 | 2016-11-28 | -1.2 | 19.2 | 0 | 20.61 | 0
2025-11-28 | -3.1 | 21.1 | 0 | 2024-11-28 | -1.4 | 19.4 | 0 | 2023-11-28 | -5.8 | 23.8 | 0 | 2022-11-28 | 1 | 17 | 0 | 2021-11-28 | -10.9 | 28.9 | 0 | 2020-11-28 | 1.5 | 16.5 | 0 | 2019-11-28 | -0.1 | 18.1 | 0 | 2018-11-28 | -0.1 | 18.1 | 0 | 2017-11-28 | -9.1 | 27.1 | 0 | 2016-11-28 | -1.4 | 19.4 | 0 | 20.94 | 0
2025-11-28 | -3.1 | 21.1 | 0 | 2024-11-28 | -1.1 | 19.1 | 0 | 2023-11-28 | -5.4 | 23.4 | 0 | 2022-11-28 | 0.5 | 17.5 | 0 | 2021-11-28 | -10.9 | 28.9 | 0 | 2020-11-28 | 2 | 16 | 0 | 2019-11-28 | -0.4 | 18.4 | 0 | 2018-11-28 | -0.7 | 18.7 | 0 | 2017-11-28 | -8.9 | 26.9 | 0 | 2016-11-28 | -1.5 | 19.5 | 0 | 20.95 | 0
2025-11-28 | -2.8 | 20.8 | 0 | 2024-11-28 | -0.6 | 18.6 | 0 | 2023-11-28 | -4.6 | 22.6 | 0 | 2022-11-28 | 0.6 | 17.4 | 0 | 2021-11-28 | -8.9 | 26.9 | 0 | 2020-11-28 | 1.6 | 16.4 | 0 | 2019-11-28 | -0.6 | 18.6 | 0 | 2018-11-28 | 0.7 | 17.3 | 0 | 2017-11-28 | -7.6 | 25.6 | 0 | 2016-11-28 | -1.3 | 19.3 | 0 | 20.35 | 0
2025-11-28 | -2.4 | 20.4 | 0 | 2024-11-28 | 0.5 | 17.5 | 0 | 2023-11-28 | -4 | 22 | 0 | 2022-11-28 | 0.6 | 17.4 | 0 | 2021-11-28 | -7.4 | 25.4 | 0 | 2020-11-28 | 2.5 | 15.5 | 0 | 2019-11-28 | -1.6 | 19.6 | 0 | 2018-11-28 | 1.1 | 16.9 | 0 | 2017-11-28 | -6.1 | 24.1 | 0 | 2016-11-28 | -1.2 | 19.2 | 0 | 19.8 | 0
2025-11-28 | -1.7 | 19.7 | 0 | 2024-11-28 | 1.2 | 16.8 | 0 | 2023-11-28 | -4.6 | 22.6 | 0 | 2022-11-28 | 0.9 | 17.1 | 0 | 2021-11-28 | -5.5 | 23.5 | 0 | 2020-11-28 | 3 | 15 | 0 | 2019-11-28 | -2 | 20 | 0 | 2018-11-28 | 1.5 | 16.5 | 0 | 2017-11-28 | -2.7 | 20.7 | 0 | 2016-11-28 | -1 | 19 | 0 | 19.09 | 0
2025-11-28 | -1.7 | 19.7 | 0 | 2024-11-28 | 1.6 | 16.4 | 0 | 2023-11-28 | -5.1 | 23.1 | 0 | 2022-11-28 | 1.1 | 16.9 | 0 | 2021-11-28 | -5.1 | 23.1 | 0 | 2020-11-28 | 4 | 14 | 0 | 2019-11-28 | -2.2 | 20.2 | 0 | 2018-11-28 | 1.7 | 16.3 | 0 | 2017-11-28 | -0.4 | 18.4 | 0 | 2016-11-28 | -0.3 | 18.3 | 0 | 18.64 | 0
2025-11-28 | -2.4 | 20.4 | 0 | 2024-11-28 | 2 | 16 | 0 | 2023-11-28 | -4.1 | 22.1 | 0 | 2022-11-28 | 0.9 | 17.1 | 0 | 2021-11-28 | -3.3 | 21.3 | 0 | 2020-11-28 | 4.5 | 13.5 | 0 | 2019-11-28 | -2.6 | 20.6 | 0 | 2018-11-28 | 1.8 | 16.2 | 0 | 2017-11-28 | 2 | 16 | 0 | 2016-11-28 | -0.3 | 18.3 | 0 | 18.15 | 0
2025-11-28 | -2.4 | 20.4 | 0 | 2024-11-28 | 2.1 | 15.9 | 0 | 2023-11-28 | -5.2 | 23.2 | 0 | 2022-11-28 | 1 | 17 | 0 | 2021-11-28 | -2.9 | 20.9 | 0 | 2020-11-28 | 3.5 | 14.5 | 0 | 2019-11-28 | -2.9 | 20.9 | 0 | 2018-11-28 | 1.8 | 16.2 | 0 | 2017-11-28 | 3 | 15 | 0 | 2016-11-28 | -0.5 | 18.5 | 0 | 18.25 | 0
2025-11-28 | -2.5 | 20.5 | 0 | 2024-11-28 | 2.1 | 15.9 | 0 | 2023-11-28 | -5.9 | 23.9 | 0 | 2022-11-28 | 0.8 | 17.2 | 0 | 2021-11-28 | -3.1 | 21.1 | 0 | 2020-11-28 | 3.1 | 14.9 | 0 | 2019-11-28 | -2.7 | 20.7 | 0 | 2018-11-28 | 1.8 | 16.2 | 0 | 2017-11-28 | 3.8 | 14.2 | 0 | 2016-11-28 | -1 | 19 | 0 | 18.36 | 0
2025-11-28 | -2.9 | 20.9 | 0 | 2024-11-28 | 1.5 | 16.5 | 0 | 2023-11-28 | -5.3 | 23.3 | 0 | 2022-11-28 | 0.3 | 17.7 | 0 | 2021-11-28 | -3.5 | 21.5 | 0 | 2020-11-28 | 3.4 | 14.6 | 0 | 2019-11-28 | -2.6 | 20.6 | 0 | 2018-11-28 | 1.6 | 16.4 | 0 | 2017-11-28 | 2.2 | 15.8 | 0 | 2016-11-28 | -1.4 | 19.4 | 0 | 18.67 | 0
2025-11-28 | -3.2 | 21.2 | 0 | 2024-11-28 | 0.2 | 17.8 | 0 | 2023-11-28 | -5.3 | 23.3 | 0 | 2022-11-28 | -0.2 | 18.2 | 0 | 2021-11-28 | -4 | 22 | 0 | 2020-11-28 | 3.2 | 14.8 | 0 | 2019-11-28 | -2.5 | 20.5 | 0 | 2018-11-28 | 1.5 | 16.5 | 0 | 2017-11-28 | 1.2 | 16.8 | 0 | 2016-11-28 | -2.1 | 20.1 | 0 | 19.12 | 0
2025-11-28 | -3.2 | 21.2 | 0 | 2024-11-28 | 0.1 | 17.9 | 0 | 2023-11-28 | -6 | 24 | 0 | 2022-11-28 | -0.7 | 18.7 | 0 | 2021-11-28 | -3.9 | 21.9 | 0 | 2020-11-28 | 3.3 | 14.7 | 0 | 2019-11-28 | -2.4 | 20.4 | 0 | 2018-11-28 | 1.3 | 16.7 | 0 | 2017-11-28 | 0.3 | 17.7 | 0 | 2016-11-28 | -2.6 | 20.6 | 0 | 19.38 | 0
2025-11-28 | -3.6 | 21.6 | 0 | 2024-11-28 | 0.2 | 17.8 | 0 | 2023-11-28 | -6 | 24 | 0 | 2022-11-28 | -0.8 | 18.8 | 0 | 2021-11-28 | -4.1 | 22.1 | 0 | 2020-11-28 | 3.3 | 14.7 | 0 | 2019-11-28 | -2.4 | 20.4 | 0 | 2018-11-28 | 1.1 | 16.9 | 0 | 2017-11-28 | 9.2 | 8.8 | 0 | 2016-11-28 | -3 | 21 | 0 | 18.61 | 0
2025-11-28 | -2.8 | 20.8 | 0 | 2024-11-28 | 0.4 | 17.6 | 0 | 2023-11-28 | -5.4 | 23.4 | 0 | 2022-11-28 | -1.1 | 19.1 | 0 | 2021-11-28 | -4 | 22 | 0 | 2020-11-28 | 3 | 15 | 0 | 2019-11-28 | -2.2 | 20.2 | 0 | 2018-11-28 | 1.1 | 16.9 | 0 | 2017-11-28 | 9.7 | 8.3 | 0 | 2016-11-28 | -3 | 21 | 0 | 18.43 | 0
2025-11-28 | -2.4 | 20.4 | 0 | 2024-11-28 | 0.2 | 17.8 | 0 | 2023-11-28 | -5.8 | 23.8 | 0 | 2022-11-28 | -1.1 | 19.1 | 0 | 2021-11-28 | -4 | 22 | 0 | 2020-11-28 | 2.8 | 15.2 | 0 | 2019-11-28 | -2.4 | 20.4 | 0 | 2018-11-28 | 0.9 | 17.1 | 0 | 2017-11-28 | 10.1 | 7.9 | 0 | 2016-11-28 | -2.4 | 20.4 | 0 | 18.41 | 0
2025-11-28 | -2.4 | 20.4 | 0 | 2024-11-28 | -1.4 | 19.4 | 0 | 2023-11-28 | -6.1 | 24.1 | 0 | 2022-11-28 | -1.3 | 19.3 | 0 | 2021-11-28 | -4.6 | 22.6 | 0 | 2020-11-28 | 3 | 15 | 0 | 2019-11-28 | -2.6 | 20.6 | 0 | 2018-11-28 | 0.5 | 17.5 | 0 | 2017-11-28 | 10.1 | 7.9 | 0 | 2016-11-28 | -2.3 | 20.3 | 0 | 18.71 | 0
2025-11-28 | -2.2 | 20.2 | 0 | 2024-11-28 | -1.9 | 19.9 | 0 | 2023-11-28 | -6.7 | 24.7 | 0 | 2022-11-28 | -1.6 | 19.6 | 0 | 2021-11-28 | -4.7 | 22.7 | 0 | 2020-11-28 | 2.9 | 15.1 | 0 | 2019-11-28 | -2.9 | 20.9 | 0 | 2018-11-28 | 0.5 | 17.5 | 0 | 2017-11-28 | 10.2 | 7.8 | 0 | 2016-11-28 | -2.2 | 20.2 | 0 | 18.86 | 0
2025-11-29 | -2.5 | 20.5 | 0 | 2024-11-29 | -1.9 | 19.9 | 0 | 2023-11-29 | -8.1 | 26.1 | 0 | 2022-11-29 | -1.8 | 19.8 | 0 | 2021-11-29 | -5 | 23 | 0 | 2020-11-29 | 2.7 | 15.3 | 0 | 2019-11-29 | -2.9 | 20.9 | 0 | 2018-11-29 | 0.5 | 17.5 | 0 | 2017-11-29 | 10.8 | 7.2 | 0 | 2016-11-29 | -2.1 | 20.1 | 0 | 19.03 | 0
2025-11-29 | -2.6 | 20.6 | 0 | 2024-11-29 | -3.3 | 21.3 | 0 | 2023-11-29 | -8.8 | 26.8 | 0 | 2022-11-29 | -1.8 | 19.8 | 0 | 2021-11-29 | -5.7 | 23.7 | 0 | 2020-11-29 | 2.3 | 15.7 | 0 | 2019-11-29 | -3.3 | 21.3 | 0 | 2018-11-29 | 0.4 | 17.6 | 0 | 2017-11-29 | 9.3 | 8.7 | 0 | 2016-11-29 | -2 | 20 | 0 | 19.55 | 0
2025-11-29 | -3 | 21 | 0 | 2024-11-29 | -3 | 21 | 0 | 2023-11-29 | -8.2 | 26.2 | 0 | 2022-11-29 | -1.9 | 19.9 | 0 | 2021-11-29 | -5.9 | 23.9 | 0 | 2020-11-29 | 2 | 16 | 0 | 2019-11-29 | -3.4 | 21.4 | 0 | 2018-11-29 | 0.3 | 17.7 | 0 | 2017-11-29 | 6.6 | 11.4 | 0 | 2016-11-29 | -1.9 | 19.9 | 0 | 19.84 | 0
2025-11-29 | -3.3 | 21.3 | 0 | 2024-11-29 | -3.3 | 21.3 | 0 | 2023-11-29 | -7.2 | 25.2 | 0 | 2022-11-29 | -1.8 | 19.8 | 0 | 2021-11-29 | -6.5 | 24.5 | 0 | 2020-11-29 | 2.1 | 15.9 | 0 | 2019-11-29 | -3.4 | 21.4 | 0 | 2018-11-29 | 0.2 | 17.8 | 0 | 2017-11-29 | 5.3 | 12.7 | 0 | 2016-11-29 | -1.8 | 19.8 | 0 | 19.97 | 0
2025-11-29 | -3.5 | 21.5 | 0 | 2024-11-29 | -3.2 | 21.2 | 0 | 2023-11-29 | -7.1 | 25.1 | 0 | 2022-11-29 | -2 | 20 | 0 | 2021-11-29 | -6.5 | 24.5 | 0 | 2020-11-29 | 2.2 | 15.8 | 0 | 2019-11-29 | -3.7 | 21.7 | 0 | 2018-11-29 | 0.1 | 17.9 | 0 | 2017-11-29 | 5.5 | 12.5 | 0 | 2016-11-29 | -1.5 | 19.5 | 0 | 19.97 | 0
2025-11-29 | -3.9 | 21.9 | 0 | 2024-11-29 | -2.9 | 20.9 | 0 | 2023-11-29 | -6.8 | 24.8 | 0 | 2022-11-29 | -1.7 | 19.7 | 0 | 2021-11-29 | -7.2 | 25.2 | 0 | 2020-11-29 | 2.1 | 15.9 | 0 | 2019-11-29 | -4.3 | 22.3 | 0 | 2018-11-29 | -0.1 | 18.1 | 0 | 2017-11-29 | 1.6 | 16.4 | 0 | 2016-11-29 | -1.4 | 19.4 | 0 | 20.46 | 0
2025-11-29 | -4.2 | 22.2 | 0 | 2024-11-29 | -2.9 | 20.9 | 0 | 2023-11-29 | -6.6 | 24.6 | 0 | 2022-11-29 | -1.9 | 19.9 | 0 | 2021-11-29 | -8.6 | 26.6 | 0 | 2020-11-29 | 1.5 | 16.5 | 0 | 2019-11-29 | -5.1 | 23.1 | 0 | 2018-11-29 | -0.2 | 18.2 | 0 | 2017-11-29 | 2.4 | 15.6 | 0 | 2016-11-29 | -1.1 | 19.1 | 0 | 20.67 | 0
2025-11-29 | -4.2 | 22.2 | 0 | 2024-11-29 | -2.5 | 20.5 | 0 | 2023-11-29 | -6.7 | 24.7 | 0 | 2022-11-29 | -1.6 | 19.6 | 0 | 2021-11-29 | -7.5 | 25.5 | 0 | 2020-11-29 | 1.1 | 16.9 | 0 | 2019-11-29 | -5.8 | 23.8 | 0 | 2018-11-29 | -0.1 | 18.1 | 0 | 2017-11-29 | 2.9 | 15.1 | 0 | 2016-11-29 | -1.1 | 19.1 | 0 | 20.55 | 0
2025-11-29 | -3.9 | 21.9 | 0 | 2024-11-29 | -1.3 | 19.3 | 0 | 2023-11-29 | -6 | 24 | 0 | 2022-11-29 | -1.7 | 19.7 | 0 | 2021-11-29 | -7.2 | 25.2 | 0 | 2020-11-29 | 1 | 17 | 0 | 2019-11-29 | -6.4 | 24.4 | 0 | 2018-11-29 | 0 | 18 | 0 | 2017-11-29 | 4.3 | 13.7 | 0 | 2016-11-29 | -1.1 | 19.1 | 0 | 20.23 | 0
2025-11-29 | -3.6 | 21.6 | 0 | 2024-11-29 | -0.6 | 18.6 | 0 | 2023-11-29 | -5.2 | 23.2 | 0 | 2022-11-29 | -1.3 | 19.3 | 0 | 2021-11-29 | -5.6 | 23.6 | 0 | 2020-11-29 | 2.1 | 15.9 | 0 | 2019-11-29 | -5.9 | 23.9 | 0 | 2018-11-29 | 0.3 | 17.7 | 0 | 2017-11-29 | 4.3 | 13.7 | 0 | 2016-11-29 | -0.6 | 18.6 | 0 | 19.61 | 0
2025-11-29 | -2.4 | 20.4 | 0 | 2024-11-29 | 0 | 18 | 0 | 2023-11-29 | -4.2 | 22.2 | 0 | 2022-11-29 | -1.1 | 19.1 | 0 | 2021-11-29 | -4.5 | 22.5 | 0 | 2020-11-29 | 3.5 | 14.5 | 0 | 2019-11-29 | -5.8 | 23.8 | 0 | 2018-11-29 | 0.4 | 17.6 | 0 | 2017-11-29 | 2.8 | 15.2 | 0 | 2016-11-29 | -0.3 | 18.3 | 0 | 19.16 | 0
2025-11-29 | -1.6 | 19.6 | 0 | 2024-11-29 | 0.7 | 17.3 | 0 | 2023-11-29 | -3.4 | 21.4 | 0 | 2022-11-29 | -0.4 | 18.4 | 0 | 2021-11-29 | -3.2 | 21.2 | 0 | 2020-11-29 | 4.4 | 13.6 | 0 | 2019-11-29 | -5.5 | 23.5 | 0 | 2018-11-29 | 1.1 | 16.9 | 0 | 2017-11-29 | 3.2 | 14.8 | 0 | 2016-11-29 | 0 | 18 | 0 | 18.47 | 0
2025-11-29 | -1.8 | 19.8 | 0 | 2024-11-29 | 1.5 | 16.5 | 0 | 2023-11-29 | -1.3 | 19.3 | 0 | 2022-11-29 | -0.3 | 18.3 | 0 | 2021-11-29 | -3 | 21 | 0 | 2020-11-29 | 5.2 | 12.8 | 0 | 2019-11-29 | -4.8 | 22.8 | 0 | 2018-11-29 | 1.2 | 16.8 | 0 | 2017-11-29 | 3.9 | 14.1 | 0 | 2016-11-29 | 0.2 | 17.8 | 0 | 17.92 | 0
2025-11-29 | -1.2 | 19.2 | 0 | 2024-11-29 | 3.2 | 14.8 | 0 | 2023-11-29 | 0.6 | 17.4 | 0 | 2022-11-29 | 0 | 18 | 0 | 2021-11-29 | -2.6 | 20.6 | 0 | 2020-11-29 | 6.7 | 11.3 | 0 | 2019-11-29 | -4.4 | 22.4 | 0 | 2018-11-29 | 1.2 | 16.8 | 0 | 2017-11-29 | 2.9 | 15.1 | 0 | 2016-11-29 | 0.3 | 17.7 | 0 | 17.33 | 0
2025-11-29 | -1.2 | 19.2 | 0 | 2024-11-29 | 2.9 | 15.1 | 0 | 2023-11-29 | 0.5 | 17.5 | 0 | 2022-11-29 | 0.6 | 17.4 | 0 | 2021-11-29 | -1.9 | 19.9 | 0 | 2020-11-29 | 7.1 | 10.9 | 0 | 2019-11-29 | -4.1 | 22.1 | 0 | 2018-11-29 | 1.9 | 16.1 | 0 | 2017-11-29 | 2.1 | 15.9 | 0 | 2016-11-29 | 0.6 | 17.4 | 0 | 17.15 | 0
2025-11-29 | -1.2 | 19.2 | 0 | 2024-11-29 | 2.9 | 15.1 | 0 | 2023-11-29 | 0.1 | 17.9 | 0 | 2022-11-29 | 0.8 | 17.2 | 0 | 2021-11-29 | -1.8 | 19.8 | 0 | 2020-11-29 | 7.6 | 10.4 | 0 | 2019-11-29 | -4.4 | 22.4 | 0 | 2018-11-29 | 1.1 | 16.9 | 0 | 2017-11-29 | 1.7 | 16.3 | 0 | 2016-11-29 | 0.7 | 17.3 | 0 | 17.25 | 0
2025-11-29 | -2.2 | 20.2 | 0 | 2024-11-29 | 2.2 | 15.8 | 0 | 2023-11-29 | -0.6 | 18.6 | 0 | 2022-11-29 | -0.6 | 18.6 | 0 | 2021-11-29 | -2.3 | 20.3 | 0 | 2020-11-29 | 6 | 12 | 0 | 2019-11-29 | -5.6 | 23.6 | 0 | 2018-11-29 | 0.9 | 17.1 | 0 | 2017-11-29 | 0.7 | 17.3 | 0 | 2016-11-29 | 0.7 | 17.3 | 0 | 18.08 | 0
2025-11-29 | -3.1 | 21.1 | 0 | 2024-11-29 | 1.1 | 16.9 | 0 | 2023-11-29 | -0.9 | 18.9 | 0 | 2022-11-29 | -1.2 | 19.2 | 0 | 2021-11-29 | -3.4 | 21.4 | 0 | 2020-11-29 | 4.1 | 13.9 | 0 | 2019-11-29 | -6.6 | 24.6 | 0 | 2018-11-29 | 0.6 | 17.4 | 0 | 2017-11-29 | -1.6 | 19.6 | 0 | 2016-11-29 | 0.6 | 17.4 | 0 | 19.04 | 0
2025-11-29 | -4.6 | 22.6 | 0 | 2024-11-29 | 0.7 | 17.3 | 0 | 2023-11-29 | -0.8 | 18.8 | 0 | 2022-11-29 | -1.4 | 19.4 | 0 | 2021-11-29 | -3 | 21 | 0 | 2020-11-29 | 3.8 | 14.2 | 0 | 2019-11-29 | -7.3 | 25.3 | 0 | 2018-11-29 | 0.5 | 17.5 | 0 | 2017-11-29 | -2.6 | 20.6 | 0 | 2016-11-29 | 0.6 | 17.4 | 0 | 19.41 | 0
2025-11-29 | -6.4 | 24.4 | 0 | 2024-11-29 | 0.4 | 17.6 | 0 | 2023-11-29 | -1 | 19 | 0 | 2022-11-29 | -1.5 | 19.5 | 0 | 2021-11-29 | -2.9 | 20.9 | 0 | 2020-11-29 | 3.3 | 14.7 | 0 | 2019-11-29 | -7.6 | 25.6 | 0 | 2018-11-29 | 0.3 | 17.7 | 0 | 2017-11-29 | -3.3 | 21.3 | 0 | 2016-11-29 | 0.6 | 17.4 | 0 | 19.81 | 0
2025-11-29 | -5.1 | 23.1 | 0 | 2024-11-29 | -0.1 | 18.1 | 0 | 2023-11-29 | -1.1 | 19.1 | 0 | 2022-11-29 | -1.8 | 19.8 | 0 | 2021-11-29 | -3.2 | 21.2 | 0 | 2020-11-29 | 2.1 | 15.9 | 0 | 2019-11-29 | -7.6 | 25.6 | 0 | 2018-11-29 | 0 | 18 | 0 | 2017-11-29 | -2.7 | 20.7 | 0 | 2016-11-29 | 0.7 | 17.3 | 0 | 19.88 | 0
2025-11-29 | -6 | 24 | 0 | 2024-11-29 | 0 | 18 | 0 | 2023-11-29 | -1.1 | 19.1 | 0 | 2022-11-29 | -1.7 | 19.7 | 0 | 2021-11-29 | -3.2 | 21.2 | 0 | 2020-11-29 | 1.5 | 16.5 | 0 | 2019-11-29 | -7.7 | 25.7 | 0 | 2018-11-29 | -0.1 | 18.1 | 0 | 2017-11-29 | -5.3 | 23.3 | 0 | 2016-11-29 | 0.7 | 17.3 | 0 | 20.29 | 0
2025-11-29 | -5.1 | 23.1 | 0 | 2024-11-29 | -0.2 | 18.2 | 0 | 2023-11-29 | -1 | 19 | 0 | 2022-11-29 | -1.9 | 19.9 | 0 | 2021-11-29 | -3.4 | 21.4 | 0 | 2020-11-29 | 2.1 | 15.9 | 0 | 2019-11-29 | -8 | 26 | 0 | 2018-11-29 | -0.2 | 18.2 | 0 | 2017-11-29 | -5.5 | 23.5 | 0 | 2016-11-29 | 0.7 | 17.3 | 0 | 20.25 | 0
2025-11-29 | -6.1 | 24.1 | 0 | 2024-11-29 | -0.6 | 18.6 | 0 | 2023-11-29 | -0.8 | 18.8 | 0 | 2022-11-29 | -2.2 | 20.2 | 0 | 2021-11-29 | -4.3 | 22.3 | 0 | 2020-11-29 | 2.6 | 15.4 | 0 | 2019-11-29 | -8.4 | 26.4 | 0 | 2018-11-29 | -0.2 | 18.2 | 0 | 2017-11-29 | -4.9 | 22.9 | 0 | 2016-11-29 | 0.6 | 17.4 | 0 | 20.43 | 0
2025-11-30 | -4.6 | 22.6 | 0 | 2024-11-30 | -1.4 | 19.4 | 0 | 2023-11-30 | -0.7 | 18.7 | 0 | 2022-11-30 | -1.5 | 19.5 | 0 | 2021-11-30 | -4.3 | 22.3 | 0 | 2020-11-30 | 2.6 | 15.4 | 0 | 2019-11-30 | -8.8 | 26.8 | 0 | 2018-11-30 | -0.4 | 18.4 | 0 | 2017-11-30 | -7 | 25 | 0 | 2016-11-30 | 0.7 | 17.3 | 0 | 20.54 | 0
2025-11-30 | -4.3 | 22.3 | 0 | 2024-11-30 | -1.6 | 19.6 | 0 | 2023-11-30 | -1.9 | 19.9 | 0 | 2022-11-30 | -0.8 | 18.8 | 0 | 2021-11-30 | -4.3 | 22.3 | 0 | 2020-11-30 | 1.8 | 16.2 | 0 | 2019-11-30 | -8.6 | 26.6 | 0 | 2018-11-30 | -0.8 | 18.8 | 0 | 2017-11-30 | -7.3 | 25.3 | 0 | 2016-11-30 | 0.9 | 17.1 | 0 | 20.69 | 0
2025-11-30 | -4.1 | 22.1 | 0 | 2024-11-30 | -1.3 | 19.3 | 0 | 2023-11-30 | -1.6 | 19.6 | 0 | 2022-11-30 | -0.7 | 18.7 | 0 | 2021-11-30 | -4.3 | 22.3 | 0 | 2020-11-30 | 0.6 | 17.4 | 0 | 2019-11-30 | -8.7 | 26.7 | 0 | 2018-11-30 | -0.8 | 18.8 | 0 | 2017-11-30 | -6.1 | 24.1 | 0 | 2016-11-30 | 0.8 | 17.2 | 0 | 20.62 | 0
2025-11-30 | -3.9 | 21.9 | 0 | 2024-11-30 | -1.8 | 19.8 | 0 | 2023-11-30 | -1.8 | 19.8 | 0 | 2022-11-30 | -0.8 | 18.8 | 0 | 2021-11-30 | -4.7 | 22.7 | 0 | 2020-11-30 | 0.8 | 17.2 | 0 | 2019-11-30 | -8.8 | 26.8 | 0 | 2018-11-30 | -0.9 | 18.9 | 0 | 2017-11-30 | -5.5 | 23.5 | 0 | 2016-11-30 | 0.9 | 17.1 | 0 | 20.65 | 0
2025-11-30 | -3.9 | 21.9 | 0 | 2024-11-30 | -1.6 | 19.6 | 0 | 2023-11-30 | -0.5 | 18.5 | 0 | 2022-11-30 | -0.7 | 18.7 | 0 | 2021-11-30 | -5.6 | 23.6 | 0 | 2020-11-30 | 0.7 | 17.3 | 0 | 2019-11-30 | -9.4 | 27.4 | 0 | 2018-11-30 | -0.9 | 18.9 | 0 | 2017-11-30 | -6.6 | 24.6 | 0 | 2016-11-30 | 0.8 | 17.2 | 0 | 20.77 | 0
2025-11-30 | -4 | 22 | 0 | 2024-11-30 | -1.6 | 19.6 | 0 | 2023-11-30 | 0 | 18 | 0 | 2022-11-30 | -0.3 | 18.3 | 0 | 2021-11-30 | -6.5 | 24.5 | 0 | 2020-11-30 | 0.4 | 17.6 | 0 | 2019-11-30 | -9.7 | 27.7 | 0 | 2018-11-30 | -0.9 | 18.9 | 0 | 2017-11-30 | -6.4 | 24.4 | 0 | 2016-11-30 | 0.7 | 17.3 | 0 | 20.83 | 0
2025-11-30 | -4 | 22 | 0 | 2024-11-30 | -1.8 | 19.8 | 0 | 2023-11-30 | 0.4 | 17.6 | 0 | 2022-11-30 | 0.1 | 17.9 | 0 | 2021-11-30 | -6.4 | 24.4 | 0 | 2020-11-30 | -0.2 | 18.2 | 0 | 2019-11-30 | -10.7 | 28.7 | 0 | 2018-11-30 | -1.1 | 19.1 | 0 | 2017-11-30 | -7 | 25 | 0 | 2016-11-30 | 0.7 | 17.3 | 0 | 21 | 0
2025-11-30 | -3.8 | 21.8 | 0 | 2024-11-30 | -1.6 | 19.6 | 0 | 2023-11-30 | 0.9 | 17.1 | 0 | 2022-11-30 | 0.5 | 17.5 | 0 | 2021-11-30 | -6.4 | 24.4 | 0 | 2020-11-30 | 0 | 18 | 0 | 2019-11-30 | -10.8 | 28.8 | 0 | 2018-11-30 | -1.4 | 19.4 | 0 | 2017-11-30 | -6.2 | 24.2 | 0 | 2016-11-30 | 0.8 | 17.2 | 0 | 20.8 | 0
2025-11-30 | -3.6 | 21.6 | 0 | 2024-11-30 | -1.2 | 19.2 | 0 | 2023-11-30 | 1.1 | 16.9 | 0 | 2022-11-30 | 0.7 | 17.3 | 0 | 2021-11-30 | -7.5 | 25.5 | 0 | 2020-11-30 | 0.3 | 17.7 | 0 | 2019-11-30 | -10.7 | 28.7 | 0 | 2018-11-30 | -1.4 | 19.4 | 0 | 2017-11-30 | -5.2 | 23.2 | 0 | 2016-11-30 | 0.8 | 17.2 | 0 | 20.67 | 0
2025-11-30 | -3.5 | 21.5 | 0 | 2024-11-30 | -0.9 | 18.9 | 0 | 2023-11-30 | 2 | 16 | 0 | 2022-11-30 | 0.7 | 17.3 | 0 | 2021-11-30 | -4.3 | 22.3 | 0 | 2020-11-30 | 0.8 | 17.2 | 0 | 2019-11-30 | -9.8 | 27.8 | 0 | 2018-11-30 | -1.5 | 19.5 | 0 | 2017-11-30 | -3.4 | 21.4 | 0 | 2016-11-30 | 1.1 | 16.9 | 0 | 19.88 | 0
2025-11-30 | -2.8 | 20.8 | 0 | 2024-11-30 | 0.6 | 17.4 | 0 | 2023-11-30 | 3.2 | 14.8 | 0 | 2022-11-30 | 1.2 | 16.8 | 0 | 2021-11-30 | -4.3 | 22.3 | 0 | 2020-11-30 | 1.3 | 16.7 | 0 | 2019-11-30 | -9 | 27 | 0 | 2018-11-30 | -1.3 | 19.3 | 0 | 2017-11-30 | -1.1 | 19.1 | 0 | 2016-11-30 | 1.4 | 16.6 | 0 | 19.08 | 0
2025-11-30 | -2.2 | 20.2 | 0 | 2024-11-30 | 1.2 | 16.8 | 0 | 2023-11-30 | 3.4 | 14.6 | 0 | 2022-11-30 | 1.8 | 16.2 | 0 | 2021-11-30 | -3 | 21 | 0 | 2020-11-30 | 1.7 | 16.3 | 0 | 2019-11-30 | -8.1 | 26.1 | 0 | 2018-11-30 | -1.1 | 19.1 | 0 | 2017-11-30 | 0.7 | 17.3 | 0 | 2016-11-30 | 1.6 | 16.4 | 0 | 18.4 | 0
2025-11-30 | -1.7 | 19.7 | 0 | 2024-11-30 | 1.9 | 16.1 | 0 | 2023-11-30 | 4.4 | 13.6 | 0 | 2022-11-30 | 1.9 | 16.1 | 0 | 2021-11-30 | -2.1 | 20.1 | 0 | 2020-11-30 | 2.4 | 15.6 | 0 | 2019-11-30 | -6.5 | 24.5 | 0 | 2018-11-30 | -1.3 | 19.3 | 0 | 2017-11-30 | 1.8 | 16.2 | 0 | 2016-11-30 | 1.9 | 16.1 | 0 | 17.73 | 0
2025-11-30 | -1.1 | 19.1 | 0 | 2024-11-30 | 2.1 | 15.9 | 0 | 2023-11-30 | 5.8 | 12.2 | 0 | 2022-11-30 | 3 | 15 | 0 | 2021-11-30 | -1.3 | 19.3 | 0 | 2020-11-30 | 2.7 | 15.3 | 0 | 2019-11-30 | -5 | 23 | 0 | 2018-11-30 | -0.9 | 18.9 | 0 | 2017-11-30 | 2.1 | 15.9 | 0 | 2016-11-30 | 2.1 | 15.9 | 0 | 17.05 | 0
2025-11-30 | -0.6 | 18.6 | 0 | 2024-11-30 | 2.4 | 15.6 | 0 | 2023-11-30 | 5.4 | 12.6 | 0 | 2022-11-30 | 5.9 | 12.1 | 0 | 2021-11-30 | -1.2 | 19.2 | 0 | 2020-11-30 | 2.4 | 15.6 | 0 | 2019-11-30 | -4.1 | 22.1 | 0 | 2018-11-30 | -0.6 | 18.6 | 0 | 2017-11-30 | 2 | 16 | 0 | 2016-11-30 | 2.4 | 15.6 | 0 | 16.6 | 0
2025-11-30 | -0.2 | 18.2 | 0 | 2024-11-30 | 1.8 | 16.2 | 0 | 2023-11-30 | 5.3 | 12.7 | 0 | 2022-11-30 | 6.9 | 11.1 | 0 | 2021-11-30 | -1.2 | 19.2 | 0 | 2020-11-30 | 2.5 | 15.5 | 0 | 2019-11-30 | -4.8 | 22.8 | 0 | 2018-11-30 | -0.5 | 18.5 | 0 | 2017-11-30 | 1.3 | 16.7 | 0 | 2016-11-30 | 2.4 | 15.6 | 0 | 16.65 | 0
2025-11-30 | 0.2 | 17.8 | 0 | 2024-11-30 | 1.4 | 16.6 | 0 | 2023-11-30 | 4.5 | 13.5 | 0 | 2022-11-30 | 7.3 | 10.7 | 0 | 2021-11-30 | -1.3 | 19.3 | 0 | 2020-11-30 | 2.9 | 15.1 | 0 | 2019-11-30 | -6.2 | 24.2 | 0 | 2018-11-30 | -0.5 | 18.5 | 0 | 2017-11-30 | 0.6 | 17.4 | 0 | 2016-11-30 | 2.7 | 15.3 | 0 | 16.84 | 0
2025-11-30 | 0.3 | 17.7 | 0 | 2024-11-30 | -0.4 | 18.4 | 0 | 2023-11-30 | 4.5 | 13.5 | 0 | 2022-11-30 | 4.2 | 13.8 | 0 | 2021-11-30 | -1.7 | 19.7 | 0 | 2020-11-30 | 3.3 | 14.7 | 0 | 2019-11-30 | -7.7 | 25.7 | 0 | 2018-11-30 | -0.6 | 18.6 | 0 | 2017-11-30 | 0 | 18 | 0 | 2016-11-30 | 3 | 15 | 0 | 17.51 | 0
2025-11-30 | 0.9 | 17.1 | 0 | 2024-11-30 | -0.7 | 18.7 | 0 | 2023-11-30 | 4.3 | 13.7 | 0 | 2022-11-30 | 3.6 | 14.4 | 0 | 2021-11-30 | -2 | 20 | 0 | 2020-11-30 | 3.2 | 14.8 | 0 | 2019-11-30 | -8.6 | 26.6 | 0 | 2018-11-30 | -0.9 | 18.9 | 0 | 2017-11-30 | 1.4 | 16.6 | 0 | 2016-11-30 | 3.2 | 14.8 | 0 | 17.56 | 0
2025-11-30 | 1.3 | 16.7 | 0 | 2024-11-30 | -0.8 | 18.8 | 0 | 2023-11-30 | 3.9 | 14.1 | 0 | 2022-11-30 | 2.8 | 15.2 | 0 | 2021-11-30 | -2.4 | 20.4 | 0 | 2020-11-30 | 3.6 | 14.4 | 0 | 2019-11-30 | -8.8 | 26.8 | 0 | 2018-11-30 | -0.6 | 18.6 | 0 | 2017-11-30 | 1.4 | 16.6 | 0 | 2016-11-30 | 3.4 | 14.6 | 0 | 17.62 | 0
2025-11-30 | 1.6 | 16.4 | 0 | 2024-11-30 | -0.9 | 18.9 | 0 | 2023-11-30 | 4.8 | 13.2 | 0 | 2022-11-30 | 1.6 | 16.4 | 0 | 2021-11-30 | -2.6 | 20.6 | 0 | 2020-11-30 | 3.8 | 14.2 | 0 | 2019-11-30 | -9.3 | 27.3 | 0 | 2018-11-30 | -0.7 | 18.7 | 0 | 2017-11-30 | 3.7 | 14.3 | 0 | 2016-11-30 | 3.5 | 14.5 | 0 | 17.45 | 0
2025-11-30 | 1.6 | 16.4 | 0 | 2024-11-30 | -1.3 | 19.3 | 0 | 2023-11-30 | 3.7 | 14.3 | 0 | 2022-11-30 | 0.9 | 17.1 | 0 | 2021-11-30 | -3 | 21 | 0 | 2020-11-30 | 4 | 14 | 0 | 2019-11-30 | -9.6 | 27.6 | 0 | 2018-11-30 | -0.3 | 18.3 | 0 | 2017-11-30 | 4.2 | 13.8 | 0 | 2016-11-30 | 3.7 | 14.3 | 0 | 17.61 | 0
2025-11-30 | 1.2 | 16.8 | 0 | 2024-11-30 | -1.7 | 19.7 | 0 | 2023-11-30 | 4.3 | 13.7 | 0 | 2022-11-30 | 0.4 | 17.6 | 0 | 2021-11-30 | -2.6 | 20.6 | 0 | 2020-11-30 | 4.3 | 13.7 | 0 | 2019-11-30 | -10.5 | 28.5 | 0 | 2018-11-30 | -0.4 | 18.4 | 0 | 2017-11-30 | 4.1 | 13.9 | 0 | 2016-11-30 | 4.3 | 13.7 | 0 | 17.66 | 0
2025-11-30 | 0 | 18 | 0 | 2024-11-30 | -1.2 | 19.2 | 0 | 2023-11-30 | 4.5 | 13.5 | 0 | 2022-11-30 | -0.3 | 18.3 | 0 | 2021-11-30 | -2.6 | 20.6 | 0 | 2020-11-30 | 3.7 | 14.3 | 0 | 2019-11-30 | -10.7 | 28.7 | 0 | 2018-11-30 | -0.6 | 18.6 | 0 | 2017-11-30 | 4 | 14 | 0 | 2016-11-30 | 4.9 | 13.1 | 0 | 17.83 | 0
2025-12-01 | -0.9 | 18.9 | 0 | 2024-12-01 | -1.4 | 19.4 | 0 | 2023-12-01 | 5.1 | 12.9 | 0 | 2022-12-01 | -0.6 | 18.6 | 0 | 2021-12-01 | -2.5 | 20.5 | 0 | 2020-12-01 | 3.4 | 14.6 | 0 | 2019-12-01 | -10.5 | 28.5 | 0 | 2018-12-01 | -0.8 | 18.8 | 0 | 2017-12-01 | 3.9 | 14.1 | 0 | 2016-12-01 | 5.8 | 12.2 | 0 | 17.85 | 0
2025-12-01 | -1.9 | 19.9 | 0 | 2024-12-01 | -2 | 20 | 0 | 2023-12-01 | 5.1 | 12.9 | 0 | 2022-12-01 | -1.1 | 19.1 | 0 | 2021-12-01 | -2.2 | 20.2 | 0 | 2020-12-01 | 3.1 | 14.9 | 0 | 2019-12-01 | -11.6 | 29.6 | 0 | 2018-12-01 | -0.7 | 18.7 | 0 | 2017-12-01 | 3.6 | 14.4 | 0 | 2016-12-01 | 6.2 | 11.8 | 0 | 18.15 | 0
2025-12-01 | -3.1 | 21.1 | 0 | 2024-12-01 | -2.6 | 20.6 | 0 | 2023-12-01 | 5.5 | 12.5 | 0 | 2022-12-01 | -1.2 | 19.2 | 0 | 2021-12-01 | -1.2 | 19.2 | 0 | 2020-12-01 | 3.1 | 14.9 | 0 | 2019-12-01 | -12.3 | 30.3 | 0 | 2018-12-01 | -1.2 | 19.2 | 0 | 2017-12-01 | 3.5 | 14.5 | 0 | 2016-12-01 | 5.5 | 12.5 | 0 | 18.4 | 0
2025-12-01 | -4 | 22 | 0 | 2024-12-01 | -2.7 | 20.7 | 0 | 2023-12-01 | 5.8 | 12.2 | 0 | 2022-12-01 | -1.3 | 19.3 | 0 | 2021-12-01 | -0.6 | 18.6 | 0 | 2020-12-01 | 3.1 | 14.9 | 0 | 2019-12-01 | -12.1 | 30.1 | 0 | 2018-12-01 | -1.4 | 19.4 | 0 | 2017-12-01 | 3.2 | 14.8 | 0 | 2016-12-01 | 6.8 | 11.2 | 0 | 18.32 | 0
2025-12-01 | -6.4 | 24.4 | 0 | 2024-12-01 | -3.2 | 21.2 | 0 | 2023-12-01 | 5.4 | 12.6 | 0 | 2022-12-01 | -0.8 | 18.8 | 0 | 2021-12-01 | 0.3 | 17.7 | 0 | 2020-12-01 | 3.3 | 14.7 | 0 | 2019-12-01 | -13.1 | 31.1 | 0 | 2018-12-01 | -2.7 | 20.7 | 0 | 2017-12-01 | 3.3 | 14.7 | 0 | 2016-12-01 | 6.7 | 11.3 | 0 | 18.72 | 0
2025-12-01 | -7.6 | 25.6 | 0 | 2024-12-01 | -3.8 | 21.8 | 0 | 2023-12-01 | 4.7 | 13.3 | 0 | 2022-12-01 | -0.7 | 18.7 | 0 | 2021-12-01 | -0.4 | 18.4 | 0 | 2020-12-01 | 3.1 | 14.9 | 0 | 2019-12-01 | -12.6 | 30.6 | 0 | 2018-12-01 | -2.2 | 20.2 | 0 | 2017-12-01 | 2.6 | 15.4 | 0 | 2016-12-01 | 6.1 | 11.9 | 0 | 19.08 | 0
2025-12-01 | -8.9 | 26.9 | 0 | 2024-12-01 | -3.9 | 21.9 | 0 | 2023-12-01 | 4 | 14 | 0 | 2022-12-01 | -1.2 | 19.2 | 0 | 2021-12-01 | -1.7 | 19.7 | 0 | 2020-12-01 | 3.4 | 14.6 | 0 | 2019-12-01 | -12.7 | 30.7 | 0 | 2018-12-01 | -3.3 | 21.3 | 0 | 2017-12-01 | 2.4 | 15.6 | 0 | 2016-12-01 | 6.8 | 11.2 | 0 | 19.51 | 0
2025-12-01 | -9 | 27 | 0 | 2024-12-01 | -3.9 | 21.9 | 0 | 2023-12-01 | 4.4 | 13.6 | 0 | 2022-12-01 | -1.4 | 19.4 | 0 | 2021-12-01 | -2.6 | 20.6 | 0 | 2020-12-01 | 3.5 | 14.5 | 0 | 2019-12-01 | -12.8 | 30.8 | 0 | 2018-12-01 | -4 | 22 | 0 | 2017-12-01 | 2.1 | 15.9 | 0 | 2016-12-01 | 6.5 | 11.5 | 0 | 19.72 | 0
2025-12-01 | -9.5 | 27.5 | 0 | 2024-12-01 | -3.7 | 21.7 | 0 | 2023-12-01 | 3.9 | 14.1 | 0 | 2022-12-01 | -1 | 19 | 0 | 2021-12-01 | -3.3 | 21.3 | 0 | 2020-12-01 | 3.6 | 14.4 | 0 | 2019-12-01 | -12.3 | 30.3 | 0 | 2018-12-01 | -3.5 | 21.5 | 0 | 2017-12-01 | 1.9 | 16.1 | 0 | 2016-12-01 | 6.5 | 11.5 | 0 | 19.74 | 0
2025-12-01 | -9.5 | 27.5 | 0 | 2024-12-01 | -3.1 | 21.1 | 0 | 2023-12-01 | 5.7 | 12.3 | 0 | 2022-12-01 | -0.9 | 18.9 | 0 | 2021-12-01 | -3.7 | 21.7 | 0 | 2020-12-01 | 4.1 | 13.9 | 0 | 2019-12-01 | -11 | 29 | 0 | 2018-12-01 | -2.5 | 20.5 | 0 | 2017-12-01 | 2.1 | 15.9 | 0 | 2016-12-01 | 6.9 | 11.1 | 0 | 19.19 | 0
2025-12-01 | -9.5 | 27.5 | 0 | 2024-12-01 | -2 | 20 | 0 | 2023-12-01 | 7.1 | 10.9 | 0 | 2022-12-01 | -0.1 | 18.1 | 0 | 2021-12-01 | -3.6 | 21.6 | 0 | 2020-12-01 | 4.3 | 13.7 | 0 | 2019-12-01 | -10 | 28 | 0 | 2018-12-01 | -1.1 | 19.1 | 0 | 2017-12-01 | 2.1 | 15.9 | 0 | 2016-12-01 | 6.7 | 11.3 | 0 | 18.61 | 0
2025-12-01 | -9.1 | 27.1 | 0 | 2024-12-01 | -1 | 19 | 0 | 2023-12-01 | 7 | 11 | 0 | 2022-12-01 | 0.8 | 17.2 | 0 | 2021-12-01 | -3 | 21 | 0 | 2020-12-01 | 4.4 | 13.6 | 0 | 2019-12-01 | -9 | 27 | 0 | 2018-12-01 | -0.5 | 18.5 | 0 | 2017-12-01 | 2.3 | 15.7 | 0 | 2016-12-01 | 6.7 | 11.3 | 0 | 18.14 | 0
2025-12-01 | -8.3 | 26.3 | 0 | 2024-12-01 | -0.9 | 18.9 | 0 | 2023-12-01 | 7.2 | 10.8 | 0 | 2022-12-01 | 0.9 | 17.1 | 0 | 2021-12-01 | -2.2 | 20.2 | 0 | 2020-12-01 | 5.1 | 12.9 | 0 | 2019-12-01 | -8.3 | 26.3 | 0 | 2018-12-01 | 0.3 | 17.7 | 0 | 2017-12-01 | 2.4 | 15.6 | 0 | 2016-12-01 | 6.4 | 11.6 | 0 | 17.74 | 0
2025-12-01 | -8.3 | 26.3 | 0 | 2024-12-01 | -0.9 | 18.9 | 0 | 2023-12-01 | 6 | 12 | 0 | 2022-12-01 | 0.9 | 17.1 | 0 | 2021-12-01 | -1.4 | 19.4 | 0 | 2020-12-01 | 5.2 | 12.8 | 0 | 2019-12-01 | -7.4 | 25.4 | 0 | 2018-12-01 | 1 | 17 | 0 | 2017-12-01 | 2.9 | 15.1 | 0 | 2016-12-01 | 6.3 | 11.7 | 0 | 17.57 | 0
2025-12-01 | -7.7 | 25.7 | 0 | 2024-12-01 | -1.8 | 19.8 | 0 | 2023-12-01 | 5.5 | 12.5 | 0 | 2022-12-01 | 1.3 | 16.7 | 0 | 2021-12-01 | -0.7 | 18.7 | 0 | 2020-12-01 | 5.3 | 12.7 | 0 | 2019-12-01 | -7.3 | 25.3 | 0 | 2018-12-01 | 1.2 | 16.8 | 0 | 2017-12-01 | 2.8 | 15.2 | 0 | 2016-12-01 | 5.8 | 12.2 | 0 | 17.56 | 0
2025-12-01 | -8.5 | 26.5 | 0 | 2024-12-01 | -2.3 | 20.3 | 0 | 2023-12-01 | 4.8 | 13.2 | 0 | 2022-12-01 | 1.1 | 16.9 | 0 | 2021-12-01 | -0.8 | 18.8 | 0 | 2020-12-01 | 5.2 | 12.8 | 0 | 2019-12-01 | -7.5 | 25.5 | 0 | 2018-12-01 | 1.1 | 16.9 | 0 | 2017-12-01 | 2.9 | 15.1 | 0 | 2016-12-01 | 5.3 | 12.7 | 0 | 17.87 | 0
2025-12-01 | -9.1 | 27.1 | 0 | 2024-12-01 | -2.4 | 20.4 | 0 | 2023-12-01 | 4.2 | 13.8 | 0 | 2022-12-01 | 0.5 | 17.5 | 0 | 2021-12-01 | -2.4 | 20.4 | 0 | 2020-12-01 | 5.2 | 12.8 | 0 | 2019-12-01 | -7.6 | 25.6 | 0 | 2018-12-01 | 0.2 | 17.8 | 0 | 2017-12-01 | 2.5 | 15.5 | 0 | 2016-12-01 | 4.6 | 13.4 | 0 | 18.43 | 0
2025-12-01 | -9.8 | 27.8 | 0 | 2024-12-01 | -3.8 | 21.8 | 0 | 2023-12-01 | 2.9 | 15.1 | 0 | 2022-12-01 | -0.2 | 18.2 | 0 | 2021-12-01 | -3.5 | 21.5 | 0 | 2020-12-01 | 5 | 13 | 0 | 2019-12-01 | -7.7 | 25.7 | 0 | 2018-12-01 | -0.5 | 18.5 | 0 | 2017-12-01 | 1.4 | 16.6 | 0 | 2016-12-01 | 4 | 14 | 0 | 19.22 | 0
2025-12-01 | -10.9 | 28.9 | 0 | 2024-12-01 | -4.1 | 22.1 | 0 | 2023-12-01 | 1.4 | 16.6 | 0 | 2022-12-01 | -1.9 | 19.9 | 0 | 2021-12-01 | -4.4 | 22.4 | 0 | 2020-12-01 | 4 | 14 | 0 | 2019-12-01 | -7.7 | 25.7 | 0 | 2018-12-01 | -0.8 | 18.8 | 0 | 2017-12-01 | 1.1 | 16.9 | 0 | 2016-12-01 | 3.9 | 14.1 | 0 | 19.94 | 0
2025-12-01 | -10.1 | 28.1 | 0 | 2024-12-01 | -5.4 | 23.4 | 0 | 2023-12-01 | 0.9 | 17.1 | 0 | 2022-12-01 | -2.3 | 20.3 | 0 | 2021-12-01 | -2.4 | 20.4 | 0 | 2020-12-01 | 3.4 | 14.6 | 0 | 2019-12-01 | -7.5 | 25.5 | 0 | 2018-12-01 | -1.5 | 19.5 | 0 | 2017-12-01 | 0.8 | 17.2 | 0 | 2016-12-01 | 4 | 14 | 0 | 20.01 | 0
2025-12-01 | -10.9 | 28.9 | 0 | 2024-12-01 | -6.3 | 24.3 | 0 | 2023-12-01 | 0.8 | 17.2 | 0 | 2022-12-01 | -2.1 | 20.1 | 0 | 2021-12-01 | -2.6 | 20.6 | 0 | 2020-12-01 | 3.5 | 14.5 | 0 | 2019-12-01 | -7.4 | 25.4 | 0 | 2018-12-01 | -1.6 | 19.6 | 0 | 2017-12-01 | 1 | 17 | 0 | 2016-12-01 | 4.1 | 13.9 | 0 | 20.15 | 0
2025-12-01 | -10.8 | 28.8 | 0 | 2024-12-01 | -6.4 | 24.4 | 0 | 2023-12-01 | 1.3 | 16.7 | 0 | 2022-12-01 | -2.9 | 20.9 | 0 | 2021-12-01 | -2.2 | 20.2 | 0 | 2020-12-01 | 2.9 | 15.1 | 0 | 2019-12-01 | -6.6 | 24.6 | 0 | 2018-12-01 | -1.2 | 19.2 | 0 | 2017-12-01 | 0.7 | 17.3 | 0 | 2016-12-01 | 4.2 | 13.8 | 0 | 20.1 | 0
2025-12-01 | -11.5 | 29.5 | 0 | 2024-12-01 | -6.4 | 24.4 | 0 | 2023-12-01 | 1.3 | 16.7 | 0 | 2022-12-01 | -2.6 | 20.6 | 0 | 2021-12-01 | -1.8 | 19.8 | 0 | 2020-12-01 | 1.9 | 16.1 | 0 | 2019-12-01 | -6.6 | 24.6 | 0 | 2018-12-01 | -1.4 | 19.4 | 0 | 2017-12-01 | 0.8 | 17.2 | 0 | 2016-12-01 | 4.4 | 13.6 | 0 | 20.19 | 0
2025-12-01 | -10.9 | 28.9 | 0 | 2024-12-01 | -7.1 | 25.1 | 0 | 2023-12-01 | 1.2 | 16.8 | 0 | 2022-12-01 | -3.2 | 21.2 | 0 | 2021-12-01 | -1.5 | 19.5 | 0 | 2020-12-01 | 1 | 17 | 0 | 2019-12-01 | -5.5 | 23.5 | 0 | 2018-12-01 | -1.6 | 19.6 | 0 | 2017-12-01 | 0.7 | 17.3 | 0 | 2016-12-01 | 4.3 | 13.7 | 0 | 20.26 | 0
2025-12-02 | -10.1 | 28.1 | 0 | 2024-12-02 | -6.5 | 24.5 | 0 | 2023-12-02 | 0.9 | 17.1 | 0 | 2022-12-02 | -3.4 | 21.4 | 0 | 2021-12-02 | -1.2 | 19.2 | 0 | 2020-12-02 | 0.8 | 17.2 | 0 | 2019-12-02 | -5.2 | 23.2 | 0 | 2018-12-02 | -1.2 | 19.2 | 0 | 2017-12-02 | 0.2 | 17.8 | 0 | 2016-12-02 | 4.3 | 13.7 | 0 | 20.14 | 0
2025-12-02 | -9.8 | 27.8 | 0 | 2024-12-02 | -7.2 | 25.2 | 0 | 2023-12-02 | 0.8 | 17.2 | 0 | 2022-12-02 | -3.9 | 21.9 | 0 | 2021-12-02 | -0.6 | 18.6 | 0 | 2020-12-02 | 1.2 | 16.8 | 0 | 2019-12-02 | -4.7 | 22.7 | 0 | 2018-12-02 | -0.9 | 18.9 | 0 | 2017-12-02 | 0.2 | 17.8 | 0 | 2016-12-02 | 4.3 | 13.7 | 0 | 20.06 | 0
2025-12-02 | -9.4 | 27.4 | 0 | 2024-12-02 | -6.8 | 24.8 | 0 | 2023-12-02 | 0.7 | 17.3 | 0 | 2022-12-02 | -3.4 | 21.4 | 0 | 2021-12-02 | -0.6 | 18.6 | 0 | 2020-12-02 | 1.1 | 16.9 | 0 | 2019-12-02 | -4.7 | 22.7 | 0 | 2018-12-02 | -1.2 | 19.2 | 0 | 2017-12-02 | 0.1 | 17.9 | 0 | 2016-12-02 | 4.2 | 13.8 | 0 | 20 | 0
2025-12-02 | -9.3 | 27.3 | 0 | 2024-12-02 | -7 | 25 | 0 | 2023-12-02 | 0.1 | 17.9 | 0 | 2022-12-02 | -3.5 | 21.5 | 0 | 2021-12-02 | -0.9 | 18.9 | 0 | 2020-12-02 | -1 | 19 | 0 | 2019-12-02 | -4.5 | 22.5 | 0 | 2018-12-02 | -1.4 | 19.4 | 0 | 2017-12-02 | -0.1 | 18.1 | 0 | 2016-12-02 | 3.8 | 14.2 | 0 | 20.38 | 0
2025-12-02 | -9.2 | 27.2 | 0 | 2024-12-02 | -7.4 | 25.4 | 0 | 2023-12-02 | 0 | 18 | 0 | 2022-12-02 | -2.9 | 20.9 | 0 | 2021-12-02 | -0.9 | 18.9 | 0 | 2020-12-02 | -1.3 | 19.3 | 0 | 2019-12-02 | -4.3 | 22.3 | 0 | 2018-12-02 | -1.4 | 19.4 | 0 | 2017-12-02 | 0.2 | 17.8 | 0 | 2016-12-02 | 4 | 14 | 0 | 20.32 | 0
2025-12-02 | -9.7 | 27.7 | 0 | 2024-12-02 | -8.1 | 26.1 | 0 | 2023-12-02 | -0.1 | 18.1 | 0 | 2022-12-02 | -2.5 | 20.5 | 0 | 2021-12-02 | -0.3 | 18.3 | 0 | 2020-12-02 | -1.3 | 19.3 | 0 | 2019-12-02 | -4.2 | 22.2 | 0 | 2018-12-02 | -1.4 | 19.4 | 0 | 2017-12-02 | -0.3 | 18.3 | 0 | 2016-12-02 | 4 | 14 | 0 | 20.39 | 0
2025-12-02 | -10.4 | 28.4 | 0 | 2024-12-02 | -8.1 | 26.1 | 0 | 2023-12-02 | -0.2 | 18.2 | 0 | 2022-12-02 | -1.7 | 19.7 | 0 | 2021-12-02 | 0.2 | 17.8 | 0 | 2020-12-02 | -1.7 | 19.7 | 0 | 2019-12-02 | -4.5 | 22.5 | 0 | 2018-12-02 | -1.1 | 19.1 | 0 | 2017-12-02 | -0.3 | 18.3 | 0 | 2016-12-02 | 4.2 | 13.8 | 0 | 20.36 | 0
2025-12-02 | -11.1 | 29.1 | 0 | 2024-12-02 | -8.9 | 26.9 | 0 | 2023-12-02 | -0.4 | 18.4 | 0 | 2022-12-02 | -1.9 | 19.9 | 0 | 2021-12-02 | 1.4 | 16.6 | 0 | 2020-12-02 | -1.9 | 19.9 | 0 | 2019-12-02 | -5.4 | 23.4 | 0 | 2018-12-02 | -1.1 | 19.1 | 0 | 2017-12-02 | -0.4 | 18.4 | 0 | 2016-12-02 | 4.2 | 13.8 | 0 | 20.55 | 0
2025-12-02 | -10.6 | 28.6 | 0 | 2024-12-02 | -8.3 | 26.3 | 0 | 2023-12-02 | -0.5 | 18.5 | 0 | 2022-12-02 | -1.3 | 19.3 | 0 | 2021-12-02 | 2.9 | 15.1 | 0 | 2020-12-02 | -2.2 | 20.2 | 0 | 2019-12-02 | -6 | 24 | 0 | 2018-12-02 | -0.6 | 18.6 | 0 | 2017-12-02 | -0.3 | 18.3 | 0 | 2016-12-02 | 4.4 | 13.6 | 0 | 20.25 | 0
2025-12-02 | -9.9 | 27.9 | 0 | 2024-12-02 | -8.2 | 26.2 | 0 | 2023-12-02 | -0.6 | 18.6 | 0 | 2022-12-02 | -0.2 | 18.2 | 0 | 2021-12-02 | 3.4 | 14.6 | 0 | 2020-12-02 | -2.1 | 20.1 | 0 | 2019-12-02 | -4.8 | 22.8 | 0 | 2018-12-02 | -0.2 | 18.2 | 0 | 2017-12-02 | 0.4 | 17.6 | 0 | 2016-12-02 | 2.7 | 15.3 | 0 | 19.95 | 0
2025-12-02 | -9.1 | 27.1 | 0 | 2024-12-02 | -4.7 | 22.7 | 0 | 2023-12-02 | -0.8 | 18.8 | 0 | 2022-12-02 | 1.2 | 16.8 | 0 | 2021-12-02 | 4 | 14 | 0 | 2020-12-02 | -1.8 | 19.8 | 0 | 2019-12-02 | -3.4 | 21.4 | 0 | 2018-12-02 | 0 | 18 | 0 | 2017-12-02 | 1.7 | 16.3 | 0 | 2016-12-02 | 2.8 | 15.2 | 0 | 19.01 | 0
2025-12-02 | -8 | 26 | 0 | 2024-12-02 | -1.8 | 19.8 | 0 | 2023-12-02 | -0.4 | 18.4 | 0 | 2022-12-02 | 1.7 | 16.3 | 0 | 2021-12-02 | 4.5 | 13.5 | 0 | 2020-12-02 | -1.4 | 19.4 | 0 | 2019-12-02 | -2.5 | 20.5 | 0 | 2018-12-02 | 0.2 | 17.8 | 0 | 2017-12-02 | 2.8 | 15.2 | 0 | 2016-12-02 | 3.3 | 14.7 | 0 | 18.16 | 0
2025-12-02 | -7.3 | 25.3 | 0 | 2024-12-02 | -1.8 | 19.8 | 0 | 2023-12-02 | -0.2 | 18.2 | 0 | 2022-12-02 | 1.8 | 16.2 | 0 | 2021-12-02 | 5.1 | 12.9 | 0 | 2020-12-02 | -1.6 | 19.6 | 0 | 2019-12-02 | -0.9 | 18.9 | 0 | 2018-12-02 | 0.3 | 17.7 | 0 | 2017-12-02 | 4.2 | 13.8 | 0 | 2016-12-02 | 3.7 | 14.3 | 0 | 17.67 | 0
2025-12-02 | -5.9 | 23.9 | 0 | 2024-12-02 | -1.6 | 19.6 | 0 | 2023-12-02 | 0.4 | 17.6 | 0 | 2022-12-02 | 2.1 | 15.9 | 0 | 2021-12-02 | 5.7 | 12.3 | 0 | 2020-12-02 | -2.1 | 20.1 | 0 | 2019-12-02 | 0.6 | 17.4 | 0 | 2018-12-02 | 0.4 | 17.6 | 0 | 2017-12-02 | 4.4 | 13.6 | 0 | 2016-12-02 | 3.7 | 14.3 | 0 | 17.23 | 0
2025-12-02 | -5.3 | 23.3 | 0 | 2024-12-02 | -1.7 | 19.7 | 0 | 2023-12-02 | 0.7 | 17.3 | 0 | 2022-12-02 | 2 | 16 | 0 | 2021-12-02 | 6.3 | 11.7 | 0 | 2020-12-02 | -1.8 | 19.8 | 0 | 2019-12-02 | 1.6 | 16.4 | 0 | 2018-12-02 | 0.6 | 17.4 | 0 | 2017-12-02 | 4.3 | 13.7 | 0 | 2016-12-02 | 3.5 | 14.5 | 0 | 16.98 | 0
2025-12-02 | -5.5 | 23.5 | 0 | 2024-12-02 | -2 | 20 | 0 | 2023-12-02 | 0.9 | 17.1 | 0 | 2022-12-02 | 1.7 | 16.3 | 0 | 2021-12-02 | 7 | 11 | 0 | 2020-12-02 | -1.8 | 19.8 | 0 | 2019-12-02 | 1.6 | 16.4 | 0 | 2018-12-02 | 0.9 | 17.1 | 0 | 2017-12-02 | 5 | 13 | 0 | 2016-12-02 | 3 | 15 | 0 | 16.92 | 0
2025-12-02 | -6.4 | 24.4 | 0 | 2024-12-02 | -2.1 | 20.1 | 0 | 2023-12-02 | 0.8 | 17.2 | 0 | 2022-12-02 | 1.5 | 16.5 | 0 | 2021-12-02 | 6 | 12 | 0 | 2020-12-02 | -2.4 | 20.4 | 0 | 2019-12-02 | 0.2 | 17.8 | 0 | 2018-12-02 | 0.9 | 17.1 | 0 | 2017-12-02 | 1.8 | 16.2 | 0 | 2016-12-02 | 2.6 | 15.4 | 0 | 17.71 | 0
2025-12-02 | -8.3 | 26.3 | 0 | 2024-12-02 | -2.3 | 20.3 | 0 | 2023-12-02 | 0.6 | 17.4 | 0 | 2022-12-02 | 1.4 | 16.6 | 0 | 2021-12-02 | 4.3 | 13.7 | 0 | 2020-12-02 | -2.7 | 20.7 | 0 | 2019-12-02 | -1.6 | 19.6 | 0 | 2018-12-02 | 1 | 17 | 0 | 2017-12-02 | 0.6 | 17.4 | 0 | 2016-12-02 | 2 | 16 | 0 | 18.5 | 0
2025-12-02 | -9 | 27 | 0 | 2024-12-02 | -2 | 20 | 0 | 2023-12-02 | 0.8 | 17.2 | 0 | 2022-12-02 | 1.8 | 16.2 | 0 | 2021-12-02 | 4 | 14 | 0 | 2020-12-02 | -2.5 | 20.5 | 0 | 2019-12-02 | -2.4 | 20.4 | 0 | 2018-12-02 | 0.8 | 17.2 | 0 | 2017-12-02 | 0.9 | 17.1 | 0 | 2016-12-02 | 2.2 | 15.8 | 0 | 18.54 | 0
2025-12-02 | -9.2 | 27.2 | 0 | 2024-12-02 | -2.5 | 20.5 | 0 | 2023-12-02 | 0.6 | 17.4 | 0 | 2022-12-02 | 2.2 | 15.8 | 0 | 2021-12-02 | 4.3 | 13.7 | 0 | 2020-12-02 | -2.7 | 20.7 | 0 | 2019-12-02 | -2.9 | 20.9 | 0 | 2018-12-02 | 0.8 | 17.2 | 0 | 2017-12-02 | 0.6 | 17.4 | 0 | 2016-12-02 | 1.9 | 16.1 | 0 | 18.69 | 0
2025-12-02 | -8.7 | 26.7 | 0 | 2024-12-02 | -3.2 | 21.2 | 0 | 2023-12-02 | 0.4 | 17.6 | 0 | 2022-12-02 | 2.4 | 15.6 | 0 | 2021-12-02 | 3.2 | 14.8 | 0 | 2020-12-02 | -3.1 | 21.1 | 0 | 2019-12-02 | -3.5 | 21.5 | 0 | 2018-12-02 | 0.7 | 17.3 | 0 | 2017-12-02 | 0.6 | 17.4 | 0 | 2016-12-02 | 1.7 | 16.3 | 0 | 18.95 | 0
2025-12-02 | -9.5 | 27.5 | 0 | 2024-12-02 | -3.7 | 21.7 | 0 | 2023-12-02 | 0.2 | 17.8 | 0 | 2022-12-02 | 2.6 | 15.4 | 0 | 2021-12-02 | 0.8 | 17.2 | 0 | 2020-12-02 | -3.4 | 21.4 | 0 | 2019-12-02 | -4.3 | 22.3 | 0 | 2018-12-02 | 0.7 | 17.3 | 0 | 2017-12-02 | 0.4 | 17.6 | 0 | 2016-12-02 | 1.6 | 16.4 | 0 | 19.46 | 0
2025-12-02 | -12.2 | 30.2 | 0 | 2024-12-02 | -4.3 | 22.3 | 0 | 2023-12-02 | 0.2 | 17.8 | 0 | 2022-12-02 | 2.1 | 15.9 | 0 | 2021-12-02 | 0.2 | 17.8 | 0 | 2020-12-02 | -3.8 | 21.8 | 0 | 2019-12-02 | -4.9 | 22.9 | 0 | 2018-12-02 | 0.8 | 17.2 | 0 | 2017-12-02 | 0.1 | 17.9 | 0 | 2016-12-02 | 1.5 | 16.5 | 0 | 20.03 | 0
2025-12-02 | -11.8 | 29.8 | 0 | 2024-12-02 | -4.6 | 22.6 | 0 | 2023-12-02 | 0 | 18 | 0 | 2022-12-02 | 2.2 | 15.8 | 0 | 2021-12-02 | -0.2 | 18.2 | 0 | 2020-12-02 | -4.4 | 22.4 | 0 | 2019-12-02 | -5.4 | 23.4 | 0 | 2018-12-02 | 0.8 | 17.2 | 0 | 2017-12-02 | -0.2 | 18.2 | 0 | 2016-12-02 | 1.2 | 16.8 | 0 | 20.24 | 0
2025-12-03 | -12.2 | 30.2 | 0 | 2024-12-03 | -5.3 | 23.3 | 0 | 2023-12-03 | 0 | 18 | 0 | 2022-12-03 | 2.5 | 15.5 | 0 | 2021-12-03 | -0.8 | 18.8 | 0 | 2020-12-03 | -4.9 | 22.9 | 0 | 2019-12-03 | -6 | 24 | 0 | 2018-12-03 | 0.7 | 17.3 | 0 | 2017-12-03 | -0.3 | 18.3 | 0 | 2016-12-03 | 0.9 | 17.1 | 0 | 20.54 | 0
2025-12-03 | -13 | 31 | 0 | 2024-12-03 | -4.8 | 22.8 | 0 | 2023-12-03 | -0.1 | 18.1 | 0 | 2022-12-03 | 2.7 | 15.3 | 0 | 2021-12-03 | -1.2 | 19.2 | 0 | 2020-12-03 | -4.8 | 22.8 | 0 | 2019-12-03 | -7.9 | 25.9 | 0 | 2018-12-03 | 1 | 17 | 0 | 2017-12-03 | -0.3 | 18.3 | 0 | 2016-12-03 | 0.9 | 17.1 | 0 | 20.75 | 0
2025-12-03 | -13.6 | 31.6 | 0 | 2024-12-03 | -4.2 | 22.2 | 0 | 2023-12-03 | 0 | 18 | 0 | 2022-12-03 | 3 | 15 | 0 | 2021-12-03 | -1.2 | 19.2 | 0 | 2020-12-03 | -5.1 | 23.1 | 0 | 2019-12-03 | -6.5 | 24.5 | 0 | 2018-12-03 | 1 | 17 | 0 | 2017-12-03 | -0.4 | 18.4 | 0 | 2016-12-03 | 1 | 17 | 0 | 20.6 | 0
2025-12-03 | -13.2 | 31.2 | 0 | 2024-12-03 | -3.6 | 21.6 | 0 | 2023-12-03 | -0.2 | 18.2 | 0 | 2022-12-03 | 3 | 15 | 0 | 2021-12-03 | -1.9 | 19.9 | 0 | 2020-12-03 | -4.1 | 22.1 | 0 | 2019-12-03 | -7.3 | 25.3 | 0 | 2018-12-03 | 0.9 | 17.1 | 0 | 2017-12-03 | -0.4 | 18.4 | 0 | 2016-12-03 | 0.9 | 17.1 | 0 | 20.59 | 0
2025-12-03 | -12.1 | 30.1 | 0 | 2024-12-03 | -3.4 | 21.4 | 0 | 2023-12-03 | -0.4 | 18.4 | 0 | 2022-12-03 | 4.5 | 13.5 | 0 | 2021-12-03 | -2.1 | 20.1 | 0 | 2020-12-03 | -1.8 | 19.8 | 0 | 2019-12-03 | -7.3 | 25.3 | 0 | 2018-12-03 | 1.1 | 16.9 | 0 | 2017-12-03 | -0.8 | 18.8 | 0 | 2016-12-03 | 0.9 | 17.1 | 0 | 20.14 | 0
2025-12-03 | -11.6 | 29.6 | 0 | 2024-12-03 | -3.5 | 21.5 | 0 | 2023-12-03 | -0.5 | 18.5 | 0 | 2022-12-03 | 4.7 | 13.3 | 0 | 2021-12-03 | -2.9 | 20.9 | 0 | 2020-12-03 | -0.8 | 18.8 | 0 | 2019-12-03 | -9.1 | 27.1 | 0 | 2018-12-03 | 1.4 | 16.6 | 0 | 2017-12-03 | -1.6 | 19.6 | 0 | 2016-12-03 | 0.6 | 17.4 | 0 | 20.33 | 0
2025-12-03 | -10.7 | 28.7 | 0 | 2024-12-03 | -4 | 22 | 0 | 2023-12-03 | -0.6 | 18.6 | 0 | 2022-12-03 | 5.1 | 12.9 | 0 | 2021-12-03 | -3.2 | 21.2 | 0 | 2020-12-03 | -0.5 | 18.5 | 0 | 2019-12-03 | -9.3 | 27.3 | 0 | 2018-12-03 | 1.3 | 16.7 | 0 | 2017-12-03 | -2.1 | 20.1 | 0 | 2016-12-03 | 0.6 | 17.4 | 0 | 20.34 | 0
2025-12-03 | -10.3 | 28.3 | 0 | 2024-12-03 | -3.9 | 21.9 | 0 | 2023-12-03 | -0.9 | 18.9 | 0 | 2022-12-03 | 5.4 | 12.6 | 0 | 2021-12-03 | -4.6 | 22.6 | 0 | 2020-12-03 | 0.1 | 17.9 | 0 | 2019-12-03 | -9.1 | 27.1 | 0 | 2018-12-03 | 0.8 | 17.2 | 0 | 2017-12-03 | -1.5 | 19.5 | 0 | 2016-12-03 | 0.8 | 17.2 | 0 | 20.32 | 0
2025-12-03 | -9.9 | 27.9 | 0 | 2024-12-03 | -3.7 | 21.7 | 0 | 2023-12-03 | -1.1 | 19.1 | 0 | 2022-12-03 | 6.6 | 11.4 | 0 | 2021-12-03 | -5.5 | 23.5 | 0 | 2020-12-03 | 0.4 | 17.6 | 0 | 2019-12-03 | -8.6 | 26.6 | 0 | 2018-12-03 | 0.4 | 17.6 | 0 | 2017-12-03 | -1.2 | 19.2 | 0 | 2016-12-03 | 0.6 | 17.4 | 0 | 20.2 | 0
2025-12-03 | -8.9 | 26.9 | 0 | 2024-12-03 | -3.5 | 21.5 | 0 | 2023-12-03 | -1.1 | 19.1 | 0 | 2022-12-03 | 6.4 | 11.6 | 0 | 2021-12-03 | -5.6 | 23.6 | 0 | 2020-12-03 | 1 | 17 | 0 | 2019-12-03 | -5.9 | 23.9 | 0 | 2018-12-03 | -0.1 | 18.1 | 0 | 2017-12-03 | -0.2 | 18.2 | 0 | 2016-12-03 | 0.9 | 17.1 | 0 | 19.7 | 0
2025-12-03 | -7.7 | 25.7 | 0 | 2024-12-03 | -3.1 | 21.1 | 0 | 2023-12-03 | -1.2 | 19.2 | 0 | 2022-12-03 | 6.8 | 11.2 | 0 | 2021-12-03 | -5.5 | 23.5 | 0 | 2020-12-03 | 1.2 | 16.8 | 0 | 2019-12-03 | -4 | 22 | 0 | 2018-12-03 | -0.6 | 18.6 | 0 | 2017-12-03 | 0.2 | 17.8 | 0 | 2016-12-03 | 1.5 | 16.5 | 0 | 19.24 | 0
2025-12-03 | -6.1 | 24.1 | 0 | 2024-12-03 | -2.8 | 20.8 | 0 | 2023-12-03 | -1.1 | 19.1 | 0 | 2022-12-03 | 7.3 | 10.7 | 0 | 2021-12-03 | -5.8 | 23.8 | 0 | 2020-12-03 | 2.7 | 15.3 | 0 | 2019-12-03 | -2.5 | 20.5 | 0 | 2018-12-03 | -1.1 | 19.1 | 0 | 2017-12-03 | 1.1 | 16.9 | 0 | 2016-12-03 | 1.8 | 16.2 | 0 | 18.65 | 0
2025-12-03 | -5.1 | 23.1 | 0 | 2024-12-03 | -1.8 | 19.8 | 0 | 2023-12-03 | -0.8 | 18.8 | 0 | 2022-12-03 | 8 | 10 | 0 | 2021-12-03 | -5.7 | 23.7 | 0 | 2020-12-03 | 2.5 | 15.5 | 0 | 2019-12-03 | -1.4 | 19.4 | 0 | 2018-12-03 | -1.1 | 19.1 | 0 | 2017-12-03 | 2.4 | 15.6 | 0 | 2016-12-03 | 1.8 | 16.2 | 0 | 18.12 | 0
2025-12-03 | -4.3 | 22.3 | 0 | 2024-12-03 | -0.9 | 18.9 | 0 | 2023-12-03 | -0.6 | 18.6 | 0 | 2022-12-03 | 8.1 | 9.9 | 0 | 2021-12-03 | -5.3 | 23.3 | 0 | 2020-12-03 | 3 | 15 | 0 | 2019-12-03 | -0.7 | 18.7 | 0 | 2018-12-03 | -1.2 | 19.2 | 0 | 2017-12-03 | 3 | 15 | 0 | 2016-12-03 | 2.1 | 15.9 | 0 | 17.68 | 0
2025-12-03 | -3.7 | 21.7 | 0 | 2024-12-03 | -1.9 | 19.9 | 0 | 2023-12-03 | -0.5 | 18.5 | 0 | 2022-12-03 | 8.6 | 9.4 | 0 | 2021-12-03 | -4.9 | 22.9 | 0 | 2020-12-03 | 3.3 | 14.7 | 0 | 2019-12-03 | 0.2 | 17.8 | 0 | 2018-12-03 | -1.3 | 19.3 | 0 | 2017-12-03 | 3.2 | 14.8 | 0 | 2016-12-03 | 2 | 16 | 0 | 17.5 | 0
2025-12-03 | -2.3 | 20.3 | 0 | 2024-12-03 | -2.1 | 20.1 | 0 | 2023-12-03 | -0.4 | 18.4 | 0 | 2022-12-03 | 6.8 | 11.2 | 0 | 2021-12-03 | -4.7 | 22.7 | 0 | 2020-12-03 | 3.1 | 14.9 | 0 | 2019-12-03 | 0.6 | 17.4 | 0 | 2018-12-03 | -0.9 | 18.9 | 0 | 2017-12-03 | 3.4 | 14.6 | 0 | 2016-12-03 | 1.8 | 16.2 | 0 | 17.47 | 0
2025-12-03 | -1.1 | 19.1 | 0 | 2024-12-03 | -2.4 | 20.4 | 0 | 2023-12-03 | -0.3 | 18.3 | 0 | 2022-12-03 | 5 | 13 | 0 | 2021-12-03 | -5.3 | 23.3 | 0 | 2020-12-03 | 2.8 | 15.2 | 0 | 2019-12-03 | -1.4 | 19.4 | 0 | 2018-12-03 | -0.6 | 18.6 | 0 | 2017-12-03 | 2.5 | 15.5 | 0 | 2016-12-03 | 1.6 | 16.4 | 0 | 17.92 | 0
2025-12-03 | -0.1 | 18.1 | 0 | 2024-12-03 | -2.6 | 20.6 | 0 | 2023-12-03 | -0.3 | 18.3 | 0 | 2022-12-03 | 4 | 14 | 0 | 2021-12-03 | -6.5 | 24.5 | 0 | 2020-12-03 | 2.7 | 15.3 | 0 | 2019-12-03 | -3.7 | 21.7 | 0 | 2018-12-03 | -0.7 | 18.7 | 0 | 2017-12-03 | 1.4 | 16.6 | 0 | 2016-12-03 | 1.2 | 16.8 | 0 | 18.46 | 0
2025-12-03 | 0.6 | 17.4 | 0 | 2024-12-03 | -4.5 | 22.5 | 0 | 2023-12-03 | -0.2 | 18.2 | 0 | 2022-12-03 | 3.7 | 14.3 | 0 | 2021-12-03 | -6.8 | 24.8 | 0 | 2020-12-03 | 2.6 | 15.4 | 0 | 2019-12-03 | -3.5 | 21.5 | 0 | 2018-12-03 | -1.4 | 19.4 | 0 | 2017-12-03 | -0.5 | 18.5 | 0 | 2016-12-03 | 0.6 | 17.4 | 0 | 18.94 | 0
2025-12-03 | 0.8 | 17.2 | 0 | 2024-12-03 | -4.7 | 22.7 | 0 | 2023-12-03 | -0.1 | 18.1 | 0 | 2022-12-03 | 3.5 | 14.5 | 0 | 2021-12-03 | -6.8 | 24.8 | 0 | 2020-12-03 | 2.5 | 15.5 | 0 | 2019-12-03 | -3.6 | 21.6 | 0 | 2018-12-03 | -1 | 19 | 0 | 2017-12-03 | -0.8 | 18.8 | 0 | 2016-12-03 | 0.1 | 17.9 | 0 | 19.01 | 0
2025-12-03 | 0.5 | 17.5 | 0 | 2024-12-03 | -6 | 24 | 0 | 2023-12-03 | -0.1 | 18.1 | 0 | 2022-12-03 | 1.5 | 16.5 | 0 | 2021-12-03 | -6.5 | 24.5 | 0 | 2020-12-03 | 1.8 | 16.2 | 0 | 2019-12-03 | -3.6 | 21.6 | 0 | 2018-12-03 | -0.8 | 18.8 | 0 | 2017-12-03 | -2 | 20 | 0 | 2016-12-03 | -0.3 | 18.3 | 0 | 19.55 | 0
2025-12-03 | 0.1 | 17.9 | 0 | 2024-12-03 | -6.6 | 24.6 | 0 | 2023-12-03 | -0.2 | 18.2 | 0 | 2022-12-03 | 0.6 | 17.4 | 0 | 2021-12-03 | -6.8 | 24.8 | 0 | 2020-12-03 | 1.4 | 16.6 | 0 | 2019-12-03 | -5.1 | 23.1 | 0 | 2018-12-03 | -1.3 | 19.3 | 0 | 2017-12-03 | -1.3 | 19.3 | 0 | 2016-12-03 | -0.6 | 18.6 | 0 | 19.98 | 0
2025-12-03 | 0.1 | 17.9 | 0 | 2024-12-03 | -7 | 25 | 0 | 2023-12-03 | -0.3 | 18.3 | 0 | 2022-12-03 | -0.1 | 18.1 | 0 | 2021-12-03 | -6.8 | 24.8 | 0 | 2020-12-03 | 1.5 | 16.5 | 0 | 2019-12-03 | -5.4 | 23.4 | 0 | 2018-12-03 | -2.5 | 20.5 | 0 | 2017-12-03 | -0.2 | 18.2 | 0 | 2016-12-03 | -1.1 | 19.1 | 0 | 20.18 | 0
2025-12-03 | -0.9 | 18.9 | 0 | 2024-12-03 | -6.9 | 24.9 | 0 | 2023-12-03 | -0.5 | 18.5 | 0 | 2022-12-03 | -0.9 | 18.9 | 0 | 2021-12-03 | -6.9 | 24.9 | 0 | 2020-12-03 | 1.7 | 16.3 | 0 | 2019-12-03 | -5.5 | 23.5 | 0 | 2018-12-03 | -3.2 | 21.2 | 0 | 2017-12-03 | -1 | 19 | 0 | 2016-12-03 | -1.4 | 19.4 | 0 | 20.55 | 0
2025-12-04 | -1 | 19 | 0 | 2024-12-04 | -6.6 | 24.6 | 0 | 2023-12-04 | -0.6 | 18.6 | 0 | 2022-12-04 | -1.9 | 19.9 | 0 | 2021-12-04 | -7.1 | 25.1 | 0 | 2020-12-04 | 1.6 | 16.4 | 0 | 2019-12-04 | -4.8 | 22.8 | 0 | 2018-12-04 | -3.6 | 21.6 | 0 | 2017-12-04 | -3.1 | 21.1 | 0 | 2016-12-04 | -1.4 | 19.4 | 0 | 20.85 | 0
2025-12-04 | -1 | 19 | 0 | 2024-12-04 | -6.8 | 24.8 | 0 | 2023-12-04 | -0.8 | 18.8 | 0 | 2022-12-04 | -2.8 | 20.8 | 0 | 2021-12-04 | -8 | 26 | 0 | 2020-12-04 | 1.8 | 16.2 | 0 | 2019-12-04 | -5.5 | 23.5 | 0 | 2018-12-04 | -4.5 | 22.5 | 0 | 2017-12-04 | -1.8 | 19.8 | 0 | 2016-12-04 | -1.7 | 19.7 | 0 | 21.11 | 0
2025-12-04 | -2.7 | 20.7 | 0 | 2024-12-04 | -6.2 | 24.2 | 0 | 2023-12-04 | -1.2 | 19.2 | 0 | 2022-12-04 | -3.3 | 21.3 | 0 | 2021-12-04 | -9.8 | 27.8 | 0 | 2020-12-04 | 2.2 | 15.8 | 0 | 2019-12-04 | -5.4 | 23.4 | 0 | 2018-12-04 | -5.4 | 23.4 | 0 | 2017-12-04 | -1.6 | 19.6 | 0 | 2016-12-04 | -1.7 | 19.7 | 0 | 21.51 | 0
2025-12-04 | -4.1 | 22.1 | 0 | 2024-12-04 | -5.8 | 23.8 | 0 | 2023-12-04 | -1.4 | 19.4 | 0 | 2022-12-04 | -3.3 | 21.3 | 0 | 2021-12-04 | -9.8 | 27.8 | 0 | 2020-12-04 | 2.2 | 15.8 | 0 | 2019-12-04 | -5.8 | 23.8 | 0 | 2018-12-04 | -5.7 | 23.7 | 0 | 2017-12-04 | -1.4 | 19.4 | 0 | 2016-12-04 | -1.8 | 19.8 | 0 | 21.69 | 0
2025-12-04 | -4.9 | 22.9 | 0 | 2024-12-04 | -4.8 | 22.8 | 0 | 2023-12-04 | -1.5 | 19.5 | 0 | 2022-12-04 | -4.3 | 22.3 | 0 | 2021-12-04 | -9.3 | 27.3 | 0 | 2020-12-04 | 1.9 | 16.1 | 0 | 2019-12-04 | -4.9 | 22.9 | 0 | 2018-12-04 | -5.9 | 23.9 | 0 | 2017-12-04 | -1.3 | 19.3 | 0 | 2016-12-04 | -1.8 | 19.8 | 0 | 21.68 | 0
2025-12-04 | -5.9 | 23.9 | 0 | 2024-12-04 | -5.4 | 23.4 | 0 | 2023-12-04 | -1.7 | 19.7 | 0 | 2022-12-04 | -5.1 | 23.1 | 0 | 2021-12-04 | -11.8 | 29.8 | 0 | 2020-12-04 | 1.6 | 16.4 | 0 | 2019-12-04 | -4.7 | 22.7 | 0 | 2018-12-04 | -5.8 | 23.8 | 0 | 2017-12-04 | -1.2 | 19.2 | 0 | 2016-12-04 | -1.9 | 19.9 | 0 | 22.19 | 0
2025-12-04 | -6.5 | 24.5 | 0 | 2024-12-04 | -4.9 | 22.9 | 0 | 2023-12-04 | -1.6 | 19.6 | 0 | 2022-12-04 | -6 | 24 | 0 | 2021-12-04 | -11.2 | 29.2 | 0 | 2020-12-04 | 1.4 | 16.6 | 0 | 2019-12-04 | -4.3 | 22.3 | 0 | 2018-12-04 | -6 | 24 | 0 | 2017-12-04 | -1.2 | 19.2 | 0 | 2016-12-04 | -2 | 20 | 0 | 22.23 | 0
2025-12-04 | -7.9 | 25.9 | 0 | 2024-12-04 | -4.1 | 22.1 | 0 | 2023-12-04 | -1.4 | 19.4 | 0 | 2022-12-04 | -6.6 | 24.6 | 0 | 2021-12-04 | -11.5 | 29.5 | 0 | 2020-12-04 | 1.2 | 16.8 | 0 | 2019-12-04 | -4 | 22 | 0 | 2018-12-04 | -6 | 24 | 0 | 2017-12-04 | -1.3 | 19.3 | 0 | 2016-12-04 | -2.1 | 20.1 | 0 | 22.37 | 0
2025-12-04 | -8.4 | 26.4 | 0 | 2024-12-04 | -3.7 | 21.7 | 0 | 2023-12-04 | -1.8 | 19.8 | 0 | 2022-12-04 | -5 | 23 | 0 | 2021-12-04 | -9.2 | 27.2 | 0 | 2020-12-04 | 1.5 | 16.5 | 0 | 2019-12-04 | -3.6 | 21.6 | 0 | 2018-12-04 | -6.2 | 24.2 | 0 | 2017-12-04 | -1.3 | 19.3 | 0 | 2016-12-04 | -2.2 | 20.2 | 0 | 21.99 | 0
2025-12-04 | -9.7 | 27.7 | 0 | 2024-12-04 | -3 | 21 | 0 | 2023-12-04 | -1.8 | 19.8 | 0 | 2022-12-04 | -4.4 | 22.4 | 0 | 2021-12-04 | -7.6 | 25.6 | 0 | 2020-12-04 | 2 | 16 | 0 | 2019-12-04 | -2.9 | 20.9 | 0 | 2018-12-04 | -6.3 | 24.3 | 0 | 2017-12-04 | -1.4 | 19.4 | 0 | 2016-12-04 | -1.9 | 19.9 | 0 | 21.7 | 0
2025-12-04 | -10.1 | 28.1 | 0 | 2024-12-04 | -2.5 | 20.5 | 0 | 2023-12-04 | -1.8 | 19.8 | 0 | 2022-12-04 | -3.7 | 21.7 | 0 | 2021-12-04 | -6.9 | 24.9 | 0 | 2020-12-04 | 2.8 | 15.2 | 0 | 2019-12-04 | -2.3 | 20.3 | 0 | 2018-12-04 | -6.5 | 24.5 | 0 | 2017-12-04 | -1.2 | 19.2 | 0 | 2016-12-04 | -1.6 | 19.6 | 0 | 21.38 | 0
2025-12-04 | -10 | 28 | 0 | 2024-12-04 | -1.7 | 19.7 | 0 | 2023-12-04 | -1.6 | 19.6 | 0 | 2022-12-04 | -2.9 | 20.9 | 0 | 2021-12-04 | -7.1 | 25.1 | 0 | 2020-12-04 | 2.9 | 15.1 | 0 | 2019-12-04 | -1.2 | 19.2 | 0 | 2018-12-04 | -6.1 | 24.1 | 0 | 2017-12-04 | -0.6 | 18.6 | 0 | 2016-12-04 | -0.4 | 18.4 | 0 | 20.87 | 0
2025-12-04 | -9.9 | 27.9 | 0 | 2024-12-04 | -1.2 | 19.2 | 0 | 2023-12-04 | -1.5 | 19.5 | 0 | 2022-12-04 | -2.2 | 20.2 | 0 | 2021-12-04 | -6.4 | 24.4 | 0 | 2020-12-04 | 3 | 15 | 0 | 2019-12-04 | -0.8 | 18.8 | 0 | 2018-12-04 | -5.7 | 23.7 | 0 | 2017-12-04 | 0.4 | 17.6 | 0 | 2016-12-04 | -1.1 | 19.1 | 0 | 20.54 | 0
2025-12-04 | -10.2 | 28.2 | 0 | 2024-12-04 | -1.4 | 19.4 | 0 | 2023-12-04 | -1.3 | 19.3 | 0 | 2022-12-04 | -1.1 | 19.1 | 0 | 2021-12-04 | -5.7 | 23.7 | 0 | 2020-12-04 | 2.7 | 15.3 | 0 | 2019-12-04 | 0.2 | 17.8 | 0 | 2018-12-04 | -5.5 | 23.5 | 0 | 2017-12-04 | 2.5 | 15.5 | 0 | 2016-12-04 | 0.5 | 17.5 | 0 | 19.93 | 0
2025-12-04 | -10.6 | 28.6 | 0 | 2024-12-04 | -1.8 | 19.8 | 0 | 2023-12-04 | -1.4 | 19.4 | 0 | 2022-12-04 | 0.4 | 17.6 | 0 | 2021-12-04 | -5.1 | 23.1 | 0 | 2020-12-04 | 2.4 | 15.6 | 0 | 2019-12-04 | 0.2 | 17.8 | 0 | 2018-12-04 | -5.4 | 23.4 | 0 | 2017-12-04 | 2.5 | 15.5 | 0 | 2016-12-04 | 0.5 | 17.5 | 0 | 19.83 | 0
2025-12-04 | -12.5 | 30.5 | 0 | 2024-12-04 | -1.8 | 19.8 | 0 | 2023-12-04 | -1.7 | 19.7 | 0 | 2022-12-04 | 1 | 17 | 0 | 2021-12-04 | -5.6 | 23.6 | 0 | 2020-12-04 | 2.4 | 15.6 | 0 | 2019-12-04 | 0.4 | 17.6 | 0 | 2018-12-04 | -5.7 | 23.7 | 0 | 2017-12-04 | 2.5 | 15.5 | 0 | 2016-12-04 | 0 | 18 | 0 | 20.1 | 0
2025-12-04 | -13.9 | 31.9 | 0 | 2024-12-04 | -1.9 | 19.9 | 0 | 2023-12-04 | -2.1 | 20.1 | 0 | 2022-12-04 | 0.6 | 17.4 | 0 | 2021-12-04 | -6.1 | 24.1 | 0 | 2020-12-04 | 1.5 | 16.5 | 0 | 2019-12-04 | 0.2 | 17.8 | 0 | 2018-12-04 | -5.9 | 23.9 | 0 | 2017-12-04 | 2.3 | 15.7 | 0 | 2016-12-04 | -0.6 | 18.6 | 0 | 20.59 | 0
2025-12-04 | -14.5 | 32.5 | 0 | 2024-12-04 | -2 | 20 | 0 | 2023-12-04 | -2.3 | 20.3 | 0 | 2022-12-04 | -1 | 19 | 0 | 2021-12-04 | -8.2 | 26.2 | 0 | 2020-12-04 | 0.6 | 17.4 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -7.3 | 25.3 | 0 | 2017-12-04 | 2.2 | 15.8 | 0 | 2016-12-04 | -2.6 | 20.6 | 0 | 21.51 | 0
2025-12-04 | -15.6 | 33.6 | 0 | 2024-12-04 | -2 | 20 | 0 | 2023-12-04 | -2.5 | 20.5 | 0 | 2022-12-04 | -0.5 | 18.5 | 0 | 2021-12-04 | -7.2 | 25.2 | 0 | 2020-12-04 | 0.8 | 17.2 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -8.1 | 26.1 | 0 | 2017-12-04 | 1.9 | 16.1 | 0 | 2016-12-04 | -2.9 | 20.9 | 0 | 21.61 | 0
2025-12-04 | -16.9 | 34.9 | 0 | 2024-12-04 | -2.2 | 20.2 | 0 | 2023-12-04 | -2.5 | 20.5 | 0 | 2022-12-04 | -1 | 19 | 0 | 2021-12-04 | -6.7 | 24.7 | 0 | 2020-12-04 | 0.7 | 17.3 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -8.4 | 26.4 | 0 | 2017-12-04 | 1.8 | 16.2 | 0 | 2016-12-04 | -4.8 | 22.8 | 0 | 22 | 0
2025-12-04 | -18 | 36 | 0 | 2024-12-04 | -1.9 | 19.9 | 0 | 2023-12-04 | -2.6 | 20.6 | 0 | 2022-12-04 | -0.8 | 18.8 | 0 | 2021-12-04 | -7.7 | 25.7 | 0 | 2020-12-04 | 0.6 | 17.4 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -7.5 | 25.5 | 0 | 2017-12-04 | 2 | 16 | 0 | 2016-12-04 | -5.1 | 23.1 | 0 | 22.1 | 0
2025-12-04 | -16.7 | 34.7 | 0 | 2024-12-04 | -2.2 | 20.2 | 0 | 2023-12-04 | -3.1 | 21.1 | 0 | 2022-12-04 | -1.5 | 19.5 | 0 | 2021-12-04 | -9 | 27 | 0 | 2020-12-04 | 0.7 | 17.3 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -7.2 | 25.2 | 0 | 2017-12-04 | 2.3 | 15.7 | 0 | 2016-12-04 | -4.9 | 22.9 | 0 | 22.16 | 0
2025-12-04 | -18 | 36 | 0 | 2024-12-04 | -2.2 | 20.2 | 0 | 2023-12-04 | -3.2 | 21.2 | 0 | 2022-12-04 | -1.2 | 19.2 | 0 | 2021-12-04 | -8.2 | 26.2 | 0 | 2020-12-04 | 0.8 | 17.2 | 0 | 2019-12-04 | 0 | 18 | 0 | 2018-12-04 | -6.8 | 24.8 | 0 | 2017-12-04 | 2.8 | 15.2 | 0 | 2016-12-04 | -4.8 | 22.8 | 0 | 22.08 | 0
2025-12-04 | -19.3 | 37.3 | 0 | 2024-12-04 | -2.1 | 20.1 | 0 | 2023-12-04 | -3.6 | 21.6 | 0 | 2022-12-04 | -0.8 | 18.8 | 0 | 2021-12-04 | -6.9 | 24.9 | 0 | 2020-12-04 | 0.9 | 17.1 | 0 | 2019-12-04 | -0.4 | 18.4 | 0 | 2018-12-04 | -6.5 | 24.5 | 0 | 2017-12-04 | 3.2 | 14.8 | 0 | 2016-12-04 | -5.5 | 23.5 | 0 | 22.1 | 0
2025-12-05 | -18.6 | 36.6 | 0 | 2024-12-05 | -2 | 20 | 0 | 2023-12-05 | -3.1 | 21.1 | 0 | 2022-12-05 | -0.6 | 18.6 | 0 | 2021-12-05 | -7 | 25 | 0 | 2020-12-05 | 0.7 | 17.3 | 0 | 2019-12-05 | -0.8 | 18.8 | 0 | 2018-12-05 | -6.7 | 24.7 | 0 | 2017-12-05 | 3.1 | 14.9 | 0 | 2016-12-05 | -4.9 | 22.9 | 0 | 21.99 | 0
2025-12-05 | -19.1 | 37.1 | 0 | 2024-12-05 | -1.7 | 19.7 | 0 | 2023-12-05 | -3.3 | 21.3 | 0 | 2022-12-05 | -0.3 | 18.3 | 0 | 2021-12-05 | -8.7 | 26.7 | 0 | 2020-12-05 | 0.5 | 17.5 | 0 | 2019-12-05 | -0.9 | 18.9 | 0 | 2018-12-05 | -6.6 | 24.6 | 0 | 2017-12-05 | 3.6 | 14.4 | 0 | 2016-12-05 | -4.5 | 22.5 | 0 | 22.1 | 0
2025-12-05 | -20.9 | 38.9 | 0 | 2024-12-05 | -1.5 | 19.5 | 0 | 2023-12-05 | -3 | 21 | 0 | 2022-12-05 | 0.3 | 17.7 | 0 | 2021-12-05 | -10.2 | 28.2 | 0 | 2020-12-05 | 0.5 | 17.5 | 0 | 2019-12-05 | -0.6 | 18.6 | 0 | 2018-12-05 | -6.4 | 24.4 | 0 | 2017-12-05 | 3.2 | 14.8 | 0 | 2016-12-05 | -4.2 | 22.2 | 0 | 22.28 | 0
2025-12-05 | -20.5 | 38.5 | 0 | 2024-12-05 | -1.7 | 19.7 | 0 | 2023-12-05 | -3.1 | 21.1 | 0 | 2022-12-05 | 0.4 | 17.6 | 0 | 2021-12-05 | -8.7 | 26.7 | 0 | 2020-12-05 | 0.5 | 17.5 | 0 | 2019-12-05 | -1.2 | 19.2 | 0 | 2018-12-05 | -6.6 | 24.6 | 0 | 2017-12-05 | 3.9 | 14.1 | 0 | 2016-12-05 | -3.8 | 21.8 | 0 | 22.08 | 0
2025-12-05 | -21 | 39 | 0 | 2024-12-05 | -1.4 | 19.4 | 0 | 2023-12-05 | -3.2 | 21.2 | 0 | 2022-12-05 | 0.5 | 17.5 | 0 | 2021-12-05 | -10.4 | 28.4 | 0 | 2020-12-05 | 0.4 | 17.6 | 0 | 2019-12-05 | -0.8 | 18.8 | 0 | 2018-12-05 | -6.4 | 24.4 | 0 | 2017-12-05 | 6.2 | 11.8 | 0 | 2016-12-05 | -3.8 | 21.8 | 0 | 21.99 | 0
2025-12-05 | -20.1 | 38.1 | 0 | 2024-12-05 | -1.5 | 19.5 | 0 | 2023-12-05 | -3 | 21 | 0 | 2022-12-05 | 0.9 | 17.1 | 0 | 2021-12-05 | -10.5 | 28.5 | 0 | 2020-12-05 | 0.4 | 17.6 | 0 | 2019-12-05 | -0.7 | 18.7 | 0 | 2018-12-05 | -6.2 | 24.2 | 0 | 2017-12-05 | 6.6 | 11.4 | 0 | 2016-12-05 | -3.7 | 21.7 | 0 | 21.78 | 0
2025-12-05 | -20.3 | 38.3 | 0 | 2024-12-05 | -1.3 | 19.3 | 0 | 2023-12-05 | -2.9 | 20.9 | 0 | 2022-12-05 | 0.8 | 17.2 | 0 | 2021-12-05 | -12.3 | 30.3 | 0 | 2020-12-05 | 0.5 | 17.5 | 0 | 2019-12-05 | -1.3 | 19.3 | 0 | 2018-12-05 | -6.1 | 24.1 | 0 | 2017-12-05 | 7.1 | 10.9 | 0 | 2016-12-05 | -3.6 | 21.6 | 0 | 21.94 | 0
2025-12-05 | -19.7 | 37.7 | 0 | 2024-12-05 | -0.9 | 18.9 | 0 | 2023-12-05 | -3 | 21 | 0 | 2022-12-05 | 0.4 | 17.6 | 0 | 2021-12-05 | -10.5 | 28.5 | 0 | 2020-12-05 | 0.6 | 17.4 | 0 | 2019-12-05 | -2.9 | 20.9 | 0 | 2018-12-05 | -6.1 | 24.1 | 0 | 2017-12-05 | 6.6 | 11.4 | 0 | 2016-12-05 | -3.5 | 21.5 | 0 | 21.9 | 0
2025-12-05 | -18.9 | 36.9 | 0 | 2024-12-05 | -0.9 | 18.9 | 0 | 2023-12-05 | -3.2 | 21.2 | 0 | 2022-12-05 | 0.5 | 17.5 | 0 | 2021-12-05 | -9.9 | 27.9 | 0 | 2020-12-05 | 1 | 17 | 0 | 2019-12-05 | -3.3 | 21.3 | 0 | 2018-12-05 | -6 | 24 | 0 | 2017-12-05 | 7.2 | 10.8 | 0 | 2016-12-05 | -3.8 | 21.8 | 0 | 21.73 | 0
2025-12-05 | -16.6 | 34.6 | 0 | 2024-12-05 | -0.2 | 18.2 | 0 | 2023-12-05 | -3.2 | 21.2 | 0 | 2022-12-05 | 0.8 | 17.2 | 0 | 2021-12-05 | -9.2 | 27.2 | 0 | 2020-12-05 | 0.9 | 17.1 | 0 | 2019-12-05 | -3.5 | 21.5 | 0 | 2018-12-05 | -5.7 | 23.7 | 0 | 2017-12-05 | 7.2 | 10.8 | 0 | 2016-12-05 | -4 | 22 | 0 | 21.35 | 0
2025-12-05 | -14.2 | 32.2 | 0 | 2024-12-05 | 0 | 18 | 0 | 2023-12-05 | -3.4 | 21.4 | 0 | 2022-12-05 | 1.9 | 16.1 | 0 | 2021-12-05 | -7.1 | 25.1 | 0 | 2020-12-05 | 0 | 18 | 0 | 2019-12-05 | -3.6 | 21.6 | 0 | 2018-12-05 | -5.2 | 23.2 | 0 | 2017-12-05 | 7 | 11 | 0 | 2016-12-05 | -3.6 | 21.6 | 0 | 20.82 | 0
2025-12-05 | -11.5 | 29.5 | 0 | 2024-12-05 | 0.2 | 17.8 | 0 | 2023-12-05 | -3.3 | 21.3 | 0 | 2022-12-05 | 3 | 15 | 0 | 2021-12-05 | -5.2 | 23.2 | 0 | 2020-12-05 | -0.6 | 18.6 | 0 | 2019-12-05 | -4.2 | 22.2 | 0 | 2018-12-05 | -4.8 | 22.8 | 0 | 2017-12-05 | 7.4 | 10.6 | 0 | 2016-12-05 | -3 | 21 | 0 | 20.2 | 0
2025-12-05 | -11 | 29 | 0 | 2024-12-05 | 0 | 18 | 0 | 2023-12-05 | -3.4 | 21.4 | 0 | 2022-12-05 | 3.5 | 14.5 | 0 | 2021-12-05 | -4 | 22 | 0 | 2020-12-05 | -0.6 | 18.6 | 0 | 2019-12-05 | -4.3 | 22.3 | 0 | 2018-12-05 | -4.4 | 22.4 | 0 | 2017-12-05 | 8 | 10 | 0 | 2016-12-05 | -3 | 21 | 0 | 19.92 | 0
2025-12-05 | -10 | 28 | 0 | 2024-12-05 | 0 | 18 | 0 | 2023-12-05 | -3.4 | 21.4 | 0 | 2022-12-05 | 5.5 | 12.5 | 0 | 2021-12-05 | -2.9 | 20.9 | 0 | 2020-12-05 | -1.3 | 19.3 | 0 | 2019-12-05 | -4.2 | 22.2 | 0 | 2018-12-05 | -4.2 | 22.2 | 0 | 2017-12-05 | 8.4 | 9.6 | 0 | 2016-12-05 | -2.8 | 20.8 | 0 | 19.49 | 0
2025-12-05 | -10.7 | 28.7 | 0 | 2024-12-05 | 0.1 | 17.9 | 0 | 2023-12-05 | -3.5 | 21.5 | 0 | 2022-12-05 | 4.7 | 13.3 | 0 | 2021-12-05 | -3.3 | 21.3 | 0 | 2020-12-05 | -1.8 | 19.8 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4 | 22 | 0 | 2017-12-05 | 9 | 9 | 0 | 2016-12-05 | -2.7 | 20.7 | 0 | 19.61 | 0
2025-12-05 | -10.7 | 28.7 | 0 | 2024-12-05 | 0 | 18 | 0 | 2023-12-05 | -3.4 | 21.4 | 0 | 2022-12-05 | 4.2 | 13.8 | 0 | 2021-12-05 | -4 | 22 | 0 | 2020-12-05 | -2.4 | 20.4 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4 | 22 | 0 | 2017-12-05 | 9.8 | 8.2 | 0 | 2016-12-05 | -3.2 | 21.2 | 0 | 19.76 | 0
2025-12-05 | -10.9 | 28.9 | 0 | 2024-12-05 | -0.1 | 18.1 | 0 | 2023-12-05 | -3.6 | 21.6 | 0 | 2022-12-05 | 4 | 14 | 0 | 2021-12-05 | -4.4 | 22.4 | 0 | 2020-12-05 | -3.2 | 21.2 | 0 | 2019-12-05 | -4.3 | 22.3 | 0 | 2018-12-05 | -4 | 22 | 0 | 2017-12-05 | 10 | 8 | 0 | 2016-12-05 | -3.3 | 21.3 | 0 | 19.98 | 0
2025-12-05 | -10.4 | 28.4 | 0 | 2024-12-05 | -1.6 | 19.6 | 0 | 2023-12-05 | -3.9 | 21.9 | 0 | 2022-12-05 | 4 | 14 | 0 | 2021-12-05 | -4.7 | 22.7 | 0 | 2020-12-05 | -3.6 | 21.6 | 0 | 2019-12-05 | -4.1 | 22.1 | 0 | 2018-12-05 | -4.2 | 22.2 | 0 | 2017-12-05 | 10.3 | 7.7 | 0 | 2016-12-05 | -3.7 | 21.7 | 0 | 20.19 | 0
2025-12-05 | -10.5 | 28.5 | 0 | 2024-12-05 | -2.3 | 20.3 | 0 | 2023-12-05 | -4.4 | 22.4 | 0 | 2022-12-05 | 3.6 | 14.4 | 0 | 2021-12-05 | -4.7 | 22.7 | 0 | 2020-12-05 | -3.8 | 21.8 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4.2 | 22.2 | 0 | 2017-12-05 | 10.3 | 7.7 | 0 | 2016-12-05 | -3 | 21 | 0 | 20.29 | 0
2025-12-05 | -10.4 | 28.4 | 0 | 2024-12-05 | -2.5 | 20.5 | 0 | 2023-12-05 | -4.8 | 22.8 | 0 | 2022-12-05 | 3.4 | 14.6 | 0 | 2021-12-05 | -4.8 | 22.8 | 0 | 2020-12-05 | -3.5 | 21.5 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4.3 | 22.3 | 0 | 2017-12-05 | 9.4 | 8.6 | 0 | 2016-12-05 | -2.7 | 20.7 | 0 | 20.41 | 0
2025-12-05 | -9.8 | 27.8 | 0 | 2024-12-05 | -3.2 | 21.2 | 0 | 2023-12-05 | -5.2 | 23.2 | 0 | 2022-12-05 | 3.5 | 14.5 | 0 | 2021-12-05 | -5.7 | 23.7 | 0 | 2020-12-05 | -3.5 | 21.5 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4.5 | 22.5 | 0 | 2017-12-05 | 7.6 | 10.4 | 0 | 2016-12-05 | -2.4 | 20.4 | 0 | 20.71 | 0
2025-12-05 | -9.2 | 27.2 | 0 | 2024-12-05 | -3.9 | 21.9 | 0 | 2023-12-05 | -5.2 | 23.2 | 0 | 2022-12-05 | 4 | 14 | 0 | 2021-12-05 | -5.8 | 23.8 | 0 | 2020-12-05 | -4.1 | 22.1 | 0 | 2019-12-05 | -3.9 | 21.9 | 0 | 2018-12-05 | -4.5 | 22.5 | 0 | 2017-12-05 | 6.2 | 11.8 | 0 | 2016-12-05 | -2.7 | 20.7 | 0 | 20.91 | 0
2025-12-05 | -9.1 | 27.1 | 0 | 2024-12-05 | -4.1 | 22.1 | 0 | 2023-12-05 | -5.4 | 23.4 | 0 | 2022-12-05 | 4.2 | 13.8 | 0 | 2021-12-05 | -5.6 | 23.6 | 0 | 2020-12-05 | -4.5 | 22.5 | 0 | 2019-12-05 | -4.2 | 22.2 | 0 | 2018-12-05 | -5.4 | 23.4 | 0 | 2017-12-05 | 5.9 | 12.1 | 0 | 2016-12-05 | -5.8 | 23.8 | 0 | 21.4 | 0
2025-12-05 | -8.3 | 26.3 | 0 | 2024-12-05 | -5 | 23 | 0 | 2023-12-05 | -5.7 | 23.7 | 0 | 2022-12-05 | 4.4 | 13.6 | 0 | 2021-12-05 | -5.6 | 23.6 | 0 | 2020-12-05 | -4.1 | 22.1 | 0 | 2019-12-05 | -4.4 | 22.4 | 0 | 2018-12-05 | -7.4 | 25.4 | 0 | 2017-12-05 | 5.2 | 12.8 | 0 | 2016-12-05 | -3.3 | 21.3 | 0 | 21.42 | 0
2025-12-06 | -8.6 | 26.6 | 0 | 2024-12-06 | -5.4 | 23.4 | 0 | 2023-12-06 | -5.8 | 23.8 | 0 | 2022-12-06 | 4.8 | 13.2 | 0 | 2021-12-06 | -5.4 | 23.4 | 0 | 2020-12-06 | -3.6 | 21.6 | 0 | 2019-12-06 | -4.3 | 22.3 | 0 | 2018-12-06 | -8 | 26 | 0 | 2017-12-06 | 4.4 | 13.6 | 0 | 2016-12-06 | -2.7 | 20.7 | 0 | 21.46 | 0
2025-12-06 | -7.4 | 25.4 | 0 | 2024-12-06 | -6.5 | 24.5 | 0 | 2023-12-06 | -6.2 | 24.2 | 0 | 2022-12-06 | 4.4 | 13.6 | 0 | 2021-12-06 | -5.2 | 23.2 | 0 | 2020-12-06 | -3.7 | 21.7 | 0 | 2019-12-06 | -4.5 | 22.5 | 0 | 2018-12-06 | -9.8 | 27.8 | 0 | 2017-12-06 | 3.6 | 14.4 | 0 | 2016-12-06 | -2.4 | 20.4 | 0 | 21.77 | 0
2025-12-06 | -5.5 | 23.5 | 0 | 2024-12-06 | -6.3 | 24.3 | 0 | 2023-12-06 | -6.3 | 24.3 | 0 | 2022-12-06 | 4 | 14 | 0 | 2021-12-06 | -4.5 | 22.5 | 0 | 2020-12-06 | -4 | 22 | 0 | 2019-12-06 | -4.5 | 22.5 | 0 | 2018-12-06 | -10.7 | 28.7 | 0 | 2017-12-06 | 1.4 | 16.6 | 0 | 2016-12-06 | -3.3 | 21.3 | 0 | 21.97 | 0
2025-12-06 | -5.2 | 23.2 | 0 | 2024-12-06 | -6.6 | 24.6 | 0 | 2023-12-06 | -6.6 | 24.6 | 0 | 2022-12-06 | 4.4 | 13.6 | 0 | 2021-12-06 | -3.5 | 21.5 | 0 | 2020-12-06 | -3.8 | 21.8 | 0 | 2019-12-06 | -4.8 | 22.8 | 0 | 2018-12-06 | -8.8 | 26.8 | 0 | 2017-12-06 | 1.1 | 16.9 | 0 | 2016-12-06 | -2.6 | 20.6 | 0 | 21.64 | 0
2025-12-06 | -4.9 | 22.9 | 0 | 2024-12-06 | -7 | 25 | 0 | 2023-12-06 | -7 | 25 | 0 | 2022-12-06 | 4.3 | 13.7 | 0 | 2021-12-06 | -3.6 | 21.6 | 0 | 2020-12-06 | -4.3 | 22.3 | 0 | 2019-12-06 | -5.4 | 23.4 | 0 | 2018-12-06 | -7.5 | 25.5 | 0 | 2017-12-06 | 0.4 | 17.6 | 0 | 2016-12-06 | -2.4 | 20.4 | 0 | 21.74 | 0
2025-12-06 | -4.7 | 22.7 | 0 | 2024-12-06 | -8 | 26 | 0 | 2023-12-06 | -7.6 | 25.6 | 0 | 2022-12-06 | 3.3 | 14.7 | 0 | 2021-12-06 | -2.8 | 20.8 | 0 | 2020-12-06 | -4.6 | 22.6 | 0 | 2019-12-06 | -5.6 | 23.6 | 0 | 2018-12-06 | -6.6 | 24.6 | 0 | 2017-12-06 | -0.3 | 18.3 | 0 | 2016-12-06 | -2.2 | 20.2 | 0 | 21.91 | 0
2025-12-06 | -4.3 | 22.3 | 0 | 2024-12-06 | -8.8 | 26.8 | 0 | 2023-12-06 | -8.6 | 26.6 | 0 | 2022-12-06 | 3.2 | 14.8 | 0 | 2021-12-06 | -1.9 | 19.9 | 0 | 2020-12-06 | -5.1 | 23.1 | 0 | 2019-12-06 | -5.7 | 23.7 | 0 | 2018-12-06 | -6 | 24 | 0 | 2017-12-06 | -0.7 | 18.7 | 0 | 2016-12-06 | -1.4 | 19.4 | 0 | 21.93 | 0
2025-12-06 | -4.1 | 22.1 | 0 | 2024-12-06 | -9.1 | 27.1 | 0 | 2023-12-06 | -9.9 | 27.9 | 0 | 2022-12-06 | 3.5 | 14.5 | 0 | 2021-12-06 | -1.2 | 19.2 | 0 | 2020-12-06 | -5.2 | 23.2 | 0 | 2019-12-06 | -5.8 | 23.8 | 0 | 2018-12-06 | -5 | 23 | 0 | 2017-12-06 | -0.2 | 18.2 | 0 | 2016-12-06 | -3.8 | 21.8 | 0 | 22.08 | 0
2025-12-06 | -4 | 22 | 0 | 2024-12-06 | -9.2 | 27.2 | 0 | 2023-12-06 | -12.1 | 30.1 | 0 | 2022-12-06 | 3.6 | 14.4 | 0 | 2021-12-06 | -0.3 | 18.3 | 0 | 2020-12-06 | -5.5 | 23.5 | 0 | 2019-12-06 | -5.9 | 23.9 | 0 | 2018-12-06 | -4.2 | 22.2 | 0 | 2017-12-06 | -0.1 | 18.1 | 0 | 2016-12-06 | -5 | 23 | 0 | 22.27 | 0
2025-12-06 | -3.2 | 21.2 | 0 | 2024-12-06 | -9.1 | 27.1 | 0 | 2023-12-06 | -11.9 | 29.9 | 0 | 2022-12-06 | 3.2 | 14.8 | 0 | 2021-12-06 | 0.2 | 17.8 | 0 | 2020-12-06 | -4.4 | 22.4 | 0 | 2019-12-06 | -5.6 | 23.6 | 0 | 2018-12-06 | -3.3 | 21.3 | 0 | 2017-12-06 | 0.4 | 17.6 | 0 | 2016-12-06 | -3.2 | 21.2 | 0 | 21.69 | 0
2025-12-06 | -2.5 | 20.5 | 0 | 2024-12-06 | -9.1 | 27.1 | 0 | 2023-12-06 | -11.1 | 29.1 | 0 | 2022-12-06 | 4 | 14 | 0 | 2021-12-06 | 0.4 | 17.6 | 0 | 2020-12-06 | -3.9 | 21.9 | 0 | 2019-12-06 | -5.3 | 23.3 | 0 | 2018-12-06 | -2.2 | 20.2 | 0 | 2017-12-06 | 0.8 | 17.2 | 0 | 2016-12-06 | -1.4 | 19.4 | 0 | 21.03 | 0
2025-12-06 | -2.2 | 20.2 | 0 | 2024-12-06 | -8 | 26 | 0 | 2023-12-06 | -10.7 | 28.7 | 0 | 2022-12-06 | 4.5 | 13.5 | 0 | 2021-12-06 | 2 | 16 | 0 | 2020-12-06 | -3.4 | 21.4 | 0 | 2019-12-06 | -4.9 | 22.9 | 0 | 2018-12-06 | -0.8 | 18.8 | 0 | 2017-12-06 | 1.2 | 16.8 | 0 | 2016-12-06 | 0.4 | 17.6 | 0 | 20.19 | 0
2025-12-06 | -1.4 | 19.4 | 0 | 2024-12-06 | -7.9 | 25.9 | 0 | 2023-12-06 | -10.8 | 28.8 | 0 | 2022-12-06 | 4.6 | 13.4 | 0 | 2021-12-06 | 5 | 13 | 0 | 2020-12-06 | -2.6 | 20.6 | 0 | 2019-12-06 | -4.5 | 22.5 | 0 | 2018-12-06 | 0 | 18 | 0 | 2017-12-06 | 1.9 | 16.1 | 0 | 2016-12-06 | -0.1 | 18.1 | 0 | 19.58 | 0
2025-12-06 | -1 | 19 | 0 | 2024-12-06 | -7.9 | 25.9 | 0 | 2023-12-06 | -10.9 | 28.9 | 0 | 2022-12-06 | 4.2 | 13.8 | 0 | 2021-12-06 | 6.6 | 11.4 | 0 | 2020-12-06 | -1.9 | 19.9 | 0 | 2019-12-06 | -4.3 | 22.3 | 0 | 2018-12-06 | 0.3 | 17.7 | 0 | 2017-12-06 | 2.5 | 15.5 | 0 | 2016-12-06 | 1.5 | 16.5 | 0 | 19.09 | 0
2025-12-06 | 0.1 | 17.9 | 0 | 2024-12-06 | -7.8 | 25.8 | 0 | 2023-12-06 | -10.9 | 28.9 | 0 | 2022-12-06 | 3.6 | 14.4 | 0 | 2021-12-06 | 7.3 | 10.7 | 0 | 2020-12-06 | -2.2 | 20.2 | 0 | 2019-12-06 | -4.3 | 22.3 | 0 | 2018-12-06 | 0 | 18 | 0 | 2017-12-06 | 2.5 | 15.5 | 0 | 2016-12-06 | 0.9 | 17.1 | 0 | 19.08 | 0
2025-12-06 | 0 | 18 | 0 | 2024-12-06 | -7.8 | 25.8 | 0 | 2023-12-06 | -10.6 | 28.6 | 0 | 2022-12-06 | 3.1 | 14.9 | 0 | 2021-12-06 | 7.1 | 10.9 | 0 | 2020-12-06 | -2.8 | 20.8 | 0 | 2019-12-06 | -4.5 | 22.5 | 0 | 2018-12-06 | -0.4 | 18.4 | 0 | 2017-12-06 | 2.2 | 15.8 | 0 | 2016-12-06 | 0.6 | 17.4 | 0 | 19.31 | 0
2025-12-06 | 0 | 18 | 0 | 2024-12-06 | -8.5 | 26.5 | 0 | 2023-12-06 | -10.8 | 28.8 | 0 | 2022-12-06 | 2.7 | 15.3 | 0 | 2021-12-06 | 5.9 | 12.1 | 0 | 2020-12-06 | -2.4 | 20.4 | 0 | 2019-12-06 | -4.4 | 22.4 | 0 | 2018-12-06 | -0.3 | 18.3 | 0 | 2017-12-06 | 1.4 | 16.6 | 0 | 2016-12-06 | -1.3 | 19.3 | 0 | 19.77 | 0
2025-12-06 | 0 | 18 | 0 | 2024-12-06 | -9 | 27 | 0 | 2023-12-06 | -12 | 30 | 0 | 2022-12-06 | 2.4 | 15.6 | 0 | 2021-12-06 | 4.4 | 13.6 | 0 | 2020-12-06 | -3.1 | 21.1 | 0 | 2019-12-06 | -4.6 | 22.6 | 0 | 2018-12-06 | -1.5 | 19.5 | 0 | 2017-12-06 | 1.1 | 16.9 | 0 | 2016-12-06 | -0.7 | 18.7 | 0 | 20.3 | 0
2025-12-06 | -0.2 | 18.2 | 0 | 2024-12-06 | -8.6 | 26.6 | 0 | 2023-12-06 | -12.8 | 30.8 | 0 | 2022-12-06 | 2.4 | 15.6 | 0 | 2021-12-06 | 3.2 | 14.8 | 0 | 2020-12-06 | -3.7 | 21.7 | 0 | 2019-12-06 | -7.1 | 25.1 | 0 | 2018-12-06 | -1.9 | 19.9 | 0 | 2017-12-06 | 0.9 | 17.1 | 0 | 2016-12-06 | -1 | 19 | 0 | 20.88 | 0
2025-12-06 | -1.6 | 19.6 | 0 | 2024-12-06 | -8.6 | 26.6 | 0 | 2023-12-06 | -12.5 | 30.5 | 0 | 2022-12-06 | 1.8 | 16.2 | 0 | 2021-12-06 | 2.6 | 15.4 | 0 | 2020-12-06 | -4.3 | 22.3 | 0 | 2019-12-06 | -7.8 | 25.8 | 0 | 2018-12-06 | -1.6 | 19.6 | 0 | 2017-12-06 | 0.5 | 17.5 | 0 | 2016-12-06 | -1.5 | 19.5 | 0 | 21.3 | 0
2025-12-06 | -2.5 | 20.5 | 0 | 2024-12-06 | -9.3 | 27.3 | 0 | 2023-12-06 | -13.4 | 31.4 | 0 | 2022-12-06 | 1.8 | 16.2 | 0 | 2021-12-06 | 1.6 | 16.4 | 0 | 2020-12-06 | -4.7 | 22.7 | 0 | 2019-12-06 | -7.7 | 25.7 | 0 | 2018-12-06 | -1.8 | 19.8 | 0 | 2017-12-06 | 0.8 | 17.2 | 0 | 2016-12-06 | -1.6 | 19.6 | 0 | 21.68 | 0
2025-12-06 | -4.4 | 22.4 | 0 | 2024-12-06 | -9.1 | 27.1 | 0 | 2023-12-06 | -14.1 | 32.1 | 0 | 2022-12-06 | 1.7 | 16.3 | 0 | 2021-12-06 | 1.5 | 16.5 | 0 | 2020-12-06 | -4.6 | 22.6 | 0 | 2019-12-06 | -8.6 | 26.6 | 0 | 2018-12-06 | -1.1 | 19.1 | 0 | 2017-12-06 | 0 | 18 | 0 | 2016-12-06 | -1.7 | 19.7 | 0 | 22.04 | 0
2025-12-06 | -5.7 | 23.7 | 0 | 2024-12-06 | -8.6 | 26.6 | 0 | 2023-12-06 | -14.6 | 32.6 | 0 | 2022-12-06 | 2 | 16 | 0 | 2021-12-06 | 1.2 | 16.8 | 0 | 2020-12-06 | -4.8 | 22.8 | 0 | 2019-12-06 | -7.3 | 25.3 | 0 | 2018-12-06 | -1.9 | 19.9 | 0 | 2017-12-06 | 0 | 18 | 0 | 2016-12-06 | -1.8 | 19.8 | 0 | 22.15 | 0
2025-12-06 | -7.7 | 25.7 | 0 | 2024-12-06 | -8.5 | 26.5 | 0 | 2023-12-06 | -15.2 | 33.2 | 0 | 2022-12-06 | 2.1 | 15.9 | 0 | 2021-12-06 | 0.9 | 17.1 | 0 | 2020-12-06 | -5 | 23 | 0 | 2019-12-06 | -8 | 26 | 0 | 2018-12-06 | -2.9 | 20.9 | 0 | 2017-12-06 | -0.2 | 18.2 | 0 | 2016-12-06 | -1.8 | 19.8 | 0 | 22.63 | 0
2025-12-07 | -8.8 | 26.8 | 0 | 2024-12-07 | -8.3 | 26.3 | 0 | 2023-12-07 | -14.1 | 32.1 | 0 | 2022-12-07 | 2.2 | 15.8 | 0 | 2021-12-07 | -0.5 | 18.5 | 0 | 2020-12-07 | -5.2 | 23.2 | 0 | 2019-12-07 | -7.7 | 25.7 | 0 | 2018-12-07 | -5.2 | 23.2 | 0 | 2017-12-07 | -0.6 | 18.6 | 0 | 2016-12-07 | -1.9 | 19.9 | 0 | 23.01 | 0
2025-12-07 | -10 | 28 | 0 | 2024-12-07 | -7.7 | 25.7 | 0 | 2023-12-07 | -14.5 | 32.5 | 0 | 2022-12-07 | 2.7 | 15.3 | 0 | 2021-12-07 | -2.4 | 20.4 | 0 | 2020-12-07 | -5.4 | 23.4 | 0 | 2019-12-07 | -7.5 | 25.5 | 0 | 2018-12-07 | -6.7 | 24.7 | 0 | 2017-12-07 | -1.1 | 19.1 | 0 | 2016-12-07 | -2.2 | 20.2 | 0 | 23.48 | 0
2025-12-07 | -10.4 | 28.4 | 0 | 2024-12-07 | -7.5 | 25.5 | 0 | 2023-12-07 | -14.2 | 32.2 | 0 | 2022-12-07 | 2.8 | 15.2 | 0 | 2021-12-07 | -4.4 | 22.4 | 0 | 2020-12-07 | -5.5 | 23.5 | 0 | 2019-12-07 | -8.2 | 26.2 | 0 | 2018-12-07 | -7.6 | 25.6 | 0 | 2017-12-07 | -1.6 | 19.6 | 0 | 2016-12-07 | -2.2 | 20.2 | 0 | 23.88 | 0
2025-12-07 | -11.8 | 29.8 | 0 | 2024-12-07 | -7.7 | 25.7 | 0 | 2023-12-07 | -13.4 | 31.4 | 0 | 2022-12-07 | 3.1 | 14.9 | 0 | 2021-12-07 | -5.4 | 23.4 | 0 | 2020-12-07 | -5.7 | 23.7 | 0 | 2019-12-07 | -8.5 | 26.5 | 0 | 2018-12-07 | -8.6 | 26.6 | 0 | 2017-12-07 | -0.9 | 18.9 | 0 | 2016-12-07 | -2 | 20 | 0 | 24.09 | 0
2025-12-07 | -11.3 | 29.3 | 0 | 2024-12-07 | -7.4 | 25.4 | 0 | 2023-12-07 | -13.2 | 31.2 | 0 | 2022-12-07 | 3.2 | 14.8 | 0 | 2021-12-07 | -6.1 | 24.1 | 0 | 2020-12-07 | -5.8 | 23.8 | 0 | 2019-12-07 | -9 | 27 | 0 | 2018-12-07 | -9.4 | 27.4 | 0 | 2017-12-07 | -1.2 | 19.2 | 0 | 2016-12-07 | -2.2 | 20.2 | 0 | 24.24 | 0
2025-12-07 | -11.5 | 29.5 | 0 | 2024-12-07 | -7 | 25 | 0 | 2023-12-07 | -13 | 31 | 0 | 2022-12-07 | 3.5 | 14.5 | 0 | 2021-12-07 | -7.1 | 25.1 | 0 | 2020-12-07 | -5.9 | 23.9 | 0 | 2019-12-07 | -8.1 | 26.1 | 0 | 2018-12-07 | -10.5 | 28.5 | 0 | 2017-12-07 | -1.1 | 19.1 | 0 | 2016-12-07 | -2.2 | 20.2 | 0 | 24.29 | 0
2025-12-07 | -11.6 | 29.6 | 0 | 2024-12-07 | -6.6 | 24.6 | 0 | 2023-12-07 | -12.1 | 30.1 | 0 | 2022-12-07 | 3.6 | 14.4 | 0 | 2021-12-07 | -8 | 26 | 0 | 2020-12-07 | -6.3 | 24.3 | 0 | 2019-12-07 | -9.3 | 27.3 | 0 | 2018-12-07 | -11.3 | 29.3 | 0 | 2017-12-07 | -1.8 | 19.8 | 0 | 2016-12-07 | -2 | 20 | 0 | 24.54 | 0
2025-12-07 | -12.1 | 30.1 | 0 | 2024-12-07 | -7.2 | 25.2 | 0 | 2023-12-07 | -11.8 | 29.8 | 0 | 2022-12-07 | 3.6 | 14.4 | 0 | 2021-12-07 | -8.4 | 26.4 | 0 | 2020-12-07 | -6.6 | 24.6 | 0 | 2019-12-07 | -8.9 | 26.9 | 0 | 2018-12-07 | -11.9 | 29.9 | 0 | 2017-12-07 | -2.5 | 20.5 | 0 | 2016-12-07 | -1.6 | 19.6 | 0 | 24.74 | 0
2025-12-07 | -11.8 | 29.8 | 0 | 2024-12-07 | -7.5 | 25.5 | 0 | 2023-12-07 | -11.7 | 29.7 | 0 | 2022-12-07 | 3.5 | 14.5 | 0 | 2021-12-07 | -8.8 | 26.8 | 0 | 2020-12-07 | -6.7 | 24.7 | 0 | 2019-12-07 | -9.9 | 27.9 | 0 | 2018-12-07 | -12.9 | 30.9 | 0 | 2017-12-07 | -1.9 | 19.9 | 0 | 2016-12-07 | -1.4 | 19.4 | 0 | 24.91 | 0
2025-12-07 | -10.6 | 28.6 | 0 | 2024-12-07 | -7.3 | 25.3 | 0 | 2023-12-07 | -11.4 | 29.4 | 0 | 2022-12-07 | 3.6 | 14.4 | 0 | 2021-12-07 | -7.9 | 25.9 | 0 | 2020-12-07 | -6.6 | 24.6 | 0 | 2019-12-07 | -8.8 | 26.8 | 0 | 2018-12-07 | -13.1 | 31.1 | 0 | 2017-12-07 | -1 | 19 | 0 | 2016-12-07 | -0.6 | 18.6 | 0 | 24.37 | 0
2025-12-07 | -10.4 | 28.4 | 0 | 2024-12-07 | -7.2 | 25.2 | 0 | 2023-12-07 | -10.6 | 28.6 | 0 | 2022-12-07 | 4.1 | 13.9 | 0 | 2021-12-07 | -7.3 | 25.3 | 0 | 2020-12-07 | -6.2 | 24.2 | 0 | 2019-12-07 | -6.5 | 24.5 | 0 | 2018-12-07 | -12.5 | 30.5 | 0 | 2017-12-07 | -0.9 | 18.9 | 0 | 2016-12-07 | -0.3 | 18.3 | 0 | 23.78 | 0
2025-12-07 | -10.3 | 28.3 | 0 | 2024-12-07 | -6.6 | 24.6 | 0 | 2023-12-07 | -10.3 | 28.3 | 0 | 2022-12-07 | 4.1 | 13.9 | 0 | 2021-12-07 | -6.8 | 24.8 | 0 | 2020-12-07 | -6.2 | 24.2 | 0 | 2019-12-07 | -5.8 | 23.8 | 0 | 2018-12-07 | -12.5 | 30.5 | 0 | 2017-12-07 | -0.4 | 18.4 | 0 | 2016-12-07 | 0.6 | 17.4 | 0 | 23.42 | 0
2025-12-07 | -10.2 | 28.2 | 0 | 2024-12-07 | -6.3 | 24.3 | 0 | 2023-12-07 | -9.9 | 27.9 | 0 | 2022-12-07 | 4.2 | 13.8 | 0 | 2021-12-07 | -6.3 | 24.3 | 0 | 2020-12-07 | -5.1 | 23.1 | 0 | 2019-12-07 | -5.2 | 23.2 | 0 | 2018-12-07 | -11.9 | 29.9 | 0 | 2017-12-07 | 0.1 | 17.9 | 0 | 2016-12-07 | 3.5 | 14.5 | 0 | 22.71 | 0
2025-12-07 | -10.2 | 28.2 | 0 | 2024-12-07 | -6.1 | 24.1 | 0 | 2023-12-07 | -9.3 | 27.3 | 0 | 2022-12-07 | 4 | 14 | 0 | 2021-12-07 | -6.3 | 24.3 | 0 | 2020-12-07 | -3.6 | 21.6 | 0 | 2019-12-07 | -5.6 | 23.6 | 0 | 2018-12-07 | -11.8 | 29.8 | 0 | 2017-12-07 | 0.4 | 17.6 | 0 | 2016-12-07 | 4 | 14 | 0 | 22.45 | 0
2025-12-07 | -10.1 | 28.1 | 0 | 2024-12-07 | -6.2 | 24.2 | 0 | 2023-12-07 | -8.9 | 26.9 | 0 | 2022-12-07 | 4.2 | 13.8 | 0 | 2021-12-07 | -6.8 | 24.8 | 0 | 2020-12-07 | -3.2 | 21.2 | 0 | 2019-12-07 | -5.8 | 23.8 | 0 | 2018-12-07 | -11.6 | 29.6 | 0 | 2017-12-07 | 0.3 | 17.7 | 0 | 2016-12-07 | 3.9 | 14.1 | 0 | 22.42 | 0
2025-12-07 | -10.2 | 28.2 | 0 | 2024-12-07 | -6.3 | 24.3 | 0 | 2023-12-07 | -8.8 | 26.8 | 0 | 2022-12-07 | 4.3 | 13.7 | 0 | 2021-12-07 | -7.1 | 25.1 | 0 | 2020-12-07 | -3 | 21 | 0 | 2019-12-07 | -5.6 | 23.6 | 0 | 2018-12-07 | -11.9 | 29.9 | 0 | 2017-12-07 | 0.2 | 17.8 | 0 | 2016-12-07 | 3.1 | 14.9 | 0 | 22.53 | 0
2025-12-07 | -10 | 28 | 0 | 2024-12-07 | -6.6 | 24.6 | 0 | 2023-12-07 | -8.8 | 26.8 | 0 | 2022-12-07 | 4.3 | 13.7 | 0 | 2021-12-07 | -7.2 | 25.2 | 0 | 2020-12-07 | -3.5 | 21.5 | 0 | 2019-12-07 | -6.5 | 24.5 | 0 | 2018-12-07 | -12 | 30 | 0 | 2017-12-07 | -0.2 | 18.2 | 0 | 2016-12-07 | 2.8 | 15.2 | 0 | 22.77 | 0
2025-12-07 | -10.1 | 28.1 | 0 | 2024-12-07 | -7.1 | 25.1 | 0 | 2023-12-07 | -8.6 | 26.6 | 0 | 2022-12-07 | 4.1 | 13.9 | 0 | 2021-12-07 | -7.6 | 25.6 | 0 | 2020-12-07 | -4.2 | 22.2 | 0 | 2019-12-07 | -8.2 | 26.2 | 0 | 2018-12-07 | -12.6 | 30.6 | 0 | 2017-12-07 | -0.6 | 18.6 | 0 | 2016-12-07 | 2.5 | 15.5 | 0 | 23.24 | 0
2025-12-07 | -10.2 | 28.2 | 0 | 2024-12-07 | -7.5 | 25.5 | 0 | 2023-12-07 | -8.6 | 26.6 | 0 | 2022-12-07 | 4.1 | 13.9 | 0 | 2021-12-07 | -8.3 | 26.3 | 0 | 2020-12-07 | -4.2 | 22.2 | 0 | 2019-12-07 | -9.2 | 27.2 | 0 | 2018-12-07 | -13.5 | 31.5 | 0 | 2017-12-07 | -0.9 | 18.9 | 0 | 2016-12-07 | 1.8 | 16.2 | 0 | 23.65 | 0
2025-12-07 | -11.4 | 29.4 | 0 | 2024-12-07 | -7.6 | 25.6 | 0 | 2023-12-07 | -8.5 | 26.5 | 0 | 2022-12-07 | 4 | 14 | 0 | 2021-12-07 | -8.6 | 26.6 | 0 | 2020-12-07 | -5.2 | 23.2 | 0 | 2019-12-07 | -9.8 | 27.8 | 0 | 2018-12-07 | -13.6 | 31.6 | 0 | 2017-12-07 | -1 | 19 | 0 | 2016-12-07 | 0.8 | 17.2 | 0 | 24.09 | 0
2025-12-07 | -11.8 | 29.8 | 0 | 2024-12-07 | -7.4 | 25.4 | 0 | 2023-12-07 | -8.4 | 26.4 | 0 | 2022-12-07 | 3.8 | 14.2 | 0 | 2021-12-07 | -8.6 | 26.6 | 0 | 2020-12-07 | -6 | 24 | 0 | 2019-12-07 | -11.2 | 29.2 | 0 | 2018-12-07 | -13.9 | 31.9 | 0 | 2017-12-07 | -1.2 | 19.2 | 0 | 2016-12-07 | 0.5 | 17.5 | 0 | 24.42 | 0
2025-12-07 | -12.2 | 30.2 | 0 | 2024-12-07 | -7 | 25 | 0 | 2023-12-07 | -8.3 | 26.3 | 0 | 2022-12-07 | 3.4 | 14.6 | 0 | 2021-12-07 | -8.7 | 26.7 | 0 | 2020-12-07 | -7.2 | 25.2 | 0 | 2019-12-07 | -12 | 30 | 0 | 2018-12-07 | -14.5 | 32.5 | 0 | 2017-12-07 | -1.6 | 19.6 | 0 | 2016-12-07 | 0 | 18 | 0 | 24.81 | 0
2025-12-07 | -12.4 | 30.4 | 0 | 2024-12-07 | -6.7 | 24.7 | 0 | 2023-12-07 | -8.4 | 26.4 | 0 | 2022-12-07 | 3.4 | 14.6 | 0 | 2021-12-07 | -8.9 | 26.9 | 0 | 2020-12-07 | -6.3 | 24.3 | 0 | 2019-12-07 | -10.9 | 28.9 | 0 | 2018-12-07 | -14.7 | 32.7 | 0 | 2017-12-07 | -2.6 | 20.6 | 0 | 2016-12-07 | 0 | 18 | 0 | 24.75 | 0
2025-12-07 | -11.6 | 29.6 | 0 | 2024-12-07 | -5.2 | 23.2 | 0 | 2023-12-07 | -8.2 | 26.2 | 0 | 2022-12-07 | 3.1 | 14.9 | 0 | 2021-12-07 | -9.1 | 27.1 | 0 | 2020-12-07 | -6 | 24 | 0 | 2019-12-07 | -12 | 30 | 0 | 2018-12-07 | -16.2 | 34.2 | 0 | 2017-12-07 | -3 | 21 | 0 | 2016-12-07 | 0.2 | 17.8 | 0 | 24.8 | 0
2025-12-08 | -11.1 | 29.1 | 0 | 2024-12-08 | -2 | 20 | 0 | 2023-12-08 | -7.9 | 25.9 | 0 | 2022-12-08 | 2.8 | 15.2 | 0 | 2021-12-08 | -9.5 | 27.5 | 0 | 2020-12-08 | -6.6 | 24.6 | 0 | 2019-12-08 | -11.8 | 29.8 | 0 | 2018-12-08 | -18.5 | 36.5 | 0 | 2017-12-08 | -4 | 22 | 0 | 2016-12-08 | 1.1 | 16.9 | 0 | 24.75 | 0
2025-12-08 | -12.4 | 30.4 | 0 | 2024-12-08 | -1.8 | 19.8 | 0 | 2023-12-08 | -8 | 26 | 0 | 2022-12-08 | 2.9 | 15.1 | 0 | 2021-12-08 | -9.9 | 27.9 | 0 | 2020-12-08 | -7.1 | 25.1 | 0 | 2019-12-08 | -12.3 | 30.3 | 0 | 2018-12-08 | -17.8 | 35.8 | 0 | 2017-12-08 | -4 | 22 | 0 | 2016-12-08 | 1.3 | 16.7 | 0 | 24.91 | 0
2025-12-08 | -13.5 | 31.5 | 0 | 2024-12-08 | -1.7 | 19.7 | 0 | 2023-12-08 | -7.8 | 25.8 | 0 | 2022-12-08 | 2.5 | 15.5 | 0 | 2021-12-08 | -9.8 | 27.8 | 0 | 2020-12-08 | -6.7 | 24.7 | 0 | 2019-12-08 | -12.6 | 30.6 | 0 | 2018-12-08 | -17.8 | 35.8 | 0 | 2017-12-08 | -3.5 | 21.5 | 0 | 2016-12-08 | 0.5 | 17.5 | 0 | 25.04 | 0
2025-12-08 | -14.7 | 32.7 | 0 | 2024-12-08 | -1.3 | 19.3 | 0 | 2023-12-08 | -7.8 | 25.8 | 0 | 2022-12-08 | 2.6 | 15.4 | 0 | 2021-12-08 | -10 | 28 | 0 | 2020-12-08 | -6.9 | 24.9 | 0 | 2019-12-08 | -12.8 | 30.8 | 0 | 2018-12-08 | -19.1 | 37.1 | 0 | 2017-12-08 | -3.2 | 21.2 | 0 | 2016-12-08 | 0.1 | 17.9 | 0 | 25.31 | 0
2025-12-08 | -15.9 | 33.9 | 0 | 2024-12-08 | -0.9 | 18.9 | 0 | 2023-12-08 | -7.6 | 25.6 | 0 | 2022-12-08 | 2.2 | 15.8 | 0 | 2021-12-08 | -10.2 | 28.2 | 0 | 2020-12-08 | -7 | 25 | 0 | 2019-12-08 | -12.3 | 30.3 | 0 | 2018-12-08 | -19.6 | 37.6 | 0 | 2017-12-08 | -3.5 | 21.5 | 0 | 2016-12-08 | -0.1 | 18.1 | 0 | 25.49 | 0
2025-12-08 | -17.8 | 35.8 | 0 | 2024-12-08 | 0.3 | 17.7 | 0 | 2023-12-08 | -7.5 | 25.5 | 0 | 2022-12-08 | 1.7 | 16.3 | 0 | 2021-12-08 | -10.6 | 28.6 | 0 | 2020-12-08 | -7.2 | 25.2 | 0 | 2019-12-08 | -11.4 | 29.4 | 0 | 2018-12-08 | -18.4 | 36.4 | 0 | 2017-12-08 | -3.2 | 21.2 | 0 | 2016-12-08 | -0.3 | 18.3 | 0 | 25.44 | 0
2025-12-08 | -17.9 | 35.9 | 0 | 2024-12-08 | 1.2 | 16.8 | 0 | 2023-12-08 | -7.4 | 25.4 | 0 | 2022-12-08 | 1.4 | 16.6 | 0 | 2021-12-08 | -10.6 | 28.6 | 0 | 2020-12-08 | -7.8 | 25.8 | 0 | 2019-12-08 | -11.1 | 29.1 | 0 | 2018-12-08 | -18.3 | 36.3 | 0 | 2017-12-08 | -4.1 | 22.1 | 0 | 2016-12-08 | -0.4 | 18.4 | 0 | 25.5 | 0
2025-12-08 | -19.1 | 37.1 | 0 | 2024-12-08 | 1.7 | 16.3 | 0 | 2023-12-08 | -7.4 | 25.4 | 0 | 2022-12-08 | 0.2 | 17.8 | 0 | 2021-12-08 | -10.2 | 28.2 | 0 | 2020-12-08 | -8.5 | 26.5 | 0 | 2019-12-08 | -9.5 | 27.5 | 0 | 2018-12-08 | -18.4 | 36.4 | 0 | 2017-12-08 | -3.7 | 21.7 | 0 | 2016-12-08 | -0.7 | 18.7 | 0 | 25.56 | 0
2025-12-08 | -20 | 38 | 0 | 2024-12-08 | 2 | 16 | 0 | 2023-12-08 | -7.4 | 25.4 | 0 | 2022-12-08 | 0.3 | 17.7 | 0 | 2021-12-08 | -9.9 | 27.9 | 0 | 2020-12-08 | -8.8 | 26.8 | 0 | 2019-12-08 | -7.9 | 25.9 | 0 | 2018-12-08 | -19.1 | 37.1 | 0 | 2017-12-08 | -4 | 22 | 0 | 2016-12-08 | -0.3 | 18.3 | 0 | 25.51 | 0
2025-12-08 | -17.5 | 35.5 | 0 | 2024-12-08 | 2 | 16 | 0 | 2023-12-08 | -7.1 | 25.1 | 0 | 2022-12-08 | 0.3 | 17.7 | 0 | 2021-12-08 | -9.3 | 27.3 | 0 | 2020-12-08 | -9.1 | 27.1 | 0 | 2019-12-08 | -5.3 | 23.3 | 0 | 2018-12-08 | -16.3 | 34.3 | 0 | 2017-12-08 | -3 | 21 | 0 | 2016-12-08 | -0.5 | 18.5 | 0 | 24.58 | 0
2025-12-08 | -16.2 | 34.2 | 0 | 2024-12-08 | 2.6 | 15.4 | 0 | 2023-12-08 | -6.5 | 24.5 | 0 | 2022-12-08 | 0.9 | 17.1 | 0 | 2021-12-08 | -8.5 | 26.5 | 0 | 2020-12-08 | -8.4 | 26.4 | 0 | 2019-12-08 | -4.8 | 22.8 | 0 | 2018-12-08 | -13.8 | 31.8 | 0 | 2017-12-08 | -2.1 | 20.1 | 0 | 2016-12-08 | -0.2 | 18.2 | 0 | 23.7 | 0
2025-12-08 | -15 | 33 | 0 | 2024-12-08 | 1.8 | 16.2 | 0 | 2023-12-08 | -6 | 24 | 0 | 2022-12-08 | 1.3 | 16.7 | 0 | 2021-12-08 | -7.6 | 25.6 | 0 | 2020-12-08 | -8.2 | 26.2 | 0 | 2019-12-08 | -4 | 22 | 0 | 2018-12-08 | -11.8 | 29.8 | 0 | 2017-12-08 | -0.6 | 18.6 | 0 | 2016-12-08 | 0 | 18 | 0 | 23.01 | 0
2025-12-08 | -14.4 | 32.4 | 0 | 2024-12-08 | 2 | 16 | 0 | 2023-12-08 | -5.6 | 23.6 | 0 | 2022-12-08 | 1.7 | 16.3 | 0 | 2021-12-08 | -7.5 | 25.5 | 0 | 2020-12-08 | -7.7 | 25.7 | 0 | 2019-12-08 | -2.8 | 20.8 | 0 | 2018-12-08 | -10.6 | 28.6 | 0 | 2017-12-08 | -0.1 | 18.1 | 0 | 2016-12-08 | 0.9 | 17.1 | 0 | 22.41 | 0
2025-12-08 | -14 | 32 | 0 | 2024-12-08 | 1.6 | 16.4 | 0 | 2023-12-08 | -5 | 23 | 0 | 2022-12-08 | 2.5 | 15.5 | 0 | 2021-12-08 | -8.2 | 26.2 | 0 | 2020-12-08 | -7.3 | 25.3 | 0 | 2019-12-08 | -2.2 | 20.2 | 0 | 2018-12-08 | -10.1 | 28.1 | 0 | 2017-12-08 | -0.3 | 18.3 | 0 | 2016-12-08 | 1 | 17 | 0 | 22.2 | 0
2025-12-08 | -13.1 | 31.1 | 0 | 2024-12-08 | -0.4 | 18.4 | 0 | 2023-12-08 | -5 | 23 | 0 | 2022-12-08 | 2.2 | 15.8 | 0 | 2021-12-08 | -8.3 | 26.3 | 0 | 2020-12-08 | -5.6 | 23.6 | 0 | 2019-12-08 | -1.8 | 19.8 | 0 | 2018-12-08 | -8.9 | 26.9 | 0 | 2017-12-08 | 0 | 18 | 0 | 2016-12-08 | -0.4 | 18.4 | 0 | 22.13 | 0
2025-12-08 | -12.9 | 30.9 | 0 | 2024-12-08 | -0.7 | 18.7 | 0 | 2023-12-08 | -4.9 | 22.9 | 0 | 2022-12-08 | 2.4 | 15.6 | 0 | 2021-12-08 | -8.5 | 26.5 | 0 | 2020-12-08 | -5.2 | 23.2 | 0 | 2019-12-08 | -1.2 | 19.2 | 0 | 2018-12-08 | -8.2 | 26.2 | 0 | 2017-12-08 | -0.3 | 18.3 | 0 | 2016-12-08 | -0.1 | 18.1 | 0 | 21.96 | 0
2025-12-08 | -13.9 | 31.9 | 0 | 2024-12-08 | -1.6 | 19.6 | 0 | 2023-12-08 | -5.2 | 23.2 | 0 | 2022-12-08 | 1.2 | 16.8 | 0 | 2021-12-08 | -9.1 | 27.1 | 0 | 2020-12-08 | -6.3 | 24.3 | 0 | 2019-12-08 | -0.8 | 18.8 | 0 | 2018-12-08 | -8.3 | 26.3 | 0 | 2017-12-08 | -0.7 | 18.7 | 0 | 2016-12-08 | 0.5 | 17.5 | 0 | 22.42 | 0
2025-12-08 | -14.8 | 32.8 | 0 | 2024-12-08 | -2.2 | 20.2 | 0 | 2023-12-08 | -5.6 | 23.6 | 0 | 2022-12-08 | 0.1 | 17.9 | 0 | 2021-12-08 | -9.2 | 27.2 | 0 | 2020-12-08 | -7.5 | 25.5 | 0 | 2019-12-08 | 0.1 | 17.9 | 0 | 2018-12-08 | -9 | 27 | 0 | 2017-12-08 | -0.7 | 18.7 | 0 | 2016-12-08 | -0.4 | 18.4 | 0 | 22.92 | 0
2025-12-08 | -15.1 | 33.1 | 0 | 2024-12-08 | -3 | 21 | 0 | 2023-12-08 | -5.9 | 23.9 | 0 | 2022-12-08 | -1 | 19 | 0 | 2021-12-08 | -9.6 | 27.6 | 0 | 2020-12-08 | -7 | 25 | 0 | 2019-12-08 | 0.9 | 17.1 | 0 | 2018-12-08 | -8.7 | 26.7 | 0 | 2017-12-08 | -0.4 | 18.4 | 0 | 2016-12-08 | -0.9 | 18.9 | 0 | 23.07 | 0
2025-12-08 | -17.8 | 35.8 | 0 | 2024-12-08 | -4.4 | 22.4 | 0 | 2023-12-08 | -5.3 | 23.3 | 0 | 2022-12-08 | -1.2 | 19.2 | 0 | 2021-12-08 | -9.8 | 27.8 | 0 | 2020-12-08 | -7.7 | 25.7 | 0 | 2019-12-08 | 0.9 | 17.1 | 0 | 2018-12-08 | -8.1 | 26.1 | 0 | 2017-12-08 | -0.4 | 18.4 | 0 | 2016-12-08 | -1 | 19 | 0 | 23.48 | 0
2025-12-08 | -16.1 | 34.1 | 0 | 2024-12-08 | -4.9 | 22.9 | 0 | 2023-12-08 | -5.1 | 23.1 | 0 | 2022-12-08 | -2 | 20 | 0 | 2021-12-08 | -9.7 | 27.7 | 0 | 2020-12-08 | -7.9 | 25.9 | 0 | 2019-12-08 | 2.4 | 15.6 | 0 | 2018-12-08 | -7.7 | 25.7 | 0 | 2017-12-08 | -0.3 | 18.3 | 0 | 2016-12-08 | -2.7 | 20.7 | 0 | 23.4 | 0
2025-12-08 | -17.3 | 35.3 | 0 | 2024-12-08 | -4.7 | 22.7 | 0 | 2023-12-08 | -4.7 | 22.7 | 0 | 2022-12-08 | -2.3 | 20.3 | 0 | 2021-12-08 | -9.8 | 27.8 | 0 | 2020-12-08 | -7.8 | 25.8 | 0 | 2019-12-08 | 3.1 | 14.9 | 0 | 2018-12-08 | -10.1 | 28.1 | 0 | 2017-12-08 | -0.8 | 18.8 | 0 | 2016-12-08 | -2.2 | 20.2 | 0 | 23.66 | 0
2025-12-08 | -19.8 | 37.8 | 0 | 2024-12-08 | -4.5 | 22.5 | 0 | 2023-12-08 | -4.3 | 22.3 | 0 | 2022-12-08 | -2.9 | 20.9 | 0 | 2021-12-08 | -9.8 | 27.8 | 0 | 2020-12-08 | -7.4 | 25.4 | 0 | 2019-12-08 | 3.1 | 14.9 | 0 | 2018-12-08 | -9.9 | 27.9 | 0 | 2017-12-08 | -1.3 | 19.3 | 0 | 2016-12-08 | -3.2 | 21.2 | 0 | 24 | 0
2025-12-08 | -20.4 | 38.4 | 0 | 2024-12-08 | -5 | 23 | 0 | 2023-12-08 | -4.1 | 22.1 | 0 | 2022-12-08 | -3 | 21 | 0 | 2021-12-08 | -9.9 | 27.9 | 0 | 2020-12-08 | -7.1 | 25.1 | 0 | 2019-12-08 | 3.4 | 14.6 | 0 | 2018-12-08 | -9.6 | 27.6 | 0 | 2017-12-08 | -2.1 | 20.1 | 0 | 2016-12-08 | -3.8 | 21.8 | 0 | 24.16 | 0
2025-12-09 | -21.1 | 39.1 | 0 | 2024-12-09 | -4.9 | 22.9 | 0 | 2023-12-09 | -4.1 | 22.1 | 0 | 2022-12-09 | -3.6 | 21.6 | 0 | 2021-12-09 | -9.9 | 27.9 | 0 | 2020-12-09 | -7.1 | 25.1 | 0 | 2019-12-09 | 3.2 | 14.8 | 0 | 2018-12-09 | -10.3 | 28.3 | 0 | 2017-12-09 | -1.9 | 19.9 | 0 | 2016-12-09 | -4.2 | 22.2 | 0 | 24.39 | 0
2025-12-09 | -19.8 | 37.8 | 0 | 2024-12-09 | -5.1 | 23.1 | 0 | 2023-12-09 | -4 | 22 | 0 | 2022-12-09 | -4.2 | 22.2 | 0 | 2021-12-09 | -10 | 28 | 0 | 2020-12-09 | -6.6 | 24.6 | 0 | 2019-12-09 | 3.1 | 14.9 | 0 | 2018-12-09 | -10.8 | 28.8 | 0 | 2017-12-09 | -3.1 | 21.1 | 0 | 2016-12-09 | -4.4 | 22.4 | 0 | 24.49 | 0
2025-12-09 | -19.6 | 37.6 | 0 | 2024-12-09 | -5.5 | 23.5 | 0 | 2023-12-09 | -3.9 | 21.9 | 0 | 2022-12-09 | -4.3 | 22.3 | 0 | 2021-12-09 | -10.1 | 28.1 | 0 | 2020-12-09 | -5.8 | 23.8 | 0 | 2019-12-09 | 3.2 | 14.8 | 0 | 2018-12-09 | -9.5 | 27.5 | 0 | 2017-12-09 | -4.1 | 22.1 | 0 | 2016-12-09 | -4.9 | 22.9 | 0 | 24.45 | 0
2025-12-09 | -20.8 | 38.8 | 0 | 2024-12-09 | -5.6 | 23.6 | 0 | 2023-12-09 | -3.8 | 21.8 | 0 | 2022-12-09 | -4.6 | 22.6 | 0 | 2021-12-09 | -9.8 | 27.8 | 0 | 2020-12-09 | -5.1 | 23.1 | 0 | 2019-12-09 | 3.5 | 14.5 | 0 | 2018-12-09 | -9.3 | 27.3 | 0 | 2017-12-09 | -4.9 | 22.9 | 0 | 2016-12-09 | -5.2 | 23.2 | 0 | 24.56 | 0
2025-12-09 | -21.8 | 39.8 | 0 | 2024-12-09 | -5.8 | 23.8 | 0 | 2023-12-09 | -3.7 | 21.7 | 0 | 2022-12-09 | -5 | 23 | 0 | 2021-12-09 | -9.8 | 27.8 | 0 | 2020-12-09 | -4.8 | 22.8 | 0 | 2019-12-09 | 3.4 | 14.6 | 0 | 2018-12-09 | -8.5 | 26.5 | 0 | 2017-12-09 | -4.9 | 22.9 | 0 | 2016-12-09 | -5.7 | 23.7 | 0 | 24.66 | 0
2025-12-09 | -20.9 | 38.9 | 0 | 2024-12-09 | -5.9 | 23.9 | 0 | 2023-12-09 | -3.7 | 21.7 | 0 | 2022-12-09 | -5.4 | 23.4 | 0 | 2021-12-09 | -8.5 | 26.5 | 0 | 2020-12-09 | -3.9 | 21.9 | 0 | 2019-12-09 | 3.5 | 14.5 | 0 | 2018-12-09 | -7.7 | 25.7 | 0 | 2017-12-09 | -6.1 | 24.1 | 0 | 2016-12-09 | -5.8 | 23.8 | 0 | 24.44 | 0
2025-12-09 | -21.6 | 39.6 | 0 | 2024-12-09 | -5.9 | 23.9 | 0 | 2023-12-09 | -3.6 | 21.6 | 0 | 2022-12-09 | -5.4 | 23.4 | 0 | 2021-12-09 | -8 | 26 | 0 | 2020-12-09 | -3.1 | 21.1 | 0 | 2019-12-09 | 3.4 | 14.6 | 0 | 2018-12-09 | -6.3 | 24.3 | 0 | 2017-12-09 | -4.7 | 22.7 | 0 | 2016-12-09 | -6.3 | 24.3 | 0 | 24.15 | 0
2025-12-09 | -22.1 | 40.1 | 0 | 2024-12-09 | -6 | 24 | 0 | 2023-12-09 | -3.6 | 21.6 | 0 | 2022-12-09 | -5.2 | 23.2 | 0 | 2021-12-09 | -8.6 | 26.6 | 0 | 2020-12-09 | -2.1 | 20.1 | 0 | 2019-12-09 | 3.1 | 14.9 | 0 | 2018-12-09 | -3.9 | 21.9 | 0 | 2017-12-09 | -4.9 | 22.9 | 0 | 2016-12-09 | -6.5 | 24.5 | 0 | 23.98 | 0
2025-12-09 | -20.1 | 38.1 | 0 | 2024-12-09 | -6 | 24 | 0 | 2023-12-09 | -3.4 | 21.4 | 0 | 2022-12-09 | -5.3 | 23.3 | 0 | 2021-12-09 | -10.1 | 28.1 | 0 | 2020-12-09 | -0.9 | 18.9 | 0 | 2019-12-09 | 2.2 | 15.8 | 0 | 2018-12-09 | -3 | 21 | 0 | 2017-12-09 | -4.6 | 22.6 | 0 | 2016-12-09 | -7 | 25 | 0 | 23.82 | 0
2025-12-09 | -18.4 | 36.4 | 0 | 2024-12-09 | -5.6 | 23.6 | 0 | 2023-12-09 | -3 | 21 | 0 | 2022-12-09 | -4.9 | 22.9 | 0 | 2021-12-09 | -9.2 | 27.2 | 0 | 2020-12-09 | -0.5 | 18.5 | 0 | 2019-12-09 | 2.1 | 15.9 | 0 | 2018-12-09 | -2.4 | 20.4 | 0 | 2017-12-09 | -4.2 | 22.2 | 0 | 2016-12-09 | -6 | 24 | 0 | 23.21 | 0
2025-12-09 | -17.7 | 35.7 | 0 | 2024-12-09 | -5.4 | 23.4 | 0 | 2023-12-09 | -2.5 | 20.5 | 0 | 2022-12-09 | -3.9 | 21.9 | 0 | 2021-12-09 | -8.6 | 26.6 | 0 | 2020-12-09 | -0.2 | 18.2 | 0 | 2019-12-09 | 2.1 | 15.9 | 0 | 2018-12-09 | -1.6 | 19.6 | 0 | 2017-12-09 | -3.9 | 21.9 | 0 | 2016-12-09 | -5.5 | 23.5 | 0 | 22.72 | 0
2025-12-09 | -16.6 | 34.6 | 0 | 2024-12-09 | -5.7 | 23.7 | 0 | 2023-12-09 | -1.9 | 19.9 | 0 | 2022-12-09 | -2.9 | 20.9 | 0 | 2021-12-09 | -7.8 | 25.8 | 0 | 2020-12-09 | 0.2 | 17.8 | 0 | 2019-12-09 | 2.8 | 15.2 | 0 | 2018-12-09 | -2 | 20 | 0 | 2017-12-09 | -3.1 | 21.1 | 0 | 2016-12-09 | -5.2 | 23.2 | 0 | 22.22 | 0
2025-12-09 | -14.7 | 32.7 | 0 | 2024-12-09 | -6.5 | 24.5 | 0 | 2023-12-09 | -1.7 | 19.7 | 0 | 2022-12-09 | -2.3 | 20.3 | 0 | 2021-12-09 | -7.2 | 25.2 | 0 | 2020-12-09 | 0.6 | 17.4 | 0 | 2019-12-09 | 2.9 | 15.1 | 0 | 2018-12-09 | -1.7 | 19.7 | 0 | 2017-12-09 | -2.5 | 20.5 | 0 | 2016-12-09 | -5.4 | 23.4 | 0 | 21.85 | 0
2025-12-09 | -13.7 | 31.7 | 0 | 2024-12-09 | -7.3 | 25.3 | 0 | 2023-12-09 | -1.3 | 19.3 | 0 | 2022-12-09 | -1.6 | 19.6 | 0 | 2021-12-09 | -7.1 | 25.1 | 0 | 2020-12-09 | 0.7 | 17.3 | 0 | 2019-12-09 | 3.1 | 14.9 | 0 | 2018-12-09 | -1.4 | 19.4 | 0 | 2017-12-09 | -1.5 | 19.5 | 0 | 2016-12-09 | -5.2 | 23.2 | 0 | 21.53 | 0
2025-12-09 | -12.7 | 30.7 | 0 | 2024-12-09 | -7.5 | 25.5 | 0 | 2023-12-09 | -1 | 19 | 0 | 2022-12-09 | -1.2 | 19.2 | 0 | 2021-12-09 | -6.9 | 24.9 | 0 | 2020-12-09 | 0.8 | 17.2 | 0 | 2019-12-09 | 3.1 | 14.9 | 0 | 2018-12-09 | -1.4 | 19.4 | 0 | 2017-12-09 | -1.3 | 19.3 | 0 | 2016-12-09 | -5.2 | 23.2 | 0 | 21.33 | 0
2025-12-09 | -12.1 | 30.1 | 0 | 2024-12-09 | -7.6 | 25.6 | 0 | 2023-12-09 | -0.6 | 18.6 | 0 | 2022-12-09 | -1.1 | 19.1 | 0 | 2021-12-09 | -7.6 | 25.6 | 0 | 2020-12-09 | 0.7 | 17.3 | 0 | 2019-12-09 | 2.9 | 15.1 | 0 | 2018-12-09 | -1.3 | 19.3 | 0 | 2017-12-09 | -1.2 | 19.2 | 0 | 2016-12-09 | -4.2 | 22.2 | 0 | 21.21 | 0
2025-12-09 | -11.1 | 29.1 | 0 | 2024-12-09 | -8.1 | 26.1 | 0 | 2023-12-09 | -0.3 | 18.3 | 0 | 2022-12-09 | -2 | 20 | 0 | 2021-12-09 | -7 | 25 | 0 | 2020-12-09 | 0.5 | 17.5 | 0 | 2019-12-09 | 2.6 | 15.4 | 0 | 2018-12-09 | -1.1 | 19.1 | 0 | 2017-12-09 | -1.4 | 19.4 | 0 | 2016-12-09 | -5.1 | 23.1 | 0 | 21.3 | 0
2025-12-09 | -11.3 | 29.3 | 0 | 2024-12-09 | -8.1 | 26.1 | 0 | 2023-12-09 | -0.1 | 18.1 | 0 | 2022-12-09 | -3.3 | 21.3 | 0 | 2021-12-09 | -7.9 | 25.9 | 0 | 2020-12-09 | 0.4 | 17.6 | 0 | 2019-12-09 | 2.6 | 15.4 | 0 | 2018-12-09 | -1 | 19 | 0 | 2017-12-09 | -1.6 | 19.6 | 0 | 2016-12-09 | -6.3 | 24.3 | 0 | 21.66 | 0
2025-12-09 | -11.7 | 29.7 | 0 | 2024-12-09 | -7.8 | 25.8 | 0 | 2023-12-09 | 0 | 18 | 0 | 2022-12-09 | -4.5 | 22.5 | 0 | 2021-12-09 | -8.2 | 26.2 | 0 | 2020-12-09 | 0.4 | 17.6 | 0 | 2019-12-09 | 2.5 | 15.5 | 0 | 2018-12-09 | -0.7 | 18.7 | 0 | 2017-12-09 | -1.7 | 19.7 | 0 | 2016-12-09 | -7 | 25 | 0 | 21.87 | 0
2025-12-09 | -11.5 | 29.5 | 0 | 2024-12-09 | -7.2 | 25.2 | 0 | 2023-12-09 | 0.1 | 17.9 | 0 | 2022-12-09 | -5.3 | 23.3 | 0 | 2021-12-09 | -9.7 | 27.7 | 0 | 2020-12-09 | 0.5 | 17.5 | 0 | 2019-12-09 | 3.7 | 14.3 | 0 | 2018-12-09 | -0.9 | 18.9 | 0 | 2017-12-09 | -2 | 20 | 0 | 2016-12-09 | -7.5 | 25.5 | 0 | 21.98 | 0
2025-12-09 | -10.9 | 28.9 | 0 | 2024-12-09 | -6.7 | 24.7 | 0 | 2023-12-09 | 0.1 | 17.9 | 0 | 2022-12-09 | -6 | 24 | 0 | 2021-12-09 | -9.2 | 27.2 | 0 | 2020-12-09 | 0.6 | 17.4 | 0 | 2019-12-09 | 4.6 | 13.4 | 0 | 2018-12-09 | -1.7 | 19.7 | 0 | 2017-12-09 | -2.3 | 20.3 | 0 | 2016-12-09 | -8.2 | 26.2 | 0 | 21.97 | 0
2025-12-09 | -9.8 | 27.8 | 0 | 2024-12-09 | -6.2 | 24.2 | 0 | 2023-12-09 | 0.1 | 17.9 | 0 | 2022-12-09 | -6.6 | 24.6 | 0 | 2021-12-09 | -10.8 | 28.8 | 0 | 2020-12-09 | 0.9 | 17.1 | 0 | 2019-12-09 | 5.9 | 12.1 | 0 | 2018-12-09 | -2.9 | 20.9 | 0 | 2017-12-09 | -2.6 | 20.6 | 0 | 2016-12-09 | -8.8 | 26.8 | 0 | 22.08 | 0
2025-12-09 | -8.2 | 26.2 | 0 | 2024-12-09 | -6 | 24 | 0 | 2023-12-09 | 0.1 | 17.9 | 0 | 2022-12-09 | -7.3 | 25.3 | 0 | 2021-12-09 | -9.2 | 27.2 | 0 | 2020-12-09 | 1.1 | 16.9 | 0 | 2019-12-09 | 6.6 | 11.4 | 0 | 2018-12-09 | -2.7 | 20.7 | 0 | 2017-12-09 | -2.9 | 20.9 | 0 | 2016-12-09 | -9.8 | 27.8 | 0 | 21.83 | 0
2025-12-09 | -6.8 | 24.8 | 0 | 2024-12-09 | -5.4 | 23.4 | 0 | 2023-12-09 | 0.1 | 17.9 | 0 | 2022-12-09 | -7.8 | 25.8 | 0 | 2021-12-09 | -8.8 | 26.8 | 0 | 2020-12-09 | 1.1 | 16.9 | 0 | 2019-12-09 | 6.9 | 11.1 | 0 | 2018-12-09 | -2.6 | 20.6 | 0 | 2017-12-09 | -2.9 | 20.9 | 0 | 2016-12-09 | -8.5 | 26.5 | 0 | 21.47 | 0
2025-12-10 | -6.1 | 24.1 | 0 | 2024-12-10 | -5.2 | 23.2 | 0 | 2023-12-10 | 0.3 | 17.7 | 0 | 2022-12-10 | -9 | 27 | 0 | 2021-12-10 | -8 | 26 | 0 | 2020-12-10 | 1.2 | 16.8 | 0 | 2019-12-10 | 7.1 | 10.9 | 0 | 2018-12-10 | -2.9 | 20.9 | 0 | 2017-12-10 | -3 | 21 | 0 | 2016-12-10 | -8.1 | 26.1 | 0 | 21.37 | 0
2025-12-10 | -6.6 | 24.6 | 0 | 2024-12-10 | -4.8 | 22.8 | 0 | 2023-12-10 | 0.3 | 17.7 | 0 | 2022-12-10 | -9.4 | 27.4 | 0 | 2021-12-10 | -7.5 | 25.5 | 0 | 2020-12-10 | 1 | 17 | 0 | 2019-12-10 | 7.2 | 10.8 | 0 | 2018-12-10 | -4.5 | 22.5 | 0 | 2017-12-10 | -3 | 21 | 0 | 2016-12-10 | -10.1 | 28.1 | 0 | 21.74 | 0
2025-12-10 | -7 | 25 | 0 | 2024-12-10 | -4.6 | 22.6 | 0 | 2023-12-10 | 0.2 | 17.8 | 0 | 2022-12-10 | -10.4 | 28.4 | 0 | 2021-12-10 | -7.4 | 25.4 | 0 | 2020-12-10 | 1.1 | 16.9 | 0 | 2019-12-10 | 7.3 | 10.7 | 0 | 2018-12-10 | -6.5 | 24.5 | 0 | 2017-12-10 | -3.1 | 21.1 | 0 | 2016-12-10 | -10 | 28 | 0 | 22.04 | 0
2025-12-10 | -7 | 25 | 0 | 2024-12-10 | -4.6 | 22.6 | 0 | 2023-12-10 | 0.4 | 17.6 | 0 | 2022-12-10 | -10.4 | 28.4 | 0 | 2021-12-10 | -7.3 | 25.3 | 0 | 2020-12-10 | 1.1 | 16.9 | 0 | 2019-12-10 | 7.8 | 10.2 | 0 | 2018-12-10 | -7.3 | 25.3 | 0 | 2017-12-10 | -3.3 | 21.3 | 0 | 2016-12-10 | -10 | 28 | 0 | 22.06 | 0
2025-12-10 | -3.2 | 21.2 | 0 | 2024-12-10 | -4.5 | 22.5 | 0 | 2023-12-10 | 1.4 | 16.6 | 0 | 2022-12-10 | -11 | 29 | 0 | 2021-12-10 | -7.5 | 25.5 | 0 | 2020-12-10 | 1.2 | 16.8 | 0 | 2019-12-10 | 8.2 | 9.8 | 0 | 2018-12-10 | -8.7 | 26.7 | 0 | 2017-12-10 | -3.4 | 21.4 | 0 | 2016-12-10 | -10.4 | 28.4 | 0 | 21.79 | 0
2025-12-10 | -6.9 | 24.9 | 0 | 2024-12-10 | -4.3 | 22.3 | 0 | 2023-12-10 | 1.2 | 16.8 | 0 | 2022-12-10 | -11.2 | 29.2 | 0 | 2021-12-10 | -7.7 | 25.7 | 0 | 2020-12-10 | 1.2 | 16.8 | 0 | 2019-12-10 | 8.1 | 9.9 | 0 | 2018-12-10 | -10 | 28 | 0 | 2017-12-10 | -3 | 21 | 0 | 2016-12-10 | -9.7 | 27.7 | 0 | 22.23 | 0
2025-12-10 | -7 | 25 | 0 | 2024-12-10 | -4.1 | 22.1 | 0 | 2023-12-10 | 1.5 | 16.5 | 0 | 2022-12-10 | -11.2 | 29.2 | 0 | 2021-12-10 | -7.8 | 25.8 | 0 | 2020-12-10 | 0.9 | 17.1 | 0 | 2019-12-10 | 8.3 | 9.7 | 0 | 2018-12-10 | -10.4 | 28.4 | 0 | 2017-12-10 | -3.8 | 21.8 | 0 | 2016-12-10 | -10 | 28 | 0 | 22.36 | 0
2025-12-10 | -6.3 | 24.3 | 0 | 2024-12-10 | -3.9 | 21.9 | 0 | 2023-12-10 | 1.1 | 16.9 | 0 | 2022-12-10 | -11.4 | 29.4 | 0 | 2021-12-10 | -7.7 | 25.7 | 0 | 2020-12-10 | 0.6 | 17.4 | 0 | 2019-12-10 | 7.2 | 10.8 | 0 | 2018-12-10 | -10.7 | 28.7 | 0 | 2017-12-10 | -4.9 | 22.9 | 0 | 2016-12-10 | -10 | 28 | 0 | 22.6 | 0
2025-12-10 | -6.4 | 24.4 | 0 | 2024-12-10 | -3.9 | 21.9 | 0 | 2023-12-10 | 1.5 | 16.5 | 0 | 2022-12-10 | -11 | 29 | 0 | 2021-12-10 | -7.6 | 25.6 | 0 | 2020-12-10 | 0.4 | 17.6 | 0 | 2019-12-10 | 6.4 | 11.6 | 0 | 2018-12-10 | -10.6 | 28.6 | 0 | 2017-12-10 | -6 | 24 | 0 | 2016-12-10 | -10.5 | 28.5 | 0 | 22.77 | 0
2025-12-10 | -6.1 | 24.1 | 0 | 2024-12-10 | -3.6 | 21.6 | 0 | 2023-12-10 | 1.4 | 16.6 | 0 | 2022-12-10 | -9.7 | 27.7 | 0 | 2021-12-10 | -7.3 | 25.3 | 0 | 2020-12-10 | 0.2 | 17.8 | 0 | 2019-12-10 | 5.6 | 12.4 | 0 | 2018-12-10 | -9.8 | 27.8 | 0 | 2017-12-10 | -6.4 | 24.4 | 0 | 2016-12-10 | -10.2 | 28.2 | 0 | 22.59 | 0
2025-12-10 | -5.4 | 23.4 | 0 | 2024-12-10 | -3.4 | 21.4 | 0 | 2023-12-10 | 2.8 | 15.2 | 0 | 2022-12-10 | -8.5 | 26.5 | 0 | 2021-12-10 | -6.8 | 24.8 | 0 | 2020-12-10 | 0 | 18 | 0 | 2019-12-10 | 5 | 13 | 0 | 2018-12-10 | -9.2 | 27.2 | 0 | 2017-12-10 | -6.4 | 24.4 | 0 | 2016-12-10 | -9.4 | 27.4 | 0 | 22.13 | 0
2025-12-10 | -5 | 23 | 0 | 2024-12-10 | -3 | 21 | 0 | 2023-12-10 | 3.4 | 14.6 | 0 | 2022-12-10 | -6.7 | 24.7 | 0 | 2021-12-10 | -6.3 | 24.3 | 0 | 2020-12-10 | -0.2 | 18.2 | 0 | 2019-12-10 | 4.3 | 13.7 | 0 | 2018-12-10 | -8.6 | 26.6 | 0 | 2017-12-10 | -5.7 | 23.7 | 0 | 2016-12-10 | -7.9 | 25.9 | 0 | 21.57 | 0
2025-12-10 | -4.9 | 22.9 | 0 | 2024-12-10 | -2.4 | 20.4 | 0 | 2023-12-10 | 3.5 | 14.5 | 0 | 2022-12-10 | -6.2 | 24.2 | 0 | 2021-12-10 | -5.4 | 23.4 | 0 | 2020-12-10 | -0.2 | 18.2 | 0 | 2019-12-10 | 0.1 | 17.9 | 0 | 2018-12-10 | -8.1 | 26.1 | 0 | 2017-12-10 | -5.3 | 23.3 | 0 | 2016-12-10 | -6.9 | 24.9 | 0 | 21.58 | 0
2025-12-10 | -4.9 | 22.9 | 0 | 2024-12-10 | -1.9 | 19.9 | 0 | 2023-12-10 | 4 | 14 | 0 | 2022-12-10 | -5.2 | 23.2 | 0 | 2021-12-10 | -5.2 | 23.2 | 0 | 2020-12-10 | 0.1 | 17.9 | 0 | 2019-12-10 | -1.4 | 19.4 | 0 | 2018-12-10 | -7.6 | 25.6 | 0 | 2017-12-10 | -4.8 | 22.8 | 0 | 2016-12-10 | -6.5 | 24.5 | 0 | 21.34 | 0
2025-12-10 | -4.9 | 22.9 | 0 | 2024-12-10 | -1.3 | 19.3 | 0 | 2023-12-10 | 4 | 14 | 0 | 2022-12-10 | -5.3 | 23.3 | 0 | 2021-12-10 | -4.7 | 22.7 | 0 | 2020-12-10 | 0.2 | 17.8 | 0 | 2019-12-10 | -1.8 | 19.8 | 0 | 2018-12-10 | -7.5 | 25.5 | 0 | 2017-12-10 | -4.1 | 22.1 | 0 | 2016-12-10 | -6.4 | 24.4 | 0 | 21.18 | 0
2025-12-10 | -5 | 23 | 0 | 2024-12-10 | -1.1 | 19.1 | 0 | 2023-12-10 | 3.6 | 14.4 | 0 | 2022-12-10 | -5.3 | 23.3 | 0 | 2021-12-10 | -4.5 | 22.5 | 0 | 2020-12-10 | 0 | 18 | 0 | 2019-12-10 | -2.8 | 20.8 | 0 | 2018-12-10 | -7.8 | 25.8 | 0 | 2017-12-10 | -3.9 | 21.9 | 0 | 2016-12-10 | -6.3 | 24.3 | 0 | 21.31 | 0
2025-12-10 | -5 | 23 | 0 | 2024-12-10 | -0.9 | 18.9 | 0 | 2023-12-10 | 3.3 | 14.7 | 0 | 2022-12-10 | -6.6 | 24.6 | 0 | 2021-12-10 | -4.4 | 22.4 | 0 | 2020-12-10 | 0.2 | 17.8 | 0 | 2019-12-10 | -4.3 | 22.3 | 0 | 2018-12-10 | -8.7 | 26.7 | 0 | 2017-12-10 | -3.7 | 21.7 | 0 | 2016-12-10 | -7.4 | 25.4 | 0 | 21.75 | 0
2025-12-10 | -4.8 | 22.8 | 0 | 2024-12-10 | -0.6 | 18.6 | 0 | 2023-12-10 | 2.9 | 15.1 | 0 | 2022-12-10 | -7.5 | 25.5 | 0 | 2021-12-10 | -4.2 | 22.2 | 0 | 2020-12-10 | -0.1 | 18.1 | 0 | 2019-12-10 | -5.5 | 23.5 | 0 | 2018-12-10 | -9.1 | 27.1 | 0 | 2017-12-10 | -3.7 | 21.7 | 0 | 2016-12-10 | -7.9 | 25.9 | 0 | 22.05 | 0
2025-12-10 | -4.5 | 22.5 | 0 | 2024-12-10 | -0.5 | 18.5 | 0 | 2023-12-10 | 2.6 | 15.4 | 0 | 2022-12-10 | -7.7 | 25.7 | 0 | 2021-12-10 | -4.2 | 22.2 | 0 | 2020-12-10 | -0.8 | 18.8 | 0 | 2019-12-10 | -6.5 | 24.5 | 0 | 2018-12-10 | -9.6 | 27.6 | 0 | 2017-12-10 | -4 | 22 | 0 | 2016-12-10 | -8.8 | 26.8 | 0 | 22.4 | 0
2025-12-10 | -4.3 | 22.3 | 0 | 2024-12-10 | -0.3 | 18.3 | 0 | 2023-12-10 | 2.5 | 15.5 | 0 | 2022-12-10 | -7.6 | 25.6 | 0 | 2021-12-10 | -4.2 | 22.2 | 0 | 2020-12-10 | -0.7 | 18.7 | 0 | 2019-12-10 | -7 | 25 | 0 | 2018-12-10 | -11.9 | 29.9 | 0 | 2017-12-10 | -4 | 22 | 0 | 2016-12-10 | -9.1 | 27.1 | 0 | 22.66 | 0
2025-12-10 | -4 | 22 | 0 | 2024-12-10 | -0.2 | 18.2 | 0 | 2023-12-10 | 2.3 | 15.7 | 0 | 2022-12-10 | -7.8 | 25.8 | 0 | 2021-12-10 | -4 | 22 | 0 | 2020-12-10 | -0.9 | 18.9 | 0 | 2019-12-10 | -8.3 | 26.3 | 0 | 2018-12-10 | -13.1 | 31.1 | 0 | 2017-12-10 | -3.8 | 21.8 | 0 | 2016-12-10 | -10.1 | 28.1 | 0 | 22.99 | 0
2025-12-10 | -3.9 | 21.9 | 0 | 2024-12-10 | -0.1 | 18.1 | 0 | 2023-12-10 | 1.4 | 16.6 | 0 | 2022-12-10 | -7.9 | 25.9 | 0 | 2021-12-10 | -3.9 | 21.9 | 0 | 2020-12-10 | -1 | 19 | 0 | 2019-12-10 | -9.5 | 27.5 | 0 | 2018-12-10 | -12.7 | 30.7 | 0 | 2017-12-10 | -3.7 | 21.7 | 0 | 2016-12-10 | -11.4 | 29.4 | 0 | 23.27 | 0
2025-12-10 | -4 | 22 | 0 | 2024-12-10 | 0 | 18 | 0 | 2023-12-10 | 1.7 | 16.3 | 0 | 2022-12-10 | -8.1 | 26.1 | 0 | 2021-12-10 | -4.1 | 22.1 | 0 | 2020-12-10 | -1 | 19 | 0 | 2019-12-10 | -10.1 | 28.1 | 0 | 2018-12-10 | -14.4 | 32.4 | 0 | 2017-12-10 | -4.6 | 22.6 | 0 | 2016-12-10 | -11.6 | 29.6 | 0 | 23.62 | 0
2025-12-10 | -4.4 | 22.4 | 0 | 2024-12-10 | 0 | 18 | 0 | 2023-12-10 | 1.4 | 16.6 | 0 | 2022-12-10 | -8.5 | 26.5 | 0 | 2021-12-10 | -3.9 | 21.9 | 0 | 2020-12-10 | -0.9 | 18.9 | 0 | 2019-12-10 | -10.5 | 28.5 | 0 | 2018-12-10 | -12 | 30 | 0 | 2017-12-10 | -7.8 | 25.8 | 0 | 2016-12-10 | -14 | 32 | 0 | 24.06 | 0
2025-12-11 | -5 | 23 | 0 | 2024-12-11 | 0.1 | 17.9 | 0 | 2023-12-11 | 0.9 | 17.1 | 0 | 2022-12-11 | -8.5 | 26.5 | 0 | 2021-12-11 | -3.7 | 21.7 | 0 | 2020-12-11 | -0.8 | 18.8 | 0 | 2019-12-11 | -11 | 29 | 0 | 2018-12-11 | -10.7 | 28.7 | 0 | 2017-12-11 | -9 | 27 | 0 | 2016-12-11 | -14.4 | 32.4 | 0 | 24.21 | 0
2025-12-11 | -5.5 | 23.5 | 0 | 2024-12-11 | 0.2 | 17.8 | 0 | 2023-12-11 | 0.5 | 17.5 | 0 | 2022-12-11 | -8.3 | 26.3 | 0 | 2021-12-11 | -3.4 | 21.4 | 0 | 2020-12-11 | -0.6 | 18.6 | 0 | 2019-12-11 | -11.6 | 29.6 | 0 | 2018-12-11 | -9.9 | 27.9 | 0 | 2017-12-11 | -10.4 | 28.4 | 0 | 2016-12-11 | -12.2 | 30.2 | 0 | 24.12 | 0
2025-12-11 | -6.4 | 24.4 | 0 | 2024-12-11 | 0.3 | 17.7 | 0 | 2023-12-11 | 0.8 | 17.2 | 0 | 2022-12-11 | -8.3 | 26.3 | 0 | 2021-12-11 | -3.2 | 21.2 | 0 | 2020-12-11 | -0.4 | 18.4 | 0 | 2019-12-11 | -11.8 | 29.8 | 0 | 2018-12-11 | -9.5 | 27.5 | 0 | 2017-12-11 | -11.5 | 29.5 | 0 | 2016-12-11 | -10.7 | 28.7 | 0 | 24.07 | 0
2025-12-11 | -8.3 | 26.3 | 0 | 2024-12-11 | 0.3 | 17.7 | 0 | 2023-12-11 | 0.5 | 17.5 | 0 | 2022-12-11 | -8.4 | 26.4 | 0 | 2021-12-11 | -3.1 | 21.1 | 0 | 2020-12-11 | -0.2 | 18.2 | 0 | 2019-12-11 | -12.4 | 30.4 | 0 | 2018-12-11 | -9.8 | 27.8 | 0 | 2017-12-11 | -12.7 | 30.7 | 0 | 2016-12-11 | -10.9 | 28.9 | 0 | 24.5 | 0
2025-12-11 | -9.7 | 27.7 | 0 | 2024-12-11 | 0.3 | 17.7 | 0 | 2023-12-11 | 0.4 | 17.6 | 0 | 2022-12-11 | -8.5 | 26.5 | 0 | 2021-12-11 | -2.8 | 20.8 | 0 | 2020-12-11 | -0.4 | 18.4 | 0 | 2019-12-11 | -12.6 | 30.6 | 0 | 2018-12-11 | -10 | 28 | 0 | 2017-12-11 | -12.8 | 30.8 | 0 | 2016-12-11 | -10.1 | 28.1 | 0 | 24.62 | 0
2025-12-11 | -10.5 | 28.5 | 0 | 2024-12-11 | 0.5 | 17.5 | 0 | 2023-12-11 | 0.5 | 17.5 | 0 | 2022-12-11 | -8.8 | 26.8 | 0 | 2021-12-11 | -2.4 | 20.4 | 0 | 2020-12-11 | -1 | 19 | 0 | 2019-12-11 | -13.4 | 31.4 | 0 | 2018-12-11 | -9.5 | 27.5 | 0 | 2017-12-11 | -14.1 | 32.1 | 0 | 2016-12-11 | -10.2 | 28.2 | 0 | 24.89 | 0
2025-12-11 | -11.2 | 29.2 | 0 | 2024-12-11 | 0.6 | 17.4 | 0 | 2023-12-11 | 0.6 | 17.4 | 0 | 2022-12-11 | -8.9 | 26.9 | 0 | 2021-12-11 | -1.7 | 19.7 | 0 | 2020-12-11 | -0.4 | 18.4 | 0 | 2019-12-11 | -13.2 | 31.2 | 0 | 2018-12-11 | -9.3 | 27.3 | 0 | 2017-12-11 | -14.3 | 32.3 | 0 | 2016-12-11 | -10.7 | 28.7 | 0 | 24.85 | 0
2025-12-11 | -11.8 | 29.8 | 0 | 2024-12-11 | 0.6 | 17.4 | 0 | 2023-12-11 | 0.6 | 17.4 | 0 | 2022-12-11 | -8.8 | 26.8 | 0 | 2021-12-11 | -1 | 19 | 0 | 2020-12-11 | 0.2 | 17.8 | 0 | 2019-12-11 | -12.3 | 30.3 | 0 | 2018-12-11 | -9.4 | 27.4 | 0 | 2017-12-11 | -16.8 | 34.8 | 0 | 2016-12-11 | -12.6 | 30.6 | 0 | 25.13 | 0
2025-12-11 | -12.2 | 30.2 | 0 | 2024-12-11 | 0.5 | 17.5 | 0 | 2023-12-11 | 0.5 | 17.5 | 0 | 2022-12-11 | -8.5 | 26.5 | 0 | 2021-12-11 | -0.4 | 18.4 | 0 | 2020-12-11 | 0.1 | 17.9 | 0 | 2019-12-11 | -12.9 | 30.9 | 0 | 2018-12-11 | -9.3 | 27.3 | 0 | 2017-12-11 | -16 | 34 | 0 | 2016-12-11 | -13.1 | 31.1 | 0 | 25.13 | 0
2025-12-11 | -12.3 | 30.3 | 0 | 2024-12-11 | 0.7 | 17.3 | 0 | 2023-12-11 | 0.5 | 17.5 | 0 | 2022-12-11 | -8 | 26 | 0 | 2021-12-11 | 0.2 | 17.8 | 0 | 2020-12-11 | 0.2 | 17.8 | 0 | 2019-12-11 | -10.1 | 28.1 | 0 | 2018-12-11 | -9.2 | 27.2 | 0 | 2017-12-11 | -14.4 | 32.4 | 0 | 2016-12-11 | -11.2 | 29.2 | 0 | 24.36 | 0
2025-12-11 | -11.6 | 29.6 | 0 | 2024-12-11 | 1.1 | 16.9 | 0 | 2023-12-11 | 0.3 | 17.7 | 0 | 2022-12-11 | -7.5 | 25.5 | 0 | 2021-12-11 | 0.2 | 17.8 | 0 | 2020-12-11 | 1.3 | 16.7 | 0 | 2019-12-11 | -7.3 | 25.3 | 0 | 2018-12-11 | -8.7 | 26.7 | 0 | 2017-12-11 | -13 | 31 | 0 | 2016-12-11 | -8.9 | 26.9 | 0 | 23.41 | 0
2025-12-11 | -11 | 29 | 0 | 2024-12-11 | 0.8 | 17.2 | 0 | 2023-12-11 | -0.1 | 18.1 | 0 | 2022-12-11 | -7.3 | 25.3 | 0 | 2021-12-11 | 0.4 | 17.6 | 0 | 2020-12-11 | 3.2 | 14.8 | 0 | 2019-12-11 | -6.1 | 24.1 | 0 | 2018-12-11 | -8 | 26 | 0 | 2017-12-11 | -12.5 | 30.5 | 0 | 2016-12-11 | -7.6 | 25.6 | 0 | 22.82 | 0
2025-12-11 | -10.7 | 28.7 | 0 | 2024-12-11 | 1.2 | 16.8 | 0 | 2023-12-11 | -0.9 | 18.9 | 0 | 2022-12-11 | -7 | 25 | 0 | 2021-12-11 | 0.4 | 17.6 | 0 | 2020-12-11 | 3.6 | 14.4 | 0 | 2019-12-11 | -4.5 | 22.5 | 0 | 2018-12-11 | -7.5 | 25.5 | 0 | 2017-12-11 | -12.1 | 30.1 | 0 | 2016-12-11 | -6 | 24 | 0 | 22.35 | 0
2025-12-11 | -10.2 | 28.2 | 0 | 2024-12-11 | 1.1 | 16.9 | 0 | 2023-12-11 | -1 | 19 | 0 | 2022-12-11 | -6.5 | 24.5 | 0 | 2021-12-11 | 0.6 | 17.4 | 0 | 2020-12-11 | 4 | 14 | 0 | 2019-12-11 | -3.5 | 21.5 | 0 | 2018-12-11 | -7 | 25 | 0 | 2017-12-11 | -11.6 | 29.6 | 0 | 2016-12-11 | -5.8 | 23.8 | 0 | 21.99 | 0
2025-12-11 | -9.9 | 27.9 | 0 | 2024-12-11 | 1 | 17 | 0 | 2023-12-11 | -1.3 | 19.3 | 0 | 2022-12-11 | -6.2 | 24.2 | 0 | 2021-12-11 | 1.6 | 16.4 | 0 | 2020-12-11 | 4.2 | 13.8 | 0 | 2019-12-11 | -2.9 | 20.9 | 0 | 2018-12-11 | -6.6 | 24.6 | 0 | 2017-12-11 | -11.7 | 29.7 | 0 | 2016-12-11 | -5.6 | 23.6 | 0 | 21.74 | 0
2025-12-11 | -9.4 | 27.4 | 0 | 2024-12-11 | 1 | 17 | 0 | 2023-12-11 | -1.8 | 19.8 | 0 | 2022-12-11 | -6.1 | 24.1 | 0 | 2021-12-11 | 2.4 | 15.6 | 0 | 2020-12-11 | 3.7 | 14.3 | 0 | 2019-12-11 | -2.5 | 20.5 | 0 | 2018-12-11 | -6.9 | 24.9 | 0 | 2017-12-11 | -11.7 | 29.7 | 0 | 2016-12-11 | -5.3 | 23.3 | 0 | 21.66 | 0
2025-12-11 | -9.4 | 27.4 | 0 | 2024-12-11 | 1 | 17 | 0 | 2023-12-11 | -2.2 | 20.2 | 0 | 2022-12-11 | -6.2 | 24.2 | 0 | 2021-12-11 | 2.5 | 15.5 | 0 | 2020-12-11 | 3.6 | 14.4 | 0 | 2019-12-11 | -2.9 | 20.9 | 0 | 2018-12-11 | -7.2 | 25.2 | 0 | 2017-12-11 | -12.7 | 30.7 | 0 | 2016-12-11 | -5.3 | 23.3 | 0 | 21.88 | 0
2025-12-11 | -9.6 | 27.6 | 0 | 2024-12-11 | 0.8 | 17.2 | 0 | 2023-12-11 | -2.8 | 20.8 | 0 | 2022-12-11 | -6.2 | 24.2 | 0 | 2021-12-11 | 9.9 | 8.1 | 0 | 2020-12-11 | 2.8 | 15.2 | 0 | 2019-12-11 | -3.7 | 21.7 | 0 | 2018-12-11 | -7.3 | 25.3 | 0 | 2017-12-11 | -12.5 | 30.5 | 0 | 2016-12-11 | -5.3 | 23.3 | 0 | 21.39 | 0
2025-12-11 | -9.7 | 27.7 | 0 | 2024-12-11 | 0.5 | 17.5 | 0 | 2023-12-11 | -4.2 | 22.2 | 0 | 2022-12-11 | -6.3 | 24.3 | 0 | 2021-12-11 | 10.8 | 7.2 | 0 | 2020-12-11 | 2.6 | 15.4 | 0 | 2019-12-11 | -5.6 | 23.6 | 0 | 2018-12-11 | -7.4 | 25.4 | 0 | 2017-12-11 | -12.5 | 30.5 | 0 | 2016-12-11 | -6.2 | 24.2 | 0 | 21.8 | 0
2025-12-11 | -9.8 | 27.8 | 0 | 2024-12-11 | 0.6 | 17.4 | 0 | 2023-12-11 | -4.8 | 22.8 | 0 | 2022-12-11 | -6.3 | 24.3 | 0 | 2021-12-11 | 9.9 | 8.1 | 0 | 2020-12-11 | 2.3 | 15.7 | 0 | 2019-12-11 | -6.3 | 24.3 | 0 | 2018-12-11 | -7.6 | 25.6 | 0 | 2017-12-11 | -11.9 | 29.9 | 0 | 2016-12-11 | -5.8 | 23.8 | 0 | 21.97 | 0
2025-12-11 | -10.4 | 28.4 | 0 | 2024-12-11 | 0.7 | 17.3 | 0 | 2023-12-11 | -5.1 | 23.1 | 0 | 2022-12-11 | -6.4 | 24.4 | 0 | 2021-12-11 | 6.9 | 11.1 | 0 | 2020-12-11 | 2.5 | 15.5 | 0 | 2019-12-11 | -7.2 | 25.2 | 0 | 2018-12-11 | -7.5 | 25.5 | 0 | 2017-12-11 | -11.6 | 29.6 | 0 | 2016-12-11 | -6.1 | 24.1 | 0 | 22.42 | 0
2025-12-11 | -10.4 | 28.4 | 0 | 2024-12-11 | 1 | 17 | 0 | 2023-12-11 | -4.7 | 22.7 | 0 | 2022-12-11 | -6.7 | 24.7 | 0 | 2021-12-11 | 5.7 | 12.3 | 0 | 2020-12-11 | 2 | 16 | 0 | 2019-12-11 | -7.8 | 25.8 | 0 | 2018-12-11 | -7.3 | 25.3 | 0 | 2017-12-11 | -11.5 | 29.5 | 0 | 2016-12-11 | -6 | 24 | 0 | 22.57 | 0
2025-12-11 | -10.9 | 28.9 | 0 | 2024-12-11 | 1.1 | 16.9 | 0 | 2023-12-11 | -5 | 23 | 0 | 2022-12-11 | -8.2 | 26.2 | 0 | 2021-12-11 | 5 | 13 | 0 | 2020-12-11 | 2.1 | 15.9 | 0 | 2019-12-11 | -8.3 | 26.3 | 0 | 2018-12-11 | -7.2 | 25.2 | 0 | 2017-12-11 | -11.3 | 29.3 | 0 | 2016-12-11 | -5.9 | 23.9 | 0 | 22.86 | 0
2025-12-11 | -11.3 | 29.3 | 0 | 2024-12-11 | 0.7 | 17.3 | 0 | 2023-12-11 | -4.9 | 22.9 | 0 | 2022-12-11 | -7 | 25 | 0 | 2021-12-11 | 2.8 | 15.2 | 0 | 2020-12-11 | 1.4 | 16.6 | 0 | 2019-12-11 | -9.6 | 27.6 | 0 | 2018-12-11 | -7.7 | 25.7 | 0 | 2017-12-11 | -11.1 | 29.1 | 0 | 2016-12-11 | -5.8 | 23.8 | 0 | 23.25 | 0
2025-12-12 | -11.1 | 29.1 | 0 | 2024-12-12 | 1.1 | 16.9 | 0 | 2023-12-12 | -6.3 | 24.3 | 0 | 2022-12-12 | -6.4 | 24.4 | 0 | 2021-12-12 | 1.9 | 16.1 | 0 | 2020-12-12 | 1.3 | 16.7 | 0 | 2019-12-12 | -10 | 28 | 0 | 2018-12-12 | -7.5 | 25.5 | 0 | 2017-12-12 | -10.9 | 28.9 | 0 | 2016-12-12 | -5.9 | 23.9 | 0 | 23.38 | 0
2025-12-12 | -11.6 | 29.6 | 0 | 2024-12-12 | 0.4 | 17.6 | 0 | 2023-12-12 | -6.6 | 24.6 | 0 | 2022-12-12 | -6.2 | 24.2 | 0 | 2021-12-12 | 1.4 | 16.6 | 0 | 2020-12-12 | 0.6 | 17.4 | 0 | 2019-12-12 | -10.3 | 28.3 | 0 | 2018-12-12 | -7.1 | 25.1 | 0 | 2017-12-12 | -11 | 29 | 0 | 2016-12-12 | -5.8 | 23.8 | 0 | 23.62 | 0
2025-12-12 | -12 | 30 | 0 | 2024-12-12 | -0.6 | 18.6 | 0 | 2023-12-12 | -7.2 | 25.2 | 0 | 2022-12-12 | -5.9 | 23.9 | 0 | 2021-12-12 | 1.2 | 16.8 | 0 | 2020-12-12 | 1 | 17 | 0 | 2019-12-12 | -9.5 | 27.5 | 0 | 2018-12-12 | -7.5 | 25.5 | 0 | 2017-12-12 | -10.8 | 28.8 | 0 | 2016-12-12 | -5.4 | 23.4 | 0 | 23.67 | 0
2025-12-12 | -11.7 | 29.7 | 0 | 2024-12-12 | -0.9 | 18.9 | 0 | 2023-12-12 | -6.7 | 24.7 | 0 | 2022-12-12 | -5.7 | 23.7 | 0 | 2021-12-12 | 0.8 | 17.2 | 0 | 2020-12-12 | 0.9 | 17.1 | 0 | 2019-12-12 | -9.2 | 27.2 | 0 | 2018-12-12 | -7.1 | 25.1 | 0 | 2017-12-12 | -10.5 | 28.5 | 0 | 2016-12-12 | -5.3 | 23.3 | 0 | 23.54 | 0
2025-12-12 | -11.3 | 29.3 | 0 | 2024-12-12 | -0.7 | 18.7 | 0 | 2023-12-12 | -5.7 | 23.7 | 0 | 2022-12-12 | -4.9 | 22.9 | 0 | 2021-12-12 | -0.4 | 18.4 | 0 | 2020-12-12 | 1.1 | 16.9 | 0 | 2019-12-12 | -10.5 | 28.5 | 0 | 2018-12-12 | -9.1 | 27.1 | 0 | 2017-12-12 | -10.4 | 28.4 | 0 | 2016-12-12 | -5.3 | 23.3 | 0 | 23.72 | 0
2025-12-12 | -11.1 | 29.1 | 0 | 2024-12-12 | -0.7 | 18.7 | 0 | 2023-12-12 | -4.6 | 22.6 | 0 | 2022-12-12 | -4.8 | 22.8 | 0 | 2021-12-12 | -1.2 | 19.2 | 0 | 2020-12-12 | 1 | 17 | 0 | 2019-12-12 | -10.1 | 28.1 | 0 | 2018-12-12 | -7.5 | 25.5 | 0 | 2017-12-12 | -10.8 | 28.8 | 0 | 2016-12-12 | -5.7 | 23.7 | 0 | 23.55 | 0
2025-12-12 | -10.1 | 28.1 | 0 | 2024-12-12 | -1.1 | 19.1 | 0 | 2023-12-12 | -2.7 | 20.7 | 0 | 2022-12-12 | -5.2 | 23.2 | 0 | 2021-12-12 | -1.1 | 19.1 | 0 | 2020-12-12 | 1.1 | 16.9 | 0 | 2019-12-12 | -11.2 | 29.2 | 0 | 2018-12-12 | -9 | 27 | 0 | 2017-12-12 | -11 | 29 | 0 | 2016-12-12 | -5.4 | 23.4 | 0 | 23.57 | 0
2025-12-12 | -9.9 | 27.9 | 0 | 2024-12-12 | -1.3 | 19.3 | 0 | 2023-12-12 | -2 | 20 | 0 | 2022-12-12 | -6.4 | 24.4 | 0 | 2021-12-12 | -1 | 19 | 0 | 2020-12-12 | 0.6 | 17.4 | 0 | 2019-12-12 | -11.9 | 29.9 | 0 | 2018-12-12 | -8.3 | 26.3 | 0 | 2017-12-12 | -10.8 | 28.8 | 0 | 2016-12-12 | -5.3 | 23.3 | 0 | 23.63 | 0
2025-12-12 | -9.9 | 27.9 | 0 | 2024-12-12 | -1.4 | 19.4 | 0 | 2023-12-12 | -1.4 | 19.4 | 0 | 2022-12-12 | -8.4 | 26.4 | 0 | 2021-12-12 | -0.3 | 18.3 | 0 | 2020-12-12 | 0.4 | 17.6 | 0 | 2019-12-12 | -11.7 | 29.7 | 0 | 2018-12-12 | -8.7 | 26.7 | 0 | 2017-12-12 | -10.6 | 28.6 | 0 | 2016-12-12 | -5.5 | 23.5 | 0 | 23.75 | 0
2025-12-12 | -9.9 | 27.9 | 0 | 2024-12-12 | -1.5 | 19.5 | 0 | 2023-12-12 | -0.6 | 18.6 | 0 | 2022-12-12 | -7.4 | 25.4 | 0 | 2021-12-12 | 0.9 | 17.1 | 0 | 2020-12-12 | 0.4 | 17.6 | 0 | 2019-12-12 | -8.6 | 26.6 | 0 | 2018-12-12 | -8.2 | 26.2 | 0 | 2017-12-12 | -10.1 | 28.1 | 0 | 2016-12-12 | -5.2 | 23.2 | 0 | 23.02 | 0
2025-12-12 | -9 | 27 | 0 | 2024-12-12 | -1 | 19 | 0 | 2023-12-12 | 0 | 18 | 0 | 2022-12-12 | -6.5 | 24.5 | 0 | 2021-12-12 | 2.7 | 15.3 | 0 | 2020-12-12 | 0.5 | 17.5 | 0 | 2019-12-12 | -6.9 | 24.9 | 0 | 2018-12-12 | -7.9 | 25.9 | 0 | 2017-12-12 | -9.5 | 27.5 | 0 | 2016-12-12 | -4.8 | 22.8 | 0 | 22.24 | 0
2025-12-12 | -8.3 | 26.3 | 0 | 2024-12-12 | -1 | 19 | 0 | 2023-12-12 | 2.1 | 15.9 | 0 | 2022-12-12 | -6.1 | 24.1 | 0 | 2021-12-12 | 4 | 14 | 0 | 2020-12-12 | 0.4 | 17.6 | 0 | 2019-12-12 | -6.4 | 24.4 | 0 | 2018-12-12 | -7 | 25 | 0 | 2017-12-12 | -8.8 | 26.8 | 0 | 2016-12-12 | -4.8 | 22.8 | 0 | 21.59 | 0
2025-12-12 | -7.3 | 25.3 | 0 | 2024-12-12 | -1.9 | 19.9 | 0 | 2023-12-12 | 2.4 | 15.6 | 0 | 2022-12-12 | -5.4 | 23.4 | 0 | 2021-12-12 | 4.7 | 13.3 | 0 | 2020-12-12 | 0.2 | 17.8 | 0 | 2019-12-12 | -5.2 | 23.2 | 0 | 2018-12-12 | -6.1 | 24.1 | 0 | 2017-12-12 | -8.2 | 26.2 | 0 | 2016-12-12 | -4.4 | 22.4 | 0 | 21.12 | 0
2025-12-12 | -6.9 | 24.9 | 0 | 2024-12-12 | -3.2 | 21.2 | 0 | 2023-12-12 | 2.1 | 15.9 | 0 | 2022-12-12 | -4.9 | 22.9 | 0 | 2021-12-12 | 5.2 | 12.8 | 0 | 2020-12-12 | 0.2 | 17.8 | 0 | 2019-12-12 | -4.3 | 22.3 | 0 | 2018-12-12 | -6 | 24 | 0 | 2017-12-12 | -7.6 | 25.6 | 0 | 2016-12-12 | -4.3 | 22.3 | 0 | 20.97 | 0
2025-12-12 | -6.4 | 24.4 | 0 | 2024-12-12 | -3.6 | 21.6 | 0 | 2023-12-12 | 2.1 | 15.9 | 0 | 2022-12-12 | -4.4 | 22.4 | 0 | 2021-12-12 | 5.3 | 12.7 | 0 | 2020-12-12 | 0 | 18 | 0 | 2019-12-12 | -3 | 21 | 0 | 2018-12-12 | -6.5 | 24.5 | 0 | 2017-12-12 | -7 | 25 | 0 | 2016-12-12 | -4 | 22 | 0 | 20.75 | 0
2025-12-12 | -6.4 | 24.4 | 0 | 2024-12-12 | -3.6 | 21.6 | 0 | 2023-12-12 | 2.4 | 15.6 | 0 | 2022-12-12 | -4.5 | 22.5 | 0 | 2021-12-12 | 5.3 | 12.7 | 0 | 2020-12-12 | 0 | 18 | 0 | 2019-12-12 | -3.1 | 21.1 | 0 | 2018-12-12 | -7.1 | 25.1 | 0 | 2017-12-12 | -6.8 | 24.8 | 0 | 2016-12-12 | -4 | 22 | 0 | 20.78 | 0
2025-12-12 | -7 | 25 | 0 | 2024-12-12 | -3.9 | 21.9 | 0 | 2023-12-12 | 2.6 | 15.4 | 0 | 2022-12-12 | -6.4 | 24.4 | 0 | 2021-12-12 | 4.5 | 13.5 | 0 | 2020-12-12 | 0 | 18 | 0 | 2019-12-12 | -3.8 | 21.8 | 0 | 2018-12-12 | -8.3 | 26.3 | 0 | 2017-12-12 | -6.8 | 24.8 | 0 | 2016-12-12 | -3.8 | 21.8 | 0 | 21.29 | 0
2025-12-12 | -8.1 | 26.1 | 0 | 2024-12-12 | -4.1 | 22.1 | 0 | 2023-12-12 | 1.2 | 16.8 | 0 | 2022-12-12 | -6.2 | 24.2 | 0 | 2021-12-12 | 3.5 | 14.5 | 0 | 2020-12-12 | 0.1 | 17.9 | 0 | 2019-12-12 | -4.4 | 22.4 | 0 | 2018-12-12 | -9.2 | 27.2 | 0 | 2017-12-12 | -6.7 | 24.7 | 0 | 2016-12-12 | -4.4 | 22.4 | 0 | 21.83 | 0
2025-12-12 | -9.3 | 27.3 | 0 | 2024-12-12 | -6 | 24 | 0 | 2023-12-12 | 1.2 | 16.8 | 0 | 2022-12-12 | -8.5 | 26.5 | 0 | 2021-12-12 | 2.8 | 15.2 | 0 | 2020-12-12 | 0.3 | 17.7 | 0 | 2019-12-12 | -4.4 | 22.4 | 0 | 2018-12-12 | -10.8 | 28.8 | 0 | 2017-12-12 | -7.1 | 25.1 | 0 | 2016-12-12 | -3.4 | 21.4 | 0 | 22.52 | 0
2025-12-12 | -9.2 | 27.2 | 0 | 2024-12-12 | -6.8 | 24.8 | 0 | 2023-12-12 | 0.8 | 17.2 | 0 | 2022-12-12 | -9.1 | 27.1 | 0 | 2021-12-12 | 3.1 | 14.9 | 0 | 2020-12-12 | 0.5 | 17.5 | 0 | 2019-12-12 | -4.5 | 22.5 | 0 | 2018-12-12 | -11.8 | 29.8 | 0 | 2017-12-12 | -8 | 26 | 0 | 2016-12-12 | -3.7 | 21.7 | 0 | 22.87 | 0
2025-12-12 | -10.9 | 28.9 | 0 | 2024-12-12 | -7.6 | 25.6 | 0 | 2023-12-12 | 0.2 | 17.8 | 0 | 2022-12-12 | -9.6 | 27.6 | 0 | 2021-12-12 | 3.5 | 14.5 | 0 | 2020-12-12 | 0.7 | 17.3 | 0 | 2019-12-12 | -5.1 | 23.1 | 0 | 2018-12-12 | -11.8 | 29.8 | 0 | 2017-12-12 | -8.3 | 26.3 | 0 | 2016-12-12 | -3.2 | 21.2 | 0 | 23.21 | 0
2025-12-12 | -12.4 | 30.4 | 0 | 2024-12-12 | -9.5 | 27.5 | 0 | 2023-12-12 | 0 | 18 | 0 | 2022-12-12 | -8.3 | 26.3 | 0 | 2021-12-12 | 3.5 | 14.5 | 0 | 2020-12-12 | 1 | 17 | 0 | 2019-12-12 | -4.6 | 22.6 | 0 | 2018-12-12 | -12.1 | 30.1 | 0 | 2017-12-12 | -9 | 27 | 0 | 2016-12-12 | -2.9 | 20.9 | 0 | 23.43 | 0
2025-12-12 | -13.4 | 31.4 | 0 | 2024-12-12 | -9.7 | 27.7 | 0 | 2023-12-12 | -0.3 | 18.3 | 0 | 2022-12-12 | -8.5 | 26.5 | 0 | 2021-12-12 | 3.2 | 14.8 | 0 | 2020-12-12 | 1.2 | 16.8 | 0 | 2019-12-12 | -4.3 | 22.3 | 0 | 2018-12-12 | -12.7 | 30.7 | 0 | 2017-12-12 | -9.6 | 27.6 | 0 | 2016-12-12 | -3.4 | 21.4 | 0 | 23.75 | 0
2025-12-12 | -13.8 | 31.8 | 0 | 2024-12-12 | -10.4 | 28.4 | 0 | 2023-12-12 | -0.8 | 18.8 | 0 | 2022-12-12 | -8 | 26 | 0 | 2021-12-12 | 3.7 | 14.3 | 0 | 2020-12-12 | 1.5 | 16.5 | 0 | 2019-12-12 | -4.5 | 22.5 | 0 | 2018-12-12 | -13.1 | 31.1 | 0 | 2017-12-12 | -9.9 | 27.9 | 0 | 2016-12-12 | -3.3 | 21.3 | 0 | 23.86 | 0
2025-12-13 | -14.6 | 32.6 | 0 | 2024-12-13 | -10.7 | 28.7 | 0 | 2023-12-13 | -0.7 | 18.7 | 0 | 2022-12-13 | -11.2 | 29.2 | 0 | 2021-12-13 | 3.3 | 14.7 | 0 | 2020-12-13 | 1.6 | 16.4 | 0 | 2019-12-13 | -4.4 | 22.4 | 0 | 2018-12-13 | -13.8 | 31.8 | 0 | 2017-12-13 | -10.2 | 28.2 | 0 | 2016-12-13 | -3.7 | 21.7 | 0 | 24.44 | 0
2025-12-13 | -13.4 | 31.4 | 0 | 2024-12-13 | -10 | 28 | 0 | 2023-12-13 | -1.4 | 19.4 | 0 | 2022-12-13 | -11.4 | 29.4 | 0 | 2021-12-13 | 3.3 | 14.7 | 0 | 2020-12-13 | 1.8 | 16.2 | 0 | 2019-12-13 | -4.4 | 22.4 | 0 | 2018-12-13 | -14.3 | 32.3 | 0 | 2017-12-13 | -10.4 | 28.4 | 0 | 2016-12-13 | -3.9 | 21.9 | 0 | 24.41 | 0
2025-12-13 | -13.7 | 31.7 | 0 | 2024-12-13 | -9.9 | 27.9 | 0 | 2023-12-13 | -2.4 | 20.4 | 0 | 2022-12-13 | -11.3 | 29.3 | 0 | 2021-12-13 | 3 | 15 | 0 | 2020-12-13 | 1.6 | 16.4 | 0 | 2019-12-13 | -4.5 | 22.5 | 0 | 2018-12-13 | -14.6 | 32.6 | 0 | 2017-12-13 | -10.5 | 28.5 | 0 | 2016-12-13 | -4 | 22 | 0 | 24.63 | 0
2025-12-13 | -12.6 | 30.6 | 0 | 2024-12-13 | -9.5 | 27.5 | 0 | 2023-12-13 | -1.4 | 19.4 | 0 | 2022-12-13 | -10.7 | 28.7 | 0 | 2021-12-13 | 2.7 | 15.3 | 0 | 2020-12-13 | 4.4 | 13.6 | 0 | 2019-12-13 | -4.2 | 22.2 | 0 | 2018-12-13 | -14.8 | 32.8 | 0 | 2017-12-13 | -11.2 | 29.2 | 0 | 2016-12-13 | -4.2 | 22.2 | 0 | 24.15 | 0
2025-12-13 | -11.2 | 29.2 | 0 | 2024-12-13 | -8.8 | 26.8 | 0 | 2023-12-13 | -1.2 | 19.2 | 0 | 2022-12-13 | -10.7 | 28.7 | 0 | 2021-12-13 | 3.1 | 14.9 | 0 | 2020-12-13 | 5.9 | 12.1 | 0 | 2019-12-13 | -4.9 | 22.9 | 0 | 2018-12-13 | -15.1 | 33.1 | 0 | 2017-12-13 | -11.8 | 29.8 | 0 | 2016-12-13 | -4.7 | 22.7 | 0 | 23.94 | 0
2025-12-13 | -10.8 | 28.8 | 0 | 2024-12-13 | -9.9 | 27.9 | 0 | 2023-12-13 | -1.7 | 19.7 | 0 | 2022-12-13 | -11.9 | 29.9 | 0 | 2021-12-13 | 3.2 | 14.8 | 0 | 2020-12-13 | 6.5 | 11.5 | 0 | 2019-12-13 | -4.9 | 22.9 | 0 | 2018-12-13 | -15.6 | 33.6 | 0 | 2017-12-13 | -12.6 | 30.6 | 0 | 2016-12-13 | -5 | 23 | 0 | 24.27 | 0
2025-12-13 | -11.1 | 29.1 | 0 | 2024-12-13 | -10.2 | 28.2 | 0 | 2023-12-13 | -1.8 | 19.8 | 0 | 2022-12-13 | -12.6 | 30.6 | 0 | 2021-12-13 | 3.5 | 14.5 | 0 | 2020-12-13 | 6.6 | 11.4 | 0 | 2019-12-13 | -5.3 | 23.3 | 0 | 2018-12-13 | -15.6 | 33.6 | 0 | 2017-12-13 | -13.2 | 31.2 | 0 | 2016-12-13 | -5.2 | 23.2 | 0 | 24.49 | 0
2025-12-13 | -10.9 | 28.9 | 0 | 2024-12-13 | -11.1 | 29.1 | 0 | 2023-12-13 | -2.5 | 20.5 | 0 | 2022-12-13 | -12.1 | 30.1 | 0 | 2021-12-13 | 3.6 | 14.4 | 0 | 2020-12-13 | 6 | 12 | 0 | 2019-12-13 | -4.5 | 22.5 | 0 | 2018-12-13 | -15.7 | 33.7 | 0 | 2017-12-13 | -13.6 | 31.6 | 0 | 2016-12-13 | -6.1 | 24.1 | 0 | 24.69 | 0
2025-12-13 | -11.3 | 29.3 | 0 | 2024-12-13 | -11.6 | 29.6 | 0 | 2023-12-13 | -3.1 | 21.1 | 0 | 2022-12-13 | -12.4 | 30.4 | 0 | 2021-12-13 | 3.9 | 14.1 | 0 | 2020-12-13 | 4.3 | 13.7 | 0 | 2019-12-13 | -3.8 | 21.8 | 0 | 2018-12-13 | -15.7 | 33.7 | 0 | 2017-12-13 | -14.2 | 32.2 | 0 | 2016-12-13 | -5.5 | 23.5 | 0 | 24.94 | 0
2025-12-13 | -10.9 | 28.9 | 0 | 2024-12-13 | -10 | 28 | 0 | 2023-12-13 | -2.5 | 20.5 | 0 | 2022-12-13 | -9.7 | 27.7 | 0 | 2021-12-13 | 4.1 | 13.9 | 0 | 2020-12-13 | 3.1 | 14.9 | 0 | 2019-12-13 | -2.3 | 20.3 | 0 | 2018-12-13 | -14.9 | 32.9 | 0 | 2017-12-13 | -14.5 | 32.5 | 0 | 2016-12-13 | -4.6 | 22.6 | 0 | 24.22 | 0
2025-12-13 | -8.8 | 26.8 | 0 | 2024-12-13 | -8 | 26 | 0 | 2023-12-13 | -1.4 | 19.4 | 0 | 2022-12-13 | -8.2 | 26.2 | 0 | 2021-12-13 | 4.6 | 13.4 | 0 | 2020-12-13 | 0.4 | 17.6 | 0 | 2019-12-13 | -0.8 | 18.8 | 0 | 2018-12-13 | -13.3 | 31.3 | 0 | 2017-12-13 | -14.3 | 32.3 | 0 | 2016-12-13 | -3 | 21 | 0 | 23.28 | 0
2025-12-13 | -4.1 | 22.1 | 0 | 2024-12-13 | -6.8 | 24.8 | 0 | 2023-12-13 | -1.5 | 19.5 | 0 | 2022-12-13 | -7 | 25 | 0 | 2021-12-13 | 6.2 | 11.8 | 0 | 2020-12-13 | -0.9 | 18.9 | 0 | 2019-12-13 | 0.7 | 17.3 | 0 | 2018-12-13 | -12.2 | 30.2 | 0 | 2017-12-13 | -14.2 | 32.2 | 0 | 2016-12-13 | -0.8 | 18.8 | 0 | 22.06 | 0
2025-12-13 | -3.4 | 21.4 | 0 | 2024-12-13 | -6 | 24 | 0 | 2023-12-13 | -1.6 | 19.6 | 0 | 2022-12-13 | -5.5 | 23.5 | 0 | 2021-12-13 | 6.9 | 11.1 | 0 | 2020-12-13 | -1.4 | 19.4 | 0 | 2019-12-13 | 2.7 | 15.3 | 0 | 2018-12-13 | -11.2 | 29.2 | 0 | 2017-12-13 | -13.8 | 31.8 | 0 | 2016-12-13 | 0 | 18 | 0 | 21.33 | 0
2025-12-13 | -3.1 | 21.1 | 0 | 2024-12-13 | -5.3 | 23.3 | 0 | 2023-12-13 | -1.9 | 19.9 | 0 | 2022-12-13 | -4.3 | 22.3 | 0 | 2021-12-13 | 7.8 | 10.2 | 0 | 2020-12-13 | -1.8 | 19.8 | 0 | 2019-12-13 | 2.7 | 15.3 | 0 | 2018-12-13 | -10.5 | 28.5 | 0 | 2017-12-13 | -13.2 | 31.2 | 0 | 2016-12-13 | 0.1 | 17.9 | 0 | 20.95 | 0
2025-12-13 | -2.8 | 20.8 | 0 | 2024-12-13 | -5.3 | 23.3 | 0 | 2023-12-13 | -1.6 | 19.6 | 0 | 2022-12-13 | -3.3 | 21.3 | 0 | 2021-12-13 | 8.1 | 9.9 | 0 | 2020-12-13 | -1.6 | 19.6 | 0 | 2019-12-13 | 3.4 | 14.6 | 0 | 2018-12-13 | -9.8 | 27.8 | 0 | 2017-12-13 | -12.4 | 30.4 | 0 | 2016-12-13 | 0.7 | 17.3 | 0 | 20.46 | 0
2025-12-13 | -2 | 20 | 0 | 2024-12-13 | -5.4 | 23.4 | 0 | 2023-12-13 | -1.7 | 19.7 | 0 | 2022-12-13 | -3 | 21 | 0 | 2021-12-13 | 8 | 10 | 0 | 2020-12-13 | -2 | 20 | 0 | 2019-12-13 | 3.5 | 14.5 | 0 | 2018-12-13 | -9.6 | 27.6 | 0 | 2017-12-13 | -12.7 | 30.7 | 0 | 2016-12-13 | 0.9 | 17.1 | 0 | 20.4 | 0
2025-12-13 | -2.4 | 20.4 | 0 | 2024-12-13 | -7.7 | 25.7 | 0 | 2023-12-13 | -2.3 | 20.3 | 0 | 2022-12-13 | -4 | 22 | 0 | 2021-12-13 | 6.5 | 11.5 | 0 | 2020-12-13 | -2.8 | 20.8 | 0 | 2019-12-13 | 2 | 16 | 0 | 2018-12-13 | -9.5 | 27.5 | 0 | 2017-12-13 | -13.2 | 31.2 | 0 | 2016-12-13 | 0.5 | 17.5 | 0 | 21.29 | 0
2025-12-13 | -4.8 | 22.8 | 0 | 2024-12-13 | -7.8 | 25.8 | 0 | 2023-12-13 | -3.4 | 21.4 | 0 | 2022-12-13 | -5.7 | 23.7 | 0 | 2021-12-13 | 5.2 | 12.8 | 0 | 2020-12-13 | -3 | 21 | 0 | 2019-12-13 | 0.2 | 17.8 | 0 | 2018-12-13 | -9.4 | 27.4 | 0 | 2017-12-13 | -14.9 | 32.9 | 0 | 2016-12-13 | 0 | 18 | 0 | 22.36 | 0
2025-12-13 | -6.5 | 24.5 | 0 | 2024-12-13 | -9.1 | 27.1 | 0 | 2023-12-13 | -3.4 | 21.4 | 0 | 2022-12-13 | -4.7 | 22.7 | 0 | 2021-12-13 | 4.4 | 13.6 | 0 | 2020-12-13 | -2.9 | 20.9 | 0 | 2019-12-13 | 1.4 | 16.6 | 0 | 2018-12-13 | -9.4 | 27.4 | 0 | 2017-12-13 | -14.4 | 32.4 | 0 | 2016-12-13 | -0.3 | 18.3 | 0 | 22.49 | 0
2025-12-13 | -6.6 | 24.6 | 0 | 2024-12-13 | -8.1 | 26.1 | 0 | 2023-12-13 | -4.4 | 22.4 | 0 | 2022-12-13 | -4.2 | 22.2 | 0 | 2021-12-13 | 4 | 14 | 0 | 2020-12-13 | -2.9 | 20.9 | 0 | 2019-12-13 | 1.8 | 16.2 | 0 | 2018-12-13 | -9.6 | 27.6 | 0 | 2017-12-13 | -13.9 | 31.9 | 0 | 2016-12-13 | -1.1 | 19.1 | 0 | 22.5 | 0
2025-12-13 | -6.6 | 24.6 | 0 | 2024-12-13 | -7.7 | 25.7 | 0 | 2023-12-13 | -5.7 | 23.7 | 0 | 2022-12-13 | -4.7 | 22.7 | 0 | 2021-12-13 | 3.1 | 14.9 | 0 | 2020-12-13 | -3.1 | 21.1 | 0 | 2019-12-13 | 1 | 17 | 0 | 2018-12-13 | -8.9 | 26.9 | 0 | 2017-12-13 | -15.1 | 33.1 | 0 | 2016-12-13 | -1.2 | 19.2 | 0 | 22.89 | 0
2025-12-13 | -7.2 | 25.2 | 0 | 2024-12-13 | -7.8 | 25.8 | 0 | 2023-12-13 | -6.2 | 24.2 | 0 | 2022-12-13 | -4.7 | 22.7 | 0 | 2021-12-13 | 2.1 | 15.9 | 0 | 2020-12-13 | -3.4 | 21.4 | 0 | 2019-12-13 | 1 | 17 | 0 | 2018-12-13 | -8.6 | 26.6 | 0 | 2017-12-13 | -15.4 | 33.4 | 0 | 2016-12-13 | -2.3 | 20.3 | 0 | 23.25 | 0
2025-12-13 | -9 | 27 | 0 | 2024-12-13 | -7.4 | 25.4 | 0 | 2023-12-13 | -7.2 | 25.2 | 0 | 2022-12-13 | -5.1 | 23.1 | 0 | 2021-12-13 | 1.5 | 16.5 | 0 | 2020-12-13 | -3.5 | 21.5 | 0 | 2019-12-13 | 0.8 | 17.2 | 0 | 2018-12-13 | -8.5 | 26.5 | 0 | 2017-12-13 | -15.8 | 33.8 | 0 | 2016-12-13 | -3.7 | 21.7 | 0 | 23.79 | 0
2025-12-13 | -8.6 | 26.6 | 0 | 2024-12-13 | -8.3 | 26.3 | 0 | 2023-12-13 | -7.2 | 25.2 | 0 | 2022-12-13 | -5.2 | 23.2 | 0 | 2021-12-13 | 0.7 | 17.3 | 0 | 2020-12-13 | -3.7 | 21.7 | 0 | 2019-12-13 | 0.4 | 17.6 | 0 | 2018-12-13 | -8.2 | 26.2 | 0 | 2017-12-13 | -16.2 | 34.2 | 0 | 2016-12-13 | -3.5 | 21.5 | 0 | 23.98 | 0
2025-12-14 | -8.6 | 26.6 | 0 | 2024-12-14 | -9.4 | 27.4 | 0 | 2023-12-14 | -7.9 | 25.9 | 0 | 2022-12-14 | -6.4 | 24.4 | 0 | 2021-12-14 | 1.9 | 16.1 | 0 | 2020-12-14 | -3.9 | 21.9 | 0 | 2019-12-14 | 0.1 | 17.9 | 0 | 2018-12-14 | -8 | 26 | 0 | 2017-12-14 | -16.9 | 34.9 | 0 | 2016-12-14 | -4.2 | 22.2 | 0 | 24.33 | 0
2025-12-14 | -8.8 | 26.8 | 0 | 2024-12-14 | -10.2 | 28.2 | 0 | 2023-12-14 | -9.2 | 27.2 | 0 | 2022-12-14 | -7 | 25 | 0 | 2021-12-14 | 1.8 | 16.2 | 0 | 2020-12-14 | -4 | 22 | 0 | 2019-12-14 | 0 | 18 | 0 | 2018-12-14 | -7.8 | 25.8 | 0 | 2017-12-14 | -17.3 | 35.3 | 0 | 2016-12-14 | -4.2 | 22.2 | 0 | 24.67 | 0
2025-12-14 | -9.4 | 27.4 | 0 | 2024-12-14 | -10.3 | 28.3 | 0 | 2023-12-14 | -10.3 | 28.3 | 0 | 2022-12-14 | -8 | 26 | 0 | 2021-12-14 | 1.6 | 16.4 | 0 | 2020-12-14 | -4 | 22 | 0 | 2019-12-14 | -0.1 | 18.1 | 0 | 2018-12-14 | -7.6 | 25.6 | 0 | 2017-12-14 | -18.1 | 36.1 | 0 | 2016-12-14 | -4.1 | 22.1 | 0 | 25.03 | 0
2025-12-14 | -10.8 | 28.8 | 0 | 2024-12-14 | -11.3 | 29.3 | 0 | 2023-12-14 | -9.7 | 27.7 | 0 | 2022-12-14 | -8.4 | 26.4 | 0 | 2021-12-14 | 1.4 | 16.6 | 0 | 2020-12-14 | -4 | 22 | 0 | 2019-12-14 | 0.2 | 17.8 | 0 | 2018-12-14 | -8.4 | 26.4 | 0 | 2017-12-14 | -18.8 | 36.8 | 0 | 2016-12-14 | -5.2 | 23.2 | 0 | 25.5 | 0
2025-12-14 | -9.6 | 27.6 | 0 | 2024-12-14 | -11.8 | 29.8 | 0 | 2023-12-14 | -9.8 | 27.8 | 0 | 2022-12-14 | -8.9 | 26.9 | 0 | 2021-12-14 | 0.1 | 17.9 | 0 | 2020-12-14 | -3.9 | 21.9 | 0 | 2019-12-14 | 0.3 | 17.7 | 0 | 2018-12-14 | -8 | 26 | 0 | 2017-12-14 | -19.1 | 37.1 | 0 | 2016-12-14 | -6 | 24 | 0 | 25.67 | 0
2025-12-14 | -10.5 | 28.5 | 0 | 2024-12-14 | -13.1 | 31.1 | 0 | 2023-12-14 | -9.8 | 27.8 | 0 | 2022-12-14 | -9.1 | 27.1 | 0 | 2021-12-14 | 0.3 | 17.7 | 0 | 2020-12-14 | -4 | 22 | 0 | 2019-12-14 | 0.5 | 17.5 | 0 | 2018-12-14 | -7.7 | 25.7 | 0 | 2017-12-14 | -19.4 | 37.4 | 0 | 2016-12-14 | -6.8 | 24.8 | 0 | 25.96 | 0
2025-12-14 | -11.4 | 29.4 | 0 | 2024-12-14 | -12.3 | 30.3 | 0 | 2023-12-14 | -9.1 | 27.1 | 0 | 2022-12-14 | -9.8 | 27.8 | 0 | 2021-12-14 | -1.2 | 19.2 | 0 | 2020-12-14 | -4.1 | 22.1 | 0 | 2019-12-14 | 0.7 | 17.3 | 0 | 2018-12-14 | -7.5 | 25.5 | 0 | 2017-12-14 | -21.2 | 39.2 | 0 | 2016-12-14 | -7.5 | 25.5 | 0 | 26.34 | 0
2025-12-14 | -10.1 | 28.1 | 0 | 2024-12-14 | -13.9 | 31.9 | 0 | 2023-12-14 | -10 | 28 | 0 | 2022-12-14 | -11.2 | 29.2 | 0 | 2021-12-14 | -0.9 | 18.9 | 0 | 2020-12-14 | -4.3 | 22.3 | 0 | 2019-12-14 | 1.1 | 16.9 | 0 | 2018-12-14 | -7.5 | 25.5 | 0 | 2017-12-14 | -20.6 | 38.6 | 0 | 2016-12-14 | -8.2 | 26.2 | 0 | 26.56 | 0
2025-12-14 | -10.6 | 28.6 | 0 | 2024-12-14 | -12.4 | 30.4 | 0 | 2023-12-14 | -9 | 27 | 0 | 2022-12-14 | -10.1 | 28.1 | 0 | 2021-12-14 | -1 | 19 | 0 | 2020-12-14 | -4.5 | 22.5 | 0 | 2019-12-14 | 1.4 | 16.6 | 0 | 2018-12-14 | -6.7 | 24.7 | 0 | 2017-12-14 | -21.8 | 39.8 | 0 | 2016-12-14 | -7.7 | 25.7 | 0 | 26.24 | 0
2025-12-14 | -11.4 | 29.4 | 0 | 2024-12-14 | -12.3 | 30.3 | 0 | 2023-12-14 | -7.5 | 25.5 | 0 | 2022-12-14 | -8.7 | 26.7 | 0 | 2021-12-14 | -0.7 | 18.7 | 0 | 2020-12-14 | -4.2 | 22.2 | 0 | 2019-12-14 | 1.8 | 16.2 | 0 | 2018-12-14 | -5.8 | 23.8 | 0 | 2017-12-14 | -20.1 | 38.1 | 0 | 2016-12-14 | -8.3 | 26.3 | 0 | 25.72 | 0
2025-12-14 | -11.1 | 29.1 | 0 | 2024-12-14 | -10.1 | 28.1 | 0 | 2023-12-14 | -4.9 | 22.9 | 0 | 2022-12-14 | -7.5 | 25.5 | 0 | 2021-12-14 | -0.2 | 18.2 | 0 | 2020-12-14 | -3.7 | 21.7 | 0 | 2019-12-14 | 2.4 | 15.6 | 0 | 2018-12-14 | -4.5 | 22.5 | 0 | 2017-12-14 | -18.2 | 36.2 | 0 | 2016-12-14 | -7.9 | 25.9 | 0 | 24.57 | 0
2025-12-14 | -11.3 | 29.3 | 0 | 2024-12-14 | -9 | 27 | 0 | 2023-12-14 | -2.7 | 20.7 | 0 | 2022-12-14 | -6.4 | 24.4 | 0 | 2021-12-14 | 0.3 | 17.7 | 0 | 2020-12-14 | -3.2 | 21.2 | 0 | 2019-12-14 | 2.8 | 15.2 | 0 | 2018-12-14 | -2.5 | 20.5 | 0 | 2017-12-14 | -17.3 | 35.3 | 0 | 2016-12-14 | -7 | 25 | 0 | 23.63 | 0
2025-12-14 | -10.8 | 28.8 | 0 | 2024-12-14 | -8.3 | 26.3 | 0 | 2023-12-14 | -1.9 | 19.9 | 0 | 2022-12-14 | -4.5 | 22.5 | 0 | 2021-12-14 | 0.7 | 17.3 | 0 | 2020-12-14 | -2.6 | 20.6 | 0 | 2019-12-14 | 3.1 | 14.9 | 0 | 2018-12-14 | -1.1 | 19.1 | 0 | 2017-12-14 | -16.5 | 34.5 | 0 | 2016-12-14 | -6 | 24 | 0 | 22.79 | 0
2025-12-14 | -10.2 | 28.2 | 0 | 2024-12-14 | -7.2 | 25.2 | 0 | 2023-12-14 | -0.6 | 18.6 | 0 | 2022-12-14 | -3.5 | 21.5 | 0 | 2021-12-14 | 1.1 | 16.9 | 0 | 2020-12-14 | -2.2 | 20.2 | 0 | 2019-12-14 | 3.6 | 14.4 | 0 | 2018-12-14 | -0.7 | 18.7 | 0 | 2017-12-14 | -16.1 | 34.1 | 0 | 2016-12-14 | -5.6 | 23.6 | 0 | 22.14 | 0
2025-12-14 | -10.5 | 28.5 | 0 | 2024-12-14 | -7 | 25 | 0 | 2023-12-14 | 1 | 17 | 0 | 2022-12-14 | -2.9 | 20.9 | 0 | 2021-12-14 | 1.3 | 16.7 | 0 | 2020-12-14 | -2.5 | 20.5 | 0 | 2019-12-14 | 3.8 | 14.2 | 0 | 2018-12-14 | -0.2 | 18.2 | 0 | 2017-12-14 | -15.2 | 33.2 | 0 | 2016-12-14 | -5.6 | 23.6 | 0 | 21.78 | 0
2025-12-14 | -10.6 | 28.6 | 0 | 2024-12-14 | -7 | 25 | 0 | 2023-12-14 | 1.2 | 16.8 | 0 | 2022-12-14 | -2.7 | 20.7 | 0 | 2021-12-14 | 0.8 | 17.2 | 0 | 2020-12-14 | -2.6 | 20.6 | 0 | 2019-12-14 | 3.6 | 14.4 | 0 | 2018-12-14 | 0.1 | 17.9 | 0 | 2017-12-14 | -14.6 | 32.6 | 0 | 2016-12-14 | -5.9 | 23.9 | 0 | 21.77 | 0
2025-12-14 | -12.2 | 30.2 | 0 | 2024-12-14 | -7.9 | 25.9 | 0 | 2023-12-14 | 1 | 17 | 0 | 2022-12-14 | -4.2 | 22.2 | 0 | 2021-12-14 | -0.9 | 18.9 | 0 | 2020-12-14 | -2.6 | 20.6 | 0 | 2019-12-14 | 2.2 | 15.8 | 0 | 2018-12-14 | 0.1 | 17.9 | 0 | 2017-12-14 | -15.1 | 33.1 | 0 | 2016-12-14 | -5.7 | 23.7 | 0 | 22.53 | 0
2025-12-14 | -12.7 | 30.7 | 0 | 2024-12-14 | -9.7 | 27.7 | 0 | 2023-12-14 | 0.8 | 17.2 | 0 | 2022-12-14 | -4.2 | 22.2 | 0 | 2021-12-14 | -2 | 20 | 0 | 2020-12-14 | -2.6 | 20.6 | 0 | 2019-12-14 | 1.7 | 16.3 | 0 | 2018-12-14 | 0 | 18 | 0 | 2017-12-14 | -16 | 34 | 0 | 2016-12-14 | -6.1 | 24.1 | 0 | 23.08 | 0
2025-12-14 | -13.2 | 31.2 | 0 | 2024-12-14 | -10.6 | 28.6 | 0 | 2023-12-14 | 0.6 | 17.4 | 0 | 2022-12-14 | -5.1 | 23.1 | 0 | 2021-12-14 | -3.3 | 21.3 | 0 | 2020-12-14 | -1.9 | 19.9 | 0 | 2019-12-14 | 1.4 | 16.6 | 0 | 2018-12-14 | 0.2 | 17.8 | 0 | 2017-12-14 | -16.6 | 34.6 | 0 | 2016-12-14 | -6.3 | 24.3 | 0 | 23.48 | 0
2025-12-14 | -13.9 | 31.9 | 0 | 2024-12-14 | -11 | 29 | 0 | 2023-12-14 | 0.4 | 17.6 | 0 | 2022-12-14 | -6.2 | 24.2 | 0 | 2021-12-14 | -4.1 | 22.1 | 0 | 2020-12-14 | -1.6 | 19.6 | 0 | 2019-12-14 | 1.4 | 16.6 | 0 | 2018-12-14 | 0.1 | 17.9 | 0 | 2017-12-14 | -17 | 35 | 0 | 2016-12-14 | -6.6 | 24.6 | 0 | 23.85 | 0
2025-12-14 | -14.4 | 32.4 | 0 | 2024-12-14 | -11.4 | 29.4 | 0 | 2023-12-14 | 0.2 | 17.8 | 0 | 2022-12-14 | -4.3 | 22.3 | 0 | 2021-12-14 | -4.1 | 22.1 | 0 | 2020-12-14 | -2.2 | 20.2 | 0 | 2019-12-14 | 1.5 | 16.5 | 0 | 2018-12-14 | 0.1 | 17.9 | 0 | 2017-12-14 | -18 | 36 | 0 | 2016-12-14 | -7 | 25 | 0 | 23.96 | 0
2025-12-14 | -14.7 | 32.7 | 0 | 2024-12-14 | -12.6 | 30.6 | 0 | 2023-12-14 | 0.8 | 17.2 | 0 | 2022-12-14 | -4.8 | 22.8 | 0 | 2021-12-14 | -4.3 | 22.3 | 0 | 2020-12-14 | -3 | 21 | 0 | 2019-12-14 | 0.2 | 17.8 | 0 | 2018-12-14 | 1.3 | 16.7 | 0 | 2017-12-14 | -18.2 | 36.2 | 0 | 2016-12-14 | -8.3 | 26.3 | 0 | 24.36 | 0
2025-12-14 | -15.2 | 33.2 | 0 | 2024-12-14 | -12.2 | 30.2 | 0 | 2023-12-14 | 0.8 | 17.2 | 0 | 2022-12-14 | -6.5 | 24.5 | 0 | 2021-12-14 | -5 | 23 | 0 | 2020-12-14 | -3.8 | 21.8 | 0 | 2019-12-14 | 0.2 | 17.8 | 0 | 2018-12-14 | 2.1 | 15.9 | 0 | 2017-12-14 | -18.5 | 36.5 | 0 | 2016-12-14 | -8.8 | 26.8 | 0 | 24.69 | 0
2025-12-14 | -15.5 | 33.5 | 0 | 2024-12-14 | -12 | 30 | 0 | 2023-12-14 | 0.9 | 17.1 | 0 | 2022-12-14 | -6.2 | 24.2 | 0 | 2021-12-14 | -4.3 | 22.3 | 0 | 2020-12-14 | -4.6 | 22.6 | 0 | 2019-12-14 | 0.2 | 17.8 | 0 | 2018-12-14 | 1.9 | 16.1 | 0 | 2017-12-14 | -19.6 | 37.6 | 0 | 2016-12-14 | -9.2 | 27.2 | 0 | 24.84 | 0
2025-12-15 | -15.5 | 33.5 | 0 | 2024-12-15 | -14.6 | 32.6 | 0 | 2023-12-15 | 1 | 17 | 0 | 2022-12-15 | -5.5 | 23.5 | 0 | 2021-12-15 | -5.7 | 23.7 | 0 | 2020-12-15 | -4.9 | 22.9 | 0 | 2019-12-15 | 0.2 | 17.8 | 0 | 2018-12-15 | 1.8 | 16.2 | 0 | 2017-12-15 | -19.7 | 37.7 | 0 | 2016-12-15 | -9.9 | 27.9 | 0 | 25.28 | 0
2025-12-15 | -16.6 | 34.6 | 0 | 2024-12-15 | -13.5 | 31.5 | 0 | 2023-12-15 | 1.3 | 16.7 | 0 | 2022-12-15 | -4.8 | 22.8 | 0 | 2021-12-15 | -5 | 23 | 0 | 2020-12-15 | -5.7 | 23.7 | 0 | 2019-12-15 | 0 | 18 | 0 | 2018-12-15 | 1.8 | 16.2 | 0 | 2017-12-15 | -19.9 | 37.9 | 0 | 2016-12-15 | -10.9 | 28.9 | 0 | 25.33 | 0
2025-12-15 | -15.3 | 33.3 | 0 | 2024-12-15 | -14.2 | 32.2 | 0 | 2023-12-15 | 1.7 | 16.3 | 0 | 2022-12-15 | -3.8 | 21.8 | 0 | 2021-12-15 | -4.9 | 22.9 | 0 | 2020-12-15 | -6 | 24 | 0 | 2019-12-15 | -0.4 | 18.4 | 0 | 2018-12-15 | 1.1 | 16.9 | 0 | 2017-12-15 | -20 | 38 | 0 | 2016-12-15 | -10.9 | 28.9 | 0 | 25.27 | 0
2025-12-15 | -15.3 | 33.3 | 0 | 2024-12-15 | -14.5 | 32.5 | 0 | 2023-12-15 | 1.5 | 16.5 | 0 | 2022-12-15 | -2.8 | 20.8 | 0 | 2021-12-15 | -4.3 | 22.3 | 0 | 2020-12-15 | -6.8 | 24.8 | 0 | 2019-12-15 | -0.1 | 18.1 | 0 | 2018-12-15 | 1.2 | 16.8 | 0 | 2017-12-15 | -20.3 | 38.3 | 0 | 2016-12-15 | -10.3 | 28.3 | 0 | 25.17 | 0
2025-12-15 | -14.4 | 32.4 | 0 | 2024-12-15 | -15.1 | 33.1 | 0 | 2023-12-15 | 1.3 | 16.7 | 0 | 2022-12-15 | -1.4 | 19.4 | 0 | 2021-12-15 | -4.5 | 22.5 | 0 | 2020-12-15 | -7.4 | 25.4 | 0 | 2019-12-15 | 0 | 18 | 0 | 2018-12-15 | 1.4 | 16.6 | 0 | 2017-12-15 | -20.3 | 38.3 | 0 | 2016-12-15 | -10.6 | 28.6 | 0 | 25.1 | 0
2025-12-15 | -13.9 | 31.9 | 0 | 2024-12-15 | -14.7 | 32.7 | 0 | 2023-12-15 | 1.3 | 16.7 | 0 | 2022-12-15 | 0.1 | 17.9 | 0 | 2021-12-15 | -4.8 | 22.8 | 0 | 2020-12-15 | -9.1 | 27.1 | 0 | 2019-12-15 | -1.2 | 19.2 | 0 | 2018-12-15 | 1.4 | 16.6 | 0 | 2017-12-15 | -22 | 40 | 0 | 2016-12-15 | -10.2 | 28.2 | 0 | 25.31 | 0
2025-12-15 | -13.6 | 31.6 | 0 | 2024-12-15 | -14.9 | 32.9 | 0 | 2023-12-15 | 1.3 | 16.7 | 0 | 2022-12-15 | 0.7 | 17.3 | 0 | 2021-12-15 | -4.6 | 22.6 | 0 | 2020-12-15 | -10.7 | 28.7 | 0 | 2019-12-15 | -2.5 | 20.5 | 0 | 2018-12-15 | 1.2 | 16.8 | 0 | 2017-12-15 | -20 | 38 | 0 | 2016-12-15 | -11.5 | 29.5 | 0 | 25.46 | 0
2025-12-15 | -13.1 | 31.1 | 0 | 2024-12-15 | -14.8 | 32.8 | 0 | 2023-12-15 | 1.5 | 16.5 | 0 | 2022-12-15 | 1 | 17 | 0 | 2021-12-15 | -4.5 | 22.5 | 0 | 2020-12-15 | -12.6 | 30.6 | 0 | 2019-12-15 | -3.7 | 21.7 | 0 | 2018-12-15 | 1.3 | 16.7 | 0 | 2017-12-15 | -19.1 | 37.1 | 0 | 2016-12-15 | -13.6 | 31.6 | 0 | 25.76 | 0
2025-12-15 | -12.4 | 30.4 | 0 | 2024-12-15 | -14.6 | 32.6 | 0 | 2023-12-15 | 1.6 | 16.4 | 0 | 2022-12-15 | 0.9 | 17.1 | 0 | 2021-12-15 | -4.5 | 22.5 | 0 | 2020-12-15 | -13.3 | 31.3 | 0 | 2019-12-15 | -4.5 | 22.5 | 0 | 2018-12-15 | 1 | 17 | 0 | 2017-12-15 | -17.9 | 35.9 | 0 | 2016-12-15 | -15.2 | 33.2 | 0 | 25.89 | 0
2025-12-15 | -11.3 | 29.3 | 0 | 2024-12-15 | -13.3 | 31.3 | 0 | 2023-12-15 | 2.4 | 15.6 | 0 | 2022-12-15 | 1.2 | 16.8 | 0 | 2021-12-15 | -3.6 | 21.6 | 0 | 2020-12-15 | -12.7 | 30.7 | 0 | 2019-12-15 | -5.7 | 23.7 | 0 | 2018-12-15 | 1 | 17 | 0 | 2017-12-15 | -16.6 | 34.6 | 0 | 2016-12-15 | -15.4 | 33.4 | 0 | 25.4 | 0
2025-12-15 | -10.6 | 28.6 | 0 | 2024-12-15 | -11.1 | 29.1 | 0 | 2023-12-15 | 4.2 | 13.8 | 0 | 2022-12-15 | 1.2 | 16.8 | 0 | 2021-12-15 | -3 | 21 | 0 | 2020-12-15 | -11.9 | 29.9 | 0 | 2019-12-15 | -6.3 | 24.3 | 0 | 2018-12-15 | 1.8 | 16.2 | 0 | 2017-12-15 | -15 | 33 | 0 | 2016-12-15 | -15.6 | 33.6 | 0 | 24.63 | 0
2025-12-15 | -10 | 28 | 0 | 2024-12-15 | -9.6 | 27.6 | 0 | 2023-12-15 | 5.6 | 12.4 | 0 | 2022-12-15 | 1.1 | 16.9 | 0 | 2021-12-15 | -2.2 | 20.2 | 0 | 2020-12-15 | -12 | 30 | 0 | 2019-12-15 | -6.7 | 24.7 | 0 | 2018-12-15 | 2.2 | 15.8 | 0 | 2017-12-15 | -13.7 | 31.7 | 0 | 2016-12-15 | -15.2 | 33.2 | 0 | 24.05 | 0
2025-12-15 | -9.3 | 27.3 | 0 | 2024-12-15 | -8.2 | 26.2 | 0 | 2023-12-15 | 6.5 | 11.5 | 0 | 2022-12-15 | 1.5 | 16.5 | 0 | 2021-12-15 | -2.2 | 20.2 | 0 | 2020-12-15 | -11 | 29 | 0 | 2019-12-15 | -6.8 | 24.8 | 0 | 2018-12-15 | 2.6 | 15.4 | 0 | 2017-12-15 | -12.6 | 30.6 | 0 | 2016-12-15 | -14.3 | 32.3 | 0 | 23.38 | 0
2025-12-15 | -8.5 | 26.5 | 0 | 2024-12-15 | -7.1 | 25.1 | 0 | 2023-12-15 | 7.9 | 10.1 | 0 | 2022-12-15 | 1.8 | 16.2 | 0 | 2021-12-15 | -1.6 | 19.6 | 0 | 2020-12-15 | -11 | 29 | 0 | 2019-12-15 | -7 | 25 | 0 | 2018-12-15 | 2.8 | 15.2 | 0 | 2017-12-15 | -11.9 | 29.9 | 0 | 2016-12-15 | -14 | 32 | 0 | 22.86 | 0
2025-12-15 | -7.8 | 25.8 | 0 | 2024-12-15 | -6.7 | 24.7 | 0 | 2023-12-15 | 8.5 | 9.5 | 0 | 2022-12-15 | 2.2 | 15.8 | 0 | 2021-12-15 | -2 | 20 | 0 | 2020-12-15 | -11.2 | 29.2 | 0 | 2019-12-15 | -7 | 25 | 0 | 2018-12-15 | 2.9 | 15.1 | 0 | 2017-12-15 | -11.8 | 29.8 | 0 | 2016-12-15 | -14.1 | 32.1 | 0 | 22.7 | 0
2025-12-15 | -7.6 | 25.6 | 0 | 2024-12-15 | -6.7 | 24.7 | 0 | 2023-12-15 | 8.5 | 9.5 | 0 | 2022-12-15 | 2.3 | 15.7 | 0 | 2021-12-15 | -2 | 20 | 0 | 2020-12-15 | -11.2 | 29.2 | 0 | 2019-12-15 | -8.1 | 26.1 | 0 | 2018-12-15 | 2.9 | 15.1 | 0 | 2017-12-15 | -11.6 | 29.6 | 0 | 2016-12-15 | -15.7 | 33.7 | 0 | 22.92 | 0
2025-12-15 | -7 | 25 | 0 | 2024-12-15 | -7 | 25 | 0 | 2023-12-15 | 7.6 | 10.4 | 0 | 2022-12-15 | 2.4 | 15.6 | 0 | 2021-12-15 | -2.1 | 20.1 | 0 | 2020-12-15 | -12.5 | 30.5 | 0 | 2019-12-15 | -8.3 | 26.3 | 0 | 2018-12-15 | 1.9 | 16.1 | 0 | 2017-12-15 | -12.1 | 30.1 | 0 | 2016-12-15 | -16.9 | 34.9 | 0 | 23.4 | 0
2025-12-15 | -7.2 | 25.2 | 0 | 2024-12-15 | -7.7 | 25.7 | 0 | 2023-12-15 | 5.4 | 12.6 | 0 | 2022-12-15 | 2.5 | 15.5 | 0 | 2021-12-15 | -1.5 | 19.5 | 0 | 2020-12-15 | -13.4 | 31.4 | 0 | 2019-12-15 | -8.2 | 26.2 | 0 | 2018-12-15 | 1 | 17 | 0 | 2017-12-15 | -12.5 | 30.5 | 0 | 2016-12-15 | -17.7 | 35.7 | 0 | 23.93 | 0
2025-12-15 | -7.5 | 25.5 | 0 | 2024-12-15 | -7.8 | 25.8 | 0 | 2023-12-15 | 4.8 | 13.2 | 0 | 2022-12-15 | 2 | 16 | 0 | 2021-12-15 | -1.3 | 19.3 | 0 | 2020-12-15 | -13.6 | 31.6 | 0 | 2019-12-15 | -8.7 | 26.7 | 0 | 2018-12-15 | 0.6 | 17.4 | 0 | 2017-12-15 | -12.7 | 30.7 | 0 | 2016-12-15 | -18.2 | 36.2 | 0 | 24.24 | 0
2025-12-15 | -7.7 | 25.7 | 0 | 2024-12-15 | -8.1 | 26.1 | 0 | 2023-12-15 | 5.3 | 12.7 | 0 | 2022-12-15 | 1.9 | 16.1 | 0 | 2021-12-15 | -1.1 | 19.1 | 0 | 2020-12-15 | -13.6 | 31.6 | 0 | 2019-12-15 | -9.4 | 27.4 | 0 | 2018-12-15 | -1.1 | 19.1 | 0 | 2017-12-15 | -12.7 | 30.7 | 0 | 2016-12-15 | -18.8 | 36.8 | 0 | 24.53 | 0
2025-12-15 | -7.6 | 25.6 | 0 | 2024-12-15 | -8.1 | 26.1 | 0 | 2023-12-15 | 5.5 | 12.5 | 0 | 2022-12-15 | 1.5 | 16.5 | 0 | 2021-12-15 | -1.5 | 19.5 | 0 | 2020-12-15 | -14.1 | 32.1 | 0 | 2019-12-15 | -9.9 | 27.9 | 0 | 2018-12-15 | -1.6 | 19.6 | 0 | 2017-12-15 | -12.9 | 30.9 | 0 | 2016-12-15 | -19.5 | 37.5 | 0 | 24.82 | 0
2025-12-15 | -7.5 | 25.5 | 0 | 2024-12-15 | -7.9 | 25.9 | 0 | 2023-12-15 | 4.6 | 13.4 | 0 | 2022-12-15 | 1.4 | 16.6 | 0 | 2021-12-15 | -1 | 19 | 0 | 2020-12-15 | -14.7 | 32.7 | 0 | 2019-12-15 | -10.5 | 28.5 | 0 | 2018-12-15 | -1.1 | 19.1 | 0 | 2017-12-15 | -12.5 | 30.5 | 0 | 2016-12-15 | -20 | 38 | 0 | 24.92 | 0
2025-12-15 | -7.2 | 25.2 | 0 | 2024-12-15 | -7.7 | 25.7 | 0 | 2023-12-15 | 4.4 | 13.6 | 0 | 2022-12-15 | 1.3 | 16.7 | 0 | 2021-12-15 | -0.8 | 18.8 | 0 | 2020-12-15 | -15.3 | 33.3 | 0 | 2019-12-15 | -11.1 | 29.1 | 0 | 2018-12-15 | -1.7 | 19.7 | 0 | 2017-12-15 | -12.1 | 30.1 | 0 | 2016-12-15 | -19.7 | 37.7 | 0 | 24.99 | 0
2025-12-15 | -6.8 | 24.8 | 0 | 2024-12-15 | -7.4 | 25.4 | 0 | 2023-12-15 | 3.6 | 14.4 | 0 | 2022-12-15 | 1.3 | 16.7 | 0 | 2021-12-15 | -0.3 | 18.3 | 0 | 2020-12-15 | -15.9 | 33.9 | 0 | 2019-12-15 | -12.5 | 30.5 | 0 | 2018-12-15 | -2 | 20 | 0 | 2017-12-15 | -11.9 | 29.9 | 0 | 2016-12-15 | -20.1 | 38.1 | 0 | 25.2 | 0
2025-12-16 | -6.3 | 24.3 | 0 | 2024-12-16 | -7.3 | 25.3 | 0 | 2023-12-16 | 4.2 | 13.8 | 0 | 2022-12-16 | 0.8 | 17.2 | 0 | 2021-12-16 | -0.2 | 18.2 | 0 | 2020-12-16 | -16.6 | 34.6 | 0 | 2019-12-16 | -13 | 31 | 0 | 2018-12-16 | -2.6 | 20.6 | 0 | 2017-12-16 | -11.6 | 29.6 | 0 | 2016-12-16 | -20.4 | 38.4 | 0 | 25.3 | 0
2025-12-16 | -6.1 | 24.1 | 0 | 2024-12-16 | -6.8 | 24.8 | 0 | 2023-12-16 | 3.6 | 14.4 | 0 | 2022-12-16 | 0 | 18 | 0 | 2021-12-16 | -0.3 | 18.3 | 0 | 2020-12-16 | -16.7 | 34.7 | 0 | 2019-12-16 | -13 | 31 | 0 | 2018-12-16 | -3.2 | 21.2 | 0 | 2017-12-16 | -11.3 | 29.3 | 0 | 2016-12-16 | -20.8 | 38.8 | 0 | 25.46 | 0
2025-12-16 | -6.1 | 24.1 | 0 | 2024-12-16 | -6.6 | 24.6 | 0 | 2023-12-16 | 2.9 | 15.1 | 0 | 2022-12-16 | 0 | 18 | 0 | 2021-12-16 | -0.2 | 18.2 | 0 | 2020-12-16 | -16.9 | 34.9 | 0 | 2019-12-16 | -13.3 | 31.3 | 0 | 2018-12-16 | -3.9 | 21.9 | 0 | 2017-12-16 | -11.9 | 29.9 | 0 | 2016-12-16 | -21.3 | 39.3 | 0 | 25.73 | 0
2025-12-16 | -6.2 | 24.2 | 0 | 2024-12-16 | -6.1 | 24.1 | 0 | 2023-12-16 | 2.1 | 15.9 | 0 | 2022-12-16 | 0.1 | 17.9 | 0 | 2021-12-16 | 0.1 | 17.9 | 0 | 2020-12-16 | -17.4 | 35.4 | 0 | 2019-12-16 | -14.1 | 32.1 | 0 | 2018-12-16 | -4 | 22 | 0 | 2017-12-16 | -11.9 | 29.9 | 0 | 2016-12-16 | -22.1 | 40.1 | 0 | 25.95 | 0
2025-12-16 | -6.1 | 24.1 | 0 | 2024-12-16 | -5.9 | 23.9 | 0 | 2023-12-16 | 0 | 18 | 0 | 2022-12-16 | 0.2 | 17.8 | 0 | 2021-12-16 | 0.1 | 17.9 | 0 | 2020-12-16 | -17.7 | 35.7 | 0 | 2019-12-16 | -13.8 | 31.8 | 0 | 2018-12-16 | -4.8 | 22.8 | 0 | 2017-12-16 | -11.7 | 29.7 | 0 | 2016-12-16 | -22.6 | 40.6 | 0 | 26.23 | 0
2025-12-16 | -6.3 | 24.3 | 0 | 2024-12-16 | -5.7 | 23.7 | 0 | 2023-12-16 | 1.1 | 16.9 | 0 | 2022-12-16 | 0.2 | 17.8 | 0 | 2021-12-16 | 0.3 | 17.7 | 0 | 2020-12-16 | -17.9 | 35.9 | 0 | 2019-12-16 | -14.5 | 32.5 | 0 | 2018-12-16 | -3.5 | 21.5 | 0 | 2017-12-16 | -12.5 | 30.5 | 0 | 2016-12-16 | -22.9 | 40.9 | 0 | 26.17 | 0
2025-12-16 | -6.4 | 24.4 | 0 | 2024-12-16 | -5 | 23 | 0 | 2023-12-16 | 0.2 | 17.8 | 0 | 2022-12-16 | 0.1 | 17.9 | 0 | 2021-12-16 | 0.5 | 17.5 | 0 | 2020-12-16 | -18 | 36 | 0 | 2019-12-16 | -14.3 | 32.3 | 0 | 2018-12-16 | -3.5 | 21.5 | 0 | 2017-12-16 | -12.1 | 30.1 | 0 | 2016-12-16 | -26.3 | 44.3 | 0 | 26.48 | 0
2025-12-16 | -6.5 | 24.5 | 0 | 2024-12-16 | -4.2 | 22.2 | 0 | 2023-12-16 | -0.1 | 18.1 | 0 | 2022-12-16 | -0.2 | 18.2 | 0 | 2021-12-16 | 1.1 | 16.9 | 0 | 2020-12-16 | -18.2 | 36.2 | 0 | 2019-12-16 | -14 | 32 | 0 | 2018-12-16 | -3.2 | 21.2 | 0 | 2017-12-16 | -13 | 31 | 0 | 2016-12-16 | -25.5 | 43.5 | 0 | 26.38 | 0
2025-12-16 | -6.4 | 24.4 | 0 | 2024-12-16 | -4.3 | 22.3 | 0 | 2023-12-16 | -1.2 | 19.2 | 0 | 2022-12-16 | -0.4 | 18.4 | 0 | 2021-12-16 | 1.2 | 16.8 | 0 | 2020-12-16 | -18.1 | 36.1 | 0 | 2019-12-16 | -13.3 | 31.3 | 0 | 2018-12-16 | -3.6 | 21.6 | 0 | 2017-12-16 | -13.8 | 31.8 | 0 | 2016-12-16 | -26.2 | 44.2 | 0 | 26.61 | 0
2025-12-16 | -6 | 24 | 0 | 2024-12-16 | -4.2 | 22.2 | 0 | 2023-12-16 | 0.5 | 17.5 | 0 | 2022-12-16 | -0.7 | 18.7 | 0 | 2021-12-16 | 1.8 | 16.2 | 0 | 2020-12-16 | -17.4 | 35.4 | 0 | 2019-12-16 | -11.6 | 29.6 | 0 | 2018-12-16 | -3 | 21 | 0 | 2017-12-16 | -13.1 | 31.1 | 0 | 2016-12-16 | -23.7 | 41.7 | 0 | 25.74 | 0
2025-12-16 | -5.7 | 23.7 | 0 | 2024-12-16 | -3.5 | 21.5 | 0 | 2023-12-16 | 1.9 | 16.1 | 0 | 2022-12-16 | -0.6 | 18.6 | 0 | 2021-12-16 | 3.6 | 14.4 | 0 | 2020-12-16 | -16.5 | 34.5 | 0 | 2019-12-16 | -10.3 | 28.3 | 0 | 2018-12-16 | -1.4 | 19.4 | 0 | 2017-12-16 | -11.1 | 29.1 | 0 | 2016-12-16 | -21.1 | 39.1 | 0 | 24.47 | 0
2025-12-16 | -5.2 | 23.2 | 0 | 2024-12-16 | -2.6 | 20.6 | 0 | 2023-12-16 | 2.3 | 15.7 | 0 | 2022-12-16 | -0.6 | 18.6 | 0 | 2021-12-16 | 10.5 | 7.5 | 0 | 2020-12-16 | -16.1 | 34.1 | 0 | 2019-12-16 | -8.9 | 26.9 | 0 | 2018-12-16 | -0.4 | 18.4 | 0 | 2017-12-16 | -9.4 | 27.4 | 0 | 2016-12-16 | -19.6 | 37.6 | 0 | 23 | 0
2025-12-16 | -3.3 | 21.3 | 0 | 2024-12-16 | -1.4 | 19.4 | 0 | 2023-12-16 | 3 | 15 | 0 | 2022-12-16 | -0.6 | 18.6 | 0 | 2021-12-16 | 14.5 | 3.5 | 0 | 2020-12-16 | -14.9 | 32.9 | 0 | 2019-12-16 | -8 | 26 | 0 | 2018-12-16 | 0.1 | 17.9 | 0 | 2017-12-16 | -9.2 | 27.2 | 0 | 2016-12-16 | -18.7 | 36.7 | 0 | 21.85 | 0
2025-12-16 | -2.2 | 20.2 | 0 | 2024-12-16 | -0.7 | 18.7 | 0 | 2023-12-16 | 3.2 | 14.8 | 0 | 2022-12-16 | -0.7 | 18.7 | 0 | 2021-12-16 | 15.2 | 2.8 | 0 | 2020-12-16 | -14 | 32 | 0 | 2019-12-16 | -7.3 | 25.3 | 0 | 2018-12-16 | 0.5 | 17.5 | 0 | 2017-12-16 | -9 | 27 | 0 | 2016-12-16 | -17.5 | 35.5 | 0 | 21.25 | 0
2025-12-16 | -2.7 | 20.7 | 0 | 2024-12-16 | -0.3 | 18.3 | 0 | 2023-12-16 | 3.4 | 14.6 | 0 | 2022-12-16 | -0.7 | 18.7 | 0 | 2021-12-16 | 14.6 | 3.4 | 0 | 2020-12-16 | -14 | 32 | 0 | 2019-12-16 | -6.9 | 24.9 | 0 | 2018-12-16 | 0.4 | 17.6 | 0 | 2017-12-16 | -9.5 | 27.5 | 0 | 2016-12-16 | -17.1 | 35.1 | 0 | 21.28 | 0
2025-12-16 | -3.2 | 21.2 | 0 | 2024-12-16 | -0.2 | 18.2 | 0 | 2023-12-16 | 2.9 | 15.1 | 0 | 2022-12-16 | -0.8 | 18.8 | 0 | 2021-12-16 | 14.1 | 3.9 | 0 | 2020-12-16 | -13.8 | 31.8 | 0 | 2019-12-16 | -6.5 | 24.5 | 0 | 2018-12-16 | 0.2 | 17.8 | 0 | 2017-12-16 | -9.8 | 27.8 | 0 | 2016-12-16 | -16.7 | 34.7 | 0 | 21.38 | 0
2025-12-16 | -3.6 | 21.6 | 0 | 2024-12-16 | 0.1 | 17.9 | 0 | 2023-12-16 | 1.5 | 16.5 | 0 | 2022-12-16 | -0.8 | 18.8 | 0 | 2021-12-16 | 13.6 | 4.4 | 0 | 2020-12-16 | -14 | 32 | 0 | 2019-12-16 | -6.3 | 24.3 | 0 | 2018-12-16 | -0.1 | 18.1 | 0 | 2017-12-16 | -10.6 | 28.6 | 0 | 2016-12-16 | -16.9 | 34.9 | 0 | 21.71 | 0
2025-12-16 | -3.7 | 21.7 | 0 | 2024-12-16 | 0.2 | 17.8 | 0 | 2023-12-16 | -0.2 | 18.2 | 0 | 2022-12-16 | -0.7 | 18.7 | 0 | 2021-12-16 | 13.1 | 4.9 | 0 | 2020-12-16 | -13.9 | 31.9 | 0 | 2019-12-16 | -7 | 25 | 0 | 2018-12-16 | -0.1 | 18.1 | 0 | 2017-12-16 | -12.2 | 30.2 | 0 | 2016-12-16 | -17.8 | 35.8 | 0 | 22.23 | 0
2025-12-16 | -3 | 21 | 0 | 2024-12-16 | 0.3 | 17.7 | 0 | 2023-12-16 | 0.5 | 17.5 | 0 | 2022-12-16 | -0.5 | 18.5 | 0 | 2021-12-16 | 13.7 | 4.3 | 0 | 2020-12-16 | -14.2 | 32.2 | 0 | 2019-12-16 | -6.2 | 24.2 | 0 | 2018-12-16 | -0.4 | 18.4 | 0 | 2017-12-16 | -12.3 | 30.3 | 0 | 2016-12-16 | -17.5 | 35.5 | 0 | 21.96 | 0
2025-12-16 | -3 | 21 | 0 | 2024-12-16 | 0.6 | 17.4 | 0 | 2023-12-16 | 0.2 | 17.8 | 0 | 2022-12-16 | -0.2 | 18.2 | 0 | 2021-12-16 | 13.6 | 4.4 | 0 | 2020-12-16 | -14.3 | 32.3 | 0 | 2019-12-16 | -5.6 | 23.6 | 0 | 2018-12-16 | -0.8 | 18.8 | 0 | 2017-12-16 | -12.6 | 30.6 | 0 | 2016-12-16 | -17.8 | 35.8 | 0 | 21.99 | 0
2025-12-16 | -2.7 | 20.7 | 0 | 2024-12-16 | 0.8 | 17.2 | 0 | 2023-12-16 | 0 | 18 | 0 | 2022-12-16 | -0.2 | 18.2 | 0 | 2021-12-16 | 14.2 | 3.8 | 0 | 2020-12-16 | -14.2 | 32.2 | 0 | 2019-12-16 | -5.1 | 23.1 | 0 | 2018-12-16 | -0.8 | 18.8 | 0 | 2017-12-16 | -14 | 32 | 0 | 2016-12-16 | -18.8 | 36.8 | 0 | 22.08 | 0
2025-12-16 | -2.8 | 20.8 | 0 | 2024-12-16 | 1 | 17 | 0 | 2023-12-16 | -0.4 | 18.4 | 0 | 2022-12-16 | -0.3 | 18.3 | 0 | 2021-12-16 | 14 | 4 | 0 | 2020-12-16 | -13.9 | 31.9 | 0 | 2019-12-16 | -4.5 | 22.5 | 0 | 2018-12-16 | -1.2 | 19.2 | 0 | 2017-12-16 | -15.4 | 33.4 | 0 | 2016-12-16 | -19.4 | 37.4 | 0 | 22.29 | 0
2025-12-16 | -3.6 | 21.6 | 0 | 2024-12-16 | 0.8 | 17.2 | 0 | 2023-12-16 | -0.8 | 18.8 | 0 | 2022-12-16 | -0.4 | 18.4 | 0 | 2021-12-16 | 12.9 | 5.1 | 0 | 2020-12-16 | -13.6 | 31.6 | 0 | 2019-12-16 | -4.3 | 22.3 | 0 | 2018-12-16 | -0.9 | 18.9 | 0 | 2017-12-16 | -16.8 | 34.8 | 0 | 2016-12-16 | -19.3 | 37.3 | 0 | 22.6 | 0
2025-12-16 | -3 | 21 | 0 | 2024-12-16 | 0.7 | 17.3 | 0 | 2023-12-16 | -1.3 | 19.3 | 0 | 2022-12-16 | -0.4 | 18.4 | 0 | 2021-12-16 | 11.9 | 6.1 | 0 | 2020-12-16 | -13.4 | 31.4 | 0 | 2019-12-16 | -4.3 | 22.3 | 0 | 2018-12-16 | -0.8 | 18.8 | 0 | 2017-12-16 | -18 | 36 | 0 | 2016-12-16 | -18.9 | 36.9 | 0 | 22.75 | 0
2025-12-17 | -2.1 | 20.1 | 0 | 2024-12-17 | 0.4 | 17.6 | 0 | 2023-12-17 | -1.4 | 19.4 | 0 | 2022-12-17 | -0.5 | 18.5 | 0 | 2021-12-17 | 9.4 | 8.6 | 0 | 2020-12-17 | -13.3 | 31.3 | 0 | 2019-12-17 | -4.8 | 22.8 | 0 | 2018-12-17 | -0.7 | 18.7 | 0 | 2017-12-17 | -18.4 | 36.4 | 0 | 2016-12-17 | -18.4 | 36.4 | 0 | 22.98 | 0
2025-12-17 | -1.6 | 19.6 | 0 | 2024-12-17 | 0.6 | 17.4 | 0 | 2023-12-17 | -1.4 | 19.4 | 0 | 2022-12-17 | -0.5 | 18.5 | 0 | 2021-12-17 | 6.8 | 11.2 | 0 | 2020-12-17 | -13.5 | 31.5 | 0 | 2019-12-17 | -4.5 | 22.5 | 0 | 2018-12-17 | -1 | 19 | 0 | 2017-12-17 | -19 | 37 | 0 | 2016-12-17 | -17.9 | 35.9 | 0 | 23.2 | 0
2025-12-17 | -0.6 | 18.6 | 0 | 2024-12-17 | 0.9 | 17.1 | 0 | 2023-12-17 | -1.3 | 19.3 | 0 | 2022-12-17 | -0.7 | 18.7 | 0 | 2021-12-17 | 6 | 12 | 0 | 2020-12-17 | -13.2 | 31.2 | 0 | 2019-12-17 | -4.6 | 22.6 | 0 | 2018-12-17 | -0.8 | 18.8 | 0 | 2017-12-17 | -19.7 | 37.7 | 0 | 2016-12-17 | -17.3 | 35.3 | 0 | 23.13 | 0
2025-12-17 | -0.2 | 18.2 | 0 | 2024-12-17 | 1.4 | 16.6 | 0 | 2023-12-17 | -1.5 | 19.5 | 0 | 2022-12-17 | -0.9 | 18.9 | 0 | 2021-12-17 | 5.6 | 12.4 | 0 | 2020-12-17 | -12.6 | 30.6 | 0 | 2019-12-17 | -4.5 | 22.5 | 0 | 2018-12-17 | -0.7 | 18.7 | 0 | 2017-12-17 | -20.8 | 38.8 | 0 | 2016-12-17 | -16.9 | 34.9 | 0 | 23.11 | 0
2025-12-17 | 0 | 18 | 0 | 2024-12-17 | 5 | 13 | 0 | 2023-12-17 | -1.4 | 19.4 | 0 | 2022-12-17 | -1.1 | 19.1 | 0 | 2021-12-17 | 5.2 | 12.8 | 0 | 2020-12-17 | -12.2 | 30.2 | 0 | 2019-12-17 | -4.4 | 22.4 | 0 | 2018-12-17 | -0.6 | 18.6 | 0 | 2017-12-17 | -22.2 | 40.2 | 0 | 2016-12-17 | -16.3 | 34.3 | 0 | 22.8 | 0
2025-12-17 | 0.2 | 17.8 | 0 | 2024-12-17 | 5.5 | 12.5 | 0 | 2023-12-17 | -1.6 | 19.6 | 0 | 2022-12-17 | -1.2 | 19.2 | 0 | 2021-12-17 | 4.8 | 13.2 | 0 | 2020-12-17 | -12.1 | 30.1 | 0 | 2019-12-17 | -4.8 | 22.8 | 0 | 2018-12-17 | -0.6 | 18.6 | 0 | 2017-12-17 | -21 | 39 | 0 | 2016-12-17 | -15.7 | 33.7 | 0 | 22.65 | 0
2025-12-17 | 0.9 | 17.1 | 0 | 2024-12-17 | 5.5 | 12.5 | 0 | 2023-12-17 | -1.5 | 19.5 | 0 | 2022-12-17 | -1.7 | 19.7 | 0 | 2021-12-17 | 5 | 13 | 0 | 2020-12-17 | -11.7 | 29.7 | 0 | 2019-12-17 | -4.7 | 22.7 | 0 | 2018-12-17 | -0.3 | 18.3 | 0 | 2017-12-17 | -21.2 | 39.2 | 0 | 2016-12-17 | -14.8 | 32.8 | 0 | 22.45 | 0
2025-12-17 | 1.1 | 16.9 | 0 | 2024-12-17 | 5.2 | 12.8 | 0 | 2023-12-17 | -1.2 | 19.2 | 0 | 2022-12-17 | -2 | 20 | 0 | 2021-12-17 | 4.8 | 13.2 | 0 | 2020-12-17 | -11.8 | 29.8 | 0 | 2019-12-17 | -4.8 | 22.8 | 0 | 2018-12-17 | -0.4 | 18.4 | 0 | 2017-12-17 | -21.8 | 39.8 | 0 | 2016-12-17 | -14 | 32 | 0 | 22.49 | 0
2025-12-17 | 1.1 | 16.9 | 0 | 2024-12-17 | 4.8 | 13.2 | 0 | 2023-12-17 | -1.1 | 19.1 | 0 | 2022-12-17 | -2.1 | 20.1 | 0 | 2021-12-17 | 4 | 14 | 0 | 2020-12-17 | -11.8 | 29.8 | 0 | 2019-12-17 | -4.7 | 22.7 | 0 | 2018-12-17 | -0.6 | 18.6 | 0 | 2017-12-17 | -21.2 | 39.2 | 0 | 2016-12-17 | -13.3 | 31.3 | 0 | 22.49 | 0
2025-12-17 | 1.2 | 16.8 | 0 | 2024-12-17 | 4.8 | 13.2 | 0 | 2023-12-17 | -0.4 | 18.4 | 0 | 2022-12-17 | -1.4 | 19.4 | 0 | 2021-12-17 | 4.6 | 13.4 | 0 | 2020-12-17 | -11 | 29 | 0 | 2019-12-17 | -4.6 | 22.6 | 0 | 2018-12-17 | -0.5 | 18.5 | 0 | 2017-12-17 | -20.7 | 38.7 | 0 | 2016-12-17 | -13 | 31 | 0 | 22.1 | 0
2025-12-17 | 1.7 | 16.3 | 0 | 2024-12-17 | 4.7 | 13.3 | 0 | 2023-12-17 | 1 | 17 | 0 | 2022-12-17 | -0.9 | 18.9 | 0 | 2021-12-17 | 4.4 | 13.6 | 0 | 2020-12-17 | -10.1 | 28.1 | 0 | 2019-12-17 | -4 | 22 | 0 | 2018-12-17 | -0.2 | 18.2 | 0 | 2017-12-17 | -18.4 | 36.4 | 0 | 2016-12-17 | -12.1 | 30.1 | 0 | 21.39 | 0
2025-12-17 | 2.8 | 15.2 | 0 | 2024-12-17 | 4.4 | 13.6 | 0 | 2023-12-17 | 2.3 | 15.7 | 0 | 2022-12-17 | -0.6 | 18.6 | 0 | 2021-12-17 | 4.5 | 13.5 | 0 | 2020-12-17 | -9 | 27 | 0 | 2019-12-17 | -3.6 | 21.6 | 0 | 2018-12-17 | 0.1 | 17.9 | 0 | 2017-12-17 | -17 | 35 | 0 | 2016-12-17 | -11 | 29 | 0 | 20.71 | 0
2025-12-17 | 2.8 | 15.2 | 0 | 2024-12-17 | 4.6 | 13.4 | 0 | 2023-12-17 | 3.8 | 14.2 | 0 | 2022-12-17 | -0.3 | 18.3 | 0 | 2021-12-17 | 4.7 | 13.3 | 0 | 2020-12-17 | -8 | 26 | 0 | 2019-12-17 | -3.1 | 21.1 | 0 | 2018-12-17 | -0.1 | 18.1 | 0 | 2017-12-17 | -15.3 | 33.3 | 0 | 2016-12-17 | -10.3 | 28.3 | 0 | 20.12 | 0
2025-12-17 | 2.7 | 15.3 | 0 | 2024-12-17 | 5.2 | 12.8 | 0 | 2023-12-17 | 4.3 | 13.7 | 0 | 2022-12-17 | -0.1 | 18.1 | 0 | 2021-12-17 | 3.8 | 14.2 | 0 | 2020-12-17 | -6.8 | 24.8 | 0 | 2019-12-17 | -3 | 21 | 0 | 2018-12-17 | -0.1 | 18.1 | 0 | 2017-12-17 | -14.9 | 32.9 | 0 | 2016-12-17 | -9.9 | 27.9 | 0 | 19.88 | 0
2025-12-17 | 2.6 | 15.4 | 0 | 2024-12-17 | 5.2 | 12.8 | 0 | 2023-12-17 | 3.5 | 14.5 | 0 | 2022-12-17 | 0 | 18 | 0 | 2021-12-17 | 3.2 | 14.8 | 0 | 2020-12-17 | -6.2 | 24.2 | 0 | 2019-12-17 | -2.7 | 20.7 | 0 | 2018-12-17 | 0.3 | 17.7 | 0 | 2017-12-17 | -14 | 32 | 0 | 2016-12-17 | -9.3 | 27.3 | 0 | 19.74 | 0
2025-12-17 | 2.4 | 15.6 | 0 | 2024-12-17 | 5 | 13 | 0 | 2023-12-17 | 3.7 | 14.3 | 0 | 2022-12-17 | 0.2 | 17.8 | 0 | 2021-12-17 | 2.7 | 15.3 | 0 | 2020-12-17 | -6.3 | 24.3 | 0 | 2019-12-17 | -3 | 21 | 0 | 2018-12-17 | 0.2 | 17.8 | 0 | 2017-12-17 | -14.1 | 32.1 | 0 | 2016-12-17 | -9.4 | 27.4 | 0 | 19.86 | 0
2025-12-17 | 2.3 | 15.7 | 0 | 2024-12-17 | 4 | 14 | 0 | 2023-12-17 | 4 | 14 | 0 | 2022-12-17 | 0.2 | 17.8 | 0 | 2021-12-17 | 1.7 | 16.3 | 0 | 2020-12-17 | -7.1 | 25.1 | 0 | 2019-12-17 | -3.3 | 21.3 | 0 | 2018-12-17 | -1.6 | 19.6 | 0 | 2017-12-17 | -14.2 | 32.2 | 0 | 2016-12-17 | -9.6 | 27.6 | 0 | 20.36 | 0
2025-12-17 | 2.1 | 15.9 | 0 | 2024-12-17 | 2.9 | 15.1 | 0 | 2023-12-17 | 4.5 | 13.5 | 0 | 2022-12-17 | 0 | 18 | 0 | 2021-12-17 | 1.5 | 16.5 | 0 | 2020-12-17 | -8.2 | 26.2 | 0 | 2019-12-17 | -3.6 | 21.6 | 0 | 2018-12-17 | -2.5 | 20.5 | 0 | 2017-12-17 | -16.2 | 34.2 | 0 | 2016-12-17 | -9.6 | 27.6 | 0 | 20.91 | 0
2025-12-17 | 0.6 | 17.4 | 0 | 2024-12-17 | 2.6 | 15.4 | 0 | 2023-12-17 | 4.9 | 13.1 | 0 | 2022-12-17 | -0.3 | 18.3 | 0 | 2021-12-17 | 1.4 | 16.6 | 0 | 2020-12-17 | -9.7 | 27.7 | 0 | 2019-12-17 | -3.9 | 21.9 | 0 | 2018-12-17 | -3.7 | 21.7 | 0 | 2017-12-17 | -16.9 | 34.9 | 0 | 2016-12-17 | -9.7 | 27.7 | 0 | 21.47 | 0
2025-12-17 | 0.3 | 17.7 | 0 | 2024-12-17 | 2.8 | 15.2 | 0 | 2023-12-17 | 4.3 | 13.7 | 0 | 2022-12-17 | -0.6 | 18.6 | 0 | 2021-12-17 | 1 | 17 | 0 | 2020-12-17 | -10.7 | 28.7 | 0 | 2019-12-17 | -4.5 | 22.5 | 0 | 2018-12-17 | -5.5 | 23.5 | 0 | 2017-12-17 | -16.6 | 34.6 | 0 | 2016-12-17 | -9.4 | 27.4 | 0 | 21.89 | 0
2025-12-17 | -1.4 | 19.4 | 0 | 2024-12-17 | 2.7 | 15.3 | 0 | 2023-12-17 | 4.3 | 13.7 | 0 | 2022-12-17 | -0.4 | 18.4 | 0 | 2021-12-17 | 0.4 | 17.6 | 0 | 2020-12-17 | -11 | 29 | 0 | 2019-12-17 | -4.6 | 22.6 | 0 | 2018-12-17 | -6.6 | 24.6 | 0 | 2017-12-17 | -17.5 | 35.5 | 0 | 2016-12-17 | -9.3 | 27.3 | 0 | 22.34 | 0
2025-12-17 | -2.5 | 20.5 | 0 | 2024-12-17 | 2.4 | 15.6 | 0 | 2023-12-17 | 4.1 | 13.9 | 0 | 2022-12-17 | -0.6 | 18.6 | 0 | 2021-12-17 | 0 | 18 | 0 | 2020-12-17 | -11.5 | 29.5 | 0 | 2019-12-17 | -4.8 | 22.8 | 0 | 2018-12-17 | -7.2 | 25.2 | 0 | 2017-12-17 | -16.7 | 34.7 | 0 | 2016-12-17 | -9.4 | 27.4 | 0 | 22.62 | 0
2025-12-17 | -3.7 | 21.7 | 0 | 2024-12-17 | 2 | 16 | 0 | 2023-12-17 | 3.8 | 14.2 | 0 | 2022-12-17 | -0.7 | 18.7 | 0 | 2021-12-17 | -0.2 | 18.2 | 0 | 2020-12-17 | -11.5 | 29.5 | 0 | 2019-12-17 | -4.2 | 22.2 | 0 | 2018-12-17 | -7.6 | 25.6 | 0 | 2017-12-17 | -17.8 | 35.8 | 0 | 2016-12-17 | -9.1 | 27.1 | 0 | 22.9 | 0
2025-12-17 | -5.5 | 23.5 | 0 | 2024-12-17 | 2.2 | 15.8 | 0 | 2023-12-17 | 3.8 | 14.2 | 0 | 2022-12-17 | -1 | 19 | 0 | 2021-12-17 | -0.4 | 18.4 | 0 | 2020-12-17 | -13.1 | 31.1 | 0 | 2019-12-17 | -4.1 | 22.1 | 0 | 2018-12-17 | -7.7 | 25.7 | 0 | 2017-12-17 | -15.3 | 33.3 | 0 | 2016-12-17 | -8.8 | 26.8 | 0 | 22.99 | 0
2025-12-18 | -6 | 24 | 0 | 2024-12-18 | 2.1 | 15.9 | 0 | 2023-12-18 | 6.7 | 11.3 | 0 | 2022-12-18 | -1.2 | 19.2 | 0 | 2021-12-18 | -0.6 | 18.6 | 0 | 2020-12-18 | -12.1 | 30.1 | 0 | 2019-12-18 | -4.3 | 22.3 | 0 | 2018-12-18 | -8.1 | 26.1 | 0 | 2017-12-18 | -15.5 | 33.5 | 0 | 2016-12-18 | -8.5 | 26.5 | 0 | 22.75 | 0
2025-12-18 | -7.5 | 25.5 | 0 | 2024-12-18 | 1.8 | 16.2 | 0 | 2023-12-18 | 6.8 | 11.2 | 0 | 2022-12-18 | -1.3 | 19.3 | 0 | 2021-12-18 | -1.3 | 19.3 | 0 | 2020-12-18 | -12.5 | 30.5 | 0 | 2019-12-18 | -5.2 | 23.2 | 0 | 2018-12-18 | -8.3 | 26.3 | 0 | 2017-12-18 | -15.6 | 33.6 | 0 | 2016-12-18 | -8.3 | 26.3 | 0 | 23.14 | 0
2025-12-18 | -8.1 | 26.1 | 0 | 2024-12-18 | 1.8 | 16.2 | 0 | 2023-12-18 | 5 | 13 | 0 | 2022-12-18 | -1.6 | 19.6 | 0 | 2021-12-18 | -2.7 | 20.7 | 0 | 2020-12-18 | -12.5 | 30.5 | 0 | 2019-12-18 | -5.3 | 23.3 | 0 | 2018-12-18 | -8.6 | 26.6 | 0 | 2017-12-18 | -15.6 | 33.6 | 0 | 2016-12-18 | -8 | 26 | 0 | 23.56 | 0
2025-12-18 | -8.5 | 26.5 | 0 | 2024-12-18 | 1.6 | 16.4 | 0 | 2023-12-18 | 4.3 | 13.7 | 0 | 2022-12-18 | -1.9 | 19.9 | 0 | 2021-12-18 | -3 | 21 | 0 | 2020-12-18 | -13.1 | 31.1 | 0 | 2019-12-18 | -5 | 23 | 0 | 2018-12-18 | -9.1 | 27.1 | 0 | 2017-12-18 | -15.8 | 33.8 | 0 | 2016-12-18 | -7.5 | 25.5 | 0 | 23.8 | 0
2025-12-18 | -7.7 | 25.7 | 0 | 2024-12-18 | 1.1 | 16.9 | 0 | 2023-12-18 | 5.1 | 12.9 | 0 | 2022-12-18 | -3.1 | 21.1 | 0 | 2021-12-18 | -3.6 | 21.6 | 0 | 2020-12-18 | -13.4 | 31.4 | 0 | 2019-12-18 | -5.5 | 23.5 | 0 | 2018-12-18 | -9.2 | 27.2 | 0 | 2017-12-18 | -15.2 | 33.2 | 0 | 2016-12-18 | -7.3 | 25.3 | 0 | 23.88 | 0
2025-12-18 | -6.6 | 24.6 | 0 | 2024-12-18 | 0.8 | 17.2 | 0 | 2023-12-18 | 5.1 | 12.9 | 0 | 2022-12-18 | -3.7 | 21.7 | 0 | 2021-12-18 | -4.5 | 22.5 | 0 | 2020-12-18 | -13.8 | 31.8 | 0 | 2019-12-18 | -4.3 | 22.3 | 0 | 2018-12-18 | -9.3 | 27.3 | 0 | 2017-12-18 | -14.4 | 32.4 | 0 | 2016-12-18 | -6.9 | 24.9 | 0 | 23.76 | 0
2025-12-18 | -5.9 | 23.9 | 0 | 2024-12-18 | 0.6 | 17.4 | 0 | 2023-12-18 | 4.7 | 13.3 | 0 | 2022-12-18 | -4.9 | 22.9 | 0 | 2021-12-18 | -5.1 | 23.1 | 0 | 2020-12-18 | -13.4 | 31.4 | 0 | 2019-12-18 | -4.7 | 22.7 | 0 | 2018-12-18 | -9 | 27 | 0 | 2017-12-18 | -14 | 32 | 0 | 2016-12-18 | -6.2 | 24.2 | 0 | 23.79 | 0
2025-12-18 | -5.7 | 23.7 | 0 | 2024-12-18 | 0.6 | 17.4 | 0 | 2023-12-18 | 4.8 | 13.2 | 0 | 2022-12-18 | -5.7 | 23.7 | 0 | 2021-12-18 | -5.2 | 23.2 | 0 | 2020-12-18 | -14.2 | 32.2 | 0 | 2019-12-18 | -5.2 | 23.2 | 0 | 2018-12-18 | -8.7 | 26.7 | 0 | 2017-12-18 | -13.6 | 31.6 | 0 | 2016-12-18 | -6.4 | 24.4 | 0 | 23.93 | 0
2025-12-18 | -4.6 | 22.6 | 0 | 2024-12-18 | 0.6 | 17.4 | 0 | 2023-12-18 | 4.8 | 13.2 | 0 | 2022-12-18 | -5.9 | 23.9 | 0 | 2021-12-18 | -5.3 | 23.3 | 0 | 2020-12-18 | -15.6 | 33.6 | 0 | 2019-12-18 | -5.7 | 23.7 | 0 | 2018-12-18 | -8.7 | 26.7 | 0 | 2017-12-18 | -13.2 | 31.2 | 0 | 2016-12-18 | -6.8 | 24.8 | 0 | 24.04 | 0
2025-12-18 | -2.9 | 20.9 | 0 | 2024-12-18 | 1 | 17 | 0 | 2023-12-18 | 5.8 | 12.2 | 0 | 2022-12-18 | -5.4 | 23.4 | 0 | 2021-12-18 | -4.9 | 22.9 | 0 | 2020-12-18 | -12 | 30 | 0 | 2019-12-18 | -5.2 | 23.2 | 0 | 2018-12-18 | -8.7 | 26.7 | 0 | 2017-12-18 | -12.7 | 30.7 | 0 | 2016-12-18 | -6.4 | 24.4 | 0 | 23.14 | 0
2025-12-18 | -0.3 | 18.3 | 0 | 2024-12-18 | 1.7 | 16.3 | 0 | 2023-12-18 | 5.9 | 12.1 | 0 | 2022-12-18 | -4.7 | 22.7 | 0 | 2021-12-18 | -4.5 | 22.5 | 0 | 2020-12-18 | -10.1 | 28.1 | 0 | 2019-12-18 | -5.2 | 23.2 | 0 | 2018-12-18 | -8.9 | 26.9 | 0 | 2017-12-18 | -12.2 | 30.2 | 0 | 2016-12-18 | -6.4 | 24.4 | 0 | 22.47 | 0
2025-12-18 | 1 | 17 | 0 | 2024-12-18 | 1.9 | 16.1 | 0 | 2023-12-18 | 5.7 | 12.3 | 0 | 2022-12-18 | -3.4 | 21.4 | 0 | 2021-12-18 | -4.3 | 22.3 | 0 | 2020-12-18 | -8.7 | 26.7 | 0 | 2019-12-18 | -6.9 | 24.9 | 0 | 2018-12-18 | -7.8 | 25.8 | 0 | 2017-12-18 | -11.6 | 29.6 | 0 | 2016-12-18 | -6.4 | 24.4 | 0 | 22.05 | 0
2025-12-18 | 1.9 | 16.1 | 0 | 2024-12-18 | 2.1 | 15.9 | 0 | 2023-12-18 | 5.8 | 12.2 | 0 | 2022-12-18 | -3.1 | 21.1 | 0 | 2021-12-18 | -4.2 | 22.2 | 0 | 2020-12-18 | -7.4 | 25.4 | 0 | 2019-12-18 | -7.5 | 25.5 | 0 | 2018-12-18 | -7 | 25 | 0 | 2017-12-18 | -11 | 29 | 0 | 2016-12-18 | -6.4 | 24.4 | 0 | 21.68 | 0
2025-12-18 | 2.3 | 15.7 | 0 | 2024-12-18 | 0.9 | 17.1 | 0 | 2023-12-18 | 5.8 | 12.2 | 0 | 2022-12-18 | -2.3 | 20.3 | 0 | 2021-12-18 | -5.3 | 23.3 | 0 | 2020-12-18 | -6.6 | 24.6 | 0 | 2019-12-18 | -9.4 | 27.4 | 0 | 2018-12-18 | -7.1 | 25.1 | 0 | 2017-12-18 | -10.5 | 28.5 | 0 | 2016-12-18 | -8.6 | 26.6 | 0 | 22.08 | 0
2025-12-18 | 2.8 | 15.2 | 0 | 2024-12-18 | 0.9 | 17.1 | 0 | 2023-12-18 | 5.6 | 12.4 | 0 | 2022-12-18 | -2.2 | 20.2 | 0 | 2021-12-18 | -6 | 24 | 0 | 2020-12-18 | -5.5 | 23.5 | 0 | 2019-12-18 | -11.2 | 29.2 | 0 | 2018-12-18 | -6.8 | 24.8 | 0 | 2017-12-18 | -10.1 | 28.1 | 0 | 2016-12-18 | -9.6 | 27.6 | 0 | 22.21 | 0
2025-12-18 | 3.1 | 14.9 | 0 | 2024-12-18 | 0.1 | 17.9 | 0 | 2023-12-18 | 5.7 | 12.3 | 0 | 2022-12-18 | -1.8 | 19.8 | 0 | 2021-12-18 | -6.3 | 24.3 | 0 | 2020-12-18 | -5.4 | 23.4 | 0 | 2019-12-18 | -12.5 | 30.5 | 0 | 2018-12-18 | -6.8 | 24.8 | 0 | 2017-12-18 | -9.9 | 27.9 | 0 | 2016-12-18 | -10.2 | 28.2 | 0 | 22.4 | 0
2025-12-18 | 2.7 | 15.3 | 0 | 2024-12-18 | 0 | 18 | 0 | 2023-12-18 | 4.9 | 13.1 | 0 | 2022-12-18 | -1.9 | 19.9 | 0 | 2021-12-18 | -6.5 | 24.5 | 0 | 2020-12-18 | -6.7 | 24.7 | 0 | 2019-12-18 | -13.6 | 31.6 | 0 | 2018-12-18 | -7.2 | 25.2 | 0 | 2017-12-18 | -9.7 | 27.7 | 0 | 2016-12-18 | -11.6 | 29.6 | 0 | 22.96 | 0
2025-12-18 | 1.6 | 16.4 | 0 | 2024-12-18 | 0 | 18 | 0 | 2023-12-18 | 4.7 | 13.3 | 0 | 2022-12-18 | -1.8 | 19.8 | 0 | 2021-12-18 | -6.7 | 24.7 | 0 | 2020-12-18 | -8 | 26 | 0 | 2019-12-18 | -14.3 | 32.3 | 0 | 2018-12-18 | -8 | 26 | 0 | 2017-12-18 | -9.9 | 27.9 | 0 | 2016-12-18 | -13.3 | 31.3 | 0 | 23.57 | 0
2025-12-18 | 1.7 | 16.3 | 0 | 2024-12-18 | 0 | 18 | 0 | 2023-12-18 | 4.4 | 13.6 | 0 | 2022-12-18 | -1.7 | 19.7 | 0 | 2021-12-18 | -6.7 | 24.7 | 0 | 2020-12-18 | -9.4 | 27.4 | 0 | 2019-12-18 | -14.9 | 32.9 | 0 | 2018-12-18 | -8.4 | 26.4 | 0 | 2017-12-18 | -10.1 | 28.1 | 0 | 2016-12-18 | -14.1 | 32.1 | 0 | 23.92 | 0
2025-12-18 | 6.3 | 11.7 | 0 | 2024-12-18 | -0.1 | 18.1 | 0 | 2023-12-18 | 4.5 | 13.5 | 0 | 2022-12-18 | -3.4 | 21.4 | 0 | 2021-12-18 | -6.8 | 24.8 | 0 | 2020-12-18 | -8.4 | 26.4 | 0 | 2019-12-18 | -16 | 34 | 0 | 2018-12-18 | -9.4 | 27.4 | 0 | 2017-12-18 | -10.1 | 28.1 | 0 | 2016-12-18 | -14.9 | 32.9 | 0 | 23.83 | 0
2025-12-18 | 6.4 | 11.6 | 0 | 2024-12-18 | 0.1 | 17.9 | 0 | 2023-12-18 | 4.4 | 13.6 | 0 | 2022-12-18 | -4 | 22 | 0 | 2021-12-18 | -6.7 | 24.7 | 0 | 2020-12-18 | -9.2 | 27.2 | 0 | 2019-12-18 | -17.4 | 35.4 | 0 | 2018-12-18 | -10.6 | 28.6 | 0 | 2017-12-18 | -10.3 | 28.3 | 0 | 2016-12-18 | -15.9 | 33.9 | 0 | 24.32 | 0
2025-12-18 | 6.5 | 11.5 | 0 | 2024-12-18 | 0 | 18 | 0 | 2023-12-18 | 4 | 14 | 0 | 2022-12-18 | -4.1 | 22.1 | 0 | 2021-12-18 | -7.2 | 25.2 | 0 | 2020-12-18 | -11.7 | 29.7 | 0 | 2019-12-18 | -19 | 37 | 0 | 2018-12-18 | -11.2 | 29.2 | 0 | 2017-12-18 | -10.3 | 28.3 | 0 | 2016-12-18 | -16.8 | 34.8 | 0 | 24.98 | 0
2025-12-18 | 6.5 | 11.5 | 0 | 2024-12-18 | 0 | 18 | 0 | 2023-12-18 | 2.9 | 15.1 | 0 | 2022-12-18 | -5.3 | 23.3 | 0 | 2021-12-18 | -6.6 | 24.6 | 0 | 2020-12-18 | -10.7 | 28.7 | 0 | 2019-12-18 | -20.1 | 38.1 | 0 | 2018-12-18 | -11.2 | 29.2 | 0 | 2017-12-18 | -10.3 | 28.3 | 0 | 2016-12-18 | -17.6 | 35.6 | 0 | 25.24 | 0
2025-12-18 | 6.6 | 11.4 | 0 | 2024-12-18 | -0.1 | 18.1 | 0 | 2023-12-18 | 1.3 | 16.7 | 0 | 2022-12-18 | -6 | 24 | 0 | 2021-12-18 | -5.9 | 23.9 | 0 | 2020-12-18 | -12.9 | 30.9 | 0 | 2019-12-18 | -21 | 39 | 0 | 2018-12-18 | -11.4 | 29.4 | 0 | 2017-12-18 | -10.1 | 28.1 | 0 | 2016-12-18 | -18.5 | 36.5 | 0 | 25.8 | 0
2025-12-19 | 6.5 | 11.5 | 0 | 2024-12-19 | 0 | 18 | 0 | 2023-12-19 | 0.3 | 17.7 | 0 | 2022-12-19 | -6.4 | 24.4 | 0 | 2021-12-19 | -5.8 | 23.8 | 0 | 2020-12-19 | -11.6 | 29.6 | 0 | 2019-12-19 | -21.4 | 39.4 | 0 | 2018-12-19 | -12.4 | 30.4 | 0 | 2017-12-19 | -10.1 | 28.1 | 0 | 2016-12-19 | -19.4 | 37.4 | 0 | 26.03 | 0
2025-12-19 | 6.1 | 11.9 | 0 | 2024-12-19 | -0.4 | 18.4 | 0 | 2023-12-19 | -0.1 | 18.1 | 0 | 2022-12-19 | -7.9 | 25.9 | 0 | 2021-12-19 | -6.8 | 24.8 | 0 | 2020-12-19 | -13.2 | 31.2 | 0 | 2019-12-19 | -21.7 | 39.7 | 0 | 2018-12-19 | -12.1 | 30.1 | 0 | 2017-12-19 | -10 | 28 | 0 | 2016-12-19 | -20.8 | 38.8 | 0 | 26.69 | 0
2025-12-19 | 5.7 | 12.3 | 0 | 2024-12-19 | -0.7 | 18.7 | 0 | 2023-12-19 | -0.9 | 18.9 | 0 | 2022-12-19 | -7.2 | 25.2 | 0 | 2021-12-19 | -8.5 | 26.5 | 0 | 2020-12-19 | -12.1 | 30.1 | 0 | 2019-12-19 | -21.8 | 39.8 | 0 | 2018-12-19 | -11.2 | 29.2 | 0 | 2017-12-19 | -10 | 28 | 0 | 2016-12-19 | -20.5 | 38.5 | 0 | 26.72 | 0
2025-12-19 | 6.1 | 11.9 | 0 | 2024-12-19 | -1 | 19 | 0 | 2023-12-19 | -1.9 | 19.9 | 0 | 2022-12-19 | -8.7 | 26.7 | 0 | 2021-12-19 | -8.1 | 26.1 | 0 | 2020-12-19 | -12.5 | 30.5 | 0 | 2019-12-19 | -21.8 | 39.8 | 0 | 2018-12-19 | -11.6 | 29.6 | 0 | 2017-12-19 | -10.1 | 28.1 | 0 | 2016-12-19 | -21.7 | 39.7 | 0 | 27.13 | 0
2025-12-19 | 6.5 | 11.5 | 0 | 2024-12-19 | -1.4 | 19.4 | 0 | 2023-12-19 | -2.7 | 20.7 | 0 | 2022-12-19 | -6.9 | 24.9 | 0 | 2021-12-19 | -9 | 27 | 0 | 2020-12-19 | -11.1 | 29.1 | 0 | 2019-12-19 | -21.8 | 39.8 | 0 | 2018-12-19 | -11.4 | 29.4 | 0 | 2017-12-19 | -9.6 | 27.6 | 0 | 2016-12-19 | -22.8 | 40.8 | 0 | 27.02 | 0
2025-12-19 | 7.8 | 10.2 | 0 | 2024-12-19 | -1.5 | 19.5 | 0 | 2023-12-19 | -3 | 21 | 0 | 2022-12-19 | -5.8 | 23.8 | 0 | 2021-12-19 | -9.2 | 27.2 | 0 | 2020-12-19 | -13.3 | 31.3 | 0 | 2019-12-19 | -21.9 | 39.9 | 0 | 2018-12-19 | -11.5 | 29.5 | 0 | 2017-12-19 | -9.5 | 27.5 | 0 | 2016-12-19 | -24.7 | 42.7 | 0 | 27.26 | 0
2025-12-19 | 7.9 | 10.1 | 0 | 2024-12-19 | -2.8 | 20.8 | 0 | 2023-12-19 | -3.6 | 21.6 | 0 | 2022-12-19 | -5.9 | 23.9 | 0 | 2021-12-19 | -9 | 27 | 0 | 2020-12-19 | -12.8 | 30.8 | 0 | 2019-12-19 | -21.9 | 39.9 | 0 | 2018-12-19 | -11.6 | 29.6 | 0 | 2017-12-19 | -9.3 | 27.3 | 0 | 2016-12-19 | -24.4 | 42.4 | 0 | 27.34 | 0
2025-12-19 | 9 | 9 | 0 | 2024-12-19 | -3.9 | 21.9 | 0 | 2023-12-19 | -4 | 22 | 0 | 2022-12-19 | -6.6 | 24.6 | 0 | 2021-12-19 | -9.6 | 27.6 | 0 | 2020-12-19 | -12.9 | 30.9 | 0 | 2019-12-19 | -21.8 | 39.8 | 0 | 2018-12-19 | -10.2 | 28.2 | 0 | 2017-12-19 | -8.8 | 26.8 | 0 | 2016-12-19 | -23.1 | 41.1 | 0 | 27.19 | 0
2025-12-19 | 10.2 | 7.8 | 0 | 2024-12-19 | -5 | 23 | 0 | 2023-12-19 | -4.1 | 22.1 | 0 | 2022-12-19 | -6.8 | 24.8 | 0 | 2021-12-19 | -10.2 | 28.2 | 0 | 2020-12-19 | -12.9 | 30.9 | 0 | 2019-12-19 | -21.8 | 39.8 | 0 | 2018-12-19 | -9.6 | 27.6 | 0 | 2017-12-19 | -8.8 | 26.8 | 0 | 2016-12-19 | -21.8 | 39.8 | 0 | 27.08 | 0
2025-12-19 | 10.6 | 7.4 | 0 | 2024-12-19 | -5.4 | 23.4 | 0 | 2023-12-19 | -4.2 | 22.2 | 0 | 2022-12-19 | -5.8 | 23.8 | 0 | 2021-12-19 | -9.6 | 27.6 | 0 | 2020-12-19 | -9.8 | 27.8 | 0 | 2019-12-19 | -21.2 | 39.2 | 0 | 2018-12-19 | -9.2 | 27.2 | 0 | 2017-12-19 | -8 | 26 | 0 | 2016-12-19 | -20.8 | 38.8 | 0 | 26.34 | 0
2025-12-19 | 8.8 | 9.2 | 0 | 2024-12-19 | -6.9 | 24.9 | 0 | 2023-12-19 | -4.3 | 22.3 | 0 | 2022-12-19 | -3.9 | 21.9 | 0 | 2021-12-19 | -9.4 | 27.4 | 0 | 2020-12-19 | -8.2 | 26.2 | 0 | 2019-12-19 | -20.4 | 38.4 | 0 | 2018-12-19 | -7.9 | 25.9 | 0 | 2017-12-19 | -3.8 | 21.8 | 0 | 2016-12-19 | -18.7 | 36.7 | 0 | 25.47 | 0
2025-12-19 | 4.6 | 13.4 | 0 | 2024-12-19 | -7.4 | 25.4 | 0 | 2023-12-19 | -3.9 | 21.9 | 0 | 2022-12-19 | -3 | 21 | 0 | 2021-12-19 | -9.3 | 27.3 | 0 | 2020-12-19 | -7.4 | 25.4 | 0 | 2019-12-19 | -19.2 | 37.2 | 0 | 2018-12-19 | -6.3 | 24.3 | 0 | 2017-12-19 | 2.7 | 15.3 | 0 | 2016-12-19 | -17.5 | 35.5 | 0 | 24.67 | 0
2025-12-19 | 4 | 14 | 0 | 2024-12-19 | -6.9 | 24.9 | 0 | 2023-12-19 | -4.8 | 22.8 | 0 | 2022-12-19 | -2.6 | 20.6 | 0 | 2021-12-19 | -9 | 27 | 0 | 2020-12-19 | -6.1 | 24.1 | 0 | 2019-12-19 | -18.1 | 36.1 | 0 | 2018-12-19 | -4.7 | 22.7 | 0 | 2017-12-19 | 3.4 | 14.6 | 0 | 2016-12-19 | -16.1 | 34.1 | 0 | 24.09 | 0
2025-12-19 | 3.5 | 14.5 | 0 | 2024-12-19 | -7.9 | 25.9 | 0 | 2023-12-19 | -4.7 | 22.7 | 0 | 2022-12-19 | -2 | 20 | 0 | 2021-12-19 | -9.1 | 27.1 | 0 | 2020-12-19 | -4.9 | 22.9 | 0 | 2019-12-19 | -17.7 | 35.7 | 0 | 2018-12-19 | -3.3 | 21.3 | 0 | 2017-12-19 | 3.3 | 14.7 | 0 | 2016-12-19 | -15.1 | 33.1 | 0 | 23.79 | 0
2025-12-19 | 3.4 | 14.6 | 0 | 2024-12-19 | -7.6 | 25.6 | 0 | 2023-12-19 | -5.1 | 23.1 | 0 | 2022-12-19 | -1.5 | 19.5 | 0 | 2021-12-19 | -8.6 | 26.6 | 0 | 2020-12-19 | -4 | 22 | 0 | 2019-12-19 | -17.1 | 35.1 | 0 | 2018-12-19 | -2.2 | 20.2 | 0 | 2017-12-19 | 3.8 | 14.2 | 0 | 2016-12-19 | -15.3 | 33.3 | 0 | 23.42 | 0
2025-12-19 | 2.2 | 15.8 | 0 | 2024-12-19 | -8.1 | 26.1 | 0 | 2023-12-19 | -5.4 | 23.4 | 0 | 2022-12-19 | -1.2 | 19.2 | 0 | 2021-12-19 | -8.8 | 26.8 | 0 | 2020-12-19 | -3.6 | 21.6 | 0 | 2019-12-19 | -16.8 | 34.8 | 0 | 2018-12-19 | -2.1 | 20.1 | 0 | 2017-12-19 | 4 | 14 | 0 | 2016-12-19 | -14.7 | 32.7 | 0 | 23.45 | 0
2025-12-19 | 1.2 | 16.8 | 0 | 2024-12-19 | -8.5 | 26.5 | 0 | 2023-12-19 | -5.7 | 23.7 | 0 | 2022-12-19 | -1 | 19 | 0 | 2021-12-19 | -9 | 27 | 0 | 2020-12-19 | -4 | 22 | 0 | 2019-12-19 | -17.1 | 35.1 | 0 | 2018-12-19 | -3 | 21 | 0 | 2017-12-19 | 2.5 | 15.5 | 0 | 2016-12-19 | -15.3 | 33.3 | 0 | 23.99 | 0
2025-12-19 | 1.2 | 16.8 | 0 | 2024-12-19 | -9.4 | 27.4 | 0 | 2023-12-19 | -7.1 | 25.1 | 0 | 2022-12-19 | -1.2 | 19.2 | 0 | 2021-12-19 | -11 | 29 | 0 | 2020-12-19 | -4 | 22 | 0 | 2019-12-19 | -17.6 | 35.6 | 0 | 2018-12-19 | -3.5 | 21.5 | 0 | 2017-12-19 | 2.9 | 15.1 | 0 | 2016-12-19 | -15.3 | 33.3 | 0 | 24.5 | 0
2025-12-19 | 0.6 | 17.4 | 0 | 2024-12-19 | -9.8 | 27.8 | 0 | 2023-12-19 | -8.9 | 26.9 | 0 | 2022-12-19 | -1.9 | 19.9 | 0 | 2021-12-19 | -11 | 29 | 0 | 2020-12-19 | -4.3 | 22.3 | 0 | 2019-12-19 | -17.4 | 35.4 | 0 | 2018-12-19 | -3.9 | 21.9 | 0 | 2017-12-19 | 2.8 | 15.2 | 0 | 2016-12-19 | -15.2 | 33.2 | 0 | 24.9 | 0
2025-12-19 | -1.4 | 19.4 | 0 | 2024-12-19 | -10.3 | 28.3 | 0 | 2023-12-19 | -8.2 | 26.2 | 0 | 2022-12-19 | -3 | 21 | 0 | 2021-12-19 | -13.3 | 31.3 | 0 | 2020-12-19 | -4.3 | 22.3 | 0 | 2019-12-19 | -17.9 | 35.9 | 0 | 2018-12-19 | -4.1 | 22.1 | 0 | 2017-12-19 | 2.1 | 15.9 | 0 | 2016-12-19 | -15.8 | 33.8 | 0 | 25.62 | 0
2025-12-19 | -1.8 | 19.8 | 0 | 2024-12-19 | -10.6 | 28.6 | 0 | 2023-12-19 | -8.8 | 26.8 | 0 | 2022-12-19 | -4.1 | 22.1 | 0 | 2021-12-19 | -14.1 | 32.1 | 0 | 2020-12-19 | -4.1 | 22.1 | 0 | 2019-12-19 | -19 | 37 | 0 | 2018-12-19 | -5.7 | 23.7 | 0 | 2017-12-19 | 1.4 | 16.6 | 0 | 2016-12-19 | -17.6 | 35.6 | 0 | 26.44 | 0
2025-12-19 | -4.1 | 22.1 | 0 | 2024-12-19 | -10.9 | 28.9 | 0 | 2023-12-19 | -8.9 | 26.9 | 0 | 2022-12-19 | -4.5 | 22.5 | 0 | 2021-12-19 | -14.1 | 32.1 | 0 | 2020-12-19 | -3.8 | 21.8 | 0 | 2019-12-19 | -18.3 | 36.3 | 0 | 2018-12-19 | -4.2 | 22.2 | 0 | 2017-12-19 | 0.7 | 17.3 | 0 | 2016-12-19 | -17.9 | 35.9 | 0 | 26.6 | 0
2025-12-19 | -5 | 23 | 0 | 2024-12-19 | -11.1 | 29.1 | 0 | 2023-12-19 | -9.1 | 27.1 | 0 | 2022-12-19 | -4.4 | 22.4 | 0 | 2021-12-19 | -16.3 | 34.3 | 0 | 2020-12-19 | -3.7 | 21.7 | 0 | 2019-12-19 | -18.3 | 36.3 | 0 | 2018-12-19 | -4.5 | 22.5 | 0 | 2017-12-19 | 0.8 | 17.2 | 0 | 2016-12-19 | -17.1 | 35.1 | 0 | 26.87 | 0
2025-12-19 | -6.2 | 24.2 | 0 | 2024-12-19 | -11.2 | 29.2 | 0 | 2023-12-19 | -8.8 | 26.8 | 0 | 2022-12-19 | -5.5 | 23.5 | 0 | 2021-12-19 | -16.1 | 34.1 | 0 | 2020-12-19 | -3.7 | 21.7 | 0 | 2019-12-19 | -18.6 | 36.6 | 0 | 2018-12-19 | -4.8 | 22.8 | 0 | 2017-12-19 | 0.5 | 17.5 | 0 | 2016-12-19 | -15.9 | 33.9 | 0 | 27.03 | 0
2025-12-20 | -6.8 | 24.8 | 0 | 2024-12-20 | -11.3 | 29.3 | 0 | 2023-12-20 | -8.7 | 26.7 | 0 | 2022-12-20 | -5.9 | 23.9 | 0 | 2021-12-20 | -17.6 | 35.6 | 0 | 2020-12-20 | -3.9 | 21.9 | 0 | 2019-12-20 | -18.6 | 36.6 | 0 | 2018-12-20 | -6.5 | 24.5 | 0 | 2017-12-20 | -0.1 | 18.1 | 0 | 2016-12-20 | -15.6 | 33.6 | 0 | 27.5 | 0
2025-12-20 | -7.4 | 25.4 | 0 | 2024-12-20 | -11.4 | 29.4 | 0 | 2023-12-20 | -7.6 | 25.6 | 0 | 2022-12-20 | -7.4 | 25.4 | 0 | 2021-12-20 | -15.7 | 33.7 | 0 | 2020-12-20 | -3.8 | 21.8 | 0 | 2019-12-20 | -18 | 36 | 0 | 2018-12-20 | -7.1 | 25.1 | 0 | 2017-12-20 | -0.8 | 18.8 | 0 | 2016-12-20 | -20 | 38 | 0 | 27.92 | 0
2025-12-20 | -7.9 | 25.9 | 0 | 2024-12-20 | -11.7 | 29.7 | 0 | 2023-12-20 | -8.2 | 26.2 | 0 | 2022-12-20 | -7.4 | 25.4 | 0 | 2021-12-20 | -16.6 | 34.6 | 0 | 2020-12-20 | -3.7 | 21.7 | 0 | 2019-12-20 | -17.6 | 35.6 | 0 | 2018-12-20 | -7.6 | 25.6 | 0 | 2017-12-20 | -1.1 | 19.1 | 0 | 2016-12-20 | -17.7 | 35.7 | 0 | 27.95 | 0
2025-12-20 | -8.3 | 26.3 | 0 | 2024-12-20 | -11.6 | 29.6 | 0 | 2023-12-20 | -8.5 | 26.5 | 0 | 2022-12-20 | -7 | 25 | 0 | 2021-12-20 | -18 | 36 | 0 | 2020-12-20 | -3.6 | 21.6 | 0 | 2019-12-20 | -17.7 | 35.7 | 0 | 2018-12-20 | -7.9 | 25.9 | 0 | 2017-12-20 | -0.3 | 18.3 | 0 | 2016-12-20 | -12.1 | 30.1 | 0 | 27.5 | 0
2025-12-20 | -9 | 27 | 0 | 2024-12-20 | -11.6 | 29.6 | 0 | 2023-12-20 | -8.7 | 26.7 | 0 | 2022-12-20 | -7.6 | 25.6 | 0 | 2021-12-20 | -18.7 | 36.7 | 0 | 2020-12-20 | -3.6 | 21.6 | 0 | 2019-12-20 | -18.9 | 36.9 | 0 | 2018-12-20 | -7.2 | 25.2 | 0 | 2017-12-20 | -0.9 | 18.9 | 0 | 2016-12-20 | -11.8 | 29.8 | 0 | 27.8 | 0
2025-12-20 | -9.4 | 27.4 | 0 | 2024-12-20 | -11.7 | 29.7 | 0 | 2023-12-20 | -8.9 | 26.9 | 0 | 2022-12-20 | -7.9 | 25.9 | 0 | 2021-12-20 | -15.7 | 33.7 | 0 | 2020-12-20 | -3.5 | 21.5 | 0 | 2019-12-20 | -18 | 36 | 0 | 2018-12-20 | -8 | 26 | 0 | 2017-12-20 | -0.2 | 18.2 | 0 | 2016-12-20 | -11.2 | 29.2 | 0 | 27.45 | 0
2025-12-20 | -9.9 | 27.9 | 0 | 2024-12-20 | -12 | 30 | 0 | 2023-12-20 | -7 | 25 | 0 | 2022-12-20 | -7.4 | 25.4 | 0 | 2021-12-20 | -14.9 | 32.9 | 0 | 2020-12-20 | -3.4 | 21.4 | 0 | 2019-12-20 | -18 | 36 | 0 | 2018-12-20 | -7.7 | 25.7 | 0 | 2017-12-20 | -1.1 | 19.1 | 0 | 2016-12-20 | -10.6 | 28.6 | 0 | 27.2 | 0
2025-12-20 | -10.6 | 28.6 | 0 | 2024-12-20 | -11.8 | 29.8 | 0 | 2023-12-20 | -5.9 | 23.9 | 0 | 2022-12-20 | -8 | 26 | 0 | 2021-12-20 | -15.1 | 33.1 | 0 | 2020-12-20 | -3.5 | 21.5 | 0 | 2019-12-20 | -17.9 | 35.9 | 0 | 2018-12-20 | -8.2 | 26.2 | 0 | 2017-12-20 | -2 | 20 | 0 | 2016-12-20 | -10.3 | 28.3 | 0 | 27.33 | 0
2025-12-20 | -11.2 | 29.2 | 0 | 2024-12-20 | -11.6 | 29.6 | 0 | 2023-12-20 | -5.3 | 23.3 | 0 | 2022-12-20 | -8.7 | 26.7 | 0 | 2021-12-20 | -14.4 | 32.4 | 0 | 2020-12-20 | -3.5 | 21.5 | 0 | 2019-12-20 | -18 | 36 | 0 | 2018-12-20 | -8.4 | 26.4 | 0 | 2017-12-20 | -2.5 | 20.5 | 0 | 2016-12-20 | -9 | 27 | 0 | 27.26 | 0
2025-12-20 | -9.5 | 27.5 | 0 | 2024-12-20 | -11.3 | 29.3 | 0 | 2023-12-20 | -4.1 | 22.1 | 0 | 2022-12-20 | -8.8 | 26.8 | 0 | 2021-12-20 | -13.7 | 31.7 | 0 | 2020-12-20 | -3.2 | 21.2 | 0 | 2019-12-20 | -17 | 35 | 0 | 2018-12-20 | -7 | 25 | 0 | 2017-12-20 | -3.8 | 21.8 | 0 | 2016-12-20 | -7.9 | 25.9 | 0 | 26.63 | 0
2025-12-20 | -8.7 | 26.7 | 0 | 2024-12-20 | -10.9 | 28.9 | 0 | 2023-12-20 | -2.9 | 20.9 | 0 | 2022-12-20 | -6.7 | 24.7 | 0 | 2021-12-20 | -11.4 | 29.4 | 0 | 2020-12-20 | -2.7 | 20.7 | 0 | 2019-12-20 | -15.6 | 33.6 | 0 | 2018-12-20 | -4.7 | 22.7 | 0 | 2017-12-20 | -4.2 | 22.2 | 0 | 2016-12-20 | -6.7 | 24.7 | 0 | 25.45 | 0
2025-12-20 | -7.8 | 25.8 | 0 | 2024-12-20 | -10.5 | 28.5 | 0 | 2023-12-20 | -2.3 | 20.3 | 0 | 2022-12-20 | -6.5 | 24.5 | 0 | 2021-12-20 | -8.2 | 26.2 | 0 | 2020-12-20 | -2 | 20 | 0 | 2019-12-20 | -14.9 | 32.9 | 0 | 2018-12-20 | -2.7 | 20.7 | 0 | 2017-12-20 | -3.9 | 21.9 | 0 | 2016-12-20 | -5.9 | 23.9 | 0 | 24.47 | 0
2025-12-20 | -7.2 | 25.2 | 0 | 2024-12-20 | -9.8 | 27.8 | 0 | 2023-12-20 | -1.8 | 19.8 | 0 | 2022-12-20 | -5.6 | 23.6 | 0 | 2021-12-20 | -5.5 | 23.5 | 0 | 2020-12-20 | -1.6 | 19.6 | 0 | 2019-12-20 | -13.8 | 31.8 | 0 | 2018-12-20 | -0.2 | 18.2 | 0 | 2017-12-20 | -4 | 22 | 0 | 2016-12-20 | -5.6 | 23.6 | 0 | 23.51 | 0
2025-12-20 | -6.6 | 24.6 | 0 | 2024-12-20 | -9.2 | 27.2 | 0 | 2023-12-20 | -1.2 | 19.2 | 0 | 2022-12-20 | -5.1 | 23.1 | 0 | 2021-12-20 | -3.6 | 21.6 | 0 | 2020-12-20 | -1.2 | 19.2 | 0 | 2019-12-20 | -12.9 | 30.9 | 0 | 2018-12-20 | 1.1 | 16.9 | 0 | 2017-12-20 | -4 | 22 | 0 | 2016-12-20 | -5.5 | 23.5 | 0 | 22.82 | 0
2025-12-20 | -6.2 | 24.2 | 0 | 2024-12-20 | -8.8 | 26.8 | 0 | 2023-12-20 | -1.1 | 19.1 | 0 | 2022-12-20 | -4.7 | 22.7 | 0 | 2021-12-20 | -2.6 | 20.6 | 0 | 2020-12-20 | -0.8 | 18.8 | 0 | 2019-12-20 | -12.2 | 30.2 | 0 | 2018-12-20 | 1.4 | 16.6 | 0 | 2017-12-20 | -4.7 | 22.7 | 0 | 2016-12-20 | -5.1 | 23.1 | 0 | 22.48 | 0
2025-12-20 | -6.5 | 24.5 | 0 | 2024-12-20 | -8.4 | 26.4 | 0 | 2023-12-20 | -1.1 | 19.1 | 0 | 2022-12-20 | -4.9 | 22.9 | 0 | 2021-12-20 | -2 | 20 | 0 | 2020-12-20 | -0.6 | 18.6 | 0 | 2019-12-20 | -11.9 | 29.9 | 0 | 2018-12-20 | 1 | 17 | 0 | 2017-12-20 | -5.7 | 23.7 | 0 | 2016-12-20 | -4.4 | 22.4 | 0 | 22.45 | 0
2025-12-20 | -6 | 24 | 0 | 2024-12-20 | -8.1 | 26.1 | 0 | 2023-12-20 | -1.2 | 19.2 | 0 | 2022-12-20 | -5.7 | 23.7 | 0 | 2021-12-20 | -1.7 | 19.7 | 0 | 2020-12-20 | -0.4 | 18.4 | 0 | 2019-12-20 | -12.4 | 30.4 | 0 | 2018-12-20 | 0.9 | 17.1 | 0 | 2017-12-20 | -6.9 | 24.9 | 0 | 2016-12-20 | -4.4 | 22.4 | 0 | 22.59 | 0
2025-12-20 | -5.1 | 23.1 | 0 | 2024-12-20 | -7.8 | 25.8 | 0 | 2023-12-20 | -1.7 | 19.7 | 0 | 2022-12-20 | -6.9 | 24.9 | 0 | 2021-12-20 | -0.9 | 18.9 | 0 | 2020-12-20 | -0.1 | 18.1 | 0 | 2019-12-20 | -13.9 | 31.9 | 0 | 2018-12-20 | 0.5 | 17.5 | 0 | 2017-12-20 | -8 | 26 | 0 | 2016-12-20 | -4.4 | 22.4 | 0 | 22.83 | 0
2025-12-20 | -4.3 | 22.3 | 0 | 2024-12-20 | -7.5 | 25.5 | 0 | 2023-12-20 | -1.1 | 19.1 | 0 | 2022-12-20 | -5.5 | 23.5 | 0 | 2021-12-20 | -0.3 | 18.3 | 0 | 2020-12-20 | 0.1 | 17.9 | 0 | 2019-12-20 | -14.9 | 32.9 | 0 | 2018-12-20 | 0.4 | 17.6 | 0 | 2017-12-20 | -9.1 | 27.1 | 0 | 2016-12-20 | -4.9 | 22.9 | 0 | 22.71 | 0
2025-12-20 | -4.1 | 22.1 | 0 | 2024-12-20 | -7.6 | 25.6 | 0 | 2023-12-20 | -1.3 | 19.3 | 0 | 2022-12-20 | -5.5 | 23.5 | 0 | 2021-12-20 | 0.7 | 17.3 | 0 | 2020-12-20 | 0.6 | 17.4 | 0 | 2019-12-20 | -14.9 | 32.9 | 0 | 2018-12-20 | 0.5 | 17.5 | 0 | 2017-12-20 | -9.7 | 27.7 | 0 | 2016-12-20 | -4.7 | 22.7 | 0 | 22.6 | 0
2025-12-20 | -3.9 | 21.9 | 0 | 2024-12-20 | -7.7 | 25.7 | 0 | 2023-12-20 | -1.2 | 19.2 | 0 | 2022-12-20 | -5.3 | 23.3 | 0 | 2021-12-20 | 1 | 17 | 0 | 2020-12-20 | 0.7 | 17.3 | 0 | 2019-12-20 | -14.9 | 32.9 | 0 | 2018-12-20 | 0.4 | 17.6 | 0 | 2017-12-20 | -10.2 | 28.2 | 0 | 2016-12-20 | -5.2 | 23.2 | 0 | 22.63 | 0
2025-12-20 | -1.5 | 19.5 | 0 | 2024-12-20 | -7.8 | 25.8 | 0 | 2023-12-20 | -1.6 | 19.6 | 0 | 2022-12-20 | -5.3 | 23.3 | 0 | 2021-12-20 | 1.1 | 16.9 | 0 | 2020-12-20 | 0.8 | 17.2 | 0 | 2019-12-20 | -15.1 | 33.1 | 0 | 2018-12-20 | 0.4 | 17.6 | 0 | 2017-12-20 | -11.2 | 29.2 | 0 | 2016-12-20 | -4.3 | 22.3 | 0 | 22.45 | 0
2025-12-20 | -1.6 | 19.6 | 0 | 2024-12-20 | -8.1 | 26.1 | 0 | 2023-12-20 | -2.7 | 20.7 | 0 | 2022-12-20 | -5.5 | 23.5 | 0 | 2021-12-20 | 1.5 | 16.5 | 0 | 2020-12-20 | 0.9 | 17.1 | 0 | 2019-12-20 | -15.8 | 33.8 | 0 | 2018-12-20 | 0.7 | 17.3 | 0 | 2017-12-20 | -12.9 | 30.9 | 0 | 2016-12-20 | -2.9 | 20.9 | 0 | 22.64 | 0
2025-12-20 | -0.5 | 18.5 | 0 | 2024-12-20 | -8.6 | 26.6 | 0 | 2023-12-20 | -3.5 | 21.5 | 0 | 2022-12-20 | -5.5 | 23.5 | 0 | 2021-12-20 | 1.5 | 16.5 | 0 | 2020-12-20 | 1 | 17 | 0 | 2019-12-20 | -16.8 | 34.8 | 0 | 2018-12-20 | 0.8 | 17.2 | 0 | 2017-12-20 | -14 | 32 | 0 | 2016-12-20 | -0.9 | 18.9 | 0 | 22.65 | 0
2025-12-21 | 0.3 | 17.7 | 0 | 2024-12-21 | -9.2 | 27.2 | 0 | 2023-12-21 | -5.1 | 23.1 | 0 | 2022-12-21 | -5.5 | 23.5 | 0 | 2021-12-21 | 0.9 | 17.1 | 0 | 2020-12-21 | 0.9 | 17.1 | 0 | 2019-12-21 | -15.8 | 33.8 | 0 | 2018-12-21 | -0.1 | 18.1 | 0 | 2017-12-21 | -13.2 | 31.2 | 0 | 2016-12-21 | -0.6 | 18.6 | 0 | 22.74 | 0
2025-12-21 | 0.4 | 17.6 | 0 | 2024-12-21 | -9.5 | 27.5 | 0 | 2023-12-21 | -5.7 | 23.7 | 0 | 2022-12-21 | -5.4 | 23.4 | 0 | 2021-12-21 | 1.5 | 16.5 | 0 | 2020-12-21 | 0.8 | 17.2 | 0 | 2019-12-21 | -15.8 | 33.8 | 0 | 2018-12-21 | -0.3 | 18.3 | 0 | 2017-12-21 | -14.1 | 32.1 | 0 | 2016-12-21 | -0.8 | 18.8 | 0 | 22.89 | 0
2025-12-21 | 1.3 | 16.7 | 0 | 2024-12-21 | -10 | 28 | 0 | 2023-12-21 | -7.1 | 25.1 | 0 | 2022-12-21 | -5.3 | 23.3 | 0 | 2021-12-21 | 1.5 | 16.5 | 0 | 2020-12-21 | 1.1 | 16.9 | 0 | 2019-12-21 | -16.6 | 34.6 | 0 | 2018-12-21 | -0.1 | 18.1 | 0 | 2017-12-21 | -13.9 | 31.9 | 0 | 2016-12-21 | -0.9 | 18.9 | 0 | 23 | 0
2025-12-21 | 1.3 | 16.7 | 0 | 2024-12-21 | -10.3 | 28.3 | 0 | 2023-12-21 | -8.2 | 26.2 | 0 | 2022-12-21 | -5.2 | 23.2 | 0 | 2021-12-21 | 1.6 | 16.4 | 0 | 2020-12-21 | 0.9 | 17.1 | 0 | 2019-12-21 | -15.8 | 33.8 | 0 | 2018-12-21 | 0.2 | 17.8 | 0 | 2017-12-21 | -13.8 | 31.8 | 0 | 2016-12-21 | -1.2 | 19.2 | 0 | 23.05 | 0
2025-12-21 | 2.1 | 15.9 | 0 | 2024-12-21 | -10.8 | 28.8 | 0 | 2023-12-21 | -8.7 | 26.7 | 0 | 2022-12-21 | -5 | 23 | 0 | 2021-12-21 | 0.5 | 17.5 | 0 | 2020-12-21 | 1.2 | 16.8 | 0 | 2019-12-21 | -15.2 | 33.2 | 0 | 2018-12-21 | 0.4 | 17.6 | 0 | 2017-12-21 | -14.3 | 32.3 | 0 | 2016-12-21 | -2.1 | 20.1 | 0 | 23.19 | 0
2025-12-21 | 0 | 18 | 0 | 2024-12-21 | -11.5 | 29.5 | 0 | 2023-12-21 | -9.3 | 27.3 | 0 | 2022-12-21 | -4.6 | 22.6 | 0 | 2021-12-21 | -0.2 | 18.2 | 0 | 2020-12-21 | 0.5 | 17.5 | 0 | 2019-12-21 | -15.7 | 33.7 | 0 | 2018-12-21 | 1.2 | 16.8 | 0 | 2017-12-21 | -13.1 | 31.1 | 0 | 2016-12-21 | -2.8 | 20.8 | 0 | 23.55 | 0
2025-12-21 | -2.1 | 20.1 | 0 | 2024-12-21 | -12.1 | 30.1 | 0 | 2023-12-21 | -9.9 | 27.9 | 0 | 2022-12-21 | -4 | 22 | 0 | 2021-12-21 | -0.9 | 18.9 | 0 | 2020-12-21 | 0.5 | 17.5 | 0 | 2019-12-21 | -14.8 | 32.8 | 0 | 2018-12-21 | 1.7 | 16.3 | 0 | 2017-12-21 | -13.5 | 31.5 | 0 | 2016-12-21 | -2.9 | 20.9 | 0 | 23.8 | 0
2025-12-21 | -3.2 | 21.2 | 0 | 2024-12-21 | -12.7 | 30.7 | 0 | 2023-12-21 | -10.5 | 28.5 | 0 | 2022-12-21 | -3.9 | 21.9 | 0 | 2021-12-21 | -1.5 | 19.5 | 0 | 2020-12-21 | 0.8 | 17.2 | 0 | 2019-12-21 | -14.7 | 32.7 | 0 | 2018-12-21 | 2.4 | 15.6 | 0 | 2017-12-21 | -14.5 | 32.5 | 0 | 2016-12-21 | -3.1 | 21.1 | 0 | 24.09 | 0
2025-12-21 | -4 | 22 | 0 | 2024-12-21 | -12.9 | 30.9 | 0 | 2023-12-21 | -10.5 | 28.5 | 0 | 2022-12-21 | -4.6 | 22.6 | 0 | 2021-12-21 | -2.9 | 20.9 | 0 | 2020-12-21 | 0.5 | 17.5 | 0 | 2019-12-21 | -14.8 | 32.8 | 0 | 2018-12-21 | 2.5 | 15.5 | 0 | 2017-12-21 | -14.3 | 32.3 | 0 | 2016-12-21 | -2 | 20 | 0 | 24.3 | 0
2025-12-21 | -3.4 | 21.4 | 0 | 2024-12-21 | -13.2 | 31.2 | 0 | 2023-12-21 | -9.3 | 27.3 | 0 | 2022-12-21 | -3.5 | 21.5 | 0 | 2021-12-21 | -3.3 | 21.3 | 0 | 2020-12-21 | 0.7 | 17.3 | 0 | 2019-12-21 | -14.1 | 32.1 | 0 | 2018-12-21 | 2.5 | 15.5 | 0 | 2017-12-21 | -13.8 | 31.8 | 0 | 2016-12-21 | -2.3 | 20.3 | 0 | 23.97 | 0
2025-12-21 | -3.6 | 21.6 | 0 | 2024-12-21 | -12.9 | 30.9 | 0 | 2023-12-21 | -8.5 | 26.5 | 0 | 2022-12-21 | -2.3 | 20.3 | 0 | 2021-12-21 | -3.1 | 21.1 | 0 | 2020-12-21 | 1.8 | 16.2 | 0 | 2019-12-21 | -12.8 | 30.8 | 0 | 2018-12-21 | 3 | 15 | 0 | 2017-12-21 | -13.2 | 31.2 | 0 | 2016-12-21 | -1.8 | 19.8 | 0 | 23.34 | 0
2025-12-21 | -3.5 | 21.5 | 0 | 2024-12-21 | -12.8 | 30.8 | 0 | 2023-12-21 | -7.3 | 25.3 | 0 | 2022-12-21 | -1.3 | 19.3 | 0 | 2021-12-21 | -3.5 | 21.5 | 0 | 2020-12-21 | 2.5 | 15.5 | 0 | 2019-12-21 | -11.7 | 29.7 | 0 | 2018-12-21 | 3.4 | 14.6 | 0 | 2017-12-21 | -12.6 | 30.6 | 0 | 2016-12-21 | -1.3 | 19.3 | 0 | 22.81 | 0
2025-12-21 | -3.6 | 21.6 | 0 | 2024-12-21 | -12.3 | 30.3 | 0 | 2023-12-21 | -6.6 | 24.6 | 0 | 2022-12-21 | -0.6 | 18.6 | 0 | 2021-12-21 | -3.2 | 21.2 | 0 | 2020-12-21 | 3 | 15 | 0 | 2019-12-21 | -10.8 | 28.8 | 0 | 2018-12-21 | 3.8 | 14.2 | 0 | 2017-12-21 | -11.7 | 29.7 | 0 | 2016-12-21 | 0.2 | 17.8 | 0 | 22.18 | 0
2025-12-21 | -3.4 | 21.4 | 0 | 2024-12-21 | -12.3 | 30.3 | 0 | 2023-12-21 | -6 | 24 | 0 | 2022-12-21 | -0.6 | 18.6 | 0 | 2021-12-21 | -3.1 | 21.1 | 0 | 2020-12-21 | 2.7 | 15.3 | 0 | 2019-12-21 | -9.9 | 27.9 | 0 | 2018-12-21 | 4.1 | 13.9 | 0 | 2017-12-21 | -11.7 | 29.7 | 0 | 2016-12-21 | 1.3 | 16.7 | 0 | 21.89 | 0
2025-12-21 | -4.4 | 22.4 | 0 | 2024-12-21 | -12 | 30 | 0 | 2023-12-21 | -5.7 | 23.7 | 0 | 2022-12-21 | -3.5 | 21.5 | 0 | 2021-12-21 | -3.1 | 21.1 | 0 | 2020-12-21 | 2.5 | 15.5 | 0 | 2019-12-21 | -9.2 | 27.2 | 0 | 2018-12-21 | 3.7 | 14.3 | 0 | 2017-12-21 | -11.1 | 29.1 | 0 | 2016-12-21 | 2.1 | 15.9 | 0 | 22.07 | 0
2025-12-21 | -5 | 23 | 0 | 2024-12-21 | -12.2 | 30.2 | 0 | 2023-12-21 | -5.6 | 23.6 | 0 | 2022-12-21 | -3.7 | 21.7 | 0 | 2021-12-21 | -2.6 | 20.6 | 0 | 2020-12-21 | 2.1 | 15.9 | 0 | 2019-12-21 | -8.8 | 26.8 | 0 | 2018-12-21 | 4.1 | 13.9 | 0 | 2017-12-21 | -11.6 | 29.6 | 0 | 2016-12-21 | 3 | 15 | 0 | 22.03 | 0
2025-12-21 | -6.3 | 24.3 | 0 | 2024-12-21 | -13 | 31 | 0 | 2023-12-21 | -6.7 | 24.7 | 0 | 2022-12-21 | -4.3 | 22.3 | 0 | 2021-12-21 | -3.8 | 21.8 | 0 | 2020-12-21 | 1.2 | 16.8 | 0 | 2019-12-21 | -9.5 | 27.5 | 0 | 2018-12-21 | 4.5 | 13.5 | 0 | 2017-12-21 | -11.9 | 29.9 | 0 | 2016-12-21 | 2.5 | 15.5 | 0 | 22.73 | 0
2025-12-21 | -7.4 | 25.4 | 0 | 2024-12-21 | -13.5 | 31.5 | 0 | 2023-12-21 | -7.4 | 25.4 | 0 | 2022-12-21 | -4.8 | 22.8 | 0 | 2021-12-21 | -4.4 | 22.4 | 0 | 2020-12-21 | 1.2 | 16.8 | 0 | 2019-12-21 | -9.7 | 27.7 | 0 | 2018-12-21 | 3.5 | 14.5 | 0 | 2017-12-21 | -11.6 | 29.6 | 0 | 2016-12-21 | 2.2 | 15.8 | 0 | 23.19 | 0
2025-12-21 | -8.3 | 26.3 | 0 | 2024-12-21 | -14.6 | 32.6 | 0 | 2023-12-21 | -7.7 | 25.7 | 0 | 2022-12-21 | -5.2 | 23.2 | 0 | 2021-12-21 | -5 | 23 | 0 | 2020-12-21 | 1 | 17 | 0 | 2019-12-21 | -10.1 | 28.1 | 0 | 2018-12-21 | 2.9 | 15.1 | 0 | 2017-12-21 | -11.4 | 29.4 | 0 | 2016-12-21 | 1.5 | 16.5 | 0 | 23.69 | 0
2025-12-21 | -9.2 | 27.2 | 0 | 2024-12-21 | -15.7 | 33.7 | 0 | 2023-12-21 | -9.2 | 27.2 | 0 | 2022-12-21 | -7.1 | 25.1 | 0 | 2021-12-21 | -5.2 | 23.2 | 0 | 2020-12-21 | 0.8 | 17.2 | 0 | 2019-12-21 | -10 | 28 | 0 | 2018-12-21 | 3.7 | 14.3 | 0 | 2017-12-21 | -12.7 | 30.7 | 0 | 2016-12-21 | 0.7 | 17.3 | 0 | 24.39 | 0
2025-12-21 | -10.1 | 28.1 | 0 | 2024-12-21 | -16.5 | 34.5 | 0 | 2023-12-21 | -8.7 | 26.7 | 0 | 2022-12-21 | -8.1 | 26.1 | 0 | 2021-12-21 | -5.2 | 23.2 | 0 | 2020-12-21 | 0.4 | 17.6 | 0 | 2019-12-21 | -9.8 | 27.8 | 0 | 2018-12-21 | 3.5 | 14.5 | 0 | 2017-12-21 | -12.7 | 30.7 | 0 | 2016-12-21 | 0.4 | 17.6 | 0 | 24.68 | 0
2025-12-21 | -10.8 | 28.8 | 0 | 2024-12-21 | -16.8 | 34.8 | 0 | 2023-12-21 | -9 | 27 | 0 | 2022-12-21 | -7.3 | 25.3 | 0 | 2021-12-21 | -5.2 | 23.2 | 0 | 2020-12-21 | 0.4 | 17.6 | 0 | 2019-12-21 | -10.2 | 28.2 | 0 | 2018-12-21 | 3.5 | 14.5 | 0 | 2017-12-21 | -14.2 | 32.2 | 0 | 2016-12-21 | 0.1 | 17.9 | 0 | 24.95 | 0
2025-12-21 | -11.2 | 29.2 | 0 | 2024-12-21 | -17 | 35 | 0 | 2023-12-21 | -9.5 | 27.5 | 0 | 2022-12-21 | -8.1 | 26.1 | 0 | 2021-12-21 | -5.2 | 23.2 | 0 | 2020-12-21 | 0.2 | 17.8 | 0 | 2019-12-21 | -11.2 | 29.2 | 0 | 2018-12-21 | 2.8 | 15.2 | 0 | 2017-12-21 | -14.7 | 32.7 | 0 | 2016-12-21 | -0.1 | 18.1 | 0 | 25.4 | 0
2025-12-21 | -11.6 | 29.6 | 0 | 2024-12-21 | -16.6 | 34.6 | 0 | 2023-12-21 | -10.6 | 28.6 | 0 | 2022-12-21 | -8.8 | 26.8 | 0 | 2021-12-21 | -5.1 | 23.1 | 0 | 2020-12-21 | 0.1 | 17.9 | 0 | 2019-12-21 | -11.9 | 29.9 | 0 | 2018-12-21 | 2 | 16 | 0 | 2017-12-21 | -15.1 | 33.1 | 0 | 2016-12-21 | -0.3 | 18.3 | 0 | 25.79 | 0
2025-12-22 | -12.2 | 30.2 | 0 | 2024-12-22 | -16.7 | 34.7 | 0 | 2023-12-22 | -11.6 | 29.6 | 0 | 2022-12-22 | -8.9 | 26.9 | 0 | 2021-12-22 | -5.6 | 23.6 | 0 | 2020-12-22 | 0.2 | 17.8 | 0 | 2019-12-22 | -12.1 | 30.1 | 0 | 2018-12-22 | 1.8 | 16.2 | 0 | 2017-12-22 | -15.2 | 33.2 | 0 | 2016-12-22 | -0.6 | 18.6 | 0 | 26.09 | 0
2025-12-22 | -12.6 | 30.6 | 0 | 2024-12-22 | -17.4 | 35.4 | 0 | 2023-12-22 | -11.2 | 29.2 | 0 | 2022-12-22 | -10.1 | 28.1 | 0 | 2021-12-22 | -6.1 | 24.1 | 0 | 2020-12-22 | 0.1 | 17.9 | 0 | 2019-12-22 | -12 | 30 | 0 | 2018-12-22 | 1.7 | 16.3 | 0 | 2017-12-22 | -15.5 | 33.5 | 0 | 2016-12-22 | -1.5 | 19.5 | 0 | 26.46 | 0
2025-12-22 | -12 | 30 | 0 | 2024-12-22 | -17.5 | 35.5 | 0 | 2023-12-22 | -11.9 | 29.9 | 0 | 2022-12-22 | -11.2 | 29.2 | 0 | 2021-12-22 | -6.6 | 24.6 | 0 | 2020-12-22 | 0.1 | 17.9 | 0 | 2019-12-22 | -11.7 | 29.7 | 0 | 2018-12-22 | 0.8 | 17.2 | 0 | 2017-12-22 | -15.6 | 33.6 | 0 | 2016-12-22 | -1.4 | 19.4 | 0 | 26.7 | 0
2025-12-22 | -13.5 | 31.5 | 0 | 2024-12-22 | -18.5 | 36.5 | 0 | 2023-12-22 | -11.1 | 29.1 | 0 | 2022-12-22 | -11.1 | 29.1 | 0 | 2021-12-22 | -6.8 | 24.8 | 0 | 2020-12-22 | 0.1 | 17.9 | 0 | 2019-12-22 | -11.6 | 29.6 | 0 | 2018-12-22 | 0.2 | 17.8 | 0 | 2017-12-22 | -15.3 | 33.3 | 0 | 2016-12-22 | -1.2 | 19.2 | 0 | 26.88 | 0
2025-12-22 | -14.2 | 32.2 | 0 | 2024-12-22 | -18.1 | 36.1 | 0 | 2023-12-22 | -11.4 | 29.4 | 0 | 2022-12-22 | -11.7 | 29.7 | 0 | 2021-12-22 | -6.6 | 24.6 | 0 | 2020-12-22 | 0.1 | 17.9 | 0 | 2019-12-22 | -11.3 | 29.3 | 0 | 2018-12-22 | -0.4 | 18.4 | 0 | 2017-12-22 | -15.3 | 33.3 | 0 | 2016-12-22 | -1.2 | 19.2 | 0 | 27.01 | 0
2025-12-22 | -14.4 | 32.4 | 0 | 2024-12-22 | -17.6 | 35.6 | 0 | 2023-12-22 | -11.5 | 29.5 | 0 | 2022-12-22 | -11.1 | 29.1 | 0 | 2021-12-22 | -6.2 | 24.2 | 0 | 2020-12-22 | -0.3 | 18.3 | 0 | 2019-12-22 | -11.8 | 29.8 | 0 | 2018-12-22 | -1.4 | 19.4 | 0 | 2017-12-22 | -15.1 | 33.1 | 0 | 2016-12-22 | -1.1 | 19.1 | 0 | 27.05 | 0
2025-12-22 | -12.9 | 30.9 | 0 | 2024-12-22 | -17.5 | 35.5 | 0 | 2023-12-22 | -12.7 | 30.7 | 0 | 2022-12-22 | -9.9 | 27.9 | 0 | 2021-12-22 | -5.3 | 23.3 | 0 | 2020-12-22 | -1.1 | 19.1 | 0 | 2019-12-22 | -11 | 29 | 0 | 2018-12-22 | -2.1 | 20.1 | 0 | 2017-12-22 | -15 | 33 | 0 | 2016-12-22 | -0.9 | 18.9 | 0 | 26.84 | 0
2025-12-22 | -12.3 | 30.3 | 0 | 2024-12-22 | -18.2 | 36.2 | 0 | 2023-12-22 | -13.1 | 31.1 | 0 | 2022-12-22 | -9.6 | 27.6 | 0 | 2021-12-22 | -4.5 | 22.5 | 0 | 2020-12-22 | -1 | 19 | 0 | 2019-12-22 | -10.2 | 28.2 | 0 | 2018-12-22 | -2.8 | 20.8 | 0 | 2017-12-22 | -14.6 | 32.6 | 0 | 2016-12-22 | -1 | 19 | 0 | 26.73 | 0
2025-12-22 | -11.6 | 29.6 | 0 | 2024-12-22 | -19.3 | 37.3 | 0 | 2023-12-22 | -12.3 | 30.3 | 0 | 2022-12-22 | -9.1 | 27.1 | 0 | 2021-12-22 | -4.6 | 22.6 | 0 | 2020-12-22 | -0.8 | 18.8 | 0 | 2019-12-22 | -9.6 | 27.6 | 0 | 2018-12-22 | -3.2 | 21.2 | 0 | 2017-12-22 | -14.6 | 32.6 | 0 | 2016-12-22 | -1.2 | 19.2 | 0 | 26.63 | 0
2025-12-22 | -10.4 | 28.4 | 0 | 2024-12-22 | -17.4 | 35.4 | 0 | 2023-12-22 | -10.6 | 28.6 | 0 | 2022-12-22 | -8.6 | 26.6 | 0 | 2021-12-22 | -3.1 | 21.1 | 0 | 2020-12-22 | -0.4 | 18.4 | 0 | 2019-12-22 | -8.4 | 26.4 | 0 | 2018-12-22 | -3.4 | 21.4 | 0 | 2017-12-22 | -14.6 | 32.6 | 0 | 2016-12-22 | -1.2 | 19.2 | 0 | 25.81 | 0
2025-12-22 | -8.8 | 26.8 | 0 | 2024-12-22 | -16.1 | 34.1 | 0 | 2023-12-22 | -9 | 27 | 0 | 2022-12-22 | -7.5 | 25.5 | 0 | 2021-12-22 | -4.4 | 22.4 | 0 | 2020-12-22 | 0.3 | 17.7 | 0 | 2019-12-22 | -6.3 | 24.3 | 0 | 2018-12-22 | -3.4 | 21.4 | 0 | 2017-12-22 | -14.2 | 32.2 | 0 | 2016-12-22 | -1 | 19 | 0 | 25.04 | 0
2025-12-22 | -8.7 | 26.7 | 0 | 2024-12-22 | -15.2 | 33.2 | 0 | 2023-12-22 | -7.8 | 25.8 | 0 | 2022-12-22 | -5.8 | 23.8 | 0 | 2021-12-22 | -2.9 | 20.9 | 0 | 2020-12-22 | 0.3 | 17.7 | 0 | 2019-12-22 | -0.2 | 18.2 | 0 | 2018-12-22 | -4.4 | 22.4 | 0 | 2017-12-22 | -13.7 | 31.7 | 0 | 2016-12-22 | -0.9 | 18.9 | 0 | 23.93 | 0
2025-12-22 | -8.2 | 26.2 | 0 | 2024-12-22 | -14.5 | 32.5 | 0 | 2023-12-22 | -7 | 25 | 0 | 2022-12-22 | -5.4 | 23.4 | 0 | 2021-12-22 | 0.4 | 17.6 | 0 | 2020-12-22 | 1.4 | 16.6 | 0 | 2019-12-22 | 2.4 | 15.6 | 0 | 2018-12-22 | -4.4 | 22.4 | 0 | 2017-12-22 | -13.4 | 31.4 | 0 | 2016-12-22 | -0.1 | 18.1 | 0 | 22.88 | 0
2025-12-22 | -7.7 | 25.7 | 0 | 2024-12-22 | -13.9 | 31.9 | 0 | 2023-12-22 | -6.5 | 24.5 | 0 | 2022-12-22 | -4.6 | 22.6 | 0 | 2021-12-22 | 0 | 18 | 0 | 2020-12-22 | 1.2 | 16.8 | 0 | 2019-12-22 | 3.1 | 14.9 | 0 | 2018-12-22 | -4.1 | 22.1 | 0 | 2017-12-22 | -13.1 | 31.1 | 0 | 2016-12-22 | 0 | 18 | 0 | 22.56 | 0
2025-12-22 | -7.2 | 25.2 | 0 | 2024-12-22 | -13.2 | 31.2 | 0 | 2023-12-22 | -5.8 | 23.8 | 0 | 2022-12-22 | -4.5 | 22.5 | 0 | 2021-12-22 | -0.3 | 18.3 | 0 | 2020-12-22 | 0.5 | 17.5 | 0 | 2019-12-22 | 3.3 | 14.7 | 0 | 2018-12-22 | -4.2 | 22.2 | 0 | 2017-12-22 | -12.9 | 30.9 | 0 | 2016-12-22 | 0.2 | 17.8 | 0 | 22.41 | 0
2025-12-22 | -6.9 | 24.9 | 0 | 2024-12-22 | -13 | 31 | 0 | 2023-12-22 | -5.5 | 23.5 | 0 | 2022-12-22 | -4.6 | 22.6 | 0 | 2021-12-22 | -0.9 | 18.9 | 0 | 2020-12-22 | -0.7 | 18.7 | 0 | 2019-12-22 | 3.3 | 14.7 | 0 | 2018-12-22 | -4.8 | 22.8 | 0 | 2017-12-22 | -12.7 | 30.7 | 0 | 2016-12-22 | -0.2 | 18.2 | 0 | 22.6 | 0
2025-12-22 | -6.7 | 24.7 | 0 | 2024-12-22 | -13.5 | 31.5 | 0 | 2023-12-22 | -7 | 25 | 0 | 2022-12-22 | -4.7 | 22.7 | 0 | 2021-12-22 | -2.5 | 20.5 | 0 | 2020-12-22 | -1.5 | 19.5 | 0 | 2019-12-22 | 2.8 | 15.2 | 0 | 2018-12-22 | -5 | 23 | 0 | 2017-12-22 | -12.3 | 30.3 | 0 | 2016-12-22 | 0.3 | 17.7 | 0 | 23.01 | 0
2025-12-22 | -6.7 | 24.7 | 0 | 2024-12-22 | -13.8 | 31.8 | 0 | 2023-12-22 | -7.6 | 25.6 | 0 | 2022-12-22 | -5 | 23 | 0 | 2021-12-22 | -5.2 | 23.2 | 0 | 2020-12-22 | -2.8 | 20.8 | 0 | 2019-12-22 | 2.1 | 15.9 | 0 | 2018-12-22 | -5.6 | 23.6 | 0 | 2017-12-22 | -12.1 | 30.1 | 0 | 2016-12-22 | 0.4 | 17.6 | 0 | 23.63 | 0
2025-12-22 | -6.5 | 24.5 | 0 | 2024-12-22 | -14.6 | 32.6 | 0 | 2023-12-22 | -8.5 | 26.5 | 0 | 2022-12-22 | -4.9 | 22.9 | 0 | 2021-12-22 | -6.1 | 24.1 | 0 | 2020-12-22 | -3.5 | 21.5 | 0 | 2019-12-22 | 2 | 16 | 0 | 2018-12-22 | -6.4 | 24.4 | 0 | 2017-12-22 | -11.9 | 29.9 | 0 | 2016-12-22 | 0.1 | 17.9 | 0 | 24.03 | 0
2025-12-22 | -6.6 | 24.6 | 0 | 2024-12-22 | -15.2 | 33.2 | 0 | 2023-12-22 | -8.5 | 26.5 | 0 | 2022-12-22 | -4.5 | 22.5 | 0 | 2021-12-22 | -7 | 25 | 0 | 2020-12-22 | -4.2 | 22.2 | 0 | 2019-12-22 | 2.4 | 15.6 | 0 | 2018-12-22 | -7.2 | 25.2 | 0 | 2017-12-22 | -11.9 | 29.9 | 0 | 2016-12-22 | 0.1 | 17.9 | 0 | 24.26 | 0
2025-12-22 | -6.6 | 24.6 | 0 | 2024-12-22 | -15.9 | 33.9 | 0 | 2023-12-22 | -9 | 27 | 0 | 2022-12-22 | -4.2 | 22.2 | 0 | 2021-12-22 | -7.8 | 25.8 | 0 | 2020-12-22 | -4.8 | 22.8 | 0 | 2019-12-22 | 1.9 | 16.1 | 0 | 2018-12-22 | -7.8 | 25.8 | 0 | 2017-12-22 | -12 | 30 | 0 | 2016-12-22 | 0.1 | 17.9 | 0 | 24.61 | 0
2025-12-22 | -6.7 | 24.7 | 0 | 2024-12-22 | -16.2 | 34.2 | 0 | 2023-12-22 | -9.8 | 27.8 | 0 | 2022-12-22 | -3.8 | 21.8 | 0 | 2021-12-22 | -8.7 | 26.7 | 0 | 2020-12-22 | -6.5 | 24.5 | 0 | 2019-12-22 | 1.6 | 16.4 | 0 | 2018-12-22 | -8.2 | 26.2 | 0 | 2017-12-22 | -12.6 | 30.6 | 0 | 2016-12-22 | -0.3 | 18.3 | 0 | 25.12 | 0
2025-12-22 | -6.7 | 24.7 | 0 | 2024-12-22 | -17.2 | 35.2 | 0 | 2023-12-22 | -10 | 28 | 0 | 2022-12-22 | -3.2 | 21.2 | 0 | 2021-12-22 | -8.9 | 26.9 | 0 | 2020-12-22 | -7.7 | 25.7 | 0 | 2019-12-22 | 1.2 | 16.8 | 0 | 2018-12-22 | -8.8 | 26.8 | 0 | 2017-12-22 | -12.7 | 30.7 | 0 | 2016-12-22 | -0.6 | 18.6 | 0 | 25.46 | 0
2025-12-22 | -6.7 | 24.7 | 0 | 2024-12-22 | -17.2 | 35.2 | 0 | 2023-12-22 | -9.5 | 27.5 | 0 | 2022-12-22 | -2.5 | 20.5 | 0 | 2021-12-22 | -10.3 | 28.3 | 0 | 2020-12-22 | -8.2 | 26.2 | 0 | 2019-12-22 | 1.1 | 16.9 | 0 | 2018-12-22 | -9 | 27 | 0 | 2017-12-22 | -12.4 | 30.4 | 0 | 2016-12-22 | -0.9 | 18.9 | 0 | 25.56 | 0
2025-12-23 | -7.3 | 25.3 | 0 | 2024-12-23 | -17.5 | 35.5 | 0 | 2023-12-23 | -10.5 | 28.5 | 0 | 2022-12-23 | -1.5 | 19.5 | 0 | 2021-12-23 | -11.1 | 29.1 | 0 | 2020-12-23 | -8.3 | 26.3 | 0 | 2019-12-23 | 0.8 | 17.2 | 0 | 2018-12-23 | -9 | 27 | 0 | 2017-12-23 | -12.1 | 30.1 | 0 | 2016-12-23 | -1.1 | 19.1 | 0 | 25.76 | 0
2025-12-23 | -7.6 | 25.6 | 0 | 2024-12-23 | -18.1 | 36.1 | 0 | 2023-12-23 | -10.7 | 28.7 | 0 | 2022-12-23 | -1.3 | 19.3 | 0 | 2021-12-23 | -12.3 | 30.3 | 0 | 2020-12-23 | -8.3 | 26.3 | 0 | 2019-12-23 | -0.4 | 18.4 | 0 | 2018-12-23 | -9.2 | 27.2 | 0 | 2017-12-23 | -11.8 | 29.8 | 0 | 2016-12-23 | -1.8 | 19.8 | 0 | 26.15 | 0
2025-12-23 | -7.4 | 25.4 | 0 | 2024-12-23 | -17.2 | 35.2 | 0 | 2023-12-23 | -10.4 | 28.4 | 0 | 2022-12-23 | -1.3 | 19.3 | 0 | 2021-12-23 | -13 | 31 | 0 | 2020-12-23 | -8 | 26 | 0 | 2019-12-23 | -0.8 | 18.8 | 0 | 2018-12-23 | -9.6 | 27.6 | 0 | 2017-12-23 | -11.5 | 29.5 | 0 | 2016-12-23 | -1.2 | 19.2 | 0 | 26.04 | 0
2025-12-23 | -7.2 | 25.2 | 0 | 2024-12-23 | -16.3 | 34.3 | 0 | 2023-12-23 | -9.8 | 27.8 | 0 | 2022-12-23 | -0.4 | 18.4 | 0 | 2021-12-23 | -14.3 | 32.3 | 0 | 2020-12-23 | -8.5 | 26.5 | 0 | 2019-12-23 | -0.8 | 18.8 | 0 | 2018-12-23 | -10.4 | 28.4 | 0 | 2017-12-23 | -11.2 | 29.2 | 0 | 2016-12-23 | -0.7 | 18.7 | 0 | 25.96 | 0
2025-12-23 | -7.3 | 25.3 | 0 | 2024-12-23 | -15.5 | 33.5 | 0 | 2023-12-23 | -9.8 | 27.8 | 0 | 2022-12-23 | -0.3 | 18.3 | 0 | 2021-12-23 | -15 | 33 | 0 | 2020-12-23 | -9 | 27 | 0 | 2019-12-23 | -0.9 | 18.9 | 0 | 2018-12-23 | -11.1 | 29.1 | 0 | 2017-12-23 | -11 | 29 | 0 | 2016-12-23 | -0.8 | 18.8 | 0 | 26.07 | 0
2025-12-23 | -7.5 | 25.5 | 0 | 2024-12-23 | -15.2 | 33.2 | 0 | 2023-12-23 | -9.4 | 27.4 | 0 | 2022-12-23 | 0 | 18 | 0 | 2021-12-23 | -15.7 | 33.7 | 0 | 2020-12-23 | -9.6 | 27.6 | 0 | 2019-12-23 | -0.9 | 18.9 | 0 | 2018-12-23 | -11.6 | 29.6 | 0 | 2017-12-23 | -10.8 | 28.8 | 0 | 2016-12-23 | -0.4 | 18.4 | 0 | 26.11 | 0
2025-12-23 | -7 | 25 | 0 | 2024-12-23 | -14.7 | 32.7 | 0 | 2023-12-23 | -8.9 | 26.9 | 0 | 2022-12-23 | 0.2 | 17.8 | 0 | 2021-12-23 | -17.1 | 35.1 | 0 | 2020-12-23 | -10.6 | 28.6 | 0 | 2019-12-23 | 0 | 18 | 0 | 2018-12-23 | -11.7 | 29.7 | 0 | 2017-12-23 | -10.5 | 28.5 | 0 | 2016-12-23 | -1.2 | 19.2 | 0 | 26.15 | 0
2025-12-23 | -6.9 | 24.9 | 0 | 2024-12-23 | -14.7 | 32.7 | 0 | 2023-12-23 | -8.8 | 26.8 | 0 | 2022-12-23 | 0.5 | 17.5 | 0 | 2021-12-23 | -15.2 | 33.2 | 0 | 2020-12-23 | -9.8 | 27.8 | 0 | 2019-12-23 | 0.2 | 17.8 | 0 | 2018-12-23 | -12.2 | 30.2 | 0 | 2017-12-23 | -10.4 | 28.4 | 0 | 2016-12-23 | -1.5 | 19.5 | 0 | 25.88 | 0
2025-12-23 | -6.9 | 24.9 | 0 | 2024-12-23 | -14.6 | 32.6 | 0 | 2023-12-23 | -8.3 | 26.3 | 0 | 2022-12-23 | 0.8 | 17.2 | 0 | 2021-12-23 | -15.1 | 33.1 | 0 | 2020-12-23 | -9.1 | 27.1 | 0 | 2019-12-23 | 0.2 | 17.8 | 0 | 2018-12-23 | -12.6 | 30.6 | 0 | 2017-12-23 | -10.1 | 28.1 | 0 | 2016-12-23 | -1.6 | 19.6 | 0 | 25.73 | 0
2025-12-23 | -6.7 | 24.7 | 0 | 2024-12-23 | -14 | 32 | 0 | 2023-12-23 | -7.8 | 25.8 | 0 | 2022-12-23 | 1 | 17 | 0 | 2021-12-23 | -14.8 | 32.8 | 0 | 2020-12-23 | -7.8 | 25.8 | 0 | 2019-12-23 | 0.9 | 17.1 | 0 | 2018-12-23 | -11.7 | 29.7 | 0 | 2017-12-23 | -9.7 | 27.7 | 0 | 2016-12-23 | -1 | 19 | 0 | 25.16 | 0
2025-12-23 | -6.1 | 24.1 | 0 | 2024-12-23 | -13.3 | 31.3 | 0 | 2023-12-23 | -6.9 | 24.9 | 0 | 2022-12-23 | 1.3 | 16.7 | 0 | 2021-12-23 | -14.3 | 32.3 | 0 | 2020-12-23 | -7 | 25 | 0 | 2019-12-23 | 1.8 | 16.2 | 0 | 2018-12-23 | -11.3 | 29.3 | 0 | 2017-12-23 | -9.2 | 27.2 | 0 | 2016-12-23 | -0.8 | 18.8 | 0 | 24.58 | 0
2025-12-23 | -6 | 24 | 0 | 2024-12-23 | -12.4 | 30.4 | 0 | 2023-12-23 | -5.7 | 23.7 | 0 | 2022-12-23 | 1.8 | 16.2 | 0 | 2021-12-23 | -13.3 | 31.3 | 0 | 2020-12-23 | -6.6 | 24.6 | 0 | 2019-12-23 | 2.8 | 15.2 | 0 | 2018-12-23 | -10.5 | 28.5 | 0 | 2017-12-23 | -8.7 | 26.7 | 0 | 2016-12-23 | -0.2 | 18.2 | 0 | 23.88 | 0
2025-12-23 | -5.7 | 23.7 | 0 | 2024-12-23 | -11.1 | 29.1 | 0 | 2023-12-23 | -4.9 | 22.9 | 0 | 2022-12-23 | 2.4 | 15.6 | 0 | 2021-12-23 | -12.7 | 30.7 | 0 | 2020-12-23 | -6.4 | 24.4 | 0 | 2019-12-23 | 3.8 | 14.2 | 0 | 2018-12-23 | -9.9 | 27.9 | 0 | 2017-12-23 | -8.2 | 26.2 | 0 | 2016-12-23 | 0.4 | 17.6 | 0 | 23.23 | 0
2025-12-23 | -5.8 | 23.8 | 0 | 2024-12-23 | -10.5 | 28.5 | 0 | 2023-12-23 | -4 | 22 | 0 | 2022-12-23 | 1.6 | 16.4 | 0 | 2021-12-23 | -11.9 | 29.9 | 0 | 2020-12-23 | -5.7 | 23.7 | 0 | 2019-12-23 | 4.3 | 13.7 | 0 | 2018-12-23 | -9.2 | 27.2 | 0 | 2017-12-23 | -7.8 | 25.8 | 0 | 2016-12-23 | 0.6 | 17.4 | 0 | 22.84 | 0
2025-12-23 | -6.7 | 24.7 | 0 | 2024-12-23 | -9.9 | 27.9 | 0 | 2023-12-23 | -3.5 | 21.5 | 0 | 2022-12-23 | 1.8 | 16.2 | 0 | 2021-12-23 | -11 | 29 | 0 | 2020-12-23 | -5.2 | 23.2 | 0 | 2019-12-23 | 4.4 | 13.6 | 0 | 2018-12-23 | -8.9 | 26.9 | 0 | 2017-12-23 | -7.2 | 25.2 | 0 | 2016-12-23 | 1.3 | 16.7 | 0 | 22.49 | 0
2025-12-23 | -7.2 | 25.2 | 0 | 2024-12-23 | -9.8 | 27.8 | 0 | 2023-12-23 | -3.4 | 21.4 | 0 | 2022-12-23 | -1.2 | 19.2 | 0 | 2021-12-23 | -10.9 | 28.9 | 0 | 2020-12-23 | -4.9 | 22.9 | 0 | 2019-12-23 | 4 | 14 | 0 | 2018-12-23 | -8.7 | 26.7 | 0 | 2017-12-23 | -7.2 | 25.2 | 0 | 2016-12-23 | 1.2 | 16.8 | 0 | 22.81 | 0
2025-12-23 | -7.4 | 25.4 | 0 | 2024-12-23 | -10.2 | 28.2 | 0 | 2023-12-23 | -3.3 | 21.3 | 0 | 2022-12-23 | -3.7 | 21.7 | 0 | 2021-12-23 | -11.6 | 29.6 | 0 | 2020-12-23 | -5.2 | 23.2 | 0 | 2019-12-23 | 3.7 | 14.3 | 0 | 2018-12-23 | -8.9 | 26.9 | 0 | 2017-12-23 | -7.5 | 25.5 | 0 | 2016-12-23 | 0.5 | 17.5 | 0 | 23.36 | 0
2025-12-23 | -7.4 | 25.4 | 0 | 2024-12-23 | -10.1 | 28.1 | 0 | 2023-12-23 | -3.3 | 21.3 | 0 | 2022-12-23 | -5.7 | 23.7 | 0 | 2021-12-23 | -12.2 | 30.2 | 0 | 2020-12-23 | -5 | 23 | 0 | 2019-12-23 | 3.5 | 14.5 | 0 | 2018-12-23 | -9.6 | 27.6 | 0 | 2017-12-23 | -7.4 | 25.4 | 0 | 2016-12-23 | 0.4 | 17.6 | 0 | 23.68 | 0
2025-12-23 | -7.5 | 25.5 | 0 | 2024-12-23 | -10.2 | 28.2 | 0 | 2023-12-23 | -3.2 | 21.2 | 0 | 2022-12-23 | -7.2 | 25.2 | 0 | 2021-12-23 | -14 | 32 | 0 | 2020-12-23 | -4.8 | 22.8 | 0 | 2019-12-23 | 3 | 15 | 0 | 2018-12-23 | -10.4 | 28.4 | 0 | 2017-12-23 | -7.5 | 25.5 | 0 | 2016-12-23 | 1.2 | 16.8 | 0 | 24.06 | 0
2025-12-23 | -7.5 | 25.5 | 0 | 2024-12-23 | -9.9 | 27.9 | 0 | 2023-12-23 | -3.1 | 21.1 | 0 | 2022-12-23 | -8.4 | 26.4 | 0 | 2021-12-23 | -14.1 | 32.1 | 0 | 2020-12-23 | -4.7 | 22.7 | 0 | 2019-12-23 | 2.8 | 15.2 | 0 | 2018-12-23 | -11.4 | 29.4 | 0 | 2017-12-23 | -8.3 | 26.3 | 0 | 2016-12-23 | 1.2 | 16.8 | 0 | 24.34 | 0
2025-12-23 | -7.5 | 25.5 | 0 | 2024-12-23 | -9.8 | 27.8 | 0 | 2023-12-23 | -3.2 | 21.2 | 0 | 2022-12-23 | -9.5 | 27.5 | 0 | 2021-12-23 | -13.3 | 31.3 | 0 | 2020-12-23 | -5 | 23 | 0 | 2019-12-23 | 2 | 16 | 0 | 2018-12-23 | -9.3 | 27.3 | 0 | 2017-12-23 | -9.9 | 27.9 | 0 | 2016-12-23 | 1.3 | 16.7 | 0 | 24.42 | 0
2025-12-23 | -7.5 | 25.5 | 0 | 2024-12-23 | -9.8 | 27.8 | 0 | 2023-12-23 | -3.2 | 21.2 | 0 | 2022-12-23 | -10.1 | 28.1 | 0 | 2021-12-23 | -14 | 32 | 0 | 2020-12-23 | -5.5 | 23.5 | 0 | 2019-12-23 | 2 | 16 | 0 | 2018-12-23 | -9.4 | 27.4 | 0 | 2017-12-23 | -8.5 | 26.5 | 0 | 2016-12-23 | 1.3 | 16.7 | 0 | 24.47 | 0
2025-12-23 | -7.7 | 25.7 | 0 | 2024-12-23 | -9.7 | 27.7 | 0 | 2023-12-23 | -3.2 | 21.2 | 0 | 2022-12-23 | -10.4 | 28.4 | 0 | 2021-12-23 | -15.9 | 33.9 | 0 | 2020-12-23 | -5.1 | 23.1 | 0 | 2019-12-23 | 1 | 17 | 0 | 2018-12-23 | -9.2 | 27.2 | 0 | 2017-12-23 | -8.6 | 26.6 | 0 | 2016-12-23 | 0.9 | 17.1 | 0 | 24.79 | 0
2025-12-23 | -7.8 | 25.8 | 0 | 2024-12-23 | -9.8 | 27.8 | 0 | 2023-12-23 | -3.3 | 21.3 | 0 | 2022-12-23 | -10.3 | 28.3 | 0 | 2021-12-23 | -14 | 32 | 0 | 2020-12-23 | -3.7 | 21.7 | 0 | 2019-12-23 | 0.4 | 17.6 | 0 | 2018-12-23 | -8.8 | 26.8 | 0 | 2017-12-23 | -8.3 | 26.3 | 0 | 2016-12-23 | 0.7 | 17.3 | 0 | 24.49 | 0
2025-12-24 | -7.5 | 25.5 | 0 | 2024-12-24 | -9.5 | 27.5 | 0 | 2023-12-24 | -3.2 | 21.2 | 0 | 2022-12-24 | -10.3 | 28.3 | 0 | 2021-12-24 | -13.8 | 31.8 | 0 | 2020-12-24 | -3.4 | 21.4 | 0 | 2019-12-24 | -0.2 | 18.2 | 0 | 2018-12-24 | -9.4 | 27.4 | 0 | 2017-12-24 | -9.3 | 27.3 | 0 | 2016-12-24 | 0.6 | 17.4 | 0 | 24.6 | 0
2025-12-24 | -7.3 | 25.3 | 0 | 2024-12-24 | -9.3 | 27.3 | 0 | 2023-12-24 | -3.1 | 21.1 | 0 | 2022-12-24 | -10.3 | 28.3 | 0 | 2021-12-24 | -13.6 | 31.6 | 0 | 2020-12-24 | -3 | 21 | 0 | 2019-12-24 | -0.9 | 18.9 | 0 | 2018-12-24 | -9.7 | 27.7 | 0 | 2017-12-24 | -10.4 | 28.4 | 0 | 2016-12-24 | 1 | 17 | 0 | 24.66 | 0
2025-12-24 | -7 | 25 | 0 | 2024-12-24 | -9.2 | 27.2 | 0 | 2023-12-24 | -2.9 | 20.9 | 0 | 2022-12-24 | -10.4 | 28.4 | 0 | 2021-12-24 | -13.3 | 31.3 | 0 | 2020-12-24 | -2.7 | 20.7 | 0 | 2019-12-24 | -1.5 | 19.5 | 0 | 2018-12-24 | -9.6 | 27.6 | 0 | 2017-12-24 | -9.5 | 27.5 | 0 | 2016-12-24 | 1.2 | 16.8 | 0 | 24.49 | 0
2025-12-24 | -7 | 25 | 0 | 2024-12-24 | -9 | 27 | 0 | 2023-12-24 | -2.6 | 20.6 | 0 | 2022-12-24 | -10.5 | 28.5 | 0 | 2021-12-24 | -14.6 | 32.6 | 0 | 2020-12-24 | -1.8 | 19.8 | 0 | 2019-12-24 | -1.9 | 19.9 | 0 | 2018-12-24 | -9.2 | 27.2 | 0 | 2017-12-24 | -9.9 | 27.9 | 0 | 2016-12-24 | -0.1 | 18.1 | 0 | 24.66 | 0
2025-12-24 | -4.7 | 22.7 | 0 | 2024-12-24 | -8.9 | 26.9 | 0 | 2023-12-24 | -2.5 | 20.5 | 0 | 2022-12-24 | -10.5 | 28.5 | 0 | 2021-12-24 | -15.4 | 33.4 | 0 | 2020-12-24 | -1.8 | 19.8 | 0 | 2019-12-24 | -2.8 | 20.8 | 0 | 2018-12-24 | -9.2 | 27.2 | 0 | 2017-12-24 | -14.7 | 32.7 | 0 | 2016-12-24 | 0.2 | 17.8 | 0 | 25.03 | 0
2025-12-24 | -3.9 | 21.9 | 0 | 2024-12-24 | -8.8 | 26.8 | 0 | 2023-12-24 | -2.3 | 20.3 | 0 | 2022-12-24 | -10.1 | 28.1 | 0 | 2021-12-24 | -15 | 33 | 0 | 2020-12-24 | -2.2 | 20.2 | 0 | 2019-12-24 | -3.5 | 21.5 | 0 | 2018-12-24 | -9.2 | 27.2 | 0 | 2017-12-24 | -12 | 30 | 0 | 2016-12-24 | -0.4 | 18.4 | 0 | 24.74 | 0
2025-12-24 | -3.5 | 21.5 | 0 | 2024-12-24 | -8.8 | 26.8 | 0 | 2023-12-24 | -1.9 | 19.9 | 0 | 2022-12-24 | -10.1 | 28.1 | 0 | 2021-12-24 | -15.6 | 33.6 | 0 | 2020-12-24 | -2.1 | 20.1 | 0 | 2019-12-24 | -4 | 22 | 0 | 2018-12-24 | -9.3 | 27.3 | 0 | 2017-12-24 | -13.4 | 31.4 | 0 | 2016-12-24 | 0.1 | 17.9 | 0 | 24.86 | 0
2025-12-24 | -4.5 | 22.5 | 0 | 2024-12-24 | -9.5 | 27.5 | 0 | 2023-12-24 | -1.8 | 19.8 | 0 | 2022-12-24 | -9.7 | 27.7 | 0 | 2021-12-24 | -15.9 | 33.9 | 0 | 2020-12-24 | -1.7 | 19.7 | 0 | 2019-12-24 | -4.7 | 22.7 | 0 | 2018-12-24 | -9.2 | 27.2 | 0 | 2017-12-24 | -10.2 | 28.2 | 0 | 2016-12-24 | 0.3 | 17.7 | 0 | 24.69 | 0
2025-12-24 | -5.2 | 23.2 | 0 | 2024-12-24 | -9.8 | 27.8 | 0 | 2023-12-24 | -1.7 | 19.7 | 0 | 2022-12-24 | -9.4 | 27.4 | 0 | 2021-12-24 | -15.4 | 33.4 | 0 | 2020-12-24 | -1.1 | 19.1 | 0 | 2019-12-24 | -5.3 | 23.3 | 0 | 2018-12-24 | -9.1 | 27.1 | 0 | 2017-12-24 | -11.3 | 29.3 | 0 | 2016-12-24 | 0.4 | 17.6 | 0 | 24.79 | 0
2025-12-24 | -5.6 | 23.6 | 0 | 2024-12-24 | -8.1 | 26.1 | 0 | 2023-12-24 | -1.4 | 19.4 | 0 | 2022-12-24 | -9 | 27 | 0 | 2021-12-24 | -13.6 | 31.6 | 0 | 2020-12-24 | 0.2 | 17.8 | 0 | 2019-12-24 | -5.1 | 23.1 | 0 | 2018-12-24 | -8.7 | 26.7 | 0 | 2017-12-24 | -11.7 | 29.7 | 0 | 2016-12-24 | 0.5 | 17.5 | 0 | 24.25 | 0
2025-12-24 | -5.9 | 23.9 | 0 | 2024-12-24 | -7.3 | 25.3 | 0 | 2023-12-24 | -1 | 19 | 0 | 2022-12-24 | -8.8 | 26.8 | 0 | 2021-12-24 | -12.2 | 30.2 | 0 | 2020-12-24 | 1.5 | 16.5 | 0 | 2019-12-24 | -4.4 | 22.4 | 0 | 2018-12-24 | -8.8 | 26.8 | 0 | 2017-12-24 | -10.9 | 28.9 | 0 | 2016-12-24 | 0.8 | 17.2 | 0 | 23.7 | 0
2025-12-24 | -6.4 | 24.4 | 0 | 2024-12-24 | -7 | 25 | 0 | 2023-12-24 | -0.3 | 18.3 | 0 | 2022-12-24 | -8.6 | 26.6 | 0 | 2021-12-24 | -10.4 | 28.4 | 0 | 2020-12-24 | 7.1 | 10.9 | 0 | 2019-12-24 | -4.2 | 22.2 | 0 | 2018-12-24 | -8.4 | 26.4 | 0 | 2017-12-24 | -10.4 | 28.4 | 0 | 2016-12-24 | 1.6 | 16.4 | 0 | 22.7 | 0
2025-12-24 | -6.5 | 24.5 | 0 | 2024-12-24 | -7 | 25 | 0 | 2023-12-24 | -0.1 | 18.1 | 0 | 2022-12-24 | -9.2 | 27.2 | 0 | 2021-12-24 | -8.3 | 26.3 | 0 | 2020-12-24 | 7.8 | 10.2 | 0 | 2019-12-24 | -3.6 | 21.6 | 0 | 2018-12-24 | -8 | 26 | 0 | 2017-12-24 | -8.5 | 26.5 | 0 | 2016-12-24 | 2.6 | 15.4 | 0 | 22.08 | 0
2025-12-24 | -6.8 | 24.8 | 0 | 2024-12-24 | -6.3 | 24.3 | 0 | 2023-12-24 | 0.3 | 17.7 | 0 | 2022-12-24 | -8.5 | 26.5 | 0 | 2021-12-24 | -6.6 | 24.6 | 0 | 2020-12-24 | 8.1 | 9.9 | 0 | 2019-12-24 | -3.5 | 21.5 | 0 | 2018-12-24 | -7.7 | 25.7 | 0 | 2017-12-24 | -7.1 | 25.1 | 0 | 2016-12-24 | 3.2 | 14.8 | 0 | 21.49 | 0
2025-12-24 | -6.6 | 24.6 | 0 | 2024-12-24 | -5.7 | 23.7 | 0 | 2023-12-24 | 0.5 | 17.5 | 0 | 2022-12-24 | -8.3 | 26.3 | 0 | 2021-12-24 | -6.3 | 24.3 | 0 | 2020-12-24 | 8.2 | 9.8 | 0 | 2019-12-24 | -3.4 | 21.4 | 0 | 2018-12-24 | -7.2 | 25.2 | 0 | 2017-12-24 | -7 | 25 | 0 | 2016-12-24 | 3.6 | 14.4 | 0 | 21.22 | 0
2025-12-24 | -6.9 | 24.9 | 0 | 2024-12-24 | -5.4 | 23.4 | 0 | 2023-12-24 | 0.4 | 17.6 | 0 | 2022-12-24 | -8.1 | 26.1 | 0 | 2021-12-24 | -6 | 24 | 0 | 2020-12-24 | 8.3 | 9.7 | 0 | 2019-12-24 | -3.5 | 21.5 | 0 | 2018-12-24 | -6.9 | 24.9 | 0 | 2017-12-24 | -8.8 | 26.8 | 0 | 2016-12-24 | 3.2 | 14.8 | 0 | 21.37 | 0
2025-12-24 | -7.2 | 25.2 | 0 | 2024-12-24 | -6.9 | 24.9 | 0 | 2023-12-24 | 0.3 | 17.7 | 0 | 2022-12-24 | -7.8 | 25.8 | 0 | 2021-12-24 | -6.1 | 24.1 | 0 | 2020-12-24 | 8.4 | 9.6 | 0 | 2019-12-24 | -3.6 | 21.6 | 0 | 2018-12-24 | -7.5 | 25.5 | 0 | 2017-12-24 | -8.7 | 26.7 | 0 | 2016-12-24 | 2.8 | 15.2 | 0 | 21.63 | 0
2025-12-24 | -8.3 | 26.3 | 0 | 2024-12-24 | -6.6 | 24.6 | 0 | 2023-12-24 | 0.2 | 17.8 | 0 | 2022-12-24 | -7.6 | 25.6 | 0 | 2021-12-24 | -6.5 | 24.5 | 0 | 2020-12-24 | 8.5 | 9.5 | 0 | 2019-12-24 | -3.6 | 21.6 | 0 | 2018-12-24 | -8 | 26 | 0 | 2017-12-24 | -9.9 | 27.9 | 0 | 2016-12-24 | 2.5 | 15.5 | 0 | 21.93 | 0
2025-12-24 | -8.2 | 26.2 | 0 | 2024-12-24 | -8.6 | 26.6 | 0 | 2023-12-24 | 0.1 | 17.9 | 0 | 2022-12-24 | -7.4 | 25.4 | 0 | 2021-12-24 | -6.6 | 24.6 | 0 | 2020-12-24 | 8.6 | 9.4 | 0 | 2019-12-24 | -4.3 | 22.3 | 0 | 2018-12-24 | -8.5 | 26.5 | 0 | 2017-12-24 | -9.4 | 27.4 | 0 | 2016-12-24 | 2.3 | 15.7 | 0 | 22.2 | 0
2025-12-24 | -8.2 | 26.2 | 0 | 2024-12-24 | -9.9 | 27.9 | 0 | 2023-12-24 | 0.1 | 17.9 | 0 | 2022-12-24 | -7.5 | 25.5 | 0 | 2021-12-24 | -6.7 | 24.7 | 0 | 2020-12-24 | 8.8 | 9.2 | 0 | 2019-12-24 | -4.4 | 22.4 | 0 | 2018-12-24 | -9.4 | 27.4 | 0 | 2017-12-24 | -9.8 | 27.8 | 0 | 2016-12-24 | 2.5 | 15.5 | 0 | 22.45 | 0
2025-12-24 | -8.1 | 26.1 | 0 | 2024-12-24 | -8.4 | 26.4 | 0 | 2023-12-24 | 0 | 18 | 0 | 2022-12-24 | -7.5 | 25.5 | 0 | 2021-12-24 | -6.7 | 24.7 | 0 | 2020-12-24 | 8.4 | 9.6 | 0 | 2019-12-24 | -4.4 | 22.4 | 0 | 2018-12-24 | -9.9 | 27.9 | 0 | 2017-12-24 | -9.3 | 27.3 | 0 | 2016-12-24 | 2.4 | 15.6 | 0 | 22.35 | 0
2025-12-24 | -8.3 | 26.3 | 0 | 2024-12-24 | -8.2 | 26.2 | 0 | 2023-12-24 | 0 | 18 | 0 | 2022-12-24 | -7.3 | 25.3 | 0 | 2021-12-24 | -7.1 | 25.1 | 0 | 2020-12-24 | 7.5 | 10.5 | 0 | 2019-12-24 | -5.2 | 23.2 | 0 | 2018-12-24 | -10 | 28 | 0 | 2017-12-24 | -9 | 27 | 0 | 2016-12-24 | 2.3 | 15.7 | 0 | 22.53 | 0
2025-12-24 | -8.1 | 26.1 | 0 | 2024-12-24 | -8 | 26 | 0 | 2023-12-24 | -0.1 | 18.1 | 0 | 2022-12-24 | -7.5 | 25.5 | 0 | 2021-12-24 | -7.4 | 25.4 | 0 | 2020-12-24 | 7 | 11 | 0 | 2019-12-24 | -5 | 23 | 0 | 2018-12-24 | -10.8 | 28.8 | 0 | 2017-12-24 | -8.7 | 26.7 | 0 | 2016-12-24 | 2.2 | 15.8 | 0 | 22.64 | 0
2025-12-24 | -8 | 26 | 0 | 2024-12-24 | -8.3 | 26.3 | 0 | 2023-12-24 | 0 | 18 | 0 | 2022-12-24 | -7.8 | 25.8 | 0 | 2021-12-24 | -7.3 | 25.3 | 0 | 2020-12-24 | 6.6 | 11.4 | 0 | 2019-12-24 | -5.2 | 23.2 | 0 | 2018-12-24 | -11.8 | 29.8 | 0 | 2017-12-24 | -8.4 | 26.4 | 0 | 2016-12-24 | 2.3 | 15.7 | 0 | 22.79 | 0
2025-12-25 | -7.3 | 25.3 | 0 | 2024-12-25 | -8.7 | 26.7 | 0 | 2023-12-25 | 0.1 | 17.9 | 0 | 2022-12-25 | -7.7 | 25.7 | 0 | 2021-12-25 | -7.3 | 25.3 | 0 | 2020-12-25 | 5.9 | 12.1 | 0 | 2019-12-25 | -5.3 | 23.3 | 0 | 2018-12-25 | -12.6 | 30.6 | 0 | 2017-12-25 | -8.3 | 26.3 | 0 | 2016-12-25 | 2 | 16 | 0 | 22.92 | 0
2025-12-25 | -6.9 | 24.9 | 0 | 2024-12-25 | -8.9 | 26.9 | 0 | 2023-12-25 | 0.1 | 17.9 | 0 | 2022-12-25 | -7.3 | 25.3 | 0 | 2021-12-25 | -7.8 | 25.8 | 0 | 2020-12-25 | 5.7 | 12.3 | 0 | 2019-12-25 | -5.4 | 23.4 | 0 | 2018-12-25 | -14.5 | 32.5 | 0 | 2017-12-25 | -8 | 26 | 0 | 2016-12-25 | 1.9 | 16.1 | 0 | 23.11 | 0
2025-12-25 | -7 | 25 | 0 | 2024-12-25 | -8.8 | 26.8 | 0 | 2023-12-25 | 0.1 | 17.9 | 0 | 2022-12-25 | -7.6 | 25.6 | 0 | 2021-12-25 | -7.7 | 25.7 | 0 | 2020-12-25 | 5.1 | 12.9 | 0 | 2019-12-25 | -5.6 | 23.6 | 0 | 2018-12-25 | -14.3 | 32.3 | 0 | 2017-12-25 | -7.9 | 25.9 | 0 | 2016-12-25 | 0.5 | 17.5 | 0 | 23.32 | 0
2025-12-25 | -6.6 | 24.6 | 0 | 2024-12-25 | -9.3 | 27.3 | 0 | 2023-12-25 | 0 | 18 | 0 | 2022-12-25 | -7.1 | 25.1 | 0 | 2021-12-25 | -7.4 | 25.4 | 0 | 2020-12-25 | 5.3 | 12.7 | 0 | 2019-12-25 | -5.7 | 23.7 | 0 | 2018-12-25 | -15.3 | 33.3 | 0 | 2017-12-25 | -8.8 | 26.8 | 0 | 2016-12-25 | -0.4 | 18.4 | 0 | 23.53 | 0
2025-12-25 | -6.3 | 24.3 | 0 | 2024-12-25 | -9.6 | 27.6 | 0 | 2023-12-25 | 0 | 18 | 0 | 2022-12-25 | -7.2 | 25.2 | 0 | 2021-12-25 | -6.8 | 24.8 | 0 | 2020-12-25 | 5.5 | 12.5 | 0 | 2019-12-25 | -5.4 | 23.4 | 0 | 2018-12-25 | -16 | 34 | 0 | 2017-12-25 | -9 | 27 | 0 | 2016-12-25 | -2 | 20 | 0 | 23.68 | 0
2025-12-25 | -6.1 | 24.1 | 0 | 2024-12-25 | -9.8 | 27.8 | 0 | 2023-12-25 | -0.1 | 18.1 | 0 | 2022-12-25 | -6.8 | 24.8 | 0 | 2021-12-25 | -6.7 | 24.7 | 0 | 2020-12-25 | 5.8 | 12.2 | 0 | 2019-12-25 | -5.4 | 23.4 | 0 | 2018-12-25 | -16.8 | 34.8 | 0 | 2017-12-25 | -9.1 | 27.1 | 0 | 2016-12-25 | -2.9 | 20.9 | 0 | 23.79 | 0
2025-12-25 | -5.3 | 23.3 | 0 | 2024-12-25 | -9.4 | 27.4 | 0 | 2023-12-25 | -0.2 | 18.2 | 0 | 2022-12-25 | -7.2 | 25.2 | 0 | 2021-12-25 | -6.8 | 24.8 | 0 | 2020-12-25 | 5.5 | 12.5 | 0 | 2019-12-25 | -5.2 | 23.2 | 0 | 2018-12-25 | -16.7 | 34.7 | 0 | 2017-12-25 | -9.3 | 27.3 | 0 | 2016-12-25 | -4 | 22 | 0 | 23.86 | 0
2025-12-25 | -5.8 | 23.8 | 0 | 2024-12-25 | -9.3 | 27.3 | 0 | 2023-12-25 | 0 | 18 | 0 | 2022-12-25 | -7.4 | 25.4 | 0 | 2021-12-25 | -6.8 | 24.8 | 0 | 2020-12-25 | 4.8 | 13.2 | 0 | 2019-12-25 | -5.2 | 23.2 | 0 | 2018-12-25 | -17.7 | 35.7 | 0 | 2017-12-25 | -9.4 | 27.4 | 0 | 2016-12-25 | -5.4 | 23.4 | 0 | 24.22 | 0
2025-12-25 | -5.6 | 23.6 | 0 | 2024-12-25 | -9.8 | 27.8 | 0 | 2023-12-25 | 0.1 | 17.9 | 0 | 2022-12-25 | -7.3 | 25.3 | 0 | 2021-12-25 | -6.8 | 24.8 | 0 | 2020-12-25 | 4.8 | 13.2 | 0 | 2019-12-25 | -5.3 | 23.3 | 0 | 2018-12-25 | -17.6 | 35.6 | 0 | 2017-12-25 | -9.4 | 27.4 | 0 | 2016-12-25 | -5.9 | 23.9 | 0 | 24.28 | 0
2025-12-25 | -5 | 23 | 0 | 2024-12-25 | -9.7 | 27.7 | 0 | 2023-12-25 | 0.2 | 17.8 | 0 | 2022-12-25 | -6.9 | 24.9 | 0 | 2021-12-25 | -6.9 | 24.9 | 0 | 2020-12-25 | 5 | 13 | 0 | 2019-12-25 | -4.9 | 22.9 | 0 | 2018-12-25 | -16.3 | 34.3 | 0 | 2017-12-25 | -8.8 | 26.8 | 0 | 2016-12-25 | -6.4 | 24.4 | 0 | 23.97 | 0
2025-12-25 | -5.2 | 23.2 | 0 | 2024-12-25 | -9.6 | 27.6 | 0 | 2023-12-25 | 0.6 | 17.4 | 0 | 2022-12-25 | -6.2 | 24.2 | 0 | 2021-12-25 | -7 | 25 | 0 | 2020-12-25 | 4.6 | 13.4 | 0 | 2019-12-25 | -4.4 | 22.4 | 0 | 2018-12-25 | -15.2 | 33.2 | 0 | 2017-12-25 | -8.2 | 26.2 | 0 | 2016-12-25 | -6.5 | 24.5 | 0 | 23.71 | 0
2025-12-25 | -6.5 | 24.5 | 0 | 2024-12-25 | -8.8 | 26.8 | 0 | 2023-12-25 | 1 | 17 | 0 | 2022-12-25 | -6.1 | 24.1 | 0 | 2021-12-25 | -6.5 | 24.5 | 0 | 2020-12-25 | 4.6 | 13.4 | 0 | 2019-12-25 | -3.7 | 21.7 | 0 | 2018-12-25 | -14.4 | 32.4 | 0 | 2017-12-25 | -7.3 | 25.3 | 0 | 2016-12-25 | -5.9 | 23.9 | 0 | 23.36 | 0
2025-12-25 | -6.9 | 24.9 | 0 | 2024-12-25 | -7.8 | 25.8 | 0 | 2023-12-25 | 1.4 | 16.6 | 0 | 2022-12-25 | -5.9 | 23.9 | 0 | 2021-12-25 | -6 | 24 | 0 | 2020-12-25 | 4.5 | 13.5 | 0 | 2019-12-25 | -3.2 | 21.2 | 0 | 2018-12-25 | -13.2 | 31.2 | 0 | 2017-12-25 | -7.2 | 25.2 | 0 | 2016-12-25 | -5.7 | 23.7 | 0 | 23 | 0
2025-12-25 | -7.3 | 25.3 | 0 | 2024-12-25 | -8 | 26 | 0 | 2023-12-25 | 1.6 | 16.4 | 0 | 2022-12-25 | -5.2 | 23.2 | 0 | 2021-12-25 | -5.5 | 23.5 | 0 | 2020-12-25 | 3.9 | 14.1 | 0 | 2019-12-25 | -2.5 | 20.5 | 0 | 2018-12-25 | -12.3 | 30.3 | 0 | 2017-12-25 | -6.8 | 24.8 | 0 | 2016-12-25 | -5.6 | 23.6 | 0 | 22.77 | 0
2025-12-25 | -8 | 26 | 0 | 2024-12-25 | -6.5 | 24.5 | 0 | 2023-12-25 | 2 | 16 | 0 | 2022-12-25 | -5.1 | 23.1 | 0 | 2021-12-25 | -5.5 | 23.5 | 0 | 2020-12-25 | 2.6 | 15.4 | 0 | 2019-12-25 | -2.9 | 20.9 | 0 | 2018-12-25 | -11.8 | 29.8 | 0 | 2017-12-25 | -6.8 | 24.8 | 0 | 2016-12-25 | -5.3 | 23.3 | 0 | 22.73 | 0
2025-12-25 | -8.5 | 26.5 | 0 | 2024-12-25 | -7.3 | 25.3 | 0 | 2023-12-25 | 1.8 | 16.2 | 0 | 2022-12-25 | -5.1 | 23.1 | 0 | 2021-12-25 | -5.4 | 23.4 | 0 | 2020-12-25 | 1.5 | 16.5 | 0 | 2019-12-25 | -3.2 | 21.2 | 0 | 2018-12-25 | -11.8 | 29.8 | 0 | 2017-12-25 | -6.5 | 24.5 | 0 | 2016-12-25 | -5.5 | 23.5 | 0 | 23 | 0
2025-12-25 | -9.7 | 27.7 | 0 | 2024-12-25 | -7.2 | 25.2 | 0 | 2023-12-25 | 1.6 | 16.4 | 0 | 2022-12-25 | -4.8 | 22.8 | 0 | 2021-12-25 | -5 | 23 | 0 | 2020-12-25 | 1.1 | 16.9 | 0 | 2019-12-25 | -3.2 | 21.2 | 0 | 2018-12-25 | -12.5 | 30.5 | 0 | 2017-12-25 | -6.7 | 24.7 | 0 | 2016-12-25 | -5.8 | 23.8 | 0 | 23.22 | 0
2025-12-25 | -11.3 | 29.3 | 0 | 2024-12-25 | -7.8 | 25.8 | 0 | 2023-12-25 | 1.4 | 16.6 | 0 | 2022-12-25 | -5.7 | 23.7 | 0 | 2021-12-25 | -4.8 | 22.8 | 0 | 2020-12-25 | 0.9 | 17.1 | 0 | 2019-12-25 | -3.1 | 21.1 | 0 | 2018-12-25 | -12.9 | 30.9 | 0 | 2017-12-25 | -7.5 | 25.5 | 0 | 2016-12-25 | -6.4 | 24.4 | 0 | 23.72 | 0
2025-12-25 | -11.8 | 29.8 | 0 | 2024-12-25 | -8.8 | 26.8 | 0 | 2023-12-25 | 1.3 | 16.7 | 0 | 2022-12-25 | -5.5 | 23.5 | 0 | 2021-12-25 | -4.4 | 22.4 | 0 | 2020-12-25 | 0.4 | 17.6 | 0 | 2019-12-25 | -3.2 | 21.2 | 0 | 2018-12-25 | -14.1 | 32.1 | 0 | 2017-12-25 | -8.4 | 26.4 | 0 | 2016-12-25 | -7.4 | 25.4 | 0 | 24.19 | 0
2025-12-25 | -12.8 | 30.8 | 0 | 2024-12-25 | -8.8 | 26.8 | 0 | 2023-12-25 | 1.3 | 16.7 | 0 | 2022-12-25 | -6.2 | 24.2 | 0 | 2021-12-25 | -4.2 | 22.2 | 0 | 2020-12-25 | 0.1 | 17.9 | 0 | 2019-12-25 | -3.1 | 21.1 | 0 | 2018-12-25 | -14.3 | 32.3 | 0 | 2017-12-25 | -8.5 | 26.5 | 0 | 2016-12-25 | -8.1 | 26.1 | 0 | 24.46 | 0
2025-12-25 | -13.8 | 31.8 | 0 | 2024-12-25 | -8.4 | 26.4 | 0 | 2023-12-25 | 1.3 | 16.7 | 0 | 2022-12-25 | -5.6 | 23.6 | 0 | 2021-12-25 | -4.2 | 22.2 | 0 | 2020-12-25 | -0.3 | 18.3 | 0 | 2019-12-25 | -3.3 | 21.3 | 0 | 2018-12-25 | -15.2 | 33.2 | 0 | 2017-12-25 | -7.6 | 25.6 | 0 | 2016-12-25 | -9.2 | 27.2 | 0 | 24.63 | 0
2025-12-25 | -14.9 | 32.9 | 0 | 2024-12-25 | -8.2 | 26.2 | 0 | 2023-12-25 | 1.3 | 16.7 | 0 | 2022-12-25 | -5.9 | 23.9 | 0 | 2021-12-25 | -4 | 22 | 0 | 2020-12-25 | -1.7 | 19.7 | 0 | 2019-12-25 | -3.7 | 21.7 | 0 | 2018-12-25 | -15.3 | 33.3 | 0 | 2017-12-25 | -6.7 | 24.7 | 0 | 2016-12-25 | -10.3 | 28.3 | 0 | 24.94 | 0
2025-12-25 | -15.2 | 33.2 | 0 | 2024-12-25 | -8.2 | 26.2 | 0 | 2023-12-25 | 1.4 | 16.6 | 0 | 2022-12-25 | -6.2 | 24.2 | 0 | 2021-12-25 | -3.9 | 21.9 | 0 | 2020-12-25 | -3.1 | 21.1 | 0 | 2019-12-25 | -4.1 | 22.1 | 0 | 2018-12-25 | -15.1 | 33.1 | 0 | 2017-12-25 | -7.1 | 25.1 | 0 | 2016-12-25 | -11.1 | 29.1 | 0 | 25.26 | 0
2025-12-25 | -15.8 | 33.8 | 0 | 2024-12-25 | -9 | 27 | 0 | 2023-12-25 | 1.4 | 16.6 | 0 | 2022-12-25 | -7.9 | 25.9 | 0 | 2021-12-25 | -3.2 | 21.2 | 0 | 2020-12-25 | -3.2 | 21.2 | 0 | 2019-12-25 | -4.3 | 22.3 | 0 | 2018-12-25 | -14.5 | 32.5 | 0 | 2017-12-25 | -7.7 | 25.7 | 0 | 2016-12-25 | -11.8 | 29.8 | 0 | 25.6 | 0
2025-12-26 | -16.5 | 34.5 | 0 | 2024-12-26 | -8.8 | 26.8 | 0 | 2023-12-26 | 1.7 | 16.3 | 0 | 2022-12-26 | -8.5 | 26.5 | 0 | 2021-12-26 | -3 | 21 | 0 | 2020-12-26 | -3.3 | 21.3 | 0 | 2019-12-26 | -4.2 | 22.2 | 0 | 2018-12-26 | -14.9 | 32.9 | 0 | 2017-12-26 | -8.6 | 26.6 | 0 | 2016-12-26 | -11.8 | 29.8 | 0 | 25.79 | 0
2025-12-26 | -16.9 | 34.9 | 0 | 2024-12-26 | -8.6 | 26.6 | 0 | 2023-12-26 | 1.6 | 16.4 | 0 | 2022-12-26 | -8.8 | 26.8 | 0 | 2021-12-26 | -2.8 | 20.8 | 0 | 2020-12-26 | -3.2 | 21.2 | 0 | 2019-12-26 | -4.5 | 22.5 | 0 | 2018-12-26 | -15.9 | 33.9 | 0 | 2017-12-26 | -8.7 | 26.7 | 0 | 2016-12-26 | -11.8 | 29.8 | 0 | 25.96 | 0
2025-12-26 | -17.6 | 35.6 | 0 | 2024-12-26 | -9.2 | 27.2 | 0 | 2023-12-26 | 1.6 | 16.4 | 0 | 2022-12-26 | -8.7 | 26.7 | 0 | 2021-12-26 | -2.5 | 20.5 | 0 | 2020-12-26 | -3 | 21 | 0 | 2019-12-26 | -4.9 | 22.9 | 0 | 2018-12-26 | -16.1 | 34.1 | 0 | 2017-12-26 | -9.2 | 27.2 | 0 | 2016-12-26 | -10.9 | 28.9 | 0 | 26.05 | 0
2025-12-26 | -18.4 | 36.4 | 0 | 2024-12-26 | -9.5 | 27.5 | 0 | 2023-12-26 | 1.6 | 16.4 | 0 | 2022-12-26 | -8.5 | 26.5 | 0 | 2021-12-26 | -2.5 | 20.5 | 0 | 2020-12-26 | -2.6 | 20.6 | 0 | 2019-12-26 | -5.4 | 23.4 | 0 | 2018-12-26 | -16.2 | 34.2 | 0 | 2017-12-26 | -9.6 | 27.6 | 0 | 2016-12-26 | -10.8 | 28.8 | 0 | 26.19 | 0
2025-12-26 | -18.2 | 36.2 | 0 | 2024-12-26 | -9.6 | 27.6 | 0 | 2023-12-26 | 1.8 | 16.2 | 0 | 2022-12-26 | -8.8 | 26.8 | 0 | 2021-12-26 | -2.5 | 20.5 | 0 | 2020-12-26 | -3.2 | 21.2 | 0 | 2019-12-26 | -6 | 24 | 0 | 2018-12-26 | -16.5 | 34.5 | 0 | 2017-12-26 | -11.5 | 29.5 | 0 | 2016-12-26 | -11.1 | 29.1 | 0 | 26.56 | 0
2025-12-26 | -19 | 37 | 0 | 2024-12-26 | -9.3 | 27.3 | 0 | 2023-12-26 | 0.2 | 17.8 | 0 | 2022-12-26 | -9.7 | 27.7 | 0 | 2021-12-26 | -2.1 | 20.1 | 0 | 2020-12-26 | -3.1 | 21.1 | 0 | 2019-12-26 | -6.2 | 24.2 | 0 | 2018-12-26 | -14.7 | 32.7 | 0 | 2017-12-26 | -12.8 | 30.8 | 0 | 2016-12-26 | -11.3 | 29.3 | 0 | 26.8 | 0
2025-12-26 | -19.3 | 37.3 | 0 | 2024-12-26 | -9.6 | 27.6 | 0 | 2023-12-26 | -0.6 | 18.6 | 0 | 2022-12-26 | -8.8 | 26.8 | 0 | 2021-12-26 | -1.8 | 19.8 | 0 | 2020-12-26 | -3.3 | 21.3 | 0 | 2019-12-26 | -6.2 | 24.2 | 0 | 2018-12-26 | -14 | 32 | 0 | 2017-12-26 | -14.7 | 32.7 | 0 | 2016-12-26 | -11.7 | 29.7 | 0 | 27 | 0
2025-12-26 | -20.4 | 38.4 | 0 | 2024-12-26 | -9.5 | 27.5 | 0 | 2023-12-26 | 0.2 | 17.8 | 0 | 2022-12-26 | -9.5 | 27.5 | 0 | 2021-12-26 | -1.8 | 19.8 | 0 | 2020-12-26 | -5.3 | 23.3 | 0 | 2019-12-26 | -6.6 | 24.6 | 0 | 2018-12-26 | -12.9 | 30.9 | 0 | 2017-12-26 | -16.2 | 34.2 | 0 | 2016-12-26 | -11.5 | 29.5 | 0 | 27.35 | 0
2025-12-26 | -18.8 | 36.8 | 0 | 2024-12-26 | -9.7 | 27.7 | 0 | 2023-12-26 | -1.1 | 19.1 | 0 | 2022-12-26 | -9.9 | 27.9 | 0 | 2021-12-26 | -1.4 | 19.4 | 0 | 2020-12-26 | -6.6 | 24.6 | 0 | 2019-12-26 | -7.1 | 25.1 | 0 | 2018-12-26 | -12 | 30 | 0 | 2017-12-26 | -16.7 | 34.7 | 0 | 2016-12-26 | -11.9 | 29.9 | 0 | 27.52 | 0
2025-12-26 | -18.8 | 36.8 | 0 | 2024-12-26 | -9.6 | 27.6 | 0 | 2023-12-26 | 0.5 | 17.5 | 0 | 2022-12-26 | -9.7 | 27.7 | 0 | 2021-12-26 | -1.2 | 19.2 | 0 | 2020-12-26 | -7.4 | 25.4 | 0 | 2019-12-26 | -7.1 | 25.1 | 0 | 2018-12-26 | -11.4 | 29.4 | 0 | 2017-12-26 | -16.5 | 34.5 | 0 | 2016-12-26 | -11.4 | 29.4 | 0 | 27.26 | 0
2025-12-26 | -17.5 | 35.5 | 0 | 2024-12-26 | -9.9 | 27.9 | 0 | 2023-12-26 | 2.6 | 15.4 | 0 | 2022-12-26 | -9.3 | 27.3 | 0 | 2021-12-26 | -0.9 | 18.9 | 0 | 2020-12-26 | -8.1 | 26.1 | 0 | 2019-12-26 | -6.4 | 24.4 | 0 | 2018-12-26 | -9.5 | 27.5 | 0 | 2017-12-26 | -14.8 | 32.8 | 0 | 2016-12-26 | -11 | 29 | 0 | 26.48 | 0
2025-12-26 | -16.7 | 34.7 | 0 | 2024-12-26 | -8.6 | 26.6 | 0 | 2023-12-26 | 3.8 | 14.2 | 0 | 2022-12-26 | -8.8 | 26.8 | 0 | 2021-12-26 | -0.8 | 18.8 | 0 | 2020-12-26 | -8.3 | 26.3 | 0 | 2019-12-26 | -6.1 | 24.1 | 0 | 2018-12-26 | -8.3 | 26.3 | 0 | 2017-12-26 | -14.6 | 32.6 | 0 | 2016-12-26 | -10.4 | 28.4 | 0 | 25.88 | 0
2025-12-26 | -15.9 | 33.9 | 0 | 2024-12-26 | -7 | 25 | 0 | 2023-12-26 | 4.7 | 13.3 | 0 | 2022-12-26 | -8.1 | 26.1 | 0 | 2021-12-26 | -0.6 | 18.6 | 0 | 2020-12-26 | -8.3 | 26.3 | 0 | 2019-12-26 | -5.5 | 23.5 | 0 | 2018-12-26 | -7.2 | 25.2 | 0 | 2017-12-26 | -14.3 | 32.3 | 0 | 2016-12-26 | -9.6 | 27.6 | 0 | 25.18 | 0
2025-12-26 | -15.4 | 33.4 | 0 | 2024-12-26 | -6.1 | 24.1 | 0 | 2023-12-26 | 6 | 12 | 0 | 2022-12-26 | -4.9 | 22.9 | 0 | 2021-12-26 | -1.5 | 19.5 | 0 | 2020-12-26 | -8.3 | 26.3 | 0 | 2019-12-26 | -5.2 | 23.2 | 0 | 2018-12-26 | -6 | 24 | 0 | 2017-12-26 | -14.1 | 32.1 | 0 | 2016-12-26 | -9.6 | 27.6 | 0 | 24.51 | 0
2025-12-26 | -14.9 | 32.9 | 0 | 2024-12-26 | -6.6 | 24.6 | 0 | 2023-12-26 | 6.2 | 11.8 | 0 | 2022-12-26 | -4.6 | 22.6 | 0 | 2021-12-26 | -2.1 | 20.1 | 0 | 2020-12-26 | -8.2 | 26.2 | 0 | 2019-12-26 | -4.8 | 22.8 | 0 | 2018-12-26 | -5.6 | 23.6 | 0 | 2017-12-26 | -14 | 32 | 0 | 2016-12-26 | -9.2 | 27.2 | 0 | 24.38 | 0
2025-12-26 | -14.9 | 32.9 | 0 | 2024-12-26 | -6.8 | 24.8 | 0 | 2023-12-26 | 6.2 | 11.8 | 0 | 2022-12-26 | -3.9 | 21.9 | 0 | 2021-12-26 | -2 | 20 | 0 | 2020-12-26 | -8.2 | 26.2 | 0 | 2019-12-26 | -4.8 | 22.8 | 0 | 2018-12-26 | -5.7 | 23.7 | 0 | 2017-12-26 | -14.6 | 32.6 | 0 | 2016-12-26 | -8.3 | 26.3 | 0 | 24.3 | 0
2025-12-26 | -14.8 | 32.8 | 0 | 2024-12-26 | -7.2 | 25.2 | 0 | 2023-12-26 | 5 | 13 | 0 | 2022-12-26 | -3.8 | 21.8 | 0 | 2021-12-26 | -2.5 | 20.5 | 0 | 2020-12-26 | -8.5 | 26.5 | 0 | 2019-12-26 | -4.9 | 22.9 | 0 | 2018-12-26 | -6.3 | 24.3 | 0 | 2017-12-26 | -14.5 | 32.5 | 0 | 2016-12-26 | -7.6 | 25.6 | 0 | 24.51 | 0
2025-12-26 | -15.2 | 33.2 | 0 | 2024-12-26 | -7.5 | 25.5 | 0 | 2023-12-26 | 4 | 14 | 0 | 2022-12-26 | -4.3 | 22.3 | 0 | 2021-12-26 | -3.2 | 21.2 | 0 | 2020-12-26 | -8.6 | 26.6 | 0 | 2019-12-26 | -5 | 23 | 0 | 2018-12-26 | -6.2 | 24.2 | 0 | 2017-12-26 | -15.8 | 33.8 | 0 | 2016-12-26 | -5.5 | 23.5 | 0 | 24.73 | 0
2025-12-26 | -15.2 | 33.2 | 0 | 2024-12-26 | -7.7 | 25.7 | 0 | 2023-12-26 | 4.5 | 13.5 | 0 | 2022-12-26 | -4.8 | 22.8 | 0 | 2021-12-26 | -3.6 | 21.6 | 0 | 2020-12-26 | -8.6 | 26.6 | 0 | 2019-12-26 | -5.2 | 23.2 | 0 | 2018-12-26 | -6.9 | 24.9 | 0 | 2017-12-26 | -17.8 | 35.8 | 0 | 2016-12-26 | -2.8 | 20.8 | 0 | 24.81 | 0
2025-12-26 | -15 | 33 | 0 | 2024-12-26 | -7.8 | 25.8 | 0 | 2023-12-26 | 4.6 | 13.4 | 0 | 2022-12-26 | -5.2 | 23.2 | 0 | 2021-12-26 | -4.2 | 22.2 | 0 | 2020-12-26 | -8.4 | 26.4 | 0 | 2019-12-26 | -5.6 | 23.6 | 0 | 2018-12-26 | -8.1 | 26.1 | 0 | 2017-12-26 | -17.2 | 35.2 | 0 | 2016-12-26 | -0.5 | 18.5 | 0 | 24.74 | 0
2025-12-26 | -15.1 | 33.1 | 0 | 2024-12-26 | -7.8 | 25.8 | 0 | 2023-12-26 | 4.2 | 13.8 | 0 | 2022-12-26 | -5.7 | 23.7 | 0 | 2021-12-26 | -4.9 | 22.9 | 0 | 2020-12-26 | -8.3 | 26.3 | 0 | 2019-12-26 | -5.2 | 23.2 | 0 | 2018-12-26 | -9.2 | 27.2 | 0 | 2017-12-26 | -17.7 | 35.7 | 0 | 2016-12-26 | 1.1 | 16.9 | 0 | 24.86 | 0
2025-12-26 | -15.7 | 33.7 | 0 | 2024-12-26 | -7.7 | 25.7 | 0 | 2023-12-26 | 3.7 | 14.3 | 0 | 2022-12-26 | -5.9 | 23.9 | 0 | 2021-12-26 | -6.5 | 24.5 | 0 | 2020-12-26 | -8.3 | 26.3 | 0 | 2019-12-26 | -5 | 23 | 0 | 2018-12-26 | -10.2 | 28.2 | 0 | 2017-12-26 | -19 | 37 | 0 | 2016-12-26 | 1.5 | 16.5 | 0 | 25.31 | 0
2025-12-26 | -15.4 | 33.4 | 0 | 2024-12-26 | -7.8 | 25.8 | 0 | 2023-12-26 | 3.3 | 14.7 | 0 | 2022-12-26 | -6.1 | 24.1 | 0 | 2021-12-26 | -8.3 | 26.3 | 0 | 2020-12-26 | -8.4 | 26.4 | 0 | 2019-12-26 | -5.1 | 23.1 | 0 | 2018-12-26 | -9.5 | 27.5 | 0 | 2017-12-26 | -20.5 | 38.5 | 0 | 2016-12-26 | 3.1 | 14.9 | 0 | 25.47 | 0
2025-12-26 | -14.9 | 32.9 | 0 | 2024-12-26 | -7.9 | 25.9 | 0 | 2023-12-26 | 3.3 | 14.7 | 0 | 2022-12-26 | -6.2 | 24.2 | 0 | 2021-12-26 | -9.4 | 27.4 | 0 | 2020-12-26 | -8.4 | 26.4 | 0 | 2019-12-26 | -4.8 | 22.8 | 0 | 2018-12-26 | -11 | 29 | 0 | 2017-12-26 | -19.5 | 37.5 | 0 | 2016-12-26 | 4.7 | 13.3 | 0 | 25.41 | 0
2025-12-27 | -14.6 | 32.6 | 0 | 2024-12-27 | -8 | 26 | 0 | 2023-12-27 | 3.2 | 14.8 | 0 | 2022-12-27 | -6.3 | 24.3 | 0 | 2021-12-27 | -10.3 | 28.3 | 0 | 2020-12-27 | -9.4 | 27.4 | 0 | 2019-12-27 | -4.6 | 22.6 | 0 | 2018-12-27 | -11.4 | 29.4 | 0 | 2017-12-27 | -20.8 | 38.8 | 0 | 2016-12-27 | 5.2 | 12.8 | 0 | 25.7 | 0
2025-12-27 | -14.5 | 32.5 | 0 | 2024-12-27 | -7.9 | 25.9 | 0 | 2023-12-27 | 3.1 | 14.9 | 0 | 2022-12-27 | -6.8 | 24.8 | 0 | 2021-12-27 | -11.4 | 29.4 | 0 | 2020-12-27 | -9.3 | 27.3 | 0 | 2019-12-27 | -4.5 | 22.5 | 0 | 2018-12-27 | -12.3 | 30.3 | 0 | 2017-12-27 | -21.9 | 39.9 | 0 | 2016-12-27 | 5.7 | 12.3 | 0 | 25.98 | 0
2025-12-27 | -14.1 | 32.1 | 0 | 2024-12-27 | -7.9 | 25.9 | 0 | 2023-12-27 | 3.1 | 14.9 | 0 | 2022-12-27 | -7 | 25 | 0 | 2021-12-27 | -11.9 | 29.9 | 0 | 2020-12-27 | -9.3 | 27.3 | 0 | 2019-12-27 | -4.2 | 22.2 | 0 | 2018-12-27 | -13.3 | 31.3 | 0 | 2017-12-27 | -23.2 | 41.2 | 0 | 2016-12-27 | 5.5 | 12.5 | 0 | 26.23 | 0
2025-12-27 | -13.6 | 31.6 | 0 | 2024-12-27 | -8 | 26 | 0 | 2023-12-27 | 3 | 15 | 0 | 2022-12-27 | -7.2 | 25.2 | 0 | 2021-12-27 | -12.3 | 30.3 | 0 | 2020-12-27 | -9.1 | 27.1 | 0 | 2019-12-27 | -4.1 | 22.1 | 0 | 2018-12-27 | -15.3 | 33.3 | 0 | 2017-12-27 | -21.9 | 39.9 | 0 | 2016-12-27 | 5.1 | 12.9 | 0 | 26.34 | 0
2025-12-27 | -13.3 | 31.3 | 0 | 2024-12-27 | -8 | 26 | 0 | 2023-12-27 | 2.9 | 15.1 | 0 | 2022-12-27 | -7.8 | 25.8 | 0 | 2021-12-27 | -12.2 | 30.2 | 0 | 2020-12-27 | -9.1 | 27.1 | 0 | 2019-12-27 | -4.1 | 22.1 | 0 | 2018-12-27 | -15.8 | 33.8 | 0 | 2017-12-27 | -22.9 | 40.9 | 0 | 2016-12-27 | 5.5 | 12.5 | 0 | 26.48 | 0
2025-12-27 | -13.3 | 31.3 | 0 | 2024-12-27 | -7.8 | 25.8 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -8.5 | 26.5 | 0 | 2021-12-27 | -13.6 | 31.6 | 0 | 2020-12-27 | -9 | 27 | 0 | 2019-12-27 | -3.8 | 21.8 | 0 | 2018-12-27 | -17.6 | 35.6 | 0 | 2017-12-27 | -23.2 | 41.2 | 0 | 2016-12-27 | 4.6 | 13.4 | 0 | 26.94 | 0
2025-12-27 | -12.9 | 30.9 | 0 | 2024-12-27 | -8.1 | 26.1 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -9 | 27 | 0 | 2021-12-27 | -13.1 | 31.1 | 0 | 2020-12-27 | -9 | 27 | 0 | 2019-12-27 | -3.5 | 21.5 | 0 | 2018-12-27 | -15.8 | 33.8 | 0 | 2017-12-27 | -24 | 42 | 0 | 2016-12-27 | 4 | 14 | 0 | 26.86 | 0
2025-12-27 | -12.6 | 30.6 | 0 | 2024-12-27 | -8 | 26 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -9.8 | 27.8 | 0 | 2021-12-27 | -12.8 | 30.8 | 0 | 2020-12-27 | -8.7 | 26.7 | 0 | 2019-12-27 | -2.9 | 20.9 | 0 | 2018-12-27 | -17.1 | 35.1 | 0 | 2017-12-27 | -24.2 | 42.2 | 0 | 2016-12-27 | 3.5 | 14.5 | 0 | 26.98 | 0
2025-12-27 | -12.6 | 30.6 | 0 | 2024-12-27 | -8.3 | 26.3 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -10 | 28 | 0 | 2021-12-27 | -12.8 | 30.8 | 0 | 2020-12-27 | -9.6 | 27.6 | 0 | 2019-12-27 | -2.3 | 20.3 | 0 | 2018-12-27 | -16.2 | 34.2 | 0 | 2017-12-27 | -24.1 | 42.1 | 0 | 2016-12-27 | 2.9 | 15.1 | 0 | 27.02 | 0
2025-12-27 | -12.2 | 30.2 | 0 | 2024-12-27 | -8 | 26 | 0 | 2023-12-27 | 2.9 | 15.1 | 0 | 2022-12-27 | -10.1 | 28.1 | 0 | 2021-12-27 | -12.3 | 30.3 | 0 | 2020-12-27 | -9.5 | 27.5 | 0 | 2019-12-27 | -1.9 | 19.9 | 0 | 2018-12-27 | -15.3 | 33.3 | 0 | 2017-12-27 | -24.6 | 42.6 | 0 | 2016-12-27 | 2.7 | 15.3 | 0 | 26.83 | 0
2025-12-27 | -11.4 | 29.4 | 0 | 2024-12-27 | -7.5 | 25.5 | 0 | 2023-12-27 | 3 | 15 | 0 | 2022-12-27 | -9.7 | 27.7 | 0 | 2021-12-27 | -11.5 | 29.5 | 0 | 2020-12-27 | -6.8 | 24.8 | 0 | 2019-12-27 | -1.8 | 19.8 | 0 | 2018-12-27 | -13.9 | 31.9 | 0 | 2017-12-27 | -22.3 | 40.3 | 0 | 2016-12-27 | 2.2 | 15.8 | 0 | 25.97 | 0
2025-12-27 | -11.1 | 29.1 | 0 | 2024-12-27 | -6.6 | 24.6 | 0 | 2023-12-27 | 3.4 | 14.6 | 0 | 2022-12-27 | -8.3 | 26.3 | 0 | 2021-12-27 | -10.7 | 28.7 | 0 | 2020-12-27 | -6.1 | 24.1 | 0 | 2019-12-27 | -1.1 | 19.1 | 0 | 2018-12-27 | -12.8 | 30.8 | 0 | 2017-12-27 | -21.4 | 39.4 | 0 | 2016-12-27 | 1.8 | 16.2 | 0 | 25.29 | 0
2025-12-27 | -10.5 | 28.5 | 0 | 2024-12-27 | -6.1 | 24.1 | 0 | 2023-12-27 | 3.7 | 14.3 | 0 | 2022-12-27 | -7.1 | 25.1 | 0 | 2021-12-27 | -10.4 | 28.4 | 0 | 2020-12-27 | -5.6 | 23.6 | 0 | 2019-12-27 | -0.7 | 18.7 | 0 | 2018-12-27 | -12.1 | 30.1 | 0 | 2017-12-27 | -20.6 | 38.6 | 0 | 2016-12-27 | 2.3 | 15.7 | 0 | 24.71 | 0
2025-12-27 | -10.1 | 28.1 | 0 | 2024-12-27 | -5.6 | 23.6 | 0 | 2023-12-27 | 3.9 | 14.1 | 0 | 2022-12-27 | -5.7 | 23.7 | 0 | 2021-12-27 | -9.8 | 27.8 | 0 | 2020-12-27 | -5.2 | 23.2 | 0 | 2019-12-27 | -0.6 | 18.6 | 0 | 2018-12-27 | -11.5 | 29.5 | 0 | 2017-12-27 | -20.2 | 38.2 | 0 | 2016-12-27 | 2.2 | 15.8 | 0 | 24.26 | 0
2025-12-27 | -9.7 | 27.7 | 0 | 2024-12-27 | -5.1 | 23.1 | 0 | 2023-12-27 | 4 | 14 | 0 | 2022-12-27 | -5.3 | 23.3 | 0 | 2021-12-27 | -9.2 | 27.2 | 0 | 2020-12-27 | -4.5 | 22.5 | 0 | 2019-12-27 | 0.8 | 17.2 | 0 | 2018-12-27 | -11.1 | 29.1 | 0 | 2017-12-27 | -20.1 | 38.1 | 0 | 2016-12-27 | 2.2 | 15.8 | 0 | 23.8 | 0
2025-12-27 | -9.7 | 27.7 | 0 | 2024-12-27 | -5.5 | 23.5 | 0 | 2023-12-27 | 3.9 | 14.1 | 0 | 2022-12-27 | -4.5 | 22.5 | 0 | 2021-12-27 | -9.1 | 27.1 | 0 | 2020-12-27 | -4.4 | 22.4 | 0 | 2019-12-27 | 2.5 | 15.5 | 0 | 2018-12-27 | -10.8 | 28.8 | 0 | 2017-12-27 | -20.3 | 38.3 | 0 | 2016-12-27 | 2 | 16 | 0 | 23.59 | 0
2025-12-27 | -9.5 | 27.5 | 0 | 2024-12-27 | -6 | 24 | 0 | 2023-12-27 | 3.9 | 14.1 | 0 | 2022-12-27 | -4.1 | 22.1 | 0 | 2021-12-27 | -8.9 | 26.9 | 0 | 2020-12-27 | -4.6 | 22.6 | 0 | 2019-12-27 | 1.8 | 16.2 | 0 | 2018-12-27 | -10.4 | 28.4 | 0 | 2017-12-27 | -21.3 | 39.3 | 0 | 2016-12-27 | 1.6 | 16.4 | 0 | 23.75 | 0
2025-12-27 | -10.2 | 28.2 | 0 | 2024-12-27 | -6.7 | 24.7 | 0 | 2023-12-27 | 3.9 | 14.1 | 0 | 2022-12-27 | -4.2 | 22.2 | 0 | 2021-12-27 | -8.7 | 26.7 | 0 | 2020-12-27 | -4.9 | 22.9 | 0 | 2019-12-27 | 2.5 | 15.5 | 0 | 2018-12-27 | -10.5 | 28.5 | 0 | 2017-12-27 | -22 | 40 | 0 | 2016-12-27 | 0.9 | 17.1 | 0 | 23.99 | 0
2025-12-27 | -10.8 | 28.8 | 0 | 2024-12-27 | -7.3 | 25.3 | 0 | 2023-12-27 | 3.5 | 14.5 | 0 | 2022-12-27 | -4.6 | 22.6 | 0 | 2021-12-27 | -8.6 | 26.6 | 0 | 2020-12-27 | -4.8 | 22.8 | 0 | 2019-12-27 | 2 | 16 | 0 | 2018-12-27 | -10.9 | 28.9 | 0 | 2017-12-27 | -22.3 | 40.3 | 0 | 2016-12-27 | 0.2 | 17.8 | 0 | 24.36 | 0
2025-12-27 | -11.5 | 29.5 | 0 | 2024-12-27 | -7.4 | 25.4 | 0 | 2023-12-27 | 3.3 | 14.7 | 0 | 2022-12-27 | -4.4 | 22.4 | 0 | 2021-12-27 | -8.7 | 26.7 | 0 | 2020-12-27 | -4.8 | 22.8 | 0 | 2019-12-27 | 1.7 | 16.3 | 0 | 2018-12-27 | -10.4 | 28.4 | 0 | 2017-12-27 | -22.4 | 40.4 | 0 | 2016-12-27 | -0.2 | 18.2 | 0 | 24.48 | 0
2025-12-27 | -11.7 | 29.7 | 0 | 2024-12-27 | -7.4 | 25.4 | 0 | 2023-12-27 | 2.9 | 15.1 | 0 | 2022-12-27 | -4.7 | 22.7 | 0 | 2021-12-27 | -8.6 | 26.6 | 0 | 2020-12-27 | -4.8 | 22.8 | 0 | 2019-12-27 | 2.1 | 15.9 | 0 | 2018-12-27 | -10 | 28 | 0 | 2017-12-27 | -22.9 | 40.9 | 0 | 2016-12-27 | -0.4 | 18.4 | 0 | 24.55 | 0
2025-12-27 | -12.3 | 30.3 | 0 | 2024-12-27 | -7.5 | 25.5 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -4.8 | 22.8 | 0 | 2021-12-27 | -8.7 | 26.7 | 0 | 2020-12-27 | -4.8 | 22.8 | 0 | 2019-12-27 | 2.4 | 15.6 | 0 | 2018-12-27 | -10.2 | 28.2 | 0 | 2017-12-27 | -23.6 | 41.6 | 0 | 2016-12-27 | -0.7 | 18.7 | 0 | 24.74 | 0
2025-12-27 | -14.6 | 32.6 | 0 | 2024-12-27 | -7.7 | 25.7 | 0 | 2023-12-27 | 2.8 | 15.2 | 0 | 2022-12-27 | -5.4 | 23.4 | 0 | 2021-12-27 | -8.6 | 26.6 | 0 | 2020-12-27 | -4.4 | 22.4 | 0 | 2019-12-27 | 2.4 | 15.6 | 0 | 2018-12-27 | -9.6 | 27.6 | 0 | 2017-12-27 | -24 | 42 | 0 | 2016-12-27 | -0.6 | 18.6 | 0 | 24.97 | 0
2025-12-27 | -14.3 | 32.3 | 0 | 2024-12-27 | -7.8 | 25.8 | 0 | 2023-12-27 | 2.9 | 15.1 | 0 | 2022-12-27 | -5.2 | 23.2 | 0 | 2021-12-27 | -8.7 | 26.7 | 0 | 2020-12-27 | -4 | 22 | 0 | 2019-12-27 | 2 | 16 | 0 | 2018-12-27 | -9.1 | 27.1 | 0 | 2017-12-27 | -24.3 | 42.3 | 0 | 2016-12-27 | -0.6 | 18.6 | 0 | 24.91 | 0
2025-12-28 | -15.3 | 33.3 | 0 | 2024-12-28 | -7.7 | 25.7 | 0 | 2023-12-28 | 2.9 | 15.1 | 0 | 2022-12-28 | -4.7 | 22.7 | 0 | 2021-12-28 | -8.7 | 26.7 | 0 | 2020-12-28 | -3.7 | 21.7 | 0 | 2019-12-28 | 2.1 | 15.9 | 0 | 2018-12-28 | -8.9 | 26.9 | 0 | 2017-12-28 | -24.8 | 42.8 | 0 | 2016-12-28 | -0.8 | 18.8 | 0 | 24.96 | 0
2025-12-28 | -14.7 | 32.7 | 0 | 2024-12-28 | -7.7 | 25.7 | 0 | 2023-12-28 | 2.8 | 15.2 | 0 | 2022-12-28 | -5 | 23 | 0 | 2021-12-28 | -8.8 | 26.8 | 0 | 2020-12-28 | -3.6 | 21.6 | 0 | 2019-12-28 | 1.8 | 16.2 | 0 | 2018-12-28 | -8.8 | 26.8 | 0 | 2017-12-28 | -25.2 | 43.2 | 0 | 2016-12-28 | -1 | 19 | 0 | 25.02 | 0
2025-12-28 | -15.4 | 33.4 | 0 | 2024-12-28 | -7.6 | 25.6 | 0 | 2023-12-28 | 2.7 | 15.3 | 0 | 2022-12-28 | -5.3 | 23.3 | 0 | 2021-12-28 | -9.2 | 27.2 | 0 | 2020-12-28 | -3.8 | 21.8 | 0 | 2019-12-28 | 1.9 | 16.1 | 0 | 2018-12-28 | -8.3 | 26.3 | 0 | 2017-12-28 | -25.6 | 43.6 | 0 | 2016-12-28 | -1.6 | 19.6 | 0 | 25.22 | 0
2025-12-28 | -17.4 | 35.4 | 0 | 2024-12-28 | -7.8 | 25.8 | 0 | 2023-12-28 | 2.8 | 15.2 | 0 | 2022-12-28 | -4.8 | 22.8 | 0 | 2021-12-28 | -9.4 | 27.4 | 0 | 2020-12-28 | -3.7 | 21.7 | 0 | 2019-12-28 | 1.9 | 16.1 | 0 | 2018-12-28 | -6.6 | 24.6 | 0 | 2017-12-28 | -25.8 | 43.8 | 0 | 2016-12-28 | -2.1 | 20.1 | 0 | 25.29 | 0
2025-12-28 | -17.8 | 35.8 | 0 | 2024-12-28 | -8.2 | 26.2 | 0 | 2023-12-28 | 2.8 | 15.2 | 0 | 2022-12-28 | -4.3 | 22.3 | 0 | 2021-12-28 | -9.3 | 27.3 | 0 | 2020-12-28 | -3.6 | 21.6 | 0 | 2019-12-28 | 1.7 | 16.3 | 0 | 2018-12-28 | -6.4 | 24.4 | 0 | 2017-12-28 | -26.2 | 44.2 | 0 | 2016-12-28 | -3.1 | 21.1 | 0 | 25.44 | 0
2025-12-28 | -18.2 | 36.2 | 0 | 2024-12-28 | -8.2 | 26.2 | 0 | 2023-12-28 | 2.6 | 15.4 | 0 | 2022-12-28 | -4.2 | 22.2 | 0 | 2021-12-28 | -9 | 27 | 0 | 2020-12-28 | -3.3 | 21.3 | 0 | 2019-12-28 | 1.1 | 16.9 | 0 | 2018-12-28 | -5.9 | 23.9 | 0 | 2017-12-28 | -26.4 | 44.4 | 0 | 2016-12-28 | -3.8 | 21.8 | 0 | 25.53 | 0
2025-12-28 | -15.5 | 33.5 | 0 | 2024-12-28 | -8.1 | 26.1 | 0 | 2023-12-28 | 2.5 | 15.5 | 0 | 2022-12-28 | -4.1 | 22.1 | 0 | 2021-12-28 | -8.7 | 26.7 | 0 | 2020-12-28 | -2.4 | 20.4 | 0 | 2019-12-28 | 0.3 | 17.7 | 0 | 2018-12-28 | -5.2 | 23.2 | 0 | 2017-12-28 | -26.4 | 44.4 | 0 | 2016-12-28 | -4.3 | 22.3 | 0 | 25.19 | 0
2025-12-28 | -15.7 | 33.7 | 0 | 2024-12-28 | -7.8 | 25.8 | 0 | 2023-12-28 | 2.3 | 15.7 | 0 | 2022-12-28 | -3.9 | 21.9 | 0 | 2021-12-28 | -8.7 | 26.7 | 0 | 2020-12-28 | -2.7 | 20.7 | 0 | 2019-12-28 | -0.5 | 18.5 | 0 | 2018-12-28 | -4.8 | 22.8 | 0 | 2017-12-28 | -26.6 | 44.6 | 0 | 2016-12-28 | -5.4 | 23.4 | 0 | 25.38 | 0
2025-12-28 | -16.3 | 34.3 | 0 | 2024-12-28 | -7.7 | 25.7 | 0 | 2023-12-28 | 2.5 | 15.5 | 0 | 2022-12-28 | -3.7 | 21.7 | 0 | 2021-12-28 | -7.8 | 25.8 | 0 | 2020-12-28 | -1.8 | 19.8 | 0 | 2019-12-28 | -1.2 | 19.2 | 0 | 2018-12-28 | -3.5 | 21.5 | 0 | 2017-12-28 | -26.7 | 44.7 | 0 | 2016-12-28 | -6.7 | 24.7 | 0 | 25.29 | 0
2025-12-28 | -16.4 | 34.4 | 0 | 2024-12-28 | -7.3 | 25.3 | 0 | 2023-12-28 | 2.8 | 15.2 | 0 | 2022-12-28 | -3.2 | 21.2 | 0 | 2021-12-28 | -6.4 | 24.4 | 0 | 2020-12-28 | 0.3 | 17.7 | 0 | 2019-12-28 | 0.2 | 17.8 | 0 | 2018-12-28 | -2.8 | 20.8 | 0 | 2017-12-28 | -25.9 | 43.9 | 0 | 2016-12-28 | -7.1 | 25.1 | 0 | 24.58 | 0
2025-12-28 | -13.2 | 31.2 | 0 | 2024-12-28 | -6.8 | 24.8 | 0 | 2023-12-28 | 3.2 | 14.8 | 0 | 2022-12-28 | -2.6 | 20.6 | 0 | 2021-12-28 | -5.2 | 23.2 | 0 | 2020-12-28 | 0.8 | 17.2 | 0 | 2019-12-28 | 1.5 | 16.5 | 0 | 2018-12-28 | -2.8 | 20.8 | 0 | 2017-12-28 | -25.3 | 43.3 | 0 | 2016-12-28 | -7.1 | 25.1 | 0 | 23.75 | 0
2025-12-28 | -11.3 | 29.3 | 0 | 2024-12-28 | -6.3 | 24.3 | 0 | 2023-12-28 | 3.2 | 14.8 | 0 | 2022-12-28 | -1.8 | 19.8 | 0 | 2021-12-28 | -3.9 | 21.9 | 0 | 2020-12-28 | 1.3 | 16.7 | 0 | 2019-12-28 | 2 | 16 | 0 | 2018-12-28 | -1.7 | 19.7 | 0 | 2017-12-28 | -24.2 | 42.2 | 0 | 2016-12-28 | -6.6 | 24.6 | 0 | 22.93 | 0
2025-12-28 | -9.7 | 27.7 | 0 | 2024-12-28 | -5.9 | 23.9 | 0 | 2023-12-28 | 3.1 | 14.9 | 0 | 2022-12-28 | -1 | 19 | 0 | 2021-12-28 | -2.2 | 20.2 | 0 | 2020-12-28 | 2.3 | 15.7 | 0 | 2019-12-28 | 2.2 | 15.8 | 0 | 2018-12-28 | -0.3 | 18.3 | 0 | 2017-12-28 | -23.2 | 41.2 | 0 | 2016-12-28 | -6.5 | 24.5 | 0 | 22.12 | 0
2025-12-28 | -8.6 | 26.6 | 0 | 2024-12-28 | -5.7 | 23.7 | 0 | 2023-12-28 | 3.4 | 14.6 | 0 | 2022-12-28 | -0.6 | 18.6 | 0 | 2021-12-28 | -2.4 | 20.4 | 0 | 2020-12-28 | 3.4 | 14.6 | 0 | 2019-12-28 | 2.6 | 15.4 | 0 | 2018-12-28 | -0.5 | 18.5 | 0 | 2017-12-28 | -21.7 | 39.7 | 0 | 2016-12-28 | -6.4 | 24.4 | 0 | 21.65 | 0
2025-12-28 | -8.6 | 26.6 | 0 | 2024-12-28 | -5.4 | 23.4 | 0 | 2023-12-28 | 4 | 14 | 0 | 2022-12-28 | -0.2 | 18.2 | 0 | 2021-12-28 | -2.6 | 20.6 | 0 | 2020-12-28 | 3.7 | 14.3 | 0 | 2019-12-28 | 3.1 | 14.9 | 0 | 2018-12-28 | -0.4 | 18.4 | 0 | 2017-12-28 | -21.2 | 39.2 | 0 | 2016-12-28 | -6.3 | 24.3 | 0 | 21.39 | 0
2025-12-28 | -8 | 26 | 0 | 2024-12-28 | -5.2 | 23.2 | 0 | 2023-12-28 | 4 | 14 | 0 | 2022-12-28 | 0 | 18 | 0 | 2021-12-28 | -3.7 | 21.7 | 0 | 2020-12-28 | 3.3 | 14.7 | 0 | 2019-12-28 | 3.2 | 14.8 | 0 | 2018-12-28 | -0.2 | 18.2 | 0 | 2017-12-28 | -20.9 | 38.9 | 0 | 2016-12-28 | -6.5 | 24.5 | 0 | 21.4 | 0
2025-12-28 | -7.5 | 25.5 | 0 | 2024-12-28 | -5.2 | 23.2 | 0 | 2023-12-28 | 3.8 | 14.2 | 0 | 2022-12-28 | 0.1 | 17.9 | 0 | 2021-12-28 | -3 | 21 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | 2.5 | 15.5 | 0 | 2018-12-28 | 0.1 | 17.9 | 0 | 2017-12-28 | -21 | 39 | 0 | 2016-12-28 | -6.8 | 24.8 | 0 | 21.7 | 0
2025-12-28 | -7.4 | 25.4 | 0 | 2024-12-28 | -5.2 | 23.2 | 0 | 2023-12-28 | 3.6 | 14.4 | 0 | 2022-12-28 | -0.1 | 18.1 | 0 | 2021-12-28 | -2.6 | 20.6 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | 1.7 | 16.3 | 0 | 2018-12-28 | 0.2 | 17.8 | 0 | 2017-12-28 | -21.6 | 39.6 | 0 | 2016-12-28 | -7.7 | 25.7 | 0 | 21.91 | 0
2025-12-28 | -7.3 | 25.3 | 0 | 2024-12-28 | -5 | 23 | 0 | 2023-12-28 | 3.4 | 14.6 | 0 | 2022-12-28 | 0 | 18 | 0 | 2021-12-28 | -2.2 | 20.2 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | 0.7 | 17.3 | 0 | 2018-12-28 | 2.5 | 15.5 | 0 | 2017-12-28 | -21.4 | 39.4 | 0 | 2016-12-28 | -8.2 | 26.2 | 0 | 21.75 | 0
2025-12-28 | -7.4 | 25.4 | 0 | 2024-12-28 | -5.3 | 23.3 | 0 | 2023-12-28 | 3.1 | 14.9 | 0 | 2022-12-28 | -0.8 | 18.8 | 0 | 2021-12-28 | -2.3 | 20.3 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | -0.2 | 18.2 | 0 | 2018-12-28 | 4 | 14 | 0 | 2017-12-28 | -22.6 | 40.6 | 0 | 2016-12-28 | -8.3 | 26.3 | 0 | 21.98 | 0
2025-12-28 | -7.8 | 25.8 | 0 | 2024-12-28 | -5 | 23 | 0 | 2023-12-28 | 3 | 15 | 0 | 2022-12-28 | -1.6 | 19.6 | 0 | 2021-12-28 | -2.9 | 20.9 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | -0.8 | 18.8 | 0 | 2018-12-28 | 5.3 | 12.7 | 0 | 2017-12-28 | -22.6 | 40.6 | 0 | 2016-12-28 | -7.9 | 25.9 | 0 | 22.03 | 0
2025-12-28 | -7.5 | 25.5 | 0 | 2024-12-28 | -4.9 | 22.9 | 0 | 2023-12-28 | 3.1 | 14.9 | 0 | 2022-12-28 | -0.8 | 18.8 | 0 | 2021-12-28 | -2.9 | 20.9 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | -1.6 | 19.6 | 0 | 2018-12-28 | 5.8 | 12.2 | 0 | 2017-12-28 | -23.7 | 41.7 | 0 | 2016-12-28 | -8.3 | 26.3 | 0 | 22.08 | 0
2025-12-28 | -7.2 | 25.2 | 0 | 2024-12-28 | -4.5 | 22.5 | 0 | 2023-12-28 | 3 | 15 | 0 | 2022-12-28 | -0.3 | 18.3 | 0 | 2021-12-28 | -3.1 | 21.1 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | -1.6 | 19.6 | 0 | 2018-12-28 | 5.7 | 12.3 | 0 | 2017-12-28 | -23.4 | 41.4 | 0 | 2016-12-28 | -8.6 | 26.6 | 0 | 22 | 0
2025-12-28 | -6.5 | 24.5 | 0 | 2024-12-28 | -4.7 | 22.7 | 0 | 2023-12-28 | 2.7 | 15.3 | 0 | 2022-12-28 | -0.4 | 18.4 | 0 | 2021-12-28 | -2.8 | 20.8 | 0 | 2020-12-28 | 0 | 18 | 0 | 2019-12-28 | -2.2 | 20.2 | 0 | 2018-12-28 | 6.3 | 11.7 | 0 | 2017-12-28 | -23.1 | 41.1 | 0 | 2016-12-28 | -8.1 | 26.1 | 0 | 21.88 | 0
2025-12-29 | -6.2 | 24.2 | 0 | 2024-12-29 | -4.2 | 22.2 | 0 | 2023-12-29 | 2.6 | 15.4 | 0 | 2022-12-29 | -1.6 | 19.6 | 0 | 2021-12-29 | -3.4 | 21.4 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -2.9 | 20.9 | 0 | 2018-12-29 | 6.5 | 11.5 | 0 | 2017-12-29 | -24.1 | 42.1 | 0 | 2016-12-29 | -7.9 | 25.9 | 0 | 22.12 | 0
2025-12-29 | -6 | 24 | 0 | 2024-12-29 | -4.1 | 22.1 | 0 | 2023-12-29 | 2.4 | 15.6 | 0 | 2022-12-29 | -1.3 | 19.3 | 0 | 2021-12-29 | -3.9 | 21.9 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -3.2 | 21.2 | 0 | 2018-12-29 | 6.2 | 11.8 | 0 | 2017-12-29 | -24.9 | 42.9 | 0 | 2016-12-29 | -7.4 | 25.4 | 0 | 22.22 | 0
2025-12-29 | -6 | 24 | 0 | 2024-12-29 | -3.5 | 21.5 | 0 | 2023-12-29 | 2.2 | 15.8 | 0 | 2022-12-29 | -0.2 | 18.2 | 0 | 2021-12-29 | -4 | 22 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -4.1 | 22.1 | 0 | 2018-12-29 | 5.1 | 12.9 | 0 | 2017-12-29 | -23.2 | 41.2 | 0 | 2016-12-29 | -7.1 | 25.1 | 0 | 22.08 | 0
2025-12-29 | -5.6 | 23.6 | 0 | 2024-12-29 | -3.2 | 21.2 | 0 | 2023-12-29 | 2.4 | 15.6 | 0 | 2022-12-29 | -0.8 | 18.8 | 0 | 2021-12-29 | -4 | 22 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -4.1 | 22.1 | 0 | 2018-12-29 | 3.2 | 14.8 | 0 | 2017-12-29 | -24.1 | 42.1 | 0 | 2016-12-29 | -6.9 | 24.9 | 0 | 22.31 | 0
2025-12-29 | -4.5 | 22.5 | 0 | 2024-12-29 | -2.9 | 20.9 | 0 | 2023-12-29 | 2.6 | 15.4 | 0 | 2022-12-29 | -0.8 | 18.8 | 0 | 2021-12-29 | -4 | 22 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -5.2 | 23.2 | 0 | 2018-12-29 | 1.5 | 16.5 | 0 | 2017-12-29 | -23 | 41 | 0 | 2016-12-29 | -6.8 | 24.8 | 0 | 22.31 | 0
2025-12-29 | -3.8 | 21.8 | 0 | 2024-12-29 | -2.8 | 20.8 | 0 | 2023-12-29 | 2.4 | 15.6 | 0 | 2022-12-29 | -4.2 | 22.2 | 0 | 2021-12-29 | -4.1 | 22.1 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -5.9 | 23.9 | 0 | 2018-12-29 | -0.3 | 18.3 | 0 | 2017-12-29 | -22.7 | 40.7 | 0 | 2016-12-29 | -6.6 | 24.6 | 0 | 22.8 | 0
2025-12-29 | -3.7 | 21.7 | 0 | 2024-12-29 | -2.8 | 20.8 | 0 | 2023-12-29 | 2.3 | 15.7 | 0 | 2022-12-29 | -3.2 | 21.2 | 0 | 2021-12-29 | -4.4 | 22.4 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -4.9 | 22.9 | 0 | 2018-12-29 | -2.5 | 20.5 | 0 | 2017-12-29 | -22.4 | 40.4 | 0 | 2016-12-29 | -6.5 | 24.5 | 0 | 22.81 | 0
2025-12-29 | -3.4 | 21.4 | 0 | 2024-12-29 | -2.9 | 20.9 | 0 | 2023-12-29 | 2.3 | 15.7 | 0 | 2022-12-29 | -3.1 | 21.1 | 0 | 2021-12-29 | -4.5 | 22.5 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -5.6 | 23.6 | 0 | 2018-12-29 | -4.5 | 22.5 | 0 | 2017-12-29 | -22.1 | 40.1 | 0 | 2016-12-29 | -6.2 | 24.2 | 0 | 23 | 0
2025-12-29 | -2.7 | 20.7 | 0 | 2024-12-29 | -2.7 | 20.7 | 0 | 2023-12-29 | 2.4 | 15.6 | 0 | 2022-12-29 | -3.9 | 21.9 | 0 | 2021-12-29 | -4.5 | 22.5 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -5.9 | 23.9 | 0 | 2018-12-29 | -6.1 | 24.1 | 0 | 2017-12-29 | -23.4 | 41.4 | 0 | 2016-12-29 | -6.5 | 24.5 | 0 | 23.33 | 0
2025-12-29 | -1.8 | 19.8 | 0 | 2024-12-29 | -2.2 | 20.2 | 0 | 2023-12-29 | 2.8 | 15.2 | 0 | 2022-12-29 | -3.4 | 21.4 | 0 | 2021-12-29 | -4.3 | 22.3 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -3.6 | 21.6 | 0 | 2018-12-29 | -7.7 | 25.7 | 0 | 2017-12-29 | -23 | 41 | 0 | 2016-12-29 | -6.4 | 24.4 | 0 | 22.96 | 0
2025-12-29 | 0.3 | 17.7 | 0 | 2024-12-29 | -1.5 | 19.5 | 0 | 2023-12-29 | 3.2 | 14.8 | 0 | 2022-12-29 | -0.6 | 18.6 | 0 | 2021-12-29 | -4 | 22 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -2.2 | 20.2 | 0 | 2018-12-29 | -8.5 | 26.5 | 0 | 2017-12-29 | -21.5 | 39.5 | 0 | 2016-12-29 | -6.2 | 24.2 | 0 | 22.1 | 0
2025-12-29 | 1.1 | 16.9 | 0 | 2024-12-29 | -0.7 | 18.7 | 0 | 2023-12-29 | 3.6 | 14.4 | 0 | 2022-12-29 | 4 | 14 | 0 | 2021-12-29 | -3.6 | 21.6 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -1.1 | 19.1 | 0 | 2018-12-29 | -9.2 | 27.2 | 0 | 2017-12-29 | -20.9 | 38.9 | 0 | 2016-12-29 | -5.7 | 23.7 | 0 | 21.25 | 0
2025-12-29 | 2.6 | 15.4 | 0 | 2024-12-29 | -0.1 | 18.1 | 0 | 2023-12-29 | 3.9 | 14.1 | 0 | 2022-12-29 | 4.4 | 13.6 | 0 | 2021-12-29 | -3.3 | 21.3 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.4 | 18.4 | 0 | 2018-12-29 | -9.4 | 27.4 | 0 | 2017-12-29 | -19.8 | 37.8 | 0 | 2016-12-29 | -5.3 | 23.3 | 0 | 20.74 | 0
2025-12-29 | 2.3 | 15.7 | 0 | 2024-12-29 | 0.4 | 17.6 | 0 | 2023-12-29 | 4.1 | 13.9 | 0 | 2022-12-29 | 6 | 12 | 0 | 2021-12-29 | -2.9 | 20.9 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.1 | 18.1 | 0 | 2018-12-29 | -8.7 | 26.7 | 0 | 2017-12-29 | -19.7 | 37.7 | 0 | 2016-12-29 | -5 | 23 | 0 | 20.36 | 0
2025-12-29 | 1.8 | 16.2 | 0 | 2024-12-29 | 1.1 | 16.9 | 0 | 2023-12-29 | 3.4 | 14.6 | 0 | 2022-12-29 | 6.9 | 11.1 | 0 | 2021-12-29 | -2.7 | 20.7 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.1 | 18.1 | 0 | 2018-12-29 | -8.5 | 26.5 | 0 | 2017-12-29 | -19.5 | 37.5 | 0 | 2016-12-29 | -4.3 | 22.3 | 0 | 20.19 | 0
2025-12-29 | 0.7 | 17.3 | 0 | 2024-12-29 | 1.7 | 16.3 | 0 | 2023-12-29 | 3 | 15 | 0 | 2022-12-29 | 6.9 | 11.1 | 0 | 2021-12-29 | -2.7 | 20.7 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.2 | 18.2 | 0 | 2018-12-29 | -8.6 | 26.6 | 0 | 2017-12-29 | -19.3 | 37.3 | 0 | 2016-12-29 | -3.8 | 21.8 | 0 | 20.23 | 0
2025-12-29 | -0.5 | 18.5 | 0 | 2024-12-29 | 2 | 16 | 0 | 2023-12-29 | 2.1 | 15.9 | 0 | 2022-12-29 | 6.1 | 11.9 | 0 | 2021-12-29 | -3.7 | 21.7 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.4 | 18.4 | 0 | 2018-12-29 | -9.1 | 27.1 | 0 | 2017-12-29 | -18.8 | 36.8 | 0 | 2016-12-29 | -3.3 | 21.3 | 0 | 20.56 | 0
2025-12-29 | -0.6 | 18.6 | 0 | 2024-12-29 | 1.9 | 16.1 | 0 | 2023-12-29 | 1.5 | 16.5 | 0 | 2022-12-29 | 5.7 | 12.3 | 0 | 2021-12-29 | -4.6 | 22.6 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.7 | 18.7 | 0 | 2018-12-29 | -9.4 | 27.4 | 0 | 2017-12-29 | -19.5 | 37.5 | 0 | 2016-12-29 | -3.1 | 21.1 | 0 | 20.88 | 0
2025-12-29 | -1.5 | 19.5 | 0 | 2024-12-29 | 1.6 | 16.4 | 0 | 2023-12-29 | 1.8 | 16.2 | 0 | 2022-12-29 | 5.9 | 12.1 | 0 | 2021-12-29 | -5.4 | 23.4 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -0.8 | 18.8 | 0 | 2018-12-29 | -10.3 | 28.3 | 0 | 2017-12-29 | -19.9 | 37.9 | 0 | 2016-12-29 | -3.4 | 21.4 | 0 | 21.2 | 0
2025-12-29 | -1.8 | 19.8 | 0 | 2024-12-29 | 1.8 | 16.2 | 0 | 2023-12-29 | 1.9 | 16.1 | 0 | 2022-12-29 | 5.6 | 12.4 | 0 | 2021-12-29 | -6.3 | 24.3 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -1 | 19 | 0 | 2018-12-29 | -10.8 | 28.8 | 0 | 2017-12-29 | -20 | 38 | 0 | 2016-12-29 | -3.3 | 21.3 | 0 | 21.39 | 0
2025-12-29 | -4.2 | 22.2 | 0 | 2024-12-29 | 2 | 16 | 0 | 2023-12-29 | 1.4 | 16.6 | 0 | 2022-12-29 | 5.7 | 12.3 | 0 | 2021-12-29 | -6.4 | 24.4 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -1.8 | 19.8 | 0 | 2018-12-29 | -11.3 | 29.3 | 0 | 2017-12-29 | -20.4 | 38.4 | 0 | 2016-12-29 | -4 | 22 | 0 | 21.9 | 0
2025-12-29 | -6.5 | 24.5 | 0 | 2024-12-29 | 2.1 | 15.9 | 0 | 2023-12-29 | 0.6 | 17.4 | 0 | 2022-12-29 | 6.1 | 11.9 | 0 | 2021-12-29 | -5.9 | 23.9 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -2.4 | 20.4 | 0 | 2018-12-29 | -11.6 | 29.6 | 0 | 2017-12-29 | -22.1 | 40.1 | 0 | 2016-12-29 | -4.3 | 22.3 | 0 | 22.4 | 0
2025-12-29 | -8.8 | 26.8 | 0 | 2024-12-29 | 2.4 | 15.6 | 0 | 2023-12-29 | 0.5 | 17.5 | 0 | 2022-12-29 | 5.8 | 12.2 | 0 | 2021-12-29 | -5.7 | 23.7 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -3.1 | 21.1 | 0 | 2018-12-29 | -12.1 | 30.1 | 0 | 2017-12-29 | -23.3 | 41.3 | 0 | 2016-12-29 | -4.2 | 22.2 | 0 | 22.85 | 0
2025-12-29 | -9.8 | 27.8 | 0 | 2024-12-29 | 2.6 | 15.4 | 0 | 2023-12-29 | 0.3 | 17.7 | 0 | 2022-12-29 | 5.5 | 12.5 | 0 | 2021-12-29 | -5.4 | 23.4 | 0 | 2020-12-29 | 0 | 18 | 0 | 2019-12-29 | -3.6 | 21.6 | 0 | 2018-12-29 | -12.3 | 30.3 | 0 | 2017-12-29 | -23.6 | 41.6 | 0 | 2016-12-29 | -3.7 | 21.7 | 0 | 23 | 0
2025-12-30 | -9.7 | 27.7 | 0 | 2024-12-30 | 2.8 | 15.2 | 0 | 2023-12-30 | -0.9 | 18.9 | 0 | 2022-12-30 | 5.8 | 12.2 | 0 | 2021-12-30 | -5.7 | 23.7 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4 | 22 | 0 | 2018-12-30 | -13.1 | 31.1 | 0 | 2017-12-30 | -25 | 43 | 0 | 2016-12-30 | -3.5 | 21.5 | 0 | 23.33 | 0
2025-12-30 | -10.4 | 28.4 | 0 | 2024-12-30 | 3.5 | 14.5 | 0 | 2023-12-30 | -0.3 | 18.3 | 0 | 2022-12-30 | 5.7 | 12.3 | 0 | 2021-12-30 | -5.7 | 23.7 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -3.9 | 21.9 | 0 | 2018-12-30 | -13.5 | 31.5 | 0 | 2017-12-30 | -25.7 | 43.7 | 0 | 2016-12-30 | -3.5 | 21.5 | 0 | 23.38 | 0
2025-12-30 | -11.1 | 29.1 | 0 | 2024-12-30 | 4.1 | 13.9 | 0 | 2023-12-30 | -0.2 | 18.2 | 0 | 2022-12-30 | 5.8 | 12.2 | 0 | 2021-12-30 | -5.7 | 23.7 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.4 | 22.4 | 0 | 2018-12-30 | -13.3 | 31.3 | 0 | 2017-12-30 | -24.2 | 42.2 | 0 | 2016-12-30 | -3.5 | 21.5 | 0 | 23.25 | 0
2025-12-30 | -11.7 | 29.7 | 0 | 2024-12-30 | 4.3 | 13.7 | 0 | 2023-12-30 | -0.5 | 18.5 | 0 | 2022-12-30 | 5.8 | 12.2 | 0 | 2021-12-30 | -5.7 | 23.7 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.3 | 22.3 | 0 | 2018-12-30 | -13.8 | 31.8 | 0 | 2017-12-30 | -25.8 | 43.8 | 0 | 2016-12-30 | -3.2 | 21.2 | 0 | 23.49 | 0
2025-12-30 | -12.1 | 30.1 | 0 | 2024-12-30 | 4.1 | 13.9 | 0 | 2023-12-30 | -0.8 | 18.8 | 0 | 2022-12-30 | 6.2 | 11.8 | 0 | 2021-12-30 | -5.8 | 23.8 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.2 | 22.2 | 0 | 2018-12-30 | -13.4 | 31.4 | 0 | 2017-12-30 | -24.6 | 42.6 | 0 | 2016-12-30 | -2.2 | 20.2 | 0 | 23.28 | 0
2025-12-30 | -12.7 | 30.7 | 0 | 2024-12-30 | 4.9 | 13.1 | 0 | 2023-12-30 | -0.9 | 18.9 | 0 | 2022-12-30 | 6.1 | 11.9 | 0 | 2021-12-30 | -5.6 | 23.6 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.2 | 22.2 | 0 | 2018-12-30 | -13.5 | 31.5 | 0 | 2017-12-30 | -25 | 43 | 0 | 2016-12-30 | -3.1 | 21.1 | 0 | 23.4 | 0
2025-12-30 | -13.4 | 31.4 | 0 | 2024-12-30 | 3.8 | 14.2 | 0 | 2023-12-30 | -1.2 | 19.2 | 0 | 2022-12-30 | 6.5 | 11.5 | 0 | 2021-12-30 | -5.5 | 23.5 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -3.9 | 21.9 | 0 | 2018-12-30 | -13.2 | 31.2 | 0 | 2017-12-30 | -24.5 | 42.5 | 0 | 2016-12-30 | -3 | 21 | 0 | 23.44 | 0
2025-12-30 | -13.6 | 31.6 | 0 | 2024-12-30 | 2.6 | 15.4 | 0 | 2023-12-30 | -1.8 | 19.8 | 0 | 2022-12-30 | 6.4 | 11.6 | 0 | 2021-12-30 | -5.6 | 23.6 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -3.9 | 21.9 | 0 | 2018-12-30 | -13.3 | 31.3 | 0 | 2017-12-30 | -23.9 | 41.9 | 0 | 2016-12-30 | -3.4 | 21.4 | 0 | 23.65 | 0
2025-12-30 | -14 | 32 | 0 | 2024-12-30 | 4.1 | 13.9 | 0 | 2023-12-30 | -2.1 | 20.1 | 0 | 2022-12-30 | 6.2 | 11.8 | 0 | 2021-12-30 | -5.5 | 23.5 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4 | 22 | 0 | 2018-12-30 | -13 | 31 | 0 | 2017-12-30 | -23.3 | 41.3 | 0 | 2016-12-30 | -4.7 | 22.7 | 0 | 23.63 | 0
2025-12-30 | -14.2 | 32.2 | 0 | 2024-12-30 | 6 | 12 | 0 | 2023-12-30 | -2.6 | 20.6 | 0 | 2022-12-30 | 6.7 | 11.3 | 0 | 2021-12-30 | -5.3 | 23.3 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.3 | 22.3 | 0 | 2018-12-30 | -12.4 | 30.4 | 0 | 2017-12-30 | -22 | 40 | 0 | 2016-12-30 | -5.2 | 23.2 | 0 | 23.33 | 0
2025-12-30 | -14.5 | 32.5 | 0 | 2024-12-30 | 6.2 | 11.8 | 0 | 2023-12-30 | -2.9 | 20.9 | 0 | 2022-12-30 | 7.2 | 10.8 | 0 | 2021-12-30 | -4.6 | 22.6 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -4.2 | 22.2 | 0 | 2018-12-30 | -11.9 | 29.9 | 0 | 2017-12-30 | -21.1 | 39.1 | 0 | 2016-12-30 | -6.4 | 24.4 | 0 | 23.22 | 0
2025-12-30 | -14.3 | 32.3 | 0 | 2024-12-30 | 6.5 | 11.5 | 0 | 2023-12-30 | -3.3 | 21.3 | 0 | 2022-12-30 | 7.2 | 10.8 | 0 | 2021-12-30 | -3.9 | 21.9 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -3.6 | 21.6 | 0 | 2018-12-30 | -11.2 | 29.2 | 0 | 2017-12-30 | -20 | 38 | 0 | 2016-12-30 | -7.1 | 25.1 | 0 | 22.97 | 0
2025-12-30 | -14.1 | 32.1 | 0 | 2024-12-30 | 7 | 11 | 0 | 2023-12-30 | -3.5 | 21.5 | 0 | 2022-12-30 | 7.5 | 10.5 | 0 | 2021-12-30 | -3 | 21 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -3.2 | 21.2 | 0 | 2018-12-30 | -10.4 | 28.4 | 0 | 2017-12-30 | -18.9 | 36.9 | 0 | 2016-12-30 | -7.3 | 25.3 | 0 | 22.59 | 0
2025-12-30 | -13.8 | 31.8 | 0 | 2024-12-30 | 5.9 | 12.1 | 0 | 2023-12-30 | -3.6 | 21.6 | 0 | 2022-12-30 | 9.2 | 8.8 | 0 | 2021-12-30 | -1.8 | 19.8 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -2.8 | 20.8 | 0 | 2018-12-30 | -9.3 | 27.3 | 0 | 2017-12-30 | -18.1 | 36.1 | 0 | 2016-12-30 | -7.3 | 25.3 | 0 | 22.16 | 0
2025-12-30 | -13.8 | 31.8 | 0 | 2024-12-30 | 4.8 | 13.2 | 0 | 2023-12-30 | -3.9 | 21.9 | 0 | 2022-12-30 | 9.5 | 8.5 | 0 | 2021-12-30 | -1 | 19 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -2.3 | 20.3 | 0 | 2018-12-30 | -8.2 | 26.2 | 0 | 2017-12-30 | -17.6 | 35.6 | 0 | 2016-12-30 | -7.6 | 25.6 | 0 | 22.01 | 0
2025-12-30 | -13.8 | 31.8 | 0 | 2024-12-30 | 3.3 | 14.7 | 0 | 2023-12-30 | -4.2 | 22.2 | 0 | 2022-12-30 | 8.4 | 9.6 | 0 | 2021-12-30 | -1 | 19 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -2.2 | 20.2 | 0 | 2018-12-30 | -8 | 26 | 0 | 2017-12-30 | -17.3 | 35.3 | 0 | 2016-12-30 | -8.1 | 26.1 | 0 | 22.29 | 0
2025-12-30 | -14.6 | 32.6 | 0 | 2024-12-30 | 2.8 | 15.2 | 0 | 2023-12-30 | -4 | 22 | 0 | 2022-12-30 | 8.2 | 9.8 | 0 | 2021-12-30 | -1.1 | 19.1 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.6 | 19.6 | 0 | 2018-12-30 | -7.7 | 25.7 | 0 | 2017-12-30 | -17.7 | 35.7 | 0 | 2016-12-30 | -8.3 | 26.3 | 0 | 22.4 | 0
2025-12-30 | -14.8 | 32.8 | 0 | 2024-12-30 | 2.9 | 15.1 | 0 | 2023-12-30 | -4.3 | 22.3 | 0 | 2022-12-30 | 7.9 | 10.1 | 0 | 2021-12-30 | -1.4 | 19.4 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.1 | 19.1 | 0 | 2018-12-30 | -7.2 | 25.2 | 0 | 2017-12-30 | -19.7 | 37.7 | 0 | 2016-12-30 | -8.6 | 26.6 | 0 | 22.63 | 0
2025-12-30 | -14.8 | 32.8 | 0 | 2024-12-30 | 3.1 | 14.9 | 0 | 2023-12-30 | -4.5 | 22.5 | 0 | 2022-12-30 | 7.7 | 10.3 | 0 | 2021-12-30 | -1.6 | 19.6 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.4 | 19.4 | 0 | 2018-12-30 | -7.2 | 25.2 | 0 | 2017-12-30 | -19.5 | 37.5 | 0 | 2016-12-30 | -8.7 | 26.7 | 0 | 22.69 | 0
2025-12-30 | -15 | 33 | 0 | 2024-12-30 | 2.8 | 15.2 | 0 | 2023-12-30 | -4.5 | 22.5 | 0 | 2022-12-30 | 7.4 | 10.6 | 0 | 2021-12-30 | -2 | 20 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.3 | 19.3 | 0 | 2018-12-30 | -7.5 | 25.5 | 0 | 2017-12-30 | -18.2 | 36.2 | 0 | 2016-12-30 | -9.4 | 27.4 | 0 | 22.77 | 0
2025-12-30 | -15.4 | 33.4 | 0 | 2024-12-30 | 2.4 | 15.6 | 0 | 2023-12-30 | -4.4 | 22.4 | 0 | 2022-12-30 | 7.7 | 10.3 | 0 | 2021-12-30 | -2.4 | 20.4 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1 | 19 | 0 | 2018-12-30 | -7.4 | 25.4 | 0 | 2017-12-30 | -18.7 | 36.7 | 0 | 2016-12-30 | -11.3 | 29.3 | 0 | 23.05 | 0
2025-12-30 | -15.4 | 33.4 | 0 | 2024-12-30 | 2.2 | 15.8 | 0 | 2023-12-30 | -4.4 | 22.4 | 0 | 2022-12-30 | 7.9 | 10.1 | 0 | 2021-12-30 | -2.4 | 20.4 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.2 | 19.2 | 0 | 2018-12-30 | -7.3 | 25.3 | 0 | 2017-12-30 | -20 | 38 | 0 | 2016-12-30 | -10.6 | 28.6 | 0 | 23.12 | 0
2025-12-30 | -15.2 | 33.2 | 0 | 2024-12-30 | 2.3 | 15.7 | 0 | 2023-12-30 | -4.5 | 22.5 | 0 | 2022-12-30 | 7.3 | 10.7 | 0 | 2021-12-30 | -3.1 | 21.1 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1 | 19 | 0 | 2018-12-30 | -7.2 | 25.2 | 0 | 2017-12-30 | -19.4 | 37.4 | 0 | 2016-12-30 | -11.6 | 29.6 | 0 | 23.24 | 0
2025-12-30 | -14.8 | 32.8 | 0 | 2024-12-30 | 2.2 | 15.8 | 0 | 2023-12-30 | -4.8 | 22.8 | 0 | 2022-12-30 | 7.2 | 10.8 | 0 | 2021-12-30 | -4.3 | 22.3 | 0 | 2020-12-30 | 0 | 18 | 0 | 2019-12-30 | -1.2 | 19.2 | 0 | 2018-12-30 | -7.2 | 25.2 | 0 | 2017-12-30 | -20.2 | 38.2 | 0 | 2016-12-30 | -13.5 | 31.5 | 0 | 23.66 | 0
2025-12-31 | -14.7 | 32.7 | 0 | 2024-12-31 | 2 | 16 | 0 | 2023-12-31 | -4.7 | 22.7 | 0 | 2022-12-31 | 6.9 | 11.1 | 0 | 2021-12-31 | -4.9 | 22.9 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.3 | 19.3 | 0 | 2018-12-31 | -7.1 | 25.1 | 0 | 2017-12-31 | -21.5 | 39.5 | 0 | 2016-12-31 | -13.8 | 31.8 | 0 | 23.91 | 0
2025-12-31 | -14.7 | 32.7 | 0 | 2024-12-31 | 2.1 | 15.9 | 0 | 2023-12-31 | -4.9 | 22.9 | 0 | 2022-12-31 | 6.9 | 11.1 | 0 | 2021-12-31 | -4.9 | 22.9 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.4 | 19.4 | 0 | 2018-12-31 | -6.9 | 24.9 | 0 | 2017-12-31 | -22.6 | 40.6 | 0 | 2016-12-31 | -14 | 32 | 0 | 24.04 | 0
2025-12-31 | -14.4 | 32.4 | 0 | 2024-12-31 | 2 | 16 | 0 | 2023-12-31 | -5 | 23 | 0 | 2022-12-31 | 6.8 | 11.2 | 0 | 2021-12-31 | -6.5 | 24.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.4 | 19.4 | 0 | 2018-12-31 | -6.7 | 24.7 | 0 | 2017-12-31 | -22.9 | 40.9 | 0 | 2016-12-31 | -16.2 | 34.2 | 0 | 24.43 | 0
2025-12-31 | -14.4 | 32.4 | 0 | 2024-12-31 | 2.2 | 15.8 | 0 | 2023-12-31 | -4.8 | 22.8 | 0 | 2022-12-31 | 6.4 | 11.6 | 0 | 2021-12-31 | -4.3 | 22.3 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.6 | 19.6 | 0 | 2018-12-31 | -6.7 | 24.7 | 0 | 2017-12-31 | -22.7 | 40.7 | 0 | 2016-12-31 | -15.6 | 33.6 | 0 | 24.15 | 0
2025-12-31 | -15.3 | 33.3 | 0 | 2024-12-31 | 2.1 | 15.9 | 0 | 2023-12-31 | -4.9 | 22.9 | 0 | 2022-12-31 | 6.6 | 11.4 | 0 | 2021-12-31 | -4.2 | 22.2 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.7 | 19.7 | 0 | 2018-12-31 | -6.7 | 24.7 | 0 | 2017-12-31 | -22.8 | 40.8 | 0 | 2016-12-31 | -15.7 | 33.7 | 0 | 24.26 | 0
2025-12-31 | -15.6 | 33.6 | 0 | 2024-12-31 | 2.3 | 15.7 | 0 | 2023-12-31 | -5.2 | 23.2 | 0 | 2022-12-31 | 6.2 | 11.8 | 0 | 2021-12-31 | -4.2 | 22.2 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.8 | 19.8 | 0 | 2018-12-31 | -6.5 | 24.5 | 0 | 2017-12-31 | -23.3 | 41.3 | 0 | 2016-12-31 | -14.4 | 32.4 | 0 | 24.25 | 0
2025-12-31 | -16.2 | 34.2 | 0 | 2024-12-31 | 2.4 | 15.6 | 0 | 2023-12-31 | -5.6 | 23.6 | 0 | 2022-12-31 | 6.4 | 11.6 | 0 | 2021-12-31 | -4 | 22 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.8 | 19.8 | 0 | 2018-12-31 | -6.4 | 24.4 | 0 | 2017-12-31 | -23.8 | 41.8 | 0 | 2016-12-31 | -13.5 | 31.5 | 0 | 24.25 | 0
2025-12-31 | -16.5 | 34.5 | 0 | 2024-12-31 | 2.5 | 15.5 | 0 | 2023-12-31 | -5.9 | 23.9 | 0 | 2022-12-31 | 6.2 | 11.8 | 0 | 2021-12-31 | -4.1 | 22.1 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.8 | 19.8 | 0 | 2018-12-31 | -6.1 | 24.1 | 0 | 2017-12-31 | -24.5 | 42.5 | 0 | 2016-12-31 | -13.2 | 31.2 | 0 | 24.34 | 0
2025-12-31 | -15.4 | 33.4 | 0 | 2024-12-31 | 2.4 | 15.6 | 0 | 2023-12-31 | -6.4 | 24.4 | 0 | 2022-12-31 | 4.2 | 13.8 | 0 | 2021-12-31 | -3.9 | 21.9 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -1.4 | 19.4 | 0 | 2018-12-31 | -5.9 | 23.9 | 0 | 2017-12-31 | -24.3 | 42.3 | 0 | 2016-12-31 | -12.6 | 30.6 | 0 | 24.33 | 0
2025-12-31 | -13.5 | 31.5 | 0 | 2024-12-31 | 2.6 | 15.4 | 0 | 2023-12-31 | -6.5 | 24.5 | 0 | 2022-12-31 | 5.3 | 12.7 | 0 | 2021-12-31 | -3.6 | 21.6 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.8 | 18.8 | 0 | 2018-12-31 | -5.5 | 23.5 | 0 | 2017-12-31 | -23.9 | 41.9 | 0 | 2016-12-31 | -12.3 | 30.3 | 0 | 23.82 | 0
2025-12-31 | -12 | 30 | 0 | 2024-12-31 | 4 | 14 | 0 | 2023-12-31 | -6 | 24 | 0 | 2022-12-31 | 4.9 | 13.1 | 0 | 2021-12-31 | -3 | 21 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.1 | 18.1 | 0 | 2018-12-31 | -4.2 | 22.2 | 0 | 2017-12-31 | -23.1 | 41.1 | 0 | 2016-12-31 | -11.5 | 29.5 | 0 | 23.1 | 0
2025-12-31 | -10.3 | 28.3 | 0 | 2024-12-31 | 3.5 | 14.5 | 0 | 2023-12-31 | -5.8 | 23.8 | 0 | 2022-12-31 | 5.8 | 12.2 | 0 | 2021-12-31 | -2.6 | 20.6 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.2 | 17.8 | 0 | 2018-12-31 | -2.7 | 20.7 | 0 | 2017-12-31 | -22.4 | 40.4 | 0 | 2016-12-31 | -11 | 29 | 0 | 22.53 | 0
2025-12-31 | -9.4 | 27.4 | 0 | 2024-12-31 | 4 | 14 | 0 | 2023-12-31 | -5.6 | 23.6 | 0 | 2022-12-31 | 6.7 | 11.3 | 0 | 2021-12-31 | -2.5 | 20.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.5 | 17.5 | 0 | 2018-12-31 | -1.4 | 19.4 | 0 | 2017-12-31 | -21.4 | 39.4 | 0 | 2016-12-31 | -10.6 | 28.6 | 0 | 21.97 | 0
2025-12-31 | -8.9 | 26.9 | 0 | 2024-12-31 | 4.2 | 13.8 | 0 | 2023-12-31 | -5.3 | 23.3 | 0 | 2022-12-31 | 6.2 | 11.8 | 0 | 2021-12-31 | -2 | 20 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.3 | 17.7 | 0 | 2018-12-31 | -0.4 | 18.4 | 0 | 2017-12-31 | -20.5 | 38.5 | 0 | 2016-12-31 | -10 | 28 | 0 | 21.64 | 0
2025-12-31 | -8.6 | 26.6 | 0 | 2024-12-31 | 4.4 | 13.6 | 0 | 2023-12-31 | -5.4 | 23.4 | 0 | 2022-12-31 | 5 | 13 | 0 | 2021-12-31 | -1.7 | 19.7 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.2 | 17.8 | 0 | 2018-12-31 | -0.4 | 18.4 | 0 | 2017-12-31 | -20.2 | 38.2 | 0 | 2016-12-31 | -10.1 | 28.1 | 0 | 21.68 | 0
2025-12-31 | -8.1 | 26.1 | 0 | 2024-12-31 | 4.4 | 13.6 | 0 | 2023-12-31 | -5.5 | 23.5 | 0 | 2022-12-31 | 5.6 | 12.4 | 0 | 2021-12-31 | -1.5 | 19.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.2 | 17.8 | 0 | 2018-12-31 | -0.5 | 18.5 | 0 | 2017-12-31 | -20.2 | 38.2 | 0 | 2016-12-31 | -10.1 | 28.1 | 0 | 21.57 | 0
2025-12-31 | -8.2 | 26.2 | 0 | 2024-12-31 | 3.5 | 14.5 | 0 | 2023-12-31 | -5.5 | 23.5 | 0 | 2022-12-31 | 4.8 | 13.2 | 0 | 2021-12-31 | -1.5 | 19.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.1 | 17.9 | 0 | 2018-12-31 | -1.2 | 19.2 | 0 | 2017-12-31 | -20.8 | 38.8 | 0 | 2016-12-31 | -9.4 | 27.4 | 0 | 21.82 | 0
2025-12-31 | -8.7 | 26.7 | 0 | 2024-12-31 | 2.8 | 15.2 | 0 | 2023-12-31 | -5.6 | 23.6 | 0 | 2022-12-31 | 4.6 | 13.4 | 0 | 2021-12-31 | -1.4 | 19.4 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.1 | 17.9 | 0 | 2018-12-31 | -1.9 | 19.9 | 0 | 2017-12-31 | -21.4 | 39.4 | 0 | 2016-12-31 | -9.3 | 27.3 | 0 | 22.08 | 0
2025-12-31 | -8.4 | 26.4 | 0 | 2024-12-31 | 2.4 | 15.6 | 0 | 2023-12-31 | -6 | 24 | 0 | 2022-12-31 | 4.1 | 13.9 | 0 | 2021-12-31 | -1.4 | 19.4 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.1 | 17.9 | 0 | 2018-12-31 | -2.3 | 20.3 | 0 | 2017-12-31 | -21.5 | 39.5 | 0 | 2016-12-31 | -8.9 | 26.9 | 0 | 22.19 | 0
2025-12-31 | -9.7 | 27.7 | 0 | 2024-12-31 | 2.1 | 15.9 | 0 | 2023-12-31 | -6.7 | 24.7 | 0 | 2022-12-31 | 4.3 | 13.7 | 0 | 2021-12-31 | -1.5 | 19.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | 0.1 | 17.9 | 0 | 2018-12-31 | -2.5 | 20.5 | 0 | 2017-12-31 | -21.4 | 39.4 | 0 | 2016-12-31 | -8.6 | 26.6 | 0 | 22.39 | 0
2025-12-31 | -10 | 28 | 0 | 2024-12-31 | 2.4 | 15.6 | 0 | 2023-12-31 | -6.6 | 24.6 | 0 | 2022-12-31 | 4.6 | 13.4 | 0 | 2021-12-31 | -1.6 | 19.6 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.2 | 18.2 | 0 | 2018-12-31 | -2.4 | 20.4 | 0 | 2017-12-31 | -21.9 | 39.9 | 0 | 2016-12-31 | -8.8 | 26.8 | 0 | 22.45 | 0
2025-12-31 | -10.3 | 28.3 | 0 | 2024-12-31 | 2.2 | 15.8 | 0 | 2023-12-31 | -8 | 26 | 0 | 2022-12-31 | 3.7 | 14.3 | 0 | 2021-12-31 | -1.5 | 19.5 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.4 | 18.4 | 0 | 2018-12-31 | -3.1 | 21.1 | 0 | 2017-12-31 | -21.9 | 39.9 | 0 | 2016-12-31 | -8.6 | 26.6 | 0 | 22.79 | 0
2025-12-31 | -10.6 | 28.6 | 0 | 2024-12-31 | 2.4 | 15.6 | 0 | 2023-12-31 | -7.5 | 25.5 | 0 | 2022-12-31 | 3 | 15 | 0 | 2021-12-31 | -1.7 | 19.7 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.7 | 18.7 | 0 | 2018-12-31 | -2.7 | 20.7 | 0 | 2017-12-31 | -23.2 | 41.2 | 0 | 2016-12-31 | -8.4 | 26.4 | 0 | 22.94 | 0
2025-12-31 | -10.5 | 28.5 | 0 | 2024-12-31 | 1.8 | 16.2 | 0 | 2023-12-31 | -6.7 | 24.7 | 0 | 2022-12-31 | 3.1 | 14.9 | 0 | 2021-12-31 | -1.7 | 19.7 | 0 | 2020-12-31 | 0 | 18 | 0 | 2019-12-31 | -0.9 | 18.9 | 0 | 2018-12-31 | -2.1 | 20.1 | 0 | 2017-12-31 | -24.2 | 42.2 | 0 | 2016-12-31 | -8.2 | 26.2 | 0 | 22.94 | 0

## RES_Model_Actual
Date | Res Load | Actual HDD | Actual CDD | Weekend | H0 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8 | H9 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | Res Predicted | H23 | H22 | H21 | H20 | H19 | H18 | H17 | H16 | H15 | H14 | H13 | H12 | H11 | H10 | H9 | H8 | H7 | H6 | H5 | H4 | H3 | H2 | H1 | H0 | Weekend | CDD | HDD | Intercept | <- Hidden Col | Intercept | 2994.0028
2025-01-01 | 5061.0771 | 16.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4690.9951 | 234.6959 | 743.1552 | 1367.3533 | 1902.7907 | 2137.6977 | 2167.3275 | 2155.6213 | 1932.1676 | 1371.4494 | 984.7791 | 898.4894 | 960.834 | 1062.4519 | 1062.6118 | 1055.2688 | 1002.1522 | 789.8751 | 405.8476 | 0 | -329.7617 | -475.8154 | -448.7372 | -331.0276 | -118.0594 | 278.4744 | 367.1368 | 110.0031 | 2994.0028 |  | HDD | 110.0031
2025-01-01 | 4773.3872 | 16.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4445.026 | 52.8441 | 52.8537 | 52.8696 | 52.8952 | 52.9604 | 53.0731 | 53.2116 | 53.2844 | 53.3099 | 53.291 | 53.2432 | 53.1592 | 53.0552 | 52.9639 | 52.8926 | 52.8505 | 52.8344 | 52.8296 | 0 | 52.8292 | 52.8297 | 52.8317 | 52.8346 | 52.8392 | 16.8974 | 3.2112 | 0.77564 | 39.4855 |  | CDD | 367.1368
2025-01-01 | 4532.144 | 16.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4338.3167 | 0.8154 | 713.6804 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | Weekend | 278.4744
2025-01-01 | 4422.4941 | 16.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4311.2385 | 1483.6026 | 8733 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | H0 | -118.0594
2025-01-01 | 4439.2852 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4446.2919 | 19647101582.6013 | 4448064019.81 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | H1 | -331.0276
2025-01-01 | 4524.3828 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4820.0549 | [29 empty] | H2 | -448.7372
2025-01-01 | 4716.9878 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5291.9044 | [29 empty] | H3 | -475.8154
2025-01-01 | 4937.1699 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5631.9306 | [29 empty] | H4 | -329.7617
2025-01-01 | 5460.3691 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5833.2074 | [29 empty] | H5 | 0
2025-01-01 | 6072.519 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5875.3237 | [29 empty] | H6 | 405.8476
2025-01-01 | 6554.8252 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5981.6695 | [29 empty] | H7 | 789.8751
2025-01-01 | 7009.3398 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6025.5108 | [29 empty] | H8 | 1002.1522
2025-01-01 | 7151.6792 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5934.8933 | [29 empty] | H9 | 1055.2688
2025-01-01 | 7131.4199 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5861.5483 | [29 empty] | H10 | 1062.6118
2025-01-01 | 7099.2319 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5947.838 | [29 empty] | H11 | 1062.4519
2025-01-01 | 7370.6719 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6334.5083 | [29 empty] | H12 | 960.834
2025-01-01 | 7883.644 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6884.2263 | [29 empty] | H13 | 898.4894
2025-01-01 | 8038.5249 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7096.6796 | [29 empty] | H14 | 984.7791
2025-01-01 | 7530.8672 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7108.3858 | [29 empty] | H15 | 1371.4494
2025-01-01 | 7360.249 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7078.756 | [29 empty] | H16 | 1932.1676
2025-01-01 | 7098.084 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6865.8497 | [29 empty] | H17 | 2155.6213
2025-01-01 | 6740.9048 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6352.4129 | [29 empty] | H18 | 2167.3275
2025-01-01 | 6221.3071 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5783.2163 | [29 empty] | H19 | 2137.6977
2025-01-01 | 5572.9771 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5307.7579 | [29 empty] | H20 | 1902.7907
2025-01-02 | 5187.6279 | 19.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5010.0042 | [29 empty] | H21 | 1367.3533
2025-01-02 | 4939.9448 | 19.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4841.0373 | [29 empty] | H22 | 743.1552
2025-01-02 | 4792.709 | 19.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.328 | [29 empty] | H23 | 234.6959
2025-01-02 | 4831.5229 | 19.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4685.2492
2025-01-02 | 4889.7329 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4842.3032
2025-01-02 | 5196.0991 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5183.0652 | [29 empty] | H5 | The regression includes a full set of 24 hourly indicator variables.
2025-01-02 | 5604.9492 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5577.9125 | [30 empty] | Because those indicators sum to one in every observation, including a separate intercept would create perfect multicollinearity.
2025-01-02 | 5927.0771 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994.941 | [30 empty] | Accordingly, the model is estimated without an intercept so that each hourly coefficient represents the average load in that hour.
2025-01-02 | 6241.8652 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6240.219 | [30 empty] | For this reason, H5 is zero
2025-01-02 | 6340.1899 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6249.3343
2025-01-02 | 6436.0322 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6245.677
2025-01-02 | 6330.0078 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6234.5168
2025-01-02 | 6320.1538 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6099.898
2025-01-02 | 6336.3252 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6026.553
2025-01-02 | 6429.2651 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6123.8431
2025-01-02 | 6614.1748 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6543.5143
2025-01-02 | 7448.9849 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7137.2335
2025-01-02 | 8180.1289 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7437.6893
2025-01-02 | 8009.1108 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7504.3971
2025-01-02 | 7803.5161 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7496.7679
2025-01-02 | 7524.752 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7272.8613
2025-01-02 | 7060.5962 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6770.4248
2025-01-02 | 6421.9531 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6080.2248
2025-01-02 | 5935.0591 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5593.7661
2025-01-03 | 5564.894 | 21.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5274.0117
2025-01-03 | 5319.9141 | 23.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.0476
2025-01-03 | 5179.3408 | 23.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5130.3393
2025-01-03 | 5139.9019 | 23.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5114.2614
2025-01-03 | 5265.812 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5315.3166
2025-01-03 | 5527.75 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5700.0799
2025-01-03 | 5907.0791 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6127.9282
2025-01-03 | 6273.5718 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6555.9569
2025-01-03 | 6556.1431 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6856.2365
2025-01-03 | 6544.7388 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6876.3522
2025-01-03 | 6532.3379 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.6952
2025-01-03 | 6451.8208 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6806.5331
2025-01-03 | 6320.6611 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6770.9171
2025-01-03 | 6283.7041 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6697.5721
2025-01-03 | 6271.23 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6827.8631
2025-01-03 | 6535.1318 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7170.5321
2025-01-03 | 7329.6621 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7797.2523
2025-01-03 | 8117.2002 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8108.7084
2025-01-03 | 8120.292 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8241.4181
2025-01-03 | 8108.8281 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8211.7883
2025-01-03 | 7964.7021 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7987.8816
2025-01-03 | 7602.0308 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7452.4442
2025-01-03 | 7078.0981 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6850.2467
2025-01-03 | 6565.8608 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6374.7883
2025-01-04 | 6181.0029 | 29.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6366.5093
2025-01-04 | 5954.0361 | 30.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6307.5455
2025-01-04 | 5791.7412 | 31 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6233.8372
2025-01-04 | 5742.5098 | 30.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6173.7581
2025-01-04 | 5853.2422 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6352.8127
2025-01-04 | 6044.0518 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6682.5744
2025-01-04 | 6205.1621 | 31.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7110.4227
2025-01-04 | 6840.707 | 31.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7483.4499
2025-01-04 | 7706.3291 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7684.7266
2025-01-04 | 7984.9878 | 30.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7693.842
2025-01-04 | 8221.7744 | 30.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7668.1841
2025-01-04 | 8402.6914 | 29.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7624.0229
2025-01-04 | 8430.709 | 29.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7478.4037
2025-01-04 | 8170.9009 | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7361.0575
2025-01-04 | 8106.1362 | 28.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7403.346
2025-01-04 | 8205.4053 | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7724.0144
2025-01-04 | 8729.7773 | 27.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8262.732
2025-01-04 | 9067.8789 | 28.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8541.1872
2025-01-04 | 8821.1279 | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8519.8925
2025-01-04 | 8413.9756 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8512.2634
2025-01-04 | 8059.3628 | 27.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8244.3554
2025-01-04 | 7656.6211 | 27.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7686.9174
2025-01-04 | 7125.6621 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7117.7209
2025-01-04 | 6587.6709 | 28 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6587.2609
2025-01-05 | 6106.8818 | 28.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6245.5059
2025-01-05 | 5846.751 | 28 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6021.5374
2025-01-05 | 5670.8491 | 27.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5881.8272
2025-01-05 | 5583.5991 | 28.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5942.7515
2025-01-05 | 5616.6089 | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6132.8064
2025-01-05 | 5811.6699 | 29.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6473.5685
2025-01-05 | 6104.6958 | 29.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6934.4177
2025-01-05 | 6561.7588 | 29.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7340.4458
2025-01-05 | 7176.8179 | 30.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7607.7244
2025-01-05 | 7641.8579 | 30.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7726.8429
2025-01-05 | 8068.437 | 31.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7756.1866
2025-01-05 | 8445.7402 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7745.0263
2025-01-05 | 8523.8184 | 30.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7610.4075
2025-01-05 | 8384.1699 | 30.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7526.0622
2025-01-05 | 8164.728 | 30.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7612.352
2025-01-05 | 8354.6982 | 30.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7966.0213
2025-01-05 | 9197.7529 | 30.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8537.7399
2025-01-05 | 9839.6416 | 31.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8882.1969
2025-01-05 | 9521.2793 | 31.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8904.9035
2025-01-05 | 9188.5918 | 31.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8831.2725
2025-01-05 | 8798.542 | 32.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8717.3689
2025-01-05 | 8254.2754 | 32.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8214.9325
2025-01-05 | 7536.8452 | 31.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7524.7325
2025-01-05 | 6906.1221 | 32.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7082.275
2025-01-06 | 6525.439 | 33.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6528.0474
2025-01-06 | 6306.6851 | 34.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6414.0821
2025-01-06 | 6313.1211 | 34.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6318.3731
2025-01-06 | 6391.9878 | 35.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6401.2981
2025-01-06 | 6472.251 | 35.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6525.3511
2025-01-06 | 6889.0308 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6756.11
2025-01-06 | 7409.8179 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7249.9601
2025-01-06 | 7711.73 | 34.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7611.987
2025-01-06 | 7884.4038 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7758.2622
2025-01-06 | 7645.2451 | 32.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7613.3732
2025-01-06 | 7597.2632 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7587.7153
2025-01-06 | 7559.1909 | 31.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7499.5528
2025-01-06 | 7722.1841 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7331.9331
2025-01-06 | 7669.2549 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7203.5865
2025-01-06 | 7582.0859 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7168.8728
2025-01-06 | 7746.291 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7478.5409
2025-01-06 | 8687.4111 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8006.2582
2025-01-06 | 9451.4453 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8218.7115
2025-01-06 | 9282.042 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8241.4181
2025-01-06 | 9019.2939 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8288.7905
2025-01-06 | 8782.8359 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8075.8841
2025-01-06 | 8209.6709 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7584.448
2025-01-06 | 7426.6641 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6982.2505
2025-01-06 | 6864.458 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6429.7899
2025-01-07 | 6484.5098 | 28.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6055.034
2025-01-07 | 6301.835 | 28.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5831.0655
2025-01-07 | 6247.0122 | 28.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5713.3559
2025-01-07 | 6145.6338 | 28.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5664.2771
2025-01-07 | 6288.728 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5799.3304
2025-01-07 | 6574.1982 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6151.0928
2025-01-07 | 7054.5308 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6556.9404
2025-01-07 | 7411.938 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6951.9682
2025-01-07 | 7608.604 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7208.2465
2025-01-07 | 7530.9141 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7239.3625
2025-01-07 | 7492.479 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7180.7037
2025-01-07 | 7454.4678 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7114.5419
2025-01-07 | 7448.0918 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6924.9215
2025-01-07 | 7260.2471 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6785.5746
2025-01-07 | 7272.6509 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6794.8622
2025-01-07 | 7540.8389 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7115.5306
2025-01-07 | 8337.0137 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7676.2488
2025-01-07 | 9243.5518 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7998.7053
2025-01-07 | 9210.4678 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8054.4128
2025-01-07 | 9058.3701 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8112.7855
2025-01-07 | 8789.3633 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7998.8819
2025-01-07 | 8321.3906 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7584.448
2025-01-07 | 7573.9292 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7004.2511
2025-01-07 | 6953.1001 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6561.7937
2025-01-08 | 6627.5762 | 30.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6264.0399
2025-01-08 | 6423.4028 | 31.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6117.0736
2025-01-08 | 6353.1001 | 32.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6076.3662
2025-01-08 | 6290.3921 | 32.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6104.2896
2025-01-08 | 6462.4839 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6327.3455
2025-01-08 | 6812.5132 | 33.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6723.1091
2025-01-08 | 7364.6958 | 33.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7128.9567
2025-01-08 | 7697.7231 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7523.9845
2025-01-08 | 8016.291 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.2619
2025-01-08 | 7955.0708 | 33.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7778.3779
2025-01-08 | 7825.6982 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7752.72
2025-01-08 | 7842.4629 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7708.5588
2025-01-08 | 7779.874 | 32.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7551.9393
2025-01-08 | 7682.9238 | 32.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7445.5934
2025-01-08 | 7693.5771 | 31.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7410.8797
2025-01-08 | 7962.228 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7742.5484
2025-01-08 | 8831.0547 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8259.2654
2025-01-08 | 9595.5635 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8449.7181
2025-01-08 | 9470.3223 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8406.4228
2025-01-08 | 9408.4082 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8365.7927
2025-01-08 | 9041.9141 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8130.8857
2025-01-08 | 8539.376 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7628.4492
2025-01-08 | 7767.4741 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7048.2524
2025-01-08 | 7104.8501 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6583.7943
2025-01-09 | 6713.2778 | 31.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6297.0409
2025-01-09 | 6509.2881 | 31.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6139.0742
2025-01-09 | 6414.8999 | 31.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6021.3647
2025-01-09 | 6362.4072 | 31.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5983.2862
2025-01-09 | 6502.3252 | 31.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6140.3402
2025-01-09 | 6880.9131 | 31.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6492.1025
2025-01-09 | 7416.8882 | 32.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6963.952
2025-01-09 | 7751.4238 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7369.9801
2025-01-09 | 7853.8008 | 32.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7549.2562
2025-01-09 | 7714.8628 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7580.3722
2025-01-09 | 7544.0718 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7444.7112
2025-01-09 | 7423.54 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7345.5484
2025-01-09 | 7245.29 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7111.9268
2025-01-09 | 7011.6328 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6862.5768
2025-01-09 | 6959.4102 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6783.8619
2025-01-09 | 7251.791 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7104.5303
2025-01-09 | 8137.2979 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7643.2479
2025-01-09 | 8946.3369 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7910.7028
2025-01-09 | 8915.7725 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7944.4096
2025-01-09 | 8932.3477 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7958.7811
2025-01-09 | 8688.0225 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7844.8776
2025-01-09 | 8149.1699 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7342.4411
2025-01-09 | 7373.0352 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6795.2452
2025-01-09 | 6751.5142 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6330.7871
2025-01-10 | 6456.228 | 28.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6022.033
2025-01-10 | 6232.5889 | 29.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5886.067
2025-01-10 | 6110.915 | 29.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.359
2025-01-10 | 6152.2441 | 30.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5851.2824
2025-01-10 | 6269.9399 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6019.3367
2025-01-10 | 6593.3638 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6382.0994
2025-01-10 | 7008.1602 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6798.9473
2025-01-10 | 7505.3071 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7248.9767
2025-01-10 | 7596.4829 | 31.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7428.2528
2025-01-10 | 7262.6821 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7404.3672
2025-01-10 | 7030.3159 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7312.7074
2025-01-10 | 6893.9282 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7158.5431
2025-01-10 | 6766.9409 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6902.9208
2025-01-10 | 6588.8379 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6741.5734
2025-01-10 | 6678.7559 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6750.8609
2025-01-10 | 6888.9121 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7060.529
2025-01-10 | 7595.4951 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7687.2491
2025-01-10 | 8395.083 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7965.7043
2025-01-10 | 8212.458 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8098.414
2025-01-10 | 8144.4409 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8002.7823
2025-01-10 | 7937.2959 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7756.875
2025-01-10 | 7503.688 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7210.4373
2025-01-10 | 6893.314 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6630.2405
2025-01-10 | 6393.3921 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6088.7802
2025-01-11 | 5966.6421 | 26.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6047.5003
2025-01-11 | 5676.9761 | 25.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5790.5308
2025-01-11 | 5547.6729 | 25.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5628.82
2025-01-11 | 5496.3032 | 25.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5601.7418
2025-01-11 | 5526.5322 | 25.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5769.7961
2025-01-11 | 5658.6289 | 26 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6132.5588
2025-01-11 | 5975.4409 | 25.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6494.4051
2025-01-11 | 6532.3979 | 25.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6867.4323
2025-01-11 | 7133.0298 | 25.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7057.7088
2025-01-11 | 7624.7661 | 24.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7066.8241
2025-01-11 | 7796.1548 | 24.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7030.1659
2025-01-11 | 8009.1528 | 23.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6953.0038
2025-01-11 | 7874.2881 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6873.3865
2025-01-11 | 7629.1802 | 23.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6712.0391
2025-01-11 | 7470.7358 | 22.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6721.3266
2025-01-11 | 7575.6802 | 22.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7096.9965
2025-01-11 | 8118.8979 | 22.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7668.7151
2025-01-11 | 8666.3213 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8057.1734
2025-01-11 | 8289.9824 | 25.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8211.8838
2025-01-11 | 8008.4058 | 26.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8281.2568
2025-01-11 | 7735.4551 | 25.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7980.3479
2025-01-11 | 7250.9819 | 25.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7477.9115
2025-01-11 | 6797.3418 | 27.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7029.7184
2025-01-11 | 6308.6538 | 26 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6367.2546
2025-01-12 | 5934.4121 | 27.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6168.5037
2025-01-12 | 5604.0322 | 26.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.5318
2025-01-12 | 5532.23 | 25.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5661.8209
2025-01-12 | 5516.2412 | 28.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.7509
2025-01-12 | 5608.0591 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5901.7999
2025-01-12 | 5773.6299 | 27.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6319.5641
2025-01-12 | 5996.6582 | 28.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6802.4139
2025-01-12 | 6476.603 | 25.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6878.4326
2025-01-12 | 7148.0049 | 25.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7046.7084
2025-01-12 | 7683.1768 | 24.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7055.8238
2025-01-12 | 7912.3188 | 24.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7019.1656
2025-01-12 | 8059.8691 | 24.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6986.0047
2025-01-12 | 8055.0049 | 23.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6807.3846
2025-01-12 | 7970.4771 | 23.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6723.0394
2025-01-12 | 7828.8252 | 22.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6754.3275
2025-01-12 | 7961.2061 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.9972
2025-01-12 | 8480.3584 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7679.7154
2025-01-12 | 8929.9824 | 22.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7892.1687
2025-01-12 | 8830.96 | 23.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8024.8784
2025-01-12 | 8382.7471 | 23.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8017.2493
2025-01-12 | 7985.6602 | 23.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7727.3407
2025-01-12 | 7451.915 | 23.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7257.9052
2025-01-12 | 6739.4048 | 23.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6611.7065
2025-01-12 | 6090.6548 | 23.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6114.2474
2025-01-13 | 5651.5459 | 23.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5472.0174
2025-01-13 | 5378.2632 | 23.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5259.0492
2025-01-13 | 5249.6709 | 23.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5130.3393
2025-01-13 | 5236.832 | 23.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5081.2605
2025-01-13 | 5331.0679 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5227.3141
2025-01-13 | 5698.502 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5557.0759
2025-01-13 | 6088.8389 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5962.9235
2025-01-13 | 6427.7051 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6346.951
2025-01-13 | 6601.687 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6537.2274
2025-01-13 | 6522.2871 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6535.3425
2025-01-13 | 6599.5078 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6465.6833
2025-01-13 | 6596.791 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6388.5212
2025-01-13 | 6482.1411 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6220.9014
2025-01-13 | 6391.1831 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6103.5552
2025-01-13 | 6426.9868 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6057.8412
2025-01-13 | 6762.4019 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6345.5086
2025-01-13 | 7442.3442 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.2278
2025-01-13 | 8100.6919 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7173.6818
2025-01-13 | 8039.5278 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7240.3896
2025-01-13 | 7932.0928 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7254.761
2025-01-13 | 7666.772 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7041.8547
2025-01-13 | 7161.7021 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6561.4189
2025-01-13 | 6449.0322 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5959.2214
2025-01-13 | 5872.5161 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5505.7636
2025-01-14 | 5560.7339 | 21 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5186.0092
2025-01-14 | 5321.3071 | 21.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5017.0423
2025-01-14 | 5237.5181 | 22.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4987.3352
2025-01-14 | 5248.7988 | 22.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4993.258
2025-01-14 | 5447.0269 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5161.3123
2025-01-14 | 5748.5498 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5524.0749
2025-01-14 | 6275.4258 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5962.9235
2025-01-14 | 6682.9209 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6357.9513
2025-01-14 | 6768.1738 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6592.229
2025-01-14 | 6706.6421 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6689.3468
2025-01-14 | 6568.604 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6718.6905
2025-01-14 | 6460.9619 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6696.5299
2025-01-14 | 6561.0381 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6561.9111
2025-01-14 | 6468.2061 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6433.5646
2025-01-14 | 6551.5771 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6530.8546
2025-01-14 | 6879.6709 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6884.524
2025-01-14 | 7805.3032 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7467.2429
2025-01-14 | 8551.0078 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7734.6977
2025-01-14 | 8481.5439 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7779.4049
2025-01-14 | 8410.1602 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7826.7773
2025-01-14 | 8135.8511 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7701.8735
2025-01-14 | 7659.0752 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7177.4364
2025-01-14 | 7002.7158 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6597.2395
2025-01-14 | 6467.166 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6121.7811
2025-01-15 | 6064.5659 | 26.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5802.0268
2025-01-15 | 5801.8682 | 27.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5732.0626
2025-01-15 | 5745.77 | 28.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5713.3559
2025-01-15 | 5727.9141 | 29.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.279
2025-01-15 | 5876.3892 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5876.3326
2025-01-15 | 6271.0981 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6118.0918
2025-01-15 | 6775.8169 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6479.9382
2025-01-15 | 7133.606 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6852.9654
2025-01-15 | 7213.3691 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7043.2418
2025-01-15 | 7211.4658 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7085.3581
2025-01-15 | 6918.3989 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7081.7009
2025-01-15 | 6690.5552 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7015.539
2025-01-15 | 6645.2241 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6814.9183
2025-01-15 | 6489.9692 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6708.5724
2025-01-15 | 6628.7539 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6750.8609
2025-01-15 | 6939.9058 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7170.5321
2025-01-15 | 7624.3892 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7764.2513
2025-01-15 | 8482.8555 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8196.7109
2025-01-15 | 8288.083 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8208.4172
2025-01-15 | 8291.501 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8233.7889
2025-01-15 | 8086.2041 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8097.8848
2025-01-15 | 7535.7671 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7496.4455
2025-01-15 | 7009.6279 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6784.2449
2025-01-15 | 6232.7939 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6297.7861
2025-01-16 | 5851.5898 | 27 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5846.028
2025-01-16 | 5595.6641 | 27.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5644.0601
2025-01-16 | 5462.8579 | 26.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5416.3474
2025-01-16 | 5427.0332 | 25.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5279.2661
2025-01-16 | 5568 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5403.3192
2025-01-16 | 5965.3799 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5733.0809
2025-01-16 | 6389.6372 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6127.9282
2025-01-16 | 6753.3501 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6533.9563
2025-01-16 | 7026.4761 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6801.2349
2025-01-16 | 6955.3931 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6821.3506
2025-01-16 | 6823.4561 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6784.6924
2025-01-16 | 6800.853 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6718.5306
2025-01-16 | 6731.6748 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6528.9102
2025-01-16 | 6488.2822 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6378.563
2025-01-16 | 6587.106 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6420.8515
2025-01-16 | 6873.3188 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6774.5209
2025-01-16 | 7605.9248 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7390.2407
2025-01-16 | 8433.4678 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7679.6962
2025-01-16 | 8249.8633 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7801.4056
2025-01-16 | 8242.6953 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7804.7767
2025-01-16 | 7893.0918 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7580.87
2025-01-16 | 7495.5259 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7056.433
2025-01-16 | 6898.3848 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6432.2348
2025-01-16 | 6264.5962 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5923.7755
2025-01-17 | 5724.1128 | 24.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5593.0208
2025-01-17 | 5615.668 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5413.0535
2025-01-17 | 5508.019 | 24.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5284.3437
2025-01-17 | 5381.6211 | 25.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5290.2664
2025-01-17 | 5514.1279 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5502.322
2025-01-17 | 5876.0469 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.0821
2025-01-17 | 6182.0181 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6149.9288
2025-01-17 | 6603.3008 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6555.9569
2025-01-17 | 6903.4199 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6735.2331
2025-01-17 | 6824.521 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6722.3478
2025-01-17 | 6504.4292 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6619.6877
2025-01-17 | 6857.5488 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6520.5249
2025-01-17 | 6522.748 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6319.9042
2025-01-17 | 6394.3711 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6169.5571
2025-01-17 | 6390.751 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6200.8452
2025-01-17 | 6559.8472 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6554.5146
2025-01-17 | 7137.2822 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7137.2335
2025-01-17 | 7788.5068 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7371.6874
2025-01-17 | 7679.52 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7350.3927
2025-01-17 | 7513.229 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7276.7617
2025-01-17 | 7352.4932 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6986.8531
2025-01-17 | 6934.4312 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6418.4148
2025-01-17 | 6417.0068 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5750.2154
2025-01-17 | 5902.9961 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5186.7545
2025-01-18 | 5523.3242 | 17.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5090.473
2025-01-18 | 5233.6509 | 17.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4877.5048
2025-01-18 | 5089.791 | 17.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4781.7959
2025-01-18 | 4966.4409 | 18 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4776.7183
2025-01-18 | 5084.4512 | 17.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4889.771
2025-01-18 | 5183.7119 | 17.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5197.5321
2025-01-18 | 5404.3779 | 17.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5603.3797
2025-01-18 | 5887.5 | 17.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5998.4076
2025-01-18 | 6567.4912 | 16.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6133.6824
2025-01-18 | 6918.4019 | 16.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6098.7965
2025-01-18 | 7156.335 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6172.1415
2025-01-18 | 7489.7129 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6182.9818
2025-01-18 | 7503.6602 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6103.3646
2025-01-18 | 7329.084 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6085.0212
2025-01-18 | 7223.1768 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6171.3109
2025-01-18 | 7291.9282 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6557.9812
2025-01-18 | 7812.2529 | 17.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7151.7004
2025-01-18 | 7996.9399 | 17.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7386.1543
2025-01-18 | 7766.252 | 17.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7375.86
2025-01-18 | 7452.0288 | 17.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7335.2298
2025-01-18 | 7157.188 | 19 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7265.3276
2025-01-18 | 6776.459 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6916.8955
2025-01-18 | 6342.4072 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6490.703
2025-01-18 | 5916.021 | 23.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6114.2474
2025-01-19 | 5381.8281 | 25.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5948.4974
2025-01-19 | 5402.5142 | 27 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5911.5343
2025-01-19 | 5350.2002 | 28.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5914.8282
2025-01-19 | 5365.9531 | 29 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5986.7528
2025-01-19 | 5471.3608 | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6132.8064
2025-01-19 | 5719.6548 | 29.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6484.5688
2025-01-19 | 6265.0098 | 29.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6956.4183
2025-01-19 | 6653.8701 | 31.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7505.4505
2025-01-19 | 7403.5078 | 32.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7871.7319
2025-01-19 | 7951.9922 | 32.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7935.8489
2025-01-19 | 8073.7178 | 32.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7888.1903
2025-01-19 | 8232.9014 | 31.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7789.0276
2025-01-19 | 8238.3369 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7643.4084
2025-01-19 | 8334.123 | 30.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7570.0635
2025-01-19 | 8271.0293 | 30.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7645.3529
2025-01-19 | 8484.9229 | 30.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7955.021
2025-01-19 | 9041.8828 | 29.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8482.7383
2025-01-19 | 9698.418 | 29.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8717.1922
2025-01-19 | 9279.9502 | 29.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8706.8979
2025-01-19 | 9151.6338 | 29.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8677.2681
2025-01-19 | 8711.0146 | 29.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8431.3608
2025-01-19 | 8281.9912 | 29.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7928.9243
2025-01-19 | 7505.5098 | 30.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7370.7281
2025-01-19 | 6793.187 | 30.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6906.27
2025-01-20 | 6461.1948 | 31.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6330.0418
2025-01-20 | 6205.7139 | 32 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6183.0755
2025-01-20 | 6161.5952 | 33 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6175.3691
2025-01-20 | 6120.105 | 33.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6225.2931
2025-01-20 | 6314.603 | 34.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6448.3489
2025-01-20 | 6773.5161 | 35.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6888.1138
2025-01-20 | 7313.8369 | 36.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7403.9645
2025-01-20 | 7644.1001 | 36.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7831.9933
2025-01-20 | 7813.0718 | 37.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8143.2732
2025-01-20 | 7667.8691 | 36.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8042.3854
2025-01-20 | 7464.437 | 35.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8005.7272
2025-01-20 | 7276.439 | 35.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7939.5654
2025-01-20 | 7193.6572 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7749.945
2025-01-20 | 7074.7012 | 33.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7621.5985
2025-01-20 | 7084.0039 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7674.8872
2025-01-20 | 7400.3208 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.5566
2025-01-20 | 8235.2344 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8545.2736
2025-01-20 | 9261.2402 | 33.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8823.7288
2025-01-20 | 9240.8037 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9000.4397
2025-01-20 | 9127.5439 | 35.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9080.8131
2025-01-20 | 8897.2393 | 35.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8801.9048
2025-01-20 | 8429.7383 | 36.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8376.4706
2025-01-20 | 7671.9819 | 34.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7521.2659
2025-01-20 | 7081.3608 | 34.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7034.8071
2025-01-21 | 6780.7021 | 33.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6605.0496
2025-01-21 | 6673.5049 | 34.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6436.0827
2025-01-21 | 6601.9658 | 34 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6285.3722
2025-01-21 | 6531.2319 | 34.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6313.2956
2025-01-21 | 6721.937 | 35.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6602.3533
2025-01-21 | 7033.02 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7064.1188
2025-01-21 | 7537.166 | 37.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7480.9667
2025-01-21 | 7828.4419 | 37.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.9958
2025-01-21 | 7927.5298 | 37.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8132.2729
2025-01-21 | 7582.3662 | 35.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7976.3835
2025-01-21 | 7358.3179 | 33.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7763.7203
2025-01-21 | 7329.415 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7642.5569
2025-01-21 | 7247.5869 | 31.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7452.9365
2025-01-21 | 7053.5908 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7269.5884
2025-01-21 | 7163.2798 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7267.8756
2025-01-21 | 7496.1421 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7643.5456
2025-01-21 | 8457.4883 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8215.2642
2025-01-21 | 9439.0254 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8537.7206
2025-01-21 | 9284.7939 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8571.4275
2025-01-21 | 9176.7334 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8794.8049
2025-01-21 | 8967.4512 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8471.8954
2025-01-21 | 8442.6846 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7947.4583
2025-01-21 | 7669.1748 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7400.2624
2025-01-21 | 7066.0361 | 33.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6946.8046
2025-01-22 | 6714.5308 | 34.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.0515
2025-01-22 | 6616.29 | 35.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6579.0868
2025-01-22 | 6565.6831 | 36.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6527.3791
2025-01-22 | 6543.2412 | 36.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6555.3025
2025-01-22 | 6774.2529 | 36.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6701.3561
2025-01-22 | 7155.6069 | 36.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7042.1182
2025-01-22 | 7648.8081 | 37.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7513.9677
2025-01-22 | 7982.6421 | 37.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7919.9958
2025-01-22 | 8042.0659 | 38.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8220.2754
2025-01-22 | 7752.8999 | 36.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8053.3857
2025-01-22 | 7509.6338 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7851.7228
2025-01-22 | 7483.4512 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.5578
2025-01-22 | 7268.2959 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7353.9337
2025-01-22 | 7252.1079 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7137.5847
2025-01-22 | 7163.2339 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7179.8731
2025-01-22 | 7509.395 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7478.5409
2025-01-22 | 8465.7842 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8127.2617
2025-01-22 | 9319.6904 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.7165
2025-01-22 | 9210.6055 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8472.4247
2025-01-22 | 9108.2197 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8354.7924
2025-01-22 | 8853.2236 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8141.886
2025-01-22 | 8366.1768 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7562.4474
2025-01-22 | 7664.8901 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6905.2483
2025-01-22 | 7168.1289 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6407.7893
2025-01-23 | 6741.6318 | 29.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6077.0346
2025-01-23 | 6468.2832 | 29.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5886.067
2025-01-23 | 6345.6968 | 28.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5713.3559
2025-01-23 | 6268.1528 | 28.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5686.2777
2025-01-23 | 6438.561 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5843.3317
2025-01-23 | 6752.6792 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6173.0934
2025-01-23 | 7156.2832 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6567.9407
2025-01-23 | 7453.2959 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6907.967
2025-01-23 | 7687.4302 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7131.2443
2025-01-23 | 7641.8301 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7151.36
2025-01-23 | 7592.9609 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7092.7012
2025-01-23 | 7506.0908 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7026.5393
2025-01-23 | 7392.4678 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6858.9196
2025-01-23 | 7137.7632 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6730.5731
2025-01-23 | 7141.769 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6739.8606
2025-01-23 | 7385.8159 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7027.5281
2025-01-23 | 8015.9531 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7555.2454
2025-01-23 | 8886.1797 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7800.6996
2025-01-23 | 8729.3574 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7856.4071
2025-01-23 | 8520.2607 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7782.7761
2025-01-23 | 8270.0938 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7569.8697
2025-01-23 | 7844.3198 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7045.4326
2025-01-23 | 7161.4312 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6487.2364
2025-01-23 | 6580.4102 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6220.7839
2025-01-24 | 6299.875 | 28.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5967.0315
2025-01-24 | 6015.645 | 30.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5985.0698
2025-01-24 | 5972.2012 | 29.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5801.3584
2025-01-24 | 5931.188 | 31.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5950.2852
2025-01-24 | 6099.145 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250.3433
2025-01-24 | 6534.0171 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6690.1081
2025-01-24 | 7078.1792 | 35.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7260.9605
2025-01-24 | 7457.062 | 35.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7677.9889
2025-01-24 | 7620.603 | 36.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8022.2697
2025-01-24 | 7437.5068 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7965.3832
2025-01-24 | 7180.4902 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7741.7197
2025-01-24 | 6965.7739 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7631.5566
2025-01-24 | 6979.2788 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7353.9337
2025-01-24 | 6674.981 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7192.5862
2025-01-24 | 6561.9541 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7245.875
2025-01-24 | 6838.6138 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7632.5453
2025-01-24 | 7522.9712 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8248.2651
2025-01-24 | 8410.5654 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8526.7203
2025-01-24 | 8486.0879 | 33.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8835.435
2025-01-24 | 8534.9277 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8882.8074
2025-01-24 | 8368.7754 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8581.8985
2025-01-24 | 8054.8428 | 32.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7958.4587
2025-01-24 | 7586.9341 | 36.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7763.2728
2025-01-24 | 7192.5049 | 37.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7364.8165
2025-01-25 | 6847.5088 | 36.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7169.5322
2025-01-25 | 6595.5049 | 37.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7099.5681
2025-01-25 | 6518.708 | 36.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6816.8539
2025-01-25 | 6424.646 | 36.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6800.776
2025-01-25 | 6438.5669 | 35.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6880.8278
2025-01-25 | 6583.9531 | 35 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7122.587
2025-01-25 | 6727.9678 | 34.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7429.4318
2025-01-25 | 7263.8809 | 33.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7780.4583
2025-01-25 | 7994.1729 | 34.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8025.7363
2025-01-25 | 8386.4834 | 33.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7968.8498
2025-01-25 | 8332.7412 | 30.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7701.185
2025-01-25 | 8325.1123 | 27.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7371.0157
2025-01-25 | 8467.5469 | 25.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7082.3925
2025-01-25 | 8400.6895 | 24.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6899.0444
2025-01-25 | 8290.0723 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6930.3325
2025-01-25 | 8370.0732 | 24.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7339.0034
2025-01-25 | 8841.6162 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7877.7211
2025-01-25 | 9091.2832 | 24.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8090.1744
2025-01-25 | 8822.8574 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8112.8809
2025-01-25 | 8493.9697 | 24.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8072.2508
2025-01-25 | 8086.7119 | 24.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7826.3435
2025-01-25 | 7626.3838 | 23.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7224.9043
2025-01-25 | 7033.1191 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6545.7046
2025-01-25 | 6466.5449 | 23.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6070.2462
2025-01-26 | 6103.4678 | 23.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5695.4902
2025-01-26 | 5791.0308 | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5361.5186
2025-01-26 | 5672.5669 | 21.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5199.8078
2025-01-26 | 5582.5811 | 20.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5095.7274
2025-01-26 | 5562.8521 | 20.3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5175.7792
2025-01-26 | 5698.4048 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5516.5412
2025-01-26 | 5914.1768 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5933.3892
2025-01-26 | 6378.0068 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.4167
2025-01-26 | 6910.4429 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6529.6937
2025-01-26 | 7171.644 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6571.81
2025-01-26 | 7526.7642 | 21.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6733.1574
2025-01-26 | 7559.8901 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6710.9969
2025-01-26 | 7406.2959 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6521.3765
2025-01-26 | 7429.2222 | 20.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6437.0312
2025-01-26 | 7381.459 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6479.3197
2025-01-26 | 7484.2119 | 20.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6909.9912
2025-01-26 | 8131.5981 | 21.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7536.7113
2025-01-26 | 8889.3896 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.1691
2025-01-26 | 8712.2158 | 23.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8024.8784
2025-01-26 | 8442.7852 | 24.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8138.2527
2025-01-26 | 7965.4399 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7848.3442
2025-01-26 | 7474.1758 | 23.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7246.9049
2025-01-26 | 6618.5449 | 22.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6512.7036
2025-01-26 | 6062.8892 | 22.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5938.2424
2025-01-27 | 5659.4482 | 21.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5285.012
2025-01-27 | 5439.0298 | 22.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5094.0445
2025-01-27 | 5299.9209 | 22.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4987.3352
2025-01-27 | 5300.8799 | 23.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5059.2599
2025-01-27 | 5519.0352 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5194.3132
2025-01-27 | 5865.915 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5491.074
2025-01-27 | 6398.3032 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5929.9225
2025-01-27 | 6727.4888 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6368.9516
2025-01-27 | 6890.4448 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6471.2255
2025-01-27 | 6778.7632 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6458.3403
2025-01-27 | 6702.0059 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6377.6808
2025-01-27 | 6606.1948 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6245.5171
2025-01-27 | 6742.2832 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5989.8948
2025-01-27 | 6751.1001 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5828.5474
2025-01-27 | 6802.0308 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5881.8362
2025-01-27 | 7137.2959 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6246.5058
2025-01-27 | 7857.6328 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6906.2269
2025-01-27 | 8722.335 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7173.6818
2025-01-27 | 8531.9551 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7185.388
2025-01-27 | 8369.79 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7155.7582
2025-01-27 | 8004.2178 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7052.855
2025-01-27 | 7434.5249 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6594.4198
2025-01-27 | 6721.4692 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5948.221
2025-01-27 | 6057.7109 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5395.7604
2025-01-28 | 5645.8101 | 19.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5032.0048
2025-01-28 | 5424.4048 | 24.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5314.0507
2025-01-28 | 5477.5859 | 24.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5251.3427
2025-01-28 | 5386.4712 | 26.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5444.2708
2025-01-28 | 5632.7051 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832.3314
2025-01-28 | 6171.9551 | 31.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6503.1028
2025-01-28 | 6724.627 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7062.9548
2025-01-28 | 7114.2148 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7545.9851
2025-01-28 | 7189.8418 | 34.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7813.2638
2025-01-28 | 7017.9038 | 34.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7811.3788
2025-01-28 | 6789.3208 | 33.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7763.7203
2025-01-28 | 6725.686 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7642.5569
2025-01-28 | 6699.3608 | 32.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7496.9378
2025-01-28 | 6628.499 | 31.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7368.5912
2025-01-28 | 6678.6621 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7388.8791
2025-01-28 | 6979.5391 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7720.5478
2025-01-28 | 7847.2422 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8215.2642
2025-01-28 | 8826.9043 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8405.7169
2025-01-28 | 8663.6426 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8439.4237
2025-01-28 | 8671.4199 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8420.7942
2025-01-28 | 8317.8574 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8108.8851
2025-01-28 | 7847.8052 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7617.4489
2025-01-28 | 7180.9609 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7026.2518
2025-01-28 | 6606.7178 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6506.7921
2025-01-29 | 6260.9888 | 29.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6143.0365
2025-01-29 | 6108.6021 | 30.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6018.0708
2025-01-29 | 5957.0142 | 30.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5933.3622
2025-01-29 | 5844.4761 | 30.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5906.284
2025-01-29 | 6045.4429 | 31.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6085.3386
2025-01-29 | 6327.8721 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6393.0997
2025-01-29 | 6722.293 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6798.9473
2025-01-29 | 6921.7061 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7171.9745
2025-01-29 | 7122.5098 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7406.2522
2025-01-29 | 7170.3311 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7426.3678
2025-01-29 | 7026.2822 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7345.7084
2025-01-29 | 7038.5371 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7191.544
2025-01-29 | 7070.3159 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7023.9243
2025-01-29 | 6749.792 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6884.5775
2025-01-29 | 6868.6572 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6981.8675
2025-01-29 | 7136.5142 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7379.5381
2025-01-29 | 7956.5669 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7940.2563
2025-01-29 | 8802.1963 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8163.71
2025-01-29 | 8784.1963 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8164.4159
2025-01-29 | 8603.4326 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8200.788
2025-01-29 | 8420.6914 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8053.8835
2025-01-29 | 7922.7212 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7639.4496
2025-01-29 | 7277.9858 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7136.2549
2025-01-29 | 6755.771 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6858.8021
2025-01-30 | 6471.7871 | 34.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6627.0503
2025-01-30 | 6358.1362 | 35.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.0852
2025-01-30 | 6395.1558 | 35.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6417.376
2025-01-30 | 6363.6201 | 36.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6500.3009
2025-01-30 | 6618.0952 | 37.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6811.3593
2025-01-30 | 6963.0278 | 37.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7119.1204
2025-01-30 | 7523.7612 | 39.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7755.9746
2025-01-30 | 7887.394 | 39.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8085.0005
2025-01-30 | 8027.0791 | 39.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8308.2779
2025-01-30 | 7985.915 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8229.3907
2025-01-30 | 7775.7842 | 35.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7972.7262
2025-01-30 | 7673.2949 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7807.5616
2025-01-30 | 7459.0332 | 33.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7595.9406
2025-01-30 | 7402.6528 | 31.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7390.5919
2025-01-30 | 7234.4351 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7322.8772
2025-01-30 | 7287.7012 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7720.5478
2025-01-30 | 8031.7148 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8204.2639
2025-01-30 | 8794.6133 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8438.7178
2025-01-30 | 8709.0576 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8439.4237
2025-01-30 | 8581.001 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8431.7946
2025-01-30 | 8245.9346 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8196.8876
2025-01-30 | 7767.4209 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7650.4499
2025-01-30 | 7114.4829 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6982.2505
2025-01-30 | 6438.873 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6550.7933
2025-01-31 | 6055.876 | 30.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6209.0384
2025-01-31 | 5812.124 | 30.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5974.0695
2025-01-31 | 5680.792 | 32 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6065.3659
2025-01-31 | 5659.707 | 32.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6104.2896
2025-01-31 | 5818.5049 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6030.337
2025-01-31 | 6127.8511 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6305.0972
2025-01-31 | 6553.731 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6655.9432
2025-01-31 | 6871.0488 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6973.9688
2025-01-31 | 6995.7368 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7164.2453
2025-01-31 | 6959.4941 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7151.36
2025-01-31 | 6868.481 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6927.6965
2025-01-31 | 6606.604 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6707.5303
2025-01-31 | 6529.1982 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6330.9045
2025-01-31 | 6548.3101 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6158.5568
2025-01-31 | 6675.8311 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6200.8452
2025-01-31 | 6883.2979 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6576.5152
2025-01-31 | 7332.0601 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7170.2344
2025-01-31 | 7962.2808 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7404.6883
2025-01-31 | 7981.6831 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7515.3974
2025-01-31 | 7917.7339 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7672.7729
2025-01-31 | 7742.272 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7613.871
2025-01-31 | 7345.6079 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7210.4373
2025-01-31 | 6897.585 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6619.2402
2025-01-31 | 6417.7402 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6253.7849
2025-02-01 | 6048.0479 | 29.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6355.509
2025-02-01 | 5885.2788 | 30.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6307.5455
2025-02-01 | 5867.7598 | 31.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6310.8394
2025-02-01 | 5945.731 | 32.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6404.7647
2025-02-01 | 6090.0972 | 33.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6638.8209
2025-02-01 | 6360.6401 | 34.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7056.5851
2025-02-01 | 6721.729 | 35.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7594.4365
2025-02-01 | 7433.9312 | 36.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8077.4668
2025-02-01 | 8010.3779 | 37.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8377.7464
2025-02-01 | 8416.1943 | 37.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8441.8633
2025-02-01 | 8428.9072 | 37.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8427.2057
2025-02-01 | 8460.9248 | 36.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8350.0436
2025-02-01 | 8228.3896 | 35.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8127.4222
2025-02-01 | 8067.6631 | 34.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7944.0741
2025-02-01 | 7950.7241 | 33.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7909.3604
2025-02-01 | 7969.9692 | 32.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8219.0285
2025-02-01 | 8561.0342 | 32.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8735.7455
2025-02-01 | 9113.8271 | 32.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9047.2016
2025-02-01 | 9231.3721 | 34.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9278.9142
2025-02-01 | 8991.1445 | 35.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9315.2862
2025-02-01 | 8758.9707 | 36.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9146.3811
2025-02-01 | 8422.9922 | 35.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8544.9419
2025-02-01 | 8022.1069 | 37.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8129.7497
2025-02-01 | 7558.6929 | 38.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7698.2925
2025-02-02 | 7179.8721 | 39.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7455.5404
2025-02-02 | 6992.541 | 39.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7253.5725
2025-02-02 | 6884.8521 | 40.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7267.8667
2025-02-02 | 6807.4468 | 39 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7086.7841
2025-02-02 | 6952.5972 | 39.3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7265.8387
2025-02-02 | 7050.2139 | 39.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7639.6017
2025-02-02 | 7405.377 | 39.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8034.449
2025-02-02 | 7986.7441 | 39.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8374.4753
2025-02-02 | 8663.9189 | 38.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8553.7514
2025-02-02 | 9136.9072 | 37.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8430.863
2025-02-02 | 9190.7012 | 35.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8218.1997
2025-02-02 | 9237.9355 | 33.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8064.0354
2025-02-02 | 9266.6416 | 32.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7830.4138
2025-02-02 | 9182.502 | 32.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7746.0685
2025-02-02 | 9183.5732 | 32.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7788.357
2025-02-02 | 9288.3467 | 31.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8131.026
2025-02-02 | 9763.8721 | 31.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8691.7443
2025-02-02 | 10117.2256 | 31.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8893.1973
2025-02-02 | 10000.7764 | 31.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8904.9035
2025-02-02 | 9620.6553 | 31.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8897.2743
2025-02-02 | 9132.6582 | 31.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8673.3677
2025-02-02 | 8429.2012 | 31.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8126.93
2025-02-02 | 7674.1641 | 31.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7502.7318
2025-02-02 | 7014.4468 | 31.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6983.2722
2025-02-03 | 6592.4141 | 31.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6341.0421
2025-02-03 | 6303.9292 | 31.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6095.073
2025-02-03 | 6215.165 | 31 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5955.3628
2025-02-03 | 6121.9238 | 30.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5917.2843
2025-02-03 | 6223.96 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6030.337
2025-02-03 | 6474.5068 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6382.0994
2025-02-03 | 6927.6279 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6765.9464
2025-02-03 | 7236.6802 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7116.9729
2025-02-03 | 7294.3989 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7274.2484
2025-02-03 | 7255.3892 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7206.3616
2025-02-03 | 7053.563 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7059.7002
2025-02-03 | 7111.9731 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6894.5356
2025-02-03 | 7050.52 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6616.9127
2025-02-03 | 6988.0562 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6356.5624
2025-02-03 | 6867.9429 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6387.8506
2025-02-03 | 7089.8511 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6620.5165
2025-02-03 | 7751.0132 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7071.2316
2025-02-03 | 8442.5391 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7261.6843
2025-02-03 | 8185.9771 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7240.3896
2025-02-03 | 7992.835 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7188.7592
2025-02-03 | 7607.2378 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6997.8534
2025-02-03 | 7120.8848 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6561.4189
2025-02-03 | 6414.6411 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6036.2236
2025-02-03 | 5898.8071 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5527.7642
2025-02-04 | 5454.9771 | 22.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5307.0127
2025-02-04 | 5362.8682 | 23.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5259.0492
2025-02-04 | 5313.0601 | 25.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5372.3462
2025-02-04 | 5297.2529 | 25.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5356.2683
2025-02-04 | 5409.9429 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5469.321
2025-02-04 | 5705.9839 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.0821
2025-02-04 | 6254.666 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6204.9304
2025-02-04 | 6480.1069 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6621.9588
2025-02-04 | 6658.8218 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6933.2387
2025-02-04 | 6455.5361 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6986.3553
2025-02-04 | 6552.7832 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6960.6974
2025-02-04 | 6556.7598 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6938.5368
2025-02-04 | 6455.9658 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6825.9187
2025-02-04 | 6316.4312 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6763.574
2025-02-04 | 6428.8271 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6805.8625
2025-02-04 | 6485.0771 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7148.5315
2025-02-04 | 7340.8101 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7786.2519
2025-02-04 | 8369.6318 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8130.709
2025-02-04 | 8522.0078 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8274.419
2025-02-04 | 8534.0244 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8343.7921
2025-02-04 | 8420.7314 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8262.8895
2025-02-04 | 7915.355 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7771.4533
2025-02-04 | 7340.5771 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7433.2634
2025-02-04 | 6826.7441 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6880.8028
2025-02-05 | 6518.1089 | 35.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6737.0534
2025-02-05 | 6347.5752 | 33.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6381.0811
2025-02-05 | 6302.9868 | 35.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6461.3772
2025-02-05 | 6323.2778 | 34.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6269.2943
2025-02-05 | 6511.3242 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6459.3492
2025-02-05 | 6884.582 | 35.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6877.1135
2025-02-05 | 7501.9082 | 36.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7403.9645
2025-02-05 | 7849.417 | 37.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.9961
2025-02-05 | 7806.7661 | 36.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8033.27
2025-02-05 | 7549.6431 | 35.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7987.3838
2025-02-05 | 7176.145 | 34.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7829.7222
2025-02-05 | 7085.6099 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7741.5597
2025-02-05 | 7016.5181 | 32.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7562.9396
2025-02-05 | 6862.2681 | 31.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7401.5922
2025-02-05 | 6986.5479 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7377.8788
2025-02-05 | 7205.9248 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7709.5475
2025-02-05 | 7941.9399 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8226.2645
2025-02-05 | 8712.3467 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8493.7194
2025-02-05 | 8943.3447 | 31.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8637.4294
2025-02-05 | 8964.8877 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8717.8027
2025-02-05 | 8840.8594 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8548.8976
2025-02-05 | 8444.4717 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8046.4612
2025-02-05 | 7752.7979 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7576.2674
2025-02-05 | 7153.874 | 34.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7045.8075
2025-02-06 | 6708.3452 | 37.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6957.0597
2025-02-06 | 6676.0112 | 37.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6744.0915
2025-02-06 | 6522.186 | 37.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6637.3822
2025-02-06 | 6508.1348 | 37.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6621.3043
2025-02-06 | 6814.7559 | 37.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6800.359
2025-02-06 | 6939.873 | 37.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7108.12
2025-02-06 | 7513.8921 | 36.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7425.9652
2025-02-06 | 7725.0352 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7743.9908
2025-02-06 | 7827.0811 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7791.2631
2025-02-06 | 7945.1948 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7745.3769
2025-02-06 | 7951.3828 | 32.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7664.7175
2025-02-06 | 8007.5181 | 31.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7543.5541
2025-02-06 | 7728.4141 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7309.9324
2025-02-06 | 7831.54 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7225.5872
2025-02-06 | 7756.9209 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7278.876
2025-02-06 | 7830.6899 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7621.545
2025-02-06 | 8464.9902 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8149.2623
2025-02-06 | 9100.2129 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8394.7165
2025-02-06 | 9276.8301 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8384.4222
2025-02-06 | 8789.1221 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8277.7902
2025-02-06 | 8542.3877 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7943.8804
2025-02-06 | 7862.7119 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7045.4326
2025-02-06 | 7006.627 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6102.2254
2025-02-06 | 6348.3999 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5472.7626
2025-02-07 | 5948.04 | 20.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5098.0067
2025-02-07 | 5645.4609 | 20.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4874.0382
2025-02-07 | 5519.2241 | 20.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4789.3296
2025-02-07 | 5536.9502 | 21.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4861.2542
2025-02-07 | 5724.2832 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4985.3072
2025-02-07 | 6151.52 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5568.0762
2025-02-07 | 6515.7778 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5951.9232
2025-02-07 | 7051.9141 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6500.9554
2025-02-07 | 7020.4932 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6823.2356
2025-02-07 | 6816.9341 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6843.3512
2025-02-07 | 6776.5649 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6806.693
2025-02-07 | 6602.2578 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6751.5315
2025-02-07 | 6471.666 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6616.9127
2025-02-07 | 6395.7949 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6543.5677
2025-02-07 | 6520.293 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6607.8568
2025-02-07 | 6572.4878 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.5256
2025-02-07 | 7034.2158 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7511.2441
2025-02-07 | 7832.811 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7767.6987
2025-02-07 | 7951.4902 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7922.409
2025-02-07 | 7875.0088 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7980.7817
2025-02-07 | 7832.7871 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7954.8807
2025-02-07 | 7355.5581 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7397.4427
2025-02-07 | 6935.6689 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6773.2446
2025-02-07 | 6484.9858 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6451.7905
2025-02-08 | 6058.5879 | 29.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6355.509
2025-02-08 | 5809.6582 | 28.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6065.5386
2025-02-08 | 5619.5308 | 27.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5881.8272
2025-02-08 | 5570.561 | 26.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5744.7459
2025-02-08 | 5587.2031 | 26.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5890.7996
2025-02-08 | 5785.5039 | 27.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6330.5644
2025-02-08 | 6170.0151 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6780.4133
2025-02-08 | 6809.793 | 29.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7274.4439
2025-02-08 | 7215.5542 | 30.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7651.7257
2025-02-08 | 7364.6919 | 29.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7583.8388
2025-02-08 | 7416.2969 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7294.1734
2025-02-08 | 7411.4858 | 24.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7041.0063
2025-02-08 | 7008.356 | 24.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.3884
2025-02-08 | 7079.0181 | 23.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6778.0409
2025-02-08 | 6956.3608 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6787.3285
2025-02-08 | 7347.3579 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.9972
2025-02-08 | 7987.4468 | 23.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7800.7189
2025-02-08 | 8321.0449 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8068.1738
2025-02-08 | 8385.2227 | 24.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8156.8822
2025-02-08 | 7874.8242 | 25.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8171.2537
2025-02-08 | 7484.2759 | 25.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7936.3467
2025-02-08 | 6963.4858 | 25.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7411.9096
2025-02-08 | 6598.3311 | 25.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6820.7124
2025-02-08 | 6099.1011 | 26.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6378.2549
2025-02-09 | 5765.7139 | 26.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6025.4996
2025-02-09 | 5571.7642 | 26.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.5318
2025-02-09 | 5437.915 | 26.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5727.8228
2025-02-09 | 5403.5918 | 26.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5700.7446
2025-02-09 | 5438.146 | 26.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5846.7983
2025-02-09 | 5674.2852 | 26.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6198.5606
2025-02-09 | 5951.9302 | 28.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6846.4152
2025-02-09 | 6449.334 | 29.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7307.4449
2025-02-09 | 6874.521 | 27.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7288.7153
2025-02-09 | 7227.3042 | 27.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7319.8313
2025-02-09 | 7387.0459 | 25.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7162.1697
2025-02-09 | 7448.1748 | 24.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6997.005
2025-02-09 | 7525.5518 | 23.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6807.3846
2025-02-09 | 7652.4302 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6701.0387
2025-02-09 | 7575.1519 | 22.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6776.3282
2025-02-09 | 7763.522 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.9972
2025-02-09 | 8176.875 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7679.7154
2025-02-09 | 8738.4209 | 22.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7925.1697
2025-02-09 | 8678.4248 | 22.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7936.8759
2025-02-09 | 8274.4492 | 22.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7918.2464
2025-02-09 | 7881.6362 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7661.3388
2025-02-09 | 7411.3359 | 23.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7224.9043
2025-02-09 | 6680.6719 | 23.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6611.7065
2025-02-09 | 6127.4858 | 24.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6191.2496
2025-02-10 | 5695.2202 | 24.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5538.0192
2025-02-10 | 5495.2598 | 25 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5413.0535
2025-02-10 | 5391.4302 | 25.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5361.3459
2025-02-10 | 5413.8369 | 25.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5367.2686
2025-02-10 | 5522.48 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5799.3304
2025-02-10 | 5925.8052 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250.0956
2025-02-10 | 6377.2021 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6677.9439
2025-02-10 | 6777.127 | 31.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7237.9764
2025-02-10 | 6863.9722 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7395.2519
2025-02-10 | 6824.3169 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7382.3666
2025-02-10 | 6556.8359 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7279.7065
2025-02-10 | 6406.3721 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7114.5419
2025-02-10 | 6275.7031 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7012.924
2025-02-10 | 6109.2798 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6895.5778
2025-02-10 | 6147.4092 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6860.8641
2025-02-10 | 6460.165 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7159.5318
2025-02-10 | 7226.8589 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7731.2504
2025-02-10 | 8036.1748 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8020.7059
2025-02-10 | 8152.792 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8120.4147
2025-02-10 | 8122.9839 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8167.787
2025-02-10 | 7926.3701 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7932.8801
2025-02-10 | 7433.0449 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7419.4433
2025-02-10 | 6710.0112 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6861.2471
2025-02-10 | 6087.8169 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6132.7814
2025-02-11 | 5754.0352 | 27.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5890.0293
2025-02-11 | 5684.0479 | 25.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5468.0551
2025-02-11 | 5555.731 | 24.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5251.3427
2025-02-11 | 5584.9521 | 25.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5367.2686
2025-02-11 | 5760.0288 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5645.326
2025-02-11 | 6095.2808 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5997.0884
2025-02-11 | 6537.6812 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6413.9363
2025-02-11 | 6950.2612 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6764.9629
2025-02-11 | 7084.6621 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6999.2406
2025-02-11 | 6843.4941 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6898.3528
2025-02-11 | 6613.54 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6795.6927
2025-02-11 | 6433.9878 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6718.5306
2025-02-11 | 6370.2642 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6594.9121
2025-02-11 | 6355.8008 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6609.5696
2025-02-11 | 6257.5542 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6706.8597
2025-02-11 | 6574.2212 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7115.5306
2025-02-11 | 7256.793 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7665.2485
2025-02-11 | 8082.8018 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.7037
2025-02-11 | 8107.252 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8131.415
2025-02-11 | 8061.085 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8178.7874
2025-02-11 | 7955.1509 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8020.8826
2025-02-11 | 7567.165 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7518.4461
2025-02-11 | 7026.0088 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6993.2508
2025-02-11 | 6411.4268 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6605.7949
2025-02-12 | 6113.042 | 33 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6506.0468
2025-02-12 | 5967.792 | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6513.0849
2025-02-12 | 5908.2642 | 34.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6318.3731
2025-02-12 | 5866.1958 | 33.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6247.2937
2025-02-12 | 6083.0918 | 34.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6470.3496
2025-02-12 | 6544.584 | 34.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6822.1119
2025-02-12 | 7106.355 | 36.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7381.9639
2025-02-12 | 7525.627 | 36.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7776.9917
2025-02-12 | 7442.8862 | 37.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8099.2719
2025-02-12 | 7226.4458 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7888.381
2025-02-12 | 6928.168 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7719.719
2025-02-12 | 6852.7251 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7587.5553
2025-02-12 | 6751.207 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7364.934
2025-02-12 | 6550.2021 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7214.5869
2025-02-12 | 6590.3672 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7234.8747
2025-02-12 | 6800.9741 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7577.5437
2025-02-12 | 7803.9658 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8138.262
2025-02-12 | 8731.8926 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8416.7172
2025-02-12 | 8891.4707 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8505.4256
2025-02-12 | 8830.9609 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8486.7961
2025-02-12 | 8616.3857 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8251.8891
2025-02-12 | 8335.2256 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7727.4521
2025-02-12 | 7725.7402 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7202.2568
2025-02-12 | 7152.3389 | 31.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6671.7968
2025-02-13 | 6728.4219 | 31.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6319.0415
2025-02-13 | 6493.6821 | 30.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6062.072
2025-02-13 | 6354.9702 | 30.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5856.36
2025-02-13 | 6306.9438 | 29.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5763.2799
2025-02-13 | 6398.605 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5821.3311
2025-02-13 | 6561.3501 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129.0922
2025-02-13 | 6909.3618 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6501.9388
2025-02-13 | 7167.3301 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6830.9648
2025-02-13 | 7379.2358 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6988.2403
2025-02-13 | 7628.4521 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6920.3534
2025-02-13 | 7776.0698 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6839.694
2025-02-13 | 7795.8628 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6751.5315
2025-02-13 | 7716.9951 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6561.9111
2025-02-13 | 7526.7012 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6422.5643
2025-02-13 | 7417.2339 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6552.8553
2025-02-13 | 7604.3081 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.5256
2025-02-13 | 8158.9941 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7621.2472
2025-02-13 | 8764.0078 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7822.7002
2025-02-13 | 8704.999 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7889.4081
2025-02-13 | 8507.9844 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7881.7789
2025-02-13 | 8309.2871 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7690.8732
2025-02-13 | 7779.728 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7221.4377
2025-02-13 | 7114.0171 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6707.2427
2025-02-13 | 6465.9482 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6297.7861
2025-02-14 | 6156.5039 | 28.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5967.0315
2025-02-14 | 6000.3291 | 29 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5853.0661
2025-02-14 | 5924.0781 | 29.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5801.3584
2025-02-14 | 5949.5889 | 30.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873.283
2025-02-14 | 6110.5649 | 32.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6217.3423
2025-02-14 | 6513.394 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6393.0997
2025-02-14 | 6997.5098 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6919.9507
2025-02-14 | 7360.3882 | 33.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7512.9842
2025-02-14 | 7417.7202 | 32.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7593.2575
2025-02-14 | 7061.126 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7448.3685
2025-02-14 | 6709.231 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7191.704
2025-02-14 | 6595.7842 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7114.5419
2025-02-14 | 6576.541 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6902.9208
2025-02-14 | 6413.645 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6785.5746
2025-02-14 | 6353.8711 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6838.8634
2025-02-14 | 6488.48 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7148.5315
2025-02-14 | 6981.8599 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7742.2507
2025-02-14 | 7804.8062 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8031.7062
2025-02-14 | 8085.3291 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8208.4172
2025-02-14 | 8013.1919 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8519.7971
2025-02-14 | 7854.9238 | 31.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8317.891
2025-02-14 | 7565.4019 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7661.4502
2025-02-14 | 7053.749 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7037.2521
2025-02-14 | 6706.2749 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6561.7937
2025-02-15 | 6429.1538 | 31.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6619.5166
2025-02-15 | 6189.3882 | 32 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6461.5499
2025-02-15 | 6085.4541 | 31.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6255.8379
2025-02-15 | 6008.71 | 31.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6261.7606
2025-02-15 | 6095.0869 | 30.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6330.8121
2025-02-15 | 6267.1362 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6682.5744
2025-02-15 | 6556.9331 | 31.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7154.4239
2025-02-15 | 7033.0742 | 32.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7659.4549
2025-02-15 | 7509.542 | 32.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7849.7313
2025-02-15 | 7876.3042 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7737.8432
2025-02-15 | 7955.709 | 29.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7569.1813
2025-02-15 | 8077.2871 | 27.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7349.015
2025-02-15 | 8037.0688 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7126.3937
2025-02-15 | 7854.4712 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7064.0491
2025-02-15 | 7811.4858 | 26.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7139.3385
2025-02-15 | 8083.1211 | 26.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7548.0094
2025-02-15 | 8560.0127 | 27.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8229.7311
2025-02-15 | 9028.0244 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8530.1869
2025-02-15 | 8900.4932 | 28.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8563.8938
2025-02-15 | 8614.8242 | 28.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8578.2652
2025-02-15 | 8314.7217 | 28.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8354.3586
2025-02-15 | 7779.6519 | 29.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7840.9218
2025-02-15 | 7271.0669 | 29 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7205.7234
2025-02-15 | 6749.9771 | 28.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6675.2634
2025-02-16 | 6427.3091 | 28.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6333.5084
2025-02-16 | 6161.3511 | 28.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6120.5402
2025-02-16 | 6026.6729 | 28.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5947.8291
2025-02-16 | 6017.9702 | 28.1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5887.75
2025-02-16 | 6062.981 | 27.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5978.8021
2025-02-16 | 6226.7681 | 27.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6297.5635
2025-02-16 | 6548.084 | 27.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6703.4111
2025-02-16 | 6997.3481 | 27.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7098.4389
2025-02-16 | 7588.064 | 27.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7299.7156
2025-02-16 | 8187.4819 | 27.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7341.8319
2025-02-16 | 8594.083 | 27.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7316.174
2025-02-16 | 8927.3525 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7294.0135
2025-02-16 | 9130.9131 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7126.3937
2025-02-16 | 8988.2715 | 26.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7075.0494
2025-02-16 | 8969.5576 | 26.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7183.3397
2025-02-16 | 8994.3076 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7603.011
2025-02-16 | 9319.668 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8163.7292
2025-02-16 | 9608.1572 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8387.1828
2025-02-16 | 9373.9824 | 26.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8376.8885
2025-02-16 | 8967.8584 | 27.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8468.2621
2025-02-16 | 8529.1025 | 29.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8398.3598
2025-02-16 | 8105.4692 | 29.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7873.9228
2025-02-16 | 7470.0688 | 29.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7271.7253
2025-02-16 | 6897.3218 | 29.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6774.2662
2025-02-17 | 6529.855 | 29.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6154.0368
2025-02-17 | 6373.9199 | 30.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.0714
2025-02-17 | 6231.3032 | 31.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5977.3634
2025-02-17 | 6187.7808 | 31.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5983.2862
2025-02-17 | 6259.1499 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6239.343
2025-02-17 | 6509.7861 | 33.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6635.1066
2025-02-17 | 6772.146 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7084.9554
2025-02-17 | 7253.9888 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7523.9845
2025-02-17 | 7636.8809 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.2619
2025-02-17 | 7806.6621 | 33.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7767.3775
2025-02-17 | 7953.2642 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7708.7187
2025-02-17 | 7966.2559 | 32.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7642.5569
2025-02-17 | 8069.042 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7364.934
2025-02-17 | 7965.2871 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7126.5844
2025-02-17 | 8001.6289 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7102.8709
2025-02-17 | 8171.1421 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7412.539
2025-02-17 | 8741.4121 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7973.2573
2025-02-17 | 9368.8936 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8240.7122
2025-02-17 | 9393.7363 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8329.4206
2025-02-17 | 9282.333 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8398.7936
2025-02-17 | 8947.9473 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8130.8857
2025-02-17 | 8426.5391 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7705.4514
2025-02-17 | 7610.728 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7136.2549
2025-02-17 | 7040.5 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6693.7974
2025-02-18 | 6718.291 | 32.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6407.044
2025-02-18 | 6493.5718 | 32.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6282.0783
2025-02-18 | 6377.6851 | 33.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6252.3713
2025-02-18 | 6357.7402 | 34.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6302.2953
2025-02-18 | 6567.5732 | 34.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6492.3502
2025-02-18 | 6974.98 | 34.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6822.1119
2025-02-18 | 7245.498 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7249.9601
2025-02-18 | 7739.1362 | 35.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7710.9898
2025-02-18 | 7676.313 | 35.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7890.266
2025-02-18 | 7425.5801 | 34.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7855.3801
2025-02-18 | 7498.813 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7807.7215
2025-02-18 | 7107.5249 | 33.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7719.5591
2025-02-18 | 7064.0322 | 32.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7562.9396
2025-02-18 | 6923.2729 | 32.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7445.5934
2025-02-18 | 6992.1802 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7509.8825
2025-02-18 | 7122.4502 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.5528
2025-02-18 | 7948.4341 | 31.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8435.2704
2025-02-18 | 8864.8154 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8724.7259
2025-02-18 | 9077.9824 | 32.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8758.4328
2025-02-18 | 8903.7051 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8761.804
2025-02-18 | 8755.0557 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8548.8976
2025-02-18 | 8446.043 | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8013.4602
2025-02-18 | 7724.54 | 33.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7411.2627
2025-02-18 | 7127.312 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6913.8037
2025-02-19 | 6808.5669 | 34.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6638.0506
2025-02-19 | 6626.7881 | 35.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6612.0877
2025-02-19 | 6542.8979 | 36.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6582.3807
2025-02-19 | 6525.0928 | 36.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6566.3028
2025-02-19 | 6726.7021 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6624.3539
2025-02-19 | 7101.833 | 36.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6965.116
2025-02-19 | 7622.5752 | 36.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7425.9652
2025-02-19 | 7854.8721 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7633.9876
2025-02-19 | 7682.6201 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7835.2644
2025-02-19 | 7500.2788 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7734.3766
2025-02-19 | 7276.644 | 32.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7675.7178
2025-02-19 | 6956.3999 | 31.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7554.5544
2025-02-19 | 6998.9912 | 31.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7375.9343
2025-02-19 | 6821.9639 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7258.5881
2025-02-19 | 6774.605 | 29.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7201.8738
2025-02-19 | 6912.939 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7478.5409
2025-02-19 | 7673.7832 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8028.2588
2025-02-19 | 8511.4609 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8284.7134
2025-02-19 | 8769.126 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8329.4206
2025-02-19 | 8832.7578 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8321.7914
2025-02-19 | 8591.0859 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8229.8885
2025-02-19 | 8193.0547 | 30.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7727.4521
2025-02-19 | 7608.2021 | 31.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7169.2558
2025-02-19 | 7048.8018 | 31.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6660.7965
2025-02-20 | 6695.9111 | 30.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6264.0399
2025-02-20 | 6546.6841 | 30.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6018.0708
2025-02-20 | 6445.043 | 32 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6065.3659
2025-02-20 | 6499.3691 | 33.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6214.2928
2025-02-20 | 6642.2798 | 34.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6415.348
2025-02-20 | 6990.3169 | 34.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6789.111
2025-02-20 | 7545.6621 | 35.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7271.9608
2025-02-20 | 7813.4121 | 35.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7710.9898
2025-02-20 | 7625.3472 | 35.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7857.265
2025-02-20 | 7257.6338 | 33.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7767.3775
2025-02-20 | 6876.416 | 31.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7554.7143
2025-02-20 | 6684.7871 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7345.5484
2025-02-20 | 6587.6689 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7034.9246
2025-02-20 | 6338.0371 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6895.5778
2025-02-20 | 6340.8301 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6937.8662
2025-02-20 | 6722.9312 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7269.535
2025-02-20 | 7510.7261 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7819.2529
2025-02-20 | 8309.1504 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7987.7049
2025-02-20 | 8410.2871 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8087.4137
2025-02-20 | 8294.8262 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8101.7852
2025-02-20 | 7080.6191 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7844.8776
2025-02-20 | 6789.5171 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7364.4417
2025-02-20 | 7167.3511 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6795.2452
2025-02-20 | 6943.5049 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6363.788
2025-02-21 | 6349.5811 | 28.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6044.0337
2025-02-21 | 6100.4429 | 29.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5952.0689
2025-02-21 | 6042.2681 | 30.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5856.36
2025-02-21 | 6081.752 | 30.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5829.2818
2025-02-21 | 6176.0161 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5986.3358
2025-02-21 | 6551.4512 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6327.0978
2025-02-21 | 7056.7632 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6743.9457
2025-02-21 | 7377.853 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7127.9732
2025-02-21 | 7530.2222 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7329.25
2025-02-21 | 7422.187 | 29.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7338.3653
2025-02-21 | 7220.1782 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7312.7074
2025-02-21 | 6979.27 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7268.5462
2025-02-21 | 6887.3188 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7045.9249
2025-02-21 | 6606.2622 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6906.5781
2025-02-21 | 6557.9888 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7003.8681
2025-02-21 | 6740.8838 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7335.5368
2025-02-21 | 7276.3472 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896.2551
2025-02-21 | 7864.417 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8108.7084
2025-02-21 | 8142.021 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8197.4168
2025-02-21 | 8270.5371 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8101.7852
2025-02-21 | 8149.7412 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8240.8888
2025-02-21 | 7915.771 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7694.4511
2025-02-21 | 7410.7432 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7114.2543
2025-02-21 | 6974.481 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6913.8037
2025-02-22 | 6654.7988 | 32.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6762.5206
2025-02-22 | 6479.5361 | 33 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6571.5531
2025-02-22 | 6375.395 | 32.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6409.8423
2025-02-22 | 6356.2949 | 33.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6448.7659
2025-02-22 | 6519.1968 | 33.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.8218
2025-02-22 | 6721.4878 | 34.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7056.5851
2025-02-22 | 7053.0459 | 34.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7473.433
2025-02-22 | 7493.5078 | 35.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7978.464
2025-02-22 | 8066.8018 | 34.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8069.7376
2025-02-22 | 8261.0898 | 32 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7847.8464
2025-02-22 | 8209.7471 | 30.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7679.1844
2025-02-22 | 8331.4521 | 28.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492.0191
2025-02-22 | 8290.668 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7192.3956
2025-02-22 | 8114.772 | 25.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6943.0456
2025-02-22 | 8000.9629 | 24.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6919.3322
2025-02-22 | 7897.396 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7317.0028
2025-02-22 | 8241.6562 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7459.7092
2025-02-22 | 8608.4541 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7683.1628
2025-02-22 | 8620.8135 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7716.8697
2025-02-22 | 8172.1758 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7687.2399
2025-02-22 | 7737.4868 | 20.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7474.3335
2025-02-22 | 7304.25 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7015.8983
2025-02-22 | 6923.498 | 21.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6424.7011
2025-02-22 | 6377.1382 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5927.2421
2025-02-23 | 6038.2549 | 22 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5574.4868
2025-02-23 | 5751.397 | 22.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5383.5192
2025-02-23 | 5616.7881 | 22.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5287.8103
2025-02-23 | 5519.4292 | 22.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5282.7327
2025-02-23 | 5540.748 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5417.7861
2025-02-23 | 5660.916 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5747.5478
2025-02-23 | 5977.4951 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6153.3954
2025-02-23 | 6469.3442 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6537.4229
2025-02-23 | 7079.2441 | 22.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6705.6987
2025-02-23 | 7470.647 | 21.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6714.8141
2025-02-23 | 7575.9229 | 21.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6700.1565
2025-02-23 | 7457.3291 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6622.9944
2025-02-23 | 7289.0352 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6510.3762
2025-02-23 | 7266.7148 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6382.0297
2025-02-23 | 7338.6558 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6435.3184
2025-02-23 | 7693.5 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6799.9881
2025-02-23 | 8399.5723 | 19.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7349.706
2025-02-23 | 8670.8223 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7584.16
2025-02-23 | 8401.2529 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7650.8678
2025-02-23 | 8174.3711 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7621.238
2025-02-23 | 7762.0488 | 20.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7474.3335
2025-02-23 | 7173.1572 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7015.8983
2025-02-23 | 6460.5869 | 21.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6402.7005
2025-02-23 | 5784.9199 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5883.2408
2025-02-24 | 5406.0601 | 21.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5230.0105
2025-02-24 | 5155.0742 | 21.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5061.0435
2025-02-24 | 5089.3672 | 21.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4899.3327
2025-02-24 | 5056.6831 | 21.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4850.2539
2025-02-24 | 5192.9912 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4974.3069
2025-02-24 | 5530.1792 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5260.0674
2025-02-24 | 6047.0249 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5588.9128
2025-02-24 | 6374.4741 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5961.94
2025-02-24 | 6426.4902 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6130.2158
2025-02-24 | 6272.6689 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6117.3305
2025-02-24 | 5964.5771 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5970.6692
2025-02-24 | 6098.5391 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5860.5061
2025-02-24 | 6072.0249 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5648.8851
2025-02-24 | 5915.7212 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5553.5395
2025-02-24 | 5874.458 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5518.8258
2025-02-24 | 6238.8579 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5850.4945
2025-02-24 | 6534.3359 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6367.2115
2025-02-24 | 7128.6792 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6546.6639
2025-02-24 | 7056.252 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6525.3692
2025-02-24 | 6514.165 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6495.7394
2025-02-24 | 6349.3921 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6282.8331
2025-02-24 | 5809.377 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5791.3969
2025-02-24 | 5616.1309 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5233.2007
2025-02-24 | 5006.2129 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4757.7423
2025-02-25 | 4901.335 | 14.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4448.9882
2025-02-25 | 5193.521 | 14.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4269.021
2025-02-25 | 4887.3462 | 15 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4195.3127
2025-02-25 | 4830.2729 | 16 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4278.2376
2025-02-25 | 4830.3208 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4545.2947
2025-02-25 | 5200.4092 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4996.0599
2025-02-25 | 5677.1338 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5456.9091
2025-02-25 | 5930.6812 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873.9375
2025-02-25 | 5905.396 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6009.2124
2025-02-25 | 5752.377 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5908.3246
2025-02-25 | 5564.3618 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5717.662
2025-02-25 | 5502.8301 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5596.4986
2025-02-25 | 5595.9619 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5461.8798
2025-02-25 | 5584.7031 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5454.5367
2025-02-25 | 5622.752 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5617.8286
2025-02-25 | 5719.1489 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6070.5008
2025-02-25 | 6546.0498 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6675.2203
2025-02-25 | 7228.3911 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6887.6736
2025-02-25 | 7256.437 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6932.3808
2025-02-25 | 7286.0361 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6902.751
2025-02-25 | 7050.7119 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6700.845
2025-02-25 | 6522.6128 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6165.4076
2025-02-25 | 5848.043 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5552.2098
2025-02-25 | 5284.3921 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5043.7504
2025-02-26 | 4912.917 | 16.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4668.9945
2025-02-26 | 4640.8262 | 17.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4555.0291
2025-02-26 | 4550.8179 | 17.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4426.3192
2025-02-26 | 4558.1362 | 17.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4454.2426
2025-02-26 | 4690.3789 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4633.2972
2025-02-26 | 5158.8711 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4974.0593
2025-02-26 | 5610.6689 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5423.9081
2025-02-26 | 5898.4888 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5895.9381
2025-02-26 | 6042.2739 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6240.219
2025-02-26 | 5874.8291 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.3368
2025-02-26 | 5639.5562 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6256.6774
2025-02-26 | 5453.4868 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6212.5162
2025-02-26 | 5247.7339 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6022.8958
2025-02-26 | 5081.394 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5872.5486
2025-02-26 | 4999.2432 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5903.8368
2025-02-26 | 5201.7749 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6257.5061
2025-02-26 | 5926.9639 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6818.2244
2025-02-26 | 6726.3481 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7019.6774
2025-02-26 | 6950.6719 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7130.3865
2025-02-26 | 7077.3628 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7287.762
2025-02-26 | 6971.7471 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7140.8575
2025-02-26 | 6638.0459 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6616.4204
2025-02-26 | 6062.2222 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5992.2223
2025-02-26 | 5504.645 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5483.763
2025-02-27 | 5195.561 | 20.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5120.0073
2025-02-27 | 5000.1792 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4973.041
2025-02-27 | 4939.4131 | 21.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.3343
2025-02-27 | 4950.8232 | 23.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5114.2614
2025-02-27 | 5112.519 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5381.3185
2025-02-27 | 5459.2271 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5601.0771
2025-02-27 | 5966.2622 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6072.9266
2025-02-27 | 6315.9922 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6390.9522
2025-02-27 | 6369.2368 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6559.228
2025-02-27 | 6218.2739 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6557.3431
2025-02-27 | 6172.2749 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6498.6843
2025-02-27 | 6210.1089 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6454.5231
2025-02-27 | 6222.6802 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6264.9027
2025-02-27 | 6163.106 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6125.5558
2025-02-27 | 6041.2749 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6090.8421
2025-02-27 | 6257.4038 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400.5102
2025-02-27 | 6891.0928 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.2278
2025-02-27 | 7491.0649 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7140.6808
2025-02-27 | 7600.5762 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7152.3871
2025-02-27 | 7451.1001 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7144.7579
2025-02-27 | 7215.5991 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6854.8494
2025-02-27 | 6818.7969 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6209.4088
2025-02-27 | 6230.2031 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5552.2098
2025-02-27 | 5581.2168 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5054.7507
2025-02-28 | 5187.124 | 16.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.9964
2025-02-28 | 4983.2402 | 18.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4720.0338
2025-02-28 | 5000.9629 | 22.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5009.3359
2025-02-28 | 5175.168 | 25 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5268.2658
2025-02-28 | 5453.7642 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5645.326
2025-02-28 | 5834.9331 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6184.0937
2025-02-28 | 6419.061 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6666.9435
2025-02-28 | 6733.667 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7193.9751
2025-02-28 | 6647.5679 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7384.2515
2025-02-28 | 6387.2119 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7404.3672
2025-02-28 | 6193.6641 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7400.7099
2025-02-28 | 6118.8208 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7301.5472
2025-02-28 | 5974.7002 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7100.9265
2025-02-28 | 5790.4492 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6972.58
2025-02-28 | 5908.7729 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6981.8675
2025-02-28 | 6287.9282 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7313.5362
2025-02-28 | 6910.6938 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7830.2532
2025-02-28 | 7488.478 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8075.7075
2025-02-28 | 7786.2979 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8263.4187
2025-02-28 | 7822.0352 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8244.7892
2025-02-28 | 7645.1289 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8031.8829
2025-02-28 | 7277.2998 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7463.4445
2025-02-28 | 6735.6431 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6828.2461
2025-02-28 | 6200.4531 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6253.7849
2025-03-01 | 5899.2358 | 27.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6135.5028
2025-03-01 | 5551.4058 | 26.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5900.5339
2025-03-01 | 5350.499 | 26.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5771.8241
2025-03-01 | 5251.4961 | 26.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5744.7459
2025-03-01 | 5255.251 | 26.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5857.7986
2025-03-01 | 5358.7969 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6165.5597
2025-03-01 | 5642.687 | 26 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6538.4064
2025-03-01 | 6095.8052 | 25.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6845.4317
2025-03-01 | 6678.1392 | 24.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7013.7075
2025-03-01 | 7110.4082 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7000.8222
2025-03-01 | 7560.7412 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7085.1675
2025-03-01 | 7799.603 | 25.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7151.0094
2025-03-01 | 7836.7769 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7192.3956
2025-03-01 | 7725.8462 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7273.055
2025-03-01 | 7723.4209 | 28.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7348.3444
2025-03-01 | 7749.7021 | 27.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7680.0132
2025-03-01 | 8238.9658 | 28.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8306.7333
2025-03-01 | 8679.3047 | 28.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8574.1882
2025-03-01 | 8786.6094 | 29.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8706.8979
2025-03-01 | 8548.6904 | 30.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8721.2693
2025-03-01 | 8212.833 | 30.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8563.3645
2025-03-01 | 7806.458 | 31.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8093.929
2025-03-01 | 7386.873 | 32.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7546.7331
2025-03-01 | 7029.5718 | 33.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7148.2769
2025-03-02 | 6746.7139 | 33.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.5241
2025-03-02 | 6595.7148 | 35 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6791.5593
2025-03-02 | 6496.3042 | 36.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6794.8532
2025-03-02 | 6498.7441 | 37.1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6877.7782
2025-03-02 | 6635.9541 | 37.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7078.8334
2025-03-02 | 6764.5649 | 38.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7540.5989
2025-03-02 | 7215.4038 | 39 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7968.4471
2025-03-02 | 7756.7192 | 39.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8374.4753
2025-03-02 | 8270.0449 | 38.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8520.7504
2025-03-02 | 8560.8887 | 37.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8452.8636
2025-03-02 | 8640.5596 | 36.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8328.2029
2025-03-02 | 8550.4023 | 35.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8196.0392
2025-03-02 | 8331.3154 | 33.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7962.4175
2025-03-02 | 8305.0488 | 32.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0698
2025-03-02 | 8268.5693 | 31.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7733.3554
2025-03-02 | 8270.5771 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8054.0238
2025-03-02 | 8780.1416 | 30.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8548.7402
2025-03-02 | 9210.8975 | 30.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8783.1941
2025-03-02 | 9728.4639 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8849.9019
2025-03-02 | 9324.0039 | 32 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8930.2753
2025-03-02 | 9093.6816 | 33.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8871.3733
2025-03-02 | 8484.2285 | 34 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8379.9372
2025-03-02 | 7742.4678 | 37.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8173.751
2025-03-02 | 7214.2461 | 36.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7566.2888
2025-03-03 | 6688.5181 | 36.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6902.0581
2025-03-03 | 6766.3271 | 37.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6832.094
2025-03-03 | 6862.7588 | 38.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6824.3876
2025-03-03 | 6668.3691 | 40.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6929.3131
2025-03-03 | 6818.7212 | 38.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6855.3605
2025-03-03 | 7198.709 | 39.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7317.126
2025-03-03 | 7730.4971 | 40.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7876.978
2025-03-03 | 7906.936 | 40.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8250.0052
2025-03-03 | 7765.5488 | 38.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8187.2744
2025-03-03 | 7378.3862 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7789.3782
2025-03-03 | 7090.8892 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7246.7056
2025-03-03 | 6899.7471 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6971.5378
2025-03-03 | 6697.6982 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.9143
2025-03-03 | 6491.3882 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6455.5652
2025-03-03 | 6500.373 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6420.8515
2025-03-03 | 6866.6729 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6763.5205
2025-03-03 | 7636.4839 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7302.2382
2025-03-03 | 8406.3037 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7525.6918
2025-03-03 | 8449.2939 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7669.4018
2025-03-03 | 8350.6191 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7705.7739
2025-03-03 | 8047.9551 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7470.8669
2025-03-03 | 7442.6401 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6847.427
2025-03-03 | 6793.7651 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6179.2276
2025-03-03 | 6202.355 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5648.7677
2025-03-04 | 5759.397 | 21.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5274.0117
2025-03-04 | 5548.957 | 21.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5061.0435
2025-03-04 | 5403.1758 | 21.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4943.334
2025-03-04 | 5360.9238 | 21.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4850.2539
2025-03-04 | 5413.9419 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4996.3076
2025-03-04 | 5778.917 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5348.0699
2025-03-04 | 6294.1279 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5709.9163
2025-03-04 | 6452.9282 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6082.9435
2025-03-04 | 6477.3149 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6163.2168
2025-03-04 | 6249.3921 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6117.3305
2025-03-04 | 6296.7358 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6014.6705
2025-03-04 | 6321.7451 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6124.5137
2025-03-04 | 6281.3638 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5956.8939
2025-03-04 | 6103.73 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5806.5467
2025-03-04 | 6122.5249 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5958.8384
2025-03-04 | 6359.5811 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6334.5083
2025-03-04 | 7075.7651 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6884.2263
2025-03-04 | 7708.0132 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7107.6799
2025-03-04 | 7535.9238 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7130.3865
2025-03-04 | 7531.2422 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7100.7566
2025-03-04 | 7389.1719 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6832.8487
2025-03-04 | 6735.7271 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6319.412
2025-03-04 | 6078.7241 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5706.2142
2025-03-04 | 5626.061 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5186.7545
2025-03-05 | 5214.5068 | 17.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4833.9992
2025-03-05 | 4940.4292 | 17.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4632.0313
2025-03-05 | 4784.5562 | 17.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.3217
2025-03-05 | 4703.6162 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4498.2439
2025-03-05 | 4873.3481 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4633.2972
2025-03-05 | 5197.3218 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4941.0583
2025-03-05 | 5747.7739 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5346.9059
2025-03-05 | 5976.0288 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5719.9331
2025-03-05 | 6079.8931 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5910.2096
2025-03-05 | 5962.313 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5930.3252
2025-03-05 | 5877.667 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5893.667
2025-03-05 | 5845.7349 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5849.5058
2025-03-05 | 5730.376 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5692.8864
2025-03-05 | 5742.2129 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5597.5408
2025-03-05 | 5847.416 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5738.8321
2025-03-05 | 6078.6982 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6147.503
2025-03-05 | 6774.6582 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6730.2219
2025-03-05 | 7414.853 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6942.6752
2025-03-05 | 7384.9199 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6965.3818
2025-03-05 | 7240.5249 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6935.7519
2025-03-05 | 6946.356 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6689.8447
2025-03-05 | 6502.291 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6088.4054
2025-03-05 | 5840.751 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5453.2069
2025-03-05 | 5181.0498 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5010.7495
2025-03-06 | 4788.2861 | 15.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4569.9917
2025-03-06 | 4543.543 | 15.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4368.0238
2025-03-06 | 4424.561 | 14.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151.3114
2025-03-06 | 4409.231 | 13.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.2307
2025-03-06 | 4625.8579 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4215.2853
2025-03-06 | 5022.9048 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4446.0442
2025-03-06 | 5528.832 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5027.8968
2025-03-06 | 5813.2451 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5510.9272
2025-03-06 | 5894.5679 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5723.2042
2025-03-06 | 5926.6899 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5721.3193
2025-03-06 | 5869.583 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5717.662
2025-03-06 | 5955.9702 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5706.5017
2025-03-06 | 5892.9858 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5648.8851
2025-03-06 | 5853.9019 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5564.5399
2025-03-06 | 5987.5039 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5661.8299
2025-03-06 | 6315.9229 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6114.502
2025-03-06 | 7180.7119 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6906.2269
2025-03-06 | 7800.9678 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7327.6861
2025-03-06 | 7954.1709 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7416.3946
2025-03-06 | 7866.6782 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7540.7692
2025-03-06 | 7774.0479 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7580.87
2025-03-06 | 7347.1738 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7144.4355
2025-03-06 | 6736.0591 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6586.2392
2025-03-06 | 6215.8579 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6121.7811
2025-03-07 | 5900.123 | 26.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5780.0261
2025-03-07 | 5627.9341 | 26.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5567.0579
2025-03-07 | 5464.5249 | 26.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5427.3478
2025-03-07 | 5514.188 | 25.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5367.2686
2025-03-07 | 5654.9292 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5502.322
2025-03-07 | 5988.8169 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865.0846
2025-03-07 | 6535.1489 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6303.9332
2025-03-07 | 6698.4072 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6555.9569
2025-03-07 | 6619.3081 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6625.2299
2025-03-07 | 6386.8301 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.3421
2025-03-07 | 6112.0908 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6454.683
2025-03-07 | 6060.0771 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6344.5199
2025-03-07 | 6041.4502 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6143.8992
2025-03-07 | 6010.3911 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6015.5527
2025-03-07 | 6016.333 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6090.8421
2025-03-07 | 6197.5059 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6488.5127
2025-03-07 | 6741.3198 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7093.2322
2025-03-07 | 7242.9102 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7393.688
2025-03-07 | 7390.5078 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7427.3949
2025-03-07 | 7438.1118 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7441.7664
2025-03-07 | 7220.0962 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7250.8606
2025-03-07 | 6908.7158 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6792.4254
2025-03-07 | 6350.9141 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6091.2251
2025-03-07 | 5937.7671 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5615.7667
2025-03-08 | 5557.3931 | 22.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5596.4874
2025-03-08 | 5329.4521 | 23.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5515.523
2025-03-08 | 5255.208 | 24.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5485.8159
2025-03-08 | 5195.1392 | 25 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5546.7402
2025-03-08 | 5348.9849 | 25.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5780.7964
2025-03-08 | 5649.6499 | 25.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6121.5585
2025-03-08 | 6128.4678 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6571.4073
2025-03-08 | 6584.624 | 26.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6966.4351
2025-03-08 | 7116.2231 | 26.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7167.7119
2025-03-08 | 7519.7788 | 26 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7187.8275
2025-03-08 | 7645.6089 | 25.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7140.169
2025-03-08 | 7721.9419 | 24.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7063.0069
2025-03-08 | 7421.498 | 23.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6829.3853
2025-03-08 | 7045.5049 | 22.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6646.0372
2025-03-08 | 6788.2979 | 21.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6611.3235
2025-03-08 | 6795.1128 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6865.99
2025-03-08 | 7137.8472 | 19.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7338.7057
2025-03-08 | 7584.8418 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7540.1587
2025-03-08 | 7611.833 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7639.8675
2025-03-08 | 7411.895 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7687.2399
2025-03-08 | 7134.2612 | 21.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7507.3344
2025-03-08 | 6800.6191 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7015.8983
2025-03-08 | 6322.2778 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6545.7046
2025-03-08 | 5907.3369 | 23.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6136.2481
2025-03-09 | 5606.2139 | 23.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5739.4915
2025-03-09 | 5449.5649 | 23.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5537.5236
2025-03-09 | 5268.6499 | 23.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5441.8147
2025-03-09 | 5268.7129 | 24.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5458.7377
2025-03-09 | 5348.855 | 23.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5516.7889
2025-03-09 | 5474.165 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5802.5494
2025-03-09 | 5839.5342 | 22.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6131.3948
2025-03-09 | 6425.939 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6482.4214
2025-03-09 | 6862.7568 | 21.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6606.6959
2025-03-09 | 7205.127 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6571.81
2025-03-09 | 7434.9609 | 19.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6436.149
2025-03-09 | 7405.583 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6369.9872
2025-03-09 | 7284.2178 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6224.368
2025-03-09 | 7071.626 | 16.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5997.0187
2025-03-09 | 6875.0972 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6094.3087
2025-03-09 | 7203.7319 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6447.9781
2025-03-09 | 7440.2329 | 17.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7096.6988
2025-03-09 | 7574.2861 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7276.1512
2025-03-09 | 7614.25 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7287.8574
2025-03-09 | 7408.6611 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7258.2276
2025-03-09 | 6885.6719 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7089.3225
2025-03-09 | 6139.835 | 19.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6740.8905
2025-03-09 | 5633.0679 | 19 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6105.692
2025-03-09 | 5216.3711 | 18.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5586.2324
2025-03-10 | 4860.4209 | 19 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4966.0029
2025-03-10 | 4643.5991 | 18.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4731.0341
2025-03-10 | 4636.1089 | 19 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4635.3252
2025-03-10 | 4773.7759 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4608.247
2025-03-10 | 5046.5098 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4776.3013
2025-03-10 | 5408.0571 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5117.0633
2025-03-10 | 5638.6982 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5588.9128
2025-03-10 | 5834.1309 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5983.9406
2025-03-10 | 5835.564 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6229.2186
2025-03-10 | 5524.2168 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6095.3299
2025-03-10 | 5626.9731 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5937.6683
2025-03-10 | 5564.5952 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5871.5064
2025-03-10 | 5332.9189 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5670.8857
2025-03-10 | 5196.5669 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5476.5373
2025-03-10 | 5263.1108 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5507.8255
2025-03-10 | 5768.022 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5872.4952
2025-03-10 | 6413.9209 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6422.2131
2025-03-10 | 6543.6509 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6667.6673
2025-03-10 | 6581.8271 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6778.3764
2025-03-10 | 6585.0449 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6869.7501
2025-03-10 | 6255.522 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6645.8434
2025-03-10 | 5685.5762 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6231.4095
2025-03-10 | 5069.5161 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5563.2101
2025-03-10 | 4743.7051 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5065.751
2025-03-11 | 4511.2271 | 17.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.9986
2025-03-11 | 4495.3691 | 18 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4643.0316
2025-03-11 | 4457.9609 | 18.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4569.3233
2025-03-11 | 4543.2051 | 19.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4630.2476
2025-03-11 | 4795.3052 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4787.3016
2025-03-11 | 5138.0112 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5172.0649
2025-03-11 | 5358.7451 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5566.9122
2025-03-11 | 5495.1221 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.9334
2025-03-11 | 5313.6631 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5327.1929
2025-03-11 | 5151.2471 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5116.302
2025-03-11 | 5103.271 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.6423
2025-03-11 | 4916.2749 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4925.4795
2025-03-11 | 4754.2432 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4790.8607
2025-03-11 | 4662.5479 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4662.5142
2025-03-11 | 4828.7061 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4880.8076
2025-03-11 | 5302.0732 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5751.4917
2025-03-11 | 6020.8579 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6048.2024
2025-03-11 | 6131.5181 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6458.6614
2025-03-11 | 6343.7842 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6646.3727
2025-03-11 | 6483.8911 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6902.751
2025-03-11 | 6195.4761 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6854.8494
2025-03-11 | 5569.4741 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6539.4182
2025-03-11 | 5134.4082 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6014.2229
2025-03-11 | 4843.0889 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5593.7661
2025-03-12 | 4632.0352 | 21.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5285.012
2025-03-12 | 4619.6348 | 22.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5171.0467
2025-03-12 | 4660.564 | 23.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5152.3399
2025-03-12 | 4806.9639 | 24.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5224.2646
2025-03-12 | 5179.9219 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5414.3195
2025-03-12 | 5672.3701 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5821.0834
2025-03-12 | 6048.541 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6259.9319
2025-03-12 | 6143.9189 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6665.9601
2025-03-12 | 6079.833 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6823.2356
2025-03-12 | 5935.2222 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6799.35
2025-03-12 | 6077.2778 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6751.6915
2025-03-12 | 6061.481 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6674.5293
2025-03-12 | 5896.8198 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6484.9089
2025-03-12 | 5888.6479 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6334.5618
2025-03-12 | 6023.0068 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6365.8499
2025-03-12 | 6508.1919 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6730.5196
2025-03-12 | 7141.042 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7258.2369
2025-03-12 | 7118.2119 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7448.6896
2025-03-12 | 7405.2549 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7548.3984
2025-03-12 | 7389.6519 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7573.7701
2025-03-12 | 7009.1279 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7426.8656
2025-03-12 | 6367.5591 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6869.4276
2025-03-12 | 5881.7622 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6388.2336
2025-03-12 | 5552.1899 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5912.7752
2025-03-13 | 5332.291 | 24.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5593.0208
2025-03-13 | 5246.0391 | 25.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5468.0551
2025-03-13 | 5154.2192 | 26.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5416.3474
2025-03-13 | 5328.1558 | 26.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5433.2705
2025-03-13 | 5620.2051 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5623.3254
2025-03-13 | 6068.0322 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5964.0875
2025-03-13 | 6196.0732 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6347.9344
2025-03-13 | 6570.9561 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6709.9613
2025-03-13 | 6419.582 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6812.2353
2025-03-13 | 6204.2832 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6645.3456
2025-03-13 | 6184.686 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6454.683
2025-03-13 | 5852.5869 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6256.5174
2025-03-13 | 5647.4829 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6044.8964
2025-03-13 | 5411.4111 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5828.5474
2025-03-13 | 5465.5679 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5793.8337
2025-03-13 | 5868.2661 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6037.4999
2025-03-13 | 6396.0928 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6499.2153
2025-03-13 | 6498.7339 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6788.6708
2025-03-13 | 6826.2661 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7031.3836
2025-03-13 | 6800.0791 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7023.7545
2025-03-13 | 6411.3091 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6854.8494
2025-03-13 | 5851.0942 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6484.4167
2025-03-13 | 5356.21 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5871.2189
2025-03-13 | 5050.5508 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5494.7633
2025-03-14 | 4849.7031 | 21.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5230.0105
2025-03-14 | 4721.4468 | 22.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5094.0445
2025-03-14 | 4781.52 | 21.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4921.3333
2025-03-14 | 4923.0352 | 21.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4927.2561
2025-03-14 | 5246.2158 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5161.3123
2025-03-14 | 5647.8779 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5458.073
2025-03-14 | 6007.4351 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5940.9229
2025-03-14 | 6143.7539 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6258.9485
2025-03-14 | 5849.1611 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6273.2199
2025-03-14 | 5640.8638 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5985.3268
2025-03-14 | 5489.3691 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5761.6633
2025-03-14 | 5361.3501 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5398.493
2025-03-14 | 4985.3501 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5131.8704
2025-03-14 | 4978.2231 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4904.5211
2025-03-14 | 4839.7061 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4979.8105
2025-03-14 | 5224.043 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5410.482
2025-03-14 | 5746.9902 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6037.2021
2025-03-14 | 5686.3428 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6205.6542
2025-03-14 | 5890.6572 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6437.3667
2025-03-14 | 5977.9639 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6495.7394
2025-03-14 | 5780.085 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6337.8346
2025-03-14 | 5229.6919 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5868.3991
2025-03-14 | 4810.2539 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5299.2026
2025-03-14 | 4472.9971 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4856.7451
2025-03-15 | 4151.854 | 15.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4815.4652
2025-03-15 | 4100.6689 | 15.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4635.4979
2025-03-15 | 4060.6279 | 16.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4594.7906
2025-03-15 | 4131.6519 | 16.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600.7133
2025-03-15 | 4342.4458 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.767
2025-03-15 | 4653.374 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5109.5296
2025-03-15 | 5237.647 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5548.3782
2025-03-15 | 5708.4971 | 16.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5877.4041
2025-03-15 | 5907.7832 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5946.6771
2025-03-15 | 5964.3872 | 12.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5724.7859
2025-03-15 | 5966.1191 | 10.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5512.1227
2025-03-15 | 5722.6621 | 7.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5137.9521
2025-03-15 | 5540.5732 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4871.3295
2025-03-15 | 5325.8608 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4654.9805
2025-03-15 | 5211.374 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4609.2664
2025-03-15 | 5684.6929 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5028.9376
2025-03-15 | 5998.3008 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743.6603
2025-03-15 | 5860.0552 | 4.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5901.112
2025-03-15 | 5836.2061 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6308.8296
2025-03-15 | 5604.8618 | 7.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6224.1982
2025-03-15 | 5248.7949 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5956.2903
2025-03-15 | 4760.1602 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5464.8541
2025-03-15 | 4333.0132 | 12.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5390.6717
2025-03-15 | 3907.426 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4497.2014
2025-03-16 | 3662.0769 | 7.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4012.4423
2025-03-16 | 3498.6431 | 8.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3909.4772
2025-03-16 | 3406 | 9.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3835.7689
2025-03-16 | 3442.4851 | 9.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3852.692
2025-03-16 | 3571.116 | 9.3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.7447
2025-03-16 | 3821.5139 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.508
2025-03-16 | 4238.5532 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4723.3547
2025-03-16 | 4975.751 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5184.3844
2025-03-16 | 5534.9351 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5352.6602
2025-03-16 | 6012.373 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5295.7736
2025-03-16 | 6257.2588 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5160.1126
2025-03-16 | 6447.689 | 5.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4983.9477
2025-03-16 | 6356.8638 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4871.3295
2025-03-16 | 6147.1338 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4797.9845
2025-03-16 | 6150.0142 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4642.2674
2025-03-16 | 6604.6328 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4852.9326
2025-03-16 | 6967.9878 | 3.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5578.6556
2025-03-16 | 6821.5781 | 4.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5934.113
2025-03-16 | 6640.4971 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6110.8239
2025-03-16 | 6300.084 | 6.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6169.1966
2025-03-16 | 5745.7529 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6011.2918
2025-03-16 | 5116.6948 | 8.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5585.8576
2025-03-16 | 4458.207 | 9.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5049.662
2025-03-16 | 4112.5532 | 10.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4662.2061
2025-03-17 | 3794.6431 | 12.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4272.9832
2025-03-17 | 3703.7571 | 13.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4159.0178
2025-03-17 | 3704.198 | 15.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4217.3133
2025-03-17 | 3835.009 | 15.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4201.2354
2025-03-17 | 4225.3179 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4457.2922
2025-03-17 | 4749.1108 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4798.0542
2025-03-17 | 5192.8188 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5390.9072
2025-03-17 | 5517.1118 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5939.9394
2025-03-17 | 5610.4048 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6196.2177
2025-03-17 | 5673.0942 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6293.3356
2025-03-17 | 5641.8911 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6322.6792
2025-03-17 | 5692.748 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6289.5184
2025-03-17 | 5492.0981 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6209.9011
2025-03-17 | 5453.7061 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6004.5524
2025-03-17 | 5517.873 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5903.8368
2025-03-17 | 5964.3242 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6114.502
2025-03-17 | 6405.6221 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6642.2194
2025-03-17 | 6337.1431 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6898.6739
2025-03-17 | 6755.1279 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7020.3833
2025-03-17 | 6825.8008 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7254.761
2025-03-17 | 6518.3311 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7041.8547
2025-03-17 | 5919.7529 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6550.4185
2025-03-17 | 5330.6738 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6135.2264
2025-03-17 | 4990.8418 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5615.7667
2025-03-18 | 4796.6938 | 21.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5274.0117
2025-03-18 | 4689.8208 | 23 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5193.0473
2025-03-18 | 4744.6221 | 23.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5141.3396
2025-03-18 | 4839.1631 | 23.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5070.2602
2025-03-18 | 5198.5249 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5359.3179
2025-03-18 | 5763.0278 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5711.0802
2025-03-18 | 6085.3901 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6072.9266
2025-03-18 | 6028.9761 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6247.9482
2025-03-18 | 5726.7778 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6119.2155
2025-03-18 | 5412.666 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5941.3255
2025-03-18 | 5333.4482 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5728.6623
2025-03-18 | 5051.4282 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5618.4992
2025-03-18 | 4809.3901 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5417.8785
2025-03-18 | 4752.334 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5201.5295
2025-03-18 | 4805.4902 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5221.8174
2025-03-18 | 5294.6499 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520.4851
2025-03-18 | 5844.1479 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6103.204
2025-03-18 | 5974.6279 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6414.6601
2025-03-18 | 6374.0991 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6668.3733
2025-03-18 | 6371.4961 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6880.7504
2025-03-18 | 6055.7739 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6678.8443
2025-03-18 | 5402.7119 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6099.4057
2025-03-18 | 4843.9419 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5585.2107
2025-03-18 | 4461.3428 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5065.751
2025-03-19 | 4222.5059 | 16.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.9964
2025-03-19 | 4160.353 | 16.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.0282
2025-03-19 | 4153.52 | 17.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4492.3211
2025-03-19 | 4292.3262 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4608.247
2025-03-19 | 4681.9702 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4655.2978
2025-03-19 | 5270.8481 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.0608
2025-03-19 | 5661.2461 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5412.9078
2025-03-19 | 5592.1919 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5686.9322
2025-03-19 | 5357.4351 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800.2064
2025-03-19 | 5123.3091 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5666.3177
2025-03-19 | 4820.4741 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5387.6526
2025-03-19 | 4709.8252 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5156.4861
2025-03-19 | 4358.3491 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4812.8613
2025-03-19 | 4299.105 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4618.5129
2025-03-19 | 4457.0859 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4583.7992
2025-03-19 | 4861.2832 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4849.466
2025-03-19 | 5222.3428 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5399.1839
2025-03-19 | 5358.1318 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5710.6401
2025-03-19 | 5489.397 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6052.3557
2025-03-19 | 5559.311 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6308.7341
2025-03-19 | 5257.1992 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6326.8343
2025-03-19 | 4684.3169 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5780.3966
2025-03-19 | 4146.292 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5321.2032
2025-03-19 | 3750.521 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4878.7457
2025-03-20 | 3489.531 | 15.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4580.992
2025-03-20 | 3359.4089 | 7.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3509.9993
2025-03-20 | 3310.501 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3315.2876
2025-03-20 | 3435.3311 | 7.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3299.2097
2025-03-20 | 3734.7749 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500.2649
2025-03-20 | 4214.457 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4050.0329
2025-03-20 | 4563.1089 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4411.8793
2025-03-20 | 4697.2852 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4564.9002
2025-03-20 | 4513.7109 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4546.1707
2025-03-20 | 4419.334 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.2826
2025-03-20 | 4351.0088 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4309.6219
2025-03-20 | 4418.5552 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4221.4594
2025-03-20 | 4248.9922 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.8481
2025-03-20 | 4332.6382 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4398.5066
2025-03-20 | 4536.3628 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4594.7995
2025-03-20 | 5295.7568 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5333.4798
2025-03-20 | 5809.9888 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5905.1984
2025-03-20 | 5916.2891 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6150.6526
2025-03-20 | 5988.1582 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6294.3626
2025-03-20 | 5944.2271 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6396.7366
2025-03-20 | 5576.1611 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6238.8318
2025-03-20 | 4973.647 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5736.3954
2025-03-20 | 4396.8569 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5453.2069
2025-03-20 | 4125.9268 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5153.7536
2025-03-21 | 3972.667 | 18.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4878.0004
2025-03-21 | 4028.5129 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4753.0347
2025-03-21 | 4098.8999 | 20 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4745.3283
2025-03-21 | 4285.4961 | 20.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4751.2511
2025-03-21 | 4701.2129 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.3085
2025-03-21 | 5252.1079 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5491.074
2025-03-21 | 5700.9712 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5962.9235
2025-03-21 | 5845.5908 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6313.95
2025-03-21 | 5736.791 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6438.2246
2025-03-21 | 5461.9502 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.3368
2025-03-21 | 5366.082 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6245.677
2025-03-21 | 5253.105 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6069.5121
2025-03-21 | 5169.438 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5747.8879
2025-03-21 | 5045.6069 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5553.5395
2025-03-21 | 5067.459 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5463.8243
2025-03-21 | 5312.1431 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5795.493
2025-03-21 | 5739.3208 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6268.2087
2025-03-21 | 5746.0859 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6458.6614
2025-03-21 | 6085.3691 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6679.3736
2025-03-21 | 6184.541 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6748.7466
2025-03-21 | 5926.8838 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6623.8428
2025-03-21 | 5539.1792 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6099.4057
2025-03-21 | 5094.6069 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5629.212
2025-03-21 | 4709.9482 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5197.7548
2025-03-22 | 4420.585 | 18.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200.4761
2025-03-22 | 4364.8682 | 19.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5053.5098
2025-03-22 | 4334.2129 | 18.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4847.7978
2025-03-22 | 4335.8818 | 18.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4820.7196
2025-03-22 | 4515.8018 | 18.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5021.7748
2025-03-22 | 4831.1089 | 20.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5505.5409
2025-03-22 | 5401.9521 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5790.3851
2025-03-22 | 5951.562 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6053.4091
2025-03-22 | 6200.0142 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6034.6796
2025-03-22 | 6255.0581 | 13.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5768.7871
2025-03-22 | 6355.6089 | 11.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5622.1258
2025-03-22 | 6501.0308 | 11.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5610.9655
2025-03-22 | 6344.4268 | 12.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5652.3517
2025-03-22 | 6311.04 | 13.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5656.009
2025-03-22 | 6394.6548 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6292.3144
2025-03-22 | 7006.8662 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6865.99
2025-03-22 | 7263.5488 | 21.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7547.7117
2025-03-22 | 7411.3569 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7848.1675
2025-03-22 | 7101.9678 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7925.8756
2025-03-22 | 7028.5342 | 23.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7962.2477
2025-03-22 | 6765.231 | 23.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7793.3426
2025-03-22 | 6358.4238 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7312.9068
2025-03-22 | 5866.1611 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6765.7108
2025-03-22 | 5535.2891 | 26 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6367.2546
2025-03-23 | 5270.4961 | 26.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6069.5009
2025-03-23 | 5153.4731 | 27.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5955.5355
2025-03-23 | 5165.3418 | 27.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5859.8266
2025-03-23 | 5245.291 | 28 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5876.7496
2025-03-23 | 5437.1128 | 28.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6066.8046
2025-03-23 | 5743.647 | 28.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6451.5679
2025-03-23 | 6297.73 | 29.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6890.4164
2025-03-23 | 6842.5659 | 28.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7208.442
2025-03-23 | 7136.0439 | 27.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7299.7156
2025-03-23 | 7347.208 | 26.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7286.8304
2025-03-23 | 7252.7612 | 25.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7173.17
2025-03-23 | 7115.938 | 24.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7008.0053
2025-03-23 | 6948.2378 | 23.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6796.3843
2025-03-23 | 6824.6768 | 21.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6536.034
2025-03-23 | 6830.3301 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6457.3191
2025-03-23 | 7213.3262 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6821.9887
2025-03-23 | 7463.292 | 19.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7349.706
2025-03-23 | 7395.1118 | 19.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7529.1584
2025-03-23 | 7449.103 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7727.87
2025-03-23 | 7316.8882 | 22.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7852.2446
2025-03-23 | 6964.4971 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7815.3432
2025-03-23 | 6255.2979 | 23.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7213.904
2025-03-23 | 5564.1348 | 23.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6578.7055
2025-03-23 | 5253.938 | 23.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6092.2468
2025-03-24 | 4910.3999 | 22.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5362.0142
2025-03-24 | 4955.521 | 22.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5116.0451
2025-03-24 | 4918.417 | 22.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4998.3355
2025-03-24 | 5023.6611 | 21.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4927.2561
2025-03-24 | 5283.8662 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.3085
2025-03-24 | 5842.7119 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5370.0705
2025-03-24 | 6313.688 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5885.9213
2025-03-24 | 6460.6182 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6302.9497
2025-03-24 | 6438.6089 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6482.2258
2025-03-24 | 6352.7549 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6469.3406
2025-03-24 | 6258.1689 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6267.6777
2025-03-24 | 6149.3301 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6069.5121
2025-03-24 | 5997.3481 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5604.8839
2025-03-24 | 5920.8159 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5333.5333
2025-03-24 | 5876.854 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5474.8246
2025-03-24 | 6387.7598 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5817.4936
2025-03-24 | 6678.1362 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6334.2106
2025-03-24 | 6789.084 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.6633
2025-03-24 | 6909.4302 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6371.3648
2025-03-24 | 6889 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6484.7391
2025-03-24 | 6465.373 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6491.839
2025-03-24 | 5680.6201 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6044.4041
2025-03-24 | 5093.5942 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5519.2088
2025-03-24 | 4744.23 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5054.7507
2025-03-25 | 4547.9868 | 17.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4767.9973
2025-03-25 | 4443.229 | 17.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.0304
2025-03-25 | 4469.5269 | 17.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.3214
2025-03-25 | 4600.8101 | 17.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4454.2426
2025-03-25 | 4919.6279 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4567.2953
2025-03-25 | 5359.0669 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4908.0574
2025-03-25 | 5713.5581 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5335.9056
2025-03-25 | 5919.7529 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5686.9322
2025-03-25 | 5829.7969 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800.2064
2025-03-25 | 5734.7041 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5809.3218
2025-03-25 | 5788.71 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5794.6642
2025-03-25 | 5633.2241 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5728.5024
2025-03-25 | 5525.2329 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5527.8817
2025-03-25 | 5469.311 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5531.5389
2025-03-25 | 5708.1289 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5683.8305
2025-03-25 | 6423.0928 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5993.4986
2025-03-25 | 6961.2441 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6554.2169
2025-03-25 | 6926.8149 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6876.6733
2025-03-25 | 7062.688 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6998.3827
2025-03-25 | 6901.1948 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7023.7545
2025-03-25 | 6533.1089 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6810.8481
2025-03-25 | 5752.3472 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6330.4123
2025-03-25 | 5184.019 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5761.2157
2025-03-25 | 4803.5752 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5296.7576
2025-03-26 | 4581.1768 | 19.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5010.0042
2025-03-26 | 4492.2788 | 20.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.0385
2025-03-26 | 4470.8711 | 20.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800.3299
2025-03-26 | 4665.2041 | 20.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4773.2517
2025-03-26 | 5031.1118 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4908.3051
2025-03-26 | 5502.5811 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5304.0687
2025-03-26 | 5867.4619 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5698.916
2025-03-26 | 6004.6382 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994.941
2025-03-26 | 5560.9521 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6163.2168
2025-03-26 | 5369.0898 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6150.3315
2025-03-26 | 5392.627 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6069.672
2025-03-26 | 5552.814 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6014.5105
2025-03-26 | 5513.1099 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5758.8883
2025-03-26 | 5462.019 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5718.5442
2025-03-26 | 5560.5439 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5694.8308
2025-03-26 | 6244.6338 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6103.5017
2025-03-26 | 6837.3682 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6807.2241
2025-03-26 | 6829.1631 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7085.6793
2025-03-26 | 7024.0298 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7163.3874
2025-03-26 | 7031.5898 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7232.7604
2025-03-26 | 6657.1328 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6975.8528
2025-03-26 | 5952.8052 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6484.4167
2025-03-26 | 5328.9971 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5926.2204
2025-03-26 | 5000.1392 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5538.7645
2025-03-27 | 4794.2051 | 21.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5219.0101
2025-03-27 | 4702.8271 | 21.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5028.0426
2025-03-27 | 4728.7588 | 21.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4899.3327
2025-03-27 | 4887.459 | 22.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4949.2567
2025-03-27 | 5242.7329 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5128.3113
2025-03-27 | 5824.1338 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5557.0759
2025-03-27 | 6099.2402 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6039.9257
2025-03-27 | 6011.1538 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6225.9475
2025-03-27 | 5686.5181 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6152.2164
2025-03-27 | 5369.2769 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.3284
2025-03-27 | 5321.5908 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5805.6645
2025-03-27 | 5284.1479 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5640.4999
2025-03-27 | 5076.3569 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5307.8754
2025-03-27 | 4931.4512 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5157.5283
2025-03-27 | 5010.9912 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5089.8136
2025-03-27 | 5672.4678 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5465.4836
2025-03-27 | 6109.21 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6037.2021
2025-03-27 | 6325.6362 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6436.6608
2025-03-27 | 6652.4238 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6525.3692
2025-03-27 | 6724.5552 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6594.7422
2025-03-27 | 6358.5918 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6480.8387
2025-03-27 | 5660.0898 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6000.4029
2025-03-27 | 5102.7139 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5453.2069
2025-03-27 | 4712.1089 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5021.7498
2025-03-28 | 4468.7129 | 16.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.9964
2025-03-28 | 4415.0562 | 18.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4698.0332
2025-03-28 | 4472.394 | 20.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.3302
2025-03-28 | 4595.6382 | 22.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4993.258
2025-03-28 | 4995.105 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5249.3148
2025-03-28 | 5522.5122 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5656.0787
2025-03-28 | 5942.4438 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6116.9279
2025-03-28 | 6146.1689 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6423.9532
2025-03-28 | 6005.4111 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6548.2277
2025-03-28 | 5680.5801 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6513.3418
2025-03-28 | 5492.9819 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6432.6824
2025-03-28 | 5378.9639 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6267.5177
2025-03-28 | 5133.4131 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5956.8939
2025-03-28 | 5177.3091 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5784.5461
2025-03-28 | 5568.1362 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5870.8358
2025-03-28 | 6229.6611 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6213.5049
2025-03-28 | 6634.1992 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6763.2228
2025-03-28 | 6605.7578 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6997.6767
2025-03-28 | 6759.7368 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7119.3861
2025-03-28 | 6772.5972 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7155.7582
2025-03-28 | 6421.0581 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7074.8556
2025-03-28 | 5887.3691 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6616.4204
2025-03-28 | 5308.312 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6047.2239
2025-03-28 | 4569.397 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5538.7645
2025-03-29 | 4812.9409 | 21.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5497.4846
2025-03-29 | 4268.4502 | 21.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5317.5173
2025-03-29 | 4600.3418 | 21.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5210.8081
2025-03-29 | 4680.0742 | 21.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5183.7299
2025-03-29 | 4902.2578 | 21.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5329.7836
2025-03-29 | 5316.479 | 21.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5659.5453
2025-03-29 | 5815.2822 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6164.3957
2025-03-29 | 6464.4561 | 22.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6559.4235
2025-03-29 | 7087.0952 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6760.7003
2025-03-29 | 7394.085 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6813.8169
2025-03-29 | 7786.3408 | 22.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6799.1593
2025-03-29 | 7696.9092 | 22.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6787.9991
2025-03-29 | 7589.5962 | 21.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6631.3796
2025-03-29 | 7411.1421 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6481.0325
2025-03-29 | 7465.6831 | 19.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6446.3188
2025-03-29 | 7612.3398 | 18.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6722.9859
2025-03-29 | 7952.2222 | 18.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7261.7035
2025-03-29 | 7737.2769 | 19.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7617.1609
2025-03-29 | 7391.5732 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7661.8681
2025-03-29 | 7139.873 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7654.2389
2025-03-29 | 6790.1421 | 21.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7496.3341
2025-03-29 | 6211.9731 | 21.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6982.8974
2025-03-29 | 5711.2168 | 20.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6314.698
2025-03-29 | 5244.3931 | 20.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5806.2386
2025-03-30 | 4950.5298 | 20.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5409.4821
2025-03-30 | 4867.6519 | 20.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5196.5139
2025-03-30 | 4788.9839 | 20.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5045.8034
2025-03-30 | 4841.0918 | 19.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4985.7243
2025-03-30 | 4956.3428 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5142.7782
2025-03-30 | 5252.9058 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5483.5403
2025-03-30 | 5755.2588 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5889.3879
2025-03-30 | 6425.793 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6284.4157
2025-03-30 | 7011.1719 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6485.6925
2025-03-30 | 7612.2212 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6549.8094
2025-03-30 | 7845.2798 | 19.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.1515
2025-03-30 | 7736.0361 | 19.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6501.9909
2025-03-30 | 7686.583 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6345.3715
2025-03-30 | 7583.5781 | 18.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250.0259
2025-03-30 | 7494.5552 | 18.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6303.3147
2025-03-30 | 8025.2861 | 18.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6656.984
2025-03-30 | 8222.7598 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7206.7019
2025-03-30 | 7915.8301 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7419.1553
2025-03-30 | 7712.9492 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7441.8618
2025-03-30 | 7334.187 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7412.232
2025-03-30 | 6801.8091 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7166.3247
2025-03-30 | 5985.686 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6630.8873
2025-03-30 | 5369.0972 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6006.6892
2025-03-30 | 4906.6582 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5487.2296
2025-03-31 | 4639.2378 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.9998
2025-03-31 | 4535.147 | 17.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4632.0313
2025-03-31 | 4476.6812 | 17.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.3217
2025-03-31 | 4595.4878 | 17.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4487.2436
2025-03-31 | 4865.8599 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4611.2966
2025-03-31 | 5334.0361 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4919.0577
2025-03-31 | 5586.417 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5346.9059
2025-03-31 | 5779.6631 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5697.9325
2025-03-31 | 5669.1279 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5635.2017
2025-03-31 | 5481.498 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5336.3083
2025-03-31 | 5293.8188 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5178.6466
2025-03-31 | 5048.2432 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5552.4974
2025-03-31 | 5117.9941 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5131.8704
2025-03-31 | 5168.7861 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5014.5242
2025-03-31 | 5395.3311 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5023.8117
2025-03-31 | 6001.313 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5630.4883
2025-03-31 | 6476.875 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6499.2153
2025-03-31 | 6510.8579 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6821.6717
2025-03-31 | 6558.792 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6800.377
2025-03-31 | 6551.1318 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6946.7523
2025-03-31 | 6291.4268 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6799.8478
2025-03-31 | 5714.6162 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6330.4123
2025-03-31 | 4990.8311 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5761.2157
2025-03-31 | 4725.7739 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5274.757
2025-04-01 | 5095.7969 | 18.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944.0023
2025-04-01 | 4985.8149 | 19.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4775.0354
2025-04-01 | 5013.7959 | 19.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4657.3258
2025-04-01 | 5119.3999 | 19.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4652.2483
2025-04-01 | 5464.958 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4897.3047
2025-04-01 | 6088.2231 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5249.0671
2025-04-01 | 6376.106 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5786.9185
2025-04-01 | 6316.873 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6148.9453
2025-04-01 | 6053.4131 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6427.2243
2025-04-01 | 6033.666 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6436.3396
2025-04-01 | 6036.0171 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6344.6799
2025-04-01 | 6051.9932 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6267.5177
2025-04-01 | 5980.939 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6044.8964
2025-04-01 | 5858.2529 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5916.5499
2025-04-01 | 5962.4082 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5936.8377
2025-04-01 | 6530.7939 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6290.5071
2025-04-01 | 7017.5449 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6884.2263
2025-04-01 | 6977.2051 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.6802
2025-04-01 | 7341.4932 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7240.3896
2025-04-01 | 7459.5059 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7353.7639
2025-04-01 | 7159.9639 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7206.8594
2025-04-01 | 6573.1919 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6737.4239
2025-04-01 | 6029.8638 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6212.2286
2025-04-01 | 5697.9858 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5802.772
2025-04-02 | 5493.8301 | 23.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5483.0177
2025-04-02 | 5405.3872 | 24.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5358.052
2025-04-02 | 5498.7588 | 25.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5350.3456
2025-04-02 | 5608.8638 | 26.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5411.2699
2025-04-02 | 5924.3262 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5623.3254
2025-04-02 | 6512.7129 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.0862
2025-04-02 | 6894.1538 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6314.9335
2025-04-02 | 6856.9131 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6500.9554
2025-04-02 | 6549.875 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6515.2268
2025-04-02 | 6349.231 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6348.3371
2025-04-02 | 6377.5742 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6267.6777
2025-04-02 | 6483.7651 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6146.5143
2025-04-02 | 6391.334 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6055.8967
2025-04-02 | 6455.3179 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5883.5489
2025-04-02 | 6680.1348 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6013.8399
2025-04-02 | 7429.793 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6367.5093
2025-04-02 | 8148.54 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6983.2291
2025-04-02 | 7950.0708 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7228.6833
2025-04-02 | 7957.0088 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7482.3965
2025-04-02 | 7923.502 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7463.767
2025-04-02 | 7422.5352 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7184.8588
2025-04-02 | 6669.1909 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6616.4204
2025-04-02 | 6076.8481 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5926.2204
2025-04-02 | 5602.7979 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5384.7601
2025-04-03 | 5340.4009 | 19 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4966.0029
2025-04-03 | 5201.0459 | 18.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4687.0329
2025-04-03 | 5239.7212 | 18.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4547.3227
2025-04-03 | 5261.0112 | 17.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4487.2436
2025-04-03 | 5568.4238 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600.2963
2025-04-03 | 6055.9312 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4875.0564
2025-04-03 | 6261.8398 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4917.8937
2025-04-03 | 6295.6538 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5191.9181
2025-04-03 | 6187.7998 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250.1908
2025-04-03 | 6027.7759 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5127.3023
2025-04-03 | 5964.6289 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5046.6429
2025-04-03 | 5812.4028 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4793.4757
2025-04-03 | 5472.9678 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.845
2025-04-03 | 5250.2441 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3991.495
2025-04-03 | 5247.2031 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4309.2051
2025-04-03 | 5690.1328 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4512.3069
2025-04-03 | 6043.4072 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5109.7389
2025-04-03 | 6033.2578 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5325.6291
2025-04-03 | 6219.605 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5843.3498
2025-04-03 | 6379.6431 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5967.7244
2025-04-03 | 6128.3779 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5864.8211
2025-04-03 | 5525.6128 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5461.3875
2025-04-03 | 5001.0298 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4969.1932
2025-04-03 | 4499.022 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4735.7416
2025-04-04 | 4318.2202 | 13.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4382.9863
2025-04-04 | 4294.5229 | 14.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4258.0206
2025-04-04 | 4256.5508 | 14.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151.3114
2025-04-04 | 4440.563 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4388.2407
2025-04-04 | 4742.2041 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.2906
2025-04-04 | 5349.0059 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4853.0558
2025-04-04 | 5849.5752 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5225.9025
2025-04-04 | 5908.5742 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5477.9262
2025-04-04 | 5632.2778 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5624.2014
2025-04-04 | 5417.5142 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5556.3146
2025-04-04 | 5361.6782 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5442.6542
2025-04-04 | 5331.0708 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5266.4892
2025-04-04 | 5158.5142 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5032.8676
2025-04-04 | 5036.7588 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4915.5214
2025-04-04 | 5108.3828 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4869.8073
2025-04-04 | 5360.002 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5201.476
2025-04-04 | 5740.7461 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5729.1933
2025-04-04 | 5779.042 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6029.6492
2025-04-04 | 6079.0171 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6195.3598
2025-04-04 | 6296.626 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6341.735
2025-04-04 | 6081.291 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6150.8293
2025-04-04 | 5614.7051 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5736.3954
2025-04-04 | 5162.3662 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5321.2032
2025-04-04 | 4805.2231 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4889.746
2025-04-05 | 4444.5488 | 14.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4716.4623
2025-04-05 | 4332.7168 | 15 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4591.4967
2025-04-05 | 4348.6548 | 14.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4429.7859
2025-04-05 | 4413.1108 | 14.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.7083
2025-04-05 | 4587.1782 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4559.7616
2025-04-05 | 4978.1118 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944.5249
2025-04-05 | 5493.2642 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5405.3741
2025-04-05 | 6181.0059 | 15.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800.4019
2025-04-05 | 6714.7041 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6001.6787
2025-04-05 | 7103.7271 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6087.7962
2025-04-05 | 7320.082 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6139.1405
2025-04-05 | 7232.5459 | 16.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6160.9812
2025-04-05 | 7067.9258 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5993.3614
2025-04-05 | 7092.4312 | 15.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5876.0152
2025-04-05 | 7007.8379 | 14.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5830.3012
2025-04-05 | 7288.2329 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6249.9724
2025-04-05 | 7452.8008 | 14.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6788.69
2025-04-05 | 7321.458 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6935.1415
2025-04-05 | 7117.0908 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6946.8477
2025-04-05 | 6763.9248 | 14.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6983.2198
2025-04-05 | 6402.4229 | 14.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6770.3135
2025-04-05 | 5761.936 | 14.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6201.8751
2025-04-05 | 5263.604 | 14.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5577.677
2025-04-05 | 4918.5039 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5135.2195
2025-04-06 | 4597.5601 | 15.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4870.4667
2025-04-06 | 4504.6182 | 15.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4635.4979
2025-04-06 | 4391.8662 | 15.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4506.788
2025-04-06 | 4437.9399 | 15.3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4479.7099
2025-04-06 | 4533.1162 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.7638
2025-04-06 | 4876.9658 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4900.5237
2025-04-06 | 5478.9922 | 14.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5262.37
2025-04-06 | 6290.8428 | 14.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5646.3975
2025-04-06 | 6768.2759 | 14.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5836.674
2025-04-06 | 6985.377 | 13.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.7887
2025-04-06 | 6968.4141 | 13.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5776.1302
2025-04-06 | 6925.4868 | 11.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5621.9658
2025-04-06 | 6868.8931 | 11.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5531.3483
2025-04-06 | 6662.749 | 12.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5502.0046
2025-04-06 | 6672.8989 | 11.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5478.2912
2025-04-06 | 7095.2998 | 11.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5908.9627
2025-04-06 | 7394.7012 | 11.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6513.6822
2025-04-06 | 7275.0498 | 12.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6825.1383
2025-04-06 | 7223.042 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6968.8484
2025-04-06 | 7223.415 | 15.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7126.2239
2025-04-06 | 6727.6699 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6935.3182
2025-04-06 | 6009.9639 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6366.8798
2025-04-06 | 5368.9951 | 16.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5841.6845
2025-04-06 | 4992.5552 | 18.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5520.2305
2025-04-07 | 4762.3608 | 18.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4922.0017
2025-04-07 | 4738.8872 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4863.0379
2025-04-07 | 4774.6821 | 20.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4778.3293
2025-04-07 | 4867.9438 | 20.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4795.2523
2025-04-07 | 5258.6128 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5183.3129
2025-04-07 | 5892.8271 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5293.0683
2025-04-07 | 6126.1108 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5819.9194
2025-04-07 | 5963.04 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5840.9366
2025-04-07 | 5684.896 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5723.2042
2025-04-07 | 5531.6362 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5545.3142
2025-04-07 | 5466.0122 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5475.6551
2025-04-07 | 5440.835 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5343.4914
2025-04-07 | 5268.6919 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5219.8729
2025-04-07 | 5286.3511 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.5251
2025-04-07 | 5308.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4968.8102
2025-04-07 | 5796.9839 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5487.4842
2025-04-07 | 6353.5381 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6015.2015
2025-04-07 | 6538.394 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6304.657
2025-04-07 | 6554.0752 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6459.3673
2025-04-07 | 6716.894 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6539.7407
2025-04-07 | 6342.2319 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6557.8409
2025-04-07 | 5694.0752 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6044.4041
2025-04-07 | 5113.7129 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5585.2107
2025-04-07 | 4785.0308 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5175.7542
2025-04-08 | 4597.2612 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.9998
2025-04-08 | 4574.9331 | 18.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4654.0319
2025-04-08 | 4684.1489 | 18.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4558.323
2025-04-08 | 4895.1211 | 18.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4564.2458
2025-04-08 | 5247.1982 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4732.3
2025-04-08 | 5803.2939 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5205.0658
2025-04-08 | 6192.4741 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5676.9153
2025-04-08 | 6415.749 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6115.9444
2025-04-08 | 6478.5898 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6592.229
2025-04-08 | 6513.8359 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6788.3497
2025-04-08 | 6704.9741 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6839.694
2025-04-08 | 6752.126 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6872.535
2025-04-08 | 6037.6602 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6759.9168
2025-04-08 | 6037.1289 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6598.5693
2025-04-08 | 6244.3921 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6640.8578
2025-04-08 | 6938.2642 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6994.5271
2025-04-08 | 7504.1738 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7368.24
2025-04-08 | 7395.6792 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7547.6924
2025-04-08 | 7365.77 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7570.399
2025-04-08 | 7588.585 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7540.7692
2025-04-08 | 7154.8428 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7371.8641
2025-04-08 | 6405.687 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6979.4308
2025-04-08 | 5804.8911 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6520.2373
2025-04-08 | 5402.3682 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6077.7799
2025-04-09 | 5167.3008 | 24.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5571.0202
2025-04-09 | 5068.0498 | 25.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5435.0542
2025-04-09 | 5044.7959 | 26.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5493.3496
2025-04-09 | 5209.5508 | 29 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5708.2783
2025-04-09 | 5610.001 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.3339
2025-04-09 | 6234.7051 | 31.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6448.1012
2025-04-09 | 6439.791 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6644.9429
2025-04-09 | 6275.7432 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6962.9685
2025-04-09 | 5933.1328 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6867.2368
2025-04-09 | 5693.0298 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6667.3462
2025-04-09 | 5557.4648 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6531.6852
2025-04-09 | 5589.3369 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6421.5221
2025-04-09 | 5498.9292 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6198.9008
2025-04-09 | 5415.397 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5993.5521
2025-04-09 | 5520.251 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5980.839
2025-04-09 | 6308.1201 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6290.5071
2025-04-09 | 6725.9932 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6851.2253
2025-04-09 | 6703.3218 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7008.6771
2025-04-09 | 6800.998 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7042.3839
2025-04-09 | 6971.085 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7144.7579
2025-04-09 | 6668.5151 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7206.8594
2025-04-09 | 5920.1309 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6594.4198
2025-04-09 | 5287.2432 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5992.2223
2025-04-09 | 4914.8101 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5538.7645
2025-04-10 | 4703.335 | 21.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5285.012
2025-04-10 | 4694.3418 | 21.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5039.0429
2025-04-10 | 4714.5752 | 24.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5240.3424
2025-04-10 | 4801.0952 | 24.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5169.263
2025-04-10 | 5145.0898 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5590.3245
2025-04-10 | 5799.1992 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5931.0865
2025-04-10 | 6035.2378 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6226.931
2025-04-10 | 5792.9668 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6346.951
2025-04-10 | 5469.3252 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6207.218
2025-04-10 | 5322.8271 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6007.3274
2025-04-10 | 5258.312 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5838.6654
2025-04-10 | 5207.3062 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5783.5039
2025-04-10 | 4956.626 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5626.8845
2025-04-10 | 4830.5669 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5465.537
2025-04-10 | 5000.7769 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5573.8274
2025-04-10 | 5519.5298 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5883.4955
2025-04-10 | 6048.2871 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6455.214
2025-04-10 | 6317.377 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6711.6686
2025-04-10 | 6432.0229 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6778.3764
2025-04-10 | 6417.0718 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6770.7472
2025-04-10 | 6042.2168 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6623.8428
2025-04-10 | 5387.3892 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6088.4054
2025-04-10 | 4803.3701 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5453.2069
2025-04-10 | 4498.0781 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5098.752
2025-04-11 | 4334.353 | 17.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4833.9992
2025-04-11 | 4200.8569 | 17.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4621.031
2025-04-11 | 4205.1499 | 17.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.3217
2025-04-11 | 4255.002 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4498.2439
2025-04-11 | 4553.7222 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4633.2972
2025-04-11 | 4998.6309 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4963.0589
2025-04-11 | 5363.5381 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5357.9062
2025-04-11 | 5639.896 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5719.9331
2025-04-11 | 5658.4619 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5888.2089
2025-04-11 | 5635.6621 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5897.3243
2025-04-11 | 5546.0718 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5860.6661
2025-04-11 | 5672.8818 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5816.5049
2025-04-11 | 5521.25 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5670.8857
2025-04-11 | 5621.4932 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5564.5399
2025-04-11 | 5739.2651 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5584.8277
2025-04-11 | 6117.4619 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5938.497
2025-04-11 | 6461.1372 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6444.2137
2025-04-11 | 6404.7788 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6667.6673
2025-04-11 | 6420.104 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6712.3745
2025-04-11 | 6432.1528 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6759.7469
2025-04-11 | 5967.2979 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6535.8403
2025-04-11 | 5365.1719 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6022.4035
2025-04-11 | 4877.5098 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5332.2035
2025-04-11 | 4511.2788 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4823.7442
2025-04-12 | 4226.5742 | 14.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4771.4639
2025-04-12 | 4128.3501 | 15.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4613.4973
2025-04-12 | 4121.9238 | 14.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4418.7855
2025-04-12 | 4164.1602 | 14.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.7077
2025-04-12 | 4301.4219 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4559.7616
2025-04-12 | 4629.2388 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4878.523
2025-04-12 | 5275.6519 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5295.371
2025-04-12 | 5864.6528 | 14.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5635.3972
2025-04-12 | 6137.2588 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5781.6724
2025-04-12 | 6259.5381 | 12.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5713.7856
2025-04-12 | 6148.2539 | 11.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600.1252
2025-04-12 | 5980.52 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5456.9611
2025-04-12 | 5725.1348 | 9.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5267.3408
2025-04-12 | 5520.1372 | 8.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5149.9946
2025-04-12 | 5565.5122 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5214.2837
2025-04-12 | 5916.6108 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600.9539
2025-04-12 | 6130.9912 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6073.6697
2025-04-12 | 6081.4258 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6209.1208
2025-04-12 | 6017.0181 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6297.8292
2025-04-12 | 5984.085 | 9.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6466.2051
2025-04-12 | 5572.1001 | 12.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6517.3062
2025-04-12 | 5184.584 | 13.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6135.8732
2025-04-12 | 4638.125 | 13.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5489.6745
2025-04-12 | 4352.562 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5267.2233
2025-04-13 | 4182.5 | 17.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5057.4721
2025-04-13 | 4061.386 | 16.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4789.5023
2025-04-13 | 4042.9971 | 16.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4616.7912
2025-04-13 | 4072.8069 | 18.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.7208
2025-04-13 | 4227.7979 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4823.7692
2025-04-13 | 4543.0801 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5109.5296
2025-04-13 | 5133.9438 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5658.3813
2025-04-13 | 5661.374 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5668.3982
2025-04-13 | 6131.9551 | 11.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5561.6661
2025-04-13 | 6082.728 | 9.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5339.7749
2025-04-13 | 5943.584 | 8.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5248.1151
2025-04-13 | 5869.4038 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5005.9483
2025-04-13 | 5514.333 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4783.327
2025-04-13 | 5310.8018 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4621.9795
2025-04-13 | 5247.187 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4598.2661
2025-04-13 | 5648.2598 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.9336
2025-04-13 | 6014.6968 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5435.6515
2025-04-13 | 5825.4849 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5637.1045
2025-04-13 | 5911.0269 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5791.8148
2025-04-13 | 6034.5161 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6191.1972
2025-04-13 | 5707.4009 | 7.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5989.2912
2025-04-13 | 4975.3418 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5783.8632
2025-04-13 | 4312.8701 | 10.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5126.6642
2025-04-13 | 3916.9109 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5014.2161
2025-04-14 | 3660.6331 | 13.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4338.9851
2025-04-14 | 3638.645 | 14.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4269.021
2025-04-14 | 3639.405 | 16.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4360.3174
2025-04-14 | 3788.959 | 16.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4322.2389
2025-04-14 | 4192.4521 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4457.2922
2025-04-14 | 4814.3711 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4930.058
2025-04-14 | 5009.876 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5379.9069
2025-04-14 | 4985.6479 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5279.9206
2025-04-14 | 4826.5288 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5195.1892
2025-04-14 | 4534.9341 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4852.2945
2025-04-14 | 4440.9019 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4595.63
2025-04-14 | 4452.1011 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4496.4673
2025-04-14 | 4178.853 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4295.8466
2025-04-14 | 4156.4121 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.4997
2025-04-14 | 4278.2061 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4077.7848
2025-04-14 | 4856.938 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4563.4579
2025-04-14 | 5499.2178 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5179.1777
2025-04-14 | 5534.9541 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5457.6329
2025-04-14 | 5495.0698 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5568.342
2025-04-14 | 5483.3008 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5725.7175
2025-04-14 | 5086.6919 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5743.8177
2025-04-14 | 4424.6519 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5285.3825
2025-04-14 | 3802.6379 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4760.1872
2025-04-14 | 3508.8069 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4504.7351
2025-04-15 | 3311.0161 | 12.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4206.9813
2025-04-15 | 3233.2339 | 11.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3950.0119
2025-04-15 | 3188.062 | 12.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3876.3036
2025-04-15 | 3292.4441 | 13.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.2301
2025-04-15 | 3623.3081 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4193.2847
2025-04-15 | 4205.1851 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4776.0536
2025-04-15 | 4536.0669 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5038.8972
2025-04-15 | 4634.4072 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5070.9146
2025-04-15 | 4644.8511 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5052.1851
2025-04-15 | 4651.9141 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5138.3027
2025-04-15 | 4639.0049 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5057.6432
2025-04-15 | 4612.7881 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4925.4795
2025-04-15 | 4518.0112 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4856.8626
2025-04-15 | 4481.9712 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4926.5217
2025-04-15 | 4925.9419 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5430.8233
2025-04-15 | 5307.8208 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5421.4823
2025-04-15 | 5792.396 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6246.2081
2025-04-15 | 6014.9341 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6425.6605
2025-04-15 | 6029.1128 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6448.367
2025-04-15 | 6084.7578 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6682.7447
2025-04-15 | 5706.8511 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6491.839
2025-04-15 | 5168.9019 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6022.4035
2025-04-15 | 4589.2749 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5420.206
2025-04-15 | 4208.2471 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5021.7498
2025-04-16 | 4019.769 | 17.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4778.9976
2025-04-16 | 3935.8301 | 17.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.0304
2025-04-16 | 3935.0149 | 17.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.3214
2025-04-16 | 4018.5049 | 18.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4520.2445
2025-04-16 | 4443.2949 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4666.2982
2025-04-16 | 4948.4561 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5040.0611
2025-04-16 | 5347.8608 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5456.9091
2025-04-16 | 5581.9131 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5807.9356
2025-04-16 | 5558.5449 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.2111
2025-04-16 | 5547.6782 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5963.3262
2025-04-16 | 5525.1431 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5915.6676
2025-04-16 | 5572.5981 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5805.5046
2025-04-16 | 5477.7231 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5560.8826
2025-04-16 | 5501.7031 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5531.5389
2025-04-16 | 5711.8599 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5507.8255
2025-04-16 | 6116.0352 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5894.4958
2025-04-16 | 6516.333 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6356.2112
2025-04-16 | 6393.2261 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6568.6645
2025-04-16 | 6523.9722 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6767.3761
2025-04-16 | 6601.9092 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6814.7485
2025-04-16 | 6252.7969 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6678.8443
2025-04-16 | 5576.2939 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6176.4079
2025-04-16 | 4995.2959 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5574.2104
2025-04-16 | 4554.708 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5043.7504
2025-04-17 | 4300.3589 | 17.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4778.9976
2025-04-17 | 4218.4561 | 17.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4566.0294
2025-04-17 | 4218.2261 | 18.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4536.3224
2025-04-17 | 4356.522 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4498.2439
2025-04-17 | 4749.832 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4776.3013
2025-04-17 | 5289.1509 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5117.0633
2025-04-17 | 5422.27 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5467.9094
2025-04-17 | 5402.5718 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5719.9331
2025-04-17 | 5185.4292 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.208
2025-04-17 | 5003.6948 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5787.3211
2025-04-17 | 4995.7271 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5684.6611
2025-04-17 | 4754.4692 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5596.4986
2025-04-17 | 4639.7461 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5296.8751
2025-04-17 | 4516.7861 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5113.527
2025-04-17 | 4573.1548 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5089.8136
2025-04-17 | 4822.5469 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5311.4792
2025-04-17 | 5170.0542 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5839.1965
2025-04-17 | 5177.0601 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6018.6489
2025-04-17 | 5372.2632 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6129.3579
2025-04-17 | 5663.4731 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6473.7388
2025-04-17 | 5544.1118 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6194.8305
2025-04-17 | 5161.1558 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5901.4001
2025-04-17 | 4650.7788 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5398.2054
2025-04-17 | 4275.3472 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4845.7448
2025-04-18 | 4112.1069 | 16.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4668.9945
2025-04-18 | 3950.7639 | 17.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4544.0288
2025-04-18 | 3926.229 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.3189
2025-04-18 | 4006.8201 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4608.247
2025-04-18 | 4251.9111 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4688.2988
2025-04-18 | 4644.3848 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.0608
2025-04-18 | 5033.0078 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5390.9072
2025-04-18 | 5312.5708 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5499.9269
2025-04-18 | 5634.1318 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5426.1958
2025-04-18 | 5669.1201 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5182.3039
2025-04-18 | 5700.7598 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4848.6372
2025-04-18 | 5927.207 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4815.4764
2025-04-18 | 5718.6479 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4526.8532
2025-04-18 | 5583.8501 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.5082
2025-04-18 | 5634.4751 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4682.802
2025-04-18 | 5997.3911 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4904.4676
2025-04-18 | 6084.7959 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5476.1861
2025-04-18 | 5760.0552 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5446.6326
2025-04-18 | 5671.6758 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5502.3401
2025-04-18 | 5447.6738 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5604.714
2025-04-18 | 5118.5762 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5402.808
2025-04-18 | 4663.5459 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4933.3725
2025-04-18 | 4136.3428 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4485.1794
2025-04-18 | 3824.313 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4020.7213
2025-04-19 | 3519.1689 | 7.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3946.4404
2025-04-19 | 3348.9761 | 7.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.4732
2025-04-19 | 3259.75 | 7.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3670.7642
2025-04-19 | 3243.1741 | 9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.6901
2025-04-19 | 3387.4519 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3910.7431
2025-04-19 | 3761.678 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.502
2025-04-19 | 4261.8232 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4404.3456
2025-04-19 | 4842.4219 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4733.3715
2025-04-19 | 5410.918 | 5.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.6467
2025-04-19 | 5608.1699 | 4.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.7611
2025-04-19 | 5782.5889 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4621.0973
2025-04-19 | 5556.3848 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4422.9317
2025-04-19 | 5341.9341 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4490.3071
2025-04-19 | 5127.1421 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4868.5266
2025-04-19 | 5075.7651 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4844.6753
2025-04-19 | 5417.9829 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5157.9182
2025-04-19 | 5477.4399 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5248.6462
2025-04-19 | 5440.293 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5615.1039
2025-04-19 | 5260.8999 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5780.8145
2025-04-19 | 5128.3608 | 4.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5883.1885
2025-04-19 | 4924.1641 | 5.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5824.2865
2025-04-19 | 4489.394 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5607.8582
2025-04-19 | 4081.2759 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5159.6651
2025-04-19 | 3761.468 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4827.2108
2025-04-20 | 3471.002 | 13.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4661.4608
2025-04-20 | 3394.957 | 14.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4569.496
2025-04-20 | 3400.9839 | 15.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4517.7884
2025-04-20 | 3426.3579 | 15.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4501.7105
2025-04-20 | 3645.991 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.767
2025-04-20 | 4157.2212 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5076.5287
2025-04-20 | 4693.2002 | 16.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5493.3766
2025-04-20 | 5310.7578 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5789.4016
2025-04-20 | 5715.2168 | 14.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5913.6762
2025-04-20 | 5969.1348 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5856.7896
2025-04-20 | 6132.2642 | 12.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743.1292
2025-04-20 | 6089.7349 | 11.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5643.9665
2025-04-20 | 5972.396 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5366.3436
2025-04-20 | 5738.6519 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5171.9952
2025-04-20 | 5622.5479 | 8.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5170.2824
2025-04-20 | 5608.1572 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5501.9511
2025-04-20 | 5527.6719 | 8.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6095.6703
2025-04-20 | 5322.627 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6253.122
2025-04-20 | 5534.3911 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6308.8296
2025-04-20 | 5498.0298 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6488.2057
2025-04-20 | 5263.5952 | 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6605.3088
2025-04-20 | 4893.5239 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6245.8764
2025-04-20 | 4377.0708 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5544.6761
2025-04-20 | 4037.749 | 15.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5190.2211
2025-04-21 | 3802.8611 | 14.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4470.9888
2025-04-21 | 3709.4409 | 16 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4423.0253
2025-04-21 | 3706.271 | 17 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.3189
2025-04-21 | 3813.7839 | 17.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4410.2414
2025-04-21 | 4049.9919 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4710.2994
2025-04-21 | 4517.7148 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5040.0611
2025-04-21 | 4802.5039 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5203.9019
2025-04-21 | 5106.8882 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5367.9231
2025-04-21 | 5055.4912 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5338.1933
2025-04-21 | 5059.3081 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5314.3077
2025-04-21 | 5174.457 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5090.6441
2025-04-21 | 5290.5952 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4980.4811
2025-04-21 | 5288.313 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4702.8582
2025-04-21 | 5286.7739 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4673.5145
2025-04-21 | 5567.1851 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4825.8061
2025-04-21 | 6045.7041 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5454.4832
2025-04-21 | 6518.9849 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6037.2021
2025-04-21 | 6387.4722 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6381.6592
2025-04-21 | 6280.3291 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6448.367
2025-04-21 | 6179.9292 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6495.7394
2025-04-21 | 5637.2212 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6238.8318
2025-04-21 | 4970.6709 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5648.3928
2025-04-21 | 4305.4902 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5013.1944
2025-04-21 | 3838.79 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4427.7329
2025-04-22 | 3616.9929 | 10.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.9769
2025-04-22 | 3431.625 | 10.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3785.0072
2025-04-22 | 3406.6919 | 10 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3645.297
2025-04-22 | 3413.8379 | 10.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3640.2194
2025-04-22 | 3726.9541 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3775.2728
2025-04-22 | 4288.4751 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4050.0329
2025-04-22 | 4644.71 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4499.8818
2025-04-22 | 4884.9092 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4861.9087
2025-04-22 | 4698.606 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5063.1854
2025-04-22 | 4489.2368 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5006.2989
2025-04-22 | 4500.1509 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4980.641
2025-04-22 | 4606.396 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5002.4817
2025-04-22 | 4513.8481 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4790.8607
2025-04-22 | 4494.1401 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4772.5173
2025-04-22 | 4624.3999 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4781.8048
2025-04-22 | 5221.4121 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5135.4742
2025-04-22 | 5650.2109 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5740.1937
2025-04-22 | 5629.3628 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.6495
2025-04-22 | 5718.458 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6129.3579
2025-04-22 | 5862.8359 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6198.731
2025-04-22 | 5516.0811 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6040.8262
2025-04-22 | 5044.5908 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5549.39
2025-04-22 | 4441.3838 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4980.1935
2025-04-22 | 4014.4851 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4768.7426
2025-04-23 | 3777.0291 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.9873
2025-04-23 | 3673.843 | 13.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4181.0185
2025-04-23 | 3652.178 | 14.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.3111
2025-04-23 | 3810.4121 | 15.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4267.2373
2025-04-23 | 4145.2632 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4457.2922
2025-04-23 | 4671.0532 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4875.0564
2025-04-23 | 4836.1079 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5016.8965
2025-04-23 | 4796.4458 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5257.92
2025-04-23 | 4574.7949 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5316.1926
2025-04-23 | 4309.0801 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5215.3048
2025-04-23 | 4256.1289 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5057.6432
2025-04-23 | 4231.564 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4914.4792
2025-04-23 | 4023.9031 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4702.8582
2025-04-23 | 3913.5391 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4530.5104
2025-04-23 | 4013.1819 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4517.7973
2025-04-23 | 4474.5781 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4794.4644
2025-04-23 | 4889.2559 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5344.1824
2025-04-23 | 4654.541 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5578.6363
2025-04-23 | 4785.502 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5689.3454
2025-04-23 | 5253.1021 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5879.7219
2025-04-23 | 5151.5 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5798.8193
2025-04-23 | 4612.0459 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5329.3838
2025-04-23 | 3963.8479 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4881.1907
2025-04-23 | 3612.6379 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4636.7388
2025-04-24 | 3389.3999 | 12.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239.9823
2025-04-24 | 3314.158 | 13.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4126.0169
2025-04-24 | 3293.416 | 13.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.3076
2025-04-24 | 3418.5249 | 13.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4036.2307
2025-04-24 | 3734.7051 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4281.2872
2025-04-24 | 4266.5962 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4578.048
2025-04-24 | 4478.6201 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4829.8912
2025-04-24 | 4691.376 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5015.9131
2025-04-24 | 4475.4849 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5074.1857
2025-04-24 | 4377.978 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5094.3014
2025-04-24 | 4421.9639 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5156.646
2025-04-24 | 4290.6392 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4848.4773
2025-04-24 | 4008.793 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4383.8491
2025-04-24 | 3947.437 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3991.495
2025-04-24 | 4083.3291 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.2093
2025-04-24 | 4553.8701 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4409.4535
2025-04-24 | 5116.23 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.1739
2025-04-24 | 5209.418 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.6257
2025-04-24 | 5226.7178 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5326.3351
2025-04-24 | 5280.9229 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5494.7109
2025-04-24 | 4968.936 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5402.808
2025-04-24 | 4390.395 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4966.3734
2025-04-24 | 3731.0601 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4232.1722
2025-04-24 | 3381.3059 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3734.7131
2025-04-25 | 3178.8 | 5.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3491.961
2025-04-25 | 3011.6589 | 6.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3366.9953
2025-04-25 | 3024.488 | 7.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3359.2888
2025-04-25 | 3023.364 | 9.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3585.2179
2025-04-25 | 3356.625 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.2703
2025-04-25 | 3920.436 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4292.0398
2025-04-25 | 4319.106 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4433.8799
2025-04-25 | 4525.0259 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4751.9055
2025-04-25 | 4384.8359 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4920.1814
2025-04-25 | 4255.9531 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4874.2951
2025-04-25 | 4198.082 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4760.6347
2025-04-25 | 4123.7119 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4639.4713
2025-04-25 | 3974.0581 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.8525
2025-04-25 | 3966.2639 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4211.5013
2025-04-25 | 4106.1401 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4220.7888
2025-04-25 | 4618.708 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4574.4582
2025-04-25 | 5052.5498 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5091.1752
2025-04-25 | 5035.1001 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5369.6304
2025-04-25 | 5126.1001 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5524.3407
2025-04-25 | 5149.3218 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5626.7147
2025-04-25 | 4884.0122 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5435.8089
2025-04-25 | 4350.5991 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4966.3734
2025-04-25 | 3886.8149 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4430.1778
2025-04-25 | 3574.3 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3965.7197
2025-04-26 | 3273.542 | 7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3924.4398
2025-04-26 | 3138.73 | 7.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3755.4728
2025-04-26 | 3005.9729 | 7.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3681.7645
2025-04-26 | 3094.2151 | 8.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.6885
2025-04-26 | 3231.6379 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3910.7431
2025-04-26 | 3567.824 | 9.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4295.5064
2025-04-26 | 4108.1318 | 10.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.3584
2025-04-26 | 4815.9761 | 10.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5239.3859
2025-04-26 | 5315.3721 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5418.6621
2025-04-26 | 5639.0811 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5405.7768
2025-04-26 | 5714.8901 | 9.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5369.1186
2025-04-26 | 5747.1851 | 9.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5357.9583
2025-04-26 | 5650.5591 | 9.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5322.3423
2025-04-26 | 5602.6201 | 9.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5237.9971
2025-04-26 | 5728.5352 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5357.2877
2025-04-26 | 6046.5972 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743.958
2025-04-26 | 6273.6831 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.6772
2025-04-26 | 6056.9961 | 10.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6594.1318
2025-04-26 | 5754.1719 | 11.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6682.8402
2025-04-26 | 5579.4712 | 11.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6719.2123
2025-04-26 | 5315.0342 | 12.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6561.3075
2025-04-26 | 4924.5249 | 13.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6113.8726
2025-04-26 | 4445.9189 | 14.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5577.677
2025-04-26 | 4045.3411 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5113.2189
2025-04-27 | 3790.144 | 15 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4804.4648
2025-04-27 | 3660.4751 | 15 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4591.4967
2025-04-27 | 3568.7361 | 15.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4506.788
2025-04-27 | 3674.1541 | 15.1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4457.7092
2025-04-27 | 3832.7361 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4559.7616
2025-04-27 | 4187.6729 | 14.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4823.5215
2025-04-27 | 4706.498 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5185.3678
2025-04-27 | 5370.8428 | 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5492.3932
2025-04-27 | 5899.126 | 12.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5682.6696
2025-04-27 | 6029.166 | 11.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5559.7812
2025-04-27 | 5974.7031 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5171.1129
2025-04-27 | 5889.3789 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4785.942
2025-04-27 | 5560.4229 | 2.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4497.3188
2025-04-27 | 5368.8789 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4313.9707
2025-04-27 | 5338.2759 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4301.2576
2025-04-27 | 5641.6182 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4827.4951
2025-04-27 | 5862.772 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5461.6407
2025-04-27 | 5768.5439 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5464.8122
2025-04-27 | 5673.2661 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5527.8073
2025-04-27 | 5631.8911 | 2.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5729.1841
2025-04-27 | 5430.6411 | 5.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5780.2853
2025-04-27 | 4778.126 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5189.8463
2025-04-27 | 4003.408 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5016.661
2025-04-27 | 3553.085 | 8.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4409.1989
2025-04-28 | 3338.606 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3975.9747
2025-04-28 | 3203.3701 | 10.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3862.0094
2025-04-28 | 3263.6689 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3755.3001
2025-04-28 | 3371.179 | 12.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3882.2263
2025-04-28 | 3754.967 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4105.2822
2025-04-28 | 4381.4341 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4622.0492
2025-04-28 | 4529.9048 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4642.8859
2025-04-28 | 4463.6758 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4707.9043
2025-04-28 | 4255.043 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4579.1716
2025-04-28 | 4023.9109 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4346.2801
2025-04-28 | 3918.4829 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.4694
2025-04-28 | 3902.2859 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4643.8736
2025-04-28 | 3856.4031 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4799.2515
2025-04-28 | 3731.5449 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5067.33
2025-04-28 | 3839.697 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5227.047
2025-04-28 | 4279.896 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5687.1447
2025-04-28 | 4729.3931 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6174.4356
2025-04-28 | 4794.6831 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6067.4661
2025-04-28 | 4932.9941 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5528.4671
2025-04-28 | 5129.0601 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5285.7049
2025-04-28 | 4845.439 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5347.8064
2025-04-28 | 4341.5239 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4944.3728
2025-04-28 | 3742.6289 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4507.18
2025-04-28 | 3363.8479 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4108.7238
2025-04-29 | 3078.8059 | 6.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612.9644
2025-04-29 | 2975.9441 | 8.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3587.0015
2025-04-29 | 2922.1189 | 7.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3348.2885
2025-04-29 | 2979.658 | 6.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3222.2075
2025-04-29 | 3243.147 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3258.258
2025-04-29 | 3766.717 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.0166
2025-04-29 | 4105.7451 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3762.8608
2025-04-29 | 4085.1089 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3871.8805
2025-04-29 | 3912.094 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4289.8645
2025-04-29 | 3752.0171 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5444.3914
2025-04-29 | 3783.678 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5304.8798
2025-04-29 | 3764.26 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5268.0061
2025-04-29 | 3732.79 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5863.9482
2025-04-29 | 3726.397 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4553.3384
2025-04-29 | 3946.1079 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4749.7692
2025-04-29 | 4606.02 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6311.2772
2025-04-29 | 5136.1079 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7128.9912
2025-04-29 | 5168.8389 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7425.8722
2025-04-29 | 5094.3311 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5260.3332
2025-04-29 | 5116.2588 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5278.5553
2025-04-29 | 4763.8481 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5227.2167
2025-04-29 | 4261.063 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4383.3568
2025-04-29 | 3597.186 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4001.1656
2025-04-29 | 3147.5271 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4229.7272
2025-04-30 | 2943.7061 | 13 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4305.9841
2025-04-30 | 2837.7209 | 15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4313.0222
2025-04-30 | 2866.9929 | 16.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4393.3183
2025-04-30 | 3057.3989 | 17.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4476.2432
2025-04-30 | 3391.124 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644.2975
2025-04-30 | 3998.9851 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4974.0593
2025-04-30 | 4459.5298 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5445.9088
2025-04-30 | 4652.9458 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5763.9344
2025-04-30 | 4522.7881 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5877.2086
2025-04-30 | 4317.9902 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5831.3224
2025-04-30 | 4271.2349 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5717.662
2025-04-30 | 4229.0679 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5695.5014
2025-04-30 | 4145.7778 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5406.8782
2025-04-30 | 4081.375 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5179.5289
2025-04-30 | 4044.572 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5078.8133
2025-04-30 | 4524.6328 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5377.4811
2025-04-30 | 5115.1851 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5872.1974
2025-04-30 | 5187.978 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6117.6517
2025-04-30 | 5428.1191 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6173.3592
2025-04-30 | 5652.936 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6286.7335
2025-04-30 | 5301.146 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6117.8284
2025-04-30 | 4669.2051 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5747.3957
2025-04-30 | 4056.4939 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5299.2026
2025-04-30 | 3667.688 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4790.7432
2025-05-01 | 3534.8569 | 16.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4679.9948
2025-05-01 | 3425.49 | 16.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4478.0269
2025-05-01 | 3402.7261 | 17.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4426.3192
2025-05-01 | 3541.3081 | 16.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4377.2404
2025-05-01 | 3854.7209 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699.2991
2025-05-01 | 4421.335 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5062.0618
2025-05-01 | 4730.52 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5203.9019
2025-05-01 | 4660.126 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5202.9184
2025-05-01 | 4272.2241 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5096.1864
2025-05-01 | 4021.364 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4907.2961
2025-05-01 | 3970.562 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4683.6325
2025-05-01 | 3996.592 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4529.4682
2025-05-01 | 3856.5049 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4185.8434
2025-05-01 | 3778.377 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.4997
2025-05-01 | 3948.032 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4286.7907
2025-05-01 | 4599.1509 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4673.461
2025-05-01 | 5343.7422 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5278.1805
2025-05-01 | 5335.646 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5699.6398
2025-05-01 | 5410.3101 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5678.3451
2025-05-01 | 5351.0659 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5846.7209
2025-05-01 | 5044.7349 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5820.8199
2025-05-01 | 4433.1108 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5384.3853
2025-05-01 | 3890.2939 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4815.1888
2025-05-01 | 3443.0669 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4284.7288
2025-05-02 | 3213.7009 | 9.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3942.9738
2025-05-02 | 3074.8611 | 9.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3752.0062
2025-05-02 | 3018.0149 | 9.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3612.2961
2025-05-02 | 3099.606 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3618.2188
2025-05-02 | 3404.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.2715
2025-05-02 | 3865.207 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.0323
2025-05-02 | 4195.9268 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4334.8771
2025-05-02 | 4339.6548 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4520.899
2025-05-02 | 4371.1382 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4436.1676
2025-05-02 | 4220.689 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4302.2788
2025-05-02 | 4142.1221 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4243.62
2025-05-02 | 4089.0911 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4177.4582
2025-05-02 | 3993.186 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.2642
2025-05-02 | 3879.9189 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4406.4837
2025-05-02 | 3974.6121 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4786.4829
2025-05-02 | 4370.207 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5320.0079
2025-05-02 | 4689.1182 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6027.5808
2025-05-02 | 4716.0659 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5737.043
2025-05-02 | 4728.6792 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5418.3261
2025-05-02 | 4816.9912 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5329.7062
2025-05-02 | 4711.3008 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5435.8089
2025-05-02 | 4290.9409 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5043.3756
2025-05-02 | 3753.1289 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4562.1816
2025-05-02 | 3316.1609 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4141.7247
2025-05-03 | 3055.2791 | 9.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4155.4464
2025-05-03 | 2890.875 | 9.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3997.4797
2025-05-03 | 2820.6331 | 10.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3956.7724
2025-05-03 | 2846.1521 | 11.3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.6973
2025-05-03 | 3030.71 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4152.75
2025-05-03 | 3349.79 | 11.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.5124
2025-05-03 | 4011.3911 | 10.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4844.3581
2025-05-03 | 4693.4951 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5184.3844
2025-05-03 | 5093.6411 | 9.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5363.6605
2025-05-03 | 5305.7661 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5372.7758
2025-05-03 | 5418.9971 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5303.1167
2025-05-03 | 5356.5288 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5203.9539
2025-05-03 | 5192.5552 | 5.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4882.3298
2025-05-03 | 4955.1729 | 5.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4753.9833
2025-05-03 | 4787.7222 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4752.2705
2025-05-03 | 5002.9448 | 3.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5072.9389
2025-05-03 | 5296.646 | 3.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5567.6553
2025-05-03 | 5381.0068 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5769.1083
2025-05-03 | 5320.4761 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5857.8167
2025-05-03 | 5185.0151 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6026.1925
2025-05-03 | 4859.4722 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5857.2874
2025-05-03 | 4461.335 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5464.8541
2025-05-03 | 3979.5149 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4873.6569
2025-05-03 | 3553.269 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4475.2007
2025-05-04 | 3240.6479 | 9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.446
2025-05-04 | 3112.582 | 9.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030.4807
2025-05-04 | 3077.4551 | 10.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3989.7733
2025-05-04 | 3064.7019 | 11.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4083.6986
2025-05-04 | 3171.377 | 11.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4229.7522
2025-05-04 | 3468.2881 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4482.5118
2025-05-04 | 4048.8569 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.3572
2025-05-04 | 4565.2671 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4931.3772
2025-05-04 | 5049.5132 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4945.6486
2025-05-04 | 5071.7598 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.7602
2025-05-04 | 5012.5981 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4775.1017
2025-05-04 | 5000.2622 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4686.9392
2025-05-04 | 4776.562 | 1.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4387.3157
2025-05-04 | 4704.4922 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.9679
2025-05-04 | 4754.1572 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4624.3932
2025-05-04 | 5138.9829 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5341.4866
2025-05-04 | 5534.103 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5792.0638
2025-05-04 | 5618.7231 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6162.3721
2025-05-04 | 5504.5098 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5513.2322
2025-05-04 | 5431.542 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5520.316
2025-05-04 | 5084.311 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5362.2733
2025-05-04 | 4416.3628 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5024.8416
2025-05-04 | 3693.0139 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4466.6454
2025-05-04 | 3235.5271 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4211.1932
2025-05-05 | 2974.814 | 6.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546.9625
2025-05-05 | 2870.78 | 6.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3333.9943
2025-05-05 | 2852.801 | 6.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3271.2863
2025-05-05 | 2931.4961 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3288.2094
2025-05-05 | 3284.219 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500.2649
2025-05-05 | 3777.2791 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3852.0273
2025-05-05 | 4117.9512 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4268.8752
2025-05-05 | 4253.541 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4520.899
2025-05-05 | 4173.4468 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4491.1691
2025-05-05 | 4143.5801 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4445.2829
2025-05-05 | 4135.9961 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4166.6178
2025-05-05 | 4037.9961 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.1684
2025-05-05 | 3827.7859 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4175.1189
2025-05-05 | 3949.272 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4333.0564
2025-05-05 | 4126.8901 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4529.4871
2025-05-05 | 4663.7988 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4916.1574
2025-05-05 | 5248.1748 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5256.5936
2025-05-05 | 5259.1582 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5406.6199
2025-05-05 | 5325.479 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5458.3388
2025-05-05 | 5227.373 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5461.71
2025-05-05 | 4976.96 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5259.8039
2025-05-05 | 4266.957 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4757.3675
2025-05-05 | 3674.6731 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4144.1697
2025-05-05 | 3205.02 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3646.7106
2025-05-06 | 2904.104 | 4.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3337.9566
2025-05-06 | 2840.9851 | 4.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3168.9896
2025-05-06 | 2852.054 | 4.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3073.2807
2025-05-06 | 2885.6079 | 4.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.2028
2025-05-06 | 3187.7981 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.2568
2025-05-06 | 3605.7771 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3555.0188
2025-05-06 | 3898.199 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3927.8655
2025-05-06 | 4053.1389 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4256.8914
2025-05-06 | 3957.978 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4414.1669
2025-05-06 | 3796.1851 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4170.2751
2025-05-06 | 3806.8589 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4100.6159
2025-05-06 | 3826.2981 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4643.8736
2025-05-06 | 3779.991 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4652.3968
2025-05-06 | 3844.894 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4406.4837
2025-05-06 | 3998.5701 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4933.3376
2025-05-06 | 4542.7788 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5393.4352
2025-05-06 | 5139.6768 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6137.7219
2025-05-06 | 5067.5591 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6581.4576
2025-05-06 | 4995.2871 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5785.4629
2025-05-06 | 5144.2251 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5462.1237
2025-05-06 | 4889.3252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4896.7936
2025-05-06 | 4399.8169 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4449.3587
2025-05-06 | 3621.489 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3880.1621
2025-05-06 | 3208.5239 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3525.7072
2025-05-07 | 2949.0601 | 2.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3183.9522
2025-05-07 | 2725.9919 | 3.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3036.9859
2025-05-07 | 2715.251 | 3.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2897.2757
2025-05-07 | 2764.665 | 4.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.2028
2025-05-07 | 3087.6289 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3126.2543
2025-05-07 | 3589.679 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522.0179
2025-05-07 | 3820.4729 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3817.8624
2025-05-07 | 4041.0171 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4388.8952
2025-05-07 | 4035.7629 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4524.1701
2025-05-07 | 3943.4951 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4478.2839
2025-05-07 | 3904.3301 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4276.621
2025-05-07 | 3935.239 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.3095
2025-05-07 | 3926.04 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4141.8422
2025-05-07 | 3808.075 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4332.5048
2025-05-07 | 4190.5918 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4682.802
2025-05-07 | 4837.5972 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5003.4704
2025-05-07 | 5313.4971 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520.1874
2025-05-07 | 5283.0791 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5908.6457
2025-05-07 | 5393.2378 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5909.3517
2025-05-07 | 5365.4438 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5879.7219
2025-05-07 | 4981.0288 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5688.8161
2025-05-07 | 4338.1538 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5296.3828
2025-05-07 | 3708.8149 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4793.1881
2025-05-07 | 3369.3101 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4350.7307
2025-05-08 | 3167.3601 | 10.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.9757
2025-05-08 | 3052.0901 | 10.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3818.0081
2025-05-08 | 3017.0339 | 11.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.3011
2025-05-08 | 3087.1851 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3838.2251
2025-05-08 | 3400.592 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.2797
2025-05-08 | 3925.436 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.043
2025-05-08 | 4415.5161 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4807.8906
2025-05-08 | 4600.418 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5169.9175
2025-05-08 | 4559.2139 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5327.1929
2025-05-08 | 4541.915 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5281.3067
2025-05-08 | 4582.4102 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200.6473
2025-05-08 | 4543.127 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5057.4833
2025-05-08 | 4323.5669 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4834.8619
2025-05-08 | 4275.8188 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4706.5154
2025-05-08 | 4377.041 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4792.8051
2025-05-08 | 4871.1328 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5135.4742
2025-05-08 | 5429.0669 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5597.1896
2025-05-08 | 5491.7539 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5875.6448
2025-05-08 | 5520.165 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5964.3532
2025-05-08 | 5671.9072 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6088.7278
2025-05-08 | 5305.7109 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6018.8255
2025-05-08 | 4600.4189 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5472.3878
2025-05-08 | 4159.8071 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5002.1941
2025-05-08 | 3683.2151 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4625.7385
2025-05-09 | 3371.3931 | 11.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4162.9801
2025-05-09 | 3323.2371 | 11.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3906.0106
2025-05-09 | 3268.4619 | 11.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.3008
2025-05-09 | 3344.7981 | 11.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3739.2222
2025-05-09 | 3666.7029 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3907.2765
2025-05-09 | 4226.0269 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4204.0373
2025-05-09 | 4562.6069 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4576.884
2025-05-09 | 4776.1348 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4927.9106
2025-05-09 | 4692.209 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5085.1861
2025-05-09 | 4607.1938 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5061.3005
2025-05-09 | 4579.2041 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5002.6416
2025-05-09 | 4507.7139 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4980.4811
2025-05-09 | 4411.751 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4757.8597
2025-05-09 | 4388.6758 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4607.5126
2025-05-09 | 4598.9058 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4638.8008
2025-05-09 | 5055.7012 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5080.4726
2025-05-09 | 5487.9038 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5795.1952
2025-05-09 | 5558.3179 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.6495
2025-05-09 | 5607.0059 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6228.3608
2025-05-09 | 5518.6182 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6242.7322
2025-05-09 | 5316.2998 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6029.8258
2025-05-09 | 4842.877 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5494.3885
2025-05-09 | 4296.0449 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4859.19
2025-05-09 | 3835.2329 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4328.7301
2025-05-10 | 3541.21 | 10 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4254.4492
2025-05-10 | 3338.5481 | 10.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.4822
2025-05-10 | 3279.1399 | 10.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3956.7724
2025-05-10 | 3340.7871 | 10.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.6945
2025-05-10 | 3450.667 | 10.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.7494
2025-05-10 | 3843.833 | 11.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.5124
2025-05-10 | 4446.4551 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800.3569
2025-05-10 | 4926.5469 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4931.3772
2025-05-10 | 4882.4038 | 5.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.6467
2025-05-10 | 4881.3042 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4712.757
2025-05-10 | 4857.208 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4511.0941
2025-05-10 | 4615.9639 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4334.9292
2025-05-10 | 4488.6421 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4490.3071
2025-05-10 | 4289.4351 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4758.3855
2025-05-10 | 4332.126 | 0 | 2.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5321.9531
2025-05-10 | 4604.9502 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5745.337
2025-05-10 | 4905.8721 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6452.91
2025-05-10 | 4895.4492 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6199.0858
2025-05-10 | 4857.3931 | 0 | 0.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5586.6595
2025-05-10 | 4835.1992 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5575.1797
2025-05-10 | 4695.9971 | 4.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5648.2815
2025-05-10 | 4273.248 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5343.8507
2025-05-10 | 3838.207 | 8.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4950.6591
2025-05-10 | 3451.0491 | 9.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4563.2032
2025-05-11 | 3166.928 | 10.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4342.4517
2025-05-11 | 3003.0239 | 12.3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4294.4882
2025-05-11 | 2986.8569 | 13.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4330.783
2025-05-11 | 3042.333 | 14.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.7077
2025-05-11 | 3250.042 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.7638
2025-05-11 | 3628.8201 | 15.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4988.5262
2025-05-11 | 4188.0132 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5328.3719
2025-05-11 | 4728.8979 | 13.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5525.3941
2025-05-11 | 4976.395 | 12.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5616.6677
2025-05-11 | 4991.7251 | 10.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5493.7793
2025-05-11 | 4831.2471 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5215.1142
2025-05-11 | 4716.416 | 6.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5027.9489
2025-05-11 | 4665.147 | 4.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4750.326
2025-05-11 | 4546.4561 | 3.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4533.977
2025-05-11 | 4606.2222 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4466.2623
2025-05-11 | 4850.2002 | 1.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4797.9311
2025-05-11 | 5157.501 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5303.6477
2025-05-11 | 5179.4492 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5549.102
2025-05-11 | 5288.6758 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5670.8114
2025-05-11 | 5426.1982 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5740.1844
2025-05-11 | 5177.4658 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5725.2837
2025-05-11 | 4473.0718 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5365.8513
2025-05-11 | 3841.8259 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4697.6519
2025-05-11 | 3376.3511 | 6.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4266.1948
2025-05-12 | 3098.0481 | 7.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3711.9672
2025-05-12 | 3007.95 | 8.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3554.0006
2025-05-12 | 3020.665 | 9.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3590.2954
2025-05-12 | 3098.95 | 9.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3596.2182
2025-05-12 | 3393.5061 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3863.2753
2025-05-12 | 3962.4529 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4281.0395
2025-05-12 | 4215.1519 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4554.8834
2025-05-12 | 4230.4858 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4586.9008
2025-05-12 | 4040.2329 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4535.1704
2025-05-12 | 3967.1541 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.276
2025-05-12 | 3859.895 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4276.8968
2025-05-12 | 3833.9641 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.1557
2025-05-12 | 3745.5371 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5570.2387
2025-05-12 | 3666.6731 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6132.0266
2025-05-12 | 3850.6709 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6475.3121
2025-05-12 | 4332.145 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.9782
2025-05-12 | 4936.5088 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7606.269
2025-05-12 | 4942.9551 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7756.2953
2025-05-12 | 5032.8101 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7474.2921
2025-05-12 | 5238.5649 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6196.3972
2025-05-12 | 5039.585 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5043.6483
2025-05-12 | 4275.854 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4515.3606
2025-05-12 | 3683.835 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4078.1678
2025-05-12 | 3205.241 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3635.7103
2025-05-13 | 2922.011 | 4.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392.9581
2025-05-13 | 2786.8879 | 5.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.9918
2025-05-13 | 2757.98 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3205.2845
2025-05-13 | 2776.6379 | 6.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3200.2069
2025-05-13 | 3040.3611 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401.2621
2025-05-13 | 3502.9761 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3874.0279
2025-05-13 | 3864.71 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3993.8674
2025-05-13 | 3958.073 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4179.8893
2025-05-13 | 3830.4241 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4084.1575
2025-05-13 | 3803.897 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4159.4127
2025-05-13 | 3760.1299 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4680.7472
2025-05-13 | 3786.384 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5341.4335
2025-05-13 | 3750.3931 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6157.6576
2025-05-13 | 3838.2351 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6315.595
2025-05-13 | 4160.3389 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6585.4532
2025-05-13 | 4689.9429 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7449.4013
2025-05-13 | 5348.5962 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8010.1195
2025-05-13 | 5438.8091 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8123.4321
2025-05-13 | 5446.2891 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7547.7195
2025-05-13 | 5456.4121 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6416.6793
2025-05-13 | 5248.2788 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6475.4818
2025-05-13 | 4648.7231 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5205.7708
2025-05-13 | 3879.803 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4141.0085
2025-05-13 | 3369.731 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3375.5534
2025-05-14 | 3070.947 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3095.9497
2025-05-14 | 2875.415 | 2.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2948.9834
2025-05-14 | 2801.7681 | 5.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.2829
2025-05-14 | 2891.563 | 5.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3101.2041
2025-05-14 | 3160.0691 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.2577
2025-05-14 | 3590.542 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3544.0185
2025-05-14 | 3923.7219 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3608.8564
2025-05-14 | 4043.26 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4187.7284
2025-05-14 | 4000.563 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5060.8517
2025-05-14 | 4022.4021 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5150.682
2025-05-14 | 4150.4658 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5635.3029
2025-05-14 | 4166.4429 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5928.8524
2025-05-14 | 4183.6489 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5937.3755
2025-05-14 | 4225.2939 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6058.5993
2025-05-14 | 4383.3408 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6108.1753
2025-05-14 | 4834.0352 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6054.2815
2025-05-14 | 5438.0991 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6614.9997
2025-05-14 | 5493.7891 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6765.026
2025-05-14 | 5461.3901 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6483.0228
2025-05-14 | 5533.9331 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6122.9699
2025-05-14 | 5285.5688 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5777.9219
2025-05-14 | 4580.4878 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4912.0614
2025-05-14 | 3936.3811 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3773.8717
2025-05-14 | 3484.45 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3522.4081
2025-05-15 | 3139.783 | 0 | 0.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2986.0844
2025-05-15 | 2992.6311 | 1.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2849.9805
2025-05-15 | 2929.926 | 0.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2611.2675
2025-05-15 | 2967.25 | 1.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2639.1909
2025-05-15 | 3181.113 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2807.2452
2025-05-15 | 3636.571 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3192.0085
2025-05-15 | 3906.4829 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3597.8561
2025-05-15 | 4082.0181 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-05-15 | 4109.022 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.1591
2025-05-15 | 4089.9109 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.2729
2025-05-15 | 4154.6738 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4313.6104
2025-05-15 | 4252.9131 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4607.1599
2025-05-15 | 4123.9629 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4652.3968
2025-05-15 | 4272.9238 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4957.1889
2025-05-15 | 4492.813 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5227.047
2025-05-15 | 5152.2109 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6017.5678
2025-05-15 | 5886.729 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6761.8544
2025-05-15 | 5685.54 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6728.3123
2025-05-15 | 5906.7749 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6519.7365
2025-05-15 | 5871.645 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6196.3972
2025-05-15 | 5623.873 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5410.7851
2025-05-15 | 4926.9229 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4618.3519
2025-05-15 | 4253.563 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3946.164
2025-05-15 | 3627.1431 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3426.7044
2025-05-16 | 3256.968 | 1.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3029.9478
2025-05-16 | 3022.509 | 2.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2915.9824
2025-05-16 | 2919.512 | 2.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2864.2747
2025-05-16 | 2940.7649 | 4.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2969.2003
2025-05-16 | 3151.0891 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3148.2549
2025-05-16 | 3652.467 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3588.0198
2025-05-16 | 4090.001 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3630.857
2025-05-16 | 4361.7178 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4187.7284
2025-05-16 | 4459.9072 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4803.856
2025-05-16 | 4461.0571 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5591.2462
2025-05-16 | 4629.8809 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6112.5807
2025-05-16 | 4740.9839 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6002.2797
2025-05-16 | 4716.2222 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6267.7986
2025-05-16 | 4925.8682 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.7276
2025-05-16 | 5192.6582 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7466.5815
2025-05-16 | 5675.6792 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7522.8286
2025-05-16 | 6119.1338 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8156.9742
2025-05-16 | 6184.4629 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.0005
2025-05-16 | 6102.127 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8098.4247
2025-05-16 | 6019.8052 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7371.235
2025-05-16 | 5765.5171 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6255.1997
2025-05-16 | 5069.5962 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5719.7623
2025-05-16 | 4434.832 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4287.8632
2025-05-16 | 3897.7971 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3448.9808
2025-05-17 | 3475.4551 | 0.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3187.4188
2025-05-17 | 3216.29 | 1.3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.4537
2025-05-17 | 3071.605 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3153.7495
2025-05-17 | 3019.6411 | 3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3126.6713
2025-05-17 | 3079.731 | 3.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3316.7262
2025-05-17 | 3373.313 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3624.4873
2025-05-17 | 3856.749 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.3343
2025-05-17 | 4491.167 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4304.3593
2025-05-17 | 4853.4268 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4505.6361
2025-05-17 | 5105.0239 | 2.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4624.7545
2025-05-17 | 5249.0088 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4555.0954
2025-05-17 | 5342.7871 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.9348
2025-05-17 | 5265.709 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4244.3116
2025-05-17 | 5171.7461 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4427.9624
2025-05-17 | 5053.8691 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5028.2437
2025-05-17 | 5415.564 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5892.1918
2025-05-17 | 5637.3882 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6342.769
2025-05-17 | 5537.8281 | 0 | 2.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6492.7952
2025-05-17 | 5471.6489 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5615.8098
2025-05-17 | 5268.5239 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5663.1822
2025-05-17 | 4919.3418 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5428.2752
2025-05-17 | 4419.2139 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4980.8403
2025-05-17 | 3879.5791 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4554.6479
2025-05-17 | 3421.8589 | 4.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4035.1882
2025-05-18 | 3115.99 | 4.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3682.4329
2025-05-18 | 2955.4199 | 5.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3590.4681
2025-05-18 | 2816.428 | 6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3483.7589
2025-05-18 | 2781.2739 | 6.1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467.681
2025-05-18 | 2883.147 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3646.7356
2025-05-18 | 3150.1799 | 6.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3965.497
2025-05-18 | 3632.332 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4349.344
2025-05-18 | 4227.0352 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4678.37
2025-05-18 | 4733.855 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4912.6476
2025-05-18 | 4934.0371 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5053.7668
2025-05-18 | 5166.9531 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5193.1136
2025-05-18 | 5357.9829 | 8.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5247.9552
2025-05-18 | 5338.125 | 7.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5080.3354
2025-05-18 | 5235.6821 | 7.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4962.9892
2025-05-18 | 5257.0762 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5115.2808
2025-05-18 | 5682.4521 | 7.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5457.9499
2025-05-18 | 6009.8711 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6084.67
2025-05-18 | 5850.1729 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6385.1258
2025-05-18 | 5720.4951 | 9.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6506.8352
2025-05-18 | 5523.6201 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6488.2057
2025-05-18 | 5066.9482 | 9.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6264.299
2025-05-18 | 4515.6162 | 10.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5750.8623
2025-05-18 | 4065.0139 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5159.6651
2025-05-18 | 3636.158 | 10.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4684.2067
2025-05-19 | 3362.439 | 10.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.9769
2025-05-19 | 3176.96 | 11 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3873.0097
2025-05-19 | 3088.8091 | 11.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3799.3014
2025-05-19 | 3120.353 | 11.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3816.2244
2025-05-19 | 3286.158 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.28
2025-05-19 | 3601.73 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4391.0426
2025-05-19 | 4028.99 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4796.8903
2025-05-19 | 4651.647 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5147.9168
2025-05-19 | 5123.751 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5349.1936
2025-05-19 | 5493.0791 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5347.3086
2025-05-19 | 5766.7852 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5244.6485
2025-05-19 | 5855.3589 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5178.4867
2025-05-19 | 5608.2998 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4911.8641
2025-05-19 | 5478.5889 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4783.5176
2025-05-19 | 5547.5381 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4792.8051
2025-05-19 | 5888.7051 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5212.4764
2025-05-19 | 6342.0669 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5872.1974
2025-05-19 | 6260.8691 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6271.6561
2025-05-19 | 6108.3599 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6327.3636
2025-05-19 | 6040.3828 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6341.735
2025-05-19 | 5554.29 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6139.829
2025-05-19 | 4818.894 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5615.3919
2025-05-19 | 4163.0688 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5046.1954
2025-05-19 | 3684.0339 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4559.7366
2025-05-20 | 3470.438 | 12.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4283.9835
2025-05-20 | 3378.8831 | 12.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4082.0156
2025-05-20 | 3359.7991 | 14 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.3095
2025-05-20 | 3479.7209 | 14.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4102.2326
2025-05-20 | 3781.0859 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4380.29
2025-05-20 | 4350.2729 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4567.0477
2025-05-20 | 4613.6729 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4884.8928
2025-05-20 | 4590.2412 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5015.9131
2025-05-20 | 4339.9521 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4887.1804
2025-05-20 | 4206.0342 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4973.298
2025-05-20 | 4164.4902 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4782.6354
2025-05-20 | 4099.2871 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4760.4748
2025-05-20 | 4036.9551 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4537.8535
2025-05-20 | 3918.969 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4409.507
2025-05-20 | 4123.4771 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4517.7973
2025-05-20 | 4632.6011 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4871.4666
2025-05-20 | 5255.7729 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5465.1858
2025-05-20 | 5207.3682 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5677.6391
2025-05-20 | 5202.5181 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5722.3463
2025-05-20 | 5389.0142 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5758.7184
2025-05-20 | 5132.6401 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5633.8146
2025-05-20 | 4638.1592 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5175.3794
2025-05-20 | 3910.772 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4595.1825
2025-05-20 | 3499.031 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4097.7235
2025-05-21 | 3248.4351 | 8.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3799.9697
2025-05-21 | 3132.4871 | 8.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3631.0028
2025-05-21 | 3107.7219 | 9.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546.2942
2025-05-21 | 3231.262 | 9.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3541.2166
2025-05-21 | 3559.3999 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.2715
2025-05-21 | 3976.041 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4138.0354
2025-05-21 | 4245.689 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4433.8799
2025-05-21 | 4297.7778 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4729.9049
2025-05-21 | 4182.2271 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4821.1785
2025-05-21 | 4112.2842 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4819.2936
2025-05-21 | 4193.9351 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4683.6325
2025-05-21 | 4154.9521 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4650.4717
2025-05-21 | 3987.438 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4526.8532
2025-05-21 | 4018.7209 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4387.5063
2025-05-21 | 4214.6621 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4473.7961
2025-05-21 | 4825.2881 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4838.4657
2025-05-21 | 5355.6201 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5465.1858
2025-05-21 | 5441.2261 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5776.642
2025-05-21 | 5457.2251 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5722.3463
2025-05-21 | 5378.978 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5747.7181
2025-05-21 | 5153.875 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5545.8121
2025-05-21 | 4547.5708 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5054.3759
2025-05-21 | 3944.6421 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4474.1791
2025-05-21 | 3537.948 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4130.7244
2025-05-22 | 3342.522 | 9.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3876.9719
2025-05-22 | 3239.0791 | 10.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3774.0069
2025-05-22 | 3186.4351 | 10.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3667.2976
2025-05-22 | 3302.073 | 10.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3629.2191
2025-05-22 | 3525.0879 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3852.275
2025-05-22 | 4056.196 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4215.0376
2025-05-22 | 4380.7969 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4620.8853
2025-05-22 | 4598.7368 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4927.9106
2025-05-22 | 4540.71 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5085.1861
2025-05-22 | 4503.8931 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5072.3008
2025-05-22 | 4499.7432 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5035.6426
2025-05-22 | 4510.9619 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5002.4817
2025-05-22 | 4412.7891 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4878.8632
2025-05-22 | 4391.9482 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4794.5179
2025-05-22 | 4435.2939 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4858.807
2025-05-22 | 5033.479 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5223.4767
2025-05-22 | 5526.0161 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5696.1924
2025-05-22 | 5465.498 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5985.6479
2025-05-22 | 5532.313 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6041.3554
2025-05-22 | 5633.2881 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6077.7275
2025-05-22 | 5303.1602 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5941.8233
2025-05-22 | 4744.1279 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5483.3881
2025-05-22 | 4123.521 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4881.1907
2025-05-22 | 3695.3479 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4372.7313
2025-05-23 | 3438.5229 | 10.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4041.9766
2025-05-23 | 3315.9709 | 10.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3851.0091
2025-05-23 | 3231.1311 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3755.3001
2025-05-23 | 3327.373 | 11.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3750.2226
2025-05-23 | 3695.7129 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3951.2778
2025-05-23 | 4221.0742 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4281.0395
2025-05-23 | 4527.2632 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4642.8859
2025-05-23 | 4686.8892 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4982.9121
2025-05-23 | 4707.6851 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5118.187
2025-05-23 | 4492.5981 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5050.3001
2025-05-23 | 4551.2158 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.6423
2025-05-23 | 4552.8662 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4980.4811
2025-05-23 | 4366.9189 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4845.8622
2025-05-23 | 4390.063 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4618.5129
2025-05-23 | 4436.4111 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4891.808
2025-05-23 | 4894.8599 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5179.4754
2025-05-23 | 5322.1758 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5861.1971
2025-05-23 | 5382.0229 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6084.6507
2025-05-23 | 5389.8281 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6184.3595
2025-05-23 | 5374.52 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6187.7306
2025-05-23 | 5094.1362 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5974.8243
2025-05-23 | 4757.019 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5538.3897
2025-05-23 | 4173.4458 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4958.1928
2025-05-23 | 3751.9641 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4537.736
2025-05-24 | 3521.8921 | 11.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4441.4545
2025-05-24 | 3356.73 | 11.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4228.4863
2025-05-24 | 3305.707 | 12.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4165.7783
2025-05-24 | 3333.019 | 12.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4160.7008
2025-05-24 | 3490.324 | 12.3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4295.7541
2025-05-24 | 3810.1489 | 11.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4581.5146
2025-05-24 | 4413.0771 | 11.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4943.3609
2025-05-24 | 4834.1089 | 11.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5283.3872
2025-05-24 | 5186.5908 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5396.6614
2025-05-24 | 5309.1621 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5295.7736
2025-05-24 | 5404.3472 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.1139
2025-05-24 | 5381.6411 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5170.953
2025-05-24 | 5311.1011 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5069.3351
2025-05-24 | 5077.1191 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4896.9873
2025-05-24 | 5183.6802 | 6.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5016.278
2025-05-24 | 5484.8662 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5303.9455
2025-05-24 | 5798.6812 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5820.6625
2025-05-24 | 5612.3989 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6154.1192
2025-05-24 | 5359.0908 | 6.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6198.8264
2025-05-24 | 5277.8008 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6191.1972
2025-05-24 | 5097.0229 | 8.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6066.2934
2025-05-24 | 4615.5161 | 8.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5574.8573
2025-05-24 | 4074.1211 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4972.6598
2025-05-24 | 3664.2561 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4607.2045
2025-05-25 | 3460.959 | 11.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4408.4536
2025-05-25 | 3301.448 | 11.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4195.4854
2025-05-25 | 3279.4309 | 10.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3967.7727
2025-05-25 | 3272.083 | 11.3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.6973
2025-05-25 | 3409.825 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4086.7482
2025-05-25 | 3734.8569 | 10.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4383.5089
2025-05-25 | 4214.8232 | 9.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4712.3544
2025-05-25 | 4686.0322 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4942.3775
2025-05-25 | 5030.1069 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4934.6483
2025-05-25 | 5020.3101 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888.7621
2025-05-25 | 4999.8169 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4786.102
2025-05-25 | 5014.939 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4554.9354
2025-05-25 | 4928.4419 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4244.3116
2025-05-25 | 4857.749 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4225.9682
2025-05-25 | 5004.6318 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.5342
2025-05-25 | 5519.6802 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4654.927
2025-05-25 | 5838.8882 | 0 | 0.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5351.4996
2025-05-25 | 5875.4639 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5670.1054
2025-05-25 | 5726.8271 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6077.823
2025-05-25 | 5585.876 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5971.191
2025-05-25 | 5311.3149 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5714.2834
2025-05-25 | 4575.7539 | 7.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5442.8535
2025-05-25 | 3871.124 | 7.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4807.6551
2025-05-25 | 3422.0259 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4332.1967
2025-05-26 | 3198 | 8.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3788.9694
2025-05-26 | 3094.772 | 9.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3664.0037
2025-05-26 | 2999.301 | 9.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546.2942
2025-05-26 | 3103.781 | 10.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3651.2197
2025-05-26 | 3414.3689 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.2731
2025-05-26 | 3966.5559 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4127.0351
2025-05-26 | 4327.4331 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4356.8777
2025-05-26 | 4433.0508 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4509.8987
2025-05-26 | 4263.6919 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4403.1666
2025-05-26 | 4136.29 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.276
2025-05-26 | 3990.1479 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4166.7557
2025-05-26 | 3970.0701 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.7241
2025-05-26 | 3853.9199 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5460.0977
2025-05-26 | 3863.8159 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5654.7488
2025-05-26 | 3983.6001 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6181.6027
2025-05-26 | 4714.479 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6384.7046
2025-05-26 | 5229.3379 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6945.4228
2025-05-26 | 5078.8369 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6581.4576
2025-05-26 | 5127.0488 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6226.0271
2025-05-26 | 5101.7539 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5425.41
2025-05-26 | 5072.3179 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5050.798
2025-05-26 | 4467.4629 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4713.3662
2025-05-26 | 3805.103 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4188.1709
2025-05-26 | 3343.311 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3866.7169
2025-05-27 | 3026.759 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3645.9653
2025-05-27 | 2903.6521 | 7.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520.9997
2025-05-27 | 2875.9031 | 8.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.2917
2025-05-27 | 2928.1851 | 9.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3563.2172
2025-05-27 | 3246.0801 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.2703
2025-05-27 | 3760.47 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.0317
2025-05-27 | 3951.9919 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.8743
2025-05-27 | 4075.1831 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4223.8905
2025-05-27 | 3914.675 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4150.1594
2025-05-27 | 3880.134 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.1221
2025-05-27 | 3833.217 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5304.8798
2025-05-27 | 3989.697 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6112.4208
2025-05-27 | 3826.3999 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6194.3713
2025-05-27 | 3905.915 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6352.3087
2025-05-27 | 4102.1089 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6365.1711
2025-05-27 | 4845.1372 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7302.5466
2025-05-27 | 5341.5142 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7716.4101
2025-05-27 | 5383.623 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.15
2025-05-27 | 5553.3481 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7621.1469
2025-05-27 | 5533.7319 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7004.0982
2025-05-27 | 5343.0132 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5520.9261
2025-05-27 | 4737.6191 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4838.634
2025-05-27 | 3927.9971 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3803.1599
2025-05-27 | 3450.6699 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3646.7106
2025-05-28 | 3140.072 | 3.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.9534
2025-05-28 | 2983.8879 | 6.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3355.9949
2025-05-28 | 2846.7781 | 8.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3447.2914
2025-05-28 | 2974.9441 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3508.2157
2025-05-28 | 3243.3411 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.2659
2025-05-28 | 3741.748 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4039.0326
2025-05-28 | 4061.6001 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3861.8636
2025-05-28 | 4209.957 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4025.8849
2025-05-28 | 4134.2168 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4400.0055
2025-05-28 | 4003.7019 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5370.9641
2025-05-28 | 3996.4819 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5892.2986
2025-05-28 | 4185.0332 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6552.9849
2025-05-28 | 4187.4932 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.6491
2025-05-28 | 4261.8149 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6866.3002
2025-05-28 | 4484.2378 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7026.0173
2025-05-28 | 5088.9668 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7632.9697
2025-05-28 | 5701.106 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7826.5511
2025-05-28 | 5824.4268 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7829.7227
2025-05-28 | 5798.2388 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7474.2921
2025-05-28 | 5764.7632 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6233.1109
2025-05-28 | 5628.936 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5484.2124
2025-05-28 | 4949.6831 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4838.634
2025-05-28 | 4120.3882 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3803.1599
2025-05-28 | 3561.238 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3404.7037
2025-05-29 | 3230.5049 | 1.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3051.9484
2025-05-29 | 3066.345 | 1.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2871.9812
2025-05-29 | 2961.031 | 2.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2820.2735
2025-05-29 | 3021.354 | 3.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2859.1972
2025-05-29 | 3289.0591 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.2537
2025-05-29 | 3637.563 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.0154
2025-05-29 | 3971.8821 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3828.8627
2025-05-29 | 4146.4351 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4212.8902
2025-05-29 | 4198.1382 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4480.1688
2025-05-29 | 4225.6348 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.2851
2025-05-29 | 4187.4248 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4463.6263
2025-05-29 | 4241.4189 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4353.4632
2025-05-29 | 4139.5649 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.8438
2025-05-29 | 4138.2178 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4057.4969
2025-05-29 | 4249.8521 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4154.787
2025-05-29 | 4733.7788 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4420.4538
2025-05-29 | 5149.1719 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5146.1767
2025-05-29 | 5209.7549 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5292.6282
2025-05-29 | 5204.3081 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5293.3341
2025-05-29 | 5236.7412 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5373.7074
2025-05-29 | 5010.1611 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5160.8011
2025-05-29 | 4427.0918 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4636.364
2025-05-29 | 3841.968 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4045.1668
2025-05-29 | 3425.9719 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3569.7084
2025-05-30 | 3140.0481 | 3.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3260.9544
2025-05-30 | 2952.823 | 3.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.9871
2025-05-30 | 2866.0911 | 4.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3007.2788
2025-05-30 | 2906.4729 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3068.2031
2025-05-30 | 3201.9619 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3192.2562
2025-05-30 | 3574.0691 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3522.0179
2025-05-30 | 3952.186 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3894.8646
2025-05-30 | 4115.6362 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.8889
2025-05-30 | 4191.0229 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4315.1641
2025-05-30 | 4188.1079 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4247.2773
2025-05-30 | 4233.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4056.6147
2025-05-30 | 4197.0298 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4067.4551
2025-05-30 | 4118.0698 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4505.542
2025-05-30 | 4063.1211 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4590.0521
2025-05-30 | 4134.6431 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5116.906
2025-05-30 | 4590.019 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5797.2857
2025-05-30 | 5006.0332 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6504.8587
2025-05-30 | 5018.9678 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6324.4618
2025-05-30 | 5099.7192 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5568.342
2025-05-30 | 5138.3018 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5582.7134
2025-05-30 | 4964.7578 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5347.8064
2025-05-30 | 4495.7319 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4834.3697
2025-05-30 | 3962.4041 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4144.1697
2025-05-30 | 3567.1599 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3657.7109
2025-05-31 | 3236.644 | 4.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627.4313
2025-05-31 | 2990.054 | 4.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.4644
2025-05-31 | 2920.3359 | 4.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3318.7542
2025-05-31 | 2870.1121 | 5.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3368.6782
2025-05-31 | 2975.0129 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3569.7334
2025-05-31 | 3272.793 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.4995
2025-05-31 | 3749.9009 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4547.3497
2025-05-31 | 4375.1572 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5019.3797
2025-05-31 | 4751.021 | 9.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5297.6586
2025-05-31 | 5058.4668 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5449.778
2025-05-31 | 5181.1709 | 10.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5446.1208
2025-05-31 | 5504.4951 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5456.9611
2025-05-31 | 5473.0322 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5311.342
2025-05-31 | 5422.002 | 9.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5237.9971
2025-05-31 | 5329.3921 | 8.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5192.283
2025-05-31 | 5671.061 | 7.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5490.9508
2025-05-31 | 5886.1602 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5875.664
2025-05-31 | 5642.5391 | 4.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5934.113
2025-05-31 | 5342.1318 | 3.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5835.8161
2025-05-31 | 5218.1558 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5905.1891
2025-05-31 | 4957.8809 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5802.2859
2025-05-31 | 4623.2168 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5420.8529
2025-05-31 | 4148.1548 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4873.6569
2025-05-31 | 3683.377 | 8.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4475.2007
2025-06-01 | 3375.304 | 8.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.4457
2025-06-01 | 3200.2119 | 9.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3986.4794
2025-06-01 | 3159.2251 | 10.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3978.773
2025-06-01 | 3120.3511 | 11.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4061.6979
2025-06-01 | 3300.0239 | 11.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4163.7504
2025-06-01 | 3599.7141 | 11.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4504.5124
2025-06-01 | 4081.615 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.3572
2025-06-01 | 4669.292 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5140.3831
2025-06-01 | 5072.2651 | 10.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5440.6627
2025-06-01 | 5372.8242 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5449.778
2025-06-01 | 5562.6899 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5325.1173
2025-06-01 | 5488.3418 | 8.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5225.9546
2025-06-01 | 5275.0562 | 6.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4992.3329
2025-06-01 | 5163.2568 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4731.9826
2025-06-01 | 5317.4941 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4895.2746
2025-06-01 | 5733.9829 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5347.9467
2025-06-01 | 6051.6201 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5974.6669
2025-06-01 | 6096.4731 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6286.123
2025-06-01 | 6020.7832 | 8.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6374.8314
2025-06-01 | 5756.6631 | 8.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6367.2023
2025-06-01 | 5300.1792 | 9.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6231.2981
2025-06-01 | 4643.498 | 9.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5706.861
2025-06-01 | 4030.0061 | 9.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5027.6613
2025-06-01 | 3542.4609 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4497.2014
2025-06-02 | 3247.9131 | 9.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3920.9732
2025-06-02 | 3206.2939 | 10.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3851.0091
2025-06-02 | 3204.563 | 11 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3755.3001
2025-06-02 | 3216.8101 | 11.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3783.2235
2025-06-02 | 3515.217 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.2797
2025-06-02 | 3955.197 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4391.0426
2025-06-02 | 4278.3311 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4433.8799
2025-06-02 | 4310.1558 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4663.903
2025-06-02 | 4148.998 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4678.1745
2025-06-02 | 4125.333 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.2851
2025-06-02 | 4029.8521 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4221.6194
2025-06-02 | 4010.126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4056.4547
2025-06-02 | 3920.5869 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4321.9737
2025-06-02 | 3865.0381 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4369.7701
2025-06-02 | 3985.5779 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4492.7735
2025-06-02 | 4658.9072 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4806.0164
2025-06-02 | 5171.7412 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5880.7261
2025-06-02 | 5183.8511 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6214.3208
2025-06-02 | 5174.356 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6042.4587
2025-06-02 | 5215.8359 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5425.41
2025-06-02 | 5074.7031 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5215.8027
2025-06-02 | 4535.1411 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4889.3712
2025-06-02 | 3783.1531 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4375.1762
2025-06-02 | 3421.488 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3976.72
2025-06-03 | 3100.6621 | 8.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.9688
2025-06-03 | 3006.0339 | 9.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.0059
2025-06-03 | 2959.1011 | 9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3535.2939
2025-06-03 | 3029.3679 | 8.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3475.2147
2025-06-03 | 3344.408 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3599.2678
2025-06-03 | 3811.2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.0298
2025-06-03 | 4089.0181 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4290.8759
2025-06-03 | 4092.2119 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4421.8961
2025-06-03 | 3947.8069 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4271.1629
2025-06-03 | 3892.2041 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.2763
2025-06-03 | 3906.095 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4423.7515
2025-06-03 | 3925.1311 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5121.1514
2025-06-03 | 3923.2981 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5827.2345
2025-06-03 | 3964.502 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6058.5993
2025-06-03 | 4237.896 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6622.1668
2025-06-03 | 4837.3989 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7082.2645
2025-06-03 | 5342.6841 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7349.2733
2025-06-03 | 5279.5161 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7315.7312
2025-06-03 | 5302.311 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6813.4459
2025-06-03 | 5441.1152 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6269.8246
2025-06-03 | 5273.791 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5337.3577
2025-06-03 | 4684.939 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4372.3565
2025-06-03 | 4021.355 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3814.1603
2025-06-03 | 3455.301 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3569.7084
2025-06-04 | 3136.8911 | 4.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.9575
2025-06-04 | 2989.1919 | 2.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2926.9827
2025-06-04 | 2926.5969 | 2.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2831.2738
2025-06-04 | 2939.2051 | 2.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2826.1962
2025-06-04 | 3196.501 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2961.2496
2025-06-04 | 3709.741 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3236.0097
2025-06-04 | 4038.293 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3410.8508
2025-06-04 | 4311.9829 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4224.4421
2025-06-04 | 4310.687 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4767.1423
2025-06-04 | 4362.3901 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5958.3829
2025-06-04 | 4505.2832 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6699.9996
2025-06-04 | 4754.4258 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7360.6859
2025-06-04 | 4956.3188 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7846.4868
2025-06-04 | 5141.7271 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8004.4243
2025-06-04 | 5509.7358 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8457.8508
2025-06-04 | 6263.564 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8844.5211
2025-06-04 | 7015.2759 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9295.0983
2025-06-04 | 7193.3789 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9261.5562
2025-06-04 | 7085.5508 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8979.553
2025-06-04 | 7000.6558 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8582.7864
2025-06-04 | 6747.5688 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8017.4563
2025-06-04 | 6028.8281 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6931.3137
2025-06-04 | 5191.98 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5499.4147
2025-06-04 | 4591.6948 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4476.9638
2025-06-05 | 4098.5088 | 0 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683.6443
2025-06-05 | 3840.3169 | 0 | 1.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3287.1078
2025-06-05 | 3658.2881 | 0 | 1.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3132.6845
2025-06-05 | 3590.0869 | 0 | 1.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3032.179
2025-06-05 | 3828.697 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3031.3779
2025-06-05 | 4230.5601 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.567
2025-06-05 | 4548.8359 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.7009
2025-06-05 | 4806.5869 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4371.2968
2025-06-05 | 4885.8921 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4913.997
2025-06-05 | 5002.9268 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4893.6863
2025-06-05 | 5173.4321 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5011.1703
2025-06-05 | 5325.853 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5525.0019
2025-06-05 | 5386.0342 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5460.0977
2025-06-05 | 5360.4229 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5654.7488
2025-06-05 | 5646.8291 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6108.1753
2025-06-05 | 6192.5659 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6164.4225
2025-06-05 | 6685.2749 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6394.7176
2025-06-05 | 6562.6621 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6581.4576
2025-06-05 | 6451.0298 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6226.0271
2025-06-05 | 6250.3218 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6122.9699
2025-06-05 | 6130.3101 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5631.0672
2025-06-05 | 5452.5918 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4691.7793
2025-06-05 | 4677.7139 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3913.1631
2025-06-05 | 4101.1719 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3492.7062
2025-06-06 | 3693.189 | 2.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3194.9525
2025-06-06 | 3404.74 | 4.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3190.9902
2025-06-06 | 3309.842 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3095.2813
2025-06-06 | 3334.8069 | 4.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.2028
2025-06-06 | 3550.2361 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3115.254
2025-06-06 | 3908.8369 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3544.0185
2025-06-06 | 4343.9819 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3795.8617
2025-06-06 | 4604.603 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3926.882
2025-06-06 | 4766.585 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032.8687
2025-06-06 | 4841.1802 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4967.1136
2025-06-06 | 4966.2559 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5231.4524
2025-06-06 | 5061.3452 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.5661
2025-06-06 | 5013.2588 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6010.8029
2025-06-06 | 5171.1831 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6352.3087
2025-06-06 | 5619.7959 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6879.1626
2025-06-06 | 6130.0288 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.9782
2025-06-06 | 6702.0972 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7606.269
2025-06-06 | 6462.0562 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7682.868
2025-06-06 | 6394.376 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6813.4459
2025-06-06 | 6127.2939 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6526.8204
2025-06-06 | 5883.394 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5924.7766
2025-06-06 | 5362.3799 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4948.775
2025-06-06 | 4764.48 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4141.0085
2025-06-06 | 4206.2578 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3302.1261
2025-06-07 | 3767.3069 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3165.4182
2025-06-07 | 3481.1641 | 0.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3018.4518
2025-06-07 | 3307.501 | 0 | 0.6 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3044.0222
2025-06-07 | 3252.283 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2796.6619
2025-06-07 | 3361.4041 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3140.7212
2025-06-07 | 3607.623 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481.4832
2025-06-07 | 4192.248 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3715.0386
2025-06-07 | 4894.5269 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4135.7798
2025-06-07 | 5485.0288 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4751.9073
2025-06-07 | 5774.7651 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5429.1564
2025-06-07 | 6011.0488 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6023.9184
2025-06-07 | 6203.2539 | 0 | 5.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6427.6089
2025-06-07 | 6342.5308 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6546.2731
2025-06-07 | 6336.8369 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6594.0695
2025-06-07 | 6465.1279 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6937.355
2025-06-07 | 6819.9692 | 0 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7213.8842
2025-06-07 | 7112.168 | 0 | 5.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7334.0383
2025-06-07 | 7028.6958 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7153.6415
2025-06-07 | 6556.0752 | 0 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6871.6383
2025-06-07 | 6052.708 | 0 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6328.017
2025-06-07 | 5681.876 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5505.6911
2025-06-07 | 5090.665 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4694.8322
2025-06-07 | 4439.5239 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4114.6353
2025-06-07 | 3961.6631 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3727.1794
2025-06-08 | 3550.3779 | 2.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3429.4257
2025-06-08 | 3357.7419 | 3.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3315.4603
2025-06-08 | 3235.791 | 5.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384.7561
2025-06-08 | 3155.301 | 5.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445.6804
2025-06-08 | 3202.6589 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3613.7347
2025-06-08 | 3460.29 | 7.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4097.5008
2025-06-08 | 3974.541 | 5.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4250.3412
2025-06-08 | 4630.5059 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4348.3606
2025-06-08 | 5174.0132 | 0.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4307.6304
2025-06-08 | 5535.7012 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4915.1649
2025-06-08 | 5620.3442 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5656.7816
2025-06-08 | 5779.0928 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6133.8995
2025-06-08 | 5780.7339 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6252.5637
2025-06-08 | 5982.8618 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.0737
2025-06-08 | 6139.5439 | 0 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6606.9319
2025-06-08 | 6570.4209 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6699.8927
2025-06-08 | 6785.9258 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7187.1836
2025-06-08 | 6612.6709 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7300.4962
2025-06-08 | 6460.4121 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6761.4972
2025-06-08 | 6286.3701 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6438.158
2025-06-08 | 5926.0479 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5579.1185
2025-06-08 | 5277.085 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4896.8264
2025-06-08 | 4512.521 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4114.6353
2025-06-08 | 3934.0029 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3650.1772
2025-06-09 | 3552.665 | 1.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.9494
2025-06-09 | 3365.4431 | 2.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2904.9821
2025-06-09 | 3241.4341 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2710.2704
2025-06-09 | 3264.4099 | 1.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2650.1912
2025-06-09 | 3501.2971 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2829.2458
2025-06-09 | 3973.0049 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3148.0072
2025-06-09 | 4247.0308 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3454.852
2025-06-09 | 4403.166 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.8737
2025-06-09 | 4315.314 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4117.1585
2025-06-09 | 4393.9712 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4203.276
2025-06-09 | 4522.0688 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4232.6197
2025-06-09 | 4619.062 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4232.4598
2025-06-09 | 4526.439 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.8412
2025-06-09 | 4539.561 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4024.496
2025-06-09 | 4801.2832 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.7835
2025-06-09 | 5412.8501 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4438.8796
2025-06-09 | 6163.3071 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4962.8842
2025-06-09 | 6231.3789 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5182.625
2025-06-09 | 6119.4941 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5381.6124
2025-06-09 | 5923.6362 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5351.9826
2025-06-09 | 5581.8989 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5006.9346
2025-06-09 | 4994.2261 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4372.3565
2025-06-09 | 4263.6001 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3748.1584
2025-06-09 | 3800.2529 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3250.6993
2025-06-10 | 3447.446 | 0.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930.945
2025-06-10 | 3288.5439 | 1.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2783.9787
2025-06-10 | 3156.9619 | 1.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2699.27
2025-06-10 | 3238.8811 | 1.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2639.1909
2025-06-10 | 3414.4209 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2785.2446
2025-06-10 | 3831.3501 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3148.0072
2025-06-10 | 4287.251 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3476.8527
2025-06-10 | 4484.3838 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3820.5917
2025-06-10 | 4635.5732 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4583.5739
2025-06-10 | 4737.0269 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5150.682
2025-06-10 | 4788.7852 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5672.0166
2025-06-10 | 4911.418 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5268.0061
2025-06-10 | 4858.645 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5643.6661
2025-06-10 | 4875.519 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5911.7446
2025-06-10 | 5112.9751 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6144.889
2025-06-10 | 5794.9692 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6054.2815
2025-06-10 | 6309.1279 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6761.8544
2025-06-10 | 6254.936 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6728.3123
2025-06-10 | 6037.8081 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6115.886
2025-06-10 | 5745.3418 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5535.551
2025-06-10 | 5534.458 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4951.7951
2025-06-10 | 4938.3652 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4537.3612
2025-06-10 | 4247.4292 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3979.165
2025-06-10 | 3753.646 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3514.7069
2025-06-11 | 3393.907 | 3.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3304.9556
2025-06-11 | 3190.738 | 4.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3190.9902
2025-06-11 | 3115.53 | 5.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3128.2823
2025-06-11 | 3169.78 | 5.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3167.206
2025-06-11 | 3380.2241 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3302.2593
2025-06-11 | 3773.5549 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3610.0204
2025-06-11 | 4203.6572 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3861.8636
2025-06-11 | 4377.8062 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4003.8842
2025-06-11 | 4355.3809 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.1557
2025-06-11 | 4312.6499 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.6905
2025-06-11 | 4447.3779 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5121.3114
2025-06-11 | 4465.3159 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5451.5745
2025-06-11 | 4495.1768 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5276.5293
2025-06-11 | 4677.3291 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5764.8899
2025-06-11 | 4922.5151 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6108.1753
2025-06-11 | 5623.792 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6715.1277
2025-06-11 | 6135.9072 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6798.5681
2025-06-11 | 5930.542 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6728.3123
2025-06-11 | 5826.4082 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6189.3134
2025-06-11 | 5764.7749 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6122.9699
2025-06-11 | 5555.6948 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5557.6398
2025-06-11 | 4885.1519 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4372.3565
2025-06-11 | 4204.3872 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3814.1603
2025-06-11 | 3741.6311 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3349.7022
2025-06-12 | 3403.2461 | 2.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3139.9509
2025-06-12 | 3246.207 | 3.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.9871
2025-06-12 | 3157.489 | 3.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930.2766
2025-06-12 | 3160.8889 | 3.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2881.1978
2025-06-12 | 3374.9929 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3071.2527
2025-06-12 | 3850.292 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.0119
2025-06-12 | 4226.7778 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3685.8586
2025-06-12 | 4390.188 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-06-12 | 4469.543 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4117.1585
2025-06-12 | 4481.5469 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4060.2719
2025-06-12 | 4487.4609 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.3284
2025-06-12 | 4561.229 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.0231
2025-06-12 | 4595.771 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4285.26
2025-06-12 | 4610.8008 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4369.7701
2025-06-12 | 4814.209 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4492.7735
2025-06-12 | 5328.061 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.4437
2025-06-12 | 5945.686 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5440.162
2025-06-12 | 5890.6602 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5369.9062
2025-06-12 | 5706.666 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5227.3322
2025-06-12 | 5631.7681 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5406.7084
2025-06-12 | 5532.0679 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5358.8067
2025-06-12 | 4859.3511 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5021.375
2025-06-12 | 4109.7632 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4463.1787
2025-06-12 | 3583.9419 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3954.7194
2025-06-13 | 3272.9209 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3645.9653
2025-06-13 | 3060.6621 | 8.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3565.0009
2025-06-13 | 2975.26 | 9.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3623.2964
2025-06-13 | 2998.041 | 10.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3695.221
2025-06-13 | 3278.6299 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3830.2743
2025-06-13 | 3664.238 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4149.0358
2025-06-13 | 4036.7029 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4268.8752
2025-06-13 | 4174.396 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4476.8977
2025-06-13 | 4121.3818 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4645.1735
2025-06-13 | 4072.4541 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4511.2848
2025-06-13 | 4018.103 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4441.6257
2025-06-13 | 4086.9089 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4353.4632
2025-06-13 | 4046.7649 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.8438
2025-06-13 | 4095.3811 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4046.4966
2025-06-13 | 4298.7412 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4077.7848
2025-06-13 | 4528.1738 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4549.0206
2025-06-13 | 4866.4399 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5256.5936
2025-06-13 | 4865.8608 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5296.4788
2025-06-13 | 4825.354 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5227.3322
2025-06-13 | 4904.9819 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5318.7059
2025-06-13 | 4696.3389 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5237.8033
2025-06-13 | 4329.5288 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4735.3668
2025-06-13 | 3863.783 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4232.1722
2025-06-13 | 3478.8491 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3767.7141
2025-06-14 | 3223.323 | 5.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3781.4357
2025-06-14 | 3058.4009 | 7.3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.4725
2025-06-14 | 2967.1621 | 6.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3538.7605
2025-06-14 | 2954.729 | 8.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.6882
2025-06-14 | 3065.533 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3943.7441
2025-06-14 | 3318.959 | 8.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4251.5052
2025-06-14 | 3887.7119 | 6.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.3459
2025-06-14 | 4459.144 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4546.3662
2025-06-14 | 4879.2642 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4604.6389
2025-06-14 | 5044.127 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4525.7517
2025-06-14 | 5068.0122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4335.0891
2025-06-14 | 5012.606 | 0 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.6344
2025-06-14 | 4891.8491 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4894.1575
2025-06-14 | 4781.4722 | 0 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4978.6676
2025-06-14 | 4946.8638 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5505.5215
2025-06-14 | 5303.1392 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5928.9054
2025-06-14 | 5712.29 | 0 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6599.7647
2025-06-14 | 5561.2861 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6566.2226
2025-06-14 | 5399.7632 | 0 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6357.6468
2025-06-14 | 5226.3369 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5740.5981
2025-06-14 | 5051.8999 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5318.2721
2025-06-14 | 4595.8208 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4925.8388
2025-06-14 | 4130.6841 | 3.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4378.6428
2025-06-14 | 3626.6421 | 4.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4013.1876
2025-06-15 | 3295.5381 | 4.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3605.4307
2025-06-15 | 3084.1809 | 8.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3843.4753
2025-06-15 | 2958.355 | 8.9 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3802.768
2025-06-15 | 2939.886 | 9.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3852.692
2025-06-15 | 3028.0869 | 9.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.7457
2025-06-15 | 3290.3081 | 8.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4251.5052
2025-06-15 | 3763.8611 | 5.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.3434
2025-06-15 | 4502.1099 | 2.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4370.3612
2025-06-15 | 4822.3979 | 0.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4340.6314
2025-06-15 | 5131.1392 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5025.306
2025-06-15 | 5338.8159 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5583.3542
2025-06-15 | 5425.0269 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6023.7584
2025-06-15 | 5391.165 | 0 | 5.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6179.1363
2025-06-15 | 5417.9238 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6043.3643
2025-06-15 | 5662.0962 | 0 | 6.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6533.5045
2025-06-15 | 6130.5581 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.4611
2025-06-15 | 6540.3628 | 0 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7664.4614
2025-06-15 | 6605.1758 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7851.2014
2025-06-15 | 6441.5879 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7495.7708
2025-06-15 | 6281.5298 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6878.7222
2025-06-15 | 5901.272 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5762.6869
2025-06-15 | 5078.6318 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4896.8264
2025-06-15 | 4365.7461 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4433.6444
2025-06-15 | 3739.1841 | 3.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3870.1835
2025-06-16 | 3362.3279 | 4.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.9575
2025-06-16 | 3173.355 | 5.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3267.9924
2025-06-16 | 3041.614 | 5.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3139.2826
2025-06-16 | 3059.563 | 10.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3662.2201
2025-06-16 | 3324.05 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3423.2627
2025-06-16 | 3767.4441 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.0254
2025-06-16 | 4105.042 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3883.8643
2025-06-16 | 4318.064 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3981.8836
2025-06-16 | 4417.9531 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4510.1465
2025-06-16 | 4494.1079 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5517.8188
2025-06-16 | 4651.3091 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6075.867
2025-06-16 | 4875.1479 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6295.9892
2025-06-16 | 5011.916 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6488.0807
2025-06-16 | 5297.6201 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6719.4455
2025-06-16 | 5697.189 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7062.731
2025-06-16 | 6473.7041 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7706.397
2025-06-16 | 7332.769 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8156.9742
2025-06-16 | 7494.3848 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8086.7184
2025-06-16 | 7347.9482 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7621.1469
2025-06-16 | 7130.582 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7297.8076
2025-06-16 | 6708.647 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6475.4818
2025-06-16 | 5932.688 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5389.3392
2025-06-16 | 5020.0708 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4581.5727
2025-06-16 | 4351.6729 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3852.8313
2025-06-17 | 4001.3401 | 0 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3059.5118
2025-06-17 | 3737.5491 | 0.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2695.9761
2025-06-17 | 3598.4529 | 0.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2644.2685
2025-06-17 | 3579.3191 | 0.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2562.1887
2025-06-17 | 3773.053 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2697.2421
2025-06-17 | 4197.4722 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3030.7165
2025-06-17 | 4488.3179 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.7009
2025-06-17 | 4779.6021 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4297.8695
2025-06-17 | 4758.5879 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4400.0055
2025-06-17 | 4811.0249 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.8315
2025-06-17 | 4996.123 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5451.7345
2025-06-17 | 5461.6108 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5488.2882
2025-06-17 | 5655.4189 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6084.2302
2025-06-17 | 5867.1792 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6132.0266
2025-06-17 | 6331.7231 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6805.7352
2025-06-17 | 7116.2612 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7155.6918
2025-06-17 | 7899.1279 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7496.128
2025-06-17 | 7743.5928 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8050.0047
2025-06-17 | 7594.6919 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7731.2879
2025-06-17 | 7352.1182 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7150.9529
2025-06-17 | 6937.436 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6365.3407
2025-06-17 | 6160.8379 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5352.6255
2025-06-17 | 5330.8301 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4214.4359
2025-06-17 | 4666.3608 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3742.6902
2025-06-18 | 4226.0029 | 0 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.3623
2025-06-18 | 3933.9131 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3397.2488
2025-06-18 | 3802.634 | 0 | 1.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3242.8256
2025-06-18 | 3762.407 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3179.0337
2025-06-18 | 4036.6279 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.66
2025-06-18 | 4593.3848 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3654.8491
2025-06-18 | 5155.1899 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4280.9788
2025-06-18 | 5453.2148 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.2883
2025-06-18 | 5336.9731 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5354.5612
2025-06-18 | 5542.4751 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5664.6735
2025-06-18 | 5741.8979 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6002.4397
2025-06-18 | 5946.7632 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6626.4123
2025-06-18 | 6173.0552 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6891.9312
2025-06-18 | 6362.1489 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7160.0097
2025-06-18 | 6920.0659 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7209.5857
2025-06-18 | 7856.6069 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8183.6748
2025-06-18 | 8634.1475 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8817.8205
2025-06-18 | 8637.3594 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9261.5562
2025-06-18 | 8512.2432 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9163.1214
2025-06-18 | 8184.2842 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8582.7864
2025-06-18 | 7854.9888 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7613.6058
2025-06-18 | 6947.4038 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5903.3307
2025-06-18 | 5959.9922 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5536.1283
2025-06-18 | 5269.0361 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5064.3827
2025-06-19 | 4751.373 | 0 | 4.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4601.4863
2025-06-19 | 4450.2959 | 0 | 2.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3580.8172
2025-06-19 | 4184.2861 | 0 | 2.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.1076
2025-06-19 | 4122.9951 | 0 | 2.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3399.3158
2025-06-19 | 4324.2051 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3545.3694
2025-06-19 | 4719.187 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3764.9901
2025-06-19 | 5133.2861 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4207.5514
2025-06-19 | 5459.5439 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4958.7157
2025-06-19 | 5377.4741 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5427.9885
2025-06-19 | 5549.1592 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5627.9598
2025-06-19 | 5781.0908 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.585
2025-06-19 | 5991.3579 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5781.9977
2025-06-19 | 6239.3691 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6231.085
2025-06-19 | 6432.0352 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6242.1677
2025-06-19 | 6898.6768 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6585.4532
2025-06-19 | 7375.6851 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7486.1149
2025-06-19 | 7945.709 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8046.8332
2025-06-19 | 7765.0581 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8233.5731
2025-06-19 | 7658.585 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8171.852
2025-06-19 | 7256.4849 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7444.6623
2025-06-19 | 6755.3979 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6622.3365
2025-06-19 | 5889.0659 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5756.476
2025-06-19 | 5034.0811 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4471.4316
2025-06-19 | 4375.5439 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3265.4124
2025-06-20 | 3969.866 | 2.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.95
2025-06-20 | 3652.782 | 2.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2948.9834
2025-06-20 | 3549.2971 | 2.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2853.2744
2025-06-20 | 3497.875 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2848.1969
2025-06-20 | 3609.6211 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3016.2512
2025-06-20 | 3895.7451 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401.0144
2025-06-20 | 4176.0928 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3817.8624
2025-06-20 | 4459.4072 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4234.8908
2025-06-20 | 4534.5142 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4447.1679
2025-06-20 | 4486.4521 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4346.2801
2025-06-20 | 4673.2822 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.6172
2025-06-20 | 4775.1948 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.1642
2025-06-20 | 4905.832 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4689.1104
2025-06-20 | 4963.5068 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5140.7573
2025-06-20 | 5257.3608 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5410.6154
2025-06-20 | 5910.4331 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5907.4267
2025-06-20 | 6435.9341 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6431.4313
2025-06-20 | 6533.9722 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6654.8849
2025-06-20 | 6451.2749 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6519.7365
2025-06-20 | 6146.3711 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6086.2562
2025-06-20 | 5762.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4896.7936
2025-06-20 | 5225.0752 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4398.0699
2025-06-20 | 4613.7012 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4045.1668
2025-06-20 | 4108.3242 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3635.7103
2025-06-21 | 3740.4441 | 3.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3561.4294
2025-06-21 | 3477.054 | 4.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.4644
2025-06-21 | 3300.469 | 5.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3439.7576
2025-06-21 | 3293.375 | 7.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3588.6845
2025-06-21 | 3361.043 | 8.2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3844.7413
2025-06-21 | 3696.667 | 7.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4064.4999
2025-06-21 | 4272.3052 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4096.3368
2025-06-21 | 4997.7178 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4249.3577
2025-06-21 | 5484.896 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5119.0441
2025-06-21 | 5800.7832 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5649.4385
2025-06-21 | 6107.1279 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6170.7731
2025-06-21 | 6377.5562 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6501.0362
2025-06-21 | 6305.814 | 0 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6986.8372
2025-06-21 | 6792.7319 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7108.061
2025-06-21 | 7103.7368 | 0 | 8.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7414.6328
2025-06-21 | 7415.77 | 0 | 8.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7801.3031
2025-06-21 | 7570.4312 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8105.0256
2025-06-21 | 7447.4722 | 0 | 6.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7814.4877
2025-06-21 | 7505.5029 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7605.9119
2025-06-21 | 7076.5249 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7209.1453
2025-06-21 | 6746.8218 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6864.0973
2025-06-21 | 6173.3398 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6622.3693
2025-06-21 | 5594.9619 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6034.8849
2025-06-21 | 5006.1548 | 0 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4682.0109
2025-06-22 | 4361.1479 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4255.8282
2025-06-22 | 4098.252 | 0 | 3.5 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4226.4284
2025-06-22 | 3953.4651 | 0 | 2.2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3631.441
2025-06-22 | 3797.6919 | 0 | 1.3 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3273.9397
2025-06-22 | 3856.657 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456.7071
2025-06-22 | 4125.792 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3713.0414
2025-06-22 | 4687.7329 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4339.1711
2025-06-22 | 5487.0991 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200.4765
2025-06-22 | 6299.186 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6330.5955
2025-06-22 | 7140.104 | 0 | 7.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6934.4173
2025-06-22 | 7731.814 | 0 | 8.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7382.3245
2025-06-22 | 8184.7949 | 0 | 9.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7859.4424
2025-06-22 | 8523.5449 | 0 | 9.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7794.5382
2025-06-22 | 8917.5186 | 0 | 10.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7879.0483
2025-06-22 | 9307.959 | 0 | 11.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8332.4748
2025-06-22 | 9873.666 | 0 | 11.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8719.145
2025-06-22 | 10321.1738 | 0 | 10.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9022.8675
2025-06-22 | 10375.5098 | 0 | 10.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9283.0348
2025-06-22 | 10053.6953 | 0 | 10.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9147.8864
2025-06-22 | 9583.9531 | 0 | 8.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8677.6924
2025-06-22 | 9046.6191 | 0 | 7.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7892.0803
2025-06-22 | 8051.3389 | 0 | 5.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6732.5103
2025-06-22 | 7071.1118 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6218.4533
2025-06-22 | 6399.4692 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5746.7076
2025-06-23 | 5816.4248 | 0 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4931.9094
2025-06-23 | 5379.7598 | 0 | 4.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4278.3771
2025-06-23 | 5071.4551 | 0 | 4.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4197.3812
2025-06-23 | 4940.9238 | 0 | 3.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.1662
2025-06-23 | 5137.2568 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3728.9378
2025-06-23 | 5650.6108 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4205.5543
2025-06-23 | 6384.7568 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5308.9618
2025-06-23 | 7103.3779 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.1218
2025-06-23 | 7748.5269 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7630.8093
2025-06-23 | 8253.6279 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8858.7636
2025-06-23 | 8615.9297 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9416.8118
2025-06-23 | 9115.2979 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9783.7887
2025-06-23 | 9304.543 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9902.4529
2025-06-23 | 9549.2178 | 0 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9913.5356
2025-06-23 | 9835.4443 | 0 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10183.3937
2025-06-23 | 10451.5674 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10606.7777
2025-06-23 | 10913.8633 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10873.7865
2025-06-23 | 10951.6328 | 0 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10950.3854
2025-06-23 | 10835.1826 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10668.3822
2025-06-23 | 10419.3652 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 10051.3336
2025-06-23 | 9889.6953 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9375.8624
2025-06-23 | 9026.5664 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8436.5746
2025-06-23 | 7889.3652 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7335.0986
2025-06-23 | 6949.0591 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6606.3572
2025-06-24 | 6267.4131 | 0 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6216.8882
2025-06-24 | 5904.5132 | 0 | 8.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5636.7832
2025-06-24 | 5613.0889 | 0 | 7.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5335.5053
2025-06-24 | 5522.9829 | 0 | 6.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5051.4313
2025-06-24 | 5692.0869 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903.7756
2025-06-24 | 6223.228 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5343.6783
2025-06-24 | 6781.999 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300.2311
2025-06-24 | 7494.2939 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7455.2459
2025-06-24 | 7969.6938 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8218.2281
2025-06-24 | 8432.3252 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8675.1952
2025-06-24 | 8753.3213 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8939.534
2025-06-24 | 9396.9307 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9379.9382
2025-06-24 | 9418.7012 | 0 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9351.7477
2025-06-24 | 9621.2109 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9509.6851
2025-06-24 | 9255.6943 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9559.2612
2025-06-24 | 9090.4521 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8183.6748
2025-06-24 | 9312.834 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8891.2478
2025-06-24 | 9531.5156 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8380.4279
2025-06-24 | 9462.0029 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8465.5615
2025-06-24 | 9191.668 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8105.5086
2025-06-24 | 8658.8271 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7650.3195
2025-06-24 | 7878.4331 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7885.8694
2025-06-24 | 6917.7842 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6233.6882
2025-06-24 | 6193.4731 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5321.3784
2025-06-25 | 5693.4102 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4344.4906
2025-06-25 | 5381.4038 | 0 | 4.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4241.6634
2025-06-25 | 5121.3682 | 0 | 2.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3389.6803
2025-06-25 | 5009.394 | 0 | 1.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2958.7516
2025-06-25 | 5164.7808 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692.2241
2025-06-25 | 5658.7119 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3875.1311
2025-06-25 | 6085.895 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5088.6797
2025-06-25 | 6425.645 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5949.985
2025-06-25 | 6976.231 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6529.3989
2025-06-25 | 7373.5298 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6729.3702
2025-06-25 | 7621.771 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6810.1406
2025-06-25 | 7866.2388 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7177.1175
2025-06-25 | 8002.479 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6891.9312
2025-06-25 | 8126.1392 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7270.1507
2025-06-25 | 8419.2676 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7466.5815
2025-06-25 | 9075.709 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7853.2517
2025-06-25 | 9701.1211 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8230.4016
2025-06-25 | 9567.6816 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8307.0005
2025-06-25 | 9122.3623 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7951.57
2025-06-25 | 8455.4111 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7334.5213
2025-06-25 | 7725.3999 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6732.4775
2025-06-25 | 6672.7568 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5903.3307
2025-06-25 | 5697.207 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4985.4232
2025-06-25 | 5006.874 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4293.3954
2025-06-26 | 4543.9292 | 0 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683.6443
2025-06-26 | 4199.4932 | 0 | 1.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3103.5394
2025-06-26 | 4046.061 | 0.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2567.2663
2025-06-26 | 3923.313 | 1.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2661.1915
2025-06-26 | 4094.2881 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2829.2458
2025-06-26 | 4474.5508 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3192.0085
2025-06-26 | 4587.5298 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3575.8555
2025-06-26 | 4616.9268 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3926.882
2025-06-26 | 4470.688 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.1591
2025-06-26 | 4414.2661 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4181.2754
2025-06-26 | 4502.6372 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4287.6213
2025-06-26 | 4677.5068 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4232.4598
2025-06-26 | 4694.1128 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4053.8397
2025-06-26 | 4589.7729 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3980.4947
2025-06-26 | 4680.7808 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3989.7823
2025-06-26 | 5112.0562 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4512.3069
2025-06-26 | 5508.5889 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5366.7346
2025-06-26 | 5544.7041 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5994.0387
2025-06-26 | 5628.9541 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5748.7492
2025-06-26 | 5479.9561 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5351.9826
2025-06-26 | 5408.7979 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5259.8039
2025-06-26 | 4936.2129 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4922.3722
2025-06-26 | 4320.0552 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4199.1712
2025-06-26 | 3855.2649 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3745.7134
2025-06-27 | 3539.4629 | 6.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546.9625
2025-06-27 | 3334.0239 | 4.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3201.9906
2025-06-27 | 3228.0229 | 4.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.281
2025-06-27 | 3204.793 | 4.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3057.2028
2025-06-27 | 3345.4609 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3357.2609
2025-06-27 | 3739.896 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3610.0204
2025-06-27 | 4017.978 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3806.8621
2025-06-27 | 4273.917 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3937.8824
2025-06-27 | 4377.583 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4018.1557
2025-06-27 | 4571.5088 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.6905
2025-06-27 | 4712.0601 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5525.1618
2025-06-27 | 4858.6782 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5745.284
2025-06-27 | 5151.751 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6341.226
2025-06-27 | 5152.543 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5948.4583
2025-06-27 | 5251.79 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5594.1838
2025-06-27 | 5455.6709 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5283.2942
2025-06-27 | 5800.98 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4959.1714
2025-06-27 | 5772.9409 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5336.6294
2025-06-27 | 5752.6221 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5271.3335
2025-06-27 | 5721.3838 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5186.7021
2025-06-27 | 5616.2402 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4940.7948
2025-06-27 | 5094.1089 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4405.3574
2025-06-27 | 4550.5581 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3770.159
2025-06-27 | 4130.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3228.6987
2025-06-28 | 3774.9319 | 0 | 0.1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3191.1315
2025-06-28 | 3593.9319 | 0 | 0.1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2978.1633
2025-06-28 | 3427.2671 | 0 | 0.9 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3154.1632
2025-06-28 | 3355.3091 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3163.7987
2025-06-28 | 3400.0339 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3236.425
2025-06-28 | 3709.842 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3382.6183
2025-06-28 | 4168.6558 | 0 | 0.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3898.607
2025-06-28 | 4790.6831 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4466.2029
2025-06-28 | 5375.7939 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4531.6252
2025-06-28 | 5692.9058 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4768.3102
2025-06-28 | 6182.085 | 0 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.2089
2025-06-28 | 6806.0708 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.4679
2025-06-28 | 6984.9741 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7317.2603
2025-06-28 | 7057.541 | 0 | 9.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7732.1935
2025-06-28 | 7540.8169 | 0 | 9.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7891.9106
2025-06-28 | 8084.1528 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8682.4314
2025-06-28 | 8419.6123 | 0 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8876.0128
2025-06-28 | 8519.4551 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8732.3297
2025-06-28 | 8134.1958 | 0 | 5.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7569.1982
2025-06-28 | 7580.8901 | 0 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6585.0127
2025-06-28 | 6928.811 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5872.8279
2025-06-28 | 6171.1919 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4933.5401
2025-06-28 | 5382.2432 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4059.6338
2025-06-28 | 4803.0879 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3584.1754
2025-06-29 | 4338.6592 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3165.4182
2025-06-29 | 3999.207 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.4503
2025-06-29 | 3776.3601 | 0.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2911.7426
2025-06-29 | 3692.9189 | 1.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2983.6672
2025-06-29 | 3731.0649 | 1.2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3074.7193
2025-06-29 | 3885.7361 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3382.4804
2025-06-29 | 4244.4648 | 0.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.3268
2025-06-29 | 4981.1318 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4099.0661
2025-06-29 | 5482.2949 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4384.7705
2025-06-29 | 5765.3589 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4694.8829
2025-06-29 | 5882.1538 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4665.5122
2025-06-29 | 5950.0278 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4628.6386
2025-06-29 | 6106.749 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5261.2943
2025-06-29 | 6228.1992 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6006.6506
2025-06-29 | 6558.9678 | 0 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6606.9319
2025-06-29 | 7038.6138 | 0 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7103.7432
2025-06-29 | 7646.8579 | 0 | 7.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7994.8845
2025-06-29 | 7629.457 | 0 | 8.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8401.9065
2025-06-29 | 7372.4092 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8376.8991
2025-06-29 | 6901.9751 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7612.9957
2025-06-29 | 6444.9102 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6643.8152
2025-06-29 | 5781.106 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5337.3905
2025-06-29 | 4989.5591 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4272.6283
2025-06-29 | 4447.4502 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3551.1744
2025-06-30 | 3968.5559 | 0.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2974.9462
2025-06-30 | 3728.2581 | 1.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2838.9802
2025-06-30 | 3562.457 | 2.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2831.2738
2025-06-30 | 3565.032 | 2.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2837.1966
2025-06-30 | 3640.2729 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3049.2521
2025-06-30 | 4040.7129 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3302.0116
2025-06-30 | 4530.3018 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3575.8555
2025-06-30 | 5110.8252 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4187.7284
2025-06-30 | 5667.7061 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5427.9885
2025-06-30 | 6239.1489 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6215.3787
2025-06-30 | 6607.3989 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.568
2025-06-30 | 7009.855 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7177.1175
2025-06-30 | 7321.6431 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7626.2048
2025-06-30 | 7743.79 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.4285
2025-06-30 | 8263.4521 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8200.855
2025-06-30 | 8779.7256 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8807.8074
2025-06-30 | 9381.7822 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9331.812
2025-06-30 | 9325.6787 | 0 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9408.4109
2025-06-30 | 8948.3525 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9236.5487
2025-06-30 | 8654.6406 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8252.3633
2025-06-30 | 8324.0742 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7650.3195
2025-06-30 | 7559.2998 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6821.1727
2025-06-30 | 6769.8481 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6233.6882
2025-06-30 | 5989.373 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5468.2331
2025-07-01 | 5435.1572 | 0 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4417.9179
2025-07-01 | 5066.4751 | 0 | 3.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4094.8087
2025-07-01 | 4818.3188 | 0 | 3.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3903.6718
2025-07-01 | 4690.0322 | 0 | 3.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3876.5936
2025-07-01 | 4781.0669 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3949.2199
2025-07-01 | 4970.5859 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4315.6953
2025-07-01 | 5347.9199 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4905.1113
2025-07-01 | 6102.2988 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5949.985
2025-07-01 | 6908.2178 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6345.8305
2025-07-01 | 7604.4502 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6472.3745
2025-07-01 | 7837.8711 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6993.709
2025-07-01 | 8072.9502 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7213.8311
2025-07-01 | 8135.5542 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7662.9184
2025-07-01 | 8104.2021 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7563.8601
2025-07-01 | 8276.7109 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6438.5984
2025-07-01 | 8668.0225 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8257.1022
2025-07-01 | 9110.2959 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8634.2521
2025-07-01 | 9199.6807 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7609.4406
2025-07-01 | 8953.1641 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8245.2794
2025-07-01 | 8280.0693 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7591.5171
2025-07-01 | 7598.7749 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6255.1997
2025-07-01 | 7044.4019 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6050.1854
2025-07-01 | 6443.272 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4691.7137
2025-07-01 | 5640.332 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4073.1133
2025-07-02 | 5016.981 | 0 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.358
2025-07-02 | 4573.6802 | 0 | 1.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3176.9667
2025-07-02 | 4334.3569 | 0 | 0.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2581.9793
2025-07-02 | 4246.9951 | 0.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2617.1903
2025-07-02 | 4346.7891 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2807.2452
2025-07-02 | 4740.853 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3137.0069
2025-07-02 | 5132.8511 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3656.8462
2025-07-02 | 5854.9268 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4848.5747
2025-07-02 | 6281.3379 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5464.7022
2025-07-02 | 6593.146 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5884.9556
2025-07-02 | 7156.8481 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6443.0038
2025-07-02 | 7369.7012 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6993.5491
2025-07-02 | 7439.0459 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7259.068
2025-07-02 | 7664.4351 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7453.7191
2025-07-02 | 8011.8711 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7833.7183
2025-07-02 | 8715.9365 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8367.2432
2025-07-02 | 9322.9053 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8303.8289
2025-07-02 | 9193.4404 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8600.7099
2025-07-02 | 8676.668 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7400.8648
2025-07-02 | 8173.2642 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7885.2265
2025-07-02 | 7620.978 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7466.7511
2025-07-02 | 6724.2778 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6454.0359
2025-07-02 | 5775.6641 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5352.5599
2025-07-02 | 5113.2642 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4219.968
2025-07-03 | 4718.2129 | 0 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3463.3623
2025-07-03 | 4360.21 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3030.112
2025-07-03 | 4145.355 | 0 | 0.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2618.693
2025-07-03 | 4072.751 | 0.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.1893
2025-07-03 | 4181.792 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2686.2418
2025-07-03 | 4546.3789 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3016.0035
2025-07-03 | 4709.4561 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.5641
2025-07-03 | 4900.6348 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3820.5917
2025-07-03 | 5058.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3996.155
2025-07-03 | 5039.0889 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.699
2025-07-03 | 5292.687 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.1831
2025-07-03 | 5727.061 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4790.7283
2025-07-03 | 5877.1528 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5753.8071
2025-07-03 | 6152.4888 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5838.3172
2025-07-03 | 6201.5181 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4199.064
2025-07-03 | 6525.626 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5760.572
2025-07-03 | 7284.4961 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7055.5639
2025-07-03 | 7231.2129 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7389.1585
2025-07-03 | 7128.7939 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6886.8733
2025-07-03 | 6631.8672 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6233.1109
2025-07-03 | 6341.4541 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5374.0714
2025-07-03 | 5613.4331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4361.3562
2025-07-03 | 4785.7949 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3858.1615
2025-07-03 | 4154.7842 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3580.7087
2025-07-04 | 3727.415 | 3.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3282.955
2025-07-04 | 3453.927 | 5.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3267.9924
2025-07-04 | 3319.7681 | 6.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3282.2867
2025-07-04 | 3327.2471 | 6.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.2081
2025-07-04 | 3450.9519 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3423.2627
2025-07-04 | 3761.177 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3643.0213
2025-07-04 | 4126.48 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3850.8633
2025-07-04 | 4660.3281 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-07-04 | 4770.6499 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4161.1597
2025-07-04 | 4812.353 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4082.2726
2025-07-04 | 4950.623 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4460.4652
2025-07-04 | 5123.3252 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.1557
2025-07-04 | 5161.356 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5276.5293
2025-07-04 | 5356.4751 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5728.1762
2025-07-04 | 5624.9912 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6034.748
2025-07-04 | 6376.5059 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6715.1277
2025-07-04 | 7067.2778 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7165.7049
2025-07-04 | 7148.479 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7462.5859
2025-07-04 | 6970.8481 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7217.2964
2025-07-04 | 6634.9302 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6563.534
2025-07-04 | 6352.6841 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5667.7808
2025-07-04 | 5713.625 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4948.775
2025-07-04 | 4969.293 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3836.1609
2025-07-04 | 4412.4438 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3437.7047
2025-07-05 | 3924.437 | 2.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3385.4244
2025-07-05 | 3700.521 | 2.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.4584
2025-07-05 | 3465.4971 | 3.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3241.752
2025-07-05 | 3389.498 | 3.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.6738
2025-07-05 | 3443.8889 | 3.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3371.7278
2025-07-05 | 3742.261 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.4905
2025-07-05 | 4243.9761 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3931.3321
2025-07-05 | 4792.0171 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4106.3537
2025-07-05 | 5357.397 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5045.6167
2025-07-05 | 5930.3721 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6053.289
2025-07-05 | 6421.1021 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6758.1919
2025-07-05 | 6671.417 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6647.891
2025-07-05 | 6505.1641 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6656.4141
2025-07-05 | 6574.564 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7401.7704
2025-07-05 | 7042.2549 | 0 | 9.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7781.7696
2025-07-05 | 7630.3892 | 0 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.7219
2025-07-05 | 8087.0981 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9096.2949
2025-07-05 | 8263.3975 | 0 | 10.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9136.1801
2025-07-05 | 7900.752 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8670.6086
2025-07-05 | 7429.7549 | 0 | 8.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8420.6967
2025-07-05 | 7154.355 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7598.3708
2025-07-05 | 6745.126 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6879.365
2025-07-05 | 5936.4868 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6181.7396
2025-07-05 | 5399.3291 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5746.7076
2025-07-06 | 4929.3472 | 0 | 5.6 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5210.3839
2025-07-06 | 4605.3232 | 0 | 5.2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4850.561
2025-07-06 | 4445.9751 | 0 | 4.7 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4549.283
2025-07-06 | 4366.9131 | 0 | 4.8 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4558.9185
2025-07-06 | 4393.6758 | 0 | 5.3 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888.5406
2025-07-06 | 4732.8281 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5071.4476
2025-07-06 | 5342.5708 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5660.8636
2025-07-06 | 6168.7939 | 0 | 6.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6448.7416
2025-07-06 | 7097.8848 | 0 | 7.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7101.5828
2025-07-06 | 7764.458 | 0 | 9.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7668.6909
2025-07-06 | 8360.5957 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8226.7391
2025-07-06 | 9028.0391 | 0 | 13.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9291.2759
2025-07-06 | 9376.4502 | 0 | 14.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9556.7948
2025-07-06 | 9673.0439 | 0 | 12.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760.1766
2025-07-06 | 10008.7363 | 0 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6717.0729
2025-07-06 | 10408.2197 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7727.8757
2025-07-06 | 10873.5039 | 0 | 10.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9169.7223
2025-07-06 | 10853.5586 | 0 | 11.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9686.8853
2025-07-06 | 10485.7168 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8670.6086
2025-07-06 | 9894.2139 | 0 | 8.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8383.983
2025-07-06 | 9379.1973 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7818.6529
2025-07-06 | 8489.1084 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6879.365
2025-07-06 | 7411.0571 | 0 | 5.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5961.4575
2025-07-06 | 6529.5718 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5306.1434
2025-07-07 | 5862.373 | 0 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.059
2025-07-07 | 5474.396 | 0 | 3.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3911.2403
2025-07-07 | 5147.7349 | 0 | 3.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3683.3897
2025-07-07 | 4964.188 | 0 | 2.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472.7431
2025-07-07 | 5031.3579 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692.2241
2025-07-07 | 5488.7788 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4021.9859
2025-07-07 | 6175.792 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4611.4019
2025-07-07 | 6871.3672 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5178.9978
2025-07-07 | 6951.8579 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5317.8475
2025-07-07 | 7197.4561 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5444.3914
2025-07-07 | 7448.4199 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4754.1746
2025-07-07 | 7702.665 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4754.0146
2025-07-07 | 7465.7642 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4542.2557
2025-07-07 | 7697.0039 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4479.9111
2025-07-07 | 7756.7651 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4419.3461
2025-07-07 | 8067.5259 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4622.448
2025-07-07 | 8768.1318 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5219.8799
2025-07-07 | 8290.8154 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5516.7609
2025-07-07 | 7805.6841 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5601.8945
2025-07-07 | 7320.395 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5351.9826
2025-07-07 | 6841.1938 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5080.362
2025-07-07 | 5989.2939 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4434.7835
2025-07-07 | 5229.4639 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3810.5854
2025-07-07 | 4673.1138 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3265.4124
2025-07-08 | 4253.4019 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2875.9434
2025-07-08 | 4036.8669 | 0.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2684.9758
2025-07-08 | 3927.4519 | 0.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2644.2685
2025-07-08 | 3872.824 | 1.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2661.1915
2025-07-08 | 4058.686 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2818.2455
2025-07-08 | 4316.7222 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3115.0063
2025-07-08 | 4537.3901 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465.8523
2025-07-08 | 4785.3179 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3794.8783
2025-07-08 | 4943.1982 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4583.5739
2025-07-08 | 5180.5562 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5187.3957
2025-07-08 | 5410.1421 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5818.8713
2025-07-08 | 5716.9849 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6149.1344
2025-07-08 | 5788.127 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6231.085
2025-07-08 | 5934.5479 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6389.0224
2025-07-08 | 6007.8462 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6512.0258
2025-07-08 | 6588.4238 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6715.1277
2025-07-08 | 7288.3032 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7239.1323
2025-07-08 | 7196.396 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7022.0217
2025-07-08 | 7111.4019 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7364.1511
2025-07-08 | 6970.4639 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6600.2477
2025-07-08 | 6798.3589 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5998.2039
2025-07-08 | 6124.2158 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5242.4845
2025-07-08 | 5342.5151 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4434.718
2025-07-08 | 4686.7832 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3485.6945
2025-07-09 | 4191.166 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2875.9434
2025-07-09 | 3907.1499 | 0.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2695.9761
2025-07-09 | 3768.0701 | 0.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2633.2682
2025-07-09 | 3764.3159 | 1.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2716.1931
2025-07-09 | 3920.188 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2829.2458
2025-07-09 | 4306.0479 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3269.0107
2025-07-09 | 4845.6318 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3498.8533
2025-07-09 | 5338.769 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4297.8695
2025-07-09 | 5814.2461 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5611.5569
2025-07-09 | 6401.1729 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6288.8061
2025-07-09 | 6689.1221 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6406.2901
2025-07-09 | 7187.8032 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7140.4038
2025-07-09 | 7319.7822 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7038.7859
2025-07-09 | 7550.083 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7306.8644
2025-07-09 | 7829.4102 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6805.7352
2025-07-09 | 8565.7559 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7155.6918
2025-07-09 | 9239.0068 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7459.4143
2025-07-09 | 8792.748 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6765.026
2025-07-09 | 8377.417 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5969.0313
2025-07-09 | 7882.0039 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5902.6878
2025-07-09 | 7475.3638 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5557.6398
2025-07-09 | 6637.0112 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4875.3477
2025-07-09 | 5883.1489 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4251.1496
2025-07-09 | 5195.7539 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3669.2629
2025-07-10 | 4666.0288 | 0 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3059.5118
2025-07-10 | 4409.6309 | 0 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2699.6889
2025-07-10 | 4181.4302 | 1.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2677.2694
2025-07-10 | 4088.0491 | 0.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2595.1897
2025-07-10 | 4260.0068 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2818.2455
2025-07-10 | 4617.6138 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3159.0075
2025-07-10 | 5116.4658 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693.5599
2025-07-10 | 5790.8652 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4518.1516
2025-07-10 | 6310.0718 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5464.7022
2025-07-10 | 6747.5928 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5958.3829
2025-07-10 | 7132.6401 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6406.2901
2025-07-10 | 7633.3911 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.408
2025-07-10 | 7852.7681 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6928.6449
2025-07-10 | 8104.1729 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7343.5781
2025-07-10 | 8461.7959 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7209.5857
2025-07-10 | 9166.4219 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7669.6833
2025-07-10 | 9343.5322 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8230.4016
2025-07-10 | 9181.7578 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8600.7099
2025-07-10 | 9084.2227 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8281.9931
2025-07-10 | 8624.9805 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7848.5128
2025-07-10 | 8240.6865 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6842.6186
2025-07-10 | 7342.0391 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5829.9033
2025-07-10 | 6380.6738 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4838.5684
2025-07-10 | 5637.5762 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4073.1133
2025-07-11 | 5142.0669 | 0 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3353.2212
2025-07-11 | 4780.459 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3030.112
2025-07-11 | 4588.168 | 0 | 0.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2618.693
2025-07-11 | 4456.6138 | 0.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2573.189
2025-07-11 | 4588.0991 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2906.248
2025-07-11 | 5012.1519 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3082.0054
2025-07-11 | 5666.8062 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3913.842
2025-07-11 | 6415.2422 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.2883
2025-07-11 | 6876.2271 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5758.4116
2025-07-11 | 7390.4121 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6252.0924
2025-07-11 | 7807.5288 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6810.1406
2025-07-11 | 8252.9033 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7470.8269
2025-07-11 | 8483.7002 | 0 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7883.2005
2025-07-11 | 8859.4209 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7930.9969
2025-07-11 | 9091.584 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8054.0003
2025-07-11 | 9650.3857 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8807.8074
2025-07-11 | 9988.3828 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9368.5256
2025-07-11 | 9761.1934 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9371.6972
2025-07-11 | 9431.3584 | 0 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9309.9761
2025-07-11 | 8946.4229 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8803.0685
2025-07-11 | 8565.0166 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7687.0332
2025-07-11 | 7726.5508 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6160.3265
2025-07-11 | 6836.6011 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5168.9915
2025-07-11 | 6034.1548 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4476.9638
2025-07-12 | 5400.751 | 0 | 3.1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4292.5419
2025-07-12 | 5008.3628 | 0 | 2.5 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3859.2916
2025-07-12 | 4747.1318 | 0 | 2.7 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3815.0094
2025-07-12 | 4607.501 | 0 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530.9355
2025-07-12 | 4595.1738 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3199.7113
2025-07-12 | 4943.665 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3309.191
2025-07-12 | 5783.3618 | 0 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.0259
2025-07-12 | 6852.8418 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5934.75
2025-07-12 | 7777.8472 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6918.0144
2025-07-12 | 8403.7168 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7558.5498
2025-07-12 | 9071.3047 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8226.7391
2025-07-12 | 9444.2129 | 0 | 11.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8520.2886
2025-07-12 | 9624.2617 | 0 | 12.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8932.6622
2025-07-12 | 9986.8906 | 0 | 14.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9347.5954
2025-07-12 | 10271.0059 | 0 | 12.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8846.4663
2025-07-12 | 10373.7676 | 0 | 13.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9747.1281
2025-07-12 | 10518.4756 | 0 | 12.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9757.1411
2025-07-12 | 10634.2451 | 0 | 13.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10274.3042
2025-07-12 | 10490.4189 | 0 | 12.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9882.16
2025-07-12 | 9781.5879 | 0 | 10.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9338.5387
2025-07-12 | 9382.4951 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8406.0718
2025-07-12 | 8633.8555 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7319.9292
2025-07-12 | 7684.769 | 0 | 6.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6402.0216
2025-07-12 | 6978.2949 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5526.4255
2025-07-13 | 6333.7861 | 0 | 5.3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100.2428
2025-07-13 | 5944.2319 | 0 | 5.6 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4997.4157
2025-07-13 | 5652.1899 | 0 | 5.2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4732.8514
2025-07-13 | 5443.6641 | 0 | 4.6 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4485.4911
2025-07-13 | 5503.0322 | 0 | 4.5 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4594.8311
2025-07-13 | 5871.7041 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4961.3065
2025-07-13 | 6765.2358 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5881.1457
2025-07-13 | 7923.75 | 0 | 7.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6779.1647
2025-07-13 | 8896.0049 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7175.0101
2025-07-13 | 9449.5547 | 0 | 9.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7815.5456
2025-07-13 | 9976.9541 | 0 | 11.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8704.0169
2025-07-13 | 10456.4727 | 0 | 12.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8887.4254
2025-07-13 | 10578.0654 | 0 | 12.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8822.5212
2025-07-13 | 10782.5664 | 0 | 13.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9017.1723
2025-07-13 | 10544.0322 | 0 | 11.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8369.1884
2025-07-13 | 10399.2148 | 0 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6075.7602
2025-07-13 | 10701.999 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7260.6109
2025-07-13 | 10834.6934 | 0 | 6.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7924.6287
2025-07-13 | 10399.5762 | 0 | 8.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8487.0402
2025-07-13 | 9864.0908 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8053.5599
2025-07-13 | 9255.8701 | 0 | 5.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7304.6614
2025-07-13 | 8320.8584 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7283.2155
2025-07-13 | 7284.666 | 0 | 5.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6145.0259
2025-07-13 | 6533.7998 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5746.7076
2025-07-14 | 5960.0879 | 0 | 5.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4858.4821
2025-07-14 | 5609.334 | 0 | 4.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4425.2318
2025-07-14 | 5427.5488 | 0 | 3.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3903.6718
2025-07-14 | 5348.7012 | 0 | 2.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3472.7431
2025-07-14 | 5444.6362 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3398.5147
2025-07-14 | 5825.2412 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.567
2025-07-14 | 6258.8789 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3987.2693
2025-07-14 | 6614.7998 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4701.7199
2025-07-14 | 6759.8208 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5097.5654
2025-07-14 | 6988.146 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5591.2462
2025-07-14 | 7498.2241 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6222.7217
2025-07-14 | 7937.2241 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6809.9807
2025-07-14 | 8086.8442 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7369.209
2025-07-14 | 8173.2388 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7343.5781
2025-07-14 | 8564.9678 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7356.4404
2025-07-14 | 8927.127 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8367.2432
2025-07-14 | 9592.6426 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8781.1068
2025-07-14 | 9682.7305 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8820.992
2025-07-14 | 9420.3379 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8612.4162
2025-07-14 | 8885.0254 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7995.3675
2025-07-14 | 8324.5459 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6879.3322
2025-07-14 | 7423.7148 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6013.4717
2025-07-14 | 6427.8081 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5168.9915
2025-07-14 | 5680.8149 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4256.6817
2025-07-15 | 5129.9849 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3610.217
2025-07-15 | 4839.1602 | 0 | 1.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.3941
2025-07-15 | 4621.7192 | 0 | 0.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2581.9793
2025-07-15 | 4499.0439 | 0.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2617.1903
2025-07-15 | 4626.1821 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2818.2455
2025-07-15 | 4987.311 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3137.0069
2025-07-15 | 5506.7378 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3620.1325
2025-07-15 | 6119.1431 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4995.4294
2025-07-15 | 6720.1431 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6198.9758
2025-07-15 | 7133.3628 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6435.6608
2025-07-15 | 7542.624 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7103.85
2025-07-15 | 8123.3882 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7764.5363
2025-07-15 | 8429.7539 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8433.9057
2025-07-15 | 8806.1064 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8371.5611
2025-07-15 | 9309.8096 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8861.7013
2025-07-15 | 9809.6387 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9248.3715
2025-07-15 | 9947.7109 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9662.2351
2025-07-15 | 10113.8584 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9702.1203
2025-07-15 | 9934.4639 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9530.2582
2025-07-15 | 9505.4053 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8839.7821
2025-07-15 | 9074.5371 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7613.6058
2025-07-15 | 8283.8691 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6674.318
2025-07-15 | 7163.1328 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5903.2651
2025-07-15 | 6350.4219 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4990.9553
2025-07-16 | 5695.4258 | 0 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4344.4906
2025-07-16 | 5354.4189 | 0 | 3.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3911.2403
2025-07-16 | 5063.6948 | 0 | 2.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3609.9624
2025-07-16 | 4887.979 | 0 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3068.8927
2025-07-16 | 5011.9268 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3325.0874
2025-07-16 | 5463.1021 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3581.4217
2025-07-16 | 6069.019 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4537.9745
2025-07-16 | 6847.6431 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5692.9893
2025-07-16 | 7537.2988 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6859.822
2025-07-16 | 8064.397 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7794.0669
2025-07-16 | 8588.9072 | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8388.8288
2025-07-16 | 9070.208 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8902.6604
2025-07-16 | 9376.5742 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9278.3203
2025-07-16 | 9680.4238 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9436.2578
2025-07-16 | 10040.5479 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9669.4022
2025-07-16 | 10736.4629 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9945.9314
2025-07-16 | 11132.0352 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10029.3719
2025-07-16 | 11100.2822 | 0 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10583.2486
2025-07-16 | 10934.7588 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10117.677
2025-07-16 | 10517.3516 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9574.0557
2025-07-16 | 9972.1572 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8458.0204
2025-07-16 | 9137.1641 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7371.8779
2025-07-16 | 8062.5132 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6564.1114
2025-07-16 | 7259.3882 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5615.0879
2025-07-17 | 6688.7939 | 0 | 5.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4821.7684
2025-07-17 | 6191.186 | 0 | 4.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4425.2318
2025-07-17 | 5949.8721 | 0 | 3.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.3855
2025-07-17 | 5743.8452 | 0 | 3.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3766.4526
2025-07-17 | 5851.1479 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4242.9293
2025-07-17 | 6087.0752 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4499.2637
2025-07-17 | 6487.6479 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5162.1071
2025-07-17 | 6900.2671 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5582.8482
2025-07-17 | 7357.834 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6272.4031
2025-07-17 | 7911.2329 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6912.9386
2025-07-17 | 8252.4746 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7177.2774
2025-07-17 | 8518.0371 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7654.3953
2025-07-17 | 8835.6953 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6708.3628
2025-07-17 | 8714.8887 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7196.7233
2025-07-17 | 8666.3779 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6732.3079
2025-07-17 | 8591.7158 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7375.9739
2025-07-17 | 9340.752 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6982.1365
2025-07-17 | 8843.2959 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6471.3165
2025-07-17 | 8208.9365 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6262.7407
2025-07-17 | 7610.8008 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5792.5468
2025-07-17 | 7015.9351 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5153.7893
2025-07-17 | 6147.2051 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4548.3615
2025-07-17 | 5310.417 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3946.164
2025-07-17 | 4684.8252 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3448.705
2025-07-18 | 4245.8892 | 2.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3183.9522
2025-07-18 | 3954.144 | 2.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2981.9843
2025-07-18 | 3777.9541 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2985.2782
2025-07-18 | 3667.699 | 5.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3090.2038
2025-07-18 | 3799.2109 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401.2621
2025-07-18 | 4090.4041 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3808.026
2025-07-18 | 4424.668 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4004.8677
2025-07-18 | 4859.8389 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4157.8886
2025-07-18 | 5062.6909 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4172.16
2025-07-18 | 5237.5181 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.1263
2025-07-18 | 5313.4561 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644.0335
2025-07-18 | 5483.4092 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5414.8609
2025-07-18 | 5606.5229 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5643.6661
2025-07-18 | 5793.6641 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5985.1719
2025-07-18 | 6086.5752 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6291.7437
2025-07-18 | 6630.3369 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6935.4098
2025-07-18 | 7223.6641 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7716.4101
2025-07-18 | 7264.4131 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7719.5816
2025-07-18 | 6980.918 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7547.7195
2025-07-18 | 6576.5181 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6747.1024
2025-07-18 | 6206.5581 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5777.9219
2025-07-18 | 5681.8179 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4691.7793
2025-07-18 | 4973.9858 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3748.1584
2025-07-18 | 4449.9248 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3371.7028
2025-07-19 | 4045.1411 | 1.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3363.4238
2025-07-19 | 3781.6421 | 3.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3326.4606
2025-07-19 | 3584.084 | 3.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3186.7504
2025-07-19 | 3510.01 | 3.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3225.6741
2025-07-19 | 3564.5481 | 4.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3459.7303
2025-07-19 | 3833.0271 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3822.493
2025-07-19 | 4264.7212 | 2.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3975.3334
2025-07-19 | 5037.2148 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4106.3537
2025-07-19 | 5662.7012 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4641.7663
2025-07-19 | 5836.5229 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5612.7248
2025-07-19 | 5972.6382 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6207.4868
2025-07-19 | 6092.8008 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6758.032
2025-07-19 | 6224.4951 | 0 | 7.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6839.9825
2025-07-19 | 6473.188 | 0 | 7.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6997.92
2025-07-19 | 6626.2681 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7341.2054
2025-07-19 | 7088.7012 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7581.021
2025-07-19 | 7460.437 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8288.594
2025-07-19 | 7189.4658 | 0 | 7.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8291.7655
2025-07-19 | 6822.166 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7459.0572
2025-07-19 | 6581.6138 | 0 | 4.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6915.4358
2025-07-19 | 6319.249 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6203.251
2025-07-19 | 5822.7192 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5410.8179
2025-07-19 | 5201.6528 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4970.1882
2025-07-19 | 4744.4321 | 0 | 0.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3727.4552
2025-07-20 | 4340.6318 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3154.4178
2025-07-20 | 4043.458 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3051.4528
2025-07-20 | 3827.1299 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2933.7432
2025-07-20 | 3695.947 | 2.1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3027.6685
2025-07-20 | 3713.9851 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3140.7212
2025-07-20 | 3894.0259 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481.4832
2025-07-20 | 4327.415 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3843.3296
2025-07-20 | 4842.0259 | 1.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4194.3562
2025-07-20 | 5251.8501 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4351.6317
2025-07-20 | 5490.6558 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.7461
2025-07-20 | 5746.4312 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5179.5037
2025-07-20 | 6034.0332 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5473.0532
2025-07-20 | 6247.2349 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5922.1405
2025-07-20 | 6463.7681 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6483.9284
2025-07-20 | 6791.9331 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6937.355
2025-07-20 | 7447.4082 | 0 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6993.6021
2025-07-20 | 8056.981 | 0 | 6.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7480.893
2025-07-20 | 8067.2021 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7630.9193
2025-07-20 | 7726.0361 | 0 | 5.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7532.4845
2025-07-20 | 7164.3799 | 0 | 4.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7025.5769
2025-07-20 | 6643.6431 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5175.268
2025-07-20 | 5865.5898 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4896.8264
2025-07-20 | 5057.2661 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4026.6328
2025-07-20 | 4488.0439 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3606.176
2025-07-21 | 4111.8979 | 1.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3029.9478
2025-07-21 | 3805.5569 | 2.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2915.9824
2025-07-21 | 3624.916 | 3.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2930.2766
2025-07-21 | 3563.6011 | 4.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2991.2009
2025-07-21 | 3643.312 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.2565
2025-07-21 | 3934.491 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3577.0195
2025-07-21 | 4289.1011 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3850.8633
2025-07-21 | 4612.4302 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4102.8871
2025-07-21 | 4810.0708 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4172.16
2025-07-21 | 4914.6221 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4192.2757
2025-07-21 | 5020.2461 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.042
2025-07-21 | 5111.3198 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4570.4462
2025-07-21 | 5113.2041 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4578.9694
2025-07-21 | 5142.9468 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4736.9068
2025-07-21 | 5472.7539 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4639.6282
2025-07-21 | 6128.5342 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5466.8626
2025-07-21 | 6731.606 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5770.5851
2025-07-21 | 6703.5498 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5737.043
2025-07-21 | 6403.8052 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5712.0355
2025-07-21 | 5993.9531 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5205.1279
2025-07-21 | 5676.605 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5072.7986
2025-07-21 | 4939.7119 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4691.3656
2025-07-21 | 4333.2661 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4100.1684
2025-07-21 | 3840.3511 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3811.7153
2025-07-22 | 3513.3831 | 6.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3579.9635
2025-07-22 | 3321.6011 | 6.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3421.9968
2025-07-22 | 3225.947 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3315.2876
2025-07-22 | 3196.646 | 6.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3233.2078
2025-07-22 | 3327.3401 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.2668
2025-07-22 | 3653.959 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3698.0229
2025-07-22 | 3917.0859 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3916.8652
2025-07-22 | 4167.0918 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4058.8858
2025-07-22 | 4271.2202 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.1563
2025-07-22 | 4422.2778 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4489.8358
2025-07-22 | 4592.2412 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4533.8925
2025-07-22 | 4768.377 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4607.1599
2025-07-22 | 4726.147 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4835.9652
2025-07-22 | 4922.7642 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4957.1889
2025-07-22 | 5234.9438 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5557.4701
2025-07-22 | 5834.9219 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6017.5678
2025-07-22 | 6657.002 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6798.5681
2025-07-22 | 6657.5439 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6765.026
2025-07-22 | 6553.5391 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6666.5912
2025-07-22 | 6178.5508 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5865.9741
2025-07-22 | 5960.21 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4951.7951
2025-07-22 | 5284.4971 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4493.3599
2025-07-22 | 4511.5498 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3858.1615
2025-07-22 | 3949.1941 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3580.7087
2025-07-23 | 3646.592 | 3.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.9531
2025-07-23 | 3447.116 | 2.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2981.9843
2025-07-23 | 3312.4661 | 4.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3029.2794
2025-07-23 | 3274.333 | 5.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3123.2047
2025-07-23 | 3433.958 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3291.259
2025-07-23 | 3752.1111 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.0238
2025-07-23 | 4096.104 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3817.8624
2025-07-23 | 4434.9468 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3926.882
2025-07-23 | 4679.8281 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4693.7149
2025-07-23 | 4888.4438 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5517.8188
2025-07-23 | 5114.208 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6222.7217
2025-07-23 | 5408.5991 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6479.5576
2025-07-23 | 5738.3232 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6634.9354
2025-07-23 | 5999.749 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6976.4413
2025-07-23 | 6471.7612 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7136.1583
2025-07-23 | 7187.4482 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7669.6833
2025-07-23 | 8136.5332 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8634.2521
2025-07-23 | 8158.9209 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8784.2783
2025-07-23 | 7927.981 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8428.8478
2025-07-23 | 7518.8008 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7738.3718
2025-07-23 | 7048.314 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6585.6228
2025-07-23 | 6232.3042 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5499.4802
2025-07-23 | 5382.6968 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4398.0043
2025-07-23 | 4788.3872 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3375.5534
2025-07-24 | 4402.4609 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2875.9434
2025-07-24 | 4085.4561 | 1.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2783.9787
2025-07-24 | 3926.093 | 0.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600.2672
2025-07-24 | 3921.897 | 1.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2705.1928
2025-07-24 | 4093.322 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3016.2512
2025-07-24 | 4518.624 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.0119
2025-07-24 | 5151.8911 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3620.1325
2025-07-24 | 5941.521 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5252.4251
2025-07-24 | 6593.1572 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6198.9758
2025-07-24 | 7184.8989 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7426.9301
2025-07-24 | 7625.4268 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8168.5467
2025-07-24 | 8135.626 | 0 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8241.8142
2025-07-24 | 8361.749 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8727.6151
2025-07-24 | 8680.9141 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9142.5483
2025-07-24 | 9087.4971 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9522.5475
2025-07-24 | 9690.4512 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9982.6451
2025-07-24 | 10404.2832 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10543.3634
2025-07-24 | 10555.123 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10399.6802
2025-07-24 | 10275.7188 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10007.536
2025-07-24 | 9853.4131 | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9463.9147
2025-07-24 | 9450.8203 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6916.0459
2025-07-24 | 8609.0449 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5976.7581
2025-07-24 | 7420.8921 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5168.9915
2025-07-24 | 6763.665 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4697.2459
2025-07-25 | 6256.8608 | 0 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4381.2042
2025-07-25 | 5889.1328 | 0 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4131.5224
2025-07-25 | 5687.5752 | 0 | 3.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3903.6718
2025-07-25 | 5543.9492 | 0 | 3.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3803.1662
2025-07-25 | 5536.4692 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4059.3609
2025-07-25 | 5714.2471 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4205.5543
2025-07-25 | 5954.2891 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4794.9703
2025-07-25 | 6277.3872 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5362.5662
2025-07-25 | 6489.189 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6052.1211
2025-07-25 | 7121.7578 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6509.0881
2025-07-25 | 7704.2041 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6516.4312
2025-07-25 | 8101.3662 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6809.9807
2025-07-25 | 8167.6108 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7516.0637
2025-07-25 | 8539.1699 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7527.1465
2025-07-25 | 9083.7852 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7870.4319
2025-07-25 | 9516.5791 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8440.6706
2025-07-25 | 9868.4541 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8891.2478
2025-07-25 | 9728.7988 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8784.2783
2025-07-25 | 9334.957 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8538.9888
2025-07-25 | 8695.8223 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7811.7991
2025-07-25 | 8159.3091 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7099.6143
2025-07-25 | 7283.0122 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5756.476
2025-07-25 | 6342.584 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4655
2025-07-25 | 5572.0239 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3852.8313
2025-07-26 | 4986.1001 | 0 | 0.3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3264.5589
2025-07-26 | 4621.1152 | 0 | 0.6 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3161.7317
2025-07-26 | 4403.0508 | 1.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2955.7439
2025-07-26 | 4246.8101 | 1.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2928.6657
2025-07-26 | 4280.6489 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3052.7187
2025-07-26 | 4481.3608 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3525.4845
2025-07-26 | 5229.1919 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3733.3265
2025-07-26 | 6122.729 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4502.9166
2025-07-26 | 6961.665 | 0 | 4.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5816.604
2025-07-26 | 7574.7148 | 0 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6787.5626
2025-07-26 | 8089.1909 | 0 | 9.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7676.0339
2025-07-26 | 8595.665 | 0 | 9.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7932.8697
2025-07-26 | 8775.7568 | 0 | 10.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8161.675
2025-07-26 | 8982.498 | 0 | 10.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8172.7577
2025-07-26 | 9276.29 | 0 | 11.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8626.1842
2025-07-26 | 9528.1367 | 0 | 11.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8865.9998
2025-07-26 | 9720.1094 | 0 | 11.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9426.718
2025-07-26 | 9424.6416 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9319.7485
2025-07-26 | 8882.8418 | 0 | 9.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8964.318
2025-07-26 | 8503.4219 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8310.5556
2025-07-26 | 8145.856 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7341.3751
2025-07-26 | 7516.998 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6695.7967
2025-07-26 | 6688.4038 | 0 | 3.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5374.0386
2025-07-26 | 6037.9678 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4828.8656
2025-07-27 | 5532.4541 | 0 | 2.4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4035.5461
2025-07-27 | 5306.7881 | 0 | 2.5 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3859.2916
2025-07-27 | 5129.6572 | 0 | 2.5 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.5821
2025-07-27 | 4996.2671 | 0 | 2.1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3567.6492
2025-07-27 | 4980.083 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3823.8439
2025-07-27 | 5178.4268 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.8919
2025-07-27 | 5689.6719 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4779.7353
2025-07-27 | 6607.2871 | 0 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5494.1859
2025-07-27 | 7358.7139 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6293.8818
2025-07-27 | 7802.9971 | 0 | 6.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6860.9899
2025-07-27 | 8354.2373 | 0 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7088.6151
2025-07-27 | 8699.459 | 0 | 7.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7088.4551
2025-07-27 | 9224.8867 | 0 | 9.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7610.9698
2025-07-27 | 9720.2129 | 0 | 10.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7989.1893
2025-07-27 | 9989.0322 | 0 | 12.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8699.6116
2025-07-27 | 10201.5557 | 0 | 12.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9233.1366
2025-07-27 | 10879.9814 | 0 | 12.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9940.7095
2025-07-27 | 10888.0469 | 0 | 12.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10090.7358
2025-07-27 | 10358.5107 | 0 | 12 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9845.4463
2025-07-27 | 9799.2617 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9301.825
2025-07-27 | 9171.8389 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8259.2171
2025-07-27 | 8336.7891 | 0 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6989.5061
2025-07-27 | 7260.2769 | 0 | 4.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5631.0344
2025-07-27 | 6492.9771 | 0 | 4.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5085.8614
2025-07-28 | 5882.2119 | 0 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.059
2025-07-28 | 5461.645 | 0 | 4.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.2361
2025-07-28 | 5138.7388 | 0 | 3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3646.676
2025-07-28 | 5002.834 | 0 | 2.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3289.1747
2025-07-28 | 5091.7021 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3471.9421
2025-07-28 | 5366.7778 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3691.5627
2025-07-28 | 6015.5039 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4574.6882
2025-07-28 | 6726.5669 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5325.8525
2025-07-28 | 7371.5308 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6676.2536
2025-07-28 | 7967.3179 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7316.7891
2025-07-28 | 8338.291 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8095.1194
2025-07-28 | 8877.9014 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8608.9509
2025-07-28 | 9144.2568 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8874.4699
2025-07-28 | 9508.082 | 0 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9069.121
2025-07-28 | 9998.1621 | 0 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9559.2612
2025-07-28 | 10631.6201 | 0 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10202.9272
2025-07-28 | 11025.1221 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10212.9403
2025-07-28 | 10915.9482 | 0 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10619.9623
2025-07-28 | 10433.1328 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9787.2539
2025-07-28 | 9953.0225 | 0 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9390.4873
2025-07-28 | 9498.5566 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8641.5888
2025-07-28 | 8524.916 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7702.301
2025-07-28 | 7555.1279 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6784.3934
2025-07-28 | 6777.4839 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5908.7973
2025-07-29 | 6198.0142 | 0 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5152.1915
2025-07-29 | 5810.249 | 0 | 6.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5086.078
2025-07-29 | 5509.2251 | 0 | 5.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4711.3727
2025-07-29 | 5319.186 | 0 | 4.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023.4483
2025-07-29 | 5355.9722 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4169.502
2025-07-29 | 5691.1309 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.8406
2025-07-29 | 6359.5449 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5051.966
2025-07-29 | 7169.3838 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5803.1303
2025-07-29 | 7610.8428 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6235.6895
2025-07-29 | 8047.083 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6766.0839
2025-07-29 | 8334.668 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7030.4227
2025-07-29 | 8660.0039 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7507.5406
2025-07-29 | 8823.6064 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7442.6364
2025-07-29 | 9050.3057 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7894.2832
2025-07-29 | 9497.1924 | 0 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8237.5687
2025-07-29 | 10017.7324 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8734.38
2025-07-29 | 10412.5908 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8560.8247
2025-07-29 | 10242.2861 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8784.2783
2025-07-29 | 9813.5527 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8538.9888
2025-07-29 | 9461.3164 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7921.9402
2025-07-29 | 8789.0859 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7430.0374
2025-07-29 | 7861.3062 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6233.7538
2025-07-29 | 7006.9712 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5499.4147
2025-07-29 | 6090.3408 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4550.3912
2025-07-30 | 5526.9438 | 0 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3646.9307
2025-07-30 | 5120.6021 | 0 | 1.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3250.3941
2025-07-30 | 4907.3618 | 0 | 1.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2949.1161
2025-07-30 | 4751.8521 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2885.3243
2025-07-30 | 4836.6499 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.66
2025-07-30 | 5108.3848 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3728.2764
2025-07-30 | 5518.374 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840.4146
2025-07-30 | 5853.979 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5032.1431
2025-07-30 | 6442.3262 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5941.98
2025-07-30 | 6936.457 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6729.3702
2025-07-30 | 7485.71 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7287.4184
2025-07-30 | 7995.4072 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7397.3995
2025-07-30 | 8256.5586 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7222.3543
2025-07-30 | 8156.043 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7417.0054
2025-07-30 | 8213.668 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7356.4404
2025-07-30 | 8858.4717 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7596.256
2025-07-30 | 9606.9814 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8083.5469
2025-07-30 | 9155.9893 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.15
2025-07-30 | 8593.2344 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7474.2921
2025-07-30 | 8095.7432 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7114.2392
2025-07-30 | 7720.8931 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6585.6228
2025-07-30 | 6838.2031 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5683.0486
2025-07-30 | 6047.812 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4508.1453
2025-07-30 | 5334.144 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3375.5534
2025-07-31 | 4864.4722 | 0 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3206.3665
2025-07-31 | 4515.2998 | 0 | 0.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2773.1162
2025-07-31 | 4300.8511 | 0.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2578.2666
2025-07-31 | 4155.4932 | 0.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2584.1893
2025-07-31 | 4279.8599 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2763.2439
2025-07-31 | 4496.2349 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3137.0069
2025-07-31 | 4635.6992 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3542.8545
2025-07-31 | 4790.4751 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3904.8814
2025-07-31 | 4818.1992 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4069.5824
2025-07-31 | 4939.0708 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.8315
2025-07-31 | 5277.1851 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5194.7387
2025-07-31 | 5418.3691 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5084.4378
2025-07-31 | 5334.8921 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5717.0935
2025-07-31 | 5238.8442 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5140.7573
2025-07-31 | 5377.9248 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5263.7607
2025-07-31 | 5706.2979 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6237.8499
2025-07-31 | 6188.3052 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6431.4313
2025-07-31 | 6400.665 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6691.5986
2025-07-31 | 6237.7202 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6372.8818
2025-07-31 | 6004.5801 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6196.3972
2025-07-31 | 5787.9502 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5190.503
2025-07-31 | 5163.8882 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4383.3568
2025-07-31 | 4469.0801 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3814.1603
2025-07-31 | 4026.5471 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3481.7059
2025-08-01 | 3724.2019 | 2.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3183.9522
2025-08-01 | 3474.896 | 3.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3058.9865
2025-08-01 | 3337.042 | 4.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3062.2804
2025-08-01 | 3282.1331 | 5.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3123.2047
2025-08-01 | 3435.5381 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3401.2621
2025-08-01 | 3757.7839 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.0226
2025-08-01 | 4095.5171 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3927.8655
2025-08-01 | 4382.1489 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.8874
2025-08-01 | 4597.8521 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4095.1578
2025-08-01 | 4676.7549 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.699
2025-08-01 | 4830.0972 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4533.8925
2025-08-01 | 4973.4561 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.1557
2025-08-01 | 4929.9961 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5092.9609
2025-08-01 | 5042.8472 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5104.0436
2025-08-01 | 5202.3008 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5447.3291
2025-08-01 | 5782.127 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6164.4225
2025-08-01 | 6296.1162 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6431.4313
2025-08-01 | 6272.4868 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6948.5944
2025-08-01 | 6072.7241 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6776.7322
2025-08-01 | 5765.7231 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6086.2562
2025-08-01 | 5474.2778 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5520.9261
2025-08-01 | 4908.1021 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4614.3634
2025-08-01 | 4317.2959 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4331.175
2025-08-01 | 3837.2261 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3844.7163
2025-08-02 | 3548.2661 | 5.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792.436
2025-08-02 | 3413.4709 | 7.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.4735
2025-08-02 | 3225.2219 | 7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3593.762
2025-08-02 | 3152 | 7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.6838
2025-08-02 | 3254.9351 | 7.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3756.7388
2025-08-02 | 3422.5681 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.5017
2025-08-02 | 3918.6331 | 5.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.3434
2025-08-02 | 4557.1001 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4348.3606
2025-08-02 | 5081.6191 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4329.631
2025-08-02 | 5349.2388 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5282.3017
2025-08-02 | 5564.3311 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6060.632
2025-08-02 | 5810.9448 | 0 | 7.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6941.6004
2025-08-02 | 5795.6992 | 0 | 8.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7243.833
2025-08-02 | 6021.0811 | 0 | 8.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7438.4841
2025-08-02 | 6246.6812 | 0 | 9.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7671.6285
2025-08-02 | 6839.1069 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7948.1578
2025-08-02 | 7327.6719 | 0 | 9.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8802.5855
2025-08-02 | 7216.7441 | 0 | 9.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8769.0433
2025-08-02 | 6779.666 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8376.8991
2025-08-02 | 6388.7568 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7282.5726
2025-08-02 | 5932.938 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6496.9605
2025-08-02 | 5391.7612 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5153.8221
2025-08-02 | 4775.582 | 0 | 0.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4235.9146
2025-08-02 | 4289.4028 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3551.1744
2025-08-03 | 3905.772 | 1.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3319.4225
2025-08-03 | 3721.5791 | 1.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3128.455
2025-08-03 | 3566.616 | 2.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3065.747
2025-08-03 | 3489.2241 | 2.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.6704
2025-08-03 | 3549.8899 | 2.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3261.7247
2025-08-03 | 3731.998 | 3.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3635.4876
2025-08-03 | 4173.2202 | 2.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3953.3327
2025-08-03 | 4809.0581 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4172.3555
2025-08-03 | 5391.585 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4568.3389
2025-08-03 | 5874.9341 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5282.3017
2025-08-03 | 6159.9932 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6060.632
2025-08-03 | 6493.0991 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6758.032
2025-08-03 | 6684.7749 | 0 | 8.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7427.4014
2025-08-03 | 6947.2031 | 0 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7915.7619
2025-08-03 | 7241.6899 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8148.9064
2025-08-03 | 7639.9858 | 0 | 10.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8535.5766
2025-08-03 | 7840.2329 | 0 | 10.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9169.7223
2025-08-03 | 7764.5039 | 0 | 9.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9062.7528
2025-08-03 | 7195.9961 | 0 | 8.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8633.8949
2025-08-03 | 6873.1592 | 0 | 6.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7906.7052
2025-08-03 | 6557.0898 | 0 | 4.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6827.3836
2025-08-03 | 5886.5469 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5667.8136
2025-08-03 | 5221.7119 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4492.9103
2025-08-03 | 4665.439 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3562.1747
2025-08-04 | 4248.0249 | 0.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2941.9453
2025-08-04 | 3973.304 | 0.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2717.9768
2025-08-04 | 3772.7119 | 1.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2666.2691
2025-08-04 | 3671.2271 | 2.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2749.194
2025-08-04 | 3682.7061 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2829.2458
2025-08-04 | 3659.8049 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.0057
2025-08-04 | 4306.917 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531.8542
2025-08-04 | 4973.5288 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4444.7242
2025-08-04 | 5659.0752 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5281.1338
2025-08-04 | 6278.8789 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5627.9598
2025-08-04 | 6854.8389 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5818.8713
2025-08-04 | 7380.229 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.5661
2025-08-04 | 7653.5049 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5753.8071
2025-08-04 | 7828.3379 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6278.8814
2025-08-04 | 8308.4766 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6585.4532
2025-08-04 | 8712.8887 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6972.1234
2025-08-04 | 9008.9062 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7496.128
2025-08-04 | 8800.5762 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7279.0175
2025-08-04 | 8312.4834 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6850.1596
2025-08-04 | 7775.729 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6306.5383
2025-08-04 | 7117.9248 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5851.3492
2025-08-04 | 6205.6709 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4912.0614
2025-08-04 | 5321.936 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3810.5854
2025-08-04 | 4691.5151 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3261.6997
2025-08-05 | 4199.335 | 0.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2952.9456
2025-08-05 | 3890.0271 | 2.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2893.9818
2025-08-05 | 3742.4729 | 2.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2853.2744
2025-08-05 | 3669.897 | 3.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2903.1984
2025-08-05 | 3778.4109 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3016.2512
2025-08-05 | 4008.7351 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3390.0141
2025-08-05 | 4329.7871 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3751.8605
2025-08-05 | 4644.104 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4014.8846
2025-08-05 | 4780.6992 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4040.1563
2025-08-05 | 4963.5469 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4893.6863
2025-08-05 | 5327.7969 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5268.1661
2025-08-05 | 5629.4819 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.425
2025-08-05 | 5823.3882 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5974.0892
2025-08-05 | 6176.7622 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6168.7403
2025-08-05 | 6464.604 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6401.8848
2025-08-05 | 7172.0991 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6715.1277
2025-08-05 | 7773.0132 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7275.8459
2025-08-05 | 7572.5308 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7499.2996
2025-08-05 | 7290.8091 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7290.7237
2025-08-05 | 6932.9702 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6416.6793
2025-08-05 | 6522.0859 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5704.4945
2025-08-05 | 5792.7241 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4581.6383
2025-08-05 | 4991.7471 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3792.1596
2025-08-05 | 4417.187 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3272.7
2025-08-06 | 3978.207 | 1.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3018.9475
2025-08-06 | 3748.9351 | 2.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2981.9843
2025-08-06 | 3601.2229 | 3.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2952.2773
2025-08-06 | 3568.8379 | 4.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2991.2009
2025-08-06 | 3666.751 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3181.2559
2025-08-06 | 3916 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511.0176
2025-08-06 | 4197.5581 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3740.8602
2025-08-06 | 4605.7861 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3849.8799
2025-08-06 | 4922.9722 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4583.5739
2025-08-06 | 5331.6958 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5481.1051
2025-08-06 | 5598.502 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6186.0081
2025-08-06 | 6042.6558 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6663.126
2025-08-06 | 6231.6768 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7112.2133
2025-08-06 | 6658.2002 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7233.437
2025-08-06 | 7160.439 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7613.4362
2025-08-06 | 7892.6899 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7889.9654
2025-08-06 | 8511.9229 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8524.111
2025-08-06 | 8402.9971 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8674.1373
2025-08-06 | 8105.4038 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8098.4247
2025-08-06 | 7707.0732 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7150.9529
2025-08-06 | 7130.876 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6071.6313
2025-08-06 | 6227.998 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5095.6298
2025-08-06 | 5388.4121 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4544.859
2025-08-06 | 4746.9839 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4073.1133
2025-08-07 | 4262.0659 | 0 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3206.3665
2025-08-07 | 4042.7429 | 0 | 0.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2736.4026
2025-08-07 | 3815.2759 | 2.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2776.2722
2025-08-07 | 3770.925 | 3.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2881.1978
2025-08-07 | 3960.7451 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3027.2515
2025-08-07 | 4210.7212 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3423.0151
2025-08-07 | 4520.8608 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3641.8574
2025-08-07 | 5015.4258 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3857.3053
2025-08-07 | 5486.4331 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4730.4286
2025-08-07 | 5974.126 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5554.5325
2025-08-07 | 6486.7178 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6369.5765
2025-08-07 | 7114.4072 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7397.3995
2025-08-07 | 7504.3921 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7626.2048
2025-08-07 | 7855.3721 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.4285
2025-08-07 | 8405.2754 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.8593
2025-08-07 | 9041.9844 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8440.6706
2025-08-07 | 9461.2031 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9148.2436
2025-08-07 | 9347.71 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8417.1415
2025-08-07 | 8839.5332 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8098.4247
2025-08-07 | 8417.1816 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7554.8034
2025-08-07 | 7826.0352 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6548.9091
2025-08-07 | 7022.4482 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5976.7581
2025-08-07 | 6092.855 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4911.9958
2025-08-07 | 5308.561 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3375.5534
2025-08-08 | 4835.0571 | 0 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.358
2025-08-08 | 4515.1338 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2772.9783
2025-08-08 | 4328.5781 | 0.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600.2672
2025-08-08 | 4223.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2518.1875
2025-08-08 | 4302.9458 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2906.248
2025-08-08 | 4629.7441 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3390.0141
2025-08-08 | 4987.896 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3509.8536
2025-08-08 | 5411.0029 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4077.5874
2025-08-08 | 5875.5322 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4950.7107
2025-08-08 | 6612.9092 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6105.2377
2025-08-08 | 7212.1191 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7103.85
2025-08-08 | 7789.1191 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7727.8226
2025-08-08 | 8105.5371 | 0 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8103.4826
2025-08-08 | 8443.0967 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8518.4158
2025-08-08 | 8843.0029 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8824.9876
2025-08-08 | 9245.6738 | 0 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9028.0895
2025-08-08 | 9678.0107 | 0 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9441.953
2025-08-08 | 9368.3994 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9445.1246
2025-08-08 | 8970.624 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8869.4119
2025-08-08 | 8542.6309 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8105.5086
2025-08-08 | 8092.4189 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6952.7596
2025-08-08 | 7208.5942 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6050.1854
2025-08-08 | 6376.729 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5168.9915
2025-08-08 | 5731.062 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4587.1048
2025-08-09 | 5217.5649 | 0 | 1.2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3594.982
2025-08-09 | 4867.0542 | 0 | 1.3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3418.7275
2025-08-09 | 4597.6572 | 0 | 1.6 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3411.159
2025-08-09 | 4434.082 | 0 | 1.4 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.6534
2025-08-09 | 4406.5488 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3383.2797
2025-08-09 | 4625.623 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3602.9004
2025-08-09 | 5298.0049 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4339.1711
2025-08-09 | 6189.6982 | 0 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5457.4722
2025-08-09 | 7029.084 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6440.7365
2025-08-09 | 7903.5601 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7411.6951
2025-08-09 | 8521.4746 | 0 | 11.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8557.1622
2025-08-09 | 8972.0645 | 0 | 12.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8850.7117
2025-08-09 | 9219.373 | 0 | 13.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9116.2306
2025-08-09 | 9556.3477 | 0 | 14.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9421.0228
2025-08-09 | 9787.9463 | 0 | 15.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9801.0219
2025-08-09 | 10182.3076 | 0 | 14.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9893.9828
2025-08-09 | 10431.0693 | 0 | 14.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10564.8421
2025-08-09 | 10261.2627 | 0 | 14.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10751.582
2025-08-09 | 9621.4561 | 0 | 12.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10065.7284
2025-08-09 | 9013.8184 | 0 | 10.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9265.1113
2025-08-09 | 8549.8975 | 0 | 8.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8332.6444
2025-08-09 | 7776.8379 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7576.9249
2025-08-09 | 6929.0308 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6695.7311
2025-08-09 | 6282.9702 | 0 | 6.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5893.5623
2025-08-10 | 5666.8472 | 0 | 6.3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5467.3796
2025-08-10 | 5275.7432 | 0 | 5.9 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5107.5567
2025-08-10 | 5073.7832 | 0 | 5 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4659.4241
2025-08-10 | 4872.3691 | 0 | 3.7 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4155.068
2025-08-10 | 4819.4878 | 0 | 1.7 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.8481
2025-08-10 | 4933.2002 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786.4688
2025-08-10 | 5481.394 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.7395
2025-08-10 | 6531.3052 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5934.75
2025-08-10 | 7611.29 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6918.0144
2025-08-10 | 8485.5488 | 0 | 9.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7778.8319
2025-08-10 | 9070.0176 | 0 | 12.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8814.158
2025-08-10 | 9635.3535 | 0 | 13.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9291.2759
2025-08-10 | 10164.4746 | 0 | 15.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9813.7905
2025-08-10 | 10545.2236 | 0 | 15.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9971.728
2025-08-10 | 10967.5527 | 0 | 16.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10241.5861
2025-08-10 | 11355.9824 | 0 | 16.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10591.5427
2025-08-10 | 11630.3486 | 0 | 15.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11042.1199
2025-08-10 | 11335.4248 | 0 | 14.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10861.723
2025-08-10 | 10705.6562 | 0 | 13.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10396.1515
2025-08-10 | 10139.8008 | 0 | 11.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9668.9618
2025-08-10 | 9491.3271 | 0 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8846.6359
2025-08-10 | 8432.7637 | 0 | 8.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7760.4933
2025-08-10 | 7388.0762 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6695.7311
2025-08-10 | 6519.1592 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5820.1349
2025-08-11 | 5921.0352 | 0 | 5.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4858.4821
2025-08-11 | 5446.772 | 0 | 4.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.2361
2025-08-11 | 5190.9961 | 0 | 3.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3903.6718
2025-08-11 | 5063.7808 | 0 | 3.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693.0252
2025-08-11 | 5040.0928 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3435.2284
2025-08-11 | 5307.3989 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.426
2025-08-11 | 5785.3052 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023.983
2025-08-11 | 6488.3271 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5472.7072
2025-08-11 | 7176.041 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6749.681
2025-08-11 | 7719.4702 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7463.6438
2025-08-11 | 8293.7734 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8425.5425
2025-08-11 | 8931.8633 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8976.0877
2025-08-11 | 9287.248 | 0 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9241.6067
2025-08-11 | 9790.7607 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9619.8262
2025-08-11 | 10312.4717 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9669.4022
2025-08-11 | 10943.7539 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9909.2178
2025-08-11 | 11556.7744 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10873.7865
2025-08-11 | 11401.6006 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10803.5307
2025-08-11 | 10979.2881 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10264.5318
2025-08-11 | 10341.7666 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9170.2053
2025-08-11 | 9543.9785 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8237.7384
2025-08-11 | 8405.4824 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6821.1727
2025-08-11 | 7274.2119 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5719.6967
2025-08-11 | 6530.1631 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4917.528
2025-08-12 | 5925.0142 | 0 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4417.9179
2025-08-12 | 5501.2349 | 0 | 3.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4094.8087
2025-08-12 | 5195.0039 | 0 | 2.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3499.8213
2025-08-12 | 4997.7739 | 0 | 1.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3215.7474
2025-08-12 | 5037.022 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2730.243
2025-08-12 | 5278.4482 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.1439
2025-08-12 | 5836.0801 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3913.842
2025-08-12 | 6677.5352 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5252.4251
2025-08-12 | 7388.0361 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6455.9715
2025-08-12 | 7983.3779 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7537.0711
2025-08-12 | 8606.3027 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8609.1109
2025-08-12 | 9265.4189 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9306.5108
2025-08-12 | 9665.5967 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9315.034
2025-08-12 | 9979.9229 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9656.5398
2025-08-12 | 10226.083 | 0 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9706.1159
2025-08-12 | 10673.5488 | 0 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10643.4913
2025-08-12 | 11242.2881 | 0 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11020.6412
2025-08-12 | 11213.3604 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10693.3896
2025-08-12 | 10902.1514 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 10301.2454
2025-08-12 | 10384.9902 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 9684.1968
2025-08-12 | 9727.3047 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8384.5931
2025-08-12 | 8791.8516 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7408.5915
2025-08-12 | 7859.8848 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6600.825
2025-08-12 | 7156.7412 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5761.9426
2025-08-13 | 6620.6172 | 0 | 6.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5188.9052
2025-08-13 | 6249.479 | 0 | 6.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4902.5096
2025-08-13 | 5909.7739 | 0 | 5.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4637.9454
2025-08-13 | 5718.7241 | 0 | 5.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4684.2945
2025-08-13 | 5816.3472 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4720.2072
2025-08-13 | 6090.9541 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903.1142
2025-08-13 | 6441.2798 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5565.9575
2025-08-13 | 6656.187 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6170.2671
2025-08-13 | 6541.1768 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5170.9928
2025-08-13 | 6733.6611 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5481.1051
2025-08-13 | 7031.0049 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6075.867
2025-08-13 | 7314.9731 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6295.9892
2025-08-13 | 7502.917 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.7944
2025-08-13 | 7813.4668 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6903.0139
2025-08-13 | 8197.6758 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7613.4362
2025-08-13 | 8894.4531 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7963.3928
2025-08-13 | 9720.8018 | 0 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9074.8162
2025-08-13 | 9730.1826 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9224.8425
2025-08-13 | 9299.0381 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8869.4119
2025-08-13 | 8936.3369 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8215.6496
2025-08-13 | 8489.8486 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7870.6016
2025-08-13 | 7528.73 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7298.4505
2025-08-13 | 6551.1152 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6050.1198
2025-08-13 | 5904.855 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5358.0921
2025-08-14 | 5488.9902 | 0 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.059
2025-08-14 | 5184.8062 | 0 | 3.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3984.6677
2025-08-14 | 4921.873 | 0 | 2.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3609.9624
2025-08-14 | 4750.5752 | 0 | 2.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3325.8884
2025-08-14 | 4762.353 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3251.66
2025-08-14 | 4931.4961 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.426
2025-08-14 | 5278.9868 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3730.2736
2025-08-14 | 5796.6919 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4628.2926
2025-08-14 | 6220.2568 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5317.8475
2025-08-14 | 6608.915 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5884.9556
2025-08-14 | 6976.8389 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6369.5765
2025-08-14 | 7401.6611 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6663.126
2025-08-14 | 7461.4609 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6855.2175
2025-08-14 | 7664.0991 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6976.4413
2025-08-14 | 8047.4429 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6879.1626
2025-08-14 | 8716.7051 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7375.9739
2025-08-14 | 9173.8711 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.9785
2025-08-14 | 8993.6025 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7976.5774
2025-08-14 | 8416.6133 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7584.4332
2025-08-14 | 7842.0498 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6820.5298
2025-08-14 | 7159.8691 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5924.7766
2025-08-14 | 6264.7539 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4985.4887
2025-08-14 | 5349.5269 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3902.1628
2025-08-14 | 4708.1138 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3426.7044
2025-08-15 | 4227.2642 | 1.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3084.9494
2025-08-15 | 3916.083 | 2.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2915.9824
2025-08-15 | 3727.689 | 2.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2842.2741
2025-08-15 | 3622.3821 | 3.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2925.1991
2025-08-15 | 3688.366 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3126.2543
2025-08-15 | 3897.5979 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.0226
2025-08-15 | 4281.4438 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3839.863
2025-08-15 | 4685.5371 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3915.8817
2025-08-15 | 4981.9429 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4289.8645
2025-08-15 | 5317.2788 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4930.3999
2025-08-15 | 5671.1611 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.726
2025-08-15 | 5974.1128 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6149.1344
2025-08-15 | 6227.4551 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.6491
2025-08-15 | 6651.5371 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7013.1549
2025-08-15 | 7160.3662 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7172.872
2025-08-15 | 7758.731 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7889.9654
2025-08-15 | 8347.6172 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8670.9657
2025-08-15 | 8323.2598 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8674.1373
2025-08-15 | 7859.3379 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8355.4204
2025-08-15 | 7346.374 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7187.6666
2025-08-15 | 6911.0181 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5631.0672
2025-08-15 | 6213.8159 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5058.9161
2025-08-15 | 5485.2559 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4324.5769
2025-08-15 | 4890.1748 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3302.1261
2025-08-16 | 4406.29 | 0 | 0.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3337.9862
2025-08-16 | 4071.7781 | 0.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.4503
2025-08-16 | 3866.6211 | 3.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3197.7508
2025-08-16 | 3752.989 | 2.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3060.6694
2025-08-16 | 3777.573 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3360.7275
2025-08-16 | 3987.8269 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3734.4905
2025-08-16 | 4226.9692 | 2.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3986.3337
2025-08-16 | 5343.6309 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4073.3527
2025-08-16 | 6118.8369 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5155.7578
2025-08-16 | 6819.8232 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6640.7079
2025-08-16 | 7363.7251 | 0 | 9.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7786.175
2025-08-16 | 7803.375 | 0 | 10.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8300.0065
2025-08-16 | 8185.1289 | 0 | 12.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8785.8075
2025-08-16 | 8582.1074 | 0 | 13.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9127.3133
2025-08-16 | 9039.8594 | 0 | 13.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9176.8894
2025-08-16 | 9591.082 | 0 | 14.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9857.2691
2025-08-16 | 9840.8408 | 0 | 13.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10124.2779
2025-08-16 | 9642.2188 | 0 | 13.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10421.1589
2025-08-16 | 9031.2148 | 0 | 12.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9992.301
2025-08-16 | 8576.2236 | 0 | 9.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8971.4019
2025-08-16 | 8031.3169 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8112.3623
2025-08-16 | 7230.979 | 0 | 6.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7026.2198
2025-08-16 | 6435.4448 | 0 | 5.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6181.7396
2025-08-16 | 5735.4492 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5379.5708
2025-08-17 | 5223.5952 | 0 | 3.4 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.6829
2025-08-17 | 4923.2412 | 0 | 2.5 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3859.2916
2025-08-17 | 4689.541 | 0 | 2.5 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.5821
2025-08-17 | 4515.5171 | 0 | 2.2 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3604.3628
2025-08-17 | 4495.752 | 0 | 1.7 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.8481
2025-08-17 | 4629.7778 | 0 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3823.1825
2025-08-17 | 5124.9048 | 0 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5073.4447
2025-08-17 | 5813.0488 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4466.2029
2025-08-17 | 6282.1099 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4311.3432
2025-08-17 | 6095.5659 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4338.7464
2025-08-17 | 6039.4219 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.0919
2025-08-17 | 6159.877 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4532.9348
2025-08-17 | 6055.7729 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431.3169
2025-08-17 | 5901.373 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4281.1077
2025-08-17 | 5918.0781 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.8163
2025-08-17 | 6390.3711 | 0 | 4.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6149.1875
2025-08-17 | 6827.8159 | 0 | 4.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6783.3331
2025-08-17 | 6793.0171 | 0 | 4.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6933.3594
2025-08-17 | 6533.8789 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6541.2152
2025-08-17 | 6184.9331 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5887.4528
2025-08-17 | 5588.3369 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5186.2683
2025-08-17 | 4936.1128 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4760.8341
2025-08-17 | 4250.8818 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4257.6394
2025-08-17 | 3819.7451 | 3.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3881.1838
2025-08-18 | 3488.6021 | 4.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3337.9566
2025-08-18 | 3288.636 | 4.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3201.9906
2025-08-18 | 3150.1189 | 5.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3161.2832
2025-08-18 | 3187.936 | 6.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3200.2069
2025-08-18 | 3329.1899 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3511.2653
2025-08-18 | 3531.2109 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3852.0273
2025-08-18 | 3788.6841 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.8712
2025-08-18 | 4050.0259 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4344.894
2025-08-18 | 4146.5732 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4392.1663
2025-08-18 | 4254.7422 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.2763
2025-08-18 | 4493.9678 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.6172
2025-08-18 | 4534.5151 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4460.3052
2025-08-18 | 4399.6328 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4578.9694
2025-08-18 | 4417.2349 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4736.9068
2025-08-18 | 4725.144 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4786.4829
2025-08-18 | 5203.0239 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5393.4352
2025-08-18 | 5841.46 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6211.1492
2025-08-18 | 5646.7129 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6104.1798
2025-08-18 | 5420.145 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5822.1766
2025-08-18 | 5431.271 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5175.7018
2025-08-18 | 5141.311 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5050.798
2025-08-18 | 4477.689 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4845.37
2025-08-18 | 3926.7161 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4210.1715
2025-08-18 | 3562.897 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3734.7131
2025-08-19 | 3294.7371 | 5.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.9594
2025-08-19 | 3170.802 | 3.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.9874
2025-08-19 | 3101.626 | 5.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.2829
2025-08-19 | 3105.292 | 6.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3244.2081
2025-08-19 | 3238.906 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.2596
2025-08-19 | 3541.1731 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.0242
2025-08-19 | 3767.77 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4081.8699
2025-08-19 | 3931.553 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4333.8936
2025-08-19 | 4054.219 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4370.1657
2025-08-19 | 4139.4951 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4170.2751
2025-08-19 | 4396.373 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4570.6062
2025-08-19 | 4523.665 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5194.5788
2025-08-19 | 4473.7461 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5203.102
2025-08-19 | 4493.0142 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250.8983
2025-08-19 | 4666.187 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5153.6197
2025-08-19 | 5221.437 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5209.8668
2025-08-19 | 5722.2852 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5330.0209
2025-08-19 | 5694.1372 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5406.6199
2025-08-19 | 5691.9922 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5198.044
2025-08-19 | 5586.7432 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5241.7037
2025-08-19 | 5200.106 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5083.7989
2025-08-19 | 4681.9321 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4493.3599
2025-08-19 | 4049.073 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3847.1612
2025-08-19 | 3747.1851 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3360.7025
2025-08-20 | 3515.7161 | 1.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3051.9484
2025-08-20 | 3364.5991 | 1.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2860.9808
2025-08-20 | 3277.917 | 1.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2754.2716
2025-08-20 | 3256.188 | 1.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2716.1931
2025-08-20 | 3425.8 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2928.2486
2025-08-20 | 3683.968 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.0088
2025-08-20 | 3980.637 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3630.857
2025-08-20 | 4217.5059 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4091.8867
2025-08-20 | 4248.2861 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4271.1629
2025-08-20 | 4250.8271 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4368.2807
2025-08-20 | 4477.436 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4243.62
2025-08-20 | 4610.1748 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4067.4551
2025-08-20 | 4681.2261 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4835.9652
2025-08-20 | 4817.4648 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5030.6163
2025-08-20 | 5022.8521 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5484.0428
2025-08-20 | 5562.3281 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5980.8541
2025-08-20 | 6236.7148 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7018.8502
2025-08-20 | 6221.7041 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7022.0217
2025-08-20 | 6080.582 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6886.8733
2025-08-20 | 5987.21 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6343.252
2025-08-20 | 5594.2842 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5263.9304
2025-08-20 | 4931.7681 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4515.3606
2025-08-20 | 4301.8252 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3979.165
2025-08-20 | 3825.5291 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3580.7087
2025-08-21 | 3504.0649 | 5.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480.9606
2025-08-21 | 3295.542 | 5.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3278.9928
2025-08-21 | 3192.2859 | 6.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3293.287
2025-08-21 | 3175.158 | 6.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3189.2066
2025-08-21 | 3308.7991 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3346.2606
2025-08-21 | 3594.7371 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3753.0245
2025-08-21 | 3900.9551 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4059.8693
2025-08-21 | 4207.728 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.8877
2025-08-21 | 4455.4741 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4106.2961
2025-08-21 | 4596.9849 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4967.1136
2025-08-21 | 4697.5908 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.585
2025-08-21 | 4907.5498 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6369.4165
2025-08-21 | 5102.8882 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6451.367
2025-08-21 | 5277.6299 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6792.8729
2025-08-21 | 5634.8208 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6842.4489
2025-08-21 | 6299.5869 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7229.1192
2025-08-21 | 6939.125 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7863.2648
2025-08-21 | 6926.397 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8233.5731
2025-08-21 | 6819.8892 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7878.1426
2025-08-21 | 6553.333 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6343.252
2025-08-21 | 6126.915 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5631.0672
2025-08-21 | 5440.8999 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4460.359
2025-08-21 | 4579.376 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3770.159
2025-08-21 | 4043.9131 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3327.7015
2025-08-22 | 3707.7329 | 1.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3062.9487
2025-08-22 | 3508.54 | 2.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2959.9837
2025-08-22 | 3328.8879 | 3.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.2763
2025-08-22 | 3290.4741 | 2.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2771.1947
2025-08-22 | 3414.853 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3247.2577
2025-08-22 | 3722.7 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3588.0198
2025-08-22 | 4155.4048 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3883.8643
2025-08-22 | 4474.751 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3882.8808
2025-08-22 | 4829.4341 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4840.5696
2025-08-22 | 5188.7241 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6215.3787
2025-08-22 | 5472.021 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6626.5722
2025-08-22 | 5861.6602 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7250.5448
2025-08-22 | 6138.9858 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7405.9227
2025-08-22 | 6488.2129 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.4285
2025-08-22 | 6804.0718 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7870.4319
2025-08-22 | 7373.5762 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8183.6748
2025-08-22 | 7841.2788 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9295.0983
2025-08-22 | 7639.6309 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8600.7099
2025-08-22 | 7259.9932 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8355.4204
2025-08-22 | 7076.4878 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7848.5128
2025-08-22 | 6671.3662 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7136.328
2025-08-22 | 5996.2651 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6086.8991
2025-08-22 | 5276.9502 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5389.2736
2025-08-22 | 4716.8638 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4587.1048
2025-08-23 | 4247.9351 | 0 | 2.6 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.9735
2025-08-23 | 4000.6299 | 0 | 1.3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3418.7275
2025-08-23 | 3752.314 | 0 | 0.7 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3080.7359
2025-08-23 | 3682.1169 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2906.665
2025-08-23 | 3631.5249 | 1.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3140.7212
2025-08-23 | 3837.8931 | 2.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3569.4858
2025-08-23 | 4384.2549 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3821.329
2025-08-23 | 5034.2939 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4429.4892
2025-08-23 | 5701.1411 | 0 | 2.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5339.3262
2025-08-23 | 5889.8521 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5576.0112
2025-08-23 | 6400.3979 | 0 | 4.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6023.9184
2025-08-23 | 6827.0952 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7235.3098
2025-08-23 | 7094.644 | 0 | 8.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7280.5467
2025-08-23 | 7408.4932 | 0 | 9.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7805.6209
2025-08-23 | 7507.6738 | 0 | 9.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7671.6285
2025-08-23 | 7743.043 | 0 | 8.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7874.7304
2025-08-23 | 7876.2588 | 0 | 8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8141.7392
2025-08-23 | 7640.8589 | 0 | 7.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8218.3382
2025-08-23 | 7470.3081 | 0 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8009.7623
2025-08-23 | 7112.2261 | 0 | 6.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7723.1368
2025-08-23 | 6617.647 | 0 | 5.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7121.093
2025-08-23 | 6036.021 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6365.3735
2025-08-23 | 5478.5649 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5484.1797
2025-08-23 | 5001.8701 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4645.2972
2025-08-24 | 4636.9868 | 0 | 3.2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4329.2556
2025-08-24 | 4363.374 | 0 | 2.6 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3896.0053
2025-08-24 | 4220.1299 | 0 | 2.9 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3888.4368
2025-08-24 | 4024.5769 | 0 | 2.8 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3824.6449
2025-08-24 | 4019.897 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3823.8439
2025-08-24 | 4136.3501 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3749.7551
2025-08-24 | 4636.7578 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4192.3164
2025-08-24 | 5678.2231 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4539.6302
2025-08-24 | 6427.3271 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5045.6167
2025-08-24 | 6567.3242 | 0 | 4.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5906.4343
2025-08-24 | 6822.0078 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.6278
2025-08-24 | 6865.3579 | 0 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6904.8867
2025-08-24 | 7137.5352 | 0 | 6.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6729.8415
2025-08-24 | 7566.832 | 0 | 9.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7768.9072
2025-08-24 | 7876.0742 | 0 | 9.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7781.7696
2025-08-24 | 8280.54 | 0 | 9.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8131.7262
2025-08-24 | 8559.6406 | 0 | 8.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8325.3076
2025-08-24 | 8193.8105 | 0 | 9.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8842.4707
2025-08-24 | 7770.335 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7642.6255
2025-08-24 | 7365.832 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7245.859
2025-08-24 | 6850.1738 | 0 | 3.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6496.9605
2025-08-24 | 6039.208 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5337.3905
2025-08-24 | 5165.041 | 0 | 0.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4272.6283
2025-08-24 | 4620.6689 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3580.6005
2025-08-25 | 4216.2402 | 0.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.9443
2025-08-25 | 3983.5669 | 1.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2827.9799
2025-08-25 | 3836.6589 | 2.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2820.2735
2025-08-25 | 3796.7859 | 3.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2936.1994
2025-08-25 | 3911.699 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3126.2543
2025-08-25 | 4157.1748 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.0182
2025-08-25 | 4513.895 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3751.8605
2025-08-25 | 4910.6372 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-08-25 | 5176.625 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4216.4371
2025-08-25 | 5371.7368 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5077.2546
2025-08-25 | 5708.8521 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.585
2025-08-25 | 5980.4312 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5818.7113
2025-08-25 | 5929.105 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6341.226
2025-08-25 | 5980.1182 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6242.1677
2025-08-25 | 5945.2598 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6034.748
2025-08-25 | 6352.0342 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6421.4183
2025-08-25 | 6774.459 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6871.9955
2025-08-25 | 6480.9868 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6544.7439
2025-08-25 | 6372.356 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5455.0398
2025-08-25 | 5951.2319 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5388.6963
2025-08-25 | 5601.0801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4896.7936
2025-08-25 | 5003.7998 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4581.3624
2025-08-25 | 4332.8188 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4078.1678
2025-08-25 | 3933.2251 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3514.7069
2025-08-26 | 3569.8601 | 3.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3227.9534
2025-08-26 | 3376.719 | 3.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3036.9859
2025-08-26 | 3292.05 | 3.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2974.2779
2025-08-26 | 3272.032 | 3.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2925.1991
2025-08-26 | 3380.229 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3170.2555
2025-08-26 | 3731.5869 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.0166
2025-08-26 | 3990.804 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3883.8643
2025-08-26 | 4103.5278 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4212.8902
2025-08-26 | 4206.7529 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4304.1638
2025-08-26 | 4249.4502 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4258.2776
2025-08-26 | 4382.2749 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4210.6191
2025-08-26 | 4536.7739 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.1684
2025-08-26 | 4404.5708 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4101.6916
2025-08-26 | 4346.2759 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4333.0564
2025-08-26 | 4538.9619 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.7777
2025-08-26 | 5055.0039 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.4437
2025-08-26 | 5517.1069 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5403.4483
2025-08-26 | 5510.3691 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5773.7566
2025-08-26 | 5528.6069 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5418.3261
2025-08-26 | 5458.7588 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5219.7031
2025-08-26 | 5148.1851 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5226.803
2025-08-26 | 4607.3242 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4592.3628
2025-08-26 | 4007.4309 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4111.1687
2025-08-26 | 3611.6621 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3591.7091
2025-08-27 | 3340.1069 | 5.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502.9613
2025-08-27 | 3200.2561 | 6.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3410.9965
2025-08-27 | 3092.1541 | 8.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3513.2932
2025-08-27 | 3105.749 | 9.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3563.2172
2025-08-27 | 3282.2759 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.2712
2025-08-27 | 3592.3081 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3962.0304
2025-08-27 | 3753.29 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4312.8765
2025-08-27 | 4007.438 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4553.8999
2025-08-27 | 4174.3628 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4557.171
2025-08-27 | 4147.3418 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4357.2804
2025-08-27 | 4265.1182 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.6163
2025-08-27 | 4324.2949 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4497.0189
2025-08-27 | 4312.0508 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4358.6873
2025-08-27 | 4311.8071 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5067.33
2025-08-27 | 4397.064 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5373.9018
2025-08-27 | 4970.1089 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5613.7173
2025-08-27 | 5533.6851 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6101.0082
2025-08-27 | 5500.8862 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6324.4618
2025-08-27 | 5471.5278 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5748.7492
2025-08-27 | 5456.3159 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5252.704
2025-08-27 | 5149.6929 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5424.8086
2025-08-27 | 4633.9199 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4867.3706
2025-08-27 | 3949.7571 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4243.1725
2025-08-27 | 3564.7009 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3822.7156
2025-08-28 | 3283.0581 | 5.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502.9613
2025-08-28 | 3160.6909 | 5.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3234.9915
2025-08-28 | 3049.2981 | 5.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3139.2826
2025-08-28 | 3070.7061 | 5.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3134.205
2025-08-28 | 3205.189 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.2596
2025-08-28 | 3538.04 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.0226
2025-08-28 | 3845.2051 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4037.8686
2025-08-28 | 4044.062 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4311.893
2025-08-28 | 4175.8618 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4392.1663
2025-08-28 | 4276.0142 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4291.2785
2025-08-28 | 4390.1279 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4188.6184
2025-08-28 | 4583.0098 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4313.4505
2025-08-28 | 4592.147 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4395.401
2025-08-28 | 4535.8179 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3947.4938
2025-08-28 | 4602.6538 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.7832
2025-08-28 | 5138.623 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4464.455
2025-08-28 | 5633.5029 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5102.1755
2025-08-28 | 5530.3169 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5589.6366
2025-08-28 | 5508.9092 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5568.342
2025-08-28 | 5397.8862 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5494.7109
2025-08-28 | 5145.666 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5358.8067
2025-08-28 | 4513.7231 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4834.3697
2025-08-28 | 3974.855 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4199.1712
2025-08-28 | 3620.418 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3712.7125
2025-08-29 | 3343.0991 | 4.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3359.9572
2025-08-29 | 3167.0339 | 4.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3190.9902
2025-08-29 | 3072.321 | 5.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3128.2823
2025-08-29 | 3064.709 | 5.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3134.205
2025-08-29 | 3187.7581 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.2599
2025-08-29 | 3557.4109 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3676.0223
2025-08-29 | 3794.8831 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4103.8705
2025-08-29 | 4081.2261 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4355.8943
2025-08-29 | 4225.749 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4535.1704
2025-08-29 | 4347.9468 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4511.2848
2025-08-29 | 4374.771 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4463.6263
2025-08-29 | 4406.7612 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4408.4648
2025-08-29 | 4267.8579 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4218.8444
2025-08-29 | 4307.0508 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3980.4947
2025-08-29 | 4441.416 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4015.4956
2025-08-29 | 4760.2148 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4816.4651
2025-08-29 | 5162.374 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5168.1774
2025-08-29 | 5083.3672 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5380.6307
2025-08-29 | 5011.7261 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5535.341
2025-08-29 | 4983.0122 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5593.7137
2025-08-29 | 4756.6782 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5402.808
2025-08-29 | 4378.0039 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4900.3715
2025-08-29 | 3959.521 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4441.1781
2025-08-29 | 3525.2209 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3932.7188
2025-08-30 | 3238.0471 | 6.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3913.4395
2025-08-30 | 3073.978 | 7.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.4735
2025-08-30 | 2972.6621 | 6.9 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3582.7617
2025-08-30 | 2960.104 | 6.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3555.6835
2025-08-30 | 3033.479 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3778.7394
2025-08-30 | 3269.2461 | 7.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4075.5002
2025-08-30 | 3682.907 | 6.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4426.3462
2025-08-30 | 4339.019 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4744.3718
2025-08-30 | 4680.0142 | 5.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.6467
2025-08-30 | 4895.0181 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4767.7586
2025-08-30 | 4967.459 | 2.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.0966
2025-08-30 | 4967.125 | 2.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4576.9361
2025-08-30 | 4792.418 | 1.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4365.3151
2025-08-30 | 4646.2969 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.9679
2025-08-30 | 4699.7109 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4918.1026
2025-08-30 | 4914.6162 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5341.4866
2025-08-30 | 5150.6152 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5902.2048
2025-08-30 | 5038.2642 | 0 | 0.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5574.9533
2025-08-30 | 4922.5122 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5843.6553
2025-08-30 | 4839.3369 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5553.1791
2025-08-30 | 4571.1499 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5802.2859
2025-08-30 | 4303.5708 | 4.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5090.8435
2025-08-30 | 3852.6011 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4565.6482
2025-08-30 | 3406.634 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4167.192
2025-08-31 | 3225.7241 | 6.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3880.4385
2025-08-31 | 3041.502 | 6.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3645.4697
2025-08-31 | 2972.5229 | 8.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736.7661
2025-08-31 | 2923.4529 | 8.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.6889
2025-08-31 | 2969.689 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3723.7378
2025-08-31 | 3204.1521 | 7.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4086.5005
2025-08-31 | 3724.0071 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.3487
2025-08-31 | 4264.2319 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4601.3678
2025-08-31 | 4673.1968 | 2.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4538.637
2025-08-31 | 4874.9448 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.7461
2025-08-31 | 4839.5508 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5289.6448
2025-08-31 | 4967.3179 | 0 | 4.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6060.4721
2025-08-31 | 5041.8169 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6289.2773
2025-08-31 | 5092.3062 | 0 | 6.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6447.2148
2025-08-31 | 5344.5488 | 0 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6606.9319
2025-08-31 | 5740.147 | 0 | 7.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7324.0252
2025-08-31 | 6049.6538 | 0 | 7.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7848.0298
2025-08-31 | 6004.9932 | 0 | 6.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7887.915
2025-08-31 | 5703.165 | 0 | 5.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7495.7708
2025-08-31 | 5497.354 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5887.4528
2025-08-31 | 5125.4321 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5230.2696
2025-08-31 | 4685.0171 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4716.8328
2025-08-31 | 4117 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4367.6425
2025-08-31 | 3704.2949 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3925.1851
2025-09-01 | 3359.2791 | 4.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3359.9572
2025-09-01 | 3191.0449 | 5.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3223.9912
2025-09-01 | 3098.8889 | 5.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.2829
2025-09-01 | 3050.0911 | 5.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3134.205
2025-09-01 | 3077.9309 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467.264
2025-09-01 | 3252.417 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720.0235
2025-09-01 | 3663.2539 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4147.8718
2025-09-01 | 4198.1128 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4003.8842
2025-09-01 | 4704.8589 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4289.8645
2025-09-01 | 5134.5952 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5334.2504
2025-09-01 | 5545.7422 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6186.0081
2025-09-01 | 5785.2808 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6663.126
2025-09-01 | 5851.7622 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6965.3585
2025-09-01 | 6005.0688 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6499.1634
2025-09-01 | 6345.311 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7466.5815
2025-09-01 | 6722.0908 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7522.8286
2025-09-01 | 7115.2651 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8083.5469
2025-09-01 | 6857.8521 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7793.009
2025-09-01 | 6619.9668 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7070.4417
2025-09-01 | 6384.6738 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5902.6878
2025-09-01 | 5724.3638 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5557.6398
2025-09-01 | 5090.3301 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4875.3477
2025-09-01 | 4365.1689 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3994.1538
2025-09-01 | 3921.4099 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3316.7012
2025-09-02 | 3611.543 | 0 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3132.9392
2025-09-02 | 3408.7019 | 1.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2827.9799
2025-09-02 | 3303.8301 | 4.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3007.2788
2025-09-02 | 3335.063 | 4.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2969.2003
2025-09-02 | 3486.179 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2994.2505
2025-09-02 | 3795.9829 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3390.0141
2025-09-02 | 4041.6851 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3916.8652
2025-09-02 | 4277.7349 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4080.8864
2025-09-02 | 4442.9282 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4139.1591
2025-09-02 | 4823.3481 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4563.2631
2025-09-02 | 5095.8252 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5488.4482
2025-09-02 | 5368.73 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6112.4208
2025-09-02 | 5589.4502 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6377.9397
2025-09-02 | 5771.8608 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6572.5908
2025-09-02 | 6184.6011 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6512.0258
2025-09-02 | 6895.75 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7229.1192
2025-09-02 | 7581.873 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7716.4101
2025-09-02 | 7456.0239 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7168.8765
2025-09-02 | 7061.8018 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6923.587
2025-09-02 | 6770.231 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5153.7012
2025-09-02 | 6117.0869 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5153.7893
2025-09-02 | 5266.2192 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4636.364
2025-09-02 | 4475.1382 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3792.1596
2025-09-02 | 3960.8259 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3404.7037
2025-09-03 | 3593.032 | 2.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3194.9525
2025-09-03 | 3432.8911 | 3.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3091.9874
2025-09-03 | 3286.605 | 4.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3029.2794
2025-09-03 | 3267.823 | 4.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3013.2016
2025-09-03 | 3405.873 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.2565
2025-09-03 | 3835.989 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.0191
2025-09-03 | 4200.4751 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3927.8655
2025-09-03 | 4427.2559 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.8874
2025-09-03 | 4505.606 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4216.4371
2025-09-03 | 4661.7119 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5370.9641
2025-09-03 | 4872.6382 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6039.1534
2025-09-03 | 5137.98 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6442.8439
2025-09-03 | 5304.5171 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6598.2218
2025-09-03 | 5509.8999 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6866.3002
2025-09-03 | 5973.5718 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6879.1626
2025-09-03 | 6643.814 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7632.9697
2025-09-03 | 7298.1382 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.9785
2025-09-03 | 7076.1279 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7903.15
2025-09-03 | 6776.8652 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7107.1553
2025-09-03 | 6535.23 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5939.4015
2025-09-03 | 5936.1821 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4970.2209
2025-09-03 | 5202.292 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4460.359
2025-09-03 | 4488.083 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3902.1628
2025-09-03 | 3957.7671 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3327.7015
2025-09-04 | 3670.5291 | 1.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3029.9478
2025-09-04 | 3438.084 | 1.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2827.9799
2025-09-04 | 3360.114 | 2.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2798.2729
2025-09-04 | 3368.7351 | 2.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2782.195
2025-09-04 | 3512.6111 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2851.2465
2025-09-04 | 3892.1179 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.0091
2025-09-04 | 4209.4551 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3542.8545
2025-09-04 | 4361.7041 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-09-04 | 4548.4448 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4216.4371
2025-09-04 | 4760.4351 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5444.3914
2025-09-04 | 5080.0928 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.585
2025-09-04 | 5459.6719 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6956.8354
2025-09-04 | 5694.8472 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6855.2175
2025-09-04 | 5609.4878 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4847.0479
2025-09-04 | 5423.9351 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4456.0598
2025-09-04 | 5614.1289 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4651.4604
2025-09-04 | 6243.6118 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5179.1777
2025-09-04 | 6100.3818 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5501.6341
2025-09-04 | 5971.021 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5579.3423
2025-09-04 | 5864.3892 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5681.7162
2025-09-04 | 5315.3662 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5446.8092
2025-09-04 | 4713.0112 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5087.3769
2025-09-04 | 4065.8491 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4529.1806
2025-09-04 | 3612.667 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4207.7266
2025-09-05 | 3351.5779 | 9.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3909.9729
2025-09-05 | 3210.8259 | 9.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3719.0053
2025-09-05 | 3115 | 9.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3557.2945
2025-09-05 | 3112.052 | 8.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3409.2128
2025-09-05 | 3244.5869 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500.2649
2025-09-05 | 3660.739 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3775.0251
2025-09-05 | 4026.627 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4125.8712
2025-09-05 | 4237.061 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4443.8968
2025-09-05 | 4276.4932 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4436.1676
2025-09-05 | 4267.4282 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4225.2766
2025-09-05 | 4351.6758 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.1831
2025-09-05 | 4522.6611 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4790.7283
2025-09-05 | 4548.5112 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5203.102
2025-09-05 | 4685.6909 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5691.4625
2025-09-05 | 4830.124 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.7522
2025-09-05 | 5188.6348 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5944.1404
2025-09-05 | 5650.1382 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6358.004
2025-09-05 | 5629.855 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6765.026
2025-09-05 | 5571.0879 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6299.4544
2025-09-05 | 5654.7861 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6159.6836
2025-09-05 | 5263.624 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5083.7989
2025-09-05 | 4865.6348 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4592.3628
2025-09-05 | 4257.0308 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4067.1675
2025-09-05 | 3746.543 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3778.7144
2025-09-06 | 3416.606 | 5.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3748.4348
2025-09-06 | 3200.9629 | 5.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3568.4675
2025-09-06 | 3085.301 | 6.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3571.7614
2025-09-06 | 3064.657 | 7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3566.6838
2025-09-06 | 3130.5449 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3778.7394
2025-09-06 | 3315.333 | 8.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4174.503
2025-09-06 | 3738.4641 | 7.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.3487
2025-09-06 | 4288.8081 | 6.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4777.3728
2025-09-06 | 4747.5859 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4901.6473
2025-09-06 | 4951.1968 | 5.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4899.7624
2025-09-06 | 5112.772 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4896.1051
2025-09-06 | 5116.4131 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4818.943
2025-09-06 | 5004.8101 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4442.3173
2025-09-06 | 4981.9868 | 0.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4192.9673
2025-09-06 | 4920.9702 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4440.8248
2025-09-06 | 5230.2598 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5121.2045
2025-09-06 | 5533.1079 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6049.0595
2025-09-06 | 5389.229 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5721.808
2025-09-06 | 5174.1279 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5549.9458
2025-09-06 | 5072.2358 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5520.1781
2025-09-06 | 4769.4551 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5362.2733
2025-09-06 | 4341.0068 | 3.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5013.8413
2025-09-06 | 3832.252 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4400.6435
2025-09-06 | 3472.377 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4002.1873
2025-09-07 | 3232.3589 | 4.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3649.4319
2025-09-07 | 3003.5759 | 5.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3546.4669
2025-09-07 | 2985.469 | 5.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3395.7564
2025-09-07 | 2930.012 | 5.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.6801
2025-09-07 | 2939.9661 | 6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3602.7344
2025-09-07 | 3177.8391 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3998.498
2025-09-07 | 3581.0439 | 6.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4371.3447
2025-09-07 | 4139.3101 | 5.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4634.3687
2025-09-07 | 4638.4429 | 3.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4670.6408
2025-09-07 | 4867.6611 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.7514
2025-09-07 | 5054.481 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500.0938
2025-09-07 | 5152.1938 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4565.9358
2025-09-07 | 5173.7661 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4519.3195
2025-09-07 | 5184.7549 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4346.9717
2025-09-07 | 5387.7051 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4734.5342
2025-09-07 | 5793.6909 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.7771
2025-09-07 | 6139.1162 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5278.0723
2025-09-07 | 5943.3628 | 0.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5461.0995
2025-09-07 | 5719.73 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5791.8148
2025-09-07 | 5553.0122 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5894.1888
2025-09-07 | 4972.54 | 3.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5582.2796
2025-09-07 | 4415.978 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5123.8444
2025-09-07 | 3740.9141 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4796.6548
2025-09-07 | 3313.125 | 8.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4398.1985
2025-09-08 | 3025.9919 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3865.9716
2025-09-08 | 2924.949 | 9.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3752.0062
2025-09-08 | 2868.3069 | 11.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3777.3008
2025-09-08 | 2941.6621 | 11.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3761.2229
2025-09-08 | 3130.7859 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.2775
2025-09-08 | 3582.4221 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4314.0405
2025-09-08 | 3868.6089 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4763.8893
2025-09-08 | 4008.7881 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4828.9077
2025-09-08 | 3977.8191 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4744.1763
2025-09-08 | 3985.7639 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4522.2851
2025-09-08 | 4040.676 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4364.6235
2025-09-08 | 4112.9038 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4155.4576
2025-09-08 | 4047.842 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4130.8419
2025-09-08 | 4098.2578 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3991.495
2025-09-08 | 4311.9639 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4162.3503
2025-09-08 | 4886.2808 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4409.4535
2025-09-08 | 5584.374 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4959.1714
2025-09-08 | 5435.1992 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5215.626
2025-09-08 | 5324.2969 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5392.3369
2025-09-08 | 5285.4458 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5571.7131
2025-09-08 | 4817.0151 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5369.807
2025-09-08 | 4204.3442 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5351.3844
2025-09-08 | 3639.9541 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4793.1881
2025-09-08 | 3253.918 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4163.7254
2025-09-09 | 3018.2891 | 10.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008.9757
2025-09-09 | 2926.55 | 10.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3785.0072
2025-09-09 | 2872.969 | 10.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678.2979
2025-09-09 | 2903.873 | 11.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3794.2238
2025-09-09 | 3164.699 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006.2794
2025-09-09 | 3534.76 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4380.0423
2025-09-09 | 3822.2109 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4939.8943
2025-09-09 | 3939.333 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4971.9118
2025-09-09 | 3879.2949 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5074.1857
2025-09-09 | 3899.3911 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4775.2923
2025-09-09 | 4040.9331 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4353.6231
2025-09-09 | 4035.3569 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4067.4551
2025-09-09 | 3934.1411 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4468.8284
2025-09-09 | 4017.3201 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4810.3342
2025-09-09 | 4261.7241 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5116.906
2025-09-09 | 4796.1641 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5650.431
2025-09-09 | 5448.002 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6211.1492
2025-09-09 | 5453.0391 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6030.7524
2025-09-09 | 5359.3232 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5194.3313
2025-09-09 | 5294.2539 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5516.7115
2025-09-09 | 4885.0562 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5116.7998
2025-09-09 | 4274.812 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4834.3697
2025-09-09 | 3681.0371 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4243.1725
2025-09-09 | 3283.4761 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3866.7169
2025-09-10 | 3078.3911 | 5.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3502.9613
2025-09-10 | 2959.0049 | 6.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3333.9943
2025-09-10 | 2901.2051 | 7.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.2892
2025-09-10 | 2954.7749 | 7.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.21
2025-09-10 | 3121.8501 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.2703
2025-09-10 | 3606.824 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4061.0332
2025-09-10 | 3860.2219 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4422.8796
2025-09-10 | 3996.9451 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4619.9018
2025-09-10 | 3862.1069 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4535.1704
2025-09-10 | 3936.9509 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4269.2779
2025-09-10 | 3983.2209 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4144.6172
2025-09-10 | 4063.0969 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4350.1642
2025-09-10 | 4060.5869 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5239.8156
2025-09-10 | 4186.689 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5581.3215
2025-09-10 | 4469.0049 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6071.4617
2025-09-10 | 5058.6631 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6531.5593
2025-09-10 | 5696.7412 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6908.7091
2025-09-10 | 5613.5698 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7132.1628
2025-09-10 | 5474.7378 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6115.886
2025-09-10 | 5507.667 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5902.6878
2025-09-10 | 5051.8901 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5138.8005
2025-09-10 | 4445.5601 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4713.3662
2025-09-10 | 3526.5249 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4034.1665
2025-09-10 | 3134.6731 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3811.7153
2025-09-11 | 2882.856 | 4.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.9575
2025-09-11 | 2980.1731 | 5.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3234.9915
2025-09-11 | 2981.457 | 5.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.2829
2025-09-11 | 3015.6851 | 5.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3167.206
2025-09-11 | 3163.5979 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3192.2562
2025-09-11 | 3533.7219 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3687.0226
2025-09-11 | 3821.9441 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3872.8639
2025-09-11 | 3979.032 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3992.8839
2025-09-11 | 4016.637 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4161.1597
2025-09-11 | 3971.4441 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.2735
2025-09-11 | 3982.5339 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4644.0335
2025-09-11 | 4124.3281 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5121.1514
2025-09-11 | 4146.4009 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5239.8156
2025-09-11 | 4194.707 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5361.0394
2025-09-11 | 4441.9678 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5887.8933
2025-09-11 | 4948.7051 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5944.1404
2025-09-11 | 5296.1592 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6284.5766
2025-09-11 | 5363.959 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6397.8892
2025-09-11 | 5399.2451 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5455.0398
2025-09-11 | 5437.7568 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5285.7049
2025-09-11 | 4945.2769 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5193.802
2025-09-11 | 4341.9131 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4834.3697
2025-09-11 | 3783.5901 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4386.1766
2025-09-11 | 3398.8401 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3899.7178
2025-09-12 | 3087.739 | 7.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3656.9657
2025-09-12 | 2958.115 | 7.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3487.9987
2025-09-12 | 2871.9829 | 7.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403.2901
2025-09-12 | 2935.301 | 8.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3420.2132
2025-09-12 | 3077.9719 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3753.2722
2025-09-12 | 3546.0139 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3962.0304
2025-09-12 | 3871.7781 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4631.8856
2025-09-12 | 3981.8269 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4630.9021
2025-09-12 | 3974.7639 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623.1729
2025-09-12 | 4012.103 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500.2845
2025-09-12 | 4013.7981 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4298.6216
2025-09-12 | 4027.2029 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4100.456
2025-09-12 | 4031.8459 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4395.401
2025-09-12 | 4069.1721 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4663.4795
2025-09-12 | 4315.8311 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4933.3376
2025-09-12 | 4736.729 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5613.7173
2025-09-12 | 5120.8218 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5990.8672
2025-09-12 | 5024.5581 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5810.4703
2025-09-12 | 4958.564 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5271.4714
2025-09-12 | 4919.373 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5362.7071
2025-09-12 | 4603.228 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5270.8042
2025-09-12 | 4201.8799 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4889.3712
2025-09-12 | 3677.2029 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4397.1769
2025-09-12 | 3317.019 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3668.7112
2025-09-13 | 3088.072 | 4.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3693.4332
2025-09-13 | 2929.0859 | 5.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3535.4666
2025-09-13 | 2850.1011 | 5.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3406.7567
2025-09-13 | 2852.498 | 5.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.6801
2025-09-13 | 2948.429 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3624.735
2025-09-13 | 3151.8501 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3976.4973
2025-09-13 | 3655.71 | 6.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4426.3462
2025-09-13 | 4185.2739 | 6.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4755.3722
2025-09-13 | 4512.3232 | 3.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4659.6404
2025-09-13 | 4809.2222 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4536.752
2025-09-13 | 5001.0811 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4371.8028
2025-09-13 | 4961.3159 | 0 | 1.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4922.348
2025-09-13 | 4815.521 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5004.2986
2025-09-13 | 4785.0791 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5198.9497
2025-09-13 | 4768.1509 | 0 | 3.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5432.0941
2025-09-13 | 5102.5972 | 0 | 4.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6296.0422
2025-09-13 | 5314.2671 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6489.6237
2025-09-13 | 5340.687 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6713.0773
2025-09-13 | 5163.8672 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5917.0826
2025-09-13 | 5075.6929 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5520.316
2025-09-13 | 4908.877 | 0.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5241.2699
2025-09-13 | 4308.8682 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4760.8341
2025-09-13 | 3870.2219 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4246.6391
2025-09-13 | 3562.5879 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3859.1832
2025-09-14 | 3225.2109 | 4.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3638.4316
2025-09-14 | 3059.7009 | 5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3491.4653
2025-09-14 | 2939.7361 | 5.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3461.7583
2025-09-14 | 2876.959 | 4.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.6769
2025-09-14 | 2935.469 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3558.7331
2025-09-14 | 3142.948 | 6.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4020.4986
2025-09-14 | 3589.6909 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4162.3387
2025-09-14 | 4201.7378 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4524.3656
2025-09-14 | 4674.9331 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4351.6317
2025-09-14 | 5035.167 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4658.1692
2025-09-14 | 5273.3711 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5363.0721
2025-09-14 | 5406.3682 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5619.9079
2025-09-14 | 5609.8862 | 0 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5701.8585
2025-09-14 | 5661.1909 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6006.6506
2025-09-14 | 5924.1919 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6239.7951
2025-09-14 | 6385.8579 | 0 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6626.4653
2025-09-14 | 6794.7231 | 0 | 5.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7113.7562
2025-09-14 | 6604.0479 | 0 | 3.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6859.932
2025-09-14 | 6456.147 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6174.0784
2025-09-14 | 6094.5059 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5593.7434
2025-09-14 | 5384.7471 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5219.2693
2025-09-14 | 4649.0762 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4859.8369
2025-09-14 | 3990.9741 | 2.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4334.6416
2025-09-14 | 3518.896 | 4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3947.1857
2025-09-15 | 3257.907 | 4.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3370.9575
2025-09-15 | 3036.0869 | 5.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3267.9924
2025-09-15 | 2921.2 | 5.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3194.2841
2025-09-15 | 2979.499 | 7.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3332.2107
2025-09-15 | 3233.627 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3445.2634
2025-09-15 | 3601.0701 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3808.026
2025-09-15 | 3840.9829 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4224.874
2025-09-15 | 4044.0281 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4399.8955
2025-09-15 | 4022.5801 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4348.1651
2025-09-15 | 4143.6572 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4214.2763
2025-09-15 | 4279.8408 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.3284
2025-09-15 | 4431.2739 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4607.1599
2025-09-15 | 4539.9951 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4982.8199
2025-09-15 | 4632.1211 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5324.3257
2025-09-15 | 4990.6138 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5777.7522
2025-09-15 | 5675.7749 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6017.5678
2025-09-15 | 6178.8311 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6725.1407
2025-09-15 | 6144.9258 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6875.167
2025-09-15 | 5887.3579 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6042.4587
2025-09-15 | 5799.9941 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5197.7024
2025-09-15 | 5232.2588 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5226.803
2025-09-15 | 4536.751 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4768.3678
2025-09-15 | 3836.4099 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3836.1609
2025-09-15 | 3443.29 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3745.7134
2025-09-16 | 3178.5911 | 6.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3557.9628
2025-09-16 | 2991.6709 | 5.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3245.9918
2025-09-16 | 2893.509 | 6.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3271.2863
2025-09-16 | 2951.322 | 7.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3376.2119
2025-09-16 | 3205.4141 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3533.2659
2025-09-16 | 3542.0779 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3819.0263
2025-09-16 | 3847.856 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4224.874
2025-09-16 | 4002.9031 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4300.8927
2025-09-16 | 3928.1479 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4293.1635
2025-09-16 | 4041.448 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4060.2719
2025-09-16 | 4091.302 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4937.743
2025-09-16 | 4270.7129 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5598.4293
2025-09-16 | 4293.6191 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5790.5208
2025-09-16 | 4504.1758 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6352.3087
2025-09-16 | 4789.9009 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6512.0258
2025-09-16 | 5514.6011 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6935.4098
2025-09-16 | 6063.499 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7422.7007
2025-09-16 | 5901.207 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7279.0175
2025-09-16 | 5817.2822 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6299.4544
2025-09-16 | 5721.1348 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5205.1279
2025-09-16 | 5161.376 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4984.7961
2025-09-16 | 4491.3452 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4460.359
2025-09-16 | 3850.116 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4111.1687
2025-09-16 | 3461.3889 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3767.7141
2025-09-17 | 3168.803 | 4.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403.9584
2025-09-17 | 3008.6689 | 5.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3300.9934
2025-09-17 | 2927.854 | 6.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216.2848
2025-09-17 | 2947.4751 | 5.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3156.2056
2025-09-17 | 3205.5569 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3313.2596
2025-09-17 | 3481.8049 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3775.0251
2025-09-17 | 3802.137 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4202.8733
2025-09-17 | 3952.9861 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4344.894
2025-09-17 | 4044.03 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4260.1626
2025-09-17 | 4129.1499 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4082.2726
2025-09-17 | 4174.6968 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4901.0293
2025-09-17 | 4322.8218 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5268.0061
2025-09-17 | 4405.6689 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5643.6661
2025-09-17 | 4676.332 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6242.1677
2025-09-17 | 5093.5742 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6548.7395
2025-09-17 | 5783.2729 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7155.6918
2025-09-17 | 6309.6372 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7642.9827
2025-09-17 | 6148.4731 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7719.5816
2025-09-17 | 6122.9912 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6483.0228
2025-09-17 | 5929.7529 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5792.5468
2025-09-17 | 5498.6309 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5300.644
2025-09-17 | 4784.5029 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4537.3612
2025-09-17 | 4090.8821 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3935.1637
2025-09-17 | 3611.6709 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3426.7044
2025-09-18 | 3322.4819 | 2.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3106.95
2025-09-18 | 3133.2661 | 2.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2970.984
2025-09-18 | 3062.6899 | 3.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2908.276
2025-09-18 | 3062.8979 | 4.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2969.2003
2025-09-18 | 3256.0991 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3148.2549
2025-09-18 | 3617.8369 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3577.0195
2025-09-18 | 3983.717 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4081.8699
2025-09-18 | 4160.3208 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4201.8899
2025-09-18 | 4271.311 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4062.1569
2025-09-18 | 4348.9829 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4820.2589
2025-09-18 | 4511.1011 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5561.8755
2025-09-18 | 4774.7271 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6406.1302
2025-09-18 | 4758.1021 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6304.5123
2025-09-18 | 4899.3062 | 0 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6535.8771
2025-09-18 | 5104.8569 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6658.8805
2025-09-18 | 5806.0532 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6678.414
2025-09-18 | 6167.1709 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7018.8502
2025-09-18 | 6049.8838 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7279.0175
2025-09-18 | 6169.4668 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6703.3049
2025-09-18 | 6044.8999 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6306.5383
2025-09-18 | 5553.6621 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5374.0714
2025-09-18 | 4889.8511 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4460.359
2025-09-18 | 4205.4429 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3957.1643
2025-09-18 | 3687.5339 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3602.7094
2025-09-19 | 3336.6631 | 4.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403.9584
2025-09-19 | 3107.7019 | 6.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3344.9946
2025-09-19 | 3000.0391 | 6.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3249.2857
2025-09-19 | 2994.6121 | 8.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3486.215
2025-09-19 | 3203.062 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.2715
2025-09-19 | 3541.6541 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4017.032
2025-09-19 | 3914.636 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4378.8784
2025-09-19 | 4097.0801 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4641.9024
2025-09-19 | 4079.575 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4645.1735
2025-09-19 | 4114.1709 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4599.2873
2025-09-19 | 4088.6809 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4430.6253
2025-09-19 | 4086.7629 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4320.4623
2025-09-19 | 4041.728 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4152.8425
2025-09-19 | 4135.9839 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3936.4935
2025-09-19 | 4323.4912 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4309.2051
2025-09-19 | 4877.957 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4475.5933
2025-09-19 | 5269.7969 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5036.3115
2025-09-19 | 5023.25 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5226.6263
2025-09-19 | 5033.689 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5458.3388
2025-09-19 | 4931.0962 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5538.7121
2025-09-19 | 4605.7388 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5501.8108
2025-09-19 | 4147.959 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5098.3772
2025-09-19 | 3678.3469 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4562.1816
2025-09-19 | 3283.677 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4163.7254
2025-09-20 | 3010.1289 | 9.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4177.447
2025-09-20 | 2868.9961 | 10 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4041.481
2025-09-20 | 2788.001 | 12.9 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4242.7805
2025-09-20 | 2828.937 | 11.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4083.6986
2025-09-20 | 2949.761 | 12.3 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4295.7541
2025-09-20 | 3202.969 | 13.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.5193
2025-09-20 | 3698.1311 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5185.3678
2025-09-20 | 4341.811 | 11.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5283.3872
2025-09-20 | 4567.4692 | 8.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5209.6561
2025-09-20 | 4685.7651 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5009.7655
2025-09-20 | 4739.062 | 6.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5006.1082
2025-09-20 | 4649.4321 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4818.943
2025-09-20 | 4532.5171 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4585.3213
2025-09-20 | 4366.9312 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4291.9701
2025-09-20 | 4439.251 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4345.2589
2025-09-20 | 4670.0791 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4680.6403
2025-09-20 | 5040.5801 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5248.6462
2025-09-20 | 4971.5342 | 0.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5527.1014
2025-09-20 | 4893.54 | 3.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5813.8155
2025-09-20 | 4707.1191 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6191.1972
2025-09-20 | 4385.0718 | 9.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6187.2968
2025-09-20 | 4011.8921 | 10.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5761.8626
2025-09-20 | 3586.3259 | 10.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5170.6654
2025-09-20 | 3261.655 | 10.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4706.2073
2025-09-21 | 2986.0659 | 12.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4573.4583
2025-09-21 | 2854.679 | 14.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.4941
2025-09-21 | 2828.4399 | 14.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4440.7862
2025-09-21 | 2833.5601 | 15.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4534.7114
2025-09-21 | 2931.7151 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.7638
2025-09-21 | 3150.2129 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4900.5237
2025-09-21 | 3706.6851 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5306.3713
2025-09-21 | 4225.8179 | 12.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5415.391
2025-09-21 | 4538.5361 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5319.6592
2025-09-21 | 4773.9458 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5009.7655
2025-09-21 | 4826.9531 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4665.0985
2025-09-21 | 4920.4668 | 0.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4356.9298
2025-09-21 | 4866.0161 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4894.1575
2025-09-21 | 4860.0088 | 0 | 4.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5676.2275
2025-09-21 | 5087.8389 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6276.5087
2025-09-21 | 5573.6948 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6846.7474
2025-09-21 | 6054.7271 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7627.7477
2025-09-21 | 5964.436 | 0 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7630.9193
2025-09-21 | 5159.7329 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6100.651
2025-09-21 | 5499.002 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5593.7434
2025-09-21 | 5035.2441 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5175.268
2025-09-21 | 4412.3999 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4980.8403
2025-09-21 | 3725.137 | 3.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4411.6438
2025-09-21 | 3342.2859 | 2.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3793.1813
2025-09-22 | 3053.991 | 2.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3183.9522
2025-09-22 | 2884.2561 | 3.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3003.9849
2025-09-22 | 2839.2749 | 3.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2897.2757
2025-09-22 | 2864.415 | 3.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2870.1975
2025-09-22 | 3066.71 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3104.2537
2025-09-22 | 3437.094 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.0166
2025-09-22 | 3780.2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3883.8643
2025-09-22 | 3966.97 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4113.8874
2025-09-22 | 3972.7461 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4249.1622
2025-09-22 | 3949.8379 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4104.2732
2025-09-22 | 4084.0081 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4387.0378
2025-09-22 | 4220.0679 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4497.0189
2025-09-22 | 4104.498 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4652.3968
2025-09-22 | 4113.7212 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3929.2059
2025-09-22 | 4296.2642 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4022.7832
2025-09-22 | 5036.1631 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431.4541
2025-09-22 | 5612.8428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4926.1705
2025-09-22 | 5515.417 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5186.3378
2025-09-22 | 5606.9219 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5194.3313
2025-09-22 | 5502.104 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5296.7053
2025-09-22 | 4992.0151 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5017.797
2025-09-22 | 4337.3462 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4537.3612
2025-09-22 | 3804.9041 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3946.164
2025-09-22 | 3456.0259 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3437.7047
2025-09-23 | 3202.625 | 1.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3073.949
2025-09-23 | 3005.417 | 1.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2849.9805
2025-09-23 | 2944.699 | 1.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2743.2713
2025-09-23 | 2997.6189 | 1.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2716.1931
2025-09-23 | 3220.697 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2873.2471
2025-09-23 | 3568.481 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3203.0088
2025-09-23 | 3886.908 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3619.8567
2025-09-23 | 4105.8911 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3970.8833
2025-09-23 | 4104.4009 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4161.1597
2025-09-23 | 4131.6919 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4170.2751
2025-09-23 | 4227.5542 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4111.6163
2025-09-23 | 4247.4028 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4276.7368
2025-09-23 | 4190.0322 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4762.5378
2025-09-23 | 4282.6758 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5030.6163
2025-09-23 | 4645.4282 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5300.4744
2025-09-23 | 5232.3369 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5760.572
2025-09-23 | 5742.0181 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6358.004
2025-09-23 | 5727.0029 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6214.3208
2025-09-23 | 5836.1001 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5712.0355
2025-09-23 | 5749.875 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5278.5553
2025-09-23 | 5152.6182 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4929.7945
2025-09-23 | 4508.835 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4416.3577
2025-09-23 | 3899.178 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3902.1628
2025-09-23 | 3507.1899 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3371.7028
2025-09-24 | 3220.9209 | 1.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3007.9472
2025-09-24 | 3101.5039 | 1.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2871.9812
2025-09-24 | 2994.249 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2765.2719
2025-09-24 | 3009.6299 | 2.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2771.1947
2025-09-24 | 3210.385 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2917.2483
2025-09-24 | 3543.1851 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3258.0104
2025-09-24 | 3886.7859 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3641.8574
2025-09-24 | 4071.135 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4080.8864
2025-09-24 | 4002.239 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4216.1613
2025-09-24 | 4110.9438 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.699
2025-09-24 | 4196.769 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4754.1746
2025-09-24 | 4279.9619 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5451.5745
2025-09-24 | 4310.6089 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5680.3798
2025-09-24 | 4378.4141 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5838.3172
2025-09-24 | 4659.5752 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5887.8933
2025-09-24 | 5222.1372 | 0 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6531.5593
2025-09-24 | 5788.4839 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6725.1407
2025-09-24 | 5694.4731 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6508.0302
2025-09-24 | 5774.271 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5712.0355
2025-09-24 | 5630.4438 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5388.6963
2025-09-24 | 5221.9341 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4951.7951
2025-09-24 | 4552.6968 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4515.3606
2025-09-24 | 3945.24 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3935.1637
2025-09-24 | 3563.1909 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3404.7037
2025-09-25 | 3276.3811 | 2.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.9512
2025-09-25 | 3089.908 | 2.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2948.9834
2025-09-25 | 3032.2771 | 2.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2842.2741
2025-09-25 | 3038.832 | 2.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2815.1959
2025-09-25 | 3215.9319 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2972.2499
2025-09-25 | 3577.4729 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3368.0135
2025-09-25 | 3925.8679 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3828.8627
2025-09-25 | 4056.998 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4201.8899
2025-09-25 | 4136.6528 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4381.166
2025-09-25 | 4199.9619 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4401.2817
2025-09-25 | 4186.2212 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4364.6235
2025-09-25 | 4144.0669 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4298.4616
2025-09-25 | 4125.1479 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4163.8428
2025-09-25 | 4140.8921 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4046.4966
2025-09-25 | 4330.5449 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4077.7848
2025-09-25 | 4912.4839 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.4557
2025-09-25 | 5479.8149 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5069.1745
2025-09-25 | 5489.5249 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5281.6279
2025-09-25 | 5572.7651 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5293.3341
2025-09-25 | 5464.3979 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5263.7043
2025-09-25 | 5039.7588 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5039.7976
2025-09-25 | 4442.75 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4570.3621
2025-09-25 | 3756.7991 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3946.164
2025-09-25 | 3465 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3470.7056
2025-09-26 | 3190.2151 | 2.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3117.9503
2025-09-26 | 3006.689 | 2.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2948.9834
2025-09-26 | 2905.885 | 3.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2963.2776
2025-09-26 | 2945.0901 | 3.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2892.1981
2025-09-26 | 3184.1941 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3005.2508
2025-09-26 | 3552.377 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3291.0113
2025-09-26 | 3940.6521 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3707.8592
2025-09-26 | 4073.3701 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4080.8864
2025-09-26 | 4085.978 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4205.161
2025-09-26 | 4119.8052 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4170.2751
2025-09-26 | 4107.333 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4276.8968
2025-09-26 | 4127.8848 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4900.8694
2025-09-26 | 4094.6069 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4725.8241
2025-09-26 | 4189.6382 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5140.7573
2025-09-26 | 4435.1611 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5410.6154
2025-09-26 | 4840.126 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5356.7216
2025-09-26 | 5222.772 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5256.5936
2025-09-26 | 5244.9448 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5480.0472
2025-09-26 | 5305.2349 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5234.7577
2025-09-26 | 5166.7661 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5175.7018
2025-09-26 | 4779.0708 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5061.7983
2025-09-26 | 4425.9692 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4636.364
2025-09-26 | 3941.572 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4122.169
2025-09-26 | 3558.531 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3712.7125
2025-09-27 | 3164.853 | 4.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3649.4319
2025-09-27 | 3015.03 | 4.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3403.4628
2025-09-27 | 2927.323 | 4.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3307.7539
2025-09-27 | 2877.9441 | 4.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.6769
2025-09-27 | 2919.2219 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3481.7309
2025-09-27 | 3183.0879 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3833.4933
2025-09-27 | 3640.104 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239.3409
2025-09-27 | 4219.2109 | 5.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4645.369
2025-09-27 | 4658.1118 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4692.6414
2025-09-27 | 4799.8291 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4536.752
2025-09-27 | 4920.3662 | 0.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4357.0898
2025-09-27 | 4960.7192 | 0 | 0.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4555.2113
2025-09-27 | 4933.8931 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5004.2986
2025-09-27 | 4910.7578 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5125.5223
2025-09-27 | 4942.0122 | 0 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5064.9573
2025-09-27 | 5186.0122 | 0 | 1.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5341.4866
2025-09-27 | 5514.8398 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6085.7732
2025-09-27 | 5401.4028 | 0 | 2.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6199.0858
2025-09-27 | 5325.9868 | 0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5494.8064
2025-09-27 | 5117.4761 | 0.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5487.1772
2025-09-27 | 4857.1309 | 0.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5208.269
2025-09-27 | 4412.0581 | 0 | 0.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4676.5443
2025-09-27 | 3940.7561 | 0.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4048.6334
2025-09-27 | 3577.0569 | 0.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3573.175
2025-09-28 | 3254.842 | 1.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3297.4219
2025-09-28 | 3107.1411 | 2.1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3172.4562
2025-09-28 | 3005.4241 | 2.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3098.7479
2025-09-28 | 2924.8511 | 2.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3082.6701
2025-09-28 | 2996.2339 | 2.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3239.724
2025-09-28 | 3202.8789 | 2.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3569.4858
2025-09-28 | 3641.0391 | 3.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4085.3365
2025-09-28 | 4307.3999 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4392.3618
2025-09-28 | 4875.374 | 1.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4406.6332
2025-09-28 | 5086.6299 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4658.1692
2025-09-28 | 5420.0649 | 0 | 2.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5252.9311
2025-09-28 | 5558.376 | 0 | 3.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5619.9079
2025-09-28 | 5714.4829 | 0 | 4.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5848.7132
2025-09-28 | 5817.771 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5969.9369
2025-09-28 | 5884.4541 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6276.5087
2025-09-28 | 6338.0942 | 0 | 5.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6736.6064
2025-09-28 | 6587.415 | 0 | 5.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7113.7562
2025-09-28 | 6331.2769 | 0 | 3.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6786.5047
2025-09-28 | 6099.0381 | 0 | 0.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5660.0869
2025-09-28 | 5713.4878 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5593.7434
2025-09-28 | 5156.519 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5340.2727
2025-09-28 | 4371.7622 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5123.8444
2025-09-28 | 3790.134 | 7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4785.6544
2025-09-28 | 3401.501 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4288.1954
2025-09-29 | 3121.312 | 5.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3458.96
2025-09-29 | 2971.509 | 5.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3256.9921
2025-09-29 | 2882.9231 | 5.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3172.2835
2025-09-29 | 2898.8279 | 5.4 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3112.2044
2025-09-29 | 3106.7981 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3335.2602
2025-09-29 | 3436.7161 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3731.0238
2025-09-29 | 3794.823 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4422.8796
2025-09-29 | 4071.3059 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4597.9012
2025-09-29 | 4043.8521 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4326.1644
2025-09-29 | 4134.1641 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.2735
2025-09-29 | 4132.313 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4570.6062
2025-09-29 | 4337.4072 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5671.8566
2025-09-29 | 4291.2969 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.7944
2025-09-29 | 4448.498 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7013.1549
2025-09-29 | 4728.7202 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7246.2994
2025-09-29 | 5400.189 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7339.2602
2025-09-29 | 5987.625 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7899.9785
2025-09-29 | 5828.8862 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7572.7269
2025-09-29 | 5812.1079 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6666.5912
2025-09-29 | 5557.562 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5865.9741
2025-09-29 | 4991.9668 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5190.503
2025-09-29 | 4295.1499 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4504.3603
2025-09-29 | 3714.97 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4023.1662
2025-09-29 | 3383.541 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3547.7078
2025-09-30 | 3089.408 | 3.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3293.9553
2025-09-30 | 2926.99 | 3.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3003.9849
2025-09-30 | 2813.2141 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2875.2751
2025-09-30 | 2890.542 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2848.1969
2025-09-30 | 3053.4861 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3027.2515
2025-09-30 | 3398.4419 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3434.0154
2025-09-30 | 3777.217 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3938.8658
2025-09-30 | 4019.52 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4289.8924
2025-09-30 | 3974.321 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4183.1604
2025-09-30 | 3971.061 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.2729
2025-09-30 | 4117.2002 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4276.8968
2025-09-30 | 4170.0571 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4386.8779
2025-09-30 | 4129.874 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4799.2515
2025-09-30 | 4201.0049 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4700.1932
2025-09-30 | 4444.3008 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4786.4829
2025-09-30 | 5029.5181 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4879.4437
2025-09-30 | 5549.9829 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5183.1662
2025-09-30 | 5323.2319 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5226.6263
2025-09-30 | 5371.7979 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5414.3376
2025-09-30 | 5125.5732 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5516.7115
2025-09-30 | 4732.5371 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5380.8074
2025-09-30 | 4095.6079 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4999.3744
2025-09-30 | 3502.3989 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4529.1806
2025-09-30 | 3147.9829 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4141.7247
2025-10-01 | 2957.8411 | 10.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.9769
2025-10-01 | 2837.075 | 9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3653.0034
2025-10-01 | 2737.5701 | 9.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3590.2954
2025-10-01 | 2873.282 | 10.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3651.2197
2025-10-01 | 3095.1021 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3907.2765
2025-10-01 | 3468.4741 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4303.0401
2025-10-01 | 3813.304 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4697.8874
2025-10-01 | 4005.655 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4971.9118
2025-10-01 | 3921.2129 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4964.1826
2025-10-01 | 3831.9839 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4885.2954
2025-10-01 | 3802.7461 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4705.6332
2025-10-01 | 3827.0161 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4628.471
2025-10-01 | 3719.5229 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4240.845
2025-10-01 | 3701.4929 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4156.4997
2025-10-01 | 3838.8611 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4033.7835
2025-10-01 | 4415.6812 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431.4541
2025-10-01 | 4961.4932 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5058.1742
2025-10-01 | 4978.8662 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5402.6313
2025-10-01 | 5165.5698 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5645.3441
2025-10-01 | 5038.6172 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5791.7194
2025-10-01 | 4575.8428 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5611.8139
2025-10-01 | 4047.0291 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5131.3781
2025-10-01 | 3515.791 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4639.1838
2025-10-01 | 3197.7859 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4548.7363
2025-10-02 | 2942.845 | 11.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151.9798
2025-10-02 | 2836.2971 | 13.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115.0166
2025-10-02 | 2794.2661 | 15.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4228.3136
2025-10-02 | 2876.927 | 14.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4157.2342
2025-10-02 | 3173.7229 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4292.2875
2025-10-02 | 3629.106 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4677.0508
2025-10-02 | 4088.5181 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5060.8978
2025-10-02 | 4197.2568 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5235.9193
2025-10-02 | 3990.7229 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5107.1867
2025-10-02 | 3794.9771 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4907.2961
2025-10-02 | 3776.1799 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4650.6316
2025-10-02 | 3741.0481 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4430.4654
2025-10-02 | 3716.645 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.8438
2025-10-02 | 3706.5339 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3980.4947
2025-10-02 | 3889.738 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3989.7823
2025-10-02 | 4474.2832 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4438.8796
2025-10-02 | 4902.9438 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4962.8842
2025-10-02 | 4979.6528 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5292.6282
2025-10-02 | 5205.0439 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5733.3467
2025-10-02 | 5137.1509 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5758.7184
2025-10-02 | 4658.3628 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5512.8111
2025-10-02 | 4104.335 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5120.3778
2025-10-02 | 3576.134 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4540.1809
2025-10-02 | 3208.854 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4229.7272
2025-10-03 | 3003.665 | 9.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3876.9719
2025-10-03 | 2874.1299 | 11.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3961.0122
2025-10-03 | 2828.811 | 11.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3821.302
2025-10-03 | 2861.665 | 11.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3761.2229
2025-10-03 | 3132.4661 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.2775
2025-10-03 | 3574.3181 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4281.0395
2025-10-03 | 4005.803 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4829.8912
2025-10-03 | 4178.1621 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5015.9131
2025-10-03 | 4055.106 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4854.1795
2025-10-03 | 3902.075 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4489.2842
2025-10-03 | 3869.2339 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4155.6175
2025-10-03 | 3925.697 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4570.4462
2025-10-03 | 3896.7009 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5423.384
2025-10-03 | 3923.6531 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5875.0309
2025-10-03 | 4143.2651 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6401.8848
2025-10-03 | 4626.1548 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6935.4098
2025-10-03 | 4995.4248 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7275.8459
2025-10-03 | 4866.3882 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6985.3081
2025-10-03 | 4943.0908 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6079.1723
2025-10-03 | 4832.3618 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5572.2647
2025-10-03 | 4513.2568 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 4973.7958
2025-10-03 | 4097.8638 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4592.3628
2025-10-03 | 3606.3 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4001.1656
2025-10-03 | 3265.5869 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3624.71
2025-10-04 | 2973.9319 | 4.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3627.4313
2025-10-04 | 2815.7549 | 4.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.4638
2025-10-04 | 2763.9929 | 4.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3285.7533
2025-10-04 | 2764.8501 | 4.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3324.6769
2025-10-04 | 2848.918 | 5.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3503.7316
2025-10-04 | 3070.8369 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3910.4955
2025-10-04 | 3582.1919 | 7.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4459.3472
2025-10-04 | 4233.1768 | 5.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4634.3687
2025-10-04 | 4605.457 | 2.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4527.6367
2025-10-04 | 4817.0601 | 0 | 1.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4805.0239
2025-10-04 | 4944.0132 | 0 | 3.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.2089
2025-10-04 | 5009.3359 | 0 | 5.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6280.7542
2025-10-04 | 5030.605 | 0 | 6.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6766.5552
2025-10-04 | 5106.5171 | 0 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7254.9157
2025-10-04 | 5309.6948 | 0 | 8.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7451.3465
2025-10-04 | 5674.0781 | 0 | 9.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7984.8715
2025-10-04 | 6026.418 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8105.0256
2025-10-04 | 5692.938 | 0 | 6.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7961.3424
2025-10-04 | 5557.9419 | 0 | 5.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7312.2024
2025-10-04 | 5277.3628 | 0 | 3.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6621.7264
2025-10-04 | 4914.188 | 0 | 1.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5836.1142
2025-10-04 | 4464.0171 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4933.5401
2025-10-04 | 3939.459 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4089.0599
2025-10-04 | 3519.802 | 0.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3551.1744
2025-10-05 | 3184.5439 | 1.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3297.4219
2025-10-05 | 2989.0681 | 1.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3150.4556
2025-10-05 | 2855.1919 | 2.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3087.7476
2025-10-05 | 2834.5659 | 2.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.6704
2025-10-05 | 2834.6389 | 3.1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3283.7253
2025-10-05 | 3036.356 | 4.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3756.4911
2025-10-05 | 3538.334 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.3381
2025-10-05 | 4197.3789 | 3.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4414.3624
2025-10-05 | 4788.2412 | 0 | 0.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4458.1979
2025-10-05 | 5170.6938 | 0 | 3.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5576.0112
2025-10-05 | 5498.7139 | 0 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6574.6236
2025-10-05 | 5753.1948 | 0 | 8.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492.3056
2025-10-05 | 5998.022 | 0 | 10.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8088.2476
2025-10-05 | 6211.5029 | 0 | 11.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8356.3261
2025-10-05 | 6427.7881 | 0 | 11.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8552.7568
2025-10-05 | 6922.0591 | 0 | 11.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8902.7134
2025-10-05 | 7177.0112 | 0 | 10.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8949.4402
2025-10-05 | 6869.416 | 0 | 8.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8622.1886
2025-10-05 | 6632.8218 | 0 | 6.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7716.0529
2025-10-05 | 6082.4678 | 0 | 4.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6915.4358
2025-10-05 | 5393.416 | 0 | 2.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6203.251
2025-10-05 | 4721.2339 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5080.3948
2025-10-05 | 4040.752 | 0.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4026.6328
2025-10-05 | 3579.2749 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3672.1779
2025-10-06 | 3238.1919 | 1.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3062.9487
2025-10-06 | 3095.4871 | 2.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2937.983
2025-10-06 | 2986.8411 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2875.2751
2025-10-06 | 2996.8101 | 4.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3035.2022
2025-10-06 | 3193.1021 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3093.2533
2025-10-06 | 3506.085 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3478.0166
2025-10-06 | 3832.323 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3949.8661
2025-10-06 | 4093.615 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4212.8902
2025-10-06 | 4085.074 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4183.1604
2025-10-06 | 4235.8101 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4856.9726
2025-10-06 | 4477.5591 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5965.726
2025-10-06 | 4740.5601 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7066.9764
2025-10-06 | 4887.395 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7699.6321
2025-10-06 | 5064.3472 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7747.4285
2025-10-06 | 5403.6211 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7943.8593
2025-10-06 | 6032.9858 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8110.2475
2025-10-06 | 6517.1558 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8267.1153
2025-10-06 | 6346.7231 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7829.7227
2025-10-06 | 6199.9692 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7180.5827
2025-10-06 | 5966.4121 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6526.8204
2025-10-06 | 5423.1362 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5814.6355
2025-10-06 | 4683.0508 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5132.3434
2025-10-06 | 4023.1201 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4324.5769
2025-10-06 | 3601.137 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3559.1218
2025-10-07 | 3279.054 | 0.4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2919.9447
2025-10-07 | 3147.6641 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2662.9752
2025-10-07 | 3021.6299 | 1.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2688.2697
2025-10-07 | 2994.8459 | 2.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2749.194
2025-10-07 | 3198.106 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2917.2483
2025-10-07 | 3530.5959 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3214.0091
2025-10-07 | 3838.3779 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3520.8539
2025-10-07 | 4048.272 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3816.8789
2025-10-07 | 4053.999 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4326.5781
2025-10-07 | 4122.0332 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4225.2766
2025-10-07 | 4207.0229 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.6166
2025-10-07 | 4245.1958 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093.1684
2025-10-07 | 4189.168 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4358.6873
2025-10-07 | 4221.0688 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4076.0606
2025-10-07 | 4441.7949 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.7777
2025-10-07 | 5143.957 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4549.0206
2025-10-07 | 5743.0381 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5036.3115
2025-10-07 | 5796.0542 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5358.6301
2025-10-07 | 5733.6929 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5447.3385
2025-10-07 | 5554.043 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5494.7109
2025-10-07 | 4966.3638 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5380.8074
2025-10-07 | 4386.5332 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4834.3697
2025-10-07 | 3722.541 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4342.1753
2025-10-07 | 3313.542 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3822.7156
2025-10-08 | 3045.8049 | 5.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480.9606
2025-10-08 | 2858.7791 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432.9971
2025-10-08 | 2826.3069 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3315.2876
2025-10-08 | 2814.8701 | 7.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3310.21
2025-10-08 | 3039.4771 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3676.27
2025-10-08 | 3499.3049 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4061.0332
2025-10-08 | 3890.262 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4433.8799
2025-10-08 | 4092.3401 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4784.9065
2025-10-08 | 3972.103 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4667.1741
2025-10-08 | 3926.5701 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4676.2895
2025-10-08 | 3938.2991 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4694.6329
2025-10-08 | 3967.135 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4683.4726
2025-10-08 | 3890.2429 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4493.8522
2025-10-08 | 3927.7781 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4475.5088
2025-10-08 | 4069.668 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4715.8029
2025-10-08 | 4602.5181 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5091.4729
2025-10-08 | 5132.8379 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5674.1918
2025-10-08 | 5142.0928 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5908.6457
2025-10-08 | 5434.8721 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6173.3592
2025-10-08 | 5278.228 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6220.7316
2025-10-08 | 4745.1079 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6117.8284
2025-10-08 | 4283.4229 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5637.3925
2025-10-08 | 3701.606 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5046.1954
2025-10-08 | 3333.552 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4746.742
2025-10-09 | 3083.627 | 13.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4360.9857
2025-10-09 | 2940.97 | 13.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4170.0181
2025-10-09 | 2914.334 | 13.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4063.3089
2025-10-09 | 3075.21 | 14.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4069.2316
2025-10-09 | 3318.531 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4248.2863
2025-10-09 | 3809.198 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4655.0502
2025-10-09 | 4193.5049 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5115.8994
2025-10-09 | 4404.0479 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5378.9234
2025-10-09 | 4372.1089 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5448.1964
2025-10-09 | 4123.6782 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5336.3083
2025-10-09 | 4069.948 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5178.6466
2025-10-09 | 4021.23 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5090.4842
2025-10-09 | 3884.2251 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4856.8626
2025-10-09 | 3853.0701 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4750.5167
2025-10-09 | 4032.8069 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4803.8055
2025-10-09 | 4571.3101 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5157.4748
2025-10-09 | 5133.9028 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5740.1937
2025-10-09 | 5348.9302 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6117.6517
2025-10-09 | 5537.958 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6239.3611
2025-10-09 | 5567.7021 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6682.7447
2025-10-09 | 5048.769 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6601.8421
2025-10-09 | 4435.5952 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6011.4032
2025-10-09 | 3918.3689 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5497.2082
2025-10-09 | 3580.822 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5142.7532
2025-10-10 | 3401.155 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4635.9935
2025-10-10 | 3251.469 | 16.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4467.0266
2025-10-10 | 3205.9871 | 16.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4371.3177
2025-10-10 | 3299.3069 | 17.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4443.2423
2025-10-10 | 3644.884 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4622.2969
2025-10-10 | 4131.9521 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.0608
2025-10-10 | 4601.79 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5533.9113
2025-10-10 | 4772.373 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5829.9363
2025-10-10 | 4693.4229 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5657.2023
2025-10-10 | 4514.499 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5457.3117
2025-10-10 | 4377.5332 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5101.6445
2025-10-10 | 4324.0688 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4771.4751
2025-10-10 | 4211.2759 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4537.8535
2025-10-10 | 4142.5698 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4299.5038
2025-10-10 | 4171.814 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4330.792
2025-10-10 | 4562.7461 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4706.4619
2025-10-10 | 5030.2231 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5289.1808
2025-10-10 | 5138.248 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5633.6379
2025-10-10 | 5397.3721 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5909.3517
2025-10-10 | 5324.4219 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6033.7263
2025-10-10 | 4858.8721 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5886.8218
2025-10-10 | 4342.2769 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5560.3903
2025-10-10 | 3908.637 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4903.1913
2025-10-10 | 3459.7419 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4361.731
2025-10-11 | 3231.0779 | 9.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4188.4473
2025-10-11 | 3134.2271 | 9.5 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3986.4794
2025-10-11 | 3082.5439 | 10.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3945.7721
2025-10-11 | 3075.896 | 10.3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3929.6942
2025-10-11 | 3234.5559 | 11.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4196.7513
2025-10-11 | 3456.2119 | 11.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4515.5127
2025-10-11 | 4053.718 | 11.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4910.36
2025-10-11 | 4700.9678 | 10.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5261.3866
2025-10-11 | 5020.3569 | 9.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5297.6586
2025-10-11 | 5255.3511 | 5.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4943.7636
2025-10-11 | 5235.3931 | 3.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4742.1007
2025-10-11 | 5154.2471 | 2.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4565.9358
2025-10-11 | 4935.5078 | 1.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4420.3166
2025-10-11 | 4930.3872 | 1.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4335.9714
2025-10-11 | 4899.916 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4378.2598
2025-10-11 | 5006.3032 | 0.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4709.9285
2025-10-11 | 5244.2979 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5292.6474
2025-10-11 | 5222.1118 | 2.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5747.1076
2025-10-11 | 5204.6401 | 5.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6022.8214
2025-10-11 | 5024.3691 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6037.1929
2025-10-11 | 4631.7402 | 8.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6088.294
2025-10-11 | 4173.7319 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5629.8588
2025-10-11 | 3702.6521 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5060.6623
2025-10-11 | 3353.2991 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4508.2017
2025-10-12 | 3100.7791 | 8.8 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4122.4454
2025-10-12 | 2980.2241 | 10.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4118.4832
2025-10-12 | 2894.0691 | 9.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3846.7692
2025-10-12 | 2953.0759 | 11.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4061.6979
2025-10-12 | 3050.2329 | 10.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4086.7482
2025-10-12 | 3279.9741 | 10.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4427.5102
2025-10-12 | 3887.563 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.3572
2025-10-12 | 4616.3979 | 11.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5305.3878
2025-10-12 | 5102.561 | 8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5154.6545
2025-10-12 | 5364.8418 | 5.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4965.7642
2025-10-12 | 5557.8018 | 3.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4753.101
2025-10-12 | 5508.1421 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4444.9323
2025-10-12 | 5427.2979 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4306.7387
2025-10-12 | 5310.769 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4684.9582
2025-10-12 | 5203.5342 | 0 | 1.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4881.3889
2025-10-12 | 5325.6631 | 0 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.7771
2025-10-12 | 5368.5381 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.6449
2025-10-12 | 5232.6118 | 1.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5604.1036
2025-10-12 | 5153.4761 | 3.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5846.8164
2025-10-12 | 4967.1489 | 4.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5949.1904
2025-10-12 | 4617.1162 | 5.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5747.2843
2025-10-12 | 4199.3628 | 5.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5266.8485
2025-10-12 | 3688.3311 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4719.6526
2025-10-12 | 3307.1799 | 7.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4310.196
2025-10-13 | 3043.614 | 8.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3810.97
2025-10-13 | 2922.137 | 9.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3741.0059
2025-10-13 | 2837.4031 | 9.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3557.2945
2025-10-13 | 2819.771 | 11.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3739.2222
2025-10-13 | 2944.958 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.2718
2025-10-13 | 3177.5449 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4028.0323
2025-10-13 | 3635.873 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4510.8821
2025-10-13 | 4343.6958 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4872.909
2025-10-13 | 4934.0981 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4832.1788
2025-10-13 | 5394.1392 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4731.2911
2025-10-13 | 5743.231 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4650.6316
2025-10-13 | 5841.7119 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4386.4641
2025-10-13 | 5633.834 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4273.846
2025-10-13 | 5391.9692 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4178.5004
2025-10-13 | 5548.2969 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4264.7901
2025-10-13 | 5691.2598 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4695.4616
2025-10-13 | 5797.48 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5322.1818
2025-10-13 | 5688.2969 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5655.6385
2025-10-13 | 5620.998 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5821.3492
2025-10-13 | 5366.5801 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5725.7175
2025-10-13 | 4793.394 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5468.8099
2025-10-13 | 4228.2339 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 4944.3728
2025-10-13 | 3668.1631 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4386.1766
2025-10-13 | 3295.583 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4009.721
2025-10-14 | 3062.074 | 7.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678.9663
2025-10-14 | 2954.074 | 7.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3532
2025-10-14 | 2892.397 | 8.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.291
2025-10-14 | 2946.9751 | 8.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3431.2135
2025-10-14 | 3240.8889 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3555.2665
2025-10-14 | 3625.2729 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3863.0276
2025-10-14 | 3986.8469 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4279.8755
2025-10-14 | 4168.4438 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4597.9012
2025-10-14 | 4129.1328 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4744.1763
2025-10-14 | 4108.606 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4687.2898
2025-10-14 | 4053.2639 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4595.63
2025-10-14 | 4074.0471 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4331.4626
2025-10-14 | 3942.3059 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4108.8412
2025-10-14 | 3888.843 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3958.4941
2025-10-14 | 3985.2571 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4235.7777
2025-10-14 | 4524.2368 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4732.589
2025-10-14 | 5101.2432 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5293.3073
2025-10-14 | 5178.564 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5259.6272
2025-10-14 | 5338.374 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5447.3385
2025-10-14 | 5220.9888 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5538.7121
2025-10-14 | 4821.0771 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5622.8143
2025-10-14 | 4145.8862 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5043.3756
2025-10-14 | 3596.3269 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4111.1687
2025-10-14 | 3272.855 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3800.715
2025-10-15 | 3066.6311 | 6.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3634.965
2025-10-15 | 2935.8811 | 7.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3465.9981
2025-10-15 | 2856.0759 | 8.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3436.291
2025-10-15 | 2977.739 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3508.2157
2025-10-15 | 3259.0339 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742.2718
2025-10-15 | 3733.259 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4116.0348
2025-10-15 | 4055.9729 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4543.8831
2025-10-15 | 4208.5659 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5004.9128
2025-10-15 | 4219.0371 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5195.1892
2025-10-15 | 4079.7739 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5050.3001
2025-10-15 | 4020.8789 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4969.6407
2025-10-15 | 3999.4141 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4859.4776
2025-10-15 | 3885.2629 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4614.8557
2025-10-15 | 3810.199 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4464.5085
2025-10-15 | 3924.0061 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.7976
2025-10-15 | 4559.644 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5036.4713
2025-10-15 | 5157.645 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5652.1912
2025-10-15 | 5296.7158 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5996.6482
2025-10-15 | 5511.6172 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6173.3592
2025-10-15 | 5434.7832 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6330.7347
2025-10-15 | 4977.0601 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6216.8312
2025-10-15 | 4517.4302 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5813.3975
2025-10-15 | 3884.374 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5112.1972
2025-10-15 | 3563.2329 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4724.7413
2025-10-16 | 3326.303 | 12.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4261.9829
2025-10-16 | 3250.45 | 12.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4005.0134
2025-10-16 | 3181.5601 | 12.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3931.3051
2025-10-16 | 3321.2849 | 15.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4179.2348
2025-10-16 | 3662.064 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4380.29
2025-10-16 | 4131.562 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.0561
2025-10-16 | 4481.9399 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5291.9044
2025-10-16 | 4590.3472 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5477.9262
2025-10-16 | 4457.0239 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5404.1951
2025-10-16 | 4276.167 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5215.3048
2025-10-16 | 4129.6172 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5112.6448
2025-10-16 | 4160.9072 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4925.4795
2025-10-16 | 4007.0969 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4636.8563
2025-10-16 | 4001.519 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4486.5091
2025-10-16 | 4072.8391 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4528.7976
2025-10-16 | 4672.1499 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4893.4673
2025-10-16 | 5235.1431 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5487.1865
2025-10-16 | 5349.9731 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5853.6442
2025-10-16 | 5666.1821 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5964.3532
2025-10-16 | 5578.7109 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6055.7269
2025-10-16 | 5149.6699 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5919.8227
2025-10-16 | 4609.834 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5483.3881
2025-10-16 | 4017.5779 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4958.1928
2025-10-16 | 3636.551 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4548.7363
2025-10-17 | 3463.9331 | 12.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4294.9838
2025-10-17 | 3389.717 | 13.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4137.0172
2025-10-17 | 3382.125 | 14.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4140.3111
2025-10-17 | 3479.4709 | 15.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4256.237
2025-10-17 | 3805.647 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4633.2972
2025-10-17 | 4301.3989 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4919.0577
2025-10-17 | 4649.7349 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5258.9034
2025-10-17 | 4783.4419 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5730.9334
2025-10-17 | 4630.0532 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5492.1976
2025-10-17 | 4464.7139 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5303.3074
2025-10-17 | 4244.543 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.6423
2025-10-17 | 4194.2178 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4958.4804
2025-10-17 | 4078.812 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4790.8607
2025-10-17 | 4040.0061 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4662.5142
2025-10-17 | 4075.7319 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4726.8033
2025-10-17 | 4612.9849 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5047.4717
2025-10-17 | 5193.5972 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5663.1915
2025-10-17 | 5425.8198 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.6495
2025-10-17 | 5341.3599 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6184.3595
2025-10-17 | 5134.396 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6319.7344
2025-10-17 | 4842.771 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5963.824
2025-10-17 | 4330.0801 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5395.3856
2025-10-17 | 3878.1699 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4771.1875
2025-10-17 | 3531.478 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4262.7282
2025-10-18 | 3324.8279 | 10.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4287.4501
2025-10-18 | 3183.5549 | 10.1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4052.4813
2025-10-18 | 3139.918 | 10.2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3945.7721
2025-10-18 | 3141.1489 | 9.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3885.6929
2025-10-18 | 3263.2471 | 9.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4009.746
2025-10-18 | 3468.1589 | 9.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4328.5074
2025-10-18 | 3989.7839 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4723.3547
2025-10-18 | 4603.957 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5063.3809
2025-10-18 | 5028.4609 | 8.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5220.6564
2025-10-18 | 5191.9521 | 7.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5130.7689
2025-10-18 | 5237.1768 | 6.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5039.1092
2025-10-18 | 5051.062 | 3.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4763.9414
2025-10-18 | 4751.4902 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4453.3176
2025-10-18 | 4593.1582 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4291.9701
2025-10-18 | 4599.6592 | 0.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4345.2589
2025-10-18 | 4870.854 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4786.9307
2025-10-18 | 5208.835 | 1.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5325.6484
2025-10-18 | 5287.4238 | 1.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5637.1045
2025-10-18 | 5223.1021 | 4.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5901.818
2025-10-18 | 4974.5132 | 4.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5905.1891
2025-10-18 | 4550.2319 | 6.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5857.2874
2025-10-18 | 4207.0488 | 6.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5387.8519
2025-10-18 | 3712.6189 | 6.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4741.6532
2025-10-18 | 3332.0359 | 7.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4365.1976
2025-10-19 | 2740.4661 | 8.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4045.4432
2025-10-19 | 2864.77 | 8.4 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3865.476
2025-10-19 | 2784.1731 | 8.9 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3802.768
2025-10-19 | 2763.7571 | 9.7 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3863.6923
2025-10-19 | 2819.9351 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4042.7469
2025-10-19 | 3009.271 | 10.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4383.5089
2025-10-19 | 3472.7639 | 10.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4811.3572
2025-10-19 | 4082.0391 | 9.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5107.3822
2025-10-19 | 4534.2178 | 7.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5143.6542
2025-10-19 | 4753.3501 | 4.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.7611
2025-10-19 | 4941.915 | 1.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4478.0932
2025-10-19 | 5033.3838 | 0 | 2.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5142.6301
2025-10-19 | 5079.6182 | 0 | 4.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6032.2816
2025-10-19 | 5129.2612 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6594.0695
2025-10-19 | 5222.6602 | 0 | 7.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7157.637
2025-10-19 | 5548.083 | 0 | 7.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7250.5979
2025-10-19 | 5799.3618 | 0 | 6.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7627.7477
2025-10-19 | 5662.7012 | 0 | 5.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7447.3509
2025-10-19 | 5447.6431 | 0 | 4.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7091.9204
2025-10-19 | 5187.9341 | 0 | 2.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6291.3033
2025-10-19 | 4758.7222 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6276.6784
2025-10-19 | 4210.3652 | 0 | 3.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5777.9547
2025-10-19 | 3637.7451 | 0 | 2.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5006.9018
2025-10-19 | 3234.147 | 0 | 2.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4351.5878
2025-10-20 | 2995.863 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3610.217
2025-10-20 | 2804.5071 | 0 | 0.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2773.1162
2025-10-20 | 2744.542 | 0.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2633.2682
2025-10-20 | 2749.697 | 1.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2727.1934
2025-10-20 | 2962.968 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3005.2508
2025-10-20 | 3286.5979 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3379.0138
2025-10-20 | 3574.259 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3806.8621
2025-10-20 | 3915.561 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4201.8899
2025-10-20 | 4060.2949 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4370.1657
2025-10-20 | 4070.407 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4335.2798
2025-10-20 | 4268.9922 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4331.6225
2025-10-20 | 4356.6582 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4683.4726
2025-10-20 | 4247.9409 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4680.8575
2025-10-20 | 4265.4141 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4662.5142
2025-10-20 | 4562.9902 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4704.8026
2025-10-20 | 5144.0889 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5113.4735
2025-10-20 | 5684.3589 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5696.1924
2025-10-20 | 5115.2822 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5952.647
2025-10-20 | 3468.801 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5997.3542
2025-10-20 | 5071.7759 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5989.725
2025-10-20 | 5007.0601 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5754.818
2025-10-20 | 4405.2388 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5230.3809
2025-10-20 | 3804.0271 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4639.1838
2025-10-20 | 3431.2209 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4196.7263
2025-10-21 | 3166.1951 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3865.9716
2025-10-21 | 3019.3879 | 8.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3642.0031
2025-10-21 | 2970.145 | 8.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524.2935
2025-10-21 | 3056.0559 | 9.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3530.2163
2025-10-21 | 3344.854 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3764.2725
2025-10-21 | 3747.063 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4083.0339
2025-10-21 | 4155.8599 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4543.8831
2025-10-21 | 4275.2871 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4938.9109
2025-10-21 | 4170.5161 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5063.1854
2025-10-21 | 4021.1899 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4984.2983
2025-10-21 | 4036.4751 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4782.6354
2025-10-21 | 3954.835 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4716.4735
2025-10-21 | 3905.739 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4405.8497
2025-10-21 | 3846.144 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4365.5057
2025-10-21 | 4108.731 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4517.7973
2025-10-21 | 4938.771 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4981.4698
2025-10-21 | 5564.9082 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5586.1893
2025-10-21 | 5508.6338 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5897.6454
2025-10-21 | 5580.2759 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5909.3517
2025-10-21 | 5371.5688 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5890.7222
2025-10-21 | 4842.96 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 5633.8146
2025-10-21 | 4255.2632 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5208.3803
2025-10-21 | 3704.4419 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4771.1875
2025-10-21 | 3377.856 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4152.725
2025-10-22 | 3129.688 | 9.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3942.9738
2025-10-22 | 3012.979 | 9.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3708.005
2025-10-22 | 3017.946 | 10.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3678.2979
2025-10-22 | 3109.262 | 11.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3761.2229
2025-10-22 | 3369.803 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.2747
2025-10-22 | 3815.9509 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4303.0401
2025-10-22 | 4118.9302 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4697.8874
2025-10-22 | 4310.3599 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5048.914
2025-10-22 | 4327.4209 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5074.1857
2025-10-22 | 4394.5469 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5028.2995
2025-10-22 | 4443.709 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5035.6426
2025-10-22 | 4446.5981 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5057.4833
2025-10-22 | 4234.8652 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4845.8622
2025-10-22 | 4134.4888 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4739.5164
2025-10-22 | 4235.3799 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4891.808
2025-10-22 | 4931.6089 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5124.4738
2025-10-22 | 5621.9141 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5608.1899
2025-10-22 | 5693.0239 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6051.6498
2025-10-22 | 5769.2549 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6195.3598
2025-10-22 | 5601.644 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6242.7322
2025-10-22 | 5115.7578 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6117.8284
2025-10-22 | 4494.8481 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5538.3897
2025-10-22 | 3959.7849 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5068.196
2025-10-22 | 3596.6279 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4548.7363
2025-10-23 | 3355.7209 | 11.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4162.9801
2025-10-23 | 3232.5581 | 11.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3972.0125
2025-10-23 | 3214.5559 | 11.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3821.302
2025-10-23 | 3258.7051 | 11.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3794.2238
2025-10-23 | 3531.689 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3929.2772
2025-10-23 | 4012.062 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4314.0405
2025-10-23 | 4333.9351 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4697.8874
2025-10-23 | 4568.4248 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5037.9137
2025-10-23 | 4442.5562 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5206.1895
2025-10-23 | 4451.9229 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5193.3042
2025-10-23 | 4411.6318 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200.6473
2025-10-23 | 4358.5161 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5233.4883
2025-10-23 | 4295.668 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4977.866
2025-10-23 | 4237.4761 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4838.5192
2025-10-23 | 4410.5859 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4957.8098
2025-10-23 | 4917.9932 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5333.4798
2025-10-23 | 5546.981 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5883.1977
2025-10-23 | 5725.5332 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6326.6576
2025-10-23 | 5798.7461 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6261.3617
2025-10-23 | 5711.2251 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6407.7369
2025-10-23 | 5181.877 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6238.8318
2025-10-23 | 4648.8691 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5945.4013
2025-10-23 | 4091.167 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5244.201
2025-10-23 | 3703.53 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4757.7423
2025-10-24 | 3478.5591 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4415.9873
2025-10-24 | 3372.1311 | 14.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4258.0206
2025-10-24 | 3324.5601 | 13.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4074.3092
2025-10-24 | 3382.9871 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4168.2345
2025-10-24 | 3698.7681 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4248.2863
2025-10-24 | 4165.646 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4567.0477
2025-10-24 | 4493.6431 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4972.8953
2025-10-24 | 4734.1279 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5312.9215
2025-10-24 | 4612.8809 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5459.1967
2025-10-24 | 4537.5332 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5413.3105
2025-10-24 | 4518.4331 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5343.6513
2025-10-24 | 4571.4268 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5266.4892
2025-10-24 | 4511.8628 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5186.872
2025-10-24 | 4392.126 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4959.5226
2025-10-24 | 4626.2529 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5100.8139
2025-10-24 | 5099.749 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5498.4845
2025-10-24 | 5653.5918 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6059.2027
2025-10-24 | 5791.7319 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.6579
2025-10-24 | 5766.894 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6404.3658
2025-10-24 | 5524.1431 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6385.7363
2025-10-24 | 5132.1631 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6150.8293
2025-10-24 | 4704.4102 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5681.3938
2025-10-24 | 4356.0298 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5024.1947
2025-10-24 | 3941.6499 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4592.7376
2025-10-25 | 3662.344 | 12 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4474.4554
2025-10-25 | 3472.186 | 12.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4283.4879
2025-10-25 | 3456.8149 | 12.6 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4209.7796
2025-10-25 | 3483.8191 | 14.8 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4424.7083
2025-10-25 | 3702.427 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4570.7619
2025-10-25 | 4058.751 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4999.5265
2025-10-25 | 4522.0732 | 17.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5636.3807
2025-10-25 | 5076.3398 | 16.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5888.4044
2025-10-25 | 5474.3779 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5803.673
2025-10-25 | 5590.4722 | 13.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5790.7878
2025-10-25 | 5702.8799 | 11.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600.1252
2025-10-25 | 5556.0562 | 11.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5577.9646
2025-10-25 | 5272.8218 | 9.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5311.342
2025-10-25 | 5153.4492 | 9.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.9961
2025-10-25 | 5215.3359 | 9.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5258.2849
2025-10-25 | 5668.3491 | 9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5633.9549
2025-10-25 | 5961.8018 | 10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6304.6763
2025-10-25 | 6066.1191 | 10.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6616.1324
2025-10-25 | 5936.4028 | 12.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6825.8443
2025-10-25 | 5660.9131 | 14.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6972.2195
2025-10-25 | 5305.1372 | 14.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6748.3128
2025-10-25 | 4953.1768 | 14.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6278.8773
2025-10-25 | 4571.9468 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5852.6848
2025-10-25 | 4190.0752 | 17.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5476.2292
2025-10-26 | 3909.1289 | 18.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5145.4746
2025-10-26 | 3780.9729 | 17.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888.5051
2025-10-26 | 3739.8921 | 18.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4847.7978
2025-10-26 | 3768.011 | 18.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4798.7189
2025-10-26 | 3949.407 | 17.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4878.7707
2025-10-26 | 4234.854 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5186.5318
2025-10-26 | 4718.0601 | 16.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5460.3757
2025-10-26 | 5289.4692 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5943.406
2025-10-26 | 5576.5132 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5946.6771
2025-10-26 | 5742.2969 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5933.7918
2025-10-26 | 5852.8569 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5842.1321
2025-10-26 | 5809.0781 | 12.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5709.9684
2025-10-26 | 5825.043 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5553.3489
2025-10-26 | 5709.8618 | 10.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5370.0008
2025-10-26 | 5756.2988 | 11.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5522.2924
2025-10-26 | 6302.585 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5853.9611
2025-10-26 | 6613.6641 | 10.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6403.6791
2025-10-26 | 6638.3281 | 12.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6792.1374
2025-10-26 | 6465.022 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6946.8477
2025-10-26 | 6209.2109 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6939.2186
2025-10-26 | 5527.3301 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6869.3163
2025-10-26 | 4986.854 | 15.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6366.8798
2025-10-26 | 4524.9551 | 17.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5907.6864
2025-10-26 | 4123.6611 | 17.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5399.2271
2025-10-27 | 3560.4431 | 18.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4867.0001
2025-10-27 | 3326.137 | 17.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4577.0297
2025-10-27 | 3236.926 | 18.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4558.323
2025-10-27 | 3254.6321 | 19.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4630.2476
2025-10-27 | 3446.3511 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600.2963
2025-10-27 | 3785.196 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5106.063
2025-10-27 | 4195.9419 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5357.9062
2025-10-27 | 4624.0601 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5851.9369
2025-10-27 | 4816.4839 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5723.2042
2025-10-27 | 5024.2861 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5534.3139
2025-10-27 | 5205.9019 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.6523
2025-10-27 | 5355.1709 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200.4873
2025-10-27 | 5285.231 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944.8651
2025-10-27 | 5301.9438 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4783.5176
2025-10-27 | 5552.2988 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4847.8067
2025-10-27 | 6038.1021 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5146.4745
2025-10-27 | 6522.625 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5751.194
2025-10-27 | 6403.9951 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6183.6536
2025-10-27 | 6322.1851 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6283.3623
2025-10-27 | 6124.8252 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6517.74
2025-10-27 | 5547.5151 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6590.8418
2025-10-27 | 4846.3862 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6209.4088
2025-10-27 | 4214.8052 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5387.2051
2025-10-27 | 3881.793 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4933.7473
2025-10-28 | 3820.387 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4745.9967
2025-10-28 | 3759.7629 | 17.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4588.03
2025-10-28 | 3681.5959 | 17.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4437.3196
2025-10-28 | 3829.78 | 17.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4476.2432
2025-10-28 | 4148.6831 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4534.2944
2025-10-28 | 4626.8008 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4875.0564
2025-10-28 | 4894.6958 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5258.9034
2025-10-28 | 5025.416 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5686.9322
2025-10-28 | 4807.0259 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5613.2011
2025-10-28 | 4588.4048 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5358.3089
2025-10-28 | 4492.416 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5123.6451
2025-10-28 | 4431.311 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4969.4807
2025-10-28 | 4210.0039 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4746.8594
2025-10-28 | 4198.1592 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4585.512
2025-10-28 | 4376.7729 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4605.7998
2025-10-28 | 5022.2842 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4992.4701
2025-10-28 | 5671.7119 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5619.1902
2025-10-28 | 5878.4189 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6106.6514
2025-10-28 | 6007.6709 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6371.3648
2025-10-28 | 5944.0459 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6363.7357
2025-10-28 | 5443.4292 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6205.8309
2025-10-28 | 4789.2139 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5967.4019
2025-10-28 | 4318.0869 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5310.2029
2025-10-28 | 3986.894 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4790.7432
2025-10-29 | 3741.843 | 15.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4602.9926
2025-10-29 | 3666.3789 | 16.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4467.0266
2025-10-29 | 3705.6599 | 16.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4349.317
2025-10-29 | 3787.2 | 16.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4377.2404
2025-10-29 | 4160.4312 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4666.2982
2025-10-29 | 4712.2749 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4853.0558
2025-10-29 | 5054.998 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5258.9034
2025-10-29 | 5117.6309 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5598.9297
2025-10-29 | 4911.252 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5580.2002
2025-10-29 | 4680.2349 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5402.3102
2025-10-29 | 4596.3252 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5156.646
2025-10-29 | 4411.0991 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5024.4823
2025-10-29 | 4206.9521 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4779.8604
2025-10-29 | 4057.6479 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4640.5135
2025-10-29 | 4255.5869 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4726.8033
2025-10-29 | 4775.2241 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5091.4729
2025-10-29 | 5472.3149 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5740.1937
2025-10-29 | 5764.3701 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6216.6545
2025-10-29 | 5961.2339 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6470.3676
2025-10-29 | 5900.2681 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6473.7388
2025-10-29 | 5431.6831 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6370.8356
2025-10-29 | 4923.332 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5857.3988
2025-10-29 | 4417.811 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5266.2016
2025-10-29 | 4039.29 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4801.7435
2025-10-30 | 3741.074 | 15.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4580.992
2025-10-30 | 3607.468 | 15.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4346.0232
2025-10-30 | 3584.448 | 15.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4283.3152
2025-10-30 | 3711.613 | 15.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4267.2373
2025-10-30 | 4061.1931 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4358.2894
2025-10-30 | 4539.9819 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4754.053
2025-10-30 | 4847.1489 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5159.9006
2025-10-30 | 5091.3472 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5466.9259
2025-10-30 | 5061.9521 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5613.2011
2025-10-30 | 5016.7139 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5655.3174
2025-10-30 | 5117.5288 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5651.6601
2025-10-30 | 5227.6489 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5651.5002
2025-10-30 | 5109.9858 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5538.882
2025-10-30 | 5134.8672 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5410.5355
2025-10-30 | 5468.061 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5463.8243
2025-10-30 | 6171.0381 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5828.4939
2025-10-30 | 6638.4702 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400.2125
2025-10-30 | 6686.8198 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6634.6664
2025-10-30 | 6510.9019 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6646.3727
2025-10-30 | 6301.3628 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6583.7419
2025-10-30 | 5792.0659 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6282.8331
2025-10-30 | 5063.5688 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5714.3947
2025-10-30 | 4440.7759 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5057.1957
2025-10-30 | 4134.7319 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4515.7354
2025-10-31 | 3810.2571 | 11.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4162.9801
2025-10-31 | 3693.0339 | 11.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3906.0106
2025-10-31 | 3611.5701 | 10.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744.2998
2025-10-31 | 3700.3579 | 10.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3706.2213
2025-10-31 | 3981.991 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3841.2747
2025-10-31 | 4487.0298 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4226.0379
2025-10-31 | 4778.959 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4653.8862
2025-10-31 | 4997.2109 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5070.9146
2025-10-31 | 5002.2529 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5261.1911
2025-10-31 | 5070.957 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5314.3077
2025-10-31 | 5176.6792 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5354.6517
2025-10-31 | 5123.228 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5354.4917
2025-10-31 | 5138.1968 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5285.8748
2025-10-31 | 5130.4331 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5322.533
2025-10-31 | 5426.0581 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5540.8264
2025-10-31 | 5994.4111 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6015.4992
2025-10-31 | 6215.1069 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6587.2178
2025-10-31 | 6030.5068 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6777.6705
2025-10-31 | 6088.208 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6723.3749
2025-10-31 | 6089.8701 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6649.7438
2025-10-31 | 5732.4072 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6392.8362
2025-10-31 | 5268.9878 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5835.3982
2025-10-31 | 4879.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5222.2004
2025-10-31 | 4500.8799 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4713.741
2025-11-01 | 4152.0278 | 13.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4606.4592
2025-11-01 | 3960.345 | 13.1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4382.4907
2025-11-01 | 3839.436 | 13.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4264.7812
2025-11-01 | 3889.4851 | 13.6 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4292.7045
2025-11-01 | 4026.137 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4559.7616
2025-11-01 | 4336.8931 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4889.5234
2025-11-01 | 4784.9692 | 15.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5339.3722
2025-11-01 | 5440.2749 | 15.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5745.4004
2025-11-01 | 5820.1318 | 14.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5869.6749
2025-11-01 | 6108.5029 | 13.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5812.7884
2025-11-01 | 6413.814 | 13.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5831.1317
2025-11-01 | 6454.5181 | 13.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5808.9712
2025-11-01 | 6277.9751 | 12.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5619.3508
2025-11-01 | 6081.0142 | 12.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5579.0068
2025-11-01 | 6080.3198 | 12.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5621.2952
2025-11-01 | 6380.4448 | 12.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6007.9655
2025-11-01 | 6685.7651 | 12.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6579.6841
2025-11-01 | 6568.1382 | 13.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6935.1415
2025-11-01 | 6340.377 | 15.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7100.8521
2025-11-01 | 6052.1748 | 15 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7060.222
2025-11-01 | 5648.9312 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6847.3156
2025-11-01 | 5185.8809 | 14.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6256.8767
2025-11-01 | 4839.5039 | 14.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5621.6783
2025-11-01 | 4503.6938 | 14.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5102.2186
2025-11-02 | 4194.0732 | 14.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4760.4636
2025-11-02 | 3897.3679 | 14.9 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4580.4963
2025-11-02 | 3814.282 | 14.7 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4440.7862
2025-11-02 | 3775.9131 | 15 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4446.7089
2025-11-02 | 3905.0911 | 14.4 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4526.7607
2025-11-02 | 4136.5439 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944.5249
2025-11-02 | 4476.2412 | 15.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5350.3725
2025-11-02 | 5106.1431 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5756.4007
2025-11-02 | 5646.7339 | 14.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5913.6762
2025-11-02 | 6041.9639 | 13.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5856.7896
2025-11-02 | 6039.4902 | 12.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743.1292
2025-11-02 | 6187.313 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5654.9668
2025-11-02 | 6137.4038 | 11.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5542.3486
2025-11-02 | 5782.9229 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5491.0043
2025-11-02 | 5656.4941 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5467.2909
2025-11-02 | 5968.9531 | 10.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5842.9608
2025-11-02 | 6631.3589 | 11.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6425.6797
2025-11-02 | 7194.8232 | 12.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6770.1368
2025-11-02 | 6901.5742 | 12.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6825.8443
2025-11-02 | 6620.2568 | 13 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6840.2157
2025-11-02 | 6222.9302 | 13.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6671.3106
2025-11-02 | 5673.2998 | 15.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6300.8779
2025-11-02 | 4980.9468 | 16.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5786.683
2025-11-02 | 4468.75 | 15.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5168.2205
2025-11-03 | 4191.582 | 15.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4580.992
2025-11-03 | 3923.2351 | 15.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4379.0241
2025-11-03 | 3795.1919 | 16.2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4327.3164
2025-11-03 | 3798.5459 | 16.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4289.2379
2025-11-03 | 3883.1509 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4358.2894
2025-11-03 | 4265.7632 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4589.0483
2025-11-03 | 4728.7559 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4928.894
2025-11-03 | 4999.187 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5191.9181
2025-11-03 | 5088.6338 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5239.1904
2025-11-03 | 4892.582 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5138.3027
2025-11-03 | 4784.7642 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5013.6419
2025-11-03 | 4827.0088 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5068.4836
2025-11-03 | 5004.8301 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4834.8619
2025-11-03 | 4953.4858 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4772.5173
2025-11-03 | 5078.3638 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5078.8133
2025-11-03 | 5398.6138 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520.4851
2025-11-03 | 6081.6431 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6136.2049
2025-11-03 | 6783.5552 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6414.6601
2025-11-03 | 6617.4468 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6470.3676
2025-11-03 | 6381.1611 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6451.7382
2025-11-03 | 6023.9121 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6194.8305
2025-11-03 | 5591.6831 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5593.3913
2025-11-03 | 4894.9219 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4980.1935
2025-11-03 | 4427.9722 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4460.7338
2025-11-04 | 4049.5391 | 11.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4107.9785
2025-11-04 | 3917.7539 | 11.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3928.0112
2025-11-04 | 3810.9351 | 11.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3832.3023
2025-11-04 | 3792.168 | 11.9 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3827.2248
2025-11-04 | 3870.6521 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4083.2816
2025-11-04 | 4275.7212 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4490.0455
2025-11-04 | 4813.3652 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4972.8953
2025-11-04 | 5177.8188 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5378.9234
2025-11-04 | 4961.626 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5448.1964
2025-11-04 | 4753.2339 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5314.3077
2025-11-04 | 4557.8989 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5145.6457
2025-11-04 | 4496.0918 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4958.4804
2025-11-04 | 4404.353 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4768.8601
2025-11-04 | 4401.5811 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4563.5113
2025-11-04 | 4382.7969 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4792.8051
2025-11-04 | 4608.2109 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5234.477
2025-11-04 | 5360.5239 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5850.1968
2025-11-04 | 6278.6572 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6194.6539
2025-11-04 | 6303.5889 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6316.3633
2025-11-04 | 6216.686 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6484.7391
2025-11-04 | 6004.5469 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6282.8331
2025-11-04 | 5415.4961 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5890.3997
2025-11-04 | 4877.6362 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5398.2054
2025-11-04 | 4378.3169 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4790.7432
2025-11-05 | 4072.8369 | 15.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4602.9926
2025-11-05 | 3917.7771 | 16.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.0257
2025-11-05 | 3816.0291 | 17.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4481.3208
2025-11-05 | 3785.3269 | 17.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4399.241
2025-11-05 | 3896.104 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4567.2953
2025-11-05 | 4269.8291 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4864.0561
2025-11-05 | 4748.4761 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5280.9041
2025-11-05 | 5129.6118 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5532.9278
2025-11-05 | 5151.625 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5580.2002
2025-11-05 | 5083.186 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5556.3146
2025-11-05 | 5015.7012 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5552.6573
2025-11-05 | 5098.9512 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5530.4967
2025-11-05 | 5213.6372 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5417.8785
2025-11-05 | 5224.9282 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5366.5342
2025-11-05 | 5306.854 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5474.8246
2025-11-05 | 5618.105 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5883.4955
2025-11-05 | 6330.814 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6488.215
2025-11-05 | 6876.4712 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6788.6708
2025-11-05 | 6700.29 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6888.3796
2025-11-05 | 6588.7969 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6880.7504
2025-11-05 | 6320.29 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6612.8425
2025-11-05 | 5815.3232 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6033.4038
2025-11-05 | 5271.939 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5387.2051
2025-11-05 | 4730.3608 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4889.746
2025-11-06 | 4364.644 | 14.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4514.9901
2025-11-06 | 4118.707 | 14.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4291.0216
2025-11-06 | 4001.801 | 14.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4184.3123
2025-11-06 | 3905.3679 | 14.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4124.2332
2025-11-06 | 4056.855 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4303.2878
2025-11-06 | 4473.1479 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4688.0511
2025-11-06 | 4927.9209 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5082.8984
2025-11-06 | 5284.29 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5477.9262
2025-11-06 | 5377.0039 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5734.2045
2025-11-06 | 5245.0278 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5721.3193
2025-11-06 | 4993.6821 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5750.6629
2025-11-06 | 5040.1592 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5684.5011
2025-11-06 | 5006.707 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5637.8848
2025-11-06 | 4941.8701 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5608.5411
2025-11-06 | 5015.2881 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5738.8321
2025-11-06 | 5270.2622 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6048.5002
2025-11-06 | 6035.7349 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6664.22
2025-11-06 | 6858.4858 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7107.6799
2025-11-06 | 6931.9419 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7207.3886
2025-11-06 | 7041.1929 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7232.7604
2025-11-06 | 6779.832 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7272.8613
2025-11-06 | 6341.8252 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6528.4179
2025-11-06 | 5643.481 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6025.2232
2025-11-06 | 5125.228 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5560.7651
2025-11-07 | 4770.0239 | 21.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5219.0101
2025-11-07 | 4500.5571 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4973.041
2025-11-07 | 4381.9292 | 21.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.3343
2025-11-07 | 4407.3032 | 21.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4883.2548
2025-11-07 | 4518.4849 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4996.3076
2025-11-07 | 4874.5581 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5238.0668
2025-11-07 | 5237.1382 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5577.9125
2025-11-07 | 5637.4038 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5950.9397
2025-11-07 | 5763.0908 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6108.2152
2025-11-07 | 5673.3818 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6040.3284
2025-11-07 | 5496.2622 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5827.6651
2025-11-07 | 5496.3599 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5706.5017
2025-11-07 | 5436.7598 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5593.8836
2025-11-07 | 5126.606 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520.5386
2025-11-07 | 5216.1162 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5551.8268
2025-11-07 | 5544.2822 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5894.4958
2025-11-07 | 6139.6162 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6609.2184
2025-11-07 | 6554.4258 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6832.672
2025-11-07 | 6433.8081 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6756.3758
2025-11-07 | 6352.1709 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6704.7454
2025-11-07 | 6006.9399 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6447.8378
2025-11-07 | 5599.5098 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5923.4007
2025-11-07 | 5034.8472 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 4903.1913
2025-11-07 | 4469.4639 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4262.7282
2025-11-08 | 4071.2151 | 8.9 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4133.4457
2025-11-08 | 3764.6709 | 8.7 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3898.4769
2025-11-08 | 3670.5649 | 9 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3813.7683
2025-11-08 | 3660.2339 | 10.4 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3940.6945
2025-11-08 | 3652.063 | 12.7 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4339.7554
2025-11-08 | 3894.717 | 14.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4867.5227
2025-11-08 | 4375.791 | 15.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5372.3732
2025-11-08 | 4951.6201 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5866.4038
2025-11-08 | 5406.5581 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6078.6809
2025-11-08 | 5912.3662 | 16.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6142.7978
2025-11-08 | 5964.3721 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6172.1415
2025-11-08 | 6066.9639 | 16.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6193.9821
2025-11-08 | 6037.5068 | 17.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6125.3652
2025-11-08 | 5892.2642 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6052.0203
2025-11-08 | 5763.0298 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6138.31
2025-11-08 | 5846.2661 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6524.9803
2025-11-08 | 6476.6841 | 17.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7140.7001
2025-11-08 | 7078.8052 | 18.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7485.1571
2025-11-08 | 7044.063 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7661.8681
2025-11-08 | 6805.8989 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7588.237
2025-11-08 | 6466.2568 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7353.3301
2025-11-08 | 6061.4619 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6883.8945
2025-11-08 | 5646.6572 | 20.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6281.6971
2025-11-08 | 5194.251 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5817.239
2025-11-09 | 4817.0469 | 20.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5409.4821
2025-11-09 | 4582.4448 | 20.2 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5163.5129
2025-11-09 | 4463.165 | 20.5 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5078.8043
2025-11-09 | 4443.5112 | 20.5 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5051.7261
2025-11-09 | 4509.168 | 20.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5208.7801
2025-11-09 | 4677.7998 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5582.5431
2025-11-09 | 4958.5532 | 21.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5999.391
2025-11-09 | 5562.6831 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6350.4176
2025-11-09 | 6233.146 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6518.6934
2025-11-09 | 6744.0591 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6527.8087
2025-11-09 | 7290.1982 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6491.1505
2025-11-09 | 7609.02 | 19.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6457.9897
2025-11-09 | 7788.522 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6389.3727
2025-11-09 | 7784.063 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6382.0297
2025-11-09 | 7756.5732 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6435.3184
2025-11-09 | 8026.2402 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6821.9887
2025-11-09 | 8596.1504 | 19.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7393.7073
2025-11-09 | 8810.3564 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7628.1612
2025-11-09 | 8289.0889 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7650.8678
2025-11-09 | 7807.7539 | 20.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7665.2392
2025-11-09 | 7406.8311 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7452.3329
2025-11-09 | 6703.2798 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6927.8958
2025-11-09 | 6008.0469 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6303.6977
2025-11-09 | 5349.8628 | 20.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5806.2386
2025-11-10 | 4912.2578 | 20.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5175.0089
2025-11-10 | 4777.0508 | 21 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4973.041
2025-11-10 | 4720.4521 | 21 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4855.3315
2025-11-10 | 4711.1001 | 21.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4850.2539
2025-11-10 | 4803.1338 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4974.3069
2025-11-10 | 5319.4141 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5293.0683
2025-11-10 | 5662.2021 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5753.9175
2025-11-10 | 5968.8091 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6104.9441
2025-11-10 | 6122.2412 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.2211
2025-11-10 | 6157.4448 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6348.3371
2025-11-10 | 6042.166 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6322.6792
2025-11-10 | 6071.6348 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6289.5184
2025-11-10 | 6134.0532 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6165.8998
2025-11-10 | 6114.6021 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6103.5552
2025-11-10 | 6177.292 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6200.8452
2025-11-10 | 6475.7778 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6609.5162
2025-11-10 | 7261.1089 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7181.2347
2025-11-10 | 7871.4741 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7415.6887
2025-11-10 | 7646.8052 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7427.3949
2025-11-10 | 7488.6489 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7419.7657
2025-11-10 | 7213.4741 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7228.86
2025-11-10 | 6695.1118 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6704.4229
2025-11-10 | 6113.6738 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6069.2245
2025-11-10 | 5499.52 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5549.7648
2025-11-11 | 5069.2891 | 21.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5197.0095
2025-11-11 | 4864.8408 | 21.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5006.042
2025-11-11 | 4783.793 | 21.3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4888.3324
2025-11-11 | 4790.5669 | 21.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4883.2548
2025-11-11 | 4931.186 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.3085
2025-11-11 | 5271.3252 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5381.0708
2025-11-11 | 5776.2041 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5786.9185
2025-11-11 | 6114.4971 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6170.946
2025-11-11 | 6247.2422 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6372.2227
2025-11-11 | 6224.9692 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6414.339
2025-11-11 | 6182.5269 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6410.6817
2025-11-11 | 6207.5508 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6366.5205
2025-11-11 | 6343.7651 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6165.8998
2025-11-11 | 6034.394 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5982.5518
2025-11-11 | 5852.1289 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6002.8396
2025-11-11 | 6234.6299 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6378.5096
2025-11-11 | 7166.668 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6939.2278
2025-11-11 | 7836.6201 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7228.6833
2025-11-11 | 7599.918 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7262.3902
2025-11-11 | 7405.9531 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7177.7588
2025-11-11 | 7212.6719 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6997.8534
2025-11-11 | 6718.4409 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6462.416
2025-11-11 | 6025.7568 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5948.221
2025-11-11 | 5427.2749 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5527.7642
2025-11-12 | 4987.521 | 21.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5197.0095
2025-11-12 | 4785.2329 | 19.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4819.0366
2025-11-12 | 4610.6802 | 18.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4602.3243
2025-11-12 | 4637.2412 | 18.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4509.2442
2025-11-12 | 4717.9199 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4688.2988
2025-11-12 | 5081.7832 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5040.0611
2025-11-12 | 5500.2969 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5434.9084
2025-11-12 | 5883.1992 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5807.9356
2025-11-12 | 6068.2759 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5987.2117
2025-11-12 | 5891.5122 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6029.328
2025-11-12 | 5859.332 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5981.6695
2025-11-12 | 5926.772 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5970.5093
2025-11-12 | 5893.0562 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5813.8898
2025-11-12 | 5768.6401 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5707.5439
2025-11-12 | 5777.2441 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5793.8337
2025-11-12 | 6127.9258 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6202.5046
2025-11-12 | 6890.2412 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6851.2253
2025-11-12 | 7524.8311 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.6802
2025-11-12 | 7271.8052 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7097.3855
2025-11-12 | 7212.9131 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7056.7554
2025-11-12 | 7029.2119 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6766.8468
2025-11-12 | 6427.6152 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6187.4082
2025-11-12 | 5750.7349 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5585.2107
2025-11-12 | 5066.252 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5043.7504
2025-11-13 | 4714.2832 | 16.8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4723.996
2025-11-13 | 4531.2388 | 16.7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4500.0275
2025-11-13 | 4346.3149 | 16.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4404.3186
2025-11-13 | 4381.145 | 17.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4399.241
2025-11-13 | 4454.104 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4545.2947
2025-11-13 | 4832.2539 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4897.0571
2025-11-13 | 5249.8921 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5302.9047
2025-11-13 | 5635.3218 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5697.9325
2025-11-13 | 5722.5869 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5888.2089
2025-11-13 | 5636.6812 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5886.324
2025-11-13 | 5537.626 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5838.6654
2025-11-13 | 5508.9258 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5794.5043
2025-11-13 | 5421.541 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5648.8851
2025-11-13 | 5321.5508 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5509.5383
2025-11-13 | 5332.436 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5584.8277
2025-11-13 | 5520.1841 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5883.4955
2025-11-13 | 6343.3628 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6488.215
2025-11-13 | 7152.5479 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6843.6724
2025-11-13 | 6939.5459 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6844.3783
2025-11-13 | 6935.5049 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6858.7498
2025-11-13 | 6768.8662 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6612.8425
2025-11-13 | 6348.2739 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6110.406
2025-11-13 | 5651.6968 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5508.2085
2025-11-13 | 5065.0391 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5098.752
2025-11-14 | 4818.1982 | 17.7 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.9989
2025-11-14 | 4590.9312 | 18.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4654.0319
2025-11-14 | 4445.9468 | 18.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4591.3239
2025-11-14 | 4432.748 | 19.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4641.2479
2025-11-14 | 4582.4531 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4842.3032
2025-11-14 | 4906.2852 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5249.0671
2025-11-14 | 5402.4502 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5555.9119
2025-11-14 | 5746.1519 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5895.9381
2025-11-14 | 5887.043 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6053.2136
2025-11-14 | 5806.9902 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6051.3287
2025-11-14 | 5631.3638 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5992.6698
2025-11-14 | 5698.0791 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5926.508
2025-11-14 | 5619.2241 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5736.8876
2025-11-14 | 5461.999 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5564.5399
2025-11-14 | 5462.498 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5683.8305
2025-11-14 | 5782.2969 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6059.5005
2025-11-14 | 6373.79 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6873.2259
2025-11-14 | 6906.7402 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7074.6789
2025-11-14 | 6782.0781 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7108.3858
2025-11-14 | 6775.2388 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7100.7566
2025-11-14 | 6644.0942 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6975.8528
2025-11-14 | 6229.4932 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6506.4173
2025-11-14 | 5824.7178 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6047.2239
2025-11-14 | 5339.6348 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5659.768
2025-11-15 | 5045.6719 | 22.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5607.4877
2025-11-15 | 4825.583 | 22 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5361.5186
2025-11-15 | 4721.605 | 23.8 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5441.8147
2025-11-15 | 4703.7412 | 23 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5326.734
2025-11-15 | 4817.627 | 24.8 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5670.7933
2025-11-15 | 5016.0928 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5802.5494
2025-11-15 | 5457.5459 | 24.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6384.402
2025-11-15 | 6039.7231 | 25 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6812.4308
2025-11-15 | 6461.9009 | 22.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6782.7009
2025-11-15 | 6700.8032 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6637.8119
2025-11-15 | 6866.9238 | 19.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6502.1509
2025-11-15 | 6930.3828 | 18.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6391.9878
2025-11-15 | 6836.3101 | 18.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6279.3696
2025-11-15 | 6738.79 | 18.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6217.025
2025-11-15 | 6692.1738 | 18.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6325.3153
2025-11-15 | 6874.3701 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6678.9846
2025-11-15 | 7428.812 | 18.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7228.7026
2025-11-15 | 7810.3252 | 18.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7452.1562
2025-11-15 | 7475.6899 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7474.8628
2025-11-15 | 7135.2412 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7445.233
2025-11-15 | 6758.4229 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7210.326
2025-11-15 | 6304.3579 | 18.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6663.8883
2025-11-15 | 5732.8838 | 18.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6028.6899
2025-11-15 | 5207.9248 | 18.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5531.2308
2025-11-16 | 4843.4219 | 18.3 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5167.4752
2025-11-16 | 4644.2578 | 18.3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4954.507
2025-11-16 | 4489.0571 | 18.3 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4836.7974
2025-11-16 | 4467.3911 | 18.2 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4798.7189
2025-11-16 | 4506.1089 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944.7726
2025-11-16 | 4671.083 | 17.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5230.5331
2025-11-16 | 4904.0122 | 17.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5614.3801
2025-11-16 | 5439.8281 | 17.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5987.4073
2025-11-16 | 6095.4922 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6188.684
2025-11-16 | 6625.8818 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6241.8006
2025-11-16 | 6982.0752 | 17.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6227.143
2025-11-16 | 7096.3882 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6215.9828
2025-11-16 | 7148.374 | 17.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6202.3674
2025-11-16 | 7178.8232 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6008.019
2025-11-16 | 6574.8232 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6138.31
2025-11-16 | 6670.7329 | 17.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6557.9812
2025-11-16 | 8315.916 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7195.7016
2025-11-16 | 8693.7861 | 18.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7485.1571
2025-11-16 | 8223.3896 | 19 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7529.8643
2025-11-16 | 7933.6841 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7522.2352
2025-11-16 | 7557.6421 | 19.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7342.3297
2025-11-16 | 6905.5249 | 19.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6828.893
2025-11-16 | 6233.2539 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6226.6955
2025-11-16 | 5655.124 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5718.2361
2025-11-17 | 5181.269 | 20.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5109.007
2025-11-17 | 4934.479 | 20.3 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4896.0388
2025-11-17 | 4825.916 | 20.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800.3299
2025-11-17 | 4760.1089 | 20.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4751.2511
2025-11-17 | 4968.269 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4886.3044
2025-11-17 | 5335.8398 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5216.0661
2025-11-17 | 5879.252 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5643.9144
2025-11-17 | 6236.623 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6005.9413
2025-11-17 | 6277.647 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6207.218
2025-11-17 | 6263.1162 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6249.3343
2025-11-17 | 6289.9609 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6201.6758
2025-11-17 | 6258.6621 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6168.5149
2025-11-17 | 6269.9082 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6055.8967
2025-11-17 | 6240.062 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5982.5518
2025-11-17 | 6235.4971 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6090.8421
2025-11-17 | 6488.3872 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6455.5118
2025-11-17 | 7402.0679 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7038.2306
2025-11-17 | 8089.7749 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7261.6843
2025-11-17 | 7832.6021 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7262.3902
2025-11-17 | 7644.2788 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7221.7601
2025-11-17 | 7320.2231 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6986.8531
2025-11-17 | 6918.8901 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6473.4163
2025-11-17 | 6118.1201 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5849.2182
2025-11-17 | 5480.0928 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5362.7595
2025-11-18 | 5123.4541 | 19.3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4999.0039
2025-11-18 | 4960.2358 | 19.4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4797.036
2025-11-18 | 4859.5151 | 19.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4723.3277
2025-11-18 | 4813.9268 | 19.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4685.2492
2025-11-18 | 4949.4941 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4820.3025
2025-11-18 | 5242.1001 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5128.0636
2025-11-18 | 5748.0762 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5511.9106
2025-11-18 | 6110.9292 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5884.9378
2025-11-18 | 6290.9238 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6097.2149
2025-11-18 | 6062.2178 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6161.3318
2025-11-18 | 5923.3188 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6157.6745
2025-11-18 | 5906.7798 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6168.5149
2025-11-18 | 5793.2808 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6044.8964
2025-11-18 | 5568.0259 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5960.5511
2025-11-18 | 5440.5342 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6057.8412
2025-11-18 | 5629.2471 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6411.5105
2025-11-18 | 6636.4512 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7049.231
2025-11-18 | 7501.606 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7404.6883
2025-11-18 | 7373.9248 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7427.3949
2025-11-18 | 7433.5132 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7441.7664
2025-11-18 | 7185.4131 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7316.8625
2025-11-18 | 6814.6831 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6737.4239
2025-11-18 | 6227.478 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6278.2305
2025-11-18 | 5664.1948 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5835.773
2025-11-19 | 5331.896 | 24.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5538.0192
2025-11-19 | 5097.8301 | 24.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5325.051
2025-11-19 | 4990.9302 | 23.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5174.3406
2025-11-19 | 5064.6001 | 22.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4993.258
2025-11-19 | 5242.2158 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5117.311
2025-11-19 | 5582.6709 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5436.0724
2025-11-19 | 6030.999 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5841.92
2025-11-19 | 6351.501 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6258.9485
2025-11-19 | 6532.8208 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6515.2268
2025-11-19 | 6427.2578 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6535.3425
2025-11-19 | 6346.187 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6432.6824
2025-11-19 | 6423.2461 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6311.519
2025-11-19 | 6306.0679 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6165.8998
2025-11-19 | 6275.166 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5938.5505
2025-11-19 | 6280.1382 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5980.839
2025-11-19 | 6473.3472 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6334.5083
2025-11-19 | 7256.6982 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6983.2291
2025-11-19 | 8008.8379 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7283.6849
2025-11-19 | 7903.978 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7515.3974
2025-11-19 | 7788.3491 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7551.7695
2025-11-19 | 7630.2969 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7305.8622
2025-11-19 | 7132.6729 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6825.4264
2025-11-19 | 6423.1689 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6223.2289
2025-11-19 | 5814.7959 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5747.7705
2025-11-20 | 5356.7539 | 22.5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5351.0139
2025-11-20 | 5143.5962 | 22.2 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5105.0448
2025-11-20 | 5053.021 | 22.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5064.3374
2025-11-20 | 5020.127 | 23.6 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5114.2614
2025-11-20 | 5201.1592 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5271.3154
2025-11-20 | 5517.9839 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5612.0774
2025-11-20 | 5935.5801 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6028.9254
2025-11-20 | 6318.6558 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6412.9529
2025-11-20 | 6449.1899 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6570.2284
2025-11-20 | 6436.022 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6634.3453
2025-11-20 | 6268.2681 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6597.6871
2025-11-20 | 6277.6489 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6586.5268
2025-11-20 | 6169.0518 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6429.9074
2025-11-20 | 5872.437 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6301.5608
2025-11-20 | 5828.0488 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6343.8493
2025-11-20 | 6081.7021 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6730.5196
2025-11-20 | 6876.8218 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7313.2385
2025-11-20 | 7713.4458 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7536.6921
2025-11-20 | 7597.5029 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7548.3984
2025-11-20 | 7709.9141 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7529.7689
2025-11-20 | 7606.6118 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7294.8619
2025-11-20 | 7151.3398 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6781.4251
2025-11-20 | 6397.3242 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6168.2273
2025-11-20 | 5751.4678 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5648.7677
2025-11-21 | 5336.6992 | 22 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5296.0123
2025-11-21 | 5108.2358 | 21.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5072.0438
2025-11-21 | 5003.6802 | 21.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4943.334
2025-11-21 | 4955.5649 | 21.7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4905.2555
2025-11-21 | 4973.7251 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5029.3085
2025-11-21 | 5259.5151 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5326.0693
2025-11-21 | 5728.1768 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5698.916
2025-11-21 | 6034.8911 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6038.9422
2025-11-21 | 6196.1841 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6141.2161
2025-11-21 | 6171.1602 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6073.3293
2025-11-21 | 6090.8521 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6036.6711
2025-11-21 | 6111.5059 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6014.5105
2025-11-21 | 6073.5112 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5604.8839
2025-11-21 | 5845.8589 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5377.5345
2025-11-21 | 5702.396 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5199.8167
2025-11-21 | 5702.3232 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5542.4858
2025-11-21 | 6395.3198 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6422.2131
2025-11-21 | 6977.1348 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6810.6714
2025-11-21 | 6746.6099 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6855.3786
2025-11-21 | 6482.6719 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7023.7545
2025-11-21 | 6522.0928 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6810.8481
2025-11-21 | 6291.728 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6396.4142
2025-11-21 | 5872.854 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5805.217
2025-11-21 | 5338.1299 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5263.7567
2025-11-22 | 4975.814 | 20.2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376.4811
2025-11-22 | 4725.9858 | 19.1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5042.5095
2025-11-22 | 4585.731 | 19 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4913.7996
2025-11-22 | 4509.5679 | 19 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4886.7214
2025-11-22 | 4556.1338 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5098.777
2025-11-22 | 4736.5542 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5483.5403
2025-11-22 | 5128.8901 | 19.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5823.386
2025-11-22 | 5752.3882 | 19.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6185.4129
2025-11-22 | 6254.9448 | 19.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6375.6893
2025-11-22 | 6518.5869 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6362.804
2025-11-22 | 6464.0229 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6183.1418
2025-11-22 | 6512.5352 | 16 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6094.9793
2025-11-22 | 6273.915 | 15.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5916.3592
2025-11-22 | 6244.6768 | 15.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5887.0156
2025-11-22 | 6081.6719 | 15.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5940.3043
2025-11-22 | 6163.8979 | 14.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6271.973
2025-11-22 | 6829.8599 | 16.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7030.6969
2025-11-22 | 7400.79 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7419.1553
2025-11-22 | 7218.2671 | 18.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7485.8631
2025-11-22 | 7019.147 | 20.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7621.238
2025-11-22 | 6821.853 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7331.3294
2025-11-22 | 6505.8638 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6927.8958
2025-11-22 | 6106.3618 | 20.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6292.6974
2025-11-22 | 5525.1768 | 23 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6037.2452
2025-11-23 | 5198.4521 | 22.7 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5651.489
2025-11-23 | 4969.396 | 24.8 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5669.5274
2025-11-23 | 4889.397 | 23.4 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5397.8134
2025-11-23 | 4763.1792 | 23 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5326.734
2025-11-23 | 4776.106 | 22.2 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5384.7851
2025-11-23 | 4949.2422 | 21.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5659.5453
2025-11-23 | 5181.5249 | 21.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5999.391
2025-11-23 | 5710.8052 | 21 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6372.4182
2025-11-23 | 6403.3242 | 20.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6540.694
2025-11-23 | 6983.459 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6571.81
2025-11-23 | 7270.4438 | 19.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6480.1502
2025-11-23 | 7529.9121 | 19 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6424.9887
2025-11-23 | 7616.918 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6268.3693
2025-11-23 | 7630.3862 | 18.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6206.0246
2025-11-23 | 7370.5229 | 18.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6281.3141
2025-11-23 | 7688.042 | 18.3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6656.984
2025-11-23 | 8299.7881 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7206.7019
2025-11-23 | 8407.0029 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7430.1556
2025-11-23 | 8079.5591 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7441.8618
2025-11-23 | 7718.376 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7412.232
2025-11-23 | 7191.2261 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7177.325
2025-11-23 | 6617.2471 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6641.8877
2025-11-23 | 5769.3862 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6017.6895
2025-11-23 | 5127.5898 | 18.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5498.2299
2025-11-24 | 4790.7832 | 18.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4867.0001
2025-11-24 | 4531.9878 | 17.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4621.031
2025-11-24 | 4374.8188 | 17.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4481.3208
2025-11-24 | 4344.4072 | 17.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4399.241
2025-11-24 | 4449.854 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4534.2944
2025-11-24 | 4835.4258 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4886.0567
2025-11-24 | 5365.043 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5379.9069
2025-11-24 | 5737.5532 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5763.9344
2025-11-24 | 5899.5278 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5943.2105
2025-11-24 | 5716.6289 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5930.3252
2025-11-24 | 5521.1348 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5893.667
2025-11-24 | 5573.3101 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5882.5068
2025-11-24 | 5648.9761 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5780.8889
2025-11-24 | 5430.5708 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5696.5436
2025-11-24 | 5340.627 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5694.8308
2025-11-24 | 5513.748 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6004.4989
2025-11-24 | 6498.333 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6697.2209
2025-11-24 | 7335.1421 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7085.6793
2025-11-24 | 7280.7202 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7119.3861
2025-11-24 | 7163.5518 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6935.7519
2025-11-24 | 6847.0151 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6689.8447
2025-11-24 | 6350.8589 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6110.406
2025-11-24 | 5700.499 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5519.2088
2025-11-24 | 5110.3081 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5021.7498
2025-11-25 | 4688.7402 | 16.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4657.9942
2025-11-25 | 4477.3242 | 16.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4434.0257
2025-11-25 | 4305.1729 | 15.5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4250.3142
2025-11-25 | 4227.8462 | 15.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4223.236
2025-11-25 | 4289.2881 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4391.2903
2025-11-25 | 4616.0342 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4798.0542
2025-11-25 | 5071.3252 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5280.9041
2025-11-25 | 5413.0718 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5521.9275
2025-11-25 | 5527.5308 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5822.207
2025-11-25 | 5284.606 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5754.3202
2025-11-25 | 5153.311 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5574.6579
2025-11-25 | 5011.23 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5475.4952
2025-11-25 | 5001.1211 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5329.876
2025-11-25 | 4944.6572 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5256.5311
2025-11-25 | 5052.6919 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5342.8208
2025-11-25 | 5215.4829 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5740.4914
2025-11-25 | 6195.4048 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6411.2128
2025-11-25 | 6940.1348 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6733.6692
2025-11-25 | 6827.938 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6833.378
2025-11-25 | 6593.0518 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6770.7472
2025-11-25 | 6356.0962 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6535.8403
2025-11-25 | 5877.0732 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6033.4038
2025-11-25 | 5191.6689 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5453.2069
2025-11-25 | 4637.5098 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4977.7485
2025-11-26 | 4266.3872 | 15.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4624.9932
2025-11-26 | 4075.354 | 15.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4401.0247
2025-11-26 | 3899.5591 | 15.8 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4283.3152
2025-11-26 | 3888.7351 | 15.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4256.237
2025-11-26 | 3929.25 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4402.2906
2025-11-26 | 4294.167 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4743.0527
2025-11-26 | 4833.5322 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5170.9009
2025-11-26 | 5087.9268 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5532.9278
2025-11-26 | 5220.7739 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5734.2045
2025-11-26 | 5190.8911 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5765.3205
2025-11-26 | 5105.2388 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5761.6633
2025-11-26 | 5129.5649 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5728.5024
2025-11-26 | 5101.251 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5582.8832
2025-11-26 | 5012.083 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520.5386
2025-11-26 | 5010.7622 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5617.8286
2025-11-26 | 5229.7861 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6004.4989
2025-11-26 | 6083.9839 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6543.2165
2025-11-26 | 6813.271 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6755.6699
2025-11-26 | 6728.6802 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6789.3767
2025-11-26 | 6817.2202 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6737.7463
2025-11-26 | 6582.187 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6414.8368
2025-11-26 | 6133.646 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5890.3997
2025-11-26 | 5457.4531 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5332.2035
2025-11-26 | 4911.0928 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4955.7479
2025-11-27 | 4552.623 | 16.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4701.9954
2025-11-27 | 4356.4712 | 16.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4489.0272
2025-11-27 | 4259.0732 | 16.9 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4404.3186
2025-11-27 | 4305.5859 | 16.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4366.2401
2025-11-27 | 4430.8931 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4523.2941
2025-11-27 | 4788.5449 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4897.0571
2025-11-27 | 5367.9761 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5313.905
2025-11-27 | 5691.5649 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5642.9309
2025-11-27 | 5797.5181 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5855.208
2025-11-27 | 5875.1479 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5798.3215
2025-11-27 | 5666.2241 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5772.6636
2025-11-27 | 5629.2388 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5662.5005
2025-11-27 | 5417.7212 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5549.8823
2025-11-27 | 5470.5098 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5498.538
2025-11-27 | 5668.1011 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5595.828
2025-11-27 | 5919.1538 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6015.4992
2025-11-27 | 6712.5132 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6708.2212
2025-11-27 | 7361.3521 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7041.678
2025-11-27 | 7308.564 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7020.3833
2025-11-27 | 7204.0479 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7001.7538
2025-11-27 | 6993.834 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6788.8475
2025-11-27 | 6603.8408 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6275.4107
2025-11-27 | 5961.7949 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5761.2157
2025-11-27 | 5427.8838 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5274.757
2025-11-28 | 5031.0488 | 19.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5032.0048
2025-11-28 | 4818.0059 | 19.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4852.0376
2025-11-28 | 4749.1421 | 20.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4756.3286
2025-11-28 | 4685.1548 | 20.8 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4806.2526
2025-11-28 | 4844.5601 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4930.3057
2025-11-28 | 5162.4312 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5293.0683
2025-11-28 | 5659.6108 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5665.915
2025-11-28 | 5976.106 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6104.9441
2025-11-28 | 6189.3271 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6317.2211
2025-11-28 | 6221.0068 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6337.3368
2025-11-28 | 6301.644 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6300.6786
2025-11-28 | 6238.73 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6223.5165
2025-11-28 | 6360.3232 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6121.8986
2025-11-28 | 6368.0708 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6136.5561
2025-11-28 | 6362.6699 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6222.8459
2025-11-28 | 6627.8379 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6620.5165
2025-11-28 | 7271.0479 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7225.236
2025-11-28 | 7919.71 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7481.6905
2025-11-28 | 7590.062 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7493.3968
2025-11-28 | 7564.106 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7507.7682
2025-11-28 | 7360.8311 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7184.8588
2025-11-28 | 7017.6641 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6605.4201
2025-11-28 | 6505.1709 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5981.222
2025-11-28 | 5943.8799 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5450.762
2025-11-29 | 5558.9858 | 20.5 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5409.4821
2025-11-29 | 5240.082 | 20.6 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5207.5142
2025-11-29 | 5082.583 | 21 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5133.8059
2025-11-29 | 5026.8511 | 21.3 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5139.7287
2025-11-29 | 5127.8442 | 21.5 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5307.7829
2025-11-29 | 5306.5742 | 21.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5681.5459
2025-11-29 | 5726.5132 | 22.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6120.3945
2025-11-29 | 6349.9692 | 22.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6504.422
2025-11-29 | 6920.5571 | 21.9 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6683.6981
2025-11-29 | 7153.645 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6703.8138
2025-11-29 | 7042.3442 | 20.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6579.1531
2025-11-29 | 6922.249 | 19.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6490.9906
2025-11-29 | 6754.9541 | 19.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6411.3734
2025-11-29 | 6510.9648 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6283.0268
2025-11-29 | 6417.4902 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6369.3166
2025-11-29 | 6702.8408 | 19.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6755.9868
2025-11-29 | 7389.3281 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7426.7082
2025-11-29 | 7925.8511 | 21.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7749.1647
2025-11-29 | 7649.9761 | 22.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7925.8756
2025-11-29 | 7440.9731 | 24.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8094.2515
2025-11-29 | 7192.0371 | 23.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7716.3404
2025-11-29 | 6860.4009 | 24 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7279.9058
2025-11-29 | 6447.9028 | 23.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6556.7049
2025-11-29 | 5891.1138 | 24.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6158.2487
2025-11-30 | 5439.0752 | 22.6 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5640.4887
2025-11-30 | 5195.2148 | 22.3 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5394.5195
2025-11-30 | 4970.0718 | 22.1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5254.8094
2025-11-30 | 4970.9941 | 21.9 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5205.7305
2025-11-30 | 5011.083 | 21.9 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5351.7842
2025-11-30 | 5096.5918 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5692.5462
2025-11-30 | 4822.2271 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6098.3939
2025-11-30 | 5231.0308 | 21.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6460.4207
2025-11-30 | 5836.2002 | 21.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6650.6972
2025-11-30 | 6239.3691 | 21.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6692.8134
2025-11-30 | 6509.0908 | 20.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6623.1543
2025-11-30 | 7538.0718 | 20.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6556.9925
2025-11-30 | 7978.8711 | 19.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400.373
2025-11-30 | 7898.1362 | 19.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6272.0265
2025-11-30 | 7850.5278 | 18.6 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6303.3147
2025-11-30 | 8049.7012 | 18.2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6645.9837
2025-11-30 | 8623.6885 | 17.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7162.7007
2025-11-30 | 8821.7969 | 17.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7375.154
2025-11-30 | 8385.7998 | 17.1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7320.8584
2025-11-30 | 7927.2598 | 16.7 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7247.2273
2025-11-30 | 7560.2041 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6979.3194
2025-11-30 | 6860.498 | 16.4 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6443.882
2025-11-30 | 6109.9141 | 16.8 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5863.6852
2025-11-30 | 5557.0342 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5487.2296
2025-12-01 | 5119.1089 | 18.9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4955.0026
2025-12-01 | 4948.3452 | 19.9 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4852.0376
2025-12-01 | 4928.082 | 21.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4866.3318
2025-12-01 | 4972.1592 | 22 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4938.2564
2025-12-01 | 5211.5562 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5348.3176
2025-12-01 | 5588.9521 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5810.0831
2025-12-01 | 6133.7441 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6358.9348
2025-12-01 | 6579.564 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6753.9626
2025-12-01 | 6527.5942 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7021.2412
2025-12-01 | 6317.332 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7074.3578
2025-12-01 | 6340.8091 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7081.7009
2025-12-01 | 6430.1191 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7037.5397
2025-12-01 | 6382.5479 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6847.9193
2025-12-01 | 6187.4102 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6785.5746
2025-12-01 | 6252.8652 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6805.8625
2025-12-01 | 6599.7881 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7280.5353
2025-12-01 | 7759.8169 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7907.2554
2025-12-01 | 8529.0088 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8207.7112
2025-12-01 | 8425.6016 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8340.4209
2025-12-01 | 8328.6748 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8222.7886
2025-12-01 | 8049.9941 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8075.8841
2025-12-01 | 7633.3809 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7529.4464
2025-12-01 | 6887.479 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 6982.2505
2025-12-01 | 6193.543 | 28.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6407.7893
2025-12-02 | 5829.1172 | 28.1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5967.0315
2025-12-02 | 5598.6812 | 27.8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5721.0623
2025-12-02 | 5536.0718 | 27.4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5559.3515
2025-12-02 | 5524.2632 | 27.3 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5521.273
2025-12-02 | 5599.77 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5656.3264
2025-12-02 | 5901.792 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6041.0896
2025-12-02 | 6397.3291 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6523.9395
2025-12-02 | 6666.1729 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6984.9692
2025-12-02 | 6801.396 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7142.2447
2025-12-02 | 6827.0552 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7118.3591
2025-12-02 | 6787.5708 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7037.6996
2025-12-02 | 6758.667 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6916.5362
2025-12-02 | 6746.2578 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6737.9161
2025-12-02 | 6562.7661 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6521.5671
2025-12-02 | 6525.4839 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6541.855
2025-12-02 | 6840.9028 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6950.5259
2025-12-02 | 7760.2778 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7610.2469
2025-12-02 | 8570.2871 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8042.7065
2025-12-02 | 8460.8047 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8131.415
2025-12-02 | 8417.6602 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8123.7858
2025-12-02 | 8214.4785 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 7833.8772
2025-12-02 | 7687.6221 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 7386.4424
2025-12-02 | 6983.4082 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7059.2527
2025-12-02 | 6328.3242 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6506.7921
2025-12-03 | 5931.8179 | 30.2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6198.038
2025-12-03 | 5727.0132 | 31 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6073.0724
2025-12-03 | 5557.3428 | 31.6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6021.3647
2025-12-03 | 5522.9092 | 31.2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5950.2852
2025-12-03 | 5602.895 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5975.3355
2025-12-03 | 5982.4082 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6250.0956
2025-12-03 | 6515.708 | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6556.9404
2025-12-03 | 6878.3491 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6896.9667
2025-12-03 | 6915.3271 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7065.2425
2025-12-03 | 6775.1021 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7008.3559
2025-12-03 | 6727.7129 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6883.6952
2025-12-03 | 6717.3179 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6707.5303
2025-12-03 | 6770.7388 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6495.9092
2025-12-03 | 6664.4941 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6345.5621
2025-12-03 | 6684.0352 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6365.8499
2025-12-03 | 6955.5581 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6598.5158
2025-12-03 | 7763.499 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7027.2303
2025-12-03 | 8240.1826 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7140.6808
2025-12-03 | 8078.4961 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7075.3849
2025-12-03 | 8096.9019 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7023.7545
2025-12-03 | 7799.4238 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 6821.8484
2025-12-03 | 7169.7422 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6330.4123
2025-12-03 | 6499.9722 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 5706.2142
2025-12-03 | 5817.1621 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5307.7579
2025-12-04 | 5440.0112 | 19 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4966.0029
2025-12-04 | 5163.0791 | 19 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4753.0347
2025-12-04 | 5038.7119 | 20.7 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4822.3305
2025-12-04 | 5064.916 | 22.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4949.2567
2025-12-04 | 5226.8452 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5183.3129
2025-12-04 | 5594.7808 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5623.0777
2025-12-04 | 6220.1421 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6094.9272
2025-12-04 | 6436.168 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6632.9591
2025-12-04 | 6545.2832 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6900.2378
2025-12-04 | 6608.6851 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7096.3584
2025-12-04 | 6796.1279 | 28.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7147.7027
2025-12-04 | 6857.6782 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7136.5425
2025-12-04 | 6667.7759 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7023.9243
2025-12-04 | 6469.7788 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6994.5806
2025-12-04 | 6713.8018 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7124.8716
2025-12-04 | 7093.9028 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7720.5478
2025-12-04 | 8309.9873 | 31.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8435.2704
2025-12-04 | 9215.7822 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8724.7259
2025-12-04 | 9205.4043 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8857.4356
2025-12-04 | 9155.8242 | 34.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8970.8099
2025-12-04 | 9090.0908 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 8856.9064
2025-12-04 | 8614.5576 | 34.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 8178.4649
2025-12-04 | 7906.5112 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 7697.2709
2025-12-04 | 7287.7622 | 37.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7331.8156
2025-12-05 | 6926.5952 | 36.6 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6902.0581