## 2-Staff-62 c) a.
Project | MS | Metric | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Foster MS (Belleville - 13.8kV) | Reid | Load (MVA) | 12.0971 | 12.7693 | 13.0789 | 13.464 | 13.6187 | 13.9225 | 14.1664
| Bell | Load (MVA) | 15.9117 | 16.5839 | 16.8935 | 17.2786 | 17.4334 | 17.7372 | 17.9811
| Edgehill | Load (MVA) | 10.6916 | 11.3639 | 11.6735 | 12.0586 | 13.021 | 14.294 | 15.184
| Sidney | Load (MVA) | 7.6797 | 8.3519 | 8.6615 | 9.0466 | 9.2014 | 9.5052 | 9.7491
| Harder | Load (MVA) | 5.271 | 5.9432 | 6.2528 | 6.6379 | 6.7927 | 7.0965 | 7.3404
| Foster (New) | Load (MVA) | 0 | 0 | 0 | 0 | 0.96241 | 2.0738 | 3.1254
Project | MS | Metric | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Uxbridge North MS (Uxbridge - 4.16kV) | Uxbridge East | Load (MVA) | 3.9186 | 3.9793 | 4.042 | 4.1349 | 4.2342 | 4.3402 | 4.4318
| Uxbridge West | Load (MVA) | 3.3359 | 3.3965 | 3.4593 | 3.5521 | 3.6515 | 3.7574 | 3.8491
| Uxbridge North (New) | Load (MVA) | 0 | 0 | 0 | 0.092808 | 0.19217 | 0.29813 | 0.38977
Project | MS | Metric | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Port Hope 27.6kV MS (Port Hope - 27.6V) | James D Collins | Load (MVA) | 6.3746 | 6.7377 | 7.1183 | 7.5115 | 7.993 | 8.4932 | 8.9296
| Shuter | Load (MVA) | 4.5171 | 4.8803 | 5.2609 | 6.9413 | 7.4229 | 7.923 | 8.3595
| Port Hope 27.6 kV (New) | Load (MVA) | 0 | 0 | 0 | 0 | 0.48154 | 0.98168 | 1.4182
Project | MS | Metric | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Bradshaw MS (Bowanville - 13.8kV) | Bradshaw (Upgrade) | Load (MVA) | 9.1854 | 9.7453 | 10.353 | 10.9887 | 11.6996 | 12.4874 | 13.2223
| Spry | Load (MVA) | 14.531 | 15.0908 | 15.6986 | 16.3342 | 17.0452 | 17.833 | 18.5678
| Liberty North | Load (MVA) | 13.6017 | 14.1616 | 14.7693 | 15.405 | 16.1159 | 16.9037 | 17.6386
Project | MS | Metric | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Winchester West MS (Whitby - 13.8kV) | Taunton West | Load (MVA) | 19.7942 | 20.3019 | 20.5636 | 20.6754 | 20.87 | 21.1521 | 21.3836
| Baldwin | Load (MVA) | 13.2657 | 13.7735 | 14.0351 | 14.147 | 14.3415 | 14.6237 | 14.8551
| W Lawler | Load (MVA) | 33.3627 | 33.8705 | 34.1321 | 34.244 | 34.4385 | 34.7207 | 34.9521
| Conlin | Load (MVA) | 13.8789 | 14.3867 | 14.6483 | 14.7602 | 14.9547 | 15.2369 | 15.4683
| Winchester West (New) | Load (MVA) | 0 | 0 | 3.3333 | 6.6667 | 10 | 13.3333 | 16.6667

## 2-Staff-62 c) b.
Foster MS (Belleville 13.8 kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | MS Maximum Planning Capacity (MVA)
| Bell | 20 | BELL-F1 | 5.27 | 8 | 5.27 | 12.441
|  |  | BELL-F2 | 7.171 | 8 | 7.171
| Edgehill | 20 | EDGE-F1 | 7.171 | 8 | 7.171 | 14.342
|  |  | EDGE-F2 | 7.171 | 8 | 7.171
| Harder | 10 | HARD-F1 | 7.171 | 8 | 7.171 | 7.171
| Reid | 20 | REID-F1 | 7.171 | 8 | 7.171 | 14.342
|  |  | REID-F2 | 7.171 | 8 | 7.171
| Sidney | 20 | SIDN-F1 | 7.171 | 8 | 7.171 | 14.342
|  |  | SIDN-F2 | 7.171 | 8 | 7.171
[6 empty] | Maximum Planning Capacity (MVA) | 62.638
Uxbridge North MS (Uxbridge - 4.16 kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | MS Maximum Planning Capacity (MVA)
| Uxbridge East | 6.67 | UXBE-F1 | 1.5888 | 1.7787 | 1.5888 | 5.1461
|  |  | UXBE-F2 | 2.1616 | 1.7787 | 1.7787
|  |  | UXBE-F3 | 2.1616 | 1.7787 | 1.7787
| Uxbridge West | 5 | UXBW-F1 | 2.1616 | 1.3333 | 1.3333 | 4
|  |  | UXBW-F2 | 2.1616 | 1.3333 | 1.3333
|  |  | UXBW-F3 | 2.1616 | 1.3333 | 1.3333
[6 empty] | Maximum Planning Capacity (MVA) | 9.1461
Port Hope 27.6kV MS (Port Hope - 27.6kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | MS Maximum Planning Capacity (MVA)
| James D Collins | 13.33 | JAME-T1 | 14.341 | 5.332 | 5.332 | 10.664
|  |  | JAME-T1 | 14.341 | 5.332 | 5.332
| Shuter | 13.33 | SHUT-T1 | 14.341 | 5.332 | 5.332 | 10.664
|  |  | SHUT-T1 | 14.341 | 5.332 | 5.332
[6 empty] | Maximum Planning Capacity (MVA) | 21.328
Bradshaw MS (Bowmanville - 13.8kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | MS Maximum Planning Capacity (MVA)
| Bradshaw | 13.3 | BRAD-F1 | 7.171 | 3.5467 | 3.5467 | 10.64
|  |  | BRAD-F2 | 7.171 | 3.5467 | 3.5467
|  |  | BRAD-F3 | 7.171 | 3.5467 | 3.5467
| Liberty North | 25 | LIBN-F1 | 6.525 | 6.6667 | 6.525 | 19.575
|  |  | LIBN-F2 | 6.525 | 6.6667 | 6.525
|  |  | LIBN-F3 | 6.525 | 6.6667 | 6.525
| Spry | 16 | SPRY-F1 | 5.2705 | 6.4 | 5.2705 | 10.5409
|  |  | SPRY-F2 | 5.2705 | 6.4 | 5.2705
|  | 20 | SPRY-F3 | 7.1707 | 5.3333 | 5.3333 | 16
|  |  | SPRY-F4 | 7.1707 | 5.3333 | 5.3333
|  |  | SPRY-F5 | 7.1707 | 5.3333 | 5.3333
[6 empty] | Maximum Planning Capacity (MVA) | 56.7559
Winchester West MS (Whitby - 13.8kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | MS Maximum Planning Capacity (MVA)
| Baldwin | 33.3 | BALD-F1 | 7.171 | 6.66 | 6.66 | 26.64
|  |  | BALD-F2 | 7.171 | 6.66 | 6.66
|  |  | BALD-F3 | 7.171 | 6.66 | 6.66
|  |  | BALD-F4 | 7.171 | 6.66 | 6.66
| Conlin | 8 | CONL-F1 | 7.171 | 6.4 | 6.4 | 19.2
|  |  | CONL-F2 | 7.171 | 6.4 | 6.4
|  |  | CONL-F3 | 7.171 | 6.4 | 6.4
| Taunton West | 8 | TAUW-F1 | 7.171 | 6.4 | 6.4 | 19.2
|  |  | TAUW-F2 | 7.171 | 6.4 | 6.4
|  |  | TAUW-F3 | 7.171 | 6.4 | 6.4
| Lawler | 33.3 | LAWL-F1 | 0 | 6.66 | 0 | 13.32
|  |  | LAWL-F2 | 7.1707 | 6.66 | 6.66
|  |  | LAWL-F3 | 0 | 6.66 | 0
|  |  | LAWL-F4 | 7.1707 | 6.66 | 6.66
|  | 25 | LAWL-F5 | 7.1707 | 10 | 7.1707 | 14.3414
|  |  | LAWL-F6 | 7.1707 | 10 | 7.1707
[6 empty] | Maximum Planning Capacity (MVA) | 92.7014
1 Limiting Cable Capacity Along the Feeder (Egress+Trunk)
2 80% of Max Transformer Rating (ONAF) split evenly across feeders

## 2-Staff-62 c) c.
Foster MS (Belleville 13.8 kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | N-1 MS Planning Capacity (MVA)
| Bell | 20 | BELL-F1 | 5.27 | 8 | 5.27 | 12.441
|  |  | BELL-F2 | 7.171 | 8 | 7.171
| Edgehill | 20 | EDGE-F1 | 7.171 | 10 | 7.171 | -
|  |  | EDGE-F2 | 7.171 | 10 | 7.171
| Harder | 10 | HARD-F1 | 7.171 | 8 | 7.171 | 7.171
| Reid | 20 | REID-F1 | 7.171 | 8 | 7.171 | 14.342
|  |  | REID-F2 | 7.171 | 8 | 7.171
| Sidney | 20 | SIDN-F1 | 7.171 | 8 | 7.171 | 14.342
|  |  | SIDN-F2 | 7.171 | 8 | 7.171
[6 empty] | N-1 MS Planning Capacity (MVA) | 48.296
Uxbridge North MS (Uxbridge - 4.16 kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | N-1 MS Planning Capacity
| Uxbridge East | 6.67 | UXBE-F1 | 1.5888 | 1.7787 | 1.5888 | -
|  |  | UXBE-F2 | 2.1616 | 1.7787 | 1.7787
|  |  | UXBE-F3 | 2.1616 | 1.7787 | 1.7787
| Uxbridge West | 5 | UXBW-F1 | 2.1616 | 1.3333 | 1.3333 | 4
|  |  | UXBW-F2 | 2.1616 | 1.3333 | 1.3333
|  |  | UXBW-F3 | 2.1616 | 1.3333 | 1.3333
[6 empty] | N-1 MS Planning Capacity (MVA) | 4
Port Hope 27.6kV MS (Port Hope - 27.6kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | N-1 MS Planning Capacity
| James D Collins | 13.33 | JAME-T1 | 14.341 | 5.332 | 5.332 | -
|  |  | JAME-T1 | 14.341 | 5.332 | 5.332
| Shuter | 13.33 | SHUT-T1 | 14.341 | 5.332 | 5.332 | 10.664
|  |  | SHUT-T1 | 14.341 | 5.332 | 5.332
[6 empty] | N-1 MS Planning Capacity (MVA) | 10.664
Bradshaw MS (Bowmanville - 13.8kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | N-1 MS Planning Capacity (MVA)
| Bradshaw | 13.3 | BRAD-F1 | 7.171 | 3.5467 | 3.5467 | 10.64
|  |  | BRAD-F2 | 7.171 | 3.5467 | 3.5467
|  |  | BRAD-F3 | 7.171 | 3.5467 | 3.5467
| Liberty North | 25 | LIBN-F1 | 6.525 | 6.6667 | 6.525 | -
|  |  | LIBN-F2 | 6.525 | 6.6667 | 6.525
|  |  | LIBN-F3 | 6.525 | 6.6667 | 6.525
| Spry | 16 | SPRY-F1 | 5.2705 | 6.4 | 5.2705 | 10.5409
|  |  | SPRY-F2 | 5.2705 | 6.4 | 5.2705
|  | 20 | SPRY-F3 | 7.1707 | 5.3333 | 5.3333 | 16
|  |  | SPRY-F4 | 7.1707 | 5.3333 | 5.3333
|  |  | SPRY-F5 | 7.1707 | 5.3333 | 5.3333
[6 empty] | N-1 MS Planning Capacity (MVA) | 37.1809
Winchester West MS (Whitby - 13.8kV) | MS | Max Transformer Rating (MVA) | Feeder | Feeder Planning Capacity (MVA)1 | Transformer Planning Capacity per Feeder (MVA)2 | Max Planning Capacity per Feeder (MVA) | N-1 MS Planning Capacity (MVA)
| Baldwin | 33.3 | BALD-F1 | 7.171 | 6.66 | 6.66 | -
|  |  | BALD-F2 | 7.171 | 6.66 | 6.66
|  |  | BALD-F3 | 7.171 | 6.66 | 6.66
|  |  | BALD-F4 | 7.171 | 6.66 | 6.66
| Conlin | 8 | CONL-F1 | 7.171 | 6.4 | 6.4 | 19.2
|  |  | CONL-F2 | 7.171 | 6.4 | 6.4
|  |  | CONL-F3 | 7.171 | 6.4 | 6.4
| Taunton West | 8 | TAUW-F1 | 7.171 | 6.4 | 6.4 | 19.2
|  |  | TAUW-F2 | 7.171 | 6.4 | 6.4
|  |  | TAUW-F3 | 7.171 | 6.4 | 6.4
| Lawler | 33.3 | LAWL-F1 | 0 | 6.66 | 0 | 13.32
|  |  | LAWL-F2 | 7.1707 | 6.66 | 6.66
|  |  | LAWL-F3 | 0 | 6.66 | 0
|  |  | LAWL-F4 | 7.1707 | 6.66 | 6.66
|  | 25 | LAWL-F5 | 7.1707 | 10 | 7.1707 | 14.3414
|  |  | LAWL-F6 | 7.1707 | 10 | 7.1707
[6 empty] | N-1 MS Planning Capacity (MVA) | 66.0614
Please note there was an error in Exhibit 2B / Tab 4 / Schedule 3 / Appendix Table 9. The value for 85MVA for N-1 MS Planning Capacity is incorrect, the actual value is 66MVA as calculated above.
1 Limiting Cable Capacity Along the Feeder (Egress+Trunk)
2 80% of Max Transformer Rating (ONAF) split evenly across feeders