## 2026-FULL
Dry Core Transformer Losses Effective Date January 1, 2026
Implementation Date June 1, 2026
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5703 | 0.1363 |  | 8.1861
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42782 | 4.6505 | 5.0783 | 0.46262 | 5.5409
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2165 | 12.3872 | 13.6037 | 1.3155 | 14.9192
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.622 | 16.5163 | 18.1383 | 1.754 | 19.8922
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0681 | 20.778 | 22.846 | 2.2363 | 25.0823
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7575 | 28.6382 | 31.3957 | 2.9818 | 34.3774
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3251 | 33.2978 | 36.6229 | 3.5956 | 40.2185 |  | 2026 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7282 | 37.2507 | 40.9789 | 4.0314 | 45.0103 |  | LV | Network | Line & Transmission | Variable | Forgone-Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.3997 | 43.8194 | 48.2191 | 4.7576 | 52.9766 | GS 50 to 1,499 kW | 0.02332 | 4.5787 | 2.5918 | 7.6543 | 0.4527
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4743 | 54.341 | 59.8152 | 5.9196 | 65.7348 | GS 1,500 to 4,999 kW | 0.02313 | 4.5424 | 2.5712 | 7.292 | 0.4842
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5983 | 55.5876 | 61.186 | 6.0537 | 67.2397 | Large Use | 0.02716 | 5.334 | 3.0193 | 7.9119 | 0.7633
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8571 | 58.1715 | 64.0286 | 6.3335 | 70.3621
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2942 | 62.5162 | 68.8103 | 6.8062 | 75.6165
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7313 | 66.8608 | 73.5921 | 7.2789 | 80.871 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7057 | 76.7745 | 84.4803 | 8.3326 | 92.8128
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3533 | 83.3771 | 91.7304 | 9.0328 | 100.7632
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63341 | 6.7243 | 7.3577 | 0.68493 | 8.0426
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97322 | 10.19 | 11.1633 | 1.0524 | 12.2157 | WMSR | 0.0041 | Jan 1, 2026 Rate
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9464 | 20.3801 | 22.3265 | 2.1048 | 24.4313 | CBR | 0.0006 | Jan 1, 2026 Rate
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.433 | 24.7744 | 27.2074 | 2.6309 | 29.8384 | RRRP | 0.0006 | Jan 1, 2026 Rate
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.244 | 33.0325 | 36.2766 | 3.5079 | 39.7845
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8604 | 39.5329 | 43.3934 | 4.1744 | 47.5678
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.785 | 49.2836 | 54.0686 | 5.1742 | 59.2428
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.121 | 52.2324 | 57.3534 | 5.5376 | 62.891
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7987 | 58.2048 | 64.0035 | 6.2704 | 70.2739
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2817 | 63.4841 | 69.7657 | 6.7926 | 76.5584
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7699 | 68.8367 | 75.6066 | 7.3206 | 82.9272
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2586 | 74.1906 | 81.4491 | 7.849 | 89.2981
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.774 | 79.632 | 87.406 | 8.4063 | 95.8123
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.7995 | 90.4416 | 99.2411 | 9.5153 | 108.7564
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7535 | 139.8094 | 152.5629 | 13.791 | 166.3539
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7306 | 164.4933 | 179.2239 | 15.9288 | 195.1526
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7076 | 189.1772 | 205.8848 | 18.0666 | 223.9514
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.898 | 239.7869 | 261.6849 | 23.6792 | 285.3641
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5744 | 270.9628 | 295.5373 | 26.5734 | 322.1107
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8469 | 359.6804 | 392.5273 | 35.5188 | 428.0461
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1731 | 430.8208 | 469.9939 | 42.3596 | 512.3534
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0402 | 518.2122 | 565.2524 | 50.8666 | 616.1189
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.475 | 613.066 | 668.541 | 59.9876 | 728.5286
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1274 | 755.3467 | 823.4741 | 73.6691 | 897.1432
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2655 | 872.5878 | 950.8534 | 84.6319 | 1035.4853
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2026
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2027-FULL
Dry Core Transformer Losses Effective Jan 1, 2027
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.571 | 0.1363 |  | 8.6553
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42786 | 4.6505 | 5.0783 | 0.48913 | 5.5675
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2166 | 12.3872 | 13.6038 | 1.3909 | 14.9947
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.5163 | 18.1384 | 1.8545 | 19.9929
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0682 | 20.778 | 22.8462 | 2.3645 | 25.2106
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7577 | 28.6382 | 31.3959 | 3.1526 | 34.5486
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3254 | 33.2978 | 36.6232 | 3.8017 | 40.4248 |  | 2027 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7285 | 37.2507 | 40.9792 | 4.2625 | 45.2417 |  | LV | Network | Line & Transmission | Variable | Forgone-Variable Effective Until May 31, 2027
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4001 | 43.8194 | 48.2194 | 5.0302 | 53.2497 | GS 50 to 1,499 kW | 0.02392 | 4.5787 | 2.5918 | 8.0783 | 0.4527
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4747 | 54.341 | 59.8157 | 6.2588 | 66.0745 | GS 1,500 to 4,999 kW | 0.02373 | 4.5424 | 2.5712 | 7.7595 | 0.4842
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5988 | 55.5876 | 61.1865 | 6.4007 | 67.5871 | Large Use | 0.02787 | 5.334 | 3.0193 | 8.4279 | 0.7633
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8575 | 58.1715 | 64.0291 | 6.6965 | 70.7256
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2947 | 62.5162 | 68.8109 | 7.1963 | 76.0071
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7319 | 66.8608 | 73.5927 | 7.696 | 81.2887 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7064 | 76.7745 | 84.4809 | 8.8101 | 93.291
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.354 | 83.3771 | 91.7311 | 9.5505 | 101.2816
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63346 | 6.7243 | 7.3577 | 0.72419 | 8.0819
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97331 | 10.19 | 11.1634 | 1.1127 | 12.2761 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9466 | 20.3801 | 22.3267 | 2.2254 | 24.5521 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4332 | 24.7744 | 27.2076 | 2.7817 | 29.9894 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2443 | 33.0325 | 36.2768 | 3.709 | 39.9858
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8607 | 39.5329 | 43.3937 | 4.4137 | 47.8074
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7854 | 49.2836 | 54.069 | 5.4708 | 59.5397
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1214 | 52.2324 | 57.3539 | 5.8549 | 63.2088
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7992 | 58.2048 | 64.004 | 6.6297 | 70.6337
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2822 | 63.4841 | 69.7663 | 7.1819 | 76.9482
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7705 | 68.8367 | 75.6071 | 7.7402 | 83.3473
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2592 | 74.1906 | 81.4498 | 8.2988 | 89.7486
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7746 | 79.632 | 87.4066 | 8.8881 | 96.2947
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8002 | 90.4416 | 99.2419 | 10.0606 | 109.3025
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7546 | 139.8094 | 152.564 | 14.5813 | 167.1454
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7318 | 164.4933 | 179.2251 | 16.8417 | 196.0668
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.709 | 189.1772 | 205.8862 | 19.1021 | 224.9882
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.8998 | 239.7869 | 261.6867 | 25.0363 | 286.7231
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5765 | 270.9628 | 295.5393 | 28.0964 | 323.6357
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8497 | 359.6804 | 392.5301 | 37.5545 | 430.0846
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1764 | 430.8208 | 469.9971 | 44.7873 | 514.7844
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0441 | 518.2122 | 565.2563 | 53.7819 | 619.0382
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4797 | 613.066 | 668.5457 | 63.4256 | 731.9713
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1331 | 755.3467 | 823.4798 | 77.8912 | 901.371
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2721 | 872.5878 | 950.86 | 89.4824 | 1040.3424
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2027
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2028-FULL
Dry Core Transformer Losses Effective Jan 1, 2028
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5713 | 0.1363 |  | 8.7791
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42787 | 4.6505 | 5.0783 | 0.49613 | 5.5745
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.3872 | 13.6039 | 1.4108 | 15.0146
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6222 | 16.5163 | 18.1385 | 1.881 | 20.0195
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0683 | 20.778 | 22.8463 | 2.3983 | 25.2446
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7578 | 28.6382 | 31.396 | 3.1978 | 34.5938
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3255 | 33.2978 | 36.6233 | 3.8561 | 40.4794 |  | 2028 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7286 | 37.2507 | 40.9794 | 4.3235 | 45.3028 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4002 | 43.8194 | 48.2196 | 5.1022 | 53.3218 | GS 50 to 1,499 kW | 0.02421 | 4.5787 | 2.5918 | 8.7073
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4749 | 54.341 | 59.8159 | 6.3484 | 66.1643 | GS 1,500 to 4,999 kW | 0.02402 | 4.5424 | 2.5712 | 8.4583
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.599 | 55.5876 | 61.1867 | 6.4923 | 67.6789 | Large Use | 0.02821 | 5.334 | 3.0193 | 9.1718
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8578 | 58.1715 | 64.0293 | 6.7923 | 70.8216
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.295 | 62.5162 | 68.8111 | 7.2992 | 76.1103
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7322 | 66.8608 | 73.5929 | 7.8061 | 81.3991 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7067 | 76.7745 | 84.4812 | 8.9362 | 93.4174
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3544 | 83.3771 | 91.7314 | 9.6872 | 101.4186
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63349 | 6.7243 | 7.3578 | 0.73455 | 8.0923
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97334 | 10.19 | 11.1634 | 1.1286 | 12.292 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9467 | 20.3801 | 22.3268 | 2.2572 | 24.584 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4333 | 24.7744 | 27.2077 | 2.8215 | 30.0293 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2444 | 33.0325 | 36.277 | 3.762 | 40.039
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8609 | 39.5329 | 43.3938 | 4.4768 | 47.8707
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7856 | 49.2836 | 54.0691 | 5.549 | 59.6182
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1216 | 52.2324 | 57.3541 | 5.9387 | 63.2928
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7994 | 58.2048 | 64.0042 | 6.7246 | 70.7288
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2824 | 63.4841 | 69.7665 | 7.2847 | 77.0512
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7707 | 68.8367 | 75.6074 | 7.8509 | 83.4583
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2595 | 74.1906 | 81.45 | 8.4176 | 89.8676
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7749 | 79.632 | 87.407 | 9.0153 | 96.4222
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8006 | 90.4416 | 99.2422 | 10.2046 | 109.4468
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7551 | 139.8094 | 152.5645 | 14.79 | 167.3545
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7324 | 164.4933 | 179.2257 | 17.0827 | 196.3084
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7097 | 189.1772 | 205.8868 | 19.3754 | 225.2622
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9007 | 239.7869 | 261.6876 | 25.3945 | 287.0821
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5775 | 270.9628 | 295.5403 | 28.4984 | 324.0387
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.851 | 359.6804 | 392.5314 | 38.0918 | 430.6232
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.178 | 430.8208 | 469.9987 | 45.4281 | 515.4268
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.046 | 518.2122 | 565.2582 | 54.5513 | 619.8096
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.482 | 613.066 | 668.548 | 64.3331 | 732.881
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1358 | 755.3467 | 823.4826 | 79.0056 | 902.4882
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2753 | 872.5878 | 950.8631 | 90.7626 | 1041.6258
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2028
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2029-FULL
Dry Core Transformer Losses Effective Jan 1, 2029
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5717 | 0.1363 |  | 9.317
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.4279 | 4.6505 | 5.0784 | 0.52653 | 5.6049
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2167 | 12.3872 | 13.6039 | 1.4972 | 15.1011
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6223 | 16.5163 | 18.1386 | 1.9963 | 20.1348
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0684 | 20.778 | 22.8464 | 2.5452 | 25.3916
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.758 | 28.6382 | 31.3962 | 3.3937 | 34.7898
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3257 | 33.2978 | 36.6235 | 4.0923 | 40.7158 |  | 2029 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7289 | 37.2507 | 40.9796 | 4.5884 | 45.5679 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4005 | 43.8194 | 48.2198 | 5.4148 | 53.6346 | GS 50 to 1,499 kW | 0.0246 | 4.5787 | 2.5918 | 9.0386
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4752 | 54.341 | 59.8162 | 6.7373 | 66.5535 | GS 1,500 to 4,999 kW | 0.02441 | 4.5424 | 2.5712 | 8.8266
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5993 | 55.5876 | 61.187 | 6.89 | 68.077 | Large Use | 0.02866 | 5.334 | 3.0193 | 10.0857
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8581 | 58.1715 | 64.0296 | 7.2084 | 71.238
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2953 | 62.5162 | 68.8115 | 7.7464 | 76.5579
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7325 | 66.8608 | 73.5933 | 8.2844 | 81.8777 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7071 | 76.7745 | 84.4816 | 9.4836 | 93.9653
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3548 | 83.3771 | 91.7319 | 10.2806 | 102.0125
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63352 | 6.7243 | 7.3578 | 0.77955 | 8.1374
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.9734 | 10.19 | 11.1634 | 1.1978 | 12.3612 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9468 | 20.3801 | 22.3269 | 2.3955 | 24.7224 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4335 | 24.7744 | 27.2079 | 2.9944 | 30.2022 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2446 | 33.0325 | 36.2772 | 3.9925 | 40.2697
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8611 | 39.5329 | 43.3941 | 4.7511 | 48.1452
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7858 | 49.2836 | 54.0694 | 5.889 | 59.9584
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1219 | 52.2324 | 57.3543 | 6.3025 | 63.6569
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.7997 | 58.2048 | 64.0045 | 7.1366 | 71.1411
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2828 | 63.4841 | 69.7669 | 7.731 | 77.4978
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7711 | 68.8367 | 75.6078 | 8.3319 | 83.9396
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2598 | 74.1906 | 81.4504 | 8.9332 | 90.3837
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7753 | 79.632 | 87.4074 | 9.5676 | 96.9749
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8011 | 90.4416 | 99.2427 | 10.8297 | 110.0724
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7558 | 139.8094 | 152.5652 | 15.696 | 168.2613
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7332 | 164.4933 | 179.2265 | 18.1292 | 197.3557
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7106 | 189.1772 | 205.8878 | 20.5624 | 226.4501
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9019 | 239.7869 | 261.6888 | 26.9503 | 288.6391
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5788 | 270.9628 | 295.5417 | 30.2443 | 325.7859
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8528 | 359.6804 | 392.5332 | 40.4254 | 432.9586
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1801 | 430.8208 | 470.0009 | 48.2111 | 518.212
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0486 | 518.2122 | 565.2608 | 57.8933 | 623.1541
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.485 | 613.066 | 668.551 | 68.2743 | 736.8252
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1395 | 755.3467 | 823.4863 | 83.8457 | 907.332
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2795 | 872.5878 | 950.8674 | 96.323 | 1047.1904
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2029
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2030-FULL
Dry Core Transformer Losses Effective Jan 1, 2030
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.5722 | 0.1363 |  | 9.7906
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.42792 | 4.6505 | 5.0784 | 0.55329 | 5.6317
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2168 | 12.3872 | 13.604 | 1.5733 | 15.1773
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6224 | 16.5163 | 18.1387 | 2.0977 | 20.2364
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.0686 | 20.778 | 22.8465 | 2.6746 | 25.5211
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.7581 | 28.6382 | 31.3964 | 3.5662 | 34.9625
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.3259 | 33.2978 | 36.6237 | 4.3003 | 40.924 |  | 2030 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.7291 | 37.2507 | 40.9798 | 4.8216 | 45.8014 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.4007 | 43.8194 | 48.2201 | 5.69 | 53.9101 | GS 50 to 1,499 kW | 0.02504 | 4.5787 | 2.5918 | 9.3416
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.4756 | 54.341 | 59.8165 | 7.0798 | 66.8963 | GS 1,500 to 4,999 kW | 0.02484 | 4.5424 | 2.5712 | 9.1635
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.5997 | 55.5876 | 61.1873 | 7.2402 | 68.4276 | Large Use | 0.02917 | 5.334 | 3.0193 | 10.8666
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.8585 | 58.1715 | 64.03 | 7.5748 | 71.6048
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.2957 | 62.5162 | 68.8119 | 8.1401 | 76.952
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.7329 | 66.8608 | 73.5937 | 8.7055 | 82.2992 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.7076 | 76.7745 | 84.4821 | 9.9657 | 94.4478
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.3553 | 83.3771 | 91.7324 | 10.8032 | 102.5356
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.63356 | 6.7243 | 7.3578 | 0.81918 | 8.177
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.97346 | 10.19 | 11.1635 | 1.2587 | 12.4222 | WMSR | 0.0041
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9469 | 20.3801 | 22.327 | 2.5173 | 24.8443 | CBR | 0.0006
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4336 | 24.7744 | 27.208 | 3.1466 | 30.3546 | RRRP | 0.0006
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.2448 | 33.0325 | 36.2774 | 4.1955 | 40.4728
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.8613 | 39.5329 | 43.3943 | 4.9926 | 48.3869
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.7861 | 49.2836 | 54.0697 | 6.1883 | 60.258
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.1222 | 52.2324 | 57.3547 | 6.6229 | 63.9775
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.8001 | 58.2048 | 64.0049 | 7.4993 | 71.5042
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.2832 | 63.4841 | 69.7672 | 8.1239 | 77.8912
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.7715 | 68.8367 | 75.6082 | 8.7554 | 84.3636
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.2603 | 74.1906 | 81.4509 | 9.3873 | 90.8382
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.7758 | 79.632 | 87.4079 | 10.0539 | 97.4618
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 8.8016 | 90.4416 | 99.2432 | 11.3802 | 110.6234
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 12.7566 | 139.8094 | 152.566 | 16.4939 | 169.0599
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 14.7341 | 164.4933 | 179.2274 | 19.0507 | 198.2781
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 16.7116 | 189.1772 | 205.8888 | 21.6076 | 227.4964
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 21.9032 | 239.7869 | 261.6901 | 28.3202 | 290.0103
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 24.5803 | 270.9628 | 295.5431 | 31.7816 | 327.3248
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 32.8548 | 359.6804 | 392.5352 | 42.4803 | 435.0155
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 39.1825 | 430.8208 | 470.0032 | 50.6618 | 520.665
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 47.0514 | 518.2122 | 565.2636 | 60.8361 | 626.0998
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 55.4883 | 613.066 | 668.5543 | 71.7448 | 740.2991
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 68.1437 | 755.3467 | 823.4904 | 88.1078 | 911.5982
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 78.2843 | 872.5878 | 950.8721 | 101.2193 | 1052.0914
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2030
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2026 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective Date January 1, 2026
Implementation Date June 1, 2026
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5703 | 0.1363 |  | 8.1861
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42782 | 4.6505 | 5.0783 | 0.46262 | 5.5409
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2165 | 12.3872 | 13.6037 | 1.3155 | 14.9192
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.622 | 16.5163 | 18.1383 | 1.754 | 19.8922
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0681 | 20.778 | 22.846 | 2.2363 | 25.0823
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7575 | 28.6382 | 31.3957 | 2.9818 | 34.3774
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3251 | 33.2978 | 36.6229 | 3.5956 | 40.2185
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7282 | 37.2507 | 40.9789 | 4.0314 | 45.0103
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.3997 | 43.8194 | 48.2191 | 4.7576 | 52.9766
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4743 | 54.341 | 59.8152 | 5.9196 | 65.7348
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5983 | 55.5876 | 61.186 | 6.0537 | 67.2397
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8571 | 58.1715 | 64.0286 | 6.3335 | 70.3621
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2942 | 62.5162 | 68.8103 | 6.8062 | 75.6165
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7313 | 66.8608 | 73.5921 | 7.2789 | 80.871
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7057 | 76.7745 | 84.4803 | 8.3326 | 92.8128
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3533 | 83.3771 | 91.7304 | 9.0328 | 100.7632
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63341 | 6.7243 | 7.3577 | 0.68493 | 8.0426
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97322 | 10.19 | 11.1633 | 1.0524 | 12.2157
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9464 | 20.3801 | 22.3265 | 2.1048 | 24.4313
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.433 | 24.7744 | 27.2074 | 2.6309 | 29.8384
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.244 | 33.0325 | 36.2766 | 3.5079 | 39.7845
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8604 | 39.5329 | 43.3934 | 4.1744 | 47.5678
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.785 | 49.2836 | 54.0686 | 5.1742 | 59.2428
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.121 | 52.2324 | 57.3534 | 5.5376 | 62.891
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7987 | 58.2048 | 64.0035 | 6.2704 | 70.2739
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2817 | 63.4841 | 69.7657 | 6.7926 | 76.5584
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7699 | 68.8367 | 75.6066 | 7.3206 | 82.9272
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2586 | 74.1906 | 81.4491 | 7.849 | 89.2981
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.774 | 79.632 | 87.406 | 8.4063 | 95.8123
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.7995 | 90.4416 | 99.2411 | 9.5153 | 108.7564
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7535 | 139.8094 | 152.5629 | 13.791 | 166.3539
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7306 | 164.4933 | 179.2239 | 15.9288 | 195.1526
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7076 | 189.1772 | 205.8848 | 18.0666 | 223.9514
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.898 | 239.7869 | 261.6849 | 23.6792 | 285.3641
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5744 | 270.9628 | 295.5373 | 26.5734 | 322.1107
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8469 | 359.6804 | 392.5273 | 35.5188 | 428.0461
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1731 | 430.8208 | 469.9939 | 42.3596 | 512.3534
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0402 | 518.2122 | 565.2524 | 50.8666 | 616.1189
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.475 | 613.066 | 668.541 | 59.9876 | 728.5286
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1274 | 755.3467 | 823.4741 | 73.6691 | 897.1432
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2655 | 872.5878 | 950.8534 | 84.6319 | 1035.4853
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2027 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2027
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.571 | 0.1363 |  | 8.6553
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42786 | 4.6505 | 5.0783 | 0.48913 | 5.5675
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2166 | 12.3872 | 13.6038 | 1.3909 | 14.9947
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.5163 | 18.1384 | 1.8545 | 19.9929
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0682 | 20.778 | 22.8462 | 2.3645 | 25.2106
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7577 | 28.6382 | 31.3959 | 3.1526 | 34.5486
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3254 | 33.2978 | 36.6232 | 3.8017 | 40.4248
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7285 | 37.2507 | 40.9792 | 4.2625 | 45.2417
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4001 | 43.8194 | 48.2194 | 5.0302 | 53.2497
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4747 | 54.341 | 59.8157 | 6.2588 | 66.0745
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5988 | 55.5876 | 61.1865 | 6.4007 | 67.5871
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8575 | 58.1715 | 64.0291 | 6.6965 | 70.7256
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2947 | 62.5162 | 68.8109 | 7.1963 | 76.0071
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7319 | 66.8608 | 73.5927 | 7.696 | 81.2887
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7064 | 76.7745 | 84.4809 | 8.8101 | 93.291
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.354 | 83.3771 | 91.7311 | 9.5505 | 101.2816
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63346 | 6.7243 | 7.3577 | 0.72419 | 8.0819
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97331 | 10.19 | 11.1634 | 1.1127 | 12.2761
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9466 | 20.3801 | 22.3267 | 2.2254 | 24.5521
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4332 | 24.7744 | 27.2076 | 2.7817 | 29.9894
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2443 | 33.0325 | 36.2768 | 3.709 | 39.9858
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8607 | 39.5329 | 43.3937 | 4.4137 | 47.8074
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7854 | 49.2836 | 54.069 | 5.4708 | 59.5397
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1214 | 52.2324 | 57.3539 | 5.8549 | 63.2088
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7992 | 58.2048 | 64.004 | 6.6297 | 70.6337
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2822 | 63.4841 | 69.7663 | 7.1819 | 76.9482
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7705 | 68.8367 | 75.6071 | 7.7402 | 83.3473
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2592 | 74.1906 | 81.4498 | 8.2988 | 89.7486
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7746 | 79.632 | 87.4066 | 8.8881 | 96.2947
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8002 | 90.4416 | 99.2419 | 10.0606 | 109.3025
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7546 | 139.8094 | 152.564 | 14.5813 | 167.1454
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7318 | 164.4933 | 179.2251 | 16.8417 | 196.0668
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.709 | 189.1772 | 205.8862 | 19.1021 | 224.9882
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.8998 | 239.7869 | 261.6867 | 25.0363 | 286.7231
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5765 | 270.9628 | 295.5393 | 28.0964 | 323.6357
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8497 | 359.6804 | 392.5301 | 37.5545 | 430.0846
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1764 | 430.8208 | 469.9971 | 44.7873 | 514.7844
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0441 | 518.2122 | 565.2563 | 53.7819 | 619.0382
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4797 | 613.066 | 668.5457 | 63.4256 | 731.9713
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1331 | 755.3467 | 823.4798 | 77.8912 | 901.371
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2721 | 872.5878 | 950.86 | 89.4824 | 1040.3424
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2028 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2028
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5713 | 0.1363 |  | 8.7791
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42787 | 4.6505 | 5.0783 | 0.49613 | 5.5745
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.3872 | 13.6039 | 1.4108 | 15.0146
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6222 | 16.5163 | 18.1385 | 1.881 | 20.0195
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0683 | 20.778 | 22.8463 | 2.3983 | 25.2446
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7578 | 28.6382 | 31.396 | 3.1978 | 34.5938
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3255 | 33.2978 | 36.6233 | 3.8561 | 40.4794
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7286 | 37.2507 | 40.9794 | 4.3235 | 45.3028
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4002 | 43.8194 | 48.2196 | 5.1022 | 53.3218
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4749 | 54.341 | 59.8159 | 6.3484 | 66.1643
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.599 | 55.5876 | 61.1867 | 6.4923 | 67.6789
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8578 | 58.1715 | 64.0293 | 6.7923 | 70.8216
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.295 | 62.5162 | 68.8111 | 7.2992 | 76.1103
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7322 | 66.8608 | 73.5929 | 7.8061 | 81.3991
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7067 | 76.7745 | 84.4812 | 8.9362 | 93.4174
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.3771 | 91.7314 | 9.6872 | 101.4186
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7243 | 7.3578 | 0.73455 | 8.0923
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97334 | 10.19 | 11.1634 | 1.1286 | 12.292
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.3801 | 22.3268 | 2.2572 | 24.584
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.7744 | 27.2077 | 2.8215 | 30.0293
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2444 | 33.0325 | 36.277 | 3.762 | 40.039
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.5329 | 43.3938 | 4.4768 | 47.8707
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.2836 | 54.0691 | 5.549 | 59.6182
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1216 | 52.2324 | 57.3541 | 5.9387 | 63.2928
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.2048 | 64.0042 | 6.7246 | 70.7288
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2824 | 63.4841 | 69.7665 | 7.2847 | 77.0512
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7707 | 68.8367 | 75.6074 | 7.8509 | 83.4583
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.1906 | 81.45 | 8.4176 | 89.8676
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7749 | 79.632 | 87.407 | 9.0153 | 96.4222
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.4416 | 99.2422 | 10.2046 | 109.4468
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7551 | 139.8094 | 152.5645 | 14.79 | 167.3545
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7324 | 164.4933 | 179.2257 | 17.0827 | 196.3084
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7097 | 189.1772 | 205.8868 | 19.3754 | 225.2622
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9007 | 239.7869 | 261.6876 | 25.3945 | 287.0821
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5775 | 270.9628 | 295.5403 | 28.4984 | 324.0387
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.851 | 359.6804 | 392.5314 | 38.0918 | 430.6232
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.178 | 430.8208 | 469.9987 | 45.4281 | 515.4268
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.046 | 518.2122 | 565.2582 | 54.5513 | 619.8096
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.482 | 613.066 | 668.548 | 64.3331 | 732.881
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1358 | 755.3467 | 823.4826 | 79.0056 | 902.4882
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2753 | 872.5878 | 950.8631 | 90.7626 | 1041.6258
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2029 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2029
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5717 | 0.1363 |  | 9.317
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.4279 | 4.6505 | 5.0784 | 0.52653 | 5.6049
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2167 | 12.3872 | 13.6039 | 1.4972 | 15.1011
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6223 | 16.5163 | 18.1386 | 1.9963 | 20.1348
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0684 | 20.778 | 22.8464 | 2.5452 | 25.3916
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.758 | 28.6382 | 31.3962 | 3.3937 | 34.7898
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3257 | 33.2978 | 36.6235 | 4.0923 | 40.7158
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7289 | 37.2507 | 40.9796 | 4.5884 | 45.5679
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4005 | 43.8194 | 48.2198 | 5.4148 | 53.6346
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4752 | 54.341 | 59.8162 | 6.7373 | 66.5535
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5993 | 55.5876 | 61.187 | 6.89 | 68.077
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8581 | 58.1715 | 64.0296 | 7.2084 | 71.238
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2953 | 62.5162 | 68.8115 | 7.7464 | 76.5579
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7325 | 66.8608 | 73.5933 | 8.2844 | 81.8777
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7071 | 76.7745 | 84.4816 | 9.4836 | 93.9653
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3544 | 83.3771 | 91.7319 | 10.2806 | 102.0125
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63349 | 6.7243 | 7.3578 | 0.77955 | 8.1374
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97334 | 10.19 | 11.1634 | 1.1978 | 12.3612
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9467 | 20.3801 | 22.3269 | 2.3955 | 24.7224
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4333 | 24.7744 | 27.2079 | 2.9944 | 30.2022
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2444 | 33.0325 | 36.2772 | 3.9925 | 40.2697
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8609 | 39.5329 | 43.3941 | 4.7511 | 48.1452
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7856 | 49.2836 | 54.0694 | 5.889 | 59.9584
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1216 | 52.2324 | 57.3543 | 6.3025 | 63.6569
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.7994 | 58.2048 | 64.0045 | 7.1366 | 71.1411
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2824 | 63.4841 | 69.7669 | 7.731 | 77.4978
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7707 | 68.8367 | 75.6078 | 8.3319 | 83.9396
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2595 | 74.1906 | 81.4504 | 8.9332 | 90.3837
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7749 | 79.632 | 87.4074 | 9.5676 | 96.9749
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8006 | 90.4416 | 99.2427 | 10.8297 | 110.0724
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7551 | 139.8094 | 152.5652 | 15.696 | 168.2613
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7324 | 164.4933 | 179.2265 | 18.1292 | 197.3557
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7097 | 189.1772 | 205.8878 | 20.5624 | 226.4501
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9007 | 239.7869 | 261.6888 | 26.9503 | 288.6391
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5775 | 270.9628 | 295.5417 | 30.2443 | 325.7859
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.851 | 359.6804 | 392.5332 | 40.4254 | 432.9586
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.178 | 430.8208 | 470.0009 | 48.2111 | 518.212
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.046 | 518.2122 | 565.2608 | 57.8933 | 623.1541
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.482 | 613.066 | 668.551 | 68.2743 | 736.8252
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1358 | 755.3467 | 823.4863 | 83.8457 | 907.332
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2753 | 872.5878 | 950.8674 | 96.323 | 1047.1904
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2030 PDF
PROPOSED - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2030
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2024-0115
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.5722 | 0.1363 |  | 9.7906
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.42792 | 4.6505 | 5.0784 | 0.55329 | 5.6317
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2168 | 12.3872 | 13.604 | 1.5733 | 15.1773
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6224 | 16.5163 | 18.1387 | 2.0977 | 20.2364
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.0686 | 20.778 | 22.8465 | 2.6746 | 25.5211
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.7581 | 28.6382 | 31.3964 | 3.5662 | 34.9625
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.3259 | 33.2978 | 36.6237 | 4.3003 | 40.924
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.7291 | 37.2507 | 40.9798 | 4.8216 | 45.8014
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.4007 | 43.8194 | 48.2201 | 5.69 | 53.9101
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.4756 | 54.341 | 59.8165 | 7.0798 | 66.8963
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.5997 | 55.5876 | 61.1873 | 7.2402 | 68.4276
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.8585 | 58.1715 | 64.03 | 7.5748 | 71.6048
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.2957 | 62.5162 | 68.8119 | 8.1401 | 76.952
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.7329 | 66.8608 | 73.5937 | 8.7055 | 82.2992
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.7076 | 76.7745 | 84.4821 | 9.9657 | 94.4478
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.3553 | 83.3771 | 91.7324 | 10.8032 | 102.5356
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.63356 | 6.7243 | 7.3578 | 0.81918 | 8.177
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.97346 | 10.19 | 11.1635 | 1.2587 | 12.4222
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9469 | 20.3801 | 22.327 | 2.5173 | 24.8443
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4336 | 24.7744 | 27.208 | 3.1466 | 30.3546
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.2448 | 33.0325 | 36.2774 | 4.1955 | 40.4728
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.8613 | 39.5329 | 43.3943 | 4.9926 | 48.3869
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.7861 | 49.2836 | 54.0697 | 6.1883 | 60.258
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.1222 | 52.2324 | 57.3547 | 6.6229 | 63.9775
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.8001 | 58.2048 | 64.0049 | 7.4993 | 71.5042
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.2832 | 63.4841 | 69.7672 | 8.1239 | 77.8912
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.7715 | 68.8367 | 75.6082 | 8.7554 | 84.3636
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.2603 | 74.1906 | 81.4509 | 9.3873 | 90.8382
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.7758 | 79.632 | 87.4079 | 10.0539 | 97.4618
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 8.8016 | 90.4416 | 99.2432 | 11.3802 | 110.6234
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 12.7566 | 139.8094 | 152.566 | 16.4939 | 169.0599
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 14.7341 | 164.4933 | 179.2274 | 19.0507 | 198.2781
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 16.7116 | 189.1772 | 205.8888 | 21.6076 | 227.4964
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 21.9032 | 239.7869 | 261.6901 | 28.3202 | 290.0103
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 24.5803 | 270.9628 | 295.5431 | 31.7816 | 327.3248
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 32.8548 | 359.6804 | 392.5352 | 42.4803 | 435.0155
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 39.1825 | 430.8208 | 470.0032 | 50.6618 | 520.665
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 47.0514 | 518.2122 | 565.2636 | 60.8361 | 626.0998
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 55.4883 | 613.066 | 668.5543 | 71.7448 | 740.2991
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 68.1437 | 755.3467 | 823.4904 | 88.1078 | 911.5982
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 78.2843 | 872.5878 | 950.8721 | 101.2193 | 1052.0914
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard