## 00 Cover
Benefit-Cost Analysis Data Filing Submission Template
All electricity distributors must complete both the Summary tab and the Annual Values tab to accompany their filing submission. Values in the Summary tab should be linked to the Annual Values tab or other additional tabs included by the electricity distributor using formulas.
Electricity distributors are strongly encouraged to include additional tabs providing the upstream calculations that deliver the Annual Values tab and Summary tab outputs.
Ontario Energy Board

## 01 Summary
General Information
Electricity Distributor Name | Elexicon Energy Inc.
Project or Program Name | Bradshaw Battery Storage Station Deferal
Description of NWS(s) (<150 words) | Elexicon proposes to administer a 13 MW/53 MWh (4-hour) distribution battery to defer the expansion of the Bradshaw MS Upgrade by 4 years to 2035
Year for Net Present Value | 2026
Constant Dollar Year (i.e., nominal values deflated to this year) | 2026
Distribution Service Test
DST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV (Millions 2026 $)
Distribution Capacity Benefit | Distribution Capacity (Deferral or Avoidance Benefit) | 1.151
Total DST Benefit |  | 1.151
DST Costs
(Add more rows as required)
Cost | Cost Type | NPV (Millions 2026 $)
Capital Cost (Nominal $) | BESS Acquisition Cost | 17.5453
Fixed O&M (Nominal $) | BESS Operations, Maintenance, and Administrative (OM&A) Costs | 6.5558
Total DST Cost |  | 24.1011
NPV Net DST Benefit | -22.9501
Energy System Test (NOT APPLICABLE)
EST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV
Benefit 1 [replace name]
Benefit 2 [replace name]
Benefit 3 [replace name]
Benefit 4 [replace name]
Benefit 5 [replace name]
Benefit 6 [replace name]
Total EST Benefit
EST Costs
(Add more rows as required)
Cost | Cost Type | NPV
Cost 1 [replace name]
Cost 2 [replace name]
Cost 3 [replace name]
Cost 4 [replace name]
Cost 5 [replace name]
Cost 6 [replace name]
Total EST Cost
NPV Net EST Benefit

## 02 Annual Values
Use only such rows as are required. Insert additional columns as required.
| Distribution Service Benefits | Distribution Service Costs
Calendar Year | Distribution Capacity Benefit | Capital Cost (Nominal $) | Fixed O&M (Nominal $)
2026 | 0 | 0 | 0
2027 | 0 | 0 | 0
2028 | 0 | 0 | 0
2029 | 0 | 0 | 0
2030 | 0 | 0 | 0
2031 | 0.916 | 2.1661 | 0.80935
2032 | 0.87559 | 2.1236 | 0.79348
2033 | 0.83641 | 2.082 | 0.77792
2034 | 0.79843 | 2.0411 | 0.76267
2035 | -0.15438 | 2.0011 | 0.74772
2036 | -0.14965 | 1.9619 | 0.73305
2037 | -0.14503 | 1.9234 | 0.71868
2038 | -0.14055 | 1.8857 | 0.70459
2039 | -0.13618 | 1.8487 | 0.69077
2040 | -0.13193 | 1.8125 | 0.67723
2041 | -0.1278 | 1.7769 | 0.66395
2042 | -0.12377 | 1.7421 | 0.65093
2043 | -0.11986 | 1.7079 | 0.63817
2044 | -0.11605 | 1.6745 | 0.62565
2045 | -0.11234 | 1.6416 | 0.61339
2046 | -0.10874 | 0 | 0
2047 | -0.10523 | 0 | 0
2048 | -0.10182 | 0 | 0
2049 | -0.098499 | 0 | 0
2050 | -0.095271 | 0 | 0
2051 | -0.092133 | 0 | 0
2052 | -0.089081 | 0 | 0
2053 | -0.086113 | 0 | 0
2054 | -0.083228 | 0 | 0
2055 | -0.080422 | 0 | 0
2056 | -0.077695 | 0 | 0
2057 | -0.075043 | 0 | 0
2058 | -0.072466 | 0 | 0
2059 | -0.069961 | 0 | 0
2060 | -0.067526 | 0 | 0
2061 | -0.06516 | 0 | 0
2062 | -0.06286 | 0 | 0
2063 | -0.060626 | 0 | 0
2064 | -0.058455 | 0 | 0
2065 | -0.056346 | 0 | 0
2066 | -0.054298 | 0 | 0
2067 | -0.052308 | 0 | 0
2068 | -0.050375 | 0 | 0
2069 | -0.048498 | 0 | 0
2070 | -0.046675 | 0 | 0
2071 | -0.044904 | 0 | 0
2072 | -0.033018 | 0 | 0
2073 | -0.02158 | 0 | 0
2074 | -0.010579 | 0 | 0
2075 | 0 | 0 | 0
NPV | 1.151 | 17.5453 | 6.5558

## Inputs and Assumptions
Assumptions
Calculated Value
Economic Assumption | Value | Source |  | Manual Input
Debt % | 60% | Assumed
Equity % | 40%
Allowed Return on Equity (ROE) | 9.21% | Ontario Energy Board, 2024 Cost of Capital Parameters, October 2023
Deemed Long-Term Debt Rate | 4.88%
Federal Tax Rate | 15% | Government of Canada, Corporation Tax Rates, May 2022
Provincial Tax Rate | 11.5% | Government of Canada, Ontario – Provincial corporation tax, August 2023
Pre-tax Weighted Average Cost of Capital (WACC) | 7.94% | Calculated
O&M (percentage of capital expenditure) | 1.5% | Assumed
Inflation Rate | 2% | IESO Guide for NWAs
Social Discount Rate | 4%
Capital Recovery Factor | 11.94% | Calculated
LDC Calculations Inputs - Traditional Asset (Poles and Wires)
Inputs | Value | Source
Asset Life (years) | 40 | Assumed
Asset Cost (Millions $ - Nominal) | 8.47 | From DSP Budget
Asset Depreciation | Straight-line 2.5% per year for 40 years | Assumed
Depreciation | 2.5% | Assumed
LDC Calculations Inputs - Non Wire Solution Costs and Benefits (Millions $)
Inputs | Value | Source
Battery Storage Cost (2026 $) | 38.9967 | Per LDC Calculations
Distribution Capacity Benefit (2026 $) | 1.151 | Per LDC Calculations
Cost 1 Capital Cost Nominal ($) | 35.8729 | Per LDC Calculations
Cost 2 Fixed O&M (Nominal $) | 13.4038 | Per LDC Calculations
LDC Calculations Inputs - Traditional Solution Expenditure Timelines (Millions $)
Year | Cost ($M) | Source
2029 | 2.19 | Elexicon DSP
2030 | 2.29 | Elexicon DSP
2031 | 3.99 | Elexicon DSP
Total | 8.47 | Elexicon DSP
LDC Calculations Inputs - Non-Wire Solution Parameters
Inputs | Value | Source
Battery Specs
Battery Size (MW) | 13.2 | Based on projected load growth; accounts for 10% efficiency loss
Hours | 4 | Based on number of consecutive hours in violation in 2031
Battery Discharge (MWh) | 52.8 | Calculated
Average Useful Life | 15 | Informed by Industry Research and EnergyAnalytics, 2025
Capital Cost ($/MW) - 2026 (8-hr battery) | 2717644.7873 | Calculated, including price reductions from 2024-2026 in NREL ATB
Fixed O&M ($/MW-year) - 2026 (8-hr battery) | 67696.1664 | Calculated, including price reductions from 2024-2026 in NREL ATB
Deferral Period (years) | 4 | Assumed
4-hour to 8-hour cost ratio
Capital Cost ($/kW)-2024 (4-hr battery) | 3051 | IESO, 2024
Fixed O&M ($/kW-year)-2024 (4-hr battery) | 76 | IESO, 2024
Capital Cost ($/kW) | 1.7424 | Calculated Using NREL ATB Baseline Capex ratio between 8-hr and 4-hr storage systems in 2026
Fixed O&M ($/kW-year) | 1.7919 | Calculated Using NREL ATB Baseline Fixed O&M ratio between 8-hr and 4-hr storage systems in 2026
Capital Cost ($/kW)-2024 (8-hr battery) | 5316.1403 | Calculated
Fixed O&M ($/kW-year)-2024 (8-hr battery) | 136.1837 | Calculated
2024-2026 Price Reduction | 14.38% | Calculated Using NREL ATB Baseline cost reduction in 4-hour battery storage in 2026 vs 2024 |  |  | Capital Cost ($/MW) - 2026 (4-hr battery)
Capital Cost ($/MW) - 2026 (4-hr battery) | 2717644.7873 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (4-hr battery) | 67696.1664 | Calculated Using IESO, 2024
Capital Cost ($/MW) - 2026 (8-hr battery) | 4735293.6262 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (8-hr battery) | 121304.1519 | Calculated Using IESO, 2024
Actual Asset Costs - Millions $ (Nominal)
Year | Inflation Index | Traditional Poles and Wires | Deferral via NWS
2026 | 100%
2027 | 102%
2028 | 104%
2029 | 106.1% | 2.19
2030 | 108.2% | 2.29 | 0
2031 | 110.4% | 3.99 | 0
2032 | 112.6% |  | 0
2033 | 114.9% |  | 2.3705
2034 | 117.2% |  | 2.4788
2035 | 119.5% |  | 4.3189
2036 | 121.9% |  | 0
2037 | 124.3% |  | 0
2038 | 126.8% |  | 0
2039 | 129.4% |  | 0
2040 | 131.9% |  | 0
2041 | 134.6% |  | 0
2042 | 137.3% |  | 0
2043 | 140% |  | 0
2044 | 142.8%
2045 | 145.7%
2046 | 148.6%
2047 | 151.6%
2048 | 154.6%
2049 | 157.7%
2050 | 160.8%
2051 | 164.1%
2052 | 167.3%
2053 | 170.7%
2054 | 174.1%
2055 | 177.6%
2056 | 181.1%
2057 | 184.8%
2058 | 188.5%
2059 | 192.2%
2060 | 196.1%
2061 | 200%
2062 | 204%
2063 | 208.1%
2064 | 212.2%
2065 | 216.5%
2066 | 220.8%
2067 | 225.2%
2068 | 229.7%
2069 | 234.3%
2070 | 239%
2071 | 243.8%
2072 | 248.7%
2073 | 253.6%
2074 | 258.7%
2075 | 263.9%
2076 | 269.2%
2077 | 274.5%
2078 | 280%
2079 | 285.6%
2080 | 291.3%

## Elexicon Calculations
Battery Storage |  |  |  |  | Alternative (Expansion) | [9 empty] | NPV Summary
|  |  | NPV | 24.1011 |  |  |  | NPV | 7.927 |  |  |  | NPV | 6.7761
|  |  |  | Cost - Millions (2026 $) |  | Installed at Time of Need |  |  |  |  | Deferred Installation |  |  |  |  | Cost of NWA | 24.1011
[8 empty] | Nominal | 2026 $ |  |  |  | Nominal | 2026 $ |  | Total Benefit of NWA | 1.151
| Calendar Year | Cost 1 Capital Cost Nominal ($) | Cost 2 Fixed O&M (Nominal $) | Battery Storage Cost | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements |  | Net Benefit | -22.9501
| 2026 |  |  | 0 | 2026 | 0 |  | 0 | 0 | 2026 | 0 | 0 | 0 | 0
| 2027 |  |  | 0 | 2027 | 0 |  | 0 | 0 | 2027 | 0 | 0 | 0 | 0
| 2028 |  |  | 0 | 2028 | 0 |  | 0 | 0 | 2028 | 0 | 0 | 0 | 0
| 2029 |  |  | 0 | 2029 | 0 |  | 0 | 0 | 2029 | 0 | 0 | 0 | 0
| 2030 |  |  | 0 | 2030 | 0 |  | 0 | 0 | 2030 | 0 | 0 | 0 | 0
| 2031 | 2.1661 | 0.80935 | 2.9754 | 2031 | 8.47 | -0.21175 | 1.0113 | 0.916 | 2031 | 0 | 0 | 0 | 0
| 2032 | 2.1236 | 0.79348 | 2.9171 | 2032 | 8.2583 | -0.21175 | 0.98606 | 0.87559 | 2032 | 0 | 0 | 0 | 0
| 2033 | 2.082 | 0.77792 | 2.8599 | 2033 | 8.0465 | -0.21175 | 0.96077 | 0.83641 | 2033 | 0 | 0 | 0 | 0
| 2034 | 2.0411 | 0.76267 | 2.8038 | 2034 | 7.8347 | -0.21175 | 0.93549 | 0.79843 | 2034 | 0 | 0 | 0 | 0
| 2035 | 2.0011 | 0.74772 | 2.7488 | 2035 | 7.623 | -0.21175 | 0.9102 | 0.76162 | 2035 | 9.1682 | -0.22921 | 1.0947 | 0.916
| 2036 | 1.9619 | 0.73305 | 2.6949 | 2036 | 7.4112 | -0.21175 | 0.88492 | 0.72594 | 2036 | 8.939 | -0.22921 | 1.0673 | 0.87559
| 2037 | 1.9234 | 0.71868 | 2.6421 | 2037 | 7.1995 | -0.21175 | 0.85964 | 0.69138 | 2037 | 8.7098 | -0.22921 | 1.04 | 0.83641
| 2038 | 1.8857 | 0.70459 | 2.5903 | 2038 | 6.9877 | -0.21175 | 0.83435 | 0.65788 | 2038 | 8.4806 | -0.22921 | 1.0126 | 0.79843
| 2039 | 1.8487 | 0.69077 | 2.5395 | 2039 | 6.776 | -0.21175 | 0.80907 | 0.62544 | 2039 | 8.2514 | -0.22921 | 0.98524 | 0.76162
| 2040 | 1.8125 | 0.67723 | 2.4897 | 2040 | 6.5642 | -0.21175 | 0.78379 | 0.59401 | 2040 | 8.0222 | -0.22921 | 0.95787 | 0.72594
| 2041 | 1.7769 | 0.66395 | 2.4409 | 2041 | 6.3525 | -0.21175 | 0.7585 | 0.56358 | 2041 | 7.793 | -0.22921 | 0.9305 | 0.69138
| 2042 | 1.7421 | 0.65093 | 2.393 | 2042 | 6.1407 | -0.21175 | 0.73322 | 0.53411 | 2042 | 7.5638 | -0.22921 | 0.90313 | 0.65788
| 2043 | 1.7079 | 0.63817 | 2.3461 | 2043 | 5.929 | -0.21175 | 0.70794 | 0.50558 | 2043 | 7.3346 | -0.22921 | 0.87576 | 0.62544
| 2044 | 1.6745 | 0.62565 | 2.3001 | 2044 | 5.7172 | -0.21175 | 0.68265 | 0.47797 | 2044 | 7.1054 | -0.22921 | 0.8484 | 0.59401
| 2045 | 1.6416 | 0.61339 | 2.255 | 2045 | 5.5055 | -0.21175 | 0.65737 | 0.45124 | 2045 | 6.8762 | -0.22921 | 0.82103 | 0.56358
| 2046 |  |  |  | 2046 | 5.2937 | -0.21175 | 0.63209 | 0.42538 | 2046 | 6.6469 | -0.22921 | 0.79366 | 0.53411
| 2047 |  |  |  | 2047 | 5.082 | -0.21175 | 0.6068 | 0.40035 | 2047 | 6.4177 | -0.22921 | 0.76629 | 0.50558
| 2048 |  |  |  | 2048 | 4.8702 | -0.21175 | 0.58152 | 0.37615 | 2048 | 6.1885 | -0.22921 | 0.73893 | 0.47797
| 2049 |  |  |  | 2049 | 4.6585 | -0.21175 | 0.55624 | 0.35274 | 2049 | 5.9593 | -0.22921 | 0.71156 | 0.45124
| 2050 |  |  |  | 2050 | 4.4467 | -0.21175 | 0.53095 | 0.3301 | 2050 | 5.7301 | -0.22921 | 0.68419 | 0.42538
| 2051 |  |  |  | 2051 | 4.235 | -0.21175 | 0.50567 | 0.30822 | 2051 | 5.5009 | -0.22921 | 0.65682 | 0.40035
| 2052 |  |  |  | 2052 | 4.0232 | -0.21175 | 0.48039 | 0.28707 | 2052 | 5.2717 | -0.22921 | 0.62946 | 0.37615
| 2053 |  |  |  | 2053 | 3.8115 | -0.21175 | 0.4551 | 0.26663 | 2053 | 5.0425 | -0.22921 | 0.60209 | 0.35274
| 2054 |  |  |  | 2054 | 3.5997 | -0.21175 | 0.42982 | 0.24688 | 2054 | 4.8133 | -0.22921 | 0.57472 | 0.3301
| 2055 |  |  |  | 2055 | 3.388 | -0.21175 | 0.40454 | 0.2278 | 2055 | 4.5841 | -0.22921 | 0.54735 | 0.30822
| 2056 |  |  |  | 2056 | 3.1762 | -0.21175 | 0.37925 | 0.20937 | 2056 | 4.3549 | -0.22921 | 0.51999 | 0.28707
| 2057 |  |  |  | 2057 | 2.9645 | -0.21175 | 0.35397 | 0.19158 | 2057 | 4.1257 | -0.22921 | 0.49262 | 0.26663
| 2058 |  |  |  | 2058 | 2.7527 | -0.21175 | 0.32869 | 0.17441 | 2058 | 3.8965 | -0.22921 | 0.46525 | 0.24688
| 2059 |  |  |  | 2059 | 2.541 | -0.21175 | 0.3034 | 0.15784 | 2059 | 3.6673 | -0.22921 | 0.43788 | 0.2278
| 2060 |  |  |  | 2060 | 2.3292 | -0.21175 | 0.27812 | 0.14185 | 2060 | 3.4381 | -0.22921 | 0.41051 | 0.20937
| 2061 |  |  |  | 2061 | 2.1175 | -0.21175 | 0.25283 | 0.12642 | 2061 | 3.2089 | -0.22921 | 0.38315 | 0.19158
| 2062 |  |  |  | 2062 | 1.9057 | -0.21175 | 0.22755 | 0.11155 | 2062 | 2.9797 | -0.22921 | 0.35578 | 0.17441
| 2063 |  |  |  | 2063 | 1.694 | -0.21175 | 0.20227 | 0.097212 | 2063 | 2.7505 | -0.22921 | 0.32841 | 0.15784
| 2064 |  |  |  | 2064 | 1.4822 | -0.21175 | 0.17698 | 0.083393 | 2064 | 2.5213 | -0.22921 | 0.30104 | 0.14185
| 2065 |  |  |  | 2065 | 1.2705 | -0.21175 | 0.1517 | 0.070078 | 2065 | 2.2921 | -0.22921 | 0.27368 | 0.12642
| 2066 |  |  |  | 2066 | 1.0587 | -0.21175 | 0.12642 | 0.057253 | 2066 | 2.0628 | -0.22921 | 0.24631 | 0.11155
| 2067 |  |  |  | 2067 | 0.847 | -0.21175 | 0.10113 | 0.044904 | 2067 | 1.8336 | -0.22921 | 0.21894 | 0.097212
| 2068 |  |  |  | 2068 | 0.63525 | -0.21175 | 0.07585 | 0.033018 | 2068 | 1.6044 | -0.22921 | 0.19157 | 0.083393
| 2069 |  |  |  | 2069 | 0.4235 | -0.21175 | 0.050567 | 0.02158 | 2069 | 1.3752 | -0.22921 | 0.16421 | 0.070078
| 2070 |  |  |  | 2070 | 0.21175 | -0.21175 | 0.025283 | 0.010579 | 2070 | 1.146 | -0.22921 | 0.13684 | 0.057253
| 2071 |  |  |  | 2071 | -5.7176e-15 | -0.21175 | -6.827e-16 | -2.8004e-16 | 2071 | 0.91682 | -0.22921 | 0.10947 | 0.044904
| 2072 |  |  |  | 2072 |  |  |  |  | 2072 | 0.68762 | -0.22921 | 0.082103 | 0.033018
| 2073 |  |  |  | 2073 |  |  |  |  | 2073 | 0.45841 | -0.22921 | 0.054735 | 0.02158
| 2074 |  |  |  | 2074 |  |  |  |  | 2074 | 0.22921 | -0.22921 | 0.027368 | 0.010579
| 2075 |  |  |  | 2075 |  |  |  |  | 2075 | 0 | -0.22921 | 0 | 0
| 2076 |  |  |  | 2076 |  |  |  |  | 2076 | 0 | -0.22921 | 0 | 0

## BESS Inputs
Min MW BESS
Deferral length | Year | Bradshaw
1 | 2032 | 9
2 | 2033 | 10
3 | 2034 | 11
4 | 2035 | 12
Duration | Hours
Bradshaw | 4
CapEx for Deferred traditional solution - years of spend
Deferral length | Year1 | Year2 | Year3
1 | 2030 | 2031 | 2032
2 | 2031 | 2032 | 2033
3 | 2032 | 2033 | 2034
4 | 2033 | 2034 | 2035

## Input Calculation >>
The following tabs show how the battery solution was sized

## BESS Duration
Date | Hour | Date-Time | BRADSHAW MS 2025 (MVA) | BRADSHAW MS 2031 (MVA) | Exceeds Planning Capacity (Y/N) | MVA exceeding peak | Consecutive hours | Total consecutive length | Duration Determination
2025-01-01 | 00 | 2031-01-01 | 4 | 5.0315 | N | 0 |  |  |  | Bradshaw 2031
2025-01-01 | 01 | 2031-01-01 01:00 | 3.61 | 4.541 | N | 0 |  |  | 2031 PEAK (MVA) | 19.95
2025-01-01 | 02 | 2031-01-01 02:00 | 3.44 | 4.3271 | N | 0 |  |  | # of hours exceeding | 80
2025-01-01 | 03 | 2031-01-01 03:00 | 3.22 | 4.0504 | N | 0 |  |  | % of hours | 0.9132%
2025-01-01 | 04 | 2031-01-01 04:00 | 3.1 | 3.8994 | N | 0 |  |  | MVA > N-1
2025-01-01 | 05 | 2031-01-01 05:00 | 3.04 | 3.824 | N | 0 |  |  | avg | 1.282
2025-01-01 | 06 | 2031-01-01 06:00 | 3.11 | 3.912 | N | 0 |  |  | max | 9.31
2025-01-01 | 07 | 2031-01-01 07:00 | 3.3 | 4.151 | N | 0 |  |  | median | 0.32244
2025-01-01 | 08 | 2031-01-01 08:00 | 3.39 | 4.2642 | N | 0 |  |  | MW>N-1
2025-01-01 | 09 | 2031-01-01 09:00 | 3.58 | 4.5032 | N | 0 |  |  | avg | 1.1538
2025-01-01 | 10 | 2031-01-01 10:00 | 3.87 | 4.868 | N | 0 |  |  | max | 8.379
2025-01-01 | 11 | 2031-01-01 11:00 | 4.24 | 5.3334 | N | 0 |  |  | median | 0.29019
2025-01-01 | 12 | 2031-01-01 12:00 | 4.56 | 5.7359 | N | 0 |  |  | # of consecutive hours
2025-01-01 | 13 | 2031-01-01 13:00 | 4.59 | 5.7737 | N | 0 |  |  | avg | 3.3333
2025-01-01 | 14 | 2031-01-01 14:00 | 4.68 | 5.8869 | N | 0 |  |  | max | 11
2025-01-01 | 15 | 2031-01-01 15:00 | 4.46 | 5.6102 | N | 0 |  |  | median | 2
2025-01-01 | 16 | 2031-01-01 16:00 | 4.75 | 5.9749 | N | 0
2025-01-01 | 17 | 2031-01-01 17:00 | 5.03 | 6.3271 | N | 0
2025-01-01 | 18 | 2031-01-01 18:00 | 5.38 | 6.7674 | N | 0
2025-01-01 | 19 | 2031-01-01 19:00 | 5.34 | 6.7171 | N | 0
2025-01-01 | 20 | 2031-01-01 20:00 | 5.07 | 6.3775 | N | 0
2025-01-01 | 21 | 2031-01-01 21:00 | 4.84 | 6.0881 | N | 0
2025-01-01 | 22 | 2031-01-01 22:00 | 4.58 | 5.7611 | N | 0
2025-01-01 | 23 | 2031-01-01 23:00 | 4.35 | 5.4718 | N | 0
2025-01-02 | 00 | 2031-01-02 | 4.02 | 5.0567 | N | 0
2025-01-02 | 01 | 2031-01-02 01:00 | 3.62 | 4.5535 | N | 0
2025-01-02 | 02 | 2031-01-02 02:00 | 3.36 | 4.2265 | N | 0
2025-01-02 | 03 | 2031-01-02 03:00 | 3.31 | 4.1636 | N | 0
2025-01-02 | 04 | 2031-01-02 04:00 | 3.25 | 4.0881 | N | 0
2025-01-02 | 05 | 2031-01-02 05:00 | 3.21 | 4.0378 | N | 0
2025-01-02 | 06 | 2031-01-02 06:00 | 3.43 | 4.3145 | N | 0
2025-01-02 | 07 | 2031-01-02 07:00 | 3.57 | 4.4906 | N | 0
2025-01-02 | 08 | 2031-01-02 08:00 | 3.94 | 4.9561 | N | 0
2025-01-02 | 09 | 2031-01-02 09:00 | 4.14 | 5.2076 | N | 0
2025-01-02 | 10 | 2031-01-02 10:00 | 4.31 | 5.4215 | N | 0
2025-01-02 | 11 | 2031-01-02 11:00 | 4.4 | 5.5347 | N | 0
2025-01-02 | 12 | 2031-01-02 12:00 | 4.53 | 5.6982 | N | 0
2025-01-02 | 13 | 2031-01-02 13:00 | 4.59 | 5.7737 | N | 0
2025-01-02 | 14 | 2031-01-02 14:00 | 4.54 | 5.7108 | N | 0
2025-01-02 | 15 | 2031-01-02 15:00 | 4.49 | 5.6479 | N | 0
2025-01-02 | 16 | 2031-01-02 16:00 | 4.72 | 5.9372 | N | 0
2025-01-02 | 17 | 2031-01-02 17:00 | 5.28 | 6.6416 | N | 0
2025-01-02 | 18 | 2031-01-02 18:00 | 5.7 | 7.1699 | N | 0
2025-01-02 | 19 | 2031-01-02 19:00 | 5.62 | 7.0693 | N | 0
2025-01-02 | 20 | 2031-01-02 20:00 | 5.27 | 6.629 | N | 0
2025-01-02 | 21 | 2031-01-02 21:00 | 5.21 | 6.5536 | N | 0
2025-01-02 | 22 | 2031-01-02 22:00 | 4.9 | 6.1636 | N | 0
2025-01-02 | 23 | 2031-01-02 23:00 | 4.64 | 5.8366 | N | 0
2025-01-03 | 00 | 2031-01-03 | 4.28 | 5.3837 | N | 0
2025-01-03 | 01 | 2031-01-03 01:00 | 3.96 | 4.9812 | N | 0
2025-01-03 | 02 | 2031-01-03 02:00 | 3.58 | 4.5032 | N | 0
2025-01-03 | 03 | 2031-01-03 03:00 | 3.6 | 4.5284 | N | 0
2025-01-03 | 04 | 2031-01-03 04:00 | 3.46 | 4.3523 | N | 0
2025-01-03 | 05 | 2031-01-03 05:00 | 3.46 | 4.3523 | N | 0
2025-01-03 | 06 | 2031-01-03 06:00 | 3.82 | 4.8051 | N | 0
2025-01-03 | 07 | 2031-01-03 07:00 | 3.91 | 4.9183 | N | 0
2025-01-03 | 08 | 2031-01-03 08:00 | 4.1 | 5.1573 | N | 0
2025-01-03 | 09 | 2031-01-03 09:00 | 4.33 | 5.4466 | N | 0
2025-01-03 | 10 | 2031-01-03 10:00 | 4.39 | 5.5221 | N | 0
2025-01-03 | 11 | 2031-01-03 11:00 | 4.59 | 5.7737 | N | 0
2025-01-03 | 12 | 2031-01-03 12:00 | 4.84 | 6.0881 | N | 0
2025-01-03 | 13 | 2031-01-03 13:00 | 4.73 | 5.9498 | N | 0
2025-01-03 | 14 | 2031-01-03 14:00 | 4.83 | 6.0756 | N | 0
2025-01-03 | 15 | 2031-01-03 15:00 | 4.8 | 6.0378 | N | 0
2025-01-03 | 16 | 2031-01-03 16:00 | 4.81 | 6.0504 | N | 0
2025-01-03 | 17 | 2031-01-03 17:00 | 5.19 | 6.5284 | N | 0
2025-01-03 | 18 | 2031-01-03 18:00 | 5.63 | 7.0819 | N | 0
2025-01-03 | 19 | 2031-01-03 19:00 | 5.66 | 7.1196 | N | 0
2025-01-03 | 20 | 2031-01-03 20:00 | 5.39 | 6.78 | N | 0
2025-01-03 | 21 | 2031-01-03 21:00 | 5.21 | 6.5536 | N | 0
2025-01-03 | 22 | 2031-01-03 22:00 | 5.05 | 6.3523 | N | 0
2025-01-03 | 23 | 2031-01-03 23:00 | 4.79 | 6.0253 | N | 0
2025-01-04 | 00 | 2031-01-04 | 4.46 | 5.6102 | N | 0
2025-01-04 | 01 | 2031-01-04 01:00 | 4.12 | 5.1825 | N | 0
2025-01-04 | 02 | 2031-01-04 02:00 | 3.94 | 4.9561 | N | 0
2025-01-04 | 03 | 2031-01-04 03:00 | 3.73 | 4.6919 | N | 0
2025-01-04 | 04 | 2031-01-04 04:00 | 3.71 | 4.6667 | N | 0
2025-01-04 | 05 | 2031-01-04 05:00 | 3.66 | 4.6038 | N | 0
2025-01-04 | 06 | 2031-01-04 06:00 | 3.8 | 4.7799 | N | 0
2025-01-04 | 07 | 2031-01-04 07:00 | 3.86 | 4.8554 | N | 0
2025-01-04 | 08 | 2031-01-04 08:00 | 4.14 | 5.2076 | N | 0
2025-01-04 | 09 | 2031-01-04 09:00 | 4.38 | 5.5095 | N | 0
2025-01-04 | 10 | 2031-01-04 10:00 | 4.59 | 5.7737 | N | 0
2025-01-04 | 11 | 2031-01-04 11:00 | 4.78 | 6.0127 | N | 0
2025-01-04 | 12 | 2031-01-04 12:00 | 5.03 | 6.3271 | N | 0
2025-01-04 | 13 | 2031-01-04 13:00 | 5.27 | 6.629 | N | 0
2025-01-04 | 14 | 2031-01-04 14:00 | 5.17 | 6.5032 | N | 0
2025-01-04 | 15 | 2031-01-04 15:00 | 5.34 | 6.7171 | N | 0
2025-01-04 | 16 | 2031-01-04 16:00 | 5.27 | 6.629 | N | 0
2025-01-04 | 17 | 2031-01-04 17:00 | 5.52 | 6.9435 | N | 0
2025-01-04 | 18 | 2031-01-04 18:00 | 5.82 | 7.3209 | N | 0
2025-01-04 | 19 | 2031-01-04 19:00 | 5.82 | 7.3209 | N | 0
2025-01-04 | 20 | 2031-01-04 20:00 | 5.58 | 7.019 | N | 0
2025-01-04 | 21 | 2031-01-04 21:00 | 5.45 | 6.8555 | N | 0
2025-01-04 | 22 | 2031-01-04 22:00 | 5.12 | 6.4404 | N | 0
2025-01-04 | 23 | 2031-01-04 23:00 | 4.87 | 6.1259 | N | 0
2025-01-05 | 00 | 2031-01-05 | 4.51 | 5.673 | N | 0
2025-01-05 | 01 | 2031-01-05 01:00 | 4.2 | 5.2831 | N | 0
2025-01-05 | 02 | 2031-01-05 02:00 | 3.93 | 4.9435 | N | 0
2025-01-05 | 03 | 2031-01-05 03:00 | 3.72 | 4.6793 | N | 0
2025-01-05 | 04 | 2031-01-05 04:00 | 3.64 | 4.5787 | N | 0
2025-01-05 | 05 | 2031-01-05 05:00 | 3.7 | 4.6542 | N | 0
2025-01-05 | 06 | 2031-01-05 06:00 | 3.67 | 4.6164 | N | 0
2025-01-05 | 07 | 2031-01-05 07:00 | 3.74 | 4.7045 | N | 0
2025-01-05 | 08 | 2031-01-05 08:00 | 4.12 | 5.1825 | N | 0
2025-01-05 | 09 | 2031-01-05 09:00 | 4.26 | 5.3586 | N | 0
2025-01-05 | 10 | 2031-01-05 10:00 | 4.63 | 5.824 | N | 0
2025-01-05 | 11 | 2031-01-05 11:00 | 4.95 | 6.2265 | N | 0
2025-01-05 | 12 | 2031-01-05 12:00 | 5.16 | 6.4907 | N | 0
2025-01-05 | 13 | 2031-01-05 13:00 | 5.39 | 6.78 | N | 0
2025-01-05 | 14 | 2031-01-05 14:00 | 5.47 | 6.8806 | N | 0
2025-01-05 | 15 | 2031-01-05 15:00 | 5.32 | 6.6919 | N | 0
2025-01-05 | 16 | 2031-01-05 16:00 | 5.51 | 6.9309 | N | 0
2025-01-05 | 17 | 2031-01-05 17:00 | 5.92 | 7.4467 | N | 0
2025-01-05 | 18 | 2031-01-05 18:00 | 6.2 | 7.7989 | N | 0
2025-01-05 | 19 | 2031-01-05 19:00 | 5.99 | 7.5347 | N | 0
2025-01-05 | 20 | 2031-01-05 20:00 | 5.73 | 7.2077 | N | 0
2025-01-05 | 21 | 2031-01-05 21:00 | 5.61 | 7.0567 | N | 0
2025-01-05 | 22 | 2031-01-05 22:00 | 5.16 | 6.4907 | N | 0
2025-01-05 | 23 | 2031-01-05 23:00 | 4.78 | 6.0127 | N | 0
2025-01-06 | 00 | 2031-01-06 | 4.28 | 5.3837 | N | 0
2025-01-06 | 01 | 2031-01-06 01:00 | 3.88 | 4.8806 | N | 0
2025-01-06 | 02 | 2031-01-06 02:00 | 3.68 | 4.629 | N | 0
2025-01-06 | 03 | 2031-01-06 03:00 | 3.65 | 4.5913 | N | 0
2025-01-06 | 04 | 2031-01-06 04:00 | 3.55 | 4.4655 | N | 0
2025-01-06 | 05 | 2031-01-06 05:00 | 3.59 | 4.5158 | N | 0
2025-01-06 | 06 | 2031-01-06 06:00 | 4.05 | 5.0944 | N | 0
2025-01-06 | 07 | 2031-01-06 07:00 | 4.34 | 5.4592 | N | 0
2025-01-06 | 08 | 2031-01-06 08:00 | 4.93 | 6.2014 | N | 0
2025-01-06 | 09 | 2031-01-06 09:00 | 5.11 | 6.4278 | N | 0
2025-01-06 | 10 | 2031-01-06 10:00 | 5.1 | 6.4152 | N | 0
2025-01-06 | 11 | 2031-01-06 11:00 | 5.31 | 6.6794 | N | 0
2025-01-06 | 12 | 2031-01-06 12:00 | 5.28 | 6.6416 | N | 0
2025-01-06 | 13 | 2031-01-06 13:00 | 5.13 | 6.4529 | N | 0
2025-01-06 | 14 | 2031-01-06 14:00 | 5.17 | 6.5032 | N | 0
2025-01-06 | 15 | 2031-01-06 15:00 | 5.1 | 6.4152 | N | 0
2025-01-06 | 16 | 2031-01-06 16:00 | 5.19 | 6.5284 | N | 0
2025-01-06 | 17 | 2031-01-06 17:00 | 5.83 | 7.3334 | N | 0
2025-01-06 | 18 | 2031-01-06 18:00 | 6.32 | 7.9498 | N | 0
2025-01-06 | 19 | 2031-01-06 19:00 | 6.21 | 7.8114 | N | 0
2025-01-06 | 20 | 2031-01-06 20:00 | 6.02 | 7.5724 | N | 0
2025-01-06 | 21 | 2031-01-06 21:00 | 5.84 | 7.346 | N | 0
2025-01-06 | 22 | 2031-01-06 22:00 | 5.55 | 6.9812 | N | 0
2025-01-06 | 23 | 2031-01-06 23:00 | 5.26 | 6.6165 | N | 0
2025-01-07 | 00 | 2031-01-07 | 4.56 | 5.7359 | N | 0
2025-01-07 | 01 | 2031-01-07 01:00 | 4.14 | 5.2076 | N | 0
2025-01-07 | 02 | 2031-01-07 02:00 | 3.96 | 4.9812 | N | 0
2025-01-07 | 03 | 2031-01-07 03:00 | 3.89 | 4.8932 | N | 0
2025-01-07 | 04 | 2031-01-07 04:00 | 3.89 | 4.8932 | N | 0
2025-01-07 | 05 | 2031-01-07 05:00 | 3.84 | 4.8303 | N | 0
2025-01-07 | 06 | 2031-01-07 06:00 | 4.2 | 5.2831 | N | 0
2025-01-07 | 07 | 2031-01-07 07:00 | 4.61 | 5.7988 | N | 0
2025-01-07 | 08 | 2031-01-07 08:00 | 5.02 | 6.3146 | N | 0
2025-01-07 | 09 | 2031-01-07 09:00 | 5.08 | 6.39 | N | 0
2025-01-07 | 10 | 2031-01-07 10:00 | 5.23 | 6.5787 | N | 0
2025-01-07 | 11 | 2031-01-07 11:00 | 5.25 | 6.6039 | N | 0
2025-01-07 | 12 | 2031-01-07 12:00 | 5.09 | 6.4026 | N | 0
2025-01-07 | 13 | 2031-01-07 13:00 | 5.12 | 6.4404 | N | 0
2025-01-07 | 14 | 2031-01-07 14:00 | 5.18 | 6.5158 | N | 0
2025-01-07 | 15 | 2031-01-07 15:00 | 5.06 | 6.3649 | N | 0
2025-01-07 | 16 | 2031-01-07 16:00 | 5.31 | 6.6794 | N | 0
2025-01-07 | 17 | 2031-01-07 17:00 | 5.82 | 7.3209 | N | 0
2025-01-07 | 18 | 2031-01-07 18:00 | 6.33 | 7.9624 | N | 0
2025-01-07 | 19 | 2031-01-07 19:00 | 6.2 | 7.7989 | N | 0
2025-01-07 | 20 | 2031-01-07 20:00 | 5.89 | 7.4089 | N | 0
2025-01-07 | 21 | 2031-01-07 21:00 | 5.78 | 7.2706 | N | 0
2025-01-07 | 22 | 2031-01-07 22:00 | 5.58 | 7.019 | N | 0
2025-01-07 | 23 | 2031-01-07 23:00 | 5.16 | 6.4907 | N | 0
2025-01-08 | 00 | 2031-01-08 | 4.73 | 5.9498 | N | 0
2025-01-08 | 01 | 2031-01-08 01:00 | 4.24 | 5.3334 | N | 0
2025-01-08 | 02 | 2031-01-08 02:00 | 4.16 | 5.2328 | N | 0
2025-01-08 | 03 | 2031-01-08 03:00 | 3.96 | 4.9812 | N | 0
2025-01-08 | 04 | 2031-01-08 04:00 | 3.95 | 4.9686 | N | 0
2025-01-08 | 05 | 2031-01-08 05:00 | 4.11 | 5.1699 | N | 0
2025-01-08 | 06 | 2031-01-08 06:00 | 4.43 | 5.5724 | N | 0
2025-01-08 | 07 | 2031-01-08 07:00 | 4.93 | 6.2014 | N | 0
2025-01-08 | 08 | 2031-01-08 08:00 | 5.33 | 6.7045 | N | 0
2025-01-08 | 09 | 2031-01-08 09:00 | 5.51 | 6.9309 | N | 0
2025-01-08 | 10 | 2031-01-08 10:00 | 5.44 | 6.8429 | N | 0
2025-01-08 | 11 | 2031-01-08 11:00 | 5.39 | 6.78 | N | 0
2025-01-08 | 12 | 2031-01-08 12:00 | 5.56 | 6.9938 | N | 0
2025-01-08 | 13 | 2031-01-08 13:00 | 5.46 | 6.868 | N | 0
2025-01-08 | 14 | 2031-01-08 14:00 | 5.34 | 6.7171 | N | 0
2025-01-08 | 15 | 2031-01-08 15:00 | 5.25 | 6.6039 | N | 0
2025-01-08 | 16 | 2031-01-08 16:00 | 5.3 | 6.6668 | N | 0
2025-01-08 | 17 | 2031-01-08 17:00 | 6.01 | 7.5599 | N | 0
2025-01-08 | 18 | 2031-01-08 18:00 | 6.39 | 8.0379 | N | 0
2025-01-08 | 19 | 2031-01-08 19:00 | 6.27 | 7.8869 | N | 0
2025-01-08 | 20 | 2031-01-08 20:00 | 6.15 | 7.736 | N | 0
2025-01-08 | 21 | 2031-01-08 21:00 | 6.21 | 7.8114 | N | 0
2025-01-08 | 22 | 2031-01-08 22:00 | 5.84 | 7.346 | N | 0
2025-01-08 | 23 | 2031-01-08 23:00 | 5.32 | 6.6919 | N | 0
2025-01-09 | 00 | 2031-01-09 | 4.77 | 6.0001 | N | 0
2025-01-09 | 01 | 2031-01-09 01:00 | 4.46 | 5.6102 | N | 0
2025-01-09 | 02 | 2031-01-09 02:00 | 4.12 | 5.1825 | N | 0
2025-01-09 | 03 | 2031-01-09 03:00 | 4.13 | 5.1951 | N | 0
2025-01-09 | 04 | 2031-01-09 04:00 | 4.03 | 5.0693 | N | 0
2025-01-09 | 05 | 2031-01-09 05:00 | 4.14 | 5.2076 | N | 0
2025-01-09 | 06 | 2031-01-09 06:00 | 4.44 | 5.585 | N | 0
2025-01-09 | 07 | 2031-01-09 07:00 | 4.82 | 6.063 | N | 0
2025-01-09 | 08 | 2031-01-09 08:00 | 5.12 | 6.4404 | N | 0
2025-01-09 | 09 | 2031-01-09 09:00 | 5.29 | 6.6542 | N | 0
2025-01-09 | 10 | 2031-01-09 10:00 | 5.26 | 6.6165 | N | 0
2025-01-09 | 11 | 2031-01-09 11:00 | 5.31 | 6.6794 | N | 0
2025-01-09 | 12 | 2031-01-09 12:00 | 5.31 | 6.6794 | N | 0
2025-01-09 | 13 | 2031-01-09 13:00 | 5.24 | 6.5913 | N | 0
2025-01-09 | 14 | 2031-01-09 14:00 | 5.24 | 6.5913 | N | 0
2025-01-09 | 15 | 2031-01-09 15:00 | 5.21 | 6.5536 | N | 0
2025-01-09 | 16 | 2031-01-09 16:00 | 5.32 | 6.6919 | N | 0
2025-01-09 | 17 | 2031-01-09 17:00 | 5.82 | 7.3209 | N | 0
2025-01-09 | 18 | 2031-01-09 18:00 | 6.29 | 7.9121 | N | 0
2025-01-09 | 19 | 2031-01-09 19:00 | 6.25 | 7.8618 | N | 0
2025-01-09 | 20 | 2031-01-09 20:00 | 6.06 | 7.6228 | N | 0
2025-01-09 | 21 | 2031-01-09 21:00 | 5.95 | 7.4844 | N | 0
2025-01-09 | 22 | 2031-01-09 22:00 | 5.68 | 7.1448 | N | 0
2025-01-09 | 23 | 2031-01-09 23:00 | 5.24 | 6.5913 | N | 0
2025-01-10 | 00 | 2031-01-10 | 4.64 | 5.8366 | N | 0
2025-01-10 | 01 | 2031-01-10 01:00 | 4.35 | 5.4718 | N | 0
2025-01-10 | 02 | 2031-01-10 02:00 | 4 | 5.0315 | N | 0
2025-01-10 | 03 | 2031-01-10 03:00 | 4 | 5.0315 | N | 0
2025-01-10 | 04 | 2031-01-10 04:00 | 4 | 5.0315 | N | 0
2025-01-10 | 05 | 2031-01-10 05:00 | 3.95 | 4.9686 | N | 0
2025-01-10 | 06 | 2031-01-10 06:00 | 4.15 | 5.2202 | N | 0
2025-01-10 | 07 | 2031-01-10 07:00 | 4.66 | 5.8617 | N | 0
2025-01-10 | 08 | 2031-01-10 08:00 | 5.07 | 6.3775 | N | 0
2025-01-10 | 09 | 2031-01-10 09:00 | 5.26 | 6.6165 | N | 0
2025-01-10 | 10 | 2031-01-10 10:00 | 5.34 | 6.7171 | N | 0
2025-01-10 | 11 | 2031-01-10 11:00 | 5.33 | 6.7045 | N | 0
2025-01-10 | 12 | 2031-01-10 12:00 | 5.27 | 6.629 | N | 0
2025-01-10 | 13 | 2031-01-10 13:00 | 5.19 | 6.5284 | N | 0
2025-01-10 | 14 | 2031-01-10 14:00 | 5.08 | 6.39 | N | 0
2025-01-10 | 15 | 2031-01-10 15:00 | 5.11 | 6.4278 | N | 0
2025-01-10 | 16 | 2031-01-10 16:00 | 5.33 | 6.7045 | N | 0
2025-01-10 | 17 | 2031-01-10 17:00 | 5.66 | 7.1196 | N | 0
2025-01-10 | 18 | 2031-01-10 18:00 | 5.93 | 7.4592 | N | 0
2025-01-10 | 19 | 2031-01-10 19:00 | 5.93 | 7.4592 | N | 0
2025-01-10 | 20 | 2031-01-10 20:00 | 5.69 | 7.1573 | N | 0
2025-01-10 | 21 | 2031-01-10 21:00 | 5.51 | 6.9309 | N | 0
2025-01-10 | 22 | 2031-01-10 22:00 | 5.35 | 6.7297 | N | 0
2025-01-10 | 23 | 2031-01-10 23:00 | 5.08 | 6.39 | N | 0
2025-01-11 | 00 | 2031-01-11 | 4.59 | 5.7737 | N | 0
2025-01-11 | 01 | 2031-01-11 01:00 | 4.07 | 5.1196 | N | 0
2025-01-11 | 02 | 2031-01-11 02:00 | 3.84 | 4.8303 | N | 0
2025-01-11 | 03 | 2031-01-11 03:00 | 3.69 | 4.6416 | N | 0
2025-01-11 | 04 | 2031-01-11 04:00 | 3.6 | 4.5284 | N | 0
2025-01-11 | 05 | 2031-01-11 05:00 | 3.55 | 4.4655 | N | 0
2025-01-11 | 06 | 2031-01-11 06:00 | 3.61 | 4.541 | N | 0
2025-01-11 | 07 | 2031-01-11 07:00 | 3.87 | 4.868 | N | 0
2025-01-11 | 08 | 2031-01-11 08:00 | 4.13 | 5.1951 | N | 0
2025-01-11 | 09 | 2031-01-11 09:00 | 4.43 | 5.5724 | N | 0
2025-01-11 | 10 | 2031-01-11 10:00 | 4.72 | 5.9372 | N | 0
2025-01-11 | 11 | 2031-01-11 11:00 | 4.82 | 6.063 | N | 0
2025-01-11 | 12 | 2031-01-11 12:00 | 4.93 | 6.2014 | N | 0
2025-01-11 | 13 | 2031-01-11 13:00 | 4.99 | 6.2768 | N | 0
2025-01-11 | 14 | 2031-01-11 14:00 | 4.96 | 6.2391 | N | 0
2025-01-11 | 15 | 2031-01-11 15:00 | 4.95 | 6.2265 | N | 0
2025-01-11 | 16 | 2031-01-11 16:00 | 5.02 | 6.3146 | N | 0
2025-01-11 | 17 | 2031-01-11 17:00 | 5.3 | 6.6668 | N | 0
2025-01-11 | 18 | 2031-01-11 18:00 | 5.64 | 7.0945 | N | 0
2025-01-11 | 19 | 2031-01-11 19:00 | 5.46 | 6.868 | N | 0
2025-01-11 | 20 | 2031-01-11 20:00 | 5.31 | 6.6794 | N | 0
2025-01-11 | 21 | 2031-01-11 21:00 | 5.1 | 6.4152 | N | 0
2025-01-11 | 22 | 2031-01-11 22:00 | 4.81 | 6.0504 | N | 0
2025-01-11 | 23 | 2031-01-11 23:00 | 4.57 | 5.7485 | N | 0
2025-01-12 | 00 | 2031-01-12 | 4.32 | 5.434 | N | 0
2025-01-12 | 01 | 2031-01-12 01:00 | 4.04 | 5.0818 | N | 0
2025-01-12 | 02 | 2031-01-12 02:00 | 3.75 | 4.7171 | N | 0
2025-01-12 | 03 | 2031-01-12 03:00 | 3.49 | 4.39 | N | 0
2025-01-12 | 04 | 2031-01-12 04:00 | 3.51 | 4.4152 | N | 0
2025-01-12 | 05 | 2031-01-12 05:00 | 3.53 | 4.4403 | N | 0
2025-01-12 | 06 | 2031-01-12 06:00 | 3.55 | 4.4655 | N | 0
2025-01-12 | 07 | 2031-01-12 07:00 | 3.64 | 4.5787 | N | 0
2025-01-12 | 08 | 2031-01-12 08:00 | 3.98 | 5.0064 | N | 0
2025-01-12 | 09 | 2031-01-12 09:00 | 4.27 | 5.3712 | N | 0
2025-01-12 | 10 | 2031-01-12 10:00 | 4.56 | 5.7359 | N | 0
2025-01-12 | 11 | 2031-01-12 11:00 | 4.75 | 5.9749 | N | 0
2025-01-12 | 12 | 2031-01-12 12:00 | 4.95 | 6.2265 | N | 0
2025-01-12 | 13 | 2031-01-12 13:00 | 5.02 | 6.3146 | N | 0
2025-01-12 | 14 | 2031-01-12 14:00 | 4.92 | 6.1888 | N | 0
2025-01-12 | 15 | 2031-01-12 15:00 | 5.08 | 6.39 | N | 0
2025-01-12 | 16 | 2031-01-12 16:00 | 5.27 | 6.629 | N | 0
2025-01-12 | 17 | 2031-01-12 17:00 | 5.89 | 7.4089 | N | 0
2025-01-12 | 18 | 2031-01-12 18:00 | 6.13 | 7.7108 | N | 0
2025-01-12 | 19 | 2031-01-12 19:00 | 5.75 | 7.2328 | N | 0
2025-01-12 | 20 | 2031-01-12 20:00 | 5.45 | 6.8555 | N | 0
2025-01-12 | 21 | 2031-01-12 21:00 | 5.26 | 6.6165 | N | 0
2025-01-12 | 22 | 2031-01-12 22:00 | 5 | 6.2894 | N | 0
2025-01-12 | 23 | 2031-01-12 23:00 | 4.56 | 5.7359 | N | 0
2025-01-13 | 00 | 2031-01-13 | 4.15 | 5.2202 | N | 0
2025-01-13 | 01 | 2031-01-13 01:00 | 3.74 | 4.7045 | N | 0
2025-01-13 | 02 | 2031-01-13 02:00 | 3.48 | 4.3774 | N | 0
2025-01-13 | 03 | 2031-01-13 03:00 | 3.35 | 4.2139 | N | 0
2025-01-13 | 04 | 2031-01-13 04:00 | 3.31 | 4.1636 | N | 0
2025-01-13 | 05 | 2031-01-13 05:00 | 3.33 | 4.1887 | N | 0
2025-01-13 | 06 | 2031-01-13 06:00 | 3.5 | 4.4026 | N | 0
2025-01-13 | 07 | 2031-01-13 07:00 | 4.02 | 5.0567 | N | 0
2025-01-13 | 08 | 2031-01-13 08:00 | 4.46 | 5.6102 | N | 0
2025-01-13 | 09 | 2031-01-13 09:00 | 4.67 | 5.8743 | N | 0
2025-01-13 | 10 | 2031-01-13 10:00 | 4.63 | 5.824 | N | 0
2025-01-13 | 11 | 2031-01-13 11:00 | 4.84 | 6.0881 | N | 0
2025-01-13 | 12 | 2031-01-13 12:00 | 4.89 | 6.151 | N | 0
2025-01-13 | 13 | 2031-01-13 13:00 | 4.96 | 6.2391 | N | 0
2025-01-13 | 14 | 2031-01-13 14:00 | 5.04 | 6.3397 | N | 0
2025-01-13 | 15 | 2031-01-13 15:00 | 5.09 | 6.4026 | N | 0
2025-01-13 | 16 | 2031-01-13 16:00 | 5.08 | 6.39 | N | 0
2025-01-13 | 17 | 2031-01-13 17:00 | 5.48 | 6.8932 | N | 0
2025-01-13 | 18 | 2031-01-13 18:00 | 5.93 | 7.4592 | N | 0
2025-01-13 | 19 | 2031-01-13 19:00 | 5.94 | 7.4718 | N | 0
2025-01-13 | 20 | 2031-01-13 20:00 | 5.71 | 7.1825 | N | 0
2025-01-13 | 21 | 2031-01-13 21:00 | 5.52 | 6.9435 | N | 0
2025-01-13 | 22 | 2031-01-13 22:00 | 5.3 | 6.6668 | N | 0
2025-01-13 | 23 | 2031-01-13 23:00 | 4.83 | 6.0756 | N | 0
2025-01-14 | 00 | 2031-01-14 | 4.29 | 5.3963 | N | 0
2025-01-14 | 01 | 2031-01-14 01:00 | 3.89 | 4.8932 | N | 0
2025-01-14 | 02 | 2031-01-14 02:00 | 3.77 | 4.7422 | N | 0
2025-01-14 | 03 | 2031-01-14 03:00 | 3.69 | 4.6416 | N | 0
2025-01-14 | 04 | 2031-01-14 04:00 | 3.68 | 4.629 | N | 0
2025-01-14 | 05 | 2031-01-14 05:00 | 3.74 | 4.7045 | N | 0
2025-01-14 | 06 | 2031-01-14 06:00 | 4.03 | 5.0693 | N | 0
2025-01-14 | 07 | 2031-01-14 07:00 | 4.44 | 5.585 | N | 0
2025-01-14 | 08 | 2031-01-14 08:00 | 4.9 | 6.1636 | N | 0
2025-01-14 | 09 | 2031-01-14 09:00 | 5.04 | 6.3397 | N | 0
2025-01-14 | 10 | 2031-01-14 10:00 | 5.1 | 6.4152 | N | 0
2025-01-14 | 11 | 2031-01-14 11:00 | 5.11 | 6.4278 | N | 0
2025-01-14 | 12 | 2031-01-14 12:00 | 4.98 | 6.2642 | N | 0
2025-01-14 | 13 | 2031-01-14 13:00 | 5.15 | 6.4781 | N | 0
2025-01-14 | 14 | 2031-01-14 14:00 | 4.9 | 6.1636 | N | 0
2025-01-14 | 15 | 2031-01-14 15:00 | 4.89 | 6.151 | N | 0
2025-01-14 | 16 | 2031-01-14 16:00 | 5.02 | 6.3146 | N | 0
2025-01-14 | 17 | 2031-01-14 17:00 | 5.57 | 7.0064 | N | 0
2025-01-14 | 18 | 2031-01-14 18:00 | 6.12 | 7.6982 | N | 0
2025-01-14 | 19 | 2031-01-14 19:00 | 5.98 | 7.5221 | N | 0
2025-01-14 | 20 | 2031-01-14 20:00 | 5.84 | 7.346 | N | 0
2025-01-14 | 21 | 2031-01-14 21:00 | 5.66 | 7.1196 | N | 0
2025-01-14 | 22 | 2031-01-14 22:00 | 5.47 | 6.8806 | N | 0
2025-01-14 | 23 | 2031-01-14 23:00 | 5.09 | 6.4026 | N | 0
2025-01-15 | 00 | 2031-01-15 | 4.56 | 5.7359 | N | 0
2025-01-15 | 01 | 2031-01-15 01:00 | 4.15 | 5.2202 | N | 0
2025-01-15 | 02 | 2031-01-15 02:00 | 3.92 | 4.9309 | N | 0
2025-01-15 | 03 | 2031-01-15 03:00 | 3.78 | 4.7548 | N | 0
2025-01-15 | 04 | 2031-01-15 04:00 | 3.85 | 4.8428 | N | 0
2025-01-15 | 05 | 2031-01-15 05:00 | 3.94 | 4.9561 | N | 0
2025-01-15 | 06 | 2031-01-15 06:00 | 4.18 | 5.2579 | N | 0
2025-01-15 | 07 | 2031-01-15 07:00 | 4.75 | 5.9749 | N | 0
2025-01-15 | 08 | 2031-01-15 08:00 | 5.01 | 6.302 | N | 0
2025-01-15 | 09 | 2031-01-15 09:00 | 5.13 | 6.4529 | N | 0
2025-01-15 | 10 | 2031-01-15 10:00 | 5.19 | 6.5284 | N | 0
2025-01-15 | 11 | 2031-01-15 11:00 | 5.17 | 6.5032 | N | 0
2025-01-15 | 12 | 2031-01-15 12:00 | 5.23 | 6.5787 | N | 0
2025-01-15 | 13 | 2031-01-15 13:00 | 5.24 | 6.5913 | N | 0
2025-01-15 | 14 | 2031-01-15 14:00 | 5.13 | 6.4529 | N | 0
2025-01-15 | 15 | 2031-01-15 15:00 | 5.03 | 6.3271 | N | 0
2025-01-15 | 16 | 2031-01-15 16:00 | 5.2 | 6.541 | N | 0
2025-01-15 | 17 | 2031-01-15 17:00 | 5.74 | 7.2202 | N | 0
2025-01-15 | 18 | 2031-01-15 18:00 | 6.14 | 7.7234 | N | 0
2025-01-15 | 19 | 2031-01-15 19:00 | 5.95 | 7.4844 | N | 0
2025-01-15 | 20 | 2031-01-15 20:00 | 5.8 | 7.2957 | N | 0
2025-01-15 | 21 | 2031-01-15 21:00 | 5.72 | 7.1951 | N | 0
2025-01-15 | 22 | 2031-01-15 22:00 | 5.39 | 6.78 | N | 0
2025-01-15 | 23 | 2031-01-15 23:00 | 5.03 | 6.3271 | N | 0
2025-01-16 | 00 | 2031-01-16 | 4.52 | 5.6856 | N | 0
2025-01-16 | 01 | 2031-01-16 01:00 | 4.05 | 5.0944 | N | 0
2025-01-16 | 02 | 2031-01-16 02:00 | 3.81 | 4.7925 | N | 0
2025-01-16 | 03 | 2031-01-16 03:00 | 3.68 | 4.629 | N | 0
2025-01-16 | 04 | 2031-01-16 04:00 | 3.69 | 4.6416 | N | 0
2025-01-16 | 05 | 2031-01-16 05:00 | 3.72 | 4.6793 | N | 0
2025-01-16 | 06 | 2031-01-16 06:00 | 4 | 5.0315 | N | 0
2025-01-16 | 07 | 2031-01-16 07:00 | 4.43 | 5.5724 | N | 0
2025-01-16 | 08 | 2031-01-16 08:00 | 4.75 | 5.9749 | N | 0
2025-01-16 | 09 | 2031-01-16 09:00 | 4.88 | 6.1385 | N | 0
2025-01-16 | 10 | 2031-01-16 10:00 | 4.98 | 6.2642 | N | 0
2025-01-16 | 11 | 2031-01-16 11:00 | 5.12 | 6.4404 | N | 0
2025-01-16 | 12 | 2031-01-16 12:00 | 5.26 | 6.6165 | N | 0
2025-01-16 | 13 | 2031-01-16 13:00 | 5.21 | 6.5536 | N | 0
2025-01-16 | 14 | 2031-01-16 14:00 | 5.1 | 6.4152 | N | 0
2025-01-16 | 15 | 2031-01-16 15:00 | 5.23 | 6.5787 | N | 0
2025-01-16 | 16 | 2031-01-16 16:00 | 5.13 | 6.4529 | N | 0
2025-01-16 | 17 | 2031-01-16 17:00 | 5.42 | 6.8177 | N | 0
2025-01-16 | 18 | 2031-01-16 18:00 | 5.94 | 7.4718 | N | 0
2025-01-16 | 19 | 2031-01-16 19:00 | 5.99 | 7.5347 | N | 0
2025-01-16 | 20 | 2031-01-16 20:00 | 5.66 | 7.1196 | N | 0
2025-01-16 | 21 | 2031-01-16 21:00 | 5.57 | 7.0064 | N | 0
2025-01-16 | 22 | 2031-01-16 22:00 | 5.28 | 6.6416 | N | 0
2025-01-16 | 23 | 2031-01-16 23:00 | 5.06 | 6.3649 | N | 0
2025-01-17 | 00 | 2031-01-17 | 4.37 | 5.4969 | N | 0
2025-01-17 | 01 | 2031-01-17 01:00 | 3.97 | 4.9938 | N | 0
2025-01-17 | 02 | 2031-01-17 02:00 | 3.85 | 4.8428 | N | 0
2025-01-17 | 03 | 2031-01-17 03:00 | 3.68 | 4.629 | N | 0
2025-01-17 | 04 | 2031-01-17 04:00 | 3.54 | 4.4529 | N | 0
2025-01-17 | 05 | 2031-01-17 05:00 | 3.59 | 4.5158 | N | 0
2025-01-17 | 06 | 2031-01-17 06:00 | 3.7 | 4.6542 | N | 0
2025-01-17 | 07 | 2031-01-17 07:00 | 4.18 | 5.2579 | N | 0
2025-01-17 | 08 | 2031-01-17 08:00 | 4.62 | 5.8114 | N | 0
2025-01-17 | 09 | 2031-01-17 09:00 | 4.7 | 5.912 | N | 0
2025-01-17 | 10 | 2031-01-17 10:00 | 4.68 | 5.8869 | N | 0
2025-01-17 | 11 | 2031-01-17 11:00 | 4.73 | 5.9498 | N | 0
2025-01-17 | 12 | 2031-01-17 12:00 | 4.83 | 6.0756 | N | 0
2025-01-17 | 13 | 2031-01-17 13:00 | 4.9 | 6.1636 | N | 0
2025-01-17 | 14 | 2031-01-17 14:00 | 4.94 | 6.2139 | N | 0
2025-01-17 | 15 | 2031-01-17 15:00 | 4.96 | 6.2391 | N | 0
2025-01-17 | 16 | 2031-01-17 16:00 | 4.91 | 6.1762 | N | 0
2025-01-17 | 17 | 2031-01-17 17:00 | 5.36 | 6.7422 | N | 0
2025-01-17 | 18 | 2031-01-17 18:00 | 5.64 | 7.0945 | N | 0
2025-01-17 | 19 | 2031-01-17 19:00 | 5.58 | 7.019 | N | 0
2025-01-17 | 20 | 2031-01-17 20:00 | 5.35 | 6.7297 | N | 0
2025-01-17 | 21 | 2031-01-17 21:00 | 5.25 | 6.6039 | N | 0
2025-01-17 | 22 | 2031-01-17 22:00 | 5 | 6.2894 | N | 0
2025-01-17 | 23 | 2031-01-17 23:00 | 4.78 | 6.0127 | N | 0
2025-01-18 | 00 | 2031-01-18 | 4.22 | 5.3083 | N | 0
2025-01-18 | 01 | 2031-01-18 01:00 | 3.75 | 4.7171 | N | 0
2025-01-18 | 02 | 2031-01-18 02:00 | 3.55 | 4.4655 | N | 0
2025-01-18 | 03 | 2031-01-18 03:00 | 3.39 | 4.2642 | N | 0
2025-01-18 | 04 | 2031-01-18 04:00 | 3.37 | 4.2391 | N | 0
2025-01-18 | 05 | 2031-01-18 05:00 | 3.38 | 4.2516 | N | 0
2025-01-18 | 06 | 2031-01-18 06:00 | 3.48 | 4.3774 | N | 0
2025-01-18 | 07 | 2031-01-18 07:00 | 3.58 | 4.5032 | N | 0
2025-01-18 | 08 | 2031-01-18 08:00 | 3.87 | 4.868 | N | 0
2025-01-18 | 09 | 2031-01-18 09:00 | 4.25 | 5.346 | N | 0
2025-01-18 | 10 | 2031-01-18 10:00 | 4.51 | 5.673 | N | 0
2025-01-18 | 11 | 2031-01-18 11:00 | 4.84 | 6.0881 | N | 0
2025-01-18 | 12 | 2031-01-18 12:00 | 4.9 | 6.1636 | N | 0
2025-01-18 | 13 | 2031-01-18 13:00 | 5.06 | 6.3649 | N | 0
2025-01-18 | 14 | 2031-01-18 14:00 | 5.07 | 6.3775 | N | 0
2025-01-18 | 15 | 2031-01-18 15:00 | 5.01 | 6.302 | N | 0
2025-01-18 | 16 | 2031-01-18 16:00 | 4.95 | 6.2265 | N | 0
2025-01-18 | 17 | 2031-01-18 17:00 | 5.26 | 6.6165 | N | 0
2025-01-18 | 18 | 2031-01-18 18:00 | 5.47 | 6.8806 | N | 0
2025-01-18 | 19 | 2031-01-18 19:00 | 5.62 | 7.0693 | N | 0
2025-01-18 | 20 | 2031-01-18 20:00 | 5.37 | 6.7548 | N | 0
2025-01-18 | 21 | 2031-01-18 21:00 | 5.18 | 6.5158 | N | 0
2025-01-18 | 22 | 2031-01-18 22:00 | 4.96 | 6.2391 | N | 0
2025-01-18 | 23 | 2031-01-18 23:00 | 4.68 | 5.8869 | N | 0
2025-01-19 | 00 | 2031-01-19 | 4.41 | 5.5473 | N | 0
2025-01-19 | 01 | 2031-01-19 01:00 | 4.14 | 5.2076 | N | 0
2025-01-19 | 02 | 2031-01-19 02:00 | 3.84 | 4.8303 | N | 0
2025-01-19 | 03 | 2031-01-19 03:00 | 3.74 | 4.7045 | N | 0
2025-01-19 | 04 | 2031-01-19 04:00 | 3.79 | 4.7674 | N | 0
2025-01-19 | 05 | 2031-01-19 05:00 | 3.72 | 4.6793 | N | 0
2025-01-19 | 06 | 2031-01-19 06:00 | 3.83 | 4.8177 | N | 0
2025-01-19 | 07 | 2031-01-19 07:00 | 4.04 | 5.0818 | N | 0
2025-01-19 | 08 | 2031-01-19 08:00 | 4.2 | 5.2831 | N | 0
2025-01-19 | 09 | 2031-01-19 09:00 | 4.7 | 5.912 | N | 0
2025-01-19 | 10 | 2031-01-19 10:00 | 4.93 | 6.2014 | N | 0
2025-01-19 | 11 | 2031-01-19 11:00 | 5.2 | 6.541 | N | 0
2025-01-19 | 12 | 2031-01-19 12:00 | 5.38 | 6.7674 | N | 0
2025-01-19 | 13 | 2031-01-19 13:00 | 5.44 | 6.8429 | N | 0
2025-01-19 | 14 | 2031-01-19 14:00 | 5.51 | 6.9309 | N | 0
2025-01-19 | 15 | 2031-01-19 15:00 | 5.51 | 6.9309 | N | 0
2025-01-19 | 16 | 2031-01-19 16:00 | 5.58 | 7.019 | N | 0
2025-01-19 | 17 | 2031-01-19 17:00 | 5.93 | 7.4592 | N | 0
2025-01-19 | 18 | 2031-01-19 18:00 | 6.42 | 8.0756 | N | 0
2025-01-19 | 19 | 2031-01-19 19:00 | 6.28 | 7.8995 | N | 0
2025-01-19 | 20 | 2031-01-19 20:00 | 5.95 | 7.4844 | N | 0
2025-01-19 | 21 | 2031-01-19 21:00 | 5.66 | 7.1196 | N | 0
2025-01-19 | 22 | 2031-01-19 22:00 | 5.38 | 6.7674 | N | 0
2025-01-19 | 23 | 2031-01-19 23:00 | 5.11 | 6.4278 | N | 0
2025-01-20 | 00 | 2031-01-20 | 4.69 | 5.8995 | N | 0
2025-01-20 | 01 | 2031-01-20 01:00 | 4.23 | 5.3208 | N | 0
2025-01-20 | 02 | 2031-01-20 02:00 | 3.94 | 4.9561 | N | 0
2025-01-20 | 03 | 2031-01-20 03:00 | 4.01 | 5.0441 | N | 0
2025-01-20 | 04 | 2031-01-20 04:00 | 3.95 | 4.9686 | N | 0
2025-01-20 | 05 | 2031-01-20 05:00 | 3.91 | 4.9183 | N | 0
2025-01-20 | 06 | 2031-01-20 06:00 | 4.28 | 5.3837 | N | 0
2025-01-20 | 07 | 2031-01-20 07:00 | 4.7 | 5.912 | N | 0
2025-01-20 | 08 | 2031-01-20 08:00 | 5.1 | 6.4152 | N | 0
2025-01-20 | 09 | 2031-01-20 09:00 | 5.32 | 6.6919 | N | 0
2025-01-20 | 10 | 2031-01-20 10:00 | 5.37 | 6.7548 | N | 0
2025-01-20 | 11 | 2031-01-20 11:00 | 5.38 | 6.7674 | N | 0
2025-01-20 | 12 | 2031-01-20 12:00 | 5.42 | 6.8177 | N | 0
2025-01-20 | 13 | 2031-01-20 13:00 | 5.48 | 6.8932 | N | 0
2025-01-20 | 14 | 2031-01-20 14:00 | 5.41 | 6.8051 | N | 0
2025-01-20 | 15 | 2031-01-20 15:00 | 5.65 | 7.107 | N | 0
2025-01-20 | 16 | 2031-01-20 16:00 | 5.73 | 7.2077 | N | 0
2025-01-20 | 17 | 2031-01-20 17:00 | 6.01 | 7.5599 | N | 0
2025-01-20 | 18 | 2031-01-20 18:00 | 6.51 | 8.1888 | N | 0
2025-01-20 | 19 | 2031-01-20 19:00 | 6.55 | 8.2391 | N | 0
2025-01-20 | 20 | 2031-01-20 20:00 | 6.21 | 7.8114 | N | 0
2025-01-20 | 21 | 2031-01-20 21:00 | 6.16 | 7.7485 | N | 0
2025-01-20 | 22 | 2031-01-20 22:00 | 5.92 | 7.4467 | N | 0
2025-01-20 | 23 | 2031-01-20 23:00 | 5.56 | 6.9938 | N | 0
2025-01-21 | 00 | 2031-01-21 | 5.03 | 6.3271 | N | 0
2025-01-21 | 01 | 2031-01-21 01:00 | 4.61 | 5.7988 | N | 0
2025-01-21 | 02 | 2031-01-21 02:00 | 4.37 | 5.4969 | N | 0
2025-01-21 | 03 | 2031-01-21 03:00 | 4.22 | 5.3083 | N | 0
2025-01-21 | 04 | 2031-01-21 04:00 | 4.28 | 5.3837 | N | 0
2025-01-21 | 05 | 2031-01-21 05:00 | 4.3 | 5.4089 | N | 0
2025-01-21 | 06 | 2031-01-21 06:00 | 4.61 | 5.7988 | N | 0
2025-01-21 | 07 | 2031-01-21 07:00 | 4.99 | 6.2768 | N | 0
2025-01-21 | 08 | 2031-01-21 08:00 | 5.42 | 6.8177 | N | 0
2025-01-21 | 09 | 2031-01-21 09:00 | 5.61 | 7.0567 | N | 0
2025-01-21 | 10 | 2031-01-21 10:00 | 5.51 | 6.9309 | N | 0
2025-01-21 | 11 | 2031-01-21 11:00 | 5.43 | 6.8303 | N | 0
2025-01-21 | 12 | 2031-01-21 12:00 | 5.52 | 6.9435 | N | 0
2025-01-21 | 13 | 2031-01-21 13:00 | 5.53 | 6.9561 | N | 0
2025-01-21 | 14 | 2031-01-21 14:00 | 5.63 | 7.0819 | N | 0
2025-01-21 | 15 | 2031-01-21 15:00 | 5.54 | 6.9687 | N | 0
2025-01-21 | 16 | 2031-01-21 16:00 | 5.62 | 7.0693 | N | 0
2025-01-21 | 17 | 2031-01-21 17:00 | 6.1 | 7.6731 | N | 0
2025-01-21 | 18 | 2031-01-21 18:00 | 6.62 | 8.3272 | N | 0
2025-01-21 | 19 | 2031-01-21 19:00 | 6.49 | 8.1637 | N | 0
2025-01-21 | 20 | 2031-01-21 20:00 | 6.43 | 8.0882 | N | 0
2025-01-21 | 21 | 2031-01-21 21:00 | 6.32 | 7.9498 | N | 0
2025-01-21 | 22 | 2031-01-21 22:00 | 6.07 | 7.6353 | N | 0
2025-01-21 | 23 | 2031-01-21 23:00 | 5.59 | 7.0316 | N | 0
2025-01-22 | 00 | 2031-01-22 | 5.1 | 6.4152 | N | 0
2025-01-22 | 01 | 2031-01-22 01:00 | 4.71 | 5.9246 | N | 0
2025-01-22 | 02 | 2031-01-22 02:00 | 4.49 | 5.6479 | N | 0
2025-01-22 | 03 | 2031-01-22 03:00 | 4.35 | 5.4718 | N | 0
2025-01-22 | 04 | 2031-01-22 04:00 | 4.31 | 5.4215 | N | 0
2025-01-22 | 05 | 2031-01-22 05:00 | 4.36 | 5.4844 | N | 0
2025-01-22 | 06 | 2031-01-22 06:00 | 4.77 | 6.0001 | N | 0
2025-01-22 | 07 | 2031-01-22 07:00 | 5.13 | 6.4529 | N | 0
2025-01-22 | 08 | 2031-01-22 08:00 | 5.52 | 6.9435 | N | 0
2025-01-22 | 09 | 2031-01-22 09:00 | 5.72 | 7.1951 | N | 0
2025-01-22 | 10 | 2031-01-22 10:00 | 5.8 | 7.2957 | N | 0
2025-01-22 | 11 | 2031-01-22 11:00 | 5.78 | 7.2706 | N | 0
2025-01-22 | 12 | 2031-01-22 12:00 | 5.88 | 7.3963 | N | 0
2025-01-22 | 13 | 2031-01-22 13:00 | 5.94 | 7.4718 | N | 0
2025-01-22 | 14 | 2031-01-22 14:00 | 5.98 | 7.5221 | N | 0
2025-01-22 | 15 | 2031-01-22 15:00 | 5.78 | 7.2706 | N | 0
2025-01-22 | 16 | 2031-01-22 16:00 | 5.8 | 7.2957 | N | 0
2025-01-22 | 17 | 2031-01-22 17:00 | 6.29 | 7.9121 | N | 0
2025-01-22 | 18 | 2031-01-22 18:00 | 6.58 | 8.2769 | N | 0
2025-01-22 | 19 | 2031-01-22 19:00 | 6.65 | 8.3649 | N | 0
2025-01-22 | 20 | 2031-01-22 20:00 | 6.36 | 8.0001 | N | 0
2025-01-22 | 21 | 2031-01-22 21:00 | 6.11 | 7.6857 | N | 0
2025-01-22 | 22 | 2031-01-22 22:00 | 5.89 | 7.4089 | N | 0
2025-01-22 | 23 | 2031-01-22 23:00 | 5.57 | 7.0064 | N | 0
2025-01-23 | 00 | 2031-01-23 | 4.95 | 6.2265 | N | 0
2025-01-23 | 01 | 2031-01-23 01:00 | 4.48 | 5.6353 | N | 0
2025-01-23 | 02 | 2031-01-23 02:00 | 4.16 | 5.2328 | N | 0
2025-01-23 | 03 | 2031-01-23 03:00 | 4.07 | 5.1196 | N | 0
2025-01-23 | 04 | 2031-01-23 04:00 | 4.02 | 5.0567 | N | 0
2025-01-23 | 05 | 2031-01-23 05:00 | 4.02 | 5.0567 | N | 0
2025-01-23 | 06 | 2031-01-23 06:00 | 4.21 | 5.2957 | N | 0
2025-01-23 | 07 | 2031-01-23 07:00 | 4.6 | 5.7863 | N | 0
2025-01-23 | 08 | 2031-01-23 08:00 | 4.91 | 6.1762 | N | 0
2025-01-23 | 09 | 2031-01-23 09:00 | 5.12 | 6.4404 | N | 0
2025-01-23 | 10 | 2031-01-23 10:00 | 5.15 | 6.4781 | N | 0
2025-01-23 | 11 | 2031-01-23 11:00 | 5.33 | 6.7045 | N | 0
2025-01-23 | 12 | 2031-01-23 12:00 | 5.34 | 6.7171 | N | 0
2025-01-23 | 13 | 2031-01-23 13:00 | 5.45 | 6.8555 | N | 0
2025-01-23 | 14 | 2031-01-23 14:00 | 5.34 | 6.7171 | N | 0
2025-01-23 | 15 | 2031-01-23 15:00 | 5.25 | 6.6039 | N | 0
2025-01-23 | 16 | 2031-01-23 16:00 | 5.26 | 6.6165 | N | 0
2025-01-23 | 17 | 2031-01-23 17:00 | 5.75 | 7.2328 | N | 0
2025-01-23 | 18 | 2031-01-23 18:00 | 6.05 | 7.6102 | N | 0
2025-01-23 | 19 | 2031-01-23 19:00 | 6 | 7.5473 | N | 0
2025-01-23 | 20 | 2031-01-23 20:00 | 5.78 | 7.2706 | N | 0
2025-01-23 | 21 | 2031-01-23 21:00 | 5.77 | 7.258 | N | 0
2025-01-23 | 22 | 2031-01-23 22:00 | 5.48 | 6.8932 | N | 0
2025-01-23 | 23 | 2031-01-23 23:00 | 5.12 | 6.4404 | N | 0
2025-01-24 | 00 | 2031-01-24 | 4.58 | 5.7611 | N | 0
2025-01-24 | 01 | 2031-01-24 01:00 | 4.32 | 5.434 | N | 0
2025-01-24 | 02 | 2031-01-24 02:00 | 3.95 | 4.9686 | N | 0
2025-01-24 | 03 | 2031-01-24 03:00 | 3.86 | 4.8554 | N | 0
2025-01-24 | 04 | 2031-01-24 04:00 | 3.86 | 4.8554 | N | 0
2025-01-24 | 05 | 2031-01-24 05:00 | 3.86 | 4.8554 | N | 0
2025-01-24 | 06 | 2031-01-24 06:00 | 4.03 | 5.0693 | N | 0
2025-01-24 | 07 | 2031-01-24 07:00 | 4.61 | 5.7988 | N | 0
2025-01-24 | 08 | 2031-01-24 08:00 | 5.02 | 6.3146 | N | 0
2025-01-24 | 09 | 2031-01-24 09:00 | 5.12 | 6.4404 | N | 0
2025-01-24 | 10 | 2031-01-24 10:00 | 5.35 | 6.7297 | N | 0
2025-01-24 | 11 | 2031-01-24 11:00 | 5.22 | 6.5661 | N | 0
2025-01-24 | 12 | 2031-01-24 12:00 | 5.32 | 6.6919 | N | 0
2025-01-24 | 13 | 2031-01-24 13:00 | 5.18 | 6.5158 | N | 0
2025-01-24 | 14 | 2031-01-24 14:00 | 4.97 | 6.2517 | N | 0
2025-01-24 | 15 | 2031-01-24 15:00 | 4.97 | 6.2517 | N | 0
2025-01-24 | 16 | 2031-01-24 16:00 | 5.12 | 6.4404 | N | 0
2025-01-24 | 17 | 2031-01-24 17:00 | 5.51 | 6.9309 | N | 0
2025-01-24 | 18 | 2031-01-24 18:00 | 5.86 | 7.3712 | N | 0
2025-01-24 | 19 | 2031-01-24 19:00 | 5.93 | 7.4592 | N | 0
2025-01-24 | 20 | 2031-01-24 20:00 | 5.74 | 7.2202 | N | 0
2025-01-24 | 21 | 2031-01-24 21:00 | 5.58 | 7.019 | N | 0
2025-01-24 | 22 | 2031-01-24 22:00 | 5.57 | 7.0064 | N | 0
2025-01-24 | 23 | 2031-01-24 23:00 | 5.17 | 6.5032 | N | 0
2025-01-25 | 00 | 2031-01-25 | 4.64 | 5.8366 | N | 0
2025-01-25 | 01 | 2031-01-25 01:00 | 4.27 | 5.3712 | N | 0
2025-01-25 | 02 | 2031-01-25 02:00 | 4.02 | 5.0567 | N | 0
2025-01-25 | 03 | 2031-01-25 03:00 | 3.88 | 4.8806 | N | 0
2025-01-25 | 04 | 2031-01-25 04:00 | 3.73 | 4.6919 | N | 0
2025-01-25 | 05 | 2031-01-25 05:00 | 3.77 | 4.7422 | N | 0
2025-01-25 | 06 | 2031-01-25 06:00 | 3.83 | 4.8177 | N | 0
2025-01-25 | 07 | 2031-01-25 07:00 | 4.07 | 5.1196 | N | 0
2025-01-25 | 08 | 2031-01-25 08:00 | 4.32 | 5.434 | N | 0
2025-01-25 | 09 | 2031-01-25 09:00 | 4.7 | 5.912 | N | 0
2025-01-25 | 10 | 2031-01-25 10:00 | 5.04 | 6.3397 | N | 0
2025-01-25 | 11 | 2031-01-25 11:00 | 5.19 | 6.5284 | N | 0
2025-01-25 | 12 | 2031-01-25 12:00 | 5.48 | 6.8932 | N | 0
2025-01-25 | 13 | 2031-01-25 13:00 | 5.48 | 6.8932 | N | 0
2025-01-25 | 14 | 2031-01-25 14:00 | 5.48 | 6.8932 | N | 0
2025-01-25 | 15 | 2031-01-25 15:00 | 5.32 | 6.6919 | N | 0
2025-01-25 | 16 | 2031-01-25 16:00 | 5.36 | 6.7422 | N | 0
2025-01-25 | 17 | 2031-01-25 17:00 | 5.62 | 7.0693 | N | 0
2025-01-25 | 18 | 2031-01-25 18:00 | 5.82 | 7.3209 | N | 0
2025-01-25 | 19 | 2031-01-25 19:00 | 5.77 | 7.258 | N | 0
2025-01-25 | 20 | 2031-01-25 20:00 | 5.39 | 6.78 | N | 0
2025-01-25 | 21 | 2031-01-25 21:00 | 5.24 | 6.5913 | N | 0
2025-01-25 | 22 | 2031-01-25 22:00 | 5.19 | 6.5284 | N | 0
2025-01-25 | 23 | 2031-01-25 23:00 | 4.61 | 5.7988 | N | 0
2025-01-26 | 00 | 2031-01-26 | 4.4 | 5.5347 | N | 0
2025-01-26 | 01 | 2031-01-26 01:00 | 4.03 | 5.0693 | N | 0
2025-01-26 | 02 | 2031-01-26 02:00 | 3.8 | 4.7799 | N | 0
2025-01-26 | 03 | 2031-01-26 03:00 | 3.71 | 4.6667 | N | 0
2025-01-26 | 04 | 2031-01-26 04:00 | 3.57 | 4.4906 | N | 0
2025-01-26 | 05 | 2031-01-26 05:00 | 3.59 | 4.5158 | N | 0
2025-01-26 | 06 | 2031-01-26 06:00 | 3.59 | 4.5158 | N | 0
2025-01-26 | 07 | 2031-01-26 07:00 | 3.75 | 4.7171 | N | 0
2025-01-26 | 08 | 2031-01-26 08:00 | 4.02 | 5.0567 | N | 0
2025-01-26 | 09 | 2031-01-26 09:00 | 4.2 | 5.2831 | N | 0
2025-01-26 | 10 | 2031-01-26 10:00 | 4.54 | 5.7108 | N | 0
2025-01-26 | 11 | 2031-01-26 11:00 | 4.58 | 5.7611 | N | 0
2025-01-26 | 12 | 2031-01-26 12:00 | 4.83 | 6.0756 | N | 0
2025-01-26 | 13 | 2031-01-26 13:00 | 5.12 | 6.4404 | N | 0
2025-01-26 | 14 | 2031-01-26 14:00 | 5.02 | 6.3146 | N | 0
2025-01-26 | 15 | 2031-01-26 15:00 | 5.04 | 6.3397 | N | 0
2025-01-26 | 16 | 2031-01-26 16:00 | 5.13 | 6.4529 | N | 0
2025-01-26 | 17 | 2031-01-26 17:00 | 5.52 | 6.9435 | N | 0
2025-01-26 | 18 | 2031-01-26 18:00 | 5.92 | 7.4467 | N | 0
2025-01-26 | 19 | 2031-01-26 19:00 | 5.82 | 7.3209 | N | 0
2025-01-26 | 20 | 2031-01-26 20:00 | 5.57 | 7.0064 | N | 0
2025-01-26 | 21 | 2031-01-26 21:00 | 5.37 | 6.7548 | N | 0
2025-01-26 | 22 | 2031-01-26 22:00 | 5.18 | 6.5158 | N | 0
2025-01-26 | 23 | 2031-01-26 23:00 | 4.8 | 6.0378 | N | 0
2025-01-27 | 00 | 2031-01-27 | 4.3 | 5.4089 | N | 0
2025-01-27 | 01 | 2031-01-27 01:00 | 3.96 | 4.9812 | N | 0
2025-01-27 | 02 | 2031-01-27 02:00 | 3.79 | 4.7674 | N | 0
2025-01-27 | 03 | 2031-01-27 03:00 | 3.63 | 4.5661 | N | 0
2025-01-27 | 04 | 2031-01-27 04:00 | 3.53 | 4.4403 | N | 0
2025-01-27 | 05 | 2031-01-27 05:00 | 3.7 | 4.6542 | N | 0
2025-01-27 | 06 | 2031-01-27 06:00 | 3.91 | 4.9183 | N | 0
2025-01-27 | 07 | 2031-01-27 07:00 | 4.31 | 5.4215 | N | 0
2025-01-27 | 08 | 2031-01-27 08:00 | 4.81 | 6.0504 | N | 0
2025-01-27 | 09 | 2031-01-27 09:00 | 4.76 | 5.9875 | N | 0
2025-01-27 | 10 | 2031-01-27 10:00 | 4.85 | 6.1007 | N | 0
2025-01-27 | 11 | 2031-01-27 11:00 | 4.83 | 6.0756 | N | 0
2025-01-27 | 12 | 2031-01-27 12:00 | 4.93 | 6.2014 | N | 0
2025-01-27 | 13 | 2031-01-27 13:00 | 5.09 | 6.4026 | N | 0
2025-01-27 | 14 | 2031-01-27 14:00 | 5.03 | 6.3271 | N | 0
2025-01-27 | 15 | 2031-01-27 15:00 | 4.89 | 6.151 | N | 0
2025-01-27 | 16 | 2031-01-27 16:00 | 4.93 | 6.2014 | N | 0
2025-01-27 | 17 | 2031-01-27 17:00 | 5.54 | 6.9687 | N | 0
2025-01-27 | 18 | 2031-01-27 18:00 | 5.97 | 7.5096 | N | 0
2025-01-27 | 19 | 2031-01-27 19:00 | 6.03 | 7.585 | N | 0
2025-01-27 | 20 | 2031-01-27 20:00 | 5.72 | 7.1951 | N | 0
2025-01-27 | 21 | 2031-01-27 21:00 | 5.65 | 7.107 | N | 0
2025-01-27 | 22 | 2031-01-27 22:00 | 5.28 | 6.6416 | N | 0
2025-01-27 | 23 | 2031-01-27 23:00 | 4.86 | 6.1133 | N | 0
2025-01-28 | 00 | 2031-01-28 | 4.38 | 5.5095 | N | 0
2025-01-28 | 01 | 2031-01-28 01:00 | 3.93 | 4.9435 | N | 0
2025-01-28 | 02 | 2031-01-28 02:00 | 3.71 | 4.6667 | N | 0
2025-01-28 | 03 | 2031-01-28 03:00 | 3.54 | 4.4529 | N | 0
2025-01-28 | 04 | 2031-01-28 04:00 | 3.56 | 4.4781 | N | 0
2025-01-28 | 05 | 2031-01-28 05:00 | 3.68 | 4.629 | N | 0
2025-01-28 | 06 | 2031-01-28 06:00 | 3.95 | 4.9686 | N | 0
2025-01-28 | 07 | 2031-01-28 07:00 | 4.38 | 5.5095 | N | 0
2025-01-28 | 08 | 2031-01-28 08:00 | 5.04 | 6.3397 | N | 0
2025-01-28 | 09 | 2031-01-28 09:00 | 5.08 | 6.39 | N | 0
2025-01-28 | 10 | 2031-01-28 10:00 | 5.07 | 6.3775 | N | 0
2025-01-28 | 11 | 2031-01-28 11:00 | 5.07 | 6.3775 | N | 0
2025-01-28 | 12 | 2031-01-28 12:00 | 5.15 | 6.4781 | N | 0
2025-01-28 | 13 | 2031-01-28 13:00 | 5.17 | 6.5032 | N | 0
2025-01-28 | 14 | 2031-01-28 14:00 | 5 | 6.2894 | N | 0
2025-01-28 | 15 | 2031-01-28 15:00 | 5.04 | 6.3397 | N | 0
2025-01-28 | 16 | 2031-01-28 16:00 | 5.21 | 6.5536 | N | 0
2025-01-28 | 17 | 2031-01-28 17:00 | 5.7 | 7.1699 | N | 0
2025-01-28 | 18 | 2031-01-28 18:00 | 6.12 | 7.6982 | N | 0
2025-01-28 | 19 | 2031-01-28 19:00 | 6.02 | 7.5724 | N | 0
2025-01-28 | 20 | 2031-01-28 20:00 | 5.58 | 7.019 | N | 0
2025-01-28 | 21 | 2031-01-28 21:00 | 5.52 | 6.9435 | N | 0
2025-01-28 | 22 | 2031-01-28 22:00 | 5.35 | 6.7297 | N | 0
2025-01-28 | 23 | 2031-01-28 23:00 | 5 | 6.2894 | N | 0
2025-01-29 | 00 | 2031-01-29 | 4.35 | 5.4718 | N | 0
2025-01-29 | 01 | 2031-01-29 01:00 | 3.93 | 4.9435 | N | 0
2025-01-29 | 02 | 2031-01-29 02:00 | 3.64 | 4.5787 | N | 0
2025-01-29 | 03 | 2031-01-29 03:00 | 3.57 | 4.4906 | N | 0
2025-01-29 | 04 | 2031-01-29 04:00 | 3.43 | 4.3145 | N | 0
2025-01-29 | 05 | 2031-01-29 05:00 | 3.47 | 4.3648 | N | 0
2025-01-29 | 06 | 2031-01-29 06:00 | 3.64 | 4.5787 | N | 0
2025-01-29 | 07 | 2031-01-29 07:00 | 4.14 | 5.2076 | N | 0
2025-01-29 | 08 | 2031-01-29 08:00 | 4.47 | 5.6227 | N | 0
2025-01-29 | 09 | 2031-01-29 09:00 | 4.47 | 5.6227 | N | 0
2025-01-29 | 10 | 2031-01-29 10:00 | 4.78 | 6.0127 | N | 0
2025-01-29 | 11 | 2031-01-29 11:00 | 4.73 | 5.9498 | N | 0
2025-01-29 | 12 | 2031-01-29 12:00 | 4.73 | 5.9498 | N | 0
2025-01-29 | 13 | 2031-01-29 13:00 | 4.98 | 6.2642 | N | 0
2025-01-29 | 14 | 2031-01-29 14:00 | 4.92 | 6.1888 | N | 0
2025-01-29 | 15 | 2031-01-29 15:00 | 4.98 | 6.2642 | N | 0
2025-01-29 | 16 | 2031-01-29 16:00 | 5.17 | 6.5032 | N | 0
2025-01-29 | 17 | 2031-01-29 17:00 | 5.49 | 6.9058 | N | 0
2025-01-29 | 18 | 2031-01-29 18:00 | 6.02 | 7.5724 | N | 0
2025-01-29 | 19 | 2031-01-29 19:00 | 5.93 | 7.4592 | N | 0
2025-01-29 | 20 | 2031-01-29 20:00 | 5.78 | 7.2706 | N | 0
2025-01-29 | 21 | 2031-01-29 21:00 | 5.72 | 7.1951 | N | 0
2025-01-29 | 22 | 2031-01-29 22:00 | 5.47 | 6.8806 | N | 0
2025-01-29 | 23 | 2031-01-29 23:00 | 5.1 | 6.4152 | N | 0
2025-01-30 | 00 | 2031-01-30 | 4.49 | 5.6479 | N | 0
2025-01-30 | 01 | 2031-01-30 01:00 | 4.07 | 5.1196 | N | 0
2025-01-30 | 02 | 2031-01-30 02:00 | 3.95 | 4.9686 | N | 0
2025-01-30 | 03 | 2031-01-30 03:00 | 3.78 | 4.7548 | N | 0
2025-01-30 | 04 | 2031-01-30 04:00 | 3.77 | 4.7422 | N | 0
2025-01-30 | 05 | 2031-01-30 05:00 | 3.86 | 4.8554 | N | 0
2025-01-30 | 06 | 2031-01-30 06:00 | 3.99 | 5.0189 | N | 0
2025-01-30 | 07 | 2031-01-30 07:00 | 4.49 | 5.6479 | N | 0
2025-01-30 | 08 | 2031-01-30 08:00 | 4.99 | 6.2768 | N | 0
2025-01-30 | 09 | 2031-01-30 09:00 | 4.97 | 6.2517 | N | 0
2025-01-30 | 10 | 2031-01-30 10:00 | 5.17 | 6.5032 | N | 0
2025-01-30 | 11 | 2031-01-30 11:00 | 5.07 | 6.3775 | N | 0
2025-01-30 | 12 | 2031-01-30 12:00 | 5.05 | 6.3523 | N | 0
2025-01-30 | 13 | 2031-01-30 13:00 | 5.11 | 6.4278 | N | 0
2025-01-30 | 14 | 2031-01-30 14:00 | 5.02 | 6.3146 | N | 0
2025-01-30 | 15 | 2031-01-30 15:00 | 5.01 | 6.302 | N | 0
2025-01-30 | 16 | 2031-01-30 16:00 | 5.07 | 6.3775 | N | 0
2025-01-30 | 17 | 2031-01-30 17:00 | 5.46 | 6.868 | N | 0
2025-01-30 | 18 | 2031-01-30 18:00 | 5.81 | 7.3083 | N | 0
2025-01-30 | 19 | 2031-01-30 19:00 | 5.82 | 7.3209 | N | 0
2025-01-30 | 20 | 2031-01-30 20:00 | 5.49 | 6.9058 | N | 0
2025-01-30 | 21 | 2031-01-30 21:00 | 5.42 | 6.8177 | N | 0
2025-01-30 | 22 | 2031-01-30 22:00 | 5.17 | 6.5032 | N | 0
2025-01-30 | 23 | 2031-01-30 23:00 | 5.1 | 6.4152 | N | 0
2025-01-31 | 00 | 2031-01-31 | 4.3 | 5.4089 | N | 0
2025-01-31 | 01 | 2031-01-31 01:00 | 3.98 | 5.0064 | N | 0
2025-01-31 | 02 | 2031-01-31 02:00 | 3.79 | 4.7674 | N | 0
2025-01-31 | 03 | 2031-01-31 03:00 | 3.64 | 4.5787 | N | 0
2025-01-31 | 04 | 2031-01-31 04:00 | 3.62 | 4.5535 | N | 0
2025-01-31 | 05 | 2031-01-31 05:00 | 3.69 | 4.6416 | N | 0
2025-01-31 | 06 | 2031-01-31 06:00 | 3.86 | 4.8554 | N | 0
2025-01-31 | 07 | 2031-01-31 07:00 | 4.23 | 5.3208 | N | 0
2025-01-31 | 08 | 2031-01-31 08:00 | 4.52 | 5.6856 | N | 0
2025-01-31 | 09 | 2031-01-31 09:00 | 4.72 | 5.9372 | N | 0
2025-01-31 | 10 | 2031-01-31 10:00 | 4.86 | 6.1133 | N | 0
2025-01-31 | 11 | 2031-01-31 11:00 | 4.86 | 6.1133 | N | 0
2025-01-31 | 12 | 2031-01-31 12:00 | 4.93 | 6.2014 | N | 0
2025-01-31 | 13 | 2031-01-31 13:00 | 4.92 | 6.1888 | N | 0
2025-01-31 | 14 | 2031-01-31 14:00 | 4.89 | 6.151 | N | 0
2025-01-31 | 15 | 2031-01-31 15:00 | 4.82 | 6.063 | N | 0
2025-01-31 | 16 | 2031-01-31 16:00 | 4.86 | 6.1133 | N | 0
2025-01-31 | 17 | 2031-01-31 17:00 | 5.08 | 6.39 | N | 0
2025-01-31 | 18 | 2031-01-31 18:00 | 5.36 | 6.7422 | N | 0
2025-01-31 | 19 | 2031-01-31 19:00 | 5.34 | 6.7171 | N | 0
2025-01-31 | 20 | 2031-01-31 20:00 | 5.2 | 6.541 | N | 0
2025-01-31 | 21 | 2031-01-31 21:00 | 5.17 | 6.5032 | N | 0
2025-01-31 | 22 | 2031-01-31 22:00 | 4.99 | 6.2768 | N | 0
2025-01-31 | 23 | 2031-01-31 23:00 | 4.57 | 5.7485 | N | 0
2025-02-01 | 00 | 2031-02-01 | 4.22 | 5.3083 | N | 0
2025-02-01 | 01 | 2031-02-01 01:00 | 4.17 | 5.2454 | N | 0
2025-02-01 | 02 | 2031-02-01 02:00 | 3.99 | 5.0189 | N | 0
2025-02-01 | 03 | 2031-02-01 03:00 | 3.82 | 4.8051 | N | 0
2025-02-01 | 04 | 2031-02-01 04:00 | 3.77 | 4.7422 | N | 0
2025-02-01 | 05 | 2031-02-01 05:00 | 3.79 | 4.7674 | N | 0
2025-02-01 | 06 | 2031-02-01 06:00 | 3.93 | 4.9435 | N | 0
2025-02-01 | 07 | 2031-02-01 07:00 | 4.17 | 5.2454 | N | 0
2025-02-01 | 08 | 2031-02-01 08:00 | 4.53 | 5.6982 | N | 0
2025-02-01 | 09 | 2031-02-01 09:00 | 4.76 | 5.9875 | N | 0
2025-02-01 | 10 | 2031-02-01 10:00 | 5 | 6.2894 | N | 0
2025-02-01 | 11 | 2031-02-01 11:00 | 5.02 | 6.3146 | N | 0
2025-02-01 | 12 | 2031-02-01 12:00 | 5.27 | 6.629 | N | 0
2025-02-01 | 13 | 2031-02-01 13:00 | 5.38 | 6.7674 | N | 0
2025-02-01 | 14 | 2031-02-01 14:00 | 5.28 | 6.6416 | N | 0
2025-02-01 | 15 | 2031-02-01 15:00 | 5.14 | 6.4655 | N | 0
2025-02-01 | 16 | 2031-02-01 16:00 | 5.34 | 6.7171 | N | 0
2025-02-01 | 17 | 2031-02-01 17:00 | 5.39 | 6.78 | N | 0
2025-02-01 | 18 | 2031-02-01 18:00 | 5.74 | 7.2202 | N | 0
2025-02-01 | 19 | 2031-02-01 19:00 | 5.97 | 7.5096 | N | 0
2025-02-01 | 20 | 2031-02-01 20:00 | 5.74 | 7.2202 | N | 0
2025-02-01 | 21 | 2031-02-01 21:00 | 5.56 | 6.9938 | N | 0
2025-02-01 | 22 | 2031-02-01 22:00 | 5.35 | 6.7297 | N | 0
2025-02-01 | 23 | 2031-02-01 23:00 | 5.12 | 6.4404 | N | 0
2025-02-02 | 00 | 2031-02-02 | 4.84 | 6.0881 | N | 0
2025-02-02 | 01 | 2031-02-02 01:00 | 4.6 | 5.7863 | N | 0
2025-02-02 | 02 | 2031-02-02 02:00 | 4.29 | 5.3963 | N | 0
2025-02-02 | 03 | 2031-02-02 03:00 | 4.15 | 5.2202 | N | 0
2025-02-02 | 04 | 2031-02-02 04:00 | 4.18 | 5.2579 | N | 0
2025-02-02 | 05 | 2031-02-02 05:00 | 4.04 | 5.0818 | N | 0
2025-02-02 | 06 | 2031-02-02 06:00 | 4.18 | 5.2579 | N | 0
2025-02-02 | 07 | 2031-02-02 07:00 | 4.18 | 5.2579 | N | 0
2025-02-02 | 08 | 2031-02-02 08:00 | 4.52 | 5.6856 | N | 0
2025-02-02 | 09 | 2031-02-02 09:00 | 4.86 | 6.1133 | N | 0
2025-02-02 | 10 | 2031-02-02 10:00 | 5.05 | 6.3523 | N | 0
2025-02-02 | 11 | 2031-02-02 11:00 | 5.34 | 6.7171 | N | 0
2025-02-02 | 12 | 2031-02-02 12:00 | 5.57 | 7.0064 | N | 0
2025-02-02 | 13 | 2031-02-02 13:00 | 5.67 | 7.1322 | N | 0
2025-02-02 | 14 | 2031-02-02 14:00 | 5.76 | 7.2454 | N | 0
2025-02-02 | 15 | 2031-02-02 15:00 | 5.58 | 7.019 | N | 0
2025-02-02 | 16 | 2031-02-02 16:00 | 5.67 | 7.1322 | N | 0
2025-02-02 | 17 | 2031-02-02 17:00 | 5.98 | 7.5221 | N | 0
2025-02-02 | 18 | 2031-02-02 18:00 | 6.18 | 7.7737 | N | 0
2025-02-02 | 19 | 2031-02-02 19:00 | 6.26 | 7.8743 | N | 0
2025-02-02 | 20 | 2031-02-02 20:00 | 5.94 | 7.4718 | N | 0
2025-02-02 | 21 | 2031-02-02 21:00 | 5.64 | 7.0945 | N | 0
2025-02-02 | 22 | 2031-02-02 22:00 | 5.39 | 6.78 | N | 0
2025-02-02 | 23 | 2031-02-02 23:00 | 4.74 | 5.9624 | N | 0
2025-02-03 | 00 | 2031-02-03 | 4.48 | 5.6353 | N | 0
2025-02-03 | 01 | 2031-02-03 01:00 | 4.04 | 5.0818 | N | 0
2025-02-03 | 02 | 2031-02-03 02:00 | 3.73 | 4.6919 | N | 0
2025-02-03 | 03 | 2031-02-03 03:00 | 3.73 | 4.6919 | N | 0
2025-02-03 | 04 | 2031-02-03 04:00 | 3.57 | 4.4906 | N | 0
2025-02-03 | 05 | 2031-02-03 05:00 | 3.55 | 4.4655 | N | 0
2025-02-03 | 06 | 2031-02-03 06:00 | 3.88 | 4.8806 | N | 0
2025-02-03 | 07 | 2031-02-03 07:00 | 4.2 | 5.2831 | N | 0
2025-02-03 | 08 | 2031-02-03 08:00 | 4.72 | 5.9372 | N | 0
2025-02-03 | 09 | 2031-02-03 09:00 | 4.8 | 6.0378 | N | 0
2025-02-03 | 10 | 2031-02-03 10:00 | 4.83 | 6.0756 | N | 0
2025-02-03 | 11 | 2031-02-03 11:00 | 5.01 | 6.302 | N | 0
2025-02-03 | 12 | 2031-02-03 12:00 | 5.08 | 6.39 | N | 0
2025-02-03 | 13 | 2031-02-03 13:00 | 5.14 | 6.4655 | N | 0
2025-02-03 | 14 | 2031-02-03 14:00 | 5.07 | 6.3775 | N | 0
2025-02-03 | 15 | 2031-02-03 15:00 | 4.96 | 6.2391 | N | 0
2025-02-03 | 16 | 2031-02-03 16:00 | 5.06 | 6.3649 | N | 0
2025-02-03 | 17 | 2031-02-03 17:00 | 5.38 | 6.7674 | N | 0
2025-02-03 | 18 | 2031-02-03 18:00 | 5.89 | 7.4089 | N | 0
2025-02-03 | 19 | 2031-02-03 19:00 | 5.75 | 7.2328 | N | 0
2025-02-03 | 20 | 2031-02-03 20:00 | 5.54 | 6.9687 | N | 0
2025-02-03 | 21 | 2031-02-03 21:00 | 5.42 | 6.8177 | N | 0
2025-02-03 | 22 | 2031-02-03 22:00 | 5.08 | 6.39 | N | 0
2025-02-03 | 23 | 2031-02-03 23:00 | 4.69 | 5.8995 | N | 0
2025-02-04 | 00 | 2031-02-04 | 4.11 | 5.1699 | N | 0
2025-02-04 | 01 | 2031-02-04 01:00 | 3.75 | 4.7171 | N | 0
2025-02-04 | 02 | 2031-02-04 02:00 | 3.58 | 4.5032 | N | 0
2025-02-04 | 03 | 2031-02-04 03:00 | 3.42 | 4.302 | N | 0
2025-02-04 | 04 | 2031-02-04 04:00 | 3.39 | 4.2642 | N | 0
2025-02-04 | 05 | 2031-02-04 05:00 | 3.39 | 4.2642 | N | 0
2025-02-04 | 06 | 2031-02-04 06:00 | 3.68 | 4.629 | N | 0
2025-02-04 | 07 | 2031-02-04 07:00 | 4.18 | 5.2579 | N | 0
2025-02-04 | 08 | 2031-02-04 08:00 | 4.63 | 5.824 | N | 0
2025-02-04 | 09 | 2031-02-04 09:00 | 4.74 | 5.9624 | N | 0
2025-02-04 | 10 | 2031-02-04 10:00 | 4.61 | 5.7988 | N | 0
2025-02-04 | 11 | 2031-02-04 11:00 | 4.77 | 6.0001 | N | 0
2025-02-04 | 12 | 2031-02-04 12:00 | 5.01 | 6.302 | N | 0
2025-02-04 | 13 | 2031-02-04 13:00 | 5.01 | 6.302 | N | 0
2025-02-04 | 14 | 2031-02-04 14:00 | 4.84 | 6.0881 | N | 0
2025-02-04 | 15 | 2031-02-04 15:00 | 4.75 | 5.9749 | N | 0
2025-02-04 | 16 | 2031-02-04 16:00 | 4.81 | 6.0504 | N | 0
2025-02-04 | 17 | 2031-02-04 17:00 | 5.25 | 6.6039 | N | 0
2025-02-04 | 18 | 2031-02-04 18:00 | 5.7 | 7.1699 | N | 0
2025-02-04 | 19 | 2031-02-04 19:00 | 5.97 | 7.5096 | N | 0
2025-02-04 | 20 | 2031-02-04 20:00 | 5.63 | 7.0819 | N | 0
2025-02-04 | 21 | 2031-02-04 21:00 | 5.68 | 7.1448 | N | 0
2025-02-04 | 22 | 2031-02-04 22:00 | 5.61 | 7.0567 | N | 0
2025-02-04 | 23 | 2031-02-04 23:00 | 4.97 | 6.2517 | N | 0
2025-02-05 | 00 | 2031-02-05 | 4.61 | 5.7988 | N | 0
2025-02-05 | 01 | 2031-02-05 01:00 | 4.15 | 5.2202 | N | 0
2025-02-05 | 02 | 2031-02-05 02:00 | 4.05 | 5.0944 | N | 0
2025-02-05 | 03 | 2031-02-05 03:00 | 3.98 | 5.0064 | N | 0
2025-02-05 | 04 | 2031-02-05 04:00 | 3.85 | 4.8428 | N | 0
2025-02-05 | 05 | 2031-02-05 05:00 | 3.87 | 4.868 | N | 0
2025-02-05 | 06 | 2031-02-05 06:00 | 4.08 | 5.1322 | N | 0
2025-02-05 | 07 | 2031-02-05 07:00 | 4.62 | 5.8114 | N | 0
2025-02-05 | 08 | 2031-02-05 08:00 | 4.96 | 6.2391 | N | 0
2025-02-05 | 09 | 2031-02-05 09:00 | 4.89 | 6.151 | N | 0
2025-02-05 | 10 | 2031-02-05 10:00 | 4.91 | 6.1762 | N | 0
2025-02-05 | 11 | 2031-02-05 11:00 | 4.92 | 6.1888 | N | 0
2025-02-05 | 12 | 2031-02-05 12:00 | 5.02 | 6.3146 | N | 0
2025-02-05 | 13 | 2031-02-05 13:00 | 4.97 | 6.2517 | N | 0
2025-02-05 | 14 | 2031-02-05 14:00 | 4.93 | 6.2014 | N | 0
2025-02-05 | 15 | 2031-02-05 15:00 | 4.84 | 6.0881 | N | 0
2025-02-05 | 16 | 2031-02-05 16:00 | 4.94 | 6.2139 | N | 0
2025-02-05 | 17 | 2031-02-05 17:00 | 5.27 | 6.629 | N | 0
2025-02-05 | 18 | 2031-02-05 18:00 | 5.9 | 7.4215 | N | 0
2025-02-05 | 19 | 2031-02-05 19:00 | 5.89 | 7.4089 | N | 0
2025-02-05 | 20 | 2031-02-05 20:00 | 5.79 | 7.2831 | N | 0
2025-02-05 | 21 | 2031-02-05 21:00 | 5.67 | 7.1322 | N | 0
2025-02-05 | 22 | 2031-02-05 22:00 | 5.4 | 6.7926 | N | 0
2025-02-05 | 23 | 2031-02-05 23:00 | 5.22 | 6.5661 | N | 0
2025-02-06 | 00 | 2031-02-06 | 4.5 | 5.6605 | N | 0
2025-02-06 | 01 | 2031-02-06 01:00 | 4.29 | 5.3963 | N | 0
2025-02-06 | 02 | 2031-02-06 02:00 | 3.9 | 4.9057 | N | 0
2025-02-06 | 03 | 2031-02-06 03:00 | 3.86 | 4.8554 | N | 0
2025-02-06 | 04 | 2031-02-06 04:00 | 3.76 | 4.7296 | N | 0
2025-02-06 | 05 | 2031-02-06 05:00 | 3.76 | 4.7296 | N | 0
2025-02-06 | 06 | 2031-02-06 06:00 | 4.05 | 5.0944 | N | 0
2025-02-06 | 07 | 2031-02-06 07:00 | 4.27 | 5.3712 | N | 0
2025-02-06 | 08 | 2031-02-06 08:00 | 4.84 | 6.0881 | N | 0
2025-02-06 | 09 | 2031-02-06 09:00 | 4.97 | 6.2517 | N | 0
2025-02-06 | 10 | 2031-02-06 10:00 | 5.12 | 6.4404 | N | 0
2025-02-06 | 11 | 2031-02-06 11:00 | 5.22 | 6.5661 | N | 0
2025-02-06 | 12 | 2031-02-06 12:00 | 5.25 | 6.6039 | N | 0
2025-02-06 | 13 | 2031-02-06 13:00 | 5.26 | 6.6165 | N | 0
2025-02-06 | 14 | 2031-02-06 14:00 | 5.3 | 6.6668 | N | 0
2025-02-06 | 15 | 2031-02-06 15:00 | 5.09 | 6.4026 | N | 0
2025-02-06 | 16 | 2031-02-06 16:00 | 5.03 | 6.3271 | N | 0
2025-02-06 | 17 | 2031-02-06 17:00 | 5.42 | 6.8177 | N | 0
2025-02-06 | 18 | 2031-02-06 18:00 | 5.86 | 7.3712 | N | 0
2025-02-06 | 19 | 2031-02-06 19:00 | 5.92 | 7.4467 | N | 0
2025-02-06 | 20 | 2031-02-06 20:00 | 5.47 | 6.8806 | N | 0
2025-02-06 | 21 | 2031-02-06 21:00 | 5.43 | 6.8303 | N | 0
2025-02-06 | 22 | 2031-02-06 22:00 | 5.18 | 6.5158 | N | 0
2025-02-06 | 23 | 2031-02-06 23:00 | 4.64 | 5.8366 | N | 0
2025-02-07 | 00 | 2031-02-07 | 4.22 | 5.3083 | N | 0
2025-02-07 | 01 | 2031-02-07 01:00 | 3.87 | 4.868 | N | 0
2025-02-07 | 02 | 2031-02-07 02:00 | 3.7 | 4.6542 | N | 0
2025-02-07 | 03 | 2031-02-07 03:00 | 3.57 | 4.4906 | N | 0
2025-02-07 | 04 | 2031-02-07 04:00 | 3.54 | 4.4529 | N | 0
2025-02-07 | 05 | 2031-02-07 05:00 | 3.57 | 4.4906 | N | 0
2025-02-07 | 06 | 2031-02-07 06:00 | 3.89 | 4.8932 | N | 0
2025-02-07 | 07 | 2031-02-07 07:00 | 4.32 | 5.434 | N | 0
2025-02-07 | 08 | 2031-02-07 08:00 | 4.74 | 5.9624 | N | 0
2025-02-07 | 09 | 2031-02-07 09:00 | 4.84 | 6.0881 | N | 0
2025-02-07 | 10 | 2031-02-07 10:00 | 4.92 | 6.1888 | N | 0
2025-02-07 | 11 | 2031-02-07 11:00 | 4.94 | 6.2139 | N | 0
2025-02-07 | 12 | 2031-02-07 12:00 | 4.99 | 6.2768 | N | 0
2025-02-07 | 13 | 2031-02-07 13:00 | 4.98 | 6.2642 | N | 0
2025-02-07 | 14 | 2031-02-07 14:00 | 4.94 | 6.2139 | N | 0
2025-02-07 | 15 | 2031-02-07 15:00 | 4.94 | 6.2139 | N | 0
2025-02-07 | 16 | 2031-02-07 16:00 | 4.96 | 6.2391 | N | 0
2025-02-07 | 17 | 2031-02-07 17:00 | 5.25 | 6.6039 | N | 0
2025-02-07 | 18 | 2031-02-07 18:00 | 5.66 | 7.1196 | N | 0
2025-02-07 | 19 | 2031-02-07 19:00 | 5.64 | 7.0945 | N | 0
2025-02-07 | 20 | 2031-02-07 20:00 | 5.54 | 6.9687 | N | 0
2025-02-07 | 21 | 2031-02-07 21:00 | 5.45 | 6.8555 | N | 0
2025-02-07 | 22 | 2031-02-07 22:00 | 5.17 | 6.5032 | N | 0
2025-02-07 | 23 | 2031-02-07 23:00 | 5.02 | 6.3146 | N | 0
2025-02-08 | 00 | 2031-02-08 | 4.5 | 5.6605 | N | 0
2025-02-08 | 01 | 2031-02-08 01:00 | 4.14 | 5.2076 | N | 0
2025-02-08 | 02 | 2031-02-08 02:00 | 3.91 | 4.9183 | N | 0
2025-02-08 | 03 | 2031-02-08 03:00 | 3.65 | 4.5913 | N | 0
2025-02-08 | 04 | 2031-02-08 04:00 | 3.72 | 4.6793 | N | 0
2025-02-08 | 05 | 2031-02-08 05:00 | 3.62 | 4.5535 | N | 0
2025-02-08 | 06 | 2031-02-08 06:00 | 3.69 | 4.6416 | N | 0
2025-02-08 | 07 | 2031-02-08 07:00 | 3.99 | 5.0189 | N | 0
2025-02-08 | 08 | 2031-02-08 08:00 | 4.36 | 5.4844 | N | 0
2025-02-08 | 09 | 2031-02-08 09:00 | 4.45 | 5.5976 | N | 0
2025-02-08 | 10 | 2031-02-08 10:00 | 4.66 | 5.8617 | N | 0
2025-02-08 | 11 | 2031-02-08 11:00 | 4.77 | 6.0001 | N | 0
2025-02-08 | 12 | 2031-02-08 12:00 | 4.93 | 6.2014 | N | 0
2025-02-08 | 13 | 2031-02-08 13:00 | 5.29 | 6.6542 | N | 0
2025-02-08 | 14 | 2031-02-08 14:00 | 5.14 | 6.4655 | N | 0
2025-02-08 | 15 | 2031-02-08 15:00 | 5.2 | 6.541 | N | 0
2025-02-08 | 16 | 2031-02-08 16:00 | 5.06 | 6.3649 | N | 0
2025-02-08 | 17 | 2031-02-08 17:00 | 5.34 | 6.7171 | N | 0
2025-02-08 | 18 | 2031-02-08 18:00 | 5.55 | 6.9812 | N | 0
2025-02-08 | 19 | 2031-02-08 19:00 | 5.65 | 7.107 | N | 0
2025-02-08 | 20 | 2031-02-08 20:00 | 5.47 | 6.8806 | N | 0
2025-02-08 | 21 | 2031-02-08 21:00 | 5.22 | 6.5661 | N | 0
2025-02-08 | 22 | 2031-02-08 22:00 | 5.08 | 6.39 | N | 0
2025-02-08 | 23 | 2031-02-08 23:00 | 4.77 | 6.0001 | N | 0
2025-02-09 | 00 | 2031-02-09 | 4.29 | 5.3963 | N | 0
2025-02-09 | 01 | 2031-02-09 01:00 | 3.99 | 5.0189 | N | 0
2025-02-09 | 02 | 2031-02-09 02:00 | 3.86 | 4.8554 | N | 0
2025-02-09 | 03 | 2031-02-09 03:00 | 3.65 | 4.5913 | N | 0
2025-02-09 | 04 | 2031-02-09 04:00 | 3.57 | 4.4906 | N | 0
2025-02-09 | 05 | 2031-02-09 05:00 | 3.51 | 4.4152 | N | 0
2025-02-09 | 06 | 2031-02-09 06:00 | 3.55 | 4.4655 | N | 0
2025-02-09 | 07 | 2031-02-09 07:00 | 3.75 | 4.7171 | N | 0
2025-02-09 | 08 | 2031-02-09 08:00 | 3.96 | 4.9812 | N | 0
2025-02-09 | 09 | 2031-02-09 09:00 | 4.23 | 5.3208 | N | 0
2025-02-09 | 10 | 2031-02-09 10:00 | 4.6 | 5.7863 | N | 0
2025-02-09 | 11 | 2031-02-09 11:00 | 4.82 | 6.063 | N | 0
2025-02-09 | 12 | 2031-02-09 12:00 | 5.1 | 6.4152 | N | 0
2025-02-09 | 13 | 2031-02-09 13:00 | 5.14 | 6.4655 | N | 0
2025-02-09 | 14 | 2031-02-09 14:00 | 5.06 | 6.3649 | N | 0
2025-02-09 | 15 | 2031-02-09 15:00 | 5.14 | 6.4655 | N | 0
2025-02-09 | 16 | 2031-02-09 16:00 | 5.13 | 6.4529 | N | 0
2025-02-09 | 17 | 2031-02-09 17:00 | 5.48 | 6.8932 | N | 0
2025-02-09 | 18 | 2031-02-09 18:00 | 5.91 | 7.4341 | N | 0
2025-02-09 | 19 | 2031-02-09 19:00 | 6.01 | 7.5599 | N | 0
2025-02-09 | 20 | 2031-02-09 20:00 | 5.57 | 7.0064 | N | 0
2025-02-09 | 21 | 2031-02-09 21:00 | 5.31 | 6.6794 | N | 0
2025-02-09 | 22 | 2031-02-09 22:00 | 4.95 | 6.2265 | N | 0
2025-02-09 | 23 | 2031-02-09 23:00 | 4.64 | 5.8366 | N | 0
2025-02-10 | 00 | 2031-02-10 | 4.35 | 5.4718 | N | 0
2025-02-10 | 01 | 2031-02-10 01:00 | 3.84 | 4.8303 | N | 0
2025-02-10 | 02 | 2031-02-10 02:00 | 3.61 | 4.541 | N | 0
2025-02-10 | 03 | 2031-02-10 03:00 | 3.53 | 4.4403 | N | 0
2025-02-10 | 04 | 2031-02-10 04:00 | 3.51 | 4.4152 | N | 0
2025-02-10 | 05 | 2031-02-10 05:00 | 3.53 | 4.4403 | N | 0
2025-02-10 | 06 | 2031-02-10 06:00 | 3.85 | 4.8428 | N | 0
2025-02-10 | 07 | 2031-02-10 07:00 | 4.16 | 5.2328 | N | 0
2025-02-10 | 08 | 2031-02-10 08:00 | 4.61 | 5.7988 | N | 0
2025-02-10 | 09 | 2031-02-10 09:00 | 4.77 | 6.0001 | N | 0
2025-02-10 | 10 | 2031-02-10 10:00 | 4.86 | 6.1133 | N | 0
2025-02-10 | 11 | 2031-02-10 11:00 | 4.86 | 6.1133 | N | 0
2025-02-10 | 12 | 2031-02-10 12:00 | 4.96 | 6.2391 | N | 0
2025-02-10 | 13 | 2031-02-10 13:00 | 5.09 | 6.4026 | N | 0
2025-02-10 | 14 | 2031-02-10 14:00 | 5.01 | 6.302 | N | 0
2025-02-10 | 15 | 2031-02-10 15:00 | 4.98 | 6.2642 | N | 0
2025-02-10 | 16 | 2031-02-10 16:00 | 5.1 | 6.4152 | N | 0
2025-02-10 | 17 | 2031-02-10 17:00 | 5.52 | 6.9435 | N | 0
2025-02-10 | 18 | 2031-02-10 18:00 | 5.88 | 7.3963 | N | 0
2025-02-10 | 19 | 2031-02-10 19:00 | 5.91 | 7.4341 | N | 0
2025-02-10 | 20 | 2031-02-10 20:00 | 5.64 | 7.0945 | N | 0
2025-02-10 | 21 | 2031-02-10 21:00 | 5.52 | 6.9435 | N | 0
2025-02-10 | 22 | 2031-02-10 22:00 | 5.31 | 6.6794 | N | 0
2025-02-10 | 23 | 2031-02-10 23:00 | 4.89 | 6.151 | N | 0
2025-02-11 | 00 | 2031-02-11 | 4.43 | 5.5724 | N | 0
2025-02-11 | 01 | 2031-02-11 01:00 | 3.97 | 4.9938 | N | 0
2025-02-11 | 02 | 2031-02-11 02:00 | 3.71 | 4.6667 | N | 0
2025-02-11 | 03 | 2031-02-11 03:00 | 3.65 | 4.5913 | N | 0
2025-02-11 | 04 | 2031-02-11 04:00 | 3.64 | 4.5787 | N | 0
2025-02-11 | 05 | 2031-02-11 05:00 | 3.79 | 4.7674 | N | 0
2025-02-11 | 06 | 2031-02-11 06:00 | 4.01 | 5.0441 | N | 0
2025-02-11 | 07 | 2031-02-11 07:00 | 4.52 | 5.6856 | N | 0
2025-02-11 | 08 | 2031-02-11 08:00 | 4.88 | 6.1385 | N | 0
2025-02-11 | 09 | 2031-02-11 09:00 | 5.03 | 6.3271 | N | 0
2025-02-11 | 10 | 2031-02-11 10:00 | 5.06 | 6.3649 | N | 0
2025-02-11 | 11 | 2031-02-11 11:00 | 5 | 6.2894 | N | 0
2025-02-11 | 12 | 2031-02-11 12:00 | 4.89 | 6.151 | N | 0
2025-02-11 | 13 | 2031-02-11 13:00 | 4.81 | 6.0504 | N | 0
2025-02-11 | 14 | 2031-02-11 14:00 | 4.94 | 6.2139 | N | 0
2025-02-11 | 15 | 2031-02-11 15:00 | 4.84 | 6.0881 | N | 0
2025-02-11 | 16 | 2031-02-11 16:00 | 4.85 | 6.1007 | N | 0
2025-02-11 | 17 | 2031-02-11 17:00 | 5.26 | 6.6165 | N | 0
2025-02-11 | 18 | 2031-02-11 18:00 | 5.69 | 7.1573 | N | 0
2025-02-11 | 19 | 2031-02-11 19:00 | 5.69 | 7.1573 | N | 0
2025-02-11 | 20 | 2031-02-11 20:00 | 5.64 | 7.0945 | N | 0
2025-02-11 | 21 | 2031-02-11 21:00 | 5.49 | 6.9058 | N | 0
2025-02-11 | 22 | 2031-02-11 22:00 | 5.32 | 6.6919 | N | 0
2025-02-11 | 23 | 2031-02-11 23:00 | 5 | 6.2894 | N | 0
2025-02-12 | 00 | 2031-02-12 | 4.31 | 5.4215 | N | 0
2025-02-12 | 01 | 2031-02-12 01:00 | 3.88 | 4.8806 | N | 0
2025-02-12 | 02 | 2031-02-12 02:00 | 3.8 | 4.7799 | N | 0
2025-02-12 | 03 | 2031-02-12 03:00 | 3.71 | 4.6667 | N | 0
2025-02-12 | 04 | 2031-02-12 04:00 | 3.72 | 4.6793 | N | 0
2025-02-12 | 05 | 2031-02-12 05:00 | 3.79 | 4.7674 | N | 0
2025-02-12 | 06 | 2031-02-12 06:00 | 3.9 | 4.9057 | N | 0
2025-02-12 | 07 | 2031-02-12 07:00 | 4.4 | 5.5347 | N | 0
2025-02-12 | 08 | 2031-02-12 08:00 | 4.79 | 6.0253 | N | 0
2025-02-12 | 09 | 2031-02-12 09:00 | 4.86 | 6.1133 | N | 0
2025-02-12 | 10 | 2031-02-12 10:00 | 4.97 | 6.2517 | N | 0
2025-02-12 | 11 | 2031-02-12 11:00 | 4.98 | 6.2642 | N | 0
2025-02-12 | 12 | 2031-02-12 12:00 | 4.91 | 6.1762 | N | 0
2025-02-12 | 13 | 2031-02-12 13:00 | 4.97 | 6.2517 | N | 0
2025-02-12 | 14 | 2031-02-12 14:00 | 4.96 | 6.2391 | N | 0
2025-02-12 | 15 | 2031-02-12 15:00 | 5.08 | 6.39 | N | 0
2025-02-12 | 16 | 2031-02-12 16:00 | 5.15 | 6.4781 | N | 0
2025-02-12 | 17 | 2031-02-12 17:00 | 5.69 | 7.1573 | N | 0
2025-02-12 | 18 | 2031-02-12 18:00 | 5.92 | 7.4467 | N | 0
2025-02-12 | 19 | 2031-02-12 19:00 | 6.1 | 7.6731 | N | 0
2025-02-12 | 20 | 2031-02-12 20:00 | 5.91 | 7.4341 | N | 0
2025-02-12 | 21 | 2031-02-12 21:00 | 5.68 | 7.1448 | N | 0
2025-02-12 | 22 | 2031-02-12 22:00 | 5.41 | 6.8051 | N | 0
2025-02-12 | 23 | 2031-02-12 23:00 | 5.02 | 6.3146 | N | 0
2025-02-13 | 00 | 2031-02-13 | 4.62 | 5.8114 | N | 0
2025-02-13 | 01 | 2031-02-13 01:00 | 4.05 | 5.0944 | N | 0
2025-02-13 | 02 | 2031-02-13 02:00 | 3.93 | 4.9435 | N | 0
2025-02-13 | 03 | 2031-02-13 03:00 | 3.69 | 4.6416 | N | 0
2025-02-13 | 04 | 2031-02-13 04:00 | 3.75 | 4.7171 | N | 0
2025-02-13 | 05 | 2031-02-13 05:00 | 3.66 | 4.6038 | N | 0
2025-02-13 | 06 | 2031-02-13 06:00 | 3.84 | 4.8303 | N | 0
2025-02-13 | 07 | 2031-02-13 07:00 | 4.21 | 5.2957 | N | 0
2025-02-13 | 08 | 2031-02-13 08:00 | 4.38 | 5.5095 | N | 0
2025-02-13 | 09 | 2031-02-13 09:00 | 4.6 | 5.7863 | N | 0
2025-02-13 | 10 | 2031-02-13 10:00 | 4.89 | 6.151 | N | 0
2025-02-13 | 11 | 2031-02-13 11:00 | 5.03 | 6.3271 | N | 0
2025-02-13 | 12 | 2031-02-13 12:00 | 5.09 | 6.4026 | N | 0
2025-02-13 | 13 | 2031-02-13 13:00 | 5.37 | 6.7548 | N | 0
2025-02-13 | 14 | 2031-02-13 14:00 | 5.29 | 6.6542 | N | 0
2025-02-13 | 15 | 2031-02-13 15:00 | 5.13 | 6.4529 | N | 0
2025-02-13 | 16 | 2031-02-13 16:00 | 5.17 | 6.5032 | N | 0
2025-02-13 | 17 | 2031-02-13 17:00 | 5.41 | 6.8051 | N | 0
2025-02-13 | 18 | 2031-02-13 18:00 | 5.8 | 7.2957 | N | 0
2025-02-13 | 19 | 2031-02-13 19:00 | 5.85 | 7.3586 | N | 0
2025-02-13 | 20 | 2031-02-13 20:00 | 5.61 | 7.0567 | N | 0
2025-02-13 | 21 | 2031-02-13 21:00 | 5.51 | 6.9309 | N | 0
2025-02-13 | 22 | 2031-02-13 22:00 | 5.3 | 6.6668 | N | 0
2025-02-13 | 23 | 2031-02-13 23:00 | 4.89 | 6.151 | N | 0
2025-02-14 | 00 | 2031-02-14 | 4.36 | 5.4844 | N | 0
2025-02-14 | 01 | 2031-02-14 01:00 | 4.01 | 5.0441 | N | 0
2025-02-14 | 02 | 2031-02-14 02:00 | 3.8 | 4.7799 | N | 0
2025-02-14 | 03 | 2031-02-14 03:00 | 3.78 | 4.7548 | N | 0
2025-02-14 | 04 | 2031-02-14 04:00 | 3.63 | 4.5661 | N | 0
2025-02-14 | 05 | 2031-02-14 05:00 | 3.68 | 4.629 | N | 0
2025-02-14 | 06 | 2031-02-14 06:00 | 3.94 | 4.9561 | N | 0
2025-02-14 | 07 | 2031-02-14 07:00 | 4.35 | 5.4718 | N | 0
2025-02-14 | 08 | 2031-02-14 08:00 | 4.92 | 6.1888 | N | 0
2025-02-14 | 09 | 2031-02-14 09:00 | 4.85 | 6.1007 | N | 0
2025-02-14 | 10 | 2031-02-14 10:00 | 5 | 6.2894 | N | 0
2025-02-14 | 11 | 2031-02-14 11:00 | 5.01 | 6.302 | N | 0
2025-02-14 | 12 | 2031-02-14 12:00 | 4.99 | 6.2768 | N | 0
2025-02-14 | 13 | 2031-02-14 13:00 | 5.22 | 6.5661 | N | 0
2025-02-14 | 14 | 2031-02-14 14:00 | 5.19 | 6.5284 | N | 0
2025-02-14 | 15 | 2031-02-14 15:00 | 5.01 | 6.302 | N | 0
2025-02-14 | 16 | 2031-02-14 16:00 | 5.01 | 6.302 | N | 0
2025-02-14 | 17 | 2031-02-14 17:00 | 5.22 | 6.5661 | N | 0
2025-02-14 | 18 | 2031-02-14 18:00 | 5.52 | 6.9435 | N | 0
2025-02-14 | 19 | 2031-02-14 19:00 | 5.56 | 6.9938 | N | 0
2025-02-14 | 20 | 2031-02-14 20:00 | 5.53 | 6.9561 | N | 0
2025-02-14 | 21 | 2031-02-14 21:00 | 5.44 | 6.8429 | N | 0
2025-02-14 | 22 | 2031-02-14 22:00 | 5.25 | 6.6039 | N | 0
2025-02-14 | 23 | 2031-02-14 23:00 | 4.84 | 6.0881 | N | 0
2025-02-15 | 00 | 2031-02-15 | 4.49 | 5.6479 | N | 0
2025-02-15 | 01 | 2031-02-15 01:00 | 4.03 | 5.0693 | N | 0
2025-02-15 | 02 | 2031-02-15 02:00 | 3.9 | 4.9057 | N | 0
2025-02-15 | 03 | 2031-02-15 03:00 | 3.76 | 4.7296 | N | 0
2025-02-15 | 04 | 2031-02-15 04:00 | 3.71 | 4.6667 | N | 0
2025-02-15 | 05 | 2031-02-15 05:00 | 3.68 | 4.629 | N | 0
2025-02-15 | 06 | 2031-02-15 06:00 | 3.75 | 4.7171 | N | 0
2025-02-15 | 07 | 2031-02-15 07:00 | 3.9 | 4.9057 | N | 0
2025-02-15 | 08 | 2031-02-15 08:00 | 4.1 | 5.1573 | N | 0
2025-02-15 | 09 | 2031-02-15 09:00 | 4.45 | 5.5976 | N | 0
2025-02-15 | 10 | 2031-02-15 10:00 | 4.66 | 5.8617 | N | 0
2025-02-15 | 11 | 2031-02-15 11:00 | 4.88 | 6.1385 | N | 0
2025-02-15 | 12 | 2031-02-15 12:00 | 5.06 | 6.3649 | N | 0
2025-02-15 | 13 | 2031-02-15 13:00 | 5.18 | 6.5158 | N | 0
2025-02-15 | 14 | 2031-02-15 14:00 | 5.17 | 6.5032 | N | 0
2025-02-15 | 15 | 2031-02-15 15:00 | 5.2 | 6.541 | N | 0
2025-02-15 | 16 | 2031-02-15 16:00 | 5.16 | 6.4907 | N | 0
2025-02-15 | 17 | 2031-02-15 17:00 | 5.43 | 6.8303 | N | 0
2025-02-15 | 18 | 2031-02-15 18:00 | 5.7 | 7.1699 | N | 0
2025-02-15 | 19 | 2031-02-15 19:00 | 5.75 | 7.2328 | N | 0
2025-02-15 | 20 | 2031-02-15 20:00 | 5.48 | 6.8932 | N | 0
2025-02-15 | 21 | 2031-02-15 21:00 | 5.35 | 6.7297 | N | 0
2025-02-15 | 22 | 2031-02-15 22:00 | 5.05 | 6.3523 | N | 0
2025-02-15 | 23 | 2031-02-15 23:00 | 4.73 | 5.9498 | N | 0
2025-02-16 | 00 | 2031-02-16 | 4.43 | 5.5724 | N | 0
2025-02-16 | 01 | 2031-02-16 01:00 | 4.1 | 5.1573 | N | 0
2025-02-16 | 02 | 2031-02-16 02:00 | 3.89 | 4.8932 | N | 0
2025-02-16 | 03 | 2031-02-16 03:00 | 3.84 | 4.8303 | N | 0
2025-02-16 | 04 | 2031-02-16 04:00 | 3.64 | 4.5787 | N | 0
2025-02-16 | 05 | 2031-02-16 05:00 | 3.71 | 4.6667 | N | 0
2025-02-16 | 06 | 2031-02-16 06:00 | 3.84 | 4.8303 | N | 0
2025-02-16 | 07 | 2031-02-16 07:00 | 3.9 | 4.9057 | N | 0
2025-02-16 | 08 | 2031-02-16 08:00 | 4.11 | 5.1699 | N | 0
2025-02-16 | 09 | 2031-02-16 09:00 | 4.54 | 5.7108 | N | 0
2025-02-16 | 10 | 2031-02-16 10:00 | 4.97 | 6.2517 | N | 0
2025-02-16 | 11 | 2031-02-16 11:00 | 5.17 | 6.5032 | N | 0
2025-02-16 | 12 | 2031-02-16 12:00 | 5.38 | 6.7674 | N | 0
2025-02-16 | 13 | 2031-02-16 13:00 | 5.56 | 6.9938 | N | 0
2025-02-16 | 14 | 2031-02-16 14:00 | 5.53 | 6.9561 | N | 0
2025-02-16 | 15 | 2031-02-16 15:00 | 5.39 | 6.78 | N | 0
2025-02-16 | 16 | 2031-02-16 16:00 | 5.43 | 6.8303 | N | 0
2025-02-16 | 17 | 2031-02-16 17:00 | 5.81 | 7.3083 | N | 0
2025-02-16 | 18 | 2031-02-16 18:00 | 5.97 | 7.5096 | N | 0
2025-02-16 | 19 | 2031-02-16 19:00 | 5.95 | 7.4844 | N | 0
2025-02-16 | 20 | 2031-02-16 20:00 | 5.69 | 7.1573 | N | 0
2025-02-16 | 21 | 2031-02-16 21:00 | 5.53 | 6.9561 | N | 0
2025-02-16 | 22 | 2031-02-16 22:00 | 5.19 | 6.5284 | N | 0
2025-02-16 | 23 | 2031-02-16 23:00 | 4.92 | 6.1888 | N | 0
2025-02-17 | 00 | 2031-02-17 | 4.59 | 5.7737 | N | 0
2025-02-17 | 01 | 2031-02-17 01:00 | 4.32 | 5.434 | N | 0
2025-02-17 | 02 | 2031-02-17 02:00 | 3.99 | 5.0189 | N | 0
2025-02-17 | 03 | 2031-02-17 03:00 | 3.9 | 4.9057 | N | 0
2025-02-17 | 04 | 2031-02-17 04:00 | 3.85 | 4.8428 | N | 0
2025-02-17 | 05 | 2031-02-17 05:00 | 3.96 | 4.9812 | N | 0
2025-02-17 | 06 | 2031-02-17 06:00 | 3.94 | 4.9561 | N | 0
2025-02-17 | 07 | 2031-02-17 07:00 | 4.21 | 5.2957 | N | 0
2025-02-17 | 08 | 2031-02-17 08:00 | 4.3 | 5.4089 | N | 0
2025-02-17 | 09 | 2031-02-17 09:00 | 4.48 | 5.6353 | N | 0
2025-02-17 | 10 | 2031-02-17 10:00 | 4.75 | 5.9749 | N | 0
2025-02-17 | 11 | 2031-02-17 11:00 | 4.91 | 6.1762 | N | 0
2025-02-17 | 12 | 2031-02-17 12:00 | 5.09 | 6.4026 | N | 0
2025-02-17 | 13 | 2031-02-17 13:00 | 5.41 | 6.8051 | N | 0
2025-02-17 | 14 | 2031-02-17 14:00 | 5.36 | 6.7422 | N | 0
2025-02-17 | 15 | 2031-02-17 15:00 | 5.22 | 6.5661 | N | 0
2025-02-17 | 16 | 2031-02-17 16:00 | 5.29 | 6.6542 | N | 0
2025-02-17 | 17 | 2031-02-17 17:00 | 5.93 | 7.4592 | N | 0
2025-02-17 | 18 | 2031-02-17 18:00 | 6.14 | 7.7234 | N | 0
2025-02-17 | 19 | 2031-02-17 19:00 | 6.11 | 7.6857 | N | 0
2025-02-17 | 20 | 2031-02-17 20:00 | 5.9 | 7.4215 | N | 0
2025-02-17 | 21 | 2031-02-17 21:00 | 5.69 | 7.1573 | N | 0
2025-02-17 | 22 | 2031-02-17 22:00 | 5.51 | 6.9309 | N | 0
2025-02-17 | 23 | 2031-02-17 23:00 | 5.2 | 6.541 | N | 0
2025-02-18 | 00 | 2031-02-18 | 4.65 | 5.8491 | N | 0
2025-02-18 | 01 | 2031-02-18 01:00 | 4.35 | 5.4718 | N | 0
2025-02-18 | 02 | 2031-02-18 02:00 | 4.09 | 5.1447 | N | 0
2025-02-18 | 03 | 2031-02-18 03:00 | 4.03 | 5.0693 | N | 0
2025-02-18 | 04 | 2031-02-18 04:00 | 3.9 | 4.9057 | N | 0
2025-02-18 | 05 | 2031-02-18 05:00 | 4.07 | 5.1196 | N | 0
2025-02-18 | 06 | 2031-02-18 06:00 | 4.36 | 5.4844 | N | 0
2025-02-18 | 07 | 2031-02-18 07:00 | 4.62 | 5.8114 | N | 0
2025-02-18 | 08 | 2031-02-18 08:00 | 4.97 | 6.2517 | N | 0
2025-02-18 | 09 | 2031-02-18 09:00 | 5.19 | 6.5284 | N | 0
2025-02-18 | 10 | 2031-02-18 10:00 | 5.25 | 6.6039 | N | 0
2025-02-18 | 11 | 2031-02-18 11:00 | 5.19 | 6.5284 | N | 0
2025-02-18 | 12 | 2031-02-18 12:00 | 5.34 | 6.7171 | N | 0
2025-02-18 | 13 | 2031-02-18 13:00 | 5.4 | 6.7926 | N | 0
2025-02-18 | 14 | 2031-02-18 14:00 | 5.37 | 6.7548 | N | 0
2025-02-18 | 15 | 2031-02-18 15:00 | 5.34 | 6.7171 | N | 0
2025-02-18 | 16 | 2031-02-18 16:00 | 5.4 | 6.7926 | N | 0
2025-02-18 | 17 | 2031-02-18 17:00 | 5.66 | 7.1196 | N | 0
2025-02-18 | 18 | 2031-02-18 18:00 | 6.21 | 7.8114 | N | 0
2025-02-18 | 19 | 2031-02-18 19:00 | 6.03 | 7.585 | N | 0
2025-02-18 | 20 | 2031-02-18 20:00 | 5.89 | 7.4089 | N | 0
2025-02-18 | 21 | 2031-02-18 21:00 | 5.85 | 7.3586 | N | 0
2025-02-18 | 22 | 2031-02-18 22:00 | 5.59 | 7.0316 | N | 0
2025-02-18 | 23 | 2031-02-18 23:00 | 5.25 | 6.6039 | N | 0
2025-02-19 | 00 | 2031-02-19 | 4.55 | 5.7234 | N | 0
2025-02-19 | 01 | 2031-02-19 01:00 | 4.26 | 5.3586 | N | 0
2025-02-19 | 02 | 2031-02-19 02:00 | 3.97 | 4.9938 | N | 0
2025-02-19 | 03 | 2031-02-19 03:00 | 3.92 | 4.9309 | N | 0
2025-02-19 | 04 | 2031-02-19 04:00 | 3.94 | 4.9561 | N | 0
2025-02-19 | 05 | 2031-02-19 05:00 | 3.96 | 4.9812 | N | 0
2025-02-19 | 06 | 2031-02-19 06:00 | 4.2 | 5.2831 | N | 0
2025-02-19 | 07 | 2031-02-19 07:00 | 4.78 | 6.0127 | N | 0
2025-02-19 | 08 | 2031-02-19 08:00 | 5.08 | 6.39 | N | 0
2025-02-19 | 09 | 2031-02-19 09:00 | 5 | 6.2894 | N | 0
2025-02-19 | 10 | 2031-02-19 10:00 | 5.07 | 6.3775 | N | 0
2025-02-19 | 11 | 2031-02-19 11:00 | 5.11 | 6.4278 | N | 0
2025-02-19 | 12 | 2031-02-19 12:00 | 5.14 | 6.4655 | N | 0
2025-02-19 | 13 | 2031-02-19 13:00 | 5.13 | 6.4529 | N | 0
2025-02-19 | 14 | 2031-02-19 14:00 | 5.08 | 6.39 | N | 0
2025-02-19 | 15 | 2031-02-19 15:00 | 5.15 | 6.4781 | N | 0
2025-02-19 | 16 | 2031-02-19 16:00 | 5.14 | 6.4655 | N | 0
2025-02-19 | 17 | 2031-02-19 17:00 | 5.66 | 7.1196 | N | 0
2025-02-19 | 18 | 2031-02-19 18:00 | 5.98 | 7.5221 | N | 0
2025-02-19 | 19 | 2031-02-19 19:00 | 6.02 | 7.5724 | N | 0
2025-02-19 | 20 | 2031-02-19 20:00 | 5.97 | 7.5096 | N | 0
2025-02-19 | 21 | 2031-02-19 21:00 | 5.73 | 7.2077 | N | 0
2025-02-19 | 22 | 2031-02-19 22:00 | 5.7 | 7.1699 | N | 0
2025-02-19 | 23 | 2031-02-19 23:00 | 5.25 | 6.6039 | N | 0
2025-02-20 | 00 | 2031-02-20 | 4.65 | 5.8491 | N | 0
2025-02-20 | 01 | 2031-02-20 01:00 | 4.26 | 5.3586 | N | 0
2025-02-20 | 02 | 2031-02-20 02:00 | 4.16 | 5.2328 | N | 0
2025-02-20 | 03 | 2031-02-20 03:00 | 4.03 | 5.0693 | N | 0
2025-02-20 | 04 | 2031-02-20 04:00 | 3.94 | 4.9561 | N | 0
2025-02-20 | 05 | 2031-02-20 05:00 | 3.95 | 4.9686 | N | 0
2025-02-20 | 06 | 2031-02-20 06:00 | 4.11 | 5.1699 | N | 0
2025-02-20 | 07 | 2031-02-20 07:00 | 4.65 | 5.8491 | N | 0
2025-02-20 | 08 | 2031-02-20 08:00 | 5.03 | 6.3271 | N | 0
2025-02-20 | 09 | 2031-02-20 09:00 | 5.07 | 6.3775 | N | 0
2025-02-20 | 10 | 2031-02-20 10:00 | 5.21 | 6.5536 | N | 0
2025-02-20 | 11 | 2031-02-20 11:00 | 5.27 | 6.629 | N | 0
2025-02-20 | 12 | 2031-02-20 12:00 | 5.4 | 6.7926 | N | 0
2025-02-20 | 13 | 2031-02-20 13:00 | 5.4 | 6.7926 | N | 0
2025-02-20 | 14 | 2031-02-20 14:00 | 5.3 | 6.6668 | N | 0
2025-02-20 | 15 | 2031-02-20 15:00 | 5.2 | 6.541 | N | 0
2025-02-20 | 16 | 2031-02-20 16:00 | 5.19 | 6.5284 | N | 0
2025-02-20 | 17 | 2031-02-20 17:00 | 5.64 | 7.0945 | N | 0
2025-02-20 | 18 | 2031-02-20 18:00 | 6.03 | 7.585 | N | 0
2025-02-20 | 19 | 2031-02-20 19:00 | 6.12 | 7.6982 | N | 0
2025-02-20 | 20 | 2031-02-20 20:00 | 6.06 | 7.6228 | N | 0
2025-02-20 | 21 | 2031-02-20 21:00 | 5.87 | 7.3838 | N | 0
2025-02-20 | 22 | 2031-02-20 22:00 | 5.63 | 7.0819 | N | 0
2025-02-20 | 23 | 2031-02-20 23:00 | 5.21 | 6.5536 | N | 0
2025-02-21 | 00 | 2031-02-21 | 4.68 | 5.8869 | N | 0
2025-02-21 | 01 | 2031-02-21 01:00 | 4.3 | 5.4089 | N | 0
2025-02-21 | 02 | 2031-02-21 02:00 | 4.12 | 5.1825 | N | 0
2025-02-21 | 03 | 2031-02-21 03:00 | 4.08 | 5.1322 | N | 0
2025-02-21 | 04 | 2031-02-21 04:00 | 3.97 | 4.9938 | N | 0
2025-02-21 | 05 | 2031-02-21 05:00 | 4.07 | 5.1196 | N | 0
2025-02-21 | 06 | 2031-02-21 06:00 | 4.29 | 5.3963 | N | 0
2025-02-21 | 07 | 2031-02-21 07:00 | 4.8 | 6.0378 | N | 0
2025-02-21 | 08 | 2031-02-21 08:00 | 5.08 | 6.39 | N | 0
2025-02-21 | 09 | 2031-02-21 09:00 | 5.24 | 6.5913 | N | 0
2025-02-21 | 10 | 2031-02-21 10:00 | 5.31 | 6.6794 | N | 0
2025-02-21 | 11 | 2031-02-21 11:00 | 5.43 | 6.8303 | N | 0
2025-02-21 | 12 | 2031-02-21 12:00 | 5.24 | 6.5913 | N | 0
2025-02-21 | 13 | 2031-02-21 13:00 | 5.25 | 6.6039 | N | 0
2025-02-21 | 14 | 2031-02-21 14:00 | 5.18 | 6.5158 | N | 0
2025-02-21 | 15 | 2031-02-21 15:00 | 5.08 | 6.39 | N | 0
2025-02-21 | 16 | 2031-02-21 16:00 | 5.15 | 6.4781 | N | 0
2025-02-21 | 17 | 2031-02-21 17:00 | 5.34 | 6.7171 | N | 0
2025-02-21 | 18 | 2031-02-21 18:00 | 5.78 | 7.2706 | N | 0
2025-02-21 | 19 | 2031-02-21 19:00 | 5.84 | 7.346 | N | 0
2025-02-21 | 20 | 2031-02-21 20:00 | 5.85 | 7.3586 | N | 0
2025-02-21 | 21 | 2031-02-21 21:00 | 5.64 | 7.0945 | N | 0
2025-02-21 | 22 | 2031-02-21 22:00 | 5.42 | 6.8177 | N | 0
2025-02-21 | 23 | 2031-02-21 23:00 | 5.21 | 6.5536 | N | 0
2025-02-22 | 00 | 2031-02-22 | 4.74 | 5.9624 | N | 0
2025-02-22 | 01 | 2031-02-22 01:00 | 4.35 | 5.4718 | N | 0
2025-02-22 | 02 | 2031-02-22 02:00 | 4.07 | 5.1196 | N | 0
2025-02-22 | 03 | 2031-02-22 03:00 | 4.04 | 5.0818 | N | 0
2025-02-22 | 04 | 2031-02-22 04:00 | 4 | 5.0315 | N | 0
2025-02-22 | 05 | 2031-02-22 05:00 | 3.95 | 4.9686 | N | 0
2025-02-22 | 06 | 2031-02-22 06:00 | 3.99 | 5.0189 | N | 0
2025-02-22 | 07 | 2031-02-22 07:00 | 4.25 | 5.346 | N | 0
2025-02-22 | 08 | 2031-02-22 08:00 | 4.52 | 5.6856 | N | 0
2025-02-22 | 09 | 2031-02-22 09:00 | 4.79 | 6.0253 | N | 0
2025-02-22 | 10 | 2031-02-22 10:00 | 5.11 | 6.4278 | N | 0
2025-02-22 | 11 | 2031-02-22 11:00 | 5.25 | 6.6039 | N | 0
2025-02-22 | 12 | 2031-02-22 12:00 | 5.26 | 6.6165 | N | 0
2025-02-22 | 13 | 2031-02-22 13:00 | 5.35 | 6.7297 | N | 0
2025-02-22 | 14 | 2031-02-22 14:00 | 5.38 | 6.7674 | N | 0
2025-02-22 | 15 | 2031-02-22 15:00 | 5.22 | 6.5661 | N | 0
2025-02-22 | 16 | 2031-02-22 16:00 | 5.3 | 6.6668 | N | 0
2025-02-22 | 17 | 2031-02-22 17:00 | 5.43 | 6.8303 | N | 0
2025-02-22 | 18 | 2031-02-22 18:00 | 5.61 | 7.0567 | N | 0
2025-02-22 | 19 | 2031-02-22 19:00 | 5.62 | 7.0693 | N | 0
2025-02-22 | 20 | 2031-02-22 20:00 | 5.47 | 6.8806 | N | 0
2025-02-22 | 21 | 2031-02-22 21:00 | 5.24 | 6.5913 | N | 0
2025-02-22 | 22 | 2031-02-22 22:00 | 5.1 | 6.4152 | N | 0
2025-02-22 | 23 | 2031-02-22 23:00 | 4.81 | 6.0504 | N | 0
2025-02-23 | 00 | 2031-02-23 | 4.41 | 5.5473 | N | 0
2025-02-23 | 01 | 2031-02-23 01:00 | 4.02 | 5.0567 | N | 0
2025-02-23 | 02 | 2031-02-23 02:00 | 3.75 | 4.7171 | N | 0
2025-02-23 | 03 | 2031-02-23 03:00 | 3.68 | 4.629 | N | 0
2025-02-23 | 04 | 2031-02-23 04:00 | 3.62 | 4.5535 | N | 0
2025-02-23 | 05 | 2031-02-23 05:00 | 3.62 | 4.5535 | N | 0
2025-02-23 | 06 | 2031-02-23 06:00 | 3.73 | 4.6919 | N | 0
2025-02-23 | 07 | 2031-02-23 07:00 | 3.86 | 4.8554 | N | 0
2025-02-23 | 08 | 2031-02-23 08:00 | 4.06 | 5.107 | N | 0
2025-02-23 | 09 | 2031-02-23 09:00 | 4.37 | 5.4969 | N | 0
2025-02-23 | 10 | 2031-02-23 10:00 | 4.52 | 5.6856 | N | 0
2025-02-23 | 11 | 2031-02-23 11:00 | 4.79 | 6.0253 | N | 0
2025-02-23 | 12 | 2031-02-23 12:00 | 4.89 | 6.151 | N | 0
2025-02-23 | 13 | 2031-02-23 13:00 | 5.08 | 6.39 | N | 0
2025-02-23 | 14 | 2031-02-23 14:00 | 5.16 | 6.4907 | N | 0
2025-02-23 | 15 | 2031-02-23 15:00 | 5.25 | 6.6039 | N | 0
2025-02-23 | 16 | 2031-02-23 16:00 | 5.25 | 6.6039 | N | 0
2025-02-23 | 17 | 2031-02-23 17:00 | 5.54 | 6.9687 | N | 0
2025-02-23 | 18 | 2031-02-23 18:00 | 5.64 | 7.0945 | N | 0
2025-02-23 | 19 | 2031-02-23 19:00 | 5.69 | 7.1573 | N | 0
2025-02-23 | 20 | 2031-02-23 20:00 | 5.5 | 6.9183 | N | 0
2025-02-23 | 21 | 2031-02-23 21:00 | 5.3 | 6.6668 | N | 0
2025-02-23 | 22 | 2031-02-23 22:00 | 5.01 | 6.302 | N | 0
2025-02-23 | 23 | 2031-02-23 23:00 | 4.66 | 5.8617 | N | 0
2025-02-24 | 00 | 2031-02-24 | 4.09 | 5.1447 | N | 0
2025-02-24 | 01 | 2031-02-24 01:00 | 3.78 | 4.7548 | N | 0
2025-02-24 | 02 | 2031-02-24 02:00 | 3.51 | 4.4152 | N | 0
2025-02-24 | 03 | 2031-02-24 03:00 | 3.44 | 4.3271 | N | 0
2025-02-24 | 04 | 2031-02-24 04:00 | 3.36 | 4.2265 | N | 0
2025-02-24 | 05 | 2031-02-24 05:00 | 3.36 | 4.2265 | N | 0
2025-02-24 | 06 | 2031-02-24 06:00 | 3.64 | 4.5787 | N | 0
2025-02-24 | 07 | 2031-02-24 07:00 | 3.98 | 5.0064 | N | 0
2025-02-24 | 08 | 2031-02-24 08:00 | 4.45 | 5.5976 | N | 0
2025-02-24 | 09 | 2031-02-24 09:00 | 4.54 | 5.7108 | N | 0
2025-02-24 | 10 | 2031-02-24 10:00 | 4.65 | 5.8491 | N | 0
2025-02-24 | 11 | 2031-02-24 11:00 | 4.61 | 5.7988 | N | 0
2025-02-24 | 12 | 2031-02-24 12:00 | 4.71 | 5.9246 | N | 0
2025-02-24 | 13 | 2031-02-24 13:00 | 4.83 | 6.0756 | N | 0
2025-02-24 | 14 | 2031-02-24 14:00 | 4.76 | 5.9875 | N | 0
2025-02-24 | 15 | 2031-02-24 15:00 | 4.73 | 5.9498 | N | 0
2025-02-24 | 16 | 2031-02-24 16:00 | 4.67 | 5.8743 | N | 0
2025-02-24 | 17 | 2031-02-24 17:00 | 4.96 | 6.2391 | N | 0
2025-02-24 | 18 | 2031-02-24 18:00 | 5.35 | 6.7297 | N | 0
2025-02-24 | 19 | 2031-02-24 19:00 | 5.44 | 6.8429 | N | 0
2025-02-24 | 20 | 2031-02-24 20:00 | 5.25 | 6.6039 | N | 0
2025-02-24 | 21 | 2031-02-24 21:00 | 5.13 | 6.4529 | N | 0
2025-02-24 | 22 | 2031-02-24 22:00 | 4.88 | 6.1385 | N | 0
2025-02-24 | 23 | 2031-02-24 23:00 | 4.44 | 5.585 | N | 0
2025-02-25 | 00 | 2031-02-25 | 3.89 | 4.8932 | N | 0
2025-02-25 | 01 | 2031-02-25 01:00 | 3.52 | 4.4277 | N | 0
2025-02-25 | 02 | 2031-02-25 02:00 | 3.36 | 4.2265 | N | 0
2025-02-25 | 03 | 2031-02-25 03:00 | 3.31 | 4.1636 | N | 0
2025-02-25 | 04 | 2031-02-25 04:00 | 3.29 | 4.1384 | N | 0
2025-02-25 | 05 | 2031-02-25 05:00 | 3.25 | 4.0881 | N | 0
2025-02-25 | 06 | 2031-02-25 06:00 | 3.55 | 4.4655 | N | 0
2025-02-25 | 07 | 2031-02-25 07:00 | 4.01 | 5.0441 | N | 0
2025-02-25 | 08 | 2031-02-25 08:00 | 4.45 | 5.5976 | N | 0
2025-02-25 | 09 | 2031-02-25 09:00 | 4.47 | 5.6227 | N | 0
2025-02-25 | 10 | 2031-02-25 10:00 | 4.45 | 5.5976 | N | 0
2025-02-25 | 11 | 2031-02-25 11:00 | 4.55 | 5.7234 | N | 0
2025-02-25 | 12 | 2031-02-25 12:00 | 4.58 | 5.7611 | N | 0
2025-02-25 | 13 | 2031-02-25 13:00 | 4.37 | 5.4969 | N | 0
2025-02-25 | 14 | 2031-02-25 14:00 | 4.33 | 5.4466 | N | 0
2025-02-25 | 15 | 2031-02-25 15:00 | 4.57 | 5.7485 | N | 0
2025-02-25 | 16 | 2031-02-25 16:00 | 4.61 | 5.7988 | N | 0
2025-02-25 | 17 | 2031-02-25 17:00 | 4.85 | 6.1007 | N | 0
2025-02-25 | 18 | 2031-02-25 18:00 | 5.27 | 6.629 | N | 0
2025-02-25 | 19 | 2031-02-25 19:00 | 5.31 | 6.6794 | N | 0
2025-02-25 | 20 | 2031-02-25 20:00 | 5.1 | 6.4152 | N | 0
2025-02-25 | 21 | 2031-02-25 21:00 | 5.02 | 6.3146 | N | 0
2025-02-25 | 22 | 2031-02-25 22:00 | 4.89 | 6.151 | N | 0
2025-02-25 | 23 | 2031-02-25 23:00 | 4.48 | 5.6353 | N | 0
2025-02-26 | 00 | 2031-02-26 | 3.85 | 4.8428 | N | 0
2025-02-26 | 01 | 2031-02-26 01:00 | 3.47 | 4.3648 | N | 0
2025-02-26 | 02 | 2031-02-26 02:00 | 3.34 | 4.2013 | N | 0
2025-02-26 | 03 | 2031-02-26 03:00 | 3.18 | 4.0001 | N | 0
2025-02-26 | 04 | 2031-02-26 04:00 | 3.21 | 4.0378 | N | 0
2025-02-26 | 05 | 2031-02-26 05:00 | 3.26 | 4.1007 | N | 0
2025-02-26 | 06 | 2031-02-26 06:00 | 3.54 | 4.4529 | N | 0
2025-02-26 | 07 | 2031-02-26 07:00 | 3.87 | 4.868 | N | 0
2025-02-26 | 08 | 2031-02-26 08:00 | 4.31 | 5.4215 | N | 0
2025-02-26 | 09 | 2031-02-26 09:00 | 4.27 | 5.3712 | N | 0
2025-02-26 | 10 | 2031-02-26 10:00 | 4.34 | 5.4592 | N | 0
2025-02-26 | 11 | 2031-02-26 11:00 | 4.27 | 5.3712 | N | 0
2025-02-26 | 12 | 2031-02-26 12:00 | 4.23 | 5.3208 | N | 0
2025-02-26 | 13 | 2031-02-26 13:00 | 4.35 | 5.4718 | N | 0
2025-02-26 | 14 | 2031-02-26 14:00 | 4.33 | 5.4466 | N | 0
2025-02-26 | 15 | 2031-02-26 15:00 | 4.26 | 5.3586 | N | 0
2025-02-26 | 16 | 2031-02-26 16:00 | 4.44 | 5.585 | N | 0
2025-02-26 | 17 | 2031-02-26 17:00 | 4.75 | 5.9749 | N | 0
2025-02-26 | 18 | 2031-02-26 18:00 | 5.05 | 6.3523 | N | 0
2025-02-26 | 19 | 2031-02-26 19:00 | 5.13 | 6.4529 | N | 0
2025-02-26 | 20 | 2031-02-26 20:00 | 5.15 | 6.4781 | N | 0
2025-02-26 | 21 | 2031-02-26 21:00 | 5.06 | 6.3649 | N | 0
2025-02-26 | 22 | 2031-02-26 22:00 | 4.85 | 6.1007 | N | 0
2025-02-26 | 23 | 2031-02-26 23:00 | 4.58 | 5.7611 | N | 0
2025-02-27 | 00 | 2031-02-27 | 3.96 | 4.9812 | N | 0
2025-02-27 | 01 | 2031-02-27 01:00 | 3.6 | 4.5284 | N | 0
2025-02-27 | 02 | 2031-02-27 02:00 | 3.32 | 4.1762 | N | 0
2025-02-27 | 03 | 2031-02-27 03:00 | 3.18 | 4.0001 | N | 0
2025-02-27 | 04 | 2031-02-27 04:00 | 3.22 | 4.0504 | N | 0
2025-02-27 | 05 | 2031-02-27 05:00 | 3.25 | 4.0881 | N | 0
2025-02-27 | 06 | 2031-02-27 06:00 | 3.36 | 4.2265 | N | 0
2025-02-27 | 07 | 2031-02-27 07:00 | 3.87 | 4.868 | N | 0
2025-02-27 | 08 | 2031-02-27 08:00 | 4.26 | 5.3586 | N | 0
2025-02-27 | 09 | 2031-02-27 09:00 | 4.41 | 5.5473 | N | 0
2025-02-27 | 10 | 2031-02-27 10:00 | 4.48 | 5.6353 | N | 0
2025-02-27 | 11 | 2031-02-27 11:00 | 4.51 | 5.673 | N | 0
2025-02-27 | 12 | 2031-02-27 12:00 | 4.41 | 5.5473 | N | 0
2025-02-27 | 13 | 2031-02-27 13:00 | 4.49 | 5.6479 | N | 0
2025-02-27 | 14 | 2031-02-27 14:00 | 4.43 | 5.5724 | N | 0
2025-02-27 | 15 | 2031-02-27 15:00 | 4.56 | 5.7359 | N | 0
2025-02-27 | 16 | 2031-02-27 16:00 | 4.56 | 5.7359 | N | 0
2025-02-27 | 17 | 2031-02-27 17:00 | 4.98 | 6.2642 | N | 0
2025-02-27 | 18 | 2031-02-27 18:00 | 5.17 | 6.5032 | N | 0
2025-02-27 | 19 | 2031-02-27 19:00 | 5.22 | 6.5661 | N | 0
2025-02-27 | 20 | 2031-02-27 20:00 | 5.06 | 6.3649 | N | 0
2025-02-27 | 21 | 2031-02-27 21:00 | 5 | 6.2894 | N | 0
2025-02-27 | 22 | 2031-02-27 22:00 | 4.74 | 5.9624 | N | 0
2025-02-27 | 23 | 2031-02-27 23:00 | 4.44 | 5.585 | N | 0
2025-02-28 | 00 | 2031-02-28 | 3.96 | 4.9812 | N | 0
2025-02-28 | 01 | 2031-02-28 01:00 | 3.58 | 4.5032 | N | 0
2025-02-28 | 02 | 2031-02-28 02:00 | 3.46 | 4.3523 | N | 0
2025-02-28 | 03 | 2031-02-28 03:00 | 3.38 | 4.2516 | N | 0
2025-02-28 | 04 | 2031-02-28 04:00 | 3.4 | 4.2768 | N | 0
2025-02-28 | 05 | 2031-02-28 05:00 | 3.38 | 4.2516 | N | 0
2025-02-28 | 06 | 2031-02-28 06:00 | 3.7 | 4.6542 | N | 0
2025-02-28 | 07 | 2031-02-28 07:00 | 4.11 | 5.1699 | N | 0
2025-02-28 | 08 | 2031-02-28 08:00 | 4.39 | 5.5221 | N | 0
2025-02-28 | 09 | 2031-02-28 09:00 | 4.47 | 5.6227 | N | 0
2025-02-28 | 10 | 2031-02-28 10:00 | 4.64 | 5.8366 | N | 0
2025-02-28 | 11 | 2031-02-28 11:00 | 4.68 | 5.8869 | N | 0
2025-02-28 | 12 | 2031-02-28 12:00 | 4.83 | 6.0756 | N | 0
2025-02-28 | 13 | 2031-02-28 13:00 | 4.86 | 6.1133 | N | 0
2025-02-28 | 14 | 2031-02-28 14:00 | 4.81 | 6.0504 | N | 0
2025-02-28 | 15 | 2031-02-28 15:00 | 4.89 | 6.151 | N | 0
2025-02-28 | 16 | 2031-02-28 16:00 | 5.06 | 6.3649 | N | 0
2025-02-28 | 17 | 2031-02-28 17:00 | 5.22 | 6.5661 | N | 0
2025-02-28 | 18 | 2031-02-28 18:00 | 5.46 | 6.868 | N | 0
2025-02-28 | 19 | 2031-02-28 19:00 | 5.39 | 6.78 | N | 0
2025-02-28 | 20 | 2031-02-28 20:00 | 5.28 | 6.6416 | N | 0
2025-02-28 | 21 | 2031-02-28 21:00 | 5.08 | 6.39 | N | 0
2025-02-28 | 22 | 2031-02-28 22:00 | 4.99 | 6.2768 | N | 0
2025-02-28 | 23 | 2031-02-28 23:00 | 4.63 | 5.824 | N | 0
2025-03-01 | 00 | 2031-03-01 | 4.06 | 5.107 | N | 0
2025-03-01 | 01 | 2031-03-01 01:00 | 3.7 | 4.6542 | N | 0
2025-03-01 | 02 | 2031-03-01 02:00 | 3.43 | 4.3145 | N | 0
2025-03-01 | 03 | 2031-03-01 03:00 | 3.35 | 4.2139 | N | 0
2025-03-01 | 04 | 2031-03-01 04:00 | 3.2 | 4.0252 | N | 0
2025-03-01 | 05 | 2031-03-01 05:00 | 3.25 | 4.0881 | N | 0
2025-03-01 | 06 | 2031-03-01 06:00 | 3.37 | 4.2391 | N | 0
2025-03-01 | 07 | 2031-03-01 07:00 | 3.71 | 4.6667 | N | 0
2025-03-01 | 08 | 2031-03-01 08:00 | 4.03 | 5.0693 | N | 0
2025-03-01 | 09 | 2031-03-01 09:00 | 4.56 | 5.7359 | N | 0
2025-03-01 | 10 | 2031-03-01 10:00 | 4.77 | 6.0001 | N | 0
2025-03-01 | 11 | 2031-03-01 11:00 | 4.94 | 6.2139 | N | 0
2025-03-01 | 12 | 2031-03-01 12:00 | 5.06 | 6.3649 | N | 0
2025-03-01 | 13 | 2031-03-01 13:00 | 5.08 | 6.39 | N | 0
2025-03-01 | 14 | 2031-03-01 14:00 | 4.93 | 6.2014 | N | 0
2025-03-01 | 15 | 2031-03-01 15:00 | 4.98 | 6.2642 | N | 0
2025-03-01 | 16 | 2031-03-01 16:00 | 4.98 | 6.2642 | N | 0
2025-03-01 | 17 | 2031-03-01 17:00 | 5.29 | 6.6542 | N | 0
2025-03-01 | 18 | 2031-03-01 18:00 | 5.54 | 6.9687 | N | 0
2025-03-01 | 19 | 2031-03-01 19:00 | 5.72 | 7.1951 | N | 0
2025-03-01 | 20 | 2031-03-01 20:00 | 5.69 | 7.1573 | N | 0
2025-03-01 | 21 | 2031-03-01 21:00 | 5.63 | 7.0819 | N | 0
2025-03-01 | 22 | 2031-03-01 22:00 | 5.14 | 6.4655 | N | 0
2025-03-01 | 23 | 2031-03-01 23:00 | 4.95 | 6.2265 | N | 0
2025-03-02 | 00 | 2031-03-02 | 4.72 | 5.9372 | N | 0
2025-03-02 | 01 | 2031-03-02 01:00 | 4.48 | 5.6353 | N | 0
2025-03-02 | 02 | 2031-03-02 02:00 | 4.11 | 5.1699 | N | 0
2025-03-02 | 03 | 2031-03-02 03:00 | 4.08 | 5.1322 | N | 0
2025-03-02 | 04 | 2031-03-02 04:00 | 4.07 | 5.1196 | N | 0
2025-03-02 | 05 | 2031-03-02 05:00 | 4.04 | 5.0818 | N | 0
2025-03-02 | 06 | 2031-03-02 06:00 | 4.08 | 5.1322 | N | 0
2025-03-02 | 07 | 2031-03-02 07:00 | 4.25 | 5.346 | N | 0
2025-03-02 | 08 | 2031-03-02 08:00 | 4.46 | 5.6102 | N | 0
2025-03-02 | 09 | 2031-03-02 09:00 | 4.99 | 6.2768 | N | 0
2025-03-02 | 10 | 2031-03-02 10:00 | 5.07 | 6.3775 | N | 0
2025-03-02 | 11 | 2031-03-02 11:00 | 5.41 | 6.8051 | N | 0
2025-03-02 | 12 | 2031-03-02 12:00 | 5.41 | 6.8051 | N | 0
2025-03-02 | 13 | 2031-03-02 13:00 | 5.48 | 6.8932 | N | 0
2025-03-02 | 14 | 2031-03-02 14:00 | 5.47 | 6.8806 | N | 0
2025-03-02 | 15 | 2031-03-02 15:00 | 5.37 | 6.7548 | N | 0
2025-03-02 | 16 | 2031-03-02 16:00 | 5.54 | 6.9687 | N | 0
2025-03-02 | 17 | 2031-03-02 17:00 | 5.69 | 7.1573 | N | 0
2025-03-02 | 18 | 2031-03-02 18:00 | 5.92 | 7.4467 | N | 0
2025-03-02 | 19 | 2031-03-02 19:00 | 6.06 | 7.6228 | N | 0
2025-03-02 | 20 | 2031-03-02 20:00 | 6.04 | 7.5976 | N | 0
2025-03-02 | 21 | 2031-03-02 21:00 | 5.58 | 7.019 | N | 0
2025-03-02 | 22 | 2031-03-02 22:00 | 5.33 | 6.7045 | N | 0
2025-03-02 | 23 | 2031-03-02 23:00 | 5.12 | 6.4404 | N | 0
2025-03-03 | 00 | 2031-03-03 | 4.47 | 5.6227 | N | 0
2025-03-03 | 01 | 2031-03-03 01:00 | 4.23 | 5.3208 | N | 0
2025-03-03 | 02 | 2031-03-03 02:00 | 4.03 | 5.0693 | N | 0
2025-03-03 | 03 | 2031-03-03 03:00 | 3.86 | 4.8554 | N | 0
2025-03-03 | 04 | 2031-03-03 04:00 | 3.87 | 4.868 | N | 0
2025-03-03 | 05 | 2031-03-03 05:00 | 3.98 | 5.0064 | N | 0
2025-03-03 | 06 | 2031-03-03 06:00 | 4.21 | 5.2957 | N | 0
2025-03-03 | 07 | 2031-03-03 07:00 | 4.67 | 5.8743 | N | 0
2025-03-03 | 08 | 2031-03-03 08:00 | 4.89 | 6.151 | N | 0
2025-03-03 | 09 | 2031-03-03 09:00 | 4.99 | 6.2768 | N | 0
2025-03-03 | 10 | 2031-03-03 10:00 | 4.9 | 6.1636 | N | 0
2025-03-03 | 11 | 2031-03-03 11:00 | 4.89 | 6.151 | N | 0
2025-03-03 | 12 | 2031-03-03 12:00 | 4.86 | 6.1133 | N | 0
2025-03-03 | 13 | 2031-03-03 13:00 | 4.8 | 6.0378 | N | 0
2025-03-03 | 14 | 2031-03-03 14:00 | 4.76 | 5.9875 | N | 0
2025-03-03 | 15 | 2031-03-03 15:00 | 4.62 | 5.8114 | N | 0
2025-03-03 | 16 | 2031-03-03 16:00 | 4.82 | 6.063 | N | 0
2025-03-03 | 17 | 2031-03-03 17:00 | 5.17 | 6.5032 | N | 0
2025-03-03 | 18 | 2031-03-03 18:00 | 5.48 | 6.8932 | N | 0
2025-03-03 | 19 | 2031-03-03 19:00 | 5.49 | 6.9058 | N | 0
2025-03-03 | 20 | 2031-03-03 20:00 | 5.41 | 6.8051 | N | 0
2025-03-03 | 21 | 2031-03-03 21:00 | 5.25 | 6.6039 | N | 0
2025-03-03 | 22 | 2031-03-03 22:00 | 5.05 | 6.3523 | N | 0
2025-03-03 | 23 | 2031-03-03 23:00 | 4.69 | 5.8995 | N | 0
2025-03-04 | 00 | 2031-03-04 | 4.08 | 5.1322 | N | 0
2025-03-04 | 01 | 2031-03-04 01:00 | 3.73 | 4.6919 | N | 0
2025-03-04 | 02 | 2031-03-04 02:00 | 3.54 | 4.4529 | N | 0
2025-03-04 | 03 | 2031-03-04 03:00 | 3.44 | 4.3271 | N | 0
2025-03-04 | 04 | 2031-03-04 04:00 | 3.36 | 4.2265 | N | 0
2025-03-04 | 05 | 2031-03-04 05:00 | 3.42 | 4.302 | N | 0
2025-03-04 | 06 | 2031-03-04 06:00 | 3.68 | 4.629 | N | 0
2025-03-04 | 07 | 2031-03-04 07:00 | 4.08 | 5.1322 | N | 0
2025-03-04 | 08 | 2031-03-04 08:00 | 4.45 | 5.5976 | N | 0
2025-03-04 | 09 | 2031-03-04 09:00 | 4.52 | 5.6856 | N | 0
2025-03-04 | 10 | 2031-03-04 10:00 | 4.49 | 5.6479 | N | 0
2025-03-04 | 11 | 2031-03-04 11:00 | 4.49 | 5.6479 | N | 0
2025-03-04 | 12 | 2031-03-04 12:00 | 4.68 | 5.8869 | N | 0
2025-03-04 | 13 | 2031-03-04 13:00 | 4.71 | 5.9246 | N | 0
2025-03-04 | 14 | 2031-03-04 14:00 | 4.74 | 5.9624 | N | 0
2025-03-04 | 15 | 2031-03-04 15:00 | 4.68 | 5.8869 | N | 0
2025-03-04 | 16 | 2031-03-04 16:00 | 4.65 | 5.8491 | N | 0
2025-03-04 | 17 | 2031-03-04 17:00 | 4.98 | 6.2642 | N | 0
2025-03-04 | 18 | 2031-03-04 18:00 | 5.23 | 6.5787 | N | 0
2025-03-04 | 19 | 2031-03-04 19:00 | 5.26 | 6.6165 | N | 0
2025-03-04 | 20 | 2031-03-04 20:00 | 5.05 | 6.3523 | N | 0
2025-03-04 | 21 | 2031-03-04 21:00 | 4.92 | 6.1888 | N | 0
2025-03-04 | 22 | 2031-03-04 22:00 | 4.79 | 6.0253 | N | 0
2025-03-04 | 23 | 2031-03-04 23:00 | 4.43 | 5.5724 | N | 0
2025-03-05 | 00 | 2031-03-05 | 3.82 | 4.8051 | N | 0
2025-03-05 | 01 | 2031-03-05 01:00 | 3.48 | 4.3774 | N | 0
2025-03-05 | 02 | 2031-03-05 02:00 | 3.25 | 4.0881 | N | 0
2025-03-05 | 03 | 2031-03-05 03:00 | 3.2 | 4.0252 | N | 0
2025-03-05 | 04 | 2031-03-05 04:00 | 3.15 | 3.9623 | N | 0
2025-03-05 | 05 | 2031-03-05 05:00 | 3.15 | 3.9623 | N | 0
2025-03-05 | 06 | 2031-03-05 06:00 | 3.33 | 4.1887 | N | 0
2025-03-05 | 07 | 2031-03-05 07:00 | 3.8 | 4.7799 | N | 0
2025-03-05 | 08 | 2031-03-05 08:00 | 4.2 | 5.2831 | N | 0
2025-03-05 | 09 | 2031-03-05 09:00 | 4.36 | 5.4844 | N | 0
2025-03-05 | 10 | 2031-03-05 10:00 | 4.49 | 5.6479 | N | 0
2025-03-05 | 11 | 2031-03-05 11:00 | 4.53 | 5.6982 | N | 0
2025-03-05 | 12 | 2031-03-05 12:00 | 4.65 | 5.8491 | N | 0
2025-03-05 | 13 | 2031-03-05 13:00 | 4.56 | 5.7359 | N | 0
2025-03-05 | 14 | 2031-03-05 14:00 | 4.58 | 5.7611 | N | 0
2025-03-05 | 15 | 2031-03-05 15:00 | 4.51 | 5.673 | N | 0
2025-03-05 | 16 | 2031-03-05 16:00 | 4.53 | 5.6982 | N | 0
2025-03-05 | 17 | 2031-03-05 17:00 | 4.78 | 6.0127 | N | 0
2025-03-05 | 18 | 2031-03-05 18:00 | 5.15 | 6.4781 | N | 0
2025-03-05 | 19 | 2031-03-05 19:00 | 5.02 | 6.3146 | N | 0
2025-03-05 | 20 | 2031-03-05 20:00 | 4.96 | 6.2391 | N | 0
2025-03-05 | 21 | 2031-03-05 21:00 | 4.83 | 6.0756 | N | 0
2025-03-05 | 22 | 2031-03-05 22:00 | 4.68 | 5.8869 | N | 0
2025-03-05 | 23 | 2031-03-05 23:00 | 4.4 | 5.5347 | N | 0
2025-03-06 | 00 | 2031-03-06 | 3.74 | 4.7045 | N | 0
2025-03-06 | 01 | 2031-03-06 01:00 | 3.48 | 4.3774 | N | 0
2025-03-06 | 02 | 2031-03-06 02:00 | 3.25 | 4.0881 | N | 0
2025-03-06 | 03 | 2031-03-06 03:00 | 3.2 | 4.0252 | N | 0
2025-03-06 | 04 | 2031-03-06 04:00 | 3.18 | 4.0001 | N | 0
2025-03-06 | 05 | 2031-03-06 05:00 | 3.1 | 3.8994 | N | 0
2025-03-06 | 06 | 2031-03-06 06:00 | 3.45 | 4.3397 | N | 0
2025-03-06 | 07 | 2031-03-06 07:00 | 3.87 | 4.868 | N | 0
2025-03-06 | 08 | 2031-03-06 08:00 | 4.16 | 5.2328 | N | 0
2025-03-06 | 09 | 2031-03-06 09:00 | 4.29 | 5.3963 | N | 0
2025-03-06 | 10 | 2031-03-06 10:00 | 4.46 | 5.6102 | N | 0
2025-03-06 | 11 | 2031-03-06 11:00 | 4.48 | 5.6353 | N | 0
2025-03-06 | 12 | 2031-03-06 12:00 | 4.61 | 5.7988 | N | 0
2025-03-06 | 13 | 2031-03-06 13:00 | 4.93 | 6.2014 | N | 0
2025-03-06 | 14 | 2031-03-06 14:00 | 4.89 | 6.151 | N | 0
2025-03-06 | 15 | 2031-03-06 15:00 | 4.75 | 5.9749 | N | 0
2025-03-06 | 16 | 2031-03-06 16:00 | 4.92 | 6.1888 | N | 0
2025-03-06 | 17 | 2031-03-06 17:00 | 5.16 | 6.4907 | N | 0
2025-03-06 | 18 | 2031-03-06 18:00 | 5.53 | 6.9561 | N | 0
2025-03-06 | 19 | 2031-03-06 19:00 | 5.49 | 6.9058 | N | 0
2025-03-06 | 20 | 2031-03-06 20:00 | 5.41 | 6.8051 | N | 0
2025-03-06 | 21 | 2031-03-06 21:00 | 5.28 | 6.6416 | N | 0
2025-03-06 | 22 | 2031-03-06 22:00 | 5.11 | 6.4278 | N | 0
2025-03-06 | 23 | 2031-03-06 23:00 | 4.72 | 5.9372 | N | 0
2025-03-07 | 00 | 2031-03-07 | 4.19 | 5.2705 | N | 0
2025-03-07 | 01 | 2031-03-07 01:00 | 3.8 | 4.7799 | N | 0
2025-03-07 | 02 | 2031-03-07 02:00 | 3.55 | 4.4655 | N | 0
2025-03-07 | 03 | 2031-03-07 03:00 | 3.38 | 4.2516 | N | 0
2025-03-07 | 04 | 2031-03-07 04:00 | 3.32 | 4.1762 | N | 0
2025-03-07 | 05 | 2031-03-07 05:00 | 3.43 | 4.3145 | N | 0
2025-03-07 | 06 | 2031-03-07 06:00 | 3.65 | 4.5913 | N | 0
2025-03-07 | 07 | 2031-03-07 07:00 | 4.06 | 5.107 | N | 0
2025-03-07 | 08 | 2031-03-07 08:00 | 4.28 | 5.3837 | N | 0
2025-03-07 | 09 | 2031-03-07 09:00 | 4.45 | 5.5976 | N | 0
2025-03-07 | 10 | 2031-03-07 10:00 | 4.52 | 5.6856 | N | 0
2025-03-07 | 11 | 2031-03-07 11:00 | 4.65 | 5.8491 | N | 0
2025-03-07 | 12 | 2031-03-07 12:00 | 4.7 | 5.912 | N | 0
2025-03-07 | 13 | 2031-03-07 13:00 | 4.69 | 5.8995 | N | 0
2025-03-07 | 14 | 2031-03-07 14:00 | 4.63 | 5.824 | N | 0
2025-03-07 | 15 | 2031-03-07 15:00 | 4.44 | 5.585 | N | 0
2025-03-07 | 16 | 2031-03-07 16:00 | 4.39 | 5.5221 | N | 0
2025-03-07 | 17 | 2031-03-07 17:00 | 4.66 | 5.8617 | N | 0
2025-03-07 | 18 | 2031-03-07 18:00 | 4.87 | 6.1259 | N | 0
2025-03-07 | 19 | 2031-03-07 19:00 | 4.95 | 6.2265 | N | 0
2025-03-07 | 20 | 2031-03-07 20:00 | 5.17 | 6.5032 | N | 0
2025-03-07 | 21 | 2031-03-07 21:00 | 5.04 | 6.3397 | N | 0
2025-03-07 | 22 | 2031-03-07 22:00 | 4.82 | 6.063 | N | 0
2025-03-07 | 23 | 2031-03-07 23:00 | 4.63 | 5.824 | N | 0
2025-03-08 | 00 | 2031-03-08 | 4.13 | 5.1951 | N | 0
2025-03-08 | 01 | 2031-03-08 01:00 | 3.73 | 4.6919 | N | 0
2025-03-08 | 02 | 2031-03-08 02:00 | 3.57 | 4.4906 | N | 0
2025-03-08 | 03 | 2031-03-08 03:00 | 3.45 | 4.3397 | N | 0
2025-03-08 | 04 | 2031-03-08 04:00 | 3.36 | 4.2265 | N | 0
2025-03-08 | 05 | 2031-03-08 05:00 | 3.37 | 4.2391 | N | 0
2025-03-08 | 06 | 2031-03-08 06:00 | 3.55 | 4.4655 | N | 0
2025-03-08 | 07 | 2031-03-08 07:00 | 3.74 | 4.7045 | N | 0
2025-03-08 | 08 | 2031-03-08 08:00 | 3.98 | 5.0064 | N | 0
2025-03-08 | 09 | 2031-03-08 09:00 | 4.2 | 5.2831 | N | 0
2025-03-08 | 10 | 2031-03-08 10:00 | 4.39 | 5.5221 | N | 0
2025-03-08 | 11 | 2031-03-08 11:00 | 4.49 | 5.6479 | N | 0
2025-03-08 | 12 | 2031-03-08 12:00 | 4.73 | 5.9498 | N | 0
2025-03-08 | 13 | 2031-03-08 13:00 | 4.64 | 5.8366 | N | 0
2025-03-08 | 14 | 2031-03-08 14:00 | 4.73 | 5.9498 | N | 0
2025-03-08 | 15 | 2031-03-08 15:00 | 4.55 | 5.7234 | N | 0
2025-03-08 | 16 | 2031-03-08 16:00 | 4.48 | 5.6353 | N | 0
2025-03-08 | 17 | 2031-03-08 17:00 | 4.68 | 5.8869 | N | 0
2025-03-08 | 18 | 2031-03-08 18:00 | 5.08 | 6.39 | N | 0
2025-03-08 | 19 | 2031-03-08 19:00 | 4.99 | 6.2768 | N | 0
2025-03-08 | 20 | 2031-03-08 20:00 | 4.98 | 6.2642 | N | 0
2025-03-08 | 21 | 2031-03-08 21:00 | 4.84 | 6.0881 | N | 0
2025-03-08 | 22 | 2031-03-08 22:00 | 4.66 | 5.8617 | N | 0
2025-03-08 | 23 | 2031-03-08 23:00 | 4.5 | 5.6605 | N | 0
2025-03-09 | 00 | 2031-03-09 | 4.11 | 5.1699 | N | 0
2025-03-09 | 01 | 2031-03-09 01:00 | 3.85 | 4.8428 | N | 0
2025-03-09 | 02 | 2031-03-09 02:00 | 3.58 | 4.5032 | N | 0
2025-03-09 | 03 | 2031-03-09 03:00 | 3.51 | 4.4152 | N | 0
2025-03-09 | 04 | 2031-03-09 04:00 | 3.38 | 4.2516 | N | 0
2025-03-09 | 05 | 2031-03-09 05:00 | 3.31 | 4.1636 | N | 0
2025-03-09 | 06 | 2031-03-09 06:00 | 3.41 | 4.2894 | N | 0
2025-03-09 | 07 | 2031-03-09 07:00 | 3.73 | 4.6919 | N | 0
2025-03-09 | 08 | 2031-03-09 08:00 | 3.95 | 4.9686 | N | 0
2025-03-09 | 09 | 2031-03-09 09:00 | 4.04 | 5.0818 | N | 0
2025-03-09 | 10 | 2031-03-09 10:00 | 4.08 | 5.1322 | N | 0
2025-03-09 | 11 | 2031-03-09 11:00 | 4.27 | 5.3712 | N | 0
2025-03-09 | 12 | 2031-03-09 12:00 | 4.55 | 5.7234 | N | 0
2025-03-09 | 13 | 2031-03-09 13:00 | 4.37 | 5.4969 | N | 0
2025-03-09 | 14 | 2031-03-09 14:00 | 4.31 | 5.4215 | N | 0
2025-03-09 | 15 | 2031-03-09 15:00 | 4.4 | 5.5347 | N | 0
2025-03-09 | 16 | 2031-03-09 16:00 | 4.69 | 5.8995 | N | 0
2025-03-09 | 17 | 2031-03-09 17:00 | 4.79 | 6.0253 | N | 0
2025-03-09 | 18 | 2031-03-09 18:00 | 4.73 | 5.9498 | N | 0
2025-03-09 | 19 | 2031-03-09 19:00 | 4.91 | 6.1762 | N | 0
2025-03-09 | 20 | 2031-03-09 20:00 | 4.86 | 6.1133 | N | 0
2025-03-09 | 21 | 2031-03-09 21:00 | 4.7 | 5.912 | N | 0
2025-03-09 | 22 | 2031-03-09 22:00 | 4.36 | 5.4844 | N | 0
2025-03-09 | 23 | 2031-03-09 23:00 | 4.01 | 5.0441 | N | 0
2025-03-10 | 00 | 2031-03-10 | 3.47 | 4.3648 | N | 0
2025-03-10 | 01 | 2031-03-10 01:00 | 3.2 | 4.0252 | N | 0
2025-03-10 | 02 | 2031-03-10 02:00 | 3.08 | 3.8743 | N | 0
2025-03-10 | 03 | 2031-03-10 03:00 | 3.03 | 3.8114 | N | 0
2025-03-10 | 04 | 2031-03-10 04:00 | 3.08 | 3.8743 | N | 0
2025-03-10 | 05 | 2031-03-10 05:00 | 3.15 | 3.9623 | N | 0
2025-03-10 | 06 | 2031-03-10 06:00 | 3.66 | 4.6038 | N | 0
2025-03-10 | 07 | 2031-03-10 07:00 | 3.84 | 4.8303 | N | 0
2025-03-10 | 08 | 2031-03-10 08:00 | 4.06 | 5.107 | N | 0
2025-03-10 | 09 | 2031-03-10 09:00 | 4.08 | 5.1322 | N | 0
2025-03-10 | 10 | 2031-03-10 10:00 | 4.04 | 5.0818 | N | 0
2025-03-10 | 11 | 2031-03-10 11:00 | 4.02 | 5.0567 | N | 0
2025-03-10 | 12 | 2031-03-10 12:00 | 4.21 | 5.2957 | N | 0
2025-03-10 | 13 | 2031-03-10 13:00 | 4.05 | 5.0944 | N | 0
2025-03-10 | 14 | 2031-03-10 14:00 | 3.84 | 4.8303 | N | 0
2025-03-10 | 15 | 2031-03-10 15:00 | 3.91 | 4.9183 | N | 0
2025-03-10 | 16 | 2031-03-10 16:00 | 4.11 | 5.1699 | N | 0
2025-03-10 | 17 | 2031-03-10 17:00 | 4.49 | 5.6479 | N | 0
2025-03-10 | 18 | 2031-03-10 18:00 | 4.51 | 5.673 | N | 0
2025-03-10 | 19 | 2031-03-10 19:00 | 4.62 | 5.8114 | N | 0
2025-03-10 | 20 | 2031-03-10 20:00 | 4.66 | 5.8617 | N | 0
2025-03-10 | 21 | 2031-03-10 21:00 | 4.52 | 5.6856 | N | 0
2025-03-10 | 22 | 2031-03-10 22:00 | 4.24 | 5.3334 | N | 0
2025-03-10 | 23 | 2031-03-10 23:00 | 3.7 | 4.6542 | N | 0
2025-03-11 | 00 | 2031-03-11 | 3.37 | 4.2391 | N | 0
2025-03-11 | 01 | 2031-03-11 01:00 | 3.07 | 3.8617 | N | 0
2025-03-11 | 02 | 2031-03-11 02:00 | 2.98 | 3.7485 | N | 0
2025-03-11 | 03 | 2031-03-11 03:00 | 2.98 | 3.7485 | N | 0
2025-03-11 | 04 | 2031-03-11 04:00 | 3.07 | 3.8617 | N | 0
2025-03-11 | 05 | 2031-03-11 05:00 | 3.19 | 4.0126 | N | 0
2025-03-11 | 06 | 2031-03-11 06:00 | 3.66 | 4.6038 | N | 0
2025-03-11 | 07 | 2031-03-11 07:00 | 3.88 | 4.8806 | N | 0
2025-03-11 | 08 | 2031-03-11 08:00 | 3.92 | 4.9309 | N | 0
2025-03-11 | 09 | 2031-03-11 09:00 | 4 | 5.0315 | N | 0
2025-03-11 | 10 | 2031-03-11 10:00 | 4 | 5.0315 | N | 0
2025-03-11 | 11 | 2031-03-11 11:00 | 3.96 | 4.9812 | N | 0
2025-03-11 | 12 | 2031-03-11 12:00 | 4.02 | 5.0567 | N | 0
2025-03-11 | 13 | 2031-03-11 13:00 | 3.93 | 4.9435 | N | 0
2025-03-11 | 14 | 2031-03-11 14:00 | 3.93 | 4.9435 | N | 0
2025-03-11 | 15 | 2031-03-11 15:00 | 4.05 | 5.0944 | N | 0
2025-03-11 | 16 | 2031-03-11 16:00 | 4.22 | 5.3083 | N | 0
2025-03-11 | 17 | 2031-03-11 17:00 | 4.47 | 5.6227 | N | 0
2025-03-11 | 18 | 2031-03-11 18:00 | 4.61 | 5.7988 | N | 0
2025-03-11 | 19 | 2031-03-11 19:00 | 4.81 | 6.0504 | N | 0
2025-03-11 | 20 | 2031-03-11 20:00 | 4.73 | 5.9498 | N | 0
2025-03-11 | 21 | 2031-03-11 21:00 | 4.72 | 5.9372 | N | 0
2025-03-11 | 22 | 2031-03-11 22:00 | 4.38 | 5.5095 | N | 0
2025-03-11 | 23 | 2031-03-11 23:00 | 3.7 | 4.6542 | N | 0
2025-03-12 | 00 | 2031-03-12 | 3.44 | 4.3271 | N | 0
2025-03-12 | 01 | 2031-03-12 01:00 | 3.2 | 4.0252 | N | 0
2025-03-12 | 02 | 2031-03-12 02:00 | 3.13 | 3.9372 | N | 0
2025-03-12 | 03 | 2031-03-12 03:00 | 3.21 | 4.0378 | N | 0
2025-03-12 | 04 | 2031-03-12 04:00 | 3.22 | 4.0504 | N | 0
2025-03-12 | 05 | 2031-03-12 05:00 | 3.47 | 4.3648 | N | 0
2025-03-12 | 06 | 2031-03-12 06:00 | 3.92 | 4.9309 | N | 0
2025-03-12 | 07 | 2031-03-12 07:00 | 4.01 | 5.0441 | N | 0
2025-03-12 | 08 | 2031-03-12 08:00 | 4.24 | 5.3334 | N | 0
2025-03-12 | 09 | 2031-03-12 09:00 | 4.34 | 5.4592 | N | 0
2025-03-12 | 10 | 2031-03-12 10:00 | 4.39 | 5.5221 | N | 0
2025-03-12 | 11 | 2031-03-12 11:00 | 4.54 | 5.7108 | N | 0
2025-03-12 | 12 | 2031-03-12 12:00 | 4.64 | 5.8366 | N | 0
2025-03-12 | 13 | 2031-03-12 13:00 | 4.71 | 5.9246 | N | 0
2025-03-12 | 14 | 2031-03-12 14:00 | 4.6 | 5.7863 | N | 0
2025-03-12 | 15 | 2031-03-12 15:00 | 4.59 | 5.7737 | N | 0
2025-03-12 | 16 | 2031-03-12 16:00 | 4.84 | 6.0881 | N | 0
2025-03-12 | 17 | 2031-03-12 17:00 | 4.93 | 6.2014 | N | 0
2025-03-12 | 18 | 2031-03-12 18:00 | 4.92 | 6.1888 | N | 0
2025-03-12 | 19 | 2031-03-12 19:00 | 5.02 | 6.3146 | N | 0
2025-03-12 | 20 | 2031-03-12 20:00 | 5.04 | 6.3397 | N | 0
2025-03-12 | 21 | 2031-03-12 21:00 | 4.85 | 6.1007 | N | 0
2025-03-12 | 22 | 2031-03-12 22:00 | 4.53 | 5.6982 | N | 0
2025-03-12 | 23 | 2031-03-12 23:00 | 4.14 | 5.2076 | N | 0
2025-03-13 | 00 | 2031-03-13 | 3.66 | 4.6038 | N | 0
2025-03-13 | 01 | 2031-03-13 01:00 | 3.46 | 4.3523 | N | 0
2025-03-13 | 02 | 2031-03-13 02:00 | 3.29 | 4.1384 | N | 0
2025-03-13 | 03 | 2031-03-13 03:00 | 3.38 | 4.2516 | N | 0
2025-03-13 | 04 | 2031-03-13 04:00 | 3.38 | 4.2516 | N | 0
2025-03-13 | 05 | 2031-03-13 05:00 | 3.62 | 4.5535 | N | 0
2025-03-13 | 06 | 2031-03-13 06:00 | 4.03 | 5.0693 | N | 0
2025-03-13 | 07 | 2031-03-13 07:00 | 4.14 | 5.2076 | N | 0
2025-03-13 | 08 | 2031-03-13 08:00 | 4.34 | 5.4592 | N | 0
2025-03-13 | 09 | 2031-03-13 09:00 | 4.25 | 5.346 | N | 0
2025-03-13 | 10 | 2031-03-13 10:00 | 4.28 | 5.3837 | N | 0
2025-03-13 | 11 | 2031-03-13 11:00 | 4.3 | 5.4089 | N | 0
2025-03-13 | 12 | 2031-03-13 12:00 | 4.27 | 5.3712 | N | 0
2025-03-13 | 13 | 2031-03-13 13:00 | 4.24 | 5.3334 | N | 0
2025-03-13 | 14 | 2031-03-13 14:00 | 4.19 | 5.2705 | N | 0
2025-03-13 | 15 | 2031-03-13 15:00 | 4.02 | 5.0567 | N | 0
2025-03-13 | 16 | 2031-03-13 16:00 | 4.43 | 5.5724 | N | 0
2025-03-13 | 17 | 2031-03-13 17:00 | 4.69 | 5.8995 | N | 0
2025-03-13 | 18 | 2031-03-13 18:00 | 4.6 | 5.7863 | N | 0
2025-03-13 | 19 | 2031-03-13 19:00 | 4.74 | 5.9624 | N | 0
2025-03-13 | 20 | 2031-03-13 20:00 | 4.75 | 5.9749 | N | 0
2025-03-13 | 21 | 2031-03-13 21:00 | 4.67 | 5.8743 | N | 0
2025-03-13 | 22 | 2031-03-13 22:00 | 4.33 | 5.4466 | N | 0
2025-03-13 | 23 | 2031-03-13 23:00 | 3.87 | 4.868 | N | 0
2025-03-14 | 00 | 2031-03-14 | 3.62 | 4.5535 | N | 0
2025-03-14 | 01 | 2031-03-14 01:00 | 3.29 | 4.1384 | N | 0
2025-03-14 | 02 | 2031-03-14 02:00 | 3.17 | 3.9875 | N | 0
2025-03-14 | 03 | 2031-03-14 03:00 | 3.2 | 4.0252 | N | 0
2025-03-14 | 04 | 2031-03-14 04:00 | 3.19 | 4.0126 | N | 0
2025-03-14 | 05 | 2031-03-14 05:00 | 3.27 | 4.1133 | N | 0
2025-03-14 | 06 | 2031-03-14 06:00 | 3.86 | 4.8554 | N | 0
2025-03-14 | 07 | 2031-03-14 07:00 | 4.03 | 5.0693 | N | 0
2025-03-14 | 08 | 2031-03-14 08:00 | 4.19 | 5.2705 | N | 0
2025-03-14 | 09 | 2031-03-14 09:00 | 4.26 | 5.3586 | N | 0
2025-03-14 | 10 | 2031-03-14 10:00 | 4.03 | 5.0693 | N | 0
2025-03-14 | 11 | 2031-03-14 11:00 | 4.1 | 5.1573 | N | 0
2025-03-14 | 12 | 2031-03-14 12:00 | 4.12 | 5.1825 | N | 0
2025-03-14 | 13 | 2031-03-14 13:00 | 4.05 | 5.0944 | N | 0
2025-03-14 | 14 | 2031-03-14 14:00 | 3.93 | 4.9435 | N | 0
2025-03-14 | 15 | 2031-03-14 15:00 | 3.82 | 4.8051 | N | 0
2025-03-14 | 16 | 2031-03-14 16:00 | 3.97 | 4.9938 | N | 0
2025-03-14 | 17 | 2031-03-14 17:00 | 4.19 | 5.2705 | N | 0
2025-03-14 | 18 | 2031-03-14 18:00 | 4.3 | 5.4089 | N | 0
2025-03-14 | 19 | 2031-03-14 19:00 | 4.27 | 5.3712 | N | 0
2025-03-14 | 20 | 2031-03-14 20:00 | 4.38 | 5.5095 | N | 0
2025-03-14 | 21 | 2031-03-14 21:00 | 4.19 | 5.2705 | N | 0
2025-03-14 | 22 | 2031-03-14 22:00 | 4.04 | 5.0818 | N | 0
2025-03-14 | 23 | 2031-03-14 23:00 | 3.6 | 4.5284 | N | 0
2025-03-15 | 00 | 2031-03-15 | 3.21 | 4.0378 | N | 0
2025-03-15 | 01 | 2031-03-15 01:00 | 3.01 | 3.7862 | N | 0
2025-03-15 | 02 | 2031-03-15 02:00 | 2.83 | 3.5598 | N | 0
2025-03-15 | 03 | 2031-03-15 03:00 | 2.72 | 3.4214 | N | 0
2025-03-15 | 04 | 2031-03-15 04:00 | 2.75 | 3.4592 | N | 0
2025-03-15 | 05 | 2031-03-15 05:00 | 2.8 | 3.5221 | N | 0
2025-03-15 | 06 | 2031-03-15 06:00 | 2.95 | 3.7108 | N | 0
2025-03-15 | 07 | 2031-03-15 07:00 | 3.24 | 4.0755 | N | 0
2025-03-15 | 08 | 2031-03-15 08:00 | 3.44 | 4.3271 | N | 0
2025-03-15 | 09 | 2031-03-15 09:00 | 3.71 | 4.6667 | N | 0
2025-03-15 | 10 | 2031-03-15 10:00 | 4.01 | 5.0441 | N | 0
2025-03-15 | 11 | 2031-03-15 11:00 | 4.1 | 5.1573 | N | 0
2025-03-15 | 12 | 2031-03-15 12:00 | 4.2 | 5.2831 | N | 0
2025-03-15 | 13 | 2031-03-15 13:00 | 4.32 | 5.434 | N | 0
2025-03-15 | 14 | 2031-03-15 14:00 | 4.24 | 5.3334 | N | 0
2025-03-15 | 15 | 2031-03-15 15:00 | 4 | 5.0315 | N | 0
2025-03-15 | 16 | 2031-03-15 16:00 | 4.04 | 5.0818 | N | 0
2025-03-15 | 17 | 2031-03-15 17:00 | 4.23 | 5.3208 | N | 0
2025-03-15 | 18 | 2031-03-15 18:00 | 4.23 | 5.3208 | N | 0
2025-03-15 | 19 | 2031-03-15 19:00 | 4.17 | 5.2454 | N | 0
2025-03-15 | 20 | 2031-03-15 20:00 | 4.15 | 5.2202 | N | 0
2025-03-15 | 21 | 2031-03-15 21:00 | 3.97 | 4.9938 | N | 0
2025-03-15 | 22 | 2031-03-15 22:00 | 3.73 | 4.6919 | N | 0
2025-03-15 | 23 | 2031-03-15 23:00 | 3.49 | 4.39 | N | 0
2025-03-16 | 00 | 2031-03-16 | 3.11 | 3.912 | N | 0
2025-03-16 | 01 | 2031-03-16 01:00 | 2.87 | 3.6101 | N | 0
2025-03-16 | 02 | 2031-03-16 02:00 | 2.72 | 3.4214 | N | 0
2025-03-16 | 03 | 2031-03-16 03:00 | 2.68 | 3.3711 | N | 0
2025-03-16 | 04 | 2031-03-16 04:00 | 2.66 | 3.346 | N | 0
2025-03-16 | 05 | 2031-03-16 05:00 | 2.71 | 3.4089 | N | 0
2025-03-16 | 06 | 2031-03-16 06:00 | 2.75 | 3.4592 | N | 0
2025-03-16 | 07 | 2031-03-16 07:00 | 3.01 | 3.7862 | N | 0
2025-03-16 | 08 | 2031-03-16 08:00 | 3.29 | 4.1384 | N | 0
2025-03-16 | 09 | 2031-03-16 09:00 | 3.52 | 4.4277 | N | 0
2025-03-16 | 10 | 2031-03-16 10:00 | 3.8 | 4.7799 | N | 0
2025-03-16 | 11 | 2031-03-16 11:00 | 4.17 | 5.2454 | N | 0
2025-03-16 | 12 | 2031-03-16 12:00 | 4.12 | 5.1825 | N | 0
2025-03-16 | 13 | 2031-03-16 13:00 | 4.09 | 5.1447 | N | 0
2025-03-16 | 14 | 2031-03-16 14:00 | 4.14 | 5.2076 | N | 0
2025-03-16 | 15 | 2031-03-16 15:00 | 4.38 | 5.5095 | N | 0
2025-03-16 | 16 | 2031-03-16 16:00 | 4.73 | 5.9498 | N | 0
2025-03-16 | 17 | 2031-03-16 17:00 | 4.63 | 5.824 | N | 0
2025-03-16 | 18 | 2031-03-16 18:00 | 4.55 | 5.7234 | N | 0
2025-03-16 | 19 | 2031-03-16 19:00 | 4.33 | 5.4466 | N | 0
2025-03-16 | 20 | 2031-03-16 20:00 | 4.35 | 5.4718 | N | 0
2025-03-16 | 21 | 2031-03-16 21:00 | 4.2 | 5.2831 | N | 0
2025-03-16 | 22 | 2031-03-16 22:00 | 3.78 | 4.7548 | N | 0
2025-03-16 | 23 | 2031-03-16 23:00 | 3.53 | 4.4403 | N | 0
2025-03-17 | 00 | 2031-03-17 | 3.16 | 3.9749 | N | 0
2025-03-17 | 01 | 2031-03-17 01:00 | 2.91 | 3.6604 | N | 0
2025-03-17 | 02 | 2031-03-17 02:00 | 2.81 | 3.5346 | N | 0
2025-03-17 | 03 | 2031-03-17 03:00 | 2.76 | 3.4718 | N | 0
2025-03-17 | 04 | 2031-03-17 04:00 | 2.86 | 3.5975 | N | 0
2025-03-17 | 05 | 2031-03-17 05:00 | 3.13 | 3.9372 | N | 0
2025-03-17 | 06 | 2031-03-17 06:00 | 3.63 | 4.5661 | N | 0
2025-03-17 | 07 | 2031-03-17 07:00 | 4.11 | 5.1699 | N | 0
2025-03-17 | 08 | 2031-03-17 08:00 | 4.26 | 5.3586 | N | 0
2025-03-17 | 09 | 2031-03-17 09:00 | 4.36 | 5.4844 | N | 0
2025-03-17 | 10 | 2031-03-17 10:00 | 4.32 | 5.434 | N | 0
2025-03-17 | 11 | 2031-03-17 11:00 | 4.28 | 5.3837 | N | 0
2025-03-17 | 12 | 2031-03-17 12:00 | 4.31 | 5.4215 | N | 0
2025-03-17 | 13 | 2031-03-17 13:00 | 4.28 | 5.3837 | N | 0
2025-03-17 | 14 | 2031-03-17 14:00 | 4.19 | 5.2705 | N | 0
2025-03-17 | 15 | 2031-03-17 15:00 | 4.16 | 5.2328 | N | 0
2025-03-17 | 16 | 2031-03-17 16:00 | 4.39 | 5.5221 | N | 0
2025-03-17 | 17 | 2031-03-17 17:00 | 4.67 | 5.8743 | N | 0
2025-03-17 | 18 | 2031-03-17 18:00 | 4.56 | 5.7359 | N | 0
2025-03-17 | 19 | 2031-03-17 19:00 | 4.66 | 5.8617 | N | 0
2025-03-17 | 20 | 2031-03-17 20:00 | 4.79 | 6.0253 | N | 0
2025-03-17 | 21 | 2031-03-17 21:00 | 4.69 | 5.8995 | N | 0
2025-03-17 | 22 | 2031-03-17 22:00 | 4.35 | 5.4718 | N | 0
2025-03-17 | 23 | 2031-03-17 23:00 | 3.81 | 4.7925 | N | 0
2025-03-18 | 00 | 2031-03-18 | 3.47 | 4.3648 | N | 0
2025-03-18 | 01 | 2031-03-18 01:00 | 3.22 | 4.0504 | N | 0
2025-03-18 | 02 | 2031-03-18 02:00 | 3.16 | 3.9749 | N | 0
2025-03-18 | 03 | 2031-03-18 03:00 | 3.14 | 3.9497 | N | 0
2025-03-18 | 04 | 2031-03-18 04:00 | 3.05 | 3.8365 | N | 0
2025-03-18 | 05 | 2031-03-18 05:00 | 3.29 | 4.1384 | N | 0
2025-03-18 | 06 | 2031-03-18 06:00 | 3.85 | 4.8428 | N | 0
2025-03-18 | 07 | 2031-03-18 07:00 | 4.17 | 5.2454 | N | 0
2025-03-18 | 08 | 2031-03-18 08:00 | 4.18 | 5.2579 | N | 0
2025-03-18 | 09 | 2031-03-18 09:00 | 4.21 | 5.2957 | N | 0
2025-03-18 | 10 | 2031-03-18 10:00 | 4.06 | 5.107 | N | 0
2025-03-18 | 11 | 2031-03-18 11:00 | 4.14 | 5.2076 | N | 0
2025-03-18 | 12 | 2031-03-18 12:00 | 4.11 | 5.1699 | N | 0
2025-03-18 | 13 | 2031-03-18 13:00 | 4.07 | 5.1196 | N | 0
2025-03-18 | 14 | 2031-03-18 14:00 | 3.91 | 4.9183 | N | 0
2025-03-18 | 15 | 2031-03-18 15:00 | 4.1 | 5.1573 | N | 0
2025-03-18 | 16 | 2031-03-18 16:00 | 4.12 | 5.1825 | N | 0
2025-03-18 | 17 | 2031-03-18 17:00 | 4.45 | 5.5976 | N | 0
2025-03-18 | 18 | 2031-03-18 18:00 | 4.48 | 5.6353 | N | 0
2025-03-18 | 19 | 2031-03-18 19:00 | 4.44 | 5.585 | N | 0
2025-03-18 | 20 | 2031-03-18 20:00 | 4.47 | 5.6227 | N | 0
2025-03-18 | 21 | 2031-03-18 21:00 | 4.4 | 5.5347 | N | 0
2025-03-18 | 22 | 2031-03-18 22:00 | 4.13 | 5.1951 | N | 0
2025-03-18 | 23 | 2031-03-18 23:00 | 3.51 | 4.4152 | N | 0
2025-03-19 | 00 | 2031-03-19 | 3.25 | 4.0881 | N | 0
2025-03-19 | 01 | 2031-03-19 01:00 | 2.99 | 3.7611 | N | 0
2025-03-19 | 02 | 2031-03-19 02:00 | 2.88 | 3.6227 | N | 0
2025-03-19 | 03 | 2031-03-19 03:00 | 2.83 | 3.5598 | N | 0
2025-03-19 | 04 | 2031-03-19 04:00 | 2.85 | 3.585 | N | 0
2025-03-19 | 05 | 2031-03-19 05:00 | 3.04 | 3.824 | N | 0
2025-03-19 | 06 | 2031-03-19 06:00 | 3.54 | 4.4529 | N | 0
2025-03-19 | 07 | 2031-03-19 07:00 | 3.98 | 5.0064 | N | 0
2025-03-19 | 08 | 2031-03-19 08:00 | 4.01 | 5.0441 | N | 0
2025-03-19 | 09 | 2031-03-19 09:00 | 4.04 | 5.0818 | N | 0
2025-03-19 | 10 | 2031-03-19 10:00 | 3.99 | 5.0189 | N | 0
2025-03-19 | 11 | 2031-03-19 11:00 | 3.88 | 4.8806 | N | 0
2025-03-19 | 12 | 2031-03-19 12:00 | 3.87 | 4.868 | N | 0
2025-03-19 | 13 | 2031-03-19 13:00 | 3.74 | 4.7045 | N | 0
2025-03-19 | 14 | 2031-03-19 14:00 | 3.68 | 4.629 | N | 0
2025-03-19 | 15 | 2031-03-19 15:00 | 3.67 | 4.6164 | N | 0
2025-03-19 | 16 | 2031-03-19 16:00 | 4.05 | 5.0944 | N | 0
2025-03-19 | 17 | 2031-03-19 17:00 | 4.21 | 5.2957 | N | 0
2025-03-19 | 18 | 2031-03-19 18:00 | 4.19 | 5.2705 | N | 0
2025-03-19 | 19 | 2031-03-19 19:00 | 4.15 | 5.2202 | N | 0
2025-03-19 | 20 | 2031-03-19 20:00 | 4.22 | 5.3083 | N | 0
2025-03-19 | 21 | 2031-03-19 21:00 | 4.11 | 5.1699 | N | 0
2025-03-19 | 22 | 2031-03-19 22:00 | 3.77 | 4.7422 | N | 0
2025-03-19 | 23 | 2031-03-19 23:00 | 3.15 | 3.9623 | N | 0
2025-03-20 | 00 | 2031-03-20 | 2.9 | 3.6479 | N | 0
2025-03-20 | 01 | 2031-03-20 01:00 | 2.64 | 3.3208 | N | 0
2025-03-20 | 02 | 2031-03-20 02:00 | 2.57 | 3.2328 | N | 0
2025-03-20 | 03 | 2031-03-20 03:00 | 2.53 | 3.1824 | N | 0
2025-03-20 | 04 | 2031-03-20 04:00 | 2.52 | 3.1699 | N | 0
2025-03-20 | 05 | 2031-03-20 05:00 | 2.78 | 3.4969 | N | 0
2025-03-20 | 06 | 2031-03-20 06:00 | 3.17 | 3.9875 | N | 0
2025-03-20 | 07 | 2031-03-20 07:00 | 3.66 | 4.6038 | N | 0
2025-03-20 | 08 | 2031-03-20 08:00 | 3.82 | 4.8051 | N | 0
2025-03-20 | 09 | 2031-03-20 09:00 | 3.87 | 4.868 | N | 0
2025-03-20 | 10 | 2031-03-20 10:00 | 3.8 | 4.7799 | N | 0
2025-03-20 | 11 | 2031-03-20 11:00 | 3.95 | 4.9686 | N | 0
2025-03-20 | 12 | 2031-03-20 12:00 | 4.07 | 5.1196 | N | 0
2025-03-20 | 13 | 2031-03-20 13:00 | 4.18 | 5.2579 | N | 0
2025-03-20 | 14 | 2031-03-20 14:00 | 4.14 | 5.2076 | N | 0
2025-03-20 | 15 | 2031-03-20 15:00 | 4.16 | 5.2328 | N | 0
2025-03-20 | 16 | 2031-03-20 16:00 | 4.67 | 5.8743 | N | 0
2025-03-20 | 17 | 2031-03-20 17:00 | 4.74 | 5.9624 | N | 0
2025-03-20 | 18 | 2031-03-20 18:00 | 4.56 | 5.7359 | N | 0
2025-03-20 | 19 | 2031-03-20 19:00 | 4.76 | 5.9875 | N | 0
2025-03-20 | 20 | 2031-03-20 20:00 | 4.87 | 6.1259 | N | 0
2025-03-20 | 21 | 2031-03-20 21:00 | 4.74 | 5.9624 | N | 0
2025-03-20 | 22 | 2031-03-20 22:00 | 4.33 | 5.4466 | N | 0
2025-03-20 | 23 | 2031-03-20 23:00 | 3.87 | 4.868 | N | 0
2025-03-21 | 00 | 2031-03-21 | 3.44 | 4.3271 | N | 0
2025-03-21 | 01 | 2031-03-21 01:00 | 3.22 | 4.0504 | N | 0
2025-03-21 | 02 | 2031-03-21 02:00 | 3.1 | 3.8994 | N | 0
2025-03-21 | 03 | 2031-03-21 03:00 | 3.08 | 3.8743 | N | 0
2025-03-21 | 04 | 2031-03-21 04:00 | 3.14 | 3.9497 | N | 0
2025-03-21 | 05 | 2031-03-21 05:00 | 3.27 | 4.1133 | N | 0
2025-03-21 | 06 | 2031-03-21 06:00 | 3.86 | 4.8554 | N | 0
2025-03-21 | 07 | 2031-03-21 07:00 | 4.27 | 5.3712 | N | 0
2025-03-21 | 08 | 2031-03-21 08:00 | 4.33 | 5.4466 | N | 0
2025-03-21 | 09 | 2031-03-21 09:00 | 4.18 | 5.2579 | N | 0
2025-03-21 | 10 | 2031-03-21 10:00 | 4.21 | 5.2957 | N | 0
2025-03-21 | 11 | 2031-03-21 11:00 | 4.23 | 5.3208 | N | 0
2025-03-21 | 12 | 2031-03-21 12:00 | 4.32 | 5.434 | N | 0
2025-03-21 | 13 | 2031-03-21 13:00 | 4.29 | 5.3963 | N | 0
2025-03-21 | 14 | 2031-03-21 14:00 | 4.17 | 5.2454 | N | 0
2025-03-21 | 15 | 2031-03-21 15:00 | 4.2 | 5.2831 | N | 0
2025-03-21 | 16 | 2031-03-21 16:00 | 4.29 | 5.3963 | N | 0
2025-03-21 | 17 | 2031-03-21 17:00 | 4.48 | 5.6353 | N | 0
2025-03-21 | 18 | 2031-03-21 18:00 | 4.48 | 5.6353 | N | 0
2025-03-21 | 19 | 2031-03-21 19:00 | 4.49 | 5.6479 | N | 0
2025-03-21 | 20 | 2031-03-21 20:00 | 4.68 | 5.8869 | N | 0
2025-03-21 | 21 | 2031-03-21 21:00 | 4.57 | 5.7485 | N | 0
2025-03-21 | 22 | 2031-03-21 22:00 | 4.24 | 5.3334 | N | 0
2025-03-21 | 23 | 2031-03-21 23:00 | 3.77 | 4.7422 | N | 0
2025-03-22 | 00 | 2031-03-22 | 3.52 | 4.4277 | N | 0
2025-03-22 | 01 | 2031-03-22 01:00 | 3.24 | 4.0755 | N | 0
2025-03-22 | 02 | 2031-03-22 02:00 | 3.08 | 3.8743 | N | 0
2025-03-22 | 03 | 2031-03-22 03:00 | 2.98 | 3.7485 | N | 0
2025-03-22 | 04 | 2031-03-22 04:00 | 3.03 | 3.8114 | N | 0
2025-03-22 | 05 | 2031-03-22 05:00 | 3.07 | 3.8617 | N | 0
2025-03-22 | 06 | 2031-03-22 06:00 | 3.2 | 4.0252 | N | 0
2025-03-22 | 07 | 2031-03-22 07:00 | 3.4 | 4.2768 | N | 0
2025-03-22 | 08 | 2031-03-22 08:00 | 3.89 | 4.8932 | N | 0
2025-03-22 | 09 | 2031-03-22 09:00 | 4.14 | 5.2076 | N | 0
2025-03-22 | 10 | 2031-03-22 10:00 | 4.47 | 5.6227 | N | 0
2025-03-22 | 11 | 2031-03-22 11:00 | 4.7 | 5.912 | N | 0
2025-03-22 | 12 | 2031-03-22 12:00 | 4.75 | 5.9749 | N | 0
2025-03-22 | 13 | 2031-03-22 13:00 | 4.64 | 5.8366 | N | 0
2025-03-22 | 14 | 2031-03-22 14:00 | 4.45 | 5.5976 | N | 0
2025-03-22 | 15 | 2031-03-22 15:00 | 4.4 | 5.5347 | N | 0
2025-03-22 | 16 | 2031-03-22 16:00 | 4.64 | 5.8366 | N | 0
2025-03-22 | 17 | 2031-03-22 17:00 | 4.92 | 6.1888 | N | 0
2025-03-22 | 18 | 2031-03-22 18:00 | 4.95 | 6.2265 | N | 0
2025-03-22 | 19 | 2031-03-22 19:00 | 4.88 | 6.1385 | N | 0
2025-03-22 | 20 | 2031-03-22 20:00 | 4.87 | 6.1259 | N | 0
2025-03-22 | 21 | 2031-03-22 21:00 | 4.74 | 5.9624 | N | 0
2025-03-22 | 22 | 2031-03-22 22:00 | 4.47 | 5.6227 | N | 0
2025-03-22 | 23 | 2031-03-22 23:00 | 4.25 | 5.346 | N | 0
2025-03-23 | 00 | 2031-03-23 | 3.77 | 4.7422 | N | 0
2025-03-23 | 01 | 2031-03-23 01:00 | 3.57 | 4.4906 | N | 0
2025-03-23 | 02 | 2031-03-23 02:00 | 3.38 | 4.2516 | N | 0
2025-03-23 | 03 | 2031-03-23 03:00 | 3.37 | 4.2391 | N | 0
2025-03-23 | 04 | 2031-03-23 04:00 | 3.37 | 4.2391 | N | 0
2025-03-23 | 05 | 2031-03-23 05:00 | 3.45 | 4.3397 | N | 0
2025-03-23 | 06 | 2031-03-23 06:00 | 3.67 | 4.6164 | N | 0
2025-03-23 | 07 | 2031-03-23 07:00 | 3.94 | 4.9561 | N | 0
2025-03-23 | 08 | 2031-03-23 08:00 | 4.23 | 5.3208 | N | 0
2025-03-23 | 09 | 2031-03-23 09:00 | 4.28 | 5.3837 | N | 0
2025-03-23 | 10 | 2031-03-23 10:00 | 4.44 | 5.585 | N | 0
2025-03-23 | 11 | 2031-03-23 11:00 | 4.59 | 5.7737 | N | 0
2025-03-23 | 12 | 2031-03-23 12:00 | 4.59 | 5.7737 | N | 0
2025-03-23 | 13 | 2031-03-23 13:00 | 4.74 | 5.9624 | N | 0
2025-03-23 | 14 | 2031-03-23 14:00 | 4.71 | 5.9246 | N | 0
2025-03-23 | 15 | 2031-03-23 15:00 | 4.63 | 5.824 | N | 0
2025-03-23 | 16 | 2031-03-23 16:00 | 4.92 | 6.1888 | N | 0
2025-03-23 | 17 | 2031-03-23 17:00 | 5.15 | 6.4781 | N | 0
2025-03-23 | 18 | 2031-03-23 18:00 | 5.04 | 6.3397 | N | 0
2025-03-23 | 19 | 2031-03-23 19:00 | 5.21 | 6.5536 | N | 0
2025-03-23 | 20 | 2031-03-23 20:00 | 5.03 | 6.3271 | N | 0
2025-03-23 | 21 | 2031-03-23 21:00 | 4.85 | 6.1007 | N | 0
2025-03-23 | 22 | 2031-03-23 22:00 | 4.39 | 5.5221 | N | 0
2025-03-23 | 23 | 2031-03-23 23:00 | 4.14 | 5.2076 | N | 0
2025-03-24 | 00 | 2031-03-24 | 3.63 | 4.5661 | N | 0
2025-03-24 | 01 | 2031-03-24 01:00 | 3.39 | 4.2642 | N | 0
2025-03-24 | 02 | 2031-03-24 02:00 | 3.27 | 4.1133 | N | 0
2025-03-24 | 03 | 2031-03-24 03:00 | 3.24 | 4.0755 | N | 0
2025-03-24 | 04 | 2031-03-24 04:00 | 3.24 | 4.0755 | N | 0
2025-03-24 | 05 | 2031-03-24 05:00 | 3.47 | 4.3648 | N | 0
2025-03-24 | 06 | 2031-03-24 06:00 | 3.81 | 4.7925 | N | 0
2025-03-24 | 07 | 2031-03-24 07:00 | 4.18 | 5.2579 | N | 0
2025-03-24 | 08 | 2031-03-24 08:00 | 4.34 | 5.4592 | N | 0
2025-03-24 | 09 | 2031-03-24 09:00 | 4.32 | 5.434 | N | 0
2025-03-24 | 10 | 2031-03-24 10:00 | 4.41 | 5.5473 | N | 0
2025-03-24 | 11 | 2031-03-24 11:00 | 4.58 | 5.7611 | N | 0
2025-03-24 | 12 | 2031-03-24 12:00 | 4.56 | 5.7359 | N | 0
2025-03-24 | 13 | 2031-03-24 13:00 | 4.63 | 5.824 | N | 0
2025-03-24 | 14 | 2031-03-24 14:00 | 4.45 | 5.5976 | N | 0
2025-03-24 | 15 | 2031-03-24 15:00 | 4.69 | 5.8995 | N | 0
2025-03-24 | 16 | 2031-03-24 16:00 | 5.04 | 6.3397 | N | 0
2025-03-24 | 17 | 2031-03-24 17:00 | 5.17 | 6.5032 | N | 0
2025-03-24 | 18 | 2031-03-24 18:00 | 5.11 | 6.4278 | N | 0
2025-03-24 | 19 | 2031-03-24 19:00 | 4.98 | 6.2642 | N | 0
2025-03-24 | 20 | 2031-03-24 20:00 | 4.94 | 6.2139 | N | 0
2025-03-24 | 21 | 2031-03-24 21:00 | 4.67 | 5.8743 | N | 0
2025-03-24 | 22 | 2031-03-24 22:00 | 4.46 | 5.6102 | N | 0
2025-03-24 | 23 | 2031-03-24 23:00 | 3.81 | 4.7925 | N | 0
2025-03-25 | 00 | 2031-03-25 | 3.42 | 4.302 | N | 0
2025-03-25 | 01 | 2031-03-25 01:00 | 3.16 | 3.9749 | N | 0
2025-03-25 | 02 | 2031-03-25 02:00 | 3.08 | 3.8743 | N | 0
2025-03-25 | 03 | 2031-03-25 03:00 | 3.02 | 3.7988 | N | 0
2025-03-25 | 04 | 2031-03-25 04:00 | 3.03 | 3.8114 | N | 0
2025-03-25 | 05 | 2031-03-25 05:00 | 3.26 | 4.1007 | N | 0
2025-03-25 | 06 | 2031-03-25 06:00 | 3.81 | 4.7925 | N | 0
2025-03-25 | 07 | 2031-03-25 07:00 | 4.15 | 5.2202 | N | 0
2025-03-25 | 08 | 2031-03-25 08:00 | 4.35 | 5.4718 | N | 0
2025-03-25 | 09 | 2031-03-25 09:00 | 4.35 | 5.4718 | N | 0
2025-03-25 | 10 | 2031-03-25 10:00 | 4.38 | 5.5095 | N | 0
2025-03-25 | 11 | 2031-03-25 11:00 | 4.43 | 5.5724 | N | 0
2025-03-25 | 12 | 2031-03-25 12:00 | 4.4 | 5.5347 | N | 0
2025-03-25 | 13 | 2031-03-25 13:00 | 4.38 | 5.5095 | N | 0
2025-03-25 | 14 | 2031-03-25 14:00 | 4.44 | 5.585 | N | 0
2025-03-25 | 15 | 2031-03-25 15:00 | 4.51 | 5.673 | N | 0
2025-03-25 | 16 | 2031-03-25 16:00 | 4.8 | 6.0378 | N | 0
2025-03-25 | 17 | 2031-03-25 17:00 | 5.07 | 6.3775 | N | 0
2025-03-25 | 18 | 2031-03-25 18:00 | 4.97 | 6.2517 | N | 0
2025-03-25 | 19 | 2031-03-25 19:00 | 4.9 | 6.1636 | N | 0
2025-03-25 | 20 | 2031-03-25 20:00 | 4.96 | 6.2391 | N | 0
2025-03-25 | 21 | 2031-03-25 21:00 | 4.68 | 5.8869 | N | 0
2025-03-25 | 22 | 2031-03-25 22:00 | 4.31 | 5.4215 | N | 0
2025-03-25 | 23 | 2031-03-25 23:00 | 3.76 | 4.7296 | N | 0
2025-03-26 | 00 | 2031-03-26 | 3.51 | 4.4152 | N | 0
2025-03-26 | 01 | 2031-03-26 01:00 | 3.2 | 4.0252 | N | 0
2025-03-26 | 02 | 2031-03-26 02:00 | 3.16 | 3.9749 | N | 0
2025-03-26 | 03 | 2031-03-26 03:00 | 3.05 | 3.8365 | N | 0
2025-03-26 | 04 | 2031-03-26 04:00 | 3.16 | 3.9749 | N | 0
2025-03-26 | 05 | 2031-03-26 05:00 | 3.41 | 4.2894 | N | 0
2025-03-26 | 06 | 2031-03-26 06:00 | 3.91 | 4.9183 | N | 0
2025-03-26 | 07 | 2031-03-26 07:00 | 4.11 | 5.1699 | N | 0
2025-03-26 | 08 | 2031-03-26 08:00 | 4.47 | 5.6227 | N | 0
2025-03-26 | 09 | 2031-03-26 09:00 | 4.36 | 5.4844 | N | 0
2025-03-26 | 10 | 2031-03-26 10:00 | 4.23 | 5.3208 | N | 0
2025-03-26 | 11 | 2031-03-26 11:00 | 4.4 | 5.5347 | N | 0
2025-03-26 | 12 | 2031-03-26 12:00 | 4.42 | 5.5598 | N | 0
2025-03-26 | 13 | 2031-03-26 13:00 | 4.3 | 5.4089 | N | 0
2025-03-26 | 14 | 2031-03-26 14:00 | 4.26 | 5.3586 | N | 0
2025-03-26 | 15 | 2031-03-26 15:00 | 4.32 | 5.434 | N | 0
2025-03-26 | 16 | 2031-03-26 16:00 | 4.5 | 5.6605 | N | 0
2025-03-26 | 17 | 2031-03-26 17:00 | 4.81 | 6.0504 | N | 0
2025-03-26 | 18 | 2031-03-26 18:00 | 4.83 | 6.0756 | N | 0
2025-03-26 | 19 | 2031-03-26 19:00 | 4.8 | 6.0378 | N | 0
2025-03-26 | 20 | 2031-03-26 20:00 | 4.93 | 6.2014 | N | 0
2025-03-26 | 21 | 2031-03-26 21:00 | 4.85 | 6.1007 | N | 0
2025-03-26 | 22 | 2031-03-26 22:00 | 4.46 | 5.6102 | N | 0
2025-03-26 | 23 | 2031-03-26 23:00 | 3.86 | 4.8554 | N | 0
2025-03-27 | 00 | 2031-03-27 | 3.56 | 4.4781 | N | 0
2025-03-27 | 01 | 2031-03-27 01:00 | 3.37 | 4.2391 | N | 0
2025-03-27 | 02 | 2031-03-27 02:00 | 3.26 | 4.1007 | N | 0
2025-03-27 | 03 | 2031-03-27 03:00 | 3.22 | 4.0504 | N | 0
2025-03-27 | 04 | 2031-03-27 04:00 | 3.27 | 4.1133 | N | 0
2025-03-27 | 05 | 2031-03-27 05:00 | 3.53 | 4.4403 | N | 0
2025-03-27 | 06 | 2031-03-27 06:00 | 4.12 | 5.1825 | N | 0
2025-03-27 | 07 | 2031-03-27 07:00 | 4.35 | 5.4718 | N | 0
2025-03-27 | 08 | 2031-03-27 08:00 | 4.38 | 5.5095 | N | 0
2025-03-27 | 09 | 2031-03-27 09:00 | 4.25 | 5.346 | N | 0
2025-03-27 | 10 | 2031-03-27 10:00 | 4.28 | 5.3837 | N | 0
2025-03-27 | 11 | 2031-03-27 11:00 | 4.3 | 5.4089 | N | 0
2025-03-27 | 12 | 2031-03-27 12:00 | 4.3 | 5.4089 | N | 0
2025-03-27 | 13 | 2031-03-27 13:00 | 4.14 | 5.2076 | N | 0
2025-03-27 | 14 | 2031-03-27 14:00 | 4.07 | 5.1196 | N | 0
2025-03-27 | 15 | 2031-03-27 15:00 | 4.19 | 5.2705 | N | 0
2025-03-27 | 16 | 2031-03-27 16:00 | 4.54 | 5.7108 | N | 0
2025-03-27 | 17 | 2031-03-27 17:00 | 4.61 | 5.7988 | N | 0
2025-03-27 | 18 | 2031-03-27 18:00 | 4.6 | 5.7863 | N | 0
2025-03-27 | 19 | 2031-03-27 19:00 | 4.74 | 5.9624 | N | 0
2025-03-27 | 20 | 2031-03-27 20:00 | 4.74 | 5.9624 | N | 0
2025-03-27 | 21 | 2031-03-27 21:00 | 4.58 | 5.7611 | N | 0
2025-03-27 | 22 | 2031-03-27 22:00 | 4.22 | 5.3083 | N | 0
2025-03-27 | 23 | 2031-03-27 23:00 | 3.71 | 4.6667 | N | 0
2025-03-28 | 00 | 2031-03-28 | 3.28 | 4.1259 | N | 0
2025-03-28 | 01 | 2031-03-28 01:00 | 3.05 | 3.8365 | N | 0
2025-03-28 | 02 | 2031-03-28 02:00 | 2.97 | 3.7359 | N | 0
2025-03-28 | 03 | 2031-03-28 03:00 | 2.99 | 3.7611 | N | 0
2025-03-28 | 04 | 2031-03-28 04:00 | 2.98 | 3.7485 | N | 0
2025-03-28 | 05 | 2031-03-28 05:00 | 3.25 | 4.0881 | N | 0
2025-03-28 | 06 | 2031-03-28 06:00 | 3.71 | 4.6667 | N | 0
2025-03-28 | 07 | 2031-03-28 07:00 | 4.15 | 5.2202 | N | 0
2025-03-28 | 08 | 2031-03-28 08:00 | 4.28 | 5.3837 | N | 0
2025-03-28 | 09 | 2031-03-28 09:00 | 4.44 | 5.585 | N | 0
2025-03-28 | 10 | 2031-03-28 10:00 | 4.56 | 5.7359 | N | 0
2025-03-28 | 11 | 2031-03-28 11:00 | 4.6 | 5.7863 | N | 0
2025-03-28 | 12 | 2031-03-28 12:00 | 4.66 | 5.8617 | N | 0
2025-03-28 | 13 | 2031-03-28 13:00 | 4.61 | 5.7988 | N | 0
2025-03-28 | 14 | 2031-03-28 14:00 | 4.51 | 5.673 | N | 0
2025-03-28 | 15 | 2031-03-28 15:00 | 4.55 | 5.7234 | N | 0
2025-03-28 | 16 | 2031-03-28 16:00 | 4.8 | 6.0378 | N | 0
2025-03-28 | 17 | 2031-03-28 17:00 | 4.97 | 6.2517 | N | 0
2025-03-28 | 18 | 2031-03-28 18:00 | 4.97 | 6.2517 | N | 0
2025-03-28 | 19 | 2031-03-28 19:00 | 4.96 | 6.2391 | N | 0
2025-03-28 | 20 | 2031-03-28 20:00 | 4.81 | 6.0504 | N | 0
2025-03-28 | 21 | 2031-03-28 21:00 | 4.65 | 5.8491 | N | 0
2025-03-28 | 22 | 2031-03-28 22:00 | 4.36 | 5.4844 | N | 0
2025-03-28 | 23 | 2031-03-28 23:00 | 4.05 | 5.0944 | N | 0
2025-03-29 | 00 | 2031-03-29 | 3.67 | 4.6164 | N | 0
2025-03-29 | 01 | 2031-03-29 01:00 | 3.33 | 4.1887 | N | 0
2025-03-29 | 02 | 2031-03-29 02:00 | 3.16 | 3.9749 | N | 0
2025-03-29 | 03 | 2031-03-29 03:00 | 3.1 | 3.8994 | N | 0
2025-03-29 | 04 | 2031-03-29 04:00 | 3.07 | 3.8617 | N | 0
2025-03-29 | 05 | 2031-03-29 05:00 | 3.16 | 3.9749 | N | 0
2025-03-29 | 06 | 2031-03-29 06:00 | 3.29 | 4.1384 | N | 0
2025-03-29 | 07 | 2031-03-29 07:00 | 3.57 | 4.4906 | N | 0
2025-03-29 | 08 | 2031-03-29 08:00 | 4.02 | 5.0567 | N | 0
2025-03-29 | 09 | 2031-03-29 09:00 | 4.32 | 5.434 | N | 0
2025-03-29 | 10 | 2031-03-29 10:00 | 4.56 | 5.7359 | N | 0
2025-03-29 | 11 | 2031-03-29 11:00 | 4.89 | 6.151 | N | 0
2025-03-29 | 12 | 2031-03-29 12:00 | 4.95 | 6.2265 | N | 0
2025-03-29 | 13 | 2031-03-29 13:00 | 4.88 | 6.1385 | N | 0
2025-03-29 | 14 | 2031-03-29 14:00 | 4.88 | 6.1385 | N | 0
2025-03-29 | 15 | 2031-03-29 15:00 | 4.93 | 6.2014 | N | 0
2025-03-29 | 16 | 2031-03-29 16:00 | 5.22 | 6.5661 | N | 0
2025-03-29 | 17 | 2031-03-29 17:00 | 5.27 | 6.629 | N | 0
2025-03-29 | 18 | 2031-03-29 18:00 | 5.06 | 6.3649 | N | 0
2025-03-29 | 19 | 2031-03-29 19:00 | 5.05 | 6.3523 | N | 0
2025-03-29 | 20 | 2031-03-29 20:00 | 4.89 | 6.151 | N | 0
2025-03-29 | 21 | 2031-03-29 21:00 | 4.83 | 6.0756 | N | 0
2025-03-29 | 22 | 2031-03-29 22:00 | 4.34 | 5.4592 | N | 0
2025-03-29 | 23 | 2031-03-29 23:00 | 4.17 | 5.2454 | N | 0
2025-03-30 | 00 | 2031-03-30 | 3.72 | 4.6793 | N | 0
2025-03-30 | 01 | 2031-03-30 01:00 | 3.43 | 4.3145 | N | 0
2025-03-30 | 02 | 2031-03-30 02:00 | 3.31 | 4.1636 | N | 0
2025-03-30 | 03 | 2031-03-30 03:00 | 3.22 | 4.0504 | N | 0
2025-03-30 | 04 | 2031-03-30 04:00 | 3.21 | 4.0378 | N | 0
2025-03-30 | 05 | 2031-03-30 05:00 | 3.22 | 4.0504 | N | 0
2025-03-30 | 06 | 2031-03-30 06:00 | 3.34 | 4.2013 | N | 0
2025-03-30 | 07 | 2031-03-30 07:00 | 3.59 | 4.5158 | N | 0
2025-03-30 | 08 | 2031-03-30 08:00 | 4.03 | 5.0693 | N | 0
2025-03-30 | 09 | 2031-03-30 09:00 | 4.26 | 5.3586 | N | 0
2025-03-30 | 10 | 2031-03-30 10:00 | 4.56 | 5.7359 | N | 0
2025-03-30 | 11 | 2031-03-30 11:00 | 4.97 | 6.2517 | N | 0
2025-03-30 | 12 | 2031-03-30 12:00 | 5.17 | 6.5032 | N | 0
2025-03-30 | 13 | 2031-03-30 13:00 | 5.08 | 6.39 | N | 0
2025-03-30 | 14 | 2031-03-30 14:00 | 5.05 | 6.3523 | N | 0
2025-03-30 | 15 | 2031-03-30 15:00 | 5.09 | 6.4026 | N | 0
2025-03-30 | 16 | 2031-03-30 16:00 | 5.23 | 6.5787 | N | 0
2025-03-30 | 17 | 2031-03-30 17:00 | 5.45 | 6.8555 | N | 0
2025-03-30 | 18 | 2031-03-30 18:00 | 5.26 | 6.6165 | N | 0
2025-03-30 | 19 | 2031-03-30 19:00 | 4.91 | 6.1762 | N | 0
2025-03-30 | 20 | 2031-03-30 20:00 | 4.86 | 6.1133 | N | 0
2025-03-30 | 21 | 2031-03-30 21:00 | 4.62 | 5.8114 | N | 0
2025-03-30 | 22 | 2031-03-30 22:00 | 4.29 | 5.3963 | N | 0
2025-03-30 | 23 | 2031-03-30 23:00 | 3.73 | 4.6919 | N | 0
2025-03-31 | 00 | 2031-03-31 | 3.41 | 4.2894 | N | 0
2025-03-31 | 01 | 2031-03-31 01:00 | 3.11 | 3.912 | N | 0
2025-03-31 | 02 | 2031-03-31 02:00 | 2.92 | 3.673 | N | 0
2025-03-31 | 03 | 2031-03-31 03:00 | 2.84 | 3.5724 | N | 0
2025-03-31 | 04 | 2031-03-31 04:00 | 2.86 | 3.5975 | N | 0
2025-03-31 | 05 | 2031-03-31 05:00 | 3.12 | 3.9246 | N | 0
2025-03-31 | 06 | 2031-03-31 06:00 | 3.41 | 4.2894 | N | 0
2025-03-31 | 07 | 2031-03-31 07:00 | 3.61 | 4.541 | N | 0
2025-03-31 | 08 | 2031-03-31 08:00 | 3.78 | 4.7548 | N | 0
2025-03-31 | 09 | 2031-03-31 09:00 | 3.99 | 5.0189 | N | 0
2025-03-31 | 10 | 2031-03-31 10:00 | 4.07 | 5.1196 | N | 0
2025-03-31 | 11 | 2031-03-31 11:00 | 4.13 | 5.1951 | N | 0
2025-03-31 | 12 | 2031-03-31 12:00 | 4.23 | 5.3208 | N | 0
2025-03-31 | 13 | 2031-03-31 13:00 | 4.12 | 5.1825 | N | 0
2025-03-31 | 14 | 2031-03-31 14:00 | 4.06 | 5.107 | N | 0
2025-03-31 | 15 | 2031-03-31 15:00 | 4.22 | 5.3083 | N | 0
2025-03-31 | 16 | 2031-03-31 16:00 | 4.62 | 5.8114 | N | 0
2025-03-31 | 17 | 2031-03-31 17:00 | 4.92 | 6.1888 | N | 0
2025-03-31 | 18 | 2031-03-31 18:00 | 4.76 | 5.9875 | N | 0
2025-03-31 | 19 | 2031-03-31 19:00 | 4.71 | 5.9246 | N | 0
2025-03-31 | 20 | 2031-03-31 20:00 | 4.77 | 6.0001 | N | 0
2025-03-31 | 21 | 2031-03-31 21:00 | 4.73 | 5.9498 | N | 0
2025-03-31 | 22 | 2031-03-31 22:00 | 4.4 | 5.5347 | N | 0
2025-03-31 | 23 | 2031-03-31 23:00 | 3.82 | 4.8051 | N | 0
2025-04-01 | 00 | 2031-04-01 | 3.44 | 4.3271 | N | 0
2025-04-01 | 01 | 2031-04-01 01:00 | 3.22 | 4.0504 | N | 0
2025-04-01 | 02 | 2031-04-01 02:00 | 3.14 | 3.9497 | N | 0
2025-04-01 | 03 | 2031-04-01 03:00 | 3.1 | 3.8994 | N | 0
2025-04-01 | 04 | 2031-04-01 04:00 | 3.07 | 3.8617 | N | 0
2025-04-01 | 05 | 2031-04-01 05:00 | 3.25 | 4.0881 | N | 0
2025-04-01 | 06 | 2031-04-01 06:00 | 3.67 | 4.6164 | N | 0
2025-04-01 | 07 | 2031-04-01 07:00 | 3.95 | 4.9686 | N | 0
2025-04-01 | 08 | 2031-04-01 08:00 | 4.26 | 5.3586 | N | 0
2025-04-01 | 09 | 2031-04-01 09:00 | 4.28 | 5.3837 | N | 0
2025-04-01 | 10 | 2031-04-01 10:00 | 4.12 | 5.1825 | N | 0
2025-04-01 | 11 | 2031-04-01 11:00 | 4.3 | 5.4089 | N | 0
2025-04-01 | 12 | 2031-04-01 12:00 | 4.35 | 5.4718 | N | 0
2025-04-01 | 13 | 2031-04-01 13:00 | 4.35 | 5.4718 | N | 0
2025-04-01 | 14 | 2031-04-01 14:00 | 4.22 | 5.3083 | N | 0
2025-04-01 | 15 | 2031-04-01 15:00 | 4.12 | 5.1825 | N | 0
2025-04-01 | 16 | 2031-04-01 16:00 | 4.51 | 5.673 | N | 0
2025-04-01 | 17 | 2031-04-01 17:00 | 4.72 | 5.9372 | N | 0
2025-04-01 | 18 | 2031-04-01 18:00 | 4.69 | 5.8995 | N | 0
2025-04-01 | 19 | 2031-04-01 19:00 | 4.7 | 5.912 | N | 0
2025-04-01 | 20 | 2031-04-01 20:00 | 4.76 | 5.9875 | N | 0
2025-04-01 | 21 | 2031-04-01 21:00 | 4.76 | 5.9875 | N | 0
2025-04-01 | 22 | 2031-04-01 22:00 | 4.31 | 5.4215 | N | 0
2025-04-01 | 23 | 2031-04-01 23:00 | 3.72 | 4.6793 | N | 0
2025-04-02 | 00 | 2031-04-02 | 3.48 | 4.3774 | N | 0
2025-04-02 | 01 | 2031-04-02 01:00 | 3.23 | 4.063 | N | 0
2025-04-02 | 02 | 2031-04-02 02:00 | 3.23 | 4.063 | N | 0
2025-04-02 | 03 | 2031-04-02 03:00 | 3.11 | 3.912 | N | 0
2025-04-02 | 04 | 2031-04-02 04:00 | 3.19 | 4.0126 | N | 0
2025-04-02 | 05 | 2031-04-02 05:00 | 3.46 | 4.3523 | N | 0
2025-04-02 | 06 | 2031-04-02 06:00 | 3.85 | 4.8428 | N | 0
2025-04-02 | 07 | 2031-04-02 07:00 | 4.27 | 5.3712 | N | 0
2025-04-02 | 08 | 2031-04-02 08:00 | 4.5 | 5.6605 | N | 0
2025-04-02 | 09 | 2031-04-02 09:00 | 4.62 | 5.8114 | N | 0
2025-04-02 | 10 | 2031-04-02 10:00 | 4.74 | 5.9624 | N | 0
2025-04-02 | 11 | 2031-04-02 11:00 | 4.72 | 5.9372 | N | 0
2025-04-02 | 12 | 2031-04-02 12:00 | 4.95 | 6.2265 | N | 0
2025-04-02 | 13 | 2031-04-02 13:00 | 4.83 | 6.0756 | N | 0
2025-04-02 | 14 | 2031-04-02 14:00 | 4.79 | 6.0253 | N | 0
2025-04-02 | 15 | 2031-04-02 15:00 | 4.92 | 6.1888 | N | 0
2025-04-02 | 16 | 2031-04-02 16:00 | 5.4 | 6.7926 | N | 0
2025-04-02 | 17 | 2031-04-02 17:00 | 5.67 | 7.1322 | N | 0
2025-04-02 | 18 | 2031-04-02 18:00 | 5.41 | 6.8051 | N | 0
2025-04-02 | 19 | 2031-04-02 19:00 | 5.28 | 6.6416 | N | 0
2025-04-02 | 20 | 2031-04-02 20:00 | 5.13 | 6.4529 | N | 0
2025-04-02 | 21 | 2031-04-02 21:00 | 4.93 | 6.2014 | N | 0
2025-04-02 | 22 | 2031-04-02 22:00 | 4.52 | 5.6856 | N | 0
2025-04-02 | 23 | 2031-04-02 23:00 | 3.9 | 4.9057 | N | 0
2025-04-03 | 00 | 2031-04-03 | 3.52 | 4.4277 | N | 0
2025-04-03 | 01 | 2031-04-03 01:00 | 3.17 | 3.9875 | N | 0
2025-04-03 | 02 | 2031-04-03 02:00 | 3.08 | 3.8743 | N | 0
2025-04-03 | 03 | 2031-04-03 03:00 | 3.02 | 3.7988 | N | 0
2025-04-03 | 04 | 2031-04-03 04:00 | 3.01 | 3.7862 | N | 0
2025-04-03 | 05 | 2031-04-03 05:00 | 3.17 | 3.9875 | N | 0
2025-04-03 | 06 | 2031-04-03 06:00 | 3.57 | 4.4906 | N | 0
2025-04-03 | 07 | 2031-04-03 07:00 | 3.98 | 5.0064 | N | 0
2025-04-03 | 08 | 2031-04-03 08:00 | 4.16 | 5.2328 | N | 0
2025-04-03 | 09 | 2031-04-03 09:00 | 4.15 | 5.2202 | N | 0
2025-04-03 | 10 | 2031-04-03 10:00 | 4.21 | 5.2957 | N | 0
2025-04-03 | 11 | 2031-04-03 11:00 | 3.99 | 5.0189 | N | 0
2025-04-03 | 12 | 2031-04-03 12:00 | 3.91 | 4.9183 | N | 0
2025-04-03 | 13 | 2031-04-03 13:00 | 3.86 | 4.8554 | N | 0
2025-04-03 | 14 | 2031-04-03 14:00 | 3.74 | 4.7045 | N | 0
2025-04-03 | 15 | 2031-04-03 15:00 | 3.72 | 4.6793 | N | 0
2025-04-03 | 16 | 2031-04-03 16:00 | 4.06 | 5.107 | N | 0
2025-04-03 | 17 | 2031-04-03 17:00 | 4.23 | 5.3208 | N | 0
2025-04-03 | 18 | 2031-04-03 18:00 | 4.26 | 5.3586 | N | 0
2025-04-03 | 19 | 2031-04-03 19:00 | 4.2 | 5.2831 | N | 0
2025-04-03 | 20 | 2031-04-03 20:00 | 4.32 | 5.434 | N | 0
2025-04-03 | 21 | 2031-04-03 21:00 | 4.21 | 5.2957 | N | 0
2025-04-03 | 22 | 2031-04-03 22:00 | 3.92 | 4.9309 | N | 0
2025-04-03 | 23 | 2031-04-03 23:00 | 3.38 | 4.2516 | N | 0
2025-04-04 | 00 | 2031-04-04 | 3.04 | 3.824 | N | 0
2025-04-04 | 01 | 2031-04-04 01:00 | 2.83 | 3.5598 | N | 0
2025-04-04 | 02 | 2031-04-04 02:00 | 2.81 | 3.5346 | N | 0
2025-04-04 | 03 | 2031-04-04 03:00 | 2.71 | 3.4089 | N | 0
2025-04-04 | 04 | 2031-04-04 04:00 | 2.78 | 3.4969 | N | 0
2025-04-04 | 05 | 2031-04-04 05:00 | 3.2 | 4.0252 | N | 0
2025-04-04 | 06 | 2031-04-04 06:00 | 3.51 | 4.4152 | N | 0
2025-04-04 | 07 | 2031-04-04 07:00 | 3.9 | 4.9057 | N | 0
2025-04-04 | 08 | 2031-04-04 08:00 | 3.93 | 4.9435 | N | 0
2025-04-04 | 09 | 2031-04-04 09:00 | 3.93 | 4.9435 | N | 0
2025-04-04 | 10 | 2031-04-04 10:00 | 3.88 | 4.8806 | N | 0
2025-04-04 | 11 | 2031-04-04 11:00 | 3.99 | 5.0189 | N | 0
2025-04-04 | 12 | 2031-04-04 12:00 | 3.98 | 5.0064 | N | 0
2025-04-04 | 13 | 2031-04-04 13:00 | 3.84 | 4.8303 | N | 0
2025-04-04 | 14 | 2031-04-04 14:00 | 3.87 | 4.868 | N | 0
2025-04-04 | 15 | 2031-04-04 15:00 | 3.83 | 4.8177 | N | 0
2025-04-04 | 16 | 2031-04-04 16:00 | 4.01 | 5.0441 | N | 0
2025-04-04 | 17 | 2031-04-04 17:00 | 4.32 | 5.434 | N | 0
2025-04-04 | 18 | 2031-04-04 18:00 | 4.29 | 5.3963 | N | 0
2025-04-04 | 19 | 2031-04-04 19:00 | 4.28 | 5.3837 | N | 0
2025-04-04 | 20 | 2031-04-04 20:00 | 4.4 | 5.5347 | N | 0
2025-04-04 | 21 | 2031-04-04 21:00 | 4.31 | 5.4215 | N | 0
2025-04-04 | 22 | 2031-04-04 22:00 | 4 | 5.0315 | N | 0
2025-04-04 | 23 | 2031-04-04 23:00 | 3.65 | 4.5913 | N | 0
2025-04-05 | 00 | 2031-04-05 | 3.32 | 4.1762 | N | 0
2025-04-05 | 01 | 2031-04-05 01:00 | 3.04 | 3.824 | N | 0
2025-04-05 | 02 | 2031-04-05 02:00 | 2.89 | 3.6353 | N | 0
2025-04-05 | 03 | 2031-04-05 03:00 | 2.79 | 3.5095 | N | 0
2025-04-05 | 04 | 2031-04-05 04:00 | 2.77 | 3.4843 | N | 0
2025-04-05 | 05 | 2031-04-05 05:00 | 2.88 | 3.6227 | N | 0
2025-04-05 | 06 | 2031-04-05 06:00 | 3.04 | 3.824 | N | 0
2025-04-05 | 07 | 2031-04-05 07:00 | 3.31 | 4.1636 | N | 0
2025-04-05 | 08 | 2031-04-05 08:00 | 3.78 | 4.7548 | N | 0
2025-04-05 | 09 | 2031-04-05 09:00 | 4.06 | 5.107 | N | 0
2025-04-05 | 10 | 2031-04-05 10:00 | 4.28 | 5.3837 | N | 0
2025-04-05 | 11 | 2031-04-05 11:00 | 4.43 | 5.5724 | N | 0
2025-04-05 | 12 | 2031-04-05 12:00 | 4.49 | 5.6479 | N | 0
2025-04-05 | 13 | 2031-04-05 13:00 | 4.43 | 5.5724 | N | 0
2025-04-05 | 14 | 2031-04-05 14:00 | 4.33 | 5.4466 | N | 0
2025-04-05 | 15 | 2031-04-05 15:00 | 4.35 | 5.4718 | N | 0
2025-04-05 | 16 | 2031-04-05 16:00 | 4.47 | 5.6227 | N | 0
2025-04-05 | 17 | 2031-04-05 17:00 | 4.53 | 5.6982 | N | 0
2025-04-05 | 18 | 2031-04-05 18:00 | 4.6 | 5.7863 | N | 0
2025-04-05 | 19 | 2031-04-05 19:00 | 4.45 | 5.5976 | N | 0
2025-04-05 | 20 | 2031-04-05 20:00 | 4.43 | 5.5724 | N | 0
2025-04-05 | 21 | 2031-04-05 21:00 | 4.34 | 5.4592 | N | 0
2025-04-05 | 22 | 2031-04-05 22:00 | 3.94 | 4.9561 | N | 0
2025-04-05 | 23 | 2031-04-05 23:00 | 3.65 | 4.5913 | N | 0
2025-04-06 | 00 | 2031-04-06 | 3.38 | 4.2516 | N | 0
2025-04-06 | 01 | 2031-04-06 01:00 | 3.02 | 3.7988 | N | 0
2025-04-06 | 02 | 2031-04-06 02:00 | 2.94 | 3.6982 | N | 0
2025-04-06 | 03 | 2031-04-06 03:00 | 2.88 | 3.6227 | N | 0
2025-04-06 | 04 | 2031-04-06 04:00 | 2.88 | 3.6227 | N | 0
2025-04-06 | 05 | 2031-04-06 05:00 | 2.99 | 3.7611 | N | 0
2025-04-06 | 06 | 2031-04-06 06:00 | 3.09 | 3.8869 | N | 0
2025-04-06 | 07 | 2031-04-06 07:00 | 3.43 | 4.3145 | N | 0
2025-04-06 | 08 | 2031-04-06 08:00 | 3.7 | 4.6542 | N | 0
2025-04-06 | 09 | 2031-04-06 09:00 | 3.97 | 4.9938 | N | 0
2025-04-06 | 10 | 2031-04-06 10:00 | 4.13 | 5.1951 | N | 0
2025-04-06 | 11 | 2031-04-06 11:00 | 4.24 | 5.3334 | N | 0
2025-04-06 | 12 | 2031-04-06 12:00 | 4.29 | 5.3963 | N | 0
2025-04-06 | 13 | 2031-04-06 13:00 | 4.25 | 5.346 | N | 0
2025-04-06 | 14 | 2031-04-06 14:00 | 4.21 | 5.2957 | N | 0
2025-04-06 | 15 | 2031-04-06 15:00 | 4.29 | 5.3963 | N | 0
2025-04-06 | 16 | 2031-04-06 16:00 | 4.59 | 5.7737 | N | 0
2025-04-06 | 17 | 2031-04-06 17:00 | 4.72 | 5.9372 | N | 0
2025-04-06 | 18 | 2031-04-06 18:00 | 4.78 | 6.0127 | N | 0
2025-04-06 | 19 | 2031-04-06 19:00 | 4.74 | 5.9624 | N | 0
2025-04-06 | 20 | 2031-04-06 20:00 | 4.53 | 5.6982 | N | 0
2025-04-06 | 21 | 2031-04-06 21:00 | 4.43 | 5.5724 | N | 0
2025-04-06 | 22 | 2031-04-06 22:00 | 4.34 | 5.4592 | N | 0
2025-04-06 | 23 | 2031-04-06 23:00 | 3.68 | 4.629 | N | 0
2025-04-07 | 00 | 2031-04-07 | 3.37 | 4.2391 | N | 0
2025-04-07 | 01 | 2031-04-07 01:00 | 3.11 | 3.912 | N | 0
2025-04-07 | 02 | 2031-04-07 02:00 | 3.01 | 3.7862 | N | 0
2025-04-07 | 03 | 2031-04-07 03:00 | 2.93 | 3.6856 | N | 0
2025-04-07 | 04 | 2031-04-07 04:00 | 3.06 | 3.8491 | N | 0
2025-04-07 | 05 | 2031-04-07 05:00 | 3.29 | 4.1384 | N | 0
2025-04-07 | 06 | 2031-04-07 06:00 | 3.77 | 4.7422 | N | 0
2025-04-07 | 07 | 2031-04-07 07:00 | 4.14 | 5.2076 | N | 0
2025-04-07 | 08 | 2031-04-07 08:00 | 4.09 | 5.1447 | N | 0
2025-04-07 | 09 | 2031-04-07 09:00 | 4.09 | 5.1447 | N | 0
2025-04-07 | 10 | 2031-04-07 10:00 | 4.16 | 5.2328 | N | 0
2025-04-07 | 11 | 2031-04-07 11:00 | 4.06 | 5.107 | N | 0
2025-04-07 | 12 | 2031-04-07 12:00 | 4.11 | 5.1699 | N | 0
2025-04-07 | 13 | 2031-04-07 13:00 | 4.09 | 5.1447 | N | 0
2025-04-07 | 14 | 2031-04-07 14:00 | 3.96 | 4.9812 | N | 0
2025-04-07 | 15 | 2031-04-07 15:00 | 4.02 | 5.0567 | N | 0
2025-04-07 | 16 | 2031-04-07 16:00 | 4.47 | 5.6227 | N | 0
2025-04-07 | 17 | 2031-04-07 17:00 | 4.8 | 6.0378 | N | 0
2025-04-07 | 18 | 2031-04-07 18:00 | 4.88 | 6.1385 | N | 0
2025-04-07 | 19 | 2031-04-07 19:00 | 4.64 | 5.8366 | N | 0
2025-04-07 | 20 | 2031-04-07 20:00 | 4.88 | 6.1385 | N | 0
2025-04-07 | 21 | 2031-04-07 21:00 | 4.68 | 5.8869 | N | 0
2025-04-07 | 22 | 2031-04-07 22:00 | 4.29 | 5.3963 | N | 0
2025-04-07 | 23 | 2031-04-07 23:00 | 3.91 | 4.9183 | N | 0
2025-04-08 | 00 | 2031-04-08 | 3.55 | 4.4655 | N | 0
2025-04-08 | 01 | 2031-04-08 01:00 | 3.33 | 4.1887 | N | 0
2025-04-08 | 02 | 2031-04-08 02:00 | 3.22 | 4.0504 | N | 0
2025-04-08 | 03 | 2031-04-08 03:00 | 3.19 | 4.0126 | N | 0
2025-04-08 | 04 | 2031-04-08 04:00 | 3.3 | 4.151 | N | 0
2025-04-08 | 05 | 2031-04-08 05:00 | 3.59 | 4.5158 | N | 0
2025-04-08 | 06 | 2031-04-08 06:00 | 4.05 | 5.0944 | N | 0
2025-04-08 | 07 | 2031-04-08 07:00 | 4.46 | 5.6102 | N | 0
2025-04-08 | 08 | 2031-04-08 08:00 | 4.75 | 5.9749 | N | 0
2025-04-08 | 09 | 2031-04-08 09:00 | 4.72 | 5.9372 | N | 0
2025-04-08 | 10 | 2031-04-08 10:00 | 4.73 | 5.9498 | N | 0
2025-04-08 | 11 | 2031-04-08 11:00 | 4.73 | 5.9498 | N | 0
2025-04-08 | 12 | 2031-04-08 12:00 | 4.97 | 6.2517 | N | 0
2025-04-08 | 13 | 2031-04-08 13:00 | 4.76 | 5.9875 | N | 0
2025-04-08 | 14 | 2031-04-08 14:00 | 4.56 | 5.7359 | N | 0
2025-04-08 | 15 | 2031-04-08 15:00 | 4.64 | 5.8366 | N | 0
2025-04-08 | 16 | 2031-04-08 16:00 | 5.01 | 6.302 | N | 0
2025-04-08 | 17 | 2031-04-08 17:00 | 5.15 | 6.4781 | N | 0
2025-04-08 | 18 | 2031-04-08 18:00 | 5.06 | 6.3649 | N | 0
2025-04-08 | 19 | 2031-04-08 19:00 | 5.16 | 6.4907 | N | 0
2025-04-08 | 20 | 2031-04-08 20:00 | 5.2 | 6.541 | N | 0
2025-04-08 | 21 | 2031-04-08 21:00 | 5.13 | 6.4529 | N | 0
2025-04-08 | 22 | 2031-04-08 22:00 | 4.55 | 5.7234 | N | 0
2025-04-08 | 23 | 2031-04-08 23:00 | 3.95 | 4.9686 | N | 0
2025-04-09 | 00 | 2031-04-09 | 3.71 | 4.6667 | N | 0
2025-04-09 | 01 | 2031-04-09 01:00 | 3.48 | 4.3774 | N | 0
2025-04-09 | 02 | 2031-04-09 02:00 | 3.44 | 4.3271 | N | 0
2025-04-09 | 03 | 2031-04-09 03:00 | 3.43 | 4.3145 | N | 0
2025-04-09 | 04 | 2031-04-09 04:00 | 3.42 | 4.302 | N | 0
2025-04-09 | 05 | 2031-04-09 05:00 | 3.67 | 4.6164 | N | 0
2025-04-09 | 06 | 2031-04-09 06:00 | 4.09 | 5.1447 | N | 0
2025-04-09 | 07 | 2031-04-09 07:00 | 4.43 | 5.5724 | N | 0
2025-04-09 | 08 | 2031-04-09 08:00 | 4.47 | 5.6227 | N | 0
2025-04-09 | 09 | 2031-04-09 09:00 | 4.45 | 5.5976 | N | 0
2025-04-09 | 10 | 2031-04-09 10:00 | 4.44 | 5.585 | N | 0
2025-04-09 | 11 | 2031-04-09 11:00 | 4.52 | 5.6856 | N | 0
2025-04-09 | 12 | 2031-04-09 12:00 | 4.48 | 5.6353 | N | 0
2025-04-09 | 13 | 2031-04-09 13:00 | 4.46 | 5.6102 | N | 0
2025-04-09 | 14 | 2031-04-09 14:00 | 4.32 | 5.434 | N | 0
2025-04-09 | 15 | 2031-04-09 15:00 | 4.34 | 5.4592 | N | 0
2025-04-09 | 16 | 2031-04-09 16:00 | 4.67 | 5.8743 | N | 0
2025-04-09 | 17 | 2031-04-09 17:00 | 4.95 | 6.2265 | N | 0
2025-04-09 | 18 | 2031-04-09 18:00 | 4.92 | 6.1888 | N | 0
2025-04-09 | 19 | 2031-04-09 19:00 | 4.85 | 6.1007 | N | 0
2025-04-09 | 20 | 2031-04-09 20:00 | 4.97 | 6.2517 | N | 0
2025-04-09 | 21 | 2031-04-09 21:00 | 4.82 | 6.063 | N | 0
2025-04-09 | 22 | 2031-04-09 22:00 | 4.5 | 5.6605 | N | 0
2025-04-09 | 23 | 2031-04-09 23:00 | 3.8 | 4.7799 | N | 0
2025-04-10 | 00 | 2031-04-10 | 3.48 | 4.3774 | N | 0
2025-04-10 | 01 | 2031-04-10 01:00 | 3.24 | 4.0755 | N | 0
2025-04-10 | 02 | 2031-04-10 02:00 | 3.14 | 3.9497 | N | 0
2025-04-10 | 03 | 2031-04-10 03:00 | 3.07 | 3.8617 | N | 0
2025-04-10 | 04 | 2031-04-10 04:00 | 3.14 | 3.9497 | N | 0
2025-04-10 | 05 | 2031-04-10 05:00 | 3.37 | 4.2391 | N | 0
2025-04-10 | 06 | 2031-04-10 06:00 | 3.85 | 4.8428 | N | 0
2025-04-10 | 07 | 2031-04-10 07:00 | 4.34 | 5.4592 | N | 0
2025-04-10 | 08 | 2031-04-10 08:00 | 4.37 | 5.4969 | N | 0
2025-04-10 | 09 | 2031-04-10 09:00 | 4.46 | 5.6102 | N | 0
2025-04-10 | 10 | 2031-04-10 10:00 | 4.37 | 5.4969 | N | 0
2025-04-10 | 11 | 2031-04-10 11:00 | 4.42 | 5.5598 | N | 0
2025-04-10 | 12 | 2031-04-10 12:00 | 4.52 | 5.6856 | N | 0
2025-04-10 | 13 | 2031-04-10 13:00 | 4.43 | 5.5724 | N | 0
2025-04-10 | 14 | 2031-04-10 14:00 | 4.43 | 5.5724 | N | 0
2025-04-10 | 15 | 2031-04-10 15:00 | 4.47 | 5.6227 | N | 0
2025-04-10 | 16 | 2031-04-10 16:00 | 4.86 | 6.1133 | N | 0
2025-04-10 | 17 | 2031-04-10 17:00 | 5 | 6.2894 | N | 0
2025-04-10 | 18 | 2031-04-10 18:00 | 4.94 | 6.2139 | N | 0
2025-04-10 | 19 | 2031-04-10 19:00 | 4.83 | 6.0756 | N | 0
2025-04-10 | 20 | 2031-04-10 20:00 | 4.95 | 6.2265 | N | 0
2025-04-10 | 21 | 2031-04-10 21:00 | 4.74 | 5.9624 | N | 0
2025-04-10 | 22 | 2031-04-10 22:00 | 4.4 | 5.5347 | N | 0
2025-04-10 | 23 | 2031-04-10 23:00 | 3.78 | 4.7548 | N | 0
2025-04-11 | 00 | 2031-04-11 | 3.5 | 4.4026 | N | 0
2025-04-11 | 01 | 2031-04-11 01:00 | 3.24 | 4.0755 | N | 0
2025-04-11 | 02 | 2031-04-11 02:00 | 3.13 | 3.9372 | N | 0
2025-04-11 | 03 | 2031-04-11 03:00 | 3.08 | 3.8743 | N | 0
2025-04-11 | 04 | 2031-04-11 04:00 | 3.07 | 3.8617 | N | 0
2025-04-11 | 05 | 2031-04-11 05:00 | 3.26 | 4.1007 | N | 0
2025-04-11 | 06 | 2031-04-11 06:00 | 3.55 | 4.4655 | N | 0
2025-04-11 | 07 | 2031-04-11 07:00 | 4 | 5.0315 | N | 0
2025-04-11 | 08 | 2031-04-11 08:00 | 4.15 | 5.2202 | N | 0
2025-04-11 | 09 | 2031-04-11 09:00 | 4.26 | 5.3586 | N | 0
2025-04-11 | 10 | 2031-04-11 10:00 | 4.44 | 5.585 | N | 0
2025-04-11 | 11 | 2031-04-11 11:00 | 4.58 | 5.7611 | N | 0
2025-04-11 | 12 | 2031-04-11 12:00 | 4.72 | 5.9372 | N | 0
2025-04-11 | 13 | 2031-04-11 13:00 | 4.59 | 5.7737 | N | 0
2025-04-11 | 14 | 2031-04-11 14:00 | 4.59 | 5.7737 | N | 0
2025-04-11 | 15 | 2031-04-11 15:00 | 4.57 | 5.7485 | N | 0
2025-04-11 | 16 | 2031-04-11 16:00 | 4.77 | 6.0001 | N | 0
2025-04-11 | 17 | 2031-04-11 17:00 | 4.81 | 6.0504 | N | 0
2025-04-11 | 18 | 2031-04-11 18:00 | 4.77 | 6.0001 | N | 0
2025-04-11 | 19 | 2031-04-11 19:00 | 4.71 | 5.9246 | N | 0
2025-04-11 | 20 | 2031-04-11 20:00 | 4.75 | 5.9749 | N | 0
2025-04-11 | 21 | 2031-04-11 21:00 | 4.5 | 5.6605 | N | 0
2025-04-11 | 22 | 2031-04-11 22:00 | 4.23 | 5.3208 | N | 0
2025-04-11 | 23 | 2031-04-11 23:00 | 3.92 | 4.9309 | N | 0
2025-04-12 | 00 | 2031-04-12 | 3.49 | 4.39 | N | 0
2025-04-12 | 01 | 2031-04-12 01:00 | 3.2 | 4.0252 | N | 0
2025-04-12 | 02 | 2031-04-12 02:00 | 3.08 | 3.8743 | N | 0
2025-04-12 | 03 | 2031-04-12 03:00 | 2.99 | 3.7611 | N | 0
2025-04-12 | 04 | 2031-04-12 04:00 | 2.99 | 3.7611 | N | 0
2025-04-12 | 05 | 2031-04-12 05:00 | 3.03 | 3.8114 | N | 0
2025-04-12 | 06 | 2031-04-12 06:00 | 3.24 | 4.0755 | N | 0
2025-04-12 | 07 | 2031-04-12 07:00 | 3.64 | 4.5787 | N | 0
2025-04-12 | 08 | 2031-04-12 08:00 | 3.95 | 4.9686 | N | 0
2025-04-12 | 09 | 2031-04-12 09:00 | 4.08 | 5.1322 | N | 0
2025-04-12 | 10 | 2031-04-12 10:00 | 4.27 | 5.3712 | N | 0
2025-04-12 | 11 | 2031-04-12 11:00 | 4.38 | 5.5095 | N | 0
2025-04-12 | 12 | 2031-04-12 12:00 | 4.44 | 5.585 | N | 0
2025-04-12 | 13 | 2031-04-12 13:00 | 4.37 | 5.4969 | N | 0
2025-04-12 | 14 | 2031-04-12 14:00 | 4.34 | 5.4592 | N | 0
2025-04-12 | 15 | 2031-04-12 15:00 | 4.25 | 5.346 | N | 0
2025-04-12 | 16 | 2031-04-12 16:00 | 4.35 | 5.4718 | N | 0
2025-04-12 | 17 | 2031-04-12 17:00 | 4.37 | 5.4969 | N | 0
2025-04-12 | 18 | 2031-04-12 18:00 | 4.36 | 5.4844 | N | 0
2025-04-12 | 19 | 2031-04-12 19:00 | 4.42 | 5.5598 | N | 0
2025-04-12 | 20 | 2031-04-12 20:00 | 4.38 | 5.5095 | N | 0
2025-04-12 | 21 | 2031-04-12 21:00 | 4.29 | 5.3963 | N | 0
2025-04-12 | 22 | 2031-04-12 22:00 | 4.04 | 5.0818 | N | 0
2025-04-12 | 23 | 2031-04-12 23:00 | 3.76 | 4.7296 | N | 0
2025-04-13 | 00 | 2031-04-13 | 3.43 | 4.3145 | N | 0
2025-04-13 | 01 | 2031-04-13 01:00 | 3.14 | 3.9497 | N | 0
2025-04-13 | 02 | 2031-04-13 02:00 | 3.05 | 3.8365 | N | 0
2025-04-13 | 03 | 2031-04-13 03:00 | 3.01 | 3.7862 | N | 0
2025-04-13 | 04 | 2031-04-13 04:00 | 3.07 | 3.8617 | N | 0
2025-04-13 | 05 | 2031-04-13 05:00 | 3.04 | 3.824 | N | 0
2025-04-13 | 06 | 2031-04-13 06:00 | 3.23 | 4.063 | N | 0
2025-04-13 | 07 | 2031-04-13 07:00 | 3.49 | 4.39 | N | 0
2025-04-13 | 08 | 2031-04-13 08:00 | 3.64 | 4.5787 | N | 0
2025-04-13 | 09 | 2031-04-13 09:00 | 3.92 | 4.9309 | N | 0
2025-04-13 | 10 | 2031-04-13 10:00 | 3.91 | 4.9183 | N | 0
2025-04-13 | 11 | 2031-04-13 11:00 | 3.94 | 4.9561 | N | 0
2025-04-13 | 12 | 2031-04-13 12:00 | 4.05 | 5.0944 | N | 0
2025-04-13 | 13 | 2031-04-13 13:00 | 4.12 | 5.1825 | N | 0
2025-04-13 | 14 | 2031-04-13 14:00 | 4.01 | 5.0441 | N | 0
2025-04-13 | 15 | 2031-04-13 15:00 | 4.1 | 5.1573 | N | 0
2025-04-13 | 16 | 2031-04-13 16:00 | 4.23 | 5.3208 | N | 0
2025-04-13 | 17 | 2031-04-13 17:00 | 4.39 | 5.5221 | N | 0
2025-04-13 | 18 | 2031-04-13 18:00 | 4.37 | 5.4969 | N | 0
2025-04-13 | 19 | 2031-04-13 19:00 | 4.27 | 5.3712 | N | 0
2025-04-13 | 20 | 2031-04-13 20:00 | 4.29 | 5.3963 | N | 0
2025-04-13 | 21 | 2031-04-13 21:00 | 4.1 | 5.1573 | N | 0
2025-04-13 | 22 | 2031-04-13 22:00 | 3.79 | 4.7674 | N | 0
2025-04-13 | 23 | 2031-04-13 23:00 | 3.44 | 4.3271 | N | 0
2025-04-14 | 00 | 2031-04-14 | 3.04 | 3.824 | N | 0
2025-04-14 | 01 | 2031-04-14 01:00 | 2.82 | 3.5472 | N | 0
2025-04-14 | 02 | 2031-04-14 02:00 | 2.77 | 3.4843 | N | 0
2025-04-14 | 03 | 2031-04-14 03:00 | 2.68 | 3.3711 | N | 0
2025-04-14 | 04 | 2031-04-14 04:00 | 2.73 | 3.434 | N | 0
2025-04-14 | 05 | 2031-04-14 05:00 | 3.01 | 3.7862 | N | 0
2025-04-14 | 06 | 2031-04-14 06:00 | 3.39 | 4.2642 | N | 0
2025-04-14 | 07 | 2031-04-14 07:00 | 3.83 | 4.8177 | N | 0
2025-04-14 | 08 | 2031-04-14 08:00 | 4.03 | 5.0693 | N | 0
2025-04-14 | 09 | 2031-04-14 09:00 | 3.99 | 5.0189 | N | 0
2025-04-14 | 10 | 2031-04-14 10:00 | 3.99 | 5.0189 | N | 0
2025-04-14 | 11 | 2031-04-14 11:00 | 3.89 | 4.8932 | N | 0
2025-04-14 | 12 | 2031-04-14 12:00 | 3.92 | 4.9309 | N | 0
2025-04-14 | 13 | 2031-04-14 13:00 | 3.9 | 4.9057 | N | 0
2025-04-14 | 14 | 2031-04-14 14:00 | 3.88 | 4.8806 | N | 0
2025-04-14 | 15 | 2031-04-14 15:00 | 3.89 | 4.8932 | N | 0
2025-04-14 | 16 | 2031-04-14 16:00 | 4.31 | 5.4215 | N | 0
2025-04-14 | 17 | 2031-04-14 17:00 | 4.38 | 5.5095 | N | 0
2025-04-14 | 18 | 2031-04-14 18:00 | 4.3 | 5.4089 | N | 0
2025-04-14 | 19 | 2031-04-14 19:00 | 4.14 | 5.2076 | N | 0
2025-04-14 | 20 | 2031-04-14 20:00 | 4.3 | 5.4089 | N | 0
2025-04-14 | 21 | 2031-04-14 21:00 | 4.14 | 5.2076 | N | 0
2025-04-14 | 22 | 2031-04-14 22:00 | 3.74 | 4.7045 | N | 0
2025-04-14 | 23 | 2031-04-14 23:00 | 3.2 | 4.0252 | N | 0
2025-04-15 | 00 | 2031-04-15 | 2.96 | 3.7233 | N | 0
2025-04-15 | 01 | 2031-04-15 01:00 | 2.73 | 3.434 | N | 0
2025-04-15 | 02 | 2031-04-15 02:00 | 2.63 | 3.3082 | N | 0
2025-04-15 | 03 | 2031-04-15 03:00 | 2.58 | 3.2453 | N | 0
2025-04-15 | 04 | 2031-04-15 04:00 | 2.63 | 3.3082 | N | 0
2025-04-15 | 05 | 2031-04-15 05:00 | 2.88 | 3.6227 | N | 0
2025-04-15 | 06 | 2031-04-15 06:00 | 3.22 | 4.0504 | N | 0
2025-04-15 | 07 | 2031-04-15 07:00 | 3.66 | 4.6038 | N | 0
2025-04-15 | 08 | 2031-04-15 08:00 | 3.87 | 4.868 | N | 0
2025-04-15 | 09 | 2031-04-15 09:00 | 3.84 | 4.8303 | N | 0
2025-04-15 | 10 | 2031-04-15 10:00 | 3.97 | 4.9938 | N | 0
2025-04-15 | 11 | 2031-04-15 11:00 | 4.01 | 5.0441 | N | 0
2025-04-15 | 12 | 2031-04-15 12:00 | 3.98 | 5.0064 | N | 0
2025-04-15 | 13 | 2031-04-15 13:00 | 3.96 | 4.9812 | N | 0
2025-04-15 | 14 | 2031-04-15 14:00 | 3.92 | 4.9309 | N | 0
2025-04-15 | 15 | 2031-04-15 15:00 | 3.98 | 5.0064 | N | 0
2025-04-15 | 16 | 2031-04-15 16:00 | 4.35 | 5.4718 | N | 0
2025-04-15 | 17 | 2031-04-15 17:00 | 4.82 | 6.063 | N | 0
2025-04-15 | 18 | 2031-04-15 18:00 | 4.76 | 5.9875 | N | 0
2025-04-15 | 19 | 2031-04-15 19:00 | 4.63 | 5.824 | N | 0
2025-04-15 | 20 | 2031-04-15 20:00 | 4.7 | 5.912 | N | 0
2025-04-15 | 21 | 2031-04-15 21:00 | 4.48 | 5.6353 | N | 0
2025-04-15 | 22 | 2031-04-15 22:00 | 4.15 | 5.2202 | N | 0
2025-04-15 | 23 | 2031-04-15 23:00 | 3.57 | 4.4906 | N | 0
2025-04-16 | 00 | 2031-04-16 | 3.28 | 4.1259 | N | 0
2025-04-16 | 01 | 2031-04-16 01:00 | 3.03 | 3.8114 | N | 0
2025-04-16 | 02 | 2031-04-16 02:00 | 2.97 | 3.7359 | N | 0
2025-04-16 | 03 | 2031-04-16 03:00 | 2.94 | 3.6982 | N | 0
2025-04-16 | 04 | 2031-04-16 04:00 | 2.95 | 3.7108 | N | 0
2025-04-16 | 05 | 2031-04-16 05:00 | 3.21 | 4.0378 | N | 0
2025-04-16 | 06 | 2031-04-16 06:00 | 3.59 | 4.5158 | N | 0
2025-04-16 | 07 | 2031-04-16 07:00 | 4.16 | 5.2328 | N | 0
2025-04-16 | 08 | 2031-04-16 08:00 | 4.27 | 5.3712 | N | 0
2025-04-16 | 09 | 2031-04-16 09:00 | 4.3 | 5.4089 | N | 0
2025-04-16 | 10 | 2031-04-16 10:00 | 4.4 | 5.5347 | N | 0
2025-04-16 | 11 | 2031-04-16 11:00 | 4.42 | 5.5598 | N | 0
2025-04-16 | 12 | 2031-04-16 12:00 | 4.57 | 5.7485 | N | 0
2025-04-16 | 13 | 2031-04-16 13:00 | 4.47 | 5.6227 | N | 0
2025-04-16 | 14 | 2031-04-16 14:00 | 4.32 | 5.434 | N | 0
2025-04-16 | 15 | 2031-04-16 15:00 | 4.36 | 5.4844 | N | 0
2025-04-16 | 16 | 2031-04-16 16:00 | 4.7 | 5.912 | N | 0
2025-04-16 | 17 | 2031-04-16 17:00 | 4.84 | 6.0881 | N | 0
2025-04-16 | 18 | 2031-04-16 18:00 | 4.66 | 5.8617 | N | 0
2025-04-16 | 19 | 2031-04-16 19:00 | 4.55 | 5.7234 | N | 0
2025-04-16 | 20 | 2031-04-16 20:00 | 4.75 | 5.9749 | N | 0
2025-04-16 | 21 | 2031-04-16 21:00 | 4.67 | 5.8743 | N | 0
2025-04-16 | 22 | 2031-04-16 22:00 | 4.38 | 5.5095 | N | 0
2025-04-16 | 23 | 2031-04-16 23:00 | 3.73 | 4.6919 | N | 0
2025-04-17 | 00 | 2031-04-17 | 3.38 | 4.2516 | N | 0
2025-04-17 | 01 | 2031-04-17 01:00 | 3.16 | 3.9749 | N | 0
2025-04-17 | 02 | 2031-04-17 02:00 | 3.08 | 3.8743 | N | 0
2025-04-17 | 03 | 2031-04-17 03:00 | 3.05 | 3.8365 | N | 0
2025-04-17 | 04 | 2031-04-17 04:00 | 3.15 | 3.9623 | N | 0
2025-04-17 | 05 | 2031-04-17 05:00 | 3.32 | 4.1762 | N | 0
2025-04-17 | 06 | 2031-04-17 06:00 | 3.77 | 4.7422 | N | 0
2025-04-17 | 07 | 2031-04-17 07:00 | 4.12 | 5.1825 | N | 0
2025-04-17 | 08 | 2031-04-17 08:00 | 4.08 | 5.1322 | N | 0
2025-04-17 | 09 | 2031-04-17 09:00 | 4.15 | 5.2202 | N | 0
2025-04-17 | 10 | 2031-04-17 10:00 | 4.09 | 5.1447 | N | 0
2025-04-17 | 11 | 2031-04-17 11:00 | 3.99 | 5.0189 | N | 0
2025-04-17 | 12 | 2031-04-17 12:00 | 4.08 | 5.1322 | N | 0
2025-04-17 | 13 | 2031-04-17 13:00 | 4.08 | 5.1322 | N | 0
2025-04-17 | 14 | 2031-04-17 14:00 | 3.97 | 4.9938 | N | 0
2025-04-17 | 15 | 2031-04-17 15:00 | 3.93 | 4.9435 | N | 0
2025-04-17 | 16 | 2031-04-17 16:00 | 4.12 | 5.1825 | N | 0
2025-04-17 | 17 | 2031-04-17 17:00 | 4.23 | 5.3208 | N | 0
2025-04-17 | 18 | 2031-04-17 18:00 | 4.18 | 5.2579 | N | 0
2025-04-17 | 19 | 2031-04-17 19:00 | 4.21 | 5.2957 | N | 0
2025-04-17 | 20 | 2031-04-17 20:00 | 4.48 | 5.6353 | N | 0
2025-04-17 | 21 | 2031-04-17 21:00 | 4.39 | 5.5221 | N | 0
2025-04-17 | 22 | 2031-04-17 22:00 | 4 | 5.0315 | N | 0
2025-04-17 | 23 | 2031-04-17 23:00 | 3.6 | 4.5284 | N | 0
2025-04-18 | 00 | 2031-04-18 | 3.29 | 4.1384 | N | 0
2025-04-18 | 01 | 2031-04-18 01:00 | 3.02 | 3.7988 | N | 0
2025-04-18 | 02 | 2031-04-18 02:00 | 2.89 | 3.6353 | N | 0
2025-04-18 | 03 | 2031-04-18 03:00 | 2.92 | 3.673 | N | 0
2025-04-18 | 04 | 2031-04-18 04:00 | 2.89 | 3.6353 | N | 0
2025-04-18 | 05 | 2031-04-18 05:00 | 2.93 | 3.6856 | N | 0
2025-04-18 | 06 | 2031-04-18 06:00 | 3.24 | 4.0755 | N | 0
2025-04-18 | 07 | 2031-04-18 07:00 | 3.57 | 4.4906 | N | 0
2025-04-18 | 08 | 2031-04-18 08:00 | 3.82 | 4.8051 | N | 0
2025-04-18 | 09 | 2031-04-18 09:00 | 3.99 | 5.0189 | N | 0
2025-04-18 | 10 | 2031-04-18 10:00 | 4.22 | 5.3083 | N | 0
2025-04-18 | 11 | 2031-04-18 11:00 | 4.42 | 5.5598 | N | 0
2025-04-18 | 12 | 2031-04-18 12:00 | 4.55 | 5.7234 | N | 0
2025-04-18 | 13 | 2031-04-18 13:00 | 4.55 | 5.7234 | N | 0
2025-04-18 | 14 | 2031-04-18 14:00 | 4.64 | 5.8366 | N | 0
2025-04-18 | 15 | 2031-04-18 15:00 | 4.22 | 5.3083 | N | 0
2025-04-18 | 16 | 2031-04-18 16:00 | 4.29 | 5.3963 | N | 0
2025-04-18 | 17 | 2031-04-18 17:00 | 4.32 | 5.434 | N | 0
2025-04-18 | 18 | 2031-04-18 18:00 | 4.19 | 5.2705 | N | 0
2025-04-18 | 19 | 2031-04-18 19:00 | 4.02 | 5.0567 | N | 0
2025-04-18 | 20 | 2031-04-18 20:00 | 4.27 | 5.3712 | N | 0
2025-04-18 | 21 | 2031-04-18 21:00 | 3.96 | 4.9812 | N | 0
2025-04-18 | 22 | 2031-04-18 22:00 | 3.73 | 4.6919 | N | 0
2025-04-18 | 23 | 2031-04-18 23:00 | 3.38 | 4.2516 | N | 0
2025-04-19 | 00 | 2031-04-19 | 2.97 | 3.7359 | N | 0
2025-04-19 | 01 | 2031-04-19 01:00 | 2.83 | 3.5598 | N | 0
2025-04-19 | 02 | 2031-04-19 02:00 | 2.64 | 3.3208 | N | 0
2025-04-19 | 03 | 2031-04-19 03:00 | 2.56 | 3.2202 | N | 0
2025-04-19 | 04 | 2031-04-19 04:00 | 2.49 | 3.1321 | N | 0
2025-04-19 | 05 | 2031-04-19 05:00 | 2.54 | 3.195 | N | 0
2025-04-19 | 06 | 2031-04-19 06:00 | 2.64 | 3.3208 | N | 0
2025-04-19 | 07 | 2031-04-19 07:00 | 2.91 | 3.6604 | N | 0
2025-04-19 | 08 | 2031-04-19 08:00 | 3.24 | 4.0755 | N | 0
2025-04-19 | 09 | 2031-04-19 09:00 | 3.48 | 4.3774 | N | 0
2025-04-19 | 10 | 2031-04-19 10:00 | 3.62 | 4.5535 | N | 0
2025-04-19 | 11 | 2031-04-19 11:00 | 3.75 | 4.7171 | N | 0
2025-04-19 | 12 | 2031-04-19 12:00 | 3.72 | 4.6793 | N | 0
2025-04-19 | 13 | 2031-04-19 13:00 | 3.7 | 4.6542 | N | 0
2025-04-19 | 14 | 2031-04-19 14:00 | 3.71 | 4.6667 | N | 0
2025-04-19 | 15 | 2031-04-19 15:00 | 3.71 | 4.6667 | N | 0
2025-04-19 | 16 | 2031-04-19 16:00 | 3.86 | 4.8554 | N | 0
2025-04-19 | 17 | 2031-04-19 17:00 | 3.8 | 4.7799 | N | 0
2025-04-19 | 18 | 2031-04-19 18:00 | 3.72 | 4.6793 | N | 0
2025-04-19 | 19 | 2031-04-19 19:00 | 3.77 | 4.7422 | N | 0
2025-04-19 | 20 | 2031-04-19 20:00 | 3.84 | 4.8303 | N | 0
2025-04-19 | 21 | 2031-04-19 21:00 | 3.67 | 4.6164 | N | 0
2025-04-19 | 22 | 2031-04-19 22:00 | 3.63 | 4.5661 | N | 0
2025-04-19 | 23 | 2031-04-19 23:00 | 3.32 | 4.1762 | N | 0
2025-04-20 | 00 | 2031-04-20 | 3.07 | 3.8617 | N | 0
2025-04-20 | 01 | 2031-04-20 01:00 | 2.78 | 3.4969 | N | 0
2025-04-20 | 02 | 2031-04-20 02:00 | 2.76 | 3.4718 | N | 0
2025-04-20 | 03 | 2031-04-20 03:00 | 2.63 | 3.3082 | N | 0
2025-04-20 | 04 | 2031-04-20 04:00 | 2.68 | 3.3711 | N | 0
2025-04-20 | 05 | 2031-04-20 05:00 | 2.73 | 3.434 | N | 0
2025-04-20 | 06 | 2031-04-20 06:00 | 2.78 | 3.4969 | N | 0
2025-04-20 | 07 | 2031-04-20 07:00 | 3.24 | 4.0755 | N | 0
2025-04-20 | 08 | 2031-04-20 08:00 | 3.49 | 4.39 | N | 0
2025-04-20 | 09 | 2031-04-20 09:00 | 3.6 | 4.5284 | N | 0
2025-04-20 | 10 | 2031-04-20 10:00 | 3.85 | 4.8428 | N | 0
2025-04-20 | 11 | 2031-04-20 11:00 | 3.95 | 4.9686 | N | 0
2025-04-20 | 12 | 2031-04-20 12:00 | 4.07 | 5.1196 | N | 0
2025-04-20 | 13 | 2031-04-20 13:00 | 3.91 | 4.9183 | N | 0
2025-04-20 | 14 | 2031-04-20 14:00 | 3.98 | 5.0064 | N | 0
2025-04-20 | 15 | 2031-04-20 15:00 | 3.95 | 4.9686 | N | 0
2025-04-20 | 16 | 2031-04-20 16:00 | 4.04 | 5.0818 | N | 0
2025-04-20 | 17 | 2031-04-20 17:00 | 3.99 | 5.0189 | N | 0
2025-04-20 | 18 | 2031-04-20 18:00 | 3.82 | 4.8051 | N | 0
2025-04-20 | 19 | 2031-04-20 19:00 | 3.78 | 4.7548 | N | 0
2025-04-20 | 20 | 2031-04-20 20:00 | 3.93 | 4.9435 | N | 0
2025-04-20 | 21 | 2031-04-20 21:00 | 4.02 | 5.0567 | N | 0
2025-04-20 | 22 | 2031-04-20 22:00 | 3.84 | 4.8303 | N | 0
2025-04-20 | 23 | 2031-04-20 23:00 | 3.47 | 4.3648 | N | 0
2025-04-21 | 00 | 2031-04-21 | 3.09 | 3.8869 | N | 0
2025-04-21 | 01 | 2031-04-21 01:00 | 2.84 | 3.5724 | N | 0
2025-04-21 | 02 | 2031-04-21 02:00 | 2.74 | 3.4466 | N | 0
2025-04-21 | 03 | 2031-04-21 03:00 | 2.71 | 3.4089 | N | 0
2025-04-21 | 04 | 2031-04-21 04:00 | 2.82 | 3.5472 | N | 0
2025-04-21 | 05 | 2031-04-21 05:00 | 2.87 | 3.6101 | N | 0
2025-04-21 | 06 | 2031-04-21 06:00 | 3.18 | 4.0001 | N | 0
2025-04-21 | 07 | 2031-04-21 07:00 | 3.54 | 4.4529 | N | 0
2025-04-21 | 08 | 2031-04-21 08:00 | 3.62 | 4.5535 | N | 0
2025-04-21 | 09 | 2031-04-21 09:00 | 3.99 | 5.0189 | N | 0
2025-04-21 | 10 | 2031-04-21 10:00 | 4.2 | 5.2831 | N | 0
2025-04-21 | 11 | 2031-04-21 11:00 | 4.52 | 5.6856 | N | 0
2025-04-21 | 12 | 2031-04-21 12:00 | 4.49 | 5.6479 | N | 0
2025-04-21 | 13 | 2031-04-21 13:00 | 4.5 | 5.6605 | N | 0
2025-04-21 | 14 | 2031-04-21 14:00 | 4.48 | 5.6353 | N | 0
2025-04-21 | 15 | 2031-04-21 15:00 | 4.46 | 5.6102 | N | 0
2025-04-21 | 16 | 2031-04-21 16:00 | 4.83 | 6.0756 | N | 0
2025-04-21 | 17 | 2031-04-21 17:00 | 4.95 | 6.2265 | N | 0
2025-04-21 | 18 | 2031-04-21 18:00 | 4.69 | 5.8995 | N | 0
2025-04-21 | 19 | 2031-04-21 19:00 | 4.32 | 5.434 | N | 0
2025-04-21 | 20 | 2031-04-21 20:00 | 4.44 | 5.585 | N | 0
2025-04-21 | 21 | 2031-04-21 21:00 | 4.26 | 5.3586 | N | 0
2025-04-21 | 22 | 2031-04-21 22:00 | 3.96 | 4.9812 | N | 0
2025-04-21 | 23 | 2031-04-21 23:00 | 3.56 | 4.4781 | N | 0
2025-04-22 | 00 | 2031-04-22 | 2.99 | 3.7611 | N | 0
2025-04-22 | 01 | 2031-04-22 01:00 | 2.76 | 3.4718 | N | 0
2025-04-22 | 02 | 2031-04-22 02:00 | 2.64 | 3.3208 | N | 0
2025-04-22 | 03 | 2031-04-22 03:00 | 2.63 | 3.3082 | N | 0
2025-04-22 | 04 | 2031-04-22 04:00 | 2.65 | 3.3334 | N | 0
2025-04-22 | 05 | 2031-04-22 05:00 | 2.88 | 3.6227 | N | 0
2025-04-22 | 06 | 2031-04-22 06:00 | 3.31 | 4.1636 | N | 0
2025-04-22 | 07 | 2031-04-22 07:00 | 3.68 | 4.629 | N | 0
2025-04-22 | 08 | 2031-04-22 08:00 | 3.87 | 4.868 | N | 0
2025-04-22 | 09 | 2031-04-22 09:00 | 3.84 | 4.8303 | N | 0
2025-04-22 | 10 | 2031-04-22 10:00 | 3.88 | 4.8806 | N | 0
2025-04-22 | 11 | 2031-04-22 11:00 | 3.91 | 4.9183 | N | 0
2025-04-22 | 12 | 2031-04-22 12:00 | 3.92 | 4.9309 | N | 0
2025-04-22 | 13 | 2031-04-22 13:00 | 3.9 | 4.9057 | N | 0
2025-04-22 | 14 | 2031-04-22 14:00 | 3.89 | 4.8932 | N | 0
2025-04-22 | 15 | 2031-04-22 15:00 | 3.79 | 4.7674 | N | 0
2025-04-22 | 16 | 2031-04-22 16:00 | 4.01 | 5.0441 | N | 0
2025-04-22 | 17 | 2031-04-22 17:00 | 4.25 | 5.346 | N | 0
2025-04-22 | 18 | 2031-04-22 18:00 | 4.11 | 5.1699 | N | 0
2025-04-22 | 19 | 2031-04-22 19:00 | 4.02 | 5.0567 | N | 0
2025-04-22 | 20 | 2031-04-22 20:00 | 4.23 | 5.3208 | N | 0
2025-04-22 | 21 | 2031-04-22 21:00 | 4.2 | 5.2831 | N | 0
2025-04-22 | 22 | 2031-04-22 22:00 | 3.89 | 4.8932 | N | 0
2025-04-22 | 23 | 2031-04-22 23:00 | 3.44 | 4.3271 | N | 0
2025-04-23 | 00 | 2031-04-23 | 3.01 | 3.7862 | N | 0
2025-04-23 | 01 | 2031-04-23 01:00 | 2.82 | 3.5472 | N | 0
2025-04-23 | 02 | 2031-04-23 02:00 | 2.69 | 3.3837 | N | 0
2025-04-23 | 03 | 2031-04-23 03:00 | 2.66 | 3.346 | N | 0
2025-04-23 | 04 | 2031-04-23 04:00 | 2.72 | 3.4214 | N | 0
2025-04-23 | 05 | 2031-04-23 05:00 | 3.07 | 3.8617 | N | 0
2025-04-23 | 06 | 2031-04-23 06:00 | 3.38 | 4.2516 | N | 0
2025-04-23 | 07 | 2031-04-23 07:00 | 3.71 | 4.6667 | N | 0
2025-04-23 | 08 | 2031-04-23 08:00 | 3.75 | 4.7171 | N | 0
2025-04-23 | 09 | 2031-04-23 09:00 | 3.79 | 4.7674 | N | 0
2025-04-23 | 10 | 2031-04-23 10:00 | 3.76 | 4.7296 | N | 0
2025-04-23 | 11 | 2031-04-23 11:00 | 3.74 | 4.7045 | N | 0
2025-04-23 | 12 | 2031-04-23 12:00 | 3.77 | 4.7422 | N | 0
2025-04-23 | 13 | 2031-04-23 13:00 | 3.75 | 4.7171 | N | 0
2025-04-23 | 14 | 2031-04-23 14:00 | 3.67 | 4.6164 | N | 0
2025-04-23 | 15 | 2031-04-23 15:00 | 3.76 | 4.7296 | N | 0
2025-04-23 | 16 | 2031-04-23 16:00 | 3.87 | 4.868 | N | 0
2025-04-23 | 17 | 2031-04-23 17:00 | 4.1 | 5.1573 | N | 0
2025-04-23 | 18 | 2031-04-23 18:00 | 4.18 | 5.2579 | N | 0
2025-04-23 | 19 | 2031-04-23 19:00 | 4.18 | 5.2579 | N | 0
2025-04-23 | 20 | 2031-04-23 20:00 | 4.3 | 5.4089 | N | 0
2025-04-23 | 21 | 2031-04-23 21:00 | 4.29 | 5.3963 | N | 0
2025-04-23 | 22 | 2031-04-23 22:00 | 3.85 | 4.8428 | N | 0
2025-04-23 | 23 | 2031-04-23 23:00 | 3.31 | 4.1636 | N | 0
2025-04-24 | 00 | 2031-04-24 | 2.98 | 3.7485 | N | 0
2025-04-24 | 01 | 2031-04-24 01:00 | 2.67 | 3.3585 | N | 0
2025-04-24 | 02 | 2031-04-24 02:00 | 2.62 | 3.2956 | N | 0
2025-04-24 | 03 | 2031-04-24 03:00 | 2.56 | 3.2202 | N | 0
2025-04-24 | 04 | 2031-04-24 04:00 | 2.54 | 3.195 | N | 0
2025-04-24 | 05 | 2031-04-24 05:00 | 2.81 | 3.5346 | N | 0
2025-04-24 | 06 | 2031-04-24 06:00 | 3.07 | 3.8617 | N | 0
2025-04-24 | 07 | 2031-04-24 07:00 | 3.51 | 4.4152 | N | 0
2025-04-24 | 08 | 2031-04-24 08:00 | 3.53 | 4.4403 | N | 0
2025-04-24 | 09 | 2031-04-24 09:00 | 3.72 | 4.6793 | N | 0
2025-04-24 | 10 | 2031-04-24 10:00 | 3.88 | 4.8806 | N | 0
2025-04-24 | 11 | 2031-04-24 11:00 | 3.81 | 4.7925 | N | 0
2025-04-24 | 12 | 2031-04-24 12:00 | 3.77 | 4.7422 | N | 0
2025-04-24 | 13 | 2031-04-24 13:00 | 3.76 | 4.7296 | N | 0
2025-04-24 | 14 | 2031-04-24 14:00 | 3.71 | 4.6667 | N | 0
2025-04-24 | 15 | 2031-04-24 15:00 | 3.66 | 4.6038 | N | 0
2025-04-24 | 16 | 2031-04-24 16:00 | 3.89 | 4.8932 | N | 0
2025-04-24 | 17 | 2031-04-24 17:00 | 4.14 | 5.2076 | N | 0
2025-04-24 | 18 | 2031-04-24 18:00 | 4.17 | 5.2454 | N | 0
2025-04-24 | 19 | 2031-04-24 19:00 | 3.97 | 4.9938 | N | 0
2025-04-24 | 20 | 2031-04-24 20:00 | 4.08 | 5.1322 | N | 0
2025-04-24 | 21 | 2031-04-24 21:00 | 3.99 | 5.0189 | N | 0
2025-04-24 | 22 | 2031-04-24 22:00 | 3.68 | 4.629 | N | 0
2025-04-24 | 23 | 2031-04-24 23:00 | 3.12 | 3.9246 | N | 0
2025-04-25 | 00 | 2031-04-25 | 2.81 | 3.5346 | N | 0
2025-04-25 | 01 | 2031-04-25 01:00 | 2.53 | 3.1824 | N | 0
2025-04-25 | 02 | 2031-04-25 02:00 | 2.38 | 2.9938 | N | 0
2025-04-25 | 03 | 2031-04-25 03:00 | 2.36 | 2.9686 | N | 0
2025-04-25 | 04 | 2031-04-25 04:00 | 2.41 | 3.0315 | N | 0
2025-04-25 | 05 | 2031-04-25 05:00 | 2.62 | 3.2956 | N | 0
2025-04-25 | 06 | 2031-04-25 06:00 | 3.01 | 3.7862 | N | 0
2025-04-25 | 07 | 2031-04-25 07:00 | 3.31 | 4.1636 | N | 0
2025-04-25 | 08 | 2031-04-25 08:00 | 3.55 | 4.4655 | N | 0
2025-04-25 | 09 | 2031-04-25 09:00 | 3.55 | 4.4655 | N | 0
2025-04-25 | 10 | 2031-04-25 10:00 | 3.62 | 4.5535 | N | 0
2025-04-25 | 11 | 2031-04-25 11:00 | 3.79 | 4.7674 | N | 0
2025-04-25 | 12 | 2031-04-25 12:00 | 3.72 | 4.6793 | N | 0
2025-04-25 | 13 | 2031-04-25 13:00 | 3.7 | 4.6542 | N | 0
2025-04-25 | 14 | 2031-04-25 14:00 | 3.72 | 4.6793 | N | 0
2025-04-25 | 15 | 2031-04-25 15:00 | 3.73 | 4.6919 | N | 0
2025-04-25 | 16 | 2031-04-25 16:00 | 3.89 | 4.8932 | N | 0
2025-04-25 | 17 | 2031-04-25 17:00 | 3.93 | 4.9435 | N | 0
2025-04-25 | 18 | 2031-04-25 18:00 | 3.89 | 4.8932 | N | 0
2025-04-25 | 19 | 2031-04-25 19:00 | 3.91 | 4.9183 | N | 0
2025-04-25 | 20 | 2031-04-25 20:00 | 4 | 5.0315 | N | 0
2025-04-25 | 21 | 2031-04-25 21:00 | 3.98 | 5.0064 | N | 0
2025-04-25 | 22 | 2031-04-25 22:00 | 3.68 | 4.629 | N | 0
2025-04-25 | 23 | 2031-04-25 23:00 | 3.24 | 4.0755 | N | 0
2025-04-26 | 00 | 2031-04-26 | 2.91 | 3.6604 | N | 0
2025-04-26 | 01 | 2031-04-26 01:00 | 2.68 | 3.3711 | N | 0
2025-04-26 | 02 | 2031-04-26 02:00 | 2.48 | 3.1195 | N | 0
2025-04-26 | 03 | 2031-04-26 03:00 | 2.37 | 2.9812 | N | 0
2025-04-26 | 04 | 2031-04-26 04:00 | 2.36 | 2.9686 | N | 0
2025-04-26 | 05 | 2031-04-26 05:00 | 2.46 | 3.0944 | N | 0
2025-04-26 | 06 | 2031-04-26 06:00 | 2.58 | 3.2453 | N | 0
2025-04-26 | 07 | 2031-04-26 07:00 | 2.98 | 3.7485 | N | 0
2025-04-26 | 08 | 2031-04-26 08:00 | 3.26 | 4.1007 | N | 0
2025-04-26 | 09 | 2031-04-26 09:00 | 3.56 | 4.4781 | N | 0
2025-04-26 | 10 | 2031-04-26 10:00 | 3.84 | 4.8303 | N | 0
2025-04-26 | 11 | 2031-04-26 11:00 | 3.78 | 4.7548 | N | 0
2025-04-26 | 12 | 2031-04-26 12:00 | 3.82 | 4.8051 | N | 0
2025-04-26 | 13 | 2031-04-26 13:00 | 3.86 | 4.8554 | N | 0
2025-04-26 | 14 | 2031-04-26 14:00 | 3.86 | 4.8554 | N | 0
2025-04-26 | 15 | 2031-04-26 15:00 | 4 | 5.0315 | N | 0
2025-04-26 | 16 | 2031-04-26 16:00 | 3.93 | 4.9435 | N | 0
2025-04-26 | 17 | 2031-04-26 17:00 | 4.21 | 5.2957 | N | 0
2025-04-26 | 18 | 2031-04-26 18:00 | 4.14 | 5.2076 | N | 0
2025-04-26 | 19 | 2031-04-26 19:00 | 4.07 | 5.1196 | N | 0
2025-04-26 | 20 | 2031-04-26 20:00 | 4.07 | 5.1196 | N | 0
2025-04-26 | 21 | 2031-04-26 21:00 | 4.07 | 5.1196 | N | 0
2025-04-26 | 22 | 2031-04-26 22:00 | 3.81 | 4.7925 | N | 0
2025-04-26 | 23 | 2031-04-26 23:00 | 3.49 | 4.39 | N | 0
2025-04-27 | 00 | 2031-04-27 | 3.15 | 3.9623 | N | 0
2025-04-27 | 01 | 2031-04-27 01:00 | 2.85 | 3.585 | N | 0
2025-04-27 | 02 | 2031-04-27 02:00 | 2.72 | 3.4214 | N | 0
2025-04-27 | 03 | 2031-04-27 03:00 | 2.59 | 3.2579 | N | 0
2025-04-27 | 04 | 2031-04-27 04:00 | 2.63 | 3.3082 | N | 0
2025-04-27 | 05 | 2031-04-27 05:00 | 2.7 | 3.3963 | N | 0
2025-04-27 | 06 | 2031-04-27 06:00 | 2.84 | 3.5724 | N | 0
2025-04-27 | 07 | 2031-04-27 07:00 | 3.03 | 3.8114 | N | 0
2025-04-27 | 08 | 2031-04-27 08:00 | 3.39 | 4.2642 | N | 0
2025-04-27 | 09 | 2031-04-27 09:00 | 3.48 | 4.3774 | N | 0
2025-04-27 | 10 | 2031-04-27 10:00 | 3.6 | 4.5284 | N | 0
2025-04-27 | 11 | 2031-04-27 11:00 | 3.66 | 4.6038 | N | 0
2025-04-27 | 12 | 2031-04-27 12:00 | 3.8 | 4.7799 | N | 0
2025-04-27 | 13 | 2031-04-27 13:00 | 3.73 | 4.6919 | N | 0
2025-04-27 | 14 | 2031-04-27 14:00 | 3.59 | 4.5158 | N | 0
2025-04-27 | 15 | 2031-04-27 15:00 | 3.72 | 4.6793 | N | 0
2025-04-27 | 16 | 2031-04-27 16:00 | 3.96 | 4.9812 | N | 0
2025-04-27 | 17 | 2031-04-27 17:00 | 4.19 | 5.2705 | N | 0
2025-04-27 | 18 | 2031-04-27 18:00 | 4.16 | 5.2328 | N | 0
2025-04-27 | 19 | 2031-04-27 19:00 | 4.04 | 5.0818 | N | 0
2025-04-27 | 20 | 2031-04-27 20:00 | 4.14 | 5.2076 | N | 0
2025-04-27 | 21 | 2031-04-27 21:00 | 4.07 | 5.1196 | N | 0
2025-04-27 | 22 | 2031-04-27 22:00 | 3.77 | 4.7422 | N | 0
2025-04-27 | 23 | 2031-04-27 23:00 | 3.3 | 4.151 | N | 0
2025-04-28 | 00 | 2031-04-28 | 2.87 | 3.6101 | N | 0
2025-04-28 | 01 | 2031-04-28 01:00 | 2.6 | 3.2705 | N | 0
2025-04-28 | 02 | 2031-04-28 02:00 | 2.5 | 3.1447 | N | 0
2025-04-28 | 03 | 2031-04-28 03:00 | 2.46 | 3.0944 | N | 0
2025-04-28 | 04 | 2031-04-28 04:00 | 2.51 | 3.1573 | N | 0
2025-04-28 | 05 | 2031-04-28 05:00 | 2.85 | 3.585 | N | 0
2025-04-28 | 06 | 2031-04-28 06:00 | 3.13 | 3.9372 | N | 0
2025-04-28 | 07 | 2031-04-28 07:00 | 3.63 | 4.5661 | N | 0
2025-04-28 | 08 | 2031-04-28 08:00 | 3.52 | 4.4277 | N | 0
2025-04-28 | 09 | 2031-04-28 09:00 | 3.62 | 4.5535 | N | 0
2025-04-28 | 10 | 2031-04-28 10:00 | 3.53 | 4.4403 | N | 0
2025-04-28 | 11 | 2031-04-28 11:00 | 3.55 | 4.4655 | N | 0
2025-04-28 | 12 | 2031-04-28 12:00 | 3.75 | 4.7171 | N | 0
2025-04-28 | 13 | 2031-04-28 13:00 | 3.63 | 4.5661 | N | 0
2025-04-28 | 14 | 2031-04-28 14:00 | 3.55 | 4.4655 | N | 0
2025-04-28 | 15 | 2031-04-28 15:00 | 3.59 | 4.5158 | N | 0
2025-04-28 | 16 | 2031-04-28 16:00 | 3.89 | 4.8932 | N | 0
2025-04-28 | 17 | 2031-04-28 17:00 | 4.24 | 5.3334 | N | 0
2025-04-28 | 18 | 2031-04-28 18:00 | 4.12 | 5.1825 | N | 0
2025-04-28 | 19 | 2031-04-28 19:00 | 3.99 | 5.0189 | N | 0
2025-04-28 | 20 | 2031-04-28 20:00 | 4.22 | 5.3083 | N | 0
2025-04-28 | 21 | 2031-04-28 21:00 | 4.06 | 5.107 | N | 0
2025-04-28 | 22 | 2031-04-28 22:00 | 3.81 | 4.7925 | N | 0
2025-04-28 | 23 | 2031-04-28 23:00 | 3.2 | 4.0252 | N | 0
2025-04-29 | 00 | 2031-04-29 | 2.9 | 3.6479 | N | 0
2025-04-29 | 01 | 2031-04-29 01:00 | 2.68 | 3.3711 | N | 0
2025-04-29 | 02 | 2031-04-29 02:00 | 2.47 | 3.107 | N | 0
2025-04-29 | 03 | 2031-04-29 03:00 | 2.46 | 3.0944 | N | 0
2025-04-29 | 04 | 2031-04-29 04:00 | 2.5 | 3.1447 | N | 0
2025-04-29 | 05 | 2031-04-29 05:00 | 2.7 | 3.3963 | N | 0
2025-04-29 | 06 | 2031-04-29 06:00 | 2.96 | 3.7233 | N | 0
2025-04-29 | 07 | 2031-04-29 07:00 | 3.41 | 4.2894 | N | 0
2025-04-29 | 08 | 2031-04-29 08:00 | 3.53 | 4.4403 | N | 0
2025-04-29 | 09 | 2031-04-29 09:00 | 3.52 | 4.4277 | N | 0
2025-04-29 | 10 | 2031-04-29 10:00 | 3.56 | 4.4781 | N | 0
2025-04-29 | 11 | 2031-04-29 11:00 | 3.69 | 4.6416 | N | 0
2025-04-29 | 12 | 2031-04-29 12:00 | 3.74 | 4.7045 | N | 0
2025-04-29 | 13 | 2031-04-29 13:00 | 3.76 | 4.7296 | N | 0
2025-04-29 | 14 | 2031-04-29 14:00 | 3.67 | 4.6164 | N | 0
2025-04-29 | 15 | 2031-04-29 15:00 | 3.73 | 4.6919 | N | 0
2025-04-29 | 16 | 2031-04-29 16:00 | 3.97 | 4.9938 | N | 0
2025-04-29 | 17 | 2031-04-29 17:00 | 4.3 | 5.4089 | N | 0
2025-04-29 | 18 | 2031-04-29 18:00 | 4.3 | 5.4089 | N | 0
2025-04-29 | 19 | 2031-04-29 19:00 | 4.16 | 5.2328 | N | 0
2025-04-29 | 20 | 2031-04-29 20:00 | 4.14 | 5.2076 | N | 0
2025-04-29 | 21 | 2031-04-29 21:00 | 4.17 | 5.2454 | N | 0
2025-04-29 | 22 | 2031-04-29 22:00 | 2.01 | 2.5283 | N | 0
2025-04-29 | 23 | 2031-04-29 23:00 | 1.73 | 2.1761 | N | 0
2025-04-30 | 00 | 2031-04-30 | 3.8 | 4.7799 | N | 0
2025-04-30 | 01 | 2031-04-30 01:00 | 2.67 | 3.3585 | N | 0
2025-04-30 | 02 | 2031-04-30 02:00 | 2.52 | 3.1699 | N | 0
2025-04-30 | 03 | 2031-04-30 03:00 | 2.5 | 3.1447 | N | 0
2025-04-30 | 04 | 2031-04-30 04:00 | 2.56 | 3.2202 | N | 0
2025-04-30 | 05 | 2031-04-30 05:00 | 2.84 | 3.5724 | N | 0
2025-04-30 | 06 | 2031-04-30 06:00 | 3.25 | 4.0881 | N | 0
2025-04-30 | 07 | 2031-04-30 07:00 | 3.65 | 4.5913 | N | 0
2025-04-30 | 08 | 2031-04-30 08:00 | 3.73 | 4.6919 | N | 0
2025-04-30 | 09 | 2031-04-30 09:00 | 3.78 | 4.7548 | N | 0
2025-04-30 | 10 | 2031-04-30 10:00 | 3.71 | 4.6667 | N | 0
2025-04-30 | 11 | 2031-04-30 11:00 | 3.68 | 4.629 | N | 0
2025-04-30 | 12 | 2031-04-30 12:00 | 3.77 | 4.7422 | N | 0
2025-04-30 | 13 | 2031-04-30 13:00 | 3.7 | 4.6542 | N | 0
2025-04-30 | 14 | 2031-04-30 14:00 | 3.7 | 4.6542 | N | 0
2025-04-30 | 15 | 2031-04-30 15:00 | 3.73 | 4.6919 | N | 0
2025-04-30 | 16 | 2031-04-30 16:00 | 4.02 | 5.0567 | N | 0
2025-04-30 | 17 | 2031-04-30 17:00 | 4.21 | 5.2957 | N | 0
2025-04-30 | 18 | 2031-04-30 18:00 | 4.15 | 5.2202 | N | 0
2025-04-30 | 19 | 2031-04-30 19:00 | 4.14 | 5.2076 | N | 0
2025-04-30 | 20 | 2031-04-30 20:00 | 4.27 | 5.3712 | N | 0
2025-04-30 | 21 | 2031-04-30 21:00 | 4.21 | 5.2957 | N | 0
2025-04-30 | 22 | 2031-04-30 22:00 | 3.93 | 4.9435 | N | 0
2025-04-30 | 23 | 2031-04-30 23:00 | 3.32 | 4.1762 | N | 0
2025-05-01 | 00 | 2031-05-01 | 3.07 | 3.8617 | N | 0
2025-05-01 | 01 | 2031-05-01 01:00 | 2.83 | 3.5598 | N | 0
2025-05-01 | 02 | 2031-05-01 02:00 | 2.58 | 3.2453 | N | 0
2025-05-01 | 03 | 2031-05-01 03:00 | 2.55 | 3.2076 | N | 0
2025-05-01 | 04 | 2031-05-01 04:00 | 2.55 | 3.2076 | N | 0
2025-05-01 | 05 | 2031-05-01 05:00 | 2.83 | 3.5598 | N | 0
2025-05-01 | 06 | 2031-05-01 06:00 | 3.21 | 4.0378 | N | 0
2025-05-01 | 07 | 2031-05-01 07:00 | 3.67 | 4.6164 | N | 0
2025-05-01 | 08 | 2031-05-01 08:00 | 3.63 | 4.5661 | N | 0
2025-05-01 | 09 | 2031-05-01 09:00 | 3.68 | 4.629 | N | 0
2025-05-01 | 10 | 2031-05-01 10:00 | 3.68 | 4.629 | N | 0
2025-05-01 | 11 | 2031-05-01 11:00 | 3.79 | 4.7674 | N | 0
2025-05-01 | 12 | 2031-05-01 12:00 | 3.98 | 5.0064 | N | 0
2025-05-01 | 13 | 2031-05-01 13:00 | 3.92 | 4.9309 | N | 0
2025-05-01 | 14 | 2031-05-01 14:00 | 4.03 | 5.0693 | N | 0
2025-05-01 | 15 | 2031-05-01 15:00 | 4 | 5.0315 | N | 0
2025-05-01 | 16 | 2031-05-01 16:00 | 4.42 | 5.5598 | N | 0
2025-05-01 | 17 | 2031-05-01 17:00 | 4.6 | 5.7863 | N | 0
2025-05-01 | 18 | 2031-05-01 18:00 | 4.49 | 5.6479 | N | 0
2025-05-01 | 19 | 2031-05-01 19:00 | 4.43 | 5.5724 | N | 0
2025-05-01 | 20 | 2031-05-01 20:00 | 4.43 | 5.5724 | N | 0
2025-05-01 | 21 | 2031-05-01 21:00 | 4.38 | 5.5095 | N | 0
2025-05-01 | 22 | 2031-05-01 22:00 | 3.79 | 4.7674 | N | 0
2025-05-01 | 23 | 2031-05-01 23:00 | 3.32 | 4.1762 | N | 0
2025-05-02 | 00 | 2031-05-02 | 3.05 | 3.8365 | N | 0
2025-05-02 | 01 | 2031-05-02 01:00 | 2.79 | 3.5095 | N | 0
2025-05-02 | 02 | 2031-05-02 02:00 | 2.61 | 3.2831 | N | 0
2025-05-02 | 03 | 2031-05-02 03:00 | 2.51 | 3.1573 | N | 0
2025-05-02 | 04 | 2031-05-02 04:00 | 2.48 | 3.1195 | N | 0
2025-05-02 | 05 | 2031-05-02 05:00 | 2.73 | 3.434 | N | 0
2025-05-02 | 06 | 2031-05-02 06:00 | 3.04 | 3.824 | N | 0
2025-05-02 | 07 | 2031-05-02 07:00 | 3.5 | 4.4026 | N | 0
2025-05-02 | 08 | 2031-05-02 08:00 | 3.6 | 4.5284 | N | 0
2025-05-02 | 09 | 2031-05-02 09:00 | 3.62 | 4.5535 | N | 0
2025-05-02 | 10 | 2031-05-02 10:00 | 3.69 | 4.6416 | N | 0
2025-05-02 | 11 | 2031-05-02 11:00 | 3.79 | 4.7674 | N | 0
2025-05-02 | 12 | 2031-05-02 12:00 | 3.78 | 4.7548 | N | 0
2025-05-02 | 13 | 2031-05-02 13:00 | 3.76 | 4.7296 | N | 0
2025-05-02 | 14 | 2031-05-02 14:00 | 3.7 | 4.6542 | N | 0
2025-05-02 | 15 | 2031-05-02 15:00 | 3.78 | 4.7548 | N | 0
2025-05-02 | 16 | 2031-05-02 16:00 | 3.89 | 4.8932 | N | 0
2025-05-02 | 17 | 2031-05-02 17:00 | 3.97 | 4.9938 | N | 0
2025-05-02 | 18 | 2031-05-02 18:00 | 3.91 | 4.9183 | N | 0
2025-05-02 | 19 | 2031-05-02 19:00 | 3.79 | 4.7674 | N | 0
2025-05-02 | 20 | 2031-05-02 20:00 | 3.96 | 4.9812 | N | 0
2025-05-02 | 21 | 2031-05-02 21:00 | 3.89 | 4.8932 | N | 0
2025-05-02 | 22 | 2031-05-02 22:00 | 3.67 | 4.6164 | N | 0
2025-05-02 | 23 | 2031-05-02 23:00 | 3.31 | 4.1636 | N | 0
2025-05-03 | 00 | 2031-05-03 | 2.94 | 3.6982 | N | 0
2025-05-03 | 01 | 2031-05-03 01:00 | 2.67 | 3.3585 | N | 0
2025-05-03 | 02 | 2031-05-03 02:00 | 2.44 | 3.0692 | N | 0
2025-05-03 | 03 | 2031-05-03 03:00 | 2.41 | 3.0315 | N | 0
2025-05-03 | 04 | 2031-05-03 04:00 | 2.38 | 2.9938 | N | 0
2025-05-03 | 05 | 2031-05-03 05:00 | 2.46 | 3.0944 | N | 0
2025-05-03 | 06 | 2031-05-03 06:00 | 2.6 | 3.2705 | N | 0
2025-05-03 | 07 | 2031-05-03 07:00 | 2.95 | 3.7108 | N | 0
2025-05-03 | 08 | 2031-05-03 08:00 | 3.5 | 4.4026 | N | 0
2025-05-03 | 09 | 2031-05-03 09:00 | 3.57 | 4.4906 | N | 0
2025-05-03 | 10 | 2031-05-03 10:00 | 3.73 | 4.6919 | N | 0
2025-05-03 | 11 | 2031-05-03 11:00 | 3.89 | 4.8932 | N | 0
2025-05-03 | 12 | 2031-05-03 12:00 | 3.96 | 4.9812 | N | 0
2025-05-03 | 13 | 2031-05-03 13:00 | 3.78 | 4.7548 | N | 0
2025-05-03 | 14 | 2031-05-03 14:00 | 3.61 | 4.541 | N | 0
2025-05-03 | 15 | 2031-05-03 15:00 | 3.81 | 4.7925 | N | 0
2025-05-03 | 16 | 2031-05-03 16:00 | 3.92 | 4.9309 | N | 0
2025-05-03 | 17 | 2031-05-03 17:00 | 4.14 | 5.2076 | N | 0
2025-05-03 | 18 | 2031-05-03 18:00 | 4.03 | 5.0693 | N | 0
2025-05-03 | 19 | 2031-05-03 19:00 | 3.87 | 4.868 | N | 0
2025-05-03 | 20 | 2031-05-03 20:00 | 3.88 | 4.8806 | N | 0
2025-05-03 | 21 | 2031-05-03 21:00 | 3.89 | 4.8932 | N | 0
2025-05-03 | 22 | 2031-05-03 22:00 | 3.57 | 4.4906 | N | 0
2025-05-03 | 23 | 2031-05-03 23:00 | 3.38 | 4.2516 | N | 0
2025-05-04 | 00 | 2031-05-04 | 3.06 | 3.8491 | N | 0
2025-05-04 | 01 | 2031-05-04 01:00 | 2.81 | 3.5346 | N | 0
2025-05-04 | 02 | 2031-05-04 02:00 | 2.61 | 3.2831 | N | 0
2025-05-04 | 03 | 2031-05-04 03:00 | 2.52 | 3.1699 | N | 0
2025-05-04 | 04 | 2031-05-04 04:00 | 2.52 | 3.1699 | N | 0
2025-05-04 | 05 | 2031-05-04 05:00 | 2.51 | 3.1573 | N | 0
2025-05-04 | 06 | 2031-05-04 06:00 | 2.66 | 3.346 | N | 0
2025-05-04 | 07 | 2031-05-04 07:00 | 2.92 | 3.673 | N | 0
2025-05-04 | 08 | 2031-05-04 08:00 | 3.23 | 4.063 | N | 0
2025-05-04 | 09 | 2031-05-04 09:00 | 3.49 | 4.39 | N | 0
2025-05-04 | 10 | 2031-05-04 10:00 | 3.61 | 4.541 | N | 0
2025-05-04 | 11 | 2031-05-04 11:00 | 3.63 | 4.5661 | N | 0
2025-05-04 | 12 | 2031-05-04 12:00 | 3.8 | 4.7799 | N | 0
2025-05-04 | 13 | 2031-05-04 13:00 | 3.81 | 4.7925 | N | 0
2025-05-04 | 14 | 2031-05-04 14:00 | 3.83 | 4.8177 | N | 0
2025-05-04 | 15 | 2031-05-04 15:00 | 3.87 | 4.868 | N | 0
2025-05-04 | 16 | 2031-05-04 16:00 | 4.14 | 5.2076 | N | 0
2025-05-04 | 17 | 2031-05-04 17:00 | 4.31 | 5.4215 | N | 0
2025-05-04 | 18 | 2031-05-04 18:00 | 4.16 | 5.2328 | N | 0
2025-05-04 | 19 | 2031-05-04 19:00 | 4.2 | 5.2831 | N | 0
2025-05-04 | 20 | 2031-05-04 20:00 | 4.01 | 5.0441 | N | 0
2025-05-04 | 21 | 2031-05-04 21:00 | 4.02 | 5.0567 | N | 0
2025-05-04 | 22 | 2031-05-04 22:00 | 3.65 | 4.5913 | N | 0
2025-05-04 | 23 | 2031-05-04 23:00 | 3.25 | 4.0881 | N | 0
2025-05-05 | 00 | 2031-05-05 | 2.78 | 3.4969 | N | 0
2025-05-05 | 01 | 2031-05-05 01:00 | 2.53 | 3.1824 | N | 0
2025-05-05 | 02 | 2031-05-05 02:00 | 2.35 | 2.956 | N | 0
2025-05-05 | 03 | 2031-05-05 03:00 | 2.35 | 2.956 | N | 0
2025-05-05 | 04 | 2031-05-05 04:00 | 2.39 | 3.0063 | N | 0
2025-05-05 | 05 | 2031-05-05 05:00 | 2.58 | 3.2453 | N | 0
2025-05-05 | 06 | 2031-05-05 06:00 | 3.01 | 3.7862 | N | 0
2025-05-05 | 07 | 2031-05-05 07:00 | 3.29 | 4.1384 | N | 0
2025-05-05 | 08 | 2031-05-05 08:00 | 3.51 | 4.4152 | N | 0
2025-05-05 | 09 | 2031-05-05 09:00 | 3.55 | 4.4655 | N | 0
2025-05-05 | 10 | 2031-05-05 10:00 | 3.63 | 4.5661 | N | 0
2025-05-05 | 11 | 2031-05-05 11:00 | 3.78 | 4.7548 | N | 0
2025-05-05 | 12 | 2031-05-05 12:00 | 3.82 | 4.8051 | N | 0
2025-05-05 | 13 | 2031-05-05 13:00 | 3.79 | 4.7674 | N | 0
2025-05-05 | 14 | 2031-05-05 14:00 | 3.81 | 4.7925 | N | 0
2025-05-05 | 15 | 2031-05-05 15:00 | 3.92 | 4.9309 | N | 0
2025-05-05 | 16 | 2031-05-05 16:00 | 4.09 | 5.1447 | N | 0
2025-05-05 | 17 | 2031-05-05 17:00 | 4.39 | 5.5221 | N | 0
2025-05-05 | 18 | 2031-05-05 18:00 | 4.26 | 5.3586 | N | 0
2025-05-05 | 19 | 2031-05-05 19:00 | 4.15 | 5.2202 | N | 0
2025-05-05 | 20 | 2031-05-05 20:00 | 4.21 | 5.2957 | N | 0
2025-05-05 | 21 | 2031-05-05 21:00 | 4.1 | 5.1573 | N | 0
2025-05-05 | 22 | 2031-05-05 22:00 | 3.81 | 4.7925 | N | 0
2025-05-05 | 23 | 2031-05-05 23:00 | 3.2 | 4.0252 | N | 0
2025-05-06 | 00 | 2031-05-06 | 2.84 | 3.5724 | N | 0
2025-05-06 | 01 | 2031-05-06 01:00 | 2.51 | 3.1573 | N | 0
2025-05-06 | 02 | 2031-05-06 02:00 | 2.41 | 3.0315 | N | 0
2025-05-06 | 03 | 2031-05-06 03:00 | 2.3 | 2.8931 | N | 0
2025-05-06 | 04 | 2031-05-06 04:00 | 2.33 | 2.9309 | N | 0
2025-05-06 | 05 | 2031-05-06 05:00 | 2.5 | 3.1447 | N | 0
2025-05-06 | 06 | 2031-05-06 06:00 | 2.98 | 3.7485 | N | 0
2025-05-06 | 07 | 2031-05-06 07:00 | 3.3 | 4.151 | N | 0
2025-05-06 | 08 | 2031-05-06 08:00 | 3.58 | 4.5032 | N | 0
2025-05-06 | 09 | 2031-05-06 09:00 | 3.69 | 4.6416 | N | 0
2025-05-06 | 10 | 2031-05-06 10:00 | 3.68 | 4.629 | N | 0
2025-05-06 | 11 | 2031-05-06 11:00 | 3.59 | 4.5158 | N | 0
2025-05-06 | 12 | 2031-05-06 12:00 | 3.7 | 4.6542 | N | 0
2025-05-06 | 13 | 2031-05-06 13:00 | 3.7 | 4.6542 | N | 0
2025-05-06 | 14 | 2031-05-06 14:00 | 3.62 | 4.5535 | N | 0
2025-05-06 | 15 | 2031-05-06 15:00 | 3.72 | 4.6793 | N | 0
2025-05-06 | 16 | 2031-05-06 16:00 | 3.89 | 4.8932 | N | 0
2025-05-06 | 17 | 2031-05-06 17:00 | 4.12 | 5.1825 | N | 0
2025-05-06 | 18 | 2031-05-06 18:00 | 4.13 | 5.1951 | N | 0
2025-05-06 | 19 | 2031-05-06 19:00 | 4.07 | 5.1196 | N | 0
2025-05-06 | 20 | 2031-05-06 20:00 | 4.1 | 5.1573 | N | 0
2025-05-06 | 21 | 2031-05-06 21:00 | 4.06 | 5.107 | N | 0
2025-05-06 | 22 | 2031-05-06 22:00 | 3.69 | 4.6416 | N | 0
2025-05-06 | 23 | 2031-05-06 23:00 | 3.15 | 3.9623 | N | 0
2025-05-07 | 00 | 2031-05-07 | 2.78 | 3.4969 | N | 0
2025-05-07 | 01 | 2031-05-07 01:00 | 2.45 | 3.0818 | N | 0
2025-05-07 | 02 | 2031-05-07 02:00 | 2.38 | 2.9938 | N | 0
2025-05-07 | 03 | 2031-05-07 03:00 | 2.28 | 2.868 | N | 0
2025-05-07 | 04 | 2031-05-07 04:00 | 2.31 | 2.9057 | N | 0
2025-05-07 | 05 | 2031-05-07 05:00 | 2.46 | 3.0944 | N | 0
2025-05-07 | 06 | 2031-05-07 06:00 | 2.85 | 3.585 | N | 0
2025-05-07 | 07 | 2031-05-07 07:00 | 3.19 | 4.0126 | N | 0
2025-05-07 | 08 | 2031-05-07 08:00 | 3.38 | 4.2516 | N | 0
2025-05-07 | 09 | 2031-05-07 09:00 | 3.5 | 4.4026 | N | 0
2025-05-07 | 10 | 2031-05-07 10:00 | 3.57 | 4.4906 | N | 0
2025-05-07 | 11 | 2031-05-07 11:00 | 3.65 | 4.5913 | N | 0
2025-05-07 | 12 | 2031-05-07 12:00 | 3.67 | 4.6164 | N | 0
2025-05-07 | 13 | 2031-05-07 13:00 | 3.68 | 4.629 | N | 0
2025-05-07 | 14 | 2031-05-07 14:00 | 3.64 | 4.5787 | N | 0
2025-05-07 | 15 | 2031-05-07 15:00 | 3.91 | 4.9183 | N | 0
2025-05-07 | 16 | 2031-05-07 16:00 | 4.02 | 5.0567 | N | 0
2025-05-07 | 17 | 2031-05-07 17:00 | 4.31 | 5.4215 | N | 0
2025-05-07 | 18 | 2031-05-07 18:00 | 4.2 | 5.2831 | N | 0
2025-05-07 | 19 | 2031-05-07 19:00 | 4.14 | 5.2076 | N | 0
2025-05-07 | 20 | 2031-05-07 20:00 | 4.34 | 5.4592 | N | 0
2025-05-07 | 21 | 2031-05-07 21:00 | 4.34 | 5.4592 | N | 0
2025-05-07 | 22 | 2031-05-07 22:00 | 3.75 | 4.7171 | N | 0
2025-05-07 | 23 | 2031-05-07 23:00 | 3.18 | 4.0001 | N | 0
2025-05-08 | 00 | 2031-05-08 | 2.85 | 3.585 | N | 0
2025-05-08 | 01 | 2031-05-08 01:00 | 2.49 | 3.1321 | N | 0
2025-05-08 | 02 | 2031-05-08 02:00 | 2.42 | 3.0441 | N | 0
2025-05-08 | 03 | 2031-05-08 03:00 | 2.34 | 2.9434 | N | 0
2025-05-08 | 04 | 2031-05-08 04:00 | 2.39 | 3.0063 | N | 0
2025-05-08 | 05 | 2031-05-08 05:00 | 2.55 | 3.2076 | N | 0
2025-05-08 | 06 | 2031-05-08 06:00 | 2.97 | 3.7359 | N | 0
2025-05-08 | 07 | 2031-05-08 07:00 | 3.24 | 4.0755 | N | 0
2025-05-08 | 08 | 2031-05-08 08:00 | 3.49 | 4.39 | N | 0
2025-05-08 | 09 | 2031-05-08 09:00 | 3.5 | 4.4026 | N | 0
2025-05-08 | 10 | 2031-05-08 10:00 | 3.75 | 4.7171 | N | 0
2025-05-08 | 11 | 2031-05-08 11:00 | 3.7 | 4.6542 | N | 0
2025-05-08 | 12 | 2031-05-08 12:00 | 3.84 | 4.8303 | N | 0
2025-05-08 | 13 | 2031-05-08 13:00 | 3.76 | 4.7296 | N | 0
2025-05-08 | 14 | 2031-05-08 14:00 | 3.7 | 4.6542 | N | 0
2025-05-08 | 15 | 2031-05-08 15:00 | 3.7 | 4.6542 | N | 0
2025-05-08 | 16 | 2031-05-08 16:00 | 2.39 | 3.0063 | N | 0
2025-05-08 | 17 | 2031-05-08 17:00 | 4.54 | 5.7108 | N | 0
2025-05-08 | 18 | 2031-05-08 18:00 | 4.12 | 5.1825 | N | 0
2025-05-08 | 19 | 2031-05-08 19:00 | 4.09 | 5.1447 | N | 0
2025-05-08 | 20 | 2031-05-08 20:00 | 4.06 | 5.107 | N | 0
2025-05-08 | 21 | 2031-05-08 21:00 | 4.18 | 5.2579 | N | 0
2025-05-08 | 22 | 2031-05-08 22:00 | 3.8 | 4.7799 | N | 0
2025-05-08 | 23 | 2031-05-08 23:00 | 3.26 | 4.1007 | N | 0
2025-05-09 | 00 | 2031-05-09 | 2.86 | 3.5975 | N | 0
2025-05-09 | 01 | 2031-05-09 01:00 | 2.67 | 3.3585 | N | 0
2025-05-09 | 02 | 2031-05-09 02:00 | 2.55 | 3.2076 | N | 0
2025-05-09 | 03 | 2031-05-09 03:00 | 2.46 | 3.0944 | N | 0
2025-05-09 | 04 | 2031-05-09 04:00 | 2.53 | 3.1824 | N | 0
2025-05-09 | 05 | 2031-05-09 05:00 | 2.8 | 3.5221 | N | 0
2025-05-09 | 06 | 2031-05-09 06:00 | 3.12 | 3.9246 | N | 0
2025-05-09 | 07 | 2031-05-09 07:00 | 3.51 | 4.4152 | N | 0
2025-05-09 | 08 | 2031-05-09 08:00 | 3.5 | 4.4026 | N | 0
2025-05-09 | 09 | 2031-05-09 09:00 | 3.62 | 4.5535 | N | 0
2025-05-09 | 10 | 2031-05-09 10:00 | 3.58 | 4.5032 | N | 0
2025-05-09 | 11 | 2031-05-09 11:00 | 3.67 | 4.6164 | N | 0
2025-05-09 | 12 | 2031-05-09 12:00 | 3.81 | 4.7925 | N | 0
2025-05-09 | 13 | 2031-05-09 13:00 | 3.69 | 4.6416 | N | 0
2025-05-09 | 14 | 2031-05-09 14:00 | 3.55 | 4.4655 | N | 0
2025-05-09 | 15 | 2031-05-09 15:00 | 3.62 | 4.5535 | N | 0
2025-05-09 | 16 | 2031-05-09 16:00 | 3.9 | 4.9057 | N | 0
2025-05-09 | 17 | 2031-05-09 17:00 | 4.01 | 5.0441 | N | 0
2025-05-09 | 18 | 2031-05-09 18:00 | 3.96 | 4.9812 | N | 0
2025-05-09 | 19 | 2031-05-09 19:00 | 3.86 | 4.8554 | N | 0
2025-05-09 | 20 | 2031-05-09 20:00 | 3.96 | 4.9812 | N | 0
2025-05-09 | 21 | 2031-05-09 21:00 | 4.01 | 5.0441 | N | 0
2025-05-09 | 22 | 2031-05-09 22:00 | 3.77 | 4.7422 | N | 0
2025-05-09 | 23 | 2031-05-09 23:00 | 3.38 | 4.2516 | N | 0
2025-05-10 | 00 | 2031-05-10 | 3.05 | 3.8365 | N | 0
2025-05-10 | 01 | 2031-05-10 01:00 | 2.79 | 3.5095 | N | 0
2025-05-10 | 02 | 2031-05-10 02:00 | 2.62 | 3.2956 | N | 0
2025-05-10 | 03 | 2031-05-10 03:00 | 2.5 | 3.1447 | N | 0
2025-05-10 | 04 | 2031-05-10 04:00 | 2.5 | 3.1447 | N | 0
2025-05-10 | 05 | 2031-05-10 05:00 | 2.56 | 3.2202 | N | 0
2025-05-10 | 06 | 2031-05-10 06:00 | 2.61 | 3.2831 | N | 0
2025-05-10 | 07 | 2031-05-10 07:00 | 2.88 | 3.6227 | N | 0
2025-05-10 | 08 | 2031-05-10 08:00 | 3.32 | 4.1762 | N | 0
2025-05-10 | 09 | 2031-05-10 09:00 | 3.37 | 4.2391 | N | 0
2025-05-10 | 10 | 2031-05-10 10:00 | 3.48 | 4.3774 | N | 0
2025-05-10 | 11 | 2031-05-10 11:00 | 3.52 | 4.4277 | N | 0
2025-05-10 | 12 | 2031-05-10 12:00 | 3.56 | 4.4781 | N | 0
2025-05-10 | 13 | 2031-05-10 13:00 | 3.62 | 4.5535 | N | 0
2025-05-10 | 14 | 2031-05-10 14:00 | 3.42 | 4.302 | N | 0
2025-05-10 | 15 | 2031-05-10 15:00 | 3.46 | 4.3523 | N | 0
2025-05-10 | 16 | 2031-05-10 16:00 | 3.6 | 4.5284 | N | 0
2025-05-10 | 17 | 2031-05-10 17:00 | 3.69 | 4.6416 | N | 0
2025-05-10 | 18 | 2031-05-10 18:00 | 3.8 | 4.7799 | N | 0
2025-05-10 | 19 | 2031-05-10 19:00 | 3.7 | 4.6542 | N | 0
2025-05-10 | 20 | 2031-05-10 20:00 | 3.66 | 4.6038 | N | 0
2025-05-10 | 21 | 2031-05-10 21:00 | 3.72 | 4.6793 | N | 0
2025-05-10 | 22 | 2031-05-10 22:00 | 3.51 | 4.4152 | N | 0
2025-05-10 | 23 | 2031-05-10 23:00 | 3.13 | 3.9372 | N | 0
2025-05-11 | 00 | 2031-05-11 | 2.9 | 3.6479 | N | 0
2025-05-11 | 01 | 2031-05-11 01:00 | 2.64 | 3.3208 | N | 0
2025-05-11 | 02 | 2031-05-11 02:00 | 2.42 | 3.0441 | N | 0
2025-05-11 | 03 | 2031-05-11 03:00 | 2.33 | 2.9309 | N | 0
2025-05-11 | 04 | 2031-05-11 04:00 | 2.28 | 2.868 | N | 0
2025-05-11 | 05 | 2031-05-11 05:00 | 2.38 | 2.9938 | N | 0
2025-05-11 | 06 | 2031-05-11 06:00 | 2.5 | 3.1447 | N | 0
2025-05-11 | 07 | 2031-05-11 07:00 | 2.77 | 3.4843 | N | 0
2025-05-11 | 08 | 2031-05-11 08:00 | 3.23 | 4.063 | N | 0
2025-05-11 | 09 | 2031-05-11 09:00 | 3.35 | 4.2139 | N | 0
2025-05-11 | 10 | 2031-05-11 10:00 | 3.53 | 4.4403 | N | 0
2025-05-11 | 11 | 2031-05-11 11:00 | 3.54 | 4.4529 | N | 0
2025-05-11 | 12 | 2031-05-11 12:00 | 3.56 | 4.4781 | N | 0
2025-05-11 | 13 | 2031-05-11 13:00 | 3.65 | 4.5913 | N | 0
2025-05-11 | 14 | 2031-05-11 14:00 | 3.4 | 4.2768 | N | 0
2025-05-11 | 15 | 2031-05-11 15:00 | 3.51 | 4.4152 | N | 0
2025-05-11 | 16 | 2031-05-11 16:00 | 3.75 | 4.7171 | N | 0
2025-05-11 | 17 | 2031-05-11 17:00 | 3.96 | 4.9812 | N | 0
2025-05-11 | 18 | 2031-05-11 18:00 | 3.95 | 4.9686 | N | 0
2025-05-11 | 19 | 2031-05-11 19:00 | 4 | 5.0315 | N | 0
2025-05-11 | 20 | 2031-05-11 20:00 | 4.03 | 5.0693 | N | 0
2025-05-11 | 21 | 2031-05-11 21:00 | 4.02 | 5.0567 | N | 0
2025-05-11 | 22 | 2031-05-11 22:00 | 3.8 | 4.7799 | N | 0
2025-05-11 | 23 | 2031-05-11 23:00 | 3.37 | 4.2391 | N | 0
2025-05-12 | 00 | 2031-05-12 | 2.89 | 3.6353 | N | 0
2025-05-12 | 01 | 2031-05-12 01:00 | 2.64 | 3.3208 | N | 0
2025-05-12 | 02 | 2031-05-12 02:00 | 2.56 | 3.2202 | N | 0
2025-05-12 | 03 | 2031-05-12 03:00 | 2.51 | 3.1573 | N | 0
2025-05-12 | 04 | 2031-05-12 04:00 | 2.5 | 3.1447 | N | 0
2025-05-12 | 05 | 2031-05-12 05:00 | 2.73 | 3.434 | N | 0
2025-05-12 | 06 | 2031-05-12 06:00 | 3.11 | 3.912 | N | 0
2025-05-12 | 07 | 2031-05-12 07:00 | 3.45 | 4.3397 | N | 0
2025-05-12 | 08 | 2031-05-12 08:00 | 3.55 | 4.4655 | N | 0
2025-05-12 | 09 | 2031-05-12 09:00 | 3.5 | 4.4026 | N | 0
2025-05-12 | 10 | 2031-05-12 10:00 | 3.59 | 4.5158 | N | 0
2025-05-12 | 11 | 2031-05-12 11:00 | 3.62 | 4.5535 | N | 0
2025-05-12 | 12 | 2031-05-12 12:00 | 3.73 | 4.6919 | N | 0
2025-05-12 | 13 | 2031-05-12 13:00 | 3.74 | 4.7045 | N | 0
2025-05-12 | 14 | 2031-05-12 14:00 | 3.69 | 4.6416 | N | 0
2025-05-12 | 15 | 2031-05-12 15:00 | 3.77 | 4.7422 | N | 0
2025-05-12 | 16 | 2031-05-12 16:00 | 4.02 | 5.0567 | N | 0
2025-05-12 | 17 | 2031-05-12 17:00 | 4.28 | 5.3837 | N | 0
2025-05-12 | 18 | 2031-05-12 18:00 | 4.29 | 5.3963 | N | 0
2025-05-12 | 19 | 2031-05-12 19:00 | 4.2 | 5.2831 | N | 0
2025-05-12 | 20 | 2031-05-12 20:00 | 4.07 | 5.1196 | N | 0
2025-05-12 | 21 | 2031-05-12 21:00 | 4.06 | 5.107 | N | 0
2025-05-12 | 22 | 2031-05-12 22:00 | 3.8 | 4.7799 | N | 0
2025-05-12 | 23 | 2031-05-12 23:00 | 3.14 | 3.9497 | N | 0
2025-05-13 | 00 | 2031-05-13 | 2.72 | 3.4214 | N | 0
2025-05-13 | 01 | 2031-05-13 01:00 | 2.51 | 3.1573 | N | 0
2025-05-13 | 02 | 2031-05-13 02:00 | 2.39 | 3.0063 | N | 0
2025-05-13 | 03 | 2031-05-13 03:00 | 2.35 | 2.956 | N | 0
2025-05-13 | 04 | 2031-05-13 04:00 | 2.33 | 2.9309 | N | 0
2025-05-13 | 05 | 2031-05-13 05:00 | 2.49 | 3.1321 | N | 0
2025-05-13 | 06 | 2031-05-13 06:00 | 2.9 | 3.6479 | N | 0
2025-05-13 | 07 | 2031-05-13 07:00 | 3.25 | 4.0881 | N | 0
2025-05-13 | 08 | 2031-05-13 08:00 | 3.38 | 4.2516 | N | 0
2025-05-13 | 09 | 2031-05-13 09:00 | 3.51 | 4.4152 | N | 0
2025-05-13 | 10 | 2031-05-13 10:00 | 3.52 | 4.4277 | N | 0
2025-05-13 | 11 | 2031-05-13 11:00 | 3.72 | 4.6793 | N | 0
2025-05-13 | 12 | 2031-05-13 12:00 | 3.77 | 4.7422 | N | 0
2025-05-13 | 13 | 2031-05-13 13:00 | 3.89 | 4.8932 | N | 0
2025-05-13 | 14 | 2031-05-13 14:00 | 3.84 | 4.8303 | N | 0
2025-05-13 | 15 | 2031-05-13 15:00 | 4 | 5.0315 | N | 0
2025-05-13 | 16 | 2031-05-13 16:00 | 4.46 | 5.6102 | N | 0
2025-05-13 | 17 | 2031-05-13 17:00 | 4.6 | 5.7863 | N | 0
2025-05-13 | 18 | 2031-05-13 18:00 | 4.6 | 5.7863 | N | 0
2025-05-13 | 19 | 2031-05-13 19:00 | 4.32 | 5.434 | N | 0
2025-05-13 | 20 | 2031-05-13 20:00 | 4.2 | 5.2831 | N | 0
2025-05-13 | 21 | 2031-05-13 21:00 | 4.21 | 5.2957 | N | 0
2025-05-13 | 22 | 2031-05-13 22:00 | 3.8 | 4.7799 | N | 0
2025-05-13 | 23 | 2031-05-13 23:00 | 3.19 | 4.0126 | N | 0
2025-05-14 | 00 | 2031-05-14 | 2.82 | 3.5472 | N | 0
2025-05-14 | 01 | 2031-05-14 01:00 | 2.6 | 3.2705 | N | 0
2025-05-14 | 02 | 2031-05-14 02:00 | 2.45 | 3.0818 | N | 0
2025-05-14 | 03 | 2031-05-14 03:00 | 2.35 | 2.956 | N | 0
2025-05-14 | 04 | 2031-05-14 04:00 | 2.35 | 2.956 | N | 0
2025-05-14 | 05 | 2031-05-14 05:00 | 2.49 | 3.1321 | N | 0
2025-05-14 | 06 | 2031-05-14 06:00 | 2.88 | 3.6227 | N | 0
2025-05-14 | 07 | 2031-05-14 07:00 | 3.28 | 4.1259 | N | 0
2025-05-14 | 08 | 2031-05-14 08:00 | 3.5 | 4.4026 | N | 0
2025-05-14 | 09 | 2031-05-14 09:00 | 3.58 | 4.5032 | N | 0
2025-05-14 | 10 | 2031-05-14 10:00 | 3.73 | 4.6919 | N | 0
2025-05-14 | 11 | 2031-05-14 11:00 | 3.86 | 4.8554 | N | 0
2025-05-14 | 12 | 2031-05-14 12:00 | 3.79 | 4.7674 | N | 0
2025-05-14 | 13 | 2031-05-14 13:00 | 3.91 | 4.9183 | N | 0
2025-05-14 | 14 | 2031-05-14 14:00 | 3.86 | 4.8554 | N | 0
2025-05-14 | 15 | 2031-05-14 15:00 | 3.78 | 4.7548 | N | 0
2025-05-14 | 16 | 2031-05-14 16:00 | 4.06 | 5.107 | N | 0
2025-05-14 | 17 | 2031-05-14 17:00 | 4.36 | 5.4844 | N | 0
2025-05-14 | 18 | 2031-05-14 18:00 | 4.34 | 5.4592 | N | 0
2025-05-14 | 19 | 2031-05-14 19:00 | 4.28 | 5.3837 | N | 0
2025-05-14 | 20 | 2031-05-14 20:00 | 4.2 | 5.2831 | N | 0
2025-05-14 | 21 | 2031-05-14 21:00 | 4.21 | 5.2957 | N | 0
2025-05-14 | 22 | 2031-05-14 22:00 | 3.75 | 4.7171 | N | 0
2025-05-14 | 23 | 2031-05-14 23:00 | 3.13 | 3.9372 | N | 0
2025-05-15 | 00 | 2031-05-15 | 2.86 | 3.5975 | N | 0
2025-05-15 | 01 | 2031-05-15 01:00 | 2.49 | 3.1321 | N | 0
2025-05-15 | 02 | 2031-05-15 02:00 | 2.42 | 3.0441 | N | 0
2025-05-15 | 03 | 2031-05-15 03:00 | 2.31 | 2.9057 | N | 0
2025-05-15 | 04 | 2031-05-15 04:00 | 2.29 | 2.8805 | N | 0
2025-05-15 | 05 | 2031-05-15 05:00 | 2.52 | 3.1699 | N | 0
2025-05-15 | 06 | 2031-05-15 06:00 | 2.8 | 3.5221 | N | 0
2025-05-15 | 07 | 2031-05-15 07:00 | 3.34 | 4.2013 | N | 0
2025-05-15 | 08 | 2031-05-15 08:00 | 3.43 | 4.3145 | N | 0
2025-05-15 | 09 | 2031-05-15 09:00 | 3.53 | 4.4403 | N | 0
2025-05-15 | 10 | 2031-05-15 10:00 | 3.64 | 4.5787 | N | 0
2025-05-15 | 11 | 2031-05-15 11:00 | 3.8 | 4.7799 | N | 0
2025-05-15 | 12 | 2031-05-15 12:00 | 3.86 | 4.8554 | N | 0
2025-05-15 | 13 | 2031-05-15 13:00 | 3.89 | 4.8932 | N | 0
2025-05-15 | 14 | 2031-05-15 14:00 | 4.1 | 5.1573 | N | 0
2025-05-15 | 15 | 2031-05-15 15:00 | 4.13 | 5.1951 | N | 0
2025-05-15 | 16 | 2031-05-15 16:00 | 4.48 | 5.6353 | N | 0
2025-05-15 | 17 | 2031-05-15 17:00 | 4.81 | 6.0504 | N | 0
2025-05-15 | 18 | 2031-05-15 18:00 | 4.8 | 6.0378 | N | 0
2025-05-15 | 19 | 2031-05-15 19:00 | 4.6 | 5.7863 | N | 0
2025-05-15 | 20 | 2031-05-15 20:00 | 4.61 | 5.7988 | N | 0
2025-05-15 | 21 | 2031-05-15 21:00 | 4.45 | 5.5976 | N | 0
2025-05-15 | 22 | 2031-05-15 22:00 | 4.13 | 5.1951 | N | 0
2025-05-15 | 23 | 2031-05-15 23:00 | 3.54 | 4.4529 | N | 0
2025-05-16 | 00 | 2031-05-16 | 3.07 | 3.8617 | N | 0
2025-05-16 | 01 | 2031-05-16 01:00 | 2.67 | 3.3585 | N | 0
2025-05-16 | 02 | 2031-05-16 02:00 | 2.43 | 3.0567 | N | 0
2025-05-16 | 03 | 2031-05-16 03:00 | 2.37 | 2.9812 | N | 0
2025-05-16 | 04 | 2031-05-16 04:00 | 2.38 | 2.9938 | N | 0
2025-05-16 | 05 | 2031-05-16 05:00 | 2.45 | 3.0818 | N | 0
2025-05-16 | 06 | 2031-05-16 06:00 | 2.84 | 3.5724 | N | 0
2025-05-16 | 07 | 2031-05-16 07:00 | 3.36 | 4.2265 | N | 0
2025-05-16 | 08 | 2031-05-16 08:00 | 3.44 | 4.3271 | N | 0
2025-05-16 | 09 | 2031-05-16 09:00 | 3.67 | 4.6164 | N | 0
2025-05-16 | 10 | 2031-05-16 10:00 | 3.94 | 4.9561 | N | 0
2025-05-16 | 11 | 2031-05-16 11:00 | 4.23 | 5.3208 | N | 0
2025-05-16 | 12 | 2031-05-16 12:00 | 4.29 | 5.3963 | N | 0
2025-05-16 | 13 | 2031-05-16 13:00 | 4.4 | 5.5347 | N | 0
2025-05-16 | 14 | 2031-05-16 14:00 | 4.46 | 5.6102 | N | 0
2025-05-16 | 15 | 2031-05-16 15:00 | 4.58 | 5.7611 | N | 0
2025-05-16 | 16 | 2031-05-16 16:00 | 4.84 | 6.0881 | N | 0
2025-05-16 | 17 | 2031-05-16 17:00 | 5.02 | 6.3146 | N | 0
2025-05-16 | 18 | 2031-05-16 18:00 | 5.01 | 6.302 | N | 0
2025-05-16 | 19 | 2031-05-16 19:00 | 4.87 | 6.1259 | N | 0
2025-05-16 | 20 | 2031-05-16 20:00 | 4.62 | 5.8114 | N | 0
2025-05-16 | 21 | 2031-05-16 21:00 | 4.6 | 5.7863 | N | 0
2025-05-16 | 22 | 2031-05-16 22:00 | 4.27 | 5.3712 | N | 0
2025-05-16 | 23 | 2031-05-16 23:00 | 3.73 | 4.6919 | N | 0
2025-05-17 | 00 | 2031-05-17 | 3.26 | 4.1007 | N | 0
2025-05-17 | 01 | 2031-05-17 01:00 | 2.91 | 3.6604 | N | 0
2025-05-17 | 02 | 2031-05-17 02:00 | 2.56 | 3.2202 | N | 0
2025-05-17 | 03 | 2031-05-17 03:00 | 2.49 | 3.1321 | N | 0
2025-05-17 | 04 | 2031-05-17 04:00 | 2.38 | 2.9938 | N | 0
2025-05-17 | 05 | 2031-05-17 05:00 | 2.39 | 3.0063 | N | 0
2025-05-17 | 06 | 2031-05-17 06:00 | 2.51 | 3.1573 | N | 0
2025-05-17 | 07 | 2031-05-17 07:00 | 2.8 | 3.5221 | N | 0
2025-05-17 | 08 | 2031-05-17 08:00 | 3.25 | 4.0881 | N | 0
2025-05-17 | 09 | 2031-05-17 09:00 | 3.49 | 4.39 | N | 0
2025-05-17 | 10 | 2031-05-17 10:00 | 3.59 | 4.5158 | N | 0
2025-05-17 | 11 | 2031-05-17 11:00 | 3.78 | 4.7548 | N | 0
2025-05-17 | 12 | 2031-05-17 12:00 | 3.88 | 4.8806 | N | 0
2025-05-17 | 13 | 2031-05-17 13:00 | 3.87 | 4.868 | N | 0
2025-05-17 | 14 | 2031-05-17 14:00 | 3.93 | 4.9435 | N | 0
2025-05-17 | 15 | 2031-05-17 15:00 | 3.84 | 4.8303 | N | 0
2025-05-17 | 16 | 2031-05-17 16:00 | 3.93 | 4.9435 | N | 0
2025-05-17 | 17 | 2031-05-17 17:00 | 4.03 | 5.0693 | N | 0
2025-05-17 | 18 | 2031-05-17 18:00 | 3.91 | 4.9183 | N | 0
2025-05-17 | 19 | 2031-05-17 19:00 | 3.81 | 4.7925 | N | 0
2025-05-17 | 20 | 2031-05-17 20:00 | 3.66 | 4.6038 | N | 0
2025-05-17 | 21 | 2031-05-17 21:00 | 3.66 | 4.6038 | N | 0
2025-05-17 | 22 | 2031-05-17 22:00 | 3.46 | 4.3523 | N | 0
2025-05-17 | 23 | 2031-05-17 23:00 | 3.19 | 4.0126 | N | 0
2025-05-18 | 00 | 2031-05-18 | 2.85 | 3.585 | N | 0
2025-05-18 | 01 | 2031-05-18 01:00 | 2.58 | 3.2453 | N | 0
2025-05-18 | 02 | 2031-05-18 02:00 | 2.52 | 3.1699 | N | 0
2025-05-18 | 03 | 2031-05-18 03:00 | 2.38 | 2.9938 | N | 0
2025-05-18 | 04 | 2031-05-18 04:00 | 2.29 | 2.8805 | N | 0
2025-05-18 | 05 | 2031-05-18 05:00 | 2.27 | 2.8554 | N | 0
2025-05-18 | 06 | 2031-05-18 06:00 | 2.4 | 3.0189 | N | 0
2025-05-18 | 07 | 2031-05-18 07:00 | 2.65 | 3.3334 | N | 0
2025-05-18 | 08 | 2031-05-18 08:00 | 2.93 | 3.6856 | N | 0
2025-05-18 | 09 | 2031-05-18 09:00 | 3.26 | 4.1007 | N | 0
2025-05-18 | 10 | 2031-05-18 10:00 | 3.45 | 4.3397 | N | 0
2025-05-18 | 11 | 2031-05-18 11:00 | 3.49 | 4.39 | N | 0
2025-05-18 | 12 | 2031-05-18 12:00 | 3.59 | 4.5158 | N | 0
2025-05-18 | 13 | 2031-05-18 13:00 | 3.52 | 4.4277 | N | 0
2025-05-18 | 14 | 2031-05-18 14:00 | 3.41 | 4.2894 | N | 0
2025-05-18 | 15 | 2031-05-18 15:00 | 3.49 | 4.39 | N | 0
2025-05-18 | 16 | 2031-05-18 16:00 | 3.79 | 4.7674 | N | 0
2025-05-18 | 17 | 2031-05-18 17:00 | 3.86 | 4.8554 | N | 0
2025-05-18 | 18 | 2031-05-18 18:00 | 3.93 | 4.9435 | N | 0
2025-05-18 | 19 | 2031-05-18 19:00 | 3.62 | 4.5535 | N | 0
2025-05-18 | 20 | 2031-05-18 20:00 | 3.69 | 4.6416 | N | 0
2025-05-18 | 21 | 2031-05-18 21:00 | 3.61 | 4.541 | N | 0
2025-05-18 | 22 | 2031-05-18 22:00 | 3.47 | 4.3648 | N | 0
2025-05-18 | 23 | 2031-05-18 23:00 | 3.11 | 3.912 | N | 0
2025-05-19 | 00 | 2031-05-19 | 2.85 | 3.585 | N | 0
2025-05-19 | 01 | 2031-05-19 01:00 | 2.65 | 3.3334 | N | 0
2025-05-19 | 02 | 2031-05-19 02:00 | 2.46 | 3.0944 | N | 0
2025-05-19 | 03 | 2031-05-19 03:00 | 2.38 | 2.9938 | N | 0
2025-05-19 | 04 | 2031-05-19 04:00 | 2.37 | 2.9812 | N | 0
2025-05-19 | 05 | 2031-05-19 05:00 | 2.33 | 2.9309 | N | 0
2025-05-19 | 06 | 2031-05-19 06:00 | 2.53 | 3.1824 | N | 0
2025-05-19 | 07 | 2031-05-19 07:00 | 2.81 | 3.5346 | N | 0
2025-05-19 | 08 | 2031-05-19 08:00 | 3.09 | 3.8869 | N | 0
2025-05-19 | 09 | 2031-05-19 09:00 | 3.41 | 4.2894 | N | 0
2025-05-19 | 10 | 2031-05-19 10:00 | 3.51 | 4.4152 | N | 0
2025-05-19 | 11 | 2031-05-19 11:00 | 3.74 | 4.7045 | N | 0
2025-05-19 | 12 | 2031-05-19 12:00 | 3.84 | 4.8303 | N | 0
2025-05-19 | 13 | 2031-05-19 13:00 | 3.81 | 4.7925 | N | 0
2025-05-19 | 14 | 2031-05-19 14:00 | 3.78 | 4.7548 | N | 0
2025-05-19 | 15 | 2031-05-19 15:00 | 3.77 | 4.7422 | N | 0
2025-05-19 | 16 | 2031-05-19 16:00 | 4.04 | 5.0818 | N | 0
2025-05-19 | 17 | 2031-05-19 17:00 | 4.22 | 5.3083 | N | 0
2025-05-19 | 18 | 2031-05-19 18:00 | 4.35 | 5.4718 | N | 0
2025-05-19 | 19 | 2031-05-19 19:00 | 4.11 | 5.1699 | N | 0
2025-05-19 | 20 | 2031-05-19 20:00 | 4.08 | 5.1322 | N | 0
2025-05-19 | 21 | 2031-05-19 21:00 | 4.03 | 5.0693 | N | 0
2025-05-19 | 22 | 2031-05-19 22:00 | 3.73 | 4.6919 | N | 0
2025-05-19 | 23 | 2031-05-19 23:00 | 3.29 | 4.1384 | N | 0
2025-05-20 | 00 | 2031-05-20 | 2.98 | 3.7485 | N | 0
2025-05-20 | 01 | 2031-05-20 01:00 | 2.61 | 3.2831 | N | 0
2025-05-20 | 02 | 2031-05-20 02:00 | 2.48 | 3.1195 | N | 0
2025-05-20 | 03 | 2031-05-20 03:00 | 2.47 | 3.107 | N | 0
2025-05-20 | 04 | 2031-05-20 04:00 | 2.5 | 3.1447 | N | 0
2025-05-20 | 05 | 2031-05-20 05:00 | 2.57 | 3.2328 | N | 0
2025-05-20 | 06 | 2031-05-20 06:00 | 3.05 | 3.8365 | N | 0
2025-05-20 | 07 | 2031-05-20 07:00 | 3.38 | 4.2516 | N | 0
2025-05-20 | 08 | 2031-05-20 08:00 | 3.64 | 4.5787 | N | 0
2025-05-20 | 09 | 2031-05-20 09:00 | 3.68 | 4.629 | N | 0
2025-05-20 | 10 | 2031-05-20 10:00 | 3.68 | 4.629 | N | 0
2025-05-20 | 11 | 2031-05-20 11:00 | 3.68 | 4.629 | N | 0
2025-05-20 | 12 | 2031-05-20 12:00 | 3.69 | 4.6416 | N | 0
2025-05-20 | 13 | 2031-05-20 13:00 | 3.73 | 4.6919 | N | 0
2025-05-20 | 14 | 2031-05-20 14:00 | 3.61 | 4.541 | N | 0
2025-05-20 | 15 | 2031-05-20 15:00 | 3.68 | 4.629 | N | 0
2025-05-20 | 16 | 2031-05-20 16:00 | 3.95 | 4.9686 | N | 0
2025-05-20 | 17 | 2031-05-20 17:00 | 4.07 | 5.1196 | N | 0
2025-05-20 | 18 | 2031-05-20 18:00 | 4.21 | 5.2957 | N | 0
2025-05-20 | 19 | 2031-05-20 19:00 | 3.97 | 4.9938 | N | 0
2025-05-20 | 20 | 2031-05-20 20:00 | 3.99 | 5.0189 | N | 0
2025-05-20 | 21 | 2031-05-20 21:00 | 4.03 | 5.0693 | N | 0
2025-05-20 | 22 | 2031-05-20 22:00 | 3.65 | 4.5913 | N | 0
2025-05-20 | 23 | 2031-05-20 23:00 | 3.17 | 3.9875 | N | 0
2025-05-21 | 00 | 2031-05-21 | 2.9 | 3.6479 | N | 0
2025-05-21 | 01 | 2031-05-21 01:00 | 2.63 | 3.3082 | N | 0
2025-05-21 | 02 | 2031-05-21 02:00 | 2.52 | 3.1699 | N | 0
2025-05-21 | 03 | 2031-05-21 03:00 | 2.42 | 3.0441 | N | 0
2025-05-21 | 04 | 2031-05-21 04:00 | 2.47 | 3.107 | N | 0
2025-05-21 | 05 | 2031-05-21 05:00 | 2.51 | 3.1573 | N | 0
2025-05-21 | 06 | 2031-05-21 06:00 | 3.02 | 3.7988 | N | 0
2025-05-21 | 07 | 2031-05-21 07:00 | 3.32 | 4.1762 | N | 0
2025-05-21 | 08 | 2031-05-21 08:00 | 3.57 | 4.4906 | N | 0
2025-05-21 | 09 | 2031-05-21 09:00 | 3.62 | 4.5535 | N | 0
2025-05-21 | 10 | 2031-05-21 10:00 | 3.82 | 4.8051 | N | 0
2025-05-21 | 11 | 2031-05-21 11:00 | 3.77 | 4.7422 | N | 0
2025-05-21 | 12 | 2031-05-21 12:00 | 3.93 | 4.9435 | N | 0
2025-05-21 | 13 | 2031-05-21 13:00 | 3.98 | 5.0064 | N | 0
2025-05-21 | 14 | 2031-05-21 14:00 | 3.89 | 4.8932 | N | 0
2025-05-21 | 15 | 2031-05-21 15:00 | 4.03 | 5.0693 | N | 0
2025-05-21 | 16 | 2031-05-21 16:00 | 4.3 | 5.4089 | N | 0
2025-05-21 | 17 | 2031-05-21 17:00 | 4.6 | 5.7863 | N | 0
2025-05-21 | 18 | 2031-05-21 18:00 | 4.6 | 5.7863 | N | 0
2025-05-21 | 19 | 2031-05-21 19:00 | 4.35 | 5.4718 | N | 0
2025-05-21 | 20 | 2031-05-21 20:00 | 4.45 | 5.5976 | N | 0
2025-05-21 | 21 | 2031-05-21 21:00 | 4.35 | 5.4718 | N | 0
2025-05-21 | 22 | 2031-05-21 22:00 | 3.97 | 4.9938 | N | 0
2025-05-21 | 23 | 2031-05-21 23:00 | 3.32 | 4.1762 | N | 0
2025-05-22 | 00 | 2031-05-22 | 2.99 | 3.7611 | N | 0
2025-05-22 | 01 | 2031-05-22 01:00 | 2.71 | 3.4089 | N | 0
2025-05-22 | 02 | 2031-05-22 02:00 | 2.6 | 3.2705 | N | 0
2025-05-22 | 03 | 2031-05-22 03:00 | 2.51 | 3.1573 | N | 0
2025-05-22 | 04 | 2031-05-22 04:00 | 2.6 | 3.2705 | N | 0
2025-05-22 | 05 | 2031-05-22 05:00 | 2.67 | 3.3585 | N | 0
2025-05-22 | 06 | 2031-05-22 06:00 | 3.19 | 4.0126 | N | 0
2025-05-22 | 07 | 2031-05-22 07:00 | 3.62 | 4.5535 | N | 0
2025-05-22 | 08 | 2031-05-22 08:00 | 3.8 | 4.7799 | N | 0
2025-05-22 | 09 | 2031-05-22 09:00 | 3.95 | 4.9686 | N | 0
2025-05-22 | 10 | 2031-05-22 10:00 | 4.1 | 5.1573 | N | 0
2025-05-22 | 11 | 2031-05-22 11:00 | 4.12 | 5.1825 | N | 0
2025-05-22 | 12 | 2031-05-22 12:00 | 4.15 | 5.2202 | N | 0
2025-05-22 | 13 | 2031-05-22 13:00 | 4.16 | 5.2328 | N | 0
2025-05-22 | 14 | 2031-05-22 14:00 | 4.16 | 5.2328 | N | 0
2025-05-22 | 15 | 2031-05-22 15:00 | 4.13 | 5.1951 | N | 0
2025-05-22 | 16 | 2031-05-22 16:00 | 4.49 | 5.6479 | N | 0
2025-05-22 | 17 | 2031-05-22 17:00 | 4.74 | 5.9624 | N | 0
2025-05-22 | 18 | 2031-05-22 18:00 | 4.81 | 6.0504 | N | 0
2025-05-22 | 19 | 2031-05-22 19:00 | 4.46 | 5.6102 | N | 0
2025-05-22 | 20 | 2031-05-22 20:00 | 4.37 | 5.4969 | N | 0
2025-05-22 | 21 | 2031-05-22 21:00 | 4.28 | 5.3837 | N | 0
2025-05-22 | 22 | 2031-05-22 22:00 | 4.02 | 5.0567 | N | 0
2025-05-22 | 23 | 2031-05-22 23:00 | 3.43 | 4.3145 | N | 0
2025-05-23 | 00 | 2031-05-23 | 3.06 | 3.8491 | N | 0
2025-05-23 | 01 | 2031-05-23 01:00 | 2.77 | 3.4843 | N | 0
2025-05-23 | 02 | 2031-05-23 02:00 | 2.68 | 3.3711 | N | 0
2025-05-23 | 03 | 2031-05-23 03:00 | 2.57 | 3.2328 | N | 0
2025-05-23 | 04 | 2031-05-23 04:00 | 2.6 | 3.2705 | N | 0
2025-05-23 | 05 | 2031-05-23 05:00 | 2.72 | 3.4214 | N | 0
2025-05-23 | 06 | 2031-05-23 06:00 | 3.11 | 3.912 | N | 0
2025-05-23 | 07 | 2031-05-23 07:00 | 3.55 | 4.4655 | N | 0
2025-05-23 | 08 | 2031-05-23 08:00 | 3.76 | 4.7296 | N | 0
2025-05-23 | 09 | 2031-05-23 09:00 | 3.85 | 4.8428 | N | 0
2025-05-23 | 10 | 2031-05-23 10:00 | 3.87 | 4.868 | N | 0
2025-05-23 | 11 | 2031-05-23 11:00 | 3.97 | 4.9938 | N | 0
2025-05-23 | 12 | 2031-05-23 12:00 | 4.02 | 5.0567 | N | 0
2025-05-23 | 13 | 2031-05-23 13:00 | 3.96 | 4.9812 | N | 0
2025-05-23 | 14 | 2031-05-23 14:00 | 3.93 | 4.9435 | N | 0
2025-05-23 | 15 | 2031-05-23 15:00 | 3.95 | 4.9686 | N | 0
2025-05-23 | 16 | 2031-05-23 16:00 | 4.25 | 5.346 | N | 0
2025-05-23 | 17 | 2031-05-23 17:00 | 4.28 | 5.3837 | N | 0
2025-05-23 | 18 | 2031-05-23 18:00 | 4.49 | 5.6479 | N | 0
2025-05-23 | 19 | 2031-05-23 19:00 | 4.21 | 5.2957 | N | 0
2025-05-23 | 20 | 2031-05-23 20:00 | 4.19 | 5.2705 | N | 0
2025-05-23 | 21 | 2031-05-23 21:00 | 4.17 | 5.2454 | N | 0
2025-05-23 | 22 | 2031-05-23 22:00 | 3.95 | 4.9686 | N | 0
2025-05-23 | 23 | 2031-05-23 23:00 | 3.49 | 4.39 | N | 0
2025-05-24 | 00 | 2031-05-24 | 3.14 | 3.9497 | N | 0
2025-05-24 | 01 | 2031-05-24 01:00 | 2.85 | 3.585 | N | 0
2025-05-24 | 02 | 2031-05-24 02:00 | 2.69 | 3.3837 | N | 0
2025-05-24 | 03 | 2031-05-24 03:00 | 2.62 | 3.2956 | N | 0
2025-05-24 | 04 | 2031-05-24 04:00 | 2.54 | 3.195 | N | 0
2025-05-24 | 05 | 2031-05-24 05:00 | 2.6 | 3.2705 | N | 0
2025-05-24 | 06 | 2031-05-24 06:00 | 2.86 | 3.5975 | N | 0
2025-05-24 | 07 | 2031-05-24 07:00 | 3.02 | 3.7988 | N | 0
2025-05-24 | 08 | 2031-05-24 08:00 | 3.35 | 4.2139 | N | 0
2025-05-24 | 09 | 2031-05-24 09:00 | 3.64 | 4.5787 | N | 0
2025-05-24 | 10 | 2031-05-24 10:00 | 3.72 | 4.6793 | N | 0
2025-05-24 | 11 | 2031-05-24 11:00 | 3.8 | 4.7799 | N | 0
2025-05-24 | 12 | 2031-05-24 12:00 | 3.91 | 4.9183 | N | 0
2025-05-24 | 13 | 2031-05-24 13:00 | 3.91 | 4.9183 | N | 0
2025-05-24 | 14 | 2031-05-24 14:00 | 3.95 | 4.9686 | N | 0
2025-05-24 | 15 | 2031-05-24 15:00 | 3.84 | 4.8303 | N | 0
2025-05-24 | 16 | 2031-05-24 16:00 | 3.95 | 4.9686 | N | 0
2025-05-24 | 17 | 2031-05-24 17:00 | 4.01 | 5.0441 | N | 0
2025-05-24 | 18 | 2031-05-24 18:00 | 4.11 | 5.1699 | N | 0
2025-05-24 | 19 | 2031-05-24 19:00 | 3.74 | 4.7045 | N | 0
2025-05-24 | 20 | 2031-05-24 20:00 | 3.8 | 4.7799 | N | 0
2025-05-24 | 21 | 2031-05-24 21:00 | 3.78 | 4.7548 | N | 0
2025-05-24 | 22 | 2031-05-24 22:00 | 3.72 | 4.6793 | N | 0
2025-05-24 | 23 | 2031-05-24 23:00 | 3.43 | 4.3145 | N | 0
2025-05-25 | 00 | 2031-05-25 | 3.03 | 3.8114 | N | 0
2025-05-25 | 01 | 2031-05-25 01:00 | 2.78 | 3.4969 | N | 0
2025-05-25 | 02 | 2031-05-25 02:00 | 2.61 | 3.2831 | N | 0
2025-05-25 | 03 | 2031-05-25 03:00 | 2.51 | 3.1573 | N | 0
2025-05-25 | 04 | 2031-05-25 04:00 | 2.53 | 3.1824 | N | 0
2025-05-25 | 05 | 2031-05-25 05:00 | 2.51 | 3.1573 | N | 0
2025-05-25 | 06 | 2031-05-25 06:00 | 2.65 | 3.3334 | N | 0
2025-05-25 | 07 | 2031-05-25 07:00 | 2.99 | 3.7611 | N | 0
2025-05-25 | 08 | 2031-05-25 08:00 | 3.2 | 4.0252 | N | 0
2025-05-25 | 09 | 2031-05-25 09:00 | 3.48 | 4.3774 | N | 0
2025-05-25 | 10 | 2031-05-25 10:00 | 3.65 | 4.5913 | N | 0
2025-05-25 | 11 | 2031-05-25 11:00 | 3.87 | 4.868 | N | 0
2025-05-25 | 12 | 2031-05-25 12:00 | 3.92 | 4.9309 | N | 0
2025-05-25 | 13 | 2031-05-25 13:00 | 4.01 | 5.0441 | N | 0
2025-05-25 | 14 | 2031-05-25 14:00 | 3.93 | 4.9435 | N | 0
2025-05-25 | 15 | 2031-05-25 15:00 | 4.08 | 5.1322 | N | 0
2025-05-25 | 16 | 2031-05-25 16:00 | 4.25 | 5.346 | N | 0
2025-05-25 | 17 | 2031-05-25 17:00 | 4.53 | 5.6982 | N | 0
2025-05-25 | 18 | 2031-05-25 18:00 | 4.47 | 5.6227 | N | 0
2025-05-25 | 19 | 2031-05-25 19:00 | 4.25 | 5.346 | N | 0
2025-05-25 | 20 | 2031-05-25 20:00 | 4.17 | 5.2454 | N | 0
2025-05-25 | 21 | 2031-05-25 21:00 | 3.95 | 4.9686 | N | 0
2025-05-25 | 22 | 2031-05-25 22:00 | 3.7 | 4.6542 | N | 0
2025-05-25 | 23 | 2031-05-25 23:00 | 3.24 | 4.0755 | N | 0
2025-05-26 | 00 | 2031-05-26 | 2.87 | 3.6101 | N | 0
2025-05-26 | 01 | 2031-05-26 01:00 | 2.59 | 3.2579 | N | 0
2025-05-26 | 02 | 2031-05-26 02:00 | 2.51 | 3.1573 | N | 0
2025-05-26 | 03 | 2031-05-26 03:00 | 2.47 | 3.107 | N | 0
2025-05-26 | 04 | 2031-05-26 04:00 | 2.47 | 3.107 | N | 0
2025-05-26 | 05 | 2031-05-26 05:00 | 2.62 | 3.2956 | N | 0
2025-05-26 | 06 | 2031-05-26 06:00 | 3.03 | 3.8114 | N | 0
2025-05-26 | 07 | 2031-05-26 07:00 | 3.38 | 4.2516 | N | 0
2025-05-26 | 08 | 2031-05-26 08:00 | 3.4 | 4.2768 | N | 0
2025-05-26 | 09 | 2031-05-26 09:00 | 3.62 | 4.5535 | N | 0
2025-05-26 | 10 | 2031-05-26 10:00 | 3.59 | 4.5158 | N | 0
2025-05-26 | 11 | 2031-05-26 11:00 | 3.65 | 4.5913 | N | 0
2025-05-26 | 12 | 2031-05-26 12:00 | 3.76 | 4.7296 | N | 0
2025-05-26 | 13 | 2031-05-26 13:00 | 3.75 | 4.7171 | N | 0
2025-05-26 | 14 | 2031-05-26 14:00 | 3.7 | 4.6542 | N | 0
2025-05-26 | 15 | 2031-05-26 15:00 | 3.76 | 4.7296 | N | 0
2025-05-26 | 16 | 2031-05-26 16:00 | 4.07 | 5.1196 | N | 0
2025-05-26 | 17 | 2031-05-26 17:00 | 4.38 | 5.5095 | N | 0
2025-05-26 | 18 | 2031-05-26 18:00 | 4.41 | 5.5473 | N | 0
2025-05-26 | 19 | 2031-05-26 19:00 | 4.26 | 5.3586 | N | 0
2025-05-26 | 20 | 2031-05-26 20:00 | 4.08 | 5.1322 | N | 0
2025-05-26 | 21 | 2031-05-26 21:00 | 4.13 | 5.1951 | N | 0
2025-05-26 | 22 | 2031-05-26 22:00 | 3.76 | 4.7296 | N | 0
2025-05-26 | 23 | 2031-05-26 23:00 | 3.31 | 4.1636 | N | 0
2025-05-27 | 00 | 2031-05-27 | 2.83 | 3.5598 | N | 0
2025-05-27 | 01 | 2031-05-27 01:00 | 2.54 | 3.195 | N | 0
2025-05-27 | 02 | 2031-05-27 02:00 | 2.44 | 3.0692 | N | 0
2025-05-27 | 03 | 2031-05-27 03:00 | 2.42 | 3.0441 | N | 0
2025-05-27 | 04 | 2031-05-27 04:00 | 2.39 | 3.0063 | N | 0
2025-05-27 | 05 | 2031-05-27 05:00 | 2.54 | 3.195 | N | 0
2025-05-27 | 06 | 2031-05-27 06:00 | 2.95 | 3.7108 | N | 0
2025-05-27 | 07 | 2031-05-27 07:00 | 3.33 | 4.1887 | N | 0
2025-05-27 | 08 | 2031-05-27 08:00 | 3.4 | 4.2768 | N | 0
2025-05-27 | 09 | 2031-05-27 09:00 | 3.67 | 4.6164 | N | 0
2025-05-27 | 10 | 2031-05-27 10:00 | 3.63 | 4.5661 | N | 0
2025-05-27 | 11 | 2031-05-27 11:00 | 3.73 | 4.6919 | N | 0
2025-05-27 | 12 | 2031-05-27 12:00 | 3.79 | 4.7674 | N | 0
2025-05-27 | 13 | 2031-05-27 13:00 | 3.94 | 4.9561 | N | 0
2025-05-27 | 14 | 2031-05-27 14:00 | 4.11 | 5.1699 | N | 0
2025-05-27 | 15 | 2031-05-27 15:00 | 4.1 | 5.1573 | N | 0
2025-05-27 | 16 | 2031-05-27 16:00 | 4.35 | 5.4718 | N | 0
2025-05-27 | 17 | 2031-05-27 17:00 | 4.67 | 5.8743 | N | 0
2025-05-27 | 18 | 2031-05-27 18:00 | 4.63 | 5.824 | N | 0
2025-05-27 | 19 | 2031-05-27 19:00 | 4.42 | 5.5598 | N | 0
2025-05-27 | 20 | 2031-05-27 20:00 | 4.33 | 5.4466 | N | 0
2025-05-27 | 21 | 2031-05-27 21:00 | 4.27 | 5.3712 | N | 0
2025-05-27 | 22 | 2031-05-27 22:00 | 3.97 | 4.9938 | N | 0
2025-05-27 | 23 | 2031-05-27 23:00 | 3.37 | 4.2391 | N | 0
2025-05-28 | 00 | 2031-05-28 | 2.95 | 3.7108 | N | 0
2025-05-28 | 01 | 2031-05-28 01:00 | 2.6 | 3.2705 | N | 0
2025-05-28 | 02 | 2031-05-28 02:00 | 2.4 | 3.0189 | N | 0
2025-05-28 | 03 | 2031-05-28 03:00 | 2.36 | 2.9686 | N | 0
2025-05-28 | 04 | 2031-05-28 04:00 | 2.35 | 2.956 | N | 0
2025-05-28 | 05 | 2031-05-28 05:00 | 2.47 | 3.107 | N | 0
2025-05-28 | 06 | 2031-05-28 06:00 | 2.9 | 3.6479 | N | 0
2025-05-28 | 07 | 2031-05-28 07:00 | 3.23 | 4.063 | N | 0
2025-05-28 | 08 | 2031-05-28 08:00 | 3.32 | 4.1762 | N | 0
2025-05-28 | 09 | 2031-05-28 09:00 | 3.55 | 4.4655 | N | 0
2025-05-28 | 10 | 2031-05-28 10:00 | 3.83 | 4.8177 | N | 0
2025-05-28 | 11 | 2031-05-28 11:00 | 3.77 | 4.7422 | N | 0
2025-05-28 | 12 | 2031-05-28 12:00 | 3.97 | 4.9938 | N | 0
2025-05-28 | 13 | 2031-05-28 13:00 | 3.91 | 4.9183 | N | 0
2025-05-28 | 14 | 2031-05-28 14:00 | 4.01 | 5.0441 | N | 0
2025-05-28 | 15 | 2031-05-28 15:00 | 4.11 | 5.1699 | N | 0
2025-05-28 | 16 | 2031-05-28 16:00 | 4.18 | 5.2579 | N | 0
2025-05-28 | 17 | 2031-05-28 17:00 | 4.55 | 5.7234 | N | 0
2025-05-28 | 18 | 2031-05-28 18:00 | 4.39 | 5.5221 | N | 0
2025-05-28 | 19 | 2031-05-28 19:00 | 4.18 | 5.2579 | N | 0
2025-05-28 | 20 | 2031-05-28 20:00 | 4.22 | 5.3083 | N | 0
2025-05-28 | 21 | 2031-05-28 21:00 | 4.17 | 5.2454 | N | 0
2025-05-28 | 22 | 2031-05-28 22:00 | 3.72 | 4.6793 | N | 0
2025-05-28 | 23 | 2031-05-28 23:00 | 3.21 | 4.0378 | N | 0
2025-05-29 | 00 | 2031-05-29 | 2.83 | 3.5598 | N | 0
2025-05-29 | 01 | 2031-05-29 01:00 | 2.55 | 3.2076 | N | 0
2025-05-29 | 02 | 2031-05-29 02:00 | 2.39 | 3.0063 | N | 0
2025-05-29 | 03 | 2031-05-29 03:00 | 2.35 | 2.956 | N | 0
2025-05-29 | 04 | 2031-05-29 04:00 | 2.35 | 2.956 | N | 0
2025-05-29 | 05 | 2031-05-29 05:00 | 2.48 | 3.1195 | N | 0
2025-05-29 | 06 | 2031-05-29 06:00 | 2.88 | 3.6227 | N | 0
2025-05-29 | 07 | 2031-05-29 07:00 | 3.32 | 4.1762 | N | 0
2025-05-29 | 08 | 2031-05-29 08:00 | 3.5 | 4.4026 | N | 0
2025-05-29 | 09 | 2031-05-29 09:00 | 3.71 | 4.6667 | N | 0
2025-05-29 | 10 | 2031-05-29 10:00 | 3.82 | 4.8051 | N | 0
2025-05-29 | 11 | 2031-05-29 11:00 | 3.79 | 4.7674 | N | 0
2025-05-29 | 12 | 2031-05-29 12:00 | 3.98 | 5.0064 | N | 0
2025-05-29 | 13 | 2031-05-29 13:00 | 3.84 | 4.8303 | N | 0
2025-05-29 | 14 | 2031-05-29 14:00 | 3.87 | 4.868 | N | 0
2025-05-29 | 15 | 2031-05-29 15:00 | 3.86 | 4.8554 | N | 0
2025-05-29 | 16 | 2031-05-29 16:00 | 4.09 | 5.1447 | N | 0
2025-05-29 | 17 | 2031-05-29 17:00 | 4.28 | 5.3837 | N | 0
2025-05-29 | 18 | 2031-05-29 18:00 | 4.26 | 5.3586 | N | 0
2025-05-29 | 19 | 2031-05-29 19:00 | 4.04 | 5.0818 | N | 0
2025-05-29 | 20 | 2031-05-29 20:00 | 4.13 | 5.1951 | N | 0
2025-05-29 | 21 | 2031-05-29 21:00 | 4.05 | 5.0944 | N | 0
2025-05-29 | 22 | 2031-05-29 22:00 | 3.83 | 4.8177 | N | 0
2025-05-29 | 23 | 2031-05-29 23:00 | 3.23 | 4.063 | N | 0
2025-05-30 | 00 | 2031-05-30 | 2.86 | 3.5975 | N | 0
2025-05-30 | 01 | 2031-05-30 01:00 | 2.59 | 3.2579 | N | 0
2025-05-30 | 02 | 2031-05-30 02:00 | 2.46 | 3.0944 | N | 0
2025-05-30 | 03 | 2031-05-30 03:00 | 2.37 | 2.9812 | N | 0
2025-05-30 | 04 | 2031-05-30 04:00 | 2.33 | 2.9309 | N | 0
2025-05-30 | 05 | 2031-05-30 05:00 | 2.44 | 3.0692 | N | 0
2025-05-30 | 06 | 2031-05-30 06:00 | 2.88 | 3.6227 | N | 0
2025-05-30 | 07 | 2031-05-30 07:00 | 3.26 | 4.1007 | N | 0
2025-05-30 | 08 | 2031-05-30 08:00 | 3.52 | 4.4277 | N | 0
2025-05-30 | 09 | 2031-05-30 09:00 | 3.72 | 4.6793 | N | 0
2025-05-30 | 10 | 2031-05-30 10:00 | 3.8 | 4.7799 | N | 0
2025-05-30 | 11 | 2031-05-30 11:00 | 3.92 | 4.9309 | N | 0
2025-05-30 | 12 | 2031-05-30 12:00 | 4.03 | 5.0693 | N | 0
2025-05-30 | 13 | 2031-05-30 13:00 | 4.06 | 5.107 | N | 0
2025-05-30 | 14 | 2031-05-30 14:00 | 4.02 | 5.0567 | N | 0
2025-05-30 | 15 | 2031-05-30 15:00 | 4.23 | 5.3208 | N | 0
2025-05-30 | 16 | 2031-05-30 16:00 | 4.27 | 5.3712 | N | 0
2025-05-30 | 17 | 2031-05-30 17:00 | 4.51 | 5.673 | N | 0
2025-05-30 | 18 | 2031-05-30 18:00 | 4.51 | 5.673 | N | 0
2025-05-30 | 19 | 2031-05-30 19:00 | 4.3 | 5.4089 | N | 0
2025-05-30 | 20 | 2031-05-30 20:00 | 4.25 | 5.346 | N | 0
2025-05-30 | 21 | 2031-05-30 21:00 | 4.09 | 5.1447 | N | 0
2025-05-30 | 22 | 2031-05-30 22:00 | 3.87 | 4.868 | N | 0
2025-05-30 | 23 | 2031-05-30 23:00 | 3.48 | 4.3774 | N | 0
2025-05-31 | 00 | 2031-05-31 | 3.02 | 3.7988 | N | 0
2025-05-31 | 01 | 2031-05-31 01:00 | 2.71 | 3.4089 | N | 0
2025-05-31 | 02 | 2031-05-31 02:00 | 2.51 | 3.1573 | N | 0
2025-05-31 | 03 | 2031-05-31 03:00 | 2.42 | 3.0441 | N | 0
2025-05-31 | 04 | 2031-05-31 04:00 | 2.34 | 2.9434 | N | 0
2025-05-31 | 05 | 2031-05-31 05:00 | 2.38 | 2.9938 | N | 0
2025-05-31 | 06 | 2031-05-31 06:00 | 2.52 | 3.1699 | N | 0
2025-05-31 | 07 | 2031-05-31 07:00 | 2.77 | 3.4843 | N | 0
2025-05-31 | 08 | 2031-05-31 08:00 | 3.13 | 3.9372 | N | 0
2025-05-31 | 09 | 2031-05-31 09:00 | 3.42 | 4.302 | N | 0
2025-05-31 | 10 | 2031-05-31 10:00 | 3.69 | 4.6416 | N | 0
2025-05-31 | 11 | 2031-05-31 11:00 | 3.72 | 4.6793 | N | 0
2025-05-31 | 12 | 2031-05-31 12:00 | 3.88 | 4.8806 | N | 0
2025-05-31 | 13 | 2031-05-31 13:00 | 3.68 | 4.629 | N | 0
2025-05-31 | 14 | 2031-05-31 14:00 | 3.64 | 4.5787 | N | 0
2025-05-31 | 15 | 2031-05-31 15:00 | 3.64 | 4.5787 | N | 0
2025-05-31 | 16 | 2031-05-31 16:00 | 3.81 | 4.7925 | N | 0
2025-05-31 | 17 | 2031-05-31 17:00 | 3.91 | 4.9183 | N | 0
2025-05-31 | 18 | 2031-05-31 18:00 | 4.04 | 5.0818 | N | 0
2025-05-31 | 19 | 2031-05-31 19:00 | 3.85 | 4.8428 | N | 0
2025-05-31 | 20 | 2031-05-31 20:00 | 3.75 | 4.7171 | N | 0
2025-05-31 | 21 | 2031-05-31 21:00 | 3.75 | 4.7171 | N | 0
2025-05-31 | 22 | 2031-05-31 22:00 | 3.61 | 4.541 | N | 0
2025-05-31 | 23 | 2031-05-31 23:00 | 3.23 | 4.063 | N | 0
2025-06-01 | 00 | 2031-06-01 | 0 | 0 | N | 0
2025-06-01 | 01 | 2031-06-01 01:00 | 0 | 0 | N | 0
2025-06-01 | 02 | 2031-06-01 02:00 | 0 | 0 | N | 0
2025-06-01 | 03 | 2031-06-01 03:00 | 0 | 0 | N | 0
2025-06-01 | 04 | 2031-06-01 04:00 | 0 | 0 | N | 0
2025-06-01 | 05 | 2031-06-01 05:00 | 0 | 0 | N | 0
2025-06-01 | 06 | 2031-06-01 06:00 | 0 | 0 | N | 0
2025-06-01 | 07 | 2031-06-01 07:00 | 0 | 0 | N | 0
2025-06-01 | 08 | 2031-06-01 08:00 | 0 | 0 | N | 0
2025-06-01 | 09 | 2031-06-01 09:00 | 0 | 0 | N | 0
2025-06-01 | 10 | 2031-06-01 10:00 | 0 | 0 | N | 0
2025-06-01 | 11 | 2031-06-01 11:00 | 0 | 0 | N | 0
2025-06-01 | 12 | 2031-06-01 12:00 | 0 | 0 | N | 0
2025-06-01 | 13 | 2031-06-01 13:00 | 0 | 0 | N | 0
2025-06-01 | 14 | 2031-06-01 14:00 | 0 | 0 | N | 0
2025-06-01 | 15 | 2031-06-01 15:00 | 0 | 0 | N | 0
2025-06-01 | 16 | 2031-06-01 16:00 | 0 | 0 | N | 0
2025-06-01 | 17 | 2031-06-01 17:00 | 0 | 0 | N | 0
2025-06-01 | 18 | 2031-06-01 18:00 | 0 | 0 | N | 0
2025-06-01 | 19 | 2031-06-01 19:00 | 0 | 0 | N | 0
2025-06-01 | 20 | 2031-06-01 20:00 | 0 | 0 | N | 0
2025-06-01 | 21 | 2031-06-01 21:00 | 0 | 0 | N | 0
2025-06-01 | 22 | 2031-06-01 22:00 | 0 | 0 | N | 0
2025-06-01 | 23 | 2031-06-01 23:00 | 0 | 0 | N | 0
2025-06-02 | 00 | 2031-06-02 | 0 | 0 | N | 0
2025-06-02 | 01 | 2031-06-02 01:00 | 0 | 0 | N | 0
2025-06-02 | 02 | 2031-06-02 02:00 | 0 | 0 | N | 0
2025-06-02 | 03 | 2031-06-02 03:00 | 0 | 0 | N | 0
2025-06-02 | 04 | 2031-06-02 04:00 | 0 | 0 | N | 0
2025-06-02 | 05 | 2031-06-02 05:00 | 0 | 0 | N | 0
2025-06-02 | 06 | 2031-06-02 06:00 | 0 | 0 | N | 0
2025-06-02 | 07 | 2031-06-02 07:00 | 0 | 0 | N | 0
2025-06-02 | 08 | 2031-06-02 08:00 | 0 | 0 | N | 0
2025-06-02 | 09 | 2031-06-02 09:00 | 0 | 0 | N | 0
2025-06-02 | 10 | 2031-06-02 10:00 | 0 | 0 | N | 0
2025-06-02 | 11 | 2031-06-02 11:00 | 0 | 0 | N | 0
2025-06-02 | 12 | 2031-06-02 12:00 | 0 | 0 | N | 0
2025-06-02 | 13 | 2031-06-02 13:00 | 0 | 0 | N | 0
2025-06-02 | 14 | 2031-06-02 14:00 | 0 | 0 | N | 0
2025-06-02 | 15 | 2031-06-02 15:00 | 0 | 0 | N | 0
2025-06-02 | 16 | 2031-06-02 16:00 | 0 | 0 | N | 0
2025-06-02 | 17 | 2031-06-02 17:00 | 0 | 0 | N | 0
2025-06-02 | 18 | 2031-06-02 18:00 | 0 | 0 | N | 0
2025-06-02 | 19 | 2031-06-02 19:00 | 0 | 0 | N | 0
2025-06-02 | 20 | 2031-06-02 20:00 | 0 | 0 | N | 0
2025-06-02 | 21 | 2031-06-02 21:00 | 0 | 0 | N | 0
2025-06-02 | 22 | 2031-06-02 22:00 | 0 | 0 | N | 0
2025-06-02 | 23 | 2031-06-02 23:00 | 0 | 0 | N | 0
2025-06-03 | 00 | 2031-06-03 | 0 | 0 | N | 0
2025-06-03 | 01 | 2031-06-03 01:00 | 0 | 0 | N | 0
2025-06-03 | 02 | 2031-06-03 02:00 | 0 | 0 | N | 0
2025-06-03 | 03 | 2031-06-03 03:00 | 0 | 0 | N | 0
2025-06-03 | 04 | 2031-06-03 04:00 | 0 | 0 | N | 0
2025-06-03 | 05 | 2031-06-03 05:00 | 0 | 0 | N | 0
2025-06-03 | 06 | 2031-06-03 06:00 | 0 | 0 | N | 0
2025-06-03 | 07 | 2031-06-03 07:00 | 0 | 0 | N | 0
2025-06-03 | 08 | 2031-06-03 08:00 | 0 | 0 | N | 0
2025-06-03 | 09 | 2031-06-03 09:00 | 0 | 0 | N | 0
2025-06-03 | 10 | 2031-06-03 10:00 | 0 | 0 | N | 0
2025-06-03 | 11 | 2031-06-03 11:00 | 0 | 0 | N | 0
2025-06-03 | 12 | 2031-06-03 12:00 | 0 | 0 | N | 0
2025-06-03 | 13 | 2031-06-03 13:00 | 0 | 0 | N | 0
2025-06-03 | 14 | 2031-06-03 14:00 | 0 | 0 | N | 0
2025-06-03 | 15 | 2031-06-03 15:00 | 0 | 0 | N | 0
2025-06-03 | 16 | 2031-06-03 16:00 | 0 | 0 | N | 0
2025-06-03 | 17 | 2031-06-03 17:00 | 0 | 0 | N | 0
2025-06-03 | 18 | 2031-06-03 18:00 | 0 | 0 | N | 0
2025-06-03 | 19 | 2031-06-03 19:00 | 0 | 0 | N | 0
2025-06-03 | 20 | 2031-06-03 20:00 | 0 | 0 | N | 0
2025-06-03 | 21 | 2031-06-03 21:00 | 0 | 0 | N | 0
2025-06-03 | 22 | 2031-06-03 22:00 | 0 | 0 | N | 0
2025-06-03 | 23 | 2031-06-03 23:00 | 0 | 0 | N | 0
2025-06-04 | 00 | 2031-06-04 | 0 | 0 | N | 0
2025-06-04 | 01 | 2031-06-04 01:00 | 0 | 0 | N | 0
2025-06-04 | 02 | 2031-06-04 02:00 | 0 | 0 | N | 0
2025-06-04 | 03 | 2031-06-04 03:00 | 0 | 0 | N | 0
2025-06-04 | 04 | 2031-06-04 04:00 | 0 | 0 | N | 0
2025-06-04 | 05 | 2031-06-04 05:00 | 0 | 0 | N | 0
2025-06-04 | 06 | 2031-06-04 06:00 | 0 | 0 | N | 0
2025-06-04 | 07 | 2031-06-04 07:00 | 0 | 0 | N | 0
2025-06-04 | 08 | 2031-06-04 08:00 | 0 | 0 | N | 0
2025-06-04 | 09 | 2031-06-04 09:00 | 0 | 0 | N | 0
2025-06-04 | 10 | 2031-06-04 10:00 | 0 | 0 | N | 0
2025-06-04 | 11 | 2031-06-04 11:00 | 0 | 0 | N | 0
2025-06-04 | 12 | 2031-06-04 12:00 | 0 | 0 | N | 0
2025-06-04 | 13 | 2031-06-04 13:00 | 0 | 0 | N | 0
2025-06-04 | 14 | 2031-06-04 14:00 | 0 | 0 | N | 0
2025-06-04 | 15 | 2031-06-04 15:00 | 0 | 0 | N | 0
2025-06-04 | 16 | 2031-06-04 16:00 | 0 | 0 | N | 0
2025-06-04 | 17 | 2031-06-04 17:00 | 0 | 0 | N | 0
2025-06-04 | 18 | 2031-06-04 18:00 | 0 | 0 | N | 0
2025-06-04 | 19 | 2031-06-04 19:00 | 0 | 0 | N | 0
2025-06-04 | 20 | 2031-06-04 20:00 | 0 | 0 | N | 0
2025-06-04 | 21 | 2031-06-04 21:00 | 0 | 0 | N | 0
2025-06-04 | 22 | 2031-06-04 22:00 | 0 | 0 | N | 0
2025-06-04 | 23 | 2031-06-04 23:00 | 0 | 0 | N | 0
2025-06-05 | 00 | 2031-06-05 | 0 | 0 | N | 0
2025-06-05 | 01 | 2031-06-05 01:00 | 0 | 0 | N | 0
2025-06-05 | 02 | 2031-06-05 02:00 | 0 | 0 | N | 0
2025-06-05 | 03 | 2031-06-05 03:00 | 0 | 0 | N | 0
2025-06-05 | 04 | 2031-06-05 04:00 | 0 | 0 | N | 0
2025-06-05 | 05 | 2031-06-05 05:00 | 0 | 0 | N | 0
2025-06-05 | 06 | 2031-06-05 06:00 | 0 | 0 | N | 0
2025-06-05 | 07 | 2031-06-05 07:00 | 0 | 0 | N | 0
2025-06-05 | 08 | 2031-06-05 08:00 | 0 | 0 | N | 0
2025-06-05 | 09 | 2031-06-05 09:00 | 0 | 0 | N | 0
2025-06-05 | 10 | 2031-06-05 10:00 | 0 | 0 | N | 0
2025-06-05 | 11 | 2031-06-05 11:00 | 0 | 0 | N | 0
2025-06-05 | 12 | 2031-06-05 12:00 | 0 | 0 | N | 0
2025-06-05 | 13 | 2031-06-05 13:00 | 0 | 0 | N | 0
2025-06-05 | 14 | 2031-06-05 14:00 | 0 | 0 | N | 0
2025-06-05 | 15 | 2031-06-05 15:00 | 0 | 0 | N | 0
2025-06-05 | 16 | 2031-06-05 16:00 | 0 | 0 | N | 0
2025-06-05 | 17 | 2031-06-05 17:00 | 0 | 0 | N | 0
2025-06-05 | 18 | 2031-06-05 18:00 | 0 | 0 | N | 0
2025-06-05 | 19 | 2031-06-05 19:00 | 0 | 0 | N | 0
2025-06-05 | 20 | 2031-06-05 20:00 | 0 | 0 | N | 0
2025-06-05 | 21 | 2031-06-05 21:00 | 0 | 0 | N | 0
2025-06-05 | 22 | 2031-06-05 22:00 | 0 | 0 | N | 0
2025-06-05 | 23 | 2031-06-05 23:00 | 0 | 0 | N | 0
2025-06-06 | 00 | 2031-06-06 | 0 | 0 | N | 0
2025-06-06 | 01 | 2031-06-06 01:00 | 0 | 0 | N | 0
2025-06-06 | 02 | 2031-06-06 02:00 | 0 | 0 | N | 0
2025-06-06 | 03 | 2031-06-06 03:00 | 0 | 0 | N | 0
2025-06-06 | 04 | 2031-06-06 04:00 | 0 | 0 | N | 0
2025-06-06 | 05 | 2031-06-06 05:00 | 0 | 0 | N | 0
2025-06-06 | 06 | 2031-06-06 06:00 | 0 | 0 | N | 0
2025-06-06 | 07 | 2031-06-06 07:00 | 0 | 0 | N | 0
2025-06-06 | 08 | 2031-06-06 08:00 | 0 | 0 | N | 0
2025-06-06 | 09 | 2031-06-06 09:00 | 0 | 0 | N | 0
2025-06-06 | 10 | 2031-06-06 10:00 | 0 | 0 | N | 0
2025-06-06 | 11 | 2031-06-06 11:00 | 0 | 0 | N | 0
2025-06-06 | 12 | 2031-06-06 12:00 | 0 | 0 | N | 0
2025-06-06 | 13 | 2031-06-06 13:00 | 0 | 0 | N | 0
2025-06-06 | 14 | 2031-06-06 14:00 | 0 | 0 | N | 0
2025-06-06 | 15 | 2031-06-06 15:00 | 0 | 0 | N | 0
2025-06-06 | 16 | 2031-06-06 16:00 | 0 | 0 | N | 0
2025-06-06 | 17 | 2031-06-06 17:00 | 0 | 0 | N | 0
2025-06-06 | 18 | 2031-06-06 18:00 | 0 | 0 | N | 0
2025-06-06 | 19 | 2031-06-06 19:00 | 0 | 0 | N | 0
2025-06-06 | 20 | 2031-06-06 20:00 | 0 | 0 | N | 0
2025-06-06 | 21 | 2031-06-06 21:00 | 0 | 0 | N | 0
2025-06-06 | 22 | 2031-06-06 22:00 | 0 | 0 | N | 0
2025-06-06 | 23 | 2031-06-06 23:00 | 0 | 0 | N | 0
2025-06-07 | 00 | 2031-06-07 | 0 | 0 | N | 0
2025-06-07 | 01 | 2031-06-07 01:00 | 0 | 0 | N | 0
2025-06-07 | 02 | 2031-06-07 02:00 | 0 | 0 | N | 0
2025-06-07 | 03 | 2031-06-07 03:00 | 0 | 0 | N | 0
2025-06-07 | 04 | 2031-06-07 04:00 | 0 | 0 | N | 0
2025-06-07 | 05 | 2031-06-07 05:00 | 0 | 0 | N | 0
2025-06-07 | 06 | 2031-06-07 06:00 | 0 | 0 | N | 0
2025-06-07 | 07 | 2031-06-07 07:00 | 0 | 0 | N | 0
2025-06-07 | 08 | 2031-06-07 08:00 | 0 | 0 | N | 0
2025-06-07 | 09 | 2031-06-07 09:00 | 0 | 0 | N | 0
2025-06-07 | 10 | 2031-06-07 10:00 | 0 | 0 | N | 0
2025-06-07 | 11 | 2031-06-07 11:00 | 0 | 0 | N | 0
2025-06-07 | 12 | 2031-06-07 12:00 | 0 | 0 | N | 0
2025-06-07 | 13 | 2031-06-07 13:00 | 0 | 0 | N | 0
2025-06-07 | 14 | 2031-06-07 14:00 | 0 | 0 | N | 0
2025-06-07 | 15 | 2031-06-07 15:00 | 0 | 0 | N | 0
2025-06-07 | 16 | 2031-06-07 16:00 | 0 | 0 | N | 0
2025-06-07 | 17 | 2031-06-07 17:00 | 0 | 0 | N | 0
2025-06-07 | 18 | 2031-06-07 18:00 | 0 | 0 | N | 0
2025-06-07 | 19 | 2031-06-07 19:00 | 0 | 0 | N | 0
2025-06-07 | 20 | 2031-06-07 20:00 | 0 | 0 | N | 0
2025-06-07 | 21 | 2031-06-07 21:00 | 0 | 0 | N | 0
2025-06-07 | 22 | 2031-06-07 22:00 | 0 | 0 | N | 0
2025-06-07 | 23 | 2031-06-07 23:00 | 0 | 0 | N | 0
2025-06-08 | 00 | 2031-06-08 | 0 | 0 | N | 0
2025-06-08 | 01 | 2031-06-08 01:00 | 0 | 0 | N | 0
2025-06-08 | 02 | 2031-06-08 02:00 | 0 | 0 | N | 0
2025-06-08 | 03 | 2031-06-08 03:00 | 0 | 0 | N | 0
2025-06-08 | 04 | 2031-06-08 04:00 | 0 | 0 | N | 0
2025-06-08 | 05 | 2031-06-08 05:00 | 0 | 0 | N | 0
2025-06-08 | 06 | 2031-06-08 06:00 | 0 | 0 | N | 0
2025-06-08 | 07 | 2031-06-08 07:00 | 0 | 0 | N | 0
2025-06-08 | 08 | 2031-06-08 08:00 | 0 | 0 | N | 0
2025-06-08 | 09 | 2031-06-08 09:00 | 0 | 0 | N | 0
2025-06-08 | 10 | 2031-06-08 10:00 | 0 | 0 | N | 0
2025-06-08 | 11 | 2031-06-08 11:00 | 0 | 0 | N | 0
2025-06-08 | 12 | 2031-06-08 12:00 | 0 | 0 | N | 0
2025-06-08 | 13 | 2031-06-08 13:00 | 0 | 0 | N | 0
2025-06-08 | 14 | 2031-06-08 14:00 | 0 | 0 | N | 0
2025-06-08 | 15 | 2031-06-08 15:00 | 0 | 0 | N | 0
2025-06-08 | 16 | 2031-06-08 16:00 | 0 | 0 | N | 0
2025-06-08 | 17 | 2031-06-08 17:00 | 0 | 0 | N | 0
2025-06-08 | 18 | 2031-06-08 18:00 | 0 | 0 | N | 0
2025-06-08 | 19 | 2031-06-08 19:00 | 0 | 0 | N | 0
2025-06-08 | 20 | 2031-06-08 20:00 | 0 | 0 | N | 0
2025-06-08 | 21 | 2031-06-08 21:00 | 0 | 0 | N | 0
2025-06-08 | 22 | 2031-06-08 22:00 | 0 | 0 | N | 0
2025-06-08 | 23 | 2031-06-08 23:00 | 0 | 0 | N | 0
2025-06-09 | 00 | 2031-06-09 | 0 | 0 | N | 0
2025-06-09 | 01 | 2031-06-09 01:00 | 0 | 0 | N | 0
2025-06-09 | 02 | 2031-06-09 02:00 | 0 | 0 | N | 0
2025-06-09 | 03 | 2031-06-09 03:00 | 0 | 0 | N | 0
2025-06-09 | 04 | 2031-06-09 04:00 | 0 | 0 | N | 0
2025-06-09 | 05 | 2031-06-09 05:00 | 0 | 0 | N | 0
2025-06-09 | 06 | 2031-06-09 06:00 | 0 | 0 | N | 0
2025-06-09 | 07 | 2031-06-09 07:00 | 0 | 0 | N | 0
2025-06-09 | 08 | 2031-06-09 08:00 | 0 | 0 | N | 0
2025-06-09 | 09 | 2031-06-09 09:00 | 0 | 0 | N | 0
2025-06-09 | 10 | 2031-06-09 10:00 | 0 | 0 | N | 0
2025-06-09 | 11 | 2031-06-09 11:00 | 0 | 0 | N | 0
2025-06-09 | 12 | 2031-06-09 12:00 | 0 | 0 | N | 0
2025-06-09 | 13 | 2031-06-09 13:00 | 0 | 0 | N | 0
2025-06-09 | 14 | 2031-06-09 14:00 | 0 | 0 | N | 0
2025-06-09 | 15 | 2031-06-09 15:00 | 0 | 0 | N | 0
2025-06-09 | 16 | 2031-06-09 16:00 | 0 | 0 | N | 0
2025-06-09 | 17 | 2031-06-09 17:00 | 0 | 0 | N | 0
2025-06-09 | 18 | 2031-06-09 18:00 | 0 | 0 | N | 0
2025-06-09 | 19 | 2031-06-09 19:00 | 0 | 0 | N | 0
2025-06-09 | 20 | 2031-06-09 20:00 | 0 | 0 | N | 0
2025-06-09 | 21 | 2031-06-09 21:00 | 0 | 0 | N | 0
2025-06-09 | 22 | 2031-06-09 22:00 | 0 | 0 | N | 0
2025-06-09 | 23 | 2031-06-09 23:00 | 0 | 0 | N | 0
2025-06-10 | 00 | 2031-06-10 | 0 | 0 | N | 0
2025-06-10 | 01 | 2031-06-10 01:00 | 0 | 0 | N | 0
2025-06-10 | 02 | 2031-06-10 02:00 | 0 | 0 | N | 0
2025-06-10 | 03 | 2031-06-10 03:00 | 0 | 0 | N | 0
2025-06-10 | 04 | 2031-06-10 04:00 | 0 | 0 | N | 0
2025-06-10 | 05 | 2031-06-10 05:00 | 0 | 0 | N | 0
2025-06-10 | 06 | 2031-06-10 06:00 | 0 | 0 | N | 0
2025-06-10 | 07 | 2031-06-10 07:00 | 0 | 0 | N | 0
2025-06-10 | 08 | 2031-06-10 08:00 | 0 | 0 | N | 0
2025-06-10 | 09 | 2031-06-10 09:00 | 0 | 0 | N | 0
2025-06-10 | 10 | 2031-06-10 10:00 | 0 | 0 | N | 0
2025-06-10 | 11 | 2031-06-10 11:00 | 0 | 0 | N | 0
2025-06-10 | 12 | 2031-06-10 12:00 | 0 | 0 | N | 0
2025-06-10 | 13 | 2031-06-10 13:00 | 0 | 0 | N | 0
2025-06-10 | 14 | 2031-06-10 14:00 | 0 | 0 | N | 0
2025-06-10 | 15 | 2031-06-10 15:00 | 0 | 0 | N | 0
2025-06-10 | 16 | 2031-06-10 16:00 | 0 | 0 | N | 0
2025-06-10 | 17 | 2031-06-10 17:00 | 0 | 0 | N | 0
2025-06-10 | 18 | 2031-06-10 18:00 | 0 | 0 | N | 0
2025-06-10 | 19 | 2031-06-10 19:00 | 0 | 0 | N | 0
2025-06-10 | 20 | 2031-06-10 20:00 | 0 | 0 | N | 0
2025-06-10 | 21 | 2031-06-10 21:00 | 0 | 0 | N | 0
2025-06-10 | 22 | 2031-06-10 22:00 | 0 | 0 | N | 0
2025-06-10 | 23 | 2031-06-10 23:00 | 0 | 0 | N | 0
2025-06-11 | 00 | 2031-06-11 | 0 | 0 | N | 0
2025-06-11 | 01 | 2031-06-11 01:00 | 0 | 0 | N | 0
2025-06-11 | 02 | 2031-06-11 02:00 | 0 | 0 | N | 0
2025-06-11 | 03 | 2031-06-11 03:00 | 0 | 0 | N | 0
2025-06-11 | 04 | 2031-06-11 04:00 | 0 | 0 | N | 0
2025-06-11 | 05 | 2031-06-11 05:00 | 0 | 0 | N | 0
2025-06-11 | 06 | 2031-06-11 06:00 | 0 | 0 | N | 0
2025-06-11 | 07 | 2031-06-11 07:00 | 0 | 0 | N | 0
2025-06-11 | 08 | 2031-06-11 08:00 | 0 | 0 | N | 0
2025-06-11 | 09 | 2031-06-11 09:00 | 0 | 0 | N | 0
2025-06-11 | 10 | 2031-06-11 10:00 | 0 | 0 | N | 0
2025-06-11 | 11 | 2031-06-11 11:00 | 0 | 0 | N | 0
2025-06-11 | 12 | 2031-06-11 12:00 | 0 | 0 | N | 0
2025-06-11 | 13 | 2031-06-11 13:00 | 0 | 0 | N | 0
2025-06-11 | 14 | 2031-06-11 14:00 | 0 | 0 | N | 0
2025-06-11 | 15 | 2031-06-11 15:00 | 0 | 0 | N | 0
2025-06-11 | 16 | 2031-06-11 16:00 | 0 | 0 | N | 0
2025-06-11 | 17 | 2031-06-11 17:00 | 0 | 0 | N | 0
2025-06-11 | 18 | 2031-06-11 18:00 | 0 | 0 | N | 0
2025-06-11 | 19 | 2031-06-11 19:00 | 0 | 0 | N | 0
2025-06-11 | 20 | 2031-06-11 20:00 | 0 | 0 | N | 0
2025-06-11 | 21 | 2031-06-11 21:00 | 0 | 0 | N | 0
2025-06-11 | 22 | 2031-06-11 22:00 | 0 | 0 | N | 0
2025-06-11 | 23 | 2031-06-11 23:00 | 0 | 0 | N | 0
2025-06-12 | 00 | 2031-06-12 | 0 | 0 | N | 0
2025-06-12 | 01 | 2031-06-12 01:00 | 0 | 0 | N | 0
2025-06-12 | 02 | 2031-06-12 02:00 | 0 | 0 | N | 0
2025-06-12 | 03 | 2031-06-12 03:00 | 0 | 0 | N | 0
2025-06-12 | 04 | 2031-06-12 04:00 | 0 | 0 | N | 0
2025-06-12 | 05 | 2031-06-12 05:00 | 0 | 0 | N | 0
2025-06-12 | 06 | 2031-06-12 06:00 | 0 | 0 | N | 0
2025-06-12 | 07 | 2031-06-12 07:00 | 0 | 0 | N | 0
2025-06-12 | 08 | 2031-06-12 08:00 | 0 | 0 | N | 0
2025-06-12 | 09 | 2031-06-12 09:00 | 0 | 0 | N | 0
2025-06-12 | 10 | 2031-06-12 10:00 | 0 | 0 | N | 0
2025-06-12 | 11 | 2031-06-12 11:00 | 0 | 0 | N | 0
2025-06-12 | 12 | 2031-06-12 12:00 | 0 | 0 | N | 0
2025-06-12 | 13 | 2031-06-12 13:00 | 0 | 0 | N | 0
2025-06-12 | 14 | 2031-06-12 14:00 | 0 | 0 | N | 0
2025-06-12 | 15 | 2031-06-12 15:00 | 0 | 0 | N | 0
2025-06-12 | 16 | 2031-06-12 16:00 | 0 | 0 | N | 0
2025-06-12 | 17 | 2031-06-12 17:00 | 0 | 0 | N | 0
2025-06-12 | 18 | 2031-06-12 18:00 | 0 | 0 | N | 0
2025-06-12 | 19 | 2031-06-12 19:00 | 0 | 0 | N | 0
2025-06-12 | 20 | 2031-06-12 20:00 | 0 | 0 | N | 0
2025-06-12 | 21 | 2031-06-12 21:00 | 0 | 0 | N | 0
2025-06-12 | 22 | 2031-06-12 22:00 | 0 | 0 | N | 0
2025-06-12 | 23 | 2031-06-12 23:00 | 0 | 0 | N | 0
2025-06-13 | 00 | 2031-06-13 | 0 | 0 | N | 0
2025-06-13 | 01 | 2031-06-13 01:00 | 0 | 0 | N | 0
2025-06-13 | 02 | 2031-06-13 02:00 | 0 | 0 | N | 0
2025-06-13 | 03 | 2031-06-13 03:00 | 0 | 0 | N | 0
2025-06-13 | 04 | 2031-06-13 04:00 | 0 | 0 | N | 0
2025-06-13 | 05 | 2031-06-13 05:00 | 0 | 0 | N | 0
2025-06-13 | 06 | 2031-06-13 06:00 | 0 | 0 | N | 0
2025-06-13 | 07 | 2031-06-13 07:00 | 0 | 0 | N | 0
2025-06-13 | 08 | 2031-06-13 08:00 | 0 | 0 | N | 0
2025-06-13 | 09 | 2031-06-13 09:00 | 0 | 0 | N | 0
2025-06-13 | 10 | 2031-06-13 10:00 | 0 | 0 | N | 0
2025-06-13 | 11 | 2031-06-13 11:00 | 0 | 0 | N | 0
2025-06-13 | 12 | 2031-06-13 12:00 | 0 | 0 | N | 0
2025-06-13 | 13 | 2031-06-13 13:00 | 0 | 0 | N | 0
2025-06-13 | 14 | 2031-06-13 14:00 | 0 | 0 | N | 0
2025-06-13 | 15 | 2031-06-13 15:00 | 0 | 0 | N | 0
2025-06-13 | 16 | 2031-06-13 16:00 | 0 | 0 | N | 0
2025-06-13 | 17 | 2031-06-13 17:00 | 0 | 0 | N | 0
2025-06-13 | 18 | 2031-06-13 18:00 | 0 | 0 | N | 0
2025-06-13 | 19 | 2031-06-13 19:00 | 0 | 0 | N | 0
2025-06-13 | 20 | 2031-06-13 20:00 | 0 | 0 | N | 0
2025-06-13 | 21 | 2031-06-13 21:00 | 0 | 0 | N | 0
2025-06-13 | 22 | 2031-06-13 22:00 | 0 | 0 | N | 0
2025-06-13 | 23 | 2031-06-13 23:00 | 0 | 0 | N | 0
2025-06-14 | 00 | 2031-06-14 | 0 | 0 | N | 0
2025-06-14 | 01 | 2031-06-14 01:00 | 0 | 0 | N | 0
2025-06-14 | 02 | 2031-06-14 02:00 | 0 | 0 | N | 0
2025-06-14 | 03 | 2031-06-14 03:00 | 0 | 0 | N | 0
2025-06-14 | 04 | 2031-06-14 04:00 | 0 | 0 | N | 0
2025-06-14 | 05 | 2031-06-14 05:00 | 0 | 0 | N | 0
2025-06-14 | 06 | 2031-06-14 06:00 | 0 | 0 | N | 0
2025-06-14 | 07 | 2031-06-14 07:00 | 0 | 0 | N | 0
2025-06-14 | 08 | 2031-06-14 08:00 | 0 | 0 | N | 0
2025-06-14 | 09 | 2031-06-14 09:00 | 0 | 0 | N | 0
2025-06-14 | 10 | 2031-06-14 10:00 | 0 | 0 | N | 0
2025-06-14 | 11 | 2031-06-14 11:00 | 0 | 0 | N | 0
2025-06-14 | 12 | 2031-06-14 12:00 | 0 | 0 | N | 0
2025-06-14 | 13 | 2031-06-14 13:00 | 0 | 0 | N | 0
2025-06-14 | 14 | 2031-06-14 14:00 | 0 | 0 | N | 0
2025-06-14 | 15 | 2031-06-14 15:00 | 0 | 0 | N | 0
2025-06-14 | 16 | 2031-06-14 16:00 | 0 | 0 | N | 0
2025-06-14 | 17 | 2031-06-14 17:00 | 0 | 0 | N | 0
2025-06-14 | 18 | 2031-06-14 18:00 | 0 | 0 | N | 0
2025-06-14 | 19 | 2031-06-14 19:00 | 0 | 0 | N | 0
2025-06-14 | 20 | 2031-06-14 20:00 | 0 | 0 | N | 0
2025-06-14 | 21 | 2031-06-14 21:00 | 0 | 0 | N | 0
2025-06-14 | 22 | 2031-06-14 22:00 | 0 | 0 | N | 0
2025-06-14 | 23 | 2031-06-14 23:00 | 0 | 0 | N | 0
2025-06-15 | 00 | 2031-06-15 | 0 | 0 | N | 0
2025-06-15 | 01 | 2031-06-15 01:00 | 0 | 0 | N | 0
2025-06-15 | 02 | 2031-06-15 02:00 | 0 | 0 | N | 0
2025-06-15 | 03 | 2031-06-15 03:00 | 0 | 0 | N | 0
2025-06-15 | 04 | 2031-06-15 04:00 | 0 | 0 | N | 0
2025-06-15 | 05 | 2031-06-15 05:00 | 0 | 0 | N | 0
2025-06-15 | 06 | 2031-06-15 06:00 | 0 | 0 | N | 0
2025-06-15 | 07 | 2031-06-15 07:00 | 0 | 0 | N | 0
2025-06-15 | 08 | 2031-06-15 08:00 | 0 | 0 | N | 0
2025-06-15 | 09 | 2031-06-15 09:00 | 0 | 0 | N | 0
2025-06-15 | 10 | 2031-06-15 10:00 | 0 | 0 | N | 0
2025-06-15 | 11 | 2031-06-15 11:00 | 0 | 0 | N | 0
2025-06-15 | 12 | 2031-06-15 12:00 | 0 | 0 | N | 0
2025-06-15 | 13 | 2031-06-15 13:00 | 0 | 0 | N | 0
2025-06-15 | 14 | 2031-06-15 14:00 | 0 | 0 | N | 0
2025-06-15 | 15 | 2031-06-15 15:00 | 0 | 0 | N | 0
2025-06-15 | 16 | 2031-06-15 16:00 | 0 | 0 | N | 0
2025-06-15 | 17 | 2031-06-15 17:00 | 0 | 0 | N | 0
2025-06-15 | 18 | 2031-06-15 18:00 | 0 | 0 | N | 0
2025-06-15 | 19 | 2031-06-15 19:00 | 0 | 0 | N | 0
2025-06-15 | 20 | 2031-06-15 20:00 | 0 | 0 | N | 0
2025-06-15 | 21 | 2031-06-15 21:00 | 0 | 0 | N | 0
2025-06-15 | 22 | 2031-06-15 22:00 | 0 | 0 | N | 0
2025-06-15 | 23 | 2031-06-15 23:00 | 0 | 0 | N | 0
2025-06-16 | 00 | 2031-06-16 | 0 | 0 | N | 0
2025-06-16 | 01 | 2031-06-16 01:00 | 0 | 0 | N | 0
2025-06-16 | 02 | 2031-06-16 02:00 | 0 | 0 | N | 0
2025-06-16 | 03 | 2031-06-16 03:00 | 0 | 0 | N | 0
2025-06-16 | 04 | 2031-06-16 04:00 | 0 | 0 | N | 0
2025-06-16 | 05 | 2031-06-16 05:00 | 0 | 0 | N | 0
2025-06-16 | 06 | 2031-06-16 06:00 | 0 | 0 | N | 0
2025-06-16 | 07 | 2031-06-16 07:00 | 0 | 0 | N | 0
2025-06-16 | 08 | 2031-06-16 08:00 | 0 | 0 | N | 0
2025-06-16 | 09 | 2031-06-16 09:00 | 0 | 0 | N | 0
2025-06-16 | 10 | 2031-06-16 10:00 | 0 | 0 | N | 0
2025-06-16 | 11 | 2031-06-16 11:00 | 0 | 0 | N | 0
2025-06-16 | 12 | 2031-06-16 12:00 | 0 | 0 | N | 0
2025-06-16 | 13 | 2031-06-16 13:00 | 0 | 0 | N | 0
2025-06-16 | 14 | 2031-06-16 14:00 | 0 | 0 | N | 0
2025-06-16 | 15 | 2031-06-16 15:00 | 0 | 0 | N | 0
2025-06-16 | 16 | 2031-06-16 16:00 | 0 | 0 | N | 0
2025-06-16 | 17 | 2031-06-16 17:00 | 0 | 0 | N | 0
2025-06-16 | 18 | 2031-06-16 18:00 | 0 | 0 | N | 0
2025-06-16 | 19 | 2031-06-16 19:00 | 0 | 0 | N | 0
2025-06-16 | 20 | 2031-06-16 20:00 | 0 | 0 | N | 0
2025-06-16 | 21 | 2031-06-16 21:00 | 0 | 0 | N | 0
2025-06-16 | 22 | 2031-06-16 22:00 | 0 | 0 | N | 0
2025-06-16 | 23 | 2031-06-16 23:00 | 0 | 0 | N | 0
2025-06-17 | 00 | 2031-06-17 | 0 | 0 | N | 0
2025-06-17 | 01 | 2031-06-17 01:00 | 0 | 0 | N | 0
2025-06-17 | 02 | 2031-06-17 02:00 | 0 | 0 | N | 0
2025-06-17 | 03 | 2031-06-17 03:00 | 0 | 0 | N | 0
2025-06-17 | 04 | 2031-06-17 04:00 | 0 | 0 | N | 0
2025-06-17 | 05 | 2031-06-17 05:00 | 0 | 0 | N | 0
2025-06-17 | 06 | 2031-06-17 06:00 | 0 | 0 | N | 0
2025-06-17 | 07 | 2031-06-17 07:00 | 0 | 0 | N | 0
2025-06-17 | 08 | 2031-06-17 08:00 | 0 | 0 | N | 0
2025-06-17 | 09 | 2031-06-17 09:00 | 0 | 0 | N | 0
2025-06-17 | 10 | 2031-06-17 10:00 | 0 | 0 | N | 0
2025-06-17 | 11 | 2031-06-17 11:00 | 0 | 0 | N | 0
2025-06-17 | 12 | 2031-06-17 12:00 | 0 | 0 | N | 0
2025-06-17 | 13 | 2031-06-17 13:00 | 0 | 0 | N | 0
2025-06-17 | 14 | 2031-06-17 14:00 | 0 | 0 | N | 0
2025-06-17 | 15 | 2031-06-17 15:00 | 0 | 0 | N | 0
2025-06-17 | 16 | 2031-06-17 16:00 | 0 | 0 | N | 0
2025-06-17 | 17 | 2031-06-17 17:00 | 0 | 0 | N | 0
2025-06-17 | 18 | 2031-06-17 18:00 | 0 | 0 | N | 0
2025-06-17 | 19 | 2031-06-17 19:00 | 0 | 0 | N | 0
2025-06-17 | 20 | 2031-06-17 20:00 | 0 | 0 | N | 0
2025-06-17 | 21 | 2031-06-17 21:00 | 0 | 0 | N | 0
2025-06-17 | 22 | 2031-06-17 22:00 | 0 | 0 | N | 0
2025-06-17 | 23 | 2031-06-17 23:00 | 0 | 0 | N | 0
2025-06-18 | 00 | 2031-06-18 | 0 | 0 | N | 0
2025-06-18 | 01 | 2031-06-18 01:00 | 0 | 0 | N | 0
2025-06-18 | 02 | 2031-06-18 02:00 | 0 | 0 | N | 0
2025-06-18 | 03 | 2031-06-18 03:00 | 0 | 0 | N | 0
2025-06-18 | 04 | 2031-06-18 04:00 | 0 | 0 | N | 0
2025-06-18 | 05 | 2031-06-18 05:00 | 0 | 0 | N | 0
2025-06-18 | 06 | 2031-06-18 06:00 | 0 | 0 | N | 0
2025-06-18 | 07 | 2031-06-18 07:00 | 0 | 0 | N | 0
2025-06-18 | 08 | 2031-06-18 08:00 | 0 | 0 | N | 0
2025-06-18 | 09 | 2031-06-18 09:00 | 0 | 0 | N | 0
2025-06-18 | 10 | 2031-06-18 10:00 | 0 | 0 | N | 0
2025-06-18 | 11 | 2031-06-18 11:00 | 0 | 0 | N | 0
2025-06-18 | 12 | 2031-06-18 12:00 | 0 | 0 | N | 0
2025-06-18 | 13 | 2031-06-18 13:00 | 0 | 0 | N | 0
2025-06-18 | 14 | 2031-06-18 14:00 | 0 | 0 | N | 0
2025-06-18 | 15 | 2031-06-18 15:00 | 0 | 0 | N | 0
2025-06-18 | 16 | 2031-06-18 16:00 | 0 | 0 | N | 0
2025-06-18 | 17 | 2031-06-18 17:00 | 0 | 0 | N | 0
2025-06-18 | 18 | 2031-06-18 18:00 | 0 | 0 | N | 0
2025-06-18 | 19 | 2031-06-18 19:00 | 0 | 0 | N | 0
2025-06-18 | 20 | 2031-06-18 20:00 | 0 | 0 | N | 0
2025-06-18 | 21 | 2031-06-18 21:00 | 0 | 0 | N | 0
2025-06-18 | 22 | 2031-06-18 22:00 | 0 | 0 | N | 0
2025-06-18 | 23 | 2031-06-18 23:00 | 0 | 0 | N | 0
2025-06-19 | 00 | 2031-06-19 | 0 | 0 | N | 0
2025-06-19 | 01 | 2031-06-19 01:00 | 0 | 0 | N | 0
2025-06-19 | 02 | 2031-06-19 02:00 | 0 | 0 | N | 0
2025-06-19 | 03 | 2031-06-19 03:00 | 0 | 0 | N | 0
2025-06-19 | 04 | 2031-06-19 04:00 | 0 | 0 | N | 0
2025-06-19 | 05 | 2031-06-19 05:00 | 0 | 0 | N | 0
2025-06-19 | 06 | 2031-06-19 06:00 | 0 | 0 | N | 0
2025-06-19 | 07 | 2031-06-19 07:00 | 0 | 0 | N | 0
2025-06-19 | 08 | 2031-06-19 08:00 | 0 | 0 | N | 0
2025-06-19 | 09 | 2031-06-19 09:00 | 0 | 0 | N | 0
2025-06-19 | 10 | 2031-06-19 10:00 | 0 | 0 | N | 0
2025-06-19 | 11 | 2031-06-19 11:00 | 0 | 0 | N | 0
2025-06-19 | 12 | 2031-06-19 12:00 | 0 | 0 | N | 0
2025-06-19 | 13 | 2031-06-19 13:00 | 0 | 0 | N | 0
2025-06-19 | 14 | 2031-06-19 14:00 | 0 | 0 | N | 0
2025-06-19 | 15 | 2031-06-19 15:00 | 0 | 0 | N | 0
2025-06-19 | 16 | 2031-06-19 16:00 | 0 | 0 | N | 0
2025-06-19 | 17 | 2031-06-19 17:00 | 0 | 0 | N | 0
2025-06-19 | 18 | 2031-06-19 18:00 | 0 | 0 | N | 0
2025-06-19 | 19 | 2031-06-19 19:00 | 0 | 0 | N | 0
2025-06-19 | 20 | 2031-06-19 20:00 | 0 | 0 | N | 0
2025-06-19 | 21 | 2031-06-19 21:00 | 0 | 0 | N | 0
2025-06-19 | 22 | 2031-06-19 22:00 | 0 | 0 | N | 0
2025-06-19 | 23 | 2031-06-19 23:00 | 0 | 0 | N | 0
2025-06-20 | 00 | 2031-06-20 | 0 | 0 | N | 0
2025-06-20 | 01 | 2031-06-20 01:00 | 0 | 0 | N | 0
2025-06-20 | 02 | 2031-06-20 02:00 | 0 | 0 | N | 0
2025-06-20 | 03 | 2031-06-20 03:00 | 0 | 0 | N | 0
2025-06-20 | 04 | 2031-06-20 04:00 | 0 | 0 | N | 0
2025-06-20 | 05 | 2031-06-20 05:00 | 0 | 0 | N | 0
2025-06-20 | 06 | 2031-06-20 06:00 | 0 | 0 | N | 0
2025-06-20 | 07 | 2031-06-20 07:00 | 0 | 0 | N | 0
2025-06-20 | 08 | 2031-06-20 08:00 | 0 | 0 | N | 0
2025-06-20 | 09 | 2031-06-20 09:00 | 0 | 0 | N | 0
2025-06-20 | 10 | 2031-06-20 10:00 | 0 | 0 | N | 0
2025-06-20 | 11 | 2031-06-20 11:00 | 0 | 0 | N | 0
2025-06-20 | 12 | 2031-06-20 12:00 | 0 | 0 | N | 0
2025-06-20 | 13 | 2031-06-20 13:00 | 0 | 0 | N | 0
2025-06-20 | 14 | 2031-06-20 14:00 | 0 | 0 | N | 0
2025-06-20 | 15 | 2031-06-20 15:00 | 0 | 0 | N | 0
2025-06-20 | 16 | 2031-06-20 16:00 | 0 | 0 | N | 0
2025-06-20 | 17 | 2031-06-20 17:00 | 0 | 0 | N | 0
2025-06-20 | 18 | 2031-06-20 18:00 | 0 | 0 | N | 0
2025-06-20 | 19 | 2031-06-20 19:00 | 0 | 0 | N | 0
2025-06-20 | 20 | 2031-06-20 20:00 | 0 | 0 | N | 0
2025-06-20 | 21 | 2031-06-20 21:00 | 0 | 0 | N | 0
2025-06-20 | 22 | 2031-06-20 22:00 | 0 | 0 | N | 0
2025-06-20 | 23 | 2031-06-20 23:00 | 0 | 0 | N | 0
2025-06-21 | 00 | 2031-06-21 | 0 | 0 | N | 0
2025-06-21 | 01 | 2031-06-21 01:00 | 0 | 0 | N | 0
2025-06-21 | 02 | 2031-06-21 02:00 | 0 | 0 | N | 0
2025-06-21 | 03 | 2031-06-21 03:00 | 0 | 0 | N | 0
2025-06-21 | 04 | 2031-06-21 04:00 | 0 | 0 | N | 0
2025-06-21 | 05 | 2031-06-21 05:00 | 0 | 0 | N | 0
2025-06-21 | 06 | 2031-06-21 06:00 | 0 | 0 | N | 0
2025-06-21 | 07 | 2031-06-21 07:00 | 0 | 0 | N | 0
2025-06-21 | 08 | 2031-06-21 08:00 | 0 | 0 | N | 0
2025-06-21 | 09 | 2031-06-21 09:00 | 0 | 0 | N | 0
2025-06-21 | 10 | 2031-06-21 10:00 | 0 | 0 | N | 0
2025-06-21 | 11 | 2031-06-21 11:00 | 0 | 0 | N | 0
2025-06-21 | 12 | 2031-06-21 12:00 | 0 | 0 | N | 0
2025-06-21 | 13 | 2031-06-21 13:00 | 0 | 0 | N | 0
2025-06-21 | 14 | 2031-06-21 14:00 | 0 | 0 | N | 0
2025-06-21 | 15 | 2031-06-21 15:00 | 0 | 0 | N | 0
2025-06-21 | 16 | 2031-06-21 16:00 | 0 | 0 | N | 0
2025-06-21 | 17 | 2031-06-21 17:00 | 0 | 0 | N | 0
2025-06-21 | 18 | 2031-06-21 18:00 | 0 | 0 | N | 0
2025-06-21 | 19 | 2031-06-21 19:00 | 0 | 0 | N | 0
2025-06-21 | 20 | 2031-06-21 20:00 | 0 | 0 | N | 0
2025-06-21 | 21 | 2031-06-21 21:00 | 0 | 0 | N | 0
2025-06-21 | 22 | 2031-06-21 22:00 | 0 | 0 | N | 0
2025-06-21 | 23 | 2031-06-21 23:00 | 0 | 0 | N | 0
2025-06-22 | 00 | 2031-06-22 | 0 | 0 | N | 0
2025-06-22 | 01 | 2031-06-22 01:00 | 0 | 0 | N | 0
2025-06-22 | 02 | 2031-06-22 02:00 | 0 | 0 | N | 0
2025-06-22 | 03 | 2031-06-22 03:00 | 0 | 0 | N | 0
2025-06-22 | 04 | 2031-06-22 04:00 | 0 | 0 | N | 0
2025-06-22 | 05 | 2031-06-22 05:00 | 0 | 0 | N | 0
2025-06-22 | 06 | 2031-06-22 06:00 | 0 | 0 | N | 0
2025-06-22 | 07 | 2031-06-22 07:00 | 0 | 0 | N | 0
2025-06-22 | 08 | 2031-06-22 08:00 | 2.88 | 3.6227 | N | 0
2025-06-22 | 09 | 2031-06-22 09:00 | 2.95 | 3.7108 | N | 0
2025-06-22 | 10 | 2031-06-22 10:00 | 3.21 | 4.0378 | N | 0
2025-06-22 | 11 | 2031-06-22 11:00 | 3.78 | 4.7548 | N | 0
2025-06-22 | 12 | 2031-06-22 12:00 | 4.6 | 5.7863 | N | 0
2025-06-22 | 13 | 2031-06-22 13:00 | 5.2 | 6.541 | N | 0
2025-06-22 | 14 | 2031-06-22 14:00 | 5.56 | 6.9938 | N | 0
2025-06-22 | 15 | 2031-06-22 15:00 | 6.53 | 8.214 | N | 0
2025-06-22 | 16 | 2031-06-22 16:00 | 7.26 | 9.1322 | N | 0
2025-06-22 | 17 | 2031-06-22 17:00 | 7.5 | 9.4341 | N | 0
2025-06-22 | 18 | 2031-06-22 18:00 | 7.67 | 9.648 | N | 0
2025-06-22 | 19 | 2031-06-22 19:00 | 7.74 | 9.736 | N | 0
2025-06-22 | 20 | 2031-06-22 20:00 | 8.05 | 10.1259 | N | 0
2025-06-22 | 21 | 2031-06-22 21:00 | 8.48 | 10.6668 | Y | 0.026835 | 1 | 1
2025-06-22 | 22 | 2031-06-22 22:00 | 8.4 | 10.5662 | N | 0
2025-06-22 | 23 | 2031-06-22 23:00 | 7.96 | 10.0127 | N | 0
2025-06-23 | 00 | 2031-06-23 | 7.71 | 9.6983 | N | 0
2025-06-23 | 01 | 2031-06-23 01:00 | 7.47 | 9.3964 | N | 0
2025-06-23 | 02 | 2031-06-23 02:00 | 6.95 | 8.7423 | N | 0
2025-06-23 | 03 | 2031-06-23 03:00 | 6.04 | 7.5976 | N | 0
2025-06-23 | 04 | 2031-06-23 04:00 | 5.29 | 6.6542 | N | 0
2025-06-23 | 05 | 2031-06-23 05:00 | 4.75 | 5.9749 | N | 0
2025-06-23 | 06 | 2031-06-23 06:00 | 4.34 | 5.4592 | N | 0
2025-06-23 | 07 | 2031-06-23 07:00 | 3.98 | 5.0064 | N | 0
2025-06-23 | 08 | 2031-06-23 08:00 | 3.77 | 4.7422 | N | 0
2025-06-23 | 09 | 2031-06-23 09:00 | 3.66 | 4.6038 | N | 0
2025-06-23 | 10 | 2031-06-23 10:00 | 4.08 | 5.1322 | N | 0
2025-06-23 | 11 | 2031-06-23 11:00 | 5.23 | 6.5787 | N | 0
2025-06-23 | 12 | 2031-06-23 12:00 | 5.76 | 7.2454 | N | 0
2025-06-23 | 13 | 2031-06-23 13:00 | 6.43 | 8.0882 | N | 0
2025-06-23 | 14 | 2031-06-23 14:00 | 6.75 | 8.4907 | N | 0
2025-06-23 | 15 | 2031-06-23 15:00 | 7.18 | 9.0316 | N | 0
2025-06-23 | 16 | 2031-06-23 16:00 | 7.65 | 9.6228 | N | 0
2025-06-23 | 17 | 2031-06-23 17:00 | 7.88 | 9.9121 | N | 0
2025-06-23 | 18 | 2031-06-23 18:00 | 8 | 10.0631 | N | 0
2025-06-23 | 19 | 2031-06-23 19:00 | 8.42 | 10.5914 | N | 0
2025-06-23 | 20 | 2031-06-23 20:00 | 8.69 | 10.931 | Y | 0.29099 | 1
2025-06-23 | 21 | 2031-06-23 21:00 | 8.69 | 10.931 | Y | 0.29099 | 2
2025-06-23 | 22 | 2031-06-23 22:00 | 8.69 | 10.931 | Y | 0.29099 | 3 | 3
2025-06-23 | 23 | 2031-06-23 23:00 | 8.43 | 10.6039 | N | 0
2025-06-24 | 00 | 2031-06-24 | 7.91 | 9.9498 | N | 0
2025-06-24 | 01 | 2031-06-24 01:00 | 7.66 | 9.6354 | N | 0
2025-06-24 | 02 | 2031-06-24 02:00 | 6.92 | 8.7045 | N | 0
2025-06-24 | 03 | 2031-06-24 03:00 | 6.13 | 7.7108 | N | 0
2025-06-24 | 04 | 2031-06-24 04:00 | 5.57 | 7.0064 | N | 0
2025-06-24 | 05 | 2031-06-24 05:00 | 4.93 | 6.2014 | N | 0
2025-06-24 | 06 | 2031-06-24 06:00 | 4.31 | 5.4215 | N | 0
2025-06-24 | 07 | 2031-06-24 07:00 | 4.02 | 5.0567 | N | 0
2025-06-24 | 08 | 2031-06-24 08:00 | 3.7 | 4.6542 | N | 0
2025-06-24 | 09 | 2031-06-24 09:00 | 3.68 | 4.629 | N | 0
2025-06-24 | 10 | 2031-06-24 10:00 | 4.24 | 5.3334 | N | 0
2025-06-24 | 11 | 2031-06-24 11:00 | 5.22 | 6.5661 | N | 0
2025-06-24 | 12 | 2031-06-24 12:00 | 5.97 | 7.5096 | N | 0
2025-06-24 | 13 | 2031-06-24 13:00 | 6.51 | 8.1888 | N | 0
2025-06-24 | 14 | 2031-06-24 14:00 | 7.04 | 8.8555 | N | 0
2025-06-24 | 15 | 2031-06-24 15:00 | 7.5 | 9.4341 | N | 0
2025-06-24 | 16 | 2031-06-24 16:00 | 7.76 | 9.7612 | N | 0
2025-06-24 | 17 | 2031-06-24 17:00 | 8.06 | 10.1385 | N | 0
2025-06-24 | 18 | 2031-06-24 18:00 | 8.5 | 10.692 | Y | 0.051992 | 1
2025-06-24 | 19 | 2031-06-24 19:00 | 8.5 | 10.692 | Y | 0.051992 | 2
2025-06-24 | 20 | 2031-06-24 20:00 | 9.03 | 11.3587 | Y | 0.71867 | 3
2025-06-24 | 21 | 2031-06-24 21:00 | 9.04 | 11.3712 | Y | 0.73125 | 4
2025-06-24 | 22 | 2031-06-24 22:00 | 9.04 | 11.3712 | Y | 0.73125 | 5
2025-06-24 | 23 | 2031-06-24 23:00 | 9.04 | 11.3712 | Y | 0.73125 | 6
2025-06-25 | 00 | 2031-06-25 | 8.49 | 10.6794 | Y | 0.039414 | 7 | 7
2025-06-25 | 01 | 2031-06-25 01:00 | 8.22 | 10.3398 | N | 0
2025-06-25 | 02 | 2031-06-25 02:00 | 7.5 | 9.4341 | N | 0
2025-06-25 | 03 | 2031-06-25 03:00 | 6.51 | 8.1888 | N | 0
2025-06-25 | 04 | 2031-06-25 04:00 | 5.82 | 7.3209 | N | 0
2025-06-25 | 05 | 2031-06-25 05:00 | 5.1 | 6.4152 | N | 0
2025-06-25 | 06 | 2031-06-25 06:00 | 4.64 | 5.8366 | N | 0
2025-06-25 | 07 | 2031-06-25 07:00 | 4.42 | 5.5598 | N | 0
2025-06-25 | 08 | 2031-06-25 08:00 | 4.15 | 5.2202 | N | 0
2025-06-25 | 09 | 2031-06-25 09:00 | 4.03 | 5.0693 | N | 0
2025-06-25 | 10 | 2031-06-25 10:00 | 4.44 | 5.585 | N | 0
2025-06-25 | 11 | 2031-06-25 11:00 | 4.86 | 6.1133 | N | 0
2025-06-25 | 12 | 2031-06-25 12:00 | 5.14 | 6.4655 | N | 0
2025-06-25 | 13 | 2031-06-25 13:00 | 5.6 | 7.0441 | N | 0
2025-06-25 | 14 | 2031-06-25 14:00 | 6.24 | 7.8492 | N | 0
2025-06-25 | 15 | 2031-06-25 15:00 | 6.65 | 8.3649 | N | 0
2025-06-25 | 16 | 2031-06-25 16:00 | 6.87 | 8.6416 | N | 0
2025-06-25 | 17 | 2031-06-25 17:00 | 7.09 | 8.9184 | N | 0
2025-06-25 | 18 | 2031-06-25 18:00 | 7.1 | 8.931 | N | 0
2025-06-25 | 19 | 2031-06-25 19:00 | 7.55 | 9.497 | N | 0
2025-06-25 | 20 | 2031-06-25 20:00 | 8.02 | 10.0882 | N | 0
2025-06-25 | 21 | 2031-06-25 21:00 | 8.28 | 10.4153 | N | 0
2025-06-25 | 22 | 2031-06-25 22:00 | 8.28 | 10.4153 | N | 0
2025-06-25 | 23 | 2031-06-25 23:00 | 8.02 | 10.0882 | N | 0
2025-06-26 | 00 | 2031-06-26 | 7.51 | 9.4467 | N | 0
2025-06-26 | 01 | 2031-06-26 01:00 | 6.83 | 8.5913 | N | 0
2025-06-26 | 02 | 2031-06-26 02:00 | 6.23 | 7.8366 | N | 0
2025-06-26 | 03 | 2031-06-26 03:00 | 5.43 | 6.8303 | N | 0
2025-06-26 | 04 | 2031-06-26 04:00 | 4.75 | 5.9749 | N | 0
2025-06-26 | 05 | 2031-06-26 05:00 | 4.22 | 5.3083 | N | 0
2025-06-26 | 06 | 2031-06-26 06:00 | 3.9 | 4.9057 | N | 0
2025-06-26 | 07 | 2031-06-26 07:00 | 3.76 | 4.7296 | N | 0
2025-06-26 | 08 | 2031-06-26 08:00 | 3.53 | 4.4403 | N | 0
2025-06-26 | 09 | 2031-06-26 09:00 | 3.48 | 4.3774 | N | 0
2025-06-26 | 10 | 2031-06-26 10:00 | 3.9 | 4.9057 | N | 0
2025-06-26 | 11 | 2031-06-26 11:00 | 4.31 | 5.4215 | N | 0
2025-06-26 | 12 | 2031-06-26 12:00 | 4.6 | 5.7863 | N | 0
2025-06-26 | 13 | 2031-06-26 13:00 | 4.75 | 5.9749 | N | 0
2025-06-26 | 14 | 2031-06-26 14:00 | 4.85 | 6.1007 | N | 0
2025-06-26 | 15 | 2031-06-26 15:00 | 4.89 | 6.151 | N | 0
2025-06-26 | 16 | 2031-06-26 16:00 | 4.8 | 6.0378 | N | 0
2025-06-26 | 17 | 2031-06-26 17:00 | 4.67 | 5.8743 | N | 0
2025-06-26 | 18 | 2031-06-26 18:00 | 4.64 | 5.8366 | N | 0
2025-06-26 | 19 | 2031-06-26 19:00 | 4.6 | 5.7863 | N | 0
2025-06-26 | 20 | 2031-06-26 20:00 | 4.94 | 6.2139 | N | 0
2025-06-26 | 21 | 2031-06-26 21:00 | 5.1 | 6.4152 | N | 0
2025-06-26 | 22 | 2031-06-26 22:00 | 4.95 | 6.2265 | N | 0
2025-06-26 | 23 | 2031-06-26 23:00 | 4.81 | 6.0504 | N | 0
2025-06-27 | 00 | 2031-06-27 | 4.78 | 6.0127 | N | 0
2025-06-27 | 01 | 2031-06-27 01:00 | 4.77 | 6.0001 | N | 0
2025-06-27 | 02 | 2031-06-27 02:00 | 4.47 | 5.6227 | N | 0
2025-06-27 | 03 | 2031-06-27 03:00 | 3.87 | 4.868 | N | 0
2025-06-27 | 04 | 2031-06-27 04:00 | 3.38 | 4.2516 | N | 0
2025-06-27 | 05 | 2031-06-27 05:00 | 3.1 | 3.8994 | N | 0
2025-06-27 | 06 | 2031-06-27 06:00 | 2.8 | 3.5221 | N | 0
2025-06-27 | 07 | 2031-06-27 07:00 | 2.68 | 3.3711 | N | 0
2025-06-27 | 08 | 2031-06-27 08:00 | 2.68 | 3.3711 | N | 0
2025-06-27 | 09 | 2031-06-27 09:00 | 2.76 | 3.4718 | N | 0
2025-06-27 | 10 | 2031-06-27 10:00 | 3.17 | 3.9875 | N | 0
2025-06-27 | 11 | 2031-06-27 11:00 | 3.51 | 4.4152 | N | 0
2025-06-27 | 12 | 2031-06-27 12:00 | 3.85 | 4.8428 | N | 0
2025-06-27 | 13 | 2031-06-27 13:00 | 4.1 | 5.1573 | N | 0
2025-06-27 | 14 | 2031-06-27 14:00 | 4.26 | 5.3586 | N | 0
2025-06-27 | 15 | 2031-06-27 15:00 | 4.36 | 5.4844 | N | 0
2025-06-27 | 16 | 2031-06-27 16:00 | 4.5 | 5.6605 | N | 0
2025-06-27 | 17 | 2031-06-27 17:00 | 4.5 | 5.6605 | N | 0
2025-06-27 | 18 | 2031-06-27 18:00 | 4.46 | 5.6102 | N | 0
2025-06-27 | 19 | 2031-06-27 19:00 | 4.83 | 6.0756 | N | 0
2025-06-27 | 20 | 2031-06-27 20:00 | 5.44 | 6.8429 | N | 0
2025-06-27 | 21 | 2031-06-27 21:00 | 5.77 | 7.258 | N | 0
2025-06-27 | 22 | 2031-06-27 22:00 | 5.8 | 7.2957 | N | 0
2025-06-27 | 23 | 2031-06-27 23:00 | 5.64 | 7.0945 | N | 0
2025-06-28 | 00 | 2031-06-28 | 5.38 | 6.7674 | N | 0
2025-06-28 | 01 | 2031-06-28 01:00 | 5.33 | 6.7045 | N | 0
2025-06-28 | 02 | 2031-06-28 02:00 | 5.06 | 6.3649 | N | 0
2025-06-28 | 03 | 2031-06-28 03:00 | 4.58 | 5.7611 | N | 0
2025-06-28 | 04 | 2031-06-28 04:00 | 4.11 | 5.1699 | N | 0
2025-06-28 | 05 | 2031-06-28 05:00 | 3.59 | 4.5158 | N | 0
2025-06-28 | 06 | 2031-06-28 06:00 | 3.31 | 4.1636 | N | 0
2025-06-28 | 07 | 2031-06-28 07:00 | 3.17 | 3.9875 | N | 0
2025-06-28 | 08 | 2031-06-28 08:00 | 3.08 | 3.8743 | N | 0
2025-06-28 | 09 | 2031-06-28 09:00 | 3.06 | 3.8491 | N | 0
2025-06-28 | 10 | 2031-06-28 10:00 | 3.17 | 3.9875 | N | 0
2025-06-28 | 11 | 2031-06-28 11:00 | 3.67 | 4.6164 | N | 0
2025-06-28 | 12 | 2031-06-28 12:00 | 4.62 | 5.8114 | N | 0
2025-06-28 | 13 | 2031-06-28 13:00 | 5.18 | 6.5158 | N | 0
2025-06-28 | 14 | 2031-06-28 14:00 | 5.6 | 7.0441 | N | 0
2025-06-28 | 15 | 2031-06-28 15:00 | 5.86 | 7.3712 | N | 0
2025-06-28 | 16 | 2031-06-28 16:00 | 6.13 | 7.7108 | N | 0
2025-06-28 | 17 | 2031-06-28 17:00 | 6.19 | 7.7863 | N | 0
2025-06-28 | 18 | 2031-06-28 18:00 | 6.18 | 7.7737 | N | 0
2025-06-28 | 19 | 2031-06-28 19:00 | 6.19 | 7.7863 | N | 0
2025-06-28 | 20 | 2031-06-28 20:00 | 6.22 | 7.824 | N | 0
2025-06-28 | 21 | 2031-06-28 21:00 | 6.17 | 7.7611 | N | 0
2025-06-28 | 22 | 2031-06-28 22:00 | 5.85 | 7.3586 | N | 0
2025-06-28 | 23 | 2031-06-28 23:00 | 5.61 | 7.0567 | N | 0
2025-06-29 | 00 | 2031-06-29 | 5.1 | 6.4152 | N | 0
2025-06-29 | 01 | 2031-06-29 01:00 | 4.69 | 5.8995 | N | 0
2025-06-29 | 02 | 2031-06-29 02:00 | 4.44 | 5.585 | N | 0
2025-06-29 | 03 | 2031-06-29 03:00 | 4.02 | 5.0567 | N | 0
2025-06-29 | 04 | 2031-06-29 04:00 | 3.56 | 4.4781 | N | 0
2025-06-29 | 05 | 2031-06-29 05:00 | 3.13 | 3.9372 | N | 0
2025-06-29 | 06 | 2031-06-29 06:00 | 2.93 | 3.6856 | N | 0
2025-06-29 | 07 | 2031-06-29 07:00 | 2.8 | 3.5221 | N | 0
2025-06-29 | 08 | 2031-06-29 08:00 | 2.66 | 3.346 | N | 0
2025-06-29 | 09 | 2031-06-29 09:00 | 2.68 | 3.3711 | N | 0
2025-06-29 | 10 | 2031-06-29 10:00 | 2.72 | 3.4214 | N | 0
2025-06-29 | 11 | 2031-06-29 11:00 | 3.11 | 3.912 | N | 0
2025-06-29 | 12 | 2031-06-29 12:00 | 3.73 | 4.6919 | N | 0
2025-06-29 | 13 | 2031-06-29 13:00 | 4.19 | 5.2705 | N | 0
2025-06-29 | 14 | 2031-06-29 14:00 | 4.62 | 5.8114 | N | 0
2025-06-29 | 15 | 2031-06-29 15:00 | 4.93 | 6.2014 | N | 0
2025-06-29 | 16 | 2031-06-29 16:00 | 5.07 | 6.3775 | N | 0
2025-06-29 | 17 | 2031-06-29 17:00 | 5.04 | 6.3397 | N | 0
2025-06-29 | 18 | 2031-06-29 18:00 | 5.18 | 6.5158 | N | 0
2025-06-29 | 19 | 2031-06-29 19:00 | 5.52 | 6.9435 | N | 0
2025-06-29 | 20 | 2031-06-29 20:00 | 6.03 | 7.585 | N | 0
2025-06-29 | 21 | 2031-06-29 21:00 | 6.15 | 7.736 | N | 0
2025-06-29 | 22 | 2031-06-29 22:00 | 6.25 | 7.8618 | N | 0
2025-06-29 | 23 | 2031-06-29 23:00 | 6.09 | 7.6605 | N | 0
2025-06-30 | 00 | 2031-06-30 | 5.71 | 7.1825 | N | 0
2025-06-30 | 01 | 2031-06-30 01:00 | 5.21 | 6.5536 | N | 0
2025-06-30 | 02 | 2031-06-30 02:00 | 4.94 | 6.2139 | N | 0
2025-06-30 | 03 | 2031-06-30 03:00 | 4.34 | 5.4592 | N | 0
2025-06-30 | 04 | 2031-06-30 04:00 | 3.74 | 4.7045 | N | 0
2025-06-30 | 05 | 2031-06-30 05:00 | 3.36 | 4.2265 | N | 0
2025-06-30 | 06 | 2031-06-30 06:00 | 3.07 | 3.8617 | N | 0
2025-06-30 | 07 | 2031-06-30 07:00 | 2.9 | 3.6479 | N | 0
2025-06-30 | 08 | 2031-06-30 08:00 | 2.81 | 3.5346 | N | 0
2025-06-30 | 09 | 2031-06-30 09:00 | 2.87 | 3.6101 | N | 0
2025-06-30 | 10 | 2031-06-30 10:00 | 3.28 | 4.1259 | N | 0
2025-06-30 | 11 | 2031-06-30 11:00 | 3.75 | 4.7171 | N | 0
2025-06-30 | 12 | 2031-06-30 12:00 | 4.39 | 5.5221 | N | 0
2025-06-30 | 13 | 2031-06-30 13:00 | 4.91 | 6.1762 | N | 0
2025-06-30 | 14 | 2031-06-30 14:00 | 5.45 | 6.8555 | N | 0
2025-06-30 | 15 | 2031-06-30 15:00 | 5.74 | 7.2202 | N | 0
2025-06-30 | 16 | 2031-06-30 16:00 | 6.03 | 7.585 | N | 0
2025-06-30 | 17 | 2031-06-30 17:00 | 6.21 | 7.8114 | N | 0
2025-06-30 | 18 | 2031-06-30 18:00 | 6.09 | 7.6605 | N | 0
2025-06-30 | 19 | 2031-06-30 19:00 | 6.06 | 7.6228 | N | 0
2025-06-30 | 20 | 2031-06-30 20:00 | 5.91 | 7.4341 | N | 0
2025-06-30 | 21 | 2031-06-30 21:00 | 6.11 | 7.6857 | N | 0
2025-06-30 | 22 | 2031-06-30 22:00 | 6.07 | 7.6353 | N | 0
2025-06-30 | 23 | 2031-06-30 23:00 | 5.9 | 7.4215 | N | 0
2025-07-01 | 00 | 2031-07-01 | 5.61 | 7.0567 | N | 0
2025-07-01 | 01 | 2031-07-01 01:00 | 5.36 | 6.7422 | N | 0
2025-07-01 | 02 | 2031-07-01 02:00 | 4.97 | 6.2517 | N | 0
2025-07-01 | 03 | 2031-07-01 03:00 | 4.43 | 5.5724 | N | 0
2025-07-01 | 04 | 2031-07-01 04:00 | 4.04 | 5.0818 | N | 0
2025-07-01 | 05 | 2031-07-01 05:00 | 3.64 | 4.5787 | N | 0
2025-07-01 | 06 | 2031-07-01 06:00 | 3.37 | 4.2391 | N | 0
2025-07-01 | 07 | 2031-07-01 07:00 | 3.17 | 3.9875 | N | 0
2025-07-01 | 08 | 2031-07-01 08:00 | 3.08 | 3.8743 | N | 0
2025-07-01 | 09 | 2031-07-01 09:00 | 3.12 | 3.9246 | N | 0
2025-07-01 | 10 | 2031-07-01 10:00 | 3.29 | 4.1384 | N | 0
2025-07-01 | 11 | 2031-07-01 11:00 | 3.63 | 4.5661 | N | 0
2025-07-01 | 12 | 2031-07-01 12:00 | 4.38 | 5.5095 | N | 0
2025-07-01 | 13 | 2031-07-01 13:00 | 4.88 | 6.1385 | N | 0
2025-07-01 | 14 | 2031-07-01 14:00 | 5.46 | 6.868 | N | 0
2025-07-01 | 15 | 2031-07-01 15:00 | 5.88 | 7.3963 | N | 0
2025-07-01 | 16 | 2031-07-01 16:00 | 6.19 | 7.7863 | N | 0
2025-07-01 | 17 | 2031-07-01 17:00 | 6.57 | 8.2643 | N | 0
2025-07-01 | 18 | 2031-07-01 18:00 | 7.01 | 8.8177 | N | 0
2025-07-01 | 19 | 2031-07-01 19:00 | 6.99 | 8.7926 | N | 0
2025-07-01 | 20 | 2031-07-01 20:00 | 7.22 | 9.0819 | N | 0
2025-07-01 | 21 | 2031-07-01 21:00 | 7.47 | 9.3964 | N | 0
2025-07-01 | 22 | 2031-07-01 22:00 | 7.26 | 9.1322 | N | 0
2025-07-01 | 23 | 2031-07-01 23:00 | 7.02 | 8.8303 | N | 0
2025-07-02 | 00 | 2031-07-02 | 6.56 | 8.2517 | N | 0
2025-07-02 | 01 | 2031-07-02 01:00 | 6.03 | 7.585 | N | 0
2025-07-02 | 02 | 2031-07-02 02:00 | 5.5 | 6.9183 | N | 0
2025-07-02 | 03 | 2031-07-02 03:00 | 4.96 | 6.2391 | N | 0
2025-07-02 | 04 | 2031-07-02 04:00 | 4.49 | 5.6479 | N | 0
2025-07-02 | 05 | 2031-07-02 05:00 | 3.78 | 4.7548 | N | 0
2025-07-02 | 06 | 2031-07-02 06:00 | 3.44 | 4.3271 | N | 0
2025-07-02 | 07 | 2031-07-02 07:00 | 3.14 | 3.9497 | N | 0
2025-07-02 | 08 | 2031-07-02 08:00 | 2.96 | 3.7233 | N | 0
2025-07-02 | 09 | 2031-07-02 09:00 | 2.97 | 3.7359 | N | 0
2025-07-02 | 10 | 2031-07-02 10:00 | 3.3 | 4.151 | N | 0
2025-07-02 | 11 | 2031-07-02 11:00 | 3.88 | 4.8806 | N | 0
2025-07-02 | 12 | 2031-07-02 12:00 | 4.47 | 5.6227 | N | 0
2025-07-02 | 13 | 2031-07-02 13:00 | 4.93 | 6.2014 | N | 0
2025-07-02 | 14 | 2031-07-02 14:00 | 5.45 | 6.8555 | N | 0
2025-07-02 | 15 | 2031-07-02 15:00 | 5.64 | 7.0945 | N | 0
2025-07-02 | 16 | 2031-07-02 16:00 | 6.21 | 7.8114 | N | 0
2025-07-02 | 17 | 2031-07-02 17:00 | 6.41 | 8.063 | N | 0
2025-07-02 | 18 | 2031-07-02 18:00 | 6.62 | 8.3272 | N | 0
2025-07-02 | 19 | 2031-07-02 19:00 | 6.82 | 8.5788 | N | 0
2025-07-02 | 20 | 2031-07-02 20:00 | 7.28 | 9.1574 | N | 0
2025-07-02 | 21 | 2031-07-02 21:00 | 7.47 | 9.3964 | N | 0
2025-07-02 | 22 | 2031-07-02 22:00 | 6.78 | 8.5284 | N | 0
2025-07-02 | 23 | 2031-07-02 23:00 | 6.54 | 8.2265 | N | 0
2025-07-03 | 00 | 2031-07-03 | 6.17 | 7.7611 | N | 0
2025-07-03 | 01 | 2031-07-03 01:00 | 5.98 | 7.5221 | N | 0
2025-07-03 | 02 | 2031-07-03 02:00 | 5.46 | 6.868 | N | 0
2025-07-03 | 03 | 2031-07-03 03:00 | 4.81 | 6.0504 | N | 0
2025-07-03 | 04 | 2031-07-03 04:00 | 4.22 | 5.3083 | N | 0
2025-07-03 | 05 | 2031-07-03 05:00 | 3.65 | 4.5913 | N | 0
2025-07-03 | 06 | 2031-07-03 06:00 | 3.43 | 4.3145 | N | 0
2025-07-03 | 07 | 2031-07-03 07:00 | 3.22 | 4.0504 | N | 0
2025-07-03 | 08 | 2031-07-03 08:00 | 3.11 | 3.912 | N | 0
2025-07-03 | 09 | 2031-07-03 09:00 | 3.18 | 4.0001 | N | 0
2025-07-03 | 10 | 2031-07-03 10:00 | 3.53 | 4.4403 | N | 0
2025-07-03 | 11 | 2031-07-03 11:00 | 3.96 | 4.9812 | N | 0
2025-07-03 | 12 | 2031-07-03 12:00 | 4.05 | 5.0944 | N | 0
2025-07-03 | 13 | 2031-07-03 13:00 | 4.51 | 5.673 | N | 0
2025-07-03 | 14 | 2031-07-03 14:00 | 5.11 | 6.4278 | N | 0
2025-07-03 | 15 | 2031-07-03 15:00 | 5.54 | 6.9687 | N | 0
2025-07-03 | 16 | 2031-07-03 16:00 | 5.8 | 7.2957 | N | 0
2025-07-03 | 17 | 2031-07-03 17:00 | 5.77 | 7.258 | N | 0
2025-07-03 | 18 | 2031-07-03 18:00 | 5.99 | 7.5347 | N | 0
2025-07-03 | 19 | 2031-07-03 19:00 | 6.22 | 7.824 | N | 0
2025-07-03 | 20 | 2031-07-03 20:00 | 6.5 | 8.1762 | N | 0
2025-07-03 | 21 | 2031-07-03 21:00 | 6.64 | 8.3523 | N | 0
2025-07-03 | 22 | 2031-07-03 22:00 | 6.63 | 8.3398 | N | 0
2025-07-03 | 23 | 2031-07-03 23:00 | 6.2 | 7.7989 | N | 0
2025-07-04 | 00 | 2031-07-04 | 5.8 | 7.2957 | N | 0
2025-07-04 | 01 | 2031-07-04 01:00 | 5.45 | 6.8555 | N | 0
2025-07-04 | 02 | 2031-07-04 02:00 | 4.96 | 6.2391 | N | 0
2025-07-04 | 03 | 2031-07-04 03:00 | 4.27 | 5.3712 | N | 0
2025-07-04 | 04 | 2031-07-04 04:00 | 3.68 | 4.629 | N | 0
2025-07-04 | 05 | 2031-07-04 05:00 | 3.24 | 4.0755 | N | 0
2025-07-04 | 06 | 2031-07-04 06:00 | 2.89 | 3.6353 | N | 0
2025-07-04 | 07 | 2031-07-04 07:00 | 2.71 | 3.4089 | N | 0
2025-07-04 | 08 | 2031-07-04 08:00 | 2.68 | 3.3711 | N | 0
2025-07-04 | 09 | 2031-07-04 09:00 | 2.67 | 3.3585 | N | 0
2025-07-04 | 10 | 2031-07-04 10:00 | 3.06 | 3.8491 | N | 0
2025-07-04 | 11 | 2031-07-04 11:00 | 3.53 | 4.4403 | N | 0
2025-07-04 | 12 | 2031-07-04 12:00 | 3.98 | 5.0064 | N | 0
2025-07-04 | 13 | 2031-07-04 13:00 | 4.44 | 5.585 | N | 0
2025-07-04 | 14 | 2031-07-04 14:00 | 4.81 | 6.0504 | N | 0
2025-07-04 | 15 | 2031-07-04 15:00 | 5.04 | 6.3397 | N | 0
2025-07-04 | 16 | 2031-07-04 16:00 | 5.21 | 6.5536 | N | 0
2025-07-04 | 17 | 2031-07-04 17:00 | 5.39 | 6.78 | N | 0
2025-07-04 | 18 | 2031-07-04 18:00 | 5.58 | 7.019 | N | 0
2025-07-04 | 19 | 2031-07-04 19:00 | 5.68 | 7.1448 | N | 0
2025-07-04 | 20 | 2031-07-04 20:00 | 6.04 | 7.5976 | N | 0
2025-07-04 | 21 | 2031-07-04 21:00 | 6.43 | 8.0882 | N | 0
2025-07-04 | 22 | 2031-07-04 22:00 | 6.29 | 7.9121 | N | 0
2025-07-04 | 23 | 2031-07-04 23:00 | 5.92 | 7.4467 | N | 0
2025-07-05 | 00 | 2031-07-05 | 5.54 | 6.9687 | N | 0
2025-07-05 | 01 | 2031-07-05 01:00 | 5.26 | 6.6165 | N | 0
2025-07-05 | 02 | 2031-07-05 02:00 | 4.83 | 6.0756 | N | 0
2025-07-05 | 03 | 2031-07-05 03:00 | 4.26 | 5.3586 | N | 0
2025-07-05 | 04 | 2031-07-05 04:00 | 3.76 | 4.7296 | N | 0
2025-07-05 | 05 | 2031-07-05 05:00 | 3.29 | 4.1384 | N | 0
2025-07-05 | 06 | 2031-07-05 06:00 | 2.97 | 3.7359 | N | 0
2025-07-05 | 07 | 2031-07-05 07:00 | 2.81 | 3.5346 | N | 0
2025-07-05 | 08 | 2031-07-05 08:00 | 2.69 | 3.3837 | N | 0
2025-07-05 | 09 | 2031-07-05 09:00 | 2.68 | 3.3711 | N | 0
2025-07-05 | 10 | 2031-07-05 10:00 | 2.82 | 3.5472 | N | 0
2025-07-05 | 11 | 2031-07-05 11:00 | 3.16 | 3.9749 | N | 0
2025-07-05 | 12 | 2031-07-05 12:00 | 3.89 | 4.8932 | N | 0
2025-07-05 | 13 | 2031-07-05 13:00 | 4.38 | 5.5095 | N | 0
2025-07-05 | 14 | 2031-07-05 14:00 | 4.97 | 6.2517 | N | 0
2025-07-05 | 15 | 2031-07-05 15:00 | 5.34 | 6.7171 | N | 0
2025-07-05 | 16 | 2031-07-05 16:00 | 5.64 | 7.0945 | N | 0
2025-07-05 | 17 | 2031-07-05 17:00 | 5.78 | 7.2706 | N | 0
2025-07-05 | 18 | 2031-07-05 18:00 | 5.99 | 7.5347 | N | 0
2025-07-05 | 19 | 2031-07-05 19:00 | 6.32 | 7.9498 | N | 0
2025-07-05 | 20 | 2031-07-05 20:00 | 6.55 | 8.2391 | N | 0
2025-07-05 | 21 | 2031-07-05 21:00 | 6.75 | 8.4907 | N | 0
2025-07-05 | 22 | 2031-07-05 22:00 | 6.75 | 8.4907 | N | 0
2025-07-05 | 23 | 2031-07-05 23:00 | 6.52 | 8.2014 | N | 0
2025-07-06 | 00 | 2031-07-06 | 6.11 | 7.6857 | N | 0
2025-07-06 | 01 | 2031-07-06 01:00 | 5.92 | 7.4467 | N | 0
2025-07-06 | 02 | 2031-07-06 02:00 | 5.54 | 6.9687 | N | 0
2025-07-06 | 03 | 2031-07-06 03:00 | 5.16 | 6.4907 | N | 0
2025-07-06 | 04 | 2031-07-06 04:00 | 4.62 | 5.8114 | N | 0
2025-07-06 | 05 | 2031-07-06 05:00 | 4.09 | 5.1447 | N | 0
2025-07-06 | 06 | 2031-07-06 06:00 | 3.72 | 4.6793 | N | 0
2025-07-06 | 07 | 2031-07-06 07:00 | 3.43 | 4.3145 | N | 0
2025-07-06 | 08 | 2031-07-06 08:00 | 3.29 | 4.1384 | N | 0
2025-07-06 | 09 | 2031-07-06 09:00 | 3.17 | 3.9875 | N | 0
2025-07-06 | 10 | 2031-07-06 10:00 | 3.3 | 4.151 | N | 0
2025-07-06 | 11 | 2031-07-06 11:00 | 3.98 | 5.0064 | N | 0
2025-07-06 | 12 | 2031-07-06 12:00 | 4.96 | 6.2391 | N | 0
2025-07-06 | 13 | 2031-07-06 13:00 | 5.74 | 7.2202 | N | 0
2025-07-06 | 14 | 2031-07-06 14:00 | 6.32 | 7.9498 | N | 0
2025-07-06 | 15 | 2031-07-06 15:00 | 6.82 | 8.5788 | N | 0
2025-07-06 | 16 | 2031-07-06 16:00 | 7.23 | 9.0945 | N | 0
2025-07-06 | 17 | 2031-07-06 17:00 | 7.47 | 9.3964 | N | 0
2025-07-06 | 18 | 2031-07-06 18:00 | 7.69 | 9.6731 | N | 0
2025-07-06 | 19 | 2031-07-06 19:00 | 7.93 | 9.975 | N | 0
2025-07-06 | 20 | 2031-07-06 20:00 | 8.2 | 10.3146 | N | 0
2025-07-06 | 21 | 2031-07-06 21:00 | 8.2 | 10.3146 | N | 0
2025-07-06 | 22 | 2031-07-06 22:00 | 8.2 | 10.3146 | N | 0
2025-07-06 | 23 | 2031-07-06 23:00 | 8.2 | 10.3146 | N | 0
2025-07-07 | 00 | 2031-07-07 | 7.69 | 9.6731 | N | 0
2025-07-07 | 01 | 2031-07-07 01:00 | 7.46 | 9.3838 | N | 0
2025-07-07 | 02 | 2031-07-07 02:00 | 6.98 | 8.78 | N | 0
2025-07-07 | 03 | 2031-07-07 03:00 | 6.17 | 7.7611 | N | 0
2025-07-07 | 04 | 2031-07-07 04:00 | 5.3 | 6.6668 | N | 0
2025-07-07 | 05 | 2031-07-07 05:00 | 4.75 | 5.9749 | N | 0
2025-07-07 | 06 | 2031-07-07 06:00 | 4.31 | 5.4215 | N | 0
2025-07-07 | 07 | 2031-07-07 07:00 | 4.15 | 5.2202 | N | 0
2025-07-07 | 08 | 2031-07-07 08:00 | 4.06 | 5.107 | N | 0
2025-07-07 | 09 | 2031-07-07 09:00 | 4.01 | 5.0441 | N | 0
2025-07-07 | 10 | 2031-07-07 10:00 | 4.49 | 5.6479 | N | 0
2025-07-07 | 11 | 2031-07-07 11:00 | 5.12 | 6.4404 | N | 0
2025-07-07 | 12 | 2031-07-07 12:00 | 5.8 | 7.2957 | N | 0
2025-07-07 | 13 | 2031-07-07 13:00 | 6.48 | 8.1511 | N | 0
2025-07-07 | 14 | 2031-07-07 14:00 | 7.17 | 9.019 | N | 0
2025-07-07 | 15 | 2031-07-07 15:00 | 7.42 | 9.3335 | N | 0
2025-07-07 | 16 | 2031-07-07 16:00 | 7.68 | 9.6605 | N | 0
2025-07-07 | 17 | 2031-07-07 17:00 | 7.43 | 9.3461 | N | 0
2025-07-07 | 18 | 2031-07-07 18:00 | 7.66 | 9.6354 | N | 0
2025-07-07 | 19 | 2031-07-07 19:00 | 7.89 | 9.9247 | N | 0
2025-07-07 | 20 | 2031-07-07 20:00 | 7.89 | 9.9247 | N | 0
2025-07-07 | 21 | 2031-07-07 21:00 | 8.12 | 10.214 | N | 0
2025-07-07 | 22 | 2031-07-07 22:00 | 7.76 | 9.7612 | N | 0
2025-07-07 | 23 | 2031-07-07 23:00 | 7.26 | 9.1322 | N | 0
2025-07-08 | 00 | 2031-07-08 | 6.89 | 8.6668 | N | 0
2025-07-08 | 01 | 2031-07-08 01:00 | 6.68 | 8.4026 | N | 0
2025-07-08 | 02 | 2031-07-08 02:00 | 6.15 | 7.736 | N | 0
2025-07-08 | 03 | 2031-07-08 03:00 | 5.3 | 6.6668 | N | 0
2025-07-08 | 04 | 2031-07-08 04:00 | 4.59 | 5.7737 | N | 0
2025-07-08 | 05 | 2031-07-08 05:00 | 4.12 | 5.1825 | N | 0
2025-07-08 | 06 | 2031-07-08 06:00 | 3.84 | 4.8303 | N | 0
2025-07-08 | 07 | 2031-07-08 07:00 | 3.58 | 4.5032 | N | 0
2025-07-08 | 08 | 2031-07-08 08:00 | 3.47 | 4.3648 | N | 0
2025-07-08 | 09 | 2031-07-08 09:00 | 3.53 | 4.4403 | N | 0
2025-07-08 | 10 | 2031-07-08 10:00 | 3.89 | 4.8932 | N | 0
2025-07-08 | 11 | 2031-07-08 11:00 | 4.37 | 5.4969 | N | 0
2025-07-08 | 12 | 2031-07-08 12:00 | 4.7 | 5.912 | N | 0
2025-07-08 | 13 | 2031-07-08 13:00 | 5.14 | 6.4655 | N | 0
2025-07-08 | 14 | 2031-07-08 14:00 | 5.18 | 6.5158 | N | 0
2025-07-08 | 15 | 2031-07-08 15:00 | 5.34 | 6.7171 | N | 0
2025-07-08 | 16 | 2031-07-08 16:00 | 5.64 | 7.0945 | N | 0
2025-07-08 | 17 | 2031-07-08 17:00 | 6.06 | 7.6228 | N | 0
2025-07-08 | 18 | 2031-07-08 18:00 | 6.25 | 7.8618 | N | 0
2025-07-08 | 19 | 2031-07-08 19:00 | 6.59 | 8.2894 | N | 0
2025-07-08 | 20 | 2031-07-08 20:00 | 6.81 | 8.5662 | N | 0
2025-07-08 | 21 | 2031-07-08 21:00 | 7.17 | 9.019 | N | 0
2025-07-08 | 22 | 2031-07-08 22:00 | 7.17 | 9.019 | N | 0
2025-07-08 | 23 | 2031-07-08 23:00 | 6.74 | 8.4781 | N | 0
2025-07-09 | 00 | 2031-07-09 | 6.32 | 7.9498 | N | 0
2025-07-09 | 01 | 2031-07-09 01:00 | 6.03 | 7.585 | N | 0
2025-07-09 | 02 | 2031-07-09 02:00 | 5.65 | 7.107 | N | 0
2025-07-09 | 03 | 2031-07-09 03:00 | 4.82 | 6.063 | N | 0
2025-07-09 | 04 | 2031-07-09 04:00 | 4.16 | 5.2328 | N | 0
2025-07-09 | 05 | 2031-07-09 05:00 | 3.65 | 4.5913 | N | 0
2025-07-09 | 06 | 2031-07-09 06:00 | 3.38 | 4.2516 | N | 0
2025-07-09 | 07 | 2031-07-09 07:00 | 3.18 | 4.0001 | N | 0
2025-07-09 | 08 | 2031-07-09 08:00 | 3.05 | 3.8365 | N | 0
2025-07-09 | 09 | 2031-07-09 09:00 | 3.1 | 3.8994 | N | 0
2025-07-09 | 10 | 2031-07-09 10:00 | 3.57 | 4.4906 | N | 0
2025-07-09 | 11 | 2031-07-09 11:00 | 3.88 | 4.8806 | N | 0
2025-07-09 | 12 | 2031-07-09 12:00 | 4.24 | 5.3334 | N | 0
2025-07-09 | 13 | 2031-07-09 13:00 | 4.5 | 5.6605 | N | 0
2025-07-09 | 14 | 2031-07-09 14:00 | 5.09 | 6.4026 | N | 0
2025-07-09 | 15 | 2031-07-09 15:00 | 5.85 | 7.3586 | N | 0
2025-07-09 | 16 | 2031-07-09 16:00 | 6.2 | 7.7989 | N | 0
2025-07-09 | 17 | 2031-07-09 17:00 | 6.23 | 7.8366 | N | 0
2025-07-09 | 18 | 2031-07-09 18:00 | 6.23 | 7.8366 | N | 0
2025-07-09 | 19 | 2031-07-09 19:00 | 6.24 | 7.8492 | N | 0
2025-07-09 | 20 | 2031-07-09 20:00 | 6.93 | 8.7171 | N | 0
2025-07-09 | 21 | 2031-07-09 21:00 | 7.15 | 8.9939 | N | 0
2025-07-09 | 22 | 2031-07-09 22:00 | 7.15 | 8.9939 | N | 0
2025-07-09 | 23 | 2031-07-09 23:00 | 6.5 | 8.1762 | N | 0
2025-07-10 | 00 | 2031-07-10 | 6.27 | 7.8869 | N | 0
2025-07-10 | 01 | 2031-07-10 01:00 | 6.06 | 7.6228 | N | 0
2025-07-10 | 02 | 2031-07-10 02:00 | 5.6 | 7.0441 | N | 0
2025-07-10 | 03 | 2031-07-10 03:00 | 4.79 | 6.0253 | N | 0
2025-07-10 | 04 | 2031-07-10 04:00 | 4.17 | 5.2454 | N | 0
2025-07-10 | 05 | 2031-07-10 05:00 | 3.77 | 4.7422 | N | 0
2025-07-10 | 06 | 2031-07-10 06:00 | 3.43 | 4.3145 | N | 0
2025-07-10 | 07 | 2031-07-10 07:00 | 3.15 | 3.9623 | N | 0
2025-07-10 | 08 | 2031-07-10 08:00 | 3.06 | 3.8491 | N | 0
2025-07-10 | 09 | 2031-07-10 09:00 | 3.06 | 3.8491 | N | 0
2025-07-10 | 10 | 2031-07-10 10:00 | 3.55 | 4.4655 | N | 0
2025-07-10 | 11 | 2031-07-10 11:00 | 3.88 | 4.8806 | N | 0
2025-07-10 | 12 | 2031-07-10 12:00 | 4.61 | 5.7988 | N | 0
2025-07-10 | 13 | 2031-07-10 13:00 | 5.37 | 6.7548 | N | 0
2025-07-10 | 14 | 2031-07-10 14:00 | 5.87 | 7.3838 | N | 0
2025-07-10 | 15 | 2031-07-10 15:00 | 6.03 | 7.585 | N | 0
2025-07-10 | 16 | 2031-07-10 16:00 | 6.24 | 7.8492 | N | 0
2025-07-10 | 17 | 2031-07-10 17:00 | 6.65 | 8.3649 | N | 0
2025-07-10 | 18 | 2031-07-10 18:00 | 6.74 | 8.4781 | N | 0
2025-07-10 | 19 | 2031-07-10 19:00 | 6.83 | 8.5913 | N | 0
2025-07-10 | 20 | 2031-07-10 20:00 | 7.03 | 8.8429 | N | 0
2025-07-10 | 21 | 2031-07-10 21:00 | 7.36 | 9.258 | N | 0
2025-07-10 | 22 | 2031-07-10 22:00 | 7.34 | 9.2328 | N | 0
2025-07-10 | 23 | 2031-07-10 23:00 | 7.34 | 9.2328 | N | 0
2025-07-11 | 00 | 2031-07-11 | 7.06 | 8.8806 | N | 0
2025-07-11 | 01 | 2031-07-11 01:00 | 6.54 | 8.2265 | N | 0
2025-07-11 | 02 | 2031-07-11 02:00 | 5.94 | 7.4718 | N | 0
2025-07-11 | 03 | 2031-07-11 03:00 | 5.33 | 6.7045 | N | 0
2025-07-11 | 04 | 2031-07-11 04:00 | 4.57 | 5.7485 | N | 0
2025-07-11 | 05 | 2031-07-11 05:00 | 4.12 | 5.1825 | N | 0
2025-07-11 | 06 | 2031-07-11 06:00 | 3.73 | 4.6919 | N | 0
2025-07-11 | 07 | 2031-07-11 07:00 | 3.54 | 4.4529 | N | 0
2025-07-11 | 08 | 2031-07-11 08:00 | 3.35 | 4.2139 | N | 0
2025-07-11 | 09 | 2031-07-11 09:00 | 3.32 | 4.1762 | N | 0
2025-07-11 | 10 | 2031-07-11 10:00 | 3.69 | 4.6416 | N | 0
2025-07-11 | 11 | 2031-07-11 11:00 | 4.12 | 5.1825 | N | 0
2025-07-11 | 12 | 2031-07-11 12:00 | 4.76 | 5.9875 | N | 0
2025-07-11 | 13 | 2031-07-11 13:00 | 5.34 | 6.7171 | N | 0
2025-07-11 | 14 | 2031-07-11 14:00 | 5.87 | 7.3838 | N | 0
2025-07-11 | 15 | 2031-07-11 15:00 | 6.43 | 8.0882 | N | 0
2025-07-11 | 16 | 2031-07-11 16:00 | 6.62 | 8.3272 | N | 0
2025-07-11 | 17 | 2031-07-11 17:00 | 6.82 | 8.5788 | N | 0
2025-07-11 | 18 | 2031-07-11 18:00 | 7.25 | 9.1196 | N | 0
2025-07-11 | 19 | 2031-07-11 19:00 | 7.48 | 9.409 | N | 0
2025-07-11 | 20 | 2031-07-11 20:00 | 7.71 | 9.6983 | N | 0
2025-07-11 | 21 | 2031-07-11 21:00 | 7.89 | 9.9247 | N | 0
2025-07-11 | 22 | 2031-07-11 22:00 | 7.71 | 9.6983 | N | 0
2025-07-11 | 23 | 2031-07-11 23:00 | 7.46 | 9.3838 | N | 0
2025-07-12 | 00 | 2031-07-12 | 7.02 | 8.8303 | N | 0
2025-07-12 | 01 | 2031-07-12 01:00 | 6.64 | 8.3523 | N | 0
2025-07-12 | 02 | 2031-07-12 02:00 | 6.41 | 8.063 | N | 0
2025-07-12 | 03 | 2031-07-12 03:00 | 5.79 | 7.2831 | N | 0
2025-07-12 | 04 | 2031-07-12 04:00 | 5.11 | 6.4278 | N | 0
2025-07-12 | 05 | 2031-07-12 05:00 | 4.58 | 5.7611 | N | 0
2025-07-12 | 06 | 2031-07-12 06:00 | 4.15 | 5.2202 | N | 0
2025-07-12 | 07 | 2031-07-12 07:00 | 3.82 | 4.8051 | N | 0
2025-07-12 | 08 | 2031-07-12 08:00 | 3.65 | 4.5913 | N | 0
2025-07-12 | 09 | 2031-07-12 09:00 | 3.6 | 4.5284 | N | 0
2025-07-12 | 10 | 2031-07-12 10:00 | 3.73 | 4.6919 | N | 0
2025-07-12 | 11 | 2031-07-12 11:00 | 4.1 | 5.1573 | N | 0
2025-07-12 | 12 | 2031-07-12 12:00 | 4.82 | 6.063 | N | 0
2025-07-12 | 13 | 2031-07-12 13:00 | 5.91 | 7.4341 | N | 0
2025-07-12 | 14 | 2031-07-12 14:00 | 6.52 | 8.2014 | N | 0
2025-07-12 | 15 | 2031-07-12 15:00 | 6.95 | 8.7423 | N | 0
2025-07-12 | 16 | 2031-07-12 16:00 | 6.95 | 8.7423 | N | 0
2025-07-12 | 17 | 2031-07-12 17:00 | 7.18 | 9.0316 | N | 0
2025-07-12 | 18 | 2031-07-12 18:00 | 7.18 | 9.0316 | N | 0
2025-07-12 | 19 | 2031-07-12 19:00 | 7.5 | 9.4341 | N | 0
2025-07-12 | 20 | 2031-07-12 20:00 | 7.64 | 9.6102 | N | 0
2025-07-12 | 21 | 2031-07-12 21:00 | 7.64 | 9.6102 | N | 0
2025-07-12 | 22 | 2031-07-12 22:00 | 7.64 | 9.6102 | N | 0
2025-07-12 | 23 | 2031-07-12 23:00 | 7.44 | 9.3586 | N | 0
2025-07-13 | 00 | 2031-07-13 | 7.18 | 9.0316 | N | 0
2025-07-13 | 01 | 2031-07-13 01:00 | 6.95 | 8.7423 | N | 0
2025-07-13 | 02 | 2031-07-13 02:00 | 6.61 | 8.3146 | N | 0
2025-07-13 | 03 | 2031-07-13 03:00 | 6.07 | 7.6353 | N | 0
2025-07-13 | 04 | 2031-07-13 04:00 | 5.49 | 6.9058 | N | 0
2025-07-13 | 05 | 2031-07-13 05:00 | 4.88 | 6.1385 | N | 0
2025-07-13 | 06 | 2031-07-13 06:00 | 4.63 | 5.824 | N | 0
2025-07-13 | 07 | 2031-07-13 07:00 | 4.35 | 5.4718 | N | 0
2025-07-13 | 08 | 2031-07-13 08:00 | 4.09 | 5.1447 | N | 0
2025-07-13 | 09 | 2031-07-13 09:00 | 3.92 | 4.9309 | N | 0
2025-07-13 | 10 | 2031-07-13 10:00 | 4.03 | 5.0693 | N | 0
2025-07-13 | 11 | 2031-07-13 11:00 | 4.34 | 5.4592 | N | 0
2025-07-13 | 12 | 2031-07-13 12:00 | 5.32 | 6.6919 | N | 0
2025-07-13 | 13 | 2031-07-13 13:00 | 6.31 | 7.9372 | N | 0
2025-07-13 | 14 | 2031-07-13 14:00 | 6.66 | 8.3775 | N | 0
2025-07-13 | 15 | 2031-07-13 15:00 | 6.18 | 7.7737 | N | 0
2025-07-13 | 16 | 2031-07-13 16:00 | 6.36 | 8.0001 | N | 0
2025-07-13 | 17 | 2031-07-13 17:00 | 6.87 | 8.6416 | N | 0
2025-07-13 | 18 | 2031-07-13 18:00 | 7.1 | 8.931 | N | 0
2025-07-13 | 19 | 2031-07-13 19:00 | 7.54 | 9.4844 | N | 0
2025-07-13 | 20 | 2031-07-13 20:00 | 7.87 | 9.8995 | N | 0
2025-07-13 | 21 | 2031-07-13 21:00 | 8.02 | 10.0882 | N | 0
2025-07-13 | 22 | 2031-07-13 22:00 | 8.02 | 10.0882 | N | 0
2025-07-13 | 23 | 2031-07-13 23:00 | 7.76 | 9.7612 | N | 0
2025-07-14 | 00 | 2031-07-14 | 7.5 | 9.4341 | N | 0
2025-07-14 | 01 | 2031-07-14 01:00 | 7.02 | 8.8303 | N | 0
2025-07-14 | 02 | 2031-07-14 02:00 | 6.54 | 8.2265 | N | 0
2025-07-14 | 03 | 2031-07-14 03:00 | 5.69 | 7.1573 | N | 0
2025-07-14 | 04 | 2031-07-14 04:00 | 5 | 6.2894 | N | 0
2025-07-14 | 05 | 2031-07-14 05:00 | 4.23 | 5.3208 | N | 0
2025-07-14 | 06 | 2031-07-14 06:00 | 3.96 | 4.9812 | N | 0
2025-07-14 | 07 | 2031-07-14 07:00 | 3.62 | 4.5535 | N | 0
2025-07-14 | 08 | 2031-07-14 08:00 | 3.49 | 4.39 | N | 0
2025-07-14 | 09 | 2031-07-14 09:00 | 3.49 | 4.39 | N | 0
2025-07-14 | 10 | 2031-07-14 10:00 | 3.92 | 4.9309 | N | 0
2025-07-14 | 11 | 2031-07-14 11:00 | 4.19 | 5.2705 | N | 0
2025-07-14 | 12 | 2031-07-14 12:00 | 4.67 | 5.8743 | N | 0
2025-07-14 | 13 | 2031-07-14 13:00 | 5.02 | 6.3146 | N | 0
2025-07-14 | 14 | 2031-07-14 14:00 | 5.53 | 6.9561 | N | 0
2025-07-14 | 15 | 2031-07-14 15:00 | 5.89 | 7.4089 | N | 0
2025-07-14 | 16 | 2031-07-14 16:00 | 6.33 | 7.9624 | N | 0
2025-07-14 | 17 | 2031-07-14 17:00 | 6.74 | 8.4781 | N | 0
2025-07-14 | 18 | 2031-07-14 18:00 | 6.89 | 8.6668 | N | 0
2025-07-14 | 19 | 2031-07-14 19:00 | 7.11 | 8.9435 | N | 0
2025-07-14 | 20 | 2031-07-14 20:00 | 7.57 | 9.5222 | N | 0
2025-07-14 | 21 | 2031-07-14 21:00 | 7.86 | 9.8869 | N | 0
2025-07-14 | 22 | 2031-07-14 22:00 | 7.83 | 9.8492 | N | 0
2025-07-14 | 23 | 2031-07-14 23:00 | 7.38 | 9.2832 | N | 0
2025-07-15 | 00 | 2031-07-15 | 7.13 | 8.9687 | N | 0
2025-07-15 | 01 | 2031-07-15 01:00 | 6.68 | 8.4026 | N | 0
2025-07-15 | 02 | 2031-07-15 02:00 | 6.16 | 7.7485 | N | 0
2025-07-15 | 03 | 2031-07-15 03:00 | 5.45 | 6.8555 | N | 0
2025-07-15 | 04 | 2031-07-15 04:00 | 4.6 | 5.7863 | N | 0
2025-07-15 | 05 | 2031-07-15 05:00 | 4.04 | 5.0818 | N | 0
2025-07-15 | 06 | 2031-07-15 06:00 | 3.71 | 4.6667 | N | 0
2025-07-15 | 07 | 2031-07-15 07:00 | 3.43 | 4.3145 | N | 0
2025-07-15 | 08 | 2031-07-15 08:00 | 3.28 | 4.1259 | N | 0
2025-07-15 | 09 | 2031-07-15 09:00 | 3.22 | 4.0504 | N | 0
2025-07-15 | 10 | 2031-07-15 10:00 | 3.64 | 4.5787 | N | 0
2025-07-15 | 11 | 2031-07-15 11:00 | 4.27 | 5.3712 | N | 0
2025-07-15 | 12 | 2031-07-15 12:00 | 4.97 | 6.2517 | N | 0
2025-07-15 | 13 | 2031-07-15 13:00 | 5.64 | 7.0945 | N | 0
2025-07-15 | 14 | 2031-07-15 14:00 | 6.29 | 7.9121 | N | 0
2025-07-15 | 15 | 2031-07-15 15:00 | 6.68 | 8.4026 | N | 0
2025-07-15 | 16 | 2031-07-15 16:00 | 7.12 | 8.9561 | N | 0
2025-07-15 | 17 | 2031-07-15 17:00 | 7.12 | 8.9561 | N | 0
2025-07-15 | 18 | 2031-07-15 18:00 | 7.33 | 9.2203 | N | 0
2025-07-15 | 19 | 2031-07-15 19:00 | 7.7 | 9.6857 | N | 0
2025-07-15 | 20 | 2031-07-15 20:00 | 8.04 | 10.1134 | N | 0
2025-07-15 | 21 | 2031-07-15 21:00 | 8.09 | 10.1763 | N | 0
2025-07-15 | 22 | 2031-07-15 22:00 | 8.09 | 10.1763 | N | 0
2025-07-15 | 23 | 2031-07-15 23:00 | 7.85 | 9.8744 | N | 0
2025-07-16 | 00 | 2031-07-16 | 7.37 | 9.2706 | N | 0
2025-07-16 | 01 | 2031-07-16 01:00 | 7.14 | 8.9813 | N | 0
2025-07-16 | 02 | 2031-07-16 02:00 | 6.45 | 8.1133 | N | 0
2025-07-16 | 03 | 2031-07-16 03:00 | 5.71 | 7.1825 | N | 0
2025-07-16 | 04 | 2031-07-16 04:00 | 4.96 | 6.2391 | N | 0
2025-07-16 | 05 | 2031-07-16 05:00 | 4.38 | 5.5095 | N | 0
2025-07-16 | 06 | 2031-07-16 06:00 | 3.98 | 5.0064 | N | 0
2025-07-16 | 07 | 2031-07-16 07:00 | 3.61 | 4.541 | N | 0
2025-07-16 | 08 | 2031-07-16 08:00 | 3.5 | 4.4026 | N | 0
2025-07-16 | 09 | 2031-07-16 09:00 | 3.4 | 4.2768 | N | 0
2025-07-16 | 10 | 2031-07-16 10:00 | 3.91 | 4.9183 | N | 0
2025-07-16 | 11 | 2031-07-16 11:00 | 4.45 | 5.5976 | N | 0
2025-07-16 | 12 | 2031-07-16 12:00 | 5.16 | 6.4907 | N | 0
2025-07-16 | 13 | 2031-07-16 13:00 | 5.9 | 7.4215 | N | 0
2025-07-16 | 14 | 2031-07-16 14:00 | 6.66 | 8.3775 | N | 0
2025-07-16 | 15 | 2031-07-16 15:00 | 6.98 | 8.78 | N | 0
2025-07-16 | 16 | 2031-07-16 16:00 | 7.34 | 9.2328 | N | 0
2025-07-16 | 17 | 2031-07-16 17:00 | 7.38 | 9.2832 | N | 0
2025-07-16 | 18 | 2031-07-16 18:00 | 7.56 | 9.5096 | N | 0
2025-07-16 | 19 | 2031-07-16 19:00 | 7.99 | 10.0505 | N | 0
2025-07-16 | 20 | 2031-07-16 20:00 | 8.29 | 10.4278 | N | 0
2025-07-16 | 21 | 2031-07-16 21:00 | 8.29 | 10.4278 | N | 0
2025-07-16 | 22 | 2031-07-16 22:00 | 8.29 | 10.4278 | N | 0
2025-07-16 | 23 | 2031-07-16 23:00 | 8.03 | 10.1008 | N | 0
2025-07-17 | 00 | 2031-07-17 | 7.74 | 9.736 | N | 0
2025-07-17 | 01 | 2031-07-17 01:00 | 7.52 | 9.4593 | N | 0
2025-07-17 | 02 | 2031-07-17 02:00 | 7.07 | 8.8932 | N | 0
2025-07-17 | 03 | 2031-07-17 03:00 | 6.33 | 7.9624 | N | 0
2025-07-17 | 04 | 2031-07-17 04:00 | 5.77 | 7.258 | N | 0
2025-07-17 | 05 | 2031-07-17 05:00 | 5.34 | 6.7171 | N | 0
2025-07-17 | 06 | 2031-07-17 06:00 | 4.83 | 6.0756 | N | 0
2025-07-17 | 07 | 2031-07-17 07:00 | 4.52 | 5.6856 | N | 0
2025-07-17 | 08 | 2031-07-17 08:00 | 4.43 | 5.5724 | N | 0
2025-07-17 | 09 | 2031-07-17 09:00 | 4.33 | 5.4466 | N | 0
2025-07-17 | 10 | 2031-07-17 10:00 | 4.82 | 6.063 | N | 0
2025-07-17 | 11 | 2031-07-17 11:00 | 5.18 | 6.5158 | N | 0
2025-07-17 | 12 | 2031-07-17 12:00 | 5.62 | 7.0693 | N | 0
2025-07-17 | 13 | 2031-07-17 13:00 | 6.59 | 8.2894 | N | 0
2025-07-17 | 14 | 2031-07-17 14:00 | 7 | 8.8052 | N | 0
2025-07-17 | 15 | 2031-07-17 15:00 | 7.18 | 9.0316 | N | 0
2025-07-17 | 16 | 2031-07-17 16:00 | 7.2 | 9.0567 | N | 0
2025-07-17 | 17 | 2031-07-17 17:00 | 7.2 | 9.0567 | N | 0
2025-07-17 | 18 | 2031-07-17 18:00 | 7.18 | 9.0316 | N | 0
2025-07-17 | 19 | 2031-07-17 19:00 | 6.96 | 8.7549 | N | 0
2025-07-17 | 20 | 2031-07-17 20:00 | 7.18 | 9.0316 | N | 0
2025-07-17 | 21 | 2031-07-17 21:00 | 7.18 | 9.0316 | N | 0
2025-07-17 | 22 | 2031-07-17 22:00 | 6.95 | 8.7423 | N | 0
2025-07-17 | 23 | 2031-07-17 23:00 | 6.12 | 7.6982 | N | 0
2025-07-18 | 00 | 2031-07-18 | 5.72 | 7.1951 | N | 0
2025-07-18 | 01 | 2031-07-18 01:00 | 5.37 | 6.7548 | N | 0
2025-07-18 | 02 | 2031-07-18 02:00 | 4.95 | 6.2265 | N | 0
2025-07-18 | 03 | 2031-07-18 03:00 | 4.3 | 5.4089 | N | 0
2025-07-18 | 04 | 2031-07-18 04:00 | 3.76 | 4.7296 | N | 0
2025-07-18 | 05 | 2031-07-18 05:00 | 3.4 | 4.2768 | N | 0
2025-07-18 | 06 | 2031-07-18 06:00 | 2.98 | 3.7485 | N | 0
2025-07-18 | 07 | 2031-07-18 07:00 | 2.8 | 3.5221 | N | 0
2025-07-18 | 08 | 2031-07-18 08:00 | 2.67 | 3.3585 | N | 0
2025-07-18 | 09 | 2031-07-18 09:00 | 2.69 | 3.3837 | N | 0
2025-07-18 | 10 | 2031-07-18 10:00 | 3.08 | 3.8743 | N | 0
2025-07-18 | 11 | 2031-07-18 11:00 | 3.48 | 4.3774 | N | 0
2025-07-18 | 12 | 2031-07-18 12:00 | 3.9 | 4.9057 | N | 0
2025-07-18 | 13 | 2031-07-18 13:00 | 4.39 | 5.5221 | N | 0
2025-07-18 | 14 | 2031-07-18 14:00 | 4.54 | 5.7108 | N | 0
2025-07-18 | 15 | 2031-07-18 15:00 | 4.78 | 6.0127 | N | 0
2025-07-18 | 16 | 2031-07-18 16:00 | 4.86 | 6.1133 | N | 0
2025-07-18 | 17 | 2031-07-18 17:00 | 5.02 | 6.3146 | N | 0
2025-07-18 | 18 | 2031-07-18 18:00 | 5.08 | 6.39 | N | 0
2025-07-18 | 19 | 2031-07-18 19:00 | 5.33 | 6.7045 | N | 0
2025-07-18 | 20 | 2031-07-18 20:00 | 5.42 | 6.8177 | N | 0
2025-07-18 | 21 | 2031-07-18 21:00 | 5.65 | 7.107 | N | 0
2025-07-18 | 22 | 2031-07-18 22:00 | 5.52 | 6.9435 | N | 0
2025-07-18 | 23 | 2031-07-18 23:00 | 5.26 | 6.6165 | N | 0
2025-07-19 | 00 | 2031-07-19 | 5.06 | 6.3649 | N | 0
2025-07-19 | 01 | 2031-07-19 01:00 | 4.76 | 5.9875 | N | 0
2025-07-19 | 02 | 2031-07-19 02:00 | 4.4 | 5.5347 | N | 0
2025-07-19 | 03 | 2031-07-19 03:00 | 3.91 | 4.9183 | N | 0
2025-07-19 | 04 | 2031-07-19 04:00 | 3.47 | 4.3648 | N | 0
2025-07-19 | 05 | 2031-07-19 05:00 | 3.09 | 3.8869 | N | 0
2025-07-19 | 06 | 2031-07-19 06:00 | 2.83 | 3.5598 | N | 0
2025-07-19 | 07 | 2031-07-19 07:00 | 2.66 | 3.346 | N | 0
2025-07-19 | 08 | 2031-07-19 08:00 | 2.6 | 3.2705 | N | 0
2025-07-19 | 09 | 2031-07-19 09:00 | 2.58 | 3.2453 | N | 0
2025-07-19 | 10 | 2031-07-19 10:00 | 2.66 | 3.346 | N | 0
2025-07-19 | 11 | 2031-07-19 11:00 | 3.06 | 3.8491 | N | 0
2025-07-19 | 12 | 2031-07-19 12:00 | 3.44 | 4.3271 | N | 0
2025-07-19 | 13 | 2031-07-19 13:00 | 3.82 | 4.8051 | N | 0
2025-07-19 | 14 | 2031-07-19 14:00 | 4.18 | 5.2579 | N | 0
2025-07-19 | 15 | 2031-07-19 15:00 | 4.61 | 5.7988 | N | 0
2025-07-19 | 16 | 2031-07-19 16:00 | 4.78 | 6.0127 | N | 0
2025-07-19 | 17 | 2031-07-19 17:00 | 5.04 | 6.3397 | N | 0
2025-07-19 | 18 | 2031-07-19 18:00 | 5.08 | 6.39 | N | 0
2025-07-19 | 19 | 2031-07-19 19:00 | 5.36 | 6.7422 | N | 0
2025-07-19 | 20 | 2031-07-19 20:00 | 5.55 | 6.9812 | N | 0
2025-07-19 | 21 | 2031-07-19 21:00 | 5.55 | 6.9812 | N | 0
2025-07-19 | 22 | 2031-07-19 22:00 | 5.44 | 6.8429 | N | 0
2025-07-19 | 23 | 2031-07-19 23:00 | 5.12 | 6.4404 | N | 0
2025-07-20 | 00 | 2031-07-20 | 5.01 | 6.302 | N | 0
2025-07-20 | 01 | 2031-07-20 01:00 | 5 | 6.2894 | N | 0
2025-07-20 | 02 | 2031-07-20 02:00 | 4.7 | 5.912 | N | 0
2025-07-20 | 03 | 2031-07-20 03:00 | 4.38 | 5.5095 | N | 0
2025-07-20 | 04 | 2031-07-20 04:00 | 3.92 | 4.9309 | N | 0
2025-07-20 | 05 | 2031-07-20 05:00 | 3.49 | 4.39 | N | 0
2025-07-20 | 06 | 2031-07-20 06:00 | 3.24 | 4.0755 | N | 0
2025-07-20 | 07 | 2031-07-20 07:00 | 3.16 | 3.9749 | N | 0
2025-07-20 | 08 | 2031-07-20 08:00 | 3 | 3.7736 | N | 0
2025-07-20 | 09 | 2031-07-20 09:00 | 2.93 | 3.6856 | N | 0
2025-07-20 | 10 | 2031-07-20 10:00 | 2.96 | 3.7233 | N | 0
2025-07-20 | 11 | 2031-07-20 11:00 | 3.28 | 4.1259 | N | 0
2025-07-20 | 12 | 2031-07-20 12:00 | 3.74 | 4.7045 | N | 0
2025-07-20 | 13 | 2031-07-20 13:00 | 4.35 | 5.4718 | N | 0
2025-07-20 | 14 | 2031-07-20 14:00 | 4.9 | 6.1636 | N | 0
2025-07-20 | 15 | 2031-07-20 15:00 | 5.41 | 6.8051 | N | 0
2025-07-20 | 16 | 2031-07-20 16:00 | 5.86 | 7.3712 | N | 0
2025-07-20 | 17 | 2031-07-20 17:00 | 6.15 | 7.736 | N | 0
2025-07-20 | 18 | 2031-07-20 18:00 | 6.39 | 8.0379 | N | 0
2025-07-20 | 19 | 2031-07-20 19:00 | 6.69 | 8.4152 | N | 0
2025-07-20 | 20 | 2031-07-20 20:00 | 7.05 | 8.8681 | N | 0
2025-07-20 | 21 | 2031-07-20 21:00 | 7.25 | 9.1196 | N | 0
2025-07-20 | 22 | 2031-07-20 22:00 | 7.25 | 9.1196 | N | 0
2025-07-20 | 23 | 2031-07-20 23:00 | 6.83 | 8.5913 | N | 0
2025-07-21 | 00 | 2031-07-21 | 6.42 | 8.0756 | N | 0
2025-07-21 | 01 | 2031-07-21 01:00 | 5.95 | 7.4844 | N | 0
2025-07-21 | 02 | 2031-07-21 02:00 | 5.44 | 6.8429 | N | 0
2025-07-21 | 03 | 2031-07-21 03:00 | 4.71 | 5.9246 | N | 0
2025-07-21 | 04 | 2031-07-21 04:00 | 4.07 | 5.1196 | N | 0
2025-07-21 | 05 | 2031-07-21 05:00 | 3.63 | 4.5661 | N | 0
2025-07-21 | 06 | 2031-07-21 06:00 | 3.29 | 4.1384 | N | 0
2025-07-21 | 07 | 2031-07-21 07:00 | 3.1 | 3.8994 | N | 0
2025-07-21 | 08 | 2031-07-21 08:00 | 2.93 | 3.6856 | N | 0
2025-07-21 | 09 | 2031-07-21 09:00 | 2.9 | 3.6479 | N | 0
2025-07-21 | 10 | 2031-07-21 10:00 | 3.23 | 4.063 | N | 0
2025-07-21 | 11 | 2031-07-21 11:00 | 3.63 | 4.5661 | N | 0
2025-07-21 | 12 | 2031-07-21 12:00 | 4.1 | 5.1573 | N | 0
2025-07-21 | 13 | 2031-07-21 13:00 | 4.45 | 5.5976 | N | 0
2025-07-21 | 14 | 2031-07-21 14:00 | 4.82 | 6.063 | N | 0
2025-07-21 | 15 | 2031-07-21 15:00 | 5.02 | 6.3146 | N | 0
2025-07-21 | 16 | 2031-07-21 16:00 | 5.19 | 6.5284 | N | 0
2025-07-21 | 17 | 2031-07-21 17:00 | 5.31 | 6.6794 | N | 0
2025-07-21 | 18 | 2031-07-21 18:00 | 5.41 | 6.8051 | N | 0
2025-07-21 | 19 | 2031-07-21 19:00 | 5.58 | 7.019 | N | 0
2025-07-21 | 20 | 2031-07-21 20:00 | 5.96 | 7.497 | N | 0
2025-07-21 | 21 | 2031-07-21 21:00 | 6.26 | 7.8743 | N | 0
2025-07-21 | 22 | 2031-07-21 22:00 | 6.19 | 7.7863 | N | 0
2025-07-21 | 23 | 2031-07-21 23:00 | 5.86 | 7.3712 | N | 0
2025-07-22 | 00 | 2031-07-22 | 5.58 | 7.019 | N | 0
2025-07-22 | 01 | 2031-07-22 01:00 | 5.2 | 6.541 | N | 0
2025-07-22 | 02 | 2031-07-22 02:00 | 4.79 | 6.0253 | N | 0
2025-07-22 | 03 | 2031-07-22 03:00 | 4.1 | 5.1573 | N | 0
2025-07-22 | 04 | 2031-07-22 04:00 | 3.57 | 4.4906 | N | 0
2025-07-22 | 05 | 2031-07-22 05:00 | 3.14 | 3.9497 | N | 0
2025-07-22 | 06 | 2031-07-22 06:00 | 2.84 | 3.5724 | N | 0
2025-07-22 | 07 | 2031-07-22 07:00 | 2.75 | 3.4592 | N | 0
2025-07-22 | 08 | 2031-07-22 08:00 | 2.65 | 3.3334 | N | 0
2025-07-22 | 09 | 2031-07-22 09:00 | 2.73 | 3.434 | N | 0
2025-07-22 | 10 | 2031-07-22 10:00 | 3.12 | 3.9246 | N | 0
2025-07-22 | 11 | 2031-07-22 11:00 | 3.43 | 4.3145 | N | 0
2025-07-22 | 12 | 2031-07-22 12:00 | 3.87 | 4.868 | N | 0
2025-07-22 | 13 | 2031-07-22 13:00 | 4.19 | 5.2705 | N | 0
2025-07-22 | 14 | 2031-07-22 14:00 | 4.51 | 5.673 | N | 0
2025-07-22 | 15 | 2031-07-22 15:00 | 4.8 | 6.0378 | N | 0
2025-07-22 | 16 | 2031-07-22 16:00 | 4.99 | 6.2768 | N | 0
2025-07-22 | 17 | 2031-07-22 17:00 | 5.1 | 6.4152 | N | 0
2025-07-22 | 18 | 2031-07-22 18:00 | 5.08 | 6.39 | N | 0
2025-07-22 | 19 | 2031-07-22 19:00 | 5.46 | 6.868 | N | 0
2025-07-22 | 20 | 2031-07-22 20:00 | 5.9 | 7.4215 | N | 0
2025-07-22 | 21 | 2031-07-22 21:00 | 6.23 | 7.8366 | N | 0
2025-07-22 | 22 | 2031-07-22 22:00 | 6.1 | 7.6731 | N | 0
2025-07-22 | 23 | 2031-07-22 23:00 | 5.78 | 7.2706 | N | 0
2025-07-23 | 00 | 2031-07-23 | 5.54 | 6.9687 | N | 0
2025-07-23 | 01 | 2031-07-23 01:00 | 5.2 | 6.541 | N | 0
2025-07-23 | 02 | 2031-07-23 02:00 | 4.64 | 5.8366 | N | 0
2025-07-23 | 03 | 2031-07-23 03:00 | 4.07 | 5.1196 | N | 0
2025-07-23 | 04 | 2031-07-23 04:00 | 3.54 | 4.4529 | N | 0
2025-07-23 | 05 | 2031-07-23 05:00 | 3.12 | 3.9246 | N | 0
2025-07-23 | 06 | 2031-07-23 06:00 | 2.8 | 3.5221 | N | 0
2025-07-23 | 07 | 2031-07-23 07:00 | 2.66 | 3.346 | N | 0
2025-07-23 | 08 | 2031-07-23 08:00 | 2.61 | 3.2831 | N | 0
2025-07-23 | 09 | 2031-07-23 09:00 | 2.7 | 3.3963 | N | 0
2025-07-23 | 10 | 2031-07-23 10:00 | 3.11 | 3.912 | N | 0
2025-07-23 | 11 | 2031-07-23 11:00 | 3.41 | 4.2894 | N | 0
2025-07-23 | 12 | 2031-07-23 12:00 | 3.91 | 4.9183 | N | 0
2025-07-23 | 13 | 2031-07-23 13:00 | 4.39 | 5.5221 | N | 0
2025-07-23 | 14 | 2031-07-23 14:00 | 4.76 | 5.9875 | N | 0
2025-07-23 | 15 | 2031-07-23 15:00 | 5.04 | 6.3397 | N | 0
2025-07-23 | 16 | 2031-07-23 16:00 | 5.25 | 6.6039 | N | 0
2025-07-23 | 17 | 2031-07-23 17:00 | 5.41 | 6.8051 | N | 0
2025-07-23 | 18 | 2031-07-23 18:00 | 5.66 | 7.1196 | N | 0
2025-07-23 | 19 | 2031-07-23 19:00 | 5.97 | 7.5096 | N | 0
2025-07-23 | 20 | 2031-07-23 20:00 | 6.57 | 8.2643 | N | 0
2025-07-23 | 21 | 2031-07-23 21:00 | 6.8 | 8.5536 | N | 0
2025-07-23 | 22 | 2031-07-23 22:00 | 6.78 | 8.5284 | N | 0
2025-07-23 | 23 | 2031-07-23 23:00 | 6.39 | 8.0379 | N | 0
2025-07-24 | 00 | 2031-07-24 | 6.01 | 7.5599 | N | 0
2025-07-24 | 01 | 2031-07-24 01:00 | 5.81 | 7.3083 | N | 0
2025-07-24 | 02 | 2031-07-24 02:00 | 5.18 | 6.5158 | N | 0
2025-07-24 | 03 | 2031-07-24 03:00 | 4.53 | 5.6982 | N | 0
2025-07-24 | 04 | 2031-07-24 04:00 | 3.92 | 4.9309 | N | 0
2025-07-24 | 05 | 2031-07-24 05:00 | 3.44 | 4.3271 | N | 0
2025-07-24 | 06 | 2031-07-24 06:00 | 3.19 | 4.0126 | N | 0
2025-07-24 | 07 | 2031-07-24 07:00 | 2.99 | 3.7611 | N | 0
2025-07-24 | 08 | 2031-07-24 08:00 | 2.89 | 3.6353 | N | 0
2025-07-24 | 09 | 2031-07-24 09:00 | 2.86 | 3.5975 | N | 0
2025-07-24 | 10 | 2031-07-24 10:00 | 3.25 | 4.0881 | N | 0
2025-07-24 | 11 | 2031-07-24 11:00 | 3.74 | 4.7045 | N | 0
2025-07-24 | 12 | 2031-07-24 12:00 | 4.39 | 5.5221 | N | 0
2025-07-24 | 13 | 2031-07-24 13:00 | 4.89 | 6.151 | N | 0
2025-07-24 | 14 | 2031-07-24 14:00 | 5.62 | 7.0693 | N | 0
2025-07-24 | 15 | 2031-07-24 15:00 | 6.15 | 7.736 | N | 0
2025-07-24 | 16 | 2031-07-24 16:00 | 6.73 | 8.4655 | N | 0
2025-07-24 | 17 | 2031-07-24 17:00 | 6.99 | 8.7926 | N | 0
2025-07-24 | 18 | 2031-07-24 18:00 | 7.47 | 9.3964 | N | 0
2025-07-24 | 19 | 2031-07-24 19:00 | 7.7 | 9.6857 | N | 0
2025-07-24 | 20 | 2031-07-24 20:00 | 8.23 | 10.3524 | N | 0
2025-07-24 | 21 | 2031-07-24 21:00 | 8.48 | 10.6668 | Y | 0.026835 | 1
2025-07-24 | 22 | 2031-07-24 22:00 | 8.48 | 10.6668 | Y | 0.026835 | 2 | 2
2025-07-24 | 23 | 2031-07-24 23:00 | 8.13 | 10.2266 | N | 0
2025-07-25 | 00 | 2031-07-25 | 7.86 | 9.8869 | N | 0
2025-07-25 | 01 | 2031-07-25 01:00 | 7.23 | 9.0945 | N | 0
2025-07-25 | 02 | 2031-07-25 02:00 | 6.56 | 8.2517 | N | 0
2025-07-25 | 03 | 2031-07-25 03:00 | 5.91 | 7.4341 | N | 0
2025-07-25 | 04 | 2031-07-25 04:00 | 5.19 | 6.5284 | N | 0
2025-07-25 | 05 | 2031-07-25 05:00 | 4.65 | 5.8491 | N | 0
2025-07-25 | 06 | 2031-07-25 06:00 | 4.26 | 5.3586 | N | 0
2025-07-25 | 07 | 2031-07-25 07:00 | 4.12 | 5.1825 | N | 0
2025-07-25 | 08 | 2031-07-25 08:00 | 3.87 | 4.868 | N | 0
2025-07-25 | 09 | 2031-07-25 09:00 | 3.87 | 4.868 | N | 0
2025-07-25 | 10 | 2031-07-25 10:00 | 4.23 | 5.3208 | N | 0
2025-07-25 | 11 | 2031-07-25 11:00 | 4.65 | 5.8491 | N | 0
2025-07-25 | 12 | 2031-07-25 12:00 | 5.08 | 6.39 | N | 0
2025-07-25 | 13 | 2031-07-25 13:00 | 5.38 | 6.7674 | N | 0
2025-07-25 | 14 | 2031-07-25 14:00 | 6.01 | 7.5599 | N | 0
2025-07-25 | 15 | 2031-07-25 15:00 | 6.39 | 8.0379 | N | 0
2025-07-25 | 16 | 2031-07-25 16:00 | 6.61 | 8.3146 | N | 0
2025-07-25 | 17 | 2031-07-25 17:00 | 6.89 | 8.6668 | N | 0
2025-07-25 | 18 | 2031-07-25 18:00 | 7.11 | 8.9435 | N | 0
2025-07-25 | 19 | 2031-07-25 19:00 | 7.51 | 9.4467 | N | 0
2025-07-25 | 20 | 2031-07-25 20:00 | 7.79 | 9.7989 | N | 0
2025-07-25 | 21 | 2031-07-25 21:00 | 7.98 | 10.0379 | N | 0
2025-07-25 | 22 | 2031-07-25 22:00 | 7.98 | 10.0379 | N | 0
2025-07-25 | 23 | 2031-07-25 23:00 | 7.73 | 9.7234 | N | 0
2025-07-26 | 00 | 2031-07-26 | 7.26 | 9.1322 | N | 0
2025-07-26 | 01 | 2031-07-26 01:00 | 7.01 | 8.8177 | N | 0
2025-07-26 | 02 | 2031-07-26 02:00 | 6.44 | 8.1008 | N | 0
2025-07-26 | 03 | 2031-07-26 03:00 | 5.78 | 7.2706 | N | 0
2025-07-26 | 04 | 2031-07-26 04:00 | 5 | 6.2894 | N | 0
2025-07-26 | 05 | 2031-07-26 05:00 | 4.47 | 5.6227 | N | 0
2025-07-26 | 06 | 2031-07-26 06:00 | 3.94 | 4.9561 | N | 0
2025-07-26 | 07 | 2031-07-26 07:00 | 3.71 | 4.6667 | N | 0
2025-07-26 | 08 | 2031-07-26 08:00 | 3.51 | 4.4152 | N | 0
2025-07-26 | 09 | 2031-07-26 09:00 | 3.45 | 4.3397 | N | 0
2025-07-26 | 10 | 2031-07-26 10:00 | 3.45 | 4.3397 | N | 0
2025-07-26 | 11 | 2031-07-26 11:00 | 3.96 | 4.9812 | N | 0
2025-07-26 | 12 | 2031-07-26 12:00 | 4.75 | 5.9749 | N | 0
2025-07-26 | 13 | 2031-07-26 13:00 | 5.33 | 6.7045 | N | 0
2025-07-26 | 14 | 2031-07-26 14:00 | 5.47 | 6.8806 | N | 0
2025-07-26 | 15 | 2031-07-26 15:00 | 5.98 | 7.5221 | N | 0
2025-07-26 | 16 | 2031-07-26 16:00 | 6.49 | 8.1637 | N | 0
2025-07-26 | 17 | 2031-07-26 17:00 | 6.67 | 8.3901 | N | 0
2025-07-26 | 18 | 2031-07-26 18:00 | 6.71 | 8.4404 | N | 0
2025-07-26 | 19 | 2031-07-26 19:00 | 6.88 | 8.6542 | N | 0
2025-07-26 | 20 | 2031-07-26 20:00 | 6.65 | 8.3649 | N | 0
2025-07-26 | 21 | 2031-07-26 21:00 | 6.65 | 8.3649 | N | 0
2025-07-26 | 22 | 2031-07-26 22:00 | 6.4 | 8.0504 | N | 0
2025-07-26 | 23 | 2031-07-26 23:00 | 6.21 | 7.8114 | N | 0
2025-07-27 | 00 | 2031-07-27 | 6.2 | 7.7989 | N | 0
2025-07-27 | 01 | 2031-07-27 01:00 | 5.93 | 7.4592 | N | 0
2025-07-27 | 02 | 2031-07-27 02:00 | 5.58 | 7.019 | N | 0
2025-07-27 | 03 | 2031-07-27 03:00 | 5.14 | 6.4655 | N | 0
2025-07-27 | 04 | 2031-07-27 04:00 | 4.59 | 5.7737 | N | 0
2025-07-27 | 05 | 2031-07-27 05:00 | 4.18 | 5.2579 | N | 0
2025-07-27 | 06 | 2031-07-27 06:00 | 3.86 | 4.8554 | N | 0
2025-07-27 | 07 | 2031-07-27 07:00 | 3.67 | 4.6164 | N | 0
2025-07-27 | 08 | 2031-07-27 08:00 | 3.67 | 4.6164 | N | 0
2025-07-27 | 09 | 2031-07-27 09:00 | 3.56 | 4.4781 | N | 0
2025-07-27 | 10 | 2031-07-27 10:00 | 3.69 | 4.6416 | N | 0
2025-07-27 | 11 | 2031-07-27 11:00 | 4.06 | 5.107 | N | 0
2025-07-27 | 12 | 2031-07-27 12:00 | 5.12 | 6.4404 | N | 0
2025-07-27 | 13 | 2031-07-27 13:00 | 5.71 | 7.1825 | N | 0
2025-07-27 | 14 | 2031-07-27 14:00 | 6.06 | 7.6228 | N | 0
2025-07-27 | 15 | 2031-07-27 15:00 | 6.72 | 8.453 | N | 0
2025-07-27 | 16 | 2031-07-27 16:00 | 7.16 | 9.0064 | N | 0
2025-07-27 | 17 | 2031-07-27 17:00 | 7.61 | 9.5725 | N | 0
2025-07-27 | 18 | 2031-07-27 18:00 | 7.61 | 9.5725 | N | 0
2025-07-27 | 19 | 2031-07-27 19:00 | 7.86 | 9.8869 | N | 0
2025-07-27 | 20 | 2031-07-27 20:00 | 8.23 | 10.3524 | N | 0
2025-07-27 | 21 | 2031-07-27 21:00 | 8.33 | 10.4782 | N | 0
2025-07-27 | 22 | 2031-07-27 22:00 | 8.33 | 10.4782 | N | 0
2025-07-27 | 23 | 2031-07-27 23:00 | 8.07 | 10.1511 | N | 0
2025-07-28 | 00 | 2031-07-28 | 7.66 | 9.6354 | N | 0
2025-07-28 | 01 | 2031-07-28 01:00 | 7.33 | 9.2203 | N | 0
2025-07-28 | 02 | 2031-07-28 02:00 | 6.78 | 8.5284 | N | 0
2025-07-28 | 03 | 2031-07-28 03:00 | 5.97 | 7.5096 | N | 0
2025-07-28 | 04 | 2031-07-28 04:00 | 5.26 | 6.6165 | N | 0
2025-07-28 | 05 | 2031-07-28 05:00 | 4.67 | 5.8743 | N | 0
2025-07-28 | 06 | 2031-07-28 06:00 | 4.2 | 5.2831 | N | 0
2025-07-28 | 07 | 2031-07-28 07:00 | 3.98 | 5.0064 | N | 0
2025-07-28 | 08 | 2031-07-28 08:00 | 3.73 | 4.6919 | N | 0
2025-07-28 | 09 | 2031-07-28 09:00 | 3.65 | 4.5913 | N | 0
2025-07-28 | 10 | 2031-07-28 10:00 | 4.02 | 5.0567 | N | 0
2025-07-28 | 11 | 2031-07-28 11:00 | 4.61 | 5.7988 | N | 0
2025-07-28 | 12 | 2031-07-28 12:00 | 5.4 | 6.7926 | N | 0
2025-07-28 | 13 | 2031-07-28 13:00 | 6.13 | 7.7108 | N | 0
2025-07-28 | 14 | 2031-07-28 14:00 | 6.72 | 8.453 | N | 0
2025-07-28 | 15 | 2031-07-28 15:00 | 7.13 | 8.9687 | N | 0
2025-07-28 | 16 | 2031-07-28 16:00 | 7.31 | 9.1951 | N | 0
2025-07-28 | 17 | 2031-07-28 17:00 | 7.55 | 9.497 | N | 0
2025-07-28 | 18 | 2031-07-28 18:00 | 7.78 | 9.7863 | N | 0
2025-07-28 | 19 | 2031-07-28 19:00 | 8.02 | 10.0882 | N | 0
2025-07-28 | 20 | 2031-07-28 20:00 | 8.57 | 10.78 | Y | 0.14004 | 1
2025-07-28 | 21 | 2031-07-28 21:00 | 8.57 | 10.78 | Y | 0.14004 | 2
2025-07-28 | 22 | 2031-07-28 22:00 | 8.57 | 10.78 | Y | 0.14004 | 3 | 3
2025-07-28 | 23 | 2031-07-28 23:00 | 8.31 | 10.453 | N | 0
2025-07-29 | 00 | 2031-07-29 | 8.04 | 10.1134 | N | 0
2025-07-29 | 01 | 2031-07-29 01:00 | 7.77 | 9.7737 | N | 0
2025-07-29 | 02 | 2031-07-29 02:00 | 7.22 | 9.0819 | N | 0
2025-07-29 | 03 | 2031-07-29 03:00 | 6.24 | 7.8492 | N | 0
2025-07-29 | 04 | 2031-07-29 04:00 | 5.69 | 7.1573 | N | 0
2025-07-29 | 05 | 2031-07-29 05:00 | 5.11 | 6.4278 | N | 0
2025-07-29 | 06 | 2031-07-29 06:00 | 4.61 | 5.7988 | N | 0
2025-07-29 | 07 | 2031-07-29 07:00 | 4.36 | 5.4844 | N | 0
2025-07-29 | 08 | 2031-07-29 08:00 | 4.07 | 5.1196 | N | 0
2025-07-29 | 09 | 2031-07-29 09:00 | 3.96 | 4.9812 | N | 0
2025-07-29 | 10 | 2031-07-29 10:00 | 4.3 | 5.4089 | N | 0
2025-07-29 | 11 | 2031-07-29 11:00 | 4.9 | 6.1636 | N | 0
2025-07-29 | 12 | 2031-07-29 12:00 | 5.59 | 7.0316 | N | 0
2025-07-29 | 13 | 2031-07-29 13:00 | 6.27 | 7.8869 | N | 0
2025-07-29 | 14 | 2031-07-29 14:00 | 6.83 | 8.5913 | N | 0
2025-07-29 | 15 | 2031-07-29 15:00 | 7.28 | 9.1574 | N | 0
2025-07-29 | 16 | 2031-07-29 16:00 | 7.62 | 9.5851 | N | 0
2025-07-29 | 17 | 2031-07-29 17:00 | 7.74 | 9.736 | N | 0
2025-07-29 | 18 | 2031-07-29 18:00 | 7.91 | 9.9498 | N | 0
2025-07-29 | 19 | 2031-07-29 19:00 | 8.02 | 10.0882 | N | 0
2025-07-29 | 20 | 2031-07-29 20:00 | 8.27 | 10.4027 | N | 0
2025-07-29 | 21 | 2031-07-29 21:00 | 8.54 | 10.7423 | Y | 0.10231 | 1
2025-07-29 | 22 | 2031-07-29 22:00 | 8.54 | 10.7423 | Y | 0.10231 | 2 | 2
2025-07-29 | 23 | 2031-07-29 23:00 | 8.28 | 10.4153 | N | 0
2025-07-30 | 00 | 2031-07-30 | 7.96 | 10.0127 | N | 0
2025-07-30 | 01 | 2031-07-30 01:00 | 7.68 | 9.6605 | N | 0
2025-07-30 | 02 | 2031-07-30 02:00 | 6.91 | 8.692 | N | 0
2025-07-30 | 03 | 2031-07-30 03:00 | 6.21 | 7.8114 | N | 0
2025-07-30 | 04 | 2031-07-30 04:00 | 5.4 | 6.7926 | N | 0
2025-07-30 | 05 | 2031-07-30 05:00 | 4.74 | 5.9624 | N | 0
2025-07-30 | 06 | 2031-07-30 06:00 | 4.2 | 5.2831 | N | 0
2025-07-30 | 07 | 2031-07-30 07:00 | 3.91 | 4.9183 | N | 0
2025-07-30 | 08 | 2031-07-30 08:00 | 3.71 | 4.6667 | N | 0
2025-07-30 | 09 | 2031-07-30 09:00 | 3.6 | 4.5284 | N | 0
2025-07-30 | 10 | 2031-07-30 10:00 | 3.97 | 4.9938 | N | 0
2025-07-30 | 11 | 2031-07-30 11:00 | 4.44 | 5.585 | N | 0
2025-07-30 | 12 | 2031-07-30 12:00 | 5.14 | 6.4655 | N | 0
2025-07-30 | 13 | 2031-07-30 13:00 | 5.79 | 7.2831 | N | 0
2025-07-30 | 14 | 2031-07-30 14:00 | 6.13 | 7.7108 | N | 0
2025-07-30 | 15 | 2031-07-30 15:00 | 6.8 | 8.5536 | N | 0
2025-07-30 | 16 | 2031-07-30 16:00 | 7.28 | 9.1574 | N | 0
2025-07-30 | 17 | 2031-07-30 17:00 | 7.4 | 9.3083 | N | 0
2025-07-30 | 18 | 2031-07-30 18:00 | 7.28 | 9.1574 | N | 0
2025-07-30 | 19 | 2031-07-30 19:00 | 7.5 | 9.4341 | N | 0
2025-07-30 | 20 | 2031-07-30 20:00 | 7.64 | 9.6102 | N | 0
2025-07-30 | 21 | 2031-07-30 21:00 | 7.96 | 10.0127 | N | 0
2025-07-30 | 22 | 2031-07-30 22:00 | 7.96 | 10.0127 | N | 0
2025-07-30 | 23 | 2031-07-30 23:00 | 7.46 | 9.3838 | N | 0
2025-07-31 | 00 | 2031-07-31 | 7 | 8.8052 | N | 0
2025-07-31 | 01 | 2031-07-31 01:00 | 6.79 | 8.541 | N | 0
2025-07-31 | 02 | 2031-07-31 02:00 | 5.98 | 7.5221 | N | 0
2025-07-31 | 03 | 2031-07-31 03:00 | 5.33 | 6.7045 | N | 0
2025-07-31 | 04 | 2031-07-31 04:00 | 4.65 | 5.8491 | N | 0
2025-07-31 | 05 | 2031-07-31 05:00 | 4.17 | 5.2454 | N | 0
2025-07-31 | 06 | 2031-07-31 06:00 | 3.76 | 4.7296 | N | 0
2025-07-31 | 07 | 2031-07-31 07:00 | 3.52 | 4.4277 | N | 0
2025-07-31 | 08 | 2031-07-31 08:00 | 3.3 | 4.151 | N | 0
2025-07-31 | 09 | 2031-07-31 09:00 | 3.26 | 4.1007 | N | 0
2025-07-31 | 10 | 2031-07-31 10:00 | 3.65 | 4.5913 | N | 0
2025-07-31 | 11 | 2031-07-31 11:00 | 3.92 | 4.9309 | N | 0
2025-07-31 | 12 | 2031-07-31 12:00 | 4.45 | 5.5976 | N | 0
2025-07-31 | 13 | 2031-07-31 13:00 | 4.54 | 5.7108 | N | 0
2025-07-31 | 14 | 2031-07-31 14:00 | 4.55 | 5.7234 | N | 0
2025-07-31 | 15 | 2031-07-31 15:00 | 4.66 | 5.8617 | N | 0
2025-07-31 | 16 | 2031-07-31 16:00 | 4.79 | 6.0253 | N | 0
2025-07-31 | 17 | 2031-07-31 17:00 | 4.9 | 6.1636 | N | 0
2025-07-31 | 18 | 2031-07-31 18:00 | 4.8 | 6.0378 | N | 0
2025-07-31 | 19 | 2031-07-31 19:00 | 5.11 | 6.4278 | N | 0
2025-07-31 | 20 | 2031-07-31 20:00 | 5.7 | 7.1699 | N | 0
2025-07-31 | 21 | 2031-07-31 21:00 | 6.02 | 7.5724 | N | 0
2025-07-31 | 22 | 2031-07-31 22:00 | 5.92 | 7.4467 | N | 0
2025-07-31 | 23 | 2031-07-31 23:00 | 5.51 | 6.9309 | N | 0
2025-08-01 | 00 | 2031-08-01 | 5.29 | 6.6542 | N | 0
2025-08-01 | 01 | 2031-08-01 01:00 | 5.11 | 6.4278 | N | 0
2025-08-01 | 02 | 2031-08-01 02:00 | 4.68 | 5.8869 | N | 0
2025-08-01 | 03 | 2031-08-01 03:00 | 4.19 | 5.2705 | N | 0
2025-08-01 | 04 | 2031-08-01 04:00 | 3.6 | 4.5284 | N | 0
2025-08-01 | 05 | 2031-08-01 05:00 | 3.19 | 4.0126 | N | 0
2025-08-01 | 06 | 2031-08-01 06:00 | 2.92 | 3.673 | N | 0
2025-08-01 | 07 | 2031-08-01 07:00 | 2.75 | 3.4592 | N | 0
2025-08-01 | 08 | 2031-08-01 08:00 | 2.73 | 3.434 | N | 0
2025-08-01 | 09 | 2031-08-01 09:00 | 2.72 | 3.4214 | N | 0
2025-08-01 | 10 | 2031-08-01 10:00 | 3.02 | 3.7988 | N | 0
2025-08-01 | 11 | 2031-08-01 11:00 | 3.36 | 4.2265 | N | 0
2025-08-01 | 12 | 2031-08-01 12:00 | 3.76 | 4.7296 | N | 0
2025-08-01 | 13 | 2031-08-01 13:00 | 4.19 | 5.2705 | N | 0
2025-08-01 | 14 | 2031-08-01 14:00 | 4.46 | 5.6102 | N | 0
2025-08-01 | 15 | 2031-08-01 15:00 | 4.73 | 5.9498 | N | 0
2025-08-01 | 16 | 2031-08-01 16:00 | 4.9 | 6.1636 | N | 0
2025-08-01 | 17 | 2031-08-01 17:00 | 5.15 | 6.4781 | N | 0
2025-08-01 | 18 | 2031-08-01 18:00 | 5.22 | 6.5661 | N | 0
2025-08-01 | 19 | 2031-08-01 19:00 | 5.4 | 6.7926 | N | 0
2025-08-01 | 20 | 2031-08-01 20:00 | 5.64 | 7.0945 | N | 0
2025-08-01 | 21 | 2031-08-01 21:00 | 5.87 | 7.3838 | N | 0
2025-08-01 | 22 | 2031-08-01 22:00 | 5.82 | 7.3209 | N | 0
2025-08-01 | 23 | 2031-08-01 23:00 | 5.57 | 7.0064 | N | 0
2025-08-02 | 00 | 2031-08-02 | 5.27 | 6.629 | N | 0
2025-08-02 | 01 | 2031-08-02 01:00 | 4.96 | 6.2391 | N | 0
2025-08-02 | 02 | 2031-08-02 02:00 | 4.53 | 5.6982 | N | 0
2025-08-02 | 03 | 2031-08-02 03:00 | 4.02 | 5.0567 | N | 0
2025-08-02 | 04 | 2031-08-02 04:00 | 3.59 | 4.5158 | N | 0
2025-08-02 | 05 | 2031-08-02 05:00 | 3.23 | 4.063 | N | 0
2025-08-02 | 06 | 2031-08-02 06:00 | 2.95 | 3.7108 | N | 0
2025-08-02 | 07 | 2031-08-02 07:00 | 2.81 | 3.5346 | N | 0
2025-08-02 | 08 | 2031-08-02 08:00 | 2.64 | 3.3208 | N | 0
2025-08-02 | 09 | 2031-08-02 09:00 | 2.61 | 3.2831 | N | 0
2025-08-02 | 10 | 2031-08-02 10:00 | 2.64 | 3.3208 | N | 0
2025-08-02 | 11 | 2031-08-02 11:00 | 3.03 | 3.8114 | N | 0
2025-08-02 | 12 | 2031-08-02 12:00 | 3.47 | 4.3648 | N | 0
2025-08-02 | 13 | 2031-08-02 13:00 | 3.98 | 5.0064 | N | 0
2025-08-02 | 14 | 2031-08-02 14:00 | 4.52 | 5.6856 | N | 0
2025-08-02 | 15 | 2031-08-02 15:00 | 4.83 | 6.0756 | N | 0
2025-08-02 | 16 | 2031-08-02 16:00 | 5.12 | 6.4404 | N | 0
2025-08-02 | 17 | 2031-08-02 17:00 | 5.14 | 6.4655 | N | 0
2025-08-02 | 18 | 2031-08-02 18:00 | 5.3 | 6.6668 | N | 0
2025-08-02 | 19 | 2031-08-02 19:00 | 5.49 | 6.9058 | N | 0
2025-08-02 | 20 | 2031-08-02 20:00 | 5.66 | 7.1196 | N | 0
2025-08-02 | 21 | 2031-08-02 21:00 | 5.76 | 7.2454 | N | 0
2025-08-02 | 22 | 2031-08-02 22:00 | 5.7 | 7.1699 | N | 0
2025-08-02 | 23 | 2031-08-02 23:00 | 5.45 | 6.8555 | N | 0
2025-08-03 | 00 | 2031-08-03 | 5.1 | 6.4152 | N | 0
2025-08-03 | 01 | 2031-08-03 01:00 | 4.83 | 6.0756 | N | 0
2025-08-03 | 02 | 2031-08-03 02:00 | 4.54 | 5.7108 | N | 0
2025-08-03 | 03 | 2031-08-03 03:00 | 4.01 | 5.0441 | N | 0
2025-08-03 | 04 | 2031-08-03 04:00 | 3.58 | 4.5032 | N | 0
2025-08-03 | 05 | 2031-08-03 05:00 | 3.22 | 4.0504 | N | 0
2025-08-03 | 06 | 2031-08-03 06:00 | 2.9 | 3.6479 | N | 0
2025-08-03 | 07 | 2031-08-03 07:00 | 2.72 | 3.4214 | N | 0
2025-08-03 | 08 | 2031-08-03 08:00 | 2.62 | 3.2956 | N | 0
2025-08-03 | 09 | 2031-08-03 09:00 | 2.6 | 3.2705 | N | 0
2025-08-03 | 10 | 2031-08-03 10:00 | 2.63 | 3.3082 | N | 0
2025-08-03 | 11 | 2031-08-03 11:00 | 2.84 | 3.5724 | N | 0
2025-08-03 | 12 | 2031-08-03 12:00 | 3.36 | 4.2265 | N | 0
2025-08-03 | 13 | 2031-08-03 13:00 | 3.73 | 4.6919 | N | 0
2025-08-03 | 14 | 2031-08-03 14:00 | 4.27 | 5.3712 | N | 0
2025-08-03 | 15 | 2031-08-03 15:00 | 4.77 | 6.0001 | N | 0
2025-08-03 | 16 | 2031-08-03 16:00 | 5.1 | 6.4152 | N | 0
2025-08-03 | 17 | 2031-08-03 17:00 | 5.42 | 6.8177 | N | 0
2025-08-03 | 18 | 2031-08-03 18:00 | 5.73 | 7.2077 | N | 0
2025-08-03 | 19 | 2031-08-03 19:00 | 5.98 | 7.5221 | N | 0
2025-08-03 | 20 | 2031-08-03 20:00 | 6.14 | 7.7234 | N | 0
2025-08-03 | 21 | 2031-08-03 21:00 | 6.22 | 7.824 | N | 0
2025-08-03 | 22 | 2031-08-03 22:00 | 6.22 | 7.824 | N | 0
2025-08-03 | 23 | 2031-08-03 23:00 | 5.92 | 7.4467 | N | 0
2025-08-04 | 00 | 2031-08-04 | 5.56 | 6.9938 | N | 0
2025-08-04 | 01 | 2031-08-04 01:00 | 5.4 | 6.7926 | N | 0
2025-08-04 | 02 | 2031-08-04 02:00 | 5.01 | 6.302 | N | 0
2025-08-04 | 03 | 2031-08-04 03:00 | 4.3 | 5.4089 | N | 0
2025-08-04 | 04 | 2031-08-04 04:00 | 3.79 | 4.7674 | N | 0
2025-08-04 | 05 | 2031-08-04 05:00 | 3.38 | 4.2516 | N | 0
2025-08-04 | 06 | 2031-08-04 06:00 | 3.01 | 3.7862 | N | 0
2025-08-04 | 07 | 2031-08-04 07:00 | 2.8 | 3.5221 | N | 0
2025-08-04 | 08 | 2031-08-04 08:00 | 2.73 | 3.434 | N | 0
2025-08-04 | 09 | 2031-08-04 09:00 | 2.74 | 3.4466 | N | 0
2025-08-04 | 10 | 2031-08-04 10:00 | 2.89 | 3.6353 | N | 0
2025-08-04 | 11 | 2031-08-04 11:00 | 3.27 | 4.1133 | N | 0
2025-08-04 | 12 | 2031-08-04 12:00 | 3.79 | 4.7674 | N | 0
2025-08-04 | 13 | 2031-08-04 13:00 | 4.57 | 5.7485 | N | 0
2025-08-04 | 14 | 2031-08-04 14:00 | 5.25 | 6.6039 | N | 0
2025-08-04 | 15 | 2031-08-04 15:00 | 5.77 | 7.258 | N | 0
2025-08-04 | 16 | 2031-08-04 16:00 | 6.2 | 7.7989 | N | 0
2025-08-04 | 17 | 2031-08-04 17:00 | 6.39 | 8.0379 | N | 0
2025-08-04 | 18 | 2031-08-04 18:00 | 6.65 | 8.3649 | N | 0
2025-08-04 | 19 | 2031-08-04 19:00 | 7.01 | 8.8177 | N | 0
2025-08-04 | 20 | 2031-08-04 20:00 | 7.23 | 9.0945 | N | 0
2025-08-04 | 21 | 2031-08-04 21:00 | 7.45 | 9.3712 | N | 0
2025-08-04 | 22 | 2031-08-04 22:00 | 7.2 | 9.0567 | N | 0
2025-08-04 | 23 | 2031-08-04 23:00 | 6.85 | 8.6165 | N | 0
2025-08-05 | 00 | 2031-08-05 | 6.37 | 8.0127 | N | 0
2025-08-05 | 01 | 2031-08-05 01:00 | 6.32 | 7.9498 | N | 0
2025-08-05 | 02 | 2031-08-05 02:00 | 5.54 | 6.9687 | N | 0
2025-08-05 | 03 | 2031-08-05 03:00 | 4.83 | 6.0756 | N | 0
2025-08-05 | 04 | 2031-08-05 04:00 | 4.15 | 5.2202 | N | 0
2025-08-05 | 05 | 2031-08-05 05:00 | 3.67 | 4.6164 | N | 0
2025-08-05 | 06 | 2031-08-05 06:00 | 3.27 | 4.1133 | N | 0
2025-08-05 | 07 | 2031-08-05 07:00 | 3.17 | 3.9875 | N | 0
2025-08-05 | 08 | 2031-08-05 08:00 | 3.06 | 3.8491 | N | 0
2025-08-05 | 09 | 2031-08-05 09:00 | 3.11 | 3.912 | N | 0
2025-08-05 | 10 | 2031-08-05 10:00 | 3.25 | 4.0881 | N | 0
2025-08-05 | 11 | 2031-08-05 11:00 | 3.58 | 4.5032 | N | 0
2025-08-05 | 12 | 2031-08-05 12:00 | 4.36 | 5.4844 | N | 0
2025-08-05 | 13 | 2031-08-05 13:00 | 4.78 | 6.0127 | N | 0
2025-08-05 | 14 | 2031-08-05 14:00 | 5.23 | 6.5787 | N | 0
2025-08-05 | 15 | 2031-08-05 15:00 | 5.73 | 7.2077 | N | 0
2025-08-05 | 16 | 2031-08-05 16:00 | 6.13 | 7.7108 | N | 0
2025-08-05 | 17 | 2031-08-05 17:00 | 6.43 | 8.0882 | N | 0
2025-08-05 | 18 | 2031-08-05 18:00 | 6.69 | 8.4152 | N | 0
2025-08-05 | 19 | 2031-08-05 19:00 | 7.06 | 8.8806 | N | 0
2025-08-05 | 20 | 2031-08-05 20:00 | 7.33 | 9.2203 | N | 0
2025-08-05 | 21 | 2031-08-05 21:00 | 7.56 | 9.5096 | N | 0
2025-08-05 | 22 | 2031-08-05 22:00 | 7.45 | 9.3712 | N | 0
2025-08-05 | 23 | 2031-08-05 23:00 | 7.13 | 8.9687 | N | 0
2025-08-06 | 00 | 2031-08-06 | 6.61 | 8.3146 | N | 0
2025-08-06 | 01 | 2031-08-06 01:00 | 6.31 | 7.9372 | N | 0
2025-08-06 | 02 | 2031-08-06 02:00 | 5.52 | 6.9435 | N | 0
2025-08-06 | 03 | 2031-08-06 03:00 | 4.77 | 6.0001 | N | 0
2025-08-06 | 04 | 2031-08-06 04:00 | 4.23 | 5.3208 | N | 0
2025-08-06 | 05 | 2031-08-06 05:00 | 3.74 | 4.7045 | N | 0
2025-08-06 | 06 | 2031-08-06 06:00 | 3.33 | 4.1887 | N | 0
2025-08-06 | 07 | 2031-08-06 07:00 | 3.1 | 3.8994 | N | 0
2025-08-06 | 08 | 2031-08-06 08:00 | 3 | 3.7736 | N | 0
2025-08-06 | 09 | 2031-08-06 09:00 | 3.07 | 3.8617 | N | 0
2025-08-06 | 10 | 2031-08-06 10:00 | 3.34 | 4.2013 | N | 0
2025-08-06 | 11 | 2031-08-06 11:00 | 3.84 | 4.8303 | N | 0
2025-08-06 | 12 | 2031-08-06 12:00 | 4.25 | 5.346 | N | 0
2025-08-06 | 13 | 2031-08-06 13:00 | 4.67 | 5.8743 | N | 0
2025-08-06 | 14 | 2031-08-06 14:00 | 4.87 | 6.1259 | N | 0
2025-08-06 | 15 | 2031-08-06 15:00 | 5.19 | 6.5284 | N | 0
2025-08-06 | 16 | 2031-08-06 16:00 | 5.8 | 7.2957 | N | 0
2025-08-06 | 17 | 2031-08-06 17:00 | 6.25 | 7.8618 | N | 0
2025-08-06 | 18 | 2031-08-06 18:00 | 6.42 | 8.0756 | N | 0
2025-08-06 | 19 | 2031-08-06 19:00 | 6.85 | 8.6165 | N | 0
2025-08-06 | 20 | 2031-08-06 20:00 | 7.26 | 9.1322 | N | 0
2025-08-06 | 21 | 2031-08-06 21:00 | 7.48 | 9.409 | N | 0
2025-08-06 | 22 | 2031-08-06 22:00 | 7.48 | 9.409 | N | 0
2025-08-06 | 23 | 2031-08-06 23:00 | 7.02 | 8.8303 | N | 0
2025-08-07 | 00 | 2031-08-07 | 6.67 | 8.3901 | N | 0
2025-08-07 | 01 | 2031-08-07 01:00 | 6.34 | 7.975 | N | 0
2025-08-07 | 02 | 2031-08-07 02:00 | 5.66 | 7.1196 | N | 0
2025-08-07 | 03 | 2031-08-07 03:00 | 4.91 | 6.1762 | N | 0
2025-08-07 | 04 | 2031-08-07 04:00 | 4.4 | 5.5347 | N | 0
2025-08-07 | 05 | 2031-08-07 05:00 | 3.87 | 4.868 | N | 0
2025-08-07 | 06 | 2031-08-07 06:00 | 3.54 | 4.4529 | N | 0
2025-08-07 | 07 | 2031-08-07 07:00 | 3.34 | 4.2013 | N | 0
2025-08-07 | 08 | 2031-08-07 08:00 | 3.22 | 4.0504 | N | 0
2025-08-07 | 09 | 2031-08-07 09:00 | 3.32 | 4.1762 | N | 0
2025-08-07 | 10 | 2031-08-07 10:00 | 3.56 | 4.4781 | N | 0
2025-08-07 | 11 | 2031-08-07 11:00 | 4.18 | 5.2579 | N | 0
2025-08-07 | 12 | 2031-08-07 12:00 | 4.76 | 5.9875 | N | 0
2025-08-07 | 13 | 2031-08-07 13:00 | 5.34 | 6.7171 | N | 0
2025-08-07 | 14 | 2031-08-07 14:00 | 5.95 | 7.4844 | N | 0
2025-08-07 | 15 | 2031-08-07 15:00 | 6.19 | 7.7863 | N | 0
2025-08-07 | 16 | 2031-08-07 16:00 | 6.6 | 8.302 | N | 0
2025-08-07 | 17 | 2031-08-07 17:00 | 6.8 | 8.5536 | N | 0
2025-08-07 | 18 | 2031-08-07 18:00 | 7.02 | 8.8303 | N | 0
2025-08-07 | 19 | 2031-08-07 19:00 | 7.18 | 9.0316 | N | 0
2025-08-07 | 20 | 2031-08-07 20:00 | 7.3 | 9.1825 | N | 0
2025-08-07 | 21 | 2031-08-07 21:00 | 7.38 | 9.2832 | N | 0
2025-08-07 | 22 | 2031-08-07 22:00 | 7.16 | 9.0064 | N | 0
2025-08-07 | 23 | 2031-08-07 23:00 | 6.8 | 8.5536 | N | 0
2025-08-08 | 00 | 2031-08-08 | 6.41 | 8.063 | N | 0
2025-08-08 | 01 | 2031-08-08 01:00 | 6.2 | 7.7989 | N | 0
2025-08-08 | 02 | 2031-08-08 02:00 | 5.49 | 6.9058 | N | 0
2025-08-08 | 03 | 2031-08-08 03:00 | 4.83 | 6.0756 | N | 0
2025-08-08 | 04 | 2031-08-08 04:00 | 4.21 | 5.2957 | N | 0
2025-08-08 | 05 | 2031-08-08 05:00 | 3.72 | 4.6793 | N | 0
2025-08-08 | 06 | 2031-08-08 06:00 | 3.38 | 4.2516 | N | 0
2025-08-08 | 07 | 2031-08-08 07:00 | 3.16 | 3.9749 | N | 0
2025-08-08 | 08 | 2031-08-08 08:00 | 2.96 | 3.7233 | N | 0
2025-08-08 | 09 | 2031-08-08 09:00 | 3.02 | 3.7988 | N | 0
2025-08-08 | 10 | 2031-08-08 10:00 | 3.32 | 4.1762 | N | 0
2025-08-08 | 11 | 2031-08-08 11:00 | 3.89 | 4.8932 | N | 0
2025-08-08 | 12 | 2031-08-08 12:00 | 4.54 | 5.7108 | N | 0
2025-08-08 | 13 | 2031-08-08 13:00 | 5.17 | 6.5032 | N | 0
2025-08-08 | 14 | 2031-08-08 14:00 | 5.7 | 7.1699 | N | 0
2025-08-08 | 15 | 2031-08-08 15:00 | 6.09 | 7.6605 | N | 0
2025-08-08 | 16 | 2031-08-08 16:00 | 6.53 | 8.214 | N | 0
2025-08-08 | 17 | 2031-08-08 17:00 | 6.72 | 8.453 | N | 0
2025-08-08 | 18 | 2031-08-08 18:00 | 6.96 | 8.7549 | N | 0
2025-08-08 | 19 | 2031-08-08 19:00 | 7.18 | 9.0316 | N | 0
2025-08-08 | 20 | 2031-08-08 20:00 | 7 | 8.8052 | N | 0
2025-08-08 | 21 | 2031-08-08 21:00 | 6.85 | 8.6165 | N | 0
2025-08-08 | 22 | 2031-08-08 22:00 | 6.72 | 8.453 | N | 0
2025-08-08 | 23 | 2031-08-08 23:00 | 6.48 | 8.1511 | N | 0
2025-08-09 | 00 | 2031-08-09 | 6.28 | 7.8995 | N | 0
2025-08-09 | 01 | 2031-08-09 01:00 | 6.09 | 7.6605 | N | 0
2025-08-09 | 02 | 2031-08-09 02:00 | 5.61 | 7.0567 | N | 0
2025-08-09 | 03 | 2031-08-09 03:00 | 5.04 | 6.3397 | N | 0
2025-08-09 | 04 | 2031-08-09 04:00 | 4.53 | 5.6982 | N | 0
2025-08-09 | 05 | 2031-08-09 05:00 | 4.01 | 5.0441 | N | 0
2025-08-09 | 06 | 2031-08-09 06:00 | 3.58 | 4.5032 | N | 0
2025-08-09 | 07 | 2031-08-09 07:00 | 3.31 | 4.1636 | N | 0
2025-08-09 | 08 | 2031-08-09 08:00 | 3.18 | 4.0001 | N | 0
2025-08-09 | 09 | 2031-08-09 09:00 | 3.13 | 3.9372 | N | 0
2025-08-09 | 10 | 2031-08-09 10:00 | 3.21 | 4.0378 | N | 0
2025-08-09 | 11 | 2031-08-09 11:00 | 3.66 | 4.6038 | N | 0
2025-08-09 | 12 | 2031-08-09 12:00 | 4.4 | 5.5347 | N | 0
2025-08-09 | 13 | 2031-08-09 13:00 | 4.85 | 6.1007 | N | 0
2025-08-09 | 14 | 2031-08-09 14:00 | 5.84 | 7.346 | N | 0
2025-08-09 | 15 | 2031-08-09 15:00 | 6.47 | 8.1385 | N | 0
2025-08-09 | 16 | 2031-08-09 16:00 | 6.69 | 8.4152 | N | 0
2025-08-09 | 17 | 2031-08-09 17:00 | 6.95 | 8.7423 | N | 0
2025-08-09 | 18 | 2031-08-09 18:00 | 7.17 | 9.019 | N | 0
2025-08-09 | 19 | 2031-08-09 19:00 | 7.41 | 9.3209 | N | 0
2025-08-09 | 20 | 2031-08-09 20:00 | 7.57 | 9.5222 | N | 0
2025-08-09 | 21 | 2031-08-09 21:00 | 7.63 | 9.5976 | N | 0
2025-08-09 | 22 | 2031-08-09 22:00 | 7.58 | 9.5347 | N | 0
2025-08-09 | 23 | 2031-08-09 23:00 | 7.13 | 8.9687 | N | 0
2025-08-10 | 00 | 2031-08-10 | 6.8 | 8.5536 | N | 0
2025-08-10 | 01 | 2031-08-10 01:00 | 6.5 | 8.1762 | N | 0
2025-08-10 | 02 | 2031-08-10 02:00 | 6.08 | 7.6479 | N | 0
2025-08-10 | 03 | 2031-08-10 03:00 | 5.53 | 6.9561 | N | 0
2025-08-10 | 04 | 2031-08-10 04:00 | 5.01 | 6.302 | N | 0
2025-08-10 | 05 | 2031-08-10 05:00 | 4.39 | 5.5221 | N | 0
2025-08-10 | 06 | 2031-08-10 06:00 | 4.01 | 5.0441 | N | 0
2025-08-10 | 07 | 2031-08-10 07:00 | 3.74 | 4.7045 | N | 0
2025-08-10 | 08 | 2031-08-10 08:00 | 3.5 | 4.4026 | N | 0
2025-08-10 | 09 | 2031-08-10 09:00 | 3.37 | 4.2391 | N | 0
2025-08-10 | 10 | 2031-08-10 10:00 | 3.36 | 4.2265 | N | 0
2025-08-10 | 11 | 2031-08-10 11:00 | 3.83 | 4.8177 | N | 0
2025-08-10 | 12 | 2031-08-10 12:00 | 4.67 | 5.8743 | N | 0
2025-08-10 | 13 | 2031-08-10 13:00 | 5.55 | 6.9812 | N | 0
2025-08-10 | 14 | 2031-08-10 14:00 | 6.37 | 8.0127 | N | 0
2025-08-10 | 15 | 2031-08-10 15:00 | 7.02 | 8.8303 | N | 0
2025-08-10 | 16 | 2031-08-10 16:00 | 7.4 | 9.3083 | N | 0
2025-08-10 | 17 | 2031-08-10 17:00 | 7.48 | 9.409 | N | 0
2025-08-10 | 18 | 2031-08-10 18:00 | 7.71 | 9.6983 | N | 0
2025-08-10 | 19 | 2031-08-10 19:00 | 7.95 | 10.0002 | N | 0
2025-08-10 | 20 | 2031-08-10 20:00 | 8.19 | 10.302 | N | 0
2025-08-10 | 21 | 2031-08-10 21:00 | 8.37 | 10.5285 | N | 0
2025-08-10 | 22 | 2031-08-10 22:00 | 8.19 | 10.302 | N | 0
2025-08-10 | 23 | 2031-08-10 23:00 | 7.85 | 9.8744 | N | 0
2025-08-11 | 00 | 2031-08-11 | 7.34 | 9.2328 | N | 0
2025-08-11 | 01 | 2031-08-11 01:00 | 7.21 | 9.0693 | N | 0
2025-08-11 | 02 | 2031-08-11 02:00 | 6.55 | 8.2391 | N | 0
2025-08-11 | 03 | 2031-08-11 03:00 | 5.75 | 7.2328 | N | 0
2025-08-11 | 04 | 2031-08-11 04:00 | 5.08 | 6.39 | N | 0
2025-08-11 | 05 | 2031-08-11 05:00 | 4.55 | 5.7234 | N | 0
2025-08-11 | 06 | 2031-08-11 06:00 | 4.13 | 5.1951 | N | 0
2025-08-11 | 07 | 2031-08-11 07:00 | 3.76 | 4.7296 | N | 0
2025-08-11 | 08 | 2031-08-11 08:00 | 3.58 | 4.5032 | N | 0
2025-08-11 | 09 | 2031-08-11 09:00 | 3.53 | 4.4403 | N | 0
2025-08-11 | 10 | 2031-08-11 10:00 | 3.72 | 4.6793 | N | 0
2025-08-11 | 11 | 2031-08-11 11:00 | 4.4 | 5.5347 | N | 0
2025-08-11 | 12 | 2031-08-11 12:00 | 5.14 | 6.4655 | N | 0
2025-08-11 | 13 | 2031-08-11 13:00 | 6.05 | 7.6102 | N | 0
2025-08-11 | 14 | 2031-08-11 14:00 | 6.67 | 8.3901 | N | 0
2025-08-11 | 15 | 2031-08-11 15:00 | 7.12 | 8.9561 | N | 0
2025-08-11 | 16 | 2031-08-11 16:00 | 7.59 | 9.5473 | N | 0
2025-08-11 | 17 | 2031-08-11 17:00 | 7.59 | 9.5473 | N | 0
2025-08-11 | 18 | 2031-08-11 18:00 | 7.82 | 9.8366 | N | 0
2025-08-11 | 19 | 2031-08-11 19:00 | 8.08 | 10.1637 | N | 0
2025-08-11 | 20 | 2031-08-11 20:00 | 8.34 | 10.4907 | N | 0
2025-08-11 | 21 | 2031-08-11 21:00 | 8.59 | 10.8052 | Y | 0.1652 | 1
2025-08-11 | 22 | 2031-08-11 22:00 | 8.52 | 10.7172 | Y | 0.07715 | 2 | 2
2025-08-11 | 23 | 2031-08-11 23:00 | 8.07 | 10.1511 | N | 0
2025-08-12 | 00 | 2031-08-12 | 7.82 | 9.8366 | N | 0
2025-08-12 | 01 | 2031-08-12 01:00 | 7.47 | 9.3964 | N | 0
2025-08-12 | 02 | 2031-08-12 02:00 | 6.73 | 8.4655 | N | 0
2025-08-12 | 03 | 2031-08-12 03:00 | 5.94 | 7.4718 | N | 0
2025-08-12 | 04 | 2031-08-12 04:00 | 5.28 | 6.6416 | N | 0
2025-08-12 | 05 | 2031-08-12 05:00 | 4.64 | 5.8366 | N | 0
2025-08-12 | 06 | 2031-08-12 06:00 | 4.15 | 5.2202 | N | 0
2025-08-12 | 07 | 2031-08-12 07:00 | 3.85 | 4.8428 | N | 0
2025-08-12 | 08 | 2031-08-12 08:00 | 3.73 | 4.6919 | N | 0
2025-08-12 | 09 | 2031-08-12 09:00 | 3.74 | 4.7045 | N | 0
2025-08-12 | 10 | 2031-08-12 10:00 | 4.05 | 5.0944 | N | 0
2025-08-12 | 11 | 2031-08-12 11:00 | 4.63 | 5.824 | N | 0
2025-08-12 | 12 | 2031-08-12 12:00 | 5.35 | 6.7297 | N | 0
2025-08-12 | 13 | 2031-08-12 13:00 | 6.04 | 7.5976 | N | 0
2025-08-12 | 14 | 2031-08-12 14:00 | 6.74 | 8.4781 | N | 0
2025-08-12 | 15 | 2031-08-12 15:00 | 7.29 | 9.17 | N | 0
2025-08-12 | 16 | 2031-08-12 16:00 | 7.63 | 9.5976 | N | 0
2025-08-12 | 17 | 2031-08-12 17:00 | 8.08 | 10.1637 | N | 0
2025-08-12 | 18 | 2031-08-12 18:00 | 8.34 | 10.4907 | N | 0
2025-08-12 | 19 | 2031-08-12 19:00 | 8.34 | 10.4907 | N | 0
2025-08-12 | 20 | 2031-08-12 20:00 | 8.33 | 10.4782 | N | 0
2025-08-12 | 21 | 2031-08-12 21:00 | 8.33 | 10.4782 | N | 0
2025-08-12 | 22 | 2031-08-12 22:00 | 8.07 | 10.1511 | N | 0
2025-08-12 | 23 | 2031-08-12 23:00 | 7.58 | 9.5347 | N | 0
2025-08-13 | 00 | 2031-08-13 | 7.34 | 9.2328 | N | 0
2025-08-13 | 01 | 2031-08-13 01:00 | 7.11 | 8.9435 | N | 0
2025-08-13 | 02 | 2031-08-13 02:00 | 6.52 | 8.2014 | N | 0
2025-08-13 | 03 | 2031-08-13 03:00 | 5.65 | 7.107 | N | 0
2025-08-13 | 04 | 2031-08-13 04:00 | 5.02 | 6.3146 | N | 0
2025-08-13 | 05 | 2031-08-13 05:00 | 4.5 | 5.6605 | N | 0
2025-08-13 | 06 | 2031-08-13 06:00 | 4.1 | 5.1573 | N | 0
2025-08-13 | 07 | 2031-08-13 07:00 | 3.88 | 4.8806 | N | 0
2025-08-13 | 08 | 2031-08-13 08:00 | 3.82 | 4.8051 | N | 0
2025-08-13 | 09 | 2031-08-13 09:00 | 3.79 | 4.7674 | N | 0
2025-08-13 | 10 | 2031-08-13 10:00 | 4.09 | 5.1447 | N | 0
2025-08-13 | 11 | 2031-08-13 11:00 | 4.56 | 5.7359 | N | 0
2025-08-13 | 12 | 2031-08-13 12:00 | 5.17 | 6.5032 | N | 0
2025-08-13 | 13 | 2031-08-13 13:00 | 5.64 | 7.0945 | N | 0
2025-08-13 | 14 | 2031-08-13 14:00 | 6.02 | 7.5724 | N | 0
2025-08-13 | 15 | 2031-08-13 15:00 | 6.26 | 7.8743 | N | 0
2025-08-13 | 16 | 2031-08-13 16:00 | 6.84 | 8.6039 | N | 0
2025-08-13 | 17 | 2031-08-13 17:00 | 7.05 | 8.8681 | N | 0
2025-08-13 | 18 | 2031-08-13 18:00 | 7.44 | 9.3586 | N | 0
2025-08-13 | 19 | 2031-08-13 19:00 | 7.61 | 9.5725 | N | 0
2025-08-13 | 20 | 2031-08-13 20:00 | 8 | 10.0631 | N | 0
2025-08-13 | 21 | 2031-08-13 21:00 | 8 | 10.0631 | N | 0
2025-08-13 | 22 | 2031-08-13 22:00 | 7.85 | 9.8744 | N | 0
2025-08-13 | 23 | 2031-08-13 23:00 | 7.43 | 9.3461 | N | 0
2025-08-14 | 00 | 2031-08-14 | 7.2 | 9.0567 | N | 0
2025-08-14 | 01 | 2031-08-14 01:00 | 7.06 | 8.8806 | N | 0
2025-08-14 | 02 | 2031-08-14 02:00 | 6.2 | 7.7989 | N | 0
2025-08-14 | 03 | 2031-08-14 03:00 | 5.34 | 6.7171 | N | 0
2025-08-14 | 04 | 2031-08-14 04:00 | 4.79 | 6.0253 | N | 0
2025-08-14 | 05 | 2031-08-14 05:00 | 4.28 | 5.3837 | N | 0
2025-08-14 | 06 | 2031-08-14 06:00 | 3.81 | 4.7925 | N | 0
2025-08-14 | 07 | 2031-08-14 07:00 | 3.59 | 4.5158 | N | 0
2025-08-14 | 08 | 2031-08-14 08:00 | 3.36 | 4.2265 | N | 0
2025-08-14 | 09 | 2031-08-14 09:00 | 3.38 | 4.2516 | N | 0
2025-08-14 | 10 | 2031-08-14 10:00 | 3.59 | 4.5158 | N | 0
2025-08-14 | 11 | 2031-08-14 11:00 | 4.24 | 5.3334 | N | 0
2025-08-14 | 12 | 2031-08-14 12:00 | 4.85 | 6.1007 | N | 0
2025-08-14 | 13 | 2031-08-14 13:00 | 5.36 | 6.7422 | N | 0
2025-08-14 | 14 | 2031-08-14 14:00 | 5.92 | 7.4467 | N | 0
2025-08-14 | 15 | 2031-08-14 15:00 | 6.24 | 7.8492 | N | 0
2025-08-14 | 16 | 2031-08-14 16:00 | 6.75 | 8.4907 | N | 0
2025-08-14 | 17 | 2031-08-14 17:00 | 6.84 | 8.6039 | N | 0
2025-08-14 | 18 | 2031-08-14 18:00 | 6.89 | 8.6668 | N | 0
2025-08-14 | 19 | 2031-08-14 19:00 | 7.13 | 8.9687 | N | 0
2025-08-14 | 20 | 2031-08-14 20:00 | 7.35 | 9.2454 | N | 0
2025-08-14 | 21 | 2031-08-14 21:00 | 7.58 | 9.5347 | N | 0
2025-08-14 | 22 | 2031-08-14 22:00 | 7.58 | 9.5347 | N | 0
2025-08-14 | 23 | 2031-08-14 23:00 | 7.09 | 8.9184 | N | 0
2025-08-15 | 00 | 2031-08-15 | 6.86 | 8.6291 | N | 0
2025-08-15 | 01 | 2031-08-15 01:00 | 6.42 | 8.0756 | N | 0
2025-08-15 | 02 | 2031-08-15 02:00 | 5.77 | 7.258 | N | 0
2025-08-15 | 03 | 2031-08-15 03:00 | 5.11 | 6.4278 | N | 0
2025-08-15 | 04 | 2031-08-15 04:00 | 4.48 | 5.6353 | N | 0
2025-08-15 | 05 | 2031-08-15 05:00 | 3.85 | 4.8428 | N | 0
2025-08-15 | 06 | 2031-08-15 06:00 | 3.55 | 4.4655 | N | 0
2025-08-15 | 07 | 2031-08-15 07:00 | 3.16 | 3.9749 | N | 0
2025-08-15 | 08 | 2031-08-15 08:00 | 3.05 | 3.8365 | N | 0
2025-08-15 | 09 | 2031-08-15 09:00 | 3.02 | 3.7988 | N | 0
2025-08-15 | 10 | 2031-08-15 10:00 | 3.28 | 4.1259 | N | 0
2025-08-15 | 11 | 2031-08-15 11:00 | 3.88 | 4.8806 | N | 0
2025-08-15 | 12 | 2031-08-15 12:00 | 4.48 | 5.6353 | N | 0
2025-08-15 | 13 | 2031-08-15 13:00 | 5.14 | 6.4655 | N | 0
2025-08-15 | 14 | 2031-08-15 14:00 | 5.7 | 7.1699 | N | 0
2025-08-15 | 15 | 2031-08-15 15:00 | 6.13 | 7.7108 | N | 0
2025-08-15 | 16 | 2031-08-15 16:00 | 6.42 | 8.0756 | N | 0
2025-08-15 | 17 | 2031-08-15 17:00 | 6.63 | 8.3398 | N | 0
2025-08-15 | 18 | 2031-08-15 18:00 | 6.97 | 8.7674 | N | 0
2025-08-15 | 19 | 2031-08-15 19:00 | 7.07 | 8.8932 | N | 0
2025-08-15 | 20 | 2031-08-15 20:00 | 7.3 | 9.1825 | N | 0
2025-08-15 | 21 | 2031-08-15 21:00 | 7.61 | 9.5725 | N | 0
2025-08-15 | 22 | 2031-08-15 22:00 | 7.43 | 9.3461 | N | 0
2025-08-15 | 23 | 2031-08-15 23:00 | 7.05 | 8.8681 | N | 0
2025-08-16 | 00 | 2031-08-16 | 6.52 | 8.2014 | N | 0
2025-08-16 | 01 | 2031-08-16 01:00 | 6.15 | 7.736 | N | 0
2025-08-16 | 02 | 2031-08-16 02:00 | 5.68 | 7.1448 | N | 0
2025-08-16 | 03 | 2031-08-16 03:00 | 4.81 | 6.0504 | N | 0
2025-08-16 | 04 | 2031-08-16 04:00 | 4.24 | 5.3334 | N | 0
2025-08-16 | 05 | 2031-08-16 05:00 | 3.77 | 4.7422 | N | 0
2025-08-16 | 06 | 2031-08-16 06:00 | 3.42 | 4.302 | N | 0
2025-08-16 | 07 | 2031-08-16 07:00 | 3.21 | 4.0378 | N | 0
2025-08-16 | 08 | 2031-08-16 08:00 | 3.08 | 3.8743 | N | 0
2025-08-16 | 09 | 2031-08-16 09:00 | 2.99 | 3.7611 | N | 0
2025-08-16 | 10 | 2031-08-16 10:00 | 3 | 3.7736 | N | 0
2025-08-16 | 11 | 2031-08-16 11:00 | 3.59 | 4.5158 | N | 0
2025-08-16 | 12 | 2031-08-16 12:00 | 4.35 | 5.4718 | N | 0
2025-08-16 | 13 | 2031-08-16 13:00 | 5.22 | 6.5661 | N | 0
2025-08-16 | 14 | 2031-08-16 14:00 | 5.83 | 7.3334 | N | 0
2025-08-16 | 15 | 2031-08-16 15:00 | 6.46 | 8.1259 | N | 0
2025-08-16 | 16 | 2031-08-16 16:00 | 6.87 | 8.6416 | N | 0
2025-08-16 | 17 | 2031-08-16 17:00 | 6.93 | 8.7171 | N | 0
2025-08-16 | 18 | 2031-08-16 18:00 | 7.17 | 9.019 | N | 0
2025-08-16 | 19 | 2031-08-16 19:00 | 7.3 | 9.1825 | N | 0
2025-08-16 | 20 | 2031-08-16 20:00 | 7.29 | 9.17 | N | 0
2025-08-16 | 21 | 2031-08-16 21:00 | 7.29 | 9.17 | N | 0
2025-08-16 | 22 | 2031-08-16 22:00 | 7.29 | 9.17 | N | 0
2025-08-16 | 23 | 2031-08-16 23:00 | 7.07 | 8.8932 | N | 0
2025-08-17 | 00 | 2031-08-17 | 6.42 | 8.0756 | N | 0
2025-08-17 | 01 | 2031-08-17 01:00 | 6.25 | 7.8618 | N | 0
2025-08-17 | 02 | 2031-08-17 02:00 | 5.89 | 7.4089 | N | 0
2025-08-17 | 03 | 2031-08-17 03:00 | 5.25 | 6.6039 | N | 0
2025-08-17 | 04 | 2031-08-17 04:00 | 4.7 | 5.912 | N | 0
2025-08-17 | 05 | 2031-08-17 05:00 | 4.2 | 5.2831 | N | 0
2025-08-17 | 06 | 2031-08-17 06:00 | 3.81 | 4.7925 | N | 0
2025-08-17 | 07 | 2031-08-17 07:00 | 3.59 | 4.5158 | N | 0
2025-08-17 | 08 | 2031-08-17 08:00 | 3.46 | 4.3523 | N | 0
2025-08-17 | 09 | 2031-08-17 09:00 | 3.42 | 4.302 | N | 0
2025-08-17 | 10 | 2031-08-17 10:00 | 3.46 | 4.3523 | N | 0
2025-08-17 | 11 | 2031-08-17 11:00 | 3.74 | 4.7045 | N | 0
2025-08-17 | 12 | 2031-08-17 12:00 | 4.28 | 5.3837 | N | 0
2025-08-17 | 13 | 2031-08-17 13:00 | 4.91 | 6.1762 | N | 0
2025-08-17 | 14 | 2031-08-17 14:00 | 5.27 | 6.629 | N | 0
2025-08-17 | 15 | 2031-08-17 15:00 | 5.5 | 6.9183 | N | 0
2025-08-17 | 16 | 2031-08-17 16:00 | 5.72 | 7.1951 | N | 0
2025-08-17 | 17 | 2031-08-17 17:00 | 5.75 | 7.2328 | N | 0
2025-08-17 | 18 | 2031-08-17 18:00 | 5.66 | 7.1196 | N | 0
2025-08-17 | 19 | 2031-08-17 19:00 | 5.6 | 7.0441 | N | 0
2025-08-17 | 20 | 2031-08-17 20:00 | 6.15 | 7.736 | N | 0
2025-08-17 | 21 | 2031-08-17 21:00 | 6.48 | 8.1511 | N | 0
2025-08-17 | 22 | 2031-08-17 22:00 | 6.48 | 8.1511 | N | 0
2025-08-17 | 23 | 2031-08-17 23:00 | 6.2 | 7.7989 | N | 0
2025-08-18 | 00 | 2031-08-18 | 5.71 | 7.1825 | N | 0
2025-08-18 | 01 | 2031-08-18 01:00 | 5.27 | 6.629 | N | 0
2025-08-18 | 02 | 2031-08-18 02:00 | 4.7 | 5.912 | N | 0
2025-08-18 | 03 | 2031-08-18 03:00 | 4.13 | 5.1951 | N | 0
2025-08-18 | 04 | 2031-08-18 04:00 | 3.47 | 4.3648 | N | 0
2025-08-18 | 05 | 2031-08-18 05:00 | 3.08 | 3.8743 | N | 0
2025-08-18 | 06 | 2031-08-18 06:00 | 2.82 | 3.5472 | N | 0
2025-08-18 | 07 | 2031-08-18 07:00 | 2.73 | 3.434 | N | 0
2025-08-18 | 08 | 2031-08-18 08:00 | 2.64 | 3.3208 | N | 0
2025-08-18 | 09 | 2031-08-18 09:00 | 2.66 | 3.346 | N | 0
2025-08-18 | 10 | 2031-08-18 10:00 | 2.84 | 3.5724 | N | 0
2025-08-18 | 11 | 2031-08-18 11:00 | 3.18 | 4.0001 | N | 0
2025-08-18 | 12 | 2031-08-18 12:00 | 3.53 | 4.4403 | N | 0
2025-08-18 | 13 | 2031-08-18 13:00 | 3.82 | 4.8051 | N | 0
2025-08-18 | 14 | 2031-08-18 14:00 | 4.24 | 5.3334 | N | 0
2025-08-18 | 15 | 2031-08-18 15:00 | 4.48 | 5.6353 | N | 0
2025-08-18 | 16 | 2031-08-18 16:00 | 4.62 | 5.8114 | N | 0
2025-08-18 | 17 | 2031-08-18 17:00 | 4.76 | 5.9875 | N | 0
2025-08-18 | 18 | 2031-08-18 18:00 | 4.83 | 6.0756 | N | 0
2025-08-18 | 19 | 2031-08-18 19:00 | 5.08 | 6.39 | N | 0
2025-08-18 | 20 | 2031-08-18 20:00 | 5.49 | 6.9058 | N | 0
2025-08-18 | 21 | 2031-08-18 21:00 | 5.74 | 7.2202 | N | 0
2025-08-18 | 22 | 2031-08-18 22:00 | 5.54 | 6.9687 | N | 0
2025-08-18 | 23 | 2031-08-18 23:00 | 5.06 | 6.3649 | N | 0
2025-08-19 | 00 | 2031-08-19 | 4.88 | 6.1385 | N | 0
2025-08-19 | 01 | 2031-08-19 01:00 | 4.75 | 5.9749 | N | 0
2025-08-19 | 02 | 2031-08-19 02:00 | 4.16 | 5.2328 | N | 0
2025-08-19 | 03 | 2031-08-19 03:00 | 3.59 | 4.5158 | N | 0
2025-08-19 | 04 | 2031-08-19 04:00 | 3.2 | 4.0252 | N | 0
2025-08-19 | 05 | 2031-08-19 05:00 | 2.84 | 3.5724 | N | 0
2025-08-19 | 06 | 2031-08-19 06:00 | 2.7 | 3.3963 | N | 0
2025-08-19 | 07 | 2031-08-19 07:00 | 2.59 | 3.2579 | N | 0
2025-08-19 | 08 | 2031-08-19 08:00 | 2.57 | 3.2328 | N | 0
2025-08-19 | 09 | 2031-08-19 09:00 | 2.62 | 3.2956 | N | 0
2025-08-19 | 10 | 2031-08-19 10:00 | 2.94 | 3.6982 | N | 0
2025-08-19 | 11 | 2031-08-19 11:00 | 3.36 | 4.2265 | N | 0
2025-08-19 | 12 | 2031-08-19 12:00 | 3.63 | 4.5661 | N | 0
2025-08-19 | 13 | 2031-08-19 13:00 | 3.84 | 4.8303 | N | 0
2025-08-19 | 14 | 2031-08-19 14:00 | 4 | 5.0315 | N | 0
2025-08-19 | 15 | 2031-08-19 15:00 | 4.26 | 5.3586 | N | 0
2025-08-19 | 16 | 2031-08-19 16:00 | 4.4 | 5.5347 | N | 0
2025-08-19 | 17 | 2031-08-19 17:00 | 4.43 | 5.5724 | N | 0
2025-08-19 | 18 | 2031-08-19 18:00 | 4.55 | 5.7234 | N | 0
2025-08-19 | 19 | 2031-08-19 19:00 | 4.64 | 5.8366 | N | 0
2025-08-19 | 20 | 2031-08-19 20:00 | 4.89 | 6.151 | N | 0
2025-08-19 | 21 | 2031-08-19 21:00 | 5.19 | 6.5284 | N | 0
2025-08-19 | 22 | 2031-08-19 22:00 | 5.1 | 6.4152 | N | 0
2025-08-19 | 23 | 2031-08-19 23:00 | 4.86 | 6.1133 | N | 0
2025-08-20 | 00 | 2031-08-20 | 4.86 | 6.1133 | N | 0
2025-08-20 | 01 | 2031-08-20 01:00 | 4.57 | 5.7485 | N | 0
2025-08-20 | 02 | 2031-08-20 02:00 | 4.09 | 5.1447 | N | 0
2025-08-20 | 03 | 2031-08-20 03:00 | 3.57 | 4.4906 | N | 0
2025-08-20 | 04 | 2031-08-20 04:00 | 3.17 | 3.9875 | N | 0
2025-08-20 | 05 | 2031-08-20 05:00 | 2.94 | 3.6982 | N | 0
2025-08-20 | 06 | 2031-08-20 06:00 | 2.7 | 3.3963 | N | 0
2025-08-20 | 07 | 2031-08-20 07:00 | 2.63 | 3.3082 | N | 0
2025-08-20 | 08 | 2031-08-20 08:00 | 2.58 | 3.2453 | N | 0
2025-08-20 | 09 | 2031-08-20 09:00 | 2.71 | 3.4089 | N | 0
2025-08-20 | 10 | 2031-08-20 10:00 | 3.13 | 3.9372 | N | 0
2025-08-20 | 11 | 2031-08-20 11:00 | 3.48 | 4.3774 | N | 0
2025-08-20 | 12 | 2031-08-20 12:00 | 3.73 | 4.6919 | N | 0
2025-08-20 | 13 | 2031-08-20 13:00 | 3.9 | 4.9057 | N | 0
2025-08-20 | 14 | 2031-08-20 14:00 | 3.98 | 5.0064 | N | 0
2025-08-20 | 15 | 2031-08-20 15:00 | 4.12 | 5.1825 | N | 0
2025-08-20 | 16 | 2031-08-20 16:00 | 4.23 | 5.3208 | N | 0
2025-08-20 | 17 | 2031-08-20 17:00 | 4.36 | 5.4844 | N | 0
2025-08-20 | 18 | 2031-08-20 18:00 | 4.36 | 5.4844 | N | 0
2025-08-20 | 19 | 2031-08-20 19:00 | 4.28 | 5.3837 | N | 0
2025-08-20 | 20 | 2031-08-20 20:00 | 4.81 | 6.0504 | N | 0
2025-08-20 | 21 | 2031-08-20 21:00 | 5.05 | 6.3523 | N | 0
2025-08-20 | 22 | 2031-08-20 22:00 | 5.03 | 6.3271 | N | 0
2025-08-20 | 23 | 2031-08-20 23:00 | 4.79 | 6.0253 | N | 0
2025-08-21 | 00 | 2031-08-21 | 4.62 | 5.8114 | N | 0
2025-08-21 | 01 | 2031-08-21 01:00 | 4.53 | 5.6982 | N | 0
2025-08-21 | 02 | 2031-08-21 02:00 | 4.07 | 5.1196 | N | 0
2025-08-21 | 03 | 2031-08-21 03:00 | 3.63 | 4.5661 | N | 0
2025-08-21 | 04 | 2031-08-21 04:00 | 3.19 | 4.0126 | N | 0
2025-08-21 | 05 | 2031-08-21 05:00 | 2.94 | 3.6982 | N | 0
2025-08-21 | 06 | 2031-08-21 06:00 | 2.64 | 3.3208 | N | 0
2025-08-21 | 07 | 2031-08-21 07:00 | 2.56 | 3.2202 | N | 0
2025-08-21 | 08 | 2031-08-21 08:00 | 2.52 | 3.1699 | N | 0
2025-08-21 | 09 | 2031-08-21 09:00 | 2.63 | 3.3082 | N | 0
2025-08-21 | 10 | 2031-08-21 10:00 | 2.94 | 3.6982 | N | 0
2025-08-21 | 11 | 2031-08-21 11:00 | 3.19 | 4.0126 | N | 0
2025-08-21 | 12 | 2031-08-21 12:00 | 3.53 | 4.4403 | N | 0
2025-08-21 | 13 | 2031-08-21 13:00 | 3.84 | 4.8303 | N | 0
2025-08-21 | 14 | 2031-08-21 14:00 | 4.2 | 5.2831 | N | 0
2025-08-21 | 15 | 2031-08-21 15:00 | 4.31 | 5.4215 | N | 0
2025-08-21 | 16 | 2031-08-21 16:00 | 4.28 | 5.3837 | N | 0
2025-08-21 | 17 | 2031-08-21 17:00 | 4.37 | 5.4969 | N | 0
2025-08-21 | 18 | 2031-08-21 18:00 | 4.48 | 5.6353 | N | 0
2025-08-21 | 19 | 2031-08-21 19:00 | 4.87 | 6.1259 | N | 0
2025-08-21 | 20 | 2031-08-21 20:00 | 5.4 | 6.7926 | N | 0
2025-08-21 | 21 | 2031-08-21 21:00 | 5.65 | 7.107 | N | 0
2025-08-21 | 22 | 2031-08-21 22:00 | 5.65 | 7.107 | N | 0
2025-08-21 | 23 | 2031-08-21 23:00 | 5.48 | 6.8932 | N | 0
2025-08-22 | 00 | 2031-08-22 | 5.19 | 6.5284 | N | 0
2025-08-22 | 01 | 2031-08-22 01:00 | 5.06 | 6.3649 | N | 0
2025-08-22 | 02 | 2031-08-22 02:00 | 4.52 | 5.6856 | N | 0
2025-08-22 | 03 | 2031-08-22 03:00 | 3.87 | 4.868 | N | 0
2025-08-22 | 04 | 2031-08-22 04:00 | 3.37 | 4.2391 | N | 0
2025-08-22 | 05 | 2031-08-22 05:00 | 2.94 | 3.6982 | N | 0
2025-08-22 | 06 | 2031-08-22 06:00 | 2.73 | 3.434 | N | 0
2025-08-22 | 07 | 2031-08-22 07:00 | 2.66 | 3.346 | N | 0
2025-08-22 | 08 | 2031-08-22 08:00 | 2.57 | 3.2328 | N | 0
2025-08-22 | 09 | 2031-08-22 09:00 | 2.63 | 3.3082 | N | 0
2025-08-22 | 10 | 2031-08-22 10:00 | 2.94 | 3.6982 | N | 0
2025-08-22 | 11 | 2031-08-22 11:00 | 3.44 | 4.3271 | N | 0
2025-08-22 | 12 | 2031-08-22 12:00 | 3.95 | 4.9686 | N | 0
2025-08-22 | 13 | 2031-08-22 13:00 | 4.45 | 5.5976 | N | 0
2025-08-22 | 14 | 2031-08-22 14:00 | 4.9 | 6.1636 | N | 0
2025-08-22 | 15 | 2031-08-22 15:00 | 5.27 | 6.629 | N | 0
2025-08-22 | 16 | 2031-08-22 16:00 | 5.56 | 6.9938 | N | 0
2025-08-22 | 17 | 2031-08-22 17:00 | 5.77 | 7.258 | N | 0
2025-08-22 | 18 | 2031-08-22 18:00 | 5.93 | 7.4592 | N | 0
2025-08-22 | 19 | 2031-08-22 19:00 | 6.17 | 7.7611 | N | 0
2025-08-22 | 20 | 2031-08-22 20:00 | 6.43 | 8.0882 | N | 0
2025-08-22 | 21 | 2031-08-22 21:00 | 6.47 | 8.1385 | N | 0
2025-08-22 | 22 | 2031-08-22 22:00 | 6.35 | 7.9875 | N | 0
2025-08-22 | 23 | 2031-08-22 23:00 | 6 | 7.5473 | N | 0
2025-08-23 | 00 | 2031-08-23 | 5.69 | 7.1573 | N | 0
2025-08-23 | 01 | 2031-08-23 01:00 | 5.45 | 6.8555 | N | 0
2025-08-23 | 02 | 2031-08-23 02:00 | 4.87 | 6.1259 | N | 0
2025-08-23 | 03 | 2031-08-23 03:00 | 4.36 | 5.4844 | N | 0
2025-08-23 | 04 | 2031-08-23 04:00 | 3.88 | 4.8806 | N | 0
2025-08-23 | 05 | 2031-08-23 05:00 | 3.42 | 4.302 | N | 0
2025-08-23 | 06 | 2031-08-23 06:00 | 3.07 | 3.8617 | N | 0
2025-08-23 | 07 | 2031-08-23 07:00 | 2.89 | 3.6353 | N | 0
2025-08-23 | 08 | 2031-08-23 08:00 | 2.67 | 3.3585 | N | 0
2025-08-23 | 09 | 2031-08-23 09:00 | 2.67 | 3.3585 | N | 0
2025-08-23 | 10 | 2031-08-23 10:00 | 2.72 | 3.4214 | N | 0
2025-08-23 | 11 | 2031-08-23 11:00 | 3.15 | 3.9623 | N | 0
2025-08-23 | 12 | 2031-08-23 12:00 | 3.91 | 4.9183 | N | 0
2025-08-23 | 13 | 2031-08-23 13:00 | 4.33 | 5.4466 | N | 0
2025-08-23 | 14 | 2031-08-23 14:00 | 4.68 | 5.8869 | N | 0
2025-08-23 | 15 | 2031-08-23 15:00 | 5.27 | 6.629 | N | 0
2025-08-23 | 16 | 2031-08-23 16:00 | 5.42 | 6.8177 | N | 0
2025-08-23 | 17 | 2031-08-23 17:00 | 5.62 | 7.0693 | N | 0
2025-08-23 | 18 | 2031-08-23 18:00 | 5.63 | 7.0819 | N | 0
2025-08-23 | 19 | 2031-08-23 19:00 | 5.63 | 7.0819 | N | 0
2025-08-23 | 20 | 2031-08-23 20:00 | 5.62 | 7.0693 | N | 0
2025-08-23 | 21 | 2031-08-23 21:00 | 5.81 | 7.3083 | N | 0
2025-08-23 | 22 | 2031-08-23 22:00 | 5.76 | 7.2454 | N | 0
2025-08-23 | 23 | 2031-08-23 23:00 | 5.61 | 7.0567 | N | 0
2025-08-24 | 00 | 2031-08-24 | 5.37 | 6.7548 | N | 0
2025-08-24 | 01 | 2031-08-24 01:00 | 5.22 | 6.5661 | N | 0
2025-08-24 | 02 | 2031-08-24 02:00 | 4.96 | 6.2391 | N | 0
2025-08-24 | 03 | 2031-08-24 03:00 | 4.53 | 5.6982 | N | 0
2025-08-24 | 04 | 2031-08-24 04:00 | 4.04 | 5.0818 | N | 0
2025-08-24 | 05 | 2031-08-24 05:00 | 3.66 | 4.6038 | N | 0
2025-08-24 | 06 | 2031-08-24 06:00 | 3.41 | 4.2894 | N | 0
2025-08-24 | 07 | 2031-08-24 07:00 | 3.11 | 3.912 | N | 0
2025-08-24 | 08 | 2031-08-24 08:00 | 2.98 | 3.7485 | N | 0
2025-08-24 | 09 | 2031-08-24 09:00 | 2.86 | 3.5975 | N | 0
2025-08-24 | 10 | 2031-08-24 10:00 | 2.89 | 3.6353 | N | 0
2025-08-24 | 11 | 2031-08-24 11:00 | 3.33 | 4.1887 | N | 0
2025-08-24 | 12 | 2031-08-24 12:00 | 3.88 | 4.8806 | N | 0
2025-08-24 | 13 | 2031-08-24 13:00 | 4.36 | 5.4844 | N | 0
2025-08-24 | 14 | 2031-08-24 14:00 | 4.8 | 6.0378 | N | 0
2025-08-24 | 15 | 2031-08-24 15:00 | 5.29 | 6.6542 | N | 0
2025-08-24 | 16 | 2031-08-24 16:00 | 5.8 | 7.2957 | N | 0
2025-08-24 | 17 | 2031-08-24 17:00 | 5.92 | 7.4467 | N | 0
2025-08-24 | 18 | 2031-08-24 18:00 | 5.93 | 7.4592 | N | 0
2025-08-24 | 19 | 2031-08-24 19:00 | 6.22 | 7.824 | N | 0
2025-08-24 | 20 | 2031-08-24 20:00 | 6.3 | 7.9247 | N | 0
2025-08-24 | 21 | 2031-08-24 21:00 | 6.46 | 8.1259 | N | 0
2025-08-24 | 22 | 2031-08-24 22:00 | 6.28 | 7.8995 | N | 0
2025-08-24 | 23 | 2031-08-24 23:00 | 5.95 | 7.4844 | N | 0
2025-08-25 | 00 | 2031-08-25 | 5.6 | 7.0441 | N | 0
2025-08-25 | 01 | 2031-08-25 01:00 | 5.37 | 6.7548 | N | 0
2025-08-25 | 02 | 2031-08-25 02:00 | 4.78 | 6.0127 | N | 0
2025-08-25 | 03 | 2031-08-25 03:00 | 4.08 | 5.1322 | N | 0
2025-08-25 | 04 | 2031-08-25 04:00 | 3.56 | 4.4781 | N | 0
2025-08-25 | 05 | 2031-08-25 05:00 | 3.17 | 3.9875 | N | 0
2025-08-25 | 06 | 2031-08-25 06:00 | 2.92 | 3.673 | N | 0
2025-08-25 | 07 | 2031-08-25 07:00 | 2.79 | 3.5095 | N | 0
2025-08-25 | 08 | 2031-08-25 08:00 | 2.61 | 3.2831 | N | 0
2025-08-25 | 09 | 2031-08-25 09:00 | 2.66 | 3.346 | N | 0
2025-08-25 | 10 | 2031-08-25 10:00 | 2.95 | 3.7108 | N | 0
2025-08-25 | 11 | 2031-08-25 11:00 | 3.32 | 4.1762 | N | 0
2025-08-25 | 12 | 2031-08-25 12:00 | 3.69 | 4.6416 | N | 0
2025-08-25 | 13 | 2031-08-25 13:00 | 3.97 | 4.9938 | N | 0
2025-08-25 | 14 | 2031-08-25 14:00 | 4.5 | 5.6605 | N | 0
2025-08-25 | 15 | 2031-08-25 15:00 | 4.72 | 5.9372 | N | 0
2025-08-25 | 16 | 2031-08-25 16:00 | 4.69 | 5.8995 | N | 0
2025-08-25 | 17 | 2031-08-25 17:00 | 4.71 | 5.9246 | N | 0
2025-08-25 | 18 | 2031-08-25 18:00 | 4.61 | 5.7988 | N | 0
2025-08-25 | 19 | 2031-08-25 19:00 | 4.82 | 6.063 | N | 0
2025-08-25 | 20 | 2031-08-25 20:00 | 5.06 | 6.3649 | N | 0
2025-08-25 | 21 | 2031-08-25 21:00 | 5.31 | 6.6794 | N | 0
2025-08-25 | 22 | 2031-08-25 22:00 | 5.09 | 6.4026 | N | 0
2025-08-25 | 23 | 2031-08-25 23:00 | 4.79 | 6.0253 | N | 0
2025-08-26 | 00 | 2031-08-26 | 4.65 | 5.8491 | N | 0
2025-08-26 | 01 | 2031-08-26 01:00 | 4.5 | 5.6605 | N | 0
2025-08-26 | 02 | 2031-08-26 02:00 | 3.95 | 4.9686 | N | 0
2025-08-26 | 03 | 2031-08-26 03:00 | 3.45 | 4.3397 | N | 0
2025-08-26 | 04 | 2031-08-26 04:00 | 3.05 | 3.8365 | N | 0
2025-08-26 | 05 | 2031-08-26 05:00 | 2.72 | 3.4214 | N | 0
2025-08-26 | 06 | 2031-08-26 06:00 | 2.53 | 3.1824 | N | 0
2025-08-26 | 07 | 2031-08-26 07:00 | 2.46 | 3.0944 | N | 0
2025-08-26 | 08 | 2031-08-26 08:00 | 2.42 | 3.0441 | N | 0
2025-08-26 | 09 | 2031-08-26 09:00 | 2.49 | 3.1321 | N | 0
2025-08-26 | 10 | 2031-08-26 10:00 | 2.78 | 3.4969 | N | 0
2025-08-26 | 11 | 2031-08-26 11:00 | 3.11 | 3.912 | N | 0
2025-08-26 | 12 | 2031-08-26 12:00 | 3.36 | 4.2265 | N | 0
2025-08-26 | 13 | 2031-08-26 13:00 | 3.57 | 4.4906 | N | 0
2025-08-26 | 14 | 2031-08-26 14:00 | 3.83 | 4.8177 | N | 0
2025-08-26 | 15 | 2031-08-26 15:00 | 4.11 | 5.1699 | N | 0
2025-08-26 | 16 | 2031-08-26 16:00 | 4.18 | 5.2579 | N | 0
2025-08-26 | 17 | 2031-08-26 17:00 | 4.23 | 5.3208 | N | 0
2025-08-26 | 18 | 2031-08-26 18:00 | 4.28 | 5.3837 | N | 0
2025-08-26 | 19 | 2031-08-26 19:00 | 4.5 | 5.6605 | N | 0
2025-08-26 | 20 | 2031-08-26 20:00 | 4.6 | 5.7863 | N | 0
2025-08-26 | 21 | 2031-08-26 21:00 | 4.86 | 6.1133 | N | 0
2025-08-26 | 22 | 2031-08-26 22:00 | 4.77 | 6.0001 | N | 0
2025-08-26 | 23 | 2031-08-26 23:00 | 4.46 | 5.6102 | N | 0
2025-08-27 | 00 | 2031-08-27 | 4.45 | 5.5976 | N | 0
2025-08-27 | 01 | 2031-08-27 01:00 | 4.19 | 5.2705 | N | 0
2025-08-27 | 02 | 2031-08-27 02:00 | 3.84 | 4.8303 | N | 0
2025-08-27 | 03 | 2031-08-27 03:00 | 3.4 | 4.2768 | N | 0
2025-08-27 | 04 | 2031-08-27 04:00 | 2.99 | 3.7611 | N | 0
2025-08-27 | 05 | 2031-08-27 05:00 | 2.71 | 3.4089 | N | 0
2025-08-27 | 06 | 2031-08-27 06:00 | 2.52 | 3.1699 | N | 0
2025-08-27 | 07 | 2031-08-27 07:00 | 2.43 | 3.0567 | N | 0
2025-08-27 | 08 | 2031-08-27 08:00 | 2.34 | 2.9434 | N | 0
2025-08-27 | 09 | 2031-08-27 09:00 | 2.49 | 3.1321 | N | 0
2025-08-27 | 10 | 2031-08-27 10:00 | 2.74 | 3.4466 | N | 0
2025-08-27 | 11 | 2031-08-27 11:00 | 3.05 | 3.8365 | N | 0
2025-08-27 | 12 | 2031-08-27 12:00 | 3.35 | 4.2139 | N | 0
2025-08-27 | 13 | 2031-08-27 13:00 | 3.56 | 4.4781 | N | 0
2025-08-27 | 14 | 2031-08-27 14:00 | 3.96 | 4.9812 | N | 0
2025-08-27 | 15 | 2031-08-27 15:00 | 4.06 | 5.107 | N | 0
2025-08-27 | 16 | 2031-08-27 16:00 | 4.28 | 5.3837 | N | 0
2025-08-27 | 17 | 2031-08-27 17:00 | 4.22 | 5.3083 | N | 0
2025-08-27 | 18 | 2031-08-27 18:00 | 4.36 | 5.4844 | N | 0
2025-08-27 | 19 | 2031-08-27 19:00 | 4.36 | 5.4844 | N | 0
2025-08-27 | 20 | 2031-08-27 20:00 | 4.8 | 6.0378 | N | 0
2025-08-27 | 21 | 2031-08-27 21:00 | 5.08 | 6.39 | N | 0
2025-08-27 | 22 | 2031-08-27 22:00 | 5.08 | 6.39 | N | 0
2025-08-27 | 23 | 2031-08-27 23:00 | 4.63 | 5.824 | N | 0
2025-08-28 | 00 | 2031-08-28 | 4.58 | 5.7611 | N | 0
2025-08-28 | 01 | 2031-08-28 01:00 | 4.32 | 5.434 | N | 0
2025-08-28 | 02 | 2031-08-28 02:00 | 3.74 | 4.7045 | N | 0
2025-08-28 | 03 | 2031-08-28 03:00 | 3.3 | 4.151 | N | 0
2025-08-28 | 04 | 2031-08-28 04:00 | 2.96 | 3.7233 | N | 0
2025-08-28 | 05 | 2031-08-28 05:00 | 2.67 | 3.3585 | N | 0
2025-08-28 | 06 | 2031-08-28 06:00 | 2.51 | 3.1573 | N | 0
2025-08-28 | 07 | 2031-08-28 07:00 | 2.42 | 3.0441 | N | 0
2025-08-28 | 08 | 2031-08-28 08:00 | 2.38 | 2.9938 | N | 0
2025-08-28 | 09 | 2031-08-28 09:00 | 2.43 | 3.0567 | N | 0
2025-08-28 | 10 | 2031-08-28 10:00 | 2.85 | 3.585 | N | 0
2025-08-28 | 11 | 2031-08-28 11:00 | 3.09 | 3.8869 | N | 0
2025-08-28 | 12 | 2031-08-28 12:00 | 3.37 | 4.2391 | N | 0
2025-08-28 | 13 | 2031-08-28 13:00 | 3.55 | 4.4655 | N | 0
2025-08-28 | 14 | 2031-08-28 14:00 | 3.88 | 4.8806 | N | 0
2025-08-28 | 15 | 2031-08-28 15:00 | 4.05 | 5.0944 | N | 0
2025-08-28 | 16 | 2031-08-28 16:00 | 4.2 | 5.2831 | N | 0
2025-08-28 | 17 | 2031-08-28 17:00 | 4.14 | 5.2076 | N | 0
2025-08-28 | 18 | 2031-08-28 18:00 | 4.16 | 5.2328 | N | 0
2025-08-28 | 19 | 2031-08-28 19:00 | 4.17 | 5.2454 | N | 0
2025-08-28 | 20 | 2031-08-28 20:00 | 4.35 | 5.4718 | N | 0
2025-08-28 | 21 | 2031-08-28 21:00 | 4.52 | 5.6856 | N | 0
2025-08-28 | 22 | 2031-08-28 22:00 | 4.53 | 5.6982 | N | 0
2025-08-28 | 23 | 2031-08-28 23:00 | 4.27 | 5.3712 | N | 0
2025-08-29 | 00 | 2031-08-29 | 4.32 | 5.434 | N | 0
2025-08-29 | 01 | 2031-08-29 01:00 | 4.11 | 5.1699 | N | 0
2025-08-29 | 02 | 2031-08-29 02:00 | 3.7 | 4.6542 | N | 0
2025-08-29 | 03 | 2031-08-29 03:00 | 3.28 | 4.1259 | N | 0
2025-08-29 | 04 | 2031-08-29 04:00 | 2.9 | 3.6479 | N | 0
2025-08-29 | 05 | 2031-08-29 05:00 | 2.64 | 3.3208 | N | 0
2025-08-29 | 06 | 2031-08-29 06:00 | 2.46 | 3.0944 | N | 0
2025-08-29 | 07 | 2031-08-29 07:00 | 2.38 | 2.9938 | N | 0
2025-08-29 | 08 | 2031-08-29 08:00 | 2.31 | 2.9057 | N | 0
2025-08-29 | 09 | 2031-08-29 09:00 | 2.42 | 3.0441 | N | 0
2025-08-29 | 10 | 2031-08-29 10:00 | 2.78 | 3.4969 | N | 0
2025-08-29 | 11 | 2031-08-29 11:00 | 3.03 | 3.8114 | N | 0
2025-08-29 | 12 | 2031-08-29 12:00 | 3.29 | 4.1384 | N | 0
2025-08-29 | 13 | 2031-08-29 13:00 | 3.46 | 4.3523 | N | 0
2025-08-29 | 14 | 2031-08-29 14:00 | 3.5 | 4.4026 | N | 0
2025-08-29 | 15 | 2031-08-29 15:00 | 3.7 | 4.6542 | N | 0
2025-08-29 | 16 | 2031-08-29 16:00 | 3.69 | 4.6416 | N | 0
2025-08-29 | 17 | 2031-08-29 17:00 | 3.68 | 4.629 | N | 0
2025-08-29 | 18 | 2031-08-29 18:00 | 3.82 | 4.8051 | N | 0
2025-08-29 | 19 | 2031-08-29 19:00 | 3.91 | 4.9183 | N | 0
2025-08-29 | 20 | 2031-08-29 20:00 | 4.2 | 5.2831 | N | 0
2025-08-29 | 21 | 2031-08-29 21:00 | 4.34 | 5.4592 | N | 0
2025-08-29 | 22 | 2031-08-29 22:00 | 4.3 | 5.4089 | N | 0
2025-08-29 | 23 | 2031-08-29 23:00 | 4.08 | 5.1322 | N | 0
2025-08-30 | 00 | 2031-08-30 | 4.07 | 5.1196 | N | 0
2025-08-30 | 01 | 2031-08-30 01:00 | 3.81 | 4.7925 | N | 0
2025-08-30 | 02 | 2031-08-30 02:00 | 3.47 | 4.3648 | N | 0
2025-08-30 | 03 | 2031-08-30 03:00 | 3.07 | 3.8617 | N | 0
2025-08-30 | 04 | 2031-08-30 04:00 | 2.86 | 3.5975 | N | 0
2025-08-30 | 05 | 2031-08-30 05:00 | 2.57 | 3.2328 | N | 0
2025-08-30 | 06 | 2031-08-30 06:00 | 2.47 | 3.107 | N | 0
2025-08-30 | 07 | 2031-08-30 07:00 | 2.37 | 2.9812 | N | 0
2025-08-30 | 08 | 2031-08-30 08:00 | 2.33 | 2.9309 | N | 0
2025-08-30 | 09 | 2031-08-30 09:00 | 2.34 | 2.9434 | N | 0
2025-08-30 | 10 | 2031-08-30 10:00 | 2.38 | 2.9938 | N | 0
2025-08-30 | 11 | 2031-08-30 11:00 | 2.67 | 3.3585 | N | 0
2025-08-30 | 12 | 2031-08-30 12:00 | 2.94 | 3.6982 | N | 0
2025-08-30 | 13 | 2031-08-30 13:00 | 3.3 | 4.151 | N | 0
2025-08-30 | 14 | 2031-08-30 14:00 | 3.46 | 4.3523 | N | 0
2025-08-30 | 15 | 2031-08-30 15:00 | 3.64 | 4.5787 | N | 0
2025-08-30 | 16 | 2031-08-30 16:00 | 3.71 | 4.6667 | N | 0
2025-08-30 | 17 | 2031-08-30 17:00 | 3.78 | 4.7548 | N | 0
2025-08-30 | 18 | 2031-08-30 18:00 | 3.74 | 4.7045 | N | 0
2025-08-30 | 19 | 2031-08-30 19:00 | 3.86 | 4.8554 | N | 0
2025-08-30 | 20 | 2031-08-30 20:00 | 4.22 | 5.3083 | N | 0
2025-08-30 | 21 | 2031-08-30 21:00 | 4.23 | 5.3208 | N | 0
2025-08-30 | 22 | 2031-08-30 22:00 | 4.19 | 5.2705 | N | 0
2025-08-30 | 23 | 2031-08-30 23:00 | 3.97 | 4.9938 | N | 0
2025-08-31 | 00 | 2031-08-31 | 3.71 | 4.6667 | N | 0
2025-08-31 | 01 | 2031-08-31 01:00 | 3.6 | 4.5284 | N | 0
2025-08-31 | 02 | 2031-08-31 02:00 | 3.49 | 4.39 | N | 0
2025-08-31 | 03 | 2031-08-31 03:00 | 3.2 | 4.0252 | N | 0
2025-08-31 | 04 | 2031-08-31 04:00 | 2.88 | 3.6227 | N | 0
2025-08-31 | 05 | 2031-08-31 05:00 | 2.62 | 3.2956 | N | 0
2025-08-31 | 06 | 2031-08-31 06:00 | 2.47 | 3.107 | N | 0
2025-08-31 | 07 | 2031-08-31 07:00 | 2.35 | 2.956 | N | 0
2025-08-31 | 08 | 2031-08-31 08:00 | 2.28 | 2.868 | N | 0
2025-08-31 | 09 | 2031-08-31 09:00 | 2.33 | 2.9309 | N | 0
2025-08-31 | 10 | 2031-08-31 10:00 | 2.4 | 3.0189 | N | 0
2025-08-31 | 11 | 2031-08-31 11:00 | 2.62 | 3.2956 | N | 0
2025-08-31 | 12 | 2031-08-31 12:00 | 2.94 | 3.6982 | N | 0
2025-08-31 | 13 | 2031-08-31 13:00 | 3.26 | 4.1007 | N | 0
2025-08-31 | 14 | 2031-08-31 14:00 | 3.58 | 4.5032 | N | 0
2025-08-31 | 15 | 2031-08-31 15:00 | 3.8 | 4.7799 | N | 0
2025-08-31 | 16 | 2031-08-31 16:00 | 3.96 | 4.9812 | N | 0
2025-08-31 | 17 | 2031-08-31 17:00 | 4.13 | 5.1951 | N | 0
2025-08-31 | 18 | 2031-08-31 18:00 | 4.17 | 5.2454 | N | 0
2025-08-31 | 19 | 2031-08-31 19:00 | 4.29 | 5.3963 | N | 0
2025-08-31 | 20 | 2031-08-31 20:00 | 4.64 | 5.8366 | N | 0
2025-08-31 | 21 | 2031-08-31 21:00 | 4.63 | 5.824 | N | 0
2025-08-31 | 22 | 2031-08-31 22:00 | 4.53 | 5.6982 | N | 0
2025-08-31 | 23 | 2031-08-31 23:00 | 4.39 | 5.5221 | N | 0
2025-09-01 | 00 | 2031-09-01 | 4.23 | 5.3208 | N | 0
2025-09-01 | 01 | 2031-09-01 01:00 | 4.05 | 5.0944 | N | 0
2025-09-01 | 02 | 2031-09-01 02:00 | 3.76 | 4.7296 | N | 0
2025-09-01 | 03 | 2031-09-01 03:00 | 3.39 | 4.2642 | N | 0
2025-09-01 | 04 | 2031-09-01 04:00 | 3.02 | 3.7988 | N | 0
2025-09-01 | 05 | 2031-09-01 05:00 | 2.71 | 3.4089 | N | 0
2025-09-01 | 06 | 2031-09-01 06:00 | 2.48 | 3.1195 | N | 0
2025-09-01 | 07 | 2031-09-01 07:00 | 2.38 | 2.9938 | N | 0
2025-09-01 | 08 | 2031-09-01 08:00 | 2.32 | 2.9183 | N | 0
2025-09-01 | 09 | 2031-09-01 09:00 | 2.36 | 2.9686 | N | 0
2025-09-01 | 10 | 2031-09-01 10:00 | 2.52 | 3.1699 | N | 0
2025-09-01 | 11 | 2031-09-01 11:00 | 2.78 | 3.4969 | N | 0
2025-09-01 | 12 | 2031-09-01 12:00 | 3.24 | 4.0755 | N | 0
2025-09-01 | 13 | 2031-09-01 13:00 | 3.69 | 4.6416 | N | 0
2025-09-01 | 14 | 2031-09-01 14:00 | 3.99 | 5.0189 | N | 0
2025-09-01 | 15 | 2031-09-01 15:00 | 4.42 | 5.5598 | N | 0
2025-09-01 | 16 | 2031-09-01 16:00 | 4.64 | 5.8366 | N | 0
2025-09-01 | 17 | 2031-09-01 17:00 | 4.83 | 6.0756 | N | 0
2025-09-01 | 18 | 2031-09-01 18:00 | 5.07 | 6.3775 | N | 0
2025-09-01 | 19 | 2031-09-01 19:00 | 5.34 | 6.7171 | N | 0
2025-09-01 | 20 | 2031-09-01 20:00 | 5.88 | 7.3963 | N | 0
2025-09-01 | 21 | 2031-09-01 21:00 | 5.97 | 7.5096 | N | 0
2025-09-01 | 22 | 2031-09-01 22:00 | 5.85 | 7.3586 | N | 0
2025-09-01 | 23 | 2031-09-01 23:00 | 5.51 | 6.9309 | N | 0
2025-09-02 | 00 | 2031-09-02 | 5.15 | 6.4781 | N | 0
2025-09-02 | 01 | 2031-09-02 01:00 | 4.83 | 6.0756 | N | 0
2025-09-02 | 02 | 2031-09-02 02:00 | 4.08 | 5.1322 | N | 0
2025-09-02 | 03 | 2031-09-02 03:00 | 3.54 | 4.4529 | N | 0
2025-09-02 | 04 | 2031-09-02 04:00 | 3.02 | 3.7988 | N | 0
2025-09-02 | 05 | 2031-09-02 05:00 | 2.69 | 3.3837 | N | 0
2025-09-02 | 06 | 2031-09-02 06:00 | 2.47 | 3.107 | N | 0
2025-09-02 | 07 | 2031-09-02 07:00 | 2.35 | 2.956 | N | 0
2025-09-02 | 08 | 2031-09-02 08:00 | 2.32 | 2.9183 | N | 0
2025-09-02 | 09 | 2031-09-02 09:00 | 2.51 | 3.1573 | N | 0
2025-09-02 | 10 | 2031-09-02 10:00 | 2.87 | 3.6101 | N | 0
2025-09-02 | 11 | 2031-09-02 11:00 | 3.13 | 3.9372 | N | 0
2025-09-02 | 12 | 2031-09-02 12:00 | 3.25 | 4.0881 | N | 0
2025-09-02 | 13 | 2031-09-02 13:00 | 3.4 | 4.2768 | N | 0
2025-09-02 | 14 | 2031-09-02 14:00 | 7.69 | 9.6731 | N | 0
2025-09-02 | 15 | 2031-09-02 15:00 | 8.4 | 10.5662 | N | 0
2025-09-02 | 16 | 2031-09-02 16:00 | 8.98 | 11.2958 | Y | 0.65578 | 1
2025-09-02 | 17 | 2031-09-02 17:00 | 9.59 | 12.0631 | Y | 1.4231 | 2
2025-09-02 | 18 | 2031-09-02 18:00 | 9.88 | 12.4279 | Y | 1.7879 | 3
2025-09-02 | 19 | 2031-09-02 19:00 | 10.21 | 12.843 | Y | 2.203 | 4
2025-09-02 | 20 | 2031-09-02 20:00 | 10.95 | 13.7738 | Y | 3.1338 | 5
2025-09-02 | 21 | 2031-09-02 21:00 | 11.79 | 14.8304 | Y | 4.1904 | 6
2025-09-02 | 22 | 2031-09-02 22:00 | 9.35 | 11.7612 | Y | 1.1212 | 7 | 7
2025-09-02 | 23 | 2031-09-02 23:00 | 7.04 | 8.8555 | N | 0
2025-09-03 | 00 | 2031-09-03 | 6.82 | 8.5788 | N | 0
2025-09-03 | 01 | 2031-09-03 01:00 | 6.52 | 8.2014 | N | 0
2025-09-03 | 02 | 2031-09-03 02:00 | 5.71 | 7.1825 | N | 0
2025-09-03 | 03 | 2031-09-03 03:00 | 4.73 | 5.9498 | N | 0
2025-09-03 | 04 | 2031-09-03 04:00 | 4.19 | 5.2705 | N | 0
2025-09-03 | 05 | 2031-09-03 05:00 | 3.74 | 4.7045 | N | 0
2025-09-03 | 06 | 2031-09-03 06:00 | 3.41 | 4.2894 | N | 0
2025-09-03 | 07 | 2031-09-03 07:00 | 3.24 | 4.0755 | N | 0
2025-09-03 | 08 | 2031-09-03 08:00 | 3.1 | 3.8994 | N | 0
2025-09-03 | 09 | 2031-09-03 09:00 | 3.23 | 4.063 | N | 0
2025-09-03 | 10 | 2031-09-03 10:00 | 3.84 | 4.8303 | N | 0
2025-09-03 | 11 | 2031-09-03 11:00 | 4.28 | 5.3837 | N | 0
2025-09-03 | 12 | 2031-09-03 12:00 | 4.5 | 5.6605 | N | 0
2025-09-03 | 13 | 2031-09-03 13:00 | 5.07 | 6.3775 | N | 0
2025-09-03 | 14 | 2031-09-03 14:00 | 5.41 | 6.8051 | N | 0
2025-09-03 | 15 | 2031-09-03 15:00 | 5.69 | 7.1573 | N | 0
2025-09-03 | 16 | 2031-09-03 16:00 | 5.96 | 7.497 | N | 0
2025-09-03 | 17 | 2031-09-03 17:00 | 6.16 | 7.7485 | N | 0
2025-09-03 | 18 | 2031-09-03 18:00 | 6.35 | 7.9875 | N | 0
2025-09-03 | 19 | 2031-09-03 19:00 | 6.7 | 8.4278 | N | 0
2025-09-03 | 20 | 2031-09-03 20:00 | 7.38 | 9.2832 | N | 0
2025-09-03 | 21 | 2031-09-03 21:00 | 7.84 | 9.8618 | N | 0
2025-09-03 | 22 | 2031-09-03 22:00 | 7.7 | 9.6857 | N | 0
2025-09-03 | 23 | 2031-09-03 23:00 | 7.22 | 9.0819 | N | 0
2025-09-04 | 00 | 2031-09-04 | 7.18 | 9.0316 | N | 0
2025-09-04 | 01 | 2031-09-04 01:00 | 6.79 | 8.541 | N | 0
2025-09-04 | 02 | 2031-09-04 02:00 | 5.91 | 7.4341 | N | 0
2025-09-04 | 03 | 2031-09-04 03:00 | 5.16 | 6.4907 | N | 0
2025-09-04 | 04 | 2031-09-04 04:00 | 4.54 | 5.7108 | N | 0
2025-09-04 | 05 | 2031-09-04 05:00 | 4.06 | 5.107 | N | 0
2025-09-04 | 06 | 2031-09-04 06:00 | 3.64 | 4.5787 | N | 0
2025-09-04 | 07 | 2031-09-04 07:00 | 3.44 | 4.3271 | N | 0
2025-09-04 | 08 | 2031-09-04 08:00 | 3.3 | 4.151 | N | 0
2025-09-04 | 09 | 2031-09-04 09:00 | 3.46 | 4.3523 | N | 0
2025-09-04 | 10 | 2031-09-04 10:00 | 4.1 | 5.1573 | N | 0
2025-09-04 | 11 | 2031-09-04 11:00 | 4.65 | 5.8491 | N | 0
2025-09-04 | 12 | 2031-09-04 12:00 | 4.77 | 6.0001 | N | 0
2025-09-04 | 13 | 2031-09-04 13:00 | 4.81 | 6.0504 | N | 0
2025-09-04 | 14 | 2031-09-04 14:00 | 4.82 | 6.063 | N | 0
2025-09-04 | 15 | 2031-09-04 15:00 | 4.82 | 6.063 | N | 0
2025-09-04 | 16 | 2031-09-04 16:00 | 4.94 | 6.2139 | N | 0
2025-09-04 | 17 | 2031-09-04 17:00 | 4.82 | 6.063 | N | 0
2025-09-04 | 18 | 2031-09-04 18:00 | 4.9 | 6.1636 | N | 0
2025-09-04 | 19 | 2031-09-04 19:00 | 5.27 | 6.629 | N | 0
2025-09-04 | 20 | 2031-09-04 20:00 | 5.93 | 7.4592 | N | 0
2025-09-04 | 21 | 2031-09-04 21:00 | 6.15 | 7.736 | N | 0
2025-09-04 | 22 | 2031-09-04 22:00 | 6.15 | 7.736 | N | 0
2025-09-04 | 23 | 2031-09-04 23:00 | 5.77 | 7.258 | N | 0
2025-09-05 | 00 | 2031-09-05 | 5.77 | 7.258 | N | 0
2025-09-05 | 01 | 2031-09-05 01:00 | 5.37 | 6.7548 | N | 0
2025-09-05 | 02 | 2031-09-05 02:00 | 5.04 | 6.3397 | N | 0
2025-09-05 | 03 | 2031-09-05 03:00 | 4.31 | 5.4215 | N | 0
2025-09-05 | 04 | 2031-09-05 04:00 | 3.81 | 4.7925 | N | 0
2025-09-05 | 05 | 2031-09-05 05:00 | 3.46 | 4.3523 | N | 0
2025-09-05 | 06 | 2031-09-05 06:00 | 3.17 | 3.9875 | N | 0
2025-09-05 | 07 | 2031-09-05 07:00 | 3.12 | 3.9246 | N | 0
2025-09-05 | 08 | 2031-09-05 08:00 | 3.04 | 3.824 | N | 0
2025-09-05 | 09 | 2031-09-05 09:00 | 3.23 | 4.063 | N | 0
2025-09-05 | 10 | 2031-09-05 10:00 | 3.76 | 4.7296 | N | 0
2025-09-05 | 11 | 2031-09-05 11:00 | 4.24 | 5.3334 | N | 0
2025-09-05 | 12 | 2031-09-05 12:00 | 4.3 | 5.4089 | N | 0
2025-09-05 | 13 | 2031-09-05 13:00 | 4.41 | 5.5473 | N | 0
2025-09-05 | 14 | 2031-09-05 14:00 | 4.66 | 5.8617 | N | 0
2025-09-05 | 15 | 2031-09-05 15:00 | 5.2 | 6.541 | N | 0
2025-09-05 | 16 | 2031-09-05 16:00 | 5.2 | 6.541 | N | 0
2025-09-05 | 17 | 2031-09-05 17:00 | 5.24 | 6.5913 | N | 0
2025-09-05 | 18 | 2031-09-05 18:00 | 5.16 | 6.4907 | N | 0
2025-09-05 | 19 | 2031-09-05 19:00 | 5.46 | 6.868 | N | 0
2025-09-05 | 20 | 2031-09-05 20:00 | 5.87 | 7.3838 | N | 0
2025-09-05 | 21 | 2031-09-05 21:00 | 5.96 | 7.497 | N | 0
2025-09-05 | 22 | 2031-09-05 22:00 | 5.96 | 7.497 | N | 0
2025-09-05 | 23 | 2031-09-05 23:00 | 5.7 | 7.1699 | N | 0
2025-09-06 | 00 | 2031-09-06 | 5.73 | 7.2077 | N | 0
2025-09-06 | 01 | 2031-09-06 01:00 | 5.52 | 6.9435 | N | 0
2025-09-06 | 02 | 2031-09-06 02:00 | 4.98 | 6.2642 | N | 0
2025-09-06 | 03 | 2031-09-06 03:00 | 4.35 | 5.4718 | N | 0
2025-09-06 | 04 | 2031-09-06 04:00 | 3.82 | 4.8051 | N | 0
2025-09-06 | 05 | 2031-09-06 05:00 | 3.46 | 4.3523 | N | 0
2025-09-06 | 06 | 2031-09-06 06:00 | 3.22 | 4.0504 | N | 0
2025-09-06 | 07 | 2031-09-06 07:00 | 3.12 | 3.9246 | N | 0
2025-09-06 | 08 | 2031-09-06 08:00 | 3.02 | 3.7988 | N | 0
2025-09-06 | 09 | 2031-09-06 09:00 | 3.03 | 3.8114 | N | 0
2025-09-06 | 10 | 2031-09-06 10:00 | 3.14 | 3.9497 | N | 0
2025-09-06 | 11 | 2031-09-06 11:00 | 3.62 | 4.5535 | N | 0
2025-09-06 | 12 | 2031-09-06 12:00 | 4.04 | 5.0818 | N | 0
2025-09-06 | 13 | 2031-09-06 13:00 | 4.36 | 5.4844 | N | 0
2025-09-06 | 14 | 2031-09-06 14:00 | 4.51 | 5.673 | N | 0
2025-09-06 | 15 | 2031-09-06 15:00 | 4.8 | 6.0378 | N | 0
2025-09-06 | 16 | 2031-09-06 16:00 | 4.83 | 6.0756 | N | 0
2025-09-06 | 17 | 2031-09-06 17:00 | 5.03 | 6.3271 | N | 0
2025-09-06 | 18 | 2031-09-06 18:00 | 5.15 | 6.4781 | N | 0
2025-09-06 | 19 | 2031-09-06 19:00 | 5.15 | 6.4781 | N | 0
2025-09-06 | 20 | 2031-09-06 20:00 | 5.29 | 6.6542 | N | 0
2025-09-06 | 21 | 2031-09-06 21:00 | 5.43 | 6.8303 | N | 0
2025-09-06 | 22 | 2031-09-06 22:00 | 5.29 | 6.6542 | N | 0
2025-09-06 | 23 | 2031-09-06 23:00 | 5.1 | 6.4152 | N | 0
2025-09-07 | 00 | 2031-09-07 | 5.1 | 6.4152 | N | 0
2025-09-07 | 01 | 2031-09-07 01:00 | 4.91 | 6.1762 | N | 0
2025-09-07 | 02 | 2031-09-07 02:00 | 4.65 | 5.8491 | N | 0
2025-09-07 | 03 | 2031-09-07 03:00 | 4.24 | 5.3334 | N | 0
2025-09-07 | 04 | 2031-09-07 04:00 | 3.82 | 4.8051 | N | 0
2025-09-07 | 05 | 2031-09-07 05:00 | 3.52 | 4.4277 | N | 0
2025-09-07 | 06 | 2031-09-07 06:00 | 3.31 | 4.1636 | N | 0
2025-09-07 | 07 | 2031-09-07 07:00 | 3.13 | 3.9372 | N | 0
2025-09-07 | 08 | 2031-09-07 08:00 | 3.03 | 3.8114 | N | 0
2025-09-07 | 09 | 2031-09-07 09:00 | 3.02 | 3.7988 | N | 0
2025-09-07 | 10 | 2031-09-07 10:00 | 3.09 | 3.8869 | N | 0
2025-09-07 | 11 | 2031-09-07 11:00 | 3.53 | 4.4403 | N | 0
2025-09-07 | 12 | 2031-09-07 12:00 | 4.06 | 5.107 | N | 0
2025-09-07 | 13 | 2031-09-07 13:00 | 4.3 | 5.4089 | N | 0
2025-09-07 | 14 | 2031-09-07 14:00 | 4.72 | 5.9372 | N | 0
2025-09-07 | 15 | 2031-09-07 15:00 | 4.89 | 6.151 | N | 0
2025-09-07 | 16 | 2031-09-07 16:00 | 5.18 | 6.5158 | N | 0
2025-09-07 | 17 | 2031-09-07 17:00 | 5.16 | 6.4907 | N | 0
2025-09-07 | 18 | 2031-09-07 18:00 | 5.26 | 6.6165 | N | 0
2025-09-07 | 19 | 2031-09-07 19:00 | 5.41 | 6.8051 | N | 0
2025-09-07 | 20 | 2031-09-07 20:00 | 5.72 | 7.1951 | N | 0
2025-09-07 | 21 | 2031-09-07 21:00 | 5.96 | 7.497 | N | 0
2025-09-07 | 22 | 2031-09-07 22:00 | 5.9 | 7.4215 | N | 0
2025-09-07 | 23 | 2031-09-07 23:00 | 5.64 | 7.0945 | N | 0
2025-09-08 | 00 | 2031-09-08 | 5.5 | 6.9183 | N | 0
2025-09-08 | 01 | 2031-09-08 01:00 | 5.4 | 6.7926 | N | 0
2025-09-08 | 02 | 2031-09-08 02:00 | 4.73 | 5.9498 | N | 0
2025-09-08 | 03 | 2031-09-08 03:00 | 4.19 | 5.2705 | N | 0
2025-09-08 | 04 | 2031-09-08 04:00 | 3.66 | 4.6038 | N | 0
2025-09-08 | 05 | 2031-09-08 05:00 | 3.38 | 4.2516 | N | 0
2025-09-08 | 06 | 2031-09-08 06:00 | 3.13 | 3.9372 | N | 0
2025-09-08 | 07 | 2031-09-08 07:00 | 3.06 | 3.8491 | N | 0
2025-09-08 | 08 | 2031-09-08 08:00 | 3.01 | 3.7862 | N | 0
2025-09-08 | 09 | 2031-09-08 09:00 | 3.17 | 3.9875 | N | 0
2025-09-08 | 10 | 2031-09-08 10:00 | 3.72 | 4.6793 | N | 0
2025-09-08 | 11 | 2031-09-08 11:00 | 4.26 | 5.3586 | N | 0
2025-09-08 | 12 | 2031-09-08 12:00 | 4.27 | 5.3712 | N | 0
2025-09-08 | 13 | 2031-09-08 13:00 | 4.32 | 5.434 | N | 0
2025-09-08 | 14 | 2031-09-08 14:00 | 4.51 | 5.673 | N | 0
2025-09-08 | 15 | 2031-09-08 15:00 | 4.6 | 5.7863 | N | 0
2025-09-08 | 16 | 2031-09-08 16:00 | 4.6 | 5.7863 | N | 0
2025-09-08 | 17 | 2031-09-08 17:00 | 4.57 | 5.7485 | N | 0
2025-09-08 | 18 | 2031-09-08 18:00 | 4.61 | 5.7988 | N | 0
2025-09-08 | 19 | 2031-09-08 19:00 | 4.83 | 6.0756 | N | 0
2025-09-08 | 20 | 2031-09-08 20:00 | 5.39 | 6.78 | N | 0
2025-09-08 | 21 | 2031-09-08 21:00 | 5.62 | 7.0693 | N | 0
2025-09-08 | 22 | 2031-09-08 22:00 | 5.56 | 6.9938 | N | 0
2025-09-08 | 23 | 2031-09-08 23:00 | 5.39 | 6.78 | N | 0
2025-09-09 | 00 | 2031-09-09 | 5.49 | 6.9058 | N | 0
2025-09-09 | 01 | 2031-09-09 01:00 | 5.32 | 6.6919 | N | 0
2025-09-09 | 02 | 2031-09-09 02:00 | 4.78 | 6.0127 | N | 0
2025-09-09 | 03 | 2031-09-09 03:00 | 4.21 | 5.2957 | N | 0
2025-09-09 | 04 | 2031-09-09 04:00 | 3.65 | 4.5913 | N | 0
2025-09-09 | 05 | 2031-09-09 05:00 | 3.27 | 4.1133 | N | 0
2025-09-09 | 06 | 2031-09-09 06:00 | 3.17 | 3.9875 | N | 0
2025-09-09 | 07 | 2031-09-09 07:00 | 3 | 3.7736 | N | 0
2025-09-09 | 08 | 2031-09-09 08:00 | 3.01 | 3.7862 | N | 0
2025-09-09 | 09 | 2031-09-09 09:00 | 3.19 | 4.0126 | N | 0
2025-09-09 | 10 | 2031-09-09 10:00 | 3.75 | 4.7171 | N | 0
2025-09-09 | 11 | 2031-09-09 11:00 | 4.13 | 5.1951 | N | 0
2025-09-09 | 12 | 2031-09-09 12:00 | 4.18 | 5.2579 | N | 0
2025-09-09 | 13 | 2031-09-09 13:00 | 4.22 | 5.3083 | N | 0
2025-09-09 | 14 | 2031-09-09 14:00 | 4.44 | 5.585 | N | 0
2025-09-09 | 15 | 2031-09-09 15:00 | 4.48 | 5.6353 | N | 0
2025-09-09 | 16 | 2031-09-09 16:00 | 4.62 | 5.8114 | N | 0
2025-09-09 | 17 | 2031-09-09 17:00 | 4.76 | 5.9875 | N | 0
2025-09-09 | 18 | 2031-09-09 18:00 | 4.92 | 6.1888 | N | 0
2025-09-09 | 19 | 2031-09-09 19:00 | 5.21 | 6.5536 | N | 0
2025-09-09 | 20 | 2031-09-09 20:00 | 5.73 | 7.2077 | N | 0
2025-09-09 | 21 | 2031-09-09 21:00 | 5.93 | 7.4592 | N | 0
2025-09-09 | 22 | 2031-09-09 22:00 | 5.85 | 7.3586 | N | 0
2025-09-09 | 23 | 2031-09-09 23:00 | 5.78 | 7.2706 | N | 0
2025-09-10 | 00 | 2031-09-10 | 5.78 | 7.2706 | N | 0
2025-09-10 | 01 | 2031-09-10 01:00 | 5.53 | 6.9561 | N | 0
2025-09-10 | 02 | 2031-09-10 02:00 | 4.8 | 6.0378 | N | 0
2025-09-10 | 03 | 2031-09-10 03:00 | 4.12 | 5.1825 | N | 0
2025-09-10 | 04 | 2031-09-10 04:00 | 3.67 | 4.6164 | N | 0
2025-09-10 | 05 | 2031-09-10 05:00 | 3.34 | 4.2013 | N | 0
2025-09-10 | 06 | 2031-09-10 06:00 | 3.13 | 3.9372 | N | 0
2025-09-10 | 07 | 2031-09-10 07:00 | 3.02 | 3.7988 | N | 0
2025-09-10 | 08 | 2031-09-10 08:00 | 3.02 | 3.7988 | N | 0
2025-09-10 | 09 | 2031-09-10 09:00 | 3.25 | 4.0881 | N | 0
2025-09-10 | 10 | 2031-09-10 10:00 | 3.75 | 4.7171 | N | 0
2025-09-10 | 11 | 2031-09-10 11:00 | 4.13 | 5.1951 | N | 0
2025-09-10 | 12 | 2031-09-10 12:00 | 4.18 | 5.2579 | N | 0
2025-09-10 | 13 | 2031-09-10 13:00 | 4.44 | 5.585 | N | 0
2025-09-10 | 14 | 2031-09-10 14:00 | 4.63 | 5.824 | N | 0
2025-09-10 | 15 | 2031-09-10 15:00 | 4.97 | 6.2517 | N | 0
2025-09-10 | 16 | 2031-09-10 16:00 | 5.08 | 6.39 | N | 0
2025-09-10 | 17 | 2031-09-10 17:00 | 5.17 | 6.5032 | N | 0
2025-09-10 | 18 | 2031-09-10 18:00 | 5.37 | 6.7548 | N | 0
2025-09-10 | 19 | 2031-09-10 19:00 | 5.81 | 7.3083 | N | 0
2025-09-10 | 20 | 2031-09-10 20:00 | 6.31 | 7.9372 | N | 0
2025-09-10 | 21 | 2031-09-10 21:00 | 6.52 | 8.2014 | N | 0
2025-09-10 | 22 | 2031-09-10 22:00 | 6.41 | 8.063 | N | 0
2025-09-10 | 23 | 2031-09-10 23:00 | 6.21 | 7.8114 | N | 0
2025-09-11 | 00 | 2031-09-11 | 6.21 | 7.8114 | N | 0
2025-09-11 | 01 | 2031-09-11 01:00 | 5.88 | 7.3963 | N | 0
2025-09-11 | 02 | 2031-09-11 02:00 | 5.19 | 6.5284 | N | 0
2025-09-11 | 03 | 2031-09-11 03:00 | 4.42 | 5.5598 | N | 0
2025-09-11 | 04 | 2031-09-11 04:00 | 3.86 | 4.8554 | N | 0
2025-09-11 | 05 | 2031-09-11 05:00 | 3.48 | 4.3774 | N | 0
2025-09-11 | 06 | 2031-09-11 06:00 | 3.22 | 4.0504 | N | 0
2025-09-11 | 07 | 2031-09-11 07:00 | 3.06 | 3.8491 | N | 0
2025-09-11 | 08 | 2031-09-11 08:00 | 3.02 | 3.7988 | N | 0
2025-09-11 | 09 | 2031-09-11 09:00 | 3.21 | 4.0378 | N | 0
2025-09-11 | 10 | 2031-09-11 10:00 | 3.71 | 4.6667 | N | 0
2025-09-11 | 11 | 2031-09-11 11:00 | 4.2 | 5.2831 | N | 0
2025-09-11 | 12 | 2031-09-11 12:00 | 4.32 | 5.434 | N | 0
2025-09-11 | 13 | 2031-09-11 13:00 | 4.87 | 6.1259 | N | 0
2025-09-11 | 14 | 2031-09-11 14:00 | 5.05 | 6.3523 | N | 0
2025-09-11 | 15 | 2031-09-11 15:00 | 5.39 | 6.78 | N | 0
2025-09-11 | 16 | 2031-09-11 16:00 | 5.58 | 7.019 | N | 0
2025-09-11 | 17 | 2031-09-11 17:00 | 5.72 | 7.1951 | N | 0
2025-09-11 | 18 | 2031-09-11 18:00 | 5.92 | 7.4467 | N | 0
2025-09-11 | 19 | 2031-09-11 19:00 | 6.1 | 7.6731 | N | 0
2025-09-11 | 20 | 2031-09-11 20:00 | 6.61 | 8.3146 | N | 0
2025-09-11 | 21 | 2031-09-11 21:00 | 6.74 | 8.4781 | N | 0
2025-09-11 | 22 | 2031-09-11 22:00 | 6.73 | 8.4655 | N | 0
2025-09-11 | 23 | 2031-09-11 23:00 | 6.46 | 8.1259 | N | 0
2025-09-12 | 00 | 2031-09-12 | 6.46 | 8.1259 | N | 0
2025-09-12 | 01 | 2031-09-12 01:00 | 6.28 | 7.8995 | N | 0
2025-09-12 | 02 | 2031-09-12 02:00 | 5.39 | 6.78 | N | 0
2025-09-12 | 03 | 2031-09-12 03:00 | 4.76 | 5.9875 | N | 0
2025-09-12 | 04 | 2031-09-12 04:00 | 4.16 | 5.2328 | N | 0
2025-09-12 | 05 | 2031-09-12 05:00 | 3.62 | 4.5535 | N | 0
2025-09-12 | 06 | 2031-09-12 06:00 | 3.4 | 4.2768 | N | 0
2025-09-12 | 07 | 2031-09-12 07:00 | 3.19 | 4.0126 | N | 0
2025-09-12 | 08 | 2031-09-12 08:00 | 3.09 | 3.8869 | N | 0
2025-09-12 | 09 | 2031-09-12 09:00 | 3.24 | 4.0755 | N | 0
2025-09-12 | 10 | 2031-09-12 10:00 | 3.78 | 4.7548 | N | 0
2025-09-12 | 11 | 2031-09-12 11:00 | 4.28 | 5.3837 | N | 0
2025-09-12 | 12 | 2031-09-12 12:00 | 4.54 | 5.7108 | N | 0
2025-09-12 | 13 | 2031-09-12 13:00 | 4.7 | 5.912 | N | 0
2025-09-12 | 14 | 2031-09-12 14:00 | 5.29 | 6.6542 | N | 0
2025-09-12 | 15 | 2031-09-12 15:00 | 5.46 | 6.868 | N | 0
2025-09-12 | 16 | 2031-09-12 16:00 | 5.72 | 7.1951 | N | 0
2025-09-12 | 17 | 2031-09-12 17:00 | 5.73 | 7.2077 | N | 0
2025-09-12 | 18 | 2031-09-12 18:00 | 5.77 | 7.258 | N | 0
2025-09-12 | 19 | 2031-09-12 19:00 | 6.1 | 7.6731 | N | 0
2025-09-12 | 20 | 2031-09-12 20:00 | 6.5 | 8.1762 | N | 0
2025-09-12 | 21 | 2031-09-12 21:00 | 6.72 | 8.453 | N | 0
2025-09-12 | 22 | 2031-09-12 22:00 | 6.38 | 8.0253 | N | 0
2025-09-12 | 23 | 2031-09-12 23:00 | 6.21 | 7.8114 | N | 0
2025-09-13 | 00 | 2031-09-13 | 6.16 | 7.7485 | N | 0
2025-09-13 | 01 | 2031-09-13 01:00 | 5.81 | 7.3083 | N | 0
2025-09-13 | 02 | 2031-09-13 02:00 | 5.21 | 6.5536 | N | 0
2025-09-13 | 03 | 2031-09-13 03:00 | 4.64 | 5.8366 | N | 0
2025-09-13 | 04 | 2031-09-13 04:00 | 4.12 | 5.1825 | N | 0
2025-09-13 | 05 | 2031-09-13 05:00 | 3.66 | 4.6038 | N | 0
2025-09-13 | 06 | 2031-09-13 06:00 | 3.32 | 4.1762 | N | 0
2025-09-13 | 07 | 2031-09-13 07:00 | 3.22 | 4.0504 | N | 0
2025-09-13 | 08 | 2031-09-13 08:00 | 3.11 | 3.912 | N | 0
2025-09-13 | 09 | 2031-09-13 09:00 | 3.05 | 3.8365 | N | 0
2025-09-13 | 10 | 2031-09-13 10:00 | 3.25 | 4.0881 | N | 0
2025-09-13 | 11 | 2031-09-13 11:00 | 3.66 | 4.6038 | N | 0
2025-09-13 | 12 | 2031-09-13 12:00 | 4.21 | 5.2957 | N | 0
2025-09-13 | 13 | 2031-09-13 13:00 | 4.6 | 5.7863 | N | 0
2025-09-13 | 14 | 2031-09-13 14:00 | 4.82 | 6.063 | N | 0
2025-09-13 | 15 | 2031-09-13 15:00 | 5.08 | 6.39 | N | 0
2025-09-13 | 16 | 2031-09-13 16:00 | 5.15 | 6.4781 | N | 0
2025-09-13 | 17 | 2031-09-13 17:00 | 5.16 | 6.4907 | N | 0
2025-09-13 | 18 | 2031-09-13 18:00 | 5.11 | 6.4278 | N | 0
2025-09-13 | 19 | 2031-09-13 19:00 | 5.39 | 6.78 | N | 0
2025-09-13 | 20 | 2031-09-13 20:00 | 5.51 | 6.9309 | N | 0
2025-09-13 | 21 | 2031-09-13 21:00 | 5.83 | 7.3334 | N | 0
2025-09-13 | 22 | 2031-09-13 22:00 | 5.88 | 7.3963 | N | 0
2025-09-13 | 23 | 2031-09-13 23:00 | 5.51 | 6.9309 | N | 0
2025-09-14 | 00 | 2031-09-14 | 5.51 | 6.9309 | N | 0
2025-09-14 | 01 | 2031-09-14 01:00 | 5.45 | 6.8555 | N | 0
2025-09-14 | 02 | 2031-09-14 02:00 | 5.1 | 6.4152 | N | 0
2025-09-14 | 03 | 2031-09-14 03:00 | 4.6 | 5.7863 | N | 0
2025-09-14 | 04 | 2031-09-14 04:00 | 4.04 | 5.0818 | N | 0
2025-09-14 | 05 | 2031-09-14 05:00 | 3.69 | 4.6416 | N | 0
2025-09-14 | 06 | 2031-09-14 06:00 | 3.37 | 4.2391 | N | 0
2025-09-14 | 07 | 2031-09-14 07:00 | 3.14 | 3.9497 | N | 0
2025-09-14 | 08 | 2031-09-14 08:00 | 3.14 | 3.9497 | N | 0
2025-09-14 | 09 | 2031-09-14 09:00 | 3.05 | 3.8365 | N | 0
2025-09-14 | 10 | 2031-09-14 10:00 | 3.17 | 3.9875 | N | 0
2025-09-14 | 11 | 2031-09-14 11:00 | 3.53 | 4.4403 | N | 0
2025-09-14 | 12 | 2031-09-14 12:00 | 4.03 | 5.0693 | N | 0
2025-09-14 | 13 | 2031-09-14 13:00 | 4.79 | 6.0253 | N | 0
2025-09-14 | 14 | 2031-09-14 14:00 | 5.41 | 6.8051 | N | 0
2025-09-14 | 15 | 2031-09-14 15:00 | 6.05 | 7.6102 | N | 0
2025-09-14 | 16 | 2031-09-14 16:00 | 6.52 | 8.2014 | N | 0
2025-09-14 | 17 | 2031-09-14 17:00 | 6.92 | 8.7045 | N | 0
2025-09-14 | 18 | 2031-09-14 18:00 | 6.97 | 8.7674 | N | 0
2025-09-14 | 19 | 2031-09-14 19:00 | 7.05 | 8.8681 | N | 0
2025-09-14 | 20 | 2031-09-14 20:00 | 7.27 | 9.1448 | N | 0
2025-09-14 | 21 | 2031-09-14 21:00 | 7.58 | 9.5347 | N | 0
2025-09-14 | 22 | 2031-09-14 22:00 | 7.56 | 9.5096 | N | 0
2025-09-14 | 23 | 2031-09-14 23:00 | 7.18 | 9.0316 | N | 0
2025-09-15 | 00 | 2031-09-15 | 7.09 | 8.9184 | N | 0
2025-09-15 | 01 | 2031-09-15 01:00 | 6.54 | 8.2265 | N | 0
2025-09-15 | 02 | 2031-09-15 02:00 | 5.77 | 7.258 | N | 0
2025-09-15 | 03 | 2031-09-15 03:00 | 4.86 | 6.1133 | N | 0
2025-09-15 | 04 | 2031-09-15 04:00 | 4.26 | 5.3586 | N | 0
2025-09-15 | 05 | 2031-09-15 05:00 | 3.65 | 4.5913 | N | 0
2025-09-15 | 06 | 2031-09-15 06:00 | 3.41 | 4.2894 | N | 0
2025-09-15 | 07 | 2031-09-15 07:00 | 3.24 | 4.0755 | N | 0
2025-09-15 | 08 | 2031-09-15 08:00 | 3.14 | 3.9497 | N | 0
2025-09-15 | 09 | 2031-09-15 09:00 | 3.24 | 4.0755 | N | 0
2025-09-15 | 10 | 2031-09-15 10:00 | 3.78 | 4.7548 | N | 0
2025-09-15 | 11 | 2031-09-15 11:00 | 4.31 | 5.4215 | N | 0
2025-09-15 | 12 | 2031-09-15 12:00 | 4.43 | 5.5724 | N | 0
2025-09-15 | 13 | 2031-09-15 13:00 | 4.7 | 5.912 | N | 0
2025-09-15 | 14 | 2031-09-15 14:00 | 5.39 | 6.78 | N | 0
2025-09-15 | 15 | 2031-09-15 15:00 | 5.62 | 7.0693 | N | 0
2025-09-15 | 16 | 2031-09-15 16:00 | 5.88 | 7.3963 | N | 0
2025-09-15 | 17 | 2031-09-15 17:00 | 6.07 | 7.6353 | N | 0
2025-09-15 | 18 | 2031-09-15 18:00 | 6.27 | 7.8869 | N | 0
2025-09-15 | 19 | 2031-09-15 19:00 | 6.52 | 8.2014 | N | 0
2025-09-15 | 20 | 2031-09-15 20:00 | 7.21 | 9.0693 | N | 0
2025-09-15 | 21 | 2031-09-15 21:00 | 7.34 | 9.2328 | N | 0
2025-09-15 | 22 | 2031-09-15 22:00 | 7.14 | 8.9813 | N | 0
2025-09-15 | 23 | 2031-09-15 23:00 | 6.84 | 8.6039 | N | 0
2025-09-16 | 00 | 2031-09-16 | 6.63 | 8.3398 | N | 0
2025-09-16 | 01 | 2031-09-16 01:00 | 6.21 | 7.8114 | N | 0
2025-09-16 | 02 | 2031-09-16 02:00 | 5.39 | 6.78 | N | 0
2025-09-16 | 03 | 2031-09-16 03:00 | 4.53 | 5.6982 | N | 0
2025-09-16 | 04 | 2031-09-16 04:00 | 3.95 | 4.9686 | N | 0
2025-09-16 | 05 | 2031-09-16 05:00 | 3.58 | 4.5032 | N | 0
2025-09-16 | 06 | 2031-09-16 06:00 | 3.22 | 4.0504 | N | 0
2025-09-16 | 07 | 2031-09-16 07:00 | 3.12 | 3.9246 | N | 0
2025-09-16 | 08 | 2031-09-16 08:00 | 3.1 | 3.8994 | N | 0
2025-09-16 | 09 | 2031-09-16 09:00 | 3.22 | 4.0504 | N | 0
2025-09-16 | 10 | 2031-09-16 10:00 | 3.75 | 4.7171 | N | 0
2025-09-16 | 11 | 2031-09-16 11:00 | 4.28 | 5.3837 | N | 0
2025-09-16 | 12 | 2031-09-16 12:00 | 4.45 | 5.5976 | N | 0
2025-09-16 | 13 | 2031-09-16 13:00 | 4.95 | 6.2265 | N | 0
2025-09-16 | 14 | 2031-09-16 14:00 | 5.33 | 6.7045 | N | 0
2025-09-16 | 15 | 2031-09-16 15:00 | 5.72 | 7.1951 | N | 0
2025-09-16 | 16 | 2031-09-16 16:00 | 5.92 | 7.4467 | N | 0
2025-09-16 | 17 | 2031-09-16 17:00 | 6.09 | 7.6605 | N | 0
2025-09-16 | 18 | 2031-09-16 18:00 | 6.29 | 7.9121 | N | 0
2025-09-16 | 19 | 2031-09-16 19:00 | 6.52 | 8.2014 | N | 0
2025-09-16 | 20 | 2031-09-16 20:00 | 6.99 | 8.7926 | N | 0
2025-09-16 | 21 | 2031-09-16 21:00 | 7.4 | 9.3083 | N | 0
2025-09-16 | 22 | 2031-09-16 22:00 | 7.27 | 9.1448 | N | 0
2025-09-16 | 23 | 2031-09-16 23:00 | 6.84 | 8.6039 | N | 0
2025-09-17 | 00 | 2031-09-17 | 6.7 | 8.4278 | N | 0
2025-09-17 | 01 | 2031-09-17 01:00 | 6.21 | 7.8114 | N | 0
2025-09-17 | 02 | 2031-09-17 02:00 | 5.49 | 6.9058 | N | 0
2025-09-17 | 03 | 2031-09-17 03:00 | 4.58 | 5.7611 | N | 0
2025-09-17 | 04 | 2031-09-17 04:00 | 3.93 | 4.9435 | N | 0
2025-09-17 | 05 | 2031-09-17 05:00 | 3.53 | 4.4403 | N | 0
2025-09-17 | 06 | 2031-09-17 06:00 | 3.22 | 4.0504 | N | 0
2025-09-17 | 07 | 2031-09-17 07:00 | 3.06 | 3.8491 | N | 0
2025-09-17 | 08 | 2031-09-17 08:00 | 3.05 | 3.8365 | N | 0
2025-09-17 | 09 | 2031-09-17 09:00 | 3.28 | 4.1259 | N | 0
2025-09-17 | 10 | 2031-09-17 10:00 | 3.72 | 4.6793 | N | 0
2025-09-17 | 11 | 2031-09-17 11:00 | 4.28 | 5.3837 | N | 0
2025-09-17 | 12 | 2031-09-17 12:00 | 4.38 | 5.5095 | N | 0
2025-09-17 | 13 | 2031-09-17 13:00 | 4.57 | 5.7485 | N | 0
2025-09-17 | 14 | 2031-09-17 14:00 | 5.15 | 6.4781 | N | 0
2025-09-17 | 15 | 2031-09-17 15:00 | 5.51 | 6.9309 | N | 0
2025-09-17 | 16 | 2031-09-17 16:00 | 5.86 | 7.3712 | N | 0
2025-09-17 | 17 | 2031-09-17 17:00 | 6.2 | 7.7989 | N | 0
2025-09-17 | 18 | 2031-09-17 18:00 | 6.39 | 8.0379 | N | 0
2025-09-17 | 19 | 2031-09-17 19:00 | 6.69 | 8.4152 | N | 0
2025-09-17 | 20 | 2031-09-17 20:00 | 6.89 | 8.6668 | N | 0
2025-09-17 | 21 | 2031-09-17 21:00 | 7.24 | 9.1071 | N | 0
2025-09-17 | 22 | 2031-09-17 22:00 | 6.96 | 8.7549 | N | 0
2025-09-17 | 23 | 2031-09-17 23:00 | 6.76 | 8.5033 | N | 0
2025-09-18 | 00 | 2031-09-18 | 6.63 | 8.3398 | N | 0
2025-09-18 | 01 | 2031-09-18 01:00 | 6.31 | 7.9372 | N | 0
2025-09-18 | 02 | 2031-09-18 02:00 | 5.54 | 6.9687 | N | 0
2025-09-18 | 03 | 2031-09-18 03:00 | 4.7 | 5.912 | N | 0
2025-09-18 | 04 | 2031-09-18 04:00 | 3.96 | 4.9812 | N | 0
2025-09-18 | 05 | 2031-09-18 05:00 | 3.52 | 4.4277 | N | 0
2025-09-18 | 06 | 2031-09-18 06:00 | 3.3 | 4.151 | N | 0
2025-09-18 | 07 | 2031-09-18 07:00 | 3.09 | 3.8869 | N | 0
2025-09-18 | 08 | 2031-09-18 08:00 | 3.09 | 3.8869 | N | 0
2025-09-18 | 09 | 2031-09-18 09:00 | 3.21 | 4.0378 | N | 0
2025-09-18 | 10 | 2031-09-18 10:00 | 3.78 | 4.7548 | N | 0
2025-09-18 | 11 | 2031-09-18 11:00 | 4.27 | 5.3712 | N | 0
2025-09-18 | 12 | 2031-09-18 12:00 | 4.38 | 5.5095 | N | 0
2025-09-18 | 13 | 2031-09-18 13:00 | 4.91 | 6.1762 | N | 0
2025-09-18 | 14 | 2031-09-18 14:00 | 5.25 | 6.6039 | N | 0
2025-09-18 | 15 | 2031-09-18 15:00 | 5.5 | 6.9183 | N | 0
2025-09-18 | 16 | 2031-09-18 16:00 | 5.87 | 7.3838 | N | 0
2025-09-18 | 17 | 2031-09-18 17:00 | 6.31 | 7.9372 | N | 0
2025-09-18 | 18 | 2031-09-18 18:00 | 6.5 | 8.1762 | N | 0
2025-09-18 | 19 | 2031-09-18 19:00 | 7.13 | 8.9687 | N | 0
2025-09-18 | 20 | 2031-09-18 20:00 | 7.47 | 9.3964 | N | 0
2025-09-18 | 21 | 2031-09-18 21:00 | 7.67 | 9.648 | N | 0
2025-09-18 | 22 | 2031-09-18 22:00 | 7.62 | 9.5851 | N | 0
2025-09-18 | 23 | 2031-09-18 23:00 | 7.31 | 9.1951 | N | 0
2025-09-19 | 00 | 2031-09-19 | 7.31 | 9.1951 | N | 0
2025-09-19 | 01 | 2031-09-19 01:00 | 7 | 8.8052 | N | 0
2025-09-19 | 02 | 2031-09-19 02:00 | 6.06 | 7.6228 | N | 0
2025-09-19 | 03 | 2031-09-19 03:00 | 5.18 | 6.5158 | N | 0
2025-09-19 | 04 | 2031-09-19 04:00 | 4.48 | 5.6353 | N | 0
2025-09-19 | 05 | 2031-09-19 05:00 | 3.92 | 4.9309 | N | 0
2025-09-19 | 06 | 2031-09-19 06:00 | 3.52 | 4.4277 | N | 0
2025-09-19 | 07 | 2031-09-19 07:00 | 3.35 | 4.2139 | N | 0
2025-09-19 | 08 | 2031-09-19 08:00 | 3.24 | 4.0755 | N | 0
2025-09-19 | 09 | 2031-09-19 09:00 | 3.33 | 4.1887 | N | 0
2025-09-19 | 10 | 2031-09-19 10:00 | 3.81 | 4.7925 | N | 0
2025-09-19 | 11 | 2031-09-19 11:00 | 4.33 | 5.4466 | N | 0
2025-09-19 | 12 | 2031-09-19 12:00 | 4.51 | 5.673 | N | 0
2025-09-19 | 13 | 2031-09-19 13:00 | 4.78 | 6.0127 | N | 0
2025-09-19 | 14 | 2031-09-19 14:00 | 5.08 | 6.39 | N | 0
2025-09-19 | 15 | 2031-09-19 15:00 | 5.48 | 6.8932 | N | 0
2025-09-19 | 16 | 2031-09-19 16:00 | 5.73 | 7.2077 | N | 0
2025-09-19 | 17 | 2031-09-19 17:00 | 5.73 | 7.2077 | N | 0
2025-09-19 | 18 | 2031-09-19 18:00 | 5.75 | 7.2328 | N | 0
2025-09-19 | 19 | 2031-09-19 19:00 | 5.98 | 7.5221 | N | 0
2025-09-19 | 20 | 2031-09-19 20:00 | 6.28 | 7.8995 | N | 0
2025-09-19 | 21 | 2031-09-19 21:00 | 6.56 | 8.2517 | N | 0
2025-09-19 | 22 | 2031-09-19 22:00 | 6.35 | 7.9875 | N | 0
2025-09-19 | 23 | 2031-09-19 23:00 | 5.77 | 7.258 | N | 0
2025-09-20 | 00 | 2031-09-20 | 5.77 | 7.258 | N | 0
2025-09-20 | 01 | 2031-09-20 01:00 | 5.39 | 6.78 | N | 0
2025-09-20 | 02 | 2031-09-20 02:00 | 4.99 | 6.2768 | N | 0
2025-09-20 | 03 | 2031-09-20 03:00 | 4.4 | 5.5347 | N | 0
2025-09-20 | 04 | 2031-09-20 04:00 | 3.86 | 4.8554 | N | 0
2025-09-20 | 05 | 2031-09-20 05:00 | 3.48 | 4.3774 | N | 0
2025-09-20 | 06 | 2031-09-20 06:00 | 3.26 | 4.1007 | N | 0
2025-09-20 | 07 | 2031-09-20 07:00 | 3.05 | 3.8365 | N | 0
2025-09-20 | 08 | 2031-09-20 08:00 | 2.96 | 3.7233 | N | 0
2025-09-20 | 09 | 2031-09-20 09:00 | 3.06 | 3.8491 | N | 0
2025-09-20 | 10 | 2031-09-20 10:00 | 3.18 | 4.0001 | N | 0
2025-09-20 | 11 | 2031-09-20 11:00 | 3.48 | 4.3774 | N | 0
2025-09-20 | 12 | 2031-09-20 12:00 | 3.99 | 5.0189 | N | 0
2025-09-20 | 13 | 2031-09-20 13:00 | 4.29 | 5.3963 | N | 0
2025-09-20 | 14 | 2031-09-20 14:00 | 4.68 | 5.8869 | N | 0
2025-09-20 | 15 | 2031-09-20 15:00 | 4.72 | 5.9372 | N | 0
2025-09-20 | 16 | 2031-09-20 16:00 | 4.93 | 6.2014 | N | 0
2025-09-20 | 17 | 2031-09-20 17:00 | 4.91 | 6.1762 | N | 0
2025-09-20 | 18 | 2031-09-20 18:00 | 4.92 | 6.1888 | N | 0
2025-09-20 | 19 | 2031-09-20 19:00 | 4.82 | 6.063 | N | 0
2025-09-20 | 20 | 2031-09-20 20:00 | 5.15 | 6.4781 | N | 0
2025-09-20 | 21 | 2031-09-20 21:00 | 5.31 | 6.6794 | N | 0
2025-09-20 | 22 | 2031-09-20 22:00 | 5.16 | 6.4907 | N | 0
2025-09-20 | 23 | 2031-09-20 23:00 | 4.97 | 6.2517 | N | 0
2025-09-21 | 00 | 2031-09-21 | 4.93 | 6.2014 | N | 0
2025-09-21 | 01 | 2031-09-21 01:00 | 4.75 | 5.9749 | N | 0
2025-09-21 | 02 | 2031-09-21 02:00 | 4.38 | 5.5095 | N | 0
2025-09-21 | 03 | 2031-09-21 03:00 | 3.99 | 5.0189 | N | 0
2025-09-21 | 04 | 2031-09-21 04:00 | 3.65 | 4.5913 | N | 0
2025-09-21 | 05 | 2031-09-21 05:00 | 3.37 | 4.2391 | N | 0
2025-09-21 | 06 | 2031-09-21 06:00 | 3.06 | 3.8491 | N | 0
2025-09-21 | 07 | 2031-09-21 07:00 | 2.97 | 3.7359 | N | 0
2025-09-21 | 08 | 2031-09-21 08:00 | 2.88 | 3.6227 | N | 0
2025-09-21 | 09 | 2031-09-21 09:00 | 3.01 | 3.7862 | N | 0
2025-09-21 | 10 | 2031-09-21 10:00 | 3.05 | 3.8365 | N | 0
2025-09-21 | 11 | 2031-09-21 11:00 | 3.48 | 4.3774 | N | 0
2025-09-21 | 12 | 2031-09-21 12:00 | 3.96 | 4.9812 | N | 0
2025-09-21 | 13 | 2031-09-21 13:00 | 4.23 | 5.3208 | N | 0
2025-09-21 | 14 | 2031-09-21 14:00 | 4.71 | 5.9246 | N | 0
2025-09-21 | 15 | 2031-09-21 15:00 | 5.03 | 6.3271 | N | 0
2025-09-21 | 16 | 2031-09-21 16:00 | 5.34 | 6.7171 | N | 0
2025-09-21 | 17 | 2031-09-21 17:00 | 5.44 | 6.8429 | N | 0
2025-09-21 | 18 | 2031-09-21 18:00 | 5.62 | 7.0693 | N | 0
2025-09-21 | 19 | 2031-09-21 19:00 | 6.17 | 7.7611 | N | 0
2025-09-21 | 20 | 2031-09-21 20:00 | 6.41 | 8.063 | N | 0
2025-09-21 | 21 | 2031-09-21 21:00 | 6.84 | 8.6039 | N | 0
2025-09-21 | 22 | 2031-09-21 22:00 | 6.54 | 8.2265 | N | 0
2025-09-21 | 23 | 2031-09-21 23:00 | 6.4 | 8.0504 | N | 0
2025-09-22 | 00 | 2031-09-22 | 6.4 | 8.0504 | N | 0
2025-09-22 | 01 | 2031-09-22 01:00 | 6.02 | 7.5724 | N | 0
2025-09-22 | 02 | 2031-09-22 02:00 | 5.62 | 7.0693 | N | 0
2025-09-22 | 03 | 2031-09-22 03:00 | 4.86 | 6.1133 | N | 0
2025-09-22 | 04 | 2031-09-22 04:00 | 4.2 | 5.2831 | N | 0
2025-09-22 | 05 | 2031-09-22 05:00 | 3.82 | 4.8051 | N | 0
2025-09-22 | 06 | 2031-09-22 06:00 | 3.46 | 4.3523 | N | 0
2025-09-22 | 07 | 2031-09-22 07:00 | 3.36 | 4.2265 | N | 0
2025-09-22 | 08 | 2031-09-22 08:00 | 3.25 | 4.0881 | N | 0
2025-09-22 | 09 | 2031-09-22 09:00 | 3.49 | 4.39 | N | 0
2025-09-22 | 10 | 2031-09-22 10:00 | 3.95 | 4.9686 | N | 0
2025-09-22 | 11 | 2031-09-22 11:00 | 4.59 | 5.7737 | N | 0
2025-09-22 | 12 | 2031-09-22 12:00 | 4.82 | 6.063 | N | 0
2025-09-22 | 13 | 2031-09-22 13:00 | 5.06 | 6.3649 | N | 0
2025-09-22 | 14 | 2031-09-22 14:00 | 5.27 | 6.629 | N | 0
2025-09-22 | 15 | 2031-09-22 15:00 | 5.44 | 6.8429 | N | 0
2025-09-22 | 16 | 2031-09-22 16:00 | 5.61 | 7.0567 | N | 0
2025-09-22 | 17 | 2031-09-22 17:00 | 5.81 | 7.3083 | N | 0
2025-09-22 | 18 | 2031-09-22 18:00 | 5.83 | 7.3334 | N | 0
2025-09-22 | 19 | 2031-09-22 19:00 | 5.93 | 7.4592 | N | 0
2025-09-22 | 20 | 2031-09-22 20:00 | 6.54 | 8.2265 | N | 0
2025-09-22 | 21 | 2031-09-22 21:00 | 7.2 | 9.0567 | N | 0
2025-09-22 | 22 | 2031-09-22 22:00 | 7.02 | 8.8303 | N | 0
2025-09-22 | 23 | 2031-09-22 23:00 | 6.75 | 8.4907 | N | 0
2025-09-23 | 00 | 2031-09-23 | 6.75 | 8.4907 | N | 0
2025-09-23 | 01 | 2031-09-23 01:00 | 6.42 | 8.0756 | N | 0
2025-09-23 | 02 | 2031-09-23 02:00 | 5.58 | 7.019 | N | 0
2025-09-23 | 03 | 2031-09-23 03:00 | 4.93 | 6.2014 | N | 0
2025-09-23 | 04 | 2031-09-23 04:00 | 4.29 | 5.3963 | N | 0
2025-09-23 | 05 | 2031-09-23 05:00 | 3.87 | 4.868 | N | 0
2025-09-23 | 06 | 2031-09-23 06:00 | 3.6 | 4.5284 | N | 0
2025-09-23 | 07 | 2031-09-23 07:00 | 3.45 | 4.3397 | N | 0
2025-09-23 | 08 | 2031-09-23 08:00 | 3.38 | 4.2516 | N | 0
2025-09-23 | 09 | 2031-09-23 09:00 | 3.57 | 4.4906 | N | 0
2025-09-23 | 10 | 2031-09-23 10:00 | 4.19 | 5.2705 | N | 0
2025-09-23 | 11 | 2031-09-23 11:00 | 4.86 | 6.1133 | N | 0
2025-09-23 | 12 | 2031-09-23 12:00 | 5.02 | 6.3146 | N | 0
2025-09-23 | 13 | 2031-09-23 13:00 | 5.1 | 6.4152 | N | 0
2025-09-23 | 14 | 2031-09-23 14:00 | 5.44 | 6.8429 | N | 0
2025-09-23 | 15 | 2031-09-23 15:00 | 5.82 | 7.3209 | N | 0
2025-09-23 | 16 | 2031-09-23 16:00 | 6.18 | 7.7737 | N | 0
2025-09-23 | 17 | 2031-09-23 17:00 | 6.58 | 8.2769 | N | 0
2025-09-23 | 18 | 2031-09-23 18:00 | 6.79 | 8.541 | N | 0
2025-09-23 | 19 | 2031-09-23 19:00 | 6.98 | 8.78 | N | 0
2025-09-23 | 20 | 2031-09-23 20:00 | 7.49 | 9.4215 | N | 0
2025-09-23 | 21 | 2031-09-23 21:00 | 7.73 | 9.7234 | N | 0
2025-09-23 | 22 | 2031-09-23 22:00 | 7.55 | 9.497 | N | 0
2025-09-23 | 23 | 2031-09-23 23:00 | 7.42 | 9.3335 | N | 0
2025-09-24 | 00 | 2031-09-24 | 7.28 | 9.1574 | N | 0
2025-09-24 | 01 | 2031-09-24 01:00 | 6.87 | 8.6416 | N | 0
2025-09-24 | 02 | 2031-09-24 02:00 | 6.09 | 7.6605 | N | 0
2025-09-24 | 03 | 2031-09-24 03:00 | 5.17 | 6.5032 | N | 0
2025-09-24 | 04 | 2031-09-24 04:00 | 4.43 | 5.5724 | N | 0
2025-09-24 | 05 | 2031-09-24 05:00 | 4 | 5.0315 | N | 0
2025-09-24 | 06 | 2031-09-24 06:00 | 3.59 | 4.5158 | N | 0
2025-09-24 | 07 | 2031-09-24 07:00 | 3.4 | 4.2768 | N | 0
2025-09-24 | 08 | 2031-09-24 08:00 | 3.36 | 4.2265 | N | 0
2025-09-24 | 09 | 2031-09-24 09:00 | 3.54 | 4.4529 | N | 0
2025-09-24 | 10 | 2031-09-24 10:00 | 4.18 | 5.2579 | N | 0
2025-09-24 | 11 | 2031-09-24 11:00 | 4.73 | 5.9498 | N | 0
2025-09-24 | 12 | 2031-09-24 12:00 | 4.86 | 6.1133 | N | 0
2025-09-24 | 13 | 2031-09-24 13:00 | 5.15 | 6.4781 | N | 0
2025-09-24 | 14 | 2031-09-24 14:00 | 5.31 | 6.6794 | N | 0
2025-09-24 | 15 | 2031-09-24 15:00 | 5.61 | 7.0567 | N | 0
2025-09-24 | 16 | 2031-09-24 16:00 | 5.96 | 7.497 | N | 0
2025-09-24 | 17 | 2031-09-24 17:00 | 6.48 | 8.1511 | N | 0
2025-09-24 | 18 | 2031-09-24 18:00 | 6.37 | 8.0127 | N | 0
2025-09-24 | 19 | 2031-09-24 19:00 | 6.06 | 7.6228 | N | 0
2025-09-24 | 20 | 2031-09-24 20:00 | 6.47 | 8.1385 | N | 0
2025-09-24 | 21 | 2031-09-24 21:00 | 6.94 | 8.7297 | N | 0
2025-09-24 | 22 | 2031-09-24 22:00 | 6.82 | 8.5788 | N | 0
2025-09-24 | 23 | 2031-09-24 23:00 | 6.68 | 8.4026 | N | 0
2025-09-25 | 00 | 2031-09-25 | 6.68 | 8.4026 | N | 0
2025-09-25 | 01 | 2031-09-25 01:00 | 6.37 | 8.0127 | N | 0
2025-09-25 | 02 | 2031-09-25 02:00 | 5.6 | 7.0441 | N | 0
2025-09-25 | 03 | 2031-09-25 03:00 | 5.04 | 6.3397 | N | 0
2025-09-25 | 04 | 2031-09-25 04:00 | 4.31 | 5.4215 | N | 0
2025-09-25 | 05 | 2031-09-25 05:00 | 3.83 | 4.8177 | N | 0
2025-09-25 | 06 | 2031-09-25 06:00 | 3.56 | 4.4781 | N | 0
2025-09-25 | 07 | 2031-09-25 07:00 | 3.39 | 4.2642 | N | 0
2025-09-25 | 08 | 2031-09-25 08:00 | 3.28 | 4.1259 | N | 0
2025-09-25 | 09 | 2031-09-25 09:00 | 3.56 | 4.4781 | N | 0
2025-09-25 | 10 | 2031-09-25 10:00 | 4.16 | 5.2328 | N | 0
2025-09-25 | 11 | 2031-09-25 11:00 | 4.77 | 6.0001 | N | 0
2025-09-25 | 12 | 2031-09-25 12:00 | 4.86 | 6.1133 | N | 0
2025-09-25 | 13 | 2031-09-25 13:00 | 5.1 | 6.4152 | N | 0
2025-09-25 | 14 | 2031-09-25 14:00 | 5.21 | 6.5536 | N | 0
2025-09-25 | 15 | 2031-09-25 15:00 | 5.4 | 6.7926 | N | 0
2025-09-25 | 16 | 2031-09-25 16:00 | 5.32 | 6.6919 | N | 0
2025-09-25 | 17 | 2031-09-25 17:00 | 5.36 | 6.7422 | N | 0
2025-09-25 | 18 | 2031-09-25 18:00 | 5.32 | 6.6919 | N | 0
2025-09-25 | 19 | 2031-09-25 19:00 | 5.55 | 6.9812 | N | 0
2025-09-25 | 20 | 2031-09-25 20:00 | 6.04 | 7.5976 | N | 0
2025-09-25 | 21 | 2031-09-25 21:00 | 6.24 | 7.8492 | N | 0
2025-09-25 | 22 | 2031-09-25 22:00 | 6.23 | 7.8366 | N | 0
2025-09-25 | 23 | 2031-09-25 23:00 | 6.26 | 7.8743 | N | 0
2025-09-26 | 00 | 2031-09-26 | 6.27 | 7.8869 | N | 0
2025-09-26 | 01 | 2031-09-26 01:00 | 5.96 | 7.497 | N | 0
2025-09-26 | 02 | 2031-09-26 02:00 | 5.36 | 6.7422 | N | 0
2025-09-26 | 03 | 2031-09-26 03:00 | 4.67 | 5.8743 | N | 0
2025-09-26 | 04 | 2031-09-26 04:00 | 4.06 | 5.107 | N | 0
2025-09-26 | 05 | 2031-09-26 05:00 | 3.64 | 4.5787 | N | 0
2025-09-26 | 06 | 2031-09-26 06:00 | 3.32 | 4.1762 | N | 0
2025-09-26 | 07 | 2031-09-26 07:00 | 3.25 | 4.0881 | N | 0
2025-09-26 | 08 | 2031-09-26 08:00 | 3.13 | 3.9372 | N | 0
2025-09-26 | 09 | 2031-09-26 09:00 | 3.36 | 4.2265 | N | 0
2025-09-26 | 10 | 2031-09-26 10:00 | 3.72 | 4.6793 | N | 0
2025-09-26 | 11 | 2031-09-26 11:00 | 4.19 | 5.2705 | N | 0
2025-09-26 | 12 | 2031-09-26 12:00 | 4.6 | 5.7863 | N | 0
2025-09-26 | 13 | 2031-09-26 13:00 | 5 | 6.2894 | N | 0
2025-09-26 | 14 | 2031-09-26 14:00 | 5.37 | 6.7548 | N | 0
2025-09-26 | 15 | 2031-09-26 15:00 | 5.65 | 7.107 | N | 0
2025-09-26 | 16 | 2031-09-26 16:00 | 5.91 | 7.4341 | N | 0
2025-09-26 | 17 | 2031-09-26 17:00 | 6.16 | 7.7485 | N | 0
2025-09-26 | 18 | 2031-09-26 18:00 | 6.34 | 7.975 | N | 0
2025-09-26 | 19 | 2031-09-26 19:00 | 6.44 | 8.1008 | N | 0
2025-09-26 | 20 | 2031-09-26 20:00 | 6.68 | 8.4026 | N | 0
2025-09-26 | 21 | 2031-09-26 21:00 | 6.88 | 8.6542 | N | 0
2025-09-26 | 22 | 2031-09-26 22:00 | 6.57 | 8.2643 | N | 0
2025-09-26 | 23 | 2031-09-26 23:00 | 6.23 | 7.8366 | N | 0
2025-09-27 | 00 | 2031-09-27 | 6.19 | 7.7863 | N | 0
2025-09-27 | 01 | 2031-09-27 01:00 | 5.85 | 7.3586 | N | 0
2025-09-27 | 02 | 2031-09-27 02:00 | 5.39 | 6.78 | N | 0
2025-09-27 | 03 | 2031-09-27 03:00 | 4.63 | 5.824 | N | 0
2025-09-27 | 04 | 2031-09-27 04:00 | 4.17 | 5.2454 | N | 0
2025-09-27 | 05 | 2031-09-27 05:00 | 3.78 | 4.7548 | N | 0
2025-09-27 | 06 | 2031-09-27 06:00 | 3.4 | 4.2768 | N | 0
2025-09-27 | 07 | 2031-09-27 07:00 | 3.2 | 4.0252 | N | 0
2025-09-27 | 08 | 2031-09-27 08:00 | 3.1 | 3.8994 | N | 0
2025-09-27 | 09 | 2031-09-27 09:00 | 3.1 | 3.8994 | N | 0
2025-09-27 | 10 | 2031-09-27 10:00 | 3.21 | 4.0378 | N | 0
2025-09-27 | 11 | 2031-09-27 11:00 | 3.62 | 4.5535 | N | 0
2025-09-27 | 12 | 2031-09-27 12:00 | 4.05 | 5.0944 | N | 0
2025-09-27 | 13 | 2031-09-27 13:00 | 4.5 | 5.6605 | N | 0
2025-09-27 | 14 | 2031-09-27 14:00 | 4.99 | 6.2768 | N | 0
2025-09-27 | 15 | 2031-09-27 15:00 | 5.47 | 6.8806 | N | 0
2025-09-27 | 16 | 2031-09-27 16:00 | 5.67 | 7.1322 | N | 0
2025-09-27 | 17 | 2031-09-27 17:00 | 5.67 | 7.1322 | N | 0
2025-09-27 | 18 | 2031-09-27 18:00 | 5.82 | 7.3209 | N | 0
2025-09-27 | 19 | 2031-09-27 19:00 | 5.96 | 7.497 | N | 0
2025-09-27 | 20 | 2031-09-27 20:00 | 6.08 | 7.6479 | N | 0
2025-09-27 | 21 | 2031-09-27 21:00 | 6.25 | 7.8618 | N | 0
2025-09-27 | 22 | 2031-09-27 22:00 | 6.24 | 7.8492 | N | 0
2025-09-27 | 23 | 2031-09-27 23:00 | 6.06 | 7.6228 | N | 0
2025-09-28 | 00 | 2031-09-28 | 5.89 | 7.4089 | N | 0
2025-09-28 | 01 | 2031-09-28 01:00 | 5.64 | 7.0945 | N | 0
2025-09-28 | 02 | 2031-09-28 02:00 | 5.17 | 6.5032 | N | 0
2025-09-28 | 03 | 2031-09-28 03:00 | 4.62 | 5.8114 | N | 0
2025-09-28 | 04 | 2031-09-28 04:00 | 4.12 | 5.1825 | N | 0
2025-09-28 | 05 | 2031-09-28 05:00 | 3.65 | 4.5913 | N | 0
2025-09-28 | 06 | 2031-09-28 06:00 | 3.33 | 4.1887 | N | 0
2025-09-28 | 07 | 2031-09-28 07:00 | 3.16 | 3.9749 | N | 0
2025-09-28 | 08 | 2031-09-28 08:00 | 3.12 | 3.9246 | N | 0
2025-09-28 | 09 | 2031-09-28 09:00 | 3.02 | 3.7988 | N | 0
2025-09-28 | 10 | 2031-09-28 10:00 | 3.13 | 3.9372 | N | 0
2025-09-28 | 11 | 2031-09-28 11:00 | 3.52 | 4.4277 | N | 0
2025-09-28 | 12 | 2031-09-28 12:00 | 4.05 | 5.0944 | N | 0
2025-09-28 | 13 | 2031-09-28 13:00 | 4.69 | 5.8995 | N | 0
2025-09-28 | 14 | 2031-09-28 14:00 | 5.28 | 6.6416 | N | 0
2025-09-28 | 15 | 2031-09-28 15:00 | 5.66 | 7.1196 | N | 0
2025-09-28 | 16 | 2031-09-28 16:00 | 6 | 7.5473 | N | 0
2025-09-28 | 17 | 2031-09-28 17:00 | 6.38 | 8.0253 | N | 0
2025-09-28 | 18 | 2031-09-28 18:00 | 6.58 | 8.2769 | N | 0
2025-09-28 | 19 | 2031-09-28 19:00 | 6.74 | 8.4781 | N | 0
2025-09-28 | 20 | 2031-09-28 20:00 | 7.21 | 9.0693 | N | 0
2025-09-28 | 21 | 2031-09-28 21:00 | 7.21 | 9.0693 | N | 0
2025-09-28 | 22 | 2031-09-28 22:00 | 7.21 | 9.0693 | N | 0
2025-09-28 | 23 | 2031-09-28 23:00 | 6.76 | 8.5033 | N | 0
2025-09-29 | 00 | 2031-09-29 | 6.68 | 8.4026 | N | 0
2025-09-29 | 01 | 2031-09-29 01:00 | 5.91 | 7.4341 | N | 0
2025-09-29 | 02 | 2031-09-29 02:00 | 5.36 | 6.7422 | N | 0
2025-09-29 | 03 | 2031-09-29 03:00 | 4.56 | 5.7359 | N | 0
2025-09-29 | 04 | 2031-09-29 04:00 | 3.98 | 5.0064 | N | 0
2025-09-29 | 05 | 2031-09-29 05:00 | 3.54 | 4.4529 | N | 0
2025-09-29 | 06 | 2031-09-29 06:00 | 3.22 | 4.0504 | N | 0
2025-09-29 | 07 | 2031-09-29 07:00 | 3.13 | 3.9372 | N | 0
2025-09-29 | 08 | 2031-09-29 08:00 | 3.05 | 3.8365 | N | 0
2025-09-29 | 09 | 2031-09-29 09:00 | 3.3 | 4.151 | N | 0
2025-09-29 | 10 | 2031-09-29 10:00 | 3.68 | 4.629 | N | 0
2025-09-29 | 11 | 2031-09-29 11:00 | 4.21 | 5.2957 | N | 0
2025-09-29 | 12 | 2031-09-29 12:00 | 4.3 | 5.4089 | N | 0
2025-09-29 | 13 | 2031-09-29 13:00 | 4.56 | 5.7359 | N | 0
2025-09-29 | 14 | 2031-09-29 14:00 | 4.94 | 6.2139 | N | 0
2025-09-29 | 15 | 2031-09-29 15:00 | 5.25 | 6.6039 | N | 0
2025-09-29 | 16 | 2031-09-29 16:00 | 5.57 | 7.0064 | N | 0
2025-09-29 | 17 | 2031-09-29 17:00 | 5.57 | 7.0064 | N | 0
2025-09-29 | 18 | 2031-09-29 18:00 | 5.87 | 7.3838 | N | 0
2025-09-29 | 19 | 2031-09-29 19:00 | 6.33 | 7.9624 | N | 0
2025-09-29 | 20 | 2031-09-29 20:00 | 6.89 | 8.6668 | N | 0
2025-09-29 | 21 | 2031-09-29 21:00 | 7.26 | 9.1322 | N | 0
2025-09-29 | 22 | 2031-09-29 22:00 | 7.02 | 8.8303 | N | 0
2025-09-29 | 23 | 2031-09-29 23:00 | 6.56 | 8.2517 | N | 0
2025-09-30 | 00 | 2031-09-30 | 6.35 | 7.9875 | N | 0
2025-09-30 | 01 | 2031-09-30 01:00 | 5.79 | 7.2831 | N | 0
2025-09-30 | 02 | 2031-09-30 02:00 | 5.09 | 6.4026 | N | 0
2025-09-30 | 03 | 2031-09-30 03:00 | 4.39 | 5.5221 | N | 0
2025-09-30 | 04 | 2031-09-30 04:00 | 3.76 | 4.7296 | N | 0
2025-09-30 | 05 | 2031-09-30 05:00 | 3.29 | 4.1384 | N | 0
2025-09-30 | 06 | 2031-09-30 06:00 | 3.16 | 3.9749 | N | 0
2025-09-30 | 07 | 2031-09-30 07:00 | 3.07 | 3.8617 | N | 0
2025-09-30 | 08 | 2031-09-30 08:00 | 3.01 | 3.7862 | N | 0
2025-09-30 | 09 | 2031-09-30 09:00 | 3.15 | 3.9623 | N | 0
2025-09-30 | 10 | 2031-09-30 10:00 | 3.72 | 4.6793 | N | 0
2025-09-30 | 11 | 2031-09-30 11:00 | 4.21 | 5.2957 | N | 0
2025-09-30 | 12 | 2031-09-30 12:00 | 4.32 | 5.434 | N | 0
2025-09-30 | 13 | 2031-09-30 13:00 | 4.36 | 5.4844 | N | 0
2025-09-30 | 14 | 2031-09-30 14:00 | 4.58 | 5.7611 | N | 0
2025-09-30 | 15 | 2031-09-30 15:00 | 5.06 | 6.3649 | N | 0
2025-09-30 | 16 | 2031-09-30 16:00 | 5.34 | 6.7171 | N | 0
2025-09-30 | 17 | 2031-09-30 17:00 | 5.41 | 6.8051 | N | 0
2025-09-30 | 18 | 2031-09-30 18:00 | 5.59 | 7.0316 | N | 0
2025-09-30 | 19 | 2031-09-30 19:00 | 6.17 | 7.7611 | N | 0
2025-09-30 | 20 | 2031-09-30 20:00 | 6.45 | 8.1133 | N | 0
2025-09-30 | 21 | 2031-09-30 21:00 | 6.87 | 8.6416 | N | 0
2025-09-30 | 22 | 2031-09-30 22:00 | 6.74 | 8.4781 | N | 0
2025-09-30 | 23 | 2031-09-30 23:00 | 6.36 | 8.0001 | N | 0
2025-10-01 | 00 | 2031-10-01 | 6.05 | 7.6102 | N | 0
2025-10-01 | 01 | 2031-10-01 01:00 | 5.67 | 7.1322 | N | 0
2025-10-01 | 02 | 2031-10-01 02:00 | 4.89 | 6.151 | N | 0
2025-10-01 | 03 | 2031-10-01 03:00 | 4.22 | 5.3083 | N | 0
2025-10-01 | 04 | 2031-10-01 04:00 | 3.74 | 4.7045 | N | 0
2025-10-01 | 05 | 2031-10-01 05:00 | 3.36 | 4.2265 | N | 0
2025-10-01 | 06 | 2031-10-01 06:00 | 3.04 | 3.824 | N | 0
2025-10-01 | 07 | 2031-10-01 07:00 | 2.95 | 3.7108 | N | 0
2025-10-01 | 08 | 2031-10-01 08:00 | 3.01 | 3.7862 | N | 0
2025-10-01 | 09 | 2031-10-01 09:00 | 3.23 | 4.063 | N | 0
2025-10-01 | 10 | 2031-10-01 10:00 | 3.64 | 4.5787 | N | 0
2025-10-01 | 11 | 2031-10-01 11:00 | 4.14 | 5.2076 | N | 0
2025-10-01 | 12 | 2031-10-01 12:00 | 4.23 | 5.3208 | N | 0
2025-10-01 | 13 | 2031-10-01 13:00 | 4.24 | 5.3334 | N | 0
2025-10-01 | 14 | 2031-10-01 14:00 | 4.39 | 5.5221 | N | 0
2025-10-01 | 15 | 2031-10-01 15:00 | 4.52 | 5.6856 | N | 0
2025-10-01 | 16 | 2031-10-01 16:00 | 4.67 | 5.8743 | N | 0
2025-10-01 | 17 | 2031-10-01 17:00 | 4.67 | 5.8743 | N | 0
2025-10-01 | 18 | 2031-10-01 18:00 | 4.6 | 5.7863 | N | 0
2025-10-01 | 19 | 2031-10-01 19:00 | 4.84 | 6.0881 | N | 0
2025-10-01 | 20 | 2031-10-01 20:00 | 5.3 | 6.6668 | N | 0
2025-10-01 | 21 | 2031-10-01 21:00 | 5.66 | 7.1196 | N | 0
2025-10-01 | 22 | 2031-10-01 22:00 | 5.59 | 7.0316 | N | 0
2025-10-01 | 23 | 2031-10-01 23:00 | 5.58 | 7.019 | N | 0
2025-10-02 | 00 | 2031-10-02 | 5.54 | 6.9687 | N | 0
2025-10-02 | 01 | 2031-10-02 01:00 | 5.19 | 6.5284 | N | 0
2025-10-02 | 02 | 2031-10-02 02:00 | 4.59 | 5.7737 | N | 0
2025-10-02 | 03 | 2031-10-02 03:00 | 3.93 | 4.9435 | N | 0
2025-10-02 | 04 | 2031-10-02 04:00 | 3.49 | 4.39 | N | 0
2025-10-02 | 05 | 2031-10-02 05:00 | 3.17 | 3.9875 | N | 0
2025-10-02 | 06 | 2031-10-02 06:00 | 2.98 | 3.7485 | N | 0
2025-10-02 | 07 | 2031-10-02 07:00 | 2.88 | 3.6227 | N | 0
2025-10-02 | 08 | 2031-10-02 08:00 | 2.89 | 3.6353 | N | 0
2025-10-02 | 09 | 2031-10-02 09:00 | 3.12 | 3.9246 | N | 0
2025-10-02 | 10 | 2031-10-02 10:00 | 3.69 | 4.6416 | N | 0
2025-10-02 | 11 | 2031-10-02 11:00 | 4.12 | 5.1825 | N | 0
2025-10-02 | 12 | 2031-10-02 12:00 | 4.15 | 5.2202 | N | 0
2025-10-02 | 13 | 2031-10-02 13:00 | 4.18 | 5.2579 | N | 0
2025-10-02 | 14 | 2031-10-02 14:00 | 4.3 | 5.4089 | N | 0
2025-10-02 | 15 | 2031-10-02 15:00 | 4.45 | 5.5976 | N | 0
2025-10-02 | 16 | 2031-10-02 16:00 | 4.64 | 5.8366 | N | 0
2025-10-02 | 17 | 2031-10-02 17:00 | 4.64 | 5.8366 | N | 0
2025-10-02 | 18 | 2031-10-02 18:00 | 4.64 | 5.8366 | N | 0
2025-10-02 | 19 | 2031-10-02 19:00 | 4.68 | 5.8869 | N | 0
2025-10-02 | 20 | 2031-10-02 20:00 | 5.15 | 6.4781 | N | 0
2025-10-02 | 21 | 2031-10-02 21:00 | 5.44 | 6.8429 | N | 0
2025-10-02 | 22 | 2031-10-02 22:00 | 5.35 | 6.7297 | N | 0
2025-10-02 | 23 | 2031-10-02 23:00 | 5.5 | 6.9183 | N | 0
2025-10-03 | 00 | 2031-10-03 | 5.38 | 6.7674 | N | 0
2025-10-03 | 01 | 2031-10-03 01:00 | 5.2 | 6.541 | N | 0
2025-10-03 | 02 | 2031-10-03 02:00 | 4.57 | 5.7485 | N | 0
2025-10-03 | 03 | 2031-10-03 03:00 | 3.93 | 4.9435 | N | 0
2025-10-03 | 04 | 2031-10-03 04:00 | 3.51 | 4.4152 | N | 0
2025-10-03 | 05 | 2031-10-03 05:00 | 3.25 | 4.0881 | N | 0
2025-10-03 | 06 | 2031-10-03 06:00 | 3.03 | 3.8114 | N | 0
2025-10-03 | 07 | 2031-10-03 07:00 | 2.96 | 3.7233 | N | 0
2025-10-03 | 08 | 2031-10-03 08:00 | 2.9 | 3.6479 | N | 0
2025-10-03 | 09 | 2031-10-03 09:00 | 3.1 | 3.8994 | N | 0
2025-10-03 | 10 | 2031-10-03 10:00 | 3.64 | 4.5787 | N | 0
2025-10-03 | 11 | 2031-10-03 11:00 | 4.25 | 5.346 | N | 0
2025-10-03 | 12 | 2031-10-03 12:00 | 4.3 | 5.4089 | N | 0
2025-10-03 | 13 | 2031-10-03 13:00 | 4.28 | 5.3837 | N | 0
2025-10-03 | 14 | 2031-10-03 14:00 | 4.56 | 5.7359 | N | 0
2025-10-03 | 15 | 2031-10-03 15:00 | 4.73 | 5.9498 | N | 0
2025-10-03 | 16 | 2031-10-03 16:00 | 4.87 | 6.1259 | N | 0
2025-10-03 | 17 | 2031-10-03 17:00 | 5.11 | 6.4278 | N | 0
2025-10-03 | 18 | 2031-10-03 18:00 | 5.02 | 6.3146 | N | 0
2025-10-03 | 19 | 2031-10-03 19:00 | 5.4 | 6.7926 | N | 0
2025-10-03 | 20 | 2031-10-03 20:00 | 5.64 | 7.0945 | N | 0
2025-10-03 | 21 | 2031-10-03 21:00 | 5.88 | 7.3963 | N | 0
2025-10-03 | 22 | 2031-10-03 22:00 | 5.7 | 7.1699 | N | 0
2025-10-03 | 23 | 2031-10-03 23:00 | 5.59 | 7.0316 | N | 0
2025-10-04 | 00 | 2031-10-04 | 5.44 | 6.8429 | N | 0
2025-10-04 | 01 | 2031-10-04 01:00 | 5.19 | 6.5284 | N | 0
2025-10-04 | 02 | 2031-10-04 02:00 | 4.77 | 6.0001 | N | 0
2025-10-04 | 03 | 2031-10-04 03:00 | 4.26 | 5.3586 | N | 0
2025-10-04 | 04 | 2031-10-04 04:00 | 3.77 | 4.7422 | N | 0
2025-10-04 | 05 | 2031-10-04 05:00 | 3.42 | 4.302 | N | 0
2025-10-04 | 06 | 2031-10-04 06:00 | 3.18 | 4.0001 | N | 0
2025-10-04 | 07 | 2031-10-04 07:00 | 3.02 | 3.7988 | N | 0
2025-10-04 | 08 | 2031-10-04 08:00 | 2.91 | 3.6604 | N | 0
2025-10-04 | 09 | 2031-10-04 09:00 | 2.96 | 3.7233 | N | 0
2025-10-04 | 10 | 2031-10-04 10:00 | 3.12 | 3.9246 | N | 0
2025-10-04 | 11 | 2031-10-04 11:00 | 3.56 | 4.4781 | N | 0
2025-10-04 | 12 | 2031-10-04 12:00 | 4.02 | 5.0567 | N | 0
2025-10-04 | 13 | 2031-10-04 13:00 | 4.37 | 5.4969 | N | 0
2025-10-04 | 14 | 2031-10-04 14:00 | 4.96 | 6.2391 | N | 0
2025-10-04 | 15 | 2031-10-04 15:00 | 5.29 | 6.6542 | N | 0
2025-10-04 | 16 | 2031-10-04 16:00 | 5.6 | 7.0441 | N | 0
2025-10-04 | 17 | 2031-10-04 17:00 | 5.91 | 7.4341 | N | 0
2025-10-04 | 18 | 2031-10-04 18:00 | 6.11 | 7.6857 | N | 0
2025-10-04 | 19 | 2031-10-04 19:00 | 6.21 | 7.8114 | N | 0
2025-10-04 | 20 | 2031-10-04 20:00 | 6.41 | 8.063 | N | 0
2025-10-04 | 21 | 2031-10-04 21:00 | 6.6 | 8.302 | N | 0
2025-10-04 | 22 | 2031-10-04 22:00 | 6.45 | 8.1133 | N | 0
2025-10-04 | 23 | 2031-10-04 23:00 | 6.16 | 7.7485 | N | 0
2025-10-05 | 00 | 2031-10-05 | 5.95 | 7.4844 | N | 0
2025-10-05 | 01 | 2031-10-05 01:00 | 5.57 | 7.0064 | N | 0
2025-10-05 | 02 | 2031-10-05 02:00 | 5.11 | 6.4278 | N | 0
2025-10-05 | 03 | 2031-10-05 03:00 | 4.59 | 5.7737 | N | 0
2025-10-05 | 04 | 2031-10-05 04:00 | 4.02 | 5.0567 | N | 0
2025-10-05 | 05 | 2031-10-05 05:00 | 3.58 | 4.5032 | N | 0
2025-10-05 | 06 | 2031-10-05 06:00 | 3.29 | 4.1384 | N | 0
2025-10-05 | 07 | 2031-10-05 07:00 | 3.09 | 3.8869 | N | 0
2025-10-05 | 08 | 2031-10-05 08:00 | 2.99 | 3.7611 | N | 0
2025-10-05 | 09 | 2031-10-05 09:00 | 3 | 3.7736 | N | 0
2025-10-05 | 10 | 2031-10-05 10:00 | 3.1 | 3.8994 | N | 0
2025-10-05 | 11 | 2031-10-05 11:00 | 3.42 | 4.302 | N | 0
2025-10-05 | 12 | 2031-10-05 12:00 | 3.97 | 4.9938 | N | 0
2025-10-05 | 13 | 2031-10-05 13:00 | 4.47 | 5.6227 | N | 0
2025-10-05 | 14 | 2031-10-05 14:00 | 5.15 | 6.4781 | N | 0
2025-10-05 | 15 | 2031-10-05 15:00 | 5.88 | 7.3963 | N | 0
2025-10-05 | 16 | 2031-10-05 16:00 | 6.15 | 7.736 | N | 0
2025-10-05 | 17 | 2031-10-05 17:00 | 6.5 | 8.1762 | N | 0
2025-10-05 | 18 | 2031-10-05 18:00 | 6.9 | 8.6794 | N | 0
2025-10-05 | 19 | 2031-10-05 19:00 | 7.11 | 8.9435 | N | 0
2025-10-05 | 20 | 2031-10-05 20:00 | 7.58 | 9.5347 | N | 0
2025-10-05 | 21 | 2031-10-05 21:00 | 7.7 | 9.6857 | N | 0
2025-10-05 | 22 | 2031-10-05 22:00 | 7.32 | 9.2077 | N | 0
2025-10-05 | 23 | 2031-10-05 23:00 | 7.15 | 8.9939 | N | 0
2025-10-06 | 00 | 2031-10-06 | 6.9 | 8.6794 | N | 0
2025-10-06 | 01 | 2031-10-06 01:00 | 6.21 | 7.8114 | N | 0
2025-10-06 | 02 | 2031-10-06 02:00 | 5.37 | 6.7548 | N | 0
2025-10-06 | 03 | 2031-10-06 03:00 | 4.6 | 5.7863 | N | 0
2025-10-06 | 04 | 2031-10-06 04:00 | 3.96 | 4.9812 | N | 0
2025-10-06 | 05 | 2031-10-06 05:00 | 3.53 | 4.4403 | N | 0
2025-10-06 | 06 | 2031-10-06 06:00 | 3.23 | 4.063 | N | 0
2025-10-06 | 07 | 2031-10-06 07:00 | 3.03 | 3.8114 | N | 0
2025-10-06 | 08 | 2031-10-06 08:00 | 2.99 | 3.7611 | N | 0
2025-10-06 | 09 | 2031-10-06 09:00 | 3.17 | 3.9875 | N | 0
2025-10-06 | 10 | 2031-10-06 10:00 | 3.72 | 4.6793 | N | 0
2025-10-06 | 11 | 2031-10-06 11:00 | 4.11 | 5.1699 | N | 0
2025-10-06 | 12 | 2031-10-06 12:00 | 4.22 | 5.3083 | N | 0
2025-10-06 | 13 | 2031-10-06 13:00 | 4.59 | 5.7737 | N | 0
2025-10-06 | 14 | 2031-10-06 14:00 | 5.2 | 6.541 | N | 0
2025-10-06 | 15 | 2031-10-06 15:00 | 5.43 | 6.8303 | N | 0
2025-10-06 | 16 | 2031-10-06 16:00 | 5.7 | 7.1699 | N | 0
2025-10-06 | 17 | 2031-10-06 17:00 | 6.09 | 7.6605 | N | 0
2025-10-06 | 18 | 2031-10-06 18:00 | 6.33 | 7.9624 | N | 0
2025-10-06 | 19 | 2031-10-06 19:00 | 6.8 | 8.5536 | N | 0
2025-10-06 | 20 | 2031-10-06 20:00 | 7.16 | 9.0064 | N | 0
2025-10-06 | 21 | 2031-10-06 21:00 | 7.58 | 9.5347 | N | 0
2025-10-06 | 22 | 2031-10-06 22:00 | 7.42 | 9.3335 | N | 0
2025-10-06 | 23 | 2031-10-06 23:00 | 7.1 | 8.931 | N | 0
2025-10-07 | 00 | 2031-10-07 | 7.02 | 8.8303 | N | 0
2025-10-07 | 01 | 2031-10-07 01:00 | 6.6 | 8.302 | N | 0
2025-10-07 | 02 | 2031-10-07 02:00 | 5.91 | 7.4341 | N | 0
2025-10-07 | 03 | 2031-10-07 03:00 | 4.93 | 6.2014 | N | 0
2025-10-07 | 04 | 2031-10-07 04:00 | 4.24 | 5.3334 | N | 0
2025-10-07 | 05 | 2031-10-07 05:00 | 3.69 | 4.6416 | N | 0
2025-10-07 | 06 | 2031-10-07 06:00 | 3.35 | 4.2139 | N | 0
2025-10-07 | 07 | 2031-10-07 07:00 | 3.14 | 3.9497 | N | 0
2025-10-07 | 08 | 2031-10-07 08:00 | 3.05 | 3.8365 | N | 0
2025-10-07 | 09 | 2031-10-07 09:00 | 3.24 | 4.0755 | N | 0
2025-10-07 | 10 | 2031-10-07 10:00 | 3.81 | 4.7925 | N | 0
2025-10-07 | 11 | 2031-10-07 11:00 | 4.48 | 5.6353 | N | 0
2025-10-07 | 12 | 2031-10-07 12:00 | 4.63 | 5.824 | N | 0
2025-10-07 | 13 | 2031-10-07 13:00 | 4.86 | 6.1133 | N | 0
2025-10-07 | 14 | 2031-10-07 14:00 | 5.09 | 6.4026 | N | 0
2025-10-07 | 15 | 2031-10-07 15:00 | 5.25 | 6.6039 | N | 0
2025-10-07 | 16 | 2031-10-07 16:00 | 5.39 | 6.78 | N | 0
2025-10-07 | 17 | 2031-10-07 17:00 | 5.46 | 6.868 | N | 0
2025-10-07 | 18 | 2031-10-07 18:00 | 5.26 | 6.6165 | N | 0
2025-10-07 | 19 | 2031-10-07 19:00 | 5.26 | 6.6165 | N | 0
2025-10-07 | 20 | 2031-10-07 20:00 | 5.94 | 7.4718 | N | 0
2025-10-07 | 21 | 2031-10-07 21:00 | 6.19 | 7.7863 | N | 0
2025-10-07 | 22 | 2031-10-07 22:00 | 5.98 | 7.5221 | N | 0
2025-10-07 | 23 | 2031-10-07 23:00 | 5.92 | 7.4467 | N | 0
2025-10-08 | 00 | 2031-10-08 | 5.73 | 7.2077 | N | 0
2025-10-08 | 01 | 2031-10-08 01:00 | 5.37 | 6.7548 | N | 0
2025-10-08 | 02 | 2031-10-08 02:00 | 4.81 | 6.0504 | N | 0
2025-10-08 | 03 | 2031-10-08 03:00 | 4.21 | 5.2957 | N | 0
2025-10-08 | 04 | 2031-10-08 04:00 | 3.64 | 4.5787 | N | 0
2025-10-08 | 05 | 2031-10-08 05:00 | 3.33 | 4.1887 | N | 0
2025-10-08 | 06 | 2031-10-08 06:00 | 3.08 | 3.8743 | N | 0
2025-10-08 | 07 | 2031-10-08 07:00 | 2.9 | 3.6479 | N | 0
2025-10-08 | 08 | 2031-10-08 08:00 | 2.88 | 3.6227 | N | 0
2025-10-08 | 09 | 2031-10-08 09:00 | 3.04 | 3.824 | N | 0
2025-10-08 | 10 | 2031-10-08 10:00 | 3.66 | 4.6038 | N | 0
2025-10-08 | 11 | 2031-10-08 11:00 | 4.1 | 5.1573 | N | 0
2025-10-08 | 12 | 2031-10-08 12:00 | 4.17 | 5.2454 | N | 0
2025-10-08 | 13 | 2031-10-08 13:00 | 4.22 | 5.3083 | N | 0
2025-10-08 | 14 | 2031-10-08 14:00 | 4.36 | 5.4844 | N | 0
2025-10-08 | 15 | 2031-10-08 15:00 | 4.49 | 5.6479 | N | 0
2025-10-08 | 16 | 2031-10-08 16:00 | 4.62 | 5.8114 | N | 0
2025-10-08 | 17 | 2031-10-08 17:00 | 4.54 | 5.7108 | N | 0
2025-10-08 | 18 | 2031-10-08 18:00 | 4.53 | 5.6982 | N | 0
2025-10-08 | 19 | 2031-10-08 19:00 | 4.61 | 5.7988 | N | 0
2025-10-08 | 20 | 2031-10-08 20:00 | 5.09 | 6.4026 | N | 0
2025-10-08 | 21 | 2031-10-08 21:00 | 5.35 | 6.7297 | N | 0
2025-10-08 | 22 | 2031-10-08 22:00 | 5.35 | 6.7297 | N | 0
2025-10-08 | 23 | 2031-10-08 23:00 | 5.35 | 6.7297 | N | 0
2025-10-09 | 00 | 2031-10-09 | 5.31 | 6.6794 | N | 0
2025-10-09 | 01 | 2031-10-09 01:00 | 5.02 | 6.3146 | N | 0
2025-10-09 | 02 | 2031-10-09 02:00 | 4.57 | 5.7485 | N | 0
2025-10-09 | 03 | 2031-10-09 03:00 | 3.94 | 4.9561 | N | 0
2025-10-09 | 04 | 2031-10-09 04:00 | 3.48 | 4.3774 | N | 0
2025-10-09 | 05 | 2031-10-09 05:00 | 3.26 | 4.1007 | N | 0
2025-10-09 | 06 | 2031-10-09 06:00 | 3.06 | 3.8491 | N | 0
2025-10-09 | 07 | 2031-10-09 07:00 | 2.96 | 3.7233 | N | 0
2025-10-09 | 08 | 2031-10-09 08:00 | 2.99 | 3.7611 | N | 0
2025-10-09 | 09 | 2031-10-09 09:00 | 3.19 | 4.0126 | N | 0
2025-10-09 | 10 | 2031-10-09 10:00 | 3.83 | 4.8177 | N | 0
2025-10-09 | 11 | 2031-10-09 11:00 | 4.33 | 5.4466 | N | 0
2025-10-09 | 12 | 2031-10-09 12:00 | 4.31 | 5.4215 | N | 0
2025-10-09 | 13 | 2031-10-09 13:00 | 4.31 | 5.4215 | N | 0
2025-10-09 | 14 | 2031-10-09 14:00 | 4.45 | 5.5976 | N | 0
2025-10-09 | 15 | 2031-10-09 15:00 | 4.45 | 5.5976 | N | 0
2025-10-09 | 16 | 2031-10-09 16:00 | 4.53 | 5.6982 | N | 0
2025-10-09 | 17 | 2031-10-09 17:00 | 4.54 | 5.7108 | N | 0
2025-10-09 | 18 | 2031-10-09 18:00 | 4.39 | 5.5221 | N | 0
2025-10-09 | 19 | 2031-10-09 19:00 | 4.53 | 5.6982 | N | 0
2025-10-09 | 20 | 2031-10-09 20:00 | 4.97 | 6.2517 | N | 0
2025-10-09 | 21 | 2031-10-09 21:00 | 5.22 | 6.5661 | N | 0
2025-10-09 | 22 | 2031-10-09 22:00 | 5.37 | 6.7548 | N | 0
2025-10-09 | 23 | 2031-10-09 23:00 | 5.54 | 6.9687 | N | 0
2025-10-10 | 00 | 2031-10-10 | 5.45 | 6.8555 | N | 0
2025-10-10 | 01 | 2031-10-10 01:00 | 5.36 | 6.7422 | N | 0
2025-10-10 | 02 | 2031-10-10 02:00 | 4.73 | 5.9498 | N | 0
2025-10-10 | 03 | 2031-10-10 03:00 | 4.16 | 5.2328 | N | 0
2025-10-10 | 04 | 2031-10-10 04:00 | 3.86 | 4.8554 | N | 0
2025-10-10 | 05 | 2031-10-10 05:00 | 3.42 | 4.302 | N | 0
2025-10-10 | 06 | 2031-10-10 06:00 | 3.25 | 4.0881 | N | 0
2025-10-10 | 07 | 2031-10-10 07:00 | 3.21 | 4.0378 | N | 0
2025-10-10 | 08 | 2031-10-10 08:00 | 3.24 | 4.0755 | N | 0
2025-10-10 | 09 | 2031-10-10 09:00 | 3.41 | 4.2894 | N | 0
2025-10-10 | 10 | 2031-10-10 10:00 | 4.07 | 5.1196 | N | 0
2025-10-10 | 11 | 2031-10-10 11:00 | 4.57 | 5.7485 | N | 0
2025-10-10 | 12 | 2031-10-10 12:00 | 4.73 | 5.9498 | N | 0
2025-10-10 | 13 | 2031-10-10 13:00 | 4.65 | 5.8491 | N | 0
2025-10-10 | 14 | 2031-10-10 14:00 | 4.61 | 5.7988 | N | 0
2025-10-10 | 15 | 2031-10-10 15:00 | 4.63 | 5.824 | N | 0
2025-10-10 | 16 | 2031-10-10 16:00 | 4.73 | 5.9498 | N | 0
2025-10-10 | 17 | 2031-10-10 17:00 | 4.63 | 5.824 | N | 0
2025-10-10 | 18 | 2031-10-10 18:00 | 4.6 | 5.7863 | N | 0
2025-10-10 | 19 | 2031-10-10 19:00 | 4.73 | 5.9498 | N | 0
2025-10-10 | 20 | 2031-10-10 20:00 | 4.95 | 6.2265 | N | 0
2025-10-10 | 21 | 2031-10-10 21:00 | 5.28 | 6.6416 | N | 0
2025-10-10 | 22 | 2031-10-10 22:00 | 5.19 | 6.5284 | N | 0
2025-10-10 | 23 | 2031-10-10 23:00 | 5.23 | 6.5787 | N | 0
2025-10-11 | 00 | 2031-10-11 | 5.31 | 6.6794 | N | 0
2025-10-11 | 01 | 2031-10-11 01:00 | 5.15 | 6.4781 | N | 0
2025-10-11 | 02 | 2031-10-11 02:00 | 4.74 | 5.9624 | N | 0
2025-10-11 | 03 | 2031-10-11 03:00 | 4.11 | 5.1699 | N | 0
2025-10-11 | 04 | 2031-10-11 04:00 | 3.7 | 4.6542 | N | 0
2025-10-11 | 05 | 2031-10-11 05:00 | 3.44 | 4.3271 | N | 0
2025-10-11 | 06 | 2031-10-11 06:00 | 3.17 | 3.9875 | N | 0
2025-10-11 | 07 | 2031-10-11 07:00 | 3.05 | 3.8365 | N | 0
2025-10-11 | 08 | 2031-10-11 08:00 | 2.96 | 3.7233 | N | 0
2025-10-11 | 09 | 2031-10-11 09:00 | 3.04 | 3.824 | N | 0
2025-10-11 | 10 | 2031-10-11 10:00 | 3.2 | 4.0252 | N | 0
2025-10-11 | 11 | 2031-10-11 11:00 | 3.61 | 4.541 | N | 0
2025-10-11 | 12 | 2031-10-11 12:00 | 4.01 | 5.0441 | N | 0
2025-10-11 | 13 | 2031-10-11 13:00 | 4.64 | 5.8366 | N | 0
2025-10-11 | 14 | 2031-10-11 14:00 | 4.8 | 6.0378 | N | 0
2025-10-11 | 15 | 2031-10-11 15:00 | 5.13 | 6.4529 | N | 0
2025-10-11 | 16 | 2031-10-11 16:00 | 5.11 | 6.4278 | N | 0
2025-10-11 | 17 | 2031-10-11 17:00 | 5.12 | 6.4404 | N | 0
2025-10-11 | 18 | 2031-10-11 18:00 | 5.11 | 6.4278 | N | 0
2025-10-11 | 19 | 2031-10-11 19:00 | 5.02 | 6.3146 | N | 0
2025-10-11 | 20 | 2031-10-11 20:00 | 5.18 | 6.5158 | N | 0
2025-10-11 | 21 | 2031-10-11 21:00 | 5.24 | 6.5913 | N | 0
2025-10-11 | 22 | 2031-10-11 22:00 | 5.16 | 6.4907 | N | 0
2025-10-11 | 23 | 2031-10-11 23:00 | 5.03 | 6.3271 | N | 0
2025-10-12 | 00 | 2031-10-12 | 4.93 | 6.2014 | N | 0
2025-10-12 | 01 | 2031-10-12 01:00 | 4.7 | 5.912 | N | 0
2025-10-12 | 02 | 2031-10-12 02:00 | 4.48 | 5.6353 | N | 0
2025-10-12 | 03 | 2031-10-12 03:00 | 4.06 | 5.107 | N | 0
2025-10-12 | 04 | 2031-10-12 04:00 | 3.7 | 4.6542 | N | 0
2025-10-12 | 05 | 2031-10-12 05:00 | 3.45 | 4.3397 | N | 0
2025-10-12 | 06 | 2031-10-12 06:00 | 3.25 | 4.0881 | N | 0
2025-10-12 | 07 | 2031-10-12 07:00 | 3.1 | 3.8994 | N | 0
2025-10-12 | 08 | 2031-10-12 08:00 | 2.99 | 3.7611 | N | 0
2025-10-12 | 09 | 2031-10-12 09:00 | 3.06 | 3.8491 | N | 0
2025-10-12 | 10 | 2031-10-12 10:00 | 3.16 | 3.9749 | N | 0
2025-10-12 | 11 | 2031-10-12 11:00 | 3.51 | 4.4152 | N | 0
2025-10-12 | 12 | 2031-10-12 12:00 | 3.96 | 4.9812 | N | 0
2025-10-12 | 13 | 2031-10-12 13:00 | 4.3 | 5.4089 | N | 0
2025-10-12 | 14 | 2031-10-12 14:00 | 4.77 | 6.0001 | N | 0
2025-10-12 | 15 | 2031-10-12 15:00 | 5.09 | 6.4026 | N | 0
2025-10-12 | 16 | 2031-10-12 16:00 | 5.07 | 6.3775 | N | 0
2025-10-12 | 17 | 2031-10-12 17:00 | 5.11 | 6.4278 | N | 0
2025-10-12 | 18 | 2031-10-12 18:00 | 5.04 | 6.3397 | N | 0
2025-10-12 | 19 | 2031-10-12 19:00 | 5.24 | 6.5913 | N | 0
2025-10-12 | 20 | 2031-10-12 20:00 | 5.17 | 6.5032 | N | 0
2025-10-12 | 21 | 2031-10-12 21:00 | 5.09 | 6.4026 | N | 0
2025-10-12 | 22 | 2031-10-12 22:00 | 4.95 | 6.2265 | N | 0
2025-10-12 | 23 | 2031-10-12 23:00 | 4.88 | 6.1385 | N | 0
2025-10-13 | 00 | 2031-10-13 | 4.88 | 6.1385 | N | 0
2025-10-13 | 01 | 2031-10-13 01:00 | 4.68 | 5.8869 | N | 0
2025-10-13 | 02 | 2031-10-13 02:00 | 4.45 | 5.5976 | N | 0
2025-10-13 | 03 | 2031-10-13 03:00 | 4.13 | 5.1951 | N | 0
2025-10-13 | 04 | 2031-10-13 04:00 | 3.67 | 4.6164 | N | 0
2025-10-13 | 05 | 2031-10-13 05:00 | 3.39 | 4.2642 | N | 0
2025-10-13 | 06 | 2031-10-13 06:00 | 3.1 | 3.8994 | N | 0
2025-10-13 | 07 | 2031-10-13 07:00 | 3.01 | 3.7862 | N | 0
2025-10-13 | 08 | 2031-10-13 08:00 | 2.95 | 3.7108 | N | 0
2025-10-13 | 09 | 2031-10-13 09:00 | 3.03 | 3.8114 | N | 0
2025-10-13 | 10 | 2031-10-13 10:00 | 3.25 | 4.0881 | N | 0
2025-10-13 | 11 | 2031-10-13 11:00 | 3.55 | 4.4655 | N | 0
2025-10-13 | 12 | 2031-10-13 12:00 | 4.1 | 5.1573 | N | 0
2025-10-13 | 13 | 2031-10-13 13:00 | 4.44 | 5.585 | N | 0
2025-10-13 | 14 | 2031-10-13 14:00 | 4.84 | 6.0881 | N | 0
2025-10-13 | 15 | 2031-10-13 15:00 | 5.18 | 6.5158 | N | 0
2025-10-13 | 16 | 2031-10-13 16:00 | 5.39 | 6.78 | N | 0
2025-10-13 | 17 | 2031-10-13 17:00 | 5.38 | 6.7674 | N | 0
2025-10-13 | 18 | 2031-10-13 18:00 | 5.35 | 6.7297 | N | 0
2025-10-13 | 19 | 2031-10-13 19:00 | 5.43 | 6.8303 | N | 0
2025-10-13 | 20 | 2031-10-13 20:00 | 5.68 | 7.1448 | N | 0
2025-10-13 | 21 | 2031-10-13 21:00 | 5.74 | 7.2202 | N | 0
2025-10-13 | 22 | 2031-10-13 22:00 | 5.51 | 6.9309 | N | 0
2025-10-13 | 23 | 2031-10-13 23:00 | 5.64 | 7.0945 | N | 0
2025-10-14 | 00 | 2031-10-14 | 5.51 | 6.9309 | N | 0
2025-10-14 | 01 | 2031-10-14 01:00 | 5.13 | 6.4529 | N | 0
2025-10-14 | 02 | 2031-10-14 02:00 | 4.66 | 5.8617 | N | 0
2025-10-14 | 03 | 2031-10-14 03:00 | 3.91 | 4.9183 | N | 0
2025-10-14 | 04 | 2031-10-14 04:00 | 3.47 | 4.3648 | N | 0
2025-10-14 | 05 | 2031-10-14 05:00 | 3.15 | 3.9623 | N | 0
2025-10-14 | 06 | 2031-10-14 06:00 | 3.02 | 3.7988 | N | 0
2025-10-14 | 07 | 2031-10-14 07:00 | 2.91 | 3.6604 | N | 0
2025-10-14 | 08 | 2031-10-14 08:00 | 2.95 | 3.7108 | N | 0
2025-10-14 | 09 | 2031-10-14 09:00 | 3.1 | 3.8994 | N | 0
2025-10-14 | 10 | 2031-10-14 10:00 | 3.52 | 4.4277 | N | 0
2025-10-14 | 11 | 2031-10-14 11:00 | 4.09 | 5.1447 | N | 0
2025-10-14 | 12 | 2031-10-14 12:00 | 4.27 | 5.3712 | N | 0
2025-10-14 | 13 | 2031-10-14 13:00 | 4.28 | 5.3837 | N | 0
2025-10-14 | 14 | 2031-10-14 14:00 | 4.32 | 5.434 | N | 0
2025-10-14 | 15 | 2031-10-14 15:00 | 4.4 | 5.5347 | N | 0
2025-10-14 | 16 | 2031-10-14 16:00 | 4.62 | 5.8114 | N | 0
2025-10-14 | 17 | 2031-10-14 17:00 | 4.63 | 5.824 | N | 0
2025-10-14 | 18 | 2031-10-14 18:00 | 4.66 | 5.8617 | N | 0
2025-10-14 | 19 | 2031-10-14 19:00 | 4.76 | 5.9875 | N | 0
2025-10-14 | 20 | 2031-10-14 20:00 | 5.18 | 6.5158 | N | 0
2025-10-14 | 21 | 2031-10-14 21:00 | 5.46 | 6.868 | N | 0
2025-10-14 | 22 | 2031-10-14 22:00 | 5.48 | 6.8932 | N | 0
2025-10-14 | 23 | 2031-10-14 23:00 | 5.55 | 6.9812 | N | 0
2025-10-15 | 00 | 2031-10-15 | 5.47 | 6.8806 | N | 0
2025-10-15 | 01 | 2031-10-15 01:00 | 5.15 | 6.4781 | N | 0
2025-10-15 | 02 | 2031-10-15 02:00 | 4.65 | 5.8491 | N | 0
2025-10-15 | 03 | 2031-10-15 03:00 | 4.02 | 5.0567 | N | 0
2025-10-15 | 04 | 2031-10-15 04:00 | 3.49 | 4.39 | N | 0
2025-10-15 | 05 | 2031-10-15 05:00 | 3.22 | 4.0504 | N | 0
2025-10-15 | 06 | 2031-10-15 06:00 | 3 | 3.7736 | N | 0
2025-10-15 | 07 | 2031-10-15 07:00 | 2.9 | 3.6479 | N | 0
2025-10-15 | 08 | 2031-10-15 08:00 | 2.91 | 3.6604 | N | 0
2025-10-15 | 09 | 2031-10-15 09:00 | 3.11 | 3.912 | N | 0
2025-10-15 | 10 | 2031-10-15 10:00 | 3.68 | 4.629 | N | 0
2025-10-15 | 11 | 2031-10-15 11:00 | 4.16 | 5.2328 | N | 0
2025-10-15 | 12 | 2031-10-15 12:00 | 4.31 | 5.4215 | N | 0
2025-10-15 | 13 | 2031-10-15 13:00 | 4.33 | 5.4466 | N | 0
2025-10-15 | 14 | 2031-10-15 14:00 | 4.34 | 5.4592 | N | 0
2025-10-15 | 15 | 2031-10-15 15:00 | 4.39 | 5.5221 | N | 0
2025-10-15 | 16 | 2031-10-15 16:00 | 4.47 | 5.6227 | N | 0
2025-10-15 | 17 | 2031-10-15 17:00 | 4.37 | 5.4969 | N | 0
2025-10-15 | 18 | 2031-10-15 18:00 | 4.38 | 5.5095 | N | 0
2025-10-15 | 19 | 2031-10-15 19:00 | 4.49 | 5.6479 | N | 0
2025-10-15 | 20 | 2031-10-15 20:00 | 5.09 | 6.4026 | N | 0
2025-10-15 | 21 | 2031-10-15 21:00 | 5.28 | 6.6416 | N | 0
2025-10-15 | 22 | 2031-10-15 22:00 | 5.3 | 6.6668 | N | 0
2025-10-15 | 23 | 2031-10-15 23:00 | 5.41 | 6.8051 | N | 0
2025-10-16 | 00 | 2031-10-16 | 5.38 | 6.7674 | N | 0
2025-10-16 | 01 | 2031-10-16 01:00 | 5.08 | 6.39 | N | 0
2025-10-16 | 02 | 2031-10-16 02:00 | 4.67 | 5.8743 | N | 0
2025-10-16 | 03 | 2031-10-16 03:00 | 4.11 | 5.1699 | N | 0
2025-10-16 | 04 | 2031-10-16 04:00 | 3.61 | 4.541 | N | 0
2025-10-16 | 05 | 2031-10-16 05:00 | 3.29 | 4.1384 | N | 0
2025-10-16 | 06 | 2031-10-16 06:00 | 3.12 | 3.9246 | N | 0
2025-10-16 | 07 | 2031-10-16 07:00 | 3.07 | 3.8617 | N | 0
2025-10-16 | 08 | 2031-10-16 08:00 | 3.05 | 3.8365 | N | 0
2025-10-16 | 09 | 2031-10-16 09:00 | 3.39 | 4.2642 | N | 0
2025-10-16 | 10 | 2031-10-16 10:00 | 3.98 | 5.0064 | N | 0
2025-10-16 | 11 | 2031-10-16 11:00 | 4.46 | 5.6102 | N | 0
2025-10-16 | 12 | 2031-10-16 12:00 | 4.49 | 5.6479 | N | 0
2025-10-16 | 13 | 2031-10-16 13:00 | 4.45 | 5.5976 | N | 0
2025-10-16 | 14 | 2031-10-16 14:00 | 4.49 | 5.6479 | N | 0
2025-10-16 | 15 | 2031-10-16 15:00 | 4.47 | 5.6227 | N | 0
2025-10-16 | 16 | 2031-10-16 16:00 | 4.59 | 5.7737 | N | 0
2025-10-16 | 17 | 2031-10-16 17:00 | 4.54 | 5.7108 | N | 0
2025-10-16 | 18 | 2031-10-16 18:00 | 4.43 | 5.5724 | N | 0
2025-10-16 | 19 | 2031-10-16 19:00 | 4.6 | 5.7863 | N | 0
2025-10-16 | 20 | 2031-10-16 20:00 | 5.17 | 6.5032 | N | 0
2025-10-16 | 21 | 2031-10-16 21:00 | 5.39 | 6.78 | N | 0
2025-10-16 | 22 | 2031-10-16 22:00 | 5.36 | 6.7422 | N | 0
2025-10-16 | 23 | 2031-10-16 23:00 | 5.5 | 6.9183 | N | 0
2025-10-17 | 00 | 2031-10-17 | 5.5 | 6.9183 | N | 0
2025-10-17 | 01 | 2031-10-17 01:00 | 5.2 | 6.541 | N | 0
2025-10-17 | 02 | 2031-10-17 02:00 | 4.83 | 6.0756 | N | 0
2025-10-17 | 03 | 2031-10-17 03:00 | 4.24 | 5.3334 | N | 0
2025-10-17 | 04 | 2031-10-17 04:00 | 3.76 | 4.7296 | N | 0
2025-10-17 | 05 | 2031-10-17 05:00 | 3.47 | 4.3648 | N | 0
2025-10-17 | 06 | 2031-10-17 06:00 | 3.3 | 4.151 | N | 0
2025-10-17 | 07 | 2031-10-17 07:00 | 3.17 | 3.9875 | N | 0
2025-10-17 | 08 | 2031-10-17 08:00 | 3.12 | 3.9246 | N | 0
2025-10-17 | 09 | 2031-10-17 09:00 | 3.44 | 4.3271 | N | 0
2025-10-17 | 10 | 2031-10-17 10:00 | 3.97 | 4.9938 | N | 0
2025-10-17 | 11 | 2031-10-17 11:00 | 4.5 | 5.6605 | N | 0
2025-10-17 | 12 | 2031-10-17 12:00 | 4.65 | 5.8491 | N | 0
2025-10-17 | 13 | 2031-10-17 13:00 | 4.76 | 5.9875 | N | 0
2025-10-17 | 14 | 2031-10-17 14:00 | 4.8 | 6.0378 | N | 0
2025-10-17 | 15 | 2031-10-17 15:00 | 4.83 | 6.0756 | N | 0
2025-10-17 | 16 | 2031-10-17 16:00 | 4.83 | 6.0756 | N | 0
2025-10-17 | 17 | 2031-10-17 17:00 | 5 | 6.2894 | N | 0
2025-10-17 | 18 | 2031-10-17 18:00 | 4.97 | 6.2517 | N | 0
2025-10-17 | 19 | 2031-10-17 19:00 | 5 | 6.2894 | N | 0
2025-10-17 | 20 | 2031-10-17 20:00 | 5.31 | 6.6794 | N | 0
2025-10-17 | 21 | 2031-10-17 21:00 | 5.64 | 7.0945 | N | 0
2025-10-17 | 22 | 2031-10-17 22:00 | 5.55 | 6.9812 | N | 0
2025-10-17 | 23 | 2031-10-17 23:00 | 5.58 | 7.019 | N | 0
2025-10-18 | 00 | 2031-10-18 | 5.4 | 6.7926 | N | 0
2025-10-18 | 01 | 2031-10-18 01:00 | 5.17 | 6.5032 | N | 0
2025-10-18 | 02 | 2031-10-18 02:00 | 4.81 | 6.0504 | N | 0
2025-10-18 | 03 | 2031-10-18 03:00 | 4.24 | 5.3334 | N | 0
2025-10-18 | 04 | 2031-10-18 04:00 | 3.73 | 4.6919 | N | 0
2025-10-18 | 05 | 2031-10-18 05:00 | 3.5 | 4.4026 | N | 0
2025-10-18 | 06 | 2031-10-18 06:00 | 3.29 | 4.1384 | N | 0
2025-10-18 | 07 | 2031-10-18 07:00 | 3.09 | 3.8869 | N | 0
2025-10-18 | 08 | 2031-10-18 08:00 | 3.03 | 3.8114 | N | 0
2025-10-18 | 09 | 2031-10-18 09:00 | 3.04 | 3.824 | N | 0
2025-10-18 | 10 | 2031-10-18 10:00 | 3.2 | 4.0252 | N | 0
2025-10-18 | 11 | 2031-10-18 11:00 | 3.57 | 4.4906 | N | 0
2025-10-18 | 12 | 2031-10-18 12:00 | 4.07 | 5.1196 | N | 0
2025-10-18 | 13 | 2031-10-18 13:00 | 4.29 | 5.3963 | N | 0
2025-10-18 | 14 | 2031-10-18 14:00 | 4.41 | 5.5473 | N | 0
2025-10-18 | 15 | 2031-10-18 15:00 | 4.52 | 5.6856 | N | 0
2025-10-18 | 16 | 2031-10-18 16:00 | 4.54 | 5.7108 | N | 0
2025-10-18 | 17 | 2031-10-18 17:00 | 4.49 | 5.6479 | N | 0
2025-10-18 | 18 | 2031-10-18 18:00 | 4.52 | 5.6856 | N | 0
2025-10-18 | 19 | 2031-10-18 19:00 | 4.55 | 5.7234 | N | 0
2025-10-18 | 20 | 2031-10-18 20:00 | 4.95 | 6.2265 | N | 0
2025-10-18 | 21 | 2031-10-18 21:00 | 5.03 | 6.3271 | N | 0
2025-10-18 | 22 | 2031-10-18 22:00 | 5.15 | 6.4781 | N | 0
2025-10-18 | 23 | 2031-10-18 23:00 | 5.05 | 6.3523 | N | 0
2025-10-19 | 00 | 2031-10-19 | 4.98 | 6.2642 | N | 0
2025-10-19 | 01 | 2031-10-19 01:00 | 4.67 | 5.8743 | N | 0
2025-10-19 | 02 | 2031-10-19 02:00 | 4.35 | 5.4718 | N | 0
2025-10-19 | 03 | 2031-10-19 03:00 | 3.98 | 5.0064 | N | 0
2025-10-19 | 04 | 2031-10-19 04:00 | 3.75 | 4.7171 | N | 0
2025-10-19 | 05 | 2031-10-19 05:00 | 3.35 | 4.2139 | N | 0
2025-10-19 | 06 | 2031-10-19 06:00 | 3.12 | 3.9246 | N | 0
2025-10-19 | 07 | 2031-10-19 07:00 | 2.95 | 3.7108 | N | 0
2025-10-19 | 08 | 2031-10-19 08:00 | 2.88 | 3.6227 | N | 0
2025-10-19 | 09 | 2031-10-19 09:00 | 2.89 | 3.6353 | N | 0
2025-10-19 | 10 | 2031-10-19 10:00 | 3.09 | 3.8869 | N | 0
2025-10-19 | 11 | 2031-10-19 11:00 | 3.3 | 4.151 | N | 0
2025-10-19 | 12 | 2031-10-19 12:00 | 3.8 | 4.7799 | N | 0
2025-10-19 | 13 | 2031-10-19 13:00 | 4.2 | 5.2831 | N | 0
2025-10-19 | 14 | 2031-10-19 14:00 | 4.54 | 5.7108 | N | 0
2025-10-19 | 15 | 2031-10-19 15:00 | 4.86 | 6.1133 | N | 0
2025-10-19 | 16 | 2031-10-19 16:00 | 4.9 | 6.1636 | N | 0
2025-10-19 | 17 | 2031-10-19 17:00 | 5.07 | 6.3775 | N | 0
2025-10-19 | 18 | 2031-10-19 18:00 | 5.13 | 6.4529 | N | 0
2025-10-19 | 19 | 2031-10-19 19:00 | 5.26 | 6.6165 | N | 0
2025-10-19 | 20 | 2031-10-19 20:00 | 5.75 | 7.2328 | N | 0
2025-10-19 | 21 | 2031-10-19 21:00 | 6.03 | 7.585 | N | 0
2025-10-19 | 22 | 2031-10-19 22:00 | 5.76 | 7.2454 | N | 0
2025-10-19 | 23 | 2031-10-19 23:00 | 5.68 | 7.1448 | N | 0
2025-10-20 | 00 | 2031-10-20 | 5.54 | 6.9687 | N | 0
2025-10-20 | 01 | 2031-10-20 01:00 | 5.23 | 6.5787 | N | 0
2025-10-20 | 02 | 2031-10-20 02:00 | 4.72 | 5.9372 | N | 0
2025-10-20 | 03 | 2031-10-20 03:00 | 4.11 | 5.1699 | N | 0
2025-10-20 | 04 | 2031-10-20 04:00 | 3.66 | 4.6038 | N | 0
2025-10-20 | 05 | 2031-10-20 05:00 | 3.33 | 4.1887 | N | 0
2025-10-20 | 06 | 2031-10-20 06:00 | 3.02 | 3.7988 | N | 0
2025-10-20 | 07 | 2031-10-20 07:00 | 2.85 | 3.585 | N | 0
2025-10-20 | 08 | 2031-10-20 08:00 | 2.91 | 3.6604 | N | 0
2025-10-20 | 09 | 2031-10-20 09:00 | 3.07 | 3.8617 | N | 0
2025-10-20 | 10 | 2031-10-20 10:00 | 3.67 | 4.6164 | N | 0
2025-10-20 | 11 | 2031-10-20 11:00 | 4.21 | 5.2957 | N | 0
2025-10-20 | 12 | 2031-10-20 12:00 | 4.34 | 5.4592 | N | 0
2025-10-20 | 13 | 2031-10-20 13:00 | 4.49 | 5.6479 | N | 0
2025-10-20 | 14 | 2031-10-20 14:00 | 4.54 | 5.7108 | N | 0
2025-10-20 | 15 | 2031-10-20 15:00 | 4.56 | 5.7359 | N | 0
2025-10-20 | 16 | 2031-10-20 16:00 | 4.72 | 5.9372 | N | 0
2025-10-20 | 17 | 2031-10-20 17:00 | 4.72 | 5.9372 | N | 0
2025-10-20 | 18 | 2031-10-20 18:00 | 4.61 | 5.7988 | N | 0
2025-10-20 | 19 | 2031-10-20 19:00 | 4.78 | 6.0127 | N | 0
2025-10-20 | 20 | 2031-10-20 20:00 | 5.27 | 6.629 | N | 0
2025-10-20 | 21 | 2031-10-20 21:00 | 5.5 | 6.9183 | N | 0
2025-10-20 | 22 | 2031-10-20 22:00 | 5.52 | 6.9435 | N | 0
2025-10-20 | 23 | 2031-10-20 23:00 | 5.52 | 6.9435 | N | 0
2025-10-21 | 00 | 2031-10-21 | 5.42 | 6.8177 | N | 0
2025-10-21 | 01 | 2031-10-21 01:00 | 5.2 | 6.541 | N | 0
2025-10-21 | 02 | 2031-10-21 02:00 | 4.79 | 6.0253 | N | 0
2025-10-21 | 03 | 2031-10-21 03:00 | 4.18 | 5.2579 | N | 0
2025-10-21 | 04 | 2031-10-21 04:00 | 3.71 | 4.6667 | N | 0
2025-10-21 | 05 | 2031-10-21 05:00 | 3.44 | 4.3271 | N | 0
2025-10-21 | 06 | 2031-10-21 06:00 | 3.23 | 4.063 | N | 0
2025-10-21 | 07 | 2031-10-21 07:00 | 3.1 | 3.8994 | N | 0
2025-10-21 | 08 | 2031-10-21 08:00 | 3.13 | 3.9372 | N | 0
2025-10-21 | 09 | 2031-10-21 09:00 | 3.45 | 4.3397 | N | 0
2025-10-21 | 10 | 2031-10-21 10:00 | 3.97 | 4.9938 | N | 0
2025-10-21 | 11 | 2031-10-21 11:00 | 4.5 | 5.6605 | N | 0
2025-10-21 | 12 | 2031-10-21 12:00 | 4.5 | 5.6605 | N | 0
2025-10-21 | 13 | 2031-10-21 13:00 | 4.49 | 5.6479 | N | 0
2025-10-21 | 14 | 2031-10-21 14:00 | 4.61 | 5.7988 | N | 0
2025-10-21 | 15 | 2031-10-21 15:00 | 4.63 | 5.824 | N | 0
2025-10-21 | 16 | 2031-10-21 16:00 | 4.66 | 5.8617 | N | 0
2025-10-21 | 17 | 2031-10-21 17:00 | 4.74 | 5.9624 | N | 0
2025-10-21 | 18 | 2031-10-21 18:00 | 4.64 | 5.8366 | N | 0
2025-10-21 | 19 | 2031-10-21 19:00 | 4.65 | 5.8491 | N | 0
2025-10-21 | 20 | 2031-10-21 20:00 | 5.19 | 6.5284 | N | 0
2025-10-21 | 21 | 2031-10-21 21:00 | 5.47 | 6.8806 | N | 0
2025-10-21 | 22 | 2031-10-21 22:00 | 5.57 | 7.0064 | N | 0
2025-10-21 | 23 | 2031-10-21 23:00 | 5.53 | 6.9561 | N | 0
2025-10-22 | 00 | 2031-10-22 | 5.33 | 6.7045 | N | 0
2025-10-22 | 01 | 2031-10-22 01:00 | 5.24 | 6.5913 | N | 0
2025-10-22 | 02 | 2031-10-22 02:00 | 4.6 | 5.7863 | N | 0
2025-10-22 | 03 | 2031-10-22 03:00 | 4.05 | 5.0944 | N | 0
2025-10-22 | 04 | 2031-10-22 04:00 | 3.56 | 4.4781 | N | 0
2025-10-22 | 05 | 2031-10-22 05:00 | 3.37 | 4.2391 | N | 0
2025-10-22 | 06 | 2031-10-22 06:00 | 3.16 | 3.9749 | N | 0
2025-10-22 | 07 | 2031-10-22 07:00 | 3.09 | 3.8869 | N | 0
2025-10-22 | 08 | 2031-10-22 08:00 | 3.07 | 3.8617 | N | 0
2025-10-22 | 09 | 2031-10-22 09:00 | 3.37 | 4.2391 | N | 0
2025-10-22 | 10 | 2031-10-22 10:00 | 3.79 | 4.7674 | N | 0
2025-10-22 | 11 | 2031-10-22 11:00 | 4.33 | 5.4466 | N | 0
2025-10-22 | 12 | 2031-10-22 12:00 | 4.39 | 5.5221 | N | 0
2025-10-22 | 13 | 2031-10-22 13:00 | 4.43 | 5.5724 | N | 0
2025-10-22 | 14 | 2031-10-22 14:00 | 4.45 | 5.5976 | N | 0
2025-10-22 | 15 | 2031-10-22 15:00 | 4.52 | 5.6856 | N | 0
2025-10-22 | 16 | 2031-10-22 16:00 | 4.45 | 5.5976 | N | 0
2025-10-22 | 17 | 2031-10-22 17:00 | 4.56 | 5.7359 | N | 0
2025-10-22 | 18 | 2031-10-22 18:00 | 4.41 | 5.5473 | N | 0
2025-10-22 | 19 | 2031-10-22 19:00 | 4.67 | 5.8743 | N | 0
2025-10-22 | 20 | 2031-10-22 20:00 | 5.28 | 6.6416 | N | 0
2025-10-22 | 21 | 2031-10-22 21:00 | 5.56 | 6.9938 | N | 0
2025-10-22 | 22 | 2031-10-22 22:00 | 5.43 | 6.8303 | N | 0
2025-10-22 | 23 | 2031-10-22 23:00 | 5.51 | 6.9309 | N | 0
2025-10-23 | 00 | 2031-10-23 | 5.58 | 7.019 | N | 0
2025-10-23 | 01 | 2031-10-23 01:00 | 5.2 | 6.541 | N | 0
2025-10-23 | 02 | 2031-10-23 02:00 | 4.73 | 5.9498 | N | 0
2025-10-23 | 03 | 2031-10-23 03:00 | 4.16 | 5.2328 | N | 0
2025-10-23 | 04 | 2031-10-23 04:00 | 3.81 | 4.7925 | N | 0
2025-10-23 | 05 | 2031-10-23 05:00 | 3.53 | 4.4403 | N | 0
2025-10-23 | 06 | 2031-10-23 06:00 | 3.25 | 4.0881 | N | 0
2025-10-23 | 07 | 2031-10-23 07:00 | 3.18 | 4.0001 | N | 0
2025-10-23 | 08 | 2031-10-23 08:00 | 3.16 | 3.9749 | N | 0
2025-10-23 | 09 | 2031-10-23 09:00 | 3.51 | 4.4152 | N | 0
2025-10-23 | 10 | 2031-10-23 10:00 | 3.98 | 5.0064 | N | 0
2025-10-23 | 11 | 2031-10-23 11:00 | 4.56 | 5.7359 | N | 0
2025-10-23 | 12 | 2031-10-23 12:00 | 4.59 | 5.7737 | N | 0
2025-10-23 | 13 | 2031-10-23 13:00 | 4.57 | 5.7485 | N | 0
2025-10-23 | 14 | 2031-10-23 14:00 | 4.58 | 5.7611 | N | 0
2025-10-23 | 15 | 2031-10-23 15:00 | 4.65 | 5.8491 | N | 0
2025-10-23 | 16 | 2031-10-23 16:00 | 4.7 | 5.912 | N | 0
2025-10-23 | 17 | 2031-10-23 17:00 | 4.63 | 5.824 | N | 0
2025-10-23 | 18 | 2031-10-23 18:00 | 4.57 | 5.7485 | N | 0
2025-10-23 | 19 | 2031-10-23 19:00 | 4.67 | 5.8743 | N | 0
2025-10-23 | 20 | 2031-10-23 20:00 | 5.29 | 6.6542 | N | 0
2025-10-23 | 21 | 2031-10-23 21:00 | 5.55 | 6.9812 | N | 0
2025-10-23 | 22 | 2031-10-23 22:00 | 5.59 | 7.0316 | N | 0
2025-10-23 | 23 | 2031-10-23 23:00 | 5.58 | 7.019 | N | 0
2025-10-24 | 00 | 2031-10-24 | 5.41 | 6.8051 | N | 0
2025-10-24 | 01 | 2031-10-24 01:00 | 5.2 | 6.541 | N | 0
2025-10-24 | 02 | 2031-10-24 02:00 | 4.81 | 6.0504 | N | 0
2025-10-24 | 03 | 2031-10-24 03:00 | 4.16 | 5.2328 | N | 0
2025-10-24 | 04 | 2031-10-24 04:00 | 3.74 | 4.7045 | N | 0
2025-10-24 | 05 | 2031-10-24 05:00 | 3.49 | 4.39 | N | 0
2025-10-24 | 06 | 2031-10-24 06:00 | 3.35 | 4.2139 | N | 0
2025-10-24 | 07 | 2031-10-24 07:00 | 3.23 | 4.063 | N | 0
2025-10-24 | 08 | 2031-10-24 08:00 | 3.24 | 4.0755 | N | 0
2025-10-24 | 09 | 2031-10-24 09:00 | 3.45 | 4.3397 | N | 0
2025-10-24 | 10 | 2031-10-24 10:00 | 3.91 | 4.9183 | N | 0
2025-10-24 | 11 | 2031-10-24 11:00 | 4.23 | 5.3208 | N | 0
2025-10-24 | 12 | 2031-10-24 12:00 | 4.54 | 5.7108 | N | 0
2025-10-24 | 13 | 2031-10-24 13:00 | 4.6 | 5.7863 | N | 0
2025-10-24 | 14 | 2031-10-24 14:00 | 4.58 | 5.7611 | N | 0
2025-10-24 | 15 | 2031-10-24 15:00 | 4.79 | 6.0253 | N | 0
2025-10-24 | 16 | 2031-10-24 16:00 | 4.86 | 6.1133 | N | 0
2025-10-24 | 17 | 2031-10-24 17:00 | 4.76 | 5.9875 | N | 0
2025-10-24 | 18 | 2031-10-24 18:00 | 4.78 | 6.0127 | N | 0
2025-10-24 | 19 | 2031-10-24 19:00 | 4.7 | 5.912 | N | 0
2025-10-24 | 20 | 2031-10-24 20:00 | 5.1 | 6.4152 | N | 0
2025-10-24 | 21 | 2031-10-24 21:00 | 5.32 | 6.6919 | N | 0
2025-10-24 | 22 | 2031-10-24 22:00 | 5.36 | 6.7422 | N | 0
2025-10-24 | 23 | 2031-10-24 23:00 | 5.48 | 6.8932 | N | 0
2025-10-25 | 00 | 2031-10-25 | 5.26 | 6.6165 | N | 0
2025-10-25 | 01 | 2031-10-25 01:00 | 5.07 | 6.3775 | N | 0
2025-10-25 | 02 | 2031-10-25 02:00 | 4.82 | 6.063 | N | 0
2025-10-25 | 03 | 2031-10-25 03:00 | 4.3 | 5.4089 | N | 0
2025-10-25 | 04 | 2031-10-25 04:00 | 4.15 | 5.2202 | N | 0
2025-10-25 | 05 | 2031-10-25 05:00 | 3.75 | 4.7171 | N | 0
2025-10-25 | 06 | 2031-10-25 06:00 | 3.5 | 4.4026 | N | 0
2025-10-25 | 07 | 2031-10-25 07:00 | 3.39 | 4.2642 | N | 0
2025-10-25 | 08 | 2031-10-25 08:00 | 3.31 | 4.1636 | N | 0
2025-10-25 | 09 | 2031-10-25 09:00 | 3.42 | 4.302 | N | 0
2025-10-25 | 10 | 2031-10-25 10:00 | 3.61 | 4.541 | N | 0
2025-10-25 | 11 | 2031-10-25 11:00 | 3.98 | 5.0064 | N | 0
2025-10-25 | 12 | 2031-10-25 12:00 | 4.44 | 5.585 | N | 0
2025-10-25 | 13 | 2031-10-25 13:00 | 4.78 | 6.0127 | N | 0
2025-10-25 | 14 | 2031-10-25 14:00 | 4.82 | 6.063 | N | 0
2025-10-25 | 15 | 2031-10-25 15:00 | 4.9 | 6.1636 | N | 0
2025-10-25 | 16 | 2031-10-25 16:00 | 4.92 | 6.1888 | N | 0
2025-10-25 | 17 | 2031-10-25 17:00 | 5.14 | 6.4655 | N | 0
2025-10-25 | 18 | 2031-10-25 18:00 | 5.07 | 6.3775 | N | 0
2025-10-25 | 19 | 2031-10-25 19:00 | 5 | 6.2894 | N | 0
2025-10-25 | 20 | 2031-10-25 20:00 | 5.18 | 6.5158 | N | 0
2025-10-25 | 21 | 2031-10-25 21:00 | 5.35 | 6.7297 | N | 0
2025-10-25 | 22 | 2031-10-25 22:00 | 5.5 | 6.9183 | N | 0
2025-10-25 | 23 | 2031-10-25 23:00 | 5.53 | 6.9561 | N | 0
2025-10-26 | 00 | 2031-10-26 | 5.3 | 6.6668 | N | 0
2025-10-26 | 01 | 2031-10-26 01:00 | 5.05 | 6.3523 | N | 0
2025-10-26 | 02 | 2031-10-26 02:00 | 4.76 | 5.9875 | N | 0
2025-10-26 | 03 | 2031-10-26 03:00 | 4.43 | 5.5724 | N | 0
2025-10-26 | 04 | 2031-10-26 04:00 | 4.16 | 5.2328 | N | 0
2025-10-26 | 05 | 2031-10-26 05:00 | 3.77 | 4.7422 | N | 0
2025-10-26 | 06 | 2031-10-26 06:00 | 3.6 | 4.5284 | N | 0
2025-10-26 | 07 | 2031-10-26 07:00 | 3.5 | 4.4026 | N | 0
2025-10-26 | 08 | 2031-10-26 08:00 | 3.45 | 4.3397 | N | 0
2025-10-26 | 09 | 2031-10-26 09:00 | 3.52 | 4.4277 | N | 0
2025-10-26 | 10 | 2031-10-26 10:00 | 3.7 | 4.6542 | N | 0
2025-10-26 | 11 | 2031-10-26 11:00 | 4.12 | 5.1825 | N | 0
2025-10-26 | 12 | 2031-10-26 12:00 | 4.51 | 5.673 | N | 0
2025-10-26 | 13 | 2031-10-26 13:00 | 4.85 | 6.1007 | N | 0
2025-10-26 | 14 | 2031-10-26 14:00 | 4.92 | 6.1888 | N | 0
2025-10-26 | 15 | 2031-10-26 15:00 | 5.08 | 6.39 | N | 0
2025-10-26 | 16 | 2031-10-26 16:00 | 5.11 | 6.4278 | N | 0
2025-10-26 | 17 | 2031-10-26 17:00 | 5.28 | 6.6416 | N | 0
2025-10-26 | 18 | 2031-10-26 18:00 | 5.22 | 6.5661 | N | 0
2025-10-26 | 19 | 2031-10-26 19:00 | 5.32 | 6.6919 | N | 0
2025-10-26 | 20 | 2031-10-26 20:00 | 5.71 | 7.1825 | N | 0
2025-10-26 | 21 | 2031-10-26 21:00 | 6.15 | 7.736 | N | 0
2025-10-26 | 22 | 2031-10-26 22:00 | 6.04 | 7.5976 | N | 0
2025-10-26 | 23 | 2031-10-26 23:00 | 5.95 | 7.4844 | N | 0
2025-10-27 | 00 | 2031-10-27 | 5.86 | 7.3712 | N | 0
2025-10-27 | 01 | 2031-10-27 01:00 | 5.71 | 7.1825 | N | 0
2025-10-27 | 02 | 2031-10-27 02:00 | 5.1 | 6.4152 | N | 0
2025-10-27 | 03 | 2031-10-27 03:00 | 4.54 | 5.7108 | N | 0
2025-10-27 | 04 | 2031-10-27 04:00 | 4.03 | 5.0693 | N | 0
2025-10-27 | 05 | 2031-10-27 05:00 | 3.67 | 4.6164 | N | 0
2025-10-27 | 06 | 2031-10-27 06:00 | 3.54 | 4.4529 | N | 0
2025-10-27 | 07 | 2031-10-27 07:00 | 3.44 | 4.3271 | N | 0
2025-10-27 | 08 | 2031-10-27 08:00 | 3.55 | 4.4655 | N | 0
2025-10-27 | 09 | 2031-10-27 09:00 | 3.83 | 4.8177 | N | 0
2025-10-27 | 10 | 2031-10-27 10:00 | 4.45 | 5.5976 | N | 0
2025-10-27 | 11 | 2031-10-27 11:00 | 4.9 | 6.1636 | N | 0
2025-10-27 | 12 | 2031-10-27 12:00 | 4.95 | 6.2265 | N | 0
2025-10-27 | 13 | 2031-10-27 13:00 | 4.87 | 6.1259 | N | 0
2025-10-27 | 14 | 2031-10-27 14:00 | 4.86 | 6.1133 | N | 0
2025-10-27 | 15 | 2031-10-27 15:00 | 4.88 | 6.1385 | N | 0
2025-10-27 | 16 | 2031-10-27 16:00 | 4.86 | 6.1133 | N | 0
2025-10-27 | 17 | 2031-10-27 17:00 | 4.88 | 6.1385 | N | 0
2025-10-27 | 18 | 2031-10-27 18:00 | 4.87 | 6.1259 | N | 0
2025-10-27 | 19 | 2031-10-27 19:00 | 4.84 | 6.0881 | N | 0
2025-10-27 | 20 | 2031-10-27 20:00 | 5.55 | 6.9812 | N | 0
2025-10-27 | 21 | 2031-10-27 21:00 | 5.75 | 7.2328 | N | 0
2025-10-27 | 22 | 2031-10-27 22:00 | 5.96 | 7.497 | N | 0
2025-10-27 | 23 | 2031-10-27 23:00 | 5.96 | 7.497 | N | 0
2025-10-28 | 00 | 2031-10-28 | 5.89 | 7.4089 | N | 0
2025-10-28 | 01 | 2031-10-28 01:00 | 5.56 | 6.9938 | N | 0
2025-10-28 | 02 | 2031-10-28 02:00 | 5.12 | 6.4404 | N | 0
2025-10-28 | 03 | 2031-10-28 03:00 | 4.53 | 5.6982 | N | 0
2025-10-28 | 04 | 2031-10-28 04:00 | 4.11 | 5.1699 | N | 0
2025-10-28 | 05 | 2031-10-28 05:00 | 3.87 | 4.868 | N | 0
2025-10-28 | 06 | 2031-10-28 06:00 | 3.7 | 4.6542 | N | 0
2025-10-28 | 07 | 2031-10-28 07:00 | 3.56 | 4.4781 | N | 0
2025-10-28 | 08 | 2031-10-28 08:00 | 3.53 | 4.4403 | N | 0
2025-10-28 | 09 | 2031-10-28 09:00 | 3.71 | 4.6667 | N | 0
2025-10-28 | 10 | 2031-10-28 10:00 | 4.27 | 5.3712 | N | 0
2025-10-28 | 11 | 2031-10-28 11:00 | 4.71 | 5.9246 | N | 0
2025-10-28 | 12 | 2031-10-28 12:00 | 4.71 | 5.9246 | N | 0
2025-10-28 | 13 | 2031-10-28 13:00 | 4.67 | 5.8743 | N | 0
2025-10-28 | 14 | 2031-10-28 14:00 | 4.61 | 5.7988 | N | 0
2025-10-28 | 15 | 2031-10-28 15:00 | 4.61 | 5.7988 | N | 0
2025-10-28 | 16 | 2031-10-28 16:00 | 4.65 | 5.8491 | N | 0
2025-10-28 | 17 | 2031-10-28 17:00 | 4.8 | 6.0378 | N | 0
2025-10-28 | 18 | 2031-10-28 18:00 | 4.59 | 5.7737 | N | 0
2025-10-28 | 19 | 2031-10-28 19:00 | 4.74 | 5.9624 | N | 0
2025-10-28 | 20 | 2031-10-28 20:00 | 5.22 | 6.5661 | N | 0
2025-10-28 | 21 | 2031-10-28 21:00 | 5.6 | 7.0441 | N | 0
2025-10-28 | 22 | 2031-10-28 22:00 | 5.69 | 7.1573 | N | 0
2025-10-28 | 23 | 2031-10-28 23:00 | 5.69 | 7.1573 | N | 0
2025-10-29 | 00 | 2031-10-29 | 5.68 | 7.1448 | N | 0
2025-10-29 | 01 | 2031-10-29 01:00 | 5.43 | 6.8303 | N | 0
2025-10-29 | 02 | 2031-10-29 02:00 | 4.95 | 6.2265 | N | 0
2025-10-29 | 03 | 2031-10-29 03:00 | 4.34 | 5.4592 | N | 0
2025-10-29 | 04 | 2031-10-29 04:00 | 3.88 | 4.8806 | N | 0
2025-10-29 | 05 | 2031-10-29 05:00 | 3.62 | 4.5535 | N | 0
2025-10-29 | 06 | 2031-10-29 06:00 | 3.42 | 4.302 | N | 0
2025-10-29 | 07 | 2031-10-29 07:00 | 3.32 | 4.1762 | N | 0
2025-10-29 | 08 | 2031-10-29 08:00 | 3.41 | 4.2894 | N | 0
2025-10-29 | 09 | 2031-10-29 09:00 | 3.66 | 4.6038 | N | 0
2025-10-29 | 10 | 2031-10-29 10:00 | 4.21 | 5.2957 | N | 0
2025-10-29 | 11 | 2031-10-29 11:00 | 4.82 | 6.063 | N | 0
2025-10-29 | 12 | 2031-10-29 12:00 | 4.82 | 6.063 | N | 0
2025-10-29 | 13 | 2031-10-29 13:00 | 4.64 | 5.8366 | N | 0
2025-10-29 | 14 | 2031-10-29 14:00 | 4.64 | 5.8366 | N | 0
2025-10-29 | 15 | 2031-10-29 15:00 | 4.65 | 5.8491 | N | 0
2025-10-29 | 16 | 2031-10-29 16:00 | 4.63 | 5.824 | N | 0
2025-10-29 | 17 | 2031-10-29 17:00 | 4.73 | 5.9498 | N | 0
2025-10-29 | 18 | 2031-10-29 18:00 | 4.53 | 5.6982 | N | 0
2025-10-29 | 19 | 2031-10-29 19:00 | 4.7 | 5.912 | N | 0
2025-10-29 | 20 | 2031-10-29 20:00 | 5.24 | 6.5913 | N | 0
2025-10-29 | 21 | 2031-10-29 21:00 | 5.65 | 7.107 | N | 0
2025-10-29 | 22 | 2031-10-29 22:00 | 5.76 | 7.2454 | N | 0
2025-10-29 | 23 | 2031-10-29 23:00 | 5.96 | 7.497 | N | 0
2025-10-30 | 00 | 2031-10-30 | 5.77 | 7.258 | N | 0
2025-10-30 | 01 | 2031-10-30 01:00 | 5.5 | 6.9183 | N | 0
2025-10-30 | 02 | 2031-10-30 02:00 | 5.07 | 6.3775 | N | 0
2025-10-30 | 03 | 2031-10-30 03:00 | 4.49 | 5.6479 | N | 0
2025-10-30 | 04 | 2031-10-30 04:00 | 3.91 | 4.9183 | N | 0
2025-10-30 | 05 | 2031-10-30 05:00 | 3.55 | 4.4655 | N | 0
2025-10-30 | 06 | 2031-10-30 06:00 | 3.34 | 4.2013 | N | 0
2025-10-30 | 07 | 2031-10-30 07:00 | 3.23 | 4.063 | N | 0
2025-10-30 | 08 | 2031-10-30 08:00 | 3.26 | 4.1007 | N | 0
2025-10-30 | 09 | 2031-10-30 09:00 | 3.54 | 4.4529 | N | 0
2025-10-30 | 10 | 2031-10-30 10:00 | 4.02 | 5.0567 | N | 0
2025-10-30 | 11 | 2031-10-30 11:00 | 4.49 | 5.6479 | N | 0
2025-10-30 | 12 | 2031-10-30 12:00 | 4.62 | 5.8114 | N | 0
2025-10-30 | 13 | 2031-10-30 13:00 | 4.86 | 6.1133 | N | 0
2025-10-30 | 14 | 2031-10-30 14:00 | 4.94 | 6.2139 | N | 0
2025-10-30 | 15 | 2031-10-30 15:00 | 5.16 | 6.4907 | N | 0
2025-10-30 | 16 | 2031-10-30 16:00 | 5.16 | 6.4907 | N | 0
2025-10-30 | 17 | 2031-10-30 17:00 | 5.13 | 6.4529 | N | 0
2025-10-30 | 18 | 2031-10-30 18:00 | 5.13 | 6.4529 | N | 0
2025-10-30 | 19 | 2031-10-30 19:00 | 5.28 | 6.6416 | N | 0
2025-10-30 | 20 | 2031-10-30 20:00 | 5.86 | 7.3712 | N | 0
2025-10-30 | 21 | 2031-10-30 21:00 | 6.22 | 7.824 | N | 0
2025-10-30 | 22 | 2031-10-30 22:00 | 6.25 | 7.8618 | N | 0
2025-10-30 | 23 | 2031-10-30 23:00 | 6.06 | 7.6228 | N | 0
2025-10-31 | 00 | 2031-10-31 | 5.89 | 7.4089 | N | 0
2025-10-31 | 01 | 2031-10-31 01:00 | 5.6 | 7.0441 | N | 0
2025-10-31 | 02 | 2031-10-31 02:00 | 5.03 | 6.3271 | N | 0
2025-10-31 | 03 | 2031-10-31 03:00 | 4.41 | 5.5473 | N | 0
2025-10-31 | 04 | 2031-10-31 04:00 | 4.01 | 5.0441 | N | 0
2025-10-31 | 05 | 2031-10-31 05:00 | 3.65 | 4.5913 | N | 0
2025-10-31 | 06 | 2031-10-31 06:00 | 3.51 | 4.4152 | N | 0
2025-10-31 | 07 | 2031-10-31 07:00 | 3.4 | 4.2768 | N | 0
2025-10-31 | 08 | 2031-10-31 08:00 | 3.38 | 4.2516 | N | 0
2025-10-31 | 09 | 2031-10-31 09:00 | 3.6 | 4.5284 | N | 0
2025-10-31 | 10 | 2031-10-31 10:00 | 4.19 | 5.2705 | N | 0
2025-10-31 | 11 | 2031-10-31 11:00 | 4.68 | 5.8869 | N | 0
2025-10-31 | 12 | 2031-10-31 12:00 | 4.79 | 6.0253 | N | 0
2025-10-31 | 13 | 2031-10-31 13:00 | 5.02 | 6.3146 | N | 0
2025-10-31 | 14 | 2031-10-31 14:00 | 5.03 | 6.3271 | N | 0
2025-10-31 | 15 | 2031-10-31 15:00 | 5.1 | 6.4152 | N | 0
2025-10-31 | 16 | 2031-10-31 16:00 | 5.23 | 6.5787 | N | 0
2025-10-31 | 17 | 2031-10-31 17:00 | 5.27 | 6.629 | N | 0
2025-10-31 | 18 | 2031-10-31 18:00 | 5.39 | 6.78 | N | 0
2025-10-31 | 19 | 2031-10-31 19:00 | 5.66 | 7.1196 | N | 0
2025-10-31 | 20 | 2031-10-31 20:00 | 6.08 | 7.6479 | N | 0
2025-10-31 | 21 | 2031-10-31 21:00 | 6.03 | 7.585 | N | 0
2025-10-31 | 22 | 2031-10-31 22:00 | 5.79 | 7.2831 | N | 0
2025-10-31 | 23 | 2031-10-31 23:00 | 5.58 | 7.019 | N | 0
2025-11-01 | 00 | 2031-11-01 | 5.58 | 7.019 | N | 0
2025-11-01 | 01 | 2031-11-01 01:00 | 5.25 | 6.6039 | N | 0
2025-11-01 | 02 | 2031-11-01 02:00 | 5.02 | 6.3146 | N | 0
2025-11-01 | 03 | 2031-11-01 03:00 | 4.66 | 5.8617 | N | 0
2025-11-01 | 04 | 2031-11-01 04:00 | 4.31 | 5.4215 | N | 0
2025-11-01 | 05 | 2031-11-01 05:00 | 3.93 | 4.9435 | N | 0
2025-11-01 | 06 | 2031-11-01 06:00 | 3.68 | 4.629 | N | 0
2025-11-01 | 07 | 2031-11-01 07:00 | 3.49 | 4.39 | N | 0
2025-11-01 | 08 | 2031-11-01 08:00 | 3.41 | 4.2894 | N | 0
2025-11-01 | 09 | 2031-11-01 09:00 | 3.43 | 4.3145 | N | 0
2025-11-01 | 10 | 2031-11-01 10:00 | 3.68 | 4.629 | N | 0
2025-11-01 | 11 | 2031-11-01 11:00 | 3.99 | 5.0189 | N | 0
2025-11-01 | 12 | 2031-11-01 12:00 | 4.42 | 5.5598 | N | 0
2025-11-01 | 13 | 2031-11-01 13:00 | 4.79 | 6.0253 | N | 0
2025-11-01 | 14 | 2031-11-01 14:00 | 5.07 | 6.3775 | N | 0
2025-11-01 | 15 | 2031-11-01 15:00 | 5.07 | 6.3775 | N | 0
2025-11-01 | 16 | 2031-11-01 16:00 | 5.18 | 6.5158 | N | 0
2025-11-01 | 17 | 2031-11-01 17:00 | 5.41 | 6.8051 | N | 0
2025-11-01 | 18 | 2031-11-01 18:00 | 5.26 | 6.6165 | N | 0
2025-11-01 | 19 | 2031-11-01 19:00 | 5.26 | 6.6165 | N | 0
2025-11-01 | 20 | 2031-11-01 20:00 | 5.54 | 6.9687 | N | 0
2025-11-01 | 21 | 2031-11-01 21:00 | 5.71 | 7.1825 | N | 0
2025-11-01 | 22 | 2031-11-01 22:00 | 5.89 | 7.4089 | N | 0
2025-11-01 | 23 | 2031-11-01 23:00 | 5.83 | 7.3334 | N | 0
2025-11-02 | 00 | 2031-11-02 | 5.54 | 6.9687 | N | 0
2025-11-02 | 01 | 2031-11-02 01:00 | 5.16 | 6.4907 | N | 0
2025-11-02 | 02 | 2031-11-02 02:00 | 4.97 | 6.2517 | N | 0
2025-11-02 | 03 | 2031-11-02 03:00 | 4.75 | 5.9749 | N | 0
2025-11-02 | 04 | 2031-11-02 04:00 | 4.54 | 5.7108 | N | 0
2025-11-02 | 06 | 2031-11-02 05:00 | 3.94 | 4.9561 | N | 0
2025-11-02 | 07 | 2031-11-02 06:00 | 3.7 | 4.6542 | N | 0
2025-11-02 | 08 | 2031-11-02 07:00 | 3.62 | 4.5535 | N | 0
2025-11-02 | 09 | 2031-11-02 08:00 | 3.62 | 4.5535 | N | 0
2025-11-02 | 10 | 2031-11-02 09:00 | 3.71 | 4.6667 | N | 0
2025-11-02 | 11 | 2031-11-02 10:00 | 4 | 5.0315 | N | 0
2025-11-02 | 12 | 2031-11-02 11:00 | 4.45 | 5.5976 | N | 0
2025-11-02 | 13 | 2031-11-02 12:00 | 4.71 | 5.9246 | N | 0
2025-11-02 | 14 | 2031-11-02 13:00 | 4.93 | 6.2014 | N | 0
2025-11-02 | 15 | 2031-11-02 14:00 | 4.99 | 6.2768 | N | 0
2025-11-02 | 16 | 2031-11-02 15:00 | 5.11 | 6.4278 | N | 0
2025-11-02 | 17 | 2031-11-02 16:00 | 5.26 | 6.6165 | N | 0
2025-11-02 | 18 | 2031-11-02 17:00 | 5.31 | 6.6794 | N | 0
2025-11-02 | 19 | 2031-11-02 18:00 | 5.42 | 6.8177 | N | 0
2025-11-02 | 20 | 2031-11-02 19:00 | 5.49 | 6.9058 | N | 0
2025-11-02 | 21 | 2031-11-02 20:00 | 6.32 | 7.9498 | N | 0
2025-11-02 | 22 | 2031-11-02 21:00 | 6.51 | 8.1888 | N | 0
2025-11-02 | 23 | 2031-11-02 22:00 | 6.44 | 8.1008 | N | 0
2025-11-03 | 00 | 2031-11-02 23:00 | 5.92 | 7.4467 | N | 0
2025-11-03 | 01 | 2031-11-03 | 5.68 | 7.1448 | N | 0
2025-11-03 | 02 | 2031-11-03 01:00 | 5.33 | 6.7045 | N | 0
2025-11-03 | 03 | 2031-11-03 02:00 | 4.9 | 6.1636 | N | 0
2025-11-03 | 04 | 2031-11-03 03:00 | 4.33 | 5.4466 | N | 0
2025-11-03 | 05 | 2031-11-03 04:00 | 3.9 | 4.9057 | N | 0
2025-11-03 | 06 | 2031-11-03 05:00 | 3.62 | 4.5535 | N | 0
2025-11-03 | 07 | 2031-11-03 06:00 | 3.49 | 4.39 | N | 0
2025-11-03 | 08 | 2031-11-03 07:00 | 3.45 | 4.3397 | N | 0
2025-11-03 | 09 | 2031-11-03 08:00 | 3.48 | 4.3774 | N | 0
2025-11-03 | 10 | 2031-11-03 09:00 | 3.93 | 4.9435 | N | 0
2025-11-03 | 11 | 2031-11-03 10:00 | 4.31 | 5.4215 | N | 0
2025-11-03 | 12 | 2031-11-03 11:00 | 4.71 | 5.9246 | N | 0
2025-11-03 | 13 | 2031-11-03 12:00 | 4.8 | 6.0378 | N | 0
2025-11-03 | 14 | 2031-11-03 13:00 | 4.82 | 6.063 | N | 0
2025-11-03 | 15 | 2031-11-03 14:00 | 5 | 6.2894 | N | 0
2025-11-03 | 16 | 2031-11-03 15:00 | 5.16 | 6.4907 | N | 0
2025-11-03 | 17 | 2031-11-03 16:00 | 5.31 | 6.6794 | N | 0
2025-11-03 | 18 | 2031-11-03 17:00 | 5.27 | 6.629 | N | 0
2025-11-03 | 19 | 2031-11-03 18:00 | 5.19 | 6.5284 | N | 0
2025-11-03 | 20 | 2031-11-03 19:00 | 5.3 | 6.6668 | N | 0
2025-11-03 | 21 | 2031-11-03 20:00 | 5.92 | 7.4467 | N | 0
2025-11-03 | 22 | 2031-11-03 21:00 | 6.39 | 8.0379 | N | 0
2025-11-03 | 23 | 2031-11-03 22:00 | 6.29 | 7.9121 | N | 0
2025-11-04 | 00 | 2031-11-03 23:00 | 5.99 | 7.5347 | N | 0
2025-11-04 | 01 | 2031-11-04 | 5.8 | 7.2957 | N | 0
2025-11-04 | 02 | 2031-11-04 01:00 | 5.44 | 6.8429 | N | 0
2025-11-04 | 03 | 2031-11-04 02:00 | 4.91 | 6.1762 | N | 0
2025-11-04 | 04 | 2031-11-04 03:00 | 4.34 | 5.4592 | N | 0
2025-11-04 | 05 | 2031-11-04 04:00 | 3.93 | 4.9435 | N | 0
2025-11-04 | 06 | 2031-11-04 05:00 | 3.65 | 4.5913 | N | 0
2025-11-04 | 07 | 2031-11-04 06:00 | 3.45 | 4.3397 | N | 0
2025-11-04 | 08 | 2031-11-04 07:00 | 3.41 | 4.2894 | N | 0
2025-11-04 | 09 | 2031-11-04 08:00 | 3.43 | 4.3145 | N | 0
2025-11-04 | 10 | 2031-11-04 09:00 | 3.88 | 4.8806 | N | 0
2025-11-04 | 11 | 2031-11-04 10:00 | 4.36 | 5.4844 | N | 0
2025-11-04 | 12 | 2031-11-04 11:00 | 4.82 | 6.063 | N | 0
2025-11-04 | 13 | 2031-11-04 12:00 | 4.78 | 6.0127 | N | 0
2025-11-04 | 14 | 2031-11-04 13:00 | 4.59 | 5.7737 | N | 0
2025-11-04 | 15 | 2031-11-04 14:00 | 4.65 | 5.8491 | N | 0
2025-11-04 | 16 | 2031-11-04 15:00 | 4.69 | 5.8995 | N | 0
2025-11-04 | 17 | 2031-11-04 16:00 | 4.76 | 5.9875 | N | 0
2025-11-04 | 18 | 2031-11-04 17:00 | 4.68 | 5.8869 | N | 0
2025-11-04 | 19 | 2031-11-04 18:00 | 4.64 | 5.8366 | N | 0
2025-11-04 | 20 | 2031-11-04 19:00 | 4.82 | 6.063 | N | 0
2025-11-04 | 21 | 2031-11-04 20:00 | 5.5 | 6.9183 | N | 0
2025-11-04 | 22 | 2031-11-04 21:00 | 6.02 | 7.5724 | N | 0
2025-11-04 | 23 | 2031-11-04 22:00 | 5.96 | 7.497 | N | 0
2025-11-05 | 00 | 2031-11-04 23:00 | 5.79 | 7.2831 | N | 0
2025-11-05 | 01 | 2031-11-05 | 5.74 | 7.2202 | N | 0
2025-11-05 | 02 | 2031-11-05 01:00 | 5.37 | 6.7548 | N | 0
2025-11-05 | 03 | 2031-11-05 02:00 | 4.78 | 6.0127 | N | 0
2025-11-05 | 04 | 2031-11-05 03:00 | 4.31 | 5.4215 | N | 0
2025-11-05 | 05 | 2031-11-05 04:00 | 3.86 | 4.8554 | N | 0
2025-11-05 | 06 | 2031-11-05 05:00 | 3.6 | 4.5284 | N | 0
2025-11-05 | 07 | 2031-11-05 06:00 | 3.41 | 4.2894 | N | 0
2025-11-05 | 08 | 2031-11-05 07:00 | 3.39 | 4.2642 | N | 0
2025-11-05 | 09 | 2031-11-05 08:00 | 3.36 | 4.2265 | N | 0
2025-11-05 | 10 | 2031-11-05 09:00 | 3.65 | 4.5913 | N | 0
2025-11-05 | 11 | 2031-11-05 10:00 | 4.21 | 5.2957 | N | 0
2025-11-05 | 12 | 2031-11-05 11:00 | 4.64 | 5.8366 | N | 0
2025-11-05 | 13 | 2031-11-05 12:00 | 4.64 | 5.8366 | N | 0
2025-11-05 | 14 | 2031-11-05 13:00 | 4.73 | 5.9498 | N | 0
2025-11-05 | 15 | 2031-11-05 14:00 | 4.93 | 6.2014 | N | 0
2025-11-05 | 16 | 2031-11-05 15:00 | 5.06 | 6.3649 | N | 0
2025-11-05 | 17 | 2031-11-05 16:00 | 5.27 | 6.629 | N | 0
2025-11-05 | 18 | 2031-11-05 17:00 | 5.13 | 6.4529 | N | 0
2025-11-05 | 19 | 2031-11-05 18:00 | 5.04 | 6.3397 | N | 0
2025-11-05 | 20 | 2031-11-05 19:00 | 5.41 | 6.8051 | N | 0
2025-11-05 | 21 | 2031-11-05 20:00 | 5.93 | 7.4592 | N | 0
2025-11-05 | 22 | 2031-11-05 21:00 | 6.24 | 7.8492 | N | 0
2025-11-05 | 23 | 2031-11-05 22:00 | 6.22 | 7.824 | N | 0
2025-11-06 | 00 | 2031-11-05 23:00 | 6.07 | 7.6353 | N | 0
2025-11-06 | 01 | 2031-11-06 | 5.87 | 7.3838 | N | 0
2025-11-06 | 02 | 2031-11-06 01:00 | 5.6 | 7.0441 | N | 0
2025-11-06 | 03 | 2031-11-06 02:00 | 4.93 | 6.2014 | N | 0
2025-11-06 | 04 | 2031-11-06 03:00 | 4.35 | 5.4718 | N | 0
2025-11-06 | 05 | 2031-11-06 04:00 | 3.94 | 4.9561 | N | 0
2025-11-06 | 06 | 2031-11-06 05:00 | 3.66 | 4.6038 | N | 0
2025-11-06 | 07 | 2031-11-06 06:00 | 3.54 | 4.4529 | N | 0
2025-11-06 | 08 | 2031-11-06 07:00 | 3.44 | 4.3271 | N | 0
2025-11-06 | 09 | 2031-11-06 08:00 | 3.45 | 4.3397 | N | 0
2025-11-06 | 10 | 2031-11-06 09:00 | 3.87 | 4.868 | N | 0
2025-11-06 | 11 | 2031-11-06 10:00 | 4.39 | 5.5221 | N | 0
2025-11-06 | 12 | 2031-11-06 11:00 | 4.83 | 6.0756 | N | 0
2025-11-06 | 13 | 2031-11-06 12:00 | 4.79 | 6.0253 | N | 0
2025-11-06 | 14 | 2031-11-06 13:00 | 4.78 | 6.0127 | N | 0
2025-11-06 | 15 | 2031-11-06 14:00 | 4.79 | 6.0253 | N | 0
2025-11-06 | 16 | 2031-11-06 15:00 | 4.86 | 6.1133 | N | 0
2025-11-06 | 17 | 2031-11-06 16:00 | 5 | 6.2894 | N | 0
2025-11-06 | 18 | 2031-11-06 17:00 | 4.95 | 6.2265 | N | 0
2025-11-06 | 19 | 2031-11-06 18:00 | 4.98 | 6.2642 | N | 0
2025-11-06 | 20 | 2031-11-06 19:00 | 5.26 | 6.6165 | N | 0
2025-11-06 | 21 | 2031-11-06 20:00 | 5.85 | 7.3586 | N | 0
2025-11-06 | 22 | 2031-11-06 21:00 | 6.24 | 7.8492 | N | 0
2025-11-06 | 23 | 2031-11-06 22:00 | 6.25 | 7.8618 | N | 0
2025-11-07 | 00 | 2031-11-06 23:00 | 6.07 | 7.6353 | N | 0
2025-11-07 | 01 | 2031-11-07 | 6.05 | 7.6102 | N | 0
2025-11-07 | 02 | 2031-11-07 01:00 | 5.86 | 7.3712 | N | 0
2025-11-07 | 03 | 2031-11-07 02:00 | 5.15 | 6.4781 | N | 0
2025-11-07 | 04 | 2031-11-07 03:00 | 4.57 | 5.7485 | N | 0
2025-11-07 | 05 | 2031-11-07 04:00 | 4.25 | 5.346 | N | 0
2025-11-07 | 06 | 2031-11-07 05:00 | 3.89 | 4.8932 | N | 0
2025-11-07 | 07 | 2031-11-07 06:00 | 3.77 | 4.7422 | N | 0
2025-11-07 | 08 | 2031-11-07 07:00 | 3.64 | 4.5787 | N | 0
2025-11-07 | 09 | 2031-11-07 08:00 | 3.62 | 4.5535 | N | 0
2025-11-07 | 10 | 2031-11-07 09:00 | 3.94 | 4.9561 | N | 0
2025-11-07 | 11 | 2031-11-07 10:00 | 4.48 | 5.6353 | N | 0
2025-11-07 | 12 | 2031-11-07 11:00 | 4.86 | 6.1133 | N | 0
2025-11-07 | 13 | 2031-11-07 12:00 | 5.03 | 6.3271 | N | 0
2025-11-07 | 14 | 2031-11-07 13:00 | 4.94 | 6.2139 | N | 0
2025-11-07 | 15 | 2031-11-07 14:00 | 5.08 | 6.39 | N | 0
2025-11-07 | 16 | 2031-11-07 15:00 | 5.25 | 6.6039 | N | 0
2025-11-07 | 17 | 2031-11-07 16:00 | 5.35 | 6.7297 | N | 0
2025-11-07 | 18 | 2031-11-07 17:00 | 5.39 | 6.78 | N | 0
2025-11-07 | 19 | 2031-11-07 18:00 | 5.25 | 6.6039 | N | 0
2025-11-07 | 20 | 2031-11-07 19:00 | 5.47 | 6.8806 | N | 0
2025-11-07 | 21 | 2031-11-07 20:00 | 6.03 | 7.585 | N | 0
2025-11-07 | 22 | 2031-11-07 21:00 | 6.17 | 7.7611 | N | 0
2025-11-07 | 23 | 2031-11-07 22:00 | 5.94 | 7.4718 | N | 0
2025-11-08 | 00 | 2031-11-07 23:00 | 5.61 | 7.0567 | N | 0
2025-11-08 | 01 | 2031-11-08 | 5.58 | 7.019 | N | 0
2025-11-08 | 02 | 2031-11-08 01:00 | 5.4 | 6.7926 | N | 0
2025-11-08 | 03 | 2031-11-08 02:00 | 4.91 | 6.1762 | N | 0
2025-11-08 | 04 | 2031-11-08 03:00 | 4.45 | 5.5976 | N | 0
2025-11-08 | 05 | 2031-11-08 04:00 | 4.08 | 5.1322 | N | 0
2025-11-08 | 06 | 2031-11-08 05:00 | 3.76 | 4.7296 | N | 0
2025-11-08 | 07 | 2031-11-08 06:00 | 3.55 | 4.4655 | N | 0
2025-11-08 | 08 | 2031-11-08 07:00 | 3.42 | 4.302 | N | 0
2025-11-08 | 09 | 2031-11-08 08:00 | 3.38 | 4.2516 | N | 0
2025-11-08 | 10 | 2031-11-08 09:00 | 3.51 | 4.4152 | N | 0
2025-11-08 | 11 | 2031-11-08 10:00 | 3.75 | 4.7171 | N | 0
2025-11-08 | 12 | 2031-11-08 11:00 | 4.28 | 5.3837 | N | 0
2025-11-08 | 13 | 2031-11-08 12:00 | 4.56 | 5.7359 | N | 0
2025-11-08 | 14 | 2031-11-08 13:00 | 4.66 | 5.8617 | N | 0
2025-11-08 | 15 | 2031-11-08 14:00 | 4.89 | 6.151 | N | 0
2025-11-08 | 16 | 2031-11-08 15:00 | 5.02 | 6.3146 | N | 0
2025-11-08 | 17 | 2031-11-08 16:00 | 4.96 | 6.2391 | N | 0
2025-11-08 | 18 | 2031-11-08 17:00 | 5.04 | 6.3397 | N | 0
2025-11-08 | 19 | 2031-11-08 18:00 | 5.08 | 6.39 | N | 0
2025-11-08 | 20 | 2031-11-08 19:00 | 5.41 | 6.8051 | N | 0
2025-11-08 | 21 | 2031-11-08 20:00 | 5.7 | 7.1699 | N | 0
2025-11-08 | 22 | 2031-11-08 21:00 | 6.21 | 7.8114 | N | 0
2025-11-08 | 23 | 2031-11-08 22:00 | 6.03 | 7.585 | N | 0
2025-11-09 | 00 | 2031-11-08 23:00 | 5.74 | 7.2202 | N | 0
2025-11-09 | 01 | 2031-11-09 | 5.54 | 6.9687 | N | 0
2025-11-09 | 02 | 2031-11-09 01:00 | 5.35 | 6.7297 | N | 0
2025-11-09 | 03 | 2031-11-09 02:00 | 5.1 | 6.4152 | N | 0
2025-11-09 | 04 | 2031-11-09 03:00 | 4.58 | 5.7611 | N | 0
2025-11-09 | 05 | 2031-11-09 04:00 | 4.31 | 5.4215 | N | 0
2025-11-09 | 06 | 2031-11-09 05:00 | 3.96 | 4.9812 | N | 0
2025-11-09 | 07 | 2031-11-09 06:00 | 3.77 | 4.7422 | N | 0
2025-11-09 | 08 | 2031-11-09 07:00 | 3.71 | 4.6667 | N | 0
2025-11-09 | 09 | 2031-11-09 08:00 | 3.67 | 4.6164 | N | 0
2025-11-09 | 10 | 2031-11-09 09:00 | 3.82 | 4.8051 | N | 0
2025-11-09 | 11 | 2031-11-09 10:00 | 4 | 5.0315 | N | 0
2025-11-09 | 12 | 2031-11-09 11:00 | 4.44 | 5.585 | N | 0
2025-11-09 | 13 | 2031-11-09 12:00 | 4.95 | 6.2265 | N | 0
2025-11-09 | 14 | 2031-11-09 13:00 | 5.42 | 6.8177 | N | 0
2025-11-09 | 15 | 2031-11-09 14:00 | 5.8 | 7.2957 | N | 0
2025-11-09 | 16 | 2031-11-09 15:00 | 6.07 | 7.6353 | N | 0
2025-11-09 | 17 | 2031-11-09 16:00 | 6.4 | 8.0504 | N | 0
2025-11-09 | 18 | 2031-11-09 17:00 | 6.47 | 8.1385 | N | 0
2025-11-09 | 19 | 2031-11-09 18:00 | 6.5 | 8.1762 | N | 0
2025-11-09 | 20 | 2031-11-09 19:00 | 6.71 | 8.4404 | N | 0
2025-11-09 | 21 | 2031-11-09 20:00 | 7.32 | 9.2077 | N | 0
2025-11-09 | 22 | 2031-11-09 21:00 | 7.6 | 9.5599 | N | 0
2025-11-09 | 23 | 2031-11-09 22:00 | 7.33 | 9.2203 | N | 0
2025-11-10 | 00 | 2031-11-09 23:00 | 6.87 | 8.6416 | N | 0
2025-11-10 | 01 | 2031-11-10 | 6.56 | 8.2517 | N | 0
2025-11-10 | 02 | 2031-11-10 01:00 | 6.13 | 7.7108 | N | 0
2025-11-10 | 03 | 2031-11-10 02:00 | 5.59 | 7.0316 | N | 0
2025-11-10 | 04 | 2031-11-10 03:00 | 5.03 | 6.3271 | N | 0
2025-11-10 | 05 | 2031-11-10 04:00 | 4.51 | 5.673 | N | 0
2025-11-10 | 06 | 2031-11-10 05:00 | 4.15 | 5.2202 | N | 0
2025-11-10 | 07 | 2031-11-10 06:00 | 4.03 | 5.0693 | N | 0
2025-11-10 | 08 | 2031-11-10 07:00 | 4 | 5.0315 | N | 0
2025-11-10 | 09 | 2031-11-10 08:00 | 4.04 | 5.0818 | N | 0
2025-11-10 | 10 | 2031-11-10 09:00 | 4.42 | 5.5598 | N | 0
2025-11-10 | 11 | 2031-11-10 10:00 | 4.92 | 6.1888 | N | 0
2025-11-10 | 12 | 2031-11-10 11:00 | 5.34 | 6.7171 | N | 0
2025-11-10 | 13 | 2031-11-10 12:00 | 5.54 | 6.9687 | N | 0
2025-11-10 | 14 | 2031-11-10 13:00 | 5.62 | 7.0693 | N | 0
2025-11-10 | 15 | 2031-11-10 14:00 | 5.79 | 7.2831 | N | 0
2025-11-10 | 16 | 2031-11-10 15:00 | 5.7 | 7.1699 | N | 0
2025-11-10 | 17 | 2031-11-10 16:00 | 6 | 7.5473 | N | 0
2025-11-10 | 18 | 2031-11-10 17:00 | 5.94 | 7.4718 | N | 0
2025-11-10 | 19 | 2031-11-10 18:00 | 5.81 | 7.3083 | N | 0
2025-11-10 | 20 | 2031-11-10 19:00 | 6.02 | 7.5724 | N | 0
2025-11-10 | 21 | 2031-11-10 20:00 | 6.7 | 8.4278 | N | 0
2025-11-10 | 22 | 2031-11-10 21:00 | 7.27 | 9.1448 | N | 0
2025-11-10 | 23 | 2031-11-10 22:00 | 7.06 | 8.8806 | N | 0
2025-11-11 | 00 | 2031-11-10 23:00 | 6.79 | 8.541 | N | 0
2025-11-11 | 01 | 2031-11-11 | 6.58 | 8.2769 | N | 0
2025-11-11 | 02 | 2031-11-11 01:00 | 6.38 | 8.0253 | N | 0
2025-11-11 | 03 | 2031-11-11 02:00 | 5.75 | 7.2328 | N | 0
2025-11-11 | 04 | 2031-11-11 03:00 | 5.01 | 6.302 | N | 0
2025-11-11 | 05 | 2031-11-11 04:00 | 4.61 | 5.7988 | N | 0
2025-11-11 | 06 | 2031-11-11 05:00 | 4.33 | 5.4466 | N | 0
2025-11-11 | 07 | 2031-11-11 06:00 | 4.16 | 5.2328 | N | 0
2025-11-11 | 08 | 2031-11-11 07:00 | 4.1 | 5.1573 | N | 0
2025-11-11 | 09 | 2031-11-11 08:00 | 4.16 | 5.2328 | N | 0
2025-11-11 | 10 | 2031-11-11 09:00 | 4.49 | 5.6479 | N | 0
2025-11-11 | 11 | 2031-11-11 10:00 | 5 | 6.2894 | N | 0
2025-11-11 | 12 | 2031-11-11 11:00 | 5.46 | 6.868 | N | 0
2025-11-11 | 13 | 2031-11-11 12:00 | 5.51 | 6.9309 | N | 0
2025-11-11 | 14 | 2031-11-11 13:00 | 5.33 | 6.7045 | N | 0
2025-11-11 | 15 | 2031-11-11 14:00 | 5.33 | 6.7045 | N | 0
2025-11-11 | 16 | 2031-11-11 15:00 | 5.39 | 6.78 | N | 0
2025-11-11 | 17 | 2031-11-11 16:00 | 5.51 | 6.9309 | N | 0
2025-11-11 | 18 | 2031-11-11 17:00 | 5.52 | 6.9435 | N | 0
2025-11-11 | 19 | 2031-11-11 18:00 | 5.7 | 7.1699 | N | 0
2025-11-11 | 20 | 2031-11-11 19:00 | 5.68 | 7.1448 | N | 0
2025-11-11 | 21 | 2031-11-11 20:00 | 6.5 | 8.1762 | N | 0
2025-11-11 | 22 | 2031-11-11 21:00 | 6.99 | 8.7926 | N | 0
2025-11-11 | 23 | 2031-11-11 22:00 | 6.7 | 8.4278 | N | 0
2025-11-12 | 00 | 2031-11-11 23:00 | 6.55 | 8.2391 | N | 0
2025-11-12 | 01 | 2031-11-12 | 6.38 | 8.0253 | N | 0
2025-11-12 | 02 | 2031-11-12 01:00 | 5.95 | 7.4844 | N | 0
2025-11-12 | 03 | 2031-11-12 02:00 | 5.32 | 6.6919 | N | 0
2025-11-12 | 04 | 2031-11-12 03:00 | 4.79 | 6.0253 | N | 0
2025-11-12 | 05 | 2031-11-12 04:00 | 4.38 | 5.5095 | N | 0
2025-11-12 | 06 | 2031-11-12 05:00 | 4.06 | 5.107 | N | 0
2025-11-12 | 07 | 2031-11-12 06:00 | 3.85 | 4.8428 | N | 0
2025-11-12 | 08 | 2031-11-12 07:00 | 3.75 | 4.7171 | N | 0
2025-11-12 | 09 | 2031-11-12 08:00 | 3.77 | 4.7422 | N | 0
2025-11-12 | 10 | 2031-11-12 09:00 | 4.04 | 5.0818 | N | 0
2025-11-12 | 11 | 2031-11-12 10:00 | 4.7 | 5.912 | N | 0
2025-11-12 | 12 | 2031-11-12 11:00 | 5.12 | 6.4404 | N | 0
2025-11-12 | 13 | 2031-11-12 12:00 | 5.23 | 6.5787 | N | 0
2025-11-12 | 14 | 2031-11-12 13:00 | 5.28 | 6.6416 | N | 0
2025-11-12 | 15 | 2031-11-12 14:00 | 5.31 | 6.6794 | N | 0
2025-11-12 | 16 | 2031-11-12 15:00 | 5.31 | 6.6794 | N | 0
2025-11-12 | 17 | 2031-11-12 16:00 | 5.47 | 6.8806 | N | 0
2025-11-12 | 18 | 2031-11-12 17:00 | 5.31 | 6.6794 | N | 0
2025-11-12 | 19 | 2031-11-12 18:00 | 5.31 | 6.6794 | N | 0
2025-11-12 | 20 | 2031-11-12 19:00 | 5.5 | 6.9183 | N | 0
2025-11-12 | 21 | 2031-11-12 20:00 | 6.26 | 7.8743 | N | 0
2025-11-12 | 22 | 2031-11-12 21:00 | 6.63 | 8.3398 | N | 0
2025-11-12 | 23 | 2031-11-12 22:00 | 6.51 | 8.1888 | N | 0
2025-11-13 | 00 | 2031-11-12 23:00 | 6.15 | 7.736 | N | 0
2025-11-13 | 01 | 2031-11-13 | 6.14 | 7.7234 | N | 0
2025-11-13 | 02 | 2031-11-13 01:00 | 5.75 | 7.2328 | N | 0
2025-11-13 | 03 | 2031-11-13 02:00 | 5.17 | 6.5032 | N | 0
2025-11-13 | 04 | 2031-11-13 03:00 | 4.6 | 5.7863 | N | 0
2025-11-13 | 05 | 2031-11-13 04:00 | 4.15 | 5.2202 | N | 0
2025-11-13 | 06 | 2031-11-13 05:00 | 3.81 | 4.7925 | N | 0
2025-11-13 | 07 | 2031-11-13 06:00 | 3.71 | 4.6667 | N | 0
2025-11-13 | 08 | 2031-11-13 07:00 | 3.58 | 4.5032 | N | 0
2025-11-13 | 09 | 2031-11-13 08:00 | 3.64 | 4.5787 | N | 0
2025-11-13 | 10 | 2031-11-13 09:00 | 3.93 | 4.9435 | N | 0
2025-11-13 | 11 | 2031-11-13 10:00 | 4.48 | 5.6353 | N | 0
2025-11-13 | 12 | 2031-11-13 11:00 | 4.94 | 6.2139 | N | 0
2025-11-13 | 13 | 2031-11-13 12:00 | 4.98 | 6.2642 | N | 0
2025-11-13 | 14 | 2031-11-13 13:00 | 4.82 | 6.063 | N | 0
2025-11-13 | 15 | 2031-11-13 14:00 | 5.04 | 6.3397 | N | 0
2025-11-13 | 16 | 2031-11-13 15:00 | 5.17 | 6.5032 | N | 0
2025-11-13 | 17 | 2031-11-13 16:00 | 5.11 | 6.4278 | N | 0
2025-11-13 | 18 | 2031-11-13 17:00 | 5.17 | 6.5032 | N | 0
2025-11-13 | 19 | 2031-11-13 18:00 | 5.1 | 6.4152 | N | 0
2025-11-13 | 20 | 2031-11-13 19:00 | 5.53 | 6.9561 | N | 0
2025-11-13 | 21 | 2031-11-13 20:00 | 6.1 | 7.6731 | N | 0
2025-11-13 | 22 | 2031-11-13 21:00 | 6.52 | 8.2014 | N | 0
2025-11-13 | 23 | 2031-11-13 22:00 | 6.36 | 8.0001 | N | 0
2025-11-14 | 00 | 2031-11-13 23:00 | 6.19 | 7.7863 | N | 0
2025-11-14 | 01 | 2031-11-14 | 6 | 7.5473 | N | 0
2025-11-14 | 02 | 2031-11-14 01:00 | 5.82 | 7.3209 | N | 0
2025-11-14 | 03 | 2031-11-14 02:00 | 5.17 | 6.5032 | N | 0
2025-11-14 | 04 | 2031-11-14 03:00 | 4.58 | 5.7611 | N | 0
2025-11-14 | 05 | 2031-11-14 04:00 | 4.15 | 5.2202 | N | 0
2025-11-14 | 06 | 2031-11-14 05:00 | 3.89 | 4.8932 | N | 0
2025-11-14 | 07 | 2031-11-14 06:00 | 3.87 | 4.868 | N | 0
2025-11-14 | 08 | 2031-11-14 07:00 | 3.76 | 4.7296 | N | 0
2025-11-14 | 09 | 2031-11-14 08:00 | 3.76 | 4.7296 | N | 0
2025-11-14 | 10 | 2031-11-14 09:00 | 4.05 | 5.0944 | N | 0
2025-11-14 | 11 | 2031-11-14 10:00 | 4.58 | 5.7611 | N | 0
2025-11-14 | 12 | 2031-11-14 11:00 | 4.93 | 6.2014 | N | 0
2025-11-14 | 13 | 2031-11-14 12:00 | 5.02 | 6.3146 | N | 0
2025-11-14 | 14 | 2031-11-14 13:00 | 5.02 | 6.3146 | N | 0
2025-11-14 | 15 | 2031-11-14 14:00 | 4.98 | 6.2642 | N | 0
2025-11-14 | 16 | 2031-11-14 15:00 | 5.09 | 6.4026 | N | 0
2025-11-14 | 17 | 2031-11-14 16:00 | 5.21 | 6.5536 | N | 0
2025-11-14 | 18 | 2031-11-14 17:00 | 5.13 | 6.4529 | N | 0
2025-11-14 | 19 | 2031-11-14 18:00 | 5.11 | 6.4278 | N | 0
2025-11-14 | 20 | 2031-11-14 19:00 | 5.2 | 6.541 | N | 0
2025-11-14 | 21 | 2031-11-14 20:00 | 5.88 | 7.3963 | N | 0
2025-11-14 | 22 | 2031-11-14 21:00 | 6.32 | 7.9498 | N | 0
2025-11-14 | 23 | 2031-11-14 22:00 | 6.27 | 7.8869 | N | 0
2025-11-15 | 00 | 2031-11-14 23:00 | 6.07 | 7.6353 | N | 0
2025-11-15 | 01 | 2031-11-15 | 5.99 | 7.5347 | N | 0
2025-11-15 | 02 | 2031-11-15 01:00 | 5.8 | 7.2957 | N | 0
2025-11-15 | 03 | 2031-11-15 02:00 | 5.33 | 6.7045 | N | 0
2025-11-15 | 04 | 2031-11-15 03:00 | 4.81 | 6.0504 | N | 0
2025-11-15 | 05 | 2031-11-15 04:00 | 4.48 | 5.6353 | N | 0
2025-11-15 | 06 | 2031-11-15 05:00 | 4.14 | 5.2076 | N | 0
2025-11-15 | 07 | 2031-11-15 06:00 | 3.85 | 4.8428 | N | 0
2025-11-15 | 08 | 2031-11-15 07:00 | 3.85 | 4.8428 | N | 0
2025-11-15 | 09 | 2031-11-15 08:00 | 3.84 | 4.8303 | N | 0
2025-11-15 | 10 | 2031-11-15 09:00 | 3.83 | 4.8177 | N | 0
2025-11-15 | 11 | 2031-11-15 10:00 | 4.09 | 5.1447 | N | 0
2025-11-15 | 12 | 2031-11-15 11:00 | 4.62 | 5.8114 | N | 0
2025-11-15 | 13 | 2031-11-15 12:00 | 5.06 | 6.3649 | N | 0
2025-11-15 | 14 | 2031-11-15 13:00 | 5.17 | 6.5032 | N | 0
2025-11-15 | 15 | 2031-11-15 14:00 | 5.12 | 6.4404 | N | 0
2025-11-15 | 16 | 2031-11-15 15:00 | 5.72 | 7.1951 | N | 0
2025-11-15 | 17 | 2031-11-15 16:00 | 6 | 7.5473 | N | 0
2025-11-15 | 18 | 2031-11-15 17:00 | 5.87 | 7.3838 | N | 0
2025-11-15 | 19 | 2031-11-15 18:00 | 5.88 | 7.3963 | N | 0
2025-11-15 | 20 | 2031-11-15 19:00 | 6.06 | 7.6228 | N | 0
2025-11-15 | 21 | 2031-11-15 20:00 | 6.25 | 7.8618 | N | 0
2025-11-15 | 22 | 2031-11-15 21:00 | 6.47 | 8.1385 | N | 0
2025-11-15 | 23 | 2031-11-15 22:00 | 6.27 | 7.8869 | N | 0
2025-11-16 | 00 | 2031-11-15 23:00 | 5.98 | 7.5221 | N | 0
2025-11-16 | 01 | 2031-11-16 | 5.7 | 7.1699 | N | 0
2025-11-16 | 02 | 2031-11-16 01:00 | 5.38 | 6.7674 | N | 0
2025-11-16 | 03 | 2031-11-16 02:00 | 5.1 | 6.4152 | N | 0
2025-11-16 | 04 | 2031-11-16 03:00 | 4.58 | 5.7611 | N | 0
2025-11-16 | 05 | 2031-11-16 04:00 | 4.26 | 5.3586 | N | 0
2025-11-16 | 06 | 2031-11-16 05:00 | 3.85 | 4.8428 | N | 0
2025-11-16 | 07 | 2031-11-16 06:00 | 3.73 | 4.6919 | N | 0
2025-11-16 | 08 | 2031-11-16 07:00 | 3.63 | 4.5661 | N | 0
2025-11-16 | 09 | 2031-11-16 08:00 | 3.54 | 4.4529 | N | 0
2025-11-16 | 10 | 2031-11-16 09:00 | 3.66 | 4.6038 | N | 0
2025-11-16 | 11 | 2031-11-16 10:00 | 3.9 | 4.9057 | N | 0
2025-11-16 | 12 | 2031-11-16 11:00 | 4.41 | 5.5473 | N | 0
2025-11-16 | 13 | 2031-11-16 12:00 | 4.83 | 6.0756 | N | 0
2025-11-16 | 14 | 2031-11-16 13:00 | 5.27 | 6.629 | N | 0
2025-11-16 | 15 | 2031-11-16 14:00 | 5.64 | 7.0945 | N | 0
2025-11-16 | 16 | 2031-11-16 15:00 | 5.98 | 7.5221 | N | 0
2025-11-16 | 17 | 2031-11-16 16:00 | 5.97 | 7.5096 | N | 0
2025-11-16 | 18 | 2031-11-16 17:00 | 6.09 | 7.6605 | N | 0
2025-11-16 | 19 | 2031-11-16 18:00 | 6.15 | 7.736 | N | 0
2025-11-16 | 20 | 2031-11-16 19:00 | 6.42 | 8.0756 | N | 0
2025-11-16 | 21 | 2031-11-16 20:00 | 6.78 | 8.5284 | N | 0
2025-11-16 | 22 | 2031-11-16 21:00 | 7.18 | 9.0316 | N | 0
2025-11-16 | 23 | 2031-11-16 22:00 | 6.96 | 8.7549 | N | 0
2025-11-17 | 00 | 2031-11-16 23:00 | 6.57 | 8.2643 | N | 0
2025-11-17 | 01 | 2031-11-17 | 6.43 | 8.0882 | N | 0
2025-11-17 | 02 | 2031-11-17 01:00 | 6.11 | 7.6857 | N | 0
2025-11-17 | 03 | 2031-11-17 02:00 | 5.53 | 6.9561 | N | 0
2025-11-17 | 04 | 2031-11-17 03:00 | 5.03 | 6.3271 | N | 0
2025-11-17 | 05 | 2031-11-17 04:00 | 4.61 | 5.7988 | N | 0
2025-11-17 | 06 | 2031-11-17 05:00 | 4.17 | 5.2454 | N | 0
2025-11-17 | 07 | 2031-11-17 06:00 | 3.99 | 5.0189 | N | 0
2025-11-17 | 08 | 2031-11-17 07:00 | 3.87 | 4.868 | N | 0
2025-11-17 | 09 | 2031-11-17 08:00 | 3.91 | 4.9183 | N | 0
2025-11-17 | 10 | 2031-11-17 09:00 | 4.29 | 5.3963 | N | 0
2025-11-17 | 11 | 2031-11-17 10:00 | 4.85 | 6.1007 | N | 0
2025-11-17 | 12 | 2031-11-17 11:00 | 5.37 | 6.7548 | N | 0
2025-11-17 | 13 | 2031-11-17 12:00 | 5.37 | 6.7548 | N | 0
2025-11-17 | 14 | 2031-11-17 13:00 | 5.3 | 6.6668 | N | 0
2025-11-17 | 15 | 2031-11-17 14:00 | 5.5 | 6.9183 | N | 0
2025-11-17 | 16 | 2031-11-17 15:00 | 5.54 | 6.9687 | N | 0
2025-11-17 | 17 | 2031-11-17 16:00 | 5.72 | 7.1951 | N | 0
2025-11-17 | 18 | 2031-11-17 17:00 | 5.73 | 7.2077 | N | 0
2025-11-17 | 19 | 2031-11-17 18:00 | 5.59 | 7.0316 | N | 0
2025-11-17 | 20 | 2031-11-17 19:00 | 5.92 | 7.4467 | N | 0
2025-11-17 | 21 | 2031-11-17 20:00 | 6.71 | 8.4404 | N | 0
2025-11-17 | 22 | 2031-11-17 21:00 | 7.04 | 8.8555 | N | 0
2025-11-17 | 23 | 2031-11-17 22:00 | 6.81 | 8.5662 | N | 0
2025-11-18 | 00 | 2031-11-17 23:00 | 6.49 | 8.1637 | N | 0
2025-11-18 | 01 | 2031-11-18 | 6.38 | 8.0253 | N | 0
2025-11-18 | 02 | 2031-11-18 01:00 | 6.01 | 7.5599 | N | 0
2025-11-18 | 03 | 2031-11-18 02:00 | 5.43 | 6.8303 | N | 0
2025-11-18 | 04 | 2031-11-18 03:00 | 4.78 | 6.0127 | N | 0
2025-11-18 | 05 | 2031-11-18 04:00 | 4.46 | 5.6102 | N | 0
2025-11-18 | 06 | 2031-11-18 05:00 | 4.07 | 5.1196 | N | 0
2025-11-18 | 07 | 2031-11-18 06:00 | 3.89 | 4.8932 | N | 0
2025-11-18 | 08 | 2031-11-18 07:00 | 3.92 | 4.9309 | N | 0
2025-11-18 | 09 | 2031-11-18 08:00 | 3.9 | 4.9057 | N | 0
2025-11-18 | 10 | 2031-11-18 09:00 | 4.16 | 5.2328 | N | 0
2025-11-18 | 11 | 2031-11-18 10:00 | 4.71 | 5.9246 | N | 0
2025-11-18 | 12 | 2031-11-18 11:00 | 5.21 | 6.5536 | N | 0
2025-11-18 | 13 | 2031-11-18 12:00 | 5.28 | 6.6416 | N | 0
2025-11-18 | 14 | 2031-11-18 13:00 | 5.23 | 6.5787 | N | 0
2025-11-18 | 15 | 2031-11-18 14:00 | 5.24 | 6.5913 | N | 0
2025-11-18 | 16 | 2031-11-18 15:00 | 5.29 | 6.6542 | N | 0
2025-11-18 | 17 | 2031-11-18 16:00 | 5.43 | 6.8303 | N | 0
2025-11-18 | 18 | 2031-11-18 17:00 | 5.41 | 6.8051 | N | 0
2025-11-18 | 19 | 2031-11-18 18:00 | 5.38 | 6.7674 | N | 0
2025-11-18 | 20 | 2031-11-18 19:00 | 5.64 | 7.0945 | N | 0
2025-11-18 | 21 | 2031-11-18 20:00 | 6.32 | 7.9498 | N | 0
2025-11-18 | 22 | 2031-11-18 21:00 | 6.72 | 8.453 | N | 0
2025-11-18 | 23 | 2031-11-18 22:00 | 6.69 | 8.4152 | N | 0
2025-11-19 | 00 | 2031-11-18 23:00 | 6.5 | 8.1762 | N | 0
2025-11-19 | 01 | 2031-11-19 | 6.5 | 8.1762 | N | 0
2025-11-19 | 02 | 2031-11-19 01:00 | 6.09 | 7.6605 | N | 0
2025-11-19 | 03 | 2031-11-19 02:00 | 5.52 | 6.9435 | N | 0
2025-11-19 | 04 | 2031-11-19 03:00 | 4.94 | 6.2139 | N | 0
2025-11-19 | 05 | 2031-11-19 04:00 | 4.44 | 5.585 | N | 0
2025-11-19 | 06 | 2031-11-19 05:00 | 4.18 | 5.2579 | N | 0
2025-11-19 | 07 | 2031-11-19 06:00 | 4.03 | 5.0693 | N | 0
2025-11-19 | 08 | 2031-11-19 07:00 | 3.99 | 5.0189 | N | 0
2025-11-19 | 09 | 2031-11-19 08:00 | 4.05 | 5.0944 | N | 0
2025-11-19 | 10 | 2031-11-19 09:00 | 4.33 | 5.4466 | N | 0
2025-11-19 | 11 | 2031-11-19 10:00 | 4.78 | 6.0127 | N | 0
2025-11-19 | 12 | 2031-11-19 11:00 | 5.22 | 6.5661 | N | 0
2025-11-19 | 13 | 2031-11-19 12:00 | 5.14 | 6.4655 | N | 0
2025-11-19 | 14 | 2031-11-19 13:00 | 5.02 | 6.3146 | N | 0
2025-11-19 | 15 | 2031-11-19 14:00 | 5.01 | 6.302 | N | 0
2025-11-19 | 16 | 2031-11-19 15:00 | 5 | 6.2894 | N | 0
2025-11-19 | 17 | 2031-11-19 16:00 | 5.14 | 6.4655 | N | 0
2025-11-19 | 18 | 2031-11-19 17:00 | 4.99 | 6.2768 | N | 0
2025-11-19 | 19 | 2031-11-19 18:00 | 5 | 6.2894 | N | 0
2025-11-19 | 20 | 2031-11-19 19:00 | 5.25 | 6.6039 | N | 0
2025-11-19 | 21 | 2031-11-19 20:00 | 6.14 | 7.7234 | N | 0
2025-11-19 | 22 | 2031-11-19 21:00 | 6.62 | 8.3272 | N | 0
2025-11-19 | 23 | 2031-11-19 22:00 | 6.54 | 8.2265 | N | 0
2025-11-20 | 00 | 2031-11-19 23:00 | 6.38 | 8.0253 | N | 0
2025-11-20 | 01 | 2031-11-20 | 6.18 | 7.7737 | N | 0
2025-11-20 | 02 | 2031-11-20 01:00 | 5.98 | 7.5221 | N | 0
2025-11-20 | 03 | 2031-11-20 02:00 | 5.33 | 6.7045 | N | 0
2025-11-20 | 04 | 2031-11-20 03:00 | 4.8 | 6.0378 | N | 0
2025-11-20 | 05 | 2031-11-20 04:00 | 4.37 | 5.4969 | N | 0
2025-11-20 | 06 | 2031-11-20 05:00 | 3.91 | 4.9183 | N | 0
2025-11-20 | 07 | 2031-11-20 06:00 | 3.78 | 4.7548 | N | 0
2025-11-20 | 08 | 2031-11-20 07:00 | 3.78 | 4.7548 | N | 0
2025-11-20 | 09 | 2031-11-20 08:00 | 3.92 | 4.9309 | N | 0
2025-11-20 | 10 | 2031-11-20 09:00 | 4.17 | 5.2454 | N | 0
2025-11-20 | 11 | 2031-11-20 10:00 | 4.75 | 5.9749 | N | 0
2025-11-20 | 12 | 2031-11-20 11:00 | 5.22 | 6.5661 | N | 0
2025-11-20 | 13 | 2031-11-20 12:00 | 5.32 | 6.6919 | N | 0
2025-11-20 | 14 | 2031-11-20 13:00 | 5.07 | 6.3775 | N | 0
2025-11-20 | 15 | 2031-11-20 14:00 | 4.92 | 6.1888 | N | 0
2025-11-20 | 16 | 2031-11-20 15:00 | 4.9 | 6.1636 | N | 0
2025-11-20 | 17 | 2031-11-20 16:00 | 5.07 | 6.3775 | N | 0
2025-11-20 | 18 | 2031-11-20 17:00 | 4.91 | 6.1762 | N | 0
2025-11-20 | 19 | 2031-11-20 18:00 | 4.9 | 6.1636 | N | 0
2025-11-20 | 20 | 2031-11-20 19:00 | 5.25 | 6.6039 | N | 0
2025-11-20 | 21 | 2031-11-20 20:00 | 6.05 | 7.6102 | N | 0
2025-11-20 | 22 | 2031-11-20 21:00 | 6.58 | 8.2769 | N | 0
2025-11-20 | 23 | 2031-11-20 22:00 | 6.37 | 8.0127 | N | 0
2025-11-21 | 00 | 2031-11-20 23:00 | 6.38 | 8.0253 | N | 0
2025-11-21 | 01 | 2031-11-21 | 6.17 | 7.7611 | N | 0
2025-11-21 | 02 | 2031-11-21 01:00 | 5.99 | 7.5347 | N | 0
2025-11-21 | 03 | 2031-11-21 02:00 | 5.24 | 6.5913 | N | 0
2025-11-21 | 04 | 2031-11-21 03:00 | 4.68 | 5.8869 | N | 0
2025-11-21 | 05 | 2031-11-21 04:00 | 4.31 | 5.4215 | N | 0
2025-11-21 | 06 | 2031-11-21 05:00 | 3.98 | 5.0064 | N | 0
2025-11-21 | 07 | 2031-11-21 06:00 | 3.65 | 4.5913 | N | 0
2025-11-21 | 08 | 2031-11-21 07:00 | 3.62 | 4.5535 | N | 0
2025-11-21 | 09 | 2031-11-21 08:00 | 3.59 | 4.5158 | N | 0
2025-11-21 | 10 | 2031-11-21 09:00 | 3.91 | 4.9183 | N | 0
2025-11-21 | 11 | 2031-11-21 10:00 | 4.37 | 5.4969 | N | 0
2025-11-21 | 12 | 2031-11-21 11:00 | 4.78 | 6.0127 | N | 0
2025-11-21 | 13 | 2031-11-21 12:00 | 4.93 | 6.2014 | N | 0
2025-11-21 | 14 | 2031-11-21 13:00 | 5.07 | 6.3775 | N | 0
2025-11-21 | 15 | 2031-11-21 14:00 | 5 | 6.2894 | N | 0
2025-11-21 | 16 | 2031-11-21 15:00 | 5.15 | 6.4781 | N | 0
2025-11-21 | 17 | 2031-11-21 16:00 | 5.24 | 6.5913 | N | 0
2025-11-21 | 18 | 2031-11-21 17:00 | 5.36 | 6.7422 | N | 0
2025-11-21 | 19 | 2031-11-21 18:00 | 5.06 | 6.3649 | N | 0
2025-11-21 | 20 | 2031-11-21 19:00 | 5.25 | 6.6039 | N | 0
2025-11-21 | 21 | 2031-11-21 20:00 | 5.74 | 7.2202 | N | 0
2025-11-21 | 22 | 2031-11-21 21:00 | 6.22 | 7.824 | N | 0
2025-11-21 | 23 | 2031-11-21 22:00 | 6.03 | 7.585 | N | 0
2025-11-22 | 00 | 2031-11-21 23:00 | 6.04 | 7.5976 | N | 0
2025-11-22 | 01 | 2031-11-22 | 5.97 | 7.5096 | N | 0
2025-11-22 | 02 | 2031-11-22 01:00 | 5.78 | 7.2706 | N | 0
2025-11-22 | 03 | 2031-11-22 02:00 | 5.33 | 6.7045 | N | 0
2025-11-22 | 04 | 2031-11-22 03:00 | 4.93 | 6.2014 | N | 0
2025-11-22 | 05 | 2031-11-22 04:00 | 4.5 | 5.6605 | N | 0
2025-11-22 | 06 | 2031-11-22 05:00 | 4.11 | 5.1699 | N | 0
2025-11-22 | 07 | 2031-11-22 06:00 | 3.94 | 4.9561 | N | 0
2025-11-22 | 08 | 2031-11-22 07:00 | 3.81 | 4.7925 | N | 0
2025-11-22 | 09 | 2031-11-22 08:00 | 3.72 | 4.6793 | N | 0
2025-11-22 | 10 | 2031-11-22 09:00 | 3.81 | 4.7925 | N | 0
2025-11-22 | 11 | 2031-11-22 10:00 | 4.08 | 5.1322 | N | 0
2025-11-22 | 12 | 2031-11-22 11:00 | 4.5 | 5.6605 | N | 0
2025-11-22 | 13 | 2031-11-22 12:00 | 4.82 | 6.063 | N | 0
2025-11-22 | 14 | 2031-11-22 13:00 | 5.18 | 6.5158 | N | 0
2025-11-22 | 15 | 2031-11-22 14:00 | 5.18 | 6.5158 | N | 0
2025-11-22 | 16 | 2031-11-22 15:00 | 5.44 | 6.8429 | N | 0
2025-11-22 | 17 | 2031-11-22 16:00 | 5.6 | 7.0441 | N | 0
2025-11-22 | 18 | 2031-11-22 17:00 | 5.62 | 7.0693 | N | 0
2025-11-22 | 19 | 2031-11-22 18:00 | 5.63 | 7.0819 | N | 0
2025-11-22 | 20 | 2031-11-22 19:00 | 5.81 | 7.3083 | N | 0
2025-11-22 | 21 | 2031-11-22 20:00 | 6.2 | 7.7989 | N | 0
2025-11-22 | 22 | 2031-11-22 21:00 | 6.42 | 8.0756 | N | 0
2025-11-22 | 23 | 2031-11-22 22:00 | 6.28 | 7.8995 | N | 0
2025-11-23 | 00 | 2031-11-22 23:00 | 6.09 | 7.6605 | N | 0
2025-11-23 | 01 | 2031-11-23 | 5.84 | 7.346 | N | 0
2025-11-23 | 02 | 2031-11-23 01:00 | 5.63 | 7.0819 | N | 0
2025-11-23 | 03 | 2031-11-23 02:00 | 5.34 | 6.7171 | N | 0
2025-11-23 | 04 | 2031-11-23 03:00 | 4.89 | 6.151 | N | 0
2025-11-23 | 05 | 2031-11-23 04:00 | 4.52 | 5.6856 | N | 0
2025-11-23 | 06 | 2031-11-23 05:00 | 4.28 | 5.3837 | N | 0
2025-11-23 | 07 | 2031-11-23 06:00 | 4.02 | 5.0567 | N | 0
2025-11-23 | 08 | 2031-11-23 07:00 | 3.86 | 4.8554 | N | 0
2025-11-23 | 09 | 2031-11-23 08:00 | 3.78 | 4.7548 | N | 0
2025-11-23 | 10 | 2031-11-23 09:00 | 3.81 | 4.7925 | N | 0
2025-11-23 | 11 | 2031-11-23 10:00 | 4.02 | 5.0567 | N | 0
2025-11-23 | 12 | 2031-11-23 11:00 | 4.29 | 5.3963 | N | 0
2025-11-23 | 13 | 2031-11-23 12:00 | 4.83 | 6.0756 | N | 0
2025-11-23 | 14 | 2031-11-23 13:00 | 5.17 | 6.5032 | N | 0
2025-11-23 | 15 | 2031-11-23 14:00 | 5.49 | 6.9058 | N | 0
2025-11-23 | 16 | 2031-11-23 15:00 | 5.53 | 6.9561 | N | 0
2025-11-23 | 17 | 2031-11-23 16:00 | 5.7 | 7.1699 | N | 0
2025-11-23 | 18 | 2031-11-23 17:00 | 5.82 | 7.3209 | N | 0
2025-11-23 | 19 | 2031-11-23 18:00 | 5.81 | 7.3083 | N | 0
2025-11-23 | 20 | 2031-11-23 19:00 | 6.01 | 7.5599 | N | 0
2025-11-23 | 21 | 2031-11-23 20:00 | 6.75 | 8.4907 | N | 0
2025-11-23 | 22 | 2031-11-23 21:00 | 7 | 8.8052 | N | 0
2025-11-23 | 23 | 2031-11-23 22:00 | 6.82 | 8.5788 | N | 0
2025-11-24 | 00 | 2031-11-23 23:00 | 6.36 | 8.0001 | N | 0
2025-11-24 | 01 | 2031-11-24 | 6.34 | 7.975 | N | 0
2025-11-24 | 02 | 2031-11-24 01:00 | 5.86 | 7.3712 | N | 0
2025-11-24 | 03 | 2031-11-24 02:00 | 5.34 | 6.7171 | N | 0
2025-11-24 | 04 | 2031-11-24 03:00 | 4.71 | 5.9246 | N | 0
2025-11-24 | 05 | 2031-11-24 04:00 | 4.15 | 5.2202 | N | 0
2025-11-24 | 06 | 2031-11-24 05:00 | 3.9 | 4.9057 | N | 0
2025-11-24 | 07 | 2031-11-24 06:00 | 3.71 | 4.6667 | N | 0
2025-11-24 | 08 | 2031-11-24 07:00 | 3.7 | 4.6542 | N | 0
2025-11-24 | 09 | 2031-11-24 08:00 | 3.81 | 4.7925 | N | 0
2025-11-24 | 10 | 2031-11-24 09:00 | 4.21 | 5.2957 | N | 0
2025-11-24 | 11 | 2031-11-24 10:00 | 4.7 | 5.912 | N | 0
2025-11-24 | 12 | 2031-11-24 11:00 | 5.17 | 6.5032 | N | 0
2025-11-24 | 13 | 2031-11-24 12:00 | 5.18 | 6.5158 | N | 0
2025-11-24 | 14 | 2031-11-24 13:00 | 5.11 | 6.4278 | N | 0
2025-11-24 | 15 | 2031-11-24 14:00 | 5.05 | 6.3523 | N | 0
2025-11-24 | 16 | 2031-11-24 15:00 | 5.01 | 6.302 | N | 0
2025-11-24 | 17 | 2031-11-24 16:00 | 5.12 | 6.4404 | N | 0
2025-11-24 | 18 | 2031-11-24 17:00 | 5.08 | 6.39 | N | 0
2025-11-24 | 19 | 2031-11-24 18:00 | 5.7 | 7.1699 | N | 0
2025-11-24 | 20 | 2031-11-24 19:00 | 5.97 | 7.5096 | N | 0
2025-11-24 | 21 | 2031-11-24 20:00 | 7.05 | 8.8681 | N | 0
2025-11-24 | 22 | 2031-11-24 21:00 | 7.57 | 9.5222 | N | 0
2025-11-24 | 23 | 2031-11-24 22:00 | 7.32 | 9.2077 | N | 0
2025-11-25 | 00 | 2031-11-24 23:00 | 7.08 | 8.9058 | N | 0
2025-11-25 | 01 | 2031-11-25 | 6.86 | 8.6291 | N | 0
2025-11-25 | 02 | 2031-11-25 01:00 | 6.65 | 8.3649 | N | 0
2025-11-25 | 03 | 2031-11-25 02:00 | 5.94 | 7.4718 | N | 0
2025-11-25 | 04 | 2031-11-25 03:00 | 5.23 | 6.5787 | N | 0
2025-11-25 | 05 | 2031-11-25 04:00 | 4.68 | 5.8869 | N | 0
2025-11-25 | 06 | 2031-11-25 05:00 | 4.28 | 5.3837 | N | 0
2025-11-25 | 07 | 2031-11-25 06:00 | 4.15 | 5.2202 | N | 0
2025-11-25 | 08 | 2031-11-25 07:00 | 3.99 | 5.0189 | N | 0
2025-11-25 | 09 | 2031-11-25 08:00 | 4.11 | 5.1699 | N | 0
2025-11-25 | 10 | 2031-11-25 09:00 | 4.39 | 5.5221 | N | 0
2025-11-25 | 11 | 2031-11-25 10:00 | 4.99 | 6.2768 | N | 0
2025-11-25 | 12 | 2031-11-25 11:00 | 5.39 | 6.78 | N | 0
2025-11-25 | 13 | 2031-11-25 12:00 | 5.52 | 6.9435 | N | 0
2025-11-25 | 14 | 2031-11-25 13:00 | 5.44 | 6.8429 | N | 0
2025-11-25 | 15 | 2031-11-25 14:00 | 5.5 | 6.9183 | N | 0
2025-11-25 | 16 | 2031-11-25 15:00 | 5.5 | 6.9183 | N | 0
2025-11-25 | 17 | 2031-11-25 16:00 | 5.57 | 7.0064 | N | 0
2025-11-25 | 18 | 2031-11-25 17:00 | 5.69 | 7.1573 | N | 0
2025-11-25 | 19 | 2031-11-25 18:00 | 5.57 | 7.0064 | N | 0
2025-11-25 | 20 | 2031-11-25 19:00 | 5.94 | 7.4718 | N | 0
2025-11-25 | 21 | 2031-11-25 20:00 | 6.92 | 8.7045 | N | 0
2025-11-25 | 22 | 2031-11-25 21:00 | 7.3 | 9.1825 | N | 0
2025-11-25 | 23 | 2031-11-25 22:00 | 7.12 | 8.9561 | N | 0
2025-11-26 | 00 | 2031-11-25 23:00 | 6.9 | 8.6794 | N | 0
2025-11-26 | 01 | 2031-11-26 | 6.68 | 8.4026 | N | 0
2025-11-26 | 02 | 2031-11-26 01:00 | 6.4 | 8.0504 | N | 0
2025-11-26 | 03 | 2031-11-26 02:00 | 5.67 | 7.1322 | N | 0
2025-11-26 | 04 | 2031-11-26 03:00 | 4.91 | 6.1762 | N | 0
2025-11-26 | 05 | 2031-11-26 04:00 | 4.52 | 5.6856 | N | 0
2025-11-26 | 06 | 2031-11-26 05:00 | 4.06 | 5.107 | N | 0
2025-11-26 | 07 | 2031-11-26 06:00 | 3.92 | 4.9309 | N | 0
2025-11-26 | 08 | 2031-11-26 07:00 | 3.77 | 4.7422 | N | 0
2025-11-26 | 09 | 2031-11-26 08:00 | 3.86 | 4.8554 | N | 0
2025-11-26 | 10 | 2031-11-26 09:00 | 4.15 | 5.2202 | N | 0
2025-11-26 | 11 | 2031-11-26 10:00 | 4.75 | 5.9749 | N | 0
2025-11-26 | 12 | 2031-11-26 11:00 | 5.23 | 6.5787 | N | 0
2025-11-26 | 13 | 2031-11-26 12:00 | 5.23 | 6.5787 | N | 0
2025-11-26 | 14 | 2031-11-26 13:00 | 5.23 | 6.5787 | N | 0
2025-11-26 | 15 | 2031-11-26 14:00 | 5.3 | 6.6668 | N | 0
2025-11-26 | 16 | 2031-11-26 15:00 | 5.42 | 6.8177 | N | 0
2025-11-26 | 17 | 2031-11-26 16:00 | 5.61 | 7.0567 | N | 0
2025-11-26 | 18 | 2031-11-26 17:00 | 5.57 | 7.0064 | N | 0
2025-11-26 | 19 | 2031-11-26 18:00 | 5.74 | 7.2202 | N | 0
2025-11-26 | 20 | 2031-11-26 19:00 | 6.01 | 7.5599 | N | 0
2025-11-26 | 21 | 2031-11-26 20:00 | 7.02 | 8.8303 | N | 0
2025-11-26 | 22 | 2031-11-26 21:00 | 7.53 | 9.4718 | N | 0
2025-11-26 | 23 | 2031-11-26 22:00 | 15.86 | 19.95 | Y | 9.31 | 1
2025-11-27 | 00 | 2031-11-26 23:00 | 13.15 | 16.5411 | Y | 5.9011 | 2
2025-11-27 | 01 | 2031-11-27 | 13.19 | 16.5915 | Y | 5.9515 | 3
2025-11-27 | 02 | 2031-11-27 01:00 | 12.54 | 15.7738 | Y | 5.1338 | 4
2025-11-27 | 03 | 2031-11-27 02:00 | 11.47 | 14.4279 | Y | 3.7879 | 5
2025-11-27 | 04 | 2031-11-27 03:00 | 10.13 | 12.7423 | Y | 2.1023 | 6
2025-11-27 | 05 | 2031-11-27 04:00 | 9.34 | 11.7486 | Y | 1.1086 | 7
2025-11-27 | 06 | 2031-11-27 05:00 | 8.65 | 10.8807 | Y | 0.24067 | 8 | 8
2025-11-27 | 07 | 2031-11-27 06:00 | 8.35 | 10.5033 | N | 0
2025-11-27 | 08 | 2031-11-27 07:00 | 8.13 | 10.2266 | N | 0
2025-11-27 | 09 | 2031-11-27 08:00 | 8.15 | 10.2517 | N | 0
2025-11-27 | 10 | 2031-11-27 09:00 | 8.73 | 10.9813 | Y | 0.34131 | 1
2025-11-27 | 11 | 2031-11-27 10:00 | 10.12 | 12.7298 | Y | 2.0898 | 2
2025-11-27 | 12 | 2031-11-27 11:00 | 11.28 | 14.1889 | Y | 3.5489 | 3
2025-11-27 | 13 | 2031-11-27 12:00 | 11.57 | 14.5537 | Y | 3.9137 | 4
2025-11-27 | 14 | 2031-11-27 13:00 | 11.85 | 14.9059 | Y | 4.2659 | 5
2025-11-27 | 15 | 2031-11-27 14:00 | 11.83 | 14.8807 | Y | 4.2407 | 6
2025-11-27 | 16 | 2031-11-27 15:00 | 11.87 | 14.9311 | Y | 4.2911 | 7
2025-11-27 | 17 | 2031-11-27 16:00 | 11.78 | 14.8178 | Y | 4.1778 | 8
2025-11-27 | 18 | 2031-11-27 17:00 | 11.84 | 14.8933 | Y | 4.2533 | 9
2025-11-27 | 19 | 2031-11-27 18:00 | 12.05 | 15.1575 | Y | 4.5175 | 10
2025-11-27 | 20 | 2031-11-27 19:00 | 11.59 | 14.5788 | Y | 3.9388 | 11 | 11
2025-11-27 | 21 | 2031-11-27 20:00 | 7.34 | 9.2328 | N | 0
2025-11-27 | 22 | 2031-11-27 21:00 | 7.64 | 9.6102 | N | 0
2025-11-27 | 23 | 2031-11-27 22:00 | 7.58 | 9.5347 | N | 0
2025-11-28 | 00 | 2031-11-27 23:00 | 7.47 | 9.3964 | N | 0
2025-11-28 | 01 | 2031-11-28 | 7.32 | 9.2077 | N | 0
2025-11-28 | 02 | 2031-11-28 01:00 | 7.1 | 8.931 | N | 0
2025-11-28 | 03 | 2031-11-28 02:00 | 6.28 | 7.8995 | N | 0
2025-11-28 | 04 | 2031-11-28 03:00 | 5.57 | 7.0064 | N | 0
2025-11-28 | 05 | 2031-11-28 04:00 | 5.02 | 6.3146 | N | 0
2025-11-28 | 06 | 2031-11-28 05:00 | 4.79 | 6.0253 | N | 0
2025-11-28 | 07 | 2031-11-28 06:00 | 4.52 | 5.6856 | N | 0
2025-11-28 | 08 | 2031-11-28 07:00 | 4.52 | 5.6856 | N | 0
2025-11-28 | 09 | 2031-11-28 08:00 | 4.52 | 5.6856 | N | 0
2025-11-28 | 10 | 2031-11-28 09:00 | 4.85 | 6.1007 | N | 0
2025-11-28 | 11 | 2031-11-28 10:00 | 5.49 | 6.9058 | N | 0
2025-11-28 | 12 | 2031-11-28 11:00 | 5.83 | 7.3334 | N | 0
2025-11-28 | 13 | 2031-11-28 12:00 | 6.01 | 7.5599 | N | 0
2025-11-28 | 14 | 2031-11-28 13:00 | 6.05 | 7.6102 | N | 0
2025-11-28 | 15 | 2031-11-28 14:00 | 6.21 | 7.8114 | N | 0
2025-11-28 | 16 | 2031-11-28 15:00 | 6.31 | 7.9372 | N | 0
2025-11-28 | 17 | 2031-11-28 16:00 | 6.61 | 8.3146 | N | 0
2025-11-28 | 18 | 2031-11-28 17:00 | 6.6 | 8.302 | N | 0
2025-11-28 | 19 | 2031-11-28 18:00 | 6.53 | 8.214 | N | 0
2025-11-28 | 20 | 2031-11-28 19:00 | 6.72 | 8.453 | N | 0
2025-11-28 | 21 | 2031-11-28 20:00 | 7.42 | 9.3335 | N | 0
2025-11-28 | 22 | 2031-11-28 21:00 | 7.75 | 9.7486 | N | 0
2025-11-28 | 23 | 2031-11-28 22:00 | 7.74 | 9.736 | N | 0
2025-11-29 | 00 | 2031-11-28 23:00 | 7.45 | 9.3712 | N | 0
2025-11-29 | 01 | 2031-11-29 | 7.27 | 9.1448 | N | 0
2025-11-29 | 02 | 2031-11-29 01:00 | 7.18 | 9.0316 | N | 0
2025-11-29 | 03 | 2031-11-29 02:00 | 6.51 | 8.1888 | N | 0
2025-11-29 | 04 | 2031-11-29 03:00 | 6.03 | 7.585 | N | 0
2025-11-29 | 05 | 2031-11-29 04:00 | 5.37 | 6.7548 | N | 0
2025-11-29 | 06 | 2031-11-29 05:00 | 5.01 | 6.302 | N | 0
2025-11-29 | 07 | 2031-11-29 06:00 | 4.74 | 5.9624 | N | 0
2025-11-29 | 08 | 2031-11-29 07:00 | 4.62 | 5.8114 | N | 0
2025-11-29 | 09 | 2031-11-29 08:00 | 4.58 | 5.7611 | N | 0
2025-11-29 | 10 | 2031-11-29 09:00 | 4.67 | 5.8743 | N | 0
2025-11-29 | 11 | 2031-11-29 10:00 | 4.96 | 6.2391 | N | 0
2025-11-29 | 12 | 2031-11-29 11:00 | 5.51 | 6.9309 | N | 0
2025-11-29 | 13 | 2031-11-29 12:00 | 5.84 | 7.346 | N | 0
2025-11-29 | 14 | 2031-11-29 13:00 | 6.11 | 7.6857 | N | 0
2025-11-29 | 15 | 2031-11-29 14:00 | 6.31 | 7.9372 | N | 0
2025-11-29 | 16 | 2031-11-29 15:00 | 6.32 | 7.9498 | N | 0
2025-11-29 | 17 | 2031-11-29 16:00 | 6.54 | 8.2265 | N | 0
2025-11-29 | 18 | 2031-11-29 17:00 | 6.46 | 8.1259 | N | 0
2025-11-29 | 19 | 2031-11-29 18:00 | 6.46 | 8.1259 | N | 0
2025-11-29 | 20 | 2031-11-29 19:00 | 6.75 | 8.4907 | N | 0
2025-11-29 | 21 | 2031-11-29 20:00 | 7.31 | 9.1951 | N | 0
2025-11-29 | 22 | 2031-11-29 21:00 | 7.63 | 9.5976 | N | 0
2025-11-29 | 23 | 2031-11-29 22:00 | 7.32 | 9.2077 | N | 0
2025-11-30 | 00 | 2031-11-29 23:00 | 7.09 | 8.9184 | N | 0
2025-11-30 | 01 | 2031-11-30 | 7.09 | 8.9184 | N | 0
2025-11-30 | 02 | 2031-11-30 01:00 | 6.79 | 8.541 | N | 0
2025-11-30 | 03 | 2031-11-30 02:00 | 6.29 | 7.9121 | N | 0
2025-11-30 | 04 | 2031-11-30 03:00 | 5.77 | 7.258 | N | 0
2025-11-30 | 05 | 2031-11-30 04:00 | 5.23 | 6.5787 | N | 0
2025-11-30 | 06 | 2031-11-30 05:00 | 4.81 | 6.0504 | N | 0
2025-11-30 | 07 | 2031-11-30 06:00 | 4.64 | 5.8366 | N | 0
2025-11-30 | 08 | 2031-11-30 07:00 | 4.55 | 5.7234 | N | 0
2025-11-30 | 09 | 2031-11-30 08:00 | 4.48 | 5.6353 | N | 0
2025-11-30 | 10 | 2031-11-30 09:00 | 4.5 | 5.6605 | N | 0
2025-11-30 | 11 | 2031-11-30 10:00 | 4.76 | 5.9875 | N | 0
2025-11-30 | 12 | 2031-11-30 11:00 | 5.27 | 6.629 | N | 0
2025-11-30 | 13 | 2031-11-30 12:00 | 5.61 | 7.0567 | N | 0
2025-11-30 | 14 | 2031-11-30 13:00 | 6.13 | 7.7108 | N | 0
2025-11-30 | 15 | 2031-11-30 14:00 | 6.59 | 8.2894 | N | 0
2025-11-30 | 16 | 2031-11-30 15:00 | 6.96 | 8.7549 | N | 0
2025-11-30 | 17 | 2031-11-30 16:00 | 7.17 | 9.019 | N | 0
2025-11-30 | 18 | 2031-11-30 17:00 | 7.17 | 9.019 | N | 0
2025-11-30 | 19 | 2031-11-30 18:00 | 7.35 | 9.2454 | N | 0
2025-11-30 | 20 | 2031-11-30 19:00 | 7.6 | 9.5599 | N | 0
2025-11-30 | 21 | 2031-11-30 20:00 | 8.25 | 10.3775 | N | 0
2025-11-30 | 22 | 2031-11-30 21:00 | 8.42 | 10.5914 | N | 0
2025-11-30 | 23 | 2031-11-30 22:00 | 8.26 | 10.3901 | N | 0
2026-12-01 | 00 | 2031-11-30 23:00 | 7.74 | 9.736 | N | 0
2026-12-01 | 01 | 2031-12-01 | 7.5 | 9.4341 | N | 0
2026-12-01 | 02 | 2031-12-01 01:00 | 7.08 | 8.9058 | N | 0
2026-12-01 | 03 | 2031-12-01 02:00 | 6.64 | 8.3523 | N | 0
2026-12-01 | 04 | 2031-12-01 03:00 | 5.75 | 7.2328 | N | 0
2026-12-01 | 05 | 2031-12-01 04:00 | 5.23 | 6.5787 | N | 0
2026-12-01 | 06 | 2031-12-01 05:00 | 4.82 | 6.063 | N | 0
2026-12-01 | 07 | 2031-12-01 06:00 | 4.56 | 5.7359 | N | 0
2026-12-01 | 08 | 2031-12-01 07:00 | 4.56 | 5.7359 | N | 0
2026-12-01 | 09 | 2031-12-01 08:00 | 4.71 | 5.9246 | N | 0
2026-12-01 | 10 | 2031-12-01 09:00 | 5.16 | 6.4907 | N | 0
2026-12-01 | 11 | 2031-12-01 10:00 | 5.84 | 7.346 | N | 0
2026-12-01 | 12 | 2031-12-01 11:00 | 6.16 | 7.7485 | N | 0
2026-12-01 | 13 | 2031-12-01 12:00 | 6.28 | 7.8995 | N | 0
2026-12-01 | 14 | 2031-12-01 13:00 | 6.09 | 7.6605 | N | 0
2026-12-01 | 15 | 2031-12-01 14:00 | 6.08 | 7.6479 | N | 0
2026-12-01 | 16 | 2031-12-01 15:00 | 6.21 | 7.8114 | N | 0
2026-12-01 | 17 | 2031-12-01 16:00 | 6.32 | 7.9498 | N | 0
2026-12-01 | 18 | 2031-12-01 17:00 | 6.33 | 7.9624 | N | 0
2026-12-01 | 19 | 2031-12-01 18:00 | 6.42 | 8.0756 | N | 0
2026-12-01 | 20 | 2031-12-01 19:00 | 6.7 | 8.4278 | N | 0
2026-12-01 | 21 | 2031-12-01 20:00 | 7.83 | 9.8492 | N | 0
2026-12-01 | 22 | 2031-12-01 21:00 | 8.32 | 10.4656 | N | 0
2026-12-01 | 23 | 2031-12-01 22:00 | 8.07 | 10.1511 | N | 0
2026-12-02 | 00 | 2031-12-01 23:00 | 7.83 | 9.8492 | N | 0
2026-12-02 | 01 | 2031-12-02 | 7.83 | 9.8492 | N | 0
2026-12-02 | 02 | 2031-12-02 01:00 | 7.38 | 9.2832 | N | 0
2026-12-02 | 03 | 2031-12-02 02:00 | 6.84 | 8.6039 | N | 0
2026-12-02 | 04 | 2031-12-02 03:00 | 6.07 | 7.6353 | N | 0
2026-12-02 | 05 | 2031-12-02 04:00 | 5.44 | 6.8429 | N | 0
2026-12-02 | 06 | 2031-12-02 05:00 | 4.94 | 6.2139 | N | 0
2026-12-02 | 07 | 2031-12-02 06:00 | 4.78 | 6.0127 | N | 0
2026-12-02 | 08 | 2031-12-02 07:00 | 4.7 | 5.912 | N | 0
2026-12-02 | 09 | 2031-12-02 08:00 | 4.69 | 5.8995 | N | 0
2026-12-02 | 10 | 2031-12-02 09:00 | 5.09 | 6.4026 | N | 0
2026-12-02 | 11 | 2031-12-02 10:00 | 5.6 | 7.0441 | N | 0
2026-12-02 | 12 | 2031-12-02 11:00 | 6.08 | 7.6479 | N | 0
2026-12-02 | 13 | 2031-12-02 12:00 | 6.19 | 7.7863 | N | 0
2026-12-02 | 14 | 2031-12-02 13:00 | 6.21 | 7.8114 | N | 0
2026-12-02 | 15 | 2031-12-02 14:00 | 6.02 | 7.5724 | N | 0
2026-12-02 | 16 | 2031-12-02 15:00 | 6.01 | 7.5599 | N | 0
2026-12-02 | 17 | 2031-12-02 16:00 | 6.01 | 7.5599 | N | 0
2026-12-02 | 18 | 2031-12-02 17:00 | 5.92 | 7.4467 | N | 0
2026-12-02 | 19 | 2031-12-02 18:00 | 5.99 | 7.5347 | N | 0
2026-12-02 | 20 | 2031-12-02 19:00 | 6.47 | 8.1385 | N | 0
2026-12-02 | 21 | 2031-12-02 20:00 | 7.42 | 9.3335 | N | 0
2026-12-02 | 22 | 2031-12-02 21:00 | 8.09 | 10.1763 | N | 0
2026-12-02 | 23 | 2031-12-02 22:00 | 7.99 | 10.0505 | N | 0
2026-12-03 | 00 | 2031-12-02 23:00 | 7.81 | 9.8241 | N | 0
2026-12-03 | 01 | 2031-12-03 | 7.84 | 9.8618 | N | 0
2026-12-03 | 02 | 2031-12-03 01:00 | 7.41 | 9.3209 | N | 0
2026-12-03 | 03 | 2031-12-03 02:00 | 6.72 | 8.453 | N | 0
2026-12-03 | 04 | 2031-12-03 03:00 | 6.06 | 7.6228 | N | 0
2026-12-03 | 05 | 2031-12-03 04:00 | 5.45 | 6.8555 | N | 0
2026-12-03 | 06 | 2031-12-03 05:00 | 5.03 | 6.3271 | N | 0
2026-12-03 | 07 | 2031-12-03 06:00 | 4.85 | 6.1007 | N | 0
2026-12-03 | 08 | 2031-12-03 07:00 | 4.9 | 6.1636 | N | 0
2026-12-03 | 09 | 2031-12-03 08:00 | 5 | 6.2894 | N | 0
2026-12-03 | 10 | 2031-12-03 09:00 | 5.32 | 6.6919 | N | 0
2026-12-03 | 11 | 2031-12-03 10:00 | 5.84 | 7.346 | N | 0
2026-12-03 | 12 | 2031-12-03 11:00 | 6.42 | 8.0756 | N | 0
2026-12-03 | 13 | 2031-12-03 12:00 | 6.42 | 8.0756 | N | 0
2026-12-03 | 14 | 2031-12-03 13:00 | 6.42 | 8.0756 | N | 0
2026-12-03 | 15 | 2031-12-03 14:00 | 6.45 | 8.1133 | N | 0
2026-12-03 | 16 | 2031-12-03 15:00 | 6.5 | 8.1762 | N | 0
2026-12-03 | 17 | 2031-12-03 16:00 | 6.62 | 8.3272 | N | 0
2026-12-03 | 18 | 2031-12-03 17:00 | 6.57 | 8.2643 | N | 0
2026-12-03 | 19 | 2031-12-03 18:00 | 6.61 | 8.3146 | N | 0
2026-12-03 | 20 | 2031-12-03 19:00 | 6.81 | 8.5662 | N | 0
2026-12-03 | 21 | 2031-12-03 20:00 | 7.76 | 9.7612 | N | 0
2026-12-03 | 22 | 2031-12-03 21:00 | 8.02 | 10.0882 | N | 0
2026-12-03 | 23 | 2031-12-03 22:00 | 8.02 | 10.0882 | N | 0
2026-12-04 | 00 | 2031-12-03 23:00 | 7.74 | 9.736 | N | 0
2026-12-04 | 01 | 2031-12-04 | 7.74 | 9.736 | N | 0
2026-12-04 | 02 | 2031-12-04 01:00 | 7.46 | 9.3838 | N | 0
2026-12-04 | 03 | 2031-12-04 02:00 | 6.69 | 8.4152 | N | 0
2026-12-04 | 04 | 2031-12-04 03:00 | 6.05 | 7.6102 | N | 0
2026-12-04 | 05 | 2031-12-04 04:00 | 5.31 | 6.6794 | N | 0
2026-12-04 | 06 | 2031-12-04 05:00 | 4.96 | 6.2391 | N | 0
2026-12-04 | 07 | 2031-12-04 06:00 | 4.7 | 5.912 | N | 0
2026-12-04 | 08 | 2031-12-04 07:00 | 4.67 | 5.8743 | N | 0
2026-12-04 | 09 | 2031-12-04 08:00 | 4.82 | 6.063 | N | 0
2026-12-04 | 10 | 2031-12-04 09:00 | 5.12 | 6.4404 | N | 0
2026-12-04 | 11 | 2031-12-04 10:00 | 5.76 | 7.2454 | N | 0
2026-12-04 | 12 | 2031-12-04 11:00 | 6.2 | 7.7989 | N | 0
2026-12-04 | 13 | 2031-12-04 12:00 | 6.2 | 7.7989 | N | 0
2026-12-04 | 14 | 2031-12-04 13:00 | 6.26 | 7.8743 | N | 0
2026-12-04 | 15 | 2031-12-04 14:00 | 6.32 | 7.9498 | N | 0
2026-12-04 | 16 | 2031-12-04 15:00 | 6.31 | 7.9372 | N | 0
2026-12-04 | 17 | 2031-12-04 16:00 | 6.64 | 8.3523 | N | 0
2026-12-04 | 18 | 2031-12-04 17:00 | 6.65 | 8.3649 | N | 0
2026-12-04 | 19 | 2031-12-04 18:00 | 6.54 | 8.2265 | N | 0
2026-12-04 | 20 | 2031-12-04 19:00 | 7.02 | 8.8303 | N | 0
2026-12-04 | 21 | 2031-12-04 20:00 | 8.08 | 10.1637 | N | 0
2026-12-04 | 22 | 2031-12-04 21:00 | 8.47 | 10.6543 | Y | 0.014256 | 1
2026-12-04 | 23 | 2031-12-04 22:00 | 8.47 | 10.6543 | Y | 0.014256 | 2 | 2
2026-12-05 | 00 | 2031-12-04 23:00 | 8.44 | 10.6165 | N | 0
2026-12-05 | 01 | 2031-12-05 | 8.25 | 10.3775 | N | 0
2026-12-05 | 02 | 2031-12-05 01:00 | 8.12 | 10.214 | N | 0
2026-12-05 | 03 | 2031-12-05 02:00 | 7.41 | 9.3209 | N | 0
2026-12-05 | 04 | 2031-12-05 03:00 | 6.71 | 8.4404 | N | 0
2026-12-05 | 05 | 2031-12-05 04:00 | 6.03 | 7.585 | N | 0
2026-12-05 | 06 | 2031-12-05 05:00 | 5.72 | 7.1951 | N | 0
2026-12-05 | 07 | 2031-12-05 06:00 | 5.55 | 6.9812 | N | 0
2026-12-05 | 08 | 2031-12-05 07:00 | 5.39 | 6.78 | N | 0
2026-12-05 | 09 | 2031-12-05 08:00 | 5.45 | 6.8555 | N | 0
2026-12-05 | 10 | 2031-12-05 09:00 | 5.66 | 7.1196 | N | 0
2026-12-05 | 11 | 2031-12-05 10:00 | 6.29 | 7.9121 | N | 0
2026-12-05 | 12 | 2031-12-05 11:00 | 6.69 | 8.4152 | N | 0
2026-12-05 | 13 | 2031-12-05 12:00 | 6.69 | 8.4152 | N | 0
2026-12-05 | 14 | 2031-12-05 13:00 | 6.69 | 8.4152 | N | 0
2026-12-05 | 15 | 2031-12-05 14:00 | 6.69 | 8.4152 | N | 0
2026-12-05 | 16 | 2031-12-05 15:00 | 6.86 | 8.6291 | N | 0
2026-12-05 | 17 | 2031-12-05 16:00 | 6.93 | 8.7171 | N | 0
2026-12-05 | 18 | 2031-12-05 17:00 | 6.73 | 8.4655 | N | 0
2026-12-05 | 19 | 2031-12-05 18:00 | 6.74 | 8.4781 | N | 0
2026-12-05 | 20 | 2031-12-05 19:00 | 7.01 | 8.8177 | N | 0
2026-12-05 | 21 | 2031-12-05 20:00 | 7.86 | 9.8869 | N | 0
2026-12-05 | 22 | 2031-12-05 21:00 | 8.13 | 10.2266 | N | 0
2026-12-05 | 23 | 2031-12-05 22:00 | 7.88 | 9.9121 | N | 0
2026-12-06 | 00 | 2031-12-05 23:00 | 7.84 | 9.8618 | N | 0
2026-12-06 | 01 | 2031-12-06 | 7.66 | 9.6354 | N | 0
2026-12-06 | 02 | 2031-12-06 01:00 | 7.54 | 9.4844 | N | 0
2026-12-06 | 03 | 2031-12-06 02:00 | 6.84 | 8.6039 | N | 0
2026-12-06 | 04 | 2031-12-06 03:00 | 6.33 | 7.9624 | N | 0
2026-12-06 | 05 | 2031-12-06 04:00 | 5.64 | 7.0945 | N | 0
2026-12-06 | 06 | 2031-12-06 05:00 | 5.33 | 6.7045 | N | 0
2026-12-06 | 07 | 2031-12-06 06:00 | 5.01 | 6.302 | N | 0
2026-12-06 | 08 | 2031-12-06 07:00 | 4.85 | 6.1007 | N | 0
2026-12-06 | 09 | 2031-12-06 08:00 | 4.86 | 6.1133 | N | 0
2026-12-06 | 10 | 2031-12-06 09:00 | 4.85 | 6.1007 | N | 0
2026-12-06 | 11 | 2031-12-06 10:00 | 5.07 | 6.3775 | N | 0
2026-12-06 | 12 | 2031-12-06 11:00 | 5.57 | 7.0064 | N | 0
2026-12-06 | 13 | 2031-12-06 12:00 | 6.12 | 7.6982 | N | 0
2026-12-06 | 14 | 2031-12-06 13:00 | 6.5 | 8.1762 | N | 0
2026-12-06 | 15 | 2031-12-06 14:00 | 6.71 | 8.4404 | N | 0
2026-12-06 | 16 | 2031-12-06 15:00 | 6.92 | 8.7045 | N | 0
2026-12-06 | 17 | 2031-12-06 16:00 | 7.14 | 8.9813 | N | 0
2026-12-06 | 18 | 2031-12-06 17:00 | 7.1 | 8.931 | N | 0
2026-12-06 | 19 | 2031-12-06 18:00 | 7.05 | 8.8681 | N | 0
2026-12-06 | 20 | 2031-12-06 19:00 | 7.15 | 8.9939 | N | 0
2026-12-06 | 21 | 2031-12-06 20:00 | 7.65 | 9.6228 | N | 0
2026-12-06 | 22 | 2031-12-06 21:00 | 7.95 | 10.0002 | N | 0
2026-12-06 | 23 | 2031-12-06 22:00 | 7.68 | 9.6605 | N | 0
2026-12-07 | 00 | 2031-12-06 23:00 | 7.45 | 9.3712 | N | 0
2026-12-07 | 01 | 2031-12-07 | 7.21 | 9.0693 | N | 0
2026-12-07 | 02 | 2031-12-07 01:00 | 6.94 | 8.7297 | N | 0
2026-12-07 | 03 | 2031-12-07 02:00 | 6.51 | 8.1888 | N | 0
2026-12-07 | 04 | 2031-12-07 03:00 | 6.01 | 7.5599 | N | 0
2026-12-07 | 05 | 2031-12-07 04:00 | 5.47 | 6.8806 | N | 0
2026-12-07 | 06 | 2031-12-07 05:00 | 4.97 | 6.2517 | N | 0
2026-12-07 | 07 | 2031-12-07 06:00 | 4.86 | 6.1133 | N | 0
2026-12-07 | 08 | 2031-12-07 07:00 | 4.75 | 5.9749 | N | 0
2026-12-07 | 09 | 2031-12-07 08:00 | 4.61 | 5.7988 | N | 0
2026-12-07 | 10 | 2031-12-07 09:00 | 4.69 | 5.8995 | N | 0
2026-12-07 | 11 | 2031-12-07 10:00 | 4.89 | 6.151 | N | 0
2026-12-07 | 12 | 2031-12-07 11:00 | 5.26 | 6.6165 | N | 0
2026-12-07 | 13 | 2031-12-07 12:00 | 5.94 | 7.4718 | N | 0
2026-12-07 | 14 | 2031-12-07 13:00 | 6.39 | 8.0379 | N | 0
2026-12-07 | 15 | 2031-12-07 14:00 | 6.73 | 8.4655 | N | 0
2026-12-07 | 16 | 2031-12-07 15:00 | 7.02 | 8.8303 | N | 0
2026-12-07 | 17 | 2031-12-07 16:00 | 7.11 | 8.9435 | N | 0
2026-12-07 | 18 | 2031-12-07 17:00 | 7.31 | 9.1951 | N | 0
2026-12-07 | 19 | 2031-12-07 18:00 | 7.36 | 9.258 | N | 0
2026-12-07 | 20 | 2031-12-07 19:00 | 7.51 | 9.4467 | N | 0
2026-12-07 | 21 | 2031-12-07 20:00 | 8.49 | 10.6794 | Y | 0.039414 | 1
2026-12-07 | 22 | 2031-12-07 21:00 | 8.9 | 11.1951 | Y | 0.55515 | 2
2026-12-07 | 23 | 2031-12-07 22:00 | 8.66 | 10.8933 | Y | 0.25325 | 3 | 3
2026-12-08 | 00 | 2031-12-07 23:00 | 8.4 | 10.5662 | N | 0
2026-12-08 | 01 | 2031-12-08 | 8.09 | 10.1763 | N | 0
2026-12-08 | 02 | 2031-12-08 01:00 | 7.7 | 9.6857 | N | 0
2026-12-08 | 03 | 2031-12-08 02:00 | 6.97 | 8.7674 | N | 0
2026-12-08 | 04 | 2031-12-08 03:00 | 6.19 | 7.7863 | N | 0
2026-12-08 | 05 | 2031-12-08 04:00 | 5.72 | 7.1951 | N | 0
2026-12-08 | 06 | 2031-12-08 05:00 | 5.33 | 6.7045 | N | 0
2026-12-08 | 07 | 2031-12-08 06:00 | 5.19 | 6.5284 | N | 0
2026-12-08 | 08 | 2031-12-08 07:00 | 5.17 | 6.5032 | N | 0
2026-12-08 | 09 | 2031-12-08 08:00 | 5.41 | 6.8051 | N | 0
2026-12-08 | 10 | 2031-12-08 09:00 | 5.81 | 7.3083 | N | 0
2026-12-08 | 11 | 2031-12-08 10:00 | 6.33 | 7.9624 | N | 0
2026-12-08 | 12 | 2031-12-08 11:00 | 6.81 | 8.5662 | N | 0
2026-12-08 | 13 | 2031-12-08 12:00 | 6.88 | 8.6542 | N | 0
2026-12-08 | 14 | 2031-12-08 13:00 | 6.82 | 8.5788 | N | 0
2026-12-08 | 15 | 2031-12-08 14:00 | 6.61 | 8.3146 | N | 0
2026-12-08 | 16 | 2031-12-08 15:00 | 6.61 | 8.3146 | N | 0
2026-12-08 | 17 | 2031-12-08 16:00 | 6.7 | 8.4278 | N | 0
2026-12-08 | 18 | 2031-12-08 17:00 | 6.66 | 8.3775 | N | 0
2026-12-08 | 19 | 2031-12-08 18:00 | 6.59 | 8.2894 | N | 0
2026-12-08 | 20 | 2031-12-08 19:00 | 6.93 | 8.7171 | N | 0
2026-12-08 | 21 | 2031-12-08 20:00 | 8.22 | 10.3398 | N | 0
2026-12-08 | 22 | 2031-12-08 21:00 | 8.75 | 11.0065 | Y | 0.36646 | 1
2026-12-08 | 23 | 2031-12-08 22:00 | 8.66 | 10.8933 | Y | 0.25325 | 2
2026-12-09 | 00 | 2031-12-08 23:00 | 8.46 | 10.6417 | Y | 0.0016772 | 3 | 3
2026-12-09 | 01 | 2031-12-09 | 8.34 | 10.4907 | N | 0
2026-12-09 | 02 | 2031-12-09 01:00 | 8.08 | 10.1637 | N | 0
2026-12-09 | 03 | 2031-12-09 02:00 | 7.44 | 9.3586 | N | 0
2026-12-09 | 04 | 2031-12-09 03:00 | 6.52 | 8.2014 | N | 0
2026-12-09 | 05 | 2031-12-09 04:00 | 5.99 | 7.5347 | N | 0
2026-12-09 | 06 | 2031-12-09 05:00 | 5.48 | 6.8932 | N | 0
2026-12-09 | 07 | 2031-12-09 06:00 | 5.43 | 6.8303 | N | 0
2026-12-09 | 08 | 2031-12-09 07:00 | 5.2 | 6.541 | N | 0
2026-12-09 | 09 | 2031-12-09 08:00 | 5.26 | 6.6165 | N | 0
2026-12-09 | 10 | 2031-12-09 09:00 | 5.62 | 7.0693 | N | 0
2026-12-09 | 11 | 2031-12-09 10:00 | 6.17 | 7.7611 | N | 0
2026-12-09 | 12 | 2031-12-09 11:00 | 6.5 | 8.1762 | N | 0
2026-12-09 | 13 | 2031-12-09 12:00 | 6.55 | 8.2391 | N | 0
2026-12-09 | 14 | 2031-12-09 13:00 | 6.55 | 8.2391 | N | 0
2026-12-09 | 15 | 2031-12-09 14:00 | 6.72 | 8.453 | N | 0
2026-12-09 | 16 | 2031-12-09 15:00 | 6.56 | 8.2517 | N | 0
2026-12-09 | 17 | 2031-12-09 16:00 | 6.99 | 8.7926 | N | 0
2026-12-09 | 18 | 2031-12-09 17:00 | 6.99 | 8.7926 | N | 0
2026-12-09 | 19 | 2031-12-09 18:00 | 6.96 | 8.7549 | N | 0
2026-12-09 | 20 | 2031-12-09 19:00 | 7.27 | 9.1448 | N | 0
2026-12-09 | 21 | 2031-12-09 20:00 | 8.37 | 10.5285 | N | 0
2026-12-09 | 22 | 2031-12-09 21:00 | 8.64 | 10.8681 | Y | 0.2281 | 1 | 1
2026-12-09 | 23 | 2031-12-09 22:00 | 8.39 | 10.5536 | N | 0
2026-12-10 | 00 | 2031-12-09 23:00 | 8.37 | 10.5285 | N | 0
2026-12-10 | 01 | 2031-12-10 | 8.1 | 10.1888 | N | 0
2026-12-10 | 02 | 2031-12-10 01:00 | 7.62 | 9.5851 | N | 0
2026-12-10 | 03 | 2031-12-10 02:00 | 6.93 | 8.7171 | N | 0
2026-12-10 | 04 | 2031-12-10 03:00 | 6.15 | 7.736 | N | 0
2026-12-10 | 05 | 2031-12-10 04:00 | 5.46 | 6.868 | N | 0
2026-12-10 | 06 | 2031-12-10 05:00 | 4.96 | 6.2391 | N | 0
2026-12-10 | 07 | 2031-12-10 06:00 | 4.74 | 5.9624 | N | 0
2026-12-10 | 08 | 2031-12-10 07:00 | 4.66 | 5.8617 | N | 0
2026-12-10 | 09 | 2031-12-10 08:00 | 4.65 | 5.8491 | N | 0
2026-12-10 | 10 | 2031-12-10 09:00 | 5.06 | 6.3649 | N | 0
2026-12-10 | 11 | 2031-12-10 10:00 | 5.63 | 7.0819 | N | 0
2026-12-10 | 12 | 2031-12-10 11:00 | 5.86 | 7.3712 | N | 0
2026-12-10 | 13 | 2031-12-10 12:00 | 6.18 | 7.7737 | N | 0
2026-12-10 | 14 | 2031-12-10 13:00 | 6.36 | 8.0001 | N | 0
2026-12-10 | 15 | 2031-12-10 14:00 | 6.66 | 8.3775 | N | 0
2026-12-10 | 16 | 2031-12-10 15:00 | 6.77 | 8.5159 | N | 0
2026-12-10 | 17 | 2031-12-10 16:00 | 6.86 | 8.6291 | N | 0
2026-12-10 | 18 | 2031-12-10 17:00 | 6.85 | 8.6165 | N | 0
2026-12-10 | 19 | 2031-12-10 18:00 | 6.64 | 8.3523 | N | 0
2026-12-10 | 20 | 2031-12-10 19:00 | 6.96 | 8.7549 | N | 0
2026-12-10 | 21 | 2031-12-10 20:00 | 7.82 | 9.8366 | N | 0
2026-12-10 | 22 | 2031-12-10 21:00 | 8.26 | 10.3901 | N | 0
2026-12-10 | 23 | 2031-12-10 22:00 | 8.15 | 10.2517 | N | 0
2026-12-11 | 00 | 2031-12-10 23:00 | 7.99 | 10.0505 | N | 0
2026-12-11 | 01 | 2031-12-11 | 7.99 | 10.0505 | N | 0
2026-12-11 | 02 | 2031-12-11 01:00 | 7.59 | 9.5473 | N | 0
2026-12-11 | 03 | 2031-12-11 02:00 | 6.9 | 8.6794 | N | 0
2026-12-11 | 04 | 2031-12-11 03:00 | 6.19 | 7.7863 | N | 0
2026-12-11 | 05 | 2031-12-11 04:00 | 5.67 | 7.1322 | N | 0
2026-12-11 | 06 | 2031-12-11 05:00 | 5.37 | 6.7548 | N | 0
2026-12-11 | 07 | 2031-12-11 06:00 | 5.1 | 6.4152 | N | 0
2026-12-11 | 08 | 2031-12-11 07:00 | 5.01 | 6.302 | N | 0
2026-12-11 | 09 | 2031-12-11 08:00 | 5.23 | 6.5787 | N | 0
2026-12-11 | 10 | 2031-12-11 09:00 | 5.53 | 6.9561 | N | 0
2026-12-11 | 11 | 2031-12-11 10:00 | 6.12 | 7.6982 | N | 0
2026-12-11 | 12 | 2031-12-11 11:00 | 6.6 | 8.302 | N | 0
2026-12-11 | 13 | 2031-12-11 12:00 | 6.8 | 8.5536 | N | 0
2026-12-11 | 14 | 2031-12-11 13:00 | 6.61 | 8.3146 | N | 0
2026-12-11 | 15 | 2031-12-11 14:00 | 6.78 | 8.5284 | N | 0
2026-12-11 | 16 | 2031-12-11 15:00 | 6.81 | 8.5662 | N | 0
2026-12-11 | 17 | 2031-12-11 16:00 | 6.94 | 8.7297 | N | 0
2026-12-11 | 18 | 2031-12-11 17:00 | 6.89 | 8.6668 | N | 0
2026-12-11 | 19 | 2031-12-11 18:00 | 6.79 | 8.541 | N | 0
2026-12-11 | 20 | 2031-12-11 19:00 | 7.12 | 8.9561 | N | 0
2026-12-11 | 21 | 2031-12-11 20:00 | 7.94 | 9.9876 | N | 0
2026-12-11 | 22 | 2031-12-11 21:00 | 8.69 | 10.931 | Y | 0.29099 | 1
2026-12-11 | 23 | 2031-12-11 22:00 | 8.59 | 10.8052 | Y | 0.1652 | 2 | 2
2026-12-12 | 00 | 2031-12-11 23:00 | 8.41 | 10.5788 | N | 0
2026-12-12 | 01 | 2031-12-12 | 8.41 | 10.5788 | N | 0
2026-12-12 | 02 | 2031-12-12 01:00 | 8.11 | 10.2014 | N | 0
2026-12-12 | 03 | 2031-12-12 02:00 | 7.42 | 9.3335 | N | 0
2026-12-12 | 04 | 2031-12-12 03:00 | 6.71 | 8.4404 | N | 0
2026-12-12 | 05 | 2031-12-12 04:00 | 6.09 | 7.6605 | N | 0
2026-12-12 | 06 | 2031-12-12 05:00 | 5.64 | 7.0945 | N | 0
2026-12-12 | 07 | 2031-12-12 06:00 | 5.56 | 6.9938 | N | 0
2026-12-12 | 08 | 2031-12-12 07:00 | 5.35 | 6.7297 | N | 0
2026-12-12 | 09 | 2031-12-12 08:00 | 5.45 | 6.8555 | N | 0
2026-12-12 | 10 | 2031-12-12 09:00 | 5.59 | 7.0316 | N | 0
2026-12-12 | 11 | 2031-12-12 10:00 | 6.27 | 7.8869 | N | 0
2026-12-12 | 12 | 2031-12-12 11:00 | 6.79 | 8.541 | N | 0
2026-12-12 | 13 | 2031-12-12 12:00 | 6.79 | 8.541 | N | 0
2026-12-12 | 14 | 2031-12-12 13:00 | 6.83 | 8.5913 | N | 0
2026-12-12 | 15 | 2031-12-12 14:00 | 6.78 | 8.5284 | N | 0
2026-12-12 | 16 | 2031-12-12 15:00 | 6.78 | 8.5284 | N | 0
2026-12-12 | 17 | 2031-12-12 16:00 | 6.96 | 8.7549 | N | 0
2026-12-12 | 18 | 2031-12-12 17:00 | 6.93 | 8.7171 | N | 0
2026-12-12 | 19 | 2031-12-12 18:00 | 6.8 | 8.5536 | N | 0
2026-12-12 | 20 | 2031-12-12 19:00 | 7.03 | 8.8429 | N | 0
2026-12-12 | 21 | 2031-12-12 20:00 | 7.93 | 9.975 | N | 0
2026-12-12 | 22 | 2031-12-12 21:00 | 8.06 | 10.1385 | N | 0
2026-12-12 | 23 | 2031-12-12 22:00 | 8.06 | 10.1385 | N | 0
2026-12-13 | 00 | 2031-12-12 23:00 | 7.92 | 9.9624 | N | 0
2026-12-13 | 01 | 2031-12-13 | 7.79 | 9.7989 | N | 0
2026-12-13 | 02 | 2031-12-13 01:00 | 7.64 | 9.6102 | N | 0
2026-12-13 | 03 | 2031-12-13 02:00 | 7.18 | 9.0316 | N | 0
2026-12-13 | 04 | 2031-12-13 03:00 | 6.44 | 8.1008 | N | 0
2026-12-13 | 05 | 2031-12-13 04:00 | 5.79 | 7.2831 | N | 0
2026-12-13 | 06 | 2031-12-13 05:00 | 5.45 | 6.8555 | N | 0
2026-12-13 | 07 | 2031-12-13 06:00 | 5 | 6.2894 | N | 0
2026-12-13 | 08 | 2031-12-13 07:00 | 4.94 | 6.2139 | N | 0
2026-12-13 | 09 | 2031-12-13 08:00 | 4.79 | 6.0253 | N | 0
2026-12-13 | 10 | 2031-12-13 09:00 | 4.86 | 6.1133 | N | 0
2026-12-13 | 11 | 2031-12-13 10:00 | 5.2 | 6.541 | N | 0
2026-12-13 | 12 | 2031-12-13 11:00 | 5.68 | 7.1448 | N | 0
2026-12-13 | 13 | 2031-12-13 12:00 | 6.22 | 7.824 | N | 0
2026-12-13 | 14 | 2031-12-13 13:00 | 6.55 | 8.2391 | N | 0
2026-12-13 | 15 | 2031-12-13 14:00 | 6.9 | 8.6794 | N | 0
2026-12-13 | 16 | 2031-12-13 15:00 | 6.96 | 8.7549 | N | 0
2026-12-13 | 17 | 2031-12-13 16:00 | 7.14 | 8.9813 | N | 0
2026-12-13 | 18 | 2031-12-13 17:00 | 7.03 | 8.8429 | N | 0
2026-12-13 | 19 | 2031-12-13 18:00 | 6.98 | 8.78 | N | 0
2026-12-13 | 20 | 2031-12-13 19:00 | 7.21 | 9.0693 | N | 0
2026-12-13 | 21 | 2031-12-13 20:00 | 7.94 | 9.9876 | N | 0
2026-12-13 | 22 | 2031-12-13 21:00 | 8.22 | 10.3398 | N | 0
2026-12-13 | 23 | 2031-12-13 22:00 | 8.22 | 10.3398 | N | 0
2026-12-14 | 00 | 2031-12-13 23:00 | 7.72 | 9.7108 | N | 0
2026-12-14 | 01 | 2031-12-14 | 7.72 | 9.7108 | N | 0
2026-12-14 | 02 | 2031-12-14 01:00 | 7.26 | 9.1322 | N | 0
2026-12-14 | 03 | 2031-12-14 02:00 | 6.92 | 8.7045 | N | 0
2026-12-14 | 04 | 2031-12-14 03:00 | 6.5 | 8.1762 | N | 0
2026-12-14 | 05 | 2031-12-14 04:00 | 5.99 | 7.5347 | N | 0
2026-12-14 | 06 | 2031-12-14 05:00 | 5.54 | 6.9687 | N | 0
2026-12-14 | 07 | 2031-12-14 06:00 | 5.29 | 6.6542 | N | 0
2026-12-14 | 08 | 2031-12-14 07:00 | 5.26 | 6.6165 | N | 0
2026-12-14 | 09 | 2031-12-14 08:00 | 5.24 | 6.5913 | N | 0
2026-12-14 | 10 | 2031-12-14 09:00 | 5.43 | 6.8303 | N | 0
2026-12-14 | 11 | 2031-12-14 10:00 | 5.43 | 6.8303 | N | 0
2026-12-14 | 12 | 2031-12-14 11:00 | 6.08 | 7.6479 | N | 0
2026-12-14 | 13 | 2031-12-14 12:00 | 6.6 | 8.302 | N | 0
2026-12-14 | 14 | 2031-12-14 13:00 | 6.95 | 8.7423 | N | 0
2026-12-14 | 15 | 2031-12-14 14:00 | 7.22 | 9.0819 | N | 0
2026-12-14 | 16 | 2031-12-14 15:00 | 7.46 | 9.3838 | N | 0
2026-12-14 | 17 | 2031-12-14 16:00 | 7.62 | 9.5851 | N | 0
2026-12-14 | 18 | 2031-12-14 17:00 | 7.64 | 9.6102 | N | 0
2026-12-14 | 19 | 2031-12-14 18:00 | 7.67 | 9.648 | N | 0
2026-12-14 | 20 | 2031-12-14 19:00 | 7.99 | 10.0505 | N | 0
2026-12-14 | 21 | 2031-12-14 20:00 | 9.07 | 11.409 | Y | 0.76898 | 1
2026-12-14 | 22 | 2031-12-14 21:00 | 9.42 | 11.8492 | Y | 1.2092 | 2
2026-12-14 | 23 | 2031-12-14 22:00 | 9.41 | 11.8367 | Y | 1.1967 | 3
2026-12-15 | 00 | 2031-12-14 23:00 | 9.16 | 11.5222 | Y | 0.88219 | 4
2026-12-15 | 01 | 2031-12-15 | 8.77 | 11.0316 | Y | 0.39162 | 5 | 5
2026-12-15 | 02 | 2031-12-15 01:00 | 8.33 | 10.4782 | N | 0
2026-12-15 | 03 | 2031-12-15 02:00 | 7.48 | 9.409 | N | 0
2026-12-15 | 04 | 2031-12-15 03:00 | 6.76 | 8.5033 | N | 0
2026-12-15 | 05 | 2031-12-15 04:00 | 5.99 | 7.5347 | N | 0
2026-12-15 | 06 | 2031-12-15 05:00 | 5.7 | 7.1699 | N | 0
2026-12-15 | 07 | 2031-12-15 06:00 | 5.52 | 6.9435 | N | 0
2026-12-15 | 08 | 2031-12-15 07:00 | 5.47 | 6.8806 | N | 0
2026-12-15 | 09 | 2031-12-15 08:00 | 5.39 | 6.78 | N | 0
2026-12-15 | 10 | 2031-12-15 09:00 | 5.74 | 7.2202 | N | 0
2026-12-15 | 11 | 2031-12-15 10:00 | 6.25 | 7.8618 | N | 0
2026-12-15 | 12 | 2031-12-15 11:00 | 6.83 | 8.5913 | N | 0
2026-12-15 | 13 | 2031-12-15 12:00 | 7.06 | 8.8806 | N | 0
2026-12-15 | 14 | 2031-12-15 13:00 | 7.07 | 8.8932 | N | 0
2026-12-15 | 15 | 2031-12-15 14:00 | 7.01 | 8.8177 | N | 0
2026-12-15 | 16 | 2031-12-15 15:00 | 7.22 | 9.0819 | N | 0
2026-12-15 | 17 | 2031-12-15 16:00 | 7.4 | 9.3083 | N | 0
2026-12-15 | 18 | 2031-12-15 17:00 | 7.18 | 9.0316 | N | 0
2026-12-15 | 19 | 2031-12-15 18:00 | 7.18 | 9.0316 | N | 0
2026-12-15 | 20 | 2031-12-15 19:00 | 7.45 | 9.3712 | N | 0
2026-12-15 | 21 | 2031-12-15 20:00 | 8.24 | 10.3649 | N | 0
2026-12-15 | 22 | 2031-12-15 21:00 | 8.91 | 11.2077 | Y | 0.56772 | 1
2026-12-15 | 23 | 2031-12-15 22:00 | 8.86 | 11.1448 | Y | 0.50483 | 2
2026-12-16 | 00 | 2031-12-15 23:00 | 8.56 | 10.7675 | Y | 0.12747 | 3
2026-12-16 | 01 | 2031-12-16 | 8.49 | 10.6794 | Y | 0.039414 | 4 | 4
2026-12-16 | 02 | 2031-12-16 01:00 | 8.13 | 10.2266 | N | 0
2026-12-16 | 03 | 2031-12-16 02:00 | 7.48 | 9.409 | N | 0
2026-12-16 | 04 | 2031-12-16 03:00 | 6.41 | 8.063 | N | 0
2026-12-16 | 05 | 2031-12-16 04:00 | 5.81 | 7.3083 | N | 0
2026-12-16 | 06 | 2031-12-16 05:00 | 5.43 | 6.8303 | N | 0
2026-12-16 | 07 | 2031-12-16 06:00 | 5.24 | 6.5913 | N | 0
2026-12-16 | 08 | 2031-12-16 07:00 | 5 | 6.2894 | N | 0
2026-12-16 | 09 | 2031-12-16 08:00 | 5.1 | 6.4152 | N | 0
2026-12-16 | 10 | 2031-12-16 09:00 | 5.43 | 6.8303 | N | 0
2026-12-16 | 11 | 2031-12-16 10:00 | 6.07 | 7.6353 | N | 0
2026-12-16 | 12 | 2031-12-16 11:00 | 6.55 | 8.2391 | N | 0
2026-12-16 | 13 | 2031-12-16 12:00 | 6.58 | 8.2769 | N | 0
2026-12-16 | 14 | 2031-12-16 13:00 | 6.58 | 8.2769 | N | 0
2026-12-16 | 15 | 2031-12-16 14:00 | 6.78 | 8.5284 | N | 0
2026-12-16 | 16 | 2031-12-16 15:00 | 6.86 | 8.6291 | N | 0
2026-12-16 | 17 | 2031-12-16 16:00 | 7.01 | 8.8177 | N | 0
2026-12-16 | 18 | 2031-12-16 17:00 | 7 | 8.8052 | N | 0
2026-12-16 | 19 | 2031-12-16 18:00 | 7 | 8.8052 | N | 0
2026-12-16 | 20 | 2031-12-16 19:00 | 7.1 | 8.931 | N | 0
2026-12-16 | 21 | 2031-12-16 20:00 | 8.14 | 10.2392 | N | 0
2026-12-16 | 22 | 2031-12-16 21:00 | 8.71 | 10.9561 | Y | 0.31615 | 1
2026-12-16 | 23 | 2031-12-16 22:00 | 8.55 | 10.7549 | Y | 0.11489 | 2 | 2
2026-12-17 | 00 | 2031-12-16 23:00 | 8.16 | 10.2643 | N | 0
2026-12-17 | 01 | 2031-12-17 | 8.16 | 10.2643 | N | 0
2026-12-17 | 02 | 2031-12-17 01:00 | 7.66 | 9.6354 | N | 0
2026-12-17 | 03 | 2031-12-17 02:00 | 7 | 8.8052 | N | 0
2026-12-17 | 04 | 2031-12-17 03:00 | 6.2 | 7.7989 | N | 0
2026-12-17 | 05 | 2031-12-17 04:00 | 5.49 | 6.9058 | N | 0
2026-12-17 | 06 | 2031-12-17 05:00 | 5.06 | 6.3649 | N | 0
2026-12-17 | 07 | 2031-12-17 06:00 | 4.88 | 6.1385 | N | 0
2026-12-17 | 08 | 2031-12-17 07:00 | 4.77 | 6.0001 | N | 0
2026-12-17 | 09 | 2031-12-17 08:00 | 4.73 | 5.9498 | N | 0
2026-12-17 | 10 | 2031-12-17 09:00 | 5.09 | 6.4026 | N | 0
2026-12-17 | 11 | 2031-12-17 10:00 | 5.56 | 6.9938 | N | 0
2026-12-17 | 12 | 2031-12-17 11:00 | 5.98 | 7.5221 | N | 0
2026-12-17 | 13 | 2031-12-17 12:00 | 6.09 | 7.6605 | N | 0
2026-12-17 | 14 | 2031-12-17 13:00 | 6.16 | 7.7485 | N | 0
2026-12-17 | 15 | 2031-12-17 14:00 | 6.29 | 7.9121 | N | 0
2026-12-17 | 16 | 2031-12-17 15:00 | 6.29 | 7.9121 | N | 0
2026-12-17 | 17 | 2031-12-17 16:00 | 6.49 | 8.1637 | N | 0
2026-12-17 | 18 | 2031-12-17 17:00 | 6.38 | 8.0253 | N | 0
2026-12-17 | 19 | 2031-12-17 18:00 | 6.3 | 7.9247 | N | 0
2026-12-17 | 20 | 2031-12-17 19:00 | 6.76 | 8.5033 | N | 0
2026-12-17 | 21 | 2031-12-17 20:00 | 7.52 | 9.4593 | N | 0
2026-12-17 | 22 | 2031-12-17 21:00 | 7.94 | 9.9876 | N | 0
2026-12-17 | 23 | 2031-12-17 22:00 | 7.86 | 9.8869 | N | 0
2026-12-18 | 00 | 2031-12-17 23:00 | 7.86 | 9.8869 | N | 0
2026-12-18 | 01 | 2031-12-18 | 7.62 | 9.5851 | N | 0
2026-12-18 | 02 | 2031-12-18 01:00 | 7.34 | 9.2328 | N | 0
2026-12-18 | 03 | 2031-12-18 02:00 | 6.52 | 8.2014 | N | 0
2026-12-18 | 04 | 2031-12-18 03:00 | 5.84 | 7.346 | N | 0
2026-12-18 | 05 | 2031-12-18 04:00 | 5.28 | 6.6416 | N | 0
2026-12-18 | 06 | 2031-12-18 05:00 | 4.94 | 6.2139 | N | 0
2026-12-18 | 07 | 2031-12-18 06:00 | 4.75 | 5.9749 | N | 0
2026-12-18 | 08 | 2031-12-18 07:00 | 4.56 | 5.7359 | N | 0
2026-12-18 | 09 | 2031-12-18 08:00 | 4.58 | 5.7611 | N | 0
2026-12-18 | 10 | 2031-12-18 09:00 | 4.89 | 6.151 | N | 0
2026-12-18 | 11 | 2031-12-18 10:00 | 5.39 | 6.78 | N | 0
2026-12-18 | 12 | 2031-12-18 11:00 | 5.93 | 7.4592 | N | 0
2026-12-18 | 13 | 2031-12-18 12:00 | 5.96 | 7.497 | N | 0
2026-12-18 | 14 | 2031-12-18 13:00 | 5.96 | 7.497 | N | 0
2026-12-18 | 15 | 2031-12-18 14:00 | 6.16 | 7.7485 | N | 0
2026-12-18 | 16 | 2031-12-18 15:00 | 6.15 | 7.736 | N | 0
2026-12-18 | 17 | 2031-12-18 16:00 | 6.27 | 7.8869 | N | 0
2026-12-18 | 18 | 2031-12-18 17:00 | 6.02 | 7.5724 | N | 0
2026-12-18 | 19 | 2031-12-18 18:00 | 6.05 | 7.6102 | N | 0
2026-12-18 | 20 | 2031-12-18 19:00 | 6.4 | 8.0504 | N | 0
2026-12-18 | 21 | 2031-12-18 20:00 | 7.37 | 9.2706 | N | 0
2026-12-18 | 22 | 2031-12-18 21:00 | 7.77 | 9.7737 | N | 0
2026-12-18 | 23 | 2031-12-18 22:00 | 7.59 | 9.5473 | N | 0
2026-12-19 | 00 | 2031-12-18 23:00 | 7.43 | 9.3461 | N | 0
2026-12-19 | 01 | 2031-12-19 | 7.31 | 9.1951 | N | 0
2026-12-19 | 02 | 2031-12-19 01:00 | 7.21 | 9.0693 | N | 0
2026-12-19 | 03 | 2031-12-19 02:00 | 6.53 | 8.214 | N | 0
2026-12-19 | 04 | 2031-12-19 03:00 | 5.72 | 7.1951 | N | 0
2026-12-19 | 05 | 2031-12-19 04:00 | 5.04 | 6.3397 | N | 0
2026-12-19 | 06 | 2031-12-19 05:00 | 4.57 | 5.7485 | N | 0
2026-12-19 | 07 | 2031-12-19 06:00 | 4.31 | 5.4215 | N | 0
2026-12-19 | 08 | 2031-12-19 07:00 | 4.15 | 5.2202 | N | 0
2026-12-19 | 09 | 2031-12-19 08:00 | 4.29 | 5.3963 | N | 0
2026-12-19 | 10 | 2031-12-19 09:00 | 4.45 | 5.5976 | N | 0
2026-12-19 | 11 | 2031-12-19 10:00 | 5.16 | 6.4907 | N | 0
2026-12-19 | 12 | 2031-12-19 11:00 | 5.76 | 7.2454 | N | 0
2026-12-19 | 13 | 2031-12-19 12:00 | 5.98 | 7.5221 | N | 0
2026-12-19 | 14 | 2031-12-19 13:00 | 6.11 | 7.6857 | N | 0
2026-12-19 | 15 | 2031-12-19 14:00 | 6.35 | 7.9875 | N | 0
2026-12-19 | 16 | 2031-12-19 15:00 | 6.53 | 8.214 | N | 0
2026-12-19 | 17 | 2031-12-19 16:00 | 6.78 | 8.5284 | N | 0
2026-12-19 | 18 | 2031-12-19 17:00 | 6.82 | 8.5788 | N | 0
2026-12-19 | 19 | 2031-12-19 18:00 | 6.77 | 8.5159 | N | 0
2026-12-19 | 20 | 2031-12-19 19:00 | 7.09 | 8.9184 | N | 0
2026-12-19 | 21 | 2031-12-19 20:00 | 7.88 | 9.9121 | N | 0
2026-12-19 | 22 | 2031-12-19 21:00 | 8.26 | 10.3901 | N | 0
2026-12-19 | 23 | 2031-12-19 22:00 | 8.14 | 10.2392 | N | 0
2026-12-20 | 00 | 2031-12-19 23:00 | 7.85 | 9.8744 | N | 0
2026-12-20 | 01 | 2031-12-20 | 7.85 | 9.8744 | N | 0
2026-12-20 | 02 | 2031-12-20 01:00 | 7.58 | 9.5347 | N | 0
2026-12-20 | 03 | 2031-12-20 02:00 | 7.23 | 9.0945 | N | 0
2026-12-20 | 04 | 2031-12-20 03:00 | 6.46 | 8.1259 | N | 0
2026-12-20 | 05 | 2031-12-20 04:00 | 5.82 | 7.3209 | N | 0
2026-12-20 | 06 | 2031-12-20 05:00 | 5.44 | 6.8429 | N | 0
2026-12-20 | 07 | 2031-12-20 06:00 | 5.14 | 6.4655 | N | 0
2026-12-20 | 08 | 2031-12-20 07:00 | 4.97 | 6.2517 | N | 0
2026-12-20 | 09 | 2031-12-20 08:00 | 4.89 | 6.151 | N | 0
2026-12-20 | 10 | 2031-12-20 09:00 | 5.02 | 6.3146 | N | 0
2026-12-20 | 11 | 2031-12-20 10:00 | 5.14 | 6.4655 | N | 0
2026-12-20 | 12 | 2031-12-20 11:00 | 5.6 | 7.0441 | N | 0
2026-12-20 | 13 | 2031-12-20 12:00 | 6.27 | 7.8869 | N | 0
2026-12-20 | 14 | 2031-12-20 13:00 | 6.78 | 8.5284 | N | 0
2026-12-20 | 15 | 2031-12-20 14:00 | 7.07 | 8.8932 | N | 0
2026-12-20 | 16 | 2031-12-20 15:00 | 7.32 | 9.2077 | N | 0
2026-12-20 | 17 | 2031-12-20 16:00 | 7.36 | 9.258 | N | 0
2026-12-20 | 18 | 2031-12-20 17:00 | 7.34 | 9.2328 | N | 0
2026-12-20 | 19 | 2031-12-20 18:00 | 7.3 | 9.1825 | N | 0
2026-12-20 | 20 | 2031-12-20 19:00 | 7.37 | 9.2706 | N | 0
2026-12-20 | 21 | 2031-12-20 20:00 | 7.89 | 9.9247 | N | 0
2026-12-20 | 22 | 2031-12-20 21:00 | 7.98 | 10.0379 | N | 0
2026-12-20 | 23 | 2031-12-20 22:00 | 7.82 | 9.8366 | N | 0
2026-12-21 | 00 | 2031-12-20 23:00 | 7.49 | 9.4215 | N | 0
2026-12-21 | 01 | 2031-12-21 | 7.39 | 9.2957 | N | 0
2026-12-21 | 02 | 2031-12-21 01:00 | 7 | 8.8052 | N | 0
2026-12-21 | 03 | 2031-12-21 02:00 | 6.58 | 8.2769 | N | 0
2026-12-21 | 04 | 2031-12-21 03:00 | 6.11 | 7.6857 | N | 0
2026-12-21 | 05 | 2031-12-21 04:00 | 5.58 | 7.019 | N | 0
2026-12-21 | 06 | 2031-12-21 05:00 | 5.13 | 6.4529 | N | 0
2026-12-21 | 07 | 2031-12-21 06:00 | 4.93 | 6.2014 | N | 0
2026-12-21 | 08 | 2031-12-21 07:00 | 4.85 | 6.1007 | N | 0
2026-12-21 | 09 | 2031-12-21 08:00 | 4.85 | 6.1007 | N | 0
2026-12-21 | 10 | 2031-12-21 09:00 | 5.01 | 6.302 | N | 0
2026-12-21 | 11 | 2031-12-21 10:00 | 5.17 | 6.5032 | N | 0
2026-12-21 | 12 | 2031-12-21 11:00 | 5.51 | 6.9309 | N | 0
2026-12-21 | 13 | 2031-12-21 12:00 | 6.12 | 7.6982 | N | 0
2026-12-21 | 14 | 2031-12-21 13:00 | 6.46 | 8.1259 | N | 0
2026-12-21 | 15 | 2031-12-21 14:00 | 6.63 | 8.3398 | N | 0
2026-12-21 | 16 | 2031-12-21 15:00 | 6.87 | 8.6416 | N | 0
2026-12-21 | 17 | 2031-12-21 16:00 | 7.33 | 9.2203 | N | 0
2026-12-21 | 18 | 2031-12-21 17:00 | 7.33 | 9.2203 | N | 0
2026-12-21 | 19 | 2031-12-21 18:00 | 7.35 | 9.2454 | N | 0
2026-12-21 | 20 | 2031-12-21 19:00 | 7.58 | 9.5347 | N | 0
2026-12-21 | 21 | 2031-12-21 20:00 | 8.34 | 10.4907 | N | 0
2026-12-21 | 22 | 2031-12-21 21:00 | 8.48 | 10.6668 | Y | 0.026835 | 1
2026-12-21 | 23 | 2031-12-21 22:00 | 8.5 | 10.692 | Y | 0.051992 | 2 | 2
2026-12-22 | 00 | 2031-12-21 23:00 | 8.07 | 10.1511 | N | 0
2026-12-22 | 01 | 2031-12-22 | 8.02 | 10.0882 | N | 0
2026-12-22 | 02 | 2031-12-22 01:00 | 7.49 | 9.4215 | N | 0
2026-12-22 | 03 | 2031-12-22 02:00 | 7.06 | 8.8806 | N | 0
2026-12-22 | 04 | 2031-12-22 03:00 | 6.39 | 8.0379 | N | 0
2026-12-22 | 05 | 2031-12-22 04:00 | 5.74 | 7.2202 | N | 0
2026-12-22 | 06 | 2031-12-22 05:00 | 5.28 | 6.6416 | N | 0
2026-12-22 | 07 | 2031-12-22 06:00 | 5.04 | 6.3397 | N | 0
2026-12-22 | 08 | 2031-12-22 07:00 | 4.87 | 6.1259 | N | 0
2026-12-22 | 09 | 2031-12-22 08:00 | 4.96 | 6.2391 | N | 0
2026-12-22 | 10 | 2031-12-22 09:00 | 5.19 | 6.5284 | N | 0
2026-12-22 | 11 | 2031-12-22 10:00 | 5.63 | 7.0819 | N | 0
2026-12-22 | 12 | 2031-12-22 11:00 | 5.94 | 7.4718 | N | 0
2026-12-22 | 13 | 2031-12-22 12:00 | 6.35 | 7.9875 | N | 0
2026-12-22 | 14 | 2031-12-22 13:00 | 6.42 | 8.0756 | N | 0
2026-12-22 | 15 | 2031-12-22 14:00 | 6.54 | 8.2265 | N | 0
2026-12-22 | 16 | 2031-12-22 15:00 | 6.75 | 8.4907 | N | 0
2026-12-22 | 17 | 2031-12-22 16:00 | 6.8 | 8.5536 | N | 0
2026-12-22 | 18 | 2031-12-22 17:00 | 6.79 | 8.541 | N | 0
2026-12-22 | 19 | 2031-12-22 18:00 | 6.79 | 8.541 | N | 0
2026-12-22 | 20 | 2031-12-22 19:00 | 6.98 | 8.78 | N | 0
2026-12-22 | 21 | 2031-12-22 20:00 | 7.93 | 9.975 | N | 0
2026-12-22 | 22 | 2031-12-22 21:00 | 8.18 | 10.2895 | N | 0
2026-12-22 | 23 | 2031-12-22 22:00 | 7.99 | 10.0505 | N | 0
2026-12-23 | 00 | 2031-12-22 23:00 | 7.83 | 9.8492 | N | 0
2026-12-23 | 01 | 2031-12-23 | 7.44 | 9.3586 | N | 0
2026-12-23 | 02 | 2031-12-23 01:00 | 7.44 | 9.3586 | N | 0
2026-12-23 | 03 | 2031-12-23 02:00 | 6.74 | 8.4781 | N | 0
2026-12-23 | 04 | 2031-12-23 03:00 | 6 | 7.5473 | N | 0
2026-12-23 | 05 | 2031-12-23 04:00 | 5.49 | 6.9058 | N | 0
2026-12-23 | 06 | 2031-12-23 05:00 | 4.97 | 6.2517 | N | 0
2026-12-23 | 07 | 2031-12-23 06:00 | 4.68 | 5.8869 | N | 0
2026-12-23 | 08 | 2031-12-23 07:00 | 4.57 | 5.7485 | N | 0
2026-12-23 | 09 | 2031-12-23 08:00 | 4.57 | 5.7485 | N | 0
2026-12-23 | 10 | 2031-12-23 09:00 | 4.8 | 6.0378 | N | 0
2026-12-23 | 11 | 2031-12-23 10:00 | 5.3 | 6.6668 | N | 0
2026-12-23 | 12 | 2031-12-23 11:00 | 5.57 | 7.0064 | N | 0
2026-12-23 | 13 | 2031-12-23 12:00 | 6.02 | 7.5724 | N | 0
2026-12-23 | 14 | 2031-12-23 13:00 | 6.36 | 8.0001 | N | 0
2026-12-23 | 15 | 2031-12-23 14:00 | 6.57 | 8.2643 | N | 0
2026-12-23 | 16 | 2031-12-23 15:00 | 6.91 | 8.692 | N | 0
2026-12-23 | 17 | 2031-12-23 16:00 | 6.98 | 8.78 | N | 0
2026-12-23 | 18 | 2031-12-23 17:00 | 7 | 8.8052 | N | 0
2026-12-23 | 19 | 2031-12-23 18:00 | 6.99 | 8.7926 | N | 0
2026-12-23 | 20 | 2031-12-23 19:00 | 7.18 | 9.0316 | N | 0
2026-12-23 | 21 | 2031-12-23 20:00 | 7.72 | 9.7108 | N | 0
2026-12-23 | 22 | 2031-12-23 21:00 | 7.96 | 10.0127 | N | 0
2026-12-23 | 23 | 2031-12-23 22:00 | 7.91 | 9.9498 | N | 0
2026-12-24 | 00 | 2031-12-23 23:00 | 7.64 | 9.6102 | N | 0
2026-12-24 | 01 | 2031-12-24 | 7.64 | 9.6102 | N | 0
2026-12-24 | 02 | 2031-12-24 01:00 | 7.4 | 9.3083 | N | 0
2026-12-24 | 03 | 2031-12-24 02:00 | 6.81 | 8.5662 | N | 0
2026-12-24 | 04 | 2031-12-24 03:00 | 6.1 | 7.6731 | N | 0
2026-12-24 | 05 | 2031-12-24 04:00 | 5.5 | 6.9183 | N | 0
2026-12-24 | 06 | 2031-12-24 05:00 | 4.99 | 6.2768 | N | 0
2026-12-24 | 07 | 2031-12-24 06:00 | 4.72 | 5.9372 | N | 0
2026-12-24 | 08 | 2031-12-24 07:00 | 4.65 | 5.8491 | N | 0
2026-12-24 | 09 | 2031-12-24 08:00 | 4.65 | 5.8491 | N | 0
2026-12-24 | 10 | 2031-12-24 09:00 | 4.99 | 6.2768 | N | 0
2026-12-24 | 11 | 2031-12-24 10:00 | 5.31 | 6.6794 | N | 0
2026-12-24 | 12 | 2031-12-24 11:00 | 5.74 | 7.2202 | N | 0
2026-12-24 | 13 | 2031-12-24 12:00 | 6.24 | 7.8492 | N | 0
2026-12-24 | 14 | 2031-12-24 13:00 | 6.6 | 8.302 | N | 0
2026-12-24 | 15 | 2031-12-24 14:00 | 6.86 | 8.6291 | N | 0
2026-12-24 | 16 | 2031-12-24 15:00 | 6.96 | 8.7549 | N | 0
2026-12-24 | 17 | 2031-12-24 16:00 | 7.04 | 8.8555 | N | 0
2026-12-24 | 18 | 2031-12-24 17:00 | 7.11 | 8.9435 | N | 0
2026-12-24 | 19 | 2031-12-24 18:00 | 7.01 | 8.8177 | N | 0
2026-12-24 | 20 | 2031-12-24 19:00 | 7.12 | 8.9561 | N | 0
2026-12-24 | 21 | 2031-12-24 20:00 | 7.67 | 9.648 | N | 0
2026-12-24 | 22 | 2031-12-24 21:00 | 7.86 | 9.8869 | N | 0
2026-12-24 | 23 | 2031-12-24 22:00 | 7.66 | 9.6354 | N | 0
2026-12-25 | 00 | 2031-12-24 23:00 | 7.33 | 9.2203 | N | 0
2026-12-25 | 01 | 2031-12-25 | 7.11 | 8.9435 | N | 0
2026-12-25 | 02 | 2031-12-25 01:00 | 7.03 | 8.8429 | N | 0
2026-12-25 | 03 | 2031-12-25 02:00 | 6.58 | 8.2769 | N | 0
2026-12-25 | 04 | 2031-12-25 03:00 | 6.06 | 7.6228 | N | 0
2026-12-25 | 05 | 2031-12-25 04:00 | 5.51 | 6.9309 | N | 0
2026-12-25 | 06 | 2031-12-25 05:00 | 5.09 | 6.4026 | N | 0
2026-12-25 | 07 | 2031-12-25 06:00 | 4.8 | 6.0378 | N | 0
2026-12-25 | 08 | 2031-12-25 07:00 | 4.68 | 5.8869 | N | 0
2026-12-25 | 09 | 2031-12-25 08:00 | 4.54 | 5.7108 | N | 0
2026-12-25 | 10 | 2031-12-25 09:00 | 4.67 | 5.8743 | N | 0
2026-12-25 | 11 | 2031-12-25 10:00 | 4.97 | 6.2517 | N | 0
2026-12-25 | 12 | 2031-12-25 11:00 | 5.45 | 6.8555 | N | 0
2026-12-25 | 13 | 2031-12-25 12:00 | 6.3 | 7.9247 | N | 0
2026-12-25 | 14 | 2031-12-25 13:00 | 6.71 | 8.4404 | N | 0
2026-12-25 | 15 | 2031-12-25 14:00 | 7.06 | 8.8806 | N | 0
2026-12-25 | 16 | 2031-12-25 15:00 | 7.19 | 9.0442 | N | 0
2026-12-25 | 17 | 2031-12-25 16:00 | 7.04 | 8.8555 | N | 0
2026-12-25 | 18 | 2031-12-25 17:00 | 7.06 | 8.8806 | N | 0
2026-12-25 | 19 | 2031-12-25 18:00 | 7.02 | 8.8303 | N | 0
2026-12-25 | 20 | 2031-12-25 19:00 | 7.22 | 9.0819 | N | 0
2026-12-25 | 21 | 2031-12-25 20:00 | 7.69 | 9.6731 | N | 0
2026-12-25 | 22 | 2031-12-25 21:00 | 7.69 | 9.6731 | N | 0
2026-12-25 | 23 | 2031-12-25 22:00 | 7.21 | 9.0693 | N | 0
2026-12-26 | 00 | 2031-12-25 23:00 | 6.96 | 8.7549 | N | 0
2026-12-26 | 01 | 2031-12-26 | 7.04 | 8.8555 | N | 0
2026-12-26 | 02 | 2031-12-26 01:00 | 7.02 | 8.8303 | N | 0
2026-12-26 | 03 | 2031-12-26 02:00 | 6.82 | 8.5788 | N | 0
2026-12-26 | 04 | 2031-12-26 03:00 | 6.36 | 8.0001 | N | 0
2026-12-26 | 05 | 2031-12-26 04:00 | 5.93 | 7.4592 | N | 0
2026-12-26 | 06 | 2031-12-26 05:00 | 5.54 | 6.9687 | N | 0
2026-12-26 | 07 | 2031-12-26 06:00 | 5.35 | 6.7297 | N | 0
2026-12-26 | 08 | 2031-12-26 07:00 | 5.2 | 6.541 | N | 0
2026-12-26 | 09 | 2031-12-26 08:00 | 5.2 | 6.541 | N | 0
2026-12-26 | 10 | 2031-12-26 09:00 | 5.37 | 6.7548 | N | 0
2026-12-26 | 11 | 2031-12-26 10:00 | 5.47 | 6.8806 | N | 0
2026-12-26 | 12 | 2031-12-26 11:00 | 5.94 | 7.4718 | N | 0
2026-12-26 | 13 | 2031-12-26 12:00 | 6.44 | 8.1008 | N | 0
2026-12-26 | 14 | 2031-12-26 13:00 | 6.92 | 8.7045 | N | 0
2026-12-26 | 15 | 2031-12-26 14:00 | 7.55 | 9.497 | N | 0
2026-12-26 | 16 | 2031-12-26 15:00 | 8.08 | 10.1637 | N | 0
2026-12-26 | 17 | 2031-12-26 16:00 | 8.34 | 10.4907 | N | 0
2026-12-26 | 18 | 2031-12-26 17:00 | 8.22 | 10.3398 | N | 0
2026-12-26 | 19 | 2031-12-26 18:00 | 8.25 | 10.3775 | N | 0
2026-12-26 | 20 | 2031-12-26 19:00 | 8.32 | 10.4656 | N | 0
2026-12-26 | 21 | 2031-12-26 20:00 | 8.61 | 10.8304 | Y | 0.19036 | 1
2026-12-26 | 22 | 2031-12-26 21:00 | 8.87 | 11.1574 | Y | 0.51741 | 2
2026-12-26 | 23 | 2031-12-26 22:00 | 8.54 | 10.7423 | Y | 0.10231 | 3
2026-12-27 | 00 | 2031-12-26 23:00 | 8.48 | 10.6668 | Y | 0.026835 | 4 | 4
2026-12-27 | 01 | 2031-12-27 | 8.11 | 10.2014 | N | 0
2026-12-27 | 02 | 2031-12-27 01:00 | 7.99 | 10.0505 | N | 0
2026-12-27 | 03 | 2031-12-27 02:00 | 7.72 | 9.7108 | N | 0
2026-12-27 | 04 | 2031-12-27 03:00 | 6.88 | 8.6542 | N | 0
2026-12-27 | 05 | 2031-12-27 04:00 | 6.36 | 8.0001 | N | 0
2026-12-27 | 06 | 2031-12-27 05:00 | 5.85 | 7.3586 | N | 0
2026-12-27 | 07 | 2031-12-27 06:00 | 5.56 | 6.9938 | N | 0
2026-12-27 | 08 | 2031-12-27 07:00 | 5.25 | 6.6039 | N | 0
2026-12-27 | 09 | 2031-12-27 08:00 | 5.24 | 6.5913 | N | 0
2026-12-27 | 10 | 2031-12-27 09:00 | 5.4 | 6.7926 | N | 0
2026-12-27 | 11 | 2031-12-27 10:00 | 5.54 | 6.9687 | N | 0
2026-12-27 | 12 | 2031-12-27 11:00 | 5.92 | 7.4467 | N | 0
2026-12-27 | 13 | 2031-12-27 12:00 | 6.5 | 8.1762 | N | 0
2026-12-27 | 14 | 2031-12-27 13:00 | 6.73 | 8.4655 | N | 0
2026-12-27 | 15 | 2031-12-27 14:00 | 7.19 | 9.0442 | N | 0
2026-12-27 | 16 | 2031-12-27 15:00 | 7.33 | 9.2203 | N | 0
2026-12-27 | 17 | 2031-12-27 16:00 | 7.58 | 9.5347 | N | 0
2026-12-27 | 18 | 2031-12-27 17:00 | 7.41 | 9.3209 | N | 0
2026-12-27 | 19 | 2031-12-27 18:00 | 7.24 | 9.1071 | N | 0
2026-12-27 | 20 | 2031-12-27 19:00 | 7.45 | 9.3712 | N | 0
2026-12-27 | 21 | 2031-12-27 20:00 | 7.96 | 10.0127 | N | 0
2026-12-27 | 22 | 2031-12-27 21:00 | 8.22 | 10.3398 | N | 0
2026-12-27 | 23 | 2031-12-27 22:00 | 8.22 | 10.3398 | N | 0
2026-12-28 | 00 | 2031-12-27 23:00 | 7.92 | 9.9624 | N | 0
2026-12-28 | 01 | 2031-12-28 | 7.83 | 9.8492 | N | 0
2026-12-28 | 02 | 2031-12-28 01:00 | 7.64 | 9.6102 | N | 0
2026-12-28 | 03 | 2031-12-28 02:00 | 6.98 | 8.78 | N | 0
2026-12-28 | 04 | 2031-12-28 03:00 | 6.51 | 8.1888 | N | 0
2026-12-28 | 05 | 2031-12-28 04:00 | 6.03 | 7.585 | N | 0
2026-12-28 | 06 | 2031-12-28 05:00 | 5.57 | 7.0064 | N | 0
2026-12-28 | 07 | 2031-12-28 06:00 | 5.33 | 6.7045 | N | 0
2026-12-28 | 08 | 2031-12-28 07:00 | 5.05 | 6.3523 | N | 0
2026-12-28 | 09 | 2031-12-28 08:00 | 5 | 6.2894 | N | 0
2026-12-28 | 10 | 2031-12-28 09:00 | 5.15 | 6.4781 | N | 0
2026-12-28 | 11 | 2031-12-28 10:00 | 5.15 | 6.4781 | N | 0
2026-12-28 | 12 | 2031-12-28 11:00 | 5.48 | 6.8932 | N | 0
2026-12-28 | 13 | 2031-12-28 12:00 | 6.02 | 7.5724 | N | 0
2026-12-28 | 14 | 2031-12-28 13:00 | 6.41 | 8.063 | N | 0
2026-12-28 | 15 | 2031-12-28 14:00 | 6.82 | 8.5788 | N | 0
2026-12-28 | 16 | 2031-12-28 15:00 | 6.86 | 8.6291 | N | 0
2026-12-28 | 17 | 2031-12-28 16:00 | 7.08 | 8.9058 | N | 0
2026-12-28 | 18 | 2031-12-28 17:00 | 7.55 | 9.497 | N | 0
2026-12-28 | 19 | 2031-12-28 18:00 | 7.54 | 9.4844 | N | 0
2026-12-28 | 20 | 2031-12-28 19:00 | 7.73 | 9.7234 | N | 0
2026-12-28 | 21 | 2031-12-28 20:00 | 8.51 | 10.7046 | Y | 0.064571 | 1
2026-12-28 | 22 | 2031-12-28 21:00 | 8.72 | 10.9687 | Y | 0.32873 | 2 | 2
2026-12-28 | 23 | 2031-12-28 22:00 | 8.35 | 10.5033 | N | 0
2026-12-29 | 00 | 2031-12-28 23:00 | 8.07 | 10.1511 | N | 0
2026-12-29 | 01 | 2031-12-29 | 7.58 | 9.5347 | N | 0
2026-12-29 | 02 | 2031-12-29 01:00 | 7.29 | 9.17 | N | 0
2026-12-29 | 03 | 2031-12-29 02:00 | 6.78 | 8.5284 | N | 0
2026-12-29 | 04 | 2031-12-29 03:00 | 6.19 | 7.7863 | N | 0
2026-12-29 | 05 | 2031-12-29 04:00 | 5.54 | 6.9687 | N | 0
2026-12-29 | 06 | 2031-12-29 05:00 | 5.06 | 6.3649 | N | 0
2026-12-29 | 07 | 2031-12-29 06:00 | 4.86 | 6.1133 | N | 0
2026-12-29 | 08 | 2031-12-29 07:00 | 4.74 | 5.9624 | N | 0
2026-12-29 | 09 | 2031-12-29 08:00 | 4.58 | 5.7611 | N | 0
2026-12-29 | 10 | 2031-12-29 09:00 | 4.6 | 5.7863 | N | 0
2026-12-29 | 11 | 2031-12-29 10:00 | 4.9 | 6.1636 | N | 0
2026-12-29 | 12 | 2031-12-29 11:00 | 5.05 | 6.3523 | N | 0
2026-12-29 | 13 | 2031-12-29 12:00 | 5.48 | 6.8932 | N | 0
2026-12-29 | 14 | 2031-12-29 13:00 | 6.1 | 7.6731 | N | 0
2026-12-29 | 15 | 2031-12-29 14:00 | 6.65 | 8.3649 | N | 0
2026-12-29 | 16 | 2031-12-29 15:00 | 6.81 | 8.5662 | N | 0
2026-12-29 | 17 | 2031-12-29 16:00 | 7.24 | 9.1071 | N | 0
2026-12-29 | 18 | 2031-12-29 17:00 | 7.15 | 8.9939 | N | 0
2026-12-29 | 19 | 2031-12-29 18:00 | 6.98 | 8.78 | N | 0
2026-12-29 | 20 | 2031-12-29 19:00 | 7.12 | 8.9561 | N | 0
2026-12-29 | 21 | 2031-12-29 20:00 | 8.01 | 10.0756 | N | 0
2026-12-29 | 22 | 2031-12-29 21:00 | 8.5 | 10.692 | Y | 0.051992 | 1 | 1
2026-12-29 | 23 | 2031-12-29 22:00 | 8.36 | 10.5159 | N | 0
2026-12-30 | 00 | 2031-12-29 23:00 | 8.24 | 10.3649 | N | 0
2026-12-30 | 01 | 2031-12-30 | 8.12 | 10.214 | N | 0
2026-12-30 | 02 | 2031-12-30 01:00 | 7.78 | 9.7863 | N | 0
2026-12-30 | 03 | 2031-12-30 02:00 | 7.35 | 9.2454 | N | 0
2026-12-30 | 04 | 2031-12-30 03:00 | 6.55 | 8.2391 | N | 0
2026-12-30 | 05 | 2031-12-30 04:00 | 6.15 | 7.736 | N | 0
2026-12-30 | 06 | 2031-12-30 05:00 | 5.76 | 7.2454 | N | 0
2026-12-30 | 07 | 2031-12-30 06:00 | 5.48 | 6.8932 | N | 0
2026-12-30 | 08 | 2031-12-30 07:00 | 5.24 | 6.5913 | N | 0
2026-12-30 | 09 | 2031-12-30 08:00 | 5.24 | 6.5913 | N | 0
2026-12-30 | 10 | 2031-12-30 09:00 | 5.24 | 6.5913 | N | 0
2026-12-30 | 11 | 2031-12-30 10:00 | 5.6 | 7.0441 | N | 0
2026-12-30 | 12 | 2031-12-30 11:00 | 6.04 | 7.5976 | N | 0
2026-12-30 | 13 | 2031-12-30 12:00 | 6.36 | 8.0001 | N | 0
2026-12-30 | 14 | 2031-12-30 13:00 | 6.42 | 8.0756 | N | 0
2026-12-30 | 15 | 2031-12-30 14:00 | 6.69 | 8.4152 | N | 0
2026-12-30 | 16 | 2031-12-30 15:00 | 6.97 | 8.7674 | N | 0
2026-12-30 | 17 | 2031-12-30 16:00 | 7.01 | 8.8177 | N | 0
2026-12-30 | 18 | 2031-12-30 17:00 | 7.01 | 8.8177 | N | 0
2026-12-30 | 19 | 2031-12-30 18:00 | 7.01 | 8.8177 | N | 0
2026-12-30 | 20 | 2031-12-30 19:00 | 7.15 | 8.9939 | N | 0
2026-12-30 | 21 | 2031-12-30 20:00 | 8.08 | 10.1637 | N | 0
2026-12-30 | 22 | 2031-12-30 21:00 | 8.65 | 10.8807 | Y | 0.24067 | 1
2026-12-30 | 23 | 2031-12-30 22:00 | 8.52 | 10.7172 | Y | 0.07715 | 2 | 2
2026-12-31 | 00 | 2031-12-30 23:00 | 8.2 | 10.3146 | N | 0
2026-12-31 | 01 | 2031-12-31 | 8.2 | 10.3146 | N | 0
2026-12-31 | 02 | 2031-12-31 01:00 | 7.83 | 9.8492 | N | 0
2026-12-31 | 03 | 2031-12-31 02:00 | 7.36 | 9.258 | N | 0
2026-12-31 | 04 | 2031-12-31 03:00 | 6.74 | 8.4781 | N | 0
2026-12-31 | 05 | 2031-12-31 04:00 | 6.13 | 7.7108 | N | 0
2026-12-31 | 06 | 2031-12-31 05:00 | 5.67 | 7.1322 | N | 0
2026-12-31 | 07 | 2031-12-31 06:00 | 5.4 | 6.7926 | N | 0
2026-12-31 | 08 | 2031-12-31 07:00 | 5.24 | 6.5913 | N | 0
2026-12-31 | 09 | 2031-12-31 08:00 | 5.22 | 6.5661 | N | 0
2026-12-31 | 10 | 2031-12-31 09:00 | 5.26 | 6.6165 | N | 0
2026-12-31 | 11 | 2031-12-31 10:00 | 5.41 | 6.8051 | N | 0
2026-12-31 | 12 | 2031-12-31 11:00 | 5.79 | 7.2831 | N | 0
2026-12-31 | 13 | 2031-12-31 12:00 | 6.31 | 7.9372 | N | 0
2026-12-31 | 14 | 2031-12-31 13:00 | 6.58 | 8.2769 | N | 0
2026-12-31 | 15 | 2031-12-31 14:00 | 6.72 | 8.453 | N | 0
2026-12-31 | 16 | 2031-12-31 15:00 | 6.8 | 8.5536 | N | 0
2026-12-31 | 17 | 2031-12-31 16:00 | 7.18 | 9.0316 | N | 0
2026-12-31 | 18 | 2031-12-31 17:00 | 7.26 | 9.1322 | N | 0
2026-12-31 | 19 | 2031-12-31 18:00 | 7.1 | 8.931 | N | 0
2026-12-31 | 20 | 2031-12-31 19:00 | 7.43 | 9.3461 | N | 0
2026-12-31 | 21 | 2031-12-31 20:00 | 8.13 | 10.2266 | N | 0
2026-12-31 | 22 | 2031-12-31 21:00 | 8.52 | 10.7172 | Y | 0.07715 | 1 | 1
2026-12-31 | 23 | 2031-12-31 22:00 | 8.36 | 10.5159 | N | 0
Formulas:
Date-Time = [Date-Time, row above] + TIME(1,0,0)

## Bradshaw Forecast
Hourly Load (MVA)
Total load | 49754.6836 |  | 52099.0561 | 54553.8922 | 57124.3969 | 59816.0201 | Exceeding Planning capacity |  |  |  | BRADSHAW
Date-Time | BRADSHAW MS 2031 (MVA) | Load Shape | 2032 | 2033 | 2034 | 2035 | 2032 | 2033 | 2034 | 2035 | MW Exceeding planning capacity
2025-01-01 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0 |  | 2032 | 2033 | 2034 | 2035
2025-01-01 01:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0 | avg | 1.1538 | 0.88359 | 0.91235 | 0.98543
2025-01-01 02:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0 | max | 8.379 | 9.225 | 10.1109 | 11.0385
2025-01-01 03:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0 | median | 0.29019 | 0.39352 | 0.57777 | 0.71826
2025-01-01 04:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-01-01 05:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-01-01 06:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0 | Annual Hours Exceeding Planning Capacity After BESS Deployment
2025-01-01 07:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0 | MW BESS Size | 2032 | 2033 | 2034 | 2035
2025-01-01 08:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0 | 4 | 5 | 14 | 16 | 16
2025-01-01 09:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0 | 5 | 3 | 4 | 11 | 15
2025-01-01 10:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0 | 6 | 1 | 3 | 3 | 5
2025-01-01 11:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0 | 7 | 1 | 1 | 1 | 3
2025-01-01 12:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0 | 8 | 1 | 1 | 1 | 1
2025-01-01 13:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1
2025-01-01 14:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 1
2025-01-01 15:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 1
2025-01-01 16:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0
2025-01-01 17:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0
2025-01-01 18:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0
2025-01-01 19:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0
2025-01-01 20:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0
2025-01-01 21:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0
2025-01-01 22:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0 | BESS MW needed | 9 | 10 | 11 | 12
2025-01-01 23:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-01-02 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-02 01:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0 | Year | Min MW BESS
2025-01-02 02:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0 | 2032 | 9
2025-01-02 03:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0 | 2033 | 10
2025-01-02 04:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0 | 2034 | 11
2025-01-02 05:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0 | 2035 | 12
2025-01-02 06:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-01-02 07:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-01-02 08:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-01-02 09:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-02 10:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-01-02 11:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-01-02 12:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-01-02 13:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-01-02 14:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-01-02 15:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-01-02 16:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-01-02 17:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-01-02 18:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-01-02 19:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-01-02 20:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-01-02 21:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-01-02 22:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-01-02 23:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-01-03 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-01-03 01:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-01-03 02:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-01-03 03:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-01-03 04:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-01-03 05:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-01-03 06:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-01-03 07:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-01-03 08:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-01-03 09:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-01-03 10:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-01-03 11:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-01-03 12:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-01-03 13:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-01-03 14:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-01-03 15:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-01-03 16:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-01-03 17:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-03 18:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-01-03 19:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-01-03 20:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-01-03 21:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-01-03 22:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-01-03 23:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-01-04 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-01-04 01:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-01-04 02:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-01-04 03:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-01-04 04:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-01-04 05:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-01-04 06:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-01-04 07:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-04 08:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-04 09:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-01-04 10:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-01-04 11:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-01-04 12:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-01-04 13:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-01-04 14:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-04 15:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-04 16:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-01-04 17:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-04 18:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-04 19:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-04 20:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-04 21:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-01-04 22:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-04 23:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-01-05 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-01-05 01:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-01-05 02:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-01-05 03:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-01-05 04:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-01-05 05:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-01-05 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-01-05 07:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-01-05 08:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-01-05 09:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-01-05 10:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-01-05 11:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-01-05 12:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-01-05 13:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-01-05 14:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-01-05 15:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-05 16:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-05 17:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-01-05 18:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-01-05 19:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-01-05 20:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-01-05 21:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-01-05 22:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-01-05 23:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-01-06 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-01-06 01:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-01-06 02:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-01-06 03:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-01-06 04:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-01-06 05:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-01-06 06:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-01-06 07:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-01-06 08:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-06 09:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-01-06 10:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-06 11:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-01-06 12:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-01-06 13:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-06 14:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-06 15:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-06 16:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-06 17:00 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-01-06 18:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-01-06 19:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-01-06 20:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-01-06 21:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-01-06 22:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-01-06 23:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-07 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-01-07 01:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-07 02:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-01-07 03:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-01-07 04:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-01-07 05:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-01-07 06:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-01-07 07:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-01-07 08:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-07 09:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-07 10:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-01-07 11:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-01-07 12:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-01-07 13:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-07 14:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-01-07 15:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-01-07 16:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-01-07 17:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-07 18:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2025-01-07 19:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-01-07 20:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-01-07 21:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-01-07 22:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-07 23:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-01-08 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-01-08 01:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-01-08 02:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-01-08 03:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-01-08 04:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-08 05:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-01-08 06:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-01-08 07:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-08 08:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-01-08 09:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-08 10:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-01-08 11:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-01-08 12:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-01-08 13:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-01-08 14:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-08 15:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-01-08 16:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-01-08 17:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-01-08 18:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-01-08 19:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-01-08 20:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-01-08 21:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-01-08 22:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-01-08 23:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-09 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-01-09 01:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-01-09 02:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-01-09 03:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-01-09 04:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-01-09 05:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-09 06:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-01-09 07:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-01-09 08:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-09 09:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-01-09 10:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-09 11:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-01-09 12:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-01-09 13:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-01-09 14:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-01-09 15:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-01-09 16:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-09 17:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-09 18:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-01-09 19:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-01-09 20:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-01-09 21:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-01-09 22:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-01-09 23:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-01-10 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-01-10 01:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-01-10 02:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-01-10 03:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-01-10 04:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-01-10 05:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-10 06:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-01-10 07:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-01-10 08:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-10 09:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-10 10:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-10 11:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-01-10 12:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-01-10 13:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-10 14:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-10 15:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-01-10 16:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-01-10 17:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-01-10 18:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-10 19:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-10 20:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-01-10 21:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-10 22:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-01-10 23:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-11 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-01-11 01:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-01-11 02:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-01-11 03:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-01-11 04:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-01-11 05:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-01-11 06:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-01-11 07:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-01-11 08:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-01-11 09:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-01-11 10:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-01-11 11:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-01-11 12:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-11 13:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-01-11 14:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-01-11 15:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-01-11 16:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-11 17:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-01-11 18:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-01-11 19:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-01-11 20:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-01-11 21:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-11 22:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-01-11 23:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-01-12 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-01-12 01:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-01-12 02:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-01-12 03:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-01-12 04:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-01-12 05:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-01-12 06:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-01-12 07:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-01-12 08:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-01-12 09:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-01-12 10:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-01-12 11:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-01-12 12:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-01-12 13:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-12 14:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-01-12 15:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-12 16:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-01-12 17:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-01-12 18:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-01-12 19:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-01-12 20:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-01-12 21:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-12 22:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-01-12 23:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-01-13 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-01-13 01:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-01-13 02:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-01-13 03:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-01-13 04:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-01-13 05:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-01-13 06:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-01-13 07:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-13 08:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-01-13 09:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-01-13 10:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-01-13 11:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-01-13 12:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-01-13 13:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-01-13 14:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-13 15:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-01-13 16:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-13 17:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-13 18:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-13 19:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-01-13 20:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-01-13 21:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-13 22:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-01-13 23:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-01-14 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-01-14 01:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-01-14 02:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-01-14 03:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-01-14 04:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-01-14 05:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-01-14 06:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-01-14 07:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-01-14 08:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-01-14 09:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-14 10:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-14 11:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-01-14 12:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-01-14 13:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-01-14 14:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-01-14 15:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-01-14 16:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-14 17:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-01-14 18:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2025-01-14 19:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-01-14 20:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-01-14 21:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-01-14 22:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-01-14 23:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-01-15 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-01-15 01:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-01-15 02:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-01-15 03:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-01-15 04:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-01-15 05:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-01-15 06:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-01-15 07:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-01-15 08:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-01-15 09:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-15 10:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-15 11:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-15 12:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-01-15 13:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-01-15 14:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-15 15:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-01-15 16:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-01-15 17:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-01-15 18:00 | 7.7234 | 0.01552% | 8.0873 | 8.4684 | 8.8674 | 9.2852 | 0 | 0 | 0 | 0
2025-01-15 19:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-01-15 20:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-01-15 21:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-01-15 22:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-01-15 23:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-01-16 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-01-16 01:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-01-16 02:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-01-16 03:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-01-16 04:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-01-16 05:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-01-16 06:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-01-16 07:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-01-16 08:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-01-16 09:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-01-16 10:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-01-16 11:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-16 12:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-16 13:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-01-16 14:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-16 15:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-01-16 16:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-16 17:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-01-16 18:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-01-16 19:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-01-16 20:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-01-16 21:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-01-16 22:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-01-16 23:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-01-17 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-01-17 01:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-01-17 02:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-01-17 03:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-01-17 04:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-01-17 05:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-01-17 06:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-01-17 07:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-01-17 08:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-01-17 09:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-01-17 10:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-01-17 11:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-01-17 12:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-01-17 13:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-01-17 14:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-01-17 15:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-01-17 16:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-01-17 17:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-01-17 18:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-01-17 19:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-17 20:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-01-17 21:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-01-17 22:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-01-17 23:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-01-18 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-01-18 01:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-01-18 02:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-01-18 03:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-01-18 04:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-01-18 05:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-01-18 06:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-01-18 07:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-01-18 08:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-01-18 09:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-01-18 10:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-01-18 11:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-01-18 12:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-01-18 13:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-01-18 14:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-18 15:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-01-18 16:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-01-18 17:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-18 18:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-01-18 19:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-01-18 20:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-01-18 21:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-01-18 22:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-01-18 23:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-01-19 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-01-19 01:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-19 02:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-01-19 03:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-01-19 04:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-01-19 05:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-01-19 06:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-01-19 07:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-01-19 08:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-01-19 09:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-01-19 10:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-19 11:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-01-19 12:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-01-19 13:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-01-19 14:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-19 15:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-19 16:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-19 17:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-19 18:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-01-19 19:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-01-19 20:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-01-19 21:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-01-19 22:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-01-19 23:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-01-20 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-01-20 01:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-01-20 02:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-01-20 03:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-01-20 04:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-20 05:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-01-20 06:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-01-20 07:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-01-20 08:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-20 09:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-20 10:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-01-20 11:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-01-20 12:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-01-20 13:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-20 14:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-01-20 15:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-01-20 16:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-01-20 17:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-01-20 18:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-01-20 19:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2025-01-20 20:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-01-20 21:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-01-20 22:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-01-20 23:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-01-21 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-01-21 01:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-01-21 02:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-01-21 03:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-01-21 04:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-01-21 05:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-01-21 06:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-01-21 07:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-01-21 08:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-01-21 09:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-01-21 10:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-21 11:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-01-21 12:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-21 13:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-01-21 14:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-01-21 15:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-01-21 16:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-01-21 17:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-01-21 18:00 | 8.3272 | 0.01674% | 8.7195 | 9.1304 | 9.5606 | 10.0111 | 0 | 0 | 0 | 0
2025-01-21 19:00 | 8.1637 | 0.01641% | 8.5483 | 8.9511 | 9.3729 | 9.8145 | 0 | 0 | 0 | 0
2025-01-21 20:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-01-21 21:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-01-21 22:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-01-21 23:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-01-22 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-22 01:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-01-22 02:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-01-22 03:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-01-22 04:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-01-22 05:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-01-22 06:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-01-22 07:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-22 08:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-22 09:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-01-22 10:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-01-22 11:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-01-22 12:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-01-22 13:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-01-22 14:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-01-22 15:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-01-22 16:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-01-22 17:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-01-22 18:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2025-01-22 19:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-01-22 20:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2025-01-22 21:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-01-22 22:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-01-22 23:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-01-23 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-01-23 01:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-01-23 02:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-01-23 03:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-01-23 04:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-23 05:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-23 06:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-01-23 07:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-01-23 08:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-01-23 09:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-23 10:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-01-23 11:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-01-23 12:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-23 13:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-01-23 14:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-23 15:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-01-23 16:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-01-23 17:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-01-23 18:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-01-23 19:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-01-23 20:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-01-23 21:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-01-23 22:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-23 23:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-24 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-01-24 01:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-01-24 02:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-24 03:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-24 04:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-24 05:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-24 06:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-01-24 07:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-01-24 08:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-24 09:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-24 10:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-01-24 11:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-01-24 12:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-24 13:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-01-24 14:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-01-24 15:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-01-24 16:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-24 17:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-01-24 18:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-01-24 19:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-24 20:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-01-24 21:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-24 22:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-01-24 23:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-25 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-01-25 01:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-01-25 02:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-25 03:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-01-25 04:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-01-25 05:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-01-25 06:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-01-25 07:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-01-25 08:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-01-25 09:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-01-25 10:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-25 11:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-25 12:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-25 13:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-25 14:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-01-25 15:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-01-25 16:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-01-25 17:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-01-25 18:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-25 19:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-01-25 20:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-01-25 21:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-01-25 22:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-01-25 23:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-01-26 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-01-26 01:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-01-26 02:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-01-26 03:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-01-26 04:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-01-26 05:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-01-26 06:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-01-26 07:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-01-26 08:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-01-26 09:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-01-26 10:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-01-26 11:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-01-26 12:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-01-26 13:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-01-26 14:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-26 15:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-26 16:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-01-26 17:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-26 18:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-01-26 19:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-26 20:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-01-26 21:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-01-26 22:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-01-26 23:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-01-27 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-01-27 01:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-01-27 02:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-01-27 03:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-01-27 04:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-01-27 05:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-01-27 06:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-01-27 07:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-01-27 08:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-01-27 09:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-01-27 10:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-01-27 11:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-01-27 12:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-27 13:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-01-27 14:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-01-27 15:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-01-27 16:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-27 17:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-01-27 18:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-01-27 19:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-01-27 20:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-01-27 21:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-01-27 22:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-01-27 23:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-01-28 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-01-28 01:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-01-28 02:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-01-28 03:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-01-28 04:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-01-28 05:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-01-28 06:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-28 07:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-01-28 08:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-28 09:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-28 10:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-28 11:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-28 12:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-01-28 13:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-28 14:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-01-28 15:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-01-28 16:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-01-28 17:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-01-28 18:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2025-01-28 19:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-01-28 20:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-01-28 21:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-01-28 22:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-01-28 23:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-01-29 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-01-29 01:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-01-29 02:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-01-29 03:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-01-29 04:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-01-29 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-01-29 06:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-01-29 07:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-01-29 08:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-01-29 09:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-01-29 10:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-01-29 11:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-01-29 12:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-01-29 13:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-01-29 14:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-01-29 15:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-01-29 16:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-29 17:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-01-29 18:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-01-29 19:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-01-29 20:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-01-29 21:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-01-29 22:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-01-29 23:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-30 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-01-30 01:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-01-30 02:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-01-30 03:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-01-30 04:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-01-30 05:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-30 06:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-01-30 07:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-01-30 08:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-01-30 09:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-01-30 10:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-30 11:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-30 12:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-01-30 13:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-01-30 14:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-01-30 15:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-01-30 16:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-01-30 17:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-01-30 18:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-01-30 19:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-01-30 20:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-01-30 21:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-01-30 22:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-30 23:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-01-31 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-01-31 01:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-01-31 02:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-01-31 03:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-01-31 04:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-01-31 05:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-01-31 06:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-01-31 07:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-01-31 08:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-01-31 09:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-01-31 10:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-01-31 11:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-01-31 12:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-01-31 13:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-01-31 14:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-01-31 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-01-31 16:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-01-31 17:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-01-31 18:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-01-31 19:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-01-31 20:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-01-31 21:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-01-31 22:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-01-31 23:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-02-01 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-02-01 01:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-02-01 02:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-02-01 03:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-02-01 04:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-02-01 05:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-02-01 06:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-02-01 07:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-02-01 08:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-02-01 09:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-02-01 10:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-01 11:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-02-01 12:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-02-01 13:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-02-01 14:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-02-01 15:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-01 16:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-01 17:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-02-01 18:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-02-01 19:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-02-01 20:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-02-01 21:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-02-01 22:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-02-01 23:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-02-02 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-02 01:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-02-02 02:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-02-02 03:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-02-02 04:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-02-02 05:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-02-02 06:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-02-02 07:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-02-02 08:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-02-02 09:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-02-02 10:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-02-02 11:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-02 12:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-02-02 13:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-02-02 14:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-02-02 15:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-02-02 16:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-02-02 17:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-02-02 18:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2025-02-02 19:00 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2025-02-02 20:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-02-02 21:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-02 22:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-02-02 23:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-02-03 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-02-03 01:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-02-03 02:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-02-03 03:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-02-03 04:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-02-03 05:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-02-03 06:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-02-03 07:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-02-03 08:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-02-03 09:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-02-03 10:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-02-03 11:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-03 12:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-03 13:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-03 14:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-02-03 15:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-03 16:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-03 17:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-02-03 18:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-02-03 19:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-02-03 20:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-02-03 21:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-02-03 22:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-03 23:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-02-04 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-02-04 01:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-02-04 02:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-02-04 03:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-02-04 04:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-02-04 05:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-02-04 06:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-02-04 07:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-02-04 08:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-02-04 09:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-02-04 10:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-02-04 11:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-02-04 12:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-04 13:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-04 14:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-04 15:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-02-04 16:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-02-04 17:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-04 18:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-02-04 19:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-02-04 20:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-02-04 21:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-02-04 22:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-02-04 23:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-05 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-02-05 01:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-02-05 02:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-02-05 03:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-02-05 04:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-02-05 05:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-02-05 06:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-02-05 07:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-02-05 08:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-05 09:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-05 10:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-02-05 11:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-02-05 12:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-02-05 13:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-05 14:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-02-05 15:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-05 16:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-02-05 17:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-02-05 18:00 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-02-05 19:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-02-05 20:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-02-05 21:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-02-05 22:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-02-05 23:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-06 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-02-06 01:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-02-06 02:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-06 03:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-02-06 04:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-02-06 05:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-02-06 06:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-02-06 07:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-02-06 08:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-06 09:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-06 10:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-02-06 11:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-06 12:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-06 13:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-02-06 14:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-02-06 15:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-02-06 16:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-02-06 17:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-02-06 18:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-02-06 19:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-02-06 20:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-02-06 21:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-02-06 22:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-02-06 23:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-02-07 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-02-07 01:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-02-07 02:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-02-07 03:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-02-07 04:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-02-07 05:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-02-07 06:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-02-07 07:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-02-07 08:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-02-07 09:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-07 10:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-02-07 11:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-02-07 12:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-02-07 13:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-02-07 14:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-02-07 15:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-02-07 16:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-07 17:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-07 18:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-02-07 19:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-07 20:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-02-07 21:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-02-07 22:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-02-07 23:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-02-08 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-02-08 01:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-02-08 02:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-02-08 03:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-02-08 04:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-02-08 05:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-02-08 06:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-02-08 07:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-02-08 08:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-02-08 09:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-02-08 10:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-02-08 11:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-02-08 12:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-02-08 13:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-02-08 14:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-08 15:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-02-08 16:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-08 17:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-08 18:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-02-08 19:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-02-08 20:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-02-08 21:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-08 22:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-08 23:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-02-09 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-02-09 01:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-02-09 02:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-02-09 03:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-02-09 04:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-02-09 05:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-02-09 06:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-02-09 07:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-02-09 08:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-02-09 09:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-02-09 10:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-02-09 11:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-02-09 12:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-02-09 13:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-09 14:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-09 15:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-09 16:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-02-09 17:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-02-09 18:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-02-09 19:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-02-09 20:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-02-09 21:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-02-09 22:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-02-09 23:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-02-10 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-02-10 01:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-02-10 02:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-02-10 03:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-02-10 04:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-02-10 05:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-02-10 06:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-02-10 07:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-02-10 08:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-02-10 09:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-02-10 10:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-02-10 11:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-02-10 12:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-10 13:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-02-10 14:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-10 15:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-02-10 16:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-02-10 17:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-02-10 18:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-02-10 19:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-02-10 20:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-10 21:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-02-10 22:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-02-10 23:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-11 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-02-11 01:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-02-11 02:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-02-11 03:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-02-11 04:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-02-11 05:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-02-11 06:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-02-11 07:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-02-11 08:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-02-11 09:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-02-11 10:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-11 11:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-11 12:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-11 13:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-02-11 14:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-02-11 15:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-11 16:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-02-11 17:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-02-11 18:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-11 19:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-11 20:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-11 21:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-02-11 22:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-02-11 23:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-12 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-02-12 01:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-02-12 02:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-02-12 03:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-02-12 04:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-02-12 05:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-02-12 06:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-12 07:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-02-12 08:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-02-12 09:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-02-12 10:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-12 11:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-02-12 12:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-02-12 13:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-12 14:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-12 15:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-12 16:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-02-12 17:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-12 18:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-02-12 19:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-02-12 20:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-02-12 21:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-02-12 22:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-02-12 23:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-02-13 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-02-13 01:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-02-13 02:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-02-13 03:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-02-13 04:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-02-13 05:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-02-13 06:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-02-13 07:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-02-13 08:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-02-13 09:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-02-13 10:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-13 11:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-02-13 12:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-02-13 13:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-02-13 14:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-02-13 15:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-02-13 16:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-02-13 17:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-02-13 18:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-02-13 19:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-02-13 20:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-02-13 21:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-02-13 22:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-02-13 23:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-14 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-02-14 01:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-02-14 02:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-02-14 03:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-02-14 04:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-02-14 05:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-02-14 06:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-02-14 07:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-02-14 08:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-02-14 09:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-02-14 10:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-14 11:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-14 12:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-02-14 13:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-14 14:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-02-14 15:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-14 16:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-14 17:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-14 18:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-02-14 19:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-02-14 20:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-02-14 21:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-02-14 22:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-14 23:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-02-15 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-02-15 01:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-02-15 02:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-15 03:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-02-15 04:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-02-15 05:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-02-15 06:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-02-15 07:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-15 08:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-02-15 09:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-02-15 10:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-02-15 11:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-02-15 12:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-15 13:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-02-15 14:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-02-15 15:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-02-15 16:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-02-15 17:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-02-15 18:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-02-15 19:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-02-15 20:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-02-15 21:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-02-15 22:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-02-15 23:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-02-16 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-02-16 01:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-02-16 02:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-02-16 03:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-02-16 04:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-02-16 05:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-02-16 06:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-02-16 07:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-16 08:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-02-16 09:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-02-16 10:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-16 11:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-02-16 12:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-02-16 13:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-02-16 14:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-02-16 15:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-02-16 16:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-02-16 17:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-02-16 18:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-02-16 19:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-02-16 20:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-16 21:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-02-16 22:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-02-16 23:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-02-17 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-02-17 01:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-02-17 02:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-02-17 03:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-17 04:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-02-17 05:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-02-17 06:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-02-17 07:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-02-17 08:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-02-17 09:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-02-17 10:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-02-17 11:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-02-17 12:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-02-17 13:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-02-17 14:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-02-17 15:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-17 16:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-02-17 17:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-02-17 18:00 | 7.7234 | 0.01552% | 8.0873 | 8.4684 | 8.8674 | 9.2852 | 0 | 0 | 0 | 0
2025-02-17 19:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-02-17 20:00 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-02-17 21:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-17 22:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-02-17 23:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-02-18 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-02-18 01:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-02-18 02:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-02-18 03:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-02-18 04:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-02-18 05:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-02-18 06:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-02-18 07:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-02-18 08:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-02-18 09:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-02-18 10:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-18 11:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-02-18 12:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-18 13:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-02-18 14:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-02-18 15:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-18 16:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-02-18 17:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-02-18 18:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-02-18 19:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-02-18 20:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-02-18 21:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-02-18 22:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-02-18 23:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-19 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-02-19 01:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-02-19 02:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-02-19 03:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-02-19 04:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-02-19 05:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-02-19 06:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-02-19 07:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-02-19 08:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-19 09:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-19 10:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-02-19 11:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-02-19 12:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-19 13:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-02-19 14:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-19 15:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-02-19 16:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-02-19 17:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-02-19 18:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-02-19 19:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-02-19 20:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-02-19 21:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-02-19 22:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-02-19 23:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-20 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-02-20 01:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-02-20 02:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-02-20 03:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-02-20 04:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-02-20 05:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-02-20 06:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-02-20 07:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-02-20 08:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-02-20 09:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-02-20 10:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-02-20 11:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-02-20 12:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-02-20 13:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-02-20 14:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-02-20 15:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-02-20 16:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-02-20 17:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-20 18:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-02-20 19:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2025-02-20 20:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-02-20 21:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-02-20 22:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-02-20 23:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-02-21 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-02-21 01:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-02-21 02:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-02-21 03:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-02-21 04:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-02-21 05:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-02-21 06:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-02-21 07:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-02-21 08:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-21 09:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-02-21 10:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-02-21 11:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-02-21 12:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-02-21 13:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-21 14:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-02-21 15:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-21 16:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-02-21 17:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-02-21 18:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-02-21 19:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-02-21 20:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-02-21 21:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-21 22:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-02-21 23:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-02-22 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-02-22 01:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-02-22 02:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-02-22 03:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-02-22 04:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-02-22 05:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-02-22 06:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-02-22 07:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-02-22 08:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-02-22 09:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-02-22 10:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-02-22 11:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-22 12:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-02-22 13:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-02-22 14:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-02-22 15:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-22 16:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-02-22 17:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-02-22 18:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-02-22 19:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-02-22 20:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-02-22 21:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-02-22 22:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-02-22 23:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-02-23 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-02-23 01:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-02-23 02:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-02-23 03:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-02-23 04:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-02-23 05:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-02-23 06:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-02-23 07:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-02-23 08:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-02-23 09:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-02-23 10:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-02-23 11:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-02-23 12:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-23 13:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-23 14:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-02-23 15:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-23 16:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-23 17:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-02-23 18:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-02-23 19:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-02-23 20:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-02-23 21:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-02-23 22:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-02-23 23:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-02-24 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-02-24 01:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-02-24 02:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-02-24 03:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-02-24 04:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-02-24 05:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-02-24 06:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-02-24 07:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-02-24 08:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-02-24 09:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-02-24 10:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-02-24 11:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-02-24 12:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-02-24 13:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-02-24 14:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-02-24 15:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-02-24 16:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-02-24 17:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-02-24 18:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-02-24 19:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-02-24 20:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-02-24 21:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-02-24 22:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-02-24 23:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-02-25 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-02-25 01:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-02-25 02:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-02-25 03:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-02-25 04:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-02-25 05:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-02-25 06:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-02-25 07:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-02-25 08:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-02-25 09:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-02-25 10:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-02-25 11:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-02-25 12:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-02-25 13:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-02-25 14:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-02-25 15:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-02-25 16:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-02-25 17:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-02-25 18:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-02-25 19:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-02-25 20:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-02-25 21:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-02-25 22:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-25 23:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-02-26 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-02-26 01:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-02-26 02:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-02-26 03:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-02-26 04:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-02-26 05:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-02-26 06:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-02-26 07:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-02-26 08:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-02-26 09:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-02-26 10:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-02-26 11:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-02-26 12:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-02-26 13:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-02-26 14:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-02-26 15:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-02-26 16:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-02-26 17:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-02-26 18:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-02-26 19:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-02-26 20:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-02-26 21:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-26 22:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-02-26 23:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-02-27 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-02-27 01:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-02-27 02:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-02-27 03:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-02-27 04:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-02-27 05:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-02-27 06:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-02-27 07:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-02-27 08:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-02-27 09:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-02-27 10:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-02-27 11:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-02-27 12:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-02-27 13:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-02-27 14:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-02-27 15:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-02-27 16:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-02-27 17:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-02-27 18:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-02-27 19:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-27 20:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-27 21:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-02-27 22:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-02-27 23:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-02-28 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-02-28 01:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-02-28 02:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-02-28 03:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-02-28 04:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-02-28 05:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-02-28 06:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-02-28 07:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-02-28 08:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-02-28 09:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-02-28 10:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-02-28 11:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-02-28 12:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-02-28 13:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-02-28 14:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-02-28 15:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-02-28 16:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-02-28 17:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-02-28 18:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-02-28 19:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-02-28 20:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-02-28 21:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-02-28 22:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-02-28 23:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-01 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-03-01 01:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-03-01 02:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-03-01 03:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-03-01 04:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-01 05:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-03-01 06:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-01 07:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-03-01 08:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-01 09:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-01 10:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-03-01 11:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-03-01 12:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-03-01 13:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-03-01 14:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-03-01 15:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-03-01 16:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-03-01 17:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-03-01 18:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-03-01 19:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-03-01 20:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-03-01 21:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-03-01 22:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-03-01 23:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-03-02 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-03-02 01:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-02 02:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-02 03:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-02 04:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-03-02 05:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-02 06:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-02 07:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-03-02 08:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-03-02 09:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-03-02 10:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-03-02 11:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-03-02 12:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-03-02 13:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-03-02 14:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-03-02 15:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-03-02 16:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-03-02 17:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-03-02 18:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-03-02 19:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-03-02 20:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-03-02 21:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-03-02 22:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-03-02 23:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-03-03 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-03 01:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-03 02:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-03 03:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-03-03 04:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-03 05:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-03-03 06:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-03-03 07:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-03-03 08:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-03-03 09:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-03-03 10:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-03-03 11:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-03-03 12:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-03-03 13:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-03-03 14:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-03-03 15:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-03-03 16:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-03-03 17:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-03-03 18:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-03-03 19:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-03-03 20:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-03-03 21:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-03-03 22:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-03-03 23:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-04 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-04 01:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-03-04 02:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-03-04 03:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-03-04 04:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-03-04 05:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-03-04 06:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-03-04 07:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-04 08:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-03-04 09:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-03-04 10:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-04 11:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-04 12:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-04 13:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-03-04 14:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-04 15:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-04 16:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-03-04 17:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-03-04 18:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-03-04 19:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-03-04 20:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-03-04 21:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-04 22:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-03-04 23:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-03-05 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-03-05 01:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-03-05 02:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-03-05 03:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-05 04:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-03-05 05:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-03-05 06:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-03-05 07:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-03-05 08:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-03-05 09:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-03-05 10:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-05 11:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-03-05 12:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-03-05 13:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-05 14:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-03-05 15:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-03-05 16:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-03-05 17:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-03-05 18:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-03-05 19:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-03-05 20:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-03-05 21:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-03-05 22:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-05 23:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-06 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-03-06 01:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-03-06 02:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-03-06 03:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-06 04:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-03-06 05:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-03-06 06:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-03-06 07:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-06 08:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-03-06 09:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-03-06 10:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-03-06 11:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-06 12:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-03-06 13:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-03-06 14:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-03-06 15:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-03-06 16:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-06 17:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-03-06 18:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-03-06 19:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-03-06 20:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-03-06 21:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-03-06 22:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-03-06 23:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-03-07 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-07 01:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-03-07 02:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-03-07 03:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-03-07 04:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-03-07 05:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-03-07 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-03-07 07:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-03-07 08:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-07 09:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-03-07 10:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-03-07 11:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-03-07 12:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-03-07 13:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-07 14:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-07 15:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-03-07 16:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-03-07 17:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-03-07 18:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-03-07 19:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-03-07 20:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-03-07 21:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-03-07 22:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-03-07 23:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-08 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-03-08 01:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-03-08 02:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-03-08 03:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-03-08 04:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-03-08 05:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-08 06:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-03-08 07:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-03-08 08:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-03-08 09:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-03-08 10:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-03-08 11:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-08 12:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-08 13:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-03-08 14:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-08 15:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-03-08 16:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-08 17:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-08 18:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-03-08 19:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-03-08 20:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-03-08 21:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-03-08 22:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-03-08 23:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-03-09 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-09 01:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-03-09 02:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-03-09 03:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-03-09 04:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-03-09 05:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-03-09 06:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-03-09 07:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-03-09 08:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-03-09 09:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-09 10:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-09 11:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-03-09 12:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-03-09 13:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-03-09 14:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-03-09 15:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-09 16:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-09 17:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-03-09 18:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-09 19:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-03-09 20:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-03-09 21:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-03-09 22:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-03-09 23:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-03-10 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-03-10 01:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-10 02:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-03-10 03:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-03-10 04:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-03-10 05:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-03-10 06:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-03-10 07:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-03-10 08:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-03-10 09:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-03-10 10:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-10 11:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-03-10 12:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-03-10 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-03-10 14:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-03-10 15:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-03-10 16:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-10 17:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-10 18:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-03-10 19:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-03-10 20:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-03-10 21:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-03-10 22:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-03-10 23:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-03-11 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-11 01:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-03-11 02:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-03-11 03:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-03-11 04:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-03-11 05:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-03-11 06:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-03-11 07:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-03-11 08:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-03-11 09:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-03-11 10:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-03-11 11:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-03-11 12:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-03-11 13:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-03-11 14:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-03-11 15:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-03-11 16:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-03-11 17:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-11 18:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-03-11 19:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-03-11 20:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-11 21:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-03-11 22:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-11 23:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-03-12 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-03-12 01:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-12 02:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-03-12 03:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-03-12 04:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-12 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-03-12 06:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-03-12 07:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-03-12 08:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-03-12 09:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-03-12 10:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-03-12 11:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-03-12 12:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-03-12 13:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-03-12 14:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-03-12 15:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-03-12 16:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-03-12 17:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-03-12 18:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-12 19:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-03-12 20:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-03-12 21:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-03-12 22:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-03-12 23:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-13 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-03-13 01:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-03-13 02:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-03-13 03:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-03-13 04:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-03-13 05:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-03-13 06:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-13 07:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-13 08:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-03-13 09:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-03-13 10:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-13 11:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-03-13 12:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-03-13 13:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-03-13 14:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-13 15:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-03-13 16:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-03-13 17:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-13 18:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-03-13 19:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-13 20:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-03-13 21:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-03-13 22:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-03-13 23:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-14 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-03-14 01:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-03-14 02:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-03-14 03:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-14 04:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-03-14 05:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-03-14 06:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-03-14 07:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-14 08:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-14 09:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-03-14 10:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-14 11:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-03-14 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-03-14 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-03-14 14:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-03-14 15:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-03-14 16:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-03-14 17:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-14 18:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-03-14 19:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-03-14 20:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-14 21:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-14 22:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-14 23:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-03-15 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-03-15 01:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-03-15 02:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-03-15 03:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-03-15 04:00 | 3.4592 | 0.006952% | 3.6222 | 3.7928 | 3.9716 | 4.1587 | 0 | 0 | 0 | 0
2025-03-15 05:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-03-15 06:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-03-15 07:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-03-15 08:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-03-15 09:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-03-15 10:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-03-15 11:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-03-15 12:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-03-15 13:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-15 14:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-03-15 15:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-03-15 16:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-15 17:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-15 18:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-15 19:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-03-15 20:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-03-15 21:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-03-15 22:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-03-15 23:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-03-16 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-03-16 01:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-03-16 02:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-03-16 03:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-03-16 04:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-03-16 05:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-03-16 06:00 | 3.4592 | 0.006952% | 3.6222 | 3.7928 | 3.9716 | 4.1587 | 0 | 0 | 0 | 0
2025-03-16 07:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-03-16 08:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-03-16 09:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-03-16 10:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-03-16 11:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-03-16 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-03-16 13:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-03-16 14:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-16 15:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-16 16:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-16 17:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-16 18:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-03-16 19:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-03-16 20:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-03-16 21:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-03-16 22:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-03-16 23:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-03-17 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-17 01:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-03-17 02:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-03-17 03:00 | 3.4718 | 0.006978% | 3.6353 | 3.8066 | 3.986 | 4.1738 | 0 | 0 | 0 | 0
2025-03-17 04:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-03-17 05:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-03-17 06:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-03-17 07:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-17 08:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-03-17 09:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-03-17 10:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-17 11:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-17 12:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-03-17 13:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-17 14:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-17 15:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-03-17 16:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-03-17 17:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-03-17 18:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-17 19:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-03-17 20:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-03-17 21:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-17 22:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-03-17 23:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-03-18 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-03-18 01:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-18 02:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-18 03:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-03-18 04:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-03-18 05:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-03-18 06:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-03-18 07:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-03-18 08:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-03-18 09:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-03-18 10:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-03-18 11:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-18 12:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-18 13:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-03-18 14:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-03-18 15:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-03-18 16:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-03-18 17:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-03-18 18:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-18 19:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-03-18 20:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-18 21:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-18 22:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-03-18 23:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-03-19 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-03-19 01:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-03-19 02:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-03-19 03:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-03-19 04:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-03-19 05:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-03-19 06:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-03-19 07:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-03-19 08:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-03-19 09:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-03-19 10:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-03-19 11:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-03-19 12:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-19 13:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-03-19 14:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-03-19 15:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-03-19 16:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-03-19 17:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-03-19 18:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-19 19:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-03-19 20:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-03-19 21:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-19 22:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-03-19 23:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-03-20 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-03-20 01:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-03-20 02:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-03-20 03:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-03-20 04:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-03-20 05:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-03-20 06:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-03-20 07:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-03-20 08:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-03-20 09:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-20 10:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-03-20 11:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-03-20 12:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-03-20 13:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-03-20 14:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-20 15:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-03-20 16:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-03-20 17:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-20 18:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-20 19:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-03-20 20:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-03-20 21:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-20 22:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-03-20 23:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-03-21 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-03-21 01:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-21 02:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-03-21 03:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-03-21 04:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-03-21 05:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-03-21 06:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-03-21 07:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-03-21 08:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-03-21 09:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-03-21 10:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-03-21 11:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-21 12:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-21 13:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-03-21 14:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-03-21 15:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-03-21 16:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-03-21 17:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-21 18:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-03-21 19:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-03-21 20:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-21 21:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-03-21 22:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-03-21 23:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-03-22 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-03-22 01:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-03-22 02:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-03-22 03:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-03-22 04:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-03-22 05:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-03-22 06:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-22 07:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-03-22 08:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-03-22 09:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-22 10:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-22 11:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-03-22 12:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-03-22 13:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-03-22 14:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-03-22 15:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-22 16:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-03-22 17:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-22 18:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-03-22 19:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-03-22 20:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-03-22 21:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-22 22:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-22 23:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-03-23 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-03-23 01:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-03-23 02:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-03-23 03:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-23 04:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-23 05:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-03-23 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-03-23 07:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-03-23 08:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-23 09:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-23 10:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-03-23 11:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-03-23 12:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-03-23 13:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-23 14:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-03-23 15:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-23 16:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-23 17:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-03-23 18:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-03-23 19:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-03-23 20:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-03-23 21:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-03-23 22:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-03-23 23:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-24 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-03-24 01:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-03-24 02:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-03-24 03:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-03-24 04:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-03-24 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-03-24 06:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-03-24 07:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-03-24 08:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-03-24 09:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-24 10:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-03-24 11:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-03-24 12:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-24 13:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-03-24 14:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-03-24 15:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-03-24 16:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-03-24 17:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-03-24 18:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-03-24 19:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-03-24 20:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-03-24 21:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-03-24 22:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-03-24 23:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-03-25 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-03-25 01:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-25 02:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-03-25 03:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-03-25 04:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-03-25 05:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-03-25 06:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-03-25 07:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-03-25 08:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-03-25 09:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-03-25 10:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-25 11:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-03-25 12:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-25 13:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-25 14:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-03-25 15:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-03-25 16:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-03-25 17:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-03-25 18:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-03-25 19:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-03-25 20:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-03-25 21:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-03-25 22:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-03-25 23:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-03-26 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-03-26 01:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-03-26 02:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-26 03:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-03-26 04:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-26 05:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-03-26 06:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-03-26 07:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-03-26 08:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-03-26 09:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-03-26 10:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-26 11:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-26 12:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-03-26 13:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-03-26 14:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-03-26 15:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-26 16:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-03-26 17:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-03-26 18:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-03-26 19:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-03-26 20:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-03-26 21:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-03-26 22:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-03-26 23:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-03-27 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-03-27 01:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-03-27 02:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-03-27 03:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-27 04:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-03-27 05:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-03-27 06:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-03-27 07:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-03-27 08:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-03-27 09:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-03-27 10:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-27 11:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-03-27 12:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-03-27 13:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-03-27 14:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-03-27 15:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-03-27 16:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-03-27 17:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-03-27 18:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-03-27 19:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-27 20:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-03-27 21:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-03-27 22:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-03-27 23:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-03-28 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-03-28 01:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-03-28 02:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-03-28 03:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-03-28 04:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-03-28 05:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-03-28 06:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-03-28 07:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-03-28 08:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-03-28 09:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-03-28 10:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-28 11:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-03-28 12:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-03-28 13:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-03-28 14:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-03-28 15:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-03-28 16:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-03-28 17:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-03-28 18:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-03-28 19:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-03-28 20:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-03-28 21:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-03-28 22:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-03-28 23:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-03-29 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-03-29 01:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-03-29 02:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-29 03:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-03-29 04:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-03-29 05:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-03-29 06:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-03-29 07:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-03-29 08:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-03-29 09:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-03-29 10:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-29 11:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-03-29 12:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-03-29 13:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-03-29 14:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-03-29 15:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-03-29 16:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-03-29 17:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-03-29 18:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-03-29 19:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-03-29 20:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-03-29 21:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-03-29 22:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-03-29 23:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-03-30 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-03-30 01:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-03-30 02:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-03-30 03:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-30 04:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-03-30 05:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-03-30 06:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-03-30 07:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-03-30 08:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-03-30 09:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-03-30 10:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-03-30 11:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-03-30 12:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-03-30 13:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-03-30 14:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-03-30 15:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-03-30 16:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-03-30 17:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-03-30 18:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-03-30 19:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-03-30 20:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-03-30 21:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-03-30 22:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-03-30 23:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-03-31 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-03-31 01:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-03-31 02:00 | 3.673 | 0.007382% | 3.8461 | 4.0273 | 4.2171 | 4.4158 | 0 | 0 | 0 | 0
2025-03-31 03:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-03-31 04:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-03-31 05:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-03-31 06:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-03-31 07:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-03-31 08:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-03-31 09:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-03-31 10:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-03-31 11:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-03-31 12:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-03-31 13:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-03-31 14:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-03-31 15:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-03-31 16:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-03-31 17:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-03-31 18:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-03-31 19:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-03-31 20:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-03-31 21:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-03-31 22:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-03-31 23:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-04-01 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-04-01 01:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-04-01 02:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-04-01 03:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-04-01 04:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-01 05:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-04-01 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-04-01 07:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-04-01 08:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-04-01 09:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-04-01 10:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-01 11:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-01 12:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-04-01 13:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-04-01 14:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-04-01 15:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-01 16:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-04-01 17:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-04-01 18:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-04-01 19:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-04-01 20:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-04-01 21:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-04-01 22:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-04-01 23:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-02 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-04-02 01:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-04-02 02:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-04-02 03:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-04-02 04:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-04-02 05:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-04-02 06:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-04-02 07:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-04-02 08:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-02 09:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-04-02 10:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-04-02 11:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-04-02 12:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-04-02 13:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-04-02 14:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-04-02 15:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-04-02 16:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-04-02 17:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-04-02 18:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-04-02 19:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-04-02 20:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-04-02 21:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-04-02 22:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-04-02 23:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-04-03 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-04-03 01:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-04-03 02:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-04-03 03:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-04-03 04:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-04-03 05:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-03 06:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-04-03 07:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-04-03 08:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-03 09:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-04-03 10:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-04-03 11:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-03 12:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-03 13:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-03 14:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-04-03 15:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-04-03 16:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-03 17:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-04-03 18:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-04-03 19:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-04-03 20:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-04-03 21:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-03 22:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-03 23:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-04 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-04-04 01:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-04-04 02:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-04-04 03:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-04-04 04:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-04-04 05:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-04-04 06:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-04-04 07:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-04-04 08:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-04-04 09:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-04 10:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-04 11:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-04-04 12:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-04 13:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-04 14:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-04 15:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-04-04 16:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-04-04 17:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-04-04 18:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-04 19:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-04 20:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-04-04 21:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-04-04 22:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-04-04 23:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-04-05 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-04-05 01:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-04-05 02:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-04-05 03:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-04-05 04:00 | 3.5095 | 0.007054% | 3.6749 | 3.848 | 4.0293 | 4.2192 | 0 | 0 | 0 | 0
2025-04-05 05:00 | 3.4843 | 0.007003% | 3.6485 | 3.8204 | 4.0004 | 4.1889 | 0 | 0 | 0 | 0
2025-04-05 06:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-04-05 07:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-04-05 08:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-04-05 09:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-04-05 10:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-04-05 11:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-04-05 12:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-05 13:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-04-05 14:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-05 15:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-04-05 16:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-04-05 17:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-04-05 18:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-04-05 19:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-04-05 20:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-04-05 21:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-05 22:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-04-05 23:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-04-06 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-04-06 01:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-04-06 02:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-04-06 03:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-04-06 04:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-04-06 05:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-04-06 06:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-04-06 07:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-04-06 08:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-04-06 09:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-04-06 10:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-04-06 11:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-04-06 12:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-04-06 13:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-06 14:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-04-06 15:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-06 16:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-06 17:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-04-06 18:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-04-06 19:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-04-06 20:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-04-06 21:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-04-06 22:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-06 23:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-04-07 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-04-07 01:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-04-07 02:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-04-07 03:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-07 04:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-04-07 05:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-04-07 06:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-04-07 07:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-07 08:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-07 09:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-04-07 10:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-04-07 11:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-04-07 12:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-04-07 13:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-04-07 14:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-04-07 15:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-04-07 16:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-04-07 17:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-04-07 18:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-04-07 19:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-04-07 20:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-04-07 21:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-04-07 22:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-04-07 23:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-08 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-08 01:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-08 02:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-04-08 03:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-04-08 04:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-04-08 05:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-04-08 06:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-04-08 07:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-04-08 08:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-04-08 09:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-04-08 10:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-04-08 11:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-04-08 12:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-04-08 13:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-04-08 14:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-04-08 15:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-04-08 16:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-04-08 17:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-04-08 18:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-04-08 19:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-04-08 20:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-04-08 21:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-04-08 22:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-04-08 23:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-04-09 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-04-09 01:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-09 02:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-04-09 03:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-04-09 04:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-04-09 05:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-04-09 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-04-09 07:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-04-09 08:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-09 09:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-04-09 10:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-04-09 11:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-04-09 12:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-04-09 13:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-04-09 14:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-04-09 15:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-09 16:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-04-09 17:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-04-09 18:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-04-09 19:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-04-09 20:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-04-09 21:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-04-09 22:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-04-09 23:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-04-10 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-04-10 01:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-04-10 02:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-10 03:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-04-10 04:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-10 05:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-04-10 06:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-04-10 07:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-04-10 08:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-04-10 09:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-04-10 10:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-04-10 11:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-04-10 12:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-04-10 13:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-04-10 14:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-10 15:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-04-10 16:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-04-10 17:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-04-10 18:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-04-10 19:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-04-10 20:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-04-10 21:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-04-10 22:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-04-10 23:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-04-11 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-04-11 01:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-04-11 02:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-11 03:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-04-11 04:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-04-11 05:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-11 06:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-04-11 07:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-11 08:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-04-11 09:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-04-11 10:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-04-11 11:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-04-11 12:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-04-11 13:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-04-11 14:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-04-11 15:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-04-11 16:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-04-11 17:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-04-11 18:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-04-11 19:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-04-11 20:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-04-11 21:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-04-11 22:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-04-11 23:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-04-12 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-12 01:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-04-12 02:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-04-12 03:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-04-12 04:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-04-12 05:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-04-12 06:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-04-12 07:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-12 08:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-04-12 09:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-04-12 10:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-04-12 11:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-12 12:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-04-12 13:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-04-12 14:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-04-12 15:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-04-12 16:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-04-12 17:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-04-12 18:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-04-12 19:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-04-12 20:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-04-12 21:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-04-12 22:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-12 23:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-04-13 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-04-13 01:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-04-13 02:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-04-13 03:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-04-13 04:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-13 05:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-13 06:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-04-13 07:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-04-13 08:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-04-13 09:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-04-13 10:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-13 11:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-13 12:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-04-13 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-04-13 14:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-13 15:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-04-13 16:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-04-13 17:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-04-13 18:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-04-13 19:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-04-13 20:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-13 21:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-13 22:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-04-13 23:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-04-14 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-04-14 01:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-04-14 02:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-04-14 03:00 | 3.4843 | 0.007003% | 3.6485 | 3.8204 | 4.0004 | 4.1889 | 0 | 0 | 0 | 0
2025-04-14 04:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-04-14 05:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-04-14 06:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-14 07:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-04-14 08:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-04-14 09:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-04-14 10:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-14 11:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-14 12:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-14 13:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-14 14:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-04-14 15:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-04-14 16:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-14 17:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-04-14 18:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-04-14 19:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-14 20:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-14 21:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-14 22:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-14 23:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-04-15 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-04-15 01:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-04-15 02:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-04-15 03:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-04-15 04:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-04-15 05:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-04-15 06:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-04-15 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-04-15 08:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-04-15 09:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-04-15 10:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-15 11:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-04-15 12:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-04-15 13:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-15 14:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-04-15 15:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-15 16:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-15 17:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-04-15 18:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-04-15 19:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-04-15 20:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-04-15 21:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-04-15 22:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-04-15 23:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-04-16 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-04-16 01:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-04-16 02:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-04-16 03:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-04-16 04:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-04-16 05:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-04-16 06:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-04-16 07:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-04-16 08:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-04-16 09:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-16 10:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-16 11:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-04-16 12:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-04-16 13:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-04-16 14:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-04-16 15:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-16 16:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-04-16 17:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-04-16 18:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-04-16 19:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-04-16 20:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-04-16 21:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-04-16 22:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-04-16 23:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-04-17 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-17 01:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-04-17 02:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-04-17 03:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-04-17 04:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-04-17 05:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-04-17 06:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-04-17 07:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-17 08:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-17 09:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-04-17 10:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-04-17 11:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-04-17 12:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-17 13:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-04-17 14:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-04-17 15:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-04-17 16:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-17 17:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-17 18:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-04-17 19:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-04-17 20:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-17 21:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-04-17 22:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-04-17 23:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-04-18 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-04-18 01:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-04-18 02:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-04-18 03:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-04-18 04:00 | 3.673 | 0.007382% | 3.8461 | 4.0273 | 4.2171 | 4.4158 | 0 | 0 | 0 | 0
2025-04-18 05:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-04-18 06:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-04-18 07:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-18 08:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-04-18 09:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-04-18 10:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-18 11:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-04-18 12:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-04-18 13:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-04-18 14:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-04-18 15:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-04-18 16:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-04-18 17:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-18 18:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-18 19:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-04-18 20:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-04-18 21:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-18 22:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-04-18 23:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-19 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-04-19 01:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-04-19 02:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-04-19 03:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-04-19 04:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-04-19 05:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-04-19 06:00 | 3.195 | 0.006422% | 3.3456 | 3.5032 | 3.6683 | 3.8411 | 0 | 0 | 0 | 0
2025-04-19 07:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-04-19 08:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-04-19 09:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-19 10:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-04-19 11:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-04-19 12:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-04-19 13:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-19 14:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-04-19 15:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-19 16:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-19 17:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-04-19 18:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-04-19 19:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-19 20:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-19 21:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-19 22:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-04-19 23:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-04-20 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-04-20 01:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-20 02:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-04-20 03:00 | 3.4718 | 0.006978% | 3.6353 | 3.8066 | 3.986 | 4.1738 | 0 | 0 | 0 | 0
2025-04-20 04:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-04-20 05:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-04-20 06:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-04-20 07:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-04-20 08:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-20 09:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-04-20 10:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-04-20 11:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-04-20 12:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-04-20 13:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-04-20 14:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-20 15:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-20 16:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-04-20 17:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-04-20 18:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-20 19:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-04-20 20:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-04-20 21:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-20 22:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-04-20 23:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-21 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-04-21 01:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-04-21 02:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-04-21 03:00 | 3.4466 | 0.006927% | 3.609 | 3.779 | 3.9571 | 4.1436 | 0 | 0 | 0 | 0
2025-04-21 04:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-04-21 05:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-04-21 06:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-04-21 07:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-04-21 08:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-04-21 09:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-04-21 10:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-21 11:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-04-21 12:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-04-21 13:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-04-21 14:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-04-21 15:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-04-21 16:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-04-21 17:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-04-21 18:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-04-21 19:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-04-21 20:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-04-21 21:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-04-21 22:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-04-21 23:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-04-22 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-04-22 01:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-04-22 02:00 | 3.4718 | 0.006978% | 3.6353 | 3.8066 | 3.986 | 4.1738 | 0 | 0 | 0 | 0
2025-04-22 03:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-04-22 04:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-04-22 05:00 | 3.3334 | 0.0067% | 3.4905 | 3.6549 | 3.8271 | 4.0075 | 0 | 0 | 0 | 0
2025-04-22 06:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-04-22 07:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-04-22 08:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-04-22 09:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-04-22 10:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-22 11:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-04-22 12:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-22 13:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-04-22 14:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-04-22 15:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-22 16:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-04-22 17:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-04-22 18:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-04-22 19:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-04-22 20:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-04-22 21:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-04-22 22:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-04-22 23:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-23 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-04-23 01:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-23 02:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-04-23 03:00 | 3.3837 | 0.006801% | 3.5431 | 3.7101 | 3.8849 | 4.0679 | 0 | 0 | 0 | 0
2025-04-23 04:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-04-23 05:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-04-23 06:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-23 07:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-04-23 08:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-23 09:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-04-23 10:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-04-23 11:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-04-23 12:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-04-23 13:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-23 14:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-04-23 15:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-04-23 16:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-04-23 17:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-04-23 18:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-04-23 19:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-04-23 20:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-04-23 21:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-23 22:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-04-23 23:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-04-24 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-04-24 01:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-04-24 02:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-04-24 03:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-04-24 04:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-04-24 05:00 | 3.195 | 0.006422% | 3.3456 | 3.5032 | 3.6683 | 3.8411 | 0 | 0 | 0 | 0
2025-04-24 06:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-04-24 07:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-04-24 08:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-04-24 09:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-04-24 10:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-24 11:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-04-24 12:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-04-24 13:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-24 14:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-04-24 15:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-24 16:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-04-24 17:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-24 18:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-24 19:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-04-24 20:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-04-24 21:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-04-24 22:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-24 23:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-04-25 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-04-25 01:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-04-25 02:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-04-25 03:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-04-25 04:00 | 2.9686 | 0.005966% | 3.1085 | 3.2549 | 3.4083 | 3.5689 | 0 | 0 | 0 | 0
2025-04-25 05:00 | 3.0315 | 0.006093% | 3.1743 | 3.3239 | 3.4805 | 3.6445 | 0 | 0 | 0 | 0
2025-04-25 06:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-04-25 07:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-04-25 08:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-04-25 09:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-25 10:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-25 11:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-04-25 12:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-04-25 13:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-25 14:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-04-25 15:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-25 16:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-25 17:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-25 18:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-25 19:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-25 20:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-04-25 21:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-04-25 22:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-04-25 23:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-04-26 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-04-26 01:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-04-26 02:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-04-26 03:00 | 3.1195 | 0.00627% | 3.2665 | 3.4204 | 3.5816 | 3.7504 | 0 | 0 | 0 | 0
2025-04-26 04:00 | 2.9812 | 0.005992% | 3.1216 | 3.2687 | 3.4228 | 3.584 | 0 | 0 | 0 | 0
2025-04-26 05:00 | 2.9686 | 0.005966% | 3.1085 | 3.2549 | 3.4083 | 3.5689 | 0 | 0 | 0 | 0
2025-04-26 06:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-04-26 07:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-04-26 08:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-04-26 09:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-04-26 10:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-04-26 11:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-04-26 12:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-04-26 13:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-04-26 14:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-04-26 15:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-04-26 16:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-04-26 17:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-04-26 18:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-26 19:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-26 20:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-04-26 21:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-04-26 22:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-04-26 23:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-04-27 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-04-27 01:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-04-27 02:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-04-27 03:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-04-27 04:00 | 3.2579 | 0.006548% | 3.4114 | 3.5722 | 3.7405 | 3.9167 | 0 | 0 | 0 | 0
2025-04-27 05:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-04-27 06:00 | 3.3963 | 0.006826% | 3.5563 | 3.7239 | 3.8993 | 4.0831 | 0 | 0 | 0 | 0
2025-04-27 07:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-04-27 08:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-04-27 09:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-04-27 10:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-04-27 11:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-04-27 12:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-04-27 13:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-04-27 14:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-27 15:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-04-27 16:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-04-27 17:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-04-27 18:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-04-27 19:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-04-27 20:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-04-27 21:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-27 22:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-04-27 23:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-28 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-04-28 01:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-04-28 02:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-04-28 03:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-04-28 04:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-04-28 05:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-04-28 06:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-04-28 07:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-04-28 08:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-04-28 09:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-04-28 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-04-28 11:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-04-28 12:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-28 13:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-04-28 14:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-04-28 15:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-04-28 16:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-04-28 17:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-04-28 18:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-04-28 19:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-04-28 20:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-04-28 21:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-04-28 22:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-04-28 23:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-04-29 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-04-29 01:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-04-29 02:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-04-29 03:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-04-29 04:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-04-29 05:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-04-29 06:00 | 3.3963 | 0.006826% | 3.5563 | 3.7239 | 3.8993 | 4.0831 | 0 | 0 | 0 | 0
2025-04-29 07:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-04-29 08:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-04-29 09:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-04-29 10:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-04-29 11:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-04-29 12:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-04-29 13:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-04-29 14:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-04-29 15:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-04-29 16:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-29 17:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-04-29 18:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-29 19:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-04-29 20:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-04-29 21:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-29 22:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-04-29 23:00 | 2.5283 | 0.005082% | 2.6475 | 2.7722 | 2.9028 | 3.0396 | 0 | 0 | 0 | 0
2025-04-30 | 2.1761 | 0.004374% | 2.2787 | 2.386 | 2.4985 | 2.6162 | 0 | 0 | 0 | 0
2025-04-30 01:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-04-30 02:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-04-30 03:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-04-30 04:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-04-30 05:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-04-30 06:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-04-30 07:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-04-30 08:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-04-30 09:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-30 10:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-04-30 11:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-04-30 12:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-04-30 13:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-04-30 14:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-04-30 15:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-04-30 16:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-04-30 17:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-04-30 18:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-30 19:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-04-30 20:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-04-30 21:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-04-30 22:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-04-30 23:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-01 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-01 01:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-05-01 02:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-05-01 03:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-05-01 04:00 | 3.2076 | 0.006447% | 3.3587 | 3.517 | 3.6827 | 3.8562 | 0 | 0 | 0 | 0
2025-05-01 05:00 | 3.2076 | 0.006447% | 3.3587 | 3.517 | 3.6827 | 3.8562 | 0 | 0 | 0 | 0
2025-05-01 06:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-05-01 07:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-05-01 08:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-01 09:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-05-01 10:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-01 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-01 12:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-01 13:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-05-01 14:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-05-01 15:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-01 16:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-05-01 17:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-05-01 18:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-01 19:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-05-01 20:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-05-01 21:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-05-01 22:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-05-01 23:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-02 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-02 01:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-05-02 02:00 | 3.5095 | 0.007054% | 3.6749 | 3.848 | 4.0293 | 4.2192 | 0 | 0 | 0 | 0
2025-05-02 03:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-05-02 04:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-02 05:00 | 3.1195 | 0.00627% | 3.2665 | 3.4204 | 3.5816 | 3.7504 | 0 | 0 | 0 | 0
2025-05-02 06:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-05-02 07:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-05-02 08:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-02 09:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-05-02 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-02 11:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-02 12:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-02 13:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-02 14:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-02 15:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-02 16:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-02 17:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-02 18:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-02 19:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-02 20:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-02 21:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-02 22:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-02 23:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-03 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-05-03 01:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-05-03 02:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-05-03 03:00 | 3.0692 | 0.006169% | 3.2138 | 3.3653 | 3.5238 | 3.6899 | 0 | 0 | 0 | 0
2025-05-03 04:00 | 3.0315 | 0.006093% | 3.1743 | 3.3239 | 3.4805 | 3.6445 | 0 | 0 | 0 | 0
2025-05-03 05:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-03 06:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-05-03 07:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-03 08:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-05-03 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-03 10:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-05-03 11:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-03 12:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-03 13:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-03 14:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-03 15:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-05-03 16:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-03 17:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-05-03 18:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-05-03 19:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-03 20:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-03 21:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-05-03 22:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-03 23:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-05-04 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-04 01:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-05-04 02:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-05-04 03:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-05-04 04:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-04 05:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-04 06:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-04 07:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-05-04 08:00 | 3.673 | 0.007382% | 3.8461 | 4.0273 | 4.2171 | 4.4158 | 0 | 0 | 0 | 0
2025-05-04 09:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-05-04 10:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-04 11:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-05-04 12:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-05-04 13:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-04 14:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-04 15:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-05-04 16:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-04 17:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-05-04 18:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-05-04 19:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-05-04 20:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-05-04 21:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-04 22:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-04 23:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-05 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-05-05 01:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-05-05 02:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-05-05 03:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-05 04:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-05 05:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-05 06:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-05-05 07:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-05-05 08:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-05-05 09:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-05 10:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-05-05 11:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-05-05 12:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-05 13:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-05-05 14:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-05 15:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-05 16:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-05-05 17:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-05-05 18:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-05-05 19:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-05-05 20:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-05-05 21:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-05-05 22:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-05-05 23:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-06 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-05-06 01:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-05-06 02:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-06 03:00 | 3.0315 | 0.006093% | 3.1743 | 3.3239 | 3.4805 | 3.6445 | 0 | 0 | 0 | 0
2025-05-06 04:00 | 2.8931 | 0.005815% | 3.0294 | 3.1722 | 3.3217 | 3.4782 | 0 | 0 | 0 | 0
2025-05-06 05:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-05-06 06:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-06 07:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-05-06 08:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-05-06 09:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-05-06 10:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-06 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-06 12:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-05-06 13:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-06 14:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-06 15:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-06 16:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-06 17:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-06 18:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-05-06 19:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-06 20:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-05-06 21:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-05-06 22:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-05-06 23:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-07 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-05-07 01:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-05-07 02:00 | 3.0818 | 0.006194% | 3.227 | 3.3791 | 3.5383 | 3.705 | 0 | 0 | 0 | 0
2025-05-07 03:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-07 04:00 | 2.868 | 0.005764% | 3.0031 | 3.1446 | 3.2928 | 3.4479 | 0 | 0 | 0 | 0
2025-05-07 05:00 | 2.9057 | 0.00584% | 3.0426 | 3.186 | 3.3361 | 3.4933 | 0 | 0 | 0 | 0
2025-05-07 06:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-05-07 07:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-05-07 08:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-05-07 09:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-07 10:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-07 11:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-05-07 12:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-07 13:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-07 14:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-07 15:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-07 16:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-07 17:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-07 18:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-05-07 19:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-05-07 20:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-05-07 21:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-05-07 22:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-05-07 23:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-08 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-05-08 01:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-05-08 02:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-05-08 03:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-08 04:00 | 2.9434 | 0.005916% | 3.0821 | 3.2274 | 3.3794 | 3.5387 | 0 | 0 | 0 | 0
2025-05-08 05:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-08 06:00 | 3.2076 | 0.006447% | 3.3587 | 3.517 | 3.6827 | 3.8562 | 0 | 0 | 0 | 0
2025-05-08 07:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-05-08 08:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-05-08 09:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-08 10:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-08 11:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-08 12:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-08 13:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-08 14:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-08 15:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-08 16:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-08 17:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-08 18:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-05-08 19:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-05-08 20:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-05-08 21:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-05-08 22:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-05-08 23:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-09 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-05-09 01:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-05-09 02:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-05-09 03:00 | 3.2076 | 0.006447% | 3.3587 | 3.517 | 3.6827 | 3.8562 | 0 | 0 | 0 | 0
2025-05-09 04:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-05-09 05:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-05-09 06:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-05-09 07:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-05-09 08:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-09 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-09 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-09 11:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-05-09 12:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-09 13:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-09 14:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-09 15:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-05-09 16:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-09 17:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-05-09 18:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-09 19:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-09 20:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-09 21:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-09 22:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-09 23:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-10 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-10 01:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-05-10 02:00 | 3.5095 | 0.007054% | 3.6749 | 3.848 | 4.0293 | 4.2192 | 0 | 0 | 0 | 0
2025-05-10 03:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-05-10 04:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-10 05:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-10 06:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-05-10 07:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-05-10 08:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-05-10 09:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-10 10:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-05-10 11:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-05-10 12:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-05-10 13:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-05-10 14:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-10 15:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-05-10 16:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-05-10 17:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-05-10 18:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-10 19:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-10 20:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-10 21:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-05-10 22:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-10 23:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-11 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-05-11 01:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-05-11 02:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-05-11 03:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-11 04:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-05-11 05:00 | 2.868 | 0.005764% | 3.0031 | 3.1446 | 3.2928 | 3.4479 | 0 | 0 | 0 | 0
2025-05-11 06:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-11 07:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-11 08:00 | 3.4843 | 0.007003% | 3.6485 | 3.8204 | 4.0004 | 4.1889 | 0 | 0 | 0 | 0
2025-05-11 09:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-05-11 10:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-05-11 11:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-05-11 12:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-05-11 13:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-05-11 14:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-11 15:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-05-11 16:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-11 17:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-11 18:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-11 19:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-11 20:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-05-11 21:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-11 22:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-11 23:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-12 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-05-12 01:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-05-12 02:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-05-12 03:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-05-12 04:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-12 05:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-12 06:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-05-12 07:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-05-12 08:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-05-12 09:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-05-12 10:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-12 11:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-05-12 12:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-12 13:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-12 14:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-05-12 15:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-12 16:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-12 17:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-12 18:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-05-12 19:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-05-12 20:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-05-12 21:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-05-12 22:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-05-12 23:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-13 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-05-13 01:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-05-13 02:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-13 03:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-13 04:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-13 05:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-05-13 06:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-05-13 07:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-05-13 08:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-05-13 09:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-13 10:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-13 11:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-05-13 12:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-13 13:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-13 14:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-13 15:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-13 16:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-05-13 17:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-05-13 18:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-13 19:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-13 20:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-05-13 21:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-05-13 22:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-05-13 23:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-14 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-05-14 01:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-05-14 02:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-14 03:00 | 3.0818 | 0.006194% | 3.227 | 3.3791 | 3.5383 | 3.705 | 0 | 0 | 0 | 0
2025-05-14 04:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-14 05:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-14 06:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-05-14 07:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-05-14 08:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-05-14 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-14 10:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-05-14 11:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-14 12:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-14 13:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-14 14:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-14 15:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-14 16:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-14 17:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-05-14 18:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-05-14 19:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-05-14 20:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-05-14 21:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-05-14 22:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-05-14 23:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-15 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-05-15 01:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-05-15 02:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-05-15 03:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-15 04:00 | 2.9057 | 0.00584% | 3.0426 | 3.186 | 3.3361 | 3.4933 | 0 | 0 | 0 | 0
2025-05-15 05:00 | 2.8805 | 0.00579% | 3.0163 | 3.1584 | 3.3072 | 3.463 | 0 | 0 | 0 | 0
2025-05-15 06:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-15 07:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-05-15 08:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-05-15 09:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-05-15 10:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-05-15 11:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-15 12:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-15 13:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-15 14:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-15 15:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-05-15 16:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-15 17:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-05-15 18:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-05-15 19:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-05-15 20:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-15 21:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-05-15 22:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-05-15 23:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-16 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-05-16 01:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-05-16 02:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-05-16 03:00 | 3.0567 | 0.006143% | 3.2007 | 3.3515 | 3.5094 | 3.6748 | 0 | 0 | 0 | 0
2025-05-16 04:00 | 2.9812 | 0.005992% | 3.1216 | 3.2687 | 3.4228 | 3.584 | 0 | 0 | 0 | 0
2025-05-16 05:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-16 06:00 | 3.0818 | 0.006194% | 3.227 | 3.3791 | 3.5383 | 3.705 | 0 | 0 | 0 | 0
2025-05-16 07:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-05-16 08:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-05-16 09:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-05-16 10:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-16 11:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-05-16 12:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-05-16 13:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-05-16 14:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-05-16 15:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-05-16 16:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-05-16 17:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-05-16 18:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-05-16 19:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-05-16 20:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-05-16 21:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-05-16 22:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-16 23:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-05-17 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-17 01:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-05-17 02:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-05-17 03:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-05-17 04:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-05-17 05:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-17 06:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-17 07:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-17 08:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-05-17 09:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-05-17 10:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-17 11:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-05-17 12:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-17 13:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-05-17 14:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-17 15:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-17 16:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-17 17:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-17 18:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-17 19:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-17 20:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-17 21:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-05-17 22:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-05-17 23:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-05-18 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-05-18 01:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-05-18 02:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-05-18 03:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-18 04:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-18 05:00 | 2.8805 | 0.00579% | 3.0163 | 3.1584 | 3.3072 | 3.463 | 0 | 0 | 0 | 0
2025-05-18 06:00 | 2.8554 | 0.005739% | 2.9899 | 3.1308 | 3.2783 | 3.4328 | 0 | 0 | 0 | 0
2025-05-18 07:00 | 3.0189 | 0.006068% | 3.1612 | 3.3101 | 3.4661 | 3.6294 | 0 | 0 | 0 | 0
2025-05-18 08:00 | 3.3334 | 0.0067% | 3.4905 | 3.6549 | 3.8271 | 4.0075 | 0 | 0 | 0 | 0
2025-05-18 09:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-05-18 10:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-05-18 11:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-05-18 12:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-18 13:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-05-18 14:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-05-18 15:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-05-18 16:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-18 17:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-18 18:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-18 19:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-18 20:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-18 21:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-18 22:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-05-18 23:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-05-19 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-05-19 01:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-05-19 02:00 | 3.3334 | 0.0067% | 3.4905 | 3.6549 | 3.8271 | 4.0075 | 0 | 0 | 0 | 0
2025-05-19 03:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-05-19 04:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-19 05:00 | 2.9812 | 0.005992% | 3.1216 | 3.2687 | 3.4228 | 3.584 | 0 | 0 | 0 | 0
2025-05-19 06:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-05-19 07:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-05-19 08:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-05-19 09:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-05-19 10:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-05-19 11:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-05-19 12:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-05-19 13:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-19 14:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-19 15:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-19 16:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-19 17:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-05-19 18:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-05-19 19:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-05-19 20:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-05-19 21:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-05-19 22:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-19 23:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-20 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-05-20 01:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-05-20 02:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-05-20 03:00 | 3.1195 | 0.00627% | 3.2665 | 3.4204 | 3.5816 | 3.7504 | 0 | 0 | 0 | 0
2025-05-20 04:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-05-20 05:00 | 3.1447 | 0.00632% | 3.2929 | 3.448 | 3.6105 | 3.7806 | 0 | 0 | 0 | 0
2025-05-20 06:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-05-20 07:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-05-20 08:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-20 09:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-20 10:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-20 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-20 12:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-20 13:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-20 14:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-20 15:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-05-20 16:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-20 17:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-20 18:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-05-20 19:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-05-20 20:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-20 21:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-05-20 22:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-20 23:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-21 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-05-21 01:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-05-21 02:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-05-21 03:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-21 04:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-21 05:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-05-21 06:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-21 07:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-05-21 08:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-21 09:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-05-21 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-21 11:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-05-21 12:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-21 13:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-21 14:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-05-21 15:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-05-21 16:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-21 17:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-05-21 18:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-21 19:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-05-21 20:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-05-21 21:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-05-21 22:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-05-21 23:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-22 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-22 01:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-05-22 02:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-05-22 03:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-22 04:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-22 05:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-22 06:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-05-22 07:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-05-22 08:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-22 09:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-22 10:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-22 11:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-05-22 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-05-22 13:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-05-22 14:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-05-22 15:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-05-22 16:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-22 17:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-05-22 18:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-05-22 19:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-05-22 20:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-05-22 21:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-05-22 22:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-05-22 23:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-23 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-05-23 01:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-05-23 02:00 | 3.4843 | 0.007003% | 3.6485 | 3.8204 | 4.0004 | 4.1889 | 0 | 0 | 0 | 0
2025-05-23 03:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-05-23 04:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-05-23 05:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-23 06:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-05-23 07:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-05-23 08:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-05-23 09:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-23 10:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-05-23 11:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-23 12:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-23 13:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-23 14:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-05-23 15:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-23 16:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-23 17:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-05-23 18:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-05-23 19:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-05-23 20:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-05-23 21:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-05-23 22:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-05-23 23:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-24 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-05-24 01:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-05-24 02:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-05-24 03:00 | 3.3837 | 0.006801% | 3.5431 | 3.7101 | 3.8849 | 4.0679 | 0 | 0 | 0 | 0
2025-05-24 04:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-05-24 05:00 | 3.195 | 0.006422% | 3.3456 | 3.5032 | 3.6683 | 3.8411 | 0 | 0 | 0 | 0
2025-05-24 06:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-24 07:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-05-24 08:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-05-24 09:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-05-24 10:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-24 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-24 12:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-24 13:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-24 14:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-24 15:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-24 16:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-24 17:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-24 18:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-24 19:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-05-24 20:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-05-24 21:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-24 22:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-05-24 23:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-25 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-05-25 01:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-05-25 02:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-05-25 03:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-05-25 04:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-25 05:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-05-25 06:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-25 07:00 | 3.3334 | 0.0067% | 3.4905 | 3.6549 | 3.8271 | 4.0075 | 0 | 0 | 0 | 0
2025-05-25 08:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-05-25 09:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-05-25 10:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-05-25 11:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-25 12:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-25 13:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-05-25 14:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-25 15:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-05-25 16:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-05-25 17:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-05-25 18:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-05-25 19:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-05-25 20:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-05-25 21:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-05-25 22:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-05-25 23:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-26 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-05-26 01:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-05-26 02:00 | 3.2579 | 0.006548% | 3.4114 | 3.5722 | 3.7405 | 3.9167 | 0 | 0 | 0 | 0
2025-05-26 03:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-26 04:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-05-26 05:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-05-26 06:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-05-26 07:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-05-26 08:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-05-26 09:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-05-26 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-05-26 11:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-05-26 12:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-05-26 13:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-26 14:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-26 15:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-05-26 16:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-26 17:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-05-26 18:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-05-26 19:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-05-26 20:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-05-26 21:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-05-26 22:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-26 23:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-05-27 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-05-27 01:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-05-27 02:00 | 3.195 | 0.006422% | 3.3456 | 3.5032 | 3.6683 | 3.8411 | 0 | 0 | 0 | 0
2025-05-27 03:00 | 3.0692 | 0.006169% | 3.2138 | 3.3653 | 3.5238 | 3.6899 | 0 | 0 | 0 | 0
2025-05-27 04:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-27 05:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-27 06:00 | 3.195 | 0.006422% | 3.3456 | 3.5032 | 3.6683 | 3.8411 | 0 | 0 | 0 | 0
2025-05-27 07:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-05-27 08:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-05-27 09:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-05-27 10:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-05-27 11:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-05-27 12:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-05-27 13:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-27 14:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-05-27 15:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-05-27 16:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-05-27 17:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-05-27 18:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-05-27 19:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-05-27 20:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-05-27 21:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-05-27 22:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-05-27 23:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-28 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-05-28 01:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-05-28 02:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-05-28 03:00 | 3.0189 | 0.006068% | 3.1612 | 3.3101 | 3.4661 | 3.6294 | 0 | 0 | 0 | 0
2025-05-28 04:00 | 2.9686 | 0.005966% | 3.1085 | 3.2549 | 3.4083 | 3.5689 | 0 | 0 | 0 | 0
2025-05-28 05:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-28 06:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-05-28 07:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-05-28 08:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-05-28 09:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-28 10:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-05-28 11:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-05-28 12:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-05-28 13:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-05-28 14:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-28 15:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-05-28 16:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-05-28 17:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-05-28 18:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-05-28 19:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-05-28 20:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-05-28 21:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-05-28 22:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-05-28 23:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-29 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-05-29 01:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-05-29 02:00 | 3.2076 | 0.006447% | 3.3587 | 3.517 | 3.6827 | 3.8562 | 0 | 0 | 0 | 0
2025-05-29 03:00 | 3.0063 | 0.006042% | 3.148 | 3.2963 | 3.4516 | 3.6143 | 0 | 0 | 0 | 0
2025-05-29 04:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-29 05:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-05-29 06:00 | 3.1195 | 0.00627% | 3.2665 | 3.4204 | 3.5816 | 3.7504 | 0 | 0 | 0 | 0
2025-05-29 07:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-05-29 08:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-05-29 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-05-29 10:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-05-29 11:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-05-29 12:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-05-29 13:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-05-29 14:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-05-29 15:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-29 16:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-05-29 17:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-05-29 18:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-05-29 19:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-05-29 20:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-05-29 21:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-05-29 22:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-05-29 23:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-05-30 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-05-30 01:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-05-30 02:00 | 3.2579 | 0.006548% | 3.4114 | 3.5722 | 3.7405 | 3.9167 | 0 | 0 | 0 | 0
2025-05-30 03:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-05-30 04:00 | 2.9812 | 0.005992% | 3.1216 | 3.2687 | 3.4228 | 3.584 | 0 | 0 | 0 | 0
2025-05-30 05:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-05-30 06:00 | 3.0692 | 0.006169% | 3.2138 | 3.3653 | 3.5238 | 3.6899 | 0 | 0 | 0 | 0
2025-05-30 07:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-05-30 08:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-05-30 09:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-05-30 10:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-30 11:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-05-30 12:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-05-30 13:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-05-30 14:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-05-30 15:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-05-30 16:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-05-30 17:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-05-30 18:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-05-30 19:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-05-30 20:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-05-30 21:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-05-30 22:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-05-30 23:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-05-31 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-05-31 01:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-05-31 02:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-05-31 03:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-05-31 04:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-05-31 05:00 | 2.9434 | 0.005916% | 3.0821 | 3.2274 | 3.3794 | 3.5387 | 0 | 0 | 0 | 0
2025-05-31 06:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-05-31 07:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-05-31 08:00 | 3.4843 | 0.007003% | 3.6485 | 3.8204 | 4.0004 | 4.1889 | 0 | 0 | 0 | 0
2025-05-31 09:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-05-31 10:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-05-31 11:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-05-31 12:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-05-31 13:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-05-31 14:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-05-31 15:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-31 16:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-05-31 17:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-05-31 18:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-05-31 19:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-05-31 20:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-05-31 21:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-31 22:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-05-31 23:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-06-01 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-06-01 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-01 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-02 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-03 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-04 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-05 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-06 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-07 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-08 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-09 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-10 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-11 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-12 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-13 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-14 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-15 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-16 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-17 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-18 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-19 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-20 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-21 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-22 09:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-06-22 10:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-06-22 11:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-06-22 12:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-06-22 13:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-06-22 14:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-06-22 15:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-06-22 16:00 | 8.214 | 0.01651% | 8.601 | 9.0063 | 9.4306 | 9.875 | 0 | 0 | 0 | 0
2025-06-22 17:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-06-22 18:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-06-22 19:00 | 9.648 | 0.01939% | 10.1025 | 10.5786 | 11.077 | 11.5989 | 0 | 0 | 0 | 0.39331
2025-06-22 20:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2025-06-22 21:00 | 10.1259 | 0.02035% | 10.6031 | 11.1027 | 11.6258 | 12.1736 | 0 | 0 | 0.4164 | 0.88723
2025-06-22 22:00 | 10.6668 | 0.02144% | 11.1694 | 11.6957 | 12.2468 | 12.8239 | 0.024151 | 0.4765 | 0.95016 | 1.4461
2025-06-22 23:00 | 10.5662 | 0.02124% | 11.0641 | 11.5854 | 12.1313 | 12.7029 | 0 | 0.38166 | 0.85085 | 1.3422
2025-06-23 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2025-06-23 01:00 | 9.6983 | 0.01949% | 10.1552 | 10.6337 | 11.1348 | 11.6594 | 0 | 0 | 0 | 0.4453
2025-06-23 02:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-06-23 03:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-06-23 04:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-06-23 05:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-06-23 06:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-06-23 07:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-06-23 08:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-06-23 09:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-06-23 10:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-06-23 11:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-06-23 12:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-06-23 13:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-06-23 14:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-06-23 15:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-06-23 16:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-06-23 17:00 | 9.6228 | 0.01934% | 10.0762 | 10.551 | 11.0481 | 11.5687 | 0 | 0 | 0 | 0.36732
2025-06-23 18:00 | 9.9121 | 0.01992% | 10.3792 | 10.8682 | 11.3803 | 11.9165 | 0 | 0 | 0.20538 | 0.66627
2025-06-23 19:00 | 10.0631 | 0.02023% | 10.5372 | 11.0337 | 11.5536 | 12.098 | 0 | 0 | 0.35434 | 0.82224
2025-06-23 20:00 | 10.5914 | 0.02129% | 11.0904 | 11.613 | 12.1602 | 12.7331 | 0 | 0.40537 | 0.87568 | 1.3681
2025-06-23 21:00 | 10.931 | 0.02197% | 11.446 | 11.9854 | 12.5501 | 13.1414 | 0.26189 | 0.72544 | 1.2108 | 1.7191
2025-06-23 22:00 | 10.931 | 0.02197% | 11.446 | 11.9854 | 12.5501 | 13.1414 | 0.26189 | 0.72544 | 1.2108 | 1.7191
2025-06-23 23:00 | 10.931 | 0.02197% | 11.446 | 11.9854 | 12.5501 | 13.1414 | 0.26189 | 0.72544 | 1.2108 | 1.7191
2025-06-24 | 10.6039 | 0.02131% | 11.1036 | 11.6268 | 12.1746 | 12.7483 | 0 | 0.41723 | 0.88809 | 1.3811
2025-06-24 01:00 | 9.9498 | 0.02% | 10.4187 | 10.9096 | 11.4236 | 11.9619 | 0 | 0 | 0.24262 | 0.70526
2025-06-24 02:00 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2025-06-24 03:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2025-06-24 04:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-06-24 05:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-06-24 06:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-06-24 07:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-06-24 08:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-06-24 09:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-06-24 10:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-06-24 11:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-06-24 12:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-06-24 13:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-06-24 14:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-06-24 15:00 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2025-06-24 16:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-06-24 17:00 | 9.7612 | 0.01962% | 10.2211 | 10.7027 | 11.207 | 11.7351 | 0 | 0 | 0.056427 | 0.51029
2025-06-24 18:00 | 10.1385 | 0.02038% | 10.6162 | 11.1165 | 11.6403 | 12.1887 | 0 | 0 | 0.42881 | 0.90023
2025-06-24 19:00 | 10.692 | 0.02149% | 11.1958 | 11.7233 | 12.2757 | 12.8541 | 0.046793 | 0.50021 | 0.97498 | 1.4721
2025-06-24 20:00 | 10.692 | 0.02149% | 11.1958 | 11.7233 | 12.2757 | 12.8541 | 0.046793 | 0.50021 | 0.97498 | 1.4721
2025-06-24 21:00 | 11.3587 | 0.02283% | 11.8939 | 12.4543 | 13.0411 | 13.6556 | 0.6468 | 1.1285 | 1.6329 | 2.161
2025-06-24 22:00 | 11.3712 | 0.02285% | 11.907 | 12.4681 | 13.0556 | 13.6707 | 0.65812 | 1.1403 | 1.6453 | 2.174
2025-06-24 23:00 | 11.3712 | 0.02285% | 11.907 | 12.4681 | 13.0556 | 13.6707 | 0.65812 | 1.1403 | 1.6453 | 2.174
2025-06-25 | 11.3712 | 0.02285% | 11.907 | 12.4681 | 13.0556 | 13.6707 | 0.65812 | 1.1403 | 1.6453 | 2.174
2025-06-25 01:00 | 10.6794 | 0.02146% | 11.1826 | 11.7095 | 12.2613 | 12.839 | 0.035472 | 0.48835 | 0.96257 | 1.4591
2025-06-25 02:00 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2025-06-25 03:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-06-25 04:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-06-25 05:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-06-25 06:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-06-25 07:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-06-25 08:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-06-25 09:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-06-25 10:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-06-25 11:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-06-25 12:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-06-25 13:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-06-25 14:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-06-25 15:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-06-25 16:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-06-25 17:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-06-25 18:00 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2025-06-25 19:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2025-06-25 20:00 | 9.497 | 0.01909% | 9.9445 | 10.4131 | 10.9037 | 11.4175 | 0 | 0 | 0 | 0.23734
2025-06-25 21:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-06-25 22:00 | 10.4153 | 0.02093% | 10.906 | 11.4199 | 11.958 | 12.5214 | 0 | 0.23941 | 0.7019 | 1.1862
2025-06-25 23:00 | 10.4153 | 0.02093% | 10.906 | 11.4199 | 11.958 | 12.5214 | 0 | 0.23941 | 0.7019 | 1.1862
2025-06-26 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-06-26 01:00 | 9.4467 | 0.01899% | 9.8918 | 10.3579 | 10.8459 | 11.357 | 0 | 0 | 0 | 0.18535
2025-06-26 02:00 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2025-06-26 03:00 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-06-26 04:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-06-26 05:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-06-26 06:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-06-26 07:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-06-26 08:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-06-26 09:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-06-26 10:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-06-26 11:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-06-26 12:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-06-26 13:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-06-26 14:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-06-26 15:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-06-26 16:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-06-26 17:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-06-26 18:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-06-26 19:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-06-26 20:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-06-26 21:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-06-26 22:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-06-26 23:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-06-27 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-06-27 01:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-06-27 02:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-06-27 03:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-06-27 04:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-06-27 05:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-06-27 06:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-06-27 07:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-06-27 08:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-06-27 09:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-06-27 10:00 | 3.4718 | 0.006978% | 3.6353 | 3.8066 | 3.986 | 4.1738 | 0 | 0 | 0 | 0
2025-06-27 11:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-06-27 12:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-06-27 13:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-06-27 14:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-06-27 15:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-06-27 16:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-06-27 17:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-06-27 18:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-06-27 19:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-06-27 20:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-06-27 21:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-06-27 22:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-06-27 23:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-06-28 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-06-28 01:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-06-28 02:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-06-28 03:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-06-28 04:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-06-28 05:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-06-28 06:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-06-28 07:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-06-28 08:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-06-28 09:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-06-28 10:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-06-28 11:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-06-28 12:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-06-28 13:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-06-28 14:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-06-28 15:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-06-28 16:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-06-28 17:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-06-28 18:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-06-28 19:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2025-06-28 20:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-06-28 21:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-06-28 22:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-06-28 23:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-06-29 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-06-29 01:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-06-29 02:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-06-29 03:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-06-29 04:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-06-29 05:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-06-29 06:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-06-29 07:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-06-29 08:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-06-29 09:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-06-29 10:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-06-29 11:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-06-29 12:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-06-29 13:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-06-29 14:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-06-29 15:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-06-29 16:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-06-29 17:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-06-29 18:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-06-29 19:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-06-29 20:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-06-29 21:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-06-29 22:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-06-29 23:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-06-30 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-06-30 01:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-06-30 02:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-06-30 03:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-06-30 04:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-06-30 05:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-06-30 06:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-06-30 07:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-06-30 08:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-06-30 09:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-06-30 10:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-06-30 11:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-06-30 12:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-06-30 13:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-06-30 14:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-06-30 15:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-06-30 16:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-06-30 17:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-06-30 18:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-06-30 19:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-06-30 20:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-06-30 21:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-06-30 22:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-06-30 23:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-07-01 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-07-01 01:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-07-01 02:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-07-01 03:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-07-01 04:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-07-01 05:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-07-01 06:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-07-01 07:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-07-01 08:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-07-01 09:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-07-01 10:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-07-01 11:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-07-01 12:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-07-01 13:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-07-01 14:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-07-01 15:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-07-01 16:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-07-01 17:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-07-01 18:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2025-07-01 19:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2025-07-01 20:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2025-07-01 21:00 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2025-07-01 22:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-07-01 23:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-07-02 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-07-02 01:00 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2025-07-02 02:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-07-02 03:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-07-02 04:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-07-02 05:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-07-02 06:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-07-02 07:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-07-02 08:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-07-02 09:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-07-02 10:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-07-02 11:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-07-02 12:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-07-02 13:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-07-02 14:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-07-02 15:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-07-02 16:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-07-02 17:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-07-02 18:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-07-02 19:00 | 8.3272 | 0.01674% | 8.7195 | 9.1304 | 9.5606 | 10.0111 | 0 | 0 | 0 | 0
2025-07-02 20:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-07-02 21:00 | 9.1574 | 0.01841% | 9.5889 | 10.0407 | 10.5138 | 11.0092 | 0 | 0 | 0 | 0
2025-07-02 22:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-07-02 23:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2025-07-03 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-07-03 01:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-07-03 02:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-07-03 03:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-07-03 04:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-07-03 05:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-07-03 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-07-03 07:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-07-03 08:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-07-03 09:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-07-03 10:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-07-03 11:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-07-03 12:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-07-03 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-07-03 14:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-07-03 15:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-07-03 16:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-07-03 17:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-07-03 18:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-07-03 19:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-07-03 20:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-07-03 21:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-07-03 22:00 | 8.3523 | 0.01679% | 8.7459 | 9.158 | 9.5895 | 10.0413 | 0 | 0 | 0 | 0
2025-07-03 23:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2025-07-04 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-07-04 01:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-07-04 02:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-07-04 03:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-07-04 04:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-07-04 05:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-07-04 06:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-07-04 07:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-07-04 08:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-07-04 09:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-07-04 10:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-07-04 11:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-07-04 12:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-07-04 13:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-07-04 14:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-07-04 15:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-07-04 16:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-07-04 17:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-07-04 18:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-07-04 19:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-07-04 20:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-07-04 21:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-07-04 22:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-07-04 23:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-07-05 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-07-05 01:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-07-05 02:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-07-05 03:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-07-05 04:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-07-05 05:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-07-05 06:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-07-05 07:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-07-05 08:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-07-05 09:00 | 3.3837 | 0.006801% | 3.5431 | 3.7101 | 3.8849 | 4.0679 | 0 | 0 | 0 | 0
2025-07-05 10:00 | 3.3711 | 0.006775% | 3.53 | 3.6963 | 3.8705 | 4.0528 | 0 | 0 | 0 | 0
2025-07-05 11:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-07-05 12:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-07-05 13:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-07-05 14:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-07-05 15:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-07-05 16:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-07-05 17:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-07-05 18:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-07-05 19:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-07-05 20:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-07-05 21:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2025-07-05 22:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-07-05 23:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-07-06 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-07-06 01:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-07-06 02:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-07-06 03:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-07-06 04:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-07-06 05:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-07-06 06:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-07-06 07:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-07-06 08:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-07-06 09:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-07-06 10:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-07-06 11:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-07-06 12:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-07-06 13:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-07-06 14:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-07-06 15:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-07-06 16:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-07-06 17:00 | 9.0945 | 0.01828% | 9.523 | 9.9717 | 10.4416 | 10.9336 | 0 | 0 | 0 | 0
2025-07-06 18:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-07-06 19:00 | 9.6731 | 0.01944% | 10.1289 | 10.6062 | 11.1059 | 11.6292 | 0 | 0 | 0 | 0.41931
2025-07-06 20:00 | 9.975 | 0.02005% | 10.445 | 10.9372 | 11.4525 | 11.9921 | 0 | 0 | 0.26745 | 0.73126
2025-07-06 21:00 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2025-07-06 22:00 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2025-07-06 23:00 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2025-07-07 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2025-07-07 01:00 | 9.6731 | 0.01944% | 10.1289 | 10.6062 | 11.1059 | 11.6292 | 0 | 0 | 0 | 0.41931
2025-07-07 02:00 | 9.3838 | 0.01886% | 9.8259 | 10.2889 | 10.7737 | 11.2814 | 0 | 0 | 0 | 0.12036
2025-07-07 03:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2025-07-07 04:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-07-07 05:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-07-07 06:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-07-07 07:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-07-07 08:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-07-07 09:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-07-07 10:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-07-07 11:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-07-07 12:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-07-07 13:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-07-07 14:00 | 8.1511 | 0.01638% | 8.5351 | 8.9373 | 9.3584 | 9.7994 | 0 | 0 | 0 | 0
2025-07-07 15:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-07-07 16:00 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2025-07-07 17:00 | 9.6605 | 0.01942% | 10.1157 | 10.5924 | 11.0915 | 11.6141 | 0 | 0 | 0 | 0.40631
2025-07-07 18:00 | 9.3461 | 0.01878% | 9.7864 | 10.2476 | 10.7304 | 11.236 | 0 | 0 | 0 | 0.081366
2025-07-07 19:00 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2025-07-07 20:00 | 9.9247 | 0.01995% | 10.3923 | 10.882 | 11.3947 | 11.9316 | 0 | 0 | 0.21779 | 0.67927
2025-07-07 21:00 | 9.9247 | 0.01995% | 10.3923 | 10.882 | 11.3947 | 11.9316 | 0 | 0 | 0.21779 | 0.67927
2025-07-07 22:00 | 10.214 | 0.02053% | 10.6953 | 11.1992 | 11.7269 | 12.2795 | 0 | 0.04974 | 0.50329 | 0.97821
2025-07-07 23:00 | 9.7612 | 0.01962% | 10.2211 | 10.7027 | 11.207 | 11.7351 | 0 | 0 | 0.056427 | 0.51029
2025-07-08 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-07-08 01:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-07-08 02:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-07-08 03:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-07-08 04:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-07-08 05:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-07-08 06:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-07-08 07:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-07-08 08:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-07-08 09:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-07-08 10:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-07-08 11:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-07-08 12:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-07-08 13:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-07-08 14:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-07-08 15:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-07-08 16:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-07-08 17:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-07-08 18:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-07-08 19:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-07-08 20:00 | 8.2894 | 0.01666% | 8.68 | 9.089 | 9.5173 | 9.9657 | 0 | 0 | 0 | 0
2025-07-08 21:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2025-07-08 22:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-07-08 23:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-07-09 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-07-09 01:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-07-09 02:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-07-09 03:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-07-09 04:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-07-09 05:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-07-09 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-07-09 07:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-07-09 08:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-07-09 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-07-09 10:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-07-09 11:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-07-09 12:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-07-09 13:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-07-09 14:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-07-09 15:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-07-09 16:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-07-09 17:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-07-09 18:00 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-07-09 19:00 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-07-09 20:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-07-09 21:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2025-07-09 22:00 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2025-07-09 23:00 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2025-07-10 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-07-10 01:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-07-10 02:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-07-10 03:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-07-10 04:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-07-10 05:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-07-10 06:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-07-10 07:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-07-10 08:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-07-10 09:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-07-10 10:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-07-10 11:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-07-10 12:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-07-10 13:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-07-10 14:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-07-10 15:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-07-10 16:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-07-10 17:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-07-10 18:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-07-10 19:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-07-10 20:00 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2025-07-10 21:00 | 8.8429 | 0.01777% | 9.2596 | 9.6959 | 10.1527 | 10.6311 | 0 | 0 | 0 | 0
2025-07-10 22:00 | 9.258 | 0.01861% | 9.6942 | 10.151 | 10.6293 | 11.1302 | 0 | 0 | 0 | 0
2025-07-10 23:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-07-11 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-07-11 01:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2025-07-11 02:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-07-11 03:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-07-11 04:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-07-11 05:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-07-11 06:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-07-11 07:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-07-11 08:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-07-11 09:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-07-11 10:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-07-11 11:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-07-11 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-07-11 13:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-07-11 14:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-07-11 15:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-07-11 16:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-07-11 17:00 | 8.3272 | 0.01674% | 8.7195 | 9.1304 | 9.5606 | 10.0111 | 0 | 0 | 0 | 0
2025-07-11 18:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-07-11 19:00 | 9.1196 | 0.01833% | 9.5493 | 9.9993 | 10.4705 | 10.9638 | 0 | 0 | 0 | 0
2025-07-11 20:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2025-07-11 21:00 | 9.6983 | 0.01949% | 10.1552 | 10.6337 | 11.1348 | 11.6594 | 0 | 0 | 0 | 0.4453
2025-07-11 22:00 | 9.9247 | 0.01995% | 10.3923 | 10.882 | 11.3947 | 11.9316 | 0 | 0 | 0.21779 | 0.67927
2025-07-11 23:00 | 9.6983 | 0.01949% | 10.1552 | 10.6337 | 11.1348 | 11.6594 | 0 | 0 | 0 | 0.4453
2025-07-12 | 9.3838 | 0.01886% | 9.8259 | 10.2889 | 10.7737 | 11.2814 | 0 | 0 | 0 | 0.12036
2025-07-12 01:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-07-12 02:00 | 8.3523 | 0.01679% | 8.7459 | 9.158 | 9.5895 | 10.0413 | 0 | 0 | 0 | 0
2025-07-12 03:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-07-12 04:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-07-12 05:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-07-12 06:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-07-12 07:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-07-12 08:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-07-12 09:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-07-12 10:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-07-12 11:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-07-12 12:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-07-12 13:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-07-12 14:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-07-12 15:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-07-12 16:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-07-12 17:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-07-12 18:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-12 19:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-12 20:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-07-12 21:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2025-07-12 22:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2025-07-12 23:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2025-07-13 | 9.3586 | 0.01881% | 9.7996 | 10.2613 | 10.7448 | 11.2511 | 0 | 0 | 0 | 0.094364
2025-07-13 01:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-13 02:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-07-13 03:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2025-07-13 04:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-07-13 05:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-07-13 06:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-07-13 07:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-07-13 08:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-07-13 09:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-07-13 10:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-07-13 11:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-07-13 12:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-07-13 13:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-07-13 14:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-07-13 15:00 | 8.3775 | 0.01684% | 8.7722 | 9.1856 | 9.6184 | 10.0716 | 0 | 0 | 0 | 0
2025-07-13 16:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2025-07-13 17:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2025-07-13 18:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-07-13 19:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2025-07-13 20:00 | 9.4844 | 0.01906% | 9.9313 | 10.3993 | 10.8893 | 11.4024 | 0 | 0 | 0 | 0.22434
2025-07-13 21:00 | 9.8995 | 0.0199% | 10.366 | 10.8544 | 11.3659 | 11.9014 | 0 | 0 | 0.19297 | 0.65327
2025-07-13 22:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-07-13 23:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-07-14 | 9.7612 | 0.01962% | 10.2211 | 10.7027 | 11.207 | 11.7351 | 0 | 0 | 0.056427 | 0.51029
2025-07-14 01:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-07-14 02:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-07-14 03:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-07-14 04:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-07-14 05:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-07-14 06:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-07-14 07:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-07-14 08:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-07-14 09:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-07-14 10:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-07-14 11:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-07-14 12:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-07-14 13:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-07-14 14:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-07-14 15:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-07-14 16:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-07-14 17:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2025-07-14 18:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-07-14 19:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-07-14 20:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2025-07-14 21:00 | 9.5222 | 0.01914% | 9.9708 | 10.4406 | 10.9326 | 11.4477 | 0 | 0 | 0 | 0.26334
2025-07-14 22:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2025-07-14 23:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2025-07-15 | 9.2832 | 0.01866% | 9.7206 | 10.1786 | 10.6582 | 11.1604 | 0 | 0 | 0 | 0.016377
2025-07-15 01:00 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-07-15 02:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-07-15 03:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-07-15 04:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-07-15 05:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-07-15 06:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-07-15 07:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-07-15 08:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-07-15 09:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-07-15 10:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-07-15 11:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-07-15 12:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-07-15 13:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-07-15 14:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-07-15 15:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-07-15 16:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-07-15 17:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2025-07-15 18:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2025-07-15 19:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2025-07-15 20:00 | 9.6857 | 0.01947% | 10.1421 | 10.6199 | 11.1203 | 11.6443 | 0 | 0 | 0 | 0.43231
2025-07-15 21:00 | 10.1134 | 0.02033% | 10.5899 | 11.0889 | 11.6114 | 12.1585 | 0 | 0 | 0.40399 | 0.87423
2025-07-15 22:00 | 10.1763 | 0.02045% | 10.6558 | 11.1578 | 11.6836 | 12.2341 | 0 | 0.014177 | 0.46605 | 0.93922
2025-07-15 23:00 | 10.1763 | 0.02045% | 10.6558 | 11.1578 | 11.6836 | 12.2341 | 0 | 0.014177 | 0.46605 | 0.93922
2025-07-16 | 9.8744 | 0.01985% | 10.3396 | 10.8268 | 11.337 | 11.8712 | 0 | 0 | 0.16814 | 0.62727
2025-07-16 01:00 | 9.2706 | 0.01863% | 9.7074 | 10.1648 | 10.6438 | 11.1453 | 0 | 0 | 0 | 0.0033794
2025-07-16 02:00 | 8.9813 | 0.01805% | 9.4045 | 9.8476 | 10.3116 | 10.7975 | 0 | 0 | 0 | 0
2025-07-16 03:00 | 8.1133 | 0.01631% | 8.4956 | 8.8959 | 9.3151 | 9.754 | 0 | 0 | 0 | 0
2025-07-16 04:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-07-16 05:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-07-16 06:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-07-16 07:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-07-16 08:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-07-16 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-07-16 10:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-07-16 11:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-07-16 12:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-07-16 13:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-07-16 14:00 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-07-16 15:00 | 8.3775 | 0.01684% | 8.7722 | 9.1856 | 9.6184 | 10.0716 | 0 | 0 | 0 | 0
2025-07-16 16:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2025-07-16 17:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-07-16 18:00 | 9.2832 | 0.01866% | 9.7206 | 10.1786 | 10.6582 | 11.1604 | 0 | 0 | 0 | 0.016377
2025-07-16 19:00 | 9.5096 | 0.01911% | 9.9577 | 10.4269 | 10.9182 | 11.4326 | 0 | 0 | 0 | 0.25034
2025-07-16 20:00 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2025-07-16 21:00 | 10.4278 | 0.02096% | 10.9192 | 11.4337 | 11.9724 | 12.5365 | 0 | 0.25126 | 0.71431 | 1.1992
2025-07-16 22:00 | 10.4278 | 0.02096% | 10.9192 | 11.4337 | 11.9724 | 12.5365 | 0 | 0.25126 | 0.71431 | 1.1992
2025-07-16 23:00 | 10.4278 | 0.02096% | 10.9192 | 11.4337 | 11.9724 | 12.5365 | 0 | 0.25126 | 0.71431 | 1.1992
2025-07-17 | 10.1008 | 0.0203% | 10.5767 | 11.0751 | 11.5969 | 12.1434 | 0 | 0 | 0.39158 | 0.86123
2025-07-17 01:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2025-07-17 02:00 | 9.4593 | 0.01901% | 9.905 | 10.3717 | 10.8604 | 11.3721 | 0 | 0 | 0 | 0.19835
2025-07-17 03:00 | 8.8932 | 0.01787% | 9.3123 | 9.751 | 10.2105 | 10.6916 | 0 | 0 | 0 | 0
2025-07-17 04:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2025-07-17 05:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-07-17 06:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-07-17 07:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-07-17 08:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-07-17 09:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-07-17 10:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-07-17 11:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-07-17 12:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-07-17 13:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-07-17 14:00 | 8.2894 | 0.01666% | 8.68 | 9.089 | 9.5173 | 9.9657 | 0 | 0 | 0 | 0
2025-07-17 15:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2025-07-17 16:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-17 17:00 | 9.0567 | 0.0182% | 9.4835 | 9.9303 | 10.3982 | 10.8882 | 0 | 0 | 0 | 0
2025-07-17 18:00 | 9.0567 | 0.0182% | 9.4835 | 9.9303 | 10.3982 | 10.8882 | 0 | 0 | 0 | 0
2025-07-17 19:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-17 20:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2025-07-17 21:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-17 22:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-07-17 23:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-07-18 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2025-07-18 01:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-07-18 02:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-07-18 03:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-07-18 04:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-07-18 05:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-07-18 06:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-07-18 07:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-07-18 08:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-07-18 09:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-07-18 10:00 | 3.3837 | 0.006801% | 3.5431 | 3.7101 | 3.8849 | 4.0679 | 0 | 0 | 0 | 0
2025-07-18 11:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-07-18 12:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-07-18 13:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-07-18 14:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-07-18 15:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-07-18 16:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-07-18 17:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-07-18 18:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-07-18 19:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-07-18 20:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-07-18 21:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-07-18 22:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-07-18 23:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-07-19 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-07-19 01:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-07-19 02:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-07-19 03:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-07-19 04:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-07-19 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-07-19 06:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-07-19 07:00 | 3.5598 | 0.007155% | 3.7275 | 3.9032 | 4.0871 | 4.2797 | 0 | 0 | 0 | 0
2025-07-19 08:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-07-19 09:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-07-19 10:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-07-19 11:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-07-19 12:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-07-19 13:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-07-19 14:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-07-19 15:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-07-19 16:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-07-19 17:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-07-19 18:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-07-19 19:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-07-19 20:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-07-19 21:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-07-19 22:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-07-19 23:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-07-20 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-07-20 01:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-07-20 02:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-07-20 03:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-07-20 04:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-07-20 05:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-07-20 06:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-07-20 07:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-07-20 08:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-07-20 09:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-07-20 10:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-07-20 11:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-07-20 12:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-07-20 13:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-07-20 14:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-07-20 15:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-07-20 16:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-07-20 17:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-07-20 18:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-07-20 19:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-07-20 20:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2025-07-20 21:00 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2025-07-20 22:00 | 9.1196 | 0.01833% | 9.5493 | 9.9993 | 10.4705 | 10.9638 | 0 | 0 | 0 | 0
2025-07-20 23:00 | 9.1196 | 0.01833% | 9.5493 | 9.9993 | 10.4705 | 10.9638 | 0 | 0 | 0 | 0
2025-07-21 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2025-07-21 01:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-07-21 02:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-07-21 03:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-07-21 04:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-07-21 05:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-07-21 06:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-07-21 07:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-07-21 08:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-07-21 09:00 | 3.6856 | 0.007408% | 3.8593 | 4.0411 | 4.2315 | 4.4309 | 0 | 0 | 0 | 0
2025-07-21 10:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-07-21 11:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-07-21 12:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-07-21 13:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-07-21 14:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-07-21 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-07-21 16:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-07-21 17:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-07-21 18:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-07-21 19:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-07-21 20:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-07-21 21:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-07-21 22:00 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2025-07-21 23:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-07-22 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-07-22 01:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-07-22 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-07-22 03:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-07-22 04:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-07-22 05:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-07-22 06:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-07-22 07:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-07-22 08:00 | 3.4592 | 0.006952% | 3.6222 | 3.7928 | 3.9716 | 4.1587 | 0 | 0 | 0 | 0
2025-07-22 09:00 | 3.3334 | 0.0067% | 3.4905 | 3.6549 | 3.8271 | 4.0075 | 0 | 0 | 0 | 0
2025-07-22 10:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-07-22 11:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-07-22 12:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-07-22 13:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-07-22 14:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-07-22 15:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-07-22 16:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-07-22 17:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-07-22 18:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-07-22 19:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-07-22 20:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-07-22 21:00 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-07-22 22:00 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-07-22 23:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-07-23 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-07-23 01:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-07-23 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-07-23 03:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-07-23 04:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-07-23 05:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-07-23 06:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-07-23 07:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-07-23 08:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-07-23 09:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-07-23 10:00 | 3.3963 | 0.006826% | 3.5563 | 3.7239 | 3.8993 | 4.0831 | 0 | 0 | 0 | 0
2025-07-23 11:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-07-23 12:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-07-23 13:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-07-23 14:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-07-23 15:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-07-23 16:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-07-23 17:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-07-23 18:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-07-23 19:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-07-23 20:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-07-23 21:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2025-07-23 22:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-07-23 23:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2025-07-24 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-07-24 01:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-07-24 02:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-07-24 03:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-07-24 04:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-07-24 05:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-07-24 06:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-07-24 07:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-07-24 08:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-07-24 09:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-07-24 10:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-07-24 11:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-07-24 12:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-07-24 13:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-07-24 14:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-07-24 15:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-07-24 16:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-07-24 17:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2025-07-24 18:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2025-07-24 19:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-07-24 20:00 | 9.6857 | 0.01947% | 10.1421 | 10.6199 | 11.1203 | 11.6443 | 0 | 0 | 0 | 0.43231
2025-07-24 21:00 | 10.3524 | 0.02081% | 10.8402 | 11.3509 | 11.8858 | 12.4458 | 0 | 0.18014 | 0.63983 | 1.1212
2025-07-24 22:00 | 10.6668 | 0.02144% | 11.1694 | 11.6957 | 12.2468 | 12.8239 | 0.024151 | 0.4765 | 0.95016 | 1.4461
2025-07-24 23:00 | 10.6668 | 0.02144% | 11.1694 | 11.6957 | 12.2468 | 12.8239 | 0.024151 | 0.4765 | 0.95016 | 1.4461
2025-07-25 | 10.2266 | 0.02055% | 10.7084 | 11.213 | 11.7413 | 12.2946 | 0 | 0.061595 | 0.5157 | 0.99121
2025-07-25 01:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2025-07-25 02:00 | 9.0945 | 0.01828% | 9.523 | 9.9717 | 10.4416 | 10.9336 | 0 | 0 | 0 | 0
2025-07-25 03:00 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2025-07-25 04:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-07-25 05:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-07-25 06:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-07-25 07:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-07-25 08:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-07-25 09:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-07-25 10:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-07-25 11:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-07-25 12:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-07-25 13:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-07-25 14:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-07-25 15:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-07-25 16:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-07-25 17:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2025-07-25 18:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-07-25 19:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2025-07-25 20:00 | 9.4467 | 0.01899% | 9.8918 | 10.3579 | 10.8459 | 11.357 | 0 | 0 | 0 | 0.18535
2025-07-25 21:00 | 9.7989 | 0.01969% | 10.2606 | 10.7441 | 11.2503 | 11.7804 | 0 | 0 | 0.093666 | 0.54929
2025-07-25 22:00 | 10.0379 | 0.02017% | 10.5109 | 11.0061 | 11.5247 | 12.0677 | 0 | 0 | 0.32951 | 0.79625
2025-07-25 23:00 | 10.0379 | 0.02017% | 10.5109 | 11.0061 | 11.5247 | 12.0677 | 0 | 0 | 0.32951 | 0.79625
2025-07-26 | 9.7234 | 0.01954% | 10.1816 | 10.6613 | 11.1637 | 11.6897 | 0 | 0 | 0.019188 | 0.4713
2025-07-26 01:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-07-26 02:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2025-07-26 03:00 | 8.1008 | 0.01628% | 8.4825 | 8.8821 | 9.3006 | 9.7389 | 0 | 0 | 0 | 0
2025-07-26 04:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-07-26 05:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-07-26 06:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-07-26 07:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-07-26 08:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-07-26 09:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-07-26 10:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-07-26 11:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-07-26 12:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-07-26 13:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-07-26 14:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-07-26 15:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-07-26 16:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-07-26 17:00 | 8.1637 | 0.01641% | 8.5483 | 8.9511 | 9.3729 | 9.8145 | 0 | 0 | 0 | 0
2025-07-26 18:00 | 8.3901 | 0.01686% | 8.7854 | 9.1994 | 9.6328 | 10.0867 | 0 | 0 | 0 | 0
2025-07-26 19:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2025-07-26 20:00 | 8.6542 | 0.01739% | 9.062 | 9.489 | 9.9361 | 10.4043 | 0 | 0 | 0 | 0
2025-07-26 21:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-07-26 22:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-07-26 23:00 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2025-07-27 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-07-27 01:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-07-27 02:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-07-27 03:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-07-27 04:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-07-27 05:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-07-27 06:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-07-27 07:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-07-27 08:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-07-27 09:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-07-27 10:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-07-27 11:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-07-27 12:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-07-27 13:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-07-27 14:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-07-27 15:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-07-27 16:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-07-27 17:00 | 9.0064 | 0.0181% | 9.4308 | 9.8752 | 10.3405 | 10.8277 | 0 | 0 | 0 | 0
2025-07-27 18:00 | 9.5725 | 0.01924% | 10.0235 | 10.4958 | 10.9904 | 11.5082 | 0 | 0 | 0 | 0.31533
2025-07-27 19:00 | 9.5725 | 0.01924% | 10.0235 | 10.4958 | 10.9904 | 11.5082 | 0 | 0 | 0 | 0.31533
2025-07-27 20:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2025-07-27 21:00 | 10.3524 | 0.02081% | 10.8402 | 11.3509 | 11.8858 | 12.4458 | 0 | 0.18014 | 0.63983 | 1.1212
2025-07-27 22:00 | 10.4782 | 0.02106% | 10.9719 | 11.4888 | 12.0302 | 12.597 | 0 | 0.29868 | 0.76396 | 1.2512
2025-07-27 23:00 | 10.4782 | 0.02106% | 10.9719 | 11.4888 | 12.0302 | 12.597 | 0 | 0.29868 | 0.76396 | 1.2512
2025-07-28 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2025-07-28 01:00 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2025-07-28 02:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2025-07-28 03:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2025-07-28 04:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-07-28 05:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-07-28 06:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-07-28 07:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-07-28 08:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-07-28 09:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-07-28 10:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-07-28 11:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-07-28 12:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-07-28 13:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-07-28 14:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-07-28 15:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-07-28 16:00 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-07-28 17:00 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2025-07-28 18:00 | 9.497 | 0.01909% | 9.9445 | 10.4131 | 10.9037 | 11.4175 | 0 | 0 | 0 | 0.23734
2025-07-28 19:00 | 9.7863 | 0.01967% | 10.2474 | 10.7303 | 11.2359 | 11.7653 | 0 | 0 | 0.081253 | 0.53629
2025-07-28 20:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-07-28 21:00 | 10.78 | 0.02167% | 11.288 | 11.8199 | 12.3768 | 12.96 | 0.12604 | 0.58319 | 1.0619 | 1.5631
2025-07-28 22:00 | 10.78 | 0.02167% | 11.288 | 11.8199 | 12.3768 | 12.96 | 0.12604 | 0.58319 | 1.0619 | 1.5631
2025-07-28 23:00 | 10.78 | 0.02167% | 11.288 | 11.8199 | 12.3768 | 12.96 | 0.12604 | 0.58319 | 1.0619 | 1.5631
2025-07-29 | 10.453 | 0.02101% | 10.9455 | 11.4613 | 12.0013 | 12.5668 | 0 | 0.27497 | 0.73914 | 1.2252
2025-07-29 01:00 | 10.1134 | 0.02033% | 10.5899 | 11.0889 | 11.6114 | 12.1585 | 0 | 0 | 0.40399 | 0.87423
2025-07-29 02:00 | 9.7737 | 0.01964% | 10.2343 | 10.7165 | 11.2214 | 11.7502 | 0 | 0 | 0.06884 | 0.52329
2025-07-29 03:00 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2025-07-29 04:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-07-29 05:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-07-29 06:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-07-29 07:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-07-29 08:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-07-29 09:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-07-29 10:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-07-29 11:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-07-29 12:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-07-29 13:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-07-29 14:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-07-29 15:00 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2025-07-29 16:00 | 9.1574 | 0.01841% | 9.5889 | 10.0407 | 10.5138 | 11.0092 | 0 | 0 | 0 | 0
2025-07-29 17:00 | 9.5851 | 0.01926% | 10.0367 | 10.5096 | 11.0048 | 11.5233 | 0 | 0 | 0 | 0.32832
2025-07-29 18:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2025-07-29 19:00 | 9.9498 | 0.02% | 10.4187 | 10.9096 | 11.4236 | 11.9619 | 0 | 0 | 0.24262 | 0.70526
2025-07-29 20:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2025-07-29 21:00 | 10.4027 | 0.02091% | 10.8928 | 11.4061 | 11.9435 | 12.5063 | 0 | 0.22756 | 0.68949 | 1.1732
2025-07-29 22:00 | 10.7423 | 0.02159% | 11.2485 | 11.7785 | 12.3335 | 12.9146 | 0.092077 | 0.54762 | 1.0246 | 1.5241
2025-07-29 23:00 | 10.7423 | 0.02159% | 11.2485 | 11.7785 | 12.3335 | 12.9146 | 0.092077 | 0.54762 | 1.0246 | 1.5241
2025-07-30 | 10.4153 | 0.02093% | 10.906 | 11.4199 | 11.958 | 12.5214 | 0 | 0.23941 | 0.7019 | 1.1862
2025-07-30 01:00 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2025-07-30 02:00 | 9.6605 | 0.01942% | 10.1157 | 10.5924 | 11.0915 | 11.6141 | 0 | 0 | 0 | 0.40631
2025-07-30 03:00 | 8.692 | 0.01747% | 9.1015 | 9.5304 | 9.9794 | 10.4496 | 0 | 0 | 0 | 0
2025-07-30 04:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-07-30 05:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-07-30 06:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-07-30 07:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-07-30 08:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-07-30 09:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-07-30 10:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-07-30 11:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-07-30 12:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-07-30 13:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-07-30 14:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-07-30 15:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-07-30 16:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-07-30 17:00 | 9.1574 | 0.01841% | 9.5889 | 10.0407 | 10.5138 | 11.0092 | 0 | 0 | 0 | 0
2025-07-30 18:00 | 9.3083 | 0.01871% | 9.7469 | 10.2062 | 10.6871 | 11.1906 | 0 | 0 | 0 | 0.042373
2025-07-30 19:00 | 9.1574 | 0.01841% | 9.5889 | 10.0407 | 10.5138 | 11.0092 | 0 | 0 | 0 | 0
2025-07-30 20:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2025-07-30 21:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2025-07-30 22:00 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2025-07-30 23:00 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2025-07-31 | 9.3838 | 0.01886% | 9.8259 | 10.2889 | 10.7737 | 11.2814 | 0 | 0 | 0 | 0.12036
2025-07-31 01:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2025-07-31 02:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2025-07-31 03:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-07-31 04:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-07-31 05:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-07-31 06:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-07-31 07:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-07-31 08:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-07-31 09:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-07-31 10:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-07-31 11:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-07-31 12:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-07-31 13:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-07-31 14:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-07-31 15:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-07-31 16:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-07-31 17:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-07-31 18:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-07-31 19:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-07-31 20:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-07-31 21:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-07-31 22:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-07-31 23:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-08-01 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-08-01 01:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-08-01 02:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-08-01 03:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-08-01 04:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-08-01 05:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-08-01 06:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-08-01 07:00 | 3.673 | 0.007382% | 3.8461 | 4.0273 | 4.2171 | 4.4158 | 0 | 0 | 0 | 0
2025-08-01 08:00 | 3.4592 | 0.006952% | 3.6222 | 3.7928 | 3.9716 | 4.1587 | 0 | 0 | 0 | 0
2025-08-01 09:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-08-01 10:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-08-01 11:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-08-01 12:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-01 13:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-08-01 14:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-08-01 15:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-08-01 16:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-08-01 17:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-08-01 18:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-08-01 19:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-08-01 20:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-08-01 21:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-08-01 22:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-08-01 23:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-08-02 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-08-02 01:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-08-02 02:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-08-02 03:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-08-02 04:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-08-02 05:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-02 06:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-08-02 07:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-08-02 08:00 | 3.5346 | 0.007104% | 3.7012 | 3.8756 | 4.0582 | 4.2494 | 0 | 0 | 0 | 0
2025-08-02 09:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-08-02 10:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-08-02 11:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-08-02 12:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-08-02 13:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-08-02 14:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-08-02 15:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-08-02 16:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-08-02 17:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-08-02 18:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-08-02 19:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-08-02 20:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-08-02 21:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-08-02 22:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-08-02 23:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-08-03 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-08-03 01:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-08-03 02:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-08-03 03:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-08-03 04:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-08-03 05:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-08-03 06:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-08-03 07:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-08-03 08:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-08-03 09:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-08-03 10:00 | 3.2705 | 0.006573% | 3.4246 | 3.586 | 3.7549 | 3.9318 | 0 | 0 | 0 | 0
2025-08-03 11:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-08-03 12:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-08-03 13:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-03 14:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-08-03 15:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-08-03 16:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-08-03 17:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-08-03 18:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-08-03 19:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-08-03 20:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-08-03 21:00 | 7.7234 | 0.01552% | 8.0873 | 8.4684 | 8.8674 | 9.2852 | 0 | 0 | 0 | 0
2025-08-03 22:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-08-03 23:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-08-04 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-08-04 01:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-08-04 02:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-08-04 03:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-08-04 04:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-08-04 05:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-08-04 06:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-08-04 07:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-08-04 08:00 | 3.5221 | 0.007079% | 3.688 | 3.8618 | 4.0438 | 4.2343 | 0 | 0 | 0 | 0
2025-08-04 09:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-08-04 10:00 | 3.4466 | 0.006927% | 3.609 | 3.779 | 3.9571 | 4.1436 | 0 | 0 | 0 | 0
2025-08-04 11:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-08-04 12:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-08-04 13:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-08-04 14:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-08-04 15:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-08-04 16:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-08-04 17:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-08-04 18:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-08-04 19:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-08-04 20:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2025-08-04 21:00 | 9.0945 | 0.01828% | 9.523 | 9.9717 | 10.4416 | 10.9336 | 0 | 0 | 0 | 0
2025-08-04 22:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2025-08-04 23:00 | 9.0567 | 0.0182% | 9.4835 | 9.9303 | 10.3982 | 10.8882 | 0 | 0 | 0 | 0
2025-08-05 | 8.6165 | 0.01732% | 9.0225 | 9.4476 | 9.8928 | 10.3589 | 0 | 0 | 0 | 0
2025-08-05 01:00 | 8.0127 | 0.0161% | 8.3903 | 8.7856 | 9.1996 | 9.633 | 0 | 0 | 0 | 0
2025-08-05 02:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-08-05 03:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-08-05 04:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-08-05 05:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-08-05 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-08-05 07:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-08-05 08:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-08-05 09:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-08-05 10:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-08-05 11:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-08-05 12:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-08-05 13:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-05 14:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-08-05 15:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-08-05 16:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-08-05 17:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-08-05 18:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-08-05 19:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2025-08-05 20:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2025-08-05 21:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2025-08-05 22:00 | 9.5096 | 0.01911% | 9.9577 | 10.4269 | 10.9182 | 11.4326 | 0 | 0 | 0 | 0.25034
2025-08-05 23:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2025-08-06 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-08-06 01:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2025-08-06 02:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-08-06 03:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-08-06 04:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-08-06 05:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-08-06 06:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-06 07:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-08-06 08:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-08-06 09:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-08-06 10:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-08-06 11:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-08-06 12:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-08-06 13:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-08-06 14:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-08-06 15:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-08-06 16:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-08-06 17:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-08-06 18:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-08-06 19:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-08-06 20:00 | 8.6165 | 0.01732% | 9.0225 | 9.4476 | 9.8928 | 10.3589 | 0 | 0 | 0 | 0
2025-08-06 21:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-08-06 22:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2025-08-06 23:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2025-08-07 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-08-07 01:00 | 8.3901 | 0.01686% | 8.7854 | 9.1994 | 9.6328 | 10.0867 | 0 | 0 | 0 | 0
2025-08-07 02:00 | 7.975 | 0.01603% | 8.3507 | 8.7442 | 9.1562 | 9.5877 | 0 | 0 | 0 | 0
2025-08-07 03:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-08-07 04:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-08-07 05:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-08-07 06:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-08-07 07:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-08-07 08:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-08-07 09:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-08-07 10:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-08-07 11:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-08-07 12:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-08-07 13:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-08-07 14:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-08-07 15:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-08-07 16:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-08-07 17:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2025-08-07 18:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-08-07 19:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-08-07 20:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-08-07 21:00 | 9.1825 | 0.01846% | 9.6152 | 10.0683 | 10.5427 | 11.0394 | 0 | 0 | 0 | 0
2025-08-07 22:00 | 9.2832 | 0.01866% | 9.7206 | 10.1786 | 10.6582 | 11.1604 | 0 | 0 | 0 | 0.016377
2025-08-07 23:00 | 9.0064 | 0.0181% | 9.4308 | 9.8752 | 10.3405 | 10.8277 | 0 | 0 | 0 | 0
2025-08-08 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-08-08 01:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-08-08 02:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-08-08 03:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-08-08 04:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-08-08 05:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-08-08 06:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-08-08 07:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-08-08 08:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-08-08 09:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-08-08 10:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-08-08 11:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-08-08 12:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-08-08 13:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-08-08 14:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-08-08 15:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-08-08 16:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-08-08 17:00 | 8.214 | 0.01651% | 8.601 | 9.0063 | 9.4306 | 9.875 | 0 | 0 | 0 | 0
2025-08-08 18:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-08-08 19:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2025-08-08 20:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-08-08 21:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2025-08-08 22:00 | 8.6165 | 0.01732% | 9.0225 | 9.4476 | 9.8928 | 10.3589 | 0 | 0 | 0 | 0
2025-08-08 23:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-08-09 | 8.1511 | 0.01638% | 8.5351 | 8.9373 | 9.3584 | 9.7994 | 0 | 0 | 0 | 0
2025-08-09 01:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-08-09 02:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-08-09 03:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-08-09 04:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-08-09 05:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-08-09 06:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-08-09 07:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-08-09 08:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-08-09 09:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-08-09 10:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-08-09 11:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-08-09 12:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-08-09 13:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-08-09 14:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-08-09 15:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-08-09 16:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2025-08-09 17:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2025-08-09 18:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2025-08-09 19:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-08-09 20:00 | 9.3209 | 0.01873% | 9.7601 | 10.22 | 10.7015 | 11.2058 | 0 | 0 | 0 | 0.055371
2025-08-09 21:00 | 9.5222 | 0.01914% | 9.9708 | 10.4406 | 10.9326 | 11.4477 | 0 | 0 | 0 | 0.26334
2025-08-09 22:00 | 9.5976 | 0.01929% | 10.0499 | 10.5234 | 11.0192 | 11.5385 | 0 | 0 | 0 | 0.34132
2025-08-09 23:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-08-10 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-08-10 01:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-08-10 02:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-08-10 03:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2025-08-10 04:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-08-10 05:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-08-10 06:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-08-10 07:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-08-10 08:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-10 09:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-08-10 10:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-08-10 11:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-10 12:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-08-10 13:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-08-10 14:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-08-10 15:00 | 8.0127 | 0.0161% | 8.3903 | 8.7856 | 9.1996 | 9.633 | 0 | 0 | 0 | 0
2025-08-10 16:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-08-10 17:00 | 9.3083 | 0.01871% | 9.7469 | 10.2062 | 10.6871 | 11.1906 | 0 | 0 | 0 | 0.042373
2025-08-10 18:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2025-08-10 19:00 | 9.6983 | 0.01949% | 10.1552 | 10.6337 | 11.1348 | 11.6594 | 0 | 0 | 0 | 0.4453
2025-08-10 20:00 | 10.0002 | 0.0201% | 10.4714 | 10.9647 | 11.4814 | 12.0224 | 0 | 0 | 0.29227 | 0.75725
2025-08-10 21:00 | 10.302 | 0.02071% | 10.7875 | 11.2958 | 11.828 | 12.3853 | 0 | 0.13272 | 0.59018 | 1.0692
2025-08-10 22:00 | 10.5285 | 0.02116% | 11.0246 | 11.544 | 12.088 | 12.6575 | 0 | 0.3461 | 0.81362 | 1.3032
2025-08-10 23:00 | 10.302 | 0.02071% | 10.7875 | 11.2958 | 11.828 | 12.3853 | 0 | 0.13272 | 0.59018 | 1.0692
2025-08-11 | 9.8744 | 0.01985% | 10.3396 | 10.8268 | 11.337 | 11.8712 | 0 | 0 | 0.16814 | 0.62727
2025-08-11 01:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-08-11 02:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2025-08-11 03:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2025-08-11 04:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-08-11 05:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-08-11 06:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-08-11 07:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-08-11 08:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-08-11 09:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-08-11 10:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-08-11 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-08-11 12:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-08-11 13:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-08-11 14:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-08-11 15:00 | 8.3901 | 0.01686% | 8.7854 | 9.1994 | 9.6328 | 10.0867 | 0 | 0 | 0 | 0
2025-08-11 16:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2025-08-11 17:00 | 9.5473 | 0.01919% | 9.9972 | 10.4682 | 10.9615 | 11.478 | 0 | 0 | 0 | 0.28933
2025-08-11 18:00 | 9.5473 | 0.01919% | 9.9972 | 10.4682 | 10.9615 | 11.478 | 0 | 0 | 0 | 0.28933
2025-08-11 19:00 | 9.8366 | 0.01977% | 10.3001 | 10.7854 | 11.2936 | 11.8258 | 0 | 0 | 0.1309 | 0.58828
2025-08-11 20:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2025-08-11 21:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2025-08-11 22:00 | 10.8052 | 0.02172% | 11.3143 | 11.8474 | 12.4057 | 12.9902 | 0.14868 | 0.6069 | 1.0867 | 1.5891
2025-08-11 23:00 | 10.7172 | 0.02154% | 11.2221 | 11.7509 | 12.3046 | 12.8844 | 0.069435 | 0.52391 | 0.99981 | 1.4981
2025-08-12 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2025-08-12 01:00 | 9.8366 | 0.01977% | 10.3001 | 10.7854 | 11.2936 | 11.8258 | 0 | 0 | 0.1309 | 0.58828
2025-08-12 02:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-08-12 03:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2025-08-12 04:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-08-12 05:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-08-12 06:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-08-12 07:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-08-12 08:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-08-12 09:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-08-12 10:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-12 11:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-08-12 12:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-08-12 13:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-08-12 14:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-08-12 15:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-08-12 16:00 | 9.17 | 0.01843% | 9.602 | 10.0545 | 10.5282 | 11.0243 | 0 | 0 | 0 | 0
2025-08-12 17:00 | 9.5976 | 0.01929% | 10.0499 | 10.5234 | 11.0192 | 11.5385 | 0 | 0 | 0 | 0.34132
2025-08-12 18:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2025-08-12 19:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2025-08-12 20:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2025-08-12 21:00 | 10.4782 | 0.02106% | 10.9719 | 11.4888 | 12.0302 | 12.597 | 0 | 0.29868 | 0.76396 | 1.2512
2025-08-12 22:00 | 10.4782 | 0.02106% | 10.9719 | 11.4888 | 12.0302 | 12.597 | 0 | 0.29868 | 0.76396 | 1.2512
2025-08-12 23:00 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2025-08-13 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-08-13 01:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-08-13 02:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2025-08-13 03:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-08-13 04:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-08-13 05:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-08-13 06:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-08-13 07:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-08-13 08:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-08-13 09:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-08-13 10:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-08-13 11:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-08-13 12:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-08-13 13:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-08-13 14:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-08-13 15:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-08-13 16:00 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2025-08-13 17:00 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2025-08-13 18:00 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2025-08-13 19:00 | 9.3586 | 0.01881% | 9.7996 | 10.2613 | 10.7448 | 11.2511 | 0 | 0 | 0 | 0.094364
2025-08-13 20:00 | 9.5725 | 0.01924% | 10.0235 | 10.4958 | 10.9904 | 11.5082 | 0 | 0 | 0 | 0.31533
2025-08-13 21:00 | 10.0631 | 0.02023% | 10.5372 | 11.0337 | 11.5536 | 12.098 | 0 | 0 | 0.35434 | 0.82224
2025-08-13 22:00 | 10.0631 | 0.02023% | 10.5372 | 11.0337 | 11.5536 | 12.098 | 0 | 0 | 0.35434 | 0.82224
2025-08-13 23:00 | 9.8744 | 0.01985% | 10.3396 | 10.8268 | 11.337 | 11.8712 | 0 | 0 | 0.16814 | 0.62727
2025-08-14 | 9.3461 | 0.01878% | 9.7864 | 10.2476 | 10.7304 | 11.236 | 0 | 0 | 0 | 0.081366
2025-08-14 01:00 | 9.0567 | 0.0182% | 9.4835 | 9.9303 | 10.3982 | 10.8882 | 0 | 0 | 0 | 0
2025-08-14 02:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2025-08-14 03:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-08-14 04:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-08-14 05:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-08-14 06:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-14 07:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-08-14 08:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-14 09:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-14 10:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-08-14 11:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-14 12:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-08-14 13:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-08-14 14:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-08-14 15:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-08-14 16:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-08-14 17:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-08-14 18:00 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2025-08-14 19:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-08-14 20:00 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-08-14 21:00 | 9.2454 | 0.01858% | 9.6811 | 10.1372 | 10.6149 | 11.115 | 0 | 0 | 0 | 0
2025-08-14 22:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-08-14 23:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-08-15 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2025-08-15 01:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2025-08-15 02:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-08-15 03:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-08-15 04:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-08-15 05:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-08-15 06:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-08-15 07:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-08-15 08:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-08-15 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-08-15 10:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-08-15 11:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-08-15 12:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-08-15 13:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-08-15 14:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-08-15 15:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-08-15 16:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-08-15 17:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-08-15 18:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2025-08-15 19:00 | 8.7674 | 0.01762% | 9.1805 | 9.6131 | 10.0661 | 10.5404 | 0 | 0 | 0 | 0
2025-08-15 20:00 | 8.8932 | 0.01787% | 9.3123 | 9.751 | 10.2105 | 10.6916 | 0 | 0 | 0 | 0
2025-08-15 21:00 | 9.1825 | 0.01846% | 9.6152 | 10.0683 | 10.5427 | 11.0394 | 0 | 0 | 0 | 0
2025-08-15 22:00 | 9.5725 | 0.01924% | 10.0235 | 10.4958 | 10.9904 | 11.5082 | 0 | 0 | 0 | 0.31533
2025-08-15 23:00 | 9.3461 | 0.01878% | 9.7864 | 10.2476 | 10.7304 | 11.236 | 0 | 0 | 0 | 0.081366
2025-08-16 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2025-08-16 01:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-08-16 02:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-08-16 03:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-08-16 04:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-08-16 05:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-08-16 06:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-08-16 07:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-08-16 08:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-08-16 09:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-08-16 10:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-08-16 11:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-08-16 12:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-16 13:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-08-16 14:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-08-16 15:00 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-08-16 16:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-08-16 17:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-08-16 18:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2025-08-16 19:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-08-16 20:00 | 9.1825 | 0.01846% | 9.6152 | 10.0683 | 10.5427 | 11.0394 | 0 | 0 | 0 | 0
2025-08-16 21:00 | 9.17 | 0.01843% | 9.602 | 10.0545 | 10.5282 | 11.0243 | 0 | 0 | 0 | 0
2025-08-16 22:00 | 9.17 | 0.01843% | 9.602 | 10.0545 | 10.5282 | 11.0243 | 0 | 0 | 0 | 0
2025-08-16 23:00 | 9.17 | 0.01843% | 9.602 | 10.0545 | 10.5282 | 11.0243 | 0 | 0 | 0 | 0
2025-08-17 | 8.8932 | 0.01787% | 9.3123 | 9.751 | 10.2105 | 10.6916 | 0 | 0 | 0 | 0
2025-08-17 01:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-08-17 02:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-08-17 03:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-08-17 04:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-08-17 05:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-08-17 06:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-08-17 07:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-08-17 08:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-17 09:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-08-17 10:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-08-17 11:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-08-17 12:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-17 13:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-17 14:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-08-17 15:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-08-17 16:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-08-17 17:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-08-17 18:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-08-17 19:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-08-17 20:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-08-17 21:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-08-17 22:00 | 8.1511 | 0.01638% | 8.5351 | 8.9373 | 9.3584 | 9.7994 | 0 | 0 | 0 | 0
2025-08-17 23:00 | 8.1511 | 0.01638% | 8.5351 | 8.9373 | 9.3584 | 9.7994 | 0 | 0 | 0 | 0
2025-08-18 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-08-18 01:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-08-18 02:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-08-18 03:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-08-18 04:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-08-18 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-08-18 06:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-08-18 07:00 | 3.5472 | 0.007129% | 3.7144 | 3.8894 | 4.0726 | 4.2645 | 0 | 0 | 0 | 0
2025-08-18 08:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-08-18 09:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-08-18 10:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-08-18 11:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-08-18 12:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-08-18 13:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-08-18 14:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-08-18 15:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-08-18 16:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-08-18 17:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-08-18 18:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-08-18 19:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-08-18 20:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-08-18 21:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-08-18 22:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-08-18 23:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-08-19 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-08-19 01:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-08-19 02:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-08-19 03:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-08-19 04:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-08-19 05:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-08-19 06:00 | 3.5724 | 0.00718% | 3.7407 | 3.917 | 4.1015 | 4.2948 | 0 | 0 | 0 | 0
2025-08-19 07:00 | 3.3963 | 0.006826% | 3.5563 | 3.7239 | 3.8993 | 4.0831 | 0 | 0 | 0 | 0
2025-08-19 08:00 | 3.2579 | 0.006548% | 3.4114 | 3.5722 | 3.7405 | 3.9167 | 0 | 0 | 0 | 0
2025-08-19 09:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-08-19 10:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-08-19 11:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-19 12:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-19 13:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-08-19 14:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-08-19 15:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-08-19 16:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-08-19 17:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-08-19 18:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-08-19 19:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-08-19 20:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-08-19 21:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-08-19 22:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-08-19 23:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-08-20 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-08-20 01:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-08-20 02:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-08-20 03:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-08-20 04:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-08-20 05:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-08-20 06:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-20 07:00 | 3.3963 | 0.006826% | 3.5563 | 3.7239 | 3.8993 | 4.0831 | 0 | 0 | 0 | 0
2025-08-20 08:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-08-20 09:00 | 3.2453 | 0.006523% | 3.3982 | 3.5584 | 3.726 | 3.9016 | 0 | 0 | 0 | 0
2025-08-20 10:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-08-20 11:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-08-20 12:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-08-20 13:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-08-20 14:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-08-20 15:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-08-20 16:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-08-20 17:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-08-20 18:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-20 19:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-20 20:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-20 21:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-08-20 22:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-08-20 23:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-08-21 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-08-21 01:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-08-21 02:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-08-21 03:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-08-21 04:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-08-21 05:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-08-21 06:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-21 07:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-08-21 08:00 | 3.2202 | 0.006472% | 3.3719 | 3.5308 | 3.6972 | 3.8714 | 0 | 0 | 0 | 0
2025-08-21 09:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-08-21 10:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-08-21 11:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-21 12:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-08-21 13:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-08-21 14:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-08-21 15:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-08-21 16:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-08-21 17:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-21 18:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-08-21 19:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-08-21 20:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-08-21 21:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-08-21 22:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-08-21 23:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-08-22 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-08-22 01:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-08-22 02:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-08-22 03:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-08-22 04:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-08-22 05:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-08-22 06:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-22 07:00 | 3.434 | 0.006902% | 3.5958 | 3.7653 | 3.9427 | 4.1284 | 0 | 0 | 0 | 0
2025-08-22 08:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-08-22 09:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-08-22 10:00 | 3.3082 | 0.006649% | 3.4641 | 3.6273 | 3.7982 | 3.9772 | 0 | 0 | 0 | 0
2025-08-22 11:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-22 12:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-08-22 13:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-08-22 14:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-08-22 15:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-08-22 16:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-08-22 17:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-08-22 18:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-08-22 19:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-08-22 20:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-08-22 21:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-08-22 22:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2025-08-22 23:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2025-08-23 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-08-23 01:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-08-23 02:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-08-23 03:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-08-23 04:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-23 05:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-08-23 06:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-08-23 07:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-08-23 08:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-08-23 09:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-08-23 10:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-08-23 11:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-08-23 12:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-08-23 13:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-08-23 14:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-08-23 15:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-08-23 16:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-08-23 17:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-08-23 18:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-08-23 19:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-08-23 20:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-08-23 21:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-08-23 22:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-08-23 23:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-08-24 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-08-24 01:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-08-24 02:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-08-24 03:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-08-24 04:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-08-24 05:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-08-24 06:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-08-24 07:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-08-24 08:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-08-24 09:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-08-24 10:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-08-24 11:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-08-24 12:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-08-24 13:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-08-24 14:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-24 15:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-08-24 16:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-08-24 17:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-08-24 18:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-08-24 19:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-08-24 20:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-08-24 21:00 | 7.9247 | 0.01593% | 8.2981 | 8.689 | 9.0985 | 9.5272 | 0 | 0 | 0 | 0
2025-08-24 22:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-08-24 23:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-08-25 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-08-25 01:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-08-25 02:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-08-25 03:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-08-25 04:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-08-25 05:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-08-25 06:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-08-25 07:00 | 3.673 | 0.007382% | 3.8461 | 4.0273 | 4.2171 | 4.4158 | 0 | 0 | 0 | 0
2025-08-25 08:00 | 3.5095 | 0.007054% | 3.6749 | 3.848 | 4.0293 | 4.2192 | 0 | 0 | 0 | 0
2025-08-25 09:00 | 3.2831 | 0.006599% | 3.4378 | 3.5997 | 3.7694 | 3.947 | 0 | 0 | 0 | 0
2025-08-25 10:00 | 3.346 | 0.006725% | 3.5036 | 3.6687 | 3.8416 | 4.0226 | 0 | 0 | 0 | 0
2025-08-25 11:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-08-25 12:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-08-25 13:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-08-25 14:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-08-25 15:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-08-25 16:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-08-25 17:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-08-25 18:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-08-25 19:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-08-25 20:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-08-25 21:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-08-25 22:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-08-25 23:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-08-26 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-08-26 01:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-08-26 02:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-08-26 03:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-08-26 04:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-08-26 05:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-08-26 06:00 | 3.4214 | 0.006877% | 3.5827 | 3.7515 | 3.9282 | 4.1133 | 0 | 0 | 0 | 0
2025-08-26 07:00 | 3.1824 | 0.006396% | 3.3324 | 3.4894 | 3.6538 | 3.826 | 0 | 0 | 0 | 0
2025-08-26 08:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-08-26 09:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-08-26 10:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-08-26 11:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-08-26 12:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-08-26 13:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-08-26 14:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-08-26 15:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-08-26 16:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-08-26 17:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-08-26 18:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-08-26 19:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-26 20:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-08-26 21:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-08-26 22:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-08-26 23:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-08-27 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-08-27 01:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-08-27 02:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-08-27 03:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-08-27 04:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-08-27 05:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-08-27 06:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-08-27 07:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-08-27 08:00 | 3.0567 | 0.006143% | 3.2007 | 3.3515 | 3.5094 | 3.6748 | 0 | 0 | 0 | 0
2025-08-27 09:00 | 2.9434 | 0.005916% | 3.0821 | 3.2274 | 3.3794 | 3.5387 | 0 | 0 | 0 | 0
2025-08-27 10:00 | 3.1321 | 0.006295% | 3.2797 | 3.4342 | 3.5961 | 3.7655 | 0 | 0 | 0 | 0
2025-08-27 11:00 | 3.4466 | 0.006927% | 3.609 | 3.779 | 3.9571 | 4.1436 | 0 | 0 | 0 | 0
2025-08-27 12:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-08-27 13:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-08-27 14:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-08-27 15:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-08-27 16:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-08-27 17:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-08-27 18:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-08-27 19:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-27 20:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-08-27 21:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-08-27 22:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-08-27 23:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-08-28 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-08-28 01:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-08-28 02:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-08-28 03:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-28 04:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-08-28 05:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-08-28 06:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-08-28 07:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-08-28 08:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-08-28 09:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-08-28 10:00 | 3.0567 | 0.006143% | 3.2007 | 3.3515 | 3.5094 | 3.6748 | 0 | 0 | 0 | 0
2025-08-28 11:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-08-28 12:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-08-28 13:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-08-28 14:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-08-28 15:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-08-28 16:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-08-28 17:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-08-28 18:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-08-28 19:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-08-28 20:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-08-28 21:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-08-28 22:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-08-28 23:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-08-29 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-08-29 01:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-08-29 02:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-08-29 03:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-08-29 04:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-08-29 05:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-08-29 06:00 | 3.3208 | 0.006674% | 3.4773 | 3.6411 | 3.8127 | 3.9923 | 0 | 0 | 0 | 0
2025-08-29 07:00 | 3.0944 | 0.006219% | 3.2402 | 3.3929 | 3.5527 | 3.7201 | 0 | 0 | 0 | 0
2025-08-29 08:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-08-29 09:00 | 2.9057 | 0.00584% | 3.0426 | 3.186 | 3.3361 | 3.4933 | 0 | 0 | 0 | 0
2025-08-29 10:00 | 3.0441 | 0.006118% | 3.1875 | 3.3377 | 3.495 | 3.6596 | 0 | 0 | 0 | 0
2025-08-29 11:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-08-29 12:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-08-29 13:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-08-29 14:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-08-29 15:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-08-29 16:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-08-29 17:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-08-29 18:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-08-29 19:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-08-29 20:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-08-29 21:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-08-29 22:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-08-29 23:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-08-30 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-08-30 01:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-08-30 02:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-08-30 03:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-08-30 04:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-08-30 05:00 | 3.5975 | 0.007231% | 3.7671 | 3.9446 | 4.1304 | 4.325 | 0 | 0 | 0 | 0
2025-08-30 06:00 | 3.2328 | 0.006497% | 3.3851 | 3.5446 | 3.7116 | 3.8865 | 0 | 0 | 0 | 0
2025-08-30 07:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-08-30 08:00 | 2.9812 | 0.005992% | 3.1216 | 3.2687 | 3.4228 | 3.584 | 0 | 0 | 0 | 0
2025-08-30 09:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-08-30 10:00 | 2.9434 | 0.005916% | 3.0821 | 3.2274 | 3.3794 | 3.5387 | 0 | 0 | 0 | 0
2025-08-30 11:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-08-30 12:00 | 3.3585 | 0.00675% | 3.5168 | 3.6825 | 3.856 | 4.0377 | 0 | 0 | 0 | 0
2025-08-30 13:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-30 14:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-08-30 15:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-08-30 16:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-08-30 17:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-08-30 18:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-08-30 19:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-08-30 20:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-08-30 21:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-08-30 22:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-08-30 23:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-08-31 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-08-31 01:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-08-31 02:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-08-31 03:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-08-31 04:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-08-31 05:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-08-31 06:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-08-31 07:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-08-31 08:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-08-31 09:00 | 2.868 | 0.005764% | 3.0031 | 3.1446 | 3.2928 | 3.4479 | 0 | 0 | 0 | 0
2025-08-31 10:00 | 2.9309 | 0.005891% | 3.069 | 3.2136 | 3.365 | 3.5235 | 0 | 0 | 0 | 0
2025-08-31 11:00 | 3.0189 | 0.006068% | 3.1612 | 3.3101 | 3.4661 | 3.6294 | 0 | 0 | 0 | 0
2025-08-31 12:00 | 3.2956 | 0.006624% | 3.4509 | 3.6135 | 3.7838 | 3.9621 | 0 | 0 | 0 | 0
2025-08-31 13:00 | 3.6982 | 0.007433% | 3.8724 | 4.0549 | 4.2459 | 4.446 | 0 | 0 | 0 | 0
2025-08-31 14:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-08-31 15:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-08-31 16:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-08-31 17:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-08-31 18:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-08-31 19:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-08-31 20:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-08-31 21:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-08-31 22:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-08-31 23:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-09-01 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-09-01 01:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-09-01 02:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-09-01 03:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-09-01 04:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-09-01 05:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-01 06:00 | 3.4089 | 0.006851% | 3.5695 | 3.7377 | 3.9138 | 4.0982 | 0 | 0 | 0 | 0
2025-09-01 07:00 | 3.1195 | 0.00627% | 3.2665 | 3.4204 | 3.5816 | 3.7504 | 0 | 0 | 0 | 0
2025-09-01 08:00 | 2.9938 | 0.006017% | 3.1348 | 3.2825 | 3.4372 | 3.5992 | 0 | 0 | 0 | 0
2025-09-01 09:00 | 2.9183 | 0.005865% | 3.0558 | 3.1998 | 3.3505 | 3.5084 | 0 | 0 | 0 | 0
2025-09-01 10:00 | 2.9686 | 0.005966% | 3.1085 | 3.2549 | 3.4083 | 3.5689 | 0 | 0 | 0 | 0
2025-09-01 11:00 | 3.1699 | 0.006371% | 3.3192 | 3.4756 | 3.6394 | 3.8109 | 0 | 0 | 0 | 0
2025-09-01 12:00 | 3.4969 | 0.007028% | 3.6617 | 3.8342 | 4.0149 | 4.2041 | 0 | 0 | 0 | 0
2025-09-01 13:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-01 14:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-09-01 15:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-09-01 16:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-09-01 17:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-09-01 18:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-09-01 19:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-09-01 20:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-09-01 21:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-09-01 22:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-09-01 23:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-09-02 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-09-02 01:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-02 02:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-09-02 03:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-09-02 04:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-09-02 05:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-02 06:00 | 3.3837 | 0.006801% | 3.5431 | 3.7101 | 3.8849 | 4.0679 | 0 | 0 | 0 | 0
2025-09-02 07:00 | 3.107 | 0.006245% | 3.2534 | 3.4067 | 3.5672 | 3.7353 | 0 | 0 | 0 | 0
2025-09-02 08:00 | 2.956 | 0.005941% | 3.0953 | 3.2412 | 3.3939 | 3.5538 | 0 | 0 | 0 | 0
2025-09-02 09:00 | 2.9183 | 0.005865% | 3.0558 | 3.1998 | 3.3505 | 3.5084 | 0 | 0 | 0 | 0
2025-09-02 10:00 | 3.1573 | 0.006346% | 3.306 | 3.4618 | 3.6249 | 3.7957 | 0 | 0 | 0 | 0
2025-09-02 11:00 | 3.6101 | 0.007256% | 3.7802 | 3.9583 | 4.1449 | 4.3402 | 0 | 0 | 0 | 0
2025-09-02 12:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-02 13:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-09-02 14:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-09-02 15:00 | 9.6731 | 0.01944% | 10.1289 | 10.6062 | 11.1059 | 11.6292 | 0 | 0 | 0 | 0.41931
2025-09-02 16:00 | 10.5662 | 0.02124% | 11.0641 | 11.5854 | 12.1313 | 12.7029 | 0 | 0.38166 | 0.85085 | 1.3422
2025-09-02 17:00 | 11.2958 | 0.0227% | 11.828 | 12.3853 | 12.9689 | 13.58 | 0.5902 | 1.0692 | 1.5708 | 2.096
2025-09-02 18:00 | 12.0631 | 0.02425% | 12.6315 | 13.2267 | 13.8499 | 14.5025 | 1.2808 | 1.7923 | 2.328 | 2.8889
2025-09-02 19:00 | 12.4279 | 0.02498% | 13.0135 | 13.6266 | 14.2687 | 14.941 | 1.6091 | 2.1361 | 2.688 | 3.2658
2025-09-02 20:00 | 12.843 | 0.02581% | 13.4481 | 14.0818 | 14.7453 | 15.4401 | 1.9827 | 2.5273 | 3.0976 | 3.6948
2025-09-02 21:00 | 13.7738 | 0.02768% | 14.4228 | 15.1024 | 15.814 | 16.5591 | 2.8204 | 3.4045 | 4.0161 | 4.6566
2025-09-02 22:00 | 14.8304 | 0.02981% | 15.5292 | 16.2609 | 17.0271 | 17.8294 | 3.7714 | 4.4003 | 5.0588 | 5.7484
2025-09-02 23:00 | 11.7612 | 0.02364% | 12.3154 | 12.8956 | 13.5033 | 14.1395 | 1.0091 | 1.5078 | 2.0301 | 2.5769
2025-09-03 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2025-09-03 01:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-09-03 02:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-09-03 03:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-09-03 04:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-09-03 05:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-09-03 06:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-09-03 07:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-09-03 08:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-03 09:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-09-03 10:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-09-03 11:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-09-03 12:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-09-03 13:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-09-03 14:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-09-03 15:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-09-03 16:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-09-03 17:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-03 18:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-09-03 19:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2025-09-03 20:00 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2025-09-03 21:00 | 9.2832 | 0.01866% | 9.7206 | 10.1786 | 10.6582 | 11.1604 | 0 | 0 | 0 | 0.016377
2025-09-03 22:00 | 9.8618 | 0.01982% | 10.3265 | 10.813 | 11.3225 | 11.856 | 0 | 0 | 0.15573 | 0.61428
2025-09-03 23:00 | 9.6857 | 0.01947% | 10.1421 | 10.6199 | 11.1203 | 11.6443 | 0 | 0 | 0 | 0.43231
2025-09-04 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2025-09-04 01:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-09-04 02:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2025-09-04 03:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-09-04 04:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-09-04 05:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-09-04 06:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-09-04 07:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-09-04 08:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-09-04 09:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-09-04 10:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-09-04 11:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-09-04 12:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-09-04 13:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-09-04 14:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-09-04 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-04 16:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-04 17:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-09-04 18:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-04 19:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-09-04 20:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-09-04 21:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-09-04 22:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-09-04 23:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-09-05 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-05 01:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-05 02:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-09-05 03:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-09-05 04:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-09-05 05:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-09-05 06:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-09-05 07:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-09-05 08:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-09-05 09:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-09-05 10:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-09-05 11:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-09-05 12:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-09-05 13:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-09-05 14:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-09-05 15:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-09-05 16:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-09-05 17:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-09-05 18:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-09-05 19:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-09-05 20:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-09-05 21:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-09-05 22:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-05 23:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-06 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-09-06 01:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-09-06 02:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-09-06 03:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-09-06 04:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-09-06 05:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-09-06 06:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-09-06 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-06 08:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-09-06 09:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-06 10:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-09-06 11:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-09-06 12:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-09-06 13:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-09-06 14:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-09-06 15:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-09-06 16:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-09-06 17:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-09-06 18:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-09-06 19:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-06 20:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-06 21:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-09-06 22:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-09-06 23:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-09-07 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-09-07 01:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-09-07 02:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-09-07 03:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-09-07 04:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-09-07 05:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-09-07 06:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-09-07 07:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-09-07 08:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-07 09:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-09-07 10:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-07 11:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-09-07 12:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-09-07 13:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-09-07 14:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-09-07 15:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-09-07 16:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-09-07 17:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-09-07 18:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-09-07 19:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-09-07 20:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-09-07 21:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-09-07 22:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-07 23:00 | 7.4215 | 0.01492% | 7.7712 | 8.1374 | 8.5208 | 8.9223 | 0 | 0 | 0 | 0
2025-09-08 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-09-08 01:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-09-08 02:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-09-08 03:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-09-08 04:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-09-08 05:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-09-08 06:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-09-08 07:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-08 08:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-09-08 09:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-09-08 10:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-09-08 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-09-08 12:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-09-08 13:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-09-08 14:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-09-08 15:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-09-08 16:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-09-08 17:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-09-08 18:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-09-08 19:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-09-08 20:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-09-08 21:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-08 22:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-09-08 23:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-09-09 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-09 01:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-09-09 02:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-09-09 03:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-09-09 04:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-09-09 05:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-09-09 06:00 | 4.1133 | 0.008267% | 4.3071 | 4.51 | 4.7225 | 4.9451 | 0 | 0 | 0 | 0
2025-09-09 07:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-09-09 08:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-09-09 09:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-09-09 10:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-09-09 11:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-09-09 12:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-09-09 13:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-09-09 14:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-09-09 15:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-09-09 16:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-09-09 17:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-09-09 18:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-09-09 19:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-09-09 20:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-09-09 21:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-09-09 22:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-09-09 23:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-09-10 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-09-10 01:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-09-10 02:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-09-10 03:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-09-10 04:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-09-10 05:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-09-10 06:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-09-10 07:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-10 08:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-10 09:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-10 10:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-09-10 11:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-09-10 12:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-09-10 13:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-09-10 14:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-09-10 15:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-09-10 16:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-09-10 17:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-09-10 18:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-09-10 19:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-09-10 20:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-09-10 21:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-09-10 22:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-09-10 23:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-09-11 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-09-11 01:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-09-11 02:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-09-11 03:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-09-11 04:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-09-11 05:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-09-11 06:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-09-11 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-11 08:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-09-11 09:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-11 10:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-09-11 11:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-09-11 12:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-09-11 13:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-09-11 14:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-09-11 15:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-09-11 16:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-11 17:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-09-11 18:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-09-11 19:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-09-11 20:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-09-11 21:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2025-09-11 22:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-09-11 23:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2025-09-12 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-09-12 01:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-09-12 02:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-09-12 03:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-12 04:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-09-12 05:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-09-12 06:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-09-12 07:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-09-12 08:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-09-12 09:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-09-12 10:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-12 11:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-09-12 12:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-09-12 13:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-09-12 14:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-09-12 15:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-09-12 16:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-09-12 17:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-09-12 18:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-09-12 19:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-12 20:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-09-12 21:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-09-12 22:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-09-12 23:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-09-13 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-09-13 01:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-09-13 02:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-09-13 03:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-09-13 04:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-09-13 05:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-09-13 06:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-09-13 07:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-09-13 08:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-13 09:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-09-13 10:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-13 11:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-09-13 12:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-09-13 13:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-09-13 14:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-09-13 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-13 16:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-09-13 17:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-13 18:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-09-13 19:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-09-13 20:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-13 21:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-09-13 22:00 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-09-13 23:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-09-14 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-09-14 01:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-09-14 02:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-09-14 03:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-09-14 04:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-09-14 05:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-09-14 06:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-09-14 07:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-09-14 08:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-09-14 09:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-09-14 10:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-14 11:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-09-14 12:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-09-14 13:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-09-14 14:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-09-14 15:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-09-14 16:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-09-14 17:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-09-14 18:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2025-09-14 19:00 | 8.7674 | 0.01762% | 9.1805 | 9.6131 | 10.0661 | 10.5404 | 0 | 0 | 0 | 0
2025-09-14 20:00 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2025-09-14 21:00 | 9.1448 | 0.01838% | 9.5757 | 10.0269 | 10.4993 | 10.994 | 0 | 0 | 0 | 0
2025-09-14 22:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-09-14 23:00 | 9.5096 | 0.01911% | 9.9577 | 10.4269 | 10.9182 | 11.4326 | 0 | 0 | 0 | 0.25034
2025-09-15 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-09-15 01:00 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2025-09-15 02:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-09-15 03:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-15 04:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-09-15 05:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-09-15 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-09-15 07:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-09-15 08:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-15 09:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-09-15 10:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-15 11:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-09-15 12:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-09-15 13:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-09-15 14:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-09-15 15:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-15 16:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-09-15 17:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-09-15 18:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-09-15 19:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-09-15 20:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-09-15 21:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2025-09-15 22:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-09-15 23:00 | 8.9813 | 0.01805% | 9.4045 | 9.8476 | 10.3116 | 10.7975 | 0 | 0 | 0 | 0
2025-09-16 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2025-09-16 01:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2025-09-16 02:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-09-16 03:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-16 04:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-09-16 05:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-09-16 06:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-09-16 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-16 08:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-09-16 09:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-09-16 10:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-16 11:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-09-16 12:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-09-16 13:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-09-16 14:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-09-16 15:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-09-16 16:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-09-16 17:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-09-16 18:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-09-16 19:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-09-16 20:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-09-16 21:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2025-09-16 22:00 | 9.3083 | 0.01871% | 9.7469 | 10.2062 | 10.6871 | 11.1906 | 0 | 0 | 0 | 0.042373
2025-09-16 23:00 | 9.1448 | 0.01838% | 9.5757 | 10.0269 | 10.4993 | 10.994 | 0 | 0 | 0 | 0
2025-09-17 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2025-09-17 01:00 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2025-09-17 02:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-09-17 03:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-09-17 04:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-09-17 05:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-09-17 06:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-09-17 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-17 08:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-09-17 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-17 10:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-09-17 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-09-17 12:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-09-17 13:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-09-17 14:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-09-17 15:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-17 16:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-09-17 17:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-09-17 18:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-09-17 19:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-09-17 20:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2025-09-17 21:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-09-17 22:00 | 9.1071 | 0.0183% | 9.5362 | 9.9855 | 10.456 | 10.9487 | 0 | 0 | 0 | 0
2025-09-17 23:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2025-09-18 | 8.5033 | 0.01709% | 8.9039 | 9.3235 | 9.7628 | 10.2228 | 0 | 0 | 0 | 0
2025-09-18 01:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2025-09-18 02:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-09-18 03:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-09-18 04:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-09-18 05:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-09-18 06:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-09-18 07:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-09-18 08:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-09-18 09:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-09-18 10:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-09-18 11:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-09-18 12:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-09-18 13:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-09-18 14:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-09-18 15:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-09-18 16:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-09-18 17:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-09-18 18:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-09-18 19:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-09-18 20:00 | 8.9687 | 0.01803% | 9.3913 | 9.8338 | 10.2971 | 10.7823 | 0 | 0 | 0 | 0
2025-09-18 21:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-09-18 22:00 | 9.648 | 0.01939% | 10.1025 | 10.5786 | 11.077 | 11.5989 | 0 | 0 | 0 | 0.39331
2025-09-18 23:00 | 9.5851 | 0.01926% | 10.0367 | 10.5096 | 11.0048 | 11.5233 | 0 | 0 | 0 | 0.32832
2025-09-19 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2025-09-19 01:00 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2025-09-19 02:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2025-09-19 03:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-09-19 04:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-09-19 05:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-09-19 06:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-09-19 07:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-09-19 08:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-09-19 09:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-09-19 10:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-09-19 11:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-09-19 12:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-09-19 13:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-09-19 14:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-09-19 15:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-09-19 16:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-09-19 17:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-09-19 18:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-09-19 19:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-09-19 20:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-09-19 21:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-09-19 22:00 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2025-09-19 23:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2025-09-20 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-20 01:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-09-20 02:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-20 03:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-09-20 04:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-09-20 05:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-09-20 06:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-09-20 07:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-09-20 08:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-20 09:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-09-20 10:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-09-20 11:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-09-20 12:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-09-20 13:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-09-20 14:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-09-20 15:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-09-20 16:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-09-20 17:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-09-20 18:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-09-20 19:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-09-20 20:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-20 21:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-20 22:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-09-20 23:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-09-21 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-09-21 01:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-09-21 02:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-09-21 03:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-09-21 04:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-09-21 05:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-09-21 06:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-09-21 07:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-09-21 08:00 | 3.7359 | 0.007509% | 3.9119 | 4.0963 | 4.2893 | 4.4914 | 0 | 0 | 0 | 0
2025-09-21 09:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-09-21 10:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-09-21 11:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-21 12:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-09-21 13:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-09-21 14:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-09-21 15:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-09-21 16:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-09-21 17:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-09-21 18:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-09-21 19:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-09-21 20:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-09-21 21:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-09-21 22:00 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2025-09-21 23:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-09-22 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2025-09-22 01:00 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2025-09-22 02:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-09-22 03:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-09-22 04:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-09-22 05:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-09-22 06:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-09-22 07:00 | 4.3523 | 0.008747% | 4.5573 | 4.7721 | 4.9969 | 5.2324 | 0 | 0 | 0 | 0
2025-09-22 08:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-09-22 09:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-09-22 10:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-09-22 11:00 | 4.9686 | 0.009986% | 5.2027 | 5.4479 | 5.7046 | 5.9734 | 0 | 0 | 0 | 0
2025-09-22 12:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-09-22 13:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-09-22 14:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-09-22 15:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-09-22 16:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-09-22 17:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-09-22 18:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-09-22 19:00 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-09-22 20:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-09-22 21:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-09-22 22:00 | 9.0567 | 0.0182% | 9.4835 | 9.9303 | 10.3982 | 10.8882 | 0 | 0 | 0 | 0
2025-09-22 23:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-09-23 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-09-23 01:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-09-23 02:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-09-23 03:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-09-23 04:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-09-23 05:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-09-23 06:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-09-23 07:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-09-23 08:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-09-23 09:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-09-23 10:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-09-23 11:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-09-23 12:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-09-23 13:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-09-23 14:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-09-23 15:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-09-23 16:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-09-23 17:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2025-09-23 18:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2025-09-23 19:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2025-09-23 20:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2025-09-23 21:00 | 9.4215 | 0.01894% | 9.8655 | 10.3303 | 10.8171 | 11.3267 | 0 | 0 | 0 | 0.15935
2025-09-23 22:00 | 9.7234 | 0.01954% | 10.1816 | 10.6613 | 11.1637 | 11.6897 | 0 | 0 | 0.019188 | 0.4713
2025-09-23 23:00 | 9.497 | 0.01909% | 9.9445 | 10.4131 | 10.9037 | 11.4175 | 0 | 0 | 0 | 0.23734
2025-09-24 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2025-09-24 01:00 | 9.1574 | 0.01841% | 9.5889 | 10.0407 | 10.5138 | 11.0092 | 0 | 0 | 0 | 0
2025-09-24 02:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-09-24 03:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-09-24 04:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-09-24 05:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-09-24 06:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-09-24 07:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-09-24 08:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-09-24 09:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-09-24 10:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-09-24 11:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-09-24 12:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-09-24 13:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-09-24 14:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-09-24 15:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-09-24 16:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-09-24 17:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-24 18:00 | 8.1511 | 0.01638% | 8.5351 | 8.9373 | 9.3584 | 9.7994 | 0 | 0 | 0 | 0
2025-09-24 19:00 | 8.0127 | 0.0161% | 8.3903 | 8.7856 | 9.1996 | 9.633 | 0 | 0 | 0 | 0
2025-09-24 20:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-09-24 21:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2025-09-24 22:00 | 8.7297 | 0.01755% | 9.141 | 9.5717 | 10.0227 | 10.495 | 0 | 0 | 0 | 0
2025-09-24 23:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-09-25 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-09-25 01:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-09-25 02:00 | 8.0127 | 0.0161% | 8.3903 | 8.7856 | 9.1996 | 9.633 | 0 | 0 | 0 | 0
2025-09-25 03:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-09-25 04:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-09-25 05:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-09-25 06:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-09-25 07:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-09-25 08:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-09-25 09:00 | 4.1259 | 0.008292% | 4.3203 | 4.5238 | 4.737 | 4.9602 | 0 | 0 | 0 | 0
2025-09-25 10:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-09-25 11:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-09-25 12:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-09-25 13:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-09-25 14:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-09-25 15:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-09-25 16:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-09-25 17:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-09-25 18:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-09-25 19:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-09-25 20:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-09-25 21:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-09-25 22:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-09-25 23:00 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-09-26 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2025-09-26 01:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-09-26 02:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-26 03:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-09-26 04:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-09-26 05:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-09-26 06:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-09-26 07:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-09-26 08:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-09-26 09:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-26 10:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-09-26 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-09-26 12:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-09-26 13:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-09-26 14:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-09-26 15:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-09-26 16:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-09-26 17:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-09-26 18:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-09-26 19:00 | 7.975 | 0.01603% | 8.3507 | 8.7442 | 9.1562 | 9.5877 | 0 | 0 | 0 | 0
2025-09-26 20:00 | 8.1008 | 0.01628% | 8.4825 | 8.8821 | 9.3006 | 9.7389 | 0 | 0 | 0 | 0
2025-09-26 21:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-09-26 22:00 | 8.6542 | 0.01739% | 9.062 | 9.489 | 9.9361 | 10.4043 | 0 | 0 | 0 | 0
2025-09-26 23:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2025-09-27 | 7.8366 | 0.01575% | 8.2059 | 8.5925 | 8.9974 | 9.4213 | 0 | 0 | 0 | 0
2025-09-27 01:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-09-27 02:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-09-27 03:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-09-27 04:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-09-27 05:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-09-27 06:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-09-27 07:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-09-27 08:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-09-27 09:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-09-27 10:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-09-27 11:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-09-27 12:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-09-27 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-09-27 14:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-09-27 15:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-09-27 16:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-09-27 17:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-09-27 18:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-09-27 19:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-09-27 20:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-09-27 21:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2025-09-27 22:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-09-27 23:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-09-28 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-09-28 01:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-09-28 02:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-09-28 03:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-09-28 04:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-09-28 05:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-09-28 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-09-28 07:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-09-28 08:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-09-28 09:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-09-28 10:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-09-28 11:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-28 12:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-09-28 13:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-09-28 14:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-09-28 15:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-09-28 16:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-09-28 17:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-09-28 18:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-09-28 19:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2025-09-28 20:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-09-28 21:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2025-09-28 22:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2025-09-28 23:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2025-09-29 | 8.5033 | 0.01709% | 8.9039 | 9.3235 | 9.7628 | 10.2228 | 0 | 0 | 0 | 0
2025-09-29 01:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-09-29 02:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-09-29 03:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-09-29 04:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-09-29 05:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-09-29 06:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-09-29 07:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-09-29 08:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-09-29 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-09-29 10:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-09-29 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-09-29 12:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-09-29 13:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-09-29 14:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-09-29 15:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-09-29 16:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-09-29 17:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-09-29 18:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-09-29 19:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-09-29 20:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2025-09-29 21:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2025-09-29 22:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2025-09-29 23:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-09-30 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2025-09-30 01:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2025-09-30 02:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-09-30 03:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-09-30 04:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-09-30 05:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-09-30 06:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-09-30 07:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-09-30 08:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-09-30 09:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-09-30 10:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-09-30 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-09-30 12:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-09-30 13:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-09-30 14:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-09-30 15:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-09-30 16:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-09-30 17:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-09-30 18:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-09-30 19:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-09-30 20:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-09-30 21:00 | 8.1133 | 0.01631% | 8.4956 | 8.8959 | 9.3151 | 9.754 | 0 | 0 | 0 | 0
2025-09-30 22:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-09-30 23:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2025-10-01 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2025-10-01 01:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-10-01 02:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-10-01 03:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-10-01 04:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-10-01 05:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-10-01 06:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-10-01 07:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-10-01 08:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-10-01 09:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-10-01 10:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-10-01 11:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-10-01 12:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-10-01 13:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-10-01 14:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-10-01 15:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-10-01 16:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-10-01 17:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-01 18:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-01 19:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-01 20:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-10-01 21:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-10-01 22:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-10-01 23:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-10-02 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-10-02 01:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-10-02 02:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-10-02 03:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-02 04:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-10-02 05:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-10-02 06:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-10-02 07:00 | 3.7485 | 0.007534% | 3.9251 | 4.1101 | 4.3037 | 4.5065 | 0 | 0 | 0 | 0
2025-10-02 08:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-10-02 09:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-10-02 10:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-10-02 11:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-10-02 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-10-02 13:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-10-02 14:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-10-02 15:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-10-02 16:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-02 17:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-02 18:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-02 19:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-02 20:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-10-02 21:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-10-02 22:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-10-02 23:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-03 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-03 01:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-10-03 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-03 03:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-10-03 04:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-10-03 05:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-10-03 06:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-10-03 07:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-10-03 08:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-10-03 09:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-10-03 10:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-03 11:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-10-03 12:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-10-03 13:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-10-03 14:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-10-03 15:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-10-03 16:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-03 17:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-10-03 18:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-03 19:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-10-03 20:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-10-03 21:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-10-03 22:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-10-03 23:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-10-04 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-10-04 01:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-10-04 02:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-10-04 03:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-10-04 04:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-10-04 05:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-10-04 06:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-10-04 07:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-10-04 08:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-10-04 09:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-10-04 10:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-10-04 11:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-10-04 12:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-10-04 13:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-10-04 14:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-10-04 15:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-10-04 16:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-10-04 17:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-10-04 18:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-10-04 19:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-10-04 20:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-10-04 21:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2025-10-04 22:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2025-10-04 23:00 | 8.1133 | 0.01631% | 8.4956 | 8.8959 | 9.3151 | 9.754 | 0 | 0 | 0 | 0
2025-10-05 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2025-10-05 01:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-10-05 02:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-10-05 03:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-05 04:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-05 05:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-10-05 06:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-10-05 07:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-10-05 08:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-10-05 09:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-10-05 10:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-10-05 11:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-05 12:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-10-05 13:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-10-05 14:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-10-05 15:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-10-05 16:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-10-05 17:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-10-05 18:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-10-05 19:00 | 8.6794 | 0.01744% | 9.0883 | 9.5166 | 9.965 | 10.4345 | 0 | 0 | 0 | 0
2025-10-05 20:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2025-10-05 21:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-10-05 22:00 | 9.6857 | 0.01947% | 10.1421 | 10.6199 | 11.1203 | 11.6443 | 0 | 0 | 0 | 0.43231
2025-10-05 23:00 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2025-10-06 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2025-10-06 01:00 | 8.6794 | 0.01744% | 9.0883 | 9.5166 | 9.965 | 10.4345 | 0 | 0 | 0 | 0
2025-10-06 02:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-10-06 03:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-10-06 04:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-06 05:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-10-06 06:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-10-06 07:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-10-06 08:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-10-06 09:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-10-06 10:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-10-06 11:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-10-06 12:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-10-06 13:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-10-06 14:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-06 15:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-06 16:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-10-06 17:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-10-06 18:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-10-06 19:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2025-10-06 20:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2025-10-06 21:00 | 9.0064 | 0.0181% | 9.4308 | 9.8752 | 10.3405 | 10.8277 | 0 | 0 | 0 | 0
2025-10-06 22:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-10-06 23:00 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2025-10-07 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2025-10-07 01:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-10-07 02:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2025-10-07 03:00 | 7.4341 | 0.01494% | 7.7844 | 8.1512 | 8.5352 | 8.9374 | 0 | 0 | 0 | 0
2025-10-07 04:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-10-07 05:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-10-07 06:00 | 4.6416 | 0.009329% | 4.8603 | 5.0893 | 5.3291 | 5.5802 | 0 | 0 | 0 | 0
2025-10-07 07:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-10-07 08:00 | 3.9497 | 0.007938% | 4.1359 | 4.3307 | 4.5348 | 4.7485 | 0 | 0 | 0 | 0
2025-10-07 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-10-07 10:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-10-07 11:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-10-07 12:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-10-07 13:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-07 14:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-07 15:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-10-07 16:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-10-07 17:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-10-07 18:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-10-07 19:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-10-07 20:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-10-07 21:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-10-07 22:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-10-07 23:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-10-08 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-10-08 01:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-10-08 02:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-10-08 03:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-10-08 04:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-10-08 05:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-10-08 06:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-10-08 07:00 | 3.8743 | 0.007787% | 4.0568 | 4.248 | 4.4481 | 4.6577 | 0 | 0 | 0 | 0
2025-10-08 08:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-10-08 09:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-10-08 10:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-10-08 11:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-10-08 12:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-10-08 13:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-10-08 14:00 | 5.3083 | 0.01067% | 5.5584 | 5.8203 | 6.0945 | 6.3817 | 0 | 0 | 0 | 0
2025-10-08 15:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-10-08 16:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-08 17:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-10-08 18:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-08 19:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-10-08 20:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-08 21:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-10-08 22:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-08 23:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-09 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-09 01:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-10-09 02:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-10-09 03:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-10-09 04:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-10-09 05:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-10-09 06:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-10-09 07:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-10-09 08:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-10-09 09:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-10-09 10:00 | 4.0126 | 0.008065% | 4.2017 | 4.3997 | 4.607 | 4.8241 | 0 | 0 | 0 | 0
2025-10-09 11:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-10-09 12:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-10-09 13:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-10-09 14:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-10-09 15:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-09 16:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-09 17:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-10-09 18:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-09 19:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-10-09 20:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-10-09 21:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-10-09 22:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-10-09 23:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-10-10 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-10-10 01:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2025-10-10 02:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-10-10 03:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-10 04:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-10-10 05:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-10-10 06:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-10-10 07:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-10-10 08:00 | 4.0378 | 0.008115% | 4.2281 | 4.4273 | 4.6359 | 4.8543 | 0 | 0 | 0 | 0
2025-10-10 09:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-10-10 10:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-10-10 11:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-10-10 12:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-10-10 13:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-10 14:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-10 15:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-10 16:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-10 17:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-10 18:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-10 19:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-10 20:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-10 21:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-10-10 22:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-10-10 23:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-10-11 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-10-11 01:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-10-11 02:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-10-11 03:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-10-11 04:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-10-11 05:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-10-11 06:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-10-11 07:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-10-11 08:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-10-11 09:00 | 3.7233 | 0.007483% | 3.8988 | 4.0825 | 4.2748 | 4.4763 | 0 | 0 | 0 | 0
2025-10-11 10:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-10-11 11:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-10-11 12:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-10-11 13:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-10-11 14:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-11 15:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-10-11 16:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-10-11 17:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-11 18:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-10-11 19:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-11 20:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-10-11 21:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-10-11 22:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-10-11 23:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-10-12 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-10-12 01:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-10-12 02:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-10-12 03:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-10-12 04:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-10-12 05:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-10-12 06:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-10-12 07:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-10-12 08:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-12 09:00 | 3.7611 | 0.007559% | 3.9383 | 4.1238 | 4.3182 | 4.5216 | 0 | 0 | 0 | 0
2025-10-12 10:00 | 3.8491 | 0.007736% | 4.0305 | 4.2204 | 4.4193 | 4.6275 | 0 | 0 | 0 | 0
2025-10-12 11:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-10-12 12:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-10-12 13:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-10-12 14:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-10-12 15:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2025-10-12 16:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-10-12 17:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-10-12 18:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-12 19:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-10-12 20:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-10-12 21:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-10-12 22:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-10-12 23:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-10-13 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-10-13 01:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-10-13 02:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-10-13 03:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-13 04:00 | 5.1951 | 0.01044% | 5.4398 | 5.6962 | 5.9645 | 6.2456 | 0 | 0 | 0 | 0
2025-10-13 05:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-10-13 06:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-10-13 07:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-13 08:00 | 3.7862 | 0.00761% | 3.9646 | 4.1514 | 4.347 | 4.5519 | 0 | 0 | 0 | 0
2025-10-13 09:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-10-13 10:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-10-13 11:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-10-13 12:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-10-13 13:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-10-13 14:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-10-13 15:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-10-13 16:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-10-13 17:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-10-13 18:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-10-13 19:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-13 20:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-10-13 21:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-10-13 22:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-10-13 23:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-10-14 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-10-14 01:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-10-14 02:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-10-14 03:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-10-14 04:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-10-14 05:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-10-14 06:00 | 3.9623 | 0.007964% | 4.149 | 4.3445 | 4.5492 | 4.7636 | 0 | 0 | 0 | 0
2025-10-14 07:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-10-14 08:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-10-14 09:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-10-14 10:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-14 11:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-10-14 12:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-10-14 13:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-10-14 14:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-10-14 15:00 | 5.434 | 0.01092% | 5.6901 | 5.9582 | 6.2389 | 6.5329 | 0 | 0 | 0 | 0
2025-10-14 16:00 | 5.5347 | 0.01112% | 5.7955 | 6.0685 | 6.3545 | 6.6539 | 0 | 0 | 0 | 0
2025-10-14 17:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-10-14 18:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-14 19:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-10-14 20:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-10-14 21:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-10-14 22:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-10-14 23:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-10-15 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-10-15 01:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-10-15 02:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-10-15 03:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-15 04:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-10-15 05:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-10-15 06:00 | 4.0504 | 0.008141% | 4.2412 | 4.4411 | 4.6503 | 4.8694 | 0 | 0 | 0 | 0
2025-10-15 07:00 | 3.7736 | 0.007585% | 3.9515 | 4.1376 | 4.3326 | 4.5367 | 0 | 0 | 0 | 0
2025-10-15 08:00 | 3.6479 | 0.007332% | 3.8197 | 3.9997 | 4.1882 | 4.3855 | 0 | 0 | 0 | 0
2025-10-15 09:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-10-15 10:00 | 3.912 | 0.007863% | 4.0963 | 4.2894 | 4.4915 | 4.7031 | 0 | 0 | 0 | 0
2025-10-15 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-10-15 12:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-10-15 13:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-10-15 14:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-10-15 15:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-10-15 16:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-10-15 17:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-10-15 18:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-10-15 19:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-10-15 20:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-15 21:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-10-15 22:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-10-15 23:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-10-16 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-10-16 01:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-10-16 02:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-10-16 03:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-16 04:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-10-16 05:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-10-16 06:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-10-16 07:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-10-16 08:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-10-16 09:00 | 3.8365 | 0.007711% | 4.0173 | 4.2066 | 4.4048 | 4.6124 | 0 | 0 | 0 | 0
2025-10-16 10:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-10-16 11:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-10-16 12:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-10-16 13:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-16 14:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-16 15:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-16 16:00 | 5.6227 | 0.0113% | 5.8877 | 6.1651 | 6.4556 | 6.7598 | 0 | 0 | 0 | 0
2025-10-16 17:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-16 18:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-16 19:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-10-16 20:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-16 21:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-10-16 22:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-10-16 23:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-10-17 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-17 01:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-17 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-17 03:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-10-17 04:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-10-17 05:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-10-17 06:00 | 4.3648 | 0.008773% | 4.5705 | 4.7859 | 5.0114 | 5.2475 | 0 | 0 | 0 | 0
2025-10-17 07:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-10-17 08:00 | 3.9875 | 0.008014% | 4.1754 | 4.3721 | 4.5781 | 4.7938 | 0 | 0 | 0 | 0
2025-10-17 09:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-10-17 10:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-10-17 11:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-10-17 12:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-10-17 13:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-17 14:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-10-17 15:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-10-17 16:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-10-17 17:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-10-17 18:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-10-17 19:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-10-17 20:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-10-17 21:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-10-17 22:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-10-17 23:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-10-18 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-10-18 01:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-10-18 02:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-10-18 03:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-10-18 04:00 | 5.3334 | 0.01072% | 5.5847 | 5.8479 | 6.1234 | 6.4119 | 0 | 0 | 0 | 0
2025-10-18 05:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-10-18 06:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-10-18 07:00 | 4.1384 | 0.008318% | 4.3334 | 4.5376 | 4.7514 | 4.9753 | 0 | 0 | 0 | 0
2025-10-18 08:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-10-18 09:00 | 3.8114 | 0.00766% | 3.991 | 4.179 | 4.3759 | 4.5821 | 0 | 0 | 0 | 0
2025-10-18 10:00 | 3.824 | 0.007686% | 4.0041 | 4.1928 | 4.3904 | 4.5972 | 0 | 0 | 0 | 0
2025-10-18 11:00 | 4.0252 | 0.00809% | 4.2149 | 4.4135 | 4.6214 | 4.8392 | 0 | 0 | 0 | 0
2025-10-18 12:00 | 4.4906 | 0.009026% | 4.7022 | 4.9238 | 5.1558 | 5.3987 | 0 | 0 | 0 | 0
2025-10-18 13:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-10-18 14:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-10-18 15:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-10-18 16:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-10-18 17:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-18 18:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-18 19:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-10-18 20:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-10-18 21:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-10-18 22:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-10-18 23:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-10-19 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-10-19 01:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-10-19 02:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-19 03:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-10-19 04:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-10-19 05:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-10-19 06:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-10-19 07:00 | 3.9246 | 0.007888% | 4.1095 | 4.3031 | 4.5059 | 4.7182 | 0 | 0 | 0 | 0
2025-10-19 08:00 | 3.7108 | 0.007458% | 3.8856 | 4.0687 | 4.2604 | 4.4611 | 0 | 0 | 0 | 0
2025-10-19 09:00 | 3.6227 | 0.007281% | 3.7934 | 3.9721 | 4.1593 | 4.3553 | 0 | 0 | 0 | 0
2025-10-19 10:00 | 3.6353 | 0.007306% | 3.8066 | 3.9859 | 4.1737 | 4.3704 | 0 | 0 | 0 | 0
2025-10-19 11:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-10-19 12:00 | 4.151 | 0.008343% | 4.3466 | 4.5514 | 4.7659 | 4.9904 | 0 | 0 | 0 | 0
2025-10-19 13:00 | 4.7799 | 0.009607% | 5.0052 | 5.241 | 5.488 | 5.7465 | 0 | 0 | 0 | 0
2025-10-19 14:00 | 5.2831 | 0.01062% | 5.532 | 5.7927 | 6.0656 | 6.3514 | 0 | 0 | 0 | 0
2025-10-19 15:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-19 16:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-19 17:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-10-19 18:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-10-19 19:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-10-19 20:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-10-19 21:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-10-19 22:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-10-19 23:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-10-20 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-10-20 01:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-10-20 02:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-10-20 03:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-10-20 04:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-10-20 05:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-10-20 06:00 | 4.1887 | 0.008419% | 4.3861 | 4.5928 | 4.8092 | 5.0358 | 0 | 0 | 0 | 0
2025-10-20 07:00 | 3.7988 | 0.007635% | 3.9778 | 4.1652 | 4.3615 | 4.567 | 0 | 0 | 0 | 0
2025-10-20 08:00 | 3.585 | 0.007205% | 3.7539 | 3.9308 | 4.116 | 4.3099 | 0 | 0 | 0 | 0
2025-10-20 09:00 | 3.6604 | 0.007357% | 3.8329 | 4.0135 | 4.2026 | 4.4006 | 0 | 0 | 0 | 0
2025-10-20 10:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-10-20 11:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-10-20 12:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-10-20 13:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-10-20 14:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-20 15:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-20 16:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-10-20 17:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-10-20 18:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2025-10-20 19:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-20 20:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-10-20 21:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-10-20 22:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-20 23:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-10-21 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-10-21 01:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-10-21 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-21 03:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-10-21 04:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-10-21 05:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-10-21 06:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-10-21 07:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-10-21 08:00 | 3.8994 | 0.007837% | 4.0832 | 4.2756 | 4.477 | 4.688 | 0 | 0 | 0 | 0
2025-10-21 09:00 | 3.9372 | 0.007913% | 4.1227 | 4.3169 | 4.5203 | 4.7333 | 0 | 0 | 0 | 0
2025-10-21 10:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-10-21 11:00 | 4.9938 | 0.01004% | 5.2291 | 5.4755 | 5.7335 | 6.0036 | 0 | 0 | 0 | 0
2025-10-21 12:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-10-21 13:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-10-21 14:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-21 15:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-21 16:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-21 17:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-10-21 18:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-10-21 19:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-21 20:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-21 21:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-10-21 22:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-10-21 23:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-10-22 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-10-22 01:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-10-22 02:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-10-22 03:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-22 04:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-10-22 05:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-10-22 06:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-10-22 07:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-10-22 08:00 | 3.8869 | 0.007812% | 4.07 | 4.2618 | 4.4626 | 4.6728 | 0 | 0 | 0 | 0
2025-10-22 09:00 | 3.8617 | 0.007761% | 4.0437 | 4.2342 | 4.4337 | 4.6426 | 0 | 0 | 0 | 0
2025-10-22 10:00 | 4.2391 | 0.00852% | 4.4388 | 4.6479 | 4.867 | 5.0963 | 0 | 0 | 0 | 0
2025-10-22 11:00 | 4.7674 | 0.009582% | 4.992 | 5.2272 | 5.4735 | 5.7314 | 0 | 0 | 0 | 0
2025-10-22 12:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-10-22 13:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-10-22 14:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-10-22 15:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-22 16:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-10-22 17:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-22 18:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-10-22 19:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-10-22 20:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-22 21:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-10-22 22:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-10-22 23:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-10-23 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-10-23 01:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-10-23 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-23 03:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-23 04:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-10-23 05:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-10-23 06:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-10-23 07:00 | 4.0881 | 0.008217% | 4.2807 | 4.4824 | 4.6937 | 4.9148 | 0 | 0 | 0 | 0
2025-10-23 08:00 | 4.0001 | 0.00804% | 4.1885 | 4.3859 | 4.5926 | 4.809 | 0 | 0 | 0 | 0
2025-10-23 09:00 | 3.9749 | 0.007989% | 4.1622 | 4.3583 | 4.5637 | 4.7787 | 0 | 0 | 0 | 0
2025-10-23 10:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-10-23 11:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-10-23 12:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-10-23 13:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-23 14:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-10-23 15:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-10-23 16:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-23 17:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-10-23 18:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-23 19:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-10-23 20:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-23 21:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-10-23 22:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-10-23 23:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-10-24 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-10-24 01:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-10-24 02:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-10-24 03:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-10-24 04:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-10-24 05:00 | 4.7045 | 0.009455% | 4.9261 | 5.1583 | 5.4013 | 5.6558 | 0 | 0 | 0 | 0
2025-10-24 06:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-10-24 07:00 | 4.2139 | 0.008469% | 4.4125 | 4.6204 | 4.8381 | 5.066 | 0 | 0 | 0 | 0
2025-10-24 08:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-10-24 09:00 | 4.0755 | 0.008191% | 4.2676 | 4.4687 | 4.6792 | 4.8997 | 0 | 0 | 0 | 0
2025-10-24 10:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-10-24 11:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-10-24 12:00 | 5.3208 | 0.01069% | 5.5715 | 5.8341 | 6.109 | 6.3968 | 0 | 0 | 0 | 0
2025-10-24 13:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-24 14:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-10-24 15:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-10-24 16:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-10-24 17:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-24 18:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-10-24 19:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-10-24 20:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-10-24 21:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-10-24 22:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-10-24 23:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-10-25 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2025-10-25 01:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-10-25 02:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-10-25 03:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-10-25 04:00 | 5.4089 | 0.01087% | 5.6637 | 5.9306 | 6.2101 | 6.5027 | 0 | 0 | 0 | 0
2025-10-25 05:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-10-25 06:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-10-25 07:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-10-25 08:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-10-25 09:00 | 4.1636 | 0.008368% | 4.3598 | 4.5652 | 4.7803 | 5.0055 | 0 | 0 | 0 | 0
2025-10-25 10:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-10-25 11:00 | 4.541 | 0.009127% | 4.7549 | 4.979 | 5.2136 | 5.4592 | 0 | 0 | 0 | 0
2025-10-25 12:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-10-25 13:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-10-25 14:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-10-25 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-10-25 16:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-10-25 17:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-10-25 18:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-10-25 19:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-10-25 20:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-10-25 21:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-10-25 22:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-10-25 23:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-26 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-10-26 01:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-10-26 02:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-10-26 03:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-10-26 04:00 | 5.5724 | 0.0112% | 5.835 | 6.1099 | 6.3978 | 6.6993 | 0 | 0 | 0 | 0
2025-10-26 05:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-10-26 06:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-10-26 07:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-10-26 08:00 | 4.4026 | 0.008849% | 4.61 | 4.8272 | 5.0547 | 5.2929 | 0 | 0 | 0 | 0
2025-10-26 09:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-10-26 10:00 | 4.4277 | 0.008899% | 4.6364 | 4.8548 | 5.0836 | 5.3231 | 0 | 0 | 0 | 0
2025-10-26 11:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-10-26 12:00 | 5.1825 | 0.01042% | 5.4267 | 5.6824 | 5.9501 | 6.2305 | 0 | 0 | 0 | 0
2025-10-26 13:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-10-26 14:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-10-26 15:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-10-26 16:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-10-26 17:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-10-26 18:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-10-26 19:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-10-26 20:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-10-26 21:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-10-26 22:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-10-26 23:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-10-27 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-10-27 01:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-10-27 02:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-10-27 03:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-10-27 04:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-10-27 05:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-10-27 06:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-10-27 07:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-10-27 08:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-10-27 09:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-10-27 10:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-10-27 11:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-10-27 12:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-10-27 13:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-10-27 14:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-10-27 15:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-27 16:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-10-27 17:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-27 18:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2025-10-27 19:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2025-10-27 20:00 | 6.0881 | 0.01224% | 6.375 | 6.6754 | 6.9899 | 7.3193 | 0 | 0 | 0 | 0
2025-10-27 21:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2025-10-27 22:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-10-27 23:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-10-28 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-10-28 01:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-10-28 02:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2025-10-28 03:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-10-28 04:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-10-28 05:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-10-28 06:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-10-28 07:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-10-28 08:00 | 4.4781 | 0.009% | 4.6891 | 4.91 | 5.1414 | 5.3836 | 0 | 0 | 0 | 0
2025-10-28 09:00 | 4.4403 | 0.008924% | 4.6495 | 4.8686 | 5.098 | 5.3382 | 0 | 0 | 0 | 0
2025-10-28 10:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-10-28 11:00 | 5.3712 | 0.0108% | 5.6242 | 5.8892 | 6.1667 | 6.4573 | 0 | 0 | 0 | 0
2025-10-28 12:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-10-28 13:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-10-28 14:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-10-28 15:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-28 16:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-10-28 17:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-28 18:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-10-28 19:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-10-28 20:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-10-28 21:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-10-28 22:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-10-28 23:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-10-29 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-10-29 01:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-10-29 02:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-10-29 03:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-10-29 04:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-10-29 05:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-10-29 06:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-10-29 07:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-10-29 08:00 | 4.1762 | 0.008394% | 4.3729 | 4.579 | 4.7947 | 5.0207 | 0 | 0 | 0 | 0
2025-10-29 09:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-10-29 10:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-10-29 11:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-10-29 12:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-10-29 13:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-10-29 14:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-29 15:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-10-29 16:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-10-29 17:00 | 5.824 | 0.01171% | 6.0984 | 6.3858 | 6.6866 | 7.0017 | 0 | 0 | 0 | 0
2025-10-29 18:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-10-29 19:00 | 5.6982 | 0.01145% | 5.9667 | 6.2478 | 6.5422 | 6.8505 | 0 | 0 | 0 | 0
2025-10-29 20:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-10-29 21:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-10-29 22:00 | 7.107 | 0.01428% | 7.4419 | 7.7926 | 8.1597 | 8.5442 | 0 | 0 | 0 | 0
2025-10-29 23:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2025-10-30 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-10-30 01:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-10-30 02:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-10-30 03:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-10-30 04:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-30 05:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-10-30 06:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-10-30 07:00 | 4.2013 | 0.008444% | 4.3993 | 4.6066 | 4.8236 | 5.0509 | 0 | 0 | 0 | 0
2025-10-30 08:00 | 4.063 | 0.008166% | 4.2544 | 4.4549 | 4.6648 | 4.8846 | 0 | 0 | 0 | 0
2025-10-30 09:00 | 4.1007 | 0.008242% | 4.2939 | 4.4962 | 4.7081 | 4.9299 | 0 | 0 | 0 | 0
2025-10-30 10:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-10-30 11:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-10-30 12:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-10-30 13:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-10-30 14:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-10-30 15:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-10-30 16:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-10-30 17:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-10-30 18:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-10-30 19:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-10-30 20:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-10-30 21:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-10-30 22:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-10-30 23:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-10-31 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-10-31 01:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-10-31 02:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-10-31 03:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-10-31 04:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-10-31 05:00 | 5.0441 | 0.01014% | 5.2818 | 5.5306 | 5.7912 | 6.0641 | 0 | 0 | 0 | 0
2025-10-31 06:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-10-31 07:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-10-31 08:00 | 4.2768 | 0.008596% | 4.4783 | 4.6893 | 4.9103 | 5.1416 | 0 | 0 | 0 | 0
2025-10-31 09:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-10-31 10:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-10-31 11:00 | 5.2705 | 0.01059% | 5.5189 | 5.7789 | 6.0512 | 6.3363 | 0 | 0 | 0 | 0
2025-10-31 12:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-10-31 13:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-10-31 14:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-10-31 15:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-10-31 16:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-10-31 17:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-10-31 18:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-10-31 19:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-10-31 20:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2025-10-31 21:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2025-10-31 22:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-10-31 23:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-11-01 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-11-01 01:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-11-01 02:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-01 03:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-01 04:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-11-01 05:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-11-01 06:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-11-01 07:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-11-01 08:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-11-01 09:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-11-01 10:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-11-01 11:00 | 4.629 | 0.009304% | 4.8471 | 5.0755 | 5.3147 | 5.5651 | 0 | 0 | 0 | 0
2025-11-01 12:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-11-01 13:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-11-01 14:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-11-01 15:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-11-01 16:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-11-01 17:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-11-01 18:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-11-01 19:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-11-01 20:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-11-01 21:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-11-01 22:00 | 7.1825 | 0.01444% | 7.5209 | 7.8753 | 8.2464 | 8.6349 | 0 | 0 | 0 | 0
2025-11-01 23:00 | 7.4089 | 0.01489% | 7.758 | 8.1236 | 8.5063 | 8.9071 | 0 | 0 | 0 | 0
2025-11-02 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-11-02 01:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-11-02 02:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-11-02 03:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2025-11-02 04:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-11-02 06:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2025-11-02 07:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-11-02 08:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-11-02 09:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-11-02 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-11-02 11:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-11-02 12:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-11-02 13:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-11-02 14:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-11-02 15:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-02 16:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-11-02 17:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-11-02 18:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-11-02 19:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-02 20:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-11-02 21:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-11-02 22:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-11-02 23:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-11-03 | 8.1008 | 0.01628% | 8.4825 | 8.8821 | 9.3006 | 9.7389 | 0 | 0 | 0 | 0
2025-11-03 01:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-11-03 02:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-11-03 03:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-03 04:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-11-03 05:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-11-03 06:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-11-03 07:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-11-03 08:00 | 4.39 | 0.008823% | 4.5969 | 4.8135 | 5.0403 | 5.2777 | 0 | 0 | 0 | 0
2025-11-03 09:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-11-03 10:00 | 4.3774 | 0.008798% | 4.5837 | 4.7997 | 5.0258 | 5.2626 | 0 | 0 | 0 | 0
2025-11-03 11:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-11-03 12:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-11-03 13:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-11-03 14:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-11-03 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-11-03 16:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-03 17:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2025-11-03 18:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-03 19:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-11-03 20:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2025-11-03 21:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-11-03 22:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-11-03 23:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2025-11-04 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-11-04 01:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-11-04 02:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-11-04 03:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-11-04 04:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-11-04 05:00 | 5.4592 | 0.01097% | 5.7164 | 5.9858 | 6.2678 | 6.5632 | 0 | 0 | 0 | 0
2025-11-04 06:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-11-04 07:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-11-04 08:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-11-04 09:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-11-04 10:00 | 4.3145 | 0.008672% | 4.5178 | 4.7307 | 4.9536 | 5.187 | 0 | 0 | 0 | 0
2025-11-04 11:00 | 4.8806 | 0.009809% | 5.1105 | 5.3513 | 5.6035 | 5.8675 | 0 | 0 | 0 | 0
2025-11-04 12:00 | 5.4844 | 0.01102% | 5.7428 | 6.0134 | 6.2967 | 6.5934 | 0 | 0 | 0 | 0
2025-11-04 13:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-11-04 14:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-04 15:00 | 5.7737 | 0.0116% | 6.0457 | 6.3306 | 6.6289 | 6.9412 | 0 | 0 | 0 | 0
2025-11-04 16:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2025-11-04 17:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2025-11-04 18:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-11-04 19:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-11-04 20:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-11-04 21:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-11-04 22:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-11-04 23:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-11-05 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2025-11-05 01:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-11-05 02:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-11-05 03:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-11-05 04:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-05 05:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-11-05 06:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-11-05 07:00 | 4.5284 | 0.009101% | 4.7417 | 4.9652 | 5.1991 | 5.4441 | 0 | 0 | 0 | 0
2025-11-05 08:00 | 4.2894 | 0.008621% | 4.4915 | 4.7031 | 4.9247 | 5.1568 | 0 | 0 | 0 | 0
2025-11-05 09:00 | 4.2642 | 0.00857% | 4.4651 | 4.6755 | 4.8958 | 5.1265 | 0 | 0 | 0 | 0
2025-11-05 10:00 | 4.2265 | 0.008495% | 4.4256 | 4.6342 | 4.8525 | 5.0812 | 0 | 0 | 0 | 0
2025-11-05 11:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-11-05 12:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-11-05 13:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-11-05 14:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-11-05 15:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2025-11-05 16:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-05 17:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-11-05 18:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-11-05 19:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-11-05 20:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-11-05 21:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-11-05 22:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2025-11-05 23:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-11-06 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-11-06 01:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-11-06 02:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-11-06 03:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-11-06 04:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-06 05:00 | 5.4718 | 0.011% | 5.7296 | 5.9996 | 6.2823 | 6.5783 | 0 | 0 | 0 | 0
2025-11-06 06:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-11-06 07:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-11-06 08:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-11-06 09:00 | 4.3271 | 0.008697% | 4.531 | 4.7445 | 4.968 | 5.2021 | 0 | 0 | 0 | 0
2025-11-06 10:00 | 4.3397 | 0.008722% | 4.5442 | 4.7583 | 4.9825 | 5.2173 | 0 | 0 | 0 | 0
2025-11-06 11:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-11-06 12:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-11-06 13:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-11-06 14:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-11-06 15:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-06 16:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-11-06 17:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-11-06 18:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-06 19:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-11-06 20:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-11-06 21:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2025-11-06 22:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2025-11-06 23:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2025-11-07 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-11-07 01:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-11-07 02:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-11-07 03:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-11-07 04:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-11-07 05:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2025-11-07 06:00 | 5.346 | 0.01074% | 5.5979 | 5.8617 | 6.1379 | 6.4271 | 0 | 0 | 0 | 0
2025-11-07 07:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-11-07 08:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-11-07 09:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-11-07 10:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-11-07 11:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-11-07 12:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-11-07 13:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2025-11-07 14:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-11-07 15:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-11-07 16:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-11-07 17:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-07 18:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-11-07 19:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-11-07 20:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-07 21:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-11-07 22:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-11-07 23:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-11-08 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-11-08 01:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-11-08 02:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2025-11-08 03:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2025-11-08 04:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-11-08 05:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2025-11-08 06:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-11-08 07:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-11-08 08:00 | 4.4655 | 0.008975% | 4.6759 | 4.8962 | 5.1269 | 5.3685 | 0 | 0 | 0 | 0
2025-11-08 09:00 | 4.302 | 0.008646% | 4.5047 | 4.7169 | 4.9392 | 5.1719 | 0 | 0 | 0 | 0
2025-11-08 10:00 | 4.2516 | 0.008545% | 4.452 | 4.6617 | 4.8814 | 5.1114 | 0 | 0 | 0 | 0
2025-11-08 11:00 | 4.4152 | 0.008874% | 4.6232 | 4.841 | 5.0691 | 5.308 | 0 | 0 | 0 | 0
2025-11-08 12:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-11-08 13:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-11-08 14:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2025-11-08 15:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2025-11-08 16:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-11-08 17:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-08 18:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-11-08 19:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-11-08 20:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-11-08 21:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-11-08 22:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-08 23:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-11-09 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-11-09 01:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-11-09 02:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-11-09 03:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2025-11-09 04:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-11-09 05:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-11-09 06:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-11-09 07:00 | 4.9812 | 0.01001% | 5.2159 | 5.4617 | 5.719 | 5.9885 | 0 | 0 | 0 | 0
2025-11-09 08:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-11-09 09:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-11-09 10:00 | 4.6164 | 0.009278% | 4.8339 | 5.0617 | 5.3002 | 5.55 | 0 | 0 | 0 | 0
2025-11-09 11:00 | 4.8051 | 0.009658% | 5.0315 | 5.2686 | 5.5168 | 5.7768 | 0 | 0 | 0 | 0
2025-11-09 12:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-11-09 13:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-11-09 14:00 | 6.2265 | 0.01251% | 6.5199 | 6.8271 | 7.1488 | 7.4856 | 0 | 0 | 0 | 0
2025-11-09 15:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-11-09 16:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-11-09 17:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-11-09 18:00 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2025-11-09 19:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2025-11-09 20:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-11-09 21:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2025-11-09 22:00 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2025-11-09 23:00 | 9.5599 | 0.01921% | 10.0103 | 10.482 | 10.9759 | 11.4931 | 0 | 0 | 0 | 0.30233
2025-11-10 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2025-11-10 01:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2025-11-10 02:00 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2025-11-10 03:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-11-10 04:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-11-10 05:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-11-10 06:00 | 5.673 | 0.0114% | 5.9404 | 6.2203 | 6.5133 | 6.8202 | 0 | 0 | 0 | 0
2025-11-10 07:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-10 08:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-11-10 09:00 | 5.0315 | 0.01011% | 5.2686 | 5.5169 | 5.7768 | 6.049 | 0 | 0 | 0 | 0
2025-11-10 10:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-11-10 11:00 | 5.5598 | 0.01117% | 5.8218 | 6.0961 | 6.3834 | 6.6841 | 0 | 0 | 0 | 0
2025-11-10 12:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-11-10 13:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-11-10 14:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-11-10 15:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-11-10 16:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2025-11-10 17:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-10 18:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-11-10 19:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-11-10 20:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-11-10 21:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2025-11-10 22:00 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2025-11-10 23:00 | 9.1448 | 0.01838% | 9.5757 | 10.0269 | 10.4993 | 10.994 | 0 | 0 | 0 | 0
2025-11-11 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2025-11-11 01:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2025-11-11 02:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2025-11-11 03:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-11-11 04:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-11-11 05:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-11-11 06:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-11-11 07:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-11-11 08:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-11-11 09:00 | 5.1573 | 0.01037% | 5.4003 | 5.6548 | 5.9212 | 6.2002 | 0 | 0 | 0 | 0
2025-11-11 10:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-11-11 11:00 | 5.6479 | 0.01135% | 5.914 | 6.1927 | 6.4845 | 6.79 | 0 | 0 | 0 | 0
2025-11-11 12:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-11 13:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2025-11-11 14:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-11-11 15:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-11 16:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-11 17:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-11-11 18:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-11-11 19:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-11-11 20:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-11 21:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2025-11-11 22:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-11-11 23:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2025-11-12 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2025-11-12 01:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2025-11-12 02:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-11-12 03:00 | 7.4844 | 0.01504% | 7.837 | 8.2063 | 8.593 | 8.9979 | 0 | 0 | 0 | 0
2025-11-12 04:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-11-12 05:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-11-12 06:00 | 5.5095 | 0.01107% | 5.7691 | 6.041 | 6.3256 | 6.6236 | 0 | 0 | 0 | 0
2025-11-12 07:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-11-12 08:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-11-12 09:00 | 4.7171 | 0.009481% | 4.9393 | 5.1721 | 5.4158 | 5.6709 | 0 | 0 | 0 | 0
2025-11-12 10:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-11-12 11:00 | 5.0818 | 0.01021% | 5.3213 | 5.572 | 5.8346 | 6.1095 | 0 | 0 | 0 | 0
2025-11-12 12:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-11-12 13:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-11-12 14:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-12 15:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-11-12 16:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-12 17:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-12 18:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2025-11-12 19:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-12 20:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2025-11-12 21:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-11-12 22:00 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2025-11-12 23:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2025-11-13 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-11-13 01:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-11-13 02:00 | 7.7234 | 0.01552% | 8.0873 | 8.4684 | 8.8674 | 9.2852 | 0 | 0 | 0 | 0
2025-11-13 03:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2025-11-13 04:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-13 05:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2025-11-13 06:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-13 07:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-11-13 08:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-11-13 09:00 | 4.5032 | 0.009051% | 4.7154 | 4.9376 | 5.1702 | 5.4139 | 0 | 0 | 0 | 0
2025-11-13 10:00 | 4.5787 | 0.009203% | 4.7944 | 5.0203 | 5.2569 | 5.5046 | 0 | 0 | 0 | 0
2025-11-13 11:00 | 4.9435 | 0.009936% | 5.1764 | 5.4203 | 5.6757 | 5.9431 | 0 | 0 | 0 | 0
2025-11-13 12:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-11-13 13:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-11-13 14:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-11-13 15:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-11-13 16:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2025-11-13 17:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-13 18:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-11-13 19:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-13 20:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-11-13 21:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-11-13 22:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2025-11-13 23:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2025-11-14 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2025-11-14 01:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2025-11-14 02:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-11-14 03:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-11-14 04:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-14 05:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-11-14 06:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-14 07:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-11-14 08:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-11-14 09:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-11-14 10:00 | 4.7296 | 0.009506% | 4.9525 | 5.1858 | 5.4302 | 5.6861 | 0 | 0 | 0 | 0
2025-11-14 11:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-11-14 12:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-11-14 13:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-14 14:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-14 15:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-14 16:00 | 6.2642 | 0.01259% | 6.5594 | 6.8685 | 7.1921 | 7.531 | 0 | 0 | 0 | 0
2025-11-14 17:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2025-11-14 18:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-11-14 19:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2025-11-14 20:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-11-14 21:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2025-11-14 22:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-11-14 23:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-11-15 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-11-15 01:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2025-11-15 02:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-11-15 03:00 | 7.2957 | 0.01466% | 7.6395 | 7.9994 | 8.3764 | 8.771 | 0 | 0 | 0 | 0
2025-11-15 04:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-15 05:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-11-15 06:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-11-15 07:00 | 5.2076 | 0.01047% | 5.453 | 5.7099 | 5.979 | 6.2607 | 0 | 0 | 0 | 0
2025-11-15 08:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-11-15 09:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-11-15 10:00 | 4.8303 | 0.009708% | 5.0579 | 5.2962 | 5.5457 | 5.807 | 0 | 0 | 0 | 0
2025-11-15 11:00 | 4.8177 | 0.009683% | 5.0447 | 5.2824 | 5.5313 | 5.7919 | 0 | 0 | 0 | 0
2025-11-15 12:00 | 5.1447 | 0.01034% | 5.3871 | 5.641 | 5.9068 | 6.1851 | 0 | 0 | 0 | 0
2025-11-15 13:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-11-15 14:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-11-15 15:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-15 16:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-11-15 17:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-11-15 18:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2025-11-15 19:00 | 7.3838 | 0.01484% | 7.7317 | 8.096 | 8.4775 | 8.8769 | 0 | 0 | 0 | 0
2025-11-15 20:00 | 7.3963 | 0.01487% | 7.7448 | 8.1098 | 8.4919 | 8.892 | 0 | 0 | 0 | 0
2025-11-15 21:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2025-11-15 22:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2025-11-15 23:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2025-11-16 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2025-11-16 01:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-11-16 02:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-16 03:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-11-16 04:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2025-11-16 05:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-11-16 06:00 | 5.3586 | 0.01077% | 5.6111 | 5.8754 | 6.1523 | 6.4422 | 0 | 0 | 0 | 0
2025-11-16 07:00 | 4.8428 | 0.009733% | 5.071 | 5.31 | 5.5602 | 5.8222 | 0 | 0 | 0 | 0
2025-11-16 08:00 | 4.6919 | 0.00943% | 4.913 | 5.1445 | 5.3869 | 5.6407 | 0 | 0 | 0 | 0
2025-11-16 09:00 | 4.5661 | 0.009177% | 4.7813 | 5.0065 | 5.2424 | 5.4895 | 0 | 0 | 0 | 0
2025-11-16 10:00 | 4.4529 | 0.00895% | 4.6627 | 4.8824 | 5.1125 | 5.3534 | 0 | 0 | 0 | 0
2025-11-16 11:00 | 4.6038 | 0.009253% | 4.8208 | 5.0479 | 5.2858 | 5.5348 | 0 | 0 | 0 | 0
2025-11-16 12:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-11-16 13:00 | 5.5473 | 0.01115% | 5.8086 | 6.0823 | 6.3689 | 6.669 | 0 | 0 | 0 | 0
2025-11-16 14:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-11-16 15:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-11-16 16:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-11-16 17:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-11-16 18:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-11-16 19:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-11-16 20:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2025-11-16 21:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-11-16 22:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2025-11-16 23:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-11-17 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2025-11-17 01:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2025-11-17 02:00 | 8.0882 | 0.01626% | 8.4693 | 8.8683 | 9.2862 | 9.7238 | 0 | 0 | 0 | 0
2025-11-17 03:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-11-17 04:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-11-17 05:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2025-11-17 06:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2025-11-17 07:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-11-17 08:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-11-17 09:00 | 4.868 | 0.009784% | 5.0974 | 5.3376 | 5.5891 | 5.8524 | 0 | 0 | 0 | 0
2025-11-17 10:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-11-17 11:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-11-17 12:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-11-17 13:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-11-17 14:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-11-17 15:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-11-17 16:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-11-17 17:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2025-11-17 18:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2025-11-17 19:00 | 7.2077 | 0.01449% | 7.5473 | 7.9029 | 8.2753 | 8.6652 | 0 | 0 | 0 | 0
2025-11-17 20:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2025-11-17 21:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2025-11-17 22:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2025-11-17 23:00 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2025-11-18 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2025-11-18 01:00 | 8.1637 | 0.01641% | 8.5483 | 8.9511 | 9.3729 | 9.8145 | 0 | 0 | 0 | 0
2025-11-18 02:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-11-18 03:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-11-18 04:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-11-18 05:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-18 06:00 | 5.6102 | 0.01128% | 5.8745 | 6.1513 | 6.4411 | 6.7446 | 0 | 0 | 0 | 0
2025-11-18 07:00 | 5.1196 | 0.01029% | 5.3608 | 5.6134 | 5.8779 | 6.1549 | 0 | 0 | 0 | 0
2025-11-18 08:00 | 4.8932 | 0.009835% | 5.1237 | 5.3651 | 5.6179 | 5.8826 | 0 | 0 | 0 | 0
2025-11-18 09:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-11-18 10:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-11-18 11:00 | 5.2328 | 0.01052% | 5.4793 | 5.7375 | 6.0079 | 6.291 | 0 | 0 | 0 | 0
2025-11-18 12:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-11-18 13:00 | 6.5536 | 0.01317% | 6.8624 | 7.1857 | 7.5243 | 7.8788 | 0 | 0 | 0 | 0
2025-11-18 14:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2025-11-18 15:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-18 16:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-11-18 17:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2025-11-18 18:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2025-11-18 19:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2025-11-18 20:00 | 6.7674 | 0.0136% | 7.0863 | 7.4202 | 7.7698 | 8.1359 | 0 | 0 | 0 | 0
2025-11-18 21:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2025-11-18 22:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-11-18 23:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-11-19 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2025-11-19 01:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-11-19 02:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2025-11-19 03:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-11-19 04:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-11-19 05:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2025-11-19 06:00 | 5.585 | 0.01123% | 5.8482 | 6.1237 | 6.4122 | 6.7144 | 0 | 0 | 0 | 0
2025-11-19 07:00 | 5.2579 | 0.01057% | 5.5057 | 5.7651 | 6.0368 | 6.3212 | 0 | 0 | 0 | 0
2025-11-19 08:00 | 5.0693 | 0.01019% | 5.3081 | 5.5582 | 5.8201 | 6.0944 | 0 | 0 | 0 | 0
2025-11-19 09:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-11-19 10:00 | 5.0944 | 0.01024% | 5.3345 | 5.5858 | 5.849 | 6.1246 | 0 | 0 | 0 | 0
2025-11-19 11:00 | 5.4466 | 0.01095% | 5.7033 | 5.972 | 6.2534 | 6.548 | 0 | 0 | 0 | 0
2025-11-19 12:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-19 13:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-11-19 14:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-11-19 15:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-19 16:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-11-19 17:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-19 18:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2025-11-19 19:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-11-19 20:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-19 21:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-19 22:00 | 7.7234 | 0.01552% | 8.0873 | 8.4684 | 8.8674 | 9.2852 | 0 | 0 | 0 | 0
2025-11-19 23:00 | 8.3272 | 0.01674% | 8.7195 | 9.1304 | 9.5606 | 10.0111 | 0 | 0 | 0 | 0
2025-11-20 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-11-20 01:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-11-20 02:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2025-11-20 03:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2025-11-20 04:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-20 05:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2025-11-20 06:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-11-20 07:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-11-20 08:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-11-20 09:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-11-20 10:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-11-20 11:00 | 5.2454 | 0.01054% | 5.4925 | 5.7513 | 6.0223 | 6.3061 | 0 | 0 | 0 | 0
2025-11-20 12:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-11-20 13:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2025-11-20 14:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2025-11-20 15:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-11-20 16:00 | 6.1888 | 0.01244% | 6.4804 | 6.7857 | 7.1055 | 7.4403 | 0 | 0 | 0 | 0
2025-11-20 17:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-11-20 18:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-11-20 19:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-11-20 20:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2025-11-20 21:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-20 22:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-11-20 23:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2025-11-21 | 8.0127 | 0.0161% | 8.3903 | 8.7856 | 9.1996 | 9.633 | 0 | 0 | 0 | 0
2025-11-21 01:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2025-11-21 02:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2025-11-21 03:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2025-11-21 04:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-11-21 05:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-11-21 06:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2025-11-21 07:00 | 5.0064 | 0.01006% | 5.2423 | 5.4893 | 5.7479 | 6.0188 | 0 | 0 | 0 | 0
2025-11-21 08:00 | 4.5913 | 0.009228% | 4.8076 | 5.0341 | 5.2713 | 5.5197 | 0 | 0 | 0 | 0
2025-11-21 09:00 | 4.5535 | 0.009152% | 4.7681 | 4.9928 | 5.228 | 5.4743 | 0 | 0 | 0 | 0
2025-11-21 10:00 | 4.5158 | 0.009076% | 4.7286 | 4.9514 | 5.1847 | 5.429 | 0 | 0 | 0 | 0
2025-11-21 11:00 | 4.9183 | 0.009885% | 5.1501 | 5.3927 | 5.6468 | 5.9129 | 0 | 0 | 0 | 0
2025-11-21 12:00 | 5.4969 | 0.01105% | 5.756 | 6.0272 | 6.3112 | 6.6085 | 0 | 0 | 0 | 0
2025-11-21 13:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2025-11-21 14:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-21 15:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2025-11-21 16:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2025-11-21 17:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2025-11-21 18:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2025-11-21 19:00 | 6.7422 | 0.01355% | 7.0599 | 7.3926 | 7.7409 | 8.1057 | 0 | 0 | 0 | 0
2025-11-21 20:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2025-11-21 21:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2025-11-21 22:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-11-21 23:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2025-11-22 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-11-22 01:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2025-11-22 02:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-11-22 03:00 | 7.2706 | 0.01461% | 7.6131 | 7.9719 | 8.3475 | 8.7408 | 0 | 0 | 0 | 0
2025-11-22 04:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2025-11-22 05:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2025-11-22 06:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-11-22 07:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-11-22 08:00 | 4.9561 | 0.009961% | 5.1896 | 5.4341 | 5.6901 | 5.9583 | 0 | 0 | 0 | 0
2025-11-22 09:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-11-22 10:00 | 4.6793 | 0.009405% | 4.8998 | 5.1307 | 5.3724 | 5.6256 | 0 | 0 | 0 | 0
2025-11-22 11:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-11-22 12:00 | 5.1322 | 0.01031% | 5.374 | 5.6272 | 5.8923 | 6.17 | 0 | 0 | 0 | 0
2025-11-22 13:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-11-22 14:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2025-11-22 15:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-11-22 16:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-11-22 17:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-11-22 18:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2025-11-22 19:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2025-11-22 20:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-11-22 21:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-11-22 22:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2025-11-22 23:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2025-11-23 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-11-23 01:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2025-11-23 02:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-11-23 03:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2025-11-23 04:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-11-23 05:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2025-11-23 06:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-11-23 07:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-11-23 08:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-11-23 09:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-11-23 10:00 | 4.7548 | 0.009556% | 4.9788 | 5.2134 | 5.4591 | 5.7163 | 0 | 0 | 0 | 0
2025-11-23 11:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-11-23 12:00 | 5.0567 | 0.01016% | 5.2949 | 5.5444 | 5.8057 | 6.0792 | 0 | 0 | 0 | 0
2025-11-23 13:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2025-11-23 14:00 | 6.0756 | 0.01221% | 6.3618 | 6.6616 | 6.9755 | 7.3042 | 0 | 0 | 0 | 0
2025-11-23 15:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-23 16:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-11-23 17:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2025-11-23 18:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-23 19:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2025-11-23 20:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2025-11-23 21:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-11-23 22:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-11-23 23:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2025-11-24 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2025-11-24 01:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2025-11-24 02:00 | 7.975 | 0.01603% | 8.3507 | 8.7442 | 9.1562 | 9.5877 | 0 | 0 | 0 | 0
2025-11-24 03:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2025-11-24 04:00 | 6.7171 | 0.0135% | 7.0336 | 7.365 | 7.712 | 8.0754 | 0 | 0 | 0 | 0
2025-11-24 05:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2025-11-24 06:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-24 07:00 | 4.9057 | 0.00986% | 5.1369 | 5.3789 | 5.6324 | 5.8978 | 0 | 0 | 0 | 0
2025-11-24 08:00 | 4.6667 | 0.009379% | 4.8866 | 5.1169 | 5.358 | 5.6104 | 0 | 0 | 0 | 0
2025-11-24 09:00 | 4.6542 | 0.009354% | 4.8735 | 5.1031 | 5.3435 | 5.5953 | 0 | 0 | 0 | 0
2025-11-24 10:00 | 4.7925 | 0.009632% | 5.0183 | 5.2548 | 5.5024 | 5.7617 | 0 | 0 | 0 | 0
2025-11-24 11:00 | 5.2957 | 0.01064% | 5.5452 | 5.8065 | 6.0801 | 6.3666 | 0 | 0 | 0 | 0
2025-11-24 12:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2025-11-24 13:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2025-11-24 14:00 | 6.5158 | 0.0131% | 6.8228 | 7.1443 | 7.481 | 7.8334 | 0 | 0 | 0 | 0
2025-11-24 15:00 | 6.4278 | 0.01292% | 6.7306 | 7.0478 | 7.3799 | 7.7276 | 0 | 0 | 0 | 0
2025-11-24 16:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2025-11-24 17:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-11-24 18:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2025-11-24 19:00 | 6.39 | 0.01284% | 6.6911 | 7.0064 | 7.3365 | 7.6822 | 0 | 0 | 0 | 0
2025-11-24 20:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2025-11-24 21:00 | 7.5096 | 0.01509% | 7.8634 | 8.2339 | 8.6219 | 9.0281 | 0 | 0 | 0 | 0
2025-11-24 22:00 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2025-11-24 23:00 | 9.5222 | 0.01914% | 9.9708 | 10.4406 | 10.9326 | 11.4477 | 0 | 0 | 0 | 0.26334
2025-11-25 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2025-11-25 01:00 | 8.9058 | 0.0179% | 9.3254 | 9.7648 | 10.2249 | 10.7067 | 0 | 0 | 0 | 0
2025-11-25 02:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2025-11-25 03:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2025-11-25 04:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-11-25 05:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-25 06:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2025-11-25 07:00 | 5.3837 | 0.01082% | 5.6374 | 5.903 | 6.1812 | 6.4724 | 0 | 0 | 0 | 0
2025-11-25 08:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-25 09:00 | 5.0189 | 0.01009% | 5.2554 | 5.5031 | 5.7624 | 6.0339 | 0 | 0 | 0 | 0
2025-11-25 10:00 | 5.1699 | 0.01039% | 5.4135 | 5.6686 | 5.9357 | 6.2153 | 0 | 0 | 0 | 0
2025-11-25 11:00 | 5.5221 | 0.0111% | 5.7823 | 6.0547 | 6.34 | 6.6388 | 0 | 0 | 0 | 0
2025-11-25 12:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2025-11-25 13:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2025-11-25 14:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2025-11-25 15:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2025-11-25 16:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-11-25 17:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2025-11-25 18:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-11-25 19:00 | 7.1573 | 0.01439% | 7.4946 | 7.8477 | 8.2175 | 8.6047 | 0 | 0 | 0 | 0
2025-11-25 20:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-11-25 21:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2025-11-25 22:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2025-11-25 23:00 | 9.1825 | 0.01846% | 9.6152 | 10.0683 | 10.5427 | 11.0394 | 0 | 0 | 0 | 0
2025-11-26 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2025-11-26 01:00 | 8.6794 | 0.01744% | 9.0883 | 9.5166 | 9.965 | 10.4345 | 0 | 0 | 0 | 0
2025-11-26 02:00 | 8.4026 | 0.01689% | 8.7986 | 9.2131 | 9.6473 | 10.1018 | 0 | 0 | 0 | 0
2025-11-26 03:00 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2025-11-26 04:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2025-11-26 05:00 | 6.1762 | 0.01241% | 6.4672 | 6.7719 | 7.091 | 7.4251 | 0 | 0 | 0 | 0
2025-11-26 06:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-11-26 07:00 | 5.107 | 0.01026% | 5.3476 | 5.5996 | 5.8635 | 6.1397 | 0 | 0 | 0 | 0
2025-11-26 08:00 | 4.9309 | 0.00991% | 5.1632 | 5.4065 | 5.6613 | 5.928 | 0 | 0 | 0 | 0
2025-11-26 09:00 | 4.7422 | 0.009531% | 4.9657 | 5.1996 | 5.4446 | 5.7012 | 0 | 0 | 0 | 0
2025-11-26 10:00 | 4.8554 | 0.009759% | 5.0842 | 5.3238 | 5.5746 | 5.8373 | 0 | 0 | 0 | 0
2025-11-26 11:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2025-11-26 12:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2025-11-26 13:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-26 14:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-26 15:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-26 16:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2025-11-26 17:00 | 6.8177 | 0.0137% | 7.139 | 7.4753 | 7.8276 | 8.1964 | 0 | 0 | 0 | 0
2025-11-26 18:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-11-26 19:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-11-26 20:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2025-11-26 21:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-11-26 22:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2025-11-26 23:00 | 9.4718 | 0.01904% | 9.9181 | 10.3855 | 10.8748 | 11.3872 | 0 | 0 | 0 | 0.21134
2025-11-27 | 19.95 | 0.0401% | 20.89 | 21.8743 | 22.905 | 23.9843 | 8.379 | 9.225 | 10.1109 | 11.0385
2025-11-27 01:00 | 16.5411 | 0.03325% | 17.3205 | 18.1367 | 18.9912 | 19.8861 | 5.311 | 6.0125 | 6.747 | 7.5161
2025-11-27 02:00 | 16.5915 | 0.03335% | 17.3732 | 18.1918 | 19.049 | 19.9466 | 5.3563 | 6.0599 | 6.7966 | 7.5681
2025-11-27 03:00 | 15.7738 | 0.0317% | 16.5171 | 17.2953 | 18.1103 | 18.9636 | 4.6205 | 5.2894 | 5.9898 | 6.7232
2025-11-27 04:00 | 14.4279 | 0.029% | 15.1077 | 15.8196 | 16.565 | 17.3455 | 3.4091 | 4.021 | 4.6616 | 5.3325
2025-11-27 05:00 | 12.7423 | 0.02561% | 13.3427 | 13.9714 | 14.6297 | 15.3191 | 1.8921 | 2.4325 | 2.9983 | 3.5908
2025-11-27 06:00 | 11.7486 | 0.02361% | 12.3022 | 12.8819 | 13.4888 | 14.1244 | 0.99775 | 1.496 | 2.0177 | 2.5639
2025-11-27 07:00 | 10.8807 | 0.02187% | 11.3934 | 11.9302 | 12.4923 | 13.081 | 0.21661 | 0.67802 | 1.1612 | 1.6671
2025-11-27 08:00 | 10.5033 | 0.02111% | 10.9982 | 11.5164 | 12.0591 | 12.6273 | 0 | 0.32239 | 0.78879 | 1.2772
2025-11-27 09:00 | 10.2266 | 0.02055% | 10.7084 | 11.213 | 11.7413 | 12.2946 | 0 | 0.061595 | 0.5157 | 0.99121
2025-11-27 10:00 | 10.2517 | 0.0206% | 10.7348 | 11.2406 | 11.7702 | 12.3248 | 0 | 0.085303 | 0.54053 | 1.0172
2025-11-27 11:00 | 10.9813 | 0.02207% | 11.4987 | 12.0405 | 12.6079 | 13.2019 | 0.30717 | 0.77286 | 1.2605 | 1.7711
2025-11-27 12:00 | 12.7298 | 0.02559% | 13.3296 | 13.9576 | 14.6153 | 15.304 | 1.8808 | 2.4206 | 2.9859 | 3.5778
2025-11-27 13:00 | 14.1889 | 0.02852% | 14.8575 | 15.5575 | 16.2906 | 17.0582 | 3.194 | 3.7957 | 4.4258 | 5.0855
2025-11-27 14:00 | 14.5537 | 0.02925% | 15.2394 | 15.9575 | 16.7094 | 17.4967 | 3.5223 | 4.1395 | 4.7857 | 5.4625
2025-11-27 15:00 | 14.9059 | 0.02996% | 15.6082 | 16.3437 | 17.1138 | 17.9201 | 3.8393 | 4.4714 | 5.1333 | 5.8264
2025-11-27 16:00 | 14.8807 | 0.02991% | 15.5819 | 16.3161 | 17.0849 | 17.8899 | 3.8167 | 4.4477 | 5.1085 | 5.8004
2025-11-27 17:00 | 14.9311 | 0.03001% | 15.6346 | 16.3713 | 17.1427 | 17.9504 | 3.8619 | 4.4951 | 5.1581 | 5.8524
2025-11-27 18:00 | 14.8178 | 0.02978% | 15.516 | 16.2471 | 17.0127 | 17.8143 | 3.7601 | 4.3884 | 5.0464 | 5.7354
2025-11-27 19:00 | 14.8933 | 0.02993% | 15.5951 | 16.3299 | 17.0993 | 17.905 | 3.828 | 4.4596 | 5.1209 | 5.8134
2025-11-27 20:00 | 15.1575 | 0.03046% | 15.8717 | 16.6195 | 17.4026 | 18.2226 | 4.0657 | 4.7085 | 5.3816 | 6.0864
2025-11-27 21:00 | 14.5788 | 0.0293% | 15.2658 | 15.9851 | 16.7383 | 17.527 | 3.545 | 4.1632 | 4.8106 | 5.4885
2025-11-27 22:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2025-11-27 23:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2025-11-28 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2025-11-28 01:00 | 9.3964 | 0.01889% | 9.8391 | 10.3027 | 10.7882 | 11.2965 | 0 | 0 | 0 | 0.13336
2025-11-28 02:00 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2025-11-28 03:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2025-11-28 04:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2025-11-28 05:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2025-11-28 06:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2025-11-28 07:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2025-11-28 08:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-11-28 09:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-11-28 10:00 | 5.6856 | 0.01143% | 5.9535 | 6.234 | 6.5278 | 6.8354 | 0 | 0 | 0 | 0
2025-11-28 11:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2025-11-28 12:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2025-11-28 13:00 | 7.3334 | 0.01474% | 7.679 | 8.0408 | 8.4197 | 8.8164 | 0 | 0 | 0 | 0
2025-11-28 14:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2025-11-28 15:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2025-11-28 16:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2025-11-28 17:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-11-28 18:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2025-11-28 19:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2025-11-28 20:00 | 8.214 | 0.01651% | 8.601 | 9.0063 | 9.4306 | 9.875 | 0 | 0 | 0 | 0
2025-11-28 21:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2025-11-28 22:00 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2025-11-28 23:00 | 9.7486 | 0.01959% | 10.2079 | 10.6889 | 11.1926 | 11.7199 | 0 | 0 | 0.044014 | 0.4973
2025-11-29 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2025-11-29 01:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2025-11-29 02:00 | 9.1448 | 0.01838% | 9.5757 | 10.0269 | 10.4993 | 10.994 | 0 | 0 | 0 | 0
2025-11-29 03:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2025-11-29 04:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2025-11-29 05:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2025-11-29 06:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2025-11-29 07:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2025-11-29 08:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2025-11-29 09:00 | 5.8114 | 0.01168% | 6.0852 | 6.372 | 6.6722 | 6.9866 | 0 | 0 | 0 | 0
2025-11-29 10:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2025-11-29 11:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2025-11-29 12:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2025-11-29 13:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2025-11-29 14:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2025-11-29 15:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2025-11-29 16:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2025-11-29 17:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2025-11-29 18:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2025-11-29 19:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-11-29 20:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2025-11-29 21:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2025-11-29 22:00 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2025-11-29 23:00 | 9.5976 | 0.01929% | 10.0499 | 10.5234 | 11.0192 | 11.5385 | 0 | 0 | 0 | 0.34132
2025-11-30 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2025-11-30 01:00 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2025-11-30 02:00 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2025-11-30 03:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2025-11-30 04:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2025-11-30 05:00 | 7.258 | 0.01459% | 7.6 | 7.9581 | 8.333 | 8.7257 | 0 | 0 | 0 | 0
2025-11-30 06:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2025-11-30 07:00 | 6.0504 | 0.01216% | 6.3355 | 6.634 | 6.9466 | 7.2739 | 0 | 0 | 0 | 0
2025-11-30 08:00 | 5.8366 | 0.01173% | 6.1116 | 6.3996 | 6.7011 | 7.0168 | 0 | 0 | 0 | 0
2025-11-30 09:00 | 5.7234 | 0.0115% | 5.993 | 6.2754 | 6.5711 | 6.8807 | 0 | 0 | 0 | 0
2025-11-30 10:00 | 5.6353 | 0.01133% | 5.9008 | 6.1789 | 6.47 | 6.7749 | 0 | 0 | 0 | 0
2025-11-30 11:00 | 5.6605 | 0.01138% | 5.9272 | 6.2065 | 6.4989 | 6.8051 | 0 | 0 | 0 | 0
2025-11-30 12:00 | 5.9875 | 0.01203% | 6.2696 | 6.5651 | 6.8744 | 7.1983 | 0 | 0 | 0 | 0
2025-11-30 13:00 | 6.629 | 0.01332% | 6.9414 | 7.2685 | 7.6109 | 7.9696 | 0 | 0 | 0 | 0
2025-11-30 14:00 | 7.0567 | 0.01418% | 7.3892 | 7.7374 | 8.102 | 8.4837 | 0 | 0 | 0 | 0
2025-11-30 15:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2025-11-30 16:00 | 8.2894 | 0.01666% | 8.68 | 9.089 | 9.5173 | 9.9657 | 0 | 0 | 0 | 0
2025-11-30 17:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2025-11-30 18:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-11-30 19:00 | 9.019 | 0.01813% | 9.444 | 9.889 | 10.3549 | 10.8428 | 0 | 0 | 0 | 0
2025-11-30 20:00 | 9.2454 | 0.01858% | 9.6811 | 10.1372 | 10.6149 | 11.115 | 0 | 0 | 0 | 0
2025-11-30 21:00 | 9.5599 | 0.01921% | 10.0103 | 10.482 | 10.9759 | 11.4931 | 0 | 0 | 0 | 0.30233
2025-11-30 22:00 | 10.3775 | 0.02086% | 10.8665 | 11.3785 | 11.9147 | 12.4761 | 0 | 0.20385 | 0.66466 | 1.1472
2025-11-30 23:00 | 10.5914 | 0.02129% | 11.0904 | 11.613 | 12.1602 | 12.7331 | 0 | 0.40537 | 0.87568 | 1.3681
2026-12-01 | 10.3901 | 0.02088% | 10.8797 | 11.3923 | 11.9291 | 12.4912 | 0 | 0.2157 | 0.67707 | 1.1602
2026-12-01 01:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2026-12-01 02:00 | 9.4341 | 0.01896% | 9.8786 | 10.3441 | 10.8315 | 11.3419 | 0 | 0 | 0 | 0.17235
2026-12-01 03:00 | 8.9058 | 0.0179% | 9.3254 | 9.7648 | 10.2249 | 10.7067 | 0 | 0 | 0 | 0
2026-12-01 04:00 | 8.3523 | 0.01679% | 8.7459 | 9.158 | 9.5895 | 10.0413 | 0 | 0 | 0 | 0
2026-12-01 05:00 | 7.2328 | 0.01454% | 7.5736 | 7.9305 | 8.3042 | 8.6954 | 0 | 0 | 0 | 0
2026-12-01 06:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2026-12-01 07:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2026-12-01 08:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2026-12-01 09:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2026-12-01 10:00 | 5.9246 | 0.01191% | 6.2038 | 6.4961 | 6.8022 | 7.1227 | 0 | 0 | 0 | 0
2026-12-01 11:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2026-12-01 12:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2026-12-01 13:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2026-12-01 14:00 | 7.8995 | 0.01588% | 8.2717 | 8.6615 | 9.0696 | 9.4969 | 0 | 0 | 0 | 0
2026-12-01 15:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2026-12-01 16:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2026-12-01 17:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2026-12-01 18:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2026-12-01 19:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2026-12-01 20:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-01 21:00 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2026-12-01 22:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-01 23:00 | 10.4656 | 0.02103% | 10.9587 | 11.4751 | 12.0157 | 12.5819 | 0 | 0.28683 | 0.75155 | 1.2382
2026-12-02 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2026-12-02 01:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-02 02:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-02 03:00 | 9.2832 | 0.01866% | 9.7206 | 10.1786 | 10.6582 | 11.1604 | 0 | 0 | 0 | 0.016377
2026-12-02 04:00 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2026-12-02 05:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2026-12-02 06:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2026-12-02 07:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2026-12-02 08:00 | 6.0127 | 0.01208% | 6.296 | 6.5926 | 6.9033 | 7.2285 | 0 | 0 | 0 | 0
2026-12-02 09:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2026-12-02 10:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2026-12-02 11:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2026-12-02 12:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2026-12-02 13:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2026-12-02 14:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2026-12-02 15:00 | 7.8114 | 0.0157% | 8.1795 | 8.5649 | 8.9685 | 9.3911 | 0 | 0 | 0 | 0
2026-12-02 16:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2026-12-02 17:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2026-12-02 18:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2026-12-02 19:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2026-12-02 20:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2026-12-02 21:00 | 8.1385 | 0.01636% | 8.522 | 8.9235 | 9.344 | 9.7843 | 0 | 0 | 0 | 0
2026-12-02 22:00 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2026-12-02 23:00 | 10.1763 | 0.02045% | 10.6558 | 11.1578 | 11.6836 | 12.2341 | 0 | 0.014177 | 0.46605 | 0.93922
2026-12-03 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-03 01:00 | 9.8241 | 0.01974% | 10.287 | 10.7717 | 11.2792 | 11.8107 | 0 | 0 | 0.11849 | 0.57528
2026-12-03 02:00 | 9.8618 | 0.01982% | 10.3265 | 10.813 | 11.3225 | 11.856 | 0 | 0 | 0.15573 | 0.61428
2026-12-03 03:00 | 9.3209 | 0.01873% | 9.7601 | 10.22 | 10.7015 | 11.2058 | 0 | 0 | 0 | 0.055371
2026-12-03 04:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2026-12-03 05:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2026-12-03 06:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2026-12-03 07:00 | 6.3271 | 0.01272% | 6.6253 | 6.9374 | 7.2643 | 7.6066 | 0 | 0 | 0 | 0
2026-12-03 08:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2026-12-03 09:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2026-12-03 10:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2026-12-03 11:00 | 6.6919 | 0.01345% | 7.0072 | 7.3374 | 7.6831 | 8.0452 | 0 | 0 | 0 | 0
2026-12-03 12:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2026-12-03 13:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-03 14:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-03 15:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-03 16:00 | 8.1133 | 0.01631% | 8.4956 | 8.8959 | 9.3151 | 9.754 | 0 | 0 | 0 | 0
2026-12-03 17:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2026-12-03 18:00 | 8.3272 | 0.01674% | 8.7195 | 9.1304 | 9.5606 | 10.0111 | 0 | 0 | 0 | 0
2026-12-03 19:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2026-12-03 20:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2026-12-03 21:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2026-12-03 22:00 | 9.7612 | 0.01962% | 10.2211 | 10.7027 | 11.207 | 11.7351 | 0 | 0 | 0.056427 | 0.51029
2026-12-03 23:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2026-12-04 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2026-12-04 01:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2026-12-04 02:00 | 9.736 | 0.01957% | 10.1947 | 10.6751 | 11.1781 | 11.7048 | 0 | 0 | 0.031601 | 0.4843
2026-12-04 03:00 | 9.3838 | 0.01886% | 9.8259 | 10.2889 | 10.7737 | 11.2814 | 0 | 0 | 0 | 0.12036
2026-12-04 04:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-04 05:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2026-12-04 06:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2026-12-04 07:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2026-12-04 08:00 | 5.912 | 0.01188% | 6.1906 | 6.4823 | 6.7877 | 7.1076 | 0 | 0 | 0 | 0
2026-12-04 09:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2026-12-04 10:00 | 6.063 | 0.01219% | 6.3487 | 6.6478 | 6.961 | 7.289 | 0 | 0 | 0 | 0
2026-12-04 11:00 | 6.4404 | 0.01294% | 6.7438 | 7.0616 | 7.3943 | 7.7427 | 0 | 0 | 0 | 0
2026-12-04 12:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2026-12-04 13:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2026-12-04 14:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2026-12-04 15:00 | 7.8743 | 0.01583% | 8.2454 | 8.6339 | 9.0407 | 9.4667 | 0 | 0 | 0 | 0
2026-12-04 16:00 | 7.9498 | 0.01598% | 8.3244 | 8.7166 | 9.1273 | 9.5574 | 0 | 0 | 0 | 0
2026-12-04 17:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2026-12-04 18:00 | 8.3523 | 0.01679% | 8.7459 | 9.158 | 9.5895 | 10.0413 | 0 | 0 | 0 | 0
2026-12-04 19:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2026-12-04 20:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2026-12-04 21:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2026-12-04 22:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2026-12-04 23:00 | 10.6543 | 0.02141% | 11.1563 | 11.6819 | 12.2324 | 12.8087 | 0.01283 | 0.46464 | 0.93774 | 1.4331
2026-12-05 | 10.6543 | 0.02141% | 11.1563 | 11.6819 | 12.2324 | 12.8087 | 0.01283 | 0.46464 | 0.93774 | 1.4331
2026-12-05 01:00 | 10.6165 | 0.02134% | 11.1168 | 11.6406 | 12.189 | 12.7634 | 0 | 0.42908 | 0.90051 | 1.3941
2026-12-05 02:00 | 10.3775 | 0.02086% | 10.8665 | 11.3785 | 11.9147 | 12.4761 | 0 | 0.20385 | 0.66466 | 1.1472
2026-12-05 03:00 | 10.214 | 0.02053% | 10.6953 | 11.1992 | 11.7269 | 12.2795 | 0 | 0.04974 | 0.50329 | 0.97821
2026-12-05 04:00 | 9.3209 | 0.01873% | 9.7601 | 10.22 | 10.7015 | 11.2058 | 0 | 0 | 0 | 0.055371
2026-12-05 05:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2026-12-05 06:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2026-12-05 07:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2026-12-05 08:00 | 6.9812 | 0.01403% | 7.3102 | 7.6546 | 8.0153 | 8.393 | 0 | 0 | 0 | 0
2026-12-05 09:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2026-12-05 10:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2026-12-05 11:00 | 7.1196 | 0.01431% | 7.4551 | 7.8063 | 8.1742 | 8.5593 | 0 | 0 | 0 | 0
2026-12-05 12:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2026-12-05 13:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-05 14:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-05 15:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-05 16:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-05 17:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2026-12-05 18:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2026-12-05 19:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2026-12-05 20:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2026-12-05 21:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-05 22:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2026-12-05 23:00 | 10.2266 | 0.02055% | 10.7084 | 11.213 | 11.7413 | 12.2946 | 0 | 0.061595 | 0.5157 | 0.99121
2026-12-06 | 9.9121 | 0.01992% | 10.3792 | 10.8682 | 11.3803 | 11.9165 | 0 | 0 | 0.20538 | 0.66627
2026-12-06 01:00 | 9.8618 | 0.01982% | 10.3265 | 10.813 | 11.3225 | 11.856 | 0 | 0 | 0.15573 | 0.61428
2026-12-06 02:00 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2026-12-06 03:00 | 9.4844 | 0.01906% | 9.9313 | 10.3993 | 10.8893 | 11.4024 | 0 | 0 | 0 | 0.22434
2026-12-06 04:00 | 8.6039 | 0.01729% | 9.0093 | 9.4338 | 9.8783 | 10.3438 | 0 | 0 | 0 | 0
2026-12-06 05:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2026-12-06 06:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2026-12-06 07:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2026-12-06 08:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2026-12-06 09:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2026-12-06 10:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2026-12-06 11:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2026-12-06 12:00 | 6.3775 | 0.01282% | 6.678 | 6.9926 | 7.3221 | 7.6671 | 0 | 0 | 0 | 0
2026-12-06 13:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2026-12-06 14:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2026-12-06 15:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2026-12-06 16:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2026-12-06 17:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2026-12-06 18:00 | 8.9813 | 0.01805% | 9.4045 | 9.8476 | 10.3116 | 10.7975 | 0 | 0 | 0 | 0
2026-12-06 19:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2026-12-06 20:00 | 8.8681 | 0.01782% | 9.2859 | 9.7235 | 10.1816 | 10.6614 | 0 | 0 | 0 | 0
2026-12-06 21:00 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2026-12-06 22:00 | 9.6228 | 0.01934% | 10.0762 | 10.551 | 11.0481 | 11.5687 | 0 | 0 | 0 | 0.36732
2026-12-06 23:00 | 10.0002 | 0.0201% | 10.4714 | 10.9647 | 11.4814 | 12.0224 | 0 | 0 | 0.29227 | 0.75725
2026-12-07 | 9.6605 | 0.01942% | 10.1157 | 10.5924 | 11.0915 | 11.6141 | 0 | 0 | 0 | 0.40631
2026-12-07 01:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2026-12-07 02:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2026-12-07 03:00 | 8.7297 | 0.01755% | 9.141 | 9.5717 | 10.0227 | 10.495 | 0 | 0 | 0 | 0
2026-12-07 04:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2026-12-07 05:00 | 7.5599 | 0.01519% | 7.9161 | 8.2891 | 8.6796 | 9.0886 | 0 | 0 | 0 | 0
2026-12-07 06:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2026-12-07 07:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2026-12-07 08:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2026-12-07 09:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2026-12-07 10:00 | 5.7988 | 0.01165% | 6.0721 | 6.3582 | 6.6578 | 6.9715 | 0 | 0 | 0 | 0
2026-12-07 11:00 | 5.8995 | 0.01186% | 6.1774 | 6.4685 | 6.7733 | 7.0924 | 0 | 0 | 0 | 0
2026-12-07 12:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2026-12-07 13:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2026-12-07 14:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2026-12-07 15:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2026-12-07 16:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2026-12-07 17:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2026-12-07 18:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2026-12-07 19:00 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2026-12-07 20:00 | 9.258 | 0.01861% | 9.6942 | 10.151 | 10.6293 | 11.1302 | 0 | 0 | 0 | 0
2026-12-07 21:00 | 9.4467 | 0.01899% | 9.8918 | 10.3579 | 10.8459 | 11.357 | 0 | 0 | 0 | 0.18535
2026-12-07 22:00 | 10.6794 | 0.02146% | 11.1826 | 11.7095 | 12.2613 | 12.839 | 0.035472 | 0.48835 | 0.96257 | 1.4591
2026-12-07 23:00 | 11.1951 | 0.0225% | 11.7226 | 12.275 | 12.8534 | 13.459 | 0.49963 | 0.97438 | 1.4715 | 1.992
2026-12-08 | 10.8933 | 0.02189% | 11.4065 | 11.944 | 12.5068 | 13.0961 | 0.22793 | 0.68988 | 1.1736 | 1.6801
2026-12-08 01:00 | 10.5662 | 0.02124% | 11.0641 | 11.5854 | 12.1313 | 12.7029 | 0 | 0.38166 | 0.85085 | 1.3422
2026-12-08 02:00 | 10.1763 | 0.02045% | 10.6558 | 11.1578 | 11.6836 | 12.2341 | 0 | 0.014177 | 0.46605 | 0.93922
2026-12-08 03:00 | 9.6857 | 0.01947% | 10.1421 | 10.6199 | 11.1203 | 11.6443 | 0 | 0 | 0 | 0.43231
2026-12-08 04:00 | 8.7674 | 0.01762% | 9.1805 | 9.6131 | 10.0661 | 10.5404 | 0 | 0 | 0 | 0
2026-12-08 05:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2026-12-08 06:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2026-12-08 07:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2026-12-08 08:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2026-12-08 09:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2026-12-08 10:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2026-12-08 11:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2026-12-08 12:00 | 7.9624 | 0.016% | 8.3376 | 8.7304 | 9.1418 | 9.5725 | 0 | 0 | 0 | 0
2026-12-08 13:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2026-12-08 14:00 | 8.6542 | 0.01739% | 9.062 | 9.489 | 9.9361 | 10.4043 | 0 | 0 | 0 | 0
2026-12-08 15:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2026-12-08 16:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2026-12-08 17:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2026-12-08 18:00 | 8.4278 | 0.01694% | 8.8249 | 9.2407 | 9.6761 | 10.1321 | 0 | 0 | 0 | 0
2026-12-08 19:00 | 8.3775 | 0.01684% | 8.7722 | 9.1856 | 9.6184 | 10.0716 | 0 | 0 | 0 | 0
2026-12-08 20:00 | 8.2894 | 0.01666% | 8.68 | 9.089 | 9.5173 | 9.9657 | 0 | 0 | 0 | 0
2026-12-08 21:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2026-12-08 22:00 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-08 23:00 | 11.0065 | 0.02212% | 11.5251 | 12.0681 | 12.6368 | 13.2322 | 0.32982 | 0.79657 | 1.2853 | 1.7971
2026-12-09 | 10.8933 | 0.02189% | 11.4065 | 11.944 | 12.5068 | 13.0961 | 0.22793 | 0.68988 | 1.1736 | 1.6801
2026-12-09 01:00 | 10.6417 | 0.02139% | 11.1431 | 11.6681 | 12.2179 | 12.7936 | 0.0015095 | 0.45279 | 0.92533 | 1.4201
2026-12-09 02:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2026-12-09 03:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2026-12-09 04:00 | 9.3586 | 0.01881% | 9.7996 | 10.2613 | 10.7448 | 11.2511 | 0 | 0 | 0 | 0.094364
2026-12-09 05:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2026-12-09 06:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2026-12-09 07:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2026-12-09 08:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2026-12-09 09:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2026-12-09 10:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2026-12-09 11:00 | 7.0693 | 0.01421% | 7.4024 | 7.7512 | 8.1164 | 8.4988 | 0 | 0 | 0 | 0
2026-12-09 12:00 | 7.7611 | 0.0156% | 8.1268 | 8.5097 | 8.9107 | 9.3306 | 0 | 0 | 0 | 0
2026-12-09 13:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2026-12-09 14:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2026-12-09 15:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2026-12-09 16:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2026-12-09 17:00 | 8.2517 | 0.01658% | 8.6405 | 9.0476 | 9.474 | 9.9204 | 0 | 0 | 0 | 0
2026-12-09 18:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2026-12-09 19:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2026-12-09 20:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-09 21:00 | 9.1448 | 0.01838% | 9.5757 | 10.0269 | 10.4993 | 10.994 | 0 | 0 | 0 | 0
2026-12-09 22:00 | 10.5285 | 0.02116% | 11.0246 | 11.544 | 12.088 | 12.6575 | 0 | 0.3461 | 0.81362 | 1.3032
2026-12-09 23:00 | 10.8681 | 0.02184% | 11.3802 | 11.9164 | 12.4779 | 13.0658 | 0.20529 | 0.66617 | 1.1488 | 1.6541
2026-12-10 | 10.5536 | 0.02121% | 11.0509 | 11.5716 | 12.1168 | 12.6878 | 0 | 0.36981 | 0.83844 | 1.3292
2026-12-10 01:00 | 10.5285 | 0.02116% | 11.0246 | 11.544 | 12.088 | 12.6575 | 0 | 0.3461 | 0.81362 | 1.3032
2026-12-10 02:00 | 10.1888 | 0.02048% | 10.6689 | 11.1716 | 11.698 | 12.2492 | 0 | 0.026032 | 0.47847 | 0.95222
2026-12-10 03:00 | 9.5851 | 0.01926% | 10.0367 | 10.5096 | 11.0048 | 11.5233 | 0 | 0 | 0 | 0.32832
2026-12-10 04:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2026-12-10 05:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2026-12-10 06:00 | 6.868 | 0.0138% | 7.1916 | 7.5305 | 7.8853 | 8.2569 | 0 | 0 | 0 | 0
2026-12-10 07:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2026-12-10 08:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2026-12-10 09:00 | 5.8617 | 0.01178% | 6.1379 | 6.4271 | 6.73 | 7.0471 | 0 | 0 | 0 | 0
2026-12-10 10:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2026-12-10 11:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2026-12-10 12:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2026-12-10 13:00 | 7.3712 | 0.01482% | 7.7185 | 8.0822 | 8.463 | 8.8618 | 0 | 0 | 0 | 0
2026-12-10 14:00 | 7.7737 | 0.01562% | 8.14 | 8.5235 | 8.9252 | 9.3457 | 0 | 0 | 0 | 0
2026-12-10 15:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2026-12-10 16:00 | 8.3775 | 0.01684% | 8.7722 | 9.1856 | 9.6184 | 10.0716 | 0 | 0 | 0 | 0
2026-12-10 17:00 | 8.5159 | 0.01712% | 8.9171 | 9.3373 | 9.7772 | 10.2379 | 0 | 0 | 0 | 0
2026-12-10 18:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2026-12-10 19:00 | 8.6165 | 0.01732% | 9.0225 | 9.4476 | 9.8928 | 10.3589 | 0 | 0 | 0 | 0
2026-12-10 20:00 | 8.3523 | 0.01679% | 8.7459 | 9.158 | 9.5895 | 10.0413 | 0 | 0 | 0 | 0
2026-12-10 21:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-10 22:00 | 9.8366 | 0.01977% | 10.3001 | 10.7854 | 11.2936 | 11.8258 | 0 | 0 | 0.1309 | 0.58828
2026-12-10 23:00 | 10.3901 | 0.02088% | 10.8797 | 11.3923 | 11.9291 | 12.4912 | 0 | 0.2157 | 0.67707 | 1.1602
2026-12-11 | 10.2517 | 0.0206% | 10.7348 | 11.2406 | 11.7702 | 12.3248 | 0 | 0.085303 | 0.54053 | 1.0172
2026-12-11 01:00 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-11 02:00 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-11 03:00 | 9.5473 | 0.01919% | 9.9972 | 10.4682 | 10.9615 | 11.478 | 0 | 0 | 0 | 0.28933
2026-12-11 04:00 | 8.6794 | 0.01744% | 9.0883 | 9.5166 | 9.965 | 10.4345 | 0 | 0 | 0 | 0
2026-12-11 05:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2026-12-11 06:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2026-12-11 07:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2026-12-11 08:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2026-12-11 09:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2026-12-11 10:00 | 6.5787 | 0.01322% | 6.8887 | 7.2133 | 7.5532 | 7.9091 | 0 | 0 | 0 | 0
2026-12-11 11:00 | 6.9561 | 0.01398% | 7.2838 | 7.6271 | 7.9864 | 8.3627 | 0 | 0 | 0 | 0
2026-12-11 12:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2026-12-11 13:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2026-12-11 14:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2026-12-11 15:00 | 8.3146 | 0.01671% | 8.7064 | 9.1166 | 9.5462 | 9.996 | 0 | 0 | 0 | 0
2026-12-11 16:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-11 17:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2026-12-11 18:00 | 8.7297 | 0.01755% | 9.141 | 9.5717 | 10.0227 | 10.495 | 0 | 0 | 0 | 0
2026-12-11 19:00 | 8.6668 | 0.01742% | 9.0752 | 9.5028 | 9.9505 | 10.4194 | 0 | 0 | 0 | 0
2026-12-11 20:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2026-12-11 21:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2026-12-11 22:00 | 9.9876 | 0.02007% | 10.4582 | 10.951 | 11.4669 | 12.0073 | 0 | 0 | 0.27986 | 0.74425
2026-12-11 23:00 | 10.931 | 0.02197% | 11.446 | 11.9854 | 12.5501 | 13.1414 | 0.26189 | 0.72544 | 1.2108 | 1.7191
2026-12-12 | 10.8052 | 0.02172% | 11.3143 | 11.8474 | 12.4057 | 12.9902 | 0.14868 | 0.6069 | 1.0867 | 1.5891
2026-12-12 01:00 | 10.5788 | 0.02126% | 11.0772 | 11.5992 | 12.1457 | 12.718 | 0 | 0.39352 | 0.86327 | 1.3552
2026-12-12 02:00 | 10.5788 | 0.02126% | 11.0772 | 11.5992 | 12.1457 | 12.718 | 0 | 0.39352 | 0.86327 | 1.3552
2026-12-12 03:00 | 10.2014 | 0.0205% | 10.6821 | 11.1854 | 11.7125 | 12.2643 | 0 | 0.037886 | 0.49088 | 0.96522
2026-12-12 04:00 | 9.3335 | 0.01876% | 9.7733 | 10.2338 | 10.716 | 11.2209 | 0 | 0 | 0 | 0.068368
2026-12-12 05:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2026-12-12 06:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2026-12-12 07:00 | 7.0945 | 0.01426% | 7.4287 | 7.7788 | 8.1453 | 8.5291 | 0 | 0 | 0 | 0
2026-12-12 08:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2026-12-12 09:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2026-12-12 10:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2026-12-12 11:00 | 7.0316 | 0.01413% | 7.3629 | 7.7098 | 8.0731 | 8.4535 | 0 | 0 | 0 | 0
2026-12-12 12:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2026-12-12 13:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2026-12-12 14:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2026-12-12 15:00 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2026-12-12 16:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-12 17:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-12 18:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-12 19:00 | 8.7171 | 0.01752% | 9.1279 | 9.5579 | 10.0083 | 10.4799 | 0 | 0 | 0 | 0
2026-12-12 20:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2026-12-12 21:00 | 8.8429 | 0.01777% | 9.2596 | 9.6959 | 10.1527 | 10.6311 | 0 | 0 | 0 | 0
2026-12-12 22:00 | 9.975 | 0.02005% | 10.445 | 10.9372 | 11.4525 | 11.9921 | 0 | 0 | 0.26745 | 0.73126
2026-12-12 23:00 | 10.1385 | 0.02038% | 10.6162 | 11.1165 | 11.6403 | 12.1887 | 0 | 0 | 0.42881 | 0.90023
2026-12-13 | 10.1385 | 0.02038% | 10.6162 | 11.1165 | 11.6403 | 12.1887 | 0 | 0 | 0.42881 | 0.90023
2026-12-13 01:00 | 9.9624 | 0.02002% | 10.4318 | 10.9234 | 11.4381 | 11.977 | 0 | 0 | 0.25503 | 0.71826
2026-12-13 02:00 | 9.7989 | 0.01969% | 10.2606 | 10.7441 | 11.2503 | 11.7804 | 0 | 0 | 0.093666 | 0.54929
2026-12-13 03:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2026-12-13 04:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2026-12-13 05:00 | 8.1008 | 0.01628% | 8.4825 | 8.8821 | 9.3006 | 9.7389 | 0 | 0 | 0 | 0
2026-12-13 06:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2026-12-13 07:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2026-12-13 08:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2026-12-13 09:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2026-12-13 10:00 | 6.0253 | 0.01211% | 6.3092 | 6.6064 | 6.9177 | 7.2437 | 0 | 0 | 0 | 0
2026-12-13 11:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2026-12-13 12:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2026-12-13 13:00 | 7.1448 | 0.01436% | 7.4814 | 7.8339 | 8.2031 | 8.5896 | 0 | 0 | 0 | 0
2026-12-13 14:00 | 7.824 | 0.01573% | 8.1927 | 8.5787 | 8.9829 | 9.4062 | 0 | 0 | 0 | 0
2026-12-13 15:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2026-12-13 16:00 | 8.6794 | 0.01744% | 9.0883 | 9.5166 | 9.965 | 10.4345 | 0 | 0 | 0 | 0
2026-12-13 17:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-13 18:00 | 8.9813 | 0.01805% | 9.4045 | 9.8476 | 10.3116 | 10.7975 | 0 | 0 | 0 | 0
2026-12-13 19:00 | 8.8429 | 0.01777% | 9.2596 | 9.6959 | 10.1527 | 10.6311 | 0 | 0 | 0 | 0
2026-12-13 20:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2026-12-13 21:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2026-12-13 22:00 | 9.9876 | 0.02007% | 10.4582 | 10.951 | 11.4669 | 12.0073 | 0 | 0 | 0.27986 | 0.74425
2026-12-13 23:00 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-14 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-14 01:00 | 9.7108 | 0.01952% | 10.1684 | 10.6475 | 11.1492 | 11.6746 | 0 | 0 | 0.0067752 | 0.4583
2026-12-14 02:00 | 9.7108 | 0.01952% | 10.1684 | 10.6475 | 11.1492 | 11.6746 | 0 | 0 | 0.0067752 | 0.4583
2026-12-14 03:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2026-12-14 04:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2026-12-14 05:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2026-12-14 06:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2026-12-14 07:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2026-12-14 08:00 | 6.6542 | 0.01337% | 6.9677 | 7.296 | 7.6398 | 7.9998 | 0 | 0 | 0 | 0
2026-12-14 09:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2026-12-14 10:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-14 11:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2026-12-14 12:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2026-12-14 13:00 | 7.6479 | 0.01537% | 8.0083 | 8.3856 | 8.7807 | 9.1945 | 0 | 0 | 0 | 0
2026-12-14 14:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2026-12-14 15:00 | 8.7423 | 0.01757% | 9.1542 | 9.5855 | 10.0372 | 10.5101 | 0 | 0 | 0 | 0
2026-12-14 16:00 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2026-12-14 17:00 | 9.3838 | 0.01886% | 9.8259 | 10.2889 | 10.7737 | 11.2814 | 0 | 0 | 0 | 0.12036
2026-12-14 18:00 | 9.5851 | 0.01926% | 10.0367 | 10.5096 | 11.0048 | 11.5233 | 0 | 0 | 0 | 0.32832
2026-12-14 19:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2026-12-14 20:00 | 9.648 | 0.01939% | 10.1025 | 10.5786 | 11.077 | 11.5989 | 0 | 0 | 0 | 0.39331
2026-12-14 21:00 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-14 22:00 | 11.409 | 0.02293% | 11.9466 | 12.5095 | 13.0989 | 13.7161 | 0.69209 | 1.1759 | 1.6825 | 2.213
2026-12-14 23:00 | 11.8492 | 0.02382% | 12.4076 | 12.9922 | 13.6044 | 14.2454 | 1.0883 | 1.5908 | 2.117 | 2.6679
2026-12-15 | 11.8367 | 0.02379% | 12.3944 | 12.9784 | 13.5899 | 14.2303 | 1.077 | 1.579 | 2.1046 | 2.6549
2026-12-15 01:00 | 11.5222 | 0.02316% | 12.0651 | 12.6336 | 13.2289 | 13.8522 | 0.79397 | 1.2826 | 1.7942 | 2.33
2026-12-15 02:00 | 11.0316 | 0.02217% | 11.5514 | 12.0957 | 12.6656 | 13.2624 | 0.35246 | 0.82027 | 1.3101 | 1.8231
2026-12-15 03:00 | 10.4782 | 0.02106% | 10.9719 | 11.4888 | 12.0302 | 12.597 | 0 | 0.29868 | 0.76396 | 1.2512
2026-12-15 04:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2026-12-15 05:00 | 8.5033 | 0.01709% | 8.9039 | 9.3235 | 9.7628 | 10.2228 | 0 | 0 | 0 | 0
2026-12-15 06:00 | 7.5347 | 0.01514% | 7.8897 | 8.2615 | 8.6508 | 9.0584 | 0 | 0 | 0 | 0
2026-12-15 07:00 | 7.1699 | 0.01441% | 7.5078 | 7.8615 | 8.2319 | 8.6198 | 0 | 0 | 0 | 0
2026-12-15 08:00 | 6.9435 | 0.01396% | 7.2707 | 7.6133 | 7.972 | 8.3476 | 0 | 0 | 0 | 0
2026-12-15 09:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2026-12-15 10:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2026-12-15 11:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2026-12-15 12:00 | 7.8618 | 0.0158% | 8.2322 | 8.6201 | 9.0263 | 9.4516 | 0 | 0 | 0 | 0
2026-12-15 13:00 | 8.5913 | 0.01727% | 8.9961 | 9.42 | 9.8639 | 10.3287 | 0 | 0 | 0 | 0
2026-12-15 14:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2026-12-15 15:00 | 8.8932 | 0.01787% | 9.3123 | 9.751 | 10.2105 | 10.6916 | 0 | 0 | 0 | 0
2026-12-15 16:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-15 17:00 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2026-12-15 18:00 | 9.3083 | 0.01871% | 9.7469 | 10.2062 | 10.6871 | 11.1906 | 0 | 0 | 0 | 0.042373
2026-12-15 19:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2026-12-15 20:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2026-12-15 21:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2026-12-15 22:00 | 10.3649 | 0.02083% | 10.8533 | 11.3647 | 11.9002 | 12.4609 | 0 | 0.19199 | 0.65225 | 1.1342
2026-12-15 23:00 | 11.2077 | 0.02253% | 11.7358 | 12.2888 | 12.8678 | 13.4741 | 0.51095 | 0.98623 | 1.4839 | 2.005
2026-12-16 | 11.1448 | 0.0224% | 11.67 | 12.2198 | 12.7956 | 13.3985 | 0.45435 | 0.92696 | 1.4218 | 1.9401
2026-12-16 01:00 | 10.7675 | 0.02164% | 11.2748 | 11.8061 | 12.3624 | 12.9449 | 0.11472 | 0.57133 | 1.0495 | 1.5501
2026-12-16 02:00 | 10.6794 | 0.02146% | 11.1826 | 11.7095 | 12.2613 | 12.839 | 0.035472 | 0.48835 | 0.96257 | 1.4591
2026-12-16 03:00 | 10.2266 | 0.02055% | 10.7084 | 11.213 | 11.7413 | 12.2946 | 0 | 0.061595 | 0.5157 | 0.99121
2026-12-16 04:00 | 9.409 | 0.01891% | 9.8523 | 10.3165 | 10.8026 | 11.3116 | 0 | 0 | 0 | 0.14636
2026-12-16 05:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2026-12-16 06:00 | 7.3083 | 0.01469% | 7.6526 | 8.0132 | 8.3908 | 8.7862 | 0 | 0 | 0 | 0
2026-12-16 07:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2026-12-16 08:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-16 09:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2026-12-16 10:00 | 6.4152 | 0.01289% | 6.7175 | 7.034 | 7.3654 | 7.7125 | 0 | 0 | 0 | 0
2026-12-16 11:00 | 6.8303 | 0.01373% | 7.1521 | 7.4891 | 7.842 | 8.2115 | 0 | 0 | 0 | 0
2026-12-16 12:00 | 7.6353 | 0.01535% | 7.9951 | 8.3718 | 8.7663 | 9.1794 | 0 | 0 | 0 | 0
2026-12-16 13:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2026-12-16 14:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2026-12-16 15:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2026-12-16 16:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-16 17:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2026-12-16 18:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-16 19:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2026-12-16 20:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2026-12-16 21:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2026-12-16 22:00 | 10.2392 | 0.02058% | 10.7216 | 11.2268 | 11.7558 | 12.3097 | 0 | 0.073449 | 0.52812 | 1.0042
2026-12-16 23:00 | 10.9561 | 0.02202% | 11.4724 | 12.0129 | 12.579 | 13.1717 | 0.28453 | 0.74915 | 1.2357 | 1.7451
2026-12-17 | 10.7549 | 0.02162% | 11.2616 | 11.7923 | 12.3479 | 12.9297 | 0.1034 | 0.55948 | 1.037 | 1.5371
2026-12-17 01:00 | 10.2643 | 0.02063% | 10.748 | 11.2544 | 11.7847 | 12.34 | 0 | 0.097158 | 0.55294 | 1.0302
2026-12-17 02:00 | 10.2643 | 0.02063% | 10.748 | 11.2544 | 11.7847 | 12.34 | 0 | 0.097158 | 0.55294 | 1.0302
2026-12-17 03:00 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2026-12-17 04:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2026-12-17 05:00 | 7.7989 | 0.01567% | 8.1663 | 8.5511 | 8.954 | 9.3759 | 0 | 0 | 0 | 0
2026-12-17 06:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2026-12-17 07:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2026-12-17 08:00 | 6.1385 | 0.01234% | 6.4277 | 6.7306 | 7.0477 | 7.3798 | 0 | 0 | 0 | 0
2026-12-17 09:00 | 6.0001 | 0.01206% | 6.2828 | 6.5788 | 6.8888 | 7.2134 | 0 | 0 | 0 | 0
2026-12-17 10:00 | 5.9498 | 0.01196% | 6.2301 | 6.5237 | 6.8311 | 7.1529 | 0 | 0 | 0 | 0
2026-12-17 11:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2026-12-17 12:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2026-12-17 13:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2026-12-17 14:00 | 7.6605 | 0.0154% | 8.0215 | 8.3994 | 8.7952 | 9.2096 | 0 | 0 | 0 | 0
2026-12-17 15:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2026-12-17 16:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2026-12-17 17:00 | 7.9121 | 0.0159% | 8.2849 | 8.6753 | 9.084 | 9.512 | 0 | 0 | 0 | 0
2026-12-17 18:00 | 8.1637 | 0.01641% | 8.5483 | 8.9511 | 9.3729 | 9.8145 | 0 | 0 | 0 | 0
2026-12-17 19:00 | 8.0253 | 0.01613% | 8.4034 | 8.7994 | 9.214 | 9.6481 | 0 | 0 | 0 | 0
2026-12-17 20:00 | 7.9247 | 0.01593% | 8.2981 | 8.689 | 9.0985 | 9.5272 | 0 | 0 | 0 | 0
2026-12-17 21:00 | 8.5033 | 0.01709% | 8.9039 | 9.3235 | 9.7628 | 10.2228 | 0 | 0 | 0 | 0
2026-12-17 22:00 | 9.4593 | 0.01901% | 9.905 | 10.3717 | 10.8604 | 11.3721 | 0 | 0 | 0 | 0.19835
2026-12-17 23:00 | 9.9876 | 0.02007% | 10.4582 | 10.951 | 11.4669 | 12.0073 | 0 | 0 | 0.27986 | 0.74425
2026-12-18 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2026-12-18 01:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2026-12-18 02:00 | 9.5851 | 0.01926% | 10.0367 | 10.5096 | 11.0048 | 11.5233 | 0 | 0 | 0 | 0.32832
2026-12-18 03:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2026-12-18 04:00 | 8.2014 | 0.01648% | 8.5878 | 8.9925 | 9.4162 | 9.8599 | 0 | 0 | 0 | 0
2026-12-18 05:00 | 7.346 | 0.01476% | 7.6922 | 8.0546 | 8.4341 | 8.8315 | 0 | 0 | 0 | 0
2026-12-18 06:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2026-12-18 07:00 | 6.2139 | 0.01249% | 6.5067 | 6.8133 | 7.1343 | 7.4705 | 0 | 0 | 0 | 0
2026-12-18 08:00 | 5.9749 | 0.01201% | 6.2565 | 6.5513 | 6.86 | 7.1832 | 0 | 0 | 0 | 0
2026-12-18 09:00 | 5.7359 | 0.01153% | 6.0062 | 6.2892 | 6.5856 | 6.8959 | 0 | 0 | 0 | 0
2026-12-18 10:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2026-12-18 11:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2026-12-18 12:00 | 6.78 | 0.01363% | 7.0994 | 7.434 | 7.7842 | 8.151 | 0 | 0 | 0 | 0
2026-12-18 13:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2026-12-18 14:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2026-12-18 15:00 | 7.497 | 0.01507% | 7.8502 | 8.2201 | 8.6074 | 9.013 | 0 | 0 | 0 | 0
2026-12-18 16:00 | 7.7485 | 0.01557% | 8.1137 | 8.496 | 8.8963 | 9.3155 | 0 | 0 | 0 | 0
2026-12-18 17:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2026-12-18 18:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2026-12-18 19:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2026-12-18 20:00 | 7.6102 | 0.0153% | 7.9688 | 8.3442 | 8.7374 | 9.1491 | 0 | 0 | 0 | 0
2026-12-18 21:00 | 8.0504 | 0.01618% | 8.4298 | 8.827 | 9.2429 | 9.6784 | 0 | 0 | 0 | 0
2026-12-18 22:00 | 9.2706 | 0.01863% | 9.7074 | 10.1648 | 10.6438 | 11.1453 | 0 | 0 | 0 | 0.0033794
2026-12-18 23:00 | 9.7737 | 0.01964% | 10.2343 | 10.7165 | 11.2214 | 11.7502 | 0 | 0 | 0.06884 | 0.52329
2026-12-19 | 9.5473 | 0.01919% | 9.9972 | 10.4682 | 10.9615 | 11.478 | 0 | 0 | 0 | 0.28933
2026-12-19 01:00 | 9.3461 | 0.01878% | 9.7864 | 10.2476 | 10.7304 | 11.236 | 0 | 0 | 0 | 0.081366
2026-12-19 02:00 | 9.1951 | 0.01848% | 9.6284 | 10.0821 | 10.5571 | 11.0545 | 0 | 0 | 0 | 0
2026-12-19 03:00 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2026-12-19 04:00 | 8.214 | 0.01651% | 8.601 | 9.0063 | 9.4306 | 9.875 | 0 | 0 | 0 | 0
2026-12-19 05:00 | 7.1951 | 0.01446% | 7.5341 | 7.8891 | 8.2608 | 8.6501 | 0 | 0 | 0 | 0
2026-12-19 06:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2026-12-19 07:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2026-12-19 08:00 | 5.4215 | 0.0109% | 5.6769 | 5.9444 | 6.2245 | 6.5178 | 0 | 0 | 0 | 0
2026-12-19 09:00 | 5.2202 | 0.01049% | 5.4662 | 5.7237 | 5.9934 | 6.2758 | 0 | 0 | 0 | 0
2026-12-19 10:00 | 5.3963 | 0.01085% | 5.6506 | 5.9168 | 6.1956 | 6.4875 | 0 | 0 | 0 | 0
2026-12-19 11:00 | 5.5976 | 0.01125% | 5.8613 | 6.1375 | 6.4267 | 6.7295 | 0 | 0 | 0 | 0
2026-12-19 12:00 | 6.4907 | 0.01305% | 6.7965 | 7.1167 | 7.4521 | 7.8032 | 0 | 0 | 0 | 0
2026-12-19 13:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2026-12-19 14:00 | 7.5221 | 0.01512% | 7.8766 | 8.2477 | 8.6363 | 9.0432 | 0 | 0 | 0 | 0
2026-12-19 15:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2026-12-19 16:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2026-12-19 17:00 | 8.214 | 0.01651% | 8.601 | 9.0063 | 9.4306 | 9.875 | 0 | 0 | 0 | 0
2026-12-19 18:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-19 19:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2026-12-19 20:00 | 8.5159 | 0.01712% | 8.9171 | 9.3373 | 9.7772 | 10.2379 | 0 | 0 | 0 | 0
2026-12-19 21:00 | 8.9184 | 0.01792% | 9.3386 | 9.7786 | 10.2394 | 10.7218 | 0 | 0 | 0 | 0
2026-12-19 22:00 | 9.9121 | 0.01992% | 10.3792 | 10.8682 | 11.3803 | 11.9165 | 0 | 0 | 0.20538 | 0.66627
2026-12-19 23:00 | 10.3901 | 0.02088% | 10.8797 | 11.3923 | 11.9291 | 12.4912 | 0 | 0.2157 | 0.67707 | 1.1602
2026-12-20 | 10.2392 | 0.02058% | 10.7216 | 11.2268 | 11.7558 | 12.3097 | 0 | 0.073449 | 0.52812 | 1.0042
2026-12-20 01:00 | 9.8744 | 0.01985% | 10.3396 | 10.8268 | 11.337 | 11.8712 | 0 | 0 | 0.16814 | 0.62727
2026-12-20 02:00 | 9.8744 | 0.01985% | 10.3396 | 10.8268 | 11.337 | 11.8712 | 0 | 0 | 0.16814 | 0.62727
2026-12-20 03:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2026-12-20 04:00 | 9.0945 | 0.01828% | 9.523 | 9.9717 | 10.4416 | 10.9336 | 0 | 0 | 0 | 0
2026-12-20 05:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2026-12-20 06:00 | 7.3209 | 0.01471% | 7.6658 | 8.027 | 8.4052 | 8.8013 | 0 | 0 | 0 | 0
2026-12-20 07:00 | 6.8429 | 0.01375% | 7.1653 | 7.5029 | 7.8564 | 8.2266 | 0 | 0 | 0 | 0
2026-12-20 08:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2026-12-20 09:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2026-12-20 10:00 | 6.151 | 0.01236% | 6.4409 | 6.7444 | 7.0621 | 7.3949 | 0 | 0 | 0 | 0
2026-12-20 11:00 | 6.3146 | 0.01269% | 6.6121 | 6.9237 | 7.2499 | 7.5915 | 0 | 0 | 0 | 0
2026-12-20 12:00 | 6.4655 | 0.01299% | 6.7702 | 7.0892 | 7.4232 | 7.773 | 0 | 0 | 0 | 0
2026-12-20 13:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2026-12-20 14:00 | 7.8869 | 0.01585% | 8.2585 | 8.6477 | 9.0551 | 9.4818 | 0 | 0 | 0 | 0
2026-12-20 15:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-20 16:00 | 8.8932 | 0.01787% | 9.3123 | 9.751 | 10.2105 | 10.6916 | 0 | 0 | 0 | 0
2026-12-20 17:00 | 9.2077 | 0.01851% | 9.6415 | 10.0958 | 10.5715 | 11.0697 | 0 | 0 | 0 | 0
2026-12-20 18:00 | 9.258 | 0.01861% | 9.6942 | 10.151 | 10.6293 | 11.1302 | 0 | 0 | 0 | 0
2026-12-20 19:00 | 9.2328 | 0.01856% | 9.6679 | 10.1234 | 10.6004 | 11.0999 | 0 | 0 | 0 | 0
2026-12-20 20:00 | 9.1825 | 0.01846% | 9.6152 | 10.0683 | 10.5427 | 11.0394 | 0 | 0 | 0 | 0
2026-12-20 21:00 | 9.2706 | 0.01863% | 9.7074 | 10.1648 | 10.6438 | 11.1453 | 0 | 0 | 0 | 0.0033794
2026-12-20 22:00 | 9.9247 | 0.01995% | 10.3923 | 10.882 | 11.3947 | 11.9316 | 0 | 0 | 0.21779 | 0.67927
2026-12-20 23:00 | 10.0379 | 0.02017% | 10.5109 | 11.0061 | 11.5247 | 12.0677 | 0 | 0 | 0.32951 | 0.79625
2026-12-21 | 9.8366 | 0.01977% | 10.3001 | 10.7854 | 11.2936 | 11.8258 | 0 | 0 | 0.1309 | 0.58828
2026-12-21 01:00 | 9.4215 | 0.01894% | 9.8655 | 10.3303 | 10.8171 | 11.3267 | 0 | 0 | 0 | 0.15935
2026-12-21 02:00 | 9.2957 | 0.01868% | 9.7337 | 10.1924 | 10.6726 | 11.1755 | 0 | 0 | 0 | 0.029375
2026-12-21 03:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2026-12-21 04:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2026-12-21 05:00 | 7.6857 | 0.01545% | 8.0478 | 8.427 | 8.8241 | 9.2398 | 0 | 0 | 0 | 0
2026-12-21 06:00 | 7.019 | 0.01411% | 7.3497 | 7.696 | 8.0586 | 8.4383 | 0 | 0 | 0 | 0
2026-12-21 07:00 | 6.4529 | 0.01297% | 6.757 | 7.0754 | 7.4087 | 7.7578 | 0 | 0 | 0 | 0
2026-12-21 08:00 | 6.2014 | 0.01246% | 6.4936 | 6.7995 | 7.1199 | 7.4554 | 0 | 0 | 0 | 0
2026-12-21 09:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2026-12-21 10:00 | 6.1007 | 0.01226% | 6.3882 | 6.6892 | 7.0044 | 7.3344 | 0 | 0 | 0 | 0
2026-12-21 11:00 | 6.302 | 0.01267% | 6.5989 | 6.9099 | 7.2354 | 7.5764 | 0 | 0 | 0 | 0
2026-12-21 12:00 | 6.5032 | 0.01307% | 6.8097 | 7.1305 | 7.4665 | 7.8183 | 0 | 0 | 0 | 0
2026-12-21 13:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2026-12-21 14:00 | 7.6982 | 0.01547% | 8.061 | 8.4408 | 8.8385 | 9.255 | 0 | 0 | 0 | 0
2026-12-21 15:00 | 8.1259 | 0.01633% | 8.5088 | 8.9097 | 9.3295 | 9.7691 | 0 | 0 | 0 | 0
2026-12-21 16:00 | 8.3398 | 0.01676% | 8.7327 | 9.1442 | 9.575 | 10.0262 | 0 | 0 | 0 | 0
2026-12-21 17:00 | 8.6416 | 0.01737% | 9.0488 | 9.4752 | 9.9217 | 10.3891 | 0 | 0 | 0 | 0
2026-12-21 18:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2026-12-21 19:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2026-12-21 20:00 | 9.2454 | 0.01858% | 9.6811 | 10.1372 | 10.6149 | 11.115 | 0 | 0 | 0 | 0
2026-12-21 21:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2026-12-21 22:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2026-12-21 23:00 | 10.6668 | 0.02144% | 11.1694 | 11.6957 | 12.2468 | 12.8239 | 0.024151 | 0.4765 | 0.95016 | 1.4461
2026-12-22 | 10.692 | 0.02149% | 11.1958 | 11.7233 | 12.2757 | 12.8541 | 0.046793 | 0.50021 | 0.97498 | 1.4721
2026-12-22 01:00 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2026-12-22 02:00 | 10.0882 | 0.02028% | 10.5636 | 11.0613 | 11.5825 | 12.1282 | 0 | 0 | 0.37916 | 0.84824
2026-12-22 03:00 | 9.4215 | 0.01894% | 9.8655 | 10.3303 | 10.8171 | 11.3267 | 0 | 0 | 0 | 0.15935
2026-12-22 04:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2026-12-22 05:00 | 8.0379 | 0.01615% | 8.4166 | 8.8132 | 9.2284 | 9.6633 | 0 | 0 | 0 | 0
2026-12-22 06:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2026-12-22 07:00 | 6.6416 | 0.01335% | 6.9546 | 7.2822 | 7.6254 | 7.9847 | 0 | 0 | 0 | 0
2026-12-22 08:00 | 6.3397 | 0.01274% | 6.6384 | 6.9512 | 7.2788 | 7.6217 | 0 | 0 | 0 | 0
2026-12-22 09:00 | 6.1259 | 0.01231% | 6.4145 | 6.7168 | 7.0333 | 7.3647 | 0 | 0 | 0 | 0
2026-12-22 10:00 | 6.2391 | 0.01254% | 6.5331 | 6.8409 | 7.1632 | 7.5008 | 0 | 0 | 0 | 0
2026-12-22 11:00 | 6.5284 | 0.01312% | 6.836 | 7.1581 | 7.4954 | 7.8486 | 0 | 0 | 0 | 0
2026-12-22 12:00 | 7.0819 | 0.01423% | 7.4156 | 7.765 | 8.1308 | 8.514 | 0 | 0 | 0 | 0
2026-12-22 13:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2026-12-22 14:00 | 7.9875 | 0.01605% | 8.3639 | 8.758 | 9.1707 | 9.6028 | 0 | 0 | 0 | 0
2026-12-22 15:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-22 16:00 | 8.2265 | 0.01653% | 8.6142 | 9.0201 | 9.4451 | 9.8901 | 0 | 0 | 0 | 0
2026-12-22 17:00 | 8.4907 | 0.01707% | 8.8908 | 9.3097 | 9.7484 | 10.2077 | 0 | 0 | 0 | 0
2026-12-22 18:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2026-12-22 19:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2026-12-22 20:00 | 8.541 | 0.01717% | 8.9435 | 9.3649 | 9.8061 | 10.2682 | 0 | 0 | 0 | 0
2026-12-22 21:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2026-12-22 22:00 | 9.975 | 0.02005% | 10.445 | 10.9372 | 11.4525 | 11.9921 | 0 | 0 | 0.26745 | 0.73126
2026-12-22 23:00 | 10.2895 | 0.02068% | 10.7743 | 11.282 | 11.8136 | 12.3702 | 0 | 0.12087 | 0.57777 | 1.0562
2026-12-23 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-23 01:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-23 02:00 | 9.3586 | 0.01881% | 9.7996 | 10.2613 | 10.7448 | 11.2511 | 0 | 0 | 0 | 0.094364
2026-12-23 03:00 | 9.3586 | 0.01881% | 9.7996 | 10.2613 | 10.7448 | 11.2511 | 0 | 0 | 0 | 0.094364
2026-12-23 04:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2026-12-23 05:00 | 7.5473 | 0.01517% | 7.9029 | 8.2753 | 8.6652 | 9.0735 | 0 | 0 | 0 | 0
2026-12-23 06:00 | 6.9058 | 0.01388% | 7.2312 | 7.5719 | 7.9287 | 8.3022 | 0 | 0 | 0 | 0
2026-12-23 07:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2026-12-23 08:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2026-12-23 09:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2026-12-23 10:00 | 5.7485 | 0.01155% | 6.0194 | 6.303 | 6.6 | 6.911 | 0 | 0 | 0 | 0
2026-12-23 11:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2026-12-23 12:00 | 6.6668 | 0.0134% | 6.9809 | 7.3098 | 7.6543 | 8.0149 | 0 | 0 | 0 | 0
2026-12-23 13:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2026-12-23 14:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2026-12-23 15:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2026-12-23 16:00 | 8.2643 | 0.01661% | 8.6537 | 9.0614 | 9.4884 | 9.9355 | 0 | 0 | 0 | 0
2026-12-23 17:00 | 8.692 | 0.01747% | 9.1015 | 9.5304 | 9.9794 | 10.4496 | 0 | 0 | 0 | 0
2026-12-23 18:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2026-12-23 19:00 | 8.8052 | 0.0177% | 9.2201 | 9.6545 | 10.1094 | 10.5857 | 0 | 0 | 0 | 0
2026-12-23 20:00 | 8.7926 | 0.01767% | 9.2069 | 9.6407 | 10.095 | 10.5706 | 0 | 0 | 0 | 0
2026-12-23 21:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2026-12-23 22:00 | 9.7108 | 0.01952% | 10.1684 | 10.6475 | 11.1492 | 11.6746 | 0 | 0 | 0.0067752 | 0.4583
2026-12-23 23:00 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2026-12-24 | 9.9498 | 0.02% | 10.4187 | 10.9096 | 11.4236 | 11.9619 | 0 | 0 | 0.24262 | 0.70526
2026-12-24 01:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2026-12-24 02:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2026-12-24 03:00 | 9.3083 | 0.01871% | 9.7469 | 10.2062 | 10.6871 | 11.1906 | 0 | 0 | 0 | 0.042373
2026-12-24 04:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2026-12-24 05:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2026-12-24 06:00 | 6.9183 | 0.0139% | 7.2443 | 7.5857 | 7.9431 | 8.3174 | 0 | 0 | 0 | 0
2026-12-24 07:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2026-12-24 08:00 | 5.9372 | 0.01193% | 6.217 | 6.5099 | 6.8166 | 7.1378 | 0 | 0 | 0 | 0
2026-12-24 09:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2026-12-24 10:00 | 5.8491 | 0.01176% | 6.1248 | 6.4133 | 6.7155 | 7.032 | 0 | 0 | 0 | 0
2026-12-24 11:00 | 6.2768 | 0.01262% | 6.5726 | 6.8823 | 7.2066 | 7.5461 | 0 | 0 | 0 | 0
2026-12-24 12:00 | 6.6794 | 0.01342% | 6.9941 | 7.3236 | 7.6687 | 8.03 | 0 | 0 | 0 | 0
2026-12-24 13:00 | 7.2202 | 0.01451% | 7.5604 | 7.9167 | 8.2897 | 8.6803 | 0 | 0 | 0 | 0
2026-12-24 14:00 | 7.8492 | 0.01578% | 8.219 | 8.6063 | 9.0118 | 9.4364 | 0 | 0 | 0 | 0
2026-12-24 15:00 | 8.302 | 0.01669% | 8.6932 | 9.1028 | 9.5317 | 9.9808 | 0 | 0 | 0 | 0
2026-12-24 16:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2026-12-24 17:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-24 18:00 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2026-12-24 19:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2026-12-24 20:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-24 21:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2026-12-24 22:00 | 9.648 | 0.01939% | 10.1025 | 10.5786 | 11.077 | 11.5989 | 0 | 0 | 0 | 0.39331
2026-12-24 23:00 | 9.8869 | 0.01987% | 10.3528 | 10.8406 | 11.3514 | 11.8863 | 0 | 0 | 0.18056 | 0.64027
2026-12-25 | 9.6354 | 0.01937% | 10.0894 | 10.5648 | 11.0626 | 11.5838 | 0 | 0 | 0 | 0.38032
2026-12-25 01:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2026-12-25 02:00 | 8.9435 | 0.01798% | 9.3649 | 9.8062 | 10.2683 | 10.7521 | 0 | 0 | 0 | 0
2026-12-25 03:00 | 8.8429 | 0.01777% | 9.2596 | 9.6959 | 10.1527 | 10.6311 | 0 | 0 | 0 | 0
2026-12-25 04:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2026-12-25 05:00 | 7.6228 | 0.01532% | 7.9819 | 8.358 | 8.7519 | 9.1642 | 0 | 0 | 0 | 0
2026-12-25 06:00 | 6.9309 | 0.01393% | 7.2575 | 7.5995 | 7.9575 | 8.3325 | 0 | 0 | 0 | 0
2026-12-25 07:00 | 6.4026 | 0.01287% | 6.7043 | 7.0202 | 7.351 | 7.6973 | 0 | 0 | 0 | 0
2026-12-25 08:00 | 6.0378 | 0.01214% | 6.3223 | 6.6202 | 6.9322 | 7.2588 | 0 | 0 | 0 | 0
2026-12-25 09:00 | 5.8869 | 0.01183% | 6.1643 | 6.4547 | 6.7589 | 7.0773 | 0 | 0 | 0 | 0
2026-12-25 10:00 | 5.7108 | 0.01148% | 5.9799 | 6.2616 | 6.5567 | 6.8656 | 0 | 0 | 0 | 0
2026-12-25 11:00 | 5.8743 | 0.01181% | 6.1511 | 6.4409 | 6.7444 | 7.0622 | 0 | 0 | 0 | 0
2026-12-25 12:00 | 6.2517 | 0.01256% | 6.5462 | 6.8547 | 7.1777 | 7.5159 | 0 | 0 | 0 | 0
2026-12-25 13:00 | 6.8555 | 0.01378% | 7.1785 | 7.5167 | 7.8709 | 8.2418 | 0 | 0 | 0 | 0
2026-12-25 14:00 | 7.9247 | 0.01593% | 8.2981 | 8.689 | 9.0985 | 9.5272 | 0 | 0 | 0 | 0
2026-12-25 15:00 | 8.4404 | 0.01696% | 8.8381 | 9.2545 | 9.6906 | 10.1472 | 0 | 0 | 0 | 0
2026-12-25 16:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2026-12-25 17:00 | 9.0442 | 0.01818% | 9.4703 | 9.9165 | 10.3838 | 10.8731 | 0 | 0 | 0 | 0
2026-12-25 18:00 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2026-12-25 19:00 | 8.8806 | 0.01785% | 9.2991 | 9.7372 | 10.1961 | 10.6765 | 0 | 0 | 0 | 0
2026-12-25 20:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2026-12-25 21:00 | 9.0819 | 0.01825% | 9.5098 | 9.9579 | 10.4271 | 10.9184 | 0 | 0 | 0 | 0
2026-12-25 22:00 | 9.6731 | 0.01944% | 10.1289 | 10.6062 | 11.1059 | 11.6292 | 0 | 0 | 0 | 0.41931
2026-12-25 23:00 | 9.6731 | 0.01944% | 10.1289 | 10.6062 | 11.1059 | 11.6292 | 0 | 0 | 0 | 0.41931
2026-12-26 | 9.0693 | 0.01823% | 9.4967 | 9.9441 | 10.4127 | 10.9033 | 0 | 0 | 0 | 0
2026-12-26 01:00 | 8.7549 | 0.0176% | 9.1674 | 9.5993 | 10.0516 | 10.5253 | 0 | 0 | 0 | 0
2026-12-26 02:00 | 8.8555 | 0.0178% | 9.2727 | 9.7097 | 10.1672 | 10.6462 | 0 | 0 | 0 | 0
2026-12-26 03:00 | 8.8303 | 0.01775% | 9.2464 | 9.6821 | 10.1383 | 10.616 | 0 | 0 | 0 | 0
2026-12-26 04:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2026-12-26 05:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2026-12-26 06:00 | 7.4592 | 0.01499% | 7.8107 | 8.1787 | 8.5641 | 8.9676 | 0 | 0 | 0 | 0
2026-12-26 07:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2026-12-26 08:00 | 6.7297 | 0.01353% | 7.0468 | 7.3788 | 7.7265 | 8.0905 | 0 | 0 | 0 | 0
2026-12-26 09:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2026-12-26 10:00 | 6.541 | 0.01315% | 6.8492 | 7.1719 | 7.5098 | 7.8637 | 0 | 0 | 0 | 0
2026-12-26 11:00 | 6.7548 | 0.01358% | 7.0731 | 7.4064 | 7.7554 | 8.1208 | 0 | 0 | 0 | 0
2026-12-26 12:00 | 6.8806 | 0.01383% | 7.2048 | 7.5443 | 7.8998 | 8.272 | 0 | 0 | 0 | 0
2026-12-26 13:00 | 7.4718 | 0.01502% | 7.8239 | 8.1925 | 8.5785 | 8.9828 | 0 | 0 | 0 | 0
2026-12-26 14:00 | 8.1008 | 0.01628% | 8.4825 | 8.8821 | 9.3006 | 9.7389 | 0 | 0 | 0 | 0
2026-12-26 15:00 | 8.7045 | 0.01749% | 9.1147 | 9.5442 | 9.9939 | 10.4648 | 0 | 0 | 0 | 0
2026-12-26 16:00 | 9.497 | 0.01909% | 9.9445 | 10.4131 | 10.9037 | 11.4175 | 0 | 0 | 0 | 0.23734
2026-12-26 17:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2026-12-26 18:00 | 10.4907 | 0.02108% | 10.985 | 11.5026 | 12.0446 | 12.6122 | 0 | 0.31054 | 0.77638 | 1.2642
2026-12-26 19:00 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-26 20:00 | 10.3775 | 0.02086% | 10.8665 | 11.3785 | 11.9147 | 12.4761 | 0 | 0.20385 | 0.66466 | 1.1472
2026-12-26 21:00 | 10.4656 | 0.02103% | 10.9587 | 11.4751 | 12.0157 | 12.5819 | 0 | 0.28683 | 0.75155 | 1.2382
2026-12-26 22:00 | 10.8304 | 0.02177% | 11.3407 | 11.875 | 12.4346 | 13.0205 | 0.17132 | 0.6306 | 1.1115 | 1.6151
2026-12-26 23:00 | 11.1574 | 0.02242% | 11.6831 | 12.2336 | 12.8101 | 13.4136 | 0.46567 | 0.93882 | 1.4343 | 1.953
2026-12-27 | 10.7423 | 0.02159% | 11.2485 | 11.7785 | 12.3335 | 12.9146 | 0.092077 | 0.54762 | 1.0246 | 1.5241
2026-12-27 01:00 | 10.6668 | 0.02144% | 11.1694 | 11.6957 | 12.2468 | 12.8239 | 0.024151 | 0.4765 | 0.95016 | 1.4461
2026-12-27 02:00 | 10.2014 | 0.0205% | 10.6821 | 11.1854 | 11.7125 | 12.2643 | 0 | 0.037886 | 0.49088 | 0.96522
2026-12-27 03:00 | 10.0505 | 0.0202% | 10.524 | 11.0199 | 11.5392 | 12.0829 | 0 | 0 | 0.34192 | 0.80924
2026-12-27 04:00 | 9.7108 | 0.01952% | 10.1684 | 10.6475 | 11.1492 | 11.6746 | 0 | 0 | 0.0067752 | 0.4583
2026-12-27 05:00 | 8.6542 | 0.01739% | 9.062 | 9.489 | 9.9361 | 10.4043 | 0 | 0 | 0 | 0
2026-12-27 06:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2026-12-27 07:00 | 7.3586 | 0.01479% | 7.7053 | 8.0684 | 8.4486 | 8.8467 | 0 | 0 | 0 | 0
2026-12-27 08:00 | 6.9938 | 0.01406% | 7.3234 | 7.6684 | 8.0298 | 8.4081 | 0 | 0 | 0 | 0
2026-12-27 09:00 | 6.6039 | 0.01327% | 6.915 | 7.2409 | 7.5821 | 7.9393 | 0 | 0 | 0 | 0
2026-12-27 10:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-27 11:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2026-12-27 12:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2026-12-27 13:00 | 7.4467 | 0.01497% | 7.7975 | 8.1649 | 8.5497 | 8.9525 | 0 | 0 | 0 | 0
2026-12-27 14:00 | 8.1762 | 0.01643% | 8.5615 | 8.9649 | 9.3873 | 9.8296 | 0 | 0 | 0 | 0
2026-12-27 15:00 | 8.4655 | 0.01701% | 8.8644 | 9.2821 | 9.7195 | 10.1774 | 0 | 0 | 0 | 0
2026-12-27 16:00 | 9.0442 | 0.01818% | 9.4703 | 9.9165 | 10.3838 | 10.8731 | 0 | 0 | 0 | 0
2026-12-27 17:00 | 9.2203 | 0.01853% | 9.6547 | 10.1096 | 10.586 | 11.0848 | 0 | 0 | 0 | 0
2026-12-27 18:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2026-12-27 19:00 | 9.3209 | 0.01873% | 9.7601 | 10.22 | 10.7015 | 11.2058 | 0 | 0 | 0 | 0.055371
2026-12-27 20:00 | 9.1071 | 0.0183% | 9.5362 | 9.9855 | 10.456 | 10.9487 | 0 | 0 | 0 | 0
2026-12-27 21:00 | 9.3712 | 0.01883% | 9.8128 | 10.2751 | 10.7593 | 11.2663 | 0 | 0 | 0 | 0.10736
2026-12-27 22:00 | 10.0127 | 0.02012% | 10.4845 | 10.9785 | 11.4958 | 12.0375 | 0 | 0 | 0.30469 | 0.77025
2026-12-27 23:00 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-28 | 10.3398 | 0.02078% | 10.827 | 11.3371 | 11.8713 | 12.4307 | 0 | 0.16828 | 0.62742 | 1.1082
2026-12-28 01:00 | 9.9624 | 0.02002% | 10.4318 | 10.9234 | 11.4381 | 11.977 | 0 | 0 | 0.25503 | 0.71826
2026-12-28 02:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-28 03:00 | 9.6102 | 0.01932% | 10.063 | 10.5372 | 11.0337 | 11.5536 | 0 | 0 | 0 | 0.35432
2026-12-28 04:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2026-12-28 05:00 | 8.1888 | 0.01646% | 8.5747 | 8.9787 | 9.4017 | 9.8447 | 0 | 0 | 0 | 0
2026-12-28 06:00 | 7.585 | 0.01524% | 7.9424 | 8.3167 | 8.7085 | 9.1189 | 0 | 0 | 0 | 0
2026-12-28 07:00 | 7.0064 | 0.01408% | 7.3365 | 7.6822 | 8.0442 | 8.4232 | 0 | 0 | 0 | 0
2026-12-28 08:00 | 6.7045 | 0.01348% | 7.0204 | 7.3512 | 7.6976 | 8.0603 | 0 | 0 | 0 | 0
2026-12-28 09:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2026-12-28 10:00 | 6.2894 | 0.01264% | 6.5858 | 6.8961 | 7.221 | 7.5612 | 0 | 0 | 0 | 0
2026-12-28 11:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2026-12-28 12:00 | 6.4781 | 0.01302% | 6.7833 | 7.1029 | 7.4376 | 7.7881 | 0 | 0 | 0 | 0
2026-12-28 13:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2026-12-28 14:00 | 7.5724 | 0.01522% | 7.9292 | 8.3029 | 8.6941 | 9.1037 | 0 | 0 | 0 | 0
2026-12-28 15:00 | 8.063 | 0.01621% | 8.4429 | 8.8408 | 9.2573 | 9.6935 | 0 | 0 | 0 | 0
2026-12-28 16:00 | 8.5788 | 0.01724% | 8.983 | 9.4062 | 9.8494 | 10.3135 | 0 | 0 | 0 | 0
2026-12-28 17:00 | 8.6291 | 0.01734% | 9.0357 | 9.4614 | 9.9072 | 10.374 | 0 | 0 | 0 | 0
2026-12-28 18:00 | 8.9058 | 0.0179% | 9.3254 | 9.7648 | 10.2249 | 10.7067 | 0 | 0 | 0 | 0
2026-12-28 19:00 | 9.497 | 0.01909% | 9.9445 | 10.4131 | 10.9037 | 11.4175 | 0 | 0 | 0 | 0.23734
2026-12-28 20:00 | 9.4844 | 0.01906% | 9.9313 | 10.3993 | 10.8893 | 11.4024 | 0 | 0 | 0 | 0.22434
2026-12-28 21:00 | 9.7234 | 0.01954% | 10.1816 | 10.6613 | 11.1637 | 11.6897 | 0 | 0 | 0.019188 | 0.4713
2026-12-28 22:00 | 10.7046 | 0.02151% | 11.209 | 11.7371 | 12.2901 | 12.8692 | 0.058114 | 0.51206 | 0.9874 | 1.4851
2026-12-28 23:00 | 10.9687 | 0.02205% | 11.4856 | 12.0267 | 12.5934 | 13.1868 | 0.29585 | 0.761 | 1.2481 | 1.7581
2026-12-29 | 10.5033 | 0.02111% | 10.9982 | 11.5164 | 12.0591 | 12.6273 | 0 | 0.32239 | 0.78879 | 1.2772
2026-12-29 01:00 | 10.1511 | 0.0204% | 10.6294 | 11.1303 | 11.6547 | 12.2038 | 0 | 0 | 0.44123 | 0.91323
2026-12-29 02:00 | 9.5347 | 0.01916% | 9.984 | 10.4544 | 10.947 | 11.4628 | 0 | 0 | 0 | 0.27633
2026-12-29 03:00 | 9.17 | 0.01843% | 9.602 | 10.0545 | 10.5282 | 11.0243 | 0 | 0 | 0 | 0
2026-12-29 04:00 | 8.5284 | 0.01714% | 8.9303 | 9.3511 | 9.7917 | 10.253 | 0 | 0 | 0 | 0
2026-12-29 05:00 | 7.7863 | 0.01565% | 8.1532 | 8.5373 | 8.9396 | 9.3608 | 0 | 0 | 0 | 0
2026-12-29 06:00 | 6.9687 | 0.01401% | 7.297 | 7.6408 | 8.0009 | 8.3779 | 0 | 0 | 0 | 0
2026-12-29 07:00 | 6.3649 | 0.01279% | 6.6648 | 6.9788 | 7.3077 | 7.652 | 0 | 0 | 0 | 0
2026-12-29 08:00 | 6.1133 | 0.01229% | 6.4014 | 6.703 | 7.0188 | 7.3495 | 0 | 0 | 0 | 0
2026-12-29 09:00 | 5.9624 | 0.01198% | 6.2433 | 6.5375 | 6.8455 | 7.1681 | 0 | 0 | 0 | 0
2026-12-29 10:00 | 5.7611 | 0.01158% | 6.0326 | 6.3168 | 6.6144 | 6.9261 | 0 | 0 | 0 | 0
2026-12-29 11:00 | 5.7863 | 0.01163% | 6.0589 | 6.3444 | 6.6433 | 6.9563 | 0 | 0 | 0 | 0
2026-12-29 12:00 | 6.1636 | 0.01239% | 6.454 | 6.7581 | 7.0766 | 7.41 | 0 | 0 | 0 | 0
2026-12-29 13:00 | 6.3523 | 0.01277% | 6.6516 | 6.965 | 7.2932 | 7.6369 | 0 | 0 | 0 | 0
2026-12-29 14:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2026-12-29 15:00 | 7.6731 | 0.01542% | 8.0346 | 8.4132 | 8.8096 | 9.2247 | 0 | 0 | 0 | 0
2026-12-29 16:00 | 8.3649 | 0.01681% | 8.7591 | 9.1718 | 9.6039 | 10.0565 | 0 | 0 | 0 | 0
2026-12-29 17:00 | 8.5662 | 0.01722% | 8.9698 | 9.3924 | 9.835 | 10.2984 | 0 | 0 | 0 | 0
2026-12-29 18:00 | 9.1071 | 0.0183% | 9.5362 | 9.9855 | 10.456 | 10.9487 | 0 | 0 | 0 | 0
2026-12-29 19:00 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2026-12-29 20:00 | 8.78 | 0.01765% | 9.1937 | 9.6269 | 10.0805 | 10.5555 | 0 | 0 | 0 | 0
2026-12-29 21:00 | 8.9561 | 0.018% | 9.3781 | 9.82 | 10.2827 | 10.7672 | 0 | 0 | 0 | 0
2026-12-29 22:00 | 10.0756 | 0.02025% | 10.5504 | 11.0475 | 11.568 | 12.1131 | 0 | 0 | 0.36675 | 0.83524
2026-12-29 23:00 | 10.692 | 0.02149% | 11.1958 | 11.7233 | 12.2757 | 12.8541 | 0.046793 | 0.50021 | 0.97498 | 1.4721
2026-12-30 | 10.5159 | 0.02114% | 11.0114 | 11.5302 | 12.0735 | 12.6424 | 0 | 0.33424 | 0.8012 | 1.2902
2026-12-30 01:00 | 10.3649 | 0.02083% | 10.8533 | 11.3647 | 11.9002 | 12.4609 | 0 | 0.19199 | 0.65225 | 1.1342
2026-12-30 02:00 | 10.214 | 0.02053% | 10.6953 | 11.1992 | 11.7269 | 12.2795 | 0 | 0.04974 | 0.50329 | 0.97821
2026-12-30 03:00 | 9.7863 | 0.01967% | 10.2474 | 10.7303 | 11.2359 | 11.7653 | 0 | 0 | 0.081253 | 0.53629
2026-12-30 04:00 | 9.2454 | 0.01858% | 9.6811 | 10.1372 | 10.6149 | 11.115 | 0 | 0 | 0 | 0
2026-12-30 05:00 | 8.2391 | 0.01656% | 8.6273 | 9.0338 | 9.4595 | 9.9052 | 0 | 0 | 0 | 0
2026-12-30 06:00 | 7.736 | 0.01555% | 8.1005 | 8.4822 | 8.8818 | 9.3003 | 0 | 0 | 0 | 0
2026-12-30 07:00 | 7.2454 | 0.01456% | 7.5868 | 7.9443 | 8.3186 | 8.7106 | 0 | 0 | 0 | 0
2026-12-30 08:00 | 6.8932 | 0.01385% | 7.218 | 7.5581 | 7.9142 | 8.2871 | 0 | 0 | 0 | 0
2026-12-30 09:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-30 10:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-30 11:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-30 12:00 | 7.0441 | 0.01416% | 7.376 | 7.7236 | 8.0875 | 8.4686 | 0 | 0 | 0 | 0
2026-12-30 13:00 | 7.5976 | 0.01527% | 7.9556 | 8.3304 | 8.723 | 9.134 | 0 | 0 | 0 | 0
2026-12-30 14:00 | 8.0001 | 0.01608% | 8.3771 | 8.7718 | 9.1851 | 9.6179 | 0 | 0 | 0 | 0
2026-12-30 15:00 | 8.0756 | 0.01623% | 8.4561 | 8.8546 | 9.2718 | 9.7086 | 0 | 0 | 0 | 0
2026-12-30 16:00 | 8.4152 | 0.01691% | 8.8117 | 9.2269 | 9.6617 | 10.1169 | 0 | 0 | 0 | 0
2026-12-30 17:00 | 8.7674 | 0.01762% | 9.1805 | 9.6131 | 10.0661 | 10.5404 | 0 | 0 | 0 | 0
2026-12-30 18:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-30 19:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-30 20:00 | 8.8177 | 0.01772% | 9.2332 | 9.6683 | 10.1238 | 10.6009 | 0 | 0 | 0 | 0
2026-12-30 21:00 | 8.9939 | 0.01808% | 9.4176 | 9.8614 | 10.326 | 10.8126 | 0 | 0 | 0 | 0
2026-12-30 22:00 | 10.1637 | 0.02043% | 10.6426 | 11.144 | 11.6691 | 12.219 | 0 | 0.0023229 | 0.45364 | 0.92622
2026-12-30 23:00 | 10.8807 | 0.02187% | 11.3934 | 11.9302 | 12.4923 | 13.081 | 0.21661 | 0.67802 | 1.1612 | 1.6671
2026-12-31 | 10.7172 | 0.02154% | 11.2221 | 11.7509 | 12.3046 | 12.8844 | 0.069435 | 0.52391 | 0.99981 | 1.4981
2026-12-31 01:00 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2026-12-31 02:00 | 10.3146 | 0.02073% | 10.8006 | 11.3096 | 11.8424 | 12.4004 | 0 | 0.14458 | 0.6026 | 1.0822
2026-12-31 03:00 | 9.8492 | 0.0198% | 10.3133 | 10.7992 | 11.3081 | 11.8409 | 0 | 0 | 0.14332 | 0.60128
2026-12-31 04:00 | 9.258 | 0.01861% | 9.6942 | 10.151 | 10.6293 | 11.1302 | 0 | 0 | 0 | 0
2026-12-31 05:00 | 8.4781 | 0.01704% | 8.8776 | 9.2959 | 9.7339 | 10.1926 | 0 | 0 | 0 | 0
2026-12-31 06:00 | 7.7108 | 0.0155% | 8.0741 | 8.4546 | 8.8529 | 9.2701 | 0 | 0 | 0 | 0
2026-12-31 07:00 | 7.1322 | 0.01433% | 7.4682 | 7.8201 | 8.1886 | 8.5745 | 0 | 0 | 0 | 0
2026-12-31 08:00 | 6.7926 | 0.01365% | 7.1126 | 7.4478 | 7.7987 | 8.1661 | 0 | 0 | 0 | 0
2026-12-31 09:00 | 6.5913 | 0.01325% | 6.9019 | 7.2271 | 7.5676 | 7.9242 | 0 | 0 | 0 | 0
2026-12-31 10:00 | 6.5661 | 0.0132% | 6.8755 | 7.1995 | 7.5387 | 7.8939 | 0 | 0 | 0 | 0
2026-12-31 11:00 | 6.6165 | 0.0133% | 6.9282 | 7.2547 | 7.5965 | 7.9544 | 0 | 0 | 0 | 0
2026-12-31 12:00 | 6.8051 | 0.01368% | 7.1258 | 7.4615 | 7.8131 | 8.1813 | 0 | 0 | 0 | 0
2026-12-31 13:00 | 7.2831 | 0.01464% | 7.6263 | 7.9856 | 8.3619 | 8.7559 | 0 | 0 | 0 | 0
2026-12-31 14:00 | 7.9372 | 0.01595% | 8.3112 | 8.7028 | 9.1129 | 9.5423 | 0 | 0 | 0 | 0
2026-12-31 15:00 | 8.2769 | 0.01664% | 8.6669 | 9.0752 | 9.5028 | 9.9506 | 0 | 0 | 0 | 0
2026-12-31 16:00 | 8.453 | 0.01699% | 8.8513 | 9.2683 | 9.705 | 10.1623 | 0 | 0 | 0 | 0
2026-12-31 17:00 | 8.5536 | 0.01719% | 8.9566 | 9.3787 | 9.8206 | 10.2833 | 0 | 0 | 0 | 0
2026-12-31 18:00 | 9.0316 | 0.01815% | 9.4571 | 9.9028 | 10.3694 | 10.8579 | 0 | 0 | 0 | 0
2026-12-31 19:00 | 9.1322 | 0.01835% | 9.5625 | 10.0131 | 10.4849 | 10.9789 | 0 | 0 | 0 | 0
2026-12-31 20:00 | 8.931 | 0.01795% | 9.3518 | 9.7924 | 10.2538 | 10.737 | 0 | 0 | 0 | 0
2026-12-31 21:00 | 9.3461 | 0.01878% | 9.7864 | 10.2476 | 10.7304 | 11.236 | 0 | 0 | 0 | 0.081366
2026-12-31 22:00 | 10.2266 | 0.02055% | 10.7084 | 11.213 | 11.7413 | 12.2946 | 0 | 0.061595 | 0.5157 | 0.99121
2026-12-31 23:00 | 10.7172 | 0.02154% | 11.2221 | 11.7509 | 12.3046 | 12.8844 | 0.069435 | 0.52391 | 0.99981 | 1.4981

## Assumptions
Power factor | 0.9
1-in-10 planning criteria:
24 | hours in a day
10 | years
87600 | hours in 10 years
0.0274% | % of hours for 1-in-10 lole
2.4 | hours per year where event could occur

## 99 LookUps (hidden)
DST Benefit Types
Distribution Capacity (Deferral or Avoidance Benefit)
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Innovation & Market
Transformation
Planning Value
DST Cost Types
DER Acquisition Cost
DER Operations, Maintenance, and Administrative (OM&A) Costs
Distribution System Ancillary Services Costs
Risks (Distribution System)
EST Benefit Types
DST Benefits
Transmission Capacity
Avoided Energy Costs
Avoided Generation Capacity Costs
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Planning Value
Innovation & Market Transformation
EST Cost Types
DST Costs
DER Acquisition Cost
DER (OM&A) Costs
Energy System Ancillary Costs
Risks (Energy System)