## 00 Cover
Benefit-Cost Analysis Data Filing Submission Template
All electricity distributors must complete both the Summary tab and the Annual Values tab to accompany their filing submission. Values in the Summary tab should be linked to the Annual Values tab or other additional tabs included by the electricity distributor using formulas.
Electricity distributors are strongly encouraged to include additional tabs providing the upstream calculations that deliver the Annual Values tab and Summary tab outputs.
Ontario Energy Board

## 01 Summary
General Information
Electricity Distributor Name | Elexicon Energy Inc.
Project or Program Name | Bradshaw Battery Storage Station Deferal
Description of NWS(s) (<150 words) | Elexicon proposes to administer a 14.3 MW/114.4MWh (8-hour) distribution battery to defer the expansion of the Bradshaw MS Upgrade by 1 year to 2032
Year for Net Present Value | 2026
Constant Dollar Year (i.e., nominal values deflated to this year) | 2026
Distribution Service Test
DST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV (Millions 2026 $)
Distribution Capacity Benefit | Distribution Capacity (Deferral or Avoidance Benefit) | 0.30489
Total DST Benefit |  | 0.30489
DST Costs
(Add more rows as required)
Cost | Cost Type | NPV (Millions 2026 $)
Capital Cost (Nominal $) | BESS Acquisition Cost | 33.119
Fixed O&M (Nominal $) | BESS Operations, Maintenance, and Administrative (OM&A) Costs | 12.7262
Total DST Cost |  | 45.8451
NPV Net DST Benefit | -45.5403
Energy System Test (NOT APPLICABLE)
EST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV
Benefit 1 [replace name]
Benefit 2 [replace name]
Benefit 3 [replace name]
Benefit 4 [replace name]
Benefit 5 [replace name]
Benefit 6 [replace name]
Total EST Benefit
EST Costs
(Add more rows as required)
Cost | Cost Type | NPV
Cost 1 [replace name]
Cost 2 [replace name]
Cost 3 [replace name]
Cost 4 [replace name]
Cost 5 [replace name]
Cost 6 [replace name]
Total EST Cost
NPV Net EST Benefit

## 02 Annual Values
Use only such rows as are required. Insert additional columns as required.
| Distribution Service Benefits | Distribution Service Costs
Calendar Year | Distribution Capacity Benefit | Capital Cost (Nominal $) | Fixed O&M (Nominal $)
2026 | 0 | 0 | 0
2027 | 0 | 0 | 0
2028 | 0 | 0 | 0
2029 | 0 | 0 | 0
2030 | 0 | 0 | 0
2031 | 0.916 | 4.0888 | 1.5711
2032 | -0.040412 | 4.0086 | 1.5403
2033 | -0.039179 | 3.93 | 1.5101
2034 | -0.037979 | 3.8529 | 1.4805
2035 | -0.036812 | 3.7774 | 1.4515
2036 | -0.035675 | 3.7033 | 1.423
2037 | -0.034569 | 3.6307 | 1.3951
2038 | -0.033492 | 3.5595 | 1.3678
2039 | -0.032445 | 3.4897 | 1.3409
2040 | -0.031425 | 3.4213 | 1.3146
2041 | -0.030433 | 3.3542 | 1.2889
2042 | -0.029468 | 3.2884 | 1.2636
2043 | -0.028529 | 3.224 | 1.2388
2044 | -0.027616 | 3.1607 | 1.2145
2045 | -0.026727 | 3.0988 | 1.1907
2046 | -0.025863 | 0 | 0
2047 | -0.025022 | 0 | 0
2048 | -0.024204 | 0 | 0
2049 | -0.023409 | 0 | 0
2050 | -0.022636 | 0 | 0
2051 | -0.021884 | 0 | 0
2052 | -0.021152 | 0 | 0
2053 | -0.020441 | 0 | 0
2054 | -0.01975 | 0 | 0
2055 | -0.019078 | 0 | 0
2056 | -0.018425 | 0 | 0
2057 | -0.01779 | 0 | 0
2058 | -0.017173 | 0 | 0
2059 | -0.016573 | 0 | 0
2060 | -0.01599 | 0 | 0
2061 | -0.015424 | 0 | 0
2062 | -0.014873 | 0 | 0
2063 | -0.014339 | 0 | 0
2064 | -0.013819 | 0 | 0
2065 | -0.013315 | 0 | 0
2066 | -0.012825 | 0 | 0
2067 | -0.012349 | 0 | 0
2068 | -0.011886 | 0 | 0
2069 | -0.011438 | 0 | 0
2070 | -0.011002 | 0 | 0
2071 | -0.010579 | 0 | 0
2072 | -1.4394e-16 | 0 | 0
2073 | 0 | 0 | 0
2074 | 0 | 0 | 0
2075 | 0 | 0 | 0
NPV | 0.30489 | 33.119 | 12.7262

## Inputs and Assumptions
Assumptions
Calculated Value
Economic Assumption | Value | Source |  | Manual Input
Debt % | 60% | Assumed
Equity % | 40%
Allowed Return on Equity (ROE) | 9.21% | Ontario Energy Board, 2024 Cost of Capital Parameters, October 2023
Deemed Long-Term Debt Rate | 4.88%
Federal Tax Rate | 15% | Government of Canada, Corporation Tax Rates, May 2022
Provincial Tax Rate | 11.5% | Government of Canada, Ontario – Provincial corporation tax, August 2023
Pre-tax Weighted Average Cost of Capital (WACC) | 7.94% | Calculated
O&M (percentage of capital expenditure) | 1.5% | Assumed
Inflation Rate | 2% | IESO Guide for NWAs
Social Discount Rate | 4%
Capital Recovery Factor | 11.94% | Calculated
LDC Calculations Inputs - Traditional Asset (Poles and Wires)
Inputs | Value | Source
Asset Life (years) | 40 | Assumed
Asset Cost (Millions $ - Nominal) | 8.47 | From DSP Budget
Asset Depreciation | Straight-line 2.5% per year for 40 years | Assumed
Depreciation | 2.5% | Assumed
LDC Calculations Inputs - Non Wire Solution Costs and Benefits (Millions $)
Inputs | Value | Source
Battery Storage Cost (2026 $) | 74.1798 | Per LDC Calculations
Distribution Capacity Benefit (2026 $) | 0.30489 | Per LDC Calculations
Cost 1 Capital Cost Nominal ($) | 67.7147 | Per LDC Calculations
Cost 2 Fixed O&M (Nominal $) | 26.0197 | Per LDC Calculations
LDC Calculations Inputs - Traditional Solution Expenditure Timelines (Millions $)
Year | Cost ($M) | Source
2029 | 2.19 | Elexicon DSP
2030 | 2.29 | Elexicon DSP
2031 | 3.99 | Elexicon DSP
Total | 8.47 | Elexicon DSP
LDC Calculations Inputs - Non-Wire Solution Parameters
Inputs | Value | Source
Battery Specs
Battery Size (MW) | 14.3 | Based on projected load growth; accounts for 10% efficiency loss
Hours | 8 | Based on number of consecutive hours in violation in 2031
Battery Discharge (MWh) | 114.4 | Calculated
Average Useful Life | 15 | Informed by Industry Research and EnergyAnalytics, 2025
Capital Cost ($/MW) - 2026 (8-hr battery) | 4735293.6262 | Calculated, including price reductions from 2024-2026 in NREL ATB
Fixed O&M ($/MW-year) - 2026 (8-hr battery) | 121304.1519 | Calculated, including price reductions from 2024-2026 in NREL ATB
Deferral Period (years) | 1 | Assumed
4-hour to 8-hour cost ratio
Capital Cost ($/kW)-2024 (4-hr battery) | 3051 | IESO, 2024
Fixed O&M ($/kW-year)-2024 (4-hr battery) | 76 | IESO, 2024
Capital Cost ($/kW) | 1.7424 | Calculated Using NREL ATB Baseline Capex ratio between 8-hr and 4-hr storage systems in 2026
Fixed O&M ($/kW-year) | 1.7919 | Calculated Using NREL ATB Baseline Fixed O&M ratio between 8-hr and 4-hr storage systems in 2026
Capital Cost ($/kW)-2024 (8-hr battery) | 5316.1403 | Calculated
Fixed O&M ($/kW-year)-2024 (8-hr battery) | 136.1837 | Calculated
2024-2026 Price Reduction | 14.38% | Calculated Using NREL ATB Baseline cost reduction in 4-hour battery storage in 2026 vs 2024 |  |  | Capital Cost ($/MW) - 2026 (4-hr battery)
Capital Cost ($/MW) - 2026 (4-hr battery) | 2717644.7873 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (4-hr battery) | 67696.1664 | Calculated Using IESO, 2024
Capital Cost ($/MW) - 2026 (8-hr battery) | 4735293.6262 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (8-hr battery) | 121304.1519 | Calculated Using IESO, 2024
Actual Asset Costs - Millions $ (Nominal)
Year | Inflation Index | Traditional Poles and Wires | Deferral via NWS
2026 | 100%
2027 | 102%
2028 | 104%
2029 | 106.1% | 2.19
2030 | 108.2% | 2.29 | 2.2338
2031 | 110.4% | 3.99 | 2.3358
2032 | 112.6% |  | 4.0698
2033 | 114.9% |  | 0
2034 | 117.2% |  | 0
2035 | 119.5% |  | 0
2036 | 121.9% |  | 0
2037 | 124.3% |  | 0
2038 | 126.8% |  | 0
2039 | 129.4% |  | 0
2040 | 131.9% |  | 0
2041 | 134.6% |  | 0
2042 | 137.3% |  | 0
2043 | 140% |  | 0
2044 | 142.8%
2045 | 145.7%
2046 | 148.6%
2047 | 151.6%
2048 | 154.6%
2049 | 157.7%
2050 | 160.8%
2051 | 164.1%
2052 | 167.3%
2053 | 170.7%
2054 | 174.1%
2055 | 177.6%
2056 | 181.1%
2057 | 184.8%
2058 | 188.5%
2059 | 192.2%
2060 | 196.1%
2061 | 200%
2062 | 204%
2063 | 208.1%
2064 | 212.2%
2065 | 216.5%
2066 | 220.8%
2067 | 225.2%
2068 | 229.7%
2069 | 234.3%
2070 | 239%
2071 | 243.8%
2072 | 248.7%
2073 | 253.6%
2074 | 258.7%
2075 | 263.9%
2076 | 269.2%
2077 | 274.5%
2078 | 280%
2079 | 285.6%
2080 | 291.3%

## Elexicon Calculations
Battery Storage |  |  |  |  | Alternative (Expansion) | [9 empty] | NPV Summary
|  |  | NPV | 45.8451 |  |  |  | NPV | 7.927 |  |  |  | NPV | 7.6222
|  |  |  | Cost - Millions (2026 $) |  | Installed at Time of Need |  |  |  |  | Deferred Installation |  |  |  |  | Cost of NWA | 45.8451
[8 empty] | Nominal | 2026 $ |  |  |  | Nominal | 2026 $ |  | Total Benefit of NWA | 0.30489
| Calendar Year | Cost 1 Capital Cost Nominal ($) | Cost 2 Fixed O&M (Nominal $) | Battery Storage Cost | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements |  | Net Benefit | -45.5403
| 2026 |  |  | 0 | 2026 | 0 |  | 0 | 0 | 2026 | 0 | 0 | 0 | 0
| 2027 |  |  | 0 | 2027 | 0 |  | 0 | 0 | 2027 | 0 | 0 | 0 | 0
| 2028 |  |  | 0 | 2028 | 0 |  | 0 | 0 | 2028 | 0 | 0 | 0 | 0
| 2029 |  |  | 0 | 2029 | 0 |  | 0 | 0 | 2029 | 0 | 0 | 0 | 0
| 2030 |  |  | 0 | 2030 | 0 |  | 0 | 0 | 2030 | 0 | 0 | 0 | 0
| 2031 | 4.0888 | 1.5711 | 5.6599 | 2031 | 8.47 | -0.21175 | 1.0113 | 0.916 | 2031 | 0 | 0 | 0 | 0
| 2032 | 4.0086 | 1.5403 | 5.5489 | 2032 | 8.2583 | -0.21175 | 0.98606 | 0.87559 | 2032 | 8.6394 | -0.21598 | 1.0316 | 0.916
| 2033 | 3.93 | 1.5101 | 5.4401 | 2033 | 8.0465 | -0.21175 | 0.96077 | 0.83641 | 2033 | 8.4234 | -0.21598 | 1.0058 | 0.87559
| 2034 | 3.8529 | 1.4805 | 5.3334 | 2034 | 7.8347 | -0.21175 | 0.93549 | 0.79843 | 2034 | 8.2074 | -0.21598 | 0.97999 | 0.83641
| 2035 | 3.7774 | 1.4515 | 5.2289 | 2035 | 7.623 | -0.21175 | 0.9102 | 0.76162 | 2035 | 7.9914 | -0.21598 | 0.9542 | 0.79843
| 2036 | 3.7033 | 1.423 | 5.1263 | 2036 | 7.4112 | -0.21175 | 0.88492 | 0.72594 | 2036 | 7.7755 | -0.21598 | 0.92841 | 0.76162
| 2037 | 3.6307 | 1.3951 | 5.0258 | 2037 | 7.1995 | -0.21175 | 0.85964 | 0.69138 | 2037 | 7.5595 | -0.21598 | 0.90262 | 0.72594
| 2038 | 3.5595 | 1.3678 | 4.9273 | 2038 | 6.9877 | -0.21175 | 0.83435 | 0.65788 | 2038 | 7.3435 | -0.21598 | 0.87683 | 0.69138
| 2039 | 3.4897 | 1.3409 | 4.8307 | 2039 | 6.776 | -0.21175 | 0.80907 | 0.62544 | 2039 | 7.1275 | -0.21598 | 0.85104 | 0.65788
| 2040 | 3.4213 | 1.3146 | 4.7359 | 2040 | 6.5642 | -0.21175 | 0.78379 | 0.59401 | 2040 | 6.9115 | -0.21598 | 0.82525 | 0.62544
| 2041 | 3.3542 | 1.2889 | 4.6431 | 2041 | 6.3525 | -0.21175 | 0.7585 | 0.56358 | 2041 | 6.6955 | -0.21598 | 0.79946 | 0.59401
| 2042 | 3.2884 | 1.2636 | 4.552 | 2042 | 6.1407 | -0.21175 | 0.73322 | 0.53411 | 2042 | 6.4795 | -0.21598 | 0.77367 | 0.56358
| 2043 | 3.224 | 1.2388 | 4.4628 | 2043 | 5.929 | -0.21175 | 0.70794 | 0.50558 | 2043 | 6.2636 | -0.21598 | 0.74789 | 0.53411
| 2044 | 3.1607 | 1.2145 | 4.3753 | 2044 | 5.7172 | -0.21175 | 0.68265 | 0.47797 | 2044 | 6.0476 | -0.21598 | 0.7221 | 0.50558
| 2045 | 3.0988 | 1.1907 | 4.2895 | 2045 | 5.5055 | -0.21175 | 0.65737 | 0.45124 | 2045 | 5.8316 | -0.21598 | 0.69631 | 0.47797
| 2046 |  |  |  | 2046 | 5.2937 | -0.21175 | 0.63209 | 0.42538 | 2046 | 5.6156 | -0.21598 | 0.67052 | 0.45124
| 2047 |  |  |  | 2047 | 5.082 | -0.21175 | 0.6068 | 0.40035 | 2047 | 5.3996 | -0.21598 | 0.64473 | 0.42538
| 2048 |  |  |  | 2048 | 4.8702 | -0.21175 | 0.58152 | 0.37615 | 2048 | 5.1836 | -0.21598 | 0.61894 | 0.40035
| 2049 |  |  |  | 2049 | 4.6585 | -0.21175 | 0.55624 | 0.35274 | 2049 | 4.9677 | -0.21598 | 0.59315 | 0.37615
| 2050 |  |  |  | 2050 | 4.4467 | -0.21175 | 0.53095 | 0.3301 | 2050 | 4.7517 | -0.21598 | 0.56736 | 0.35274
| 2051 |  |  |  | 2051 | 4.235 | -0.21175 | 0.50567 | 0.30822 | 2051 | 4.5357 | -0.21598 | 0.54157 | 0.3301
| 2052 |  |  |  | 2052 | 4.0232 | -0.21175 | 0.48039 | 0.28707 | 2052 | 4.3197 | -0.21598 | 0.51578 | 0.30822
| 2053 |  |  |  | 2053 | 3.8115 | -0.21175 | 0.4551 | 0.26663 | 2053 | 4.1037 | -0.21598 | 0.48999 | 0.28707
| 2054 |  |  |  | 2054 | 3.5997 | -0.21175 | 0.42982 | 0.24688 | 2054 | 3.8877 | -0.21598 | 0.4642 | 0.26663
| 2055 |  |  |  | 2055 | 3.388 | -0.21175 | 0.40454 | 0.2278 | 2055 | 3.6717 | -0.21598 | 0.43842 | 0.24688
| 2056 |  |  |  | 2056 | 3.1762 | -0.21175 | 0.37925 | 0.20937 | 2056 | 3.4558 | -0.21598 | 0.41263 | 0.2278
| 2057 |  |  |  | 2057 | 2.9645 | -0.21175 | 0.35397 | 0.19158 | 2057 | 3.2398 | -0.21598 | 0.38684 | 0.20937
| 2058 |  |  |  | 2058 | 2.7527 | -0.21175 | 0.32869 | 0.17441 | 2058 | 3.0238 | -0.21598 | 0.36105 | 0.19158
| 2059 |  |  |  | 2059 | 2.541 | -0.21175 | 0.3034 | 0.15784 | 2059 | 2.8078 | -0.21598 | 0.33526 | 0.17441
| 2060 |  |  |  | 2060 | 2.3292 | -0.21175 | 0.27812 | 0.14185 | 2060 | 2.5918 | -0.21598 | 0.30947 | 0.15784
| 2061 |  |  |  | 2061 | 2.1175 | -0.21175 | 0.25283 | 0.12642 | 2061 | 2.3758 | -0.21598 | 0.28368 | 0.14185
| 2062 |  |  |  | 2062 | 1.9057 | -0.21175 | 0.22755 | 0.11155 | 2062 | 2.1599 | -0.21598 | 0.25789 | 0.12642
| 2063 |  |  |  | 2063 | 1.694 | -0.21175 | 0.20227 | 0.097212 | 2063 | 1.9439 | -0.21598 | 0.2321 | 0.11155
| 2064 |  |  |  | 2064 | 1.4822 | -0.21175 | 0.17698 | 0.083393 | 2064 | 1.7279 | -0.21598 | 0.20631 | 0.097212
| 2065 |  |  |  | 2065 | 1.2705 | -0.21175 | 0.1517 | 0.070078 | 2065 | 1.5119 | -0.21598 | 0.18052 | 0.083393
| 2066 |  |  |  | 2066 | 1.0587 | -0.21175 | 0.12642 | 0.057253 | 2066 | 1.2959 | -0.21598 | 0.15473 | 0.070078
| 2067 |  |  |  | 2067 | 0.847 | -0.21175 | 0.10113 | 0.044904 | 2067 | 1.0799 | -0.21598 | 0.12895 | 0.057253
| 2068 |  |  |  | 2068 | 0.63525 | -0.21175 | 0.07585 | 0.033018 | 2068 | 0.86394 | -0.21598 | 0.10316 | 0.044904
| 2069 |  |  |  | 2069 | 0.4235 | -0.21175 | 0.050567 | 0.02158 | 2069 | 0.64796 | -0.21598 | 0.077367 | 0.033018
| 2070 |  |  |  | 2070 | 0.21175 | -0.21175 | 0.025283 | 0.010579 | 2070 | 0.43197 | -0.21598 | 0.051578 | 0.02158
| 2071 |  |  |  | 2071 | -5.7176e-15 | -0.21175 | -6.827e-16 | -2.8004e-16 | 2071 | 0.21599 | -0.21598 | 0.025789 | 0.010579
| 2072 |  |  |  | 2072 |  |  |  |  | 2072 | 2.9976e-15 | -0.21598 | 3.5792e-16 | 1.4394e-16
| 2073 |  |  |  | 2073 |  |  |  |  | 2073 | 0 | -0.21598 | 0 | 0
| 2074 |  |  |  | 2074 |  |  |  |  | 2074 | 0 | -0.21598 | 0 | 0
| 2075 |  |  |  | 2075 |  |  |  |  | 2075 | 0 | -0.21598 | 0 | 0
| 2076 |  |  |  | 2076 |  |  |  |  | 2076 | 0 | -0.21598 | 0 | 0

## BESS Inputs
Min MW BESS
Deferral length | Year | Bowmanville
1 | 2032 | 13
2 | 2033 | 15
3 | 2034 | 17
4 | 2035 | 19
Duration | Hours
Bowmanville | 8
CapEx for Deferred traditional solution - years of spend
Deferral length | Year1 | Year2 | Year3
1 | 2030 | 2031 | 2032
2 | 2031 | 2032 | 2033
3 | 2032 | 2033 | 2034
4 | 2033 | 2034 | 2035

## Input Calculation >>
The following tabs show how the battery solution was sized

## BESS Duration
Date | Hour | Date-Time | BOWMANVILLE 2025 (MVA) | BOWMANVILLE 2031 (MVA) | Exceeds N-1 Capacity? Y/N | MVA exceeding peak | Consecutive hours | Total consecutive length | Duration Determination
2025-01-01 | 00 | 2031-01-01 | 17.33 | 22.7687 | N | 0 |  |  |  | Bowmanville
2025-01-01 | 01 | 2031-01-01 01:00 | 16.01 | 21.0344 | N | 0 |  |  | 2031 PEAK (MVA) | 49.4
2025-01-01 | 02 | 2031-01-01 02:00 | 15.22 | 19.9965 | N | 0 |  |  | # of hours exceeding | 383
2025-01-01 | 03 | 2031-01-01 03:00 | 14.47 | 19.0111 | N | 0 |  |  | % of hours | 4.372%
2025-01-01 | 04 | 2031-01-01 04:00 | 14.08 | 18.4987 | N | 0 |  |  | MVA > N-1
2025-01-01 | 05 | 2031-01-01 05:00 | 13.69 | 17.9863 | N | 0 |  |  | avg | 4.7071
2025-01-01 | 06 | 2031-01-01 06:00 | 13.78 | 18.1046 | N | 0 |  |  | max | 12.22
2025-01-01 | 07 | 2031-01-01 07:00 | 14.13 | 18.5644 | N | 0 |  |  | median | 4.4553
2025-01-01 | 08 | 2031-01-01 08:00 | 14.76 | 19.3921 | N | 0 |  |  | MW>N-1
2025-01-01 | 09 | 2031-01-01 09:00 | 15.63 | 20.5352 | N | 0 |  |  | avg | 4.2364
2025-01-01 | 10 | 2031-01-01 10:00 | 16.79 | 22.0592 | N | 0 |  |  | max | 10.998
2025-01-01 | 11 | 2031-01-01 11:00 | 18.13 | 23.8197 | N | 0 |  |  | median | 4.0097
2025-01-01 | 12 | 2031-01-01 12:00 | 19.7 | 25.8824 | N | 0 |  |  | # of consecutive hours
2025-01-01 | 13 | 2031-01-01 13:00 | 19.65 | 25.8168 | N | 0 |  |  | avg | 8.7045
2025-01-01 | 14 | 2031-01-01 14:00 | 20.15 | 26.4737 | N | 0 |  |  | max | 14
2025-01-01 | 15 | 2031-01-01 15:00 | 19.83 | 26.0532 | N | 0 |  |  | median | 5
2025-01-01 | 16 | 2031-01-01 16:00 | 20.48 | 26.9072 | N | 0
2025-01-01 | 17 | 2031-01-01 17:00 | 22.04 | 28.9568 | N | 0
2025-01-01 | 18 | 2031-01-01 18:00 | 23.26 | 30.5597 | N | 0
2025-01-01 | 19 | 2031-01-01 19:00 | 23.01 | 30.2312 | N | 0
2025-01-01 | 20 | 2031-01-01 20:00 | 22.23 | 29.2064 | N | 0
2025-01-01 | 21 | 2031-01-01 21:00 | 21.39 | 28.1028 | N | 0
2025-01-01 | 22 | 2031-01-01 22:00 | 20.45 | 26.8678 | N | 0
2025-01-01 | 23 | 2031-01-01 23:00 | 19.23 | 25.2649 | N | 0
2025-01-02 | 00 | 2031-01-02 | 17.4 | 22.8606 | N | 0
2025-01-02 | 01 | 2031-01-02 01:00 | 16.02 | 21.0476 | N | 0
2025-01-02 | 02 | 2031-01-02 02:00 | 15.13 | 19.8782 | N | 0
2025-01-02 | 03 | 2031-01-02 03:00 | 14.53 | 19.0899 | N | 0
2025-01-02 | 04 | 2031-01-02 04:00 | 14.21 | 18.6695 | N | 0
2025-01-02 | 05 | 2031-01-02 05:00 | 14.25 | 18.7221 | N | 0
2025-01-02 | 06 | 2031-01-02 06:00 | 14.97 | 19.668 | N | 0
2025-01-02 | 07 | 2031-01-02 07:00 | 16.22 | 21.3103 | N | 0
2025-01-02 | 08 | 2031-01-02 08:00 | 17.99 | 23.6358 | N | 0
2025-01-02 | 09 | 2031-01-02 09:00 | 18.96 | 24.9102 | N | 0
2025-01-02 | 10 | 2031-01-02 10:00 | 19.72 | 25.9087 | N | 0
2025-01-02 | 11 | 2031-01-02 11:00 | 19.61 | 25.7642 | N | 0
2025-01-02 | 12 | 2031-01-02 12:00 | 20.13 | 26.4474 | N | 0
2025-01-02 | 13 | 2031-01-02 13:00 | 20.88 | 27.4328 | N | 0
2025-01-02 | 14 | 2031-01-02 14:00 | 20.85 | 27.3934 | N | 0
2025-01-02 | 15 | 2031-01-02 15:00 | 20.67 | 27.1569 | N | 0
2025-01-02 | 16 | 2031-01-02 16:00 | 20.79 | 27.3145 | N | 0
2025-01-02 | 17 | 2031-01-02 17:00 | 22.93 | 30.1261 | N | 0
2025-01-02 | 18 | 2031-01-02 18:00 | 24.49 | 32.1757 | N | 0
2025-01-02 | 19 | 2031-01-02 19:00 | 24.53 | 32.2282 | N | 0
2025-01-02 | 20 | 2031-01-02 20:00 | 23.31 | 30.6254 | N | 0
2025-01-02 | 21 | 2031-01-02 21:00 | 23.05 | 30.2838 | N | 0
2025-01-02 | 22 | 2031-01-02 22:00 | 21.78 | 28.6152 | N | 0
2025-01-02 | 23 | 2031-01-02 23:00 | 20.81 | 27.3408 | N | 0
2025-01-03 | 00 | 2031-01-03 | 19.11 | 25.1073 | N | 0
2025-01-03 | 01 | 2031-01-03 01:00 | 17.53 | 23.0314 | N | 0
2025-01-03 | 02 | 2031-01-03 02:00 | 16.32 | 21.4417 | N | 0
2025-01-03 | 03 | 2031-01-03 03:00 | 15.87 | 20.8505 | N | 0
2025-01-03 | 04 | 2031-01-03 04:00 | 15.42 | 20.2593 | N | 0
2025-01-03 | 05 | 2031-01-03 05:00 | 15.59 | 20.4826 | N | 0
2025-01-03 | 06 | 2031-01-03 06:00 | 16.16 | 21.2315 | N | 0
2025-01-03 | 07 | 2031-01-03 07:00 | 17.59 | 23.1103 | N | 0
2025-01-03 | 08 | 2031-01-03 08:00 | 18.83 | 24.7394 | N | 0
2025-01-03 | 09 | 2031-01-03 09:00 | 19.92 | 26.1715 | N | 0
2025-01-03 | 10 | 2031-01-03 10:00 | 20.48 | 26.9072 | N | 0
2025-01-03 | 11 | 2031-01-03 11:00 | 20.85 | 27.3934 | N | 0
2025-01-03 | 12 | 2031-01-03 12:00 | 21.63 | 28.4181 | N | 0
2025-01-03 | 13 | 2031-01-03 13:00 | 21.55 | 28.313 | N | 0
2025-01-03 | 14 | 2031-01-03 14:00 | 21.78 | 28.6152 | N | 0
2025-01-03 | 15 | 2031-01-03 15:00 | 21.8 | 28.6415 | N | 0
2025-01-03 | 16 | 2031-01-03 16:00 | 21.7 | 28.5101 | N | 0
2025-01-03 | 17 | 2031-01-03 17:00 | 23.04 | 30.2706 | N | 0
2025-01-03 | 18 | 2031-01-03 18:00 | 24.55 | 32.2545 | N | 0
2025-01-03 | 19 | 2031-01-03 19:00 | 24.29 | 31.9129 | N | 0
2025-01-03 | 20 | 2031-01-03 20:00 | 23.55 | 30.9407 | N | 0
2025-01-03 | 21 | 2031-01-03 21:00 | 23.38 | 30.7173 | N | 0
2025-01-03 | 22 | 2031-01-03 22:00 | 22.44 | 29.4823 | N | 0
2025-01-03 | 23 | 2031-01-03 23:00 | 21.43 | 28.1554 | N | 0
2025-01-04 | 00 | 2031-01-04 | 19.83 | 26.0532 | N | 0
2025-01-04 | 01 | 2031-01-04 01:00 | 18.36 | 24.1219 | N | 0
2025-01-04 | 02 | 2031-01-04 02:00 | 17.33 | 22.7687 | N | 0
2025-01-04 | 03 | 2031-01-04 03:00 | 16.52 | 21.7045 | N | 0
2025-01-04 | 04 | 2031-01-04 04:00 | 16.18 | 21.2578 | N | 0
2025-01-04 | 05 | 2031-01-04 05:00 | 16.16 | 21.2315 | N | 0
2025-01-04 | 06 | 2031-01-04 06:00 | 16.38 | 21.5205 | N | 0
2025-01-04 | 07 | 2031-01-04 07:00 | 16.61 | 21.8227 | N | 0
2025-01-04 | 08 | 2031-01-04 08:00 | 18.18 | 23.8854 | N | 0
2025-01-04 | 09 | 2031-01-04 09:00 | 18.82 | 24.7263 | N | 0
2025-01-04 | 10 | 2031-01-04 10:00 | 19.69 | 25.8693 | N | 0
2025-01-04 | 11 | 2031-01-04 11:00 | 21.12 | 27.7481 | N | 0
2025-01-04 | 12 | 2031-01-04 12:00 | 22.25 | 29.2327 | N | 0
2025-01-04 | 13 | 2031-01-04 13:00 | 22.79 | 29.9422 | N | 0
2025-01-04 | 14 | 2031-01-04 14:00 | 22.85 | 30.021 | N | 0
2025-01-04 | 15 | 2031-01-04 15:00 | 22.94 | 30.1393 | N | 0
2025-01-04 | 16 | 2031-01-04 16:00 | 23.09 | 30.3363 | N | 0
2025-01-04 | 17 | 2031-01-04 17:00 | 24.16 | 31.7421 | N | 0
2025-01-04 | 18 | 2031-01-04 18:00 | 25.6 | 33.634 | N | 0
2025-01-04 | 19 | 2031-01-04 19:00 | 25.21 | 33.1216 | N | 0
2025-01-04 | 20 | 2031-01-04 20:00 | 24.76 | 32.5304 | N | 0
2025-01-04 | 21 | 2031-01-04 21:00 | 23.77 | 31.2297 | N | 0
2025-01-04 | 22 | 2031-01-04 22:00 | 22.76 | 29.9028 | N | 0
2025-01-04 | 23 | 2031-01-04 23:00 | 21.62 | 28.405 | N | 0
2025-01-05 | 00 | 2031-01-05 | 20.26 | 26.6182 | N | 0
2025-01-05 | 01 | 2031-01-05 01:00 | 18.32 | 24.0694 | N | 0
2025-01-05 | 02 | 2031-01-05 02:00 | 17.53 | 23.0314 | N | 0
2025-01-05 | 03 | 2031-01-05 03:00 | 16.59 | 21.7964 | N | 0
2025-01-05 | 04 | 2031-01-05 04:00 | 16.12 | 21.1789 | N | 0
2025-01-05 | 05 | 2031-01-05 05:00 | 15.98 | 20.995 | N | 0
2025-01-05 | 06 | 2031-01-05 06:00 | 16 | 21.0213 | N | 0
2025-01-05 | 07 | 2031-01-05 07:00 | 16.48 | 21.6519 | N | 0
2025-01-05 | 08 | 2031-01-05 08:00 | 17.48 | 22.9657 | N | 0
2025-01-05 | 09 | 2031-01-05 09:00 | 18.59 | 24.4241 | N | 0
2025-01-05 | 10 | 2031-01-05 10:00 | 19.76 | 25.9613 | N | 0
2025-01-05 | 11 | 2031-01-05 11:00 | 21.14 | 27.7744 | N | 0
2025-01-05 | 12 | 2031-01-05 12:00 | 22.33 | 29.3378 | N | 0
2025-01-05 | 13 | 2031-01-05 13:00 | 22.98 | 30.1918 | N | 0
2025-01-05 | 14 | 2031-01-05 14:00 | 22.9 | 30.0867 | N | 0
2025-01-05 | 15 | 2031-01-05 15:00 | 23.02 | 30.2444 | N | 0
2025-01-05 | 16 | 2031-01-05 16:00 | 23.44 | 30.7962 | N | 0
2025-01-05 | 17 | 2031-01-05 17:00 | 25.28 | 33.2136 | N | 0
2025-01-05 | 18 | 2031-01-05 18:00 | 27.15 | 35.6705 | N | 0
2025-01-05 | 19 | 2031-01-05 19:00 | 26.38 | 34.6588 | N | 0
2025-01-05 | 20 | 2031-01-05 20:00 | 25.08 | 32.9509 | N | 0
2025-01-05 | 21 | 2031-01-05 21:00 | 24.26 | 31.8735 | N | 0
2025-01-05 | 22 | 2031-01-05 22:00 | 22.93 | 30.1261 | N | 0
2025-01-05 | 23 | 2031-01-05 23:00 | 21.06 | 27.6693 | N | 0
2025-01-06 | 00 | 2031-01-06 | 18.66 | 24.5161 | N | 0
2025-01-06 | 01 | 2031-01-06 01:00 | 17.09 | 22.4534 | N | 0
2025-01-06 | 02 | 2031-01-06 02:00 | 15.93 | 20.9293 | N | 0
2025-01-06 | 03 | 2031-01-06 03:00 | 15.64 | 20.5483 | N | 0
2025-01-06 | 04 | 2031-01-06 04:00 | 15.42 | 20.2593 | N | 0
2025-01-06 | 05 | 2031-01-06 05:00 | 15.73 | 20.6665 | N | 0
2025-01-06 | 06 | 2031-01-06 06:00 | 17.22 | 22.6241 | N | 0
2025-01-06 | 07 | 2031-01-06 07:00 | 19.31 | 25.3701 | N | 0
2025-01-06 | 08 | 2031-01-06 08:00 | 21.57 | 28.3393 | N | 0
2025-01-06 | 09 | 2031-01-06 09:00 | 22.64 | 29.7451 | N | 0
2025-01-06 | 10 | 2031-01-06 10:00 | 22.83 | 29.9947 | N | 0
2025-01-06 | 11 | 2031-01-06 11:00 | 23.29 | 30.5991 | N | 0
2025-01-06 | 12 | 2031-01-06 12:00 | 23.79 | 31.256 | N | 0
2025-01-06 | 13 | 2031-01-06 13:00 | 22.64 | 29.7451 | N | 0
2025-01-06 | 14 | 2031-01-06 14:00 | 22.74 | 29.8765 | N | 0
2025-01-06 | 15 | 2031-01-06 15:00 | 22.81 | 29.9685 | N | 0
2025-01-06 | 16 | 2031-01-06 16:00 | 22.56 | 29.64 | N | 0
2025-01-06 | 17 | 2031-01-06 17:00 | 24.77 | 32.5436 | N | 0
2025-01-06 | 18 | 2031-01-06 18:00 | 26.9 | 35.342 | N | 0
2025-01-06 | 19 | 2031-01-06 19:00 | 26.57 | 34.9085 | N | 0
2025-01-06 | 20 | 2031-01-06 20:00 | 25.81 | 33.9099 | N | 0
2025-01-06 | 21 | 2031-01-06 21:00 | 24.79 | 32.5698 | N | 0
2025-01-06 | 22 | 2031-01-06 22:00 | 23.99 | 31.5188 | N | 0
2025-01-06 | 23 | 2031-01-06 23:00 | 22.64 | 29.7451 | N | 0
2025-01-07 | 00 | 2031-01-07 | 20.54 | 26.9861 | N | 0
2025-01-07 | 01 | 2031-01-07 01:00 | 18.76 | 24.6474 | N | 0
2025-01-07 | 02 | 2031-01-07 02:00 | 17.79 | 23.373 | N | 0
2025-01-07 | 03 | 2031-01-07 03:00 | 17.13 | 22.5059 | N | 0
2025-01-07 | 04 | 2031-01-07 04:00 | 16.85 | 22.138 | N | 0
2025-01-07 | 05 | 2031-01-07 05:00 | 17.05 | 22.4008 | N | 0
2025-01-07 | 06 | 2031-01-07 06:00 | 17.97 | 23.6095 | N | 0
2025-01-07 | 07 | 2031-01-07 07:00 | 20.23 | 26.5788 | N | 0
2025-01-07 | 08 | 2031-01-07 08:00 | 22.55 | 29.6269 | N | 0
2025-01-07 | 09 | 2031-01-07 09:00 | 23.06 | 30.2969 | N | 0
2025-01-07 | 10 | 2031-01-07 10:00 | 23.11 | 30.3626 | N | 0
2025-01-07 | 11 | 2031-01-07 11:00 | 22.94 | 30.1393 | N | 0
2025-01-07 | 12 | 2031-01-07 12:00 | 22.93 | 30.1261 | N | 0
2025-01-07 | 13 | 2031-01-07 13:00 | 23.3 | 30.6122 | N | 0
2025-01-07 | 14 | 2031-01-07 14:00 | 22.98 | 30.1918 | N | 0
2025-01-07 | 15 | 2031-01-07 15:00 | 23 | 30.2181 | N | 0
2025-01-07 | 16 | 2031-01-07 16:00 | 23.66 | 31.0852 | N | 0
2025-01-07 | 17 | 2031-01-07 17:00 | 25.55 | 33.5684 | N | 0
2025-01-07 | 18 | 2031-01-07 18:00 | 26.89 | 35.3289 | N | 0
2025-01-07 | 19 | 2031-01-07 19:00 | 26.3 | 34.5537 | N | 0
2025-01-07 | 20 | 2031-01-07 20:00 | 25.37 | 33.3319 | N | 0
2025-01-07 | 21 | 2031-01-07 21:00 | 25.04 | 32.8983 | N | 0
2025-01-07 | 22 | 2031-01-07 22:00 | 24.28 | 31.8998 | N | 0
2025-01-07 | 23 | 2031-01-07 23:00 | 22.25 | 29.2327 | N | 0
2025-01-08 | 00 | 2031-01-08 | 20.47 | 26.8941 | N | 0
2025-01-08 | 01 | 2031-01-08 01:00 | 18.93 | 24.8708 | N | 0
2025-01-08 | 02 | 2031-01-08 02:00 | 18.05 | 23.7146 | N | 0
2025-01-08 | 03 | 2031-01-08 03:00 | 17.77 | 23.3468 | N | 0
2025-01-08 | 04 | 2031-01-08 04:00 | 17.56 | 23.0709 | N | 0
2025-01-08 | 05 | 2031-01-08 05:00 | 17.93 | 23.557 | N | 0
2025-01-08 | 06 | 2031-01-08 06:00 | 19.13 | 25.1336 | N | 0
2025-01-08 | 07 | 2031-01-08 07:00 | 21.84 | 28.694 | N | 0
2025-01-08 | 08 | 2031-01-08 08:00 | 23.66 | 31.0852 | N | 0
2025-01-08 | 09 | 2031-01-08 09:00 | 24.24 | 31.8472 | N | 0
2025-01-08 | 10 | 2031-01-08 10:00 | 24.05 | 31.5976 | N | 0
2025-01-08 | 11 | 2031-01-08 11:00 | 24.28 | 31.8998 | N | 0
2025-01-08 | 12 | 2031-01-08 12:00 | 23.95 | 31.4662 | N | 0
2025-01-08 | 13 | 2031-01-08 13:00 | 24 | 31.5319 | N | 0
2025-01-08 | 14 | 2031-01-08 14:00 | 23.7 | 31.1378 | N | 0
2025-01-08 | 15 | 2031-01-08 15:00 | 23.27 | 30.5728 | N | 0
2025-01-08 | 16 | 2031-01-08 16:00 | 23.65 | 31.0721 | N | 0
2025-01-08 | 17 | 2031-01-08 17:00 | 26.24 | 34.4749 | N | 0
2025-01-08 | 18 | 2031-01-08 18:00 | 27.6 | 36.2617 | N | 0
2025-01-08 | 19 | 2031-01-08 19:00 | 27.55 | 36.196 | N | 0
2025-01-08 | 20 | 2031-01-08 20:00 | 26.19 | 34.4092 | N | 0
2025-01-08 | 21 | 2031-01-08 21:00 | 25.96 | 34.107 | N | 0
2025-01-08 | 22 | 2031-01-08 22:00 | 24.87 | 32.6749 | N | 0
2025-01-08 | 23 | 2031-01-08 23:00 | 23.04 | 30.2706 | N | 0
2025-01-09 | 00 | 2031-01-09 | 21.05 | 27.6561 | N | 0
2025-01-09 | 01 | 2031-01-09 01:00 | 20 | 26.2766 | N | 0
2025-01-09 | 02 | 2031-01-09 02:00 | 18.54 | 24.3584 | N | 0
2025-01-09 | 03 | 2031-01-09 03:00 | 18.04 | 23.7015 | N | 0
2025-01-09 | 04 | 2031-01-09 04:00 | 17.88 | 23.4913 | N | 0
2025-01-09 | 05 | 2031-01-09 05:00 | 18.02 | 23.6752 | N | 0
2025-01-09 | 06 | 2031-01-09 06:00 | 19.14 | 25.1467 | N | 0
2025-01-09 | 07 | 2031-01-09 07:00 | 21.64 | 28.4313 | N | 0
2025-01-09 | 08 | 2031-01-09 08:00 | 23.56 | 30.9538 | N | 0
2025-01-09 | 09 | 2031-01-09 09:00 | 23.82 | 31.2954 | N | 0
2025-01-09 | 10 | 2031-01-09 10:00 | 23.54 | 30.9276 | N | 0
2025-01-09 | 11 | 2031-01-09 11:00 | 23.49 | 30.8619 | N | 0
2025-01-09 | 12 | 2031-01-09 12:00 | 23.45 | 30.8093 | N | 0
2025-01-09 | 13 | 2031-01-09 13:00 | 23.38 | 30.7173 | N | 0
2025-01-09 | 14 | 2031-01-09 14:00 | 23.39 | 30.7305 | N | 0
2025-01-09 | 15 | 2031-01-09 15:00 | 23.3 | 30.6122 | N | 0
2025-01-09 | 16 | 2031-01-09 16:00 | 23.18 | 30.4546 | N | 0
2025-01-09 | 17 | 2031-01-09 17:00 | 25.54 | 33.5552 | N | 0
2025-01-09 | 18 | 2031-01-09 18:00 | 26.91 | 35.3552 | N | 0
2025-01-09 | 19 | 2031-01-09 19:00 | 26.68 | 35.053 | N | 0
2025-01-09 | 20 | 2031-01-09 20:00 | 26.2 | 34.4223 | N | 0
2025-01-09 | 21 | 2031-01-09 21:00 | 25.88 | 34.0019 | N | 0
2025-01-09 | 22 | 2031-01-09 22:00 | 24.59 | 32.3071 | N | 0
2025-01-09 | 23 | 2031-01-09 23:00 | 22.99 | 30.2049 | N | 0
2025-01-10 | 00 | 2031-01-10 | 21.1 | 27.7218 | N | 0
2025-01-10 | 01 | 2031-01-10 01:00 | 19.44 | 25.5409 | N | 0
2025-01-10 | 02 | 2031-01-10 02:00 | 18.18 | 23.8854 | N | 0
2025-01-10 | 03 | 2031-01-10 03:00 | 17.77 | 23.3468 | N | 0
2025-01-10 | 04 | 2031-01-10 04:00 | 17.64 | 23.176 | N | 0
2025-01-10 | 05 | 2031-01-10 05:00 | 17.58 | 23.0971 | N | 0
2025-01-10 | 06 | 2031-01-10 06:00 | 18.37 | 24.1351 | N | 0
2025-01-10 | 07 | 2031-01-10 07:00 | 20.47 | 26.8941 | N | 0
2025-01-10 | 08 | 2031-01-10 08:00 | 23.03 | 30.2575 | N | 0
2025-01-10 | 09 | 2031-01-10 09:00 | 23.99 | 31.5188 | N | 0
2025-01-10 | 10 | 2031-01-10 10:00 | 23.88 | 31.3743 | N | 0
2025-01-10 | 11 | 2031-01-10 11:00 | 23.84 | 31.3217 | N | 0
2025-01-10 | 12 | 2031-01-10 12:00 | 23.52 | 30.9013 | N | 0
2025-01-10 | 13 | 2031-01-10 13:00 | 23.08 | 30.3232 | N | 0
2025-01-10 | 14 | 2031-01-10 14:00 | 22.29 | 29.2853 | N | 0
2025-01-10 | 15 | 2031-01-10 15:00 | 22.69 | 29.8108 | N | 0
2025-01-10 | 16 | 2031-01-10 16:00 | 23.12 | 30.3757 | N | 0
2025-01-10 | 17 | 2031-01-10 17:00 | 24.28 | 31.8998 | N | 0
2025-01-10 | 18 | 2031-01-10 18:00 | 25.14 | 33.0297 | N | 0
2025-01-10 | 19 | 2031-01-10 19:00 | 24.95 | 32.7801 | N | 0
2025-01-10 | 20 | 2031-01-10 20:00 | 23.85 | 31.3348 | N | 0
2025-01-10 | 21 | 2031-01-10 21:00 | 23.63 | 31.0458 | N | 0
2025-01-10 | 22 | 2031-01-10 22:00 | 22.71 | 29.8371 | N | 0
2025-01-10 | 23 | 2031-01-10 23:00 | 21.78 | 28.6152 | N | 0
2025-01-11 | 00 | 2031-01-11 | 19.63 | 25.7905 | N | 0
2025-01-11 | 01 | 2031-01-11 01:00 | 17.98 | 23.6227 | N | 0
2025-01-11 | 02 | 2031-01-11 02:00 | 16.98 | 22.3088 | N | 0
2025-01-11 | 03 | 2031-01-11 03:00 | 16.22 | 21.3103 | N | 0
2025-01-11 | 04 | 2031-01-11 04:00 | 15.67 | 20.5877 | N | 0
2025-01-11 | 05 | 2031-01-11 05:00 | 15.64 | 20.5483 | N | 0
2025-01-11 | 06 | 2031-01-11 06:00 | 15.82 | 20.7848 | N | 0
2025-01-11 | 07 | 2031-01-11 07:00 | 16.68 | 21.9147 | N | 0
2025-01-11 | 08 | 2031-01-11 08:00 | 17.85 | 23.4519 | N | 0
2025-01-11 | 09 | 2031-01-11 09:00 | 19.25 | 25.2912 | N | 0
2025-01-11 | 10 | 2031-01-11 10:00 | 20.34 | 26.7233 | N | 0
2025-01-11 | 11 | 2031-01-11 11:00 | 21.12 | 27.7481 | N | 0
2025-01-11 | 12 | 2031-01-11 12:00 | 21.62 | 28.405 | N | 0
2025-01-11 | 13 | 2031-01-11 13:00 | 21.64 | 28.4313 | N | 0
2025-01-11 | 14 | 2031-01-11 14:00 | 21.41 | 28.1291 | N | 0
2025-01-11 | 15 | 2031-01-11 15:00 | 21.04 | 27.643 | N | 0
2025-01-11 | 16 | 2031-01-11 16:00 | 21.69 | 28.497 | N | 0
2025-01-11 | 17 | 2031-01-11 17:00 | 22.82 | 29.9816 | N | 0
2025-01-11 | 18 | 2031-01-11 18:00 | 24.38 | 32.0312 | N | 0
2025-01-11 | 19 | 2031-01-11 19:00 | 24.09 | 31.6502 | N | 0
2025-01-11 | 20 | 2031-01-11 20:00 | 23.05 | 30.2838 | N | 0
2025-01-11 | 21 | 2031-01-11 21:00 | 22.14 | 29.0882 | N | 0
2025-01-11 | 22 | 2031-01-11 22:00 | 21.22 | 27.8795 | N | 0
2025-01-11 | 23 | 2031-01-11 23:00 | 19.93 | 26.1846 | N | 0
2025-01-12 | 00 | 2031-01-12 | 18.43 | 24.2139 | N | 0
2025-01-12 | 01 | 2031-01-12 01:00 | 17.27 | 22.6898 | N | 0
2025-01-12 | 02 | 2031-01-12 02:00 | 16.22 | 21.3103 | N | 0
2025-01-12 | 03 | 2031-01-12 03:00 | 15.47 | 20.3249 | N | 0
2025-01-12 | 04 | 2031-01-12 04:00 | 15.05 | 19.7731 | N | 0
2025-01-12 | 05 | 2031-01-12 05:00 | 15.01 | 19.7206 | N | 0
2025-01-12 | 06 | 2031-01-12 06:00 | 15.22 | 19.9965 | N | 0
2025-01-12 | 07 | 2031-01-12 07:00 | 15.71 | 20.6403 | N | 0
2025-01-12 | 08 | 2031-01-12 08:00 | 16.84 | 22.1249 | N | 0
2025-01-12 | 09 | 2031-01-12 09:00 | 18 | 23.6489 | N | 0
2025-01-12 | 10 | 2031-01-12 10:00 | 19.38 | 25.462 | N | 0
2025-01-12 | 11 | 2031-01-12 11:00 | 20.32 | 26.697 | N | 0
2025-01-12 | 12 | 2031-01-12 12:00 | 20.89 | 27.4459 | N | 0
2025-01-12 | 13 | 2031-01-12 13:00 | 21.6 | 28.3787 | N | 0
2025-01-12 | 14 | 2031-01-12 14:00 | 21.05 | 27.6561 | N | 0
2025-01-12 | 15 | 2031-01-12 15:00 | 21.9 | 28.7729 | N | 0
2025-01-12 | 16 | 2031-01-12 16:00 | 22.62 | 29.7188 | N | 0
2025-01-12 | 17 | 2031-01-12 17:00 | 24.3 | 31.9261 | N | 0
2025-01-12 | 18 | 2031-01-12 18:00 | 25.47 | 33.4632 | N | 0
2025-01-12 | 19 | 2031-01-12 19:00 | 24.87 | 32.6749 | N | 0
2025-01-12 | 20 | 2031-01-12 20:00 | 23.55 | 30.9407 | N | 0
2025-01-12 | 21 | 2031-01-12 21:00 | 23.12 | 30.3757 | N | 0
2025-01-12 | 22 | 2031-01-12 22:00 | 21.65 | 28.4444 | N | 0
2025-01-12 | 23 | 2031-01-12 23:00 | 20.06 | 26.3554 | N | 0
2025-01-13 | 00 | 2031-01-13 | 18.06 | 23.7278 | N | 0
2025-01-13 | 01 | 2031-01-13 01:00 | 16.42 | 21.5731 | N | 0
2025-01-13 | 02 | 2031-01-13 02:00 | 15.28 | 20.0753 | N | 0
2025-01-13 | 03 | 2031-01-13 03:00 | 14.65 | 19.2476 | N | 0
2025-01-13 | 04 | 2031-01-13 04:00 | 14.35 | 18.8535 | N | 0
2025-01-13 | 05 | 2031-01-13 05:00 | 14.62 | 19.2082 | N | 0
2025-01-13 | 06 | 2031-01-13 06:00 | 15.55 | 20.4301 | N | 0
2025-01-13 | 07 | 2031-01-13 07:00 | 17.74 | 23.3073 | N | 0
2025-01-13 | 08 | 2031-01-13 08:00 | 20.32 | 26.697 | N | 0
2025-01-13 | 09 | 2031-01-13 09:00 | 20.99 | 27.5773 | N | 0
2025-01-13 | 10 | 2031-01-13 10:00 | 20.98 | 27.5641 | N | 0
2025-01-13 | 11 | 2031-01-13 11:00 | 21.23 | 27.8926 | N | 0
2025-01-13 | 12 | 2031-01-13 12:00 | 21.54 | 28.2999 | N | 0
2025-01-13 | 13 | 2031-01-13 13:00 | 22.01 | 28.9174 | N | 0
2025-01-13 | 14 | 2031-01-13 14:00 | 22.46 | 29.5086 | N | 0
2025-01-13 | 15 | 2031-01-13 15:00 | 22.28 | 29.2721 | N | 0
2025-01-13 | 16 | 2031-01-13 16:00 | 22.34 | 29.351 | N | 0
2025-01-13 | 17 | 2031-01-13 17:00 | 24.17 | 31.7553 | N | 0
2025-01-13 | 18 | 2031-01-13 18:00 | 25.57 | 33.5946 | N | 0
2025-01-13 | 19 | 2031-01-13 19:00 | 25.77 | 33.8574 | N | 0
2025-01-13 | 20 | 2031-01-13 20:00 | 24.38 | 32.0312 | N | 0
2025-01-13 | 21 | 2031-01-13 21:00 | 23.79 | 31.256 | N | 0
2025-01-13 | 22 | 2031-01-13 22:00 | 22.66 | 29.7714 | N | 0
2025-01-13 | 23 | 2031-01-13 23:00 | 21.17 | 27.8138 | N | 0
2025-01-14 | 00 | 2031-01-14 | 19.34 | 25.4095 | N | 0
2025-01-14 | 01 | 2031-01-14 01:00 | 17.68 | 23.2285 | N | 0
2025-01-14 | 02 | 2031-01-14 02:00 | 17.14 | 22.519 | N | 0
2025-01-14 | 03 | 2031-01-14 03:00 | 16.48 | 21.6519 | N | 0
2025-01-14 | 04 | 2031-01-14 04:00 | 16.28 | 21.3891 | N | 0
2025-01-14 | 05 | 2031-01-14 05:00 | 16.55 | 21.7439 | N | 0
2025-01-14 | 06 | 2031-01-14 06:00 | 17.6 | 23.1234 | N | 0
2025-01-14 | 07 | 2031-01-14 07:00 | 19.85 | 26.0795 | N | 0
2025-01-14 | 08 | 2031-01-14 08:00 | 22.23 | 29.2064 | N | 0
2025-01-14 | 09 | 2031-01-14 09:00 | 22.87 | 30.0473 | N | 0
2025-01-14 | 10 | 2031-01-14 10:00 | 22.79 | 29.9422 | N | 0
2025-01-14 | 11 | 2031-01-14 11:00 | 23.08 | 30.3232 | N | 0
2025-01-14 | 12 | 2031-01-14 12:00 | 22.76 | 29.9028 | N | 0
2025-01-14 | 13 | 2031-01-14 13:00 | 22.91 | 30.0998 | N | 0
2025-01-14 | 14 | 2031-01-14 14:00 | 22.55 | 29.6269 | N | 0
2025-01-14 | 15 | 2031-01-14 15:00 | 22.21 | 29.1802 | N | 0
2025-01-14 | 16 | 2031-01-14 16:00 | 22.02 | 28.9305 | N | 0
2025-01-14 | 17 | 2031-01-14 17:00 | 23.74 | 31.1903 | N | 0
2025-01-14 | 18 | 2031-01-14 18:00 | 26.55 | 34.8822 | N | 0
2025-01-14 | 19 | 2031-01-14 19:00 | 26.13 | 34.3304 | N | 0
2025-01-14 | 20 | 2031-01-14 20:00 | 25.04 | 32.8983 | N | 0
2025-01-14 | 21 | 2031-01-14 21:00 | 24.62 | 32.3465 | N | 0
2025-01-14 | 22 | 2031-01-14 22:00 | 23.96 | 31.4794 | N | 0
2025-01-14 | 23 | 2031-01-14 23:00 | 22.58 | 29.6663 | N | 0
2025-01-15 | 00 | 2031-01-15 | 20.44 | 26.8547 | N | 0
2025-01-15 | 01 | 2031-01-15 01:00 | 18.59 | 24.4241 | N | 0
2025-01-15 | 02 | 2031-01-15 02:00 | 17.75 | 23.3205 | N | 0
2025-01-15 | 03 | 2031-01-15 03:00 | 17.22 | 22.6241 | N | 0
2025-01-15 | 04 | 2031-01-15 04:00 | 16.93 | 22.2431 | N | 0
2025-01-15 | 05 | 2031-01-15 05:00 | 17.51 | 23.0052 | N | 0
2025-01-15 | 06 | 2031-01-15 06:00 | 18.1 | 23.7803 | N | 0
2025-01-15 | 07 | 2031-01-15 07:00 | 20.96 | 27.5379 | N | 0
2025-01-15 | 08 | 2031-01-15 08:00 | 22.78 | 29.929 | N | 0
2025-01-15 | 09 | 2031-01-15 09:00 | 23.03 | 30.2575 | N | 0
2025-01-15 | 10 | 2031-01-15 10:00 | 22.95 | 30.1524 | N | 0
2025-01-15 | 11 | 2031-01-15 11:00 | 23.31 | 30.6254 | N | 0
2025-01-15 | 12 | 2031-01-15 12:00 | 23.64 | 31.0589 | N | 0
2025-01-15 | 13 | 2031-01-15 13:00 | 23.73 | 31.1772 | N | 0
2025-01-15 | 14 | 2031-01-15 14:00 | 23.28 | 30.586 | N | 0
2025-01-15 | 15 | 2031-01-15 15:00 | 23.05 | 30.2838 | N | 0
2025-01-15 | 16 | 2031-01-15 16:00 | 23.43 | 30.783 | N | 0
2025-01-15 | 17 | 2031-01-15 17:00 | 24.66 | 32.399 | N | 0
2025-01-15 | 18 | 2031-01-15 18:00 | 26.15 | 34.3566 | N | 0
2025-01-15 | 19 | 2031-01-15 19:00 | 25.97 | 34.1202 | N | 0
2025-01-15 | 20 | 2031-01-15 20:00 | 24.84 | 32.6355 | N | 0
2025-01-15 | 21 | 2031-01-15 21:00 | 24.81 | 32.5961 | N | 0
2025-01-15 | 22 | 2031-01-15 22:00 | 23.81 | 31.2823 | N | 0
2025-01-15 | 23 | 2031-01-15 23:00 | 21.91 | 28.786 | N | 0
2025-01-16 | 00 | 2031-01-16 | 20.14 | 26.4605 | N | 0
2025-01-16 | 01 | 2031-01-16 01:00 | 18.33 | 24.0825 | N | 0
2025-01-16 | 02 | 2031-01-16 02:00 | 17.32 | 22.7555 | N | 0
2025-01-16 | 03 | 2031-01-16 03:00 | 16.67 | 21.9015 | N | 0
2025-01-16 | 04 | 2031-01-16 04:00 | 16.61 | 21.8227 | N | 0
2025-01-16 | 05 | 2031-01-16 05:00 | 16.73 | 21.9804 | N | 0
2025-01-16 | 06 | 2031-01-16 06:00 | 17.61 | 23.1365 | N | 0
2025-01-16 | 07 | 2031-01-16 07:00 | 19.56 | 25.6985 | N | 0
2025-01-16 | 08 | 2031-01-16 08:00 | 22.11 | 29.0488 | N | 0
2025-01-16 | 09 | 2031-01-16 09:00 | 22.78 | 29.929 | N | 0
2025-01-16 | 10 | 2031-01-16 10:00 | 22.72 | 29.8502 | N | 0
2025-01-16 | 11 | 2031-01-16 11:00 | 22.85 | 30.021 | N | 0
2025-01-16 | 12 | 2031-01-16 12:00 | 23.19 | 30.4677 | N | 0
2025-01-16 | 13 | 2031-01-16 13:00 | 22.99 | 30.2049 | N | 0
2025-01-16 | 14 | 2031-01-16 14:00 | 23.09 | 30.3363 | N | 0
2025-01-16 | 15 | 2031-01-16 15:00 | 23.34 | 30.6648 | N | 0
2025-01-16 | 16 | 2031-01-16 16:00 | 23.15 | 30.4152 | N | 0
2025-01-16 | 17 | 2031-01-16 17:00 | 23.64 | 31.0589 | N | 0
2025-01-16 | 18 | 2031-01-16 18:00 | 25.86 | 33.9756 | N | 0
2025-01-16 | 19 | 2031-01-16 19:00 | 25.47 | 33.4632 | N | 0
2025-01-16 | 20 | 2031-01-16 20:00 | 24.56 | 32.2677 | N | 0
2025-01-16 | 21 | 2031-01-16 21:00 | 24.32 | 31.9523 | N | 0
2025-01-16 | 22 | 2031-01-16 22:00 | 23.32 | 30.6385 | N | 0
2025-01-16 | 23 | 2031-01-16 23:00 | 22.23 | 29.2064 | N | 0
2025-01-17 | 00 | 2031-01-17 | 19.74 | 25.935 | N | 0
2025-01-17 | 01 | 2031-01-17 01:00 | 17.77 | 23.3468 | N | 0
2025-01-17 | 02 | 2031-01-17 02:00 | 17.02 | 22.3614 | N | 0
2025-01-17 | 03 | 2031-01-17 03:00 | 16.33 | 21.4548 | N | 0
2025-01-17 | 04 | 2031-01-17 04:00 | 16 | 21.0213 | N | 0
2025-01-17 | 05 | 2031-01-17 05:00 | 16 | 21.0213 | N | 0
2025-01-17 | 06 | 2031-01-17 06:00 | 16.62 | 21.8359 | N | 0
2025-01-17 | 07 | 2031-01-17 07:00 | 18.98 | 24.9365 | N | 0
2025-01-17 | 08 | 2031-01-17 08:00 | 21.08 | 27.6955 | N | 0
2025-01-17 | 09 | 2031-01-17 09:00 | 21.37 | 28.0765 | N | 0
2025-01-17 | 10 | 2031-01-17 10:00 | 21.38 | 28.0897 | N | 0
2025-01-17 | 11 | 2031-01-17 11:00 | 21.57 | 28.3393 | N | 0
2025-01-17 | 12 | 2031-01-17 12:00 | 22.06 | 28.9831 | N | 0
2025-01-17 | 13 | 2031-01-17 13:00 | 22.05 | 28.9699 | N | 0
2025-01-17 | 14 | 2031-01-17 14:00 | 21.53 | 28.2868 | N | 0
2025-01-17 | 15 | 2031-01-17 15:00 | 21.72 | 28.5364 | N | 0
2025-01-17 | 16 | 2031-01-17 16:00 | 21.69 | 28.497 | N | 0
2025-01-17 | 17 | 2031-01-17 17:00 | 23.02 | 30.2444 | N | 0
2025-01-17 | 18 | 2031-01-17 18:00 | 24.21 | 31.8078 | N | 0
2025-01-17 | 19 | 2031-01-17 19:00 | 24.07 | 31.6239 | N | 0
2025-01-17 | 20 | 2031-01-17 20:00 | 23.07 | 30.3101 | N | 0
2025-01-17 | 21 | 2031-01-17 21:00 | 22.52 | 29.5874 | N | 0
2025-01-17 | 22 | 2031-01-17 22:00 | 21.4 | 28.116 | N | 0
2025-01-17 | 23 | 2031-01-17 23:00 | 20.21 | 26.5525 | N | 0
2025-01-18 | 00 | 2031-01-18 | 18.66 | 24.5161 | N | 0
2025-01-18 | 01 | 2031-01-18 01:00 | 17.08 | 22.4402 | N | 0
2025-01-18 | 02 | 2031-01-18 02:00 | 16 | 21.0213 | N | 0
2025-01-18 | 03 | 2031-01-18 03:00 | 15.27 | 20.0622 | N | 0
2025-01-18 | 04 | 2031-01-18 04:00 | 14.71 | 19.3264 | N | 0
2025-01-18 | 05 | 2031-01-18 05:00 | 14.88 | 19.5498 | N | 0
2025-01-18 | 06 | 2031-01-18 06:00 | 15.11 | 19.852 | N | 0
2025-01-18 | 07 | 2031-01-18 07:00 | 15.73 | 20.6665 | N | 0
2025-01-18 | 08 | 2031-01-18 08:00 | 17.21 | 22.611 | N | 0
2025-01-18 | 09 | 2031-01-18 09:00 | 18.5 | 24.3059 | N | 0
2025-01-18 | 10 | 2031-01-18 10:00 | 19.95 | 26.2109 | N | 0
2025-01-18 | 11 | 2031-01-18 11:00 | 20.9 | 27.459 | N | 0
2025-01-18 | 12 | 2031-01-18 12:00 | 21.47 | 28.2079 | N | 0
2025-01-18 | 13 | 2031-01-18 13:00 | 21.87 | 28.7335 | N | 0
2025-01-18 | 14 | 2031-01-18 14:00 | 21.96 | 28.8517 | N | 0
2025-01-18 | 15 | 2031-01-18 15:00 | 21.65 | 28.4444 | N | 0
2025-01-18 | 16 | 2031-01-18 16:00 | 21.84 | 28.694 | N | 0
2025-01-18 | 17 | 2031-01-18 17:00 | 22.82 | 29.9816 | N | 0
2025-01-18 | 18 | 2031-01-18 18:00 | 24.06 | 31.6107 | N | 0
2025-01-18 | 19 | 2031-01-18 19:00 | 24.3 | 31.9261 | N | 0
2025-01-18 | 20 | 2031-01-18 20:00 | 23.1 | 30.3495 | N | 0
2025-01-18 | 21 | 2031-01-18 21:00 | 22.54 | 29.6137 | N | 0
2025-01-18 | 22 | 2031-01-18 22:00 | 21.77 | 28.6021 | N | 0
2025-01-18 | 23 | 2031-01-18 23:00 | 20.38 | 26.7759 | N | 0
2025-01-19 | 00 | 2031-01-19 | 19.32 | 25.3832 | N | 0
2025-01-19 | 01 | 2031-01-19 01:00 | 18.22 | 23.938 | N | 0
2025-01-19 | 02 | 2031-01-19 02:00 | 16.96 | 22.2826 | N | 0
2025-01-19 | 03 | 2031-01-19 03:00 | 16.33 | 21.4548 | N | 0
2025-01-19 | 04 | 2031-01-19 04:00 | 16.17 | 21.2446 | N | 0
2025-01-19 | 05 | 2031-01-19 05:00 | 16.38 | 21.5205 | N | 0
2025-01-19 | 06 | 2031-01-19 06:00 | 16.49 | 21.6651 | N | 0
2025-01-19 | 07 | 2031-01-19 07:00 | 17.1 | 22.4665 | N | 0
2025-01-19 | 08 | 2031-01-19 08:00 | 17.9 | 23.5176 | N | 0
2025-01-19 | 09 | 2031-01-19 09:00 | 19.72 | 25.9087 | N | 0
2025-01-19 | 10 | 2031-01-19 10:00 | 20.92 | 27.4853 | N | 0
2025-01-19 | 11 | 2031-01-19 11:00 | 22.31 | 29.3115 | N | 0
2025-01-19 | 12 | 2031-01-19 12:00 | 22.78 | 29.929 | N | 0
2025-01-19 | 13 | 2031-01-19 13:00 | 23.13 | 30.3889 | N | 0
2025-01-19 | 14 | 2031-01-19 14:00 | 23.24 | 30.5334 | N | 0
2025-01-19 | 15 | 2031-01-19 15:00 | 23.4 | 30.7436 | N | 0
2025-01-19 | 16 | 2031-01-19 16:00 | 24.02 | 31.5582 | N | 0
2025-01-19 | 17 | 2031-01-19 17:00 | 25.59 | 33.6209 | N | 0
2025-01-19 | 18 | 2031-01-19 18:00 | 27 | 35.4734 | N | 0
2025-01-19 | 19 | 2031-01-19 19:00 | 26.71 | 35.0924 | N | 0
2025-01-19 | 20 | 2031-01-19 20:00 | 25.63 | 33.6735 | N | 0
2025-01-19 | 21 | 2031-01-19 21:00 | 24.63 | 32.3596 | N | 0
2025-01-19 | 22 | 2031-01-19 22:00 | 23.73 | 31.1772 | N | 0
2025-01-19 | 23 | 2031-01-19 23:00 | 21.94 | 28.8254 | N | 0
2025-01-20 | 00 | 2031-01-20 | 20.07 | 26.3686 | N | 0
2025-01-20 | 01 | 2031-01-20 01:00 | 18.44 | 24.227 | N | 0
2025-01-20 | 02 | 2031-01-20 02:00 | 17.39 | 22.8475 | N | 0
2025-01-20 | 03 | 2031-01-20 03:00 | 17.17 | 22.5585 | N | 0
2025-01-20 | 04 | 2031-01-20 04:00 | 16.68 | 21.9147 | N | 0
2025-01-20 | 05 | 2031-01-20 05:00 | 17.14 | 22.519 | N | 0
2025-01-20 | 06 | 2031-01-20 06:00 | 18.19 | 23.8986 | N | 0
2025-01-20 | 07 | 2031-01-20 07:00 | 20.54 | 26.9861 | N | 0
2025-01-20 | 08 | 2031-01-20 08:00 | 22.53 | 29.6006 | N | 0
2025-01-20 | 09 | 2031-01-20 09:00 | 23.43 | 30.783 | N | 0
2025-01-20 | 10 | 2031-01-20 10:00 | 23.42 | 30.7699 | N | 0
2025-01-20 | 11 | 2031-01-20 11:00 | 23.78 | 31.2429 | N | 0
2025-01-20 | 12 | 2031-01-20 12:00 | 23.92 | 31.4268 | N | 0
2025-01-20 | 13 | 2031-01-20 13:00 | 23.68 | 31.1115 | N | 0
2025-01-20 | 14 | 2031-01-20 14:00 | 23.86 | 31.348 | N | 0
2025-01-20 | 15 | 2031-01-20 15:00 | 24.21 | 31.8078 | N | 0
2025-01-20 | 16 | 2031-01-20 16:00 | 24.68 | 32.4253 | N | 0
2025-01-20 | 17 | 2031-01-20 17:00 | 26.01 | 34.1727 | N | 0
2025-01-20 | 18 | 2031-01-20 18:00 | 27.78 | 36.4982 | N | 0
2025-01-20 | 19 | 2031-01-20 19:00 | 27.77 | 36.4851 | N | 0
2025-01-20 | 20 | 2031-01-20 20:00 | 27.14 | 35.6573 | N | 0
2025-01-20 | 21 | 2031-01-20 21:00 | 26.75 | 35.1449 | N | 0
2025-01-20 | 22 | 2031-01-20 22:00 | 26.04 | 34.2121 | N | 0
2025-01-20 | 23 | 2031-01-20 23:00 | 24.14 | 31.7159 | N | 0
2025-01-21 | 00 | 2031-01-21 | 22.44 | 29.4823 | N | 0
2025-01-21 | 01 | 2031-01-21 01:00 | 20.51 | 26.9466 | N | 0
2025-01-21 | 02 | 2031-01-21 02:00 | 19.43 | 25.5277 | N | 0
2025-01-21 | 03 | 2031-01-21 03:00 | 18.72 | 24.5949 | N | 0
2025-01-21 | 04 | 2031-01-21 04:00 | 18.54 | 24.3584 | N | 0
2025-01-21 | 05 | 2031-01-21 05:00 | 18.88 | 24.8051 | N | 0
2025-01-21 | 06 | 2031-01-21 06:00 | 19.51 | 25.6328 | N | 0
2025-01-21 | 07 | 2031-01-21 07:00 | 21.83 | 28.6809 | N | 0
2025-01-21 | 08 | 2031-01-21 08:00 | 24.05 | 31.5976 | N | 0
2025-01-21 | 09 | 2031-01-21 09:00 | 24.7 | 32.4516 | N | 0
2025-01-21 | 10 | 2031-01-21 10:00 | 24.55 | 32.2545 | N | 0
2025-01-21 | 11 | 2031-01-21 11:00 | 24.41 | 32.0706 | N | 0
2025-01-21 | 12 | 2031-01-21 12:00 | 24.65 | 32.3859 | N | 0
2025-01-21 | 13 | 2031-01-21 13:00 | 24.53 | 32.2282 | N | 0
2025-01-21 | 14 | 2031-01-21 14:00 | 24.78 | 32.5567 | N | 0
2025-01-21 | 15 | 2031-01-21 15:00 | 24.91 | 32.7275 | N | 0
2025-01-21 | 16 | 2031-01-21 16:00 | 24.96 | 32.7932 | N | 0
2025-01-21 | 17 | 2031-01-21 17:00 | 26.8 | 35.2106 | N | 0
2025-01-21 | 18 | 2031-01-21 18:00 | 28.5 | 37.4441 | Y | 0.26415 | 1 | 1
2025-01-21 | 19 | 2031-01-21 19:00 | 28.02 | 36.8135 | N | 0
2025-01-21 | 20 | 2031-01-21 20:00 | 27.27 | 35.8281 | N | 0
2025-01-21 | 21 | 2031-01-21 21:00 | 26.74 | 35.1318 | N | 0
2025-01-21 | 22 | 2031-01-21 22:00 | 26.01 | 34.1727 | N | 0
2025-01-21 | 23 | 2031-01-21 23:00 | 24.41 | 32.0706 | N | 0
2025-01-22 | 00 | 2031-01-22 | 22.63 | 29.732 | N | 0
2025-01-22 | 01 | 2031-01-22 01:00 | 21.14 | 27.7744 | N | 0
2025-01-22 | 02 | 2031-01-22 02:00 | 20.01 | 26.2897 | N | 0
2025-01-22 | 03 | 2031-01-22 03:00 | 19.41 | 25.5014 | N | 0
2025-01-22 | 04 | 2031-01-22 04:00 | 19.24 | 25.2781 | N | 0
2025-01-22 | 05 | 2031-01-22 05:00 | 19.18 | 25.1993 | N | 0
2025-01-22 | 06 | 2031-01-22 06:00 | 20.37 | 26.7627 | N | 0
2025-01-22 | 07 | 2031-01-22 07:00 | 22.65 | 29.7582 | N | 0
2025-01-22 | 08 | 2031-01-22 08:00 | 24.61 | 32.3334 | N | 0
2025-01-22 | 09 | 2031-01-22 09:00 | 25.58 | 33.6078 | N | 0
2025-01-22 | 10 | 2031-01-22 10:00 | 25.7 | 33.7654 | N | 0
2025-01-22 | 11 | 2031-01-22 11:00 | 25.67 | 33.726 | N | 0
2025-01-22 | 12 | 2031-01-22 12:00 | 26.39 | 34.672 | N | 0
2025-01-22 | 13 | 2031-01-22 13:00 | 26.46 | 34.7639 | N | 0
2025-01-22 | 14 | 2031-01-22 14:00 | 26.48 | 34.7902 | N | 0
2025-01-22 | 15 | 2031-01-22 15:00 | 26.06 | 34.2384 | N | 0
2025-01-22 | 16 | 2031-01-22 16:00 | 26.25 | 34.488 | N | 0
2025-01-22 | 17 | 2031-01-22 17:00 | 27.41 | 36.0121 | N | 0
2025-01-22 | 18 | 2031-01-22 18:00 | 28.67 | 37.6675 | Y | 0.4875 | 1
2025-01-22 | 19 | 2031-01-22 19:00 | 28.64 | 37.6281 | Y | 0.44809 | 2 | 2
2025-01-22 | 20 | 2031-01-22 20:00 | 27.67 | 36.3537 | N | 0
2025-01-22 | 21 | 2031-01-22 21:00 | 26.83 | 35.2501 | N | 0
2025-01-22 | 22 | 2031-01-22 22:00 | 25.84 | 33.9494 | N | 0
2025-01-22 | 23 | 2031-01-22 23:00 | 24.37 | 32.018 | N | 0
2025-01-23 | 00 | 2031-01-23 | 21.71 | 28.5232 | N | 0
2025-01-23 | 01 | 2031-01-23 01:00 | 20.12 | 26.4343 | N | 0
2025-01-23 | 02 | 2031-01-23 02:00 | 19.05 | 25.0285 | N | 0
2025-01-23 | 03 | 2031-01-23 03:00 | 18.4 | 24.1745 | N | 0
2025-01-23 | 04 | 2031-01-23 04:00 | 18.02 | 23.6752 | N | 0
2025-01-23 | 05 | 2031-01-23 05:00 | 18.22 | 23.938 | N | 0
2025-01-23 | 06 | 2031-01-23 06:00 | 18.74 | 24.6212 | N | 0
2025-01-23 | 07 | 2031-01-23 07:00 | 21 | 27.5904 | N | 0
2025-01-23 | 08 | 2031-01-23 08:00 | 22.75 | 29.8896 | N | 0
2025-01-23 | 09 | 2031-01-23 09:00 | 23.55 | 30.9407 | N | 0
2025-01-23 | 10 | 2031-01-23 10:00 | 24.08 | 31.637 | N | 0
2025-01-23 | 11 | 2031-01-23 11:00 | 24.4 | 32.0574 | N | 0
2025-01-23 | 12 | 2031-01-23 12:00 | 24.21 | 31.8078 | N | 0
2025-01-23 | 13 | 2031-01-23 13:00 | 24.28 | 31.8998 | N | 0
2025-01-23 | 14 | 2031-01-23 14:00 | 24.06 | 31.6107 | N | 0
2025-01-23 | 15 | 2031-01-23 15:00 | 24.18 | 31.7684 | N | 0
2025-01-23 | 16 | 2031-01-23 16:00 | 23.98 | 31.5056 | N | 0
2025-01-23 | 17 | 2031-01-23 17:00 | 24.46 | 32.1363 | N | 0
2025-01-23 | 18 | 2031-01-23 18:00 | 26.42 | 34.7114 | N | 0
2025-01-23 | 19 | 2031-01-23 19:00 | 25.89 | 34.0151 | N | 0
2025-01-23 | 20 | 2031-01-23 20:00 | 25.33 | 33.2793 | N | 0
2025-01-23 | 21 | 2031-01-23 21:00 | 24.83 | 32.6224 | N | 0
2025-01-23 | 22 | 2031-01-23 22:00 | 23.7 | 31.1378 | N | 0
2025-01-23 | 23 | 2031-01-23 23:00 | 22.49 | 29.548 | N | 0
2025-01-24 | 00 | 2031-01-24 | 20.59 | 27.0518 | N | 0
2025-01-24 | 01 | 2031-01-24 01:00 | 18.96 | 24.9102 | N | 0
2025-01-24 | 02 | 2031-01-24 02:00 | 17.83 | 23.4256 | N | 0
2025-01-24 | 03 | 2031-01-24 03:00 | 17.47 | 22.9526 | N | 0
2025-01-24 | 04 | 2031-01-24 04:00 | 16.94 | 22.2563 | N | 0
2025-01-24 | 05 | 2031-01-24 05:00 | 17.42 | 22.8869 | N | 0
2025-01-24 | 06 | 2031-01-24 06:00 | 18.49 | 24.2927 | N | 0
2025-01-24 | 07 | 2031-01-24 07:00 | 20.79 | 27.3145 | N | 0
2025-01-24 | 08 | 2031-01-24 08:00 | 22.62 | 29.7188 | N | 0
2025-01-24 | 09 | 2031-01-24 09:00 | 23.46 | 30.8224 | N | 0
2025-01-24 | 10 | 2031-01-24 10:00 | 23.97 | 31.4925 | N | 0
2025-01-24 | 11 | 2031-01-24 11:00 | 23.55 | 30.9407 | N | 0
2025-01-24 | 12 | 2031-01-24 12:00 | 23.39 | 30.7305 | N | 0
2025-01-24 | 13 | 2031-01-24 13:00 | 22.77 | 29.9159 | N | 0
2025-01-24 | 14 | 2031-01-24 14:00 | 22.4 | 29.4298 | N | 0
2025-01-24 | 15 | 2031-01-24 15:00 | 21.87 | 28.7335 | N | 0
2025-01-24 | 16 | 2031-01-24 16:00 | 21.93 | 28.8123 | N | 0
2025-01-24 | 17 | 2031-01-24 17:00 | 23.49 | 30.8619 | N | 0
2025-01-24 | 18 | 2031-01-24 18:00 | 24.64 | 32.3728 | N | 0
2025-01-24 | 19 | 2031-01-24 19:00 | 24.85 | 32.6487 | N | 0
2025-01-24 | 20 | 2031-01-24 20:00 | 24.18 | 31.7684 | N | 0
2025-01-24 | 21 | 2031-01-24 21:00 | 23.7 | 31.1378 | N | 0
2025-01-24 | 22 | 2031-01-24 22:00 | 23.63 | 31.0458 | N | 0
2025-01-24 | 23 | 2031-01-24 23:00 | 22.22 | 29.1933 | N | 0
2025-01-25 | 00 | 2031-01-25 | 20.66 | 27.1437 | N | 0
2025-01-25 | 01 | 2031-01-25 01:00 | 19.19 | 25.2124 | N | 0
2025-01-25 | 02 | 2031-01-25 02:00 | 18.21 | 23.9248 | N | 0
2025-01-25 | 03 | 2031-01-25 03:00 | 17.24 | 22.6504 | N | 0
2025-01-25 | 04 | 2031-01-25 04:00 | 16.71 | 21.9541 | N | 0
2025-01-25 | 05 | 2031-01-25 05:00 | 16.64 | 21.8621 | N | 0
2025-01-25 | 06 | 2031-01-25 06:00 | 16.86 | 22.1512 | N | 0
2025-01-25 | 07 | 2031-01-25 07:00 | 18.01 | 23.6621 | N | 0
2025-01-25 | 08 | 2031-01-25 08:00 | 18.96 | 24.9102 | N | 0
2025-01-25 | 09 | 2031-01-25 09:00 | 20.6 | 27.0649 | N | 0
2025-01-25 | 10 | 2031-01-25 10:00 | 22.26 | 29.2459 | N | 0
2025-01-25 | 11 | 2031-01-25 11:00 | 23.13 | 30.3889 | N | 0
2025-01-25 | 12 | 2031-01-25 12:00 | 24.09 | 31.6502 | N | 0
2025-01-25 | 13 | 2031-01-25 13:00 | 24.26 | 31.8735 | N | 0
2025-01-25 | 14 | 2031-01-25 14:00 | 24.28 | 31.8998 | N | 0
2025-01-25 | 15 | 2031-01-25 15:00 | 23.51 | 30.8881 | N | 0
2025-01-25 | 16 | 2031-01-25 16:00 | 23.53 | 30.9144 | N | 0
2025-01-25 | 17 | 2031-01-25 17:00 | 24.47 | 32.1494 | N | 0
2025-01-25 | 18 | 2031-01-25 18:00 | 25.21 | 33.1216 | N | 0
2025-01-25 | 19 | 2031-01-25 19:00 | 24.86 | 32.6618 | N | 0
2025-01-25 | 20 | 2031-01-25 20:00 | 23.83 | 31.3086 | N | 0
2025-01-25 | 21 | 2031-01-25 21:00 | 23.06 | 30.2969 | N | 0
2025-01-25 | 22 | 2031-01-25 22:00 | 22.38 | 29.4035 | N | 0
2025-01-25 | 23 | 2031-01-25 23:00 | 20.55 | 26.9992 | N | 0
2025-01-26 | 00 | 2031-01-26 | 19.64 | 25.8036 | N | 0
2025-01-26 | 01 | 2031-01-26 01:00 | 18.09 | 23.7672 | N | 0
2025-01-26 | 02 | 2031-01-26 02:00 | 17.06 | 22.4139 | N | 0
2025-01-26 | 03 | 2031-01-26 03:00 | 16.36 | 21.4943 | N | 0
2025-01-26 | 04 | 2031-01-26 04:00 | 15.82 | 20.7848 | N | 0
2025-01-26 | 05 | 2031-01-26 05:00 | 15.84 | 20.8111 | N | 0
2025-01-26 | 06 | 2031-01-26 06:00 | 15.93 | 20.9293 | N | 0
2025-01-26 | 07 | 2031-01-26 07:00 | 16.44 | 21.5994 | N | 0
2025-01-26 | 08 | 2031-01-26 08:00 | 17.44 | 22.9132 | N | 0
2025-01-26 | 09 | 2031-01-26 09:00 | 18.5 | 24.3059 | N | 0
2025-01-26 | 10 | 2031-01-26 10:00 | 19.3 | 25.3569 | N | 0
2025-01-26 | 11 | 2031-01-26 11:00 | 20.1 | 26.408 | N | 0
2025-01-26 | 12 | 2031-01-26 12:00 | 20.93 | 27.4985 | N | 0
2025-01-26 | 13 | 2031-01-26 13:00 | 21.76 | 28.5889 | N | 0
2025-01-26 | 14 | 2031-01-26 14:00 | 21.82 | 28.6678 | N | 0
2025-01-26 | 15 | 2031-01-26 15:00 | 22.19 | 29.1539 | N | 0
2025-01-26 | 16 | 2031-01-26 16:00 | 22.72 | 29.8502 | N | 0
2025-01-26 | 17 | 2031-01-26 17:00 | 24.23 | 31.8341 | N | 0
2025-01-26 | 18 | 2031-01-26 18:00 | 25.93 | 34.0676 | N | 0
2025-01-26 | 19 | 2031-01-26 19:00 | 25.81 | 33.9099 | N | 0
2025-01-26 | 20 | 2031-01-26 20:00 | 24.8 | 32.583 | N | 0
2025-01-26 | 21 | 2031-01-26 21:00 | 23.87 | 31.3611 | N | 0
2025-01-26 | 22 | 2031-01-26 22:00 | 22.92 | 30.113 | N | 0
2025-01-26 | 23 | 2031-01-26 23:00 | 21.03 | 27.6298 | N | 0
2025-01-27 | 00 | 2031-01-27 | 19.07 | 25.0547 | N | 0
2025-01-27 | 01 | 2031-01-27 01:00 | 17.51 | 23.0052 | N | 0
2025-01-27 | 02 | 2031-01-27 02:00 | 16.65 | 21.8753 | N | 0
2025-01-27 | 03 | 2031-01-27 03:00 | 16.1 | 21.1527 | N | 0
2025-01-27 | 04 | 2031-01-27 04:00 | 15.76 | 20.706 | N | 0
2025-01-27 | 05 | 2031-01-27 05:00 | 16.06 | 21.1001 | N | 0
2025-01-27 | 06 | 2031-01-27 06:00 | 17.19 | 22.5847 | N | 0
2025-01-27 | 07 | 2031-01-27 07:00 | 19.13 | 25.1336 | N | 0
2025-01-27 | 08 | 2031-01-27 08:00 | 21.34 | 28.0371 | N | 0
2025-01-27 | 09 | 2031-01-27 09:00 | 21.83 | 28.6809 | N | 0
2025-01-27 | 10 | 2031-01-27 10:00 | 21.66 | 28.4576 | N | 0
2025-01-27 | 11 | 2031-01-27 11:00 | 21.66 | 28.4576 | N | 0
2025-01-27 | 12 | 2031-01-27 12:00 | 22.34 | 29.351 | N | 0
2025-01-27 | 13 | 2031-01-27 13:00 | 22.87 | 30.0473 | N | 0
2025-01-27 | 14 | 2031-01-27 14:00 | 22.45 | 29.4955 | N | 0
2025-01-27 | 15 | 2031-01-27 15:00 | 22.35 | 29.3641 | N | 0
2025-01-27 | 16 | 2031-01-27 16:00 | 22.73 | 29.8634 | N | 0
2025-01-27 | 17 | 2031-01-27 17:00 | 24.79 | 32.5698 | N | 0
2025-01-27 | 18 | 2031-01-27 18:00 | 26.39 | 34.672 | N | 0
2025-01-27 | 19 | 2031-01-27 19:00 | 26.35 | 34.6194 | N | 0
2025-01-27 | 20 | 2031-01-27 20:00 | 24.96 | 32.7932 | N | 0
2025-01-27 | 21 | 2031-01-27 21:00 | 24.35 | 31.9918 | N | 0
2025-01-27 | 22 | 2031-01-27 22:00 | 23.26 | 30.5597 | N | 0
2025-01-27 | 23 | 2031-01-27 23:00 | 21.56 | 28.3262 | N | 0
2025-01-28 | 00 | 2031-01-28 | 19.62 | 25.7773 | N | 0
2025-01-28 | 01 | 2031-01-28 01:00 | 17.85 | 23.4519 | N | 0
2025-01-28 | 02 | 2031-01-28 02:00 | 17.16 | 22.5453 | N | 0
2025-01-28 | 03 | 2031-01-28 03:00 | 16.08 | 21.1264 | N | 0
2025-01-28 | 04 | 2031-01-28 04:00 | 16.08 | 21.1264 | N | 0
2025-01-28 | 05 | 2031-01-28 05:00 | 16.59 | 21.7964 | N | 0
2025-01-28 | 06 | 2031-01-28 06:00 | 17.87 | 23.4781 | N | 0
2025-01-28 | 07 | 2031-01-28 07:00 | 19.79 | 26.0007 | N | 0
2025-01-28 | 08 | 2031-01-28 08:00 | 22.12 | 29.0619 | N | 0
2025-01-28 | 09 | 2031-01-28 09:00 | 22.29 | 29.2853 | N | 0
2025-01-28 | 10 | 2031-01-28 10:00 | 22.53 | 29.6006 | N | 0
2025-01-28 | 11 | 2031-01-28 11:00 | 22.89 | 30.0736 | N | 0
2025-01-28 | 12 | 2031-01-28 12:00 | 23.36 | 30.6911 | N | 0
2025-01-28 | 13 | 2031-01-28 13:00 | 23.34 | 30.6648 | N | 0
2025-01-28 | 14 | 2031-01-28 14:00 | 22.52 | 29.5874 | N | 0
2025-01-28 | 15 | 2031-01-28 15:00 | 22.69 | 29.8108 | N | 0
2025-01-28 | 16 | 2031-01-28 16:00 | 23.58 | 30.9801 | N | 0
2025-01-28 | 17 | 2031-01-28 17:00 | 24.87 | 32.6749 | N | 0
2025-01-28 | 18 | 2031-01-28 18:00 | 26.56 | 34.8953 | N | 0
2025-01-28 | 19 | 2031-01-28 19:00 | 26.11 | 34.3041 | N | 0
2025-01-28 | 20 | 2031-01-28 20:00 | 24.66 | 32.399 | N | 0
2025-01-28 | 21 | 2031-01-28 21:00 | 24.76 | 32.5304 | N | 0
2025-01-28 | 22 | 2031-01-28 22:00 | 23.42 | 30.7699 | N | 0
2025-01-28 | 23 | 2031-01-28 23:00 | 21.87 | 28.7335 | N | 0
2025-01-29 | 00 | 2031-01-29 | 19.74 | 25.935 | N | 0
2025-01-29 | 01 | 2031-01-29 01:00 | 17.89 | 23.5044 | N | 0
2025-01-29 | 02 | 2031-01-29 02:00 | 16.84 | 22.1249 | N | 0
2025-01-29 | 03 | 2031-01-29 03:00 | 16.3 | 21.4154 | N | 0
2025-01-29 | 04 | 2031-01-29 04:00 | 15.57 | 20.4563 | N | 0
2025-01-29 | 05 | 2031-01-29 05:00 | 15.88 | 20.8636 | N | 0
2025-01-29 | 06 | 2031-01-29 06:00 | 16.77 | 22.0329 | N | 0
2025-01-29 | 07 | 2031-01-29 07:00 | 18.48 | 24.2796 | N | 0
2025-01-29 | 08 | 2031-01-29 08:00 | 20.61 | 27.078 | N | 0
2025-01-29 | 09 | 2031-01-29 09:00 | 21.07 | 27.6824 | N | 0
2025-01-29 | 10 | 2031-01-29 10:00 | 21.83 | 28.6809 | N | 0
2025-01-29 | 11 | 2031-01-29 11:00 | 21.86 | 28.7203 | N | 0
2025-01-29 | 12 | 2031-01-29 12:00 | 21.92 | 28.7991 | N | 0
2025-01-29 | 13 | 2031-01-29 13:00 | 22.54 | 29.6137 | N | 0
2025-01-29 | 14 | 2031-01-29 14:00 | 22.72 | 29.8502 | N | 0
2025-01-29 | 15 | 2031-01-29 15:00 | 22.8 | 29.9553 | N | 0
2025-01-29 | 16 | 2031-01-29 16:00 | 23.56 | 30.9538 | N | 0
2025-01-29 | 17 | 2031-01-29 17:00 | 24.27 | 31.8866 | N | 0
2025-01-29 | 18 | 2031-01-29 18:00 | 26.46 | 34.7639 | N | 0
2025-01-29 | 19 | 2031-01-29 19:00 | 26.2 | 34.4223 | N | 0
2025-01-29 | 20 | 2031-01-29 20:00 | 25.64 | 33.6866 | N | 0
2025-01-29 | 21 | 2031-01-29 21:00 | 24.87 | 32.6749 | N | 0
2025-01-29 | 22 | 2031-01-29 22:00 | 24.49 | 32.1757 | N | 0
2025-01-29 | 23 | 2031-01-29 23:00 | 22.37 | 29.3904 | N | 0
2025-01-30 | 00 | 2031-01-30 | 20.15 | 26.4737 | N | 0
2025-01-30 | 01 | 2031-01-30 01:00 | 18.74 | 24.6212 | N | 0
2025-01-30 | 02 | 2031-01-30 02:00 | 17.87 | 23.4781 | N | 0
2025-01-30 | 03 | 2031-01-30 03:00 | 17.5 | 22.992 | N | 0
2025-01-30 | 04 | 2031-01-30 04:00 | 16.94 | 22.2563 | N | 0
2025-01-30 | 05 | 2031-01-30 05:00 | 17.5 | 22.992 | N | 0
2025-01-30 | 06 | 2031-01-30 06:00 | 18.16 | 23.8591 | N | 0
2025-01-30 | 07 | 2031-01-30 07:00 | 19.99 | 26.2635 | N | 0
2025-01-30 | 08 | 2031-01-30 08:00 | 22.64 | 29.7451 | N | 0
2025-01-30 | 09 | 2031-01-30 09:00 | 23.25 | 30.5465 | N | 0
2025-01-30 | 10 | 2031-01-30 10:00 | 23.03 | 30.2575 | N | 0
2025-01-30 | 11 | 2031-01-30 11:00 | 22.96 | 30.1655 | N | 0
2025-01-30 | 12 | 2031-01-30 12:00 | 23.09 | 30.3363 | N | 0
2025-01-30 | 13 | 2031-01-30 13:00 | 22.76 | 29.9028 | N | 0
2025-01-30 | 14 | 2031-01-30 14:00 | 22.4 | 29.4298 | N | 0
2025-01-30 | 15 | 2031-01-30 15:00 | 22.93 | 30.1261 | N | 0
2025-01-30 | 16 | 2031-01-30 16:00 | 23.05 | 30.2838 | N | 0
2025-01-30 | 17 | 2031-01-30 17:00 | 23.83 | 31.3086 | N | 0
2025-01-30 | 18 | 2031-01-30 18:00 | 24.8 | 32.583 | N | 0
2025-01-30 | 19 | 2031-01-30 19:00 | 25.22 | 33.1348 | N | 0
2025-01-30 | 20 | 2031-01-30 20:00 | 24.33 | 31.9655 | N | 0
2025-01-30 | 21 | 2031-01-30 21:00 | 23.68 | 31.1115 | N | 0
2025-01-30 | 22 | 2031-01-30 22:00 | 23.06 | 30.2969 | N | 0
2025-01-30 | 23 | 2031-01-30 23:00 | 22.23 | 29.2064 | N | 0
2025-01-31 | 00 | 2031-01-31 | 19.94 | 26.1978 | N | 0
2025-01-31 | 01 | 2031-01-31 01:00 | 18.09 | 23.7672 | N | 0
2025-01-31 | 02 | 2031-01-31 02:00 | 17.53 | 23.0314 | N | 0
2025-01-31 | 03 | 2031-01-31 03:00 | 16.94 | 22.2563 | N | 0
2025-01-31 | 04 | 2031-01-31 04:00 | 16.57 | 21.7702 | N | 0
2025-01-31 | 05 | 2031-01-31 05:00 | 16.79 | 22.0592 | N | 0
2025-01-31 | 06 | 2031-01-31 06:00 | 17.19 | 22.5847 | N | 0
2025-01-31 | 07 | 2031-01-31 07:00 | 19.43 | 25.5277 | N | 0
2025-01-31 | 08 | 2031-01-31 08:00 | 21.28 | 27.9583 | N | 0
2025-01-31 | 09 | 2031-01-31 09:00 | 21.92 | 28.7991 | N | 0
2025-01-31 | 10 | 2031-01-31 10:00 | 22.23 | 29.2064 | N | 0
2025-01-31 | 11 | 2031-01-31 11:00 | 22.63 | 29.732 | N | 0
2025-01-31 | 12 | 2031-01-31 12:00 | 22.54 | 29.6137 | N | 0
2025-01-31 | 13 | 2031-01-31 13:00 | 22.38 | 29.4035 | N | 0
2025-01-31 | 14 | 2031-01-31 14:00 | 22.39 | 29.4166 | N | 0
2025-01-31 | 15 | 2031-01-31 15:00 | 21.77 | 28.6021 | N | 0
2025-01-31 | 16 | 2031-01-31 16:00 | 21.85 | 28.7072 | N | 0
2025-01-31 | 17 | 2031-01-31 17:00 | 22.14 | 29.0882 | N | 0
2025-01-31 | 18 | 2031-01-31 18:00 | 23.35 | 30.6779 | N | 0
2025-01-31 | 19 | 2031-01-31 19:00 | 23.38 | 30.7173 | N | 0
2025-01-31 | 20 | 2031-01-31 20:00 | 22.72 | 29.8502 | N | 0
2025-01-31 | 21 | 2031-01-31 21:00 | 22.47 | 29.5218 | N | 0
2025-01-31 | 22 | 2031-01-31 22:00 | 21.9 | 28.7729 | N | 0
2025-01-31 | 23 | 2031-01-31 23:00 | 20.8 | 27.3277 | N | 0
2025-02-01 | 00 | 2031-02-01 | 19.04 | 25.0153 | N | 0
2025-02-01 | 01 | 2031-02-01 01:00 | 18.49 | 24.2927 | N | 0
2025-02-01 | 02 | 2031-02-01 02:00 | 17.66 | 23.2022 | N | 0
2025-02-01 | 03 | 2031-02-01 03:00 | 16.95 | 22.2694 | N | 0
2025-02-01 | 04 | 2031-02-01 04:00 | 16.78 | 22.0461 | N | 0
2025-02-01 | 05 | 2031-02-01 05:00 | 16.85 | 22.138 | N | 0
2025-02-01 | 06 | 2031-02-01 06:00 | 17.17 | 22.5585 | N | 0
2025-02-01 | 07 | 2031-02-01 07:00 | 18.18 | 23.8854 | N | 0
2025-02-01 | 08 | 2031-02-01 08:00 | 19.61 | 25.7642 | N | 0
2025-02-01 | 09 | 2031-02-01 09:00 | 20.86 | 27.4065 | N | 0
2025-02-01 | 10 | 2031-02-01 10:00 | 22.2 | 29.167 | N | 0
2025-02-01 | 11 | 2031-02-01 11:00 | 22.62 | 29.7188 | N | 0
2025-02-01 | 12 | 2031-02-01 12:00 | 23.15 | 30.4152 | N | 0
2025-02-01 | 13 | 2031-02-01 13:00 | 23.15 | 30.4152 | N | 0
2025-02-01 | 14 | 2031-02-01 14:00 | 22.72 | 29.8502 | N | 0
2025-02-01 | 15 | 2031-02-01 15:00 | 22.46 | 29.5086 | N | 0
2025-02-01 | 16 | 2031-02-01 16:00 | 22.83 | 29.9947 | N | 0
2025-02-01 | 17 | 2031-02-01 17:00 | 23.48 | 30.8487 | N | 0
2025-02-01 | 18 | 2031-02-01 18:00 | 25.39 | 33.3581 | N | 0
2025-02-01 | 19 | 2031-02-01 19:00 | 25.6 | 33.634 | N | 0
2025-02-01 | 20 | 2031-02-01 20:00 | 24.89 | 32.7012 | N | 0
2025-02-01 | 21 | 2031-02-01 21:00 | 24.68 | 32.4253 | N | 0
2025-02-01 | 22 | 2031-02-01 22:00 | 23.87 | 31.3611 | N | 0
2025-02-01 | 23 | 2031-02-01 23:00 | 22.79 | 29.9422 | N | 0
2025-02-02 | 00 | 2031-02-02 | 21.37 | 28.0765 | N | 0
2025-02-02 | 01 | 2031-02-02 01:00 | 20.25 | 26.6051 | N | 0
2025-02-02 | 02 | 2031-02-02 02:00 | 19.12 | 25.1204 | N | 0
2025-02-02 | 03 | 2031-02-02 03:00 | 18.2 | 23.9117 | N | 0
2025-02-02 | 04 | 2031-02-02 04:00 | 17.84 | 23.4387 | N | 0
2025-02-02 | 05 | 2031-02-02 05:00 | 17.74 | 23.3073 | N | 0
2025-02-02 | 06 | 2031-02-02 06:00 | 17.9 | 23.5176 | N | 0
2025-02-02 | 07 | 2031-02-02 07:00 | 18.4 | 24.1745 | N | 0
2025-02-02 | 08 | 2031-02-02 08:00 | 19.23 | 25.2649 | N | 0
2025-02-02 | 09 | 2031-02-02 09:00 | 20.9 | 27.459 | N | 0
2025-02-02 | 10 | 2031-02-02 10:00 | 22.3 | 29.2984 | N | 0
2025-02-02 | 11 | 2031-02-02 11:00 | 23.22 | 30.5071 | N | 0
2025-02-02 | 12 | 2031-02-02 12:00 | 23.98 | 31.5056 | N | 0
2025-02-02 | 13 | 2031-02-02 13:00 | 24.41 | 32.0706 | N | 0
2025-02-02 | 14 | 2031-02-02 14:00 | 24.55 | 32.2545 | N | 0
2025-02-02 | 15 | 2031-02-02 15:00 | 24.4 | 32.0574 | N | 0
2025-02-02 | 16 | 2031-02-02 16:00 | 24.72 | 32.4779 | N | 0
2025-02-02 | 17 | 2031-02-02 17:00 | 26.33 | 34.5931 | N | 0
2025-02-02 | 18 | 2031-02-02 18:00 | 27.12 | 35.6311 | N | 0
2025-02-02 | 19 | 2031-02-02 19:00 | 27.23 | 35.7756 | N | 0
2025-02-02 | 20 | 2031-02-02 20:00 | 26.13 | 34.3304 | N | 0
2025-02-02 | 21 | 2031-02-02 21:00 | 24.96 | 32.7932 | N | 0
2025-02-02 | 22 | 2031-02-02 22:00 | 23.69 | 31.1246 | N | 0
2025-02-02 | 23 | 2031-02-02 23:00 | 21.58 | 28.3524 | N | 0
2025-02-03 | 00 | 2031-02-03 | 19.71 | 25.8956 | N | 0
2025-02-03 | 01 | 2031-02-03 01:00 | 17.81 | 23.3993 | N | 0
2025-02-03 | 02 | 2031-02-03 02:00 | 16.8 | 22.0723 | N | 0
2025-02-03 | 03 | 2031-02-03 03:00 | 16.15 | 21.2184 | N | 0
2025-02-03 | 04 | 2031-02-03 04:00 | 15.83 | 20.7979 | N | 0
2025-02-03 | 05 | 2031-02-03 05:00 | 15.9 | 20.8899 | N | 0
2025-02-03 | 06 | 2031-02-03 06:00 | 16.96 | 22.2826 | N | 0
2025-02-03 | 07 | 2031-02-03 07:00 | 19.27 | 25.3175 | N | 0
2025-02-03 | 08 | 2031-02-03 08:00 | 21.33 | 28.024 | N | 0
2025-02-03 | 09 | 2031-02-03 09:00 | 21.8 | 28.6415 | N | 0
2025-02-03 | 10 | 2031-02-03 10:00 | 22.15 | 29.1013 | N | 0
2025-02-03 | 11 | 2031-02-03 11:00 | 22.51 | 29.5743 | N | 0
2025-02-03 | 12 | 2031-02-03 12:00 | 22.86 | 30.0341 | N | 0
2025-02-03 | 13 | 2031-02-03 13:00 | 22.76 | 29.9028 | N | 0
2025-02-03 | 14 | 2031-02-03 14:00 | 22.51 | 29.5743 | N | 0
2025-02-03 | 15 | 2031-02-03 15:00 | 22.11 | 29.0488 | N | 0
2025-02-03 | 16 | 2031-02-03 16:00 | 22.57 | 29.6531 | N | 0
2025-02-03 | 17 | 2031-02-03 17:00 | 23.76 | 31.2166 | N | 0
2025-02-03 | 18 | 2031-02-03 18:00 | 25.06 | 32.9246 | N | 0
2025-02-03 | 19 | 2031-02-03 19:00 | 24.81 | 32.5961 | N | 0
2025-02-03 | 20 | 2031-02-03 20:00 | 23.6 | 31.0064 | N | 0
2025-02-03 | 21 | 2031-02-03 21:00 | 23.17 | 30.4414 | N | 0
2025-02-03 | 22 | 2031-02-03 22:00 | 21.92 | 28.7991 | N | 0
2025-02-03 | 23 | 2031-02-03 23:00 | 20.45 | 26.8678 | N | 0
2025-02-04 | 00 | 2031-02-04 | 18.28 | 24.0168 | N | 0
2025-02-04 | 01 | 2031-02-04 01:00 | 17.02 | 22.3614 | N | 0
2025-02-04 | 02 | 2031-02-04 02:00 | 16.11 | 21.1658 | N | 0
2025-02-04 | 03 | 2031-02-04 03:00 | 15.51 | 20.3775 | N | 0
2025-02-04 | 04 | 2031-02-04 04:00 | 15.27 | 20.0622 | N | 0
2025-02-04 | 05 | 2031-02-04 05:00 | 15.38 | 20.2067 | N | 0
2025-02-04 | 06 | 2031-02-04 06:00 | 16.2 | 21.284 | N | 0
2025-02-04 | 07 | 2031-02-04 07:00 | 18.77 | 24.6606 | N | 0
2025-02-04 | 08 | 2031-02-04 08:00 | 20.64 | 27.1174 | N | 0
2025-02-04 | 09 | 2031-02-04 09:00 | 21.37 | 28.0765 | N | 0
2025-02-04 | 10 | 2031-02-04 10:00 | 21.44 | 28.1685 | N | 0
2025-02-04 | 11 | 2031-02-04 11:00 | 21.97 | 28.8648 | N | 0
2025-02-04 | 12 | 2031-02-04 12:00 | 22.37 | 29.3904 | N | 0
2025-02-04 | 13 | 2031-02-04 13:00 | 22.2 | 29.167 | N | 0
2025-02-04 | 14 | 2031-02-04 14:00 | 21.85 | 28.7072 | N | 0
2025-02-04 | 15 | 2031-02-04 15:00 | 21.55 | 28.313 | N | 0
2025-02-04 | 16 | 2031-02-04 16:00 | 22.02 | 28.9305 | N | 0
2025-02-04 | 17 | 2031-02-04 17:00 | 23.3 | 30.6122 | N | 0
2025-02-04 | 18 | 2031-02-04 18:00 | 25.33 | 33.2793 | N | 0
2025-02-04 | 19 | 2031-02-04 19:00 | 25.87 | 33.9888 | N | 0
2025-02-04 | 20 | 2031-02-04 20:00 | 24.96 | 32.7932 | N | 0
2025-02-04 | 21 | 2031-02-04 21:00 | 24.69 | 32.4385 | N | 0
2025-02-04 | 22 | 2031-02-04 22:00 | 24.01 | 31.5451 | N | 0
2025-02-04 | 23 | 2031-02-04 23:00 | 22.51 | 29.5743 | N | 0
2025-02-05 | 00 | 2031-02-05 | 20.29 | 26.6576 | N | 0
2025-02-05 | 01 | 2031-02-05 01:00 | 18.86 | 24.7788 | N | 0
2025-02-05 | 02 | 2031-02-05 02:00 | 18.05 | 23.7146 | N | 0
2025-02-05 | 03 | 2031-02-05 03:00 | 17.61 | 23.1365 | N | 0
2025-02-05 | 04 | 2031-02-05 04:00 | 17.35 | 22.7949 | N | 0
2025-02-05 | 05 | 2031-02-05 05:00 | 17.42 | 22.8869 | N | 0
2025-02-05 | 06 | 2031-02-05 06:00 | 18.56 | 24.3847 | N | 0
2025-02-05 | 07 | 2031-02-05 07:00 | 20.59 | 27.0518 | N | 0
2025-02-05 | 08 | 2031-02-05 08:00 | 22.51 | 29.5743 | N | 0
2025-02-05 | 09 | 2031-02-05 09:00 | 22.52 | 29.5874 | N | 0
2025-02-05 | 10 | 2031-02-05 10:00 | 22.05 | 28.9699 | N | 0
2025-02-05 | 11 | 2031-02-05 11:00 | 22.33 | 29.3378 | N | 0
2025-02-05 | 12 | 2031-02-05 12:00 | 22.49 | 29.548 | N | 0
2025-02-05 | 13 | 2031-02-05 13:00 | 22.18 | 29.1407 | N | 0
2025-02-05 | 14 | 2031-02-05 14:00 | 21.64 | 28.4313 | N | 0
2025-02-05 | 15 | 2031-02-05 15:00 | 21.96 | 28.8517 | N | 0
2025-02-05 | 16 | 2031-02-05 16:00 | 22.45 | 29.4955 | N | 0
2025-02-05 | 17 | 2031-02-05 17:00 | 23.1 | 30.3495 | N | 0
2025-02-05 | 18 | 2031-02-05 18:00 | 25.17 | 33.0691 | N | 0
2025-02-05 | 19 | 2031-02-05 19:00 | 25.48 | 33.4764 | N | 0
2025-02-05 | 20 | 2031-02-05 20:00 | 25.25 | 33.1742 | N | 0
2025-02-05 | 21 | 2031-02-05 21:00 | 24.83 | 32.6224 | N | 0
2025-02-05 | 22 | 2031-02-05 22:00 | 23.96 | 31.4794 | N | 0
2025-02-05 | 23 | 2031-02-05 23:00 | 22.65 | 29.7582 | N | 0
2025-02-06 | 00 | 2031-02-06 | 20.58 | 27.0386 | N | 0
2025-02-06 | 01 | 2031-02-06 01:00 | 19.17 | 25.1861 | N | 0
2025-02-06 | 02 | 2031-02-06 02:00 | 17.92 | 23.5438 | N | 0
2025-02-06 | 03 | 2031-02-06 03:00 | 17.4 | 22.8606 | N | 0
2025-02-06 | 04 | 2031-02-06 04:00 | 17.24 | 22.6504 | N | 0
2025-02-06 | 05 | 2031-02-06 05:00 | 17.28 | 22.703 | N | 0
2025-02-06 | 06 | 2031-02-06 06:00 | 17.9 | 23.5176 | N | 0
2025-02-06 | 07 | 2031-02-06 07:00 | 20.06 | 26.3554 | N | 0
2025-02-06 | 08 | 2031-02-06 08:00 | 21.75 | 28.5758 | N | 0
2025-02-06 | 09 | 2031-02-06 09:00 | 22.66 | 29.7714 | N | 0
2025-02-06 | 10 | 2031-02-06 10:00 | 23.15 | 30.4152 | N | 0
2025-02-06 | 11 | 2031-02-06 11:00 | 23.31 | 30.6254 | N | 0
2025-02-06 | 12 | 2031-02-06 12:00 | 23.62 | 31.0327 | N | 0
2025-02-06 | 13 | 2031-02-06 13:00 | 23.92 | 31.4268 | N | 0
2025-02-06 | 14 | 2031-02-06 14:00 | 23.58 | 30.9801 | N | 0
2025-02-06 | 15 | 2031-02-06 15:00 | 22.98 | 30.1918 | N | 0
2025-02-06 | 16 | 2031-02-06 16:00 | 23.47 | 30.8356 | N | 0
2025-02-06 | 17 | 2031-02-06 17:00 | 24.38 | 32.0312 | N | 0
2025-02-06 | 18 | 2031-02-06 18:00 | 25.41 | 33.3844 | N | 0
2025-02-06 | 19 | 2031-02-06 19:00 | 25.68 | 33.7391 | N | 0
2025-02-06 | 20 | 2031-02-06 20:00 | 24.75 | 32.5173 | N | 0
2025-02-06 | 21 | 2031-02-06 21:00 | 24.26 | 31.8735 | N | 0
2025-02-06 | 22 | 2031-02-06 22:00 | 22.56 | 29.64 | N | 0
2025-02-06 | 23 | 2031-02-06 23:00 | 21.24 | 27.9057 | N | 0
2025-02-07 | 00 | 2031-02-07 | 19.73 | 25.9219 | N | 0
2025-02-07 | 01 | 2031-02-07 01:00 | 18.31 | 24.0562 | N | 0
2025-02-07 | 02 | 2031-02-07 02:00 | 17.03 | 22.3745 | N | 0
2025-02-07 | 03 | 2031-02-07 03:00 | 16.48 | 21.6519 | N | 0
2025-02-07 | 04 | 2031-02-07 04:00 | 16.12 | 21.1789 | N | 0
2025-02-07 | 05 | 2031-02-07 05:00 | 16.59 | 21.7964 | N | 0
2025-02-07 | 06 | 2031-02-07 06:00 | 17.5 | 22.992 | N | 0
2025-02-07 | 07 | 2031-02-07 07:00 | 20.04 | 26.3291 | N | 0
2025-02-07 | 08 | 2031-02-07 08:00 | 21.83 | 28.6809 | N | 0
2025-02-07 | 09 | 2031-02-07 09:00 | 22.31 | 29.3115 | N | 0
2025-02-07 | 10 | 2031-02-07 10:00 | 22.46 | 29.5086 | N | 0
2025-02-07 | 11 | 2031-02-07 11:00 | 22.27 | 29.259 | N | 0
2025-02-07 | 12 | 2031-02-07 12:00 | 22.49 | 29.548 | N | 0
2025-02-07 | 13 | 2031-02-07 13:00 | 22.14 | 29.0882 | N | 0
2025-02-07 | 14 | 2031-02-07 14:00 | 22.4 | 29.4298 | N | 0
2025-02-07 | 15 | 2031-02-07 15:00 | 22.28 | 29.2721 | N | 0
2025-02-07 | 16 | 2031-02-07 16:00 | 22.27 | 29.259 | N | 0
2025-02-07 | 17 | 2031-02-07 17:00 | 22.51 | 29.5743 | N | 0
2025-02-07 | 18 | 2031-02-07 18:00 | 24.2 | 31.7947 | N | 0
2025-02-07 | 19 | 2031-02-07 19:00 | 24.61 | 32.3334 | N | 0
2025-02-07 | 20 | 2031-02-07 20:00 | 23.97 | 31.4925 | N | 0
2025-02-07 | 21 | 2031-02-07 21:00 | 23.69 | 31.1246 | N | 0
2025-02-07 | 22 | 2031-02-07 22:00 | 22.56 | 29.64 | N | 0
2025-02-07 | 23 | 2031-02-07 23:00 | 22.07 | 28.9962 | N | 0
2025-02-08 | 00 | 2031-02-08 | 20.41 | 26.8153 | N | 0
2025-02-08 | 01 | 2031-02-08 01:00 | 18.69 | 24.5555 | N | 0
2025-02-08 | 02 | 2031-02-08 02:00 | 17.69 | 23.2416 | N | 0
2025-02-08 | 03 | 2031-02-08 03:00 | 16.78 | 22.0461 | N | 0
2025-02-08 | 04 | 2031-02-08 04:00 | 16.34 | 21.468 | N | 0
2025-02-08 | 05 | 2031-02-08 05:00 | 16.27 | 21.376 | N | 0
2025-02-08 | 06 | 2031-02-08 06:00 | 16.41 | 21.5599 | N | 0
2025-02-08 | 07 | 2031-02-08 07:00 | 17.55 | 23.0577 | N | 0
2025-02-08 | 08 | 2031-02-08 08:00 | 18.72 | 24.5949 | N | 0
2025-02-08 | 09 | 2031-02-08 09:00 | 19.9 | 26.1452 | N | 0
2025-02-08 | 10 | 2031-02-08 10:00 | 20.88 | 27.4328 | N | 0
2025-02-08 | 11 | 2031-02-08 11:00 | 21.44 | 28.1685 | N | 0
2025-02-08 | 12 | 2031-02-08 12:00 | 22.33 | 29.3378 | N | 0
2025-02-08 | 13 | 2031-02-08 13:00 | 23.1 | 30.3495 | N | 0
2025-02-08 | 14 | 2031-02-08 14:00 | 22.75 | 29.8896 | N | 0
2025-02-08 | 15 | 2031-02-08 15:00 | 22.69 | 29.8108 | N | 0
2025-02-08 | 16 | 2031-02-08 16:00 | 22.33 | 29.3378 | N | 0
2025-02-08 | 17 | 2031-02-08 17:00 | 23.06 | 30.2969 | N | 0
2025-02-08 | 18 | 2031-02-08 18:00 | 24.75 | 32.5173 | N | 0
2025-02-08 | 19 | 2031-02-08 19:00 | 24.89 | 32.7012 | N | 0
2025-02-08 | 20 | 2031-02-08 20:00 | 23.76 | 31.2166 | N | 0
2025-02-08 | 21 | 2031-02-08 21:00 | 23.19 | 30.4677 | N | 0
2025-02-08 | 22 | 2031-02-08 22:00 | 22.27 | 29.259 | N | 0
2025-02-08 | 23 | 2031-02-08 23:00 | 21.08 | 27.6955 | N | 0
2025-02-09 | 00 | 2031-02-09 | 19.23 | 25.2649 | N | 0
2025-02-09 | 01 | 2031-02-09 01:00 | 18.11 | 23.7935 | N | 0
2025-02-09 | 02 | 2031-02-09 02:00 | 17.09 | 22.4534 | N | 0
2025-02-09 | 03 | 2031-02-09 03:00 | 16.24 | 21.3366 | N | 0
2025-02-09 | 04 | 2031-02-09 04:00 | 15.73 | 20.6665 | N | 0
2025-02-09 | 05 | 2031-02-09 05:00 | 15.78 | 20.7322 | N | 0
2025-02-09 | 06 | 2031-02-09 06:00 | 15.8 | 20.7585 | N | 0
2025-02-09 | 07 | 2031-02-09 07:00 | 16.28 | 21.3891 | N | 0
2025-02-09 | 08 | 2031-02-09 08:00 | 17.55 | 23.0577 | N | 0
2025-02-09 | 09 | 2031-02-09 09:00 | 19.03 | 25.0022 | N | 0
2025-02-09 | 10 | 2031-02-09 10:00 | 20.24 | 26.5919 | N | 0
2025-02-09 | 11 | 2031-02-09 11:00 | 21.01 | 27.6036 | N | 0
2025-02-09 | 12 | 2031-02-09 12:00 | 21.82 | 28.6678 | N | 0
2025-02-09 | 13 | 2031-02-09 13:00 | 22.66 | 29.7714 | N | 0
2025-02-09 | 14 | 2031-02-09 14:00 | 22.16 | 29.1145 | N | 0
2025-02-09 | 15 | 2031-02-09 15:00 | 22.09 | 29.0225 | N | 0
2025-02-09 | 16 | 2031-02-09 16:00 | 22.24 | 29.2196 | N | 0
2025-02-09 | 17 | 2031-02-09 17:00 | 24.03 | 31.5713 | N | 0
2025-02-09 | 18 | 2031-02-09 18:00 | 25.83 | 33.9362 | N | 0
2025-02-09 | 19 | 2031-02-09 19:00 | 26.04 | 34.2121 | N | 0
2025-02-09 | 20 | 2031-02-09 20:00 | 24.7 | 32.4516 | N | 0
2025-02-09 | 21 | 2031-02-09 21:00 | 23.78 | 31.2429 | N | 0
2025-02-09 | 22 | 2031-02-09 22:00 | 22.26 | 29.2459 | N | 0
2025-02-09 | 23 | 2031-02-09 23:00 | 20.55 | 26.9992 | N | 0
2025-02-10 | 00 | 2031-02-10 | 19.47 | 25.5803 | N | 0
2025-02-10 | 01 | 2031-02-10 01:00 | 17.37 | 22.8212 | N | 0
2025-02-10 | 02 | 2031-02-10 02:00 | 16.29 | 21.4023 | N | 0
2025-02-10 | 03 | 2031-02-10 03:00 | 15.92 | 20.9162 | N | 0
2025-02-10 | 04 | 2031-02-10 04:00 | 15.7 | 20.6271 | N | 0
2025-02-10 | 05 | 2031-02-10 05:00 | 15.83 | 20.7979 | N | 0
2025-02-10 | 06 | 2031-02-10 06:00 | 16.9 | 22.2037 | N | 0
2025-02-10 | 07 | 2031-02-10 07:00 | 18.94 | 24.8839 | N | 0
2025-02-10 | 08 | 2031-02-10 08:00 | 20.96 | 27.5379 | N | 0
2025-02-10 | 09 | 2031-02-10 09:00 | 21.7 | 28.5101 | N | 0
2025-02-10 | 10 | 2031-02-10 10:00 | 22.06 | 28.9831 | N | 0
2025-02-10 | 11 | 2031-02-10 11:00 | 22.44 | 29.4823 | N | 0
2025-02-10 | 12 | 2031-02-10 12:00 | 22.43 | 29.4692 | N | 0
2025-02-10 | 13 | 2031-02-10 13:00 | 22.78 | 29.929 | N | 0
2025-02-10 | 14 | 2031-02-10 14:00 | 22.41 | 29.4429 | N | 0
2025-02-10 | 15 | 2031-02-10 15:00 | 22.32 | 29.3247 | N | 0
2025-02-10 | 16 | 2031-02-10 16:00 | 22.68 | 29.7977 | N | 0
2025-02-10 | 17 | 2031-02-10 17:00 | 23.79 | 31.256 | N | 0
2025-02-10 | 18 | 2031-02-10 18:00 | 25.19 | 33.0954 | N | 0
2025-02-10 | 19 | 2031-02-10 19:00 | 25.57 | 33.5946 | N | 0
2025-02-10 | 20 | 2031-02-10 20:00 | 24.53 | 32.2282 | N | 0
2025-02-10 | 21 | 2031-02-10 21:00 | 24.07 | 31.6239 | N | 0
2025-02-10 | 22 | 2031-02-10 22:00 | 23.36 | 30.6911 | N | 0
2025-02-10 | 23 | 2031-02-10 23:00 | 21.68 | 28.4838 | N | 0
2025-02-11 | 00 | 2031-02-11 | 19.82 | 26.0401 | N | 0
2025-02-11 | 01 | 2031-02-11 01:00 | 18.22 | 23.938 | N | 0
2025-02-11 | 02 | 2031-02-11 02:00 | 17.28 | 22.703 | N | 0
2025-02-11 | 03 | 2031-02-11 03:00 | 16.55 | 21.7439 | N | 0
2025-02-11 | 04 | 2031-02-11 04:00 | 16.33 | 21.4548 | N | 0
2025-02-11 | 05 | 2031-02-11 05:00 | 16.72 | 21.9672 | N | 0
2025-02-11 | 06 | 2031-02-11 06:00 | 17.75 | 23.3205 | N | 0
2025-02-11 | 07 | 2031-02-11 07:00 | 20.48 | 26.9072 | N | 0
2025-02-11 | 08 | 2031-02-11 08:00 | 22.52 | 29.5874 | N | 0
2025-02-11 | 09 | 2031-02-11 09:00 | 22.33 | 29.3378 | N | 0
2025-02-11 | 10 | 2031-02-11 10:00 | 22.6 | 29.6926 | N | 0
2025-02-11 | 11 | 2031-02-11 11:00 | 22.74 | 29.8765 | N | 0
2025-02-11 | 12 | 2031-02-11 12:00 | 22.72 | 29.8502 | N | 0
2025-02-11 | 13 | 2031-02-11 13:00 | 22.05 | 28.9699 | N | 0
2025-02-11 | 14 | 2031-02-11 14:00 | 22.31 | 29.3115 | N | 0
2025-02-11 | 15 | 2031-02-11 15:00 | 21.62 | 28.405 | N | 0
2025-02-11 | 16 | 2031-02-11 16:00 | 22.52 | 29.5874 | N | 0
2025-02-11 | 17 | 2031-02-11 17:00 | 23.33 | 30.6516 | N | 0
2025-02-11 | 18 | 2031-02-11 18:00 | 25.08 | 32.9509 | N | 0
2025-02-11 | 19 | 2031-02-11 19:00 | 25.5 | 33.5027 | N | 0
2025-02-11 | 20 | 2031-02-11 20:00 | 24.54 | 32.2414 | N | 0
2025-02-11 | 21 | 2031-02-11 21:00 | 24.26 | 31.8735 | N | 0
2025-02-11 | 22 | 2031-02-11 22:00 | 23.2 | 30.4809 | N | 0
2025-02-11 | 23 | 2031-02-11 23:00 | 21.68 | 28.4838 | N | 0
2025-02-12 | 00 | 2031-02-12 | 19.99 | 26.2635 | N | 0
2025-02-12 | 01 | 2031-02-12 01:00 | 18.17 | 23.8723 | N | 0
2025-02-12 | 02 | 2031-02-12 02:00 | 17.3 | 22.7293 | N | 0
2025-02-12 | 03 | 2031-02-12 03:00 | 16.63 | 21.849 | N | 0
2025-02-12 | 04 | 2031-02-12 04:00 | 16.71 | 21.9541 | N | 0
2025-02-12 | 05 | 2031-02-12 05:00 | 16.89 | 22.1906 | N | 0
2025-02-12 | 06 | 2031-02-12 06:00 | 18.09 | 23.7672 | N | 0
2025-02-12 | 07 | 2031-02-12 07:00 | 20.3 | 26.6707 | N | 0
2025-02-12 | 08 | 2031-02-12 08:00 | 22.82 | 29.9816 | N | 0
2025-02-12 | 09 | 2031-02-12 09:00 | 23.11 | 30.3626 | N | 0
2025-02-12 | 10 | 2031-02-12 10:00 | 23.5 | 30.875 | N | 0
2025-02-12 | 11 | 2031-02-12 11:00 | 23.07 | 30.3101 | N | 0
2025-02-12 | 12 | 2031-02-12 12:00 | 22.99 | 30.2049 | N | 0
2025-02-12 | 13 | 2031-02-12 13:00 | 23.14 | 30.402 | N | 0
2025-02-12 | 14 | 2031-02-12 14:00 | 23.08 | 30.3232 | N | 0
2025-02-12 | 15 | 2031-02-12 15:00 | 23.34 | 30.6648 | N | 0
2025-02-12 | 16 | 2031-02-12 16:00 | 24.08 | 31.637 | N | 0
2025-02-12 | 17 | 2031-02-12 17:00 | 25.21 | 33.1216 | N | 0
2025-02-12 | 18 | 2031-02-12 18:00 | 26.42 | 34.7114 | N | 0
2025-02-12 | 19 | 2031-02-12 19:00 | 26.28 | 34.5274 | N | 0
2025-02-12 | 20 | 2031-02-12 20:00 | 25.47 | 33.4632 | N | 0
2025-02-12 | 21 | 2031-02-12 21:00 | 25.01 | 32.8589 | N | 0
2025-02-12 | 22 | 2031-02-12 22:00 | 24.16 | 31.7421 | N | 0
2025-02-12 | 23 | 2031-02-12 23:00 | 22.71 | 29.8371 | N | 0
2025-02-13 | 00 | 2031-02-13 | 20.29 | 26.6576 | N | 0
2025-02-13 | 01 | 2031-02-13 01:00 | 18.78 | 24.6737 | N | 0
2025-02-13 | 02 | 2031-02-13 02:00 | 17.76 | 23.3336 | N | 0
2025-02-13 | 03 | 2031-02-13 03:00 | 17.16 | 22.5453 | N | 0
2025-02-13 | 04 | 2031-02-13 04:00 | 16.71 | 21.9541 | N | 0
2025-02-13 | 05 | 2031-02-13 05:00 | 16.84 | 22.1249 | N | 0
2025-02-13 | 06 | 2031-02-13 06:00 | 17.15 | 22.5322 | N | 0
2025-02-13 | 07 | 2031-02-13 07:00 | 19.14 | 25.1467 | N | 0
2025-02-13 | 08 | 2031-02-13 08:00 | 20.39 | 26.789 | N | 0
2025-02-13 | 09 | 2031-02-13 09:00 | 21.31 | 27.9977 | N | 0
2025-02-13 | 10 | 2031-02-13 10:00 | 22.55 | 29.6269 | N | 0
2025-02-13 | 11 | 2031-02-13 11:00 | 23.11 | 30.3626 | N | 0
2025-02-13 | 12 | 2031-02-13 12:00 | 23.62 | 31.0327 | N | 0
2025-02-13 | 13 | 2031-02-13 13:00 | 24.15 | 31.729 | N | 0
2025-02-13 | 14 | 2031-02-13 14:00 | 24.22 | 31.821 | N | 0
2025-02-13 | 15 | 2031-02-13 15:00 | 23.4 | 30.7436 | N | 0
2025-02-13 | 16 | 2031-02-13 16:00 | 23.21 | 30.494 | N | 0
2025-02-13 | 17 | 2031-02-13 17:00 | 23.72 | 31.164 | N | 0
2025-02-13 | 18 | 2031-02-13 18:00 | 24.88 | 32.6881 | N | 0
2025-02-13 | 19 | 2031-02-13 19:00 | 25.57 | 33.5946 | N | 0
2025-02-13 | 20 | 2031-02-13 20:00 | 24.4 | 32.0574 | N | 0
2025-02-13 | 21 | 2031-02-13 21:00 | 24.26 | 31.8735 | N | 0
2025-02-13 | 22 | 2031-02-13 22:00 | 23.26 | 30.5597 | N | 0
2025-02-13 | 23 | 2031-02-13 23:00 | 21.63 | 28.4181 | N | 0
2025-02-14 | 00 | 2031-02-14 | 19.89 | 26.1321 | N | 0
2025-02-14 | 01 | 2031-02-14 01:00 | 18.39 | 24.1613 | N | 0
2025-02-14 | 02 | 2031-02-14 02:00 | 17.28 | 22.703 | N | 0
2025-02-14 | 03 | 2031-02-14 03:00 | 17.08 | 22.4402 | N | 0
2025-02-14 | 04 | 2031-02-14 04:00 | 16.62 | 21.8359 | N | 0
2025-02-14 | 05 | 2031-02-14 05:00 | 16.77 | 22.0329 | N | 0
2025-02-14 | 06 | 2031-02-14 06:00 | 17.69 | 23.2416 | N | 0
2025-02-14 | 07 | 2031-02-14 07:00 | 20.21 | 26.5525 | N | 0
2025-02-14 | 08 | 2031-02-14 08:00 | 21.72 | 28.5364 | N | 0
2025-02-14 | 09 | 2031-02-14 09:00 | 22.59 | 29.6794 | N | 0
2025-02-14 | 10 | 2031-02-14 10:00 | 22.79 | 29.9422 | N | 0
2025-02-14 | 11 | 2031-02-14 11:00 | 23.12 | 30.3757 | N | 0
2025-02-14 | 12 | 2031-02-14 12:00 | 22.22 | 29.1933 | N | 0
2025-02-14 | 13 | 2031-02-14 13:00 | 22.33 | 29.3378 | N | 0
2025-02-14 | 14 | 2031-02-14 14:00 | 22.68 | 29.7977 | N | 0
2025-02-14 | 15 | 2031-02-14 15:00 | 22.61 | 29.7057 | N | 0
2025-02-14 | 16 | 2031-02-14 16:00 | 22.54 | 29.6137 | N | 0
2025-02-14 | 17 | 2031-02-14 17:00 | 22.78 | 29.929 | N | 0
2025-02-14 | 18 | 2031-02-14 18:00 | 23.46 | 30.8224 | N | 0
2025-02-14 | 19 | 2031-02-14 19:00 | 23.85 | 31.3348 | N | 0
2025-02-14 | 20 | 2031-02-14 20:00 | 23.59 | 30.9932 | N | 0
2025-02-14 | 21 | 2031-02-14 21:00 | 23.31 | 30.6254 | N | 0
2025-02-14 | 22 | 2031-02-14 22:00 | 22.56 | 29.64 | N | 0
2025-02-14 | 23 | 2031-02-14 23:00 | 21.37 | 28.0765 | N | 0
2025-02-15 | 00 | 2031-02-15 | 19.91 | 26.1584 | N | 0
2025-02-15 | 01 | 2031-02-15 01:00 | 18.39 | 24.1613 | N | 0
2025-02-15 | 02 | 2031-02-15 02:00 | 17.66 | 23.2022 | N | 0
2025-02-15 | 03 | 2031-02-15 03:00 | 16.75 | 22.0066 | N | 0
2025-02-15 | 04 | 2031-02-15 04:00 | 16.25 | 21.3497 | N | 0
2025-02-15 | 05 | 2031-02-15 05:00 | 16.32 | 21.4417 | N | 0
2025-02-15 | 06 | 2031-02-15 06:00 | 16.44 | 21.5994 | N | 0
2025-02-15 | 07 | 2031-02-15 07:00 | 17.11 | 22.4796 | N | 0
2025-02-15 | 08 | 2031-02-15 08:00 | 18.2 | 23.9117 | N | 0
2025-02-15 | 09 | 2031-02-15 09:00 | 19.69 | 25.8693 | N | 0
2025-02-15 | 10 | 2031-02-15 10:00 | 21.3 | 27.9846 | N | 0
2025-02-15 | 11 | 2031-02-15 11:00 | 22.05 | 28.9699 | N | 0
2025-02-15 | 12 | 2031-02-15 12:00 | 22.45 | 29.4955 | N | 0
2025-02-15 | 13 | 2031-02-15 13:00 | 22.79 | 29.9422 | N | 0
2025-02-15 | 14 | 2031-02-15 14:00 | 22.97 | 30.1787 | N | 0
2025-02-15 | 15 | 2031-02-15 15:00 | 23 | 30.2181 | N | 0
2025-02-15 | 16 | 2031-02-15 16:00 | 22.71 | 29.8371 | N | 0
2025-02-15 | 17 | 2031-02-15 17:00 | 23.68 | 31.1115 | N | 0
2025-02-15 | 18 | 2031-02-15 18:00 | 25.06 | 32.9246 | N | 0
2025-02-15 | 19 | 2031-02-15 19:00 | 25.1 | 32.9771 | N | 0
2025-02-15 | 20 | 2031-02-15 20:00 | 24.2 | 31.7947 | N | 0
2025-02-15 | 21 | 2031-02-15 21:00 | 23.54 | 30.9276 | N | 0
2025-02-15 | 22 | 2031-02-15 22:00 | 22.2 | 29.167 | N | 0
2025-02-15 | 23 | 2031-02-15 23:00 | 21.11 | 27.7349 | N | 0
2025-02-16 | 00 | 2031-02-16 | 19.52 | 25.646 | N | 0
2025-02-16 | 01 | 2031-02-16 01:00 | 18.29 | 24.0299 | N | 0
2025-02-16 | 02 | 2031-02-16 02:00 | 17.14 | 22.519 | N | 0
2025-02-16 | 03 | 2031-02-16 03:00 | 16.46 | 21.6256 | N | 0
2025-02-16 | 04 | 2031-02-16 04:00 | 16.16 | 21.2315 | N | 0
2025-02-16 | 05 | 2031-02-16 05:00 | 16.21 | 21.2972 | N | 0
2025-02-16 | 06 | 2031-02-16 06:00 | 16.53 | 21.7176 | N | 0
2025-02-16 | 07 | 2031-02-16 07:00 | 16.92 | 22.23 | N | 0
2025-02-16 | 08 | 2031-02-16 08:00 | 18.1 | 23.7803 | N | 0
2025-02-16 | 09 | 2031-02-16 09:00 | 19.69 | 25.8693 | N | 0
2025-02-16 | 10 | 2031-02-16 10:00 | 21.23 | 27.8926 | N | 0
2025-02-16 | 11 | 2031-02-16 11:00 | 22.26 | 29.2459 | N | 0
2025-02-16 | 12 | 2031-02-16 12:00 | 23.46 | 30.8224 | N | 0
2025-02-16 | 13 | 2031-02-16 13:00 | 24.2 | 31.7947 | N | 0
2025-02-16 | 14 | 2031-02-16 14:00 | 23.99 | 31.5188 | N | 0
2025-02-16 | 15 | 2031-02-16 15:00 | 23.64 | 31.0589 | N | 0
2025-02-16 | 16 | 2031-02-16 16:00 | 23.49 | 30.8619 | N | 0
2025-02-16 | 17 | 2031-02-16 17:00 | 24.46 | 32.1363 | N | 0
2025-02-16 | 18 | 2031-02-16 18:00 | 25.88 | 34.0019 | N | 0
2025-02-16 | 19 | 2031-02-16 19:00 | 26.03 | 34.199 | N | 0
2025-02-16 | 20 | 2031-02-16 20:00 | 25.05 | 32.9114 | N | 0
2025-02-16 | 21 | 2031-02-16 21:00 | 24.24 | 31.8472 | N | 0
2025-02-16 | 22 | 2031-02-16 22:00 | 22.81 | 29.9685 | N | 0
2025-02-16 | 23 | 2031-02-16 23:00 | 21.7 | 28.5101 | N | 0
2025-02-17 | 00 | 2031-02-17 | 19.85 | 26.0795 | N | 0
2025-02-17 | 01 | 2031-02-17 01:00 | 18.85 | 24.7657 | N | 0
2025-02-17 | 02 | 2031-02-17 02:00 | 17.56 | 23.0709 | N | 0
2025-02-17 | 03 | 2031-02-17 03:00 | 17.04 | 22.3877 | N | 0
2025-02-17 | 04 | 2031-02-17 04:00 | 16.73 | 21.9804 | N | 0
2025-02-17 | 05 | 2031-02-17 05:00 | 16.88 | 22.1774 | N | 0
2025-02-17 | 06 | 2031-02-17 06:00 | 17.25 | 22.6636 | N | 0
2025-02-17 | 07 | 2031-02-17 07:00 | 17.99 | 23.6358 | N | 0
2025-02-17 | 08 | 2031-02-17 08:00 | 18.74 | 24.6212 | N | 0
2025-02-17 | 09 | 2031-02-17 09:00 | 19.53 | 25.6591 | N | 0
2025-02-17 | 10 | 2031-02-17 10:00 | 20.36 | 26.7496 | N | 0
2025-02-17 | 11 | 2031-02-17 11:00 | 21.56 | 28.3262 | N | 0
2025-02-17 | 12 | 2031-02-17 12:00 | 22.26 | 29.2459 | N | 0
2025-02-17 | 13 | 2031-02-17 13:00 | 23.48 | 30.8487 | N | 0
2025-02-17 | 14 | 2031-02-17 14:00 | 23.53 | 30.9144 | N | 0
2025-02-17 | 15 | 2031-02-17 15:00 | 22.91 | 30.0998 | N | 0
2025-02-17 | 16 | 2031-02-17 16:00 | 23.31 | 30.6254 | N | 0
2025-02-17 | 17 | 2031-02-17 17:00 | 25.03 | 32.8852 | N | 0
2025-02-17 | 18 | 2031-02-17 18:00 | 26.18 | 34.3961 | N | 0
2025-02-17 | 19 | 2031-02-17 19:00 | 26.27 | 34.5143 | N | 0
2025-02-17 | 20 | 2031-02-17 20:00 | 25.43 | 33.4107 | N | 0
2025-02-17 | 21 | 2031-02-17 21:00 | 24.95 | 32.7801 | N | 0
2025-02-17 | 22 | 2031-02-17 22:00 | 24.12 | 31.6896 | N | 0
2025-02-17 | 23 | 2031-02-17 23:00 | 22.8 | 29.9553 | N | 0
2025-02-18 | 00 | 2031-02-18 | 20.58 | 27.0386 | N | 0
2025-02-18 | 01 | 2031-02-18 01:00 | 19.03 | 25.0022 | N | 0
2025-02-18 | 02 | 2031-02-18 02:00 | 17.92 | 23.5438 | N | 0
2025-02-18 | 03 | 2031-02-18 03:00 | 17.59 | 23.1103 | N | 0
2025-02-18 | 04 | 2031-02-18 04:00 | 17.36 | 22.8081 | N | 0
2025-02-18 | 05 | 2031-02-18 05:00 | 17.81 | 23.3993 | N | 0
2025-02-18 | 06 | 2031-02-18 06:00 | 18.52 | 24.3321 | N | 0
2025-02-18 | 07 | 2031-02-18 07:00 | 20.78 | 27.3014 | N | 0
2025-02-18 | 08 | 2031-02-18 08:00 | 22.26 | 29.2459 | N | 0
2025-02-18 | 09 | 2031-02-18 09:00 | 23.07 | 30.3101 | N | 0
2025-02-18 | 10 | 2031-02-18 10:00 | 23.09 | 30.3363 | N | 0
2025-02-18 | 11 | 2031-02-18 11:00 | 23.25 | 30.5465 | N | 0
2025-02-18 | 12 | 2031-02-18 12:00 | 24.01 | 31.5451 | N | 0
2025-02-18 | 13 | 2031-02-18 13:00 | 23.95 | 31.4662 | N | 0
2025-02-18 | 14 | 2031-02-18 14:00 | 23.73 | 31.1772 | N | 0
2025-02-18 | 15 | 2031-02-18 15:00 | 23.76 | 31.2166 | N | 0
2025-02-18 | 16 | 2031-02-18 16:00 | 24.11 | 31.6764 | N | 0
2025-02-18 | 17 | 2031-02-18 17:00 | 24.74 | 32.5041 | N | 0
2025-02-18 | 18 | 2031-02-18 18:00 | 26.01 | 34.1727 | N | 0
2025-02-18 | 19 | 2031-02-18 19:00 | 26.25 | 34.488 | N | 0
2025-02-18 | 20 | 2031-02-18 20:00 | 26.05 | 34.2253 | N | 0
2025-02-18 | 21 | 2031-02-18 21:00 | 25.47 | 33.4632 | N | 0
2025-02-18 | 22 | 2031-02-18 22:00 | 24.33 | 31.9655 | N | 0
2025-02-18 | 23 | 2031-02-18 23:00 | 22.78 | 29.929 | N | 0
2025-02-19 | 00 | 2031-02-19 | 20.53 | 26.9729 | N | 0
2025-02-19 | 01 | 2031-02-19 01:00 | 19.13 | 25.1336 | N | 0
2025-02-19 | 02 | 2031-02-19 02:00 | 17.9 | 23.5176 | N | 0
2025-02-19 | 03 | 2031-02-19 03:00 | 17.41 | 22.8738 | N | 0
2025-02-19 | 04 | 2031-02-19 04:00 | 17.17 | 22.5585 | N | 0
2025-02-19 | 05 | 2031-02-19 05:00 | 17.39 | 22.8475 | N | 0
2025-02-19 | 06 | 2031-02-19 06:00 | 18.55 | 24.3715 | N | 0
2025-02-19 | 07 | 2031-02-19 07:00 | 20.98 | 27.5641 | N | 0
2025-02-19 | 08 | 2031-02-19 08:00 | 23.06 | 30.2969 | N | 0
2025-02-19 | 09 | 2031-02-19 09:00 | 23.05 | 30.2838 | N | 0
2025-02-19 | 10 | 2031-02-19 10:00 | 23.15 | 30.4152 | N | 0
2025-02-19 | 11 | 2031-02-19 11:00 | 23.4 | 30.7436 | N | 0
2025-02-19 | 12 | 2031-02-19 12:00 | 23.37 | 30.7042 | N | 0
2025-02-19 | 13 | 2031-02-19 13:00 | 23.68 | 31.1115 | N | 0
2025-02-19 | 14 | 2031-02-19 14:00 | 23.02 | 30.2444 | N | 0
2025-02-19 | 15 | 2031-02-19 15:00 | 23.35 | 30.6779 | N | 0
2025-02-19 | 16 | 2031-02-19 16:00 | 22.98 | 30.1918 | N | 0
2025-02-19 | 17 | 2031-02-19 17:00 | 24.73 | 32.491 | N | 0
2025-02-19 | 18 | 2031-02-19 18:00 | 25.88 | 34.0019 | N | 0
2025-02-19 | 19 | 2031-02-19 19:00 | 26.29 | 34.5406 | N | 0
2025-02-19 | 20 | 2031-02-19 20:00 | 26 | 34.1596 | N | 0
2025-02-19 | 21 | 2031-02-19 21:00 | 25.51 | 33.5158 | N | 0
2025-02-19 | 22 | 2031-02-19 22:00 | 24.81 | 32.5961 | N | 0
2025-02-19 | 23 | 2031-02-19 23:00 | 23.16 | 30.4283 | N | 0
2025-02-20 | 00 | 2031-02-20 | 21.07 | 27.6824 | N | 0
2025-02-20 | 01 | 2031-02-20 01:00 | 19.81 | 26.027 | N | 0
2025-02-20 | 02 | 2031-02-20 02:00 | 18.52 | 24.3321 | N | 0
2025-02-20 | 03 | 2031-02-20 03:00 | 18.16 | 23.8591 | N | 0
2025-02-20 | 04 | 2031-02-20 04:00 | 17.66 | 23.2022 | N | 0
2025-02-20 | 05 | 2031-02-20 05:00 | 17.74 | 23.3073 | N | 0
2025-02-20 | 06 | 2031-02-20 06:00 | 18.37 | 24.1351 | N | 0
2025-02-20 | 07 | 2031-02-20 07:00 | 21.19 | 27.8401 | N | 0
2025-02-20 | 08 | 2031-02-20 08:00 | 23.32 | 30.6385 | N | 0
2025-02-20 | 09 | 2031-02-20 09:00 | 23.64 | 31.0589 | N | 0
2025-02-20 | 10 | 2031-02-20 10:00 | 23.9 | 31.4005 | N | 0
2025-02-20 | 11 | 2031-02-20 11:00 | 24.03 | 31.5713 | N | 0
2025-02-20 | 12 | 2031-02-20 12:00 | 24.48 | 32.1626 | N | 0
2025-02-20 | 13 | 2031-02-20 13:00 | 24.25 | 31.8604 | N | 0
2025-02-20 | 14 | 2031-02-20 14:00 | 23.91 | 31.4137 | N | 0
2025-02-20 | 15 | 2031-02-20 15:00 | 23.56 | 30.9538 | N | 0
2025-02-20 | 16 | 2031-02-20 16:00 | 23.76 | 31.2166 | N | 0
2025-02-20 | 17 | 2031-02-20 17:00 | 24.53 | 32.2282 | N | 0
2025-02-20 | 18 | 2031-02-20 18:00 | 26.31 | 34.5669 | N | 0
2025-02-20 | 19 | 2031-02-20 19:00 | 26.16 | 34.3698 | N | 0
2025-02-20 | 20 | 2031-02-20 20:00 | 25.9 | 34.0282 | N | 0
2025-02-20 | 21 | 2031-02-20 21:00 | 25.48 | 33.4764 | N | 0
2025-02-20 | 22 | 2031-02-20 22:00 | 24.63 | 32.3596 | N | 0
2025-02-20 | 23 | 2031-02-20 23:00 | 23.13 | 30.3889 | N | 0
2025-02-21 | 00 | 2031-02-21 | 21.26 | 27.932 | N | 0
2025-02-21 | 01 | 2031-02-21 01:00 | 19.75 | 25.9481 | N | 0
2025-02-21 | 02 | 2031-02-21 02:00 | 18.77 | 24.6606 | N | 0
2025-02-21 | 03 | 2031-02-21 03:00 | 18.27 | 24.0037 | N | 0
2025-02-21 | 04 | 2031-02-21 04:00 | 18.15 | 23.846 | N | 0
2025-02-21 | 05 | 2031-02-21 05:00 | 18.01 | 23.6621 | N | 0
2025-02-21 | 06 | 2031-02-21 06:00 | 18.81 | 24.7131 | N | 0
2025-02-21 | 07 | 2031-02-21 07:00 | 21.75 | 28.5758 | N | 0
2025-02-21 | 08 | 2031-02-21 08:00 | 23.41 | 30.7568 | N | 0
2025-02-21 | 09 | 2031-02-21 09:00 | 24.41 | 32.0706 | N | 0
2025-02-21 | 10 | 2031-02-21 10:00 | 24.78 | 32.5567 | N | 0
2025-02-21 | 11 | 2031-02-21 11:00 | 24.58 | 32.2939 | N | 0
2025-02-21 | 12 | 2031-02-21 12:00 | 24.05 | 31.5976 | N | 0
2025-02-21 | 13 | 2031-02-21 13:00 | 23.84 | 31.3217 | N | 0
2025-02-21 | 14 | 2031-02-21 14:00 | 23.82 | 31.2954 | N | 0
2025-02-21 | 15 | 2031-02-21 15:00 | 22.81 | 29.9685 | N | 0
2025-02-21 | 16 | 2031-02-21 16:00 | 22.78 | 29.929 | N | 0
2025-02-21 | 17 | 2031-02-21 17:00 | 23.49 | 30.8619 | N | 0
2025-02-21 | 18 | 2031-02-21 18:00 | 24.47 | 32.1494 | N | 0
2025-02-21 | 19 | 2031-02-21 19:00 | 24.86 | 32.6618 | N | 0
2025-02-21 | 20 | 2031-02-21 20:00 | 25.06 | 32.9246 | N | 0
2025-02-21 | 21 | 2031-02-21 21:00 | 24.37 | 32.018 | N | 0
2025-02-21 | 22 | 2031-02-21 22:00 | 23.86 | 31.348 | N | 0
2025-02-21 | 23 | 2031-02-21 23:00 | 22.64 | 29.7451 | N | 0
2025-02-22 | 00 | 2031-02-22 | 20.92 | 27.4853 | N | 0
2025-02-22 | 01 | 2031-02-22 01:00 | 19.46 | 25.5671 | N | 0
2025-02-22 | 02 | 2031-02-22 02:00 | 18.45 | 24.2402 | N | 0
2025-02-22 | 03 | 2031-02-22 03:00 | 17.77 | 23.3468 | N | 0
2025-02-22 | 04 | 2031-02-22 04:00 | 17.39 | 22.8475 | N | 0
2025-02-22 | 05 | 2031-02-22 05:00 | 17.42 | 22.8869 | N | 0
2025-02-22 | 06 | 2031-02-22 06:00 | 17.67 | 23.2154 | N | 0
2025-02-22 | 07 | 2031-02-22 07:00 | 18.42 | 24.2007 | N | 0
2025-02-22 | 08 | 2031-02-22 08:00 | 19.64 | 25.8036 | N | 0
2025-02-22 | 09 | 2031-02-22 09:00 | 21.01 | 27.6036 | N | 0
2025-02-22 | 10 | 2031-02-22 10:00 | 22.46 | 29.5086 | N | 0
2025-02-22 | 11 | 2031-02-22 11:00 | 23.01 | 30.2312 | N | 0
2025-02-22 | 12 | 2031-02-22 12:00 | 23.13 | 30.3889 | N | 0
2025-02-22 | 13 | 2031-02-22 13:00 | 23.37 | 30.7042 | N | 0
2025-02-22 | 14 | 2031-02-22 14:00 | 22.98 | 30.1918 | N | 0
2025-02-22 | 15 | 2031-02-22 15:00 | 22.6 | 29.6926 | N | 0
2025-02-22 | 16 | 2031-02-22 16:00 | 22.72 | 29.8502 | N | 0
2025-02-22 | 17 | 2031-02-22 17:00 | 23.59 | 30.9932 | N | 0
2025-02-22 | 18 | 2031-02-22 18:00 | 24.43 | 32.0969 | N | 0
2025-02-22 | 19 | 2031-02-22 19:00 | 24.87 | 32.6749 | N | 0
2025-02-22 | 20 | 2031-02-22 20:00 | 24.23 | 31.8341 | N | 0
2025-02-22 | 21 | 2031-02-22 21:00 | 23.39 | 30.7305 | N | 0
2025-02-22 | 22 | 2031-02-22 22:00 | 22.9 | 30.0867 | N | 0
2025-02-22 | 23 | 2031-02-22 23:00 | 21.25 | 27.9189 | N | 0
2025-02-23 | 00 | 2031-02-23 | 19.72 | 25.9087 | N | 0
2025-02-23 | 01 | 2031-02-23 01:00 | 18.06 | 23.7278 | N | 0
2025-02-23 | 02 | 2031-02-23 02:00 | 16.83 | 22.1118 | N | 0
2025-02-23 | 03 | 2031-02-23 03:00 | 16.35 | 21.4811 | N | 0
2025-02-23 | 04 | 2031-02-23 04:00 | 16.04 | 21.0738 | N | 0
2025-02-23 | 05 | 2031-02-23 05:00 | 15.64 | 20.5483 | N | 0
2025-02-23 | 06 | 2031-02-23 06:00 | 15.82 | 20.7848 | N | 0
2025-02-23 | 07 | 2031-02-23 07:00 | 16.54 | 21.7307 | N | 0
2025-02-23 | 08 | 2031-02-23 08:00 | 17.52 | 23.0183 | N | 0
2025-02-23 | 09 | 2031-02-23 09:00 | 18.88 | 24.8051 | N | 0
2025-02-23 | 10 | 2031-02-23 10:00 | 19.77 | 25.9744 | N | 0
2025-02-23 | 11 | 2031-02-23 11:00 | 20.44 | 26.8547 | N | 0
2025-02-23 | 12 | 2031-02-23 12:00 | 20.91 | 27.4722 | N | 0
2025-02-23 | 13 | 2031-02-23 13:00 | 21.4 | 28.116 | N | 0
2025-02-23 | 14 | 2031-02-23 14:00 | 22.07 | 28.9962 | N | 0
2025-02-23 | 15 | 2031-02-23 15:00 | 22.07 | 28.9962 | N | 0
2025-02-23 | 16 | 2031-02-23 16:00 | 22.25 | 29.2327 | N | 0
2025-02-23 | 17 | 2031-02-23 17:00 | 23.59 | 30.9932 | N | 0
2025-02-23 | 18 | 2031-02-23 18:00 | 24.55 | 32.2545 | N | 0
2025-02-23 | 19 | 2031-02-23 19:00 | 24.71 | 32.4647 | N | 0
2025-02-23 | 20 | 2031-02-23 20:00 | 24.04 | 31.5845 | N | 0
2025-02-23 | 21 | 2031-02-23 21:00 | 23.21 | 30.494 | N | 0
2025-02-23 | 22 | 2031-02-23 22:00 | 22 | 28.9043 | N | 0
2025-02-23 | 23 | 2031-02-23 23:00 | 20.45 | 26.8678 | N | 0
2025-02-24 | 00 | 2031-02-24 | 18.42 | 24.2007 | N | 0
2025-02-24 | 01 | 2031-02-24 01:00 | 16.71 | 21.9541 | N | 0
2025-02-24 | 02 | 2031-02-24 02:00 | 15.43 | 20.2724 | N | 0
2025-02-24 | 03 | 2031-02-24 03:00 | 14.92 | 19.6023 | N | 0
2025-02-24 | 04 | 2031-02-24 04:00 | 14.73 | 19.3527 | N | 0
2025-02-24 | 05 | 2031-02-24 05:00 | 14.9 | 19.5761 | N | 0
2025-02-24 | 06 | 2031-02-24 06:00 | 15.96 | 20.9687 | N | 0
2025-02-24 | 07 | 2031-02-24 07:00 | 17.94 | 23.5701 | N | 0
2025-02-24 | 08 | 2031-02-24 08:00 | 19.95 | 26.2109 | N | 0
2025-02-24 | 09 | 2031-02-24 09:00 | 20.74 | 27.2488 | N | 0
2025-02-24 | 10 | 2031-02-24 10:00 | 21.08 | 27.6955 | N | 0
2025-02-24 | 11 | 2031-02-24 11:00 | 21.24 | 27.9057 | N | 0
2025-02-24 | 12 | 2031-02-24 12:00 | 21.88 | 28.7466 | N | 0
2025-02-24 | 13 | 2031-02-24 13:00 | 21.81 | 28.6546 | N | 0
2025-02-24 | 14 | 2031-02-24 14:00 | 22.04 | 28.9568 | N | 0
2025-02-24 | 15 | 2031-02-24 15:00 | 21.27 | 27.9452 | N | 0
2025-02-24 | 16 | 2031-02-24 16:00 | 21.28 | 27.9583 | N | 0
2025-02-24 | 17 | 2031-02-24 17:00 | 22.22 | 29.1933 | N | 0
2025-02-24 | 18 | 2031-02-24 18:00 | 23.33 | 30.6516 | N | 0
2025-02-24 | 19 | 2031-02-24 19:00 | 23.53 | 30.9144 | N | 0
2025-02-24 | 20 | 2031-02-24 20:00 | 23.23 | 30.5203 | N | 0
2025-02-24 | 21 | 2031-02-24 21:00 | 22.63 | 29.732 | N | 0
2025-02-24 | 22 | 2031-02-24 22:00 | 21.92 | 28.7991 | N | 0
2025-02-24 | 23 | 2031-02-24 23:00 | 20.21 | 26.5525 | N | 0
2025-02-25 | 00 | 2031-02-25 | 18.07 | 23.7409 | N | 0
2025-02-25 | 01 | 2031-02-25 01:00 | 16.46 | 21.6256 | N | 0
2025-02-25 | 02 | 2031-02-25 02:00 | 15.44 | 20.2855 | N | 0
2025-02-25 | 03 | 2031-02-25 03:00 | 14.99 | 19.6943 | N | 0
2025-02-25 | 04 | 2031-02-25 04:00 | 14.71 | 19.3264 | N | 0
2025-02-25 | 05 | 2031-02-25 05:00 | 14.85 | 19.5104 | N | 0
2025-02-25 | 06 | 2031-02-25 06:00 | 15.9 | 20.8899 | N | 0
2025-02-25 | 07 | 2031-02-25 07:00 | 18.67 | 24.5292 | N | 0
2025-02-25 | 08 | 2031-02-25 08:00 | 20.28 | 26.6445 | N | 0
2025-02-25 | 09 | 2031-02-25 09:00 | 20.47 | 26.8941 | N | 0
2025-02-25 | 10 | 2031-02-25 10:00 | 20.75 | 27.262 | N | 0
2025-02-25 | 11 | 2031-02-25 11:00 | 20.99 | 27.5773 | N | 0
2025-02-25 | 12 | 2031-02-25 12:00 | 20.72 | 27.2226 | N | 0
2025-02-25 | 13 | 2031-02-25 13:00 | 20.37 | 26.7627 | N | 0
2025-02-25 | 14 | 2031-02-25 14:00 | 20.43 | 26.8415 | N | 0
2025-02-25 | 15 | 2031-02-25 15:00 | 21.12 | 27.7481 | N | 0
2025-02-25 | 16 | 2031-02-25 16:00 | 21.12 | 27.7481 | N | 0
2025-02-25 | 17 | 2031-02-25 17:00 | 21.71 | 28.5232 | N | 0
2025-02-25 | 18 | 2031-02-25 18:00 | 23.04 | 30.2706 | N | 0
2025-02-25 | 19 | 2031-02-25 19:00 | 23.4 | 30.7436 | N | 0
2025-02-25 | 20 | 2031-02-25 20:00 | 22.55 | 29.6269 | N | 0
2025-02-25 | 21 | 2031-02-25 21:00 | 22.05 | 28.9699 | N | 0
2025-02-25 | 22 | 2031-02-25 22:00 | 21.29 | 27.9714 | N | 0
2025-02-25 | 23 | 2031-02-25 23:00 | 19.64 | 25.8036 | N | 0
2025-02-26 | 00 | 2031-02-26 | 18 | 23.6489 | N | 0
2025-02-26 | 01 | 2031-02-26 01:00 | 16.42 | 21.5731 | N | 0
2025-02-26 | 02 | 2031-02-26 02:00 | 15.43 | 20.2724 | N | 0
2025-02-26 | 03 | 2031-02-26 03:00 | 14.9 | 19.5761 | N | 0
2025-02-26 | 04 | 2031-02-26 04:00 | 14.54 | 19.1031 | N | 0
2025-02-26 | 05 | 2031-02-26 05:00 | 14.69 | 19.3002 | N | 0
2025-02-26 | 06 | 2031-02-26 06:00 | 15.74 | 20.6797 | N | 0
2025-02-26 | 07 | 2031-02-26 07:00 | 18.19 | 23.8986 | N | 0
2025-02-26 | 08 | 2031-02-26 08:00 | 20.52 | 26.9598 | N | 0
2025-02-26 | 09 | 2031-02-26 09:00 | 20.15 | 26.4737 | N | 0
2025-02-26 | 10 | 2031-02-26 10:00 | 19.79 | 26.0007 | N | 0
2025-02-26 | 11 | 2031-02-26 11:00 | 19.43 | 25.5277 | N | 0
2025-02-26 | 12 | 2031-02-26 12:00 | 19.77 | 25.9744 | N | 0
2025-02-26 | 13 | 2031-02-26 13:00 | 19.95 | 26.2109 | N | 0
2025-02-26 | 14 | 2031-02-26 14:00 | 20.26 | 26.6182 | N | 0
2025-02-26 | 15 | 2031-02-26 15:00 | 20.16 | 26.4868 | N | 0
2025-02-26 | 16 | 2031-02-26 16:00 | 19.77 | 25.9744 | N | 0
2025-02-26 | 17 | 2031-02-26 17:00 | 20.87 | 27.4196 | N | 0
2025-02-26 | 18 | 2031-02-26 18:00 | 22.54 | 29.6137 | N | 0
2025-02-26 | 19 | 2031-02-26 19:00 | 22.69 | 29.8108 | N | 0
2025-02-26 | 20 | 2031-02-26 20:00 | 22.28 | 29.2721 | N | 0
2025-02-26 | 21 | 2031-02-26 21:00 | 22.08 | 29.0094 | N | 0
2025-02-26 | 22 | 2031-02-26 22:00 | 21.55 | 28.313 | N | 0
2025-02-26 | 23 | 2031-02-26 23:00 | 20.56 | 27.0123 | N | 0
2025-02-27 | 00 | 2031-02-27 | 17.99 | 23.6358 | N | 0
2025-02-27 | 01 | 2031-02-27 01:00 | 16.5 | 21.6782 | N | 0
2025-02-27 | 02 | 2031-02-27 02:00 | 15.35 | 20.1673 | N | 0
2025-02-27 | 03 | 2031-02-27 03:00 | 14.75 | 19.379 | N | 0
2025-02-27 | 04 | 2031-02-27 04:00 | 14.66 | 19.2607 | N | 0
2025-02-27 | 05 | 2031-02-27 05:00 | 14.78 | 19.4184 | N | 0
2025-02-27 | 06 | 2031-02-27 06:00 | 15.63 | 20.5352 | N | 0
2025-02-27 | 07 | 2031-02-27 07:00 | 18.17 | 23.8723 | N | 0
2025-02-27 | 08 | 2031-02-27 08:00 | 20.12 | 26.4343 | N | 0
2025-02-27 | 09 | 2031-02-27 09:00 | 20.37 | 26.7627 | N | 0
2025-02-27 | 10 | 2031-02-27 10:00 | 20.42 | 26.8284 | N | 0
2025-02-27 | 11 | 2031-02-27 11:00 | 20.42 | 26.8284 | N | 0
2025-02-27 | 12 | 2031-02-27 12:00 | 20.24 | 26.5919 | N | 0
2025-02-27 | 13 | 2031-02-27 13:00 | 19.87 | 26.1058 | N | 0
2025-02-27 | 14 | 2031-02-27 14:00 | 19.9 | 26.1452 | N | 0
2025-02-27 | 15 | 2031-02-27 15:00 | 19.9 | 26.1452 | N | 0
2025-02-27 | 16 | 2031-02-27 16:00 | 20.61 | 27.078 | N | 0
2025-02-27 | 17 | 2031-02-27 17:00 | 21.7 | 28.5101 | N | 0
2025-02-27 | 18 | 2031-02-27 18:00 | 22.35 | 29.3641 | N | 0
2025-02-27 | 19 | 2031-02-27 19:00 | 22.74 | 29.8765 | N | 0
2025-02-27 | 20 | 2031-02-27 20:00 | 22.25 | 29.2327 | N | 0
2025-02-27 | 21 | 2031-02-27 21:00 | 22.03 | 28.9437 | N | 0
2025-02-27 | 22 | 2031-02-27 22:00 | 21.15 | 27.7875 | N | 0
2025-02-27 | 23 | 2031-02-27 23:00 | 19.97 | 26.2372 | N | 0
2025-02-28 | 00 | 2031-02-28 | 17.91 | 23.5307 | N | 0
2025-02-28 | 01 | 2031-02-28 01:00 | 16.41 | 21.5599 | N | 0
2025-02-28 | 02 | 2031-02-28 02:00 | 15.8 | 20.7585 | N | 0
2025-02-28 | 03 | 2031-02-28 03:00 | 15.24 | 20.0228 | N | 0
2025-02-28 | 04 | 2031-02-28 04:00 | 14.97 | 19.668 | N | 0
2025-02-28 | 05 | 2031-02-28 05:00 | 15 | 19.7074 | N | 0
2025-02-28 | 06 | 2031-02-28 06:00 | 16.41 | 21.5599 | N | 0
2025-02-28 | 07 | 2031-02-28 07:00 | 18.36 | 24.1219 | N | 0
2025-02-28 | 08 | 2031-02-28 08:00 | 19.83 | 26.0532 | N | 0
2025-02-28 | 09 | 2031-02-28 09:00 | 20.17 | 26.4999 | N | 0
2025-02-28 | 10 | 2031-02-28 10:00 | 20.95 | 27.5247 | N | 0
2025-02-28 | 11 | 2031-02-28 11:00 | 21.52 | 28.2736 | N | 0
2025-02-28 | 12 | 2031-02-28 12:00 | 21.84 | 28.694 | N | 0
2025-02-28 | 13 | 2031-02-28 13:00 | 21.86 | 28.7203 | N | 0
2025-02-28 | 14 | 2031-02-28 14:00 | 21.96 | 28.8517 | N | 0
2025-02-28 | 15 | 2031-02-28 15:00 | 21.96 | 28.8517 | N | 0
2025-02-28 | 16 | 2031-02-28 16:00 | 22.4 | 29.4298 | N | 0
2025-02-28 | 17 | 2031-02-28 17:00 | 23.12 | 30.3757 | N | 0
2025-02-28 | 18 | 2031-02-28 18:00 | 23.82 | 31.2954 | N | 0
2025-02-28 | 19 | 2031-02-28 19:00 | 23.5 | 30.875 | N | 0
2025-02-28 | 20 | 2031-02-28 20:00 | 22.95 | 30.1524 | N | 0
2025-02-28 | 21 | 2031-02-28 21:00 | 22.48 | 29.5349 | N | 0
2025-02-28 | 22 | 2031-02-28 22:00 | 21.27 | 27.9452 | N | 0
2025-02-28 | 23 | 2031-02-28 23:00 | 20.3 | 26.6707 | N | 0
2025-03-01 | 00 | 2031-03-01 | 18.43 | 24.2139 | N | 0
2025-03-01 | 01 | 2031-03-01 01:00 | 16.96 | 22.2826 | N | 0
2025-03-01 | 02 | 2031-03-01 02:00 | 15.93 | 20.9293 | N | 0
2025-03-01 | 03 | 2031-03-01 03:00 | 15.03 | 19.7469 | N | 0
2025-03-01 | 04 | 2031-03-01 04:00 | 14.67 | 19.2739 | N | 0
2025-03-01 | 05 | 2031-03-01 05:00 | 14.74 | 19.3659 | N | 0
2025-03-01 | 06 | 2031-03-01 06:00 | 15.32 | 20.1279 | N | 0
2025-03-01 | 07 | 2031-03-01 07:00 | 16.38 | 21.5205 | N | 0
2025-03-01 | 08 | 2031-03-01 08:00 | 17.73 | 23.2942 | N | 0
2025-03-01 | 09 | 2031-03-01 09:00 | 19.65 | 25.8168 | N | 0
2025-03-01 | 10 | 2031-03-01 10:00 | 20.78 | 27.3014 | N | 0
2025-03-01 | 11 | 2031-03-01 11:00 | 21.48 | 28.2211 | N | 0
2025-03-01 | 12 | 2031-03-01 12:00 | 21.74 | 28.5627 | N | 0
2025-03-01 | 13 | 2031-03-01 13:00 | 22.1 | 29.0356 | N | 0
2025-03-01 | 14 | 2031-03-01 14:00 | 21.85 | 28.7072 | N | 0
2025-03-01 | 15 | 2031-03-01 15:00 | 21.64 | 28.4313 | N | 0
2025-03-01 | 16 | 2031-03-01 16:00 | 21.45 | 28.1816 | N | 0
2025-03-01 | 17 | 2031-03-01 17:00 | 22.56 | 29.64 | N | 0
2025-03-01 | 18 | 2031-03-01 18:00 | 24.33 | 31.9655 | N | 0
2025-03-01 | 19 | 2031-03-01 19:00 | 24.94 | 32.7669 | N | 0
2025-03-01 | 20 | 2031-03-01 20:00 | 24.65 | 32.3859 | N | 0
2025-03-01 | 21 | 2031-03-01 21:00 | 24.38 | 32.0312 | N | 0
2025-03-01 | 22 | 2031-03-01 22:00 | 23.06 | 30.2969 | N | 0
2025-03-01 | 23 | 2031-03-01 23:00 | 22.32 | 29.3247 | N | 0
2025-03-02 | 00 | 2031-03-02 | 20.85 | 27.3934 | N | 0
2025-03-02 | 01 | 2031-03-02 01:00 | 19.4 | 25.4883 | N | 0
2025-03-02 | 02 | 2031-03-02 02:00 | 18.58 | 24.411 | N | 0
2025-03-02 | 03 | 2031-03-02 03:00 | 17.89 | 23.5044 | N | 0
2025-03-02 | 04 | 2031-03-02 04:00 | 17.57 | 23.084 | N | 0
2025-03-02 | 05 | 2031-03-02 05:00 | 17.82 | 23.4124 | N | 0
2025-03-02 | 06 | 2031-03-02 06:00 | 17.96 | 23.5964 | N | 0
2025-03-02 | 07 | 2031-03-02 07:00 | 18.48 | 24.2796 | N | 0
2025-03-02 | 08 | 2031-03-02 08:00 | 19.24 | 25.2781 | N | 0
2025-03-02 | 09 | 2031-03-02 09:00 | 21.06 | 27.6693 | N | 0
2025-03-02 | 10 | 2031-03-02 10:00 | 22.15 | 29.1013 | N | 0
2025-03-02 | 11 | 2031-03-02 11:00 | 22.66 | 29.7714 | N | 0
2025-03-02 | 12 | 2031-03-02 12:00 | 22.83 | 29.9947 | N | 0
2025-03-02 | 13 | 2031-03-02 13:00 | 23.2 | 30.4809 | N | 0
2025-03-02 | 14 | 2031-03-02 14:00 | 23.03 | 30.2575 | N | 0
2025-03-02 | 15 | 2031-03-02 15:00 | 23.11 | 30.3626 | N | 0
2025-03-02 | 16 | 2031-03-02 16:00 | 23.5 | 30.875 | N | 0
2025-03-02 | 17 | 2031-03-02 17:00 | 24.89 | 32.7012 | N | 0
2025-03-02 | 18 | 2031-03-02 18:00 | 25.76 | 33.8443 | N | 0
2025-03-02 | 19 | 2031-03-02 19:00 | 25.81 | 33.9099 | N | 0
2025-03-02 | 20 | 2031-03-02 20:00 | 25.82 | 33.9231 | N | 0
2025-03-02 | 21 | 2031-03-02 21:00 | 24.71 | 32.4647 | N | 0
2025-03-02 | 22 | 2031-03-02 22:00 | 23.35 | 30.6779 | N | 0
2025-03-02 | 23 | 2031-03-02 23:00 | 22.38 | 29.4035 | N | 0
2025-03-03 | 00 | 2031-03-03 | 20.06 | 26.3554 | N | 0
2025-03-03 | 01 | 2031-03-03 01:00 | 18.62 | 24.4635 | N | 0
2025-03-03 | 02 | 2031-03-03 02:00 | 17.42 | 22.8869 | N | 0
2025-03-03 | 03 | 2031-03-03 03:00 | 16.79 | 22.0592 | N | 0
2025-03-03 | 04 | 2031-03-03 04:00 | 16.77 | 22.0329 | N | 0
2025-03-03 | 05 | 2031-03-03 05:00 | 17.19 | 22.5847 | N | 0
2025-03-03 | 06 | 2031-03-03 06:00 | 17.89 | 23.5044 | N | 0
2025-03-03 | 07 | 2031-03-03 07:00 | 20.03 | 26.316 | N | 0
2025-03-03 | 08 | 2031-03-03 08:00 | 21.96 | 28.8517 | N | 0
2025-03-03 | 09 | 2031-03-03 09:00 | 22.43 | 29.4692 | N | 0
2025-03-03 | 10 | 2031-03-03 10:00 | 22.03 | 28.9437 | N | 0
2025-03-03 | 11 | 2031-03-03 11:00 | 21.68 | 28.4838 | N | 0
2025-03-03 | 12 | 2031-03-03 12:00 | 21.68 | 28.4838 | N | 0
2025-03-03 | 13 | 2031-03-03 13:00 | 21.58 | 28.3524 | N | 0
2025-03-03 | 14 | 2031-03-03 14:00 | 21.44 | 28.1685 | N | 0
2025-03-03 | 15 | 2031-03-03 15:00 | 20.87 | 27.4196 | N | 0
2025-03-03 | 16 | 2031-03-03 16:00 | 21.85 | 28.7072 | N | 0
2025-03-03 | 17 | 2031-03-03 17:00 | 22.89 | 30.0736 | N | 0
2025-03-03 | 18 | 2031-03-03 18:00 | 23.67 | 31.0984 | N | 0
2025-03-03 | 19 | 2031-03-03 19:00 | 24.08 | 31.637 | N | 0
2025-03-03 | 20 | 2031-03-03 20:00 | 23.75 | 31.2035 | N | 0
2025-03-03 | 21 | 2031-03-03 21:00 | 23.14 | 30.402 | N | 0
2025-03-03 | 22 | 2031-03-03 22:00 | 22.23 | 29.2064 | N | 0
2025-03-03 | 23 | 2031-03-03 23:00 | 20.83 | 27.3671 | N | 0
2025-03-04 | 00 | 2031-03-04 | 18.63 | 24.4766 | N | 0
2025-03-04 | 01 | 2031-03-04 01:00 | 17 | 22.3351 | N | 0
2025-03-04 | 02 | 2031-03-04 02:00 | 15.87 | 20.8505 | N | 0
2025-03-04 | 03 | 2031-03-04 03:00 | 15.46 | 20.3118 | N | 0
2025-03-04 | 04 | 2031-03-04 04:00 | 15.04 | 19.76 | N | 0
2025-03-04 | 05 | 2031-03-04 05:00 | 15.33 | 20.141 | N | 0
2025-03-04 | 06 | 2031-03-04 06:00 | 16.27 | 21.376 | N | 0
2025-03-04 | 07 | 2031-03-04 07:00 | 18.05 | 23.7146 | N | 0
2025-03-04 | 08 | 2031-03-04 08:00 | 19.9 | 26.1452 | N | 0
2025-03-04 | 09 | 2031-03-04 09:00 | 20.48 | 26.9072 | N | 0
2025-03-04 | 10 | 2031-03-04 10:00 | 20.26 | 26.6182 | N | 0
2025-03-04 | 11 | 2031-03-04 11:00 | 20.84 | 27.3802 | N | 0
2025-03-04 | 12 | 2031-03-04 12:00 | 20.98 | 27.5641 | N | 0
2025-03-04 | 13 | 2031-03-04 13:00 | 21 | 27.5904 | N | 0
2025-03-04 | 14 | 2031-03-04 14:00 | 21.23 | 27.8926 | N | 0
2025-03-04 | 15 | 2031-03-04 15:00 | 21.33 | 28.024 | N | 0
2025-03-04 | 16 | 2031-03-04 16:00 | 21.11 | 27.7349 | N | 0
2025-03-04 | 17 | 2031-03-04 17:00 | 22.07 | 28.9962 | N | 0
2025-03-04 | 18 | 2031-03-04 18:00 | 23.55 | 30.9407 | N | 0
2025-03-04 | 19 | 2031-03-04 19:00 | 23.25 | 30.5465 | N | 0
2025-03-04 | 20 | 2031-03-04 20:00 | 22.61 | 29.7057 | N | 0
2025-03-04 | 21 | 2031-03-04 21:00 | 21.89 | 28.7597 | N | 0
2025-03-04 | 22 | 2031-03-04 22:00 | 21.37 | 28.0765 | N | 0
2025-03-04 | 23 | 2031-03-04 23:00 | 19.67 | 25.843 | N | 0
2025-03-05 | 00 | 2031-03-05 | 17.42 | 22.8869 | N | 0
2025-03-05 | 01 | 2031-03-05 01:00 | 16.15 | 21.2184 | N | 0
2025-03-05 | 02 | 2031-03-05 02:00 | 15.17 | 19.9308 | N | 0
2025-03-05 | 03 | 2031-03-05 03:00 | 14.64 | 19.2345 | N | 0
2025-03-05 | 04 | 2031-03-05 04:00 | 14.35 | 18.8535 | N | 0
2025-03-05 | 05 | 2031-03-05 05:00 | 14.39 | 18.906 | N | 0
2025-03-05 | 06 | 2031-03-05 06:00 | 15.1 | 19.8388 | N | 0
2025-03-05 | 07 | 2031-03-05 07:00 | 17.73 | 23.2942 | N | 0
2025-03-05 | 08 | 2031-03-05 08:00 | 19.53 | 25.6591 | N | 0
2025-03-05 | 09 | 2031-03-05 09:00 | 20.46 | 26.881 | N | 0
2025-03-05 | 10 | 2031-03-05 10:00 | 21.06 | 27.6693 | N | 0
2025-03-05 | 11 | 2031-03-05 11:00 | 21.85 | 28.7072 | N | 0
2025-03-05 | 12 | 2031-03-05 12:00 | 21.7 | 28.5101 | N | 0
2025-03-05 | 13 | 2031-03-05 13:00 | 21.32 | 28.0109 | N | 0
2025-03-05 | 14 | 2031-03-05 14:00 | 21.77 | 28.6021 | N | 0
2025-03-05 | 15 | 2031-03-05 15:00 | 21.12 | 27.7481 | N | 0
2025-03-05 | 16 | 2031-03-05 16:00 | 20.67 | 27.1569 | N | 0
2025-03-05 | 17 | 2031-03-05 17:00 | 21.37 | 28.0765 | N | 0
2025-03-05 | 18 | 2031-03-05 18:00 | 22.55 | 29.6269 | N | 0
2025-03-05 | 19 | 2031-03-05 19:00 | 22.32 | 29.3247 | N | 0
2025-03-05 | 20 | 2031-03-05 20:00 | 21.91 | 28.786 | N | 0
2025-03-05 | 21 | 2031-03-05 21:00 | 21.49 | 28.2342 | N | 0
2025-03-05 | 22 | 2031-03-05 22:00 | 20.81 | 27.3408 | N | 0
2025-03-05 | 23 | 2031-03-05 23:00 | 19.59 | 25.7379 | N | 0
2025-03-06 | 00 | 2031-03-06 | 17.19 | 22.5847 | N | 0
2025-03-06 | 01 | 2031-03-06 01:00 | 16.16 | 21.2315 | N | 0
2025-03-06 | 02 | 2031-03-06 02:00 | 15.2 | 19.9702 | N | 0
2025-03-06 | 03 | 2031-03-06 03:00 | 14.75 | 19.379 | N | 0
2025-03-06 | 04 | 2031-03-06 04:00 | 14.36 | 18.8666 | N | 0
2025-03-06 | 05 | 2031-03-06 05:00 | 14.6 | 19.1819 | N | 0
2025-03-06 | 06 | 2031-03-06 06:00 | 15.86 | 20.8373 | N | 0
2025-03-06 | 07 | 2031-03-06 07:00 | 17.45 | 22.9263 | N | 0
2025-03-06 | 08 | 2031-03-06 08:00 | 20.02 | 26.3029 | N | 0
2025-03-06 | 09 | 2031-03-06 09:00 | 20.44 | 26.8547 | N | 0
2025-03-06 | 10 | 2031-03-06 10:00 | 20.97 | 27.551 | N | 0
2025-03-06 | 11 | 2031-03-06 11:00 | 21.18 | 27.8269 | N | 0
2025-03-06 | 12 | 2031-03-06 12:00 | 21.75 | 28.5758 | N | 0
2025-03-06 | 13 | 2031-03-06 13:00 | 21.67 | 28.4707 | N | 0
2025-03-06 | 14 | 2031-03-06 14:00 | 22.07 | 28.9962 | N | 0
2025-03-06 | 15 | 2031-03-06 15:00 | 22.38 | 29.4035 | N | 0
2025-03-06 | 16 | 2031-03-06 16:00 | 22.85 | 30.021 | N | 0
2025-03-06 | 17 | 2031-03-06 17:00 | 23.08 | 30.3232 | N | 0
2025-03-06 | 18 | 2031-03-06 18:00 | 23.95 | 31.4662 | N | 0
2025-03-06 | 19 | 2031-03-06 19:00 | 23.94 | 31.4531 | N | 0
2025-03-06 | 20 | 2031-03-06 20:00 | 24.03 | 31.5713 | N | 0
2025-03-06 | 21 | 2031-03-06 21:00 | 23.15 | 30.4152 | N | 0
2025-03-06 | 22 | 2031-03-06 22:00 | 22.74 | 29.8765 | N | 0
2025-03-06 | 23 | 2031-03-06 23:00 | 21.04 | 27.643 | N | 0
2025-03-07 | 00 | 2031-03-07 | 19.11 | 25.1073 | N | 0
2025-03-07 | 01 | 2031-03-07 01:00 | 17.85 | 23.4519 | N | 0
2025-03-07 | 02 | 2031-03-07 02:00 | 16.57 | 21.7702 | N | 0
2025-03-07 | 03 | 2031-03-07 03:00 | 15.76 | 20.706 | N | 0
2025-03-07 | 04 | 2031-03-07 04:00 | 15.36 | 20.1804 | N | 0
2025-03-07 | 05 | 2031-03-07 05:00 | 15.57 | 20.4563 | N | 0
2025-03-07 | 06 | 2031-03-07 06:00 | 16.26 | 21.3629 | N | 0
2025-03-07 | 07 | 2031-03-07 07:00 | 18.69 | 24.5555 | N | 0
2025-03-07 | 08 | 2031-03-07 08:00 | 19.84 | 26.0664 | N | 0
2025-03-07 | 09 | 2031-03-07 09:00 | 20.4 | 26.8021 | N | 0
2025-03-07 | 10 | 2031-03-07 10:00 | 20.97 | 27.551 | N | 0
2025-03-07 | 11 | 2031-03-07 11:00 | 21.58 | 28.3524 | N | 0
2025-03-07 | 12 | 2031-03-07 12:00 | 21.47 | 28.2079 | N | 0
2025-03-07 | 13 | 2031-03-07 13:00 | 20.97 | 27.551 | N | 0
2025-03-07 | 14 | 2031-03-07 14:00 | 20.68 | 27.17 | N | 0
2025-03-07 | 15 | 2031-03-07 15:00 | 20.18 | 26.5131 | N | 0
2025-03-07 | 16 | 2031-03-07 16:00 | 19.91 | 26.1584 | N | 0
2025-03-07 | 17 | 2031-03-07 17:00 | 20.29 | 26.6576 | N | 0
2025-03-07 | 18 | 2031-03-07 18:00 | 21.71 | 28.5232 | N | 0
2025-03-07 | 19 | 2031-03-07 19:00 | 21.88 | 28.7466 | N | 0
2025-03-07 | 20 | 2031-03-07 20:00 | 22.06 | 28.9831 | N | 0
2025-03-07 | 21 | 2031-03-07 21:00 | 21.82 | 28.6678 | N | 0
2025-03-07 | 22 | 2031-03-07 22:00 | 20.85 | 27.3934 | N | 0
2025-03-07 | 23 | 2031-03-07 23:00 | 19.95 | 26.2109 | N | 0
2025-03-08 | 00 | 2031-03-08 | 18.24 | 23.9643 | N | 0
2025-03-08 | 01 | 2031-03-08 01:00 | 16.91 | 22.2169 | N | 0
2025-03-08 | 02 | 2031-03-08 02:00 | 16.14 | 21.2052 | N | 0
2025-03-08 | 03 | 2031-03-08 03:00 | 15.57 | 20.4563 | N | 0
2025-03-08 | 04 | 2031-03-08 04:00 | 15.23 | 20.0096 | N | 0
2025-03-08 | 05 | 2031-03-08 05:00 | 15.35 | 20.1673 | N | 0
2025-03-08 | 06 | 2031-03-08 06:00 | 15.51 | 20.3775 | N | 0
2025-03-08 | 07 | 2031-03-08 07:00 | 16.34 | 21.468 | N | 0
2025-03-08 | 08 | 2031-03-08 08:00 | 17.35 | 22.7949 | N | 0
2025-03-08 | 09 | 2031-03-08 09:00 | 18.26 | 23.9905 | N | 0
2025-03-08 | 10 | 2031-03-08 10:00 | 19.3 | 25.3569 | N | 0
2025-03-08 | 11 | 2031-03-08 11:00 | 19.64 | 25.8036 | N | 0
2025-03-08 | 12 | 2031-03-08 12:00 | 20.25 | 26.6051 | N | 0
2025-03-08 | 13 | 2031-03-08 13:00 | 20.21 | 26.5525 | N | 0
2025-03-08 | 14 | 2031-03-08 14:00 | 20.09 | 26.3948 | N | 0
2025-03-08 | 15 | 2031-03-08 15:00 | 19.74 | 25.935 | N | 0
2025-03-08 | 16 | 2031-03-08 16:00 | 19.69 | 25.8693 | N | 0
2025-03-08 | 17 | 2031-03-08 17:00 | 20.36 | 26.7496 | N | 0
2025-03-08 | 18 | 2031-03-08 18:00 | 21.82 | 28.6678 | N | 0
2025-03-08 | 19 | 2031-03-08 19:00 | 21.97 | 28.8648 | N | 0
2025-03-08 | 20 | 2031-03-08 20:00 | 21.91 | 28.786 | N | 0
2025-03-08 | 21 | 2031-03-08 21:00 | 21.54 | 28.2999 | N | 0
2025-03-08 | 22 | 2031-03-08 22:00 | 20.75 | 27.262 | N | 0
2025-03-08 | 23 | 2031-03-08 23:00 | 20.03 | 26.316 | N | 0
2025-03-09 | 00 | 2031-03-09 | 18.55 | 24.3715 | N | 0
2025-03-09 | 01 | 2031-03-09 01:00 | 16.98 | 22.3088 | N | 0
2025-03-09 | 02 | 2031-03-09 02:00 | 15.99 | 21.0081 | N | 0
2025-03-09 | 03 | 2031-03-09 03:00 | 15.39 | 20.2198 | N | 0
2025-03-09 | 04 | 2031-03-09 04:00 | 14.98 | 19.6812 | N | 0
2025-03-09 | 05 | 2031-03-09 05:00 | 14.97 | 19.668 | N | 0
2025-03-09 | 06 | 2031-03-09 06:00 | 15.07 | 19.7994 | N | 0
2025-03-09 | 07 | 2031-03-09 07:00 | 16.05 | 21.087 | N | 0
2025-03-09 | 08 | 2031-03-09 08:00 | 17.08 | 22.4402 | N | 0
2025-03-09 | 09 | 2031-03-09 09:00 | 17.43 | 22.9001 | N | 0
2025-03-09 | 10 | 2031-03-09 10:00 | 17.8 | 23.3862 | N | 0
2025-03-09 | 11 | 2031-03-09 11:00 | 18.98 | 24.9365 | N | 0
2025-03-09 | 12 | 2031-03-09 12:00 | 19.18 | 25.1993 | N | 0
2025-03-09 | 13 | 2031-03-09 13:00 | 19.15 | 25.1598 | N | 0
2025-03-09 | 14 | 2031-03-09 14:00 | 18.89 | 24.8182 | N | 0
2025-03-09 | 15 | 2031-03-09 15:00 | 19.72 | 25.9087 | N | 0
2025-03-09 | 16 | 2031-03-09 16:00 | 20.51 | 26.9466 | N | 0
2025-03-09 | 17 | 2031-03-09 17:00 | 20.95 | 27.5247 | N | 0
2025-03-09 | 18 | 2031-03-09 18:00 | 21.13 | 27.7612 | N | 0
2025-03-09 | 19 | 2031-03-09 19:00 | 21.89 | 28.7597 | N | 0
2025-03-09 | 20 | 2031-03-09 20:00 | 21.79 | 28.6284 | N | 0
2025-03-09 | 21 | 2031-03-09 21:00 | 20.78 | 27.3014 | N | 0
2025-03-09 | 22 | 2031-03-09 22:00 | 19.08 | 25.0679 | N | 0
2025-03-09 | 23 | 2031-03-09 23:00 | 17.43 | 22.9001 | N | 0
2025-03-10 | 00 | 2031-03-10 | 15.72 | 20.6534 | N | 0
2025-03-10 | 01 | 2031-03-10 01:00 | 14.46 | 18.998 | N | 0
2025-03-10 | 02 | 2031-03-10 02:00 | 13.75 | 18.0652 | N | 0
2025-03-10 | 03 | 2031-03-10 03:00 | 13.6 | 17.8681 | N | 0
2025-03-10 | 04 | 2031-03-10 04:00 | 13.67 | 17.9601 | N | 0
2025-03-10 | 05 | 2031-03-10 05:00 | 14.68 | 19.287 | N | 0
2025-03-10 | 06 | 2031-03-10 06:00 | 16.06 | 21.1001 | N | 0
2025-03-10 | 07 | 2031-03-10 07:00 | 17.76 | 23.3336 | N | 0
2025-03-10 | 08 | 2031-03-10 08:00 | 18.45 | 24.2402 | N | 0
2025-03-10 | 09 | 2031-03-10 09:00 | 18.43 | 24.2139 | N | 0
2025-03-10 | 10 | 2031-03-10 10:00 | 18.74 | 24.6212 | N | 0
2025-03-10 | 11 | 2031-03-10 11:00 | 18.58 | 24.411 | N | 0
2025-03-10 | 12 | 2031-03-10 12:00 | 18.62 | 24.4635 | N | 0
2025-03-10 | 13 | 2031-03-10 13:00 | 18.32 | 24.0694 | N | 0
2025-03-10 | 14 | 2031-03-10 14:00 | 18.37 | 24.1351 | N | 0
2025-03-10 | 15 | 2031-03-10 15:00 | 17.95 | 23.5832 | N | 0
2025-03-10 | 16 | 2031-03-10 16:00 | 18.33 | 24.0825 | N | 0
2025-03-10 | 17 | 2031-03-10 17:00 | 19.14 | 25.1467 | N | 0
2025-03-10 | 18 | 2031-03-10 18:00 | 19.35 | 25.4226 | N | 0
2025-03-10 | 19 | 2031-03-10 19:00 | 20.03 | 26.316 | N | 0
2025-03-10 | 20 | 2031-03-10 20:00 | 20.06 | 26.3554 | N | 0
2025-03-10 | 21 | 2031-03-10 21:00 | 19.75 | 25.9481 | N | 0
2025-03-10 | 22 | 2031-03-10 22:00 | 18.55 | 24.3715 | N | 0
2025-03-10 | 23 | 2031-03-10 23:00 | 16.85 | 22.138 | N | 0
2025-03-11 | 00 | 2031-03-11 | 15.25 | 20.0359 | N | 0
2025-03-11 | 01 | 2031-03-11 01:00 | 14.26 | 18.7352 | N | 0
2025-03-11 | 02 | 2031-03-11 02:00 | 13.87 | 18.2228 | N | 0
2025-03-11 | 03 | 2031-03-11 03:00 | 13.54 | 17.7893 | N | 0
2025-03-11 | 04 | 2031-03-11 04:00 | 13.87 | 18.2228 | N | 0
2025-03-11 | 05 | 2031-03-11 05:00 | 14.53 | 19.0899 | N | 0
2025-03-11 | 06 | 2031-03-11 06:00 | 16.33 | 21.4548 | N | 0
2025-03-11 | 07 | 2031-03-11 07:00 | 17.96 | 23.5964 | N | 0
2025-03-11 | 08 | 2031-03-11 08:00 | 18.23 | 23.9511 | N | 0
2025-03-11 | 09 | 2031-03-11 09:00 | 18.41 | 24.1876 | N | 0
2025-03-11 | 10 | 2031-03-11 10:00 | 18.89 | 24.8182 | N | 0
2025-03-11 | 11 | 2031-03-11 11:00 | 19.06 | 25.0416 | N | 0
2025-03-11 | 12 | 2031-03-11 12:00 | 18.82 | 24.7263 | N | 0
2025-03-11 | 13 | 2031-03-11 13:00 | 18.51 | 24.319 | N | 0
2025-03-11 | 14 | 2031-03-11 14:00 | 18.3 | 24.0431 | N | 0
2025-03-11 | 15 | 2031-03-11 15:00 | 18.44 | 24.227 | N | 0
2025-03-11 | 16 | 2031-03-11 16:00 | 18.96 | 24.9102 | N | 0
2025-03-11 | 17 | 2031-03-11 17:00 | 19.8 | 26.0138 | N | 0
2025-03-11 | 18 | 2031-03-11 18:00 | 19.87 | 26.1058 | N | 0
2025-03-11 | 19 | 2031-03-11 19:00 | 20.93 | 27.4985 | N | 0
2025-03-11 | 20 | 2031-03-11 20:00 | 21.19 | 27.8401 | N | 0
2025-03-11 | 21 | 2031-03-11 21:00 | 20.46 | 26.881 | N | 0
2025-03-11 | 22 | 2031-03-11 22:00 | 19.18 | 25.1993 | N | 0
2025-03-11 | 23 | 2031-03-11 23:00 | 17.25 | 22.6636 | N | 0
2025-03-12 | 00 | 2031-03-12 | 16.12 | 21.1789 | N | 0
2025-03-12 | 01 | 2031-03-12 01:00 | 15.15 | 19.9045 | N | 0
2025-03-12 | 02 | 2031-03-12 02:00 | 14.63 | 19.2213 | N | 0
2025-03-12 | 03 | 2031-03-12 03:00 | 14.52 | 19.0768 | N | 0
2025-03-12 | 04 | 2031-03-12 04:00 | 14.91 | 19.5892 | N | 0
2025-03-12 | 05 | 2031-03-12 05:00 | 15.67 | 20.5877 | N | 0
2025-03-12 | 06 | 2031-03-12 06:00 | 17.51 | 23.0052 | N | 0
2025-03-12 | 07 | 2031-03-12 07:00 | 19.05 | 25.0285 | N | 0
2025-03-12 | 08 | 2031-03-12 08:00 | 20.19 | 26.5262 | N | 0
2025-03-12 | 09 | 2031-03-12 09:00 | 20.51 | 26.9466 | N | 0
2025-03-12 | 10 | 2031-03-12 10:00 | 20.97 | 27.551 | N | 0
2025-03-12 | 11 | 2031-03-12 11:00 | 20.74 | 27.2488 | N | 0
2025-03-12 | 12 | 2031-03-12 12:00 | 21.11 | 27.7349 | N | 0
2025-03-12 | 13 | 2031-03-12 13:00 | 21.63 | 28.4181 | N | 0
2025-03-12 | 14 | 2031-03-12 14:00 | 21.64 | 28.4313 | N | 0
2025-03-12 | 15 | 2031-03-12 15:00 | 21.27 | 27.9452 | N | 0
2025-03-12 | 16 | 2031-03-12 16:00 | 21.76 | 28.5889 | N | 0
2025-03-12 | 17 | 2031-03-12 17:00 | 21.58 | 28.3524 | N | 0
2025-03-12 | 18 | 2031-03-12 18:00 | 22.16 | 29.1145 | N | 0
2025-03-12 | 19 | 2031-03-12 19:00 | 22.12 | 29.0619 | N | 0
2025-03-12 | 20 | 2031-03-12 20:00 | 22.1 | 29.0356 | N | 0
2025-03-12 | 21 | 2031-03-12 21:00 | 21.92 | 28.7991 | N | 0
2025-03-12 | 22 | 2031-03-12 22:00 | 20.53 | 26.9729 | N | 0
2025-03-12 | 23 | 2031-03-12 23:00 | 19.01 | 24.9759 | N | 0
2025-03-13 | 00 | 2031-03-13 | 17.09 | 22.4534 | N | 0
2025-03-13 | 01 | 2031-03-13 01:00 | 15.94 | 20.9424 | N | 0
2025-03-13 | 02 | 2031-03-13 02:00 | 15.28 | 20.0753 | N | 0
2025-03-13 | 03 | 2031-03-13 03:00 | 15.2 | 19.9702 | N | 0
2025-03-13 | 04 | 2031-03-13 04:00 | 15.25 | 20.0359 | N | 0
2025-03-13 | 05 | 2031-03-13 05:00 | 16.13 | 21.1921 | N | 0
2025-03-13 | 06 | 2031-03-13 06:00 | 17.78 | 23.3599 | N | 0
2025-03-13 | 07 | 2031-03-13 07:00 | 19.57 | 25.7116 | N | 0
2025-03-13 | 08 | 2031-03-13 08:00 | 20.05 | 26.3423 | N | 0
2025-03-13 | 09 | 2031-03-13 09:00 | 20.04 | 26.3291 | N | 0
2025-03-13 | 10 | 2031-03-13 10:00 | 19.54 | 25.6722 | N | 0
2025-03-13 | 11 | 2031-03-13 11:00 | 19.83 | 26.0532 | N | 0
2025-03-13 | 12 | 2031-03-13 12:00 | 19.91 | 26.1584 | N | 0
2025-03-13 | 13 | 2031-03-13 13:00 | 19.28 | 25.3306 | N | 0
2025-03-13 | 14 | 2031-03-13 14:00 | 18.81 | 24.7131 | N | 0
2025-03-13 | 15 | 2031-03-13 15:00 | 18.97 | 24.9234 | N | 0
2025-03-13 | 16 | 2031-03-13 16:00 | 19.5 | 25.6197 | N | 0
2025-03-13 | 17 | 2031-03-13 17:00 | 19.98 | 26.2503 | N | 0
2025-03-13 | 18 | 2031-03-13 18:00 | 19.96 | 26.224 | N | 0
2025-03-13 | 19 | 2031-03-13 19:00 | 20.48 | 26.9072 | N | 0
2025-03-13 | 20 | 2031-03-13 20:00 | 20.96 | 27.5379 | N | 0
2025-03-13 | 21 | 2031-03-13 21:00 | 20.76 | 27.2751 | N | 0
2025-03-13 | 22 | 2031-03-13 22:00 | 19.34 | 25.4095 | N | 0
2025-03-13 | 23 | 2031-03-13 23:00 | 17.6 | 23.1234 | N | 0
2025-03-14 | 00 | 2031-03-14 | 16.31 | 21.4286 | N | 0
2025-03-14 | 01 | 2031-03-14 01:00 | 15.45 | 20.2987 | N | 0
2025-03-14 | 02 | 2031-03-14 02:00 | 14.75 | 19.379 | N | 0
2025-03-14 | 03 | 2031-03-14 03:00 | 14.4 | 18.9191 | N | 0
2025-03-14 | 04 | 2031-03-14 04:00 | 14.44 | 18.9717 | N | 0
2025-03-14 | 05 | 2031-03-14 05:00 | 15.2 | 19.9702 | N | 0
2025-03-14 | 06 | 2031-03-14 06:00 | 17.04 | 22.3877 | N | 0
2025-03-14 | 07 | 2031-03-14 07:00 | 18.72 | 24.5949 | N | 0
2025-03-14 | 08 | 2031-03-14 08:00 | 19.34 | 25.4095 | N | 0
2025-03-14 | 09 | 2031-03-14 09:00 | 19.25 | 25.2912 | N | 0
2025-03-14 | 10 | 2031-03-14 10:00 | 19.21 | 25.2387 | N | 0
2025-03-14 | 11 | 2031-03-14 11:00 | 19.22 | 25.2518 | N | 0
2025-03-14 | 12 | 2031-03-14 12:00 | 19.11 | 25.1073 | N | 0
2025-03-14 | 13 | 2031-03-14 13:00 | 18.37 | 24.1351 | N | 0
2025-03-14 | 14 | 2031-03-14 14:00 | 18.11 | 23.7935 | N | 0
2025-03-14 | 15 | 2031-03-14 15:00 | 17.99 | 23.6358 | N | 0
2025-03-14 | 16 | 2031-03-14 16:00 | 18.13 | 23.8197 | N | 0
2025-03-14 | 17 | 2031-03-14 17:00 | 18.32 | 24.0694 | N | 0
2025-03-14 | 18 | 2031-03-14 18:00 | 18.42 | 24.2007 | N | 0
2025-03-14 | 19 | 2031-03-14 19:00 | 18.85 | 24.7657 | N | 0
2025-03-14 | 20 | 2031-03-14 20:00 | 19.21 | 25.2387 | N | 0
2025-03-14 | 21 | 2031-03-14 21:00 | 18.6 | 24.4372 | N | 0
2025-03-14 | 22 | 2031-03-14 22:00 | 17.59 | 23.1103 | N | 0
2025-03-14 | 23 | 2031-03-14 23:00 | 16.14 | 21.2052 | N | 0
2025-03-15 | 00 | 2031-03-15 | 14.95 | 19.6418 | N | 0
2025-03-15 | 01 | 2031-03-15 01:00 | 13.92 | 18.2885 | N | 0
2025-03-15 | 02 | 2031-03-15 02:00 | 13.15 | 17.2769 | N | 0
2025-03-15 | 03 | 2031-03-15 03:00 | 12.5 | 16.4229 | N | 0
2025-03-15 | 04 | 2031-03-15 04:00 | 12.55 | 16.4886 | N | 0
2025-03-15 | 05 | 2031-03-15 05:00 | 12.74 | 16.7382 | N | 0
2025-03-15 | 06 | 2031-03-15 06:00 | 13.47 | 17.6973 | N | 0
2025-03-15 | 07 | 2031-03-15 07:00 | 14.29 | 18.7746 | N | 0
2025-03-15 | 08 | 2031-03-15 08:00 | 15.69 | 20.614 | N | 0
2025-03-15 | 09 | 2031-03-15 09:00 | 17.19 | 22.5847 | N | 0
2025-03-15 | 10 | 2031-03-15 10:00 | 17.89 | 23.5044 | N | 0
2025-03-15 | 11 | 2031-03-15 11:00 | 18.49 | 24.2927 | N | 0
2025-03-15 | 12 | 2031-03-15 12:00 | 18.89 | 24.8182 | N | 0
2025-03-15 | 13 | 2031-03-15 13:00 | 19.12 | 25.1204 | N | 0
2025-03-15 | 14 | 2031-03-15 14:00 | 19.05 | 25.0285 | N | 0
2025-03-15 | 15 | 2031-03-15 15:00 | 17.84 | 23.4387 | N | 0
2025-03-15 | 16 | 2031-03-15 16:00 | 17.99 | 23.6358 | N | 0
2025-03-15 | 17 | 2031-03-15 17:00 | 18.55 | 24.3715 | N | 0
2025-03-15 | 18 | 2031-03-15 18:00 | 18.67 | 24.5292 | N | 0
2025-03-15 | 19 | 2031-03-15 19:00 | 18.56 | 24.3847 | N | 0
2025-03-15 | 20 | 2031-03-15 20:00 | 18.49 | 24.2927 | N | 0
2025-03-15 | 21 | 2031-03-15 21:00 | 17.9 | 23.5176 | N | 0
2025-03-15 | 22 | 2031-03-15 22:00 | 17.17 | 22.5585 | N | 0
2025-03-15 | 23 | 2031-03-15 23:00 | 15.65 | 20.5614 | N | 0
2025-03-16 | 00 | 2031-03-16 | 14.32 | 18.814 | N | 0
2025-03-16 | 01 | 2031-03-16 01:00 | 13.32 | 17.5002 | N | 0
2025-03-16 | 02 | 2031-03-16 02:00 | 12.55 | 16.4886 | N | 0
2025-03-16 | 03 | 2031-03-16 03:00 | 12.07 | 15.8579 | N | 0
2025-03-16 | 04 | 2031-03-16 04:00 | 11.9 | 15.6346 | N | 0
2025-03-16 | 05 | 2031-03-16 05:00 | 12.16 | 15.9762 | N | 0
2025-03-16 | 06 | 2031-03-16 06:00 | 12.27 | 16.1207 | N | 0
2025-03-16 | 07 | 2031-03-16 07:00 | 13.48 | 17.7104 | N | 0
2025-03-16 | 08 | 2031-03-16 08:00 | 14.88 | 19.5498 | N | 0
2025-03-16 | 09 | 2031-03-16 09:00 | 16.24 | 21.3366 | N | 0
2025-03-16 | 10 | 2031-03-16 10:00 | 17.24 | 22.6504 | N | 0
2025-03-16 | 11 | 2031-03-16 11:00 | 18.11 | 23.7935 | N | 0
2025-03-16 | 12 | 2031-03-16 12:00 | 18.79 | 24.6869 | N | 0
2025-03-16 | 13 | 2031-03-16 13:00 | 18.28 | 24.0168 | N | 0
2025-03-16 | 14 | 2031-03-16 14:00 | 18.36 | 24.1219 | N | 0
2025-03-16 | 15 | 2031-03-16 15:00 | 19.39 | 25.4752 | N | 0
2025-03-16 | 16 | 2031-03-16 16:00 | 20.89 | 27.4459 | N | 0
2025-03-16 | 17 | 2031-03-16 17:00 | 20.77 | 27.2882 | N | 0
2025-03-16 | 18 | 2031-03-16 18:00 | 20.33 | 26.7102 | N | 0
2025-03-16 | 19 | 2031-03-16 19:00 | 19.85 | 26.0795 | N | 0
2025-03-16 | 20 | 2031-03-16 20:00 | 19.86 | 26.0927 | N | 0
2025-03-16 | 21 | 2031-03-16 21:00 | 19.08 | 25.0679 | N | 0
2025-03-16 | 22 | 2031-03-16 22:00 | 17.55 | 23.0577 | N | 0
2025-03-16 | 23 | 2031-03-16 23:00 | 15.87 | 20.8505 | N | 0
2025-03-17 | 00 | 2031-03-17 | 14.07 | 18.4856 | N | 0
2025-03-17 | 01 | 2031-03-17 01:00 | 13.05 | 17.1455 | N | 0
2025-03-17 | 02 | 2031-03-17 02:00 | 12.7 | 16.6856 | N | 0
2025-03-17 | 03 | 2031-03-17 03:00 | 12.38 | 16.2652 | N | 0
2025-03-17 | 04 | 2031-03-17 04:00 | 12.83 | 16.8564 | N | 0
2025-03-17 | 05 | 2031-03-17 05:00 | 13.97 | 18.3542 | N | 0
2025-03-17 | 06 | 2031-03-17 06:00 | 16.21 | 21.2972 | N | 0
2025-03-17 | 07 | 2031-03-17 07:00 | 18.67 | 24.5292 | N | 0
2025-03-17 | 08 | 2031-03-17 08:00 | 19.23 | 25.2649 | N | 0
2025-03-17 | 09 | 2031-03-17 09:00 | 19.49 | 25.6065 | N | 0
2025-03-17 | 10 | 2031-03-17 10:00 | 19.45 | 25.554 | N | 0
2025-03-17 | 11 | 2031-03-17 11:00 | 19.64 | 25.8036 | N | 0
2025-03-17 | 12 | 2031-03-17 12:00 | 19.23 | 25.2649 | N | 0
2025-03-17 | 13 | 2031-03-17 13:00 | 19.23 | 25.2649 | N | 0
2025-03-17 | 14 | 2031-03-17 14:00 | 18.74 | 24.6212 | N | 0
2025-03-17 | 15 | 2031-03-17 15:00 | 18.6 | 24.4372 | N | 0
2025-03-17 | 16 | 2031-03-17 16:00 | 19.25 | 25.2912 | N | 0
2025-03-17 | 17 | 2031-03-17 17:00 | 20.32 | 26.697 | N | 0
2025-03-17 | 18 | 2031-03-17 18:00 | 20.32 | 26.697 | N | 0
2025-03-17 | 19 | 2031-03-17 19:00 | 20.35 | 26.7364 | N | 0
2025-03-17 | 20 | 2031-03-17 20:00 | 20.7 | 27.1963 | N | 0
2025-03-17 | 21 | 2031-03-17 21:00 | 20.05 | 26.3423 | N | 0
2025-03-17 | 22 | 2031-03-17 22:00 | 19.24 | 25.2781 | N | 0
2025-03-17 | 23 | 2031-03-17 23:00 | 17.36 | 22.8081 | N | 0
2025-03-18 | 00 | 2031-03-18 | 15.85 | 20.8242 | N | 0
2025-03-18 | 01 | 2031-03-18 01:00 | 14.85 | 19.5104 | N | 0
2025-03-18 | 02 | 2031-03-18 02:00 | 14.33 | 18.8272 | N | 0
2025-03-18 | 03 | 2031-03-18 03:00 | 14.04 | 18.4462 | N | 0
2025-03-18 | 04 | 2031-03-18 04:00 | 13.97 | 18.3542 | N | 0
2025-03-18 | 05 | 2031-03-18 05:00 | 14.88 | 19.5498 | N | 0
2025-03-18 | 06 | 2031-03-18 06:00 | 17.31 | 22.7424 | N | 0
2025-03-18 | 07 | 2031-03-18 07:00 | 19.01 | 24.9759 | N | 0
2025-03-18 | 08 | 2031-03-18 08:00 | 19.38 | 25.462 | N | 0
2025-03-18 | 09 | 2031-03-18 09:00 | 18.89 | 24.8182 | N | 0
2025-03-18 | 10 | 2031-03-18 10:00 | 19.05 | 25.0285 | N | 0
2025-03-18 | 11 | 2031-03-18 11:00 | 19.12 | 25.1204 | N | 0
2025-03-18 | 12 | 2031-03-18 12:00 | 18.69 | 24.5555 | N | 0
2025-03-18 | 13 | 2031-03-18 13:00 | 18.61 | 24.4504 | N | 0
2025-03-18 | 14 | 2031-03-18 14:00 | 18.02 | 23.6752 | N | 0
2025-03-18 | 15 | 2031-03-18 15:00 | 18.25 | 23.9774 | N | 0
2025-03-18 | 16 | 2031-03-18 16:00 | 18.46 | 24.2533 | N | 0
2025-03-18 | 17 | 2031-03-18 17:00 | 19.08 | 25.0679 | N | 0
2025-03-18 | 18 | 2031-03-18 18:00 | 19.16 | 25.173 | N | 0
2025-03-18 | 19 | 2031-03-18 19:00 | 19.68 | 25.8562 | N | 0
2025-03-18 | 20 | 2031-03-18 20:00 | 19.72 | 25.9087 | N | 0
2025-03-18 | 21 | 2031-03-18 21:00 | 19.14 | 25.1467 | N | 0
2025-03-18 | 22 | 2031-03-18 22:00 | 18.26 | 23.9905 | N | 0
2025-03-18 | 23 | 2031-03-18 23:00 | 16.27 | 21.376 | N | 0
2025-03-19 | 00 | 2031-03-19 | 14.8 | 19.4447 | N | 0
2025-03-19 | 01 | 2031-03-19 01:00 | 13.62 | 17.8944 | N | 0
2025-03-19 | 02 | 2031-03-19 02:00 | 13.14 | 17.2637 | N | 0
2025-03-19 | 03 | 2031-03-19 03:00 | 12.84 | 16.8696 | N | 0
2025-03-19 | 04 | 2031-03-19 04:00 | 13.23 | 17.382 | N | 0
2025-03-19 | 05 | 2031-03-19 05:00 | 13.99 | 18.3805 | N | 0
2025-03-19 | 06 | 2031-03-19 06:00 | 16.08 | 21.1264 | N | 0
2025-03-19 | 07 | 2031-03-19 07:00 | 18.15 | 23.846 | N | 0
2025-03-19 | 08 | 2031-03-19 08:00 | 18.74 | 24.6212 | N | 0
2025-03-19 | 09 | 2031-03-19 09:00 | 18.9 | 24.8314 | N | 0
2025-03-19 | 10 | 2031-03-19 10:00 | 18.88 | 24.8051 | N | 0
2025-03-19 | 11 | 2031-03-19 11:00 | 18.22 | 23.938 | N | 0
2025-03-19 | 12 | 2031-03-19 12:00 | 17.88 | 23.4913 | N | 0
2025-03-19 | 13 | 2031-03-19 13:00 | 17.77 | 23.3468 | N | 0
2025-03-19 | 14 | 2031-03-19 14:00 | 17.63 | 23.1628 | N | 0
2025-03-19 | 15 | 2031-03-19 15:00 | 17.54 | 23.0446 | N | 0
2025-03-19 | 16 | 2031-03-19 16:00 | 18.41 | 24.1876 | N | 0
2025-03-19 | 17 | 2031-03-19 17:00 | 18.42 | 24.2007 | N | 0
2025-03-19 | 18 | 2031-03-19 18:00 | 18.13 | 23.8197 | N | 0
2025-03-19 | 19 | 2031-03-19 19:00 | 18.61 | 24.4504 | N | 0
2025-03-19 | 20 | 2031-03-19 20:00 | 18.92 | 24.8577 | N | 0
2025-03-19 | 21 | 2031-03-19 21:00 | 18.56 | 24.3847 | N | 0
2025-03-19 | 22 | 2031-03-19 22:00 | 17.43 | 22.9001 | N | 0
2025-03-19 | 23 | 2031-03-19 23:00 | 15.42 | 20.2593 | N | 0
2025-03-20 | 00 | 2031-03-20 | 13.94 | 18.3148 | N | 0
2025-03-20 | 01 | 2031-03-20 01:00 | 12.87 | 16.909 | N | 0
2025-03-20 | 02 | 2031-03-20 02:00 | 12.35 | 16.2258 | N | 0
2025-03-20 | 03 | 2031-03-20 03:00 | 11.97 | 15.7265 | N | 0
2025-03-20 | 04 | 2031-03-20 04:00 | 11.93 | 15.674 | N | 0
2025-03-20 | 05 | 2031-03-20 05:00 | 12.73 | 16.7251 | N | 0
2025-03-20 | 06 | 2031-03-20 06:00 | 14.86 | 19.5235 | N | 0
2025-03-20 | 07 | 2031-03-20 07:00 | 17.04 | 22.3877 | N | 0
2025-03-20 | 08 | 2031-03-20 08:00 | 17.97 | 23.6095 | N | 0
2025-03-20 | 09 | 2031-03-20 09:00 | 18.26 | 23.9905 | N | 0
2025-03-20 | 10 | 2031-03-20 10:00 | 18.66 | 24.5161 | N | 0
2025-03-20 | 11 | 2031-03-20 11:00 | 19.01 | 24.9759 | N | 0
2025-03-20 | 12 | 2031-03-20 12:00 | 19 | 24.9628 | N | 0
2025-03-20 | 13 | 2031-03-20 13:00 | 19.4 | 25.4883 | N | 0
2025-03-20 | 14 | 2031-03-20 14:00 | 19.15 | 25.1598 | N | 0
2025-03-20 | 15 | 2031-03-20 15:00 | 19.26 | 25.3044 | N | 0
2025-03-20 | 16 | 2031-03-20 16:00 | 20.45 | 26.8678 | N | 0
2025-03-20 | 17 | 2031-03-20 17:00 | 21.22 | 27.8795 | N | 0
2025-03-20 | 18 | 2031-03-20 18:00 | 20.18 | 26.5131 | N | 0
2025-03-20 | 19 | 2031-03-20 19:00 | 20.82 | 27.3539 | N | 0
2025-03-20 | 20 | 2031-03-20 20:00 | 20.89 | 27.4459 | N | 0
2025-03-20 | 21 | 2031-03-20 21:00 | 21.01 | 27.6036 | N | 0
2025-03-20 | 22 | 2031-03-20 22:00 | 20.07 | 26.3686 | N | 0
2025-03-20 | 23 | 2031-03-20 23:00 | 17.82 | 23.4124 | N | 0
2025-03-21 | 00 | 2031-03-21 | 15.97 | 20.9819 | N | 0
2025-03-21 | 01 | 2031-03-21 01:00 | 14.92 | 19.6023 | N | 0
2025-03-21 | 02 | 2031-03-21 02:00 | 14.54 | 19.1031 | N | 0
2025-03-21 | 03 | 2031-03-21 03:00 | 14.06 | 18.4724 | N | 0
2025-03-21 | 04 | 2031-03-21 04:00 | 14.4 | 18.9191 | N | 0
2025-03-21 | 05 | 2031-03-21 05:00 | 14.96 | 19.6549 | N | 0
2025-03-21 | 06 | 2031-03-21 06:00 | 17.33 | 22.7687 | N | 0
2025-03-21 | 07 | 2031-03-21 07:00 | 19.65 | 25.8168 | N | 0
2025-03-21 | 08 | 2031-03-21 08:00 | 19.58 | 25.7248 | N | 0
2025-03-21 | 09 | 2031-03-21 09:00 | 19.68 | 25.8562 | N | 0
2025-03-21 | 10 | 2031-03-21 10:00 | 19.33 | 25.3963 | N | 0
2025-03-21 | 11 | 2031-03-21 11:00 | 18.97 | 24.9234 | N | 0
2025-03-21 | 12 | 2031-03-21 12:00 | 19.25 | 25.2912 | N | 0
2025-03-21 | 13 | 2031-03-21 13:00 | 19.02 | 24.989 | N | 0
2025-03-21 | 14 | 2031-03-21 14:00 | 18.75 | 24.6343 | N | 0
2025-03-21 | 15 | 2031-03-21 15:00 | 18.58 | 24.411 | N | 0
2025-03-21 | 16 | 2031-03-21 16:00 | 18.68 | 24.5423 | N | 0
2025-03-21 | 17 | 2031-03-21 17:00 | 19.11 | 25.1073 | N | 0
2025-03-21 | 18 | 2031-03-21 18:00 | 19.04 | 25.0153 | N | 0
2025-03-21 | 19 | 2031-03-21 19:00 | 19.37 | 25.4489 | N | 0
2025-03-21 | 20 | 2031-03-21 20:00 | 20 | 26.2766 | N | 0
2025-03-21 | 21 | 2031-03-21 21:00 | 19.63 | 25.7905 | N | 0
2025-03-21 | 22 | 2031-03-21 22:00 | 18.85 | 24.7657 | N | 0
2025-03-21 | 23 | 2031-03-21 23:00 | 16.98 | 22.3088 | N | 0
2025-03-22 | 00 | 2031-03-22 | 15.76 | 20.706 | N | 0
2025-03-22 | 01 | 2031-03-22 01:00 | 14.49 | 19.0374 | N | 0
2025-03-22 | 02 | 2031-03-22 02:00 | 13.46 | 17.6841 | N | 0
2025-03-22 | 03 | 2031-03-22 03:00 | 13.38 | 17.579 | N | 0
2025-03-22 | 04 | 2031-03-22 04:00 | 13.21 | 17.3557 | N | 0
2025-03-22 | 05 | 2031-03-22 05:00 | 13.52 | 17.763 | N | 0
2025-03-22 | 06 | 2031-03-22 06:00 | 13.91 | 18.2754 | N | 0
2025-03-22 | 07 | 2031-03-22 07:00 | 15.06 | 19.7863 | N | 0
2025-03-22 | 08 | 2031-03-22 08:00 | 16.74 | 21.9935 | N | 0
2025-03-22 | 09 | 2031-03-22 09:00 | 18.14 | 23.8329 | N | 0
2025-03-22 | 10 | 2031-03-22 10:00 | 19.45 | 25.554 | N | 0
2025-03-22 | 11 | 2031-03-22 11:00 | 20.42 | 26.8284 | N | 0
2025-03-22 | 12 | 2031-03-22 12:00 | 20.33 | 26.7102 | N | 0
2025-03-22 | 13 | 2031-03-22 13:00 | 20.37 | 26.7627 | N | 0
2025-03-22 | 14 | 2031-03-22 14:00 | 19.52 | 25.646 | N | 0
2025-03-22 | 15 | 2031-03-22 15:00 | 19.51 | 25.6328 | N | 0
2025-03-22 | 16 | 2031-03-22 16:00 | 20.4 | 26.8021 | N | 0
2025-03-22 | 17 | 2031-03-22 17:00 | 20.82 | 27.3539 | N | 0
2025-03-22 | 18 | 2031-03-22 18:00 | 20.95 | 27.5247 | N | 0
2025-03-22 | 19 | 2031-03-22 19:00 | 21.11 | 27.7349 | N | 0
2025-03-22 | 20 | 2031-03-22 20:00 | 21.58 | 28.3524 | N | 0
2025-03-22 | 21 | 2031-03-22 21:00 | 21 | 27.5904 | N | 0
2025-03-22 | 22 | 2031-03-22 22:00 | 19.78 | 25.9876 | N | 0
2025-03-22 | 23 | 2031-03-22 23:00 | 18.46 | 24.2533 | N | 0
2025-03-23 | 00 | 2031-03-23 | 16.9 | 22.2037 | N | 0
2025-03-23 | 01 | 2031-03-23 01:00 | 16.08 | 21.1264 | N | 0
2025-03-23 | 02 | 2031-03-23 02:00 | 15.52 | 20.3906 | N | 0
2025-03-23 | 03 | 2031-03-23 03:00 | 14.94 | 19.6286 | N | 0
2025-03-23 | 04 | 2031-03-23 04:00 | 15 | 19.7074 | N | 0
2025-03-23 | 05 | 2031-03-23 05:00 | 15.24 | 20.0228 | N | 0
2025-03-23 | 06 | 2031-03-23 06:00 | 15.72 | 20.6534 | N | 0
2025-03-23 | 07 | 2031-03-23 07:00 | 16.86 | 22.1512 | N | 0
2025-03-23 | 08 | 2031-03-23 08:00 | 17.82 | 23.4124 | N | 0
2025-03-23 | 09 | 2031-03-23 09:00 | 18.7 | 24.5686 | N | 0
2025-03-23 | 10 | 2031-03-23 10:00 | 19.21 | 25.2387 | N | 0
2025-03-23 | 11 | 2031-03-23 11:00 | 19.71 | 25.8956 | N | 0
2025-03-23 | 12 | 2031-03-23 12:00 | 20.02 | 26.3029 | N | 0
2025-03-23 | 13 | 2031-03-23 13:00 | 20.23 | 26.5788 | N | 0
2025-03-23 | 14 | 2031-03-23 14:00 | 19.97 | 26.2372 | N | 0
2025-03-23 | 15 | 2031-03-23 15:00 | 19.72 | 25.9087 | N | 0
2025-03-23 | 16 | 2031-03-23 16:00 | 21.04 | 27.643 | N | 0
2025-03-23 | 17 | 2031-03-23 17:00 | 22.44 | 29.4823 | N | 0
2025-03-23 | 18 | 2031-03-23 18:00 | 21.96 | 28.8517 | N | 0
2025-03-23 | 19 | 2031-03-23 19:00 | 22.63 | 29.732 | N | 0
2025-03-23 | 20 | 2031-03-23 20:00 | 22.56 | 29.64 | N | 0
2025-03-23 | 21 | 2031-03-23 21:00 | 21.69 | 28.497 | N | 0
2025-03-23 | 22 | 2031-03-23 22:00 | 19.93 | 26.1846 | N | 0
2025-03-23 | 23 | 2031-03-23 23:00 | 17.99 | 23.6358 | N | 0
2025-03-24 | 00 | 2031-03-24 | 16.45 | 21.6125 | N | 0
2025-03-24 | 01 | 2031-03-24 01:00 | 15.18 | 19.9439 | N | 0
2025-03-24 | 02 | 2031-03-24 02:00 | 14.5 | 19.0505 | N | 0
2025-03-24 | 03 | 2031-03-24 03:00 | 14.19 | 18.6432 | N | 0
2025-03-24 | 04 | 2031-03-24 04:00 | 14.44 | 18.9717 | N | 0
2025-03-24 | 05 | 2031-03-24 05:00 | 15.18 | 19.9439 | N | 0
2025-03-24 | 06 | 2031-03-24 06:00 | 16.91 | 22.2169 | N | 0
2025-03-24 | 07 | 2031-03-24 07:00 | 18.96 | 24.9102 | N | 0
2025-03-24 | 08 | 2031-03-24 08:00 | 19.24 | 25.2781 | N | 0
2025-03-24 | 09 | 2031-03-24 09:00 | 19.55 | 25.6854 | N | 0
2025-03-24 | 10 | 2031-03-24 10:00 | 19.81 | 26.027 | N | 0
2025-03-24 | 11 | 2031-03-24 11:00 | 20.41 | 26.8153 | N | 0
2025-03-24 | 12 | 2031-03-24 12:00 | 20.25 | 26.6051 | N | 0
2025-03-24 | 13 | 2031-03-24 13:00 | 20.38 | 26.7759 | N | 0
2025-03-24 | 14 | 2031-03-24 14:00 | 20.39 | 26.789 | N | 0
2025-03-24 | 15 | 2031-03-24 15:00 | 21.37 | 28.0765 | N | 0
2025-03-24 | 16 | 2031-03-24 16:00 | 22.16 | 29.1145 | N | 0
2025-03-24 | 17 | 2031-03-24 17:00 | 22.51 | 29.5743 | N | 0
2025-03-24 | 18 | 2031-03-24 18:00 | 22.08 | 29.0094 | N | 0
2025-03-24 | 19 | 2031-03-24 19:00 | 21.63 | 28.4181 | N | 0
2025-03-24 | 20 | 2031-03-24 20:00 | 21.49 | 28.2342 | N | 0
2025-03-24 | 21 | 2031-03-24 21:00 | 20.85 | 27.3934 | N | 0
2025-03-24 | 22 | 2031-03-24 22:00 | 19.61 | 25.7642 | N | 0
2025-03-24 | 23 | 2031-03-24 23:00 | 17.34 | 22.7818 | N | 0
2025-03-25 | 00 | 2031-03-25 | 15.68 | 20.6009 | N | 0
2025-03-25 | 01 | 2031-03-25 01:00 | 14.83 | 19.4841 | N | 0
2025-03-25 | 02 | 2031-03-25 02:00 | 14.21 | 18.6695 | N | 0
2025-03-25 | 03 | 2031-03-25 03:00 | 13.83 | 18.1703 | N | 0
2025-03-25 | 04 | 2031-03-25 04:00 | 14.03 | 18.433 | N | 0
2025-03-25 | 05 | 2031-03-25 05:00 | 14.8 | 19.4447 | N | 0
2025-03-25 | 06 | 2031-03-25 06:00 | 17.46 | 22.9395 | N | 0
2025-03-25 | 07 | 2031-03-25 07:00 | 18.93 | 24.8708 | N | 0
2025-03-25 | 08 | 2031-03-25 08:00 | 19.67 | 25.843 | N | 0
2025-03-25 | 09 | 2031-03-25 09:00 | 20.46 | 26.881 | N | 0
2025-03-25 | 10 | 2031-03-25 10:00 | 19.85 | 26.0795 | N | 0
2025-03-25 | 11 | 2031-03-25 11:00 | 20.2 | 26.5394 | N | 0
2025-03-25 | 12 | 2031-03-25 12:00 | 20.2 | 26.5394 | N | 0
2025-03-25 | 13 | 2031-03-25 13:00 | 20.44 | 26.8547 | N | 0
2025-03-25 | 14 | 2031-03-25 14:00 | 20.52 | 26.9598 | N | 0
2025-03-25 | 15 | 2031-03-25 15:00 | 20.56 | 27.0123 | N | 0
2025-03-25 | 16 | 2031-03-25 16:00 | 21.04 | 27.643 | N | 0
2025-03-25 | 17 | 2031-03-25 17:00 | 22.02 | 28.9305 | N | 0
2025-03-25 | 18 | 2031-03-25 18:00 | 21.56 | 28.3262 | N | 0
2025-03-25 | 19 | 2031-03-25 19:00 | 21.4 | 28.116 | N | 0
2025-03-25 | 20 | 2031-03-25 20:00 | 21.58 | 28.3524 | N | 0
2025-03-25 | 21 | 2031-03-25 21:00 | 20.93 | 27.4985 | N | 0
2025-03-25 | 22 | 2031-03-25 22:00 | 19.42 | 25.5146 | N | 0
2025-03-25 | 23 | 2031-03-25 23:00 | 17.54 | 23.0446 | N | 0
2025-03-26 | 00 | 2031-03-26 | 16.37 | 21.5074 | N | 0
2025-03-26 | 01 | 2031-03-26 01:00 | 14.99 | 19.6943 | N | 0
2025-03-26 | 02 | 2031-03-26 02:00 | 14.46 | 18.998 | N | 0
2025-03-26 | 03 | 2031-03-26 03:00 | 14.12 | 18.5513 | N | 0
2025-03-26 | 04 | 2031-03-26 04:00 | 14.52 | 19.0768 | N | 0
2025-03-26 | 05 | 2031-03-26 05:00 | 15.85 | 20.8242 | N | 0
2025-03-26 | 06 | 2031-03-26 06:00 | 18.2 | 23.9117 | N | 0
2025-03-26 | 07 | 2031-03-26 07:00 | 19.82 | 26.0401 | N | 0
2025-03-26 | 08 | 2031-03-26 08:00 | 20.74 | 27.2488 | N | 0
2025-03-26 | 09 | 2031-03-26 09:00 | 20.65 | 27.1306 | N | 0
2025-03-26 | 10 | 2031-03-26 10:00 | 20.14 | 26.4605 | N | 0
2025-03-26 | 11 | 2031-03-26 11:00 | 20.1 | 26.408 | N | 0
2025-03-26 | 12 | 2031-03-26 12:00 | 20.42 | 26.8284 | N | 0
2025-03-26 | 13 | 2031-03-26 13:00 | 20.38 | 26.7759 | N | 0
2025-03-26 | 14 | 2031-03-26 14:00 | 19.7 | 25.8824 | N | 0
2025-03-26 | 15 | 2031-03-26 15:00 | 19.89 | 26.1321 | N | 0
2025-03-26 | 16 | 2031-03-26 16:00 | 20.8 | 27.3277 | N | 0
2025-03-26 | 17 | 2031-03-26 17:00 | 20.95 | 27.5247 | N | 0
2025-03-26 | 18 | 2031-03-26 18:00 | 20.91 | 27.4722 | N | 0
2025-03-26 | 19 | 2031-03-26 19:00 | 20.74 | 27.2488 | N | 0
2025-03-26 | 20 | 2031-03-26 20:00 | 21.59 | 28.3656 | N | 0
2025-03-26 | 21 | 2031-03-26 21:00 | 21.59 | 28.3656 | N | 0
2025-03-26 | 22 | 2031-03-26 22:00 | 20.14 | 26.4605 | N | 0
2025-03-26 | 23 | 2031-03-26 23:00 | 18.47 | 24.2664 | N | 0
2025-03-27 | 00 | 2031-03-27 | 16.69 | 21.9278 | N | 0
2025-03-27 | 01 | 2031-03-27 01:00 | 15.77 | 20.7191 | N | 0
2025-03-27 | 02 | 2031-03-27 02:00 | 15.22 | 19.9965 | N | 0
2025-03-27 | 03 | 2031-03-27 03:00 | 14.75 | 19.379 | N | 0
2025-03-27 | 04 | 2031-03-27 04:00 | 15.25 | 20.0359 | N | 0
2025-03-27 | 05 | 2031-03-27 05:00 | 16.22 | 21.3103 | N | 0
2025-03-27 | 06 | 2031-03-27 06:00 | 18.86 | 24.7788 | N | 0
2025-03-27 | 07 | 2031-03-27 07:00 | 20.7 | 27.1963 | N | 0
2025-03-27 | 08 | 2031-03-27 08:00 | 20.55 | 26.9992 | N | 0
2025-03-27 | 09 | 2031-03-27 09:00 | 20.06 | 26.3554 | N | 0
2025-03-27 | 10 | 2031-03-27 10:00 | 20.05 | 26.3423 | N | 0
2025-03-27 | 11 | 2031-03-27 11:00 | 19.34 | 25.4095 | N | 0
2025-03-27 | 12 | 2031-03-27 12:00 | 19.49 | 25.6065 | N | 0
2025-03-27 | 13 | 2031-03-27 13:00 | 19.23 | 25.2649 | N | 0
2025-03-27 | 14 | 2031-03-27 14:00 | 19.48 | 25.5934 | N | 0
2025-03-27 | 15 | 2031-03-27 15:00 | 19.24 | 25.2781 | N | 0
2025-03-27 | 16 | 2031-03-27 16:00 | 19.41 | 25.5014 | N | 0
2025-03-27 | 17 | 2031-03-27 17:00 | 20.02 | 26.3029 | N | 0
2025-03-27 | 18 | 2031-03-27 18:00 | 20.04 | 26.3291 | N | 0
2025-03-27 | 19 | 2031-03-27 19:00 | 20.41 | 26.8153 | N | 0
2025-03-27 | 20 | 2031-03-27 20:00 | 21.14 | 27.7744 | N | 0
2025-03-27 | 21 | 2031-03-27 21:00 | 20.41 | 26.8153 | N | 0
2025-03-27 | 22 | 2031-03-27 22:00 | 19.14 | 25.1467 | N | 0
2025-03-27 | 23 | 2031-03-27 23:00 | 17.39 | 22.8475 | N | 0
2025-03-28 | 00 | 2031-03-28 | 15.45 | 20.2987 | N | 0
2025-03-28 | 01 | 2031-03-28 01:00 | 14.29 | 18.7746 | N | 0
2025-03-28 | 02 | 2031-03-28 02:00 | 13.96 | 18.3411 | N | 0
2025-03-28 | 03 | 2031-03-28 03:00 | 13.73 | 18.0389 | N | 0
2025-03-28 | 04 | 2031-03-28 04:00 | 13.92 | 18.2885 | N | 0
2025-03-28 | 05 | 2031-03-28 05:00 | 14.86 | 19.5235 | N | 0
2025-03-28 | 06 | 2031-03-28 06:00 | 17.18 | 22.5716 | N | 0
2025-03-28 | 07 | 2031-03-28 07:00 | 19.09 | 25.081 | N | 0
2025-03-28 | 08 | 2031-03-28 08:00 | 19.84 | 26.0664 | N | 0
2025-03-28 | 09 | 2031-03-28 09:00 | 19.74 | 25.935 | N | 0
2025-03-28 | 10 | 2031-03-28 10:00 | 20.76 | 27.2751 | N | 0
2025-03-28 | 11 | 2031-03-28 11:00 | 20.75 | 27.262 | N | 0
2025-03-28 | 12 | 2031-03-28 12:00 | 20.98 | 27.5641 | N | 0
2025-03-28 | 13 | 2031-03-28 13:00 | 20.62 | 27.0912 | N | 0
2025-03-28 | 14 | 2031-03-28 14:00 | 20.24 | 26.5919 | N | 0
2025-03-28 | 15 | 2031-03-28 15:00 | 20.34 | 26.7233 | N | 0
2025-03-28 | 16 | 2031-03-28 16:00 | 20.87 | 27.4196 | N | 0
2025-03-28 | 17 | 2031-03-28 17:00 | 21.6 | 28.3787 | N | 0
2025-03-28 | 18 | 2031-03-28 18:00 | 21.03 | 27.6298 | N | 0
2025-03-28 | 19 | 2031-03-28 19:00 | 20.9 | 27.459 | N | 0
2025-03-28 | 20 | 2031-03-28 20:00 | 20.98 | 27.5641 | N | 0
2025-03-28 | 21 | 2031-03-28 21:00 | 20.16 | 26.4868 | N | 0
2025-03-28 | 22 | 2031-03-28 22:00 | 19.18 | 25.1993 | N | 0
2025-03-28 | 23 | 2031-03-28 23:00 | 17.93 | 23.557 | N | 0
2025-03-29 | 00 | 2031-03-29 | 16.4 | 21.5468 | N | 0
2025-03-29 | 01 | 2031-03-29 01:00 | 15.15 | 19.9045 | N | 0
2025-03-29 | 02 | 2031-03-29 02:00 | 14.27 | 18.7484 | N | 0
2025-03-29 | 03 | 2031-03-29 03:00 | 13.92 | 18.2885 | N | 0
2025-03-29 | 04 | 2031-03-29 04:00 | 13.75 | 18.0652 | N | 0
2025-03-29 | 05 | 2031-03-29 05:00 | 13.85 | 18.1965 | N | 0
2025-03-29 | 06 | 2031-03-29 06:00 | 14.52 | 19.0768 | N | 0
2025-03-29 | 07 | 2031-03-29 07:00 | 16.03 | 21.0607 | N | 0
2025-03-29 | 08 | 2031-03-29 08:00 | 17.71 | 23.2679 | N | 0
2025-03-29 | 09 | 2031-03-29 09:00 | 18.93 | 24.8708 | N | 0
2025-03-29 | 10 | 2031-03-29 10:00 | 19.98 | 26.2503 | N | 0
2025-03-29 | 11 | 2031-03-29 11:00 | 20.97 | 27.551 | N | 0
2025-03-29 | 12 | 2031-03-29 12:00 | 21.59 | 28.3656 | N | 0
2025-03-29 | 13 | 2031-03-29 13:00 | 21.45 | 28.1816 | N | 0
2025-03-29 | 14 | 2031-03-29 14:00 | 21.32 | 28.0109 | N | 0
2025-03-29 | 15 | 2031-03-29 15:00 | 21.37 | 28.0765 | N | 0
2025-03-29 | 16 | 2031-03-29 16:00 | 21.89 | 28.7597 | N | 0
2025-03-29 | 17 | 2031-03-29 17:00 | 22.76 | 29.9028 | N | 0
2025-03-29 | 18 | 2031-03-29 18:00 | 22.33 | 29.3378 | N | 0
2025-03-29 | 19 | 2031-03-29 19:00 | 21.56 | 28.3262 | N | 0
2025-03-29 | 20 | 2031-03-29 20:00 | 21.42 | 28.1422 | N | 0
2025-03-29 | 21 | 2031-03-29 21:00 | 20.97 | 27.551 | N | 0
2025-03-29 | 22 | 2031-03-29 22:00 | 19.41 | 25.5014 | N | 0
2025-03-29 | 23 | 2031-03-29 23:00 | 18.14 | 23.8329 | N | 0
2025-03-30 | 00 | 2031-03-30 | 16.59 | 21.7964 | N | 0
2025-03-30 | 01 | 2031-03-30 01:00 | 15.6 | 20.4957 | N | 0
2025-03-30 | 02 | 2031-03-30 02:00 | 14.65 | 19.2476 | N | 0
2025-03-30 | 03 | 2031-03-30 03:00 | 14.29 | 18.7746 | N | 0
2025-03-30 | 04 | 2031-03-30 04:00 | 13.87 | 18.2228 | N | 0
2025-03-30 | 05 | 2031-03-30 05:00 | 14.21 | 18.6695 | N | 0
2025-03-30 | 06 | 2031-03-30 06:00 | 14.5 | 19.0505 | N | 0
2025-03-30 | 07 | 2031-03-30 07:00 | 15.73 | 20.6665 | N | 0
2025-03-30 | 08 | 2031-03-30 08:00 | 17.31 | 22.7424 | N | 0
2025-03-30 | 09 | 2031-03-30 09:00 | 18.51 | 24.319 | N | 0
2025-03-30 | 10 | 2031-03-30 10:00 | 20.16 | 26.4868 | N | 0
2025-03-30 | 11 | 2031-03-30 11:00 | 21.23 | 27.8926 | N | 0
2025-03-30 | 12 | 2031-03-30 12:00 | 21.92 | 28.7991 | N | 0
2025-03-30 | 13 | 2031-03-30 13:00 | 21.97 | 28.8648 | N | 0
2025-03-30 | 14 | 2031-03-30 14:00 | 21.69 | 28.497 | N | 0
2025-03-30 | 15 | 2031-03-30 15:00 | 21.85 | 28.7072 | N | 0
2025-03-30 | 16 | 2031-03-30 16:00 | 22.84 | 30.0079 | N | 0
2025-03-30 | 17 | 2031-03-30 17:00 | 23.36 | 30.6911 | N | 0
2025-03-30 | 18 | 2031-03-30 18:00 | 22.68 | 29.7977 | N | 0
2025-03-30 | 19 | 2031-03-30 19:00 | 21.68 | 28.4838 | N | 0
2025-03-30 | 20 | 2031-03-30 20:00 | 21.15 | 27.7875 | N | 0
2025-03-30 | 21 | 2031-03-30 21:00 | 20.61 | 27.078 | N | 0
2025-03-30 | 22 | 2031-03-30 22:00 | 19.19 | 25.2124 | N | 0
2025-03-30 | 23 | 2031-03-30 23:00 | 16.71 | 21.9541 | N | 0
2025-03-31 | 00 | 2031-03-31 | 15.2 | 19.9702 | N | 0
2025-03-31 | 01 | 2031-03-31 01:00 | 14.01 | 18.4068 | N | 0
2025-03-31 | 02 | 2031-03-31 02:00 | 13.06 | 17.1586 | N | 0
2025-03-31 | 03 | 2031-03-31 03:00 | 12.56 | 16.5017 | N | 0
2025-03-31 | 04 | 2031-03-31 04:00 | 12.58 | 16.528 | N | 0
2025-03-31 | 05 | 2031-03-31 05:00 | 13.57 | 17.8287 | N | 0
2025-03-31 | 06 | 2031-03-31 06:00 | 15.19 | 19.9571 | N | 0
2025-03-31 | 07 | 2031-03-31 07:00 | 16.79 | 22.0592 | N | 0
2025-03-31 | 08 | 2031-03-31 08:00 | 17.81 | 23.3993 | N | 0
2025-03-31 | 09 | 2031-03-31 09:00 | 18.49 | 24.2927 | N | 0
2025-03-31 | 10 | 2031-03-31 10:00 | 18.85 | 24.7657 | N | 0
2025-03-31 | 11 | 2031-03-31 11:00 | 19.3 | 25.3569 | N | 0
2025-03-31 | 12 | 2031-03-31 12:00 | 19.72 | 25.9087 | N | 0
2025-03-31 | 13 | 2031-03-31 13:00 | 19.32 | 25.3832 | N | 0
2025-03-31 | 14 | 2031-03-31 14:00 | 18.89 | 24.8182 | N | 0
2025-03-31 | 15 | 2031-03-31 15:00 | 19.68 | 25.8562 | N | 0
2025-03-31 | 16 | 2031-03-31 16:00 | 20.9 | 27.459 | N | 0
2025-03-31 | 17 | 2031-03-31 17:00 | 21.56 | 28.3262 | N | 0
2025-03-31 | 18 | 2031-03-31 18:00 | 21.35 | 28.0503 | N | 0
2025-03-31 | 19 | 2031-03-31 19:00 | 21.09 | 27.7087 | N | 0
2025-03-31 | 20 | 2031-03-31 20:00 | 21.37 | 28.0765 | N | 0
2025-03-31 | 21 | 2031-03-31 21:00 | 21.01 | 27.6036 | N | 0
2025-03-31 | 22 | 2031-03-31 22:00 | 19.75 | 25.9481 | N | 0
2025-03-31 | 23 | 2031-03-31 23:00 | 17.64 | 23.176 | N | 0
2025-04-01 | 00 | 2031-04-01 | 16.1 | 21.1527 | N | 0
2025-04-01 | 01 | 2031-04-01 01:00 | 14.85 | 19.5104 | N | 0
2025-04-01 | 02 | 2031-04-01 02:00 | 14.01 | 18.4068 | N | 0
2025-04-01 | 03 | 2031-04-01 03:00 | 13.69 | 17.9863 | N | 0
2025-04-01 | 04 | 2031-04-01 04:00 | 13.76 | 18.0783 | N | 0
2025-04-01 | 05 | 2031-04-01 05:00 | 15.01 | 19.7206 | N | 0
2025-04-01 | 06 | 2031-04-01 06:00 | 16.86 | 22.1512 | N | 0
2025-04-01 | 07 | 2031-04-01 07:00 | 19.04 | 25.0153 | N | 0
2025-04-01 | 08 | 2031-04-01 08:00 | 19.17 | 25.1861 | N | 0
2025-04-01 | 09 | 2031-04-01 09:00 | 19.13 | 25.1336 | N | 0
2025-04-01 | 10 | 2031-04-01 10:00 | 19.35 | 25.4226 | N | 0
2025-04-01 | 11 | 2031-04-01 11:00 | 19.55 | 25.6854 | N | 0
2025-04-01 | 12 | 2031-04-01 12:00 | 19.56 | 25.6985 | N | 0
2025-04-01 | 13 | 2031-04-01 13:00 | 19.47 | 25.5803 | N | 0
2025-04-01 | 14 | 2031-04-01 14:00 | 18.95 | 24.8971 | N | 0
2025-04-01 | 15 | 2031-04-01 15:00 | 18.78 | 24.6737 | N | 0
2025-04-01 | 16 | 2031-04-01 16:00 | 19.64 | 25.8036 | N | 0
2025-04-01 | 17 | 2031-04-01 17:00 | 20.4 | 26.8021 | N | 0
2025-04-01 | 18 | 2031-04-01 18:00 | 20.16 | 26.4868 | N | 0
2025-04-01 | 19 | 2031-04-01 19:00 | 20.52 | 26.9598 | N | 0
2025-04-01 | 20 | 2031-04-01 20:00 | 21.26 | 27.932 | N | 0
2025-04-01 | 21 | 2031-04-01 21:00 | 21.16 | 27.8006 | N | 0
2025-04-01 | 22 | 2031-04-01 22:00 | 19.54 | 25.6722 | N | 0
2025-04-01 | 23 | 2031-04-01 23:00 | 17.31 | 22.7424 | N | 0
2025-04-02 | 00 | 2031-04-02 | 15.89 | 20.8768 | N | 0
2025-04-02 | 01 | 2031-04-02 01:00 | 15.07 | 19.7994 | N | 0
2025-04-02 | 02 | 2031-04-02 02:00 | 14.5 | 19.0505 | N | 0
2025-04-02 | 03 | 2031-04-02 03:00 | 14.72 | 19.3396 | N | 0
2025-04-02 | 04 | 2031-04-02 04:00 | 14.66 | 19.2607 | N | 0
2025-04-02 | 05 | 2031-04-02 05:00 | 15.5 | 20.3644 | N | 0
2025-04-02 | 06 | 2031-04-02 06:00 | 17.65 | 23.1891 | N | 0
2025-04-02 | 07 | 2031-04-02 07:00 | 20.1 | 26.408 | N | 0
2025-04-02 | 08 | 2031-04-02 08:00 | 21.21 | 27.8663 | N | 0
2025-04-02 | 09 | 2031-04-02 09:00 | 21.7 | 28.5101 | N | 0
2025-04-02 | 10 | 2031-04-02 10:00 | 21.79 | 28.6284 | N | 0
2025-04-02 | 11 | 2031-04-02 11:00 | 22.33 | 29.3378 | N | 0
2025-04-02 | 12 | 2031-04-02 12:00 | 22.66 | 29.7714 | N | 0
2025-04-02 | 13 | 2031-04-02 13:00 | 22.52 | 29.5874 | N | 0
2025-04-02 | 14 | 2031-04-02 14:00 | 22.69 | 29.8108 | N | 0
2025-04-02 | 15 | 2031-04-02 15:00 | 23.01 | 30.2312 | N | 0
2025-04-02 | 16 | 2031-04-02 16:00 | 23.93 | 31.4399 | N | 0
2025-04-02 | 17 | 2031-04-02 17:00 | 24.71 | 32.4647 | N | 0
2025-04-02 | 18 | 2031-04-02 18:00 | 24.2 | 31.7947 | N | 0
2025-04-02 | 19 | 2031-04-02 19:00 | 23.7 | 31.1378 | N | 0
2025-04-02 | 20 | 2031-04-02 20:00 | 23.16 | 30.4283 | N | 0
2025-04-02 | 21 | 2031-04-02 21:00 | 22.15 | 29.1013 | N | 0
2025-04-02 | 22 | 2031-04-02 22:00 | 20.46 | 26.881 | N | 0
2025-04-02 | 23 | 2031-04-02 23:00 | 18.08 | 23.754 | N | 0
2025-04-03 | 00 | 2031-04-03 | 16.29 | 21.4023 | N | 0
2025-04-03 | 01 | 2031-04-03 01:00 | 15.11 | 19.852 | N | 0
2025-04-03 | 02 | 2031-04-03 02:00 | 14.18 | 18.6301 | N | 0
2025-04-03 | 03 | 2031-04-03 03:00 | 13.92 | 18.2885 | N | 0
2025-04-03 | 04 | 2031-04-03 04:00 | 13.93 | 18.3016 | N | 0
2025-04-03 | 05 | 2031-04-03 05:00 | 14.69 | 19.3002 | N | 0
2025-04-03 | 06 | 2031-04-03 06:00 | 16.7 | 21.941 | N | 0
2025-04-03 | 07 | 2031-04-03 07:00 | 19.13 | 25.1336 | N | 0
2025-04-03 | 08 | 2031-04-03 08:00 | 19.44 | 25.5409 | N | 0
2025-04-03 | 09 | 2031-04-03 09:00 | 19.48 | 25.5934 | N | 0
2025-04-03 | 10 | 2031-04-03 10:00 | 19.81 | 26.027 | N | 0
2025-04-03 | 11 | 2031-04-03 11:00 | 19.19 | 25.2124 | N | 0
2025-04-03 | 12 | 2031-04-03 12:00 | 18.69 | 24.5555 | N | 0
2025-04-03 | 13 | 2031-04-03 13:00 | 18.62 | 24.4635 | N | 0
2025-04-03 | 14 | 2031-04-03 14:00 | 18.11 | 23.7935 | N | 0
2025-04-03 | 15 | 2031-04-03 15:00 | 17.62 | 23.1497 | N | 0
2025-04-03 | 16 | 2031-04-03 16:00 | 18.18 | 23.8854 | N | 0
2025-04-03 | 17 | 2031-04-03 17:00 | 18.77 | 24.6606 | N | 0
2025-04-03 | 18 | 2031-04-03 18:00 | 19.07 | 25.0547 | N | 0
2025-04-03 | 19 | 2031-04-03 19:00 | 19.09 | 25.081 | N | 0
2025-04-03 | 20 | 2031-04-03 20:00 | 19.5 | 25.6197 | N | 0
2025-04-03 | 21 | 2031-04-03 21:00 | 19.01 | 24.9759 | N | 0
2025-04-03 | 22 | 2031-04-03 22:00 | 18.14 | 23.8329 | N | 0
2025-04-03 | 23 | 2031-04-03 23:00 | 16.43 | 21.5862 | N | 0
2025-04-04 | 00 | 2031-04-04 | 14.19 | 18.6432 | N | 0
2025-04-04 | 01 | 2031-04-04 01:00 | 13.22 | 17.3688 | N | 0
2025-04-04 | 02 | 2031-04-04 02:00 | 12.89 | 16.9353 | N | 0
2025-04-04 | 03 | 2031-04-04 03:00 | 12.52 | 16.4491 | N | 0
2025-04-04 | 04 | 2031-04-04 04:00 | 12.94 | 17.001 | N | 0
2025-04-04 | 05 | 2031-04-04 05:00 | 14.08 | 18.4987 | N | 0
2025-04-04 | 06 | 2031-04-04 06:00 | 16.05 | 21.087 | N | 0
2025-04-04 | 07 | 2031-04-04 07:00 | 17.94 | 23.5701 | N | 0
2025-04-04 | 08 | 2031-04-04 08:00 | 17.97 | 23.6095 | N | 0
2025-04-04 | 09 | 2031-04-04 09:00 | 18.12 | 23.8066 | N | 0
2025-04-04 | 10 | 2031-04-04 10:00 | 18.12 | 23.8066 | N | 0
2025-04-04 | 11 | 2031-04-04 11:00 | 17.77 | 23.3468 | N | 0
2025-04-04 | 12 | 2031-04-04 12:00 | 17.53 | 23.0314 | N | 0
2025-04-04 | 13 | 2031-04-04 13:00 | 17.37 | 22.8212 | N | 0
2025-04-04 | 14 | 2031-04-04 14:00 | 17.13 | 22.5059 | N | 0
2025-04-04 | 15 | 2031-04-04 15:00 | 17.16 | 22.5453 | N | 0
2025-04-04 | 16 | 2031-04-04 16:00 | 17.62 | 23.1497 | N | 0
2025-04-04 | 17 | 2031-04-04 17:00 | 18.73 | 24.608 | N | 0
2025-04-04 | 18 | 2031-04-04 18:00 | 18.57 | 24.3978 | N | 0
2025-04-04 | 19 | 2031-04-04 19:00 | 18.59 | 24.4241 | N | 0
2025-04-04 | 20 | 2031-04-04 20:00 | 19.06 | 25.0416 | N | 0
2025-04-04 | 21 | 2031-04-04 21:00 | 18.86 | 24.7788 | N | 0
2025-04-04 | 22 | 2031-04-04 22:00 | 17.87 | 23.4781 | N | 0
2025-04-04 | 23 | 2031-04-04 23:00 | 16.41 | 21.5599 | N | 0
2025-04-05 | 00 | 2031-04-05 | 14.91 | 19.5892 | N | 0
2025-04-05 | 01 | 2031-04-05 01:00 | 13.76 | 18.0783 | N | 0
2025-04-05 | 02 | 2031-04-05 02:00 | 13.02 | 17.1061 | N | 0
2025-04-05 | 03 | 2031-04-05 03:00 | 12.7 | 16.6856 | N | 0
2025-04-05 | 04 | 2031-04-05 04:00 | 12.44 | 16.344 | N | 0
2025-04-05 | 05 | 2031-04-05 05:00 | 12.77 | 16.7776 | N | 0
2025-04-05 | 06 | 2031-04-05 06:00 | 13.32 | 17.5002 | N | 0
2025-04-05 | 07 | 2031-04-05 07:00 | 14.83 | 19.4841 | N | 0
2025-04-05 | 08 | 2031-04-05 08:00 | 16.79 | 22.0592 | N | 0
2025-04-05 | 09 | 2031-04-05 09:00 | 18.03 | 23.6884 | N | 0
2025-04-05 | 10 | 2031-04-05 10:00 | 19.38 | 25.462 | N | 0
2025-04-05 | 11 | 2031-04-05 11:00 | 19.6 | 25.7511 | N | 0
2025-04-05 | 12 | 2031-04-05 12:00 | 19.62 | 25.7773 | N | 0
2025-04-05 | 13 | 2031-04-05 13:00 | 19.62 | 25.7773 | N | 0
2025-04-05 | 14 | 2031-04-05 14:00 | 19.15 | 25.1598 | N | 0
2025-04-05 | 15 | 2031-04-05 15:00 | 18.96 | 24.9102 | N | 0
2025-04-05 | 16 | 2031-04-05 16:00 | 19.66 | 25.8299 | N | 0
2025-04-05 | 17 | 2031-04-05 17:00 | 19.8 | 26.0138 | N | 0
2025-04-05 | 18 | 2031-04-05 18:00 | 19.91 | 26.1584 | N | 0
2025-04-05 | 19 | 2031-04-05 19:00 | 19.5 | 25.6197 | N | 0
2025-04-05 | 20 | 2031-04-05 20:00 | 19.3 | 25.3569 | N | 0
2025-04-05 | 21 | 2031-04-05 21:00 | 18.84 | 24.7526 | N | 0
2025-04-05 | 22 | 2031-04-05 22:00 | 17.68 | 23.2285 | N | 0
2025-04-05 | 23 | 2031-04-05 23:00 | 16.34 | 21.468 | N | 0
2025-04-06 | 00 | 2031-04-06 | 15.17 | 19.9308 | N | 0
2025-04-06 | 01 | 2031-04-06 01:00 | 13.73 | 18.0389 | N | 0
2025-04-06 | 02 | 2031-04-06 02:00 | 13.35 | 17.5396 | N | 0
2025-04-06 | 03 | 2031-04-06 03:00 | 12.98 | 17.0535 | N | 0
2025-04-06 | 04 | 2031-04-06 04:00 | 12.73 | 16.7251 | N | 0
2025-04-06 | 05 | 2031-04-06 05:00 | 13.05 | 17.1455 | N | 0
2025-04-06 | 06 | 2031-04-06 06:00 | 13.84 | 18.1834 | N | 0
2025-04-06 | 07 | 2031-04-06 07:00 | 14.78 | 19.4184 | N | 0
2025-04-06 | 08 | 2031-04-06 08:00 | 16.08 | 21.1264 | N | 0
2025-04-06 | 09 | 2031-04-06 09:00 | 17.27 | 22.6898 | N | 0
2025-04-06 | 10 | 2031-04-06 10:00 | 17.94 | 23.5701 | N | 0
2025-04-06 | 11 | 2031-04-06 11:00 | 18.56 | 24.3847 | N | 0
2025-04-06 | 12 | 2031-04-06 12:00 | 18.48 | 24.2796 | N | 0
2025-04-06 | 13 | 2031-04-06 13:00 | 18.4 | 24.1745 | N | 0
2025-04-06 | 14 | 2031-04-06 14:00 | 18.2 | 23.9117 | N | 0
2025-04-06 | 15 | 2031-04-06 15:00 | 18.63 | 24.4766 | N | 0
2025-04-06 | 16 | 2031-04-06 16:00 | 19.62 | 25.7773 | N | 0
2025-04-06 | 17 | 2031-04-06 17:00 | 20.32 | 26.697 | N | 0
2025-04-06 | 18 | 2031-04-06 18:00 | 20.54 | 26.9861 | N | 0
2025-04-06 | 19 | 2031-04-06 19:00 | 20.58 | 27.0386 | N | 0
2025-04-06 | 20 | 2031-04-06 20:00 | 20.64 | 27.1174 | N | 0
2025-04-06 | 21 | 2031-04-06 21:00 | 20.2 | 26.5394 | N | 0
2025-04-06 | 22 | 2031-04-06 22:00 | 19.04 | 25.0153 | N | 0
2025-04-06 | 23 | 2031-04-06 23:00 | 16.8 | 22.0723 | N | 0
2025-04-07 | 00 | 2031-04-07 | 15.13 | 19.8782 | N | 0
2025-04-07 | 01 | 2031-04-07 01:00 | 13.94 | 18.3148 | N | 0
2025-04-07 | 02 | 2031-04-07 02:00 | 13.39 | 17.5922 | N | 0
2025-04-07 | 03 | 2031-04-07 03:00 | 13.06 | 17.1586 | N | 0
2025-04-07 | 04 | 2031-04-07 04:00 | 13.5 | 17.7367 | N | 0
2025-04-07 | 05 | 2031-04-07 05:00 | 14.66 | 19.2607 | N | 0
2025-04-07 | 06 | 2031-04-07 06:00 | 16.87 | 22.1643 | N | 0
2025-04-07 | 07 | 2031-04-07 07:00 | 18.71 | 24.5818 | N | 0
2025-04-07 | 08 | 2031-04-07 08:00 | 18.71 | 24.5818 | N | 0
2025-04-07 | 09 | 2031-04-07 09:00 | 18.88 | 24.8051 | N | 0
2025-04-07 | 10 | 2031-04-07 10:00 | 18.83 | 24.7394 | N | 0
2025-04-07 | 11 | 2031-04-07 11:00 | 18.75 | 24.6343 | N | 0
2025-04-07 | 12 | 2031-04-07 12:00 | 18.85 | 24.7657 | N | 0
2025-04-07 | 13 | 2031-04-07 13:00 | 18.42 | 24.2007 | N | 0
2025-04-07 | 14 | 2031-04-07 14:00 | 18.2 | 23.9117 | N | 0
2025-04-07 | 15 | 2031-04-07 15:00 | 18.47 | 24.2664 | N | 0
2025-04-07 | 16 | 2031-04-07 16:00 | 19.67 | 25.843 | N | 0
2025-04-07 | 17 | 2031-04-07 17:00 | 21.02 | 27.6167 | N | 0
2025-04-07 | 18 | 2031-04-07 18:00 | 20.68 | 27.17 | N | 0
2025-04-07 | 19 | 2031-04-07 19:00 | 20.26 | 26.6182 | N | 0
2025-04-07 | 20 | 2031-04-07 20:00 | 20.75 | 27.262 | N | 0
2025-04-07 | 21 | 2031-04-07 21:00 | 20.28 | 26.6445 | N | 0
2025-04-07 | 22 | 2031-04-07 22:00 | 19.1 | 25.0941 | N | 0
2025-04-07 | 23 | 2031-04-07 23:00 | 17.39 | 22.8475 | N | 0
2025-04-08 | 00 | 2031-04-08 | 16.15 | 21.2184 | N | 0
2025-04-08 | 01 | 2031-04-08 01:00 | 15.22 | 19.9965 | N | 0
2025-04-08 | 02 | 2031-04-08 02:00 | 14.76 | 19.3921 | N | 0
2025-04-08 | 03 | 2031-04-08 03:00 | 14.45 | 18.9848 | N | 0
2025-04-08 | 04 | 2031-04-08 04:00 | 14.93 | 19.6155 | N | 0
2025-04-08 | 05 | 2031-04-08 05:00 | 15.92 | 20.9162 | N | 0
2025-04-08 | 06 | 2031-04-08 06:00 | 17.94 | 23.5701 | N | 0
2025-04-08 | 07 | 2031-04-08 07:00 | 20.74 | 27.2488 | N | 0
2025-04-08 | 08 | 2031-04-08 08:00 | 21.2 | 27.8532 | N | 0
2025-04-08 | 09 | 2031-04-08 09:00 | 21.68 | 28.4838 | N | 0
2025-04-08 | 10 | 2031-04-08 10:00 | 21.57 | 28.3393 | N | 0
2025-04-08 | 11 | 2031-04-08 11:00 | 21.59 | 28.3656 | N | 0
2025-04-08 | 12 | 2031-04-08 12:00 | 21.97 | 28.8648 | N | 0
2025-04-08 | 13 | 2031-04-08 13:00 | 21.29 | 27.9714 | N | 0
2025-04-08 | 14 | 2031-04-08 14:00 | 20.64 | 27.1174 | N | 0
2025-04-08 | 15 | 2031-04-08 15:00 | 20.52 | 26.9598 | N | 0
2025-04-08 | 16 | 2031-04-08 16:00 | 21.42 | 28.1422 | N | 0
2025-04-08 | 17 | 2031-04-08 17:00 | 22.37 | 29.3904 | N | 0
2025-04-08 | 18 | 2031-04-08 18:00 | 21.93 | 28.8123 | N | 0
2025-04-08 | 19 | 2031-04-08 19:00 | 22.63 | 29.732 | N | 0
2025-04-08 | 20 | 2031-04-08 20:00 | 23.12 | 30.3757 | N | 0
2025-04-08 | 21 | 2031-04-08 21:00 | 22.46 | 29.5086 | N | 0
2025-04-08 | 22 | 2031-04-08 22:00 | 20.7 | 27.1963 | N | 0
2025-04-08 | 23 | 2031-04-08 23:00 | 18.62 | 24.4635 | N | 0
2025-04-09 | 00 | 2031-04-09 | 17.19 | 22.5847 | N | 0
2025-04-09 | 01 | 2031-04-09 01:00 | 16.01 | 21.0344 | N | 0
2025-04-09 | 02 | 2031-04-09 02:00 | 15.45 | 20.2987 | N | 0
2025-04-09 | 03 | 2031-04-09 03:00 | 15.2 | 19.9702 | N | 0
2025-04-09 | 04 | 2031-04-09 04:00 | 15.36 | 20.1804 | N | 0
2025-04-09 | 05 | 2031-04-09 05:00 | 16.29 | 21.4023 | N | 0
2025-04-09 | 06 | 2031-04-09 06:00 | 19 | 24.9628 | N | 0
2025-04-09 | 07 | 2031-04-09 07:00 | 20.53 | 26.9729 | N | 0
2025-04-09 | 08 | 2031-04-09 08:00 | 20.68 | 27.17 | N | 0
2025-04-09 | 09 | 2031-04-09 09:00 | 19.94 | 26.1978 | N | 0
2025-04-09 | 10 | 2031-04-09 10:00 | 20 | 26.2766 | N | 0
2025-04-09 | 11 | 2031-04-09 11:00 | 20.22 | 26.5656 | N | 0
2025-04-09 | 12 | 2031-04-09 12:00 | 20.22 | 26.5656 | N | 0
2025-04-09 | 13 | 2031-04-09 13:00 | 20.49 | 26.9204 | N | 0
2025-04-09 | 14 | 2031-04-09 14:00 | 19.87 | 26.1058 | N | 0
2025-04-09 | 15 | 2031-04-09 15:00 | 19.49 | 25.6065 | N | 0
2025-04-09 | 16 | 2031-04-09 16:00 | 20.04 | 26.3291 | N | 0
2025-04-09 | 17 | 2031-04-09 17:00 | 20.77 | 27.2882 | N | 0
2025-04-09 | 18 | 2031-04-09 18:00 | 20.69 | 27.1831 | N | 0
2025-04-09 | 19 | 2031-04-09 19:00 | 20.95 | 27.5247 | N | 0
2025-04-09 | 20 | 2031-04-09 20:00 | 21.38 | 28.0897 | N | 0
2025-04-09 | 21 | 2031-04-09 21:00 | 21.1 | 27.7218 | N | 0
2025-04-09 | 22 | 2031-04-09 22:00 | 19.4 | 25.4883 | N | 0
2025-04-09 | 23 | 2031-04-09 23:00 | 17.52 | 23.0183 | N | 0
2025-04-10 | 00 | 2031-04-10 | 15.88 | 20.8636 | N | 0
2025-04-10 | 01 | 2031-04-10 01:00 | 15.08 | 19.8126 | N | 0
2025-04-10 | 02 | 2031-04-10 02:00 | 14.58 | 19.1556 | N | 0
2025-04-10 | 03 | 2031-04-10 03:00 | 14.3 | 18.7878 | N | 0
2025-04-10 | 04 | 2031-04-10 04:00 | 14.11 | 18.5381 | N | 0
2025-04-10 | 05 | 2031-04-10 05:00 | 15.51 | 20.3775 | N | 0
2025-04-10 | 06 | 2031-04-10 06:00 | 17.41 | 22.8738 | N | 0
2025-04-10 | 07 | 2031-04-10 07:00 | 19.57 | 25.7116 | N | 0
2025-04-10 | 08 | 2031-04-10 08:00 | 20.3 | 26.6707 | N | 0
2025-04-10 | 09 | 2031-04-10 09:00 | 20.6 | 27.0649 | N | 0
2025-04-10 | 10 | 2031-04-10 10:00 | 20.18 | 26.5131 | N | 0
2025-04-10 | 11 | 2031-04-10 11:00 | 20.3 | 26.6707 | N | 0
2025-04-10 | 12 | 2031-04-10 12:00 | 20.48 | 26.9072 | N | 0
2025-04-10 | 13 | 2031-04-10 13:00 | 20.03 | 26.316 | N | 0
2025-04-10 | 14 | 2031-04-10 14:00 | 20.12 | 26.4343 | N | 0
2025-04-10 | 15 | 2031-04-10 15:00 | 20.37 | 26.7627 | N | 0
2025-04-10 | 16 | 2031-04-10 16:00 | 21.46 | 28.1948 | N | 0
2025-04-10 | 17 | 2031-04-10 17:00 | 21.75 | 28.5758 | N | 0
2025-04-10 | 18 | 2031-04-10 18:00 | 21.56 | 28.3262 | N | 0
2025-04-10 | 19 | 2031-04-10 19:00 | 21.26 | 27.932 | N | 0
2025-04-10 | 20 | 2031-04-10 20:00 | 21.62 | 28.405 | N | 0
2025-04-10 | 21 | 2031-04-10 21:00 | 21.34 | 28.0371 | N | 0
2025-04-10 | 22 | 2031-04-10 22:00 | 20.29 | 26.6576 | N | 0
2025-04-10 | 23 | 2031-04-10 23:00 | 17.8 | 23.3862 | N | 0
2025-04-11 | 00 | 2031-04-11 | 15.86 | 20.8373 | N | 0
2025-04-11 | 01 | 2031-04-11 01:00 | 14.82 | 19.471 | N | 0
2025-04-11 | 02 | 2031-04-11 02:00 | 14.2 | 18.6564 | N | 0
2025-04-11 | 03 | 2031-04-11 03:00 | 13.95 | 18.3279 | N | 0
2025-04-11 | 04 | 2031-04-11 04:00 | 13.98 | 18.3673 | N | 0
2025-04-11 | 05 | 2031-04-11 05:00 | 14.61 | 19.1951 | N | 0
2025-04-11 | 06 | 2031-04-11 06:00 | 16.95 | 22.2694 | N | 0
2025-04-11 | 07 | 2031-04-11 07:00 | 18.51 | 24.319 | N | 0
2025-04-11 | 08 | 2031-04-11 08:00 | 19.75 | 25.9481 | N | 0
2025-04-11 | 09 | 2031-04-11 09:00 | 20.06 | 26.3554 | N | 0
2025-04-11 | 10 | 2031-04-11 10:00 | 20.35 | 26.7364 | N | 0
2025-04-11 | 11 | 2031-04-11 11:00 | 20.47 | 26.8941 | N | 0
2025-04-11 | 12 | 2031-04-11 12:00 | 20.93 | 27.4985 | N | 0
2025-04-11 | 13 | 2031-04-11 13:00 | 20.36 | 26.7496 | N | 0
2025-04-11 | 14 | 2031-04-11 14:00 | 20.27 | 26.6313 | N | 0
2025-04-11 | 15 | 2031-04-11 15:00 | 20.29 | 26.6576 | N | 0
2025-04-11 | 16 | 2031-04-11 16:00 | 20.44 | 26.8547 | N | 0
2025-04-11 | 17 | 2031-04-11 17:00 | 20.85 | 27.3934 | N | 0
2025-04-11 | 18 | 2031-04-11 18:00 | 20.31 | 26.6839 | N | 0
2025-04-11 | 19 | 2031-04-11 19:00 | 20.21 | 26.5525 | N | 0
2025-04-11 | 20 | 2031-04-11 20:00 | 20.24 | 26.5919 | N | 0
2025-04-11 | 21 | 2031-04-11 21:00 | 19.74 | 25.935 | N | 0
2025-04-11 | 22 | 2031-04-11 22:00 | 18.59 | 24.4241 | N | 0
2025-04-11 | 23 | 2031-04-11 23:00 | 17.03 | 22.3745 | N | 0
2025-04-12 | 00 | 2031-04-12 | 15.66 | 20.5746 | N | 0
2025-04-12 | 01 | 2031-04-12 01:00 | 14.57 | 19.1425 | N | 0
2025-04-12 | 02 | 2031-04-12 02:00 | 13.76 | 18.0783 | N | 0
2025-04-12 | 03 | 2031-04-12 03:00 | 13.24 | 17.3951 | N | 0
2025-04-12 | 04 | 2031-04-12 04:00 | 12.98 | 17.0535 | N | 0
2025-04-12 | 05 | 2031-04-12 05:00 | 13.38 | 17.579 | N | 0
2025-04-12 | 06 | 2031-04-12 06:00 | 13.94 | 18.3148 | N | 0
2025-04-12 | 07 | 2031-04-12 07:00 | 15.36 | 20.1804 | N | 0
2025-04-12 | 08 | 2031-04-12 08:00 | 16.9 | 22.2037 | N | 0
2025-04-12 | 09 | 2031-04-12 09:00 | 18.12 | 23.8066 | N | 0
2025-04-12 | 10 | 2031-04-12 10:00 | 18.65 | 24.5029 | N | 0
2025-04-12 | 11 | 2031-04-12 11:00 | 18.8 | 24.7 | N | 0
2025-04-12 | 12 | 2031-04-12 12:00 | 19.44 | 25.5409 | N | 0
2025-04-12 | 13 | 2031-04-12 13:00 | 18.8 | 24.7 | N | 0
2025-04-12 | 14 | 2031-04-12 14:00 | 18.6 | 24.4372 | N | 0
2025-04-12 | 15 | 2031-04-12 15:00 | 18.49 | 24.2927 | N | 0
2025-04-12 | 16 | 2031-04-12 16:00 | 18.61 | 24.4504 | N | 0
2025-04-12 | 17 | 2031-04-12 17:00 | 19.15 | 25.1598 | N | 0
2025-04-12 | 18 | 2031-04-12 18:00 | 19.23 | 25.2649 | N | 0
2025-04-12 | 19 | 2031-04-12 19:00 | 18.65 | 24.5029 | N | 0
2025-04-12 | 20 | 2031-04-12 20:00 | 18.88 | 24.8051 | N | 0
2025-04-12 | 21 | 2031-04-12 21:00 | 18.54 | 24.3584 | N | 0
2025-04-12 | 22 | 2031-04-12 22:00 | 17.54 | 23.0446 | N | 0
2025-04-12 | 23 | 2031-04-12 23:00 | 16.41 | 21.5599 | N | 0
2025-04-13 | 00 | 2031-04-13 | 15.02 | 19.7337 | N | 0
2025-04-13 | 01 | 2031-04-13 01:00 | 14.22 | 18.6827 | N | 0
2025-04-13 | 02 | 2031-04-13 02:00 | 13.43 | 17.6447 | N | 0
2025-04-13 | 03 | 2031-04-13 03:00 | 13.05 | 17.1455 | N | 0
2025-04-13 | 04 | 2031-04-13 04:00 | 13.1 | 17.2112 | N | 0
2025-04-13 | 05 | 2031-04-13 05:00 | 13.2 | 17.3426 | N | 0
2025-04-13 | 06 | 2031-04-13 06:00 | 13.72 | 18.0257 | N | 0
2025-04-13 | 07 | 2031-04-13 07:00 | 14.87 | 19.5366 | N | 0
2025-04-13 | 08 | 2031-04-13 08:00 | 15.79 | 20.7454 | N | 0
2025-04-13 | 09 | 2031-04-13 09:00 | 16.43 | 21.5862 | N | 0
2025-04-13 | 10 | 2031-04-13 10:00 | 16.9 | 22.2037 | N | 0
2025-04-13 | 11 | 2031-04-13 11:00 | 17.03 | 22.3745 | N | 0
2025-04-13 | 12 | 2031-04-13 12:00 | 17.37 | 22.8212 | N | 0
2025-04-13 | 13 | 2031-04-13 13:00 | 17.55 | 23.0577 | N | 0
2025-04-13 | 14 | 2031-04-13 14:00 | 17.17 | 22.5585 | N | 0
2025-04-13 | 15 | 2031-04-13 15:00 | 17.2 | 22.5979 | N | 0
2025-04-13 | 16 | 2031-04-13 16:00 | 18 | 23.6489 | N | 0
2025-04-13 | 17 | 2031-04-13 17:00 | 18.85 | 24.7657 | N | 0
2025-04-13 | 18 | 2031-04-13 18:00 | 18.91 | 24.8445 | N | 0
2025-04-13 | 19 | 2031-04-13 19:00 | 18.92 | 24.8577 | N | 0
2025-04-13 | 20 | 2031-04-13 20:00 | 19.52 | 25.646 | N | 0
2025-04-13 | 21 | 2031-04-13 21:00 | 18.99 | 24.9496 | N | 0
2025-04-13 | 22 | 2031-04-13 22:00 | 17.19 | 22.5847 | N | 0
2025-04-13 | 23 | 2031-04-13 23:00 | 15.46 | 20.3118 | N | 0
2025-04-14 | 00 | 2031-04-14 | 13.63 | 17.9075 | N | 0
2025-04-14 | 01 | 2031-04-14 01:00 | 12.64 | 16.6068 | N | 0
2025-04-14 | 02 | 2031-04-14 02:00 | 12.21 | 16.0419 | N | 0
2025-04-14 | 03 | 2031-04-14 03:00 | 11.89 | 15.6214 | N | 0
2025-04-14 | 04 | 2031-04-14 04:00 | 12.07 | 15.8579 | N | 0
2025-04-14 | 05 | 2031-04-14 05:00 | 13.1 | 17.2112 | N | 0
2025-04-14 | 06 | 2031-04-14 06:00 | 15.05 | 19.7731 | N | 0
2025-04-14 | 07 | 2031-04-14 07:00 | 17.23 | 22.6373 | N | 0
2025-04-14 | 08 | 2031-04-14 08:00 | 17.71 | 23.2679 | N | 0
2025-04-14 | 09 | 2031-04-14 09:00 | 18.1 | 23.7803 | N | 0
2025-04-14 | 10 | 2031-04-14 10:00 | 18.27 | 24.0037 | N | 0
2025-04-14 | 11 | 2031-04-14 11:00 | 17.91 | 23.5307 | N | 0
2025-04-14 | 12 | 2031-04-14 12:00 | 17.68 | 23.2285 | N | 0
2025-04-14 | 13 | 2031-04-14 13:00 | 17.62 | 23.1497 | N | 0
2025-04-14 | 14 | 2031-04-14 14:00 | 17.69 | 23.2416 | N | 0
2025-04-14 | 15 | 2031-04-14 15:00 | 17.56 | 23.0709 | N | 0
2025-04-14 | 16 | 2031-04-14 16:00 | 18.6 | 24.4372 | N | 0
2025-04-14 | 17 | 2031-04-14 17:00 | 19.13 | 25.1336 | N | 0
2025-04-14 | 18 | 2031-04-14 18:00 | 18.83 | 24.7394 | N | 0
2025-04-14 | 19 | 2031-04-14 19:00 | 18.25 | 23.9774 | N | 0
2025-04-14 | 20 | 2031-04-14 20:00 | 18.93 | 24.8708 | N | 0
2025-04-14 | 21 | 2031-04-14 21:00 | 18.51 | 24.319 | N | 0
2025-04-14 | 22 | 2031-04-14 22:00 | 16.86 | 22.1512 | N | 0
2025-04-14 | 23 | 2031-04-14 23:00 | 15.12 | 19.8651 | N | 0
2025-04-15 | 00 | 2031-04-15 | 13.69 | 17.9863 | N | 0
2025-04-15 | 01 | 2031-04-15 01:00 | 12.52 | 16.4491 | N | 0
2025-04-15 | 02 | 2031-04-15 02:00 | 12.08 | 15.8711 | N | 0
2025-04-15 | 03 | 2031-04-15 03:00 | 11.79 | 15.4901 | N | 0
2025-04-15 | 04 | 2031-04-15 04:00 | 11.94 | 15.6871 | N | 0
2025-04-15 | 05 | 2031-04-15 05:00 | 12.79 | 16.8039 | N | 0
2025-04-15 | 06 | 2031-04-15 06:00 | 14.65 | 19.2476 | N | 0
2025-04-15 | 07 | 2031-04-15 07:00 | 17.53 | 23.0314 | N | 0
2025-04-15 | 08 | 2031-04-15 08:00 | 17.92 | 23.5438 | N | 0
2025-04-15 | 09 | 2031-04-15 09:00 | 18.23 | 23.9511 | N | 0
2025-04-15 | 10 | 2031-04-15 10:00 | 18.79 | 24.6869 | N | 0
2025-04-15 | 11 | 2031-04-15 11:00 | 18.46 | 24.2533 | N | 0
2025-04-15 | 12 | 2031-04-15 12:00 | 18.16 | 23.8591 | N | 0
2025-04-15 | 13 | 2031-04-15 13:00 | 18.28 | 24.0168 | N | 0
2025-04-15 | 14 | 2031-04-15 14:00 | 18.02 | 23.6752 | N | 0
2025-04-15 | 15 | 2031-04-15 15:00 | 18.01 | 23.6621 | N | 0
2025-04-15 | 16 | 2031-04-15 16:00 | 19.2 | 25.2255 | N | 0
2025-04-15 | 17 | 2031-04-15 17:00 | 20.26 | 26.6182 | N | 0
2025-04-15 | 18 | 2031-04-15 18:00 | 20.22 | 26.5656 | N | 0
2025-04-15 | 19 | 2031-04-15 19:00 | 19.97 | 26.2372 | N | 0
2025-04-15 | 20 | 2031-04-15 20:00 | 20.49 | 26.9204 | N | 0
2025-04-15 | 21 | 2031-04-15 21:00 | 19.74 | 25.935 | N | 0
2025-04-15 | 22 | 2031-04-15 22:00 | 18.68 | 24.5423 | N | 0
2025-04-15 | 23 | 2031-04-15 23:00 | 16.68 | 21.9147 | N | 0
2025-04-16 | 00 | 2031-04-16 | 15.03 | 19.7469 | N | 0
2025-04-16 | 01 | 2031-04-16 01:00 | 13.99 | 18.3805 | N | 0
2025-04-16 | 02 | 2031-04-16 02:00 | 13.47 | 17.6973 | N | 0
2025-04-16 | 03 | 2031-04-16 03:00 | 13.28 | 17.4477 | N | 0
2025-04-16 | 04 | 2031-04-16 04:00 | 13.43 | 17.6447 | N | 0
2025-04-16 | 05 | 2031-04-16 05:00 | 14.4 | 18.9191 | N | 0
2025-04-16 | 06 | 2031-04-16 06:00 | 16.73 | 21.9804 | N | 0
2025-04-16 | 07 | 2031-04-16 07:00 | 18.94 | 24.8839 | N | 0
2025-04-16 | 08 | 2031-04-16 08:00 | 19.44 | 25.5409 | N | 0
2025-04-16 | 09 | 2031-04-16 09:00 | 20.15 | 26.4737 | N | 0
2025-04-16 | 10 | 2031-04-16 10:00 | 20.68 | 27.17 | N | 0
2025-04-16 | 11 | 2031-04-16 11:00 | 20.19 | 26.5262 | N | 0
2025-04-16 | 12 | 2031-04-16 12:00 | 20.97 | 27.551 | N | 0
2025-04-16 | 13 | 2031-04-16 13:00 | 20.62 | 27.0912 | N | 0
2025-04-16 | 14 | 2031-04-16 14:00 | 20.62 | 27.0912 | N | 0
2025-04-16 | 15 | 2031-04-16 15:00 | 20.4 | 26.8021 | N | 0
2025-04-16 | 16 | 2031-04-16 16:00 | 20.42 | 26.8284 | N | 0
2025-04-16 | 17 | 2031-04-16 17:00 | 20.42 | 26.8284 | N | 0
2025-04-16 | 18 | 2031-04-16 18:00 | 20.33 | 26.7102 | N | 0
2025-04-16 | 19 | 2031-04-16 19:00 | 20.07 | 26.3686 | N | 0
2025-04-16 | 20 | 2031-04-16 20:00 | 20.79 | 27.3145 | N | 0
2025-04-16 | 21 | 2031-04-16 21:00 | 20.24 | 26.5919 | N | 0
2025-04-16 | 22 | 2031-04-16 22:00 | 18.88 | 24.8051 | N | 0
2025-04-16 | 23 | 2031-04-16 23:00 | 17.15 | 22.5322 | N | 0
2025-04-17 | 00 | 2031-04-17 | 15.61 | 20.5089 | N | 0
2025-04-17 | 01 | 2031-04-17 01:00 | 14.47 | 19.0111 | N | 0
2025-04-17 | 02 | 2031-04-17 02:00 | 14.15 | 18.5907 | N | 0
2025-04-17 | 03 | 2031-04-17 03:00 | 13.91 | 18.2754 | N | 0
2025-04-17 | 04 | 2031-04-17 04:00 | 14.13 | 18.5644 | N | 0
2025-04-17 | 05 | 2031-04-17 05:00 | 15.05 | 19.7731 | N | 0
2025-04-17 | 06 | 2031-04-17 06:00 | 17.58 | 23.0971 | N | 0
2025-04-17 | 07 | 2031-04-17 07:00 | 18.82 | 24.7263 | N | 0
2025-04-17 | 08 | 2031-04-17 08:00 | 18.79 | 24.6869 | N | 0
2025-04-17 | 09 | 2031-04-17 09:00 | 19.18 | 25.1993 | N | 0
2025-04-17 | 10 | 2031-04-17 10:00 | 18.95 | 24.8971 | N | 0
2025-04-17 | 11 | 2031-04-17 11:00 | 18.59 | 24.4241 | N | 0
2025-04-17 | 12 | 2031-04-17 12:00 | 18.64 | 24.4898 | N | 0
2025-04-17 | 13 | 2031-04-17 13:00 | 18.19 | 23.8986 | N | 0
2025-04-17 | 14 | 2031-04-17 14:00 | 17.95 | 23.5832 | N | 0
2025-04-17 | 15 | 2031-04-17 15:00 | 17.98 | 23.6227 | N | 0
2025-04-17 | 16 | 2031-04-17 16:00 | 18.02 | 23.6752 | N | 0
2025-04-17 | 17 | 2031-04-17 17:00 | 17.92 | 23.5438 | N | 0
2025-04-17 | 18 | 2031-04-17 18:00 | 17.65 | 23.1891 | N | 0
2025-04-17 | 19 | 2031-04-17 19:00 | 18 | 23.6489 | N | 0
2025-04-17 | 20 | 2031-04-17 20:00 | 18.79 | 24.6869 | N | 0
2025-04-17 | 21 | 2031-04-17 21:00 | 18.62 | 24.4635 | N | 0
2025-04-17 | 22 | 2031-04-17 22:00 | 17.69 | 23.2416 | N | 0
2025-04-17 | 23 | 2031-04-17 23:00 | 16.31 | 21.4286 | N | 0
2025-04-18 | 00 | 2031-04-18 | 14.9 | 19.5761 | N | 0
2025-04-18 | 01 | 2031-04-18 01:00 | 13.77 | 18.0914 | N | 0
2025-04-18 | 02 | 2031-04-18 02:00 | 13.18 | 17.3163 | N | 0
2025-04-18 | 03 | 2031-04-18 03:00 | 12.81 | 16.8302 | N | 0
2025-04-18 | 04 | 2031-04-18 04:00 | 12.67 | 16.6462 | N | 0
2025-04-18 | 05 | 2031-04-18 05:00 | 13.02 | 17.1061 | N | 0
2025-04-18 | 06 | 2031-04-18 06:00 | 13.72 | 18.0257 | N | 0
2025-04-18 | 07 | 2031-04-18 07:00 | 15.24 | 20.0228 | N | 0
2025-04-18 | 08 | 2031-04-18 08:00 | 16.14 | 21.2052 | N | 0
2025-04-18 | 09 | 2031-04-18 09:00 | 17.06 | 22.4139 | N | 0
2025-04-18 | 10 | 2031-04-18 10:00 | 17.54 | 23.0446 | N | 0
2025-04-18 | 11 | 2031-04-18 11:00 | 18.92 | 24.8577 | N | 0
2025-04-18 | 12 | 2031-04-18 12:00 | 19.51 | 25.6328 | N | 0
2025-04-18 | 13 | 2031-04-18 13:00 | 19.42 | 25.5146 | N | 0
2025-04-18 | 14 | 2031-04-18 14:00 | 19.8 | 26.0138 | N | 0
2025-04-18 | 15 | 2031-04-18 15:00 | 18.82 | 24.7263 | N | 0
2025-04-18 | 16 | 2031-04-18 16:00 | 18.38 | 24.1482 | N | 0
2025-04-18 | 17 | 2031-04-18 17:00 | 18.29 | 24.0299 | N | 0
2025-04-18 | 18 | 2031-04-18 18:00 | 17.4 | 22.8606 | N | 0
2025-04-18 | 19 | 2031-04-18 19:00 | 17.15 | 22.5322 | N | 0
2025-04-18 | 20 | 2031-04-18 20:00 | 17.79 | 23.373 | N | 0
2025-04-18 | 21 | 2031-04-18 21:00 | 17.35 | 22.7949 | N | 0
2025-04-18 | 22 | 2031-04-18 22:00 | 16.03 | 21.0607 | N | 0
2025-04-18 | 23 | 2031-04-18 23:00 | 14.96 | 19.6549 | N | 0
2025-04-19 | 00 | 2031-04-19 | 13.54 | 17.7893 | N | 0
2025-04-19 | 01 | 2031-04-19 01:00 | 12.5 | 16.4229 | N | 0
2025-04-19 | 02 | 2031-04-19 02:00 | 11.87 | 15.5952 | N | 0
2025-04-19 | 03 | 2031-04-19 03:00 | 11.39 | 14.9645 | N | 0
2025-04-19 | 04 | 2031-04-19 04:00 | 11.11 | 14.5966 | N | 0
2025-04-19 | 05 | 2031-04-19 05:00 | 11.21 | 14.728 | N | 0
2025-04-19 | 06 | 2031-04-19 06:00 | 11.68 | 15.3455 | N | 0
2025-04-19 | 07 | 2031-04-19 07:00 | 12.94 | 17.001 | N | 0
2025-04-19 | 08 | 2031-04-19 08:00 | 14.5 | 19.0505 | N | 0
2025-04-19 | 09 | 2031-04-19 09:00 | 15.68 | 20.6009 | N | 0
2025-04-19 | 10 | 2031-04-19 10:00 | 16.35 | 21.4811 | N | 0
2025-04-19 | 11 | 2031-04-19 11:00 | 16.71 | 21.9541 | N | 0
2025-04-19 | 12 | 2031-04-19 12:00 | 16.9 | 22.2037 | N | 0
2025-04-19 | 13 | 2031-04-19 13:00 | 17 | 22.3351 | N | 0
2025-04-19 | 14 | 2031-04-19 14:00 | 16.72 | 21.9672 | N | 0
2025-04-19 | 15 | 2031-04-19 15:00 | 16.57 | 21.7702 | N | 0
2025-04-19 | 16 | 2031-04-19 16:00 | 16.93 | 22.2431 | N | 0
2025-04-19 | 17 | 2031-04-19 17:00 | 17.24 | 22.6504 | N | 0
2025-04-19 | 18 | 2031-04-19 18:00 | 16.65 | 21.8753 | N | 0
2025-04-19 | 19 | 2031-04-19 19:00 | 16.5 | 21.6782 | N | 0
2025-04-19 | 20 | 2031-04-19 20:00 | 16.92 | 22.23 | N | 0
2025-04-19 | 21 | 2031-04-19 21:00 | 16.77 | 22.0329 | N | 0
2025-04-19 | 22 | 2031-04-19 22:00 | 16.3 | 21.4154 | N | 0
2025-04-19 | 23 | 2031-04-19 23:00 | 15.28 | 20.0753 | N | 0
2025-04-20 | 00 | 2031-04-20 | 14.16 | 18.6038 | N | 0
2025-04-20 | 01 | 2031-04-20 01:00 | 12.69 | 16.6725 | N | 0
2025-04-20 | 02 | 2031-04-20 02:00 | 12.09 | 15.8842 | N | 0
2025-04-20 | 03 | 2031-04-20 03:00 | 11.76 | 15.4506 | N | 0
2025-04-20 | 04 | 2031-04-20 04:00 | 11.92 | 15.6609 | N | 0
2025-04-20 | 05 | 2031-04-20 05:00 | 12.24 | 16.0813 | N | 0
2025-04-20 | 06 | 2031-04-20 06:00 | 12.43 | 16.3309 | N | 0
2025-04-20 | 07 | 2031-04-20 07:00 | 13.88 | 18.236 | N | 0
2025-04-20 | 08 | 2031-04-20 08:00 | 15.11 | 19.852 | N | 0
2025-04-20 | 09 | 2031-04-20 09:00 | 16.09 | 21.1395 | N | 0
2025-04-20 | 10 | 2031-04-20 10:00 | 16.96 | 22.2826 | N | 0
2025-04-20 | 11 | 2031-04-20 11:00 | 17.26 | 22.6767 | N | 0
2025-04-20 | 12 | 2031-04-20 12:00 | 17.65 | 23.1891 | N | 0
2025-04-20 | 13 | 2031-04-20 13:00 | 17.64 | 23.176 | N | 0
2025-04-20 | 14 | 2031-04-20 14:00 | 17.03 | 22.3745 | N | 0
2025-04-20 | 15 | 2031-04-20 15:00 | 17.42 | 22.8869 | N | 0
2025-04-20 | 16 | 2031-04-20 16:00 | 17.51 | 23.0052 | N | 0
2025-04-20 | 17 | 2031-04-20 17:00 | 17.44 | 22.9132 | N | 0
2025-04-20 | 18 | 2031-04-20 18:00 | 16.8 | 22.0723 | N | 0
2025-04-20 | 19 | 2031-04-20 19:00 | 16.56 | 21.757 | N | 0
2025-04-20 | 20 | 2031-04-20 20:00 | 17.51 | 23.0052 | N | 0
2025-04-20 | 21 | 2031-04-20 21:00 | 17.6 | 23.1234 | N | 0
2025-04-20 | 22 | 2031-04-20 22:00 | 16.78 | 22.0461 | N | 0
2025-04-20 | 23 | 2031-04-20 23:00 | 15.57 | 20.4563 | N | 0
2025-04-21 | 00 | 2031-04-21 | 13.88 | 18.236 | N | 0
2025-04-21 | 01 | 2031-04-21 01:00 | 12.98 | 17.0535 | N | 0
2025-04-21 | 02 | 2031-04-21 02:00 | 12.29 | 16.147 | N | 0
2025-04-21 | 03 | 2031-04-21 03:00 | 11.95 | 15.7003 | N | 0
2025-04-21 | 04 | 2031-04-21 04:00 | 12.38 | 16.2652 | N | 0
2025-04-21 | 05 | 2031-04-21 05:00 | 12.83 | 16.8564 | N | 0
2025-04-21 | 06 | 2031-04-21 06:00 | 14.28 | 18.7615 | N | 0
2025-04-21 | 07 | 2031-04-21 07:00 | 16.03 | 21.0607 | N | 0
2025-04-21 | 08 | 2031-04-21 08:00 | 17.2 | 22.5979 | N | 0
2025-04-21 | 09 | 2031-04-21 09:00 | 18.66 | 24.5161 | N | 0
2025-04-21 | 10 | 2031-04-21 10:00 | 19.97 | 26.2372 | N | 0
2025-04-21 | 11 | 2031-04-21 11:00 | 20.62 | 27.0912 | N | 0
2025-04-21 | 12 | 2031-04-21 12:00 | 20.46 | 26.881 | N | 0
2025-04-21 | 13 | 2031-04-21 13:00 | 20.82 | 27.3539 | N | 0
2025-04-21 | 14 | 2031-04-21 14:00 | 20.48 | 26.9072 | N | 0
2025-04-21 | 15 | 2031-04-21 15:00 | 20.65 | 27.1306 | N | 0
2025-04-21 | 16 | 2031-04-21 16:00 | 21.1 | 27.7218 | N | 0
2025-04-21 | 17 | 2031-04-21 17:00 | 21.31 | 27.9977 | N | 0
2025-04-21 | 18 | 2031-04-21 18:00 | 20.02 | 26.3029 | N | 0
2025-04-21 | 19 | 2031-04-21 19:00 | 18.71 | 24.5818 | N | 0
2025-04-21 | 20 | 2031-04-21 20:00 | 19.52 | 25.646 | N | 0
2025-04-21 | 21 | 2031-04-21 21:00 | 19.17 | 25.1861 | N | 0
2025-04-21 | 22 | 2031-04-21 22:00 | 17.78 | 23.3599 | N | 0
2025-04-21 | 23 | 2031-04-21 23:00 | 15.67 | 20.5877 | N | 0
2025-04-22 | 00 | 2031-04-22 | 14.06 | 18.4724 | N | 0
2025-04-22 | 01 | 2031-04-22 01:00 | 12.89 | 16.9353 | N | 0
2025-04-22 | 02 | 2031-04-22 02:00 | 12.38 | 16.2652 | N | 0
2025-04-22 | 03 | 2031-04-22 03:00 | 11.89 | 15.6214 | N | 0
2025-04-22 | 04 | 2031-04-22 04:00 | 12.15 | 15.963 | N | 0
2025-04-22 | 05 | 2031-04-22 05:00 | 13.05 | 17.1455 | N | 0
2025-04-22 | 06 | 2031-04-22 06:00 | 15.01 | 19.7206 | N | 0
2025-04-22 | 07 | 2031-04-22 07:00 | 17.17 | 22.5585 | N | 0
2025-04-22 | 08 | 2031-04-22 08:00 | 18.23 | 23.9511 | N | 0
2025-04-22 | 09 | 2031-04-22 09:00 | 18.44 | 24.227 | N | 0
2025-04-22 | 10 | 2031-04-22 10:00 | 18.39 | 24.1613 | N | 0
2025-04-22 | 11 | 2031-04-22 11:00 | 18.24 | 23.9643 | N | 0
2025-04-22 | 12 | 2031-04-22 12:00 | 18.35 | 24.1088 | N | 0
2025-04-22 | 13 | 2031-04-22 13:00 | 17.93 | 23.557 | N | 0
2025-04-22 | 14 | 2031-04-22 14:00 | 17.76 | 23.3336 | N | 0
2025-04-22 | 15 | 2031-04-22 15:00 | 17.7 | 23.2548 | N | 0
2025-04-22 | 16 | 2031-04-22 16:00 | 18.07 | 23.7409 | N | 0
2025-04-22 | 17 | 2031-04-22 17:00 | 18.77 | 24.6606 | N | 0
2025-04-22 | 18 | 2031-04-22 18:00 | 18.54 | 24.3584 | N | 0
2025-04-22 | 19 | 2031-04-22 19:00 | 18.35 | 24.1088 | N | 0
2025-04-22 | 20 | 2031-04-22 20:00 | 18.68 | 24.5423 | N | 0
2025-04-22 | 21 | 2031-04-22 21:00 | 18.36 | 24.1219 | N | 0
2025-04-22 | 22 | 2031-04-22 22:00 | 17.19 | 22.5847 | N | 0
2025-04-22 | 23 | 2031-04-22 23:00 | 15.54 | 20.4169 | N | 0
2025-04-23 | 00 | 2031-04-23 | 14.06 | 18.4724 | N | 0
2025-04-23 | 01 | 2031-04-23 01:00 | 13.1 | 17.2112 | N | 0
2025-04-23 | 02 | 2031-04-23 02:00 | 12.56 | 16.5017 | N | 0
2025-04-23 | 03 | 2031-04-23 03:00 | 12.26 | 16.1076 | N | 0
2025-04-23 | 04 | 2031-04-23 04:00 | 12.4 | 16.2915 | N | 0
2025-04-23 | 05 | 2031-04-23 05:00 | 13.71 | 18.0126 | N | 0
2025-04-23 | 06 | 2031-04-23 06:00 | 15.41 | 20.2461 | N | 0
2025-04-23 | 07 | 2031-04-23 07:00 | 17.89 | 23.5044 | N | 0
2025-04-23 | 08 | 2031-04-23 08:00 | 17.72 | 23.2811 | N | 0
2025-04-23 | 09 | 2031-04-23 09:00 | 18.01 | 23.6621 | N | 0
2025-04-23 | 10 | 2031-04-23 10:00 | 17.95 | 23.5832 | N | 0
2025-04-23 | 11 | 2031-04-23 11:00 | 18 | 23.6489 | N | 0
2025-04-23 | 12 | 2031-04-23 12:00 | 17.84 | 23.4387 | N | 0
2025-04-23 | 13 | 2031-04-23 13:00 | 18.04 | 23.7015 | N | 0
2025-04-23 | 14 | 2031-04-23 14:00 | 17.52 | 23.0183 | N | 0
2025-04-23 | 15 | 2031-04-23 15:00 | 17.79 | 23.373 | N | 0
2025-04-23 | 16 | 2031-04-23 16:00 | 17.54 | 23.0446 | N | 0
2025-04-23 | 17 | 2031-04-23 17:00 | 18.21 | 23.9248 | N | 0
2025-04-23 | 18 | 2031-04-23 18:00 | 18.28 | 24.0168 | N | 0
2025-04-23 | 19 | 2031-04-23 19:00 | 18.19 | 23.8986 | N | 0
2025-04-23 | 20 | 2031-04-23 20:00 | 18.85 | 24.7657 | N | 0
2025-04-23 | 21 | 2031-04-23 21:00 | 18.85 | 24.7657 | N | 0
2025-04-23 | 22 | 2031-04-23 22:00 | 17.08 | 22.4402 | N | 0
2025-04-23 | 23 | 2031-04-23 23:00 | 15.42 | 20.2593 | N | 0
2025-04-24 | 00 | 2031-04-24 | 13.93 | 18.3016 | N | 0
2025-04-24 | 01 | 2031-04-24 01:00 | 12.68 | 16.6594 | N | 0
2025-04-24 | 02 | 2031-04-24 02:00 | 12.03 | 15.8054 | N | 0
2025-04-24 | 03 | 2031-04-24 03:00 | 11.73 | 15.4112 | N | 0
2025-04-24 | 04 | 2031-04-24 04:00 | 11.83 | 15.5426 | N | 0
2025-04-24 | 05 | 2031-04-24 05:00 | 12.63 | 16.5937 | N | 0
2025-04-24 | 06 | 2031-04-24 06:00 | 14.64 | 19.2345 | N | 0
2025-04-24 | 07 | 2031-04-24 07:00 | 16.71 | 21.9541 | N | 0
2025-04-24 | 08 | 2031-04-24 08:00 | 17 | 22.3351 | N | 0
2025-04-24 | 09 | 2031-04-24 09:00 | 17.22 | 22.6241 | N | 0
2025-04-24 | 10 | 2031-04-24 10:00 | 18.3 | 24.0431 | N | 0
2025-04-24 | 11 | 2031-04-24 11:00 | 17.91 | 23.5307 | N | 0
2025-04-24 | 12 | 2031-04-24 12:00 | 17.65 | 23.1891 | N | 0
2025-04-24 | 13 | 2031-04-24 13:00 | 17.5 | 22.992 | N | 0
2025-04-24 | 14 | 2031-04-24 14:00 | 17.19 | 22.5847 | N | 0
2025-04-24 | 15 | 2031-04-24 15:00 | 16.65 | 21.8753 | N | 0
2025-04-24 | 16 | 2031-04-24 16:00 | 17.05 | 22.4008 | N | 0
2025-04-24 | 17 | 2031-04-24 17:00 | 17.71 | 23.2679 | N | 0
2025-04-24 | 18 | 2031-04-24 18:00 | 17.85 | 23.4519 | N | 0
2025-04-24 | 19 | 2031-04-24 19:00 | 17.55 | 23.0577 | N | 0
2025-04-24 | 20 | 2031-04-24 20:00 | 17.87 | 23.4781 | N | 0
2025-04-24 | 21 | 2031-04-24 21:00 | 17.9 | 23.5176 | N | 0
2025-04-24 | 22 | 2031-04-24 22:00 | 16.69 | 21.9278 | N | 0
2025-04-24 | 23 | 2031-04-24 23:00 | 14.73 | 19.3527 | N | 0
2025-04-25 | 00 | 2031-04-25 | 13.38 | 17.579 | N | 0
2025-04-25 | 01 | 2031-04-25 01:00 | 12.2 | 16.0287 | N | 0
2025-04-25 | 02 | 2031-04-25 02:00 | 11.37 | 14.9382 | N | 0
2025-04-25 | 03 | 2031-04-25 03:00 | 11.04 | 14.5047 | N | 0
2025-04-25 | 04 | 2031-04-25 04:00 | 11.03 | 14.4915 | N | 0
2025-04-25 | 05 | 2031-04-25 05:00 | 12.01 | 15.7791 | N | 0
2025-04-25 | 06 | 2031-04-25 06:00 | 13.72 | 18.0257 | N | 0
2025-04-25 | 07 | 2031-04-25 07:00 | 15.59 | 20.4826 | N | 0
2025-04-25 | 08 | 2031-04-25 08:00 | 16.21 | 21.2972 | N | 0
2025-04-25 | 09 | 2031-04-25 09:00 | 16.46 | 21.6256 | N | 0
2025-04-25 | 10 | 2031-04-25 10:00 | 16.86 | 22.1512 | N | 0
2025-04-25 | 11 | 2031-04-25 11:00 | 17.34 | 22.7818 | N | 0
2025-04-25 | 12 | 2031-04-25 12:00 | 17.11 | 22.4796 | N | 0
2025-04-25 | 13 | 2031-04-25 13:00 | 17.2 | 22.5979 | N | 0
2025-04-25 | 14 | 2031-04-25 14:00 | 16.83 | 22.1118 | N | 0
2025-04-25 | 15 | 2031-04-25 15:00 | 16.96 | 22.2826 | N | 0
2025-04-25 | 16 | 2031-04-25 16:00 | 17.07 | 22.4271 | N | 0
2025-04-25 | 17 | 2031-04-25 17:00 | 17.32 | 22.7555 | N | 0
2025-04-25 | 18 | 2031-04-25 18:00 | 17.05 | 22.4008 | N | 0
2025-04-25 | 19 | 2031-04-25 19:00 | 17.13 | 22.5059 | N | 0
2025-04-25 | 20 | 2031-04-25 20:00 | 17.55 | 23.0577 | N | 0
2025-04-25 | 21 | 2031-04-25 21:00 | 17.65 | 23.1891 | N | 0
2025-04-25 | 22 | 2031-04-25 22:00 | 16.66 | 21.8884 | N | 0
2025-04-25 | 23 | 2031-04-25 23:00 | 15.13 | 19.8782 | N | 0
2025-04-26 | 00 | 2031-04-26 | 13.33 | 17.5134 | N | 0
2025-04-26 | 01 | 2031-04-26 01:00 | 12.25 | 16.0944 | N | 0
2025-04-26 | 02 | 2031-04-26 02:00 | 11.32 | 14.8726 | N | 0
2025-04-26 | 03 | 2031-04-26 03:00 | 10.92 | 14.347 | N | 0
2025-04-26 | 04 | 2031-04-26 04:00 | 10.78 | 14.1631 | N | 0
2025-04-26 | 05 | 2031-04-26 05:00 | 10.99 | 14.439 | N | 0
2025-04-26 | 06 | 2031-04-26 06:00 | 11.29 | 14.8331 | N | 0
2025-04-26 | 07 | 2031-04-26 07:00 | 13.38 | 17.579 | N | 0
2025-04-26 | 08 | 2031-04-26 08:00 | 14.77 | 19.4053 | N | 0
2025-04-26 | 09 | 2031-04-26 09:00 | 15.94 | 20.9424 | N | 0
2025-04-26 | 10 | 2031-04-26 10:00 | 16.63 | 21.849 | N | 0
2025-04-26 | 11 | 2031-04-26 11:00 | 16.88 | 22.1774 | N | 0
2025-04-26 | 12 | 2031-04-26 12:00 | 17.2 | 22.5979 | N | 0
2025-04-26 | 13 | 2031-04-26 13:00 | 17.11 | 22.4796 | N | 0
2025-04-26 | 14 | 2031-04-26 14:00 | 16.68 | 21.9147 | N | 0
2025-04-26 | 15 | 2031-04-26 15:00 | 17.04 | 22.3877 | N | 0
2025-04-26 | 16 | 2031-04-26 16:00 | 17.58 | 23.0971 | N | 0
2025-04-26 | 17 | 2031-04-26 17:00 | 18.03 | 23.6884 | N | 0
2025-04-26 | 18 | 2031-04-26 18:00 | 18.06 | 23.7278 | N | 0
2025-04-26 | 19 | 2031-04-26 19:00 | 18.01 | 23.6621 | N | 0
2025-04-26 | 20 | 2031-04-26 20:00 | 18.32 | 24.0694 | N | 0
2025-04-26 | 21 | 2031-04-26 21:00 | 17.96 | 23.5964 | N | 0
2025-04-26 | 22 | 2031-04-26 22:00 | 16.99 | 22.322 | N | 0
2025-04-26 | 23 | 2031-04-26 23:00 | 15.56 | 20.4432 | N | 0
2025-04-27 | 00 | 2031-04-27 | 14.47 | 19.0111 | N | 0
2025-04-27 | 01 | 2031-04-27 01:00 | 12.99 | 17.0666 | N | 0
2025-04-27 | 02 | 2031-04-27 02:00 | 12.28 | 16.1338 | N | 0
2025-04-27 | 03 | 2031-04-27 03:00 | 11.74 | 15.4244 | N | 0
2025-04-27 | 04 | 2031-04-27 04:00 | 11.58 | 15.2141 | N | 0
2025-04-27 | 05 | 2031-04-27 05:00 | 11.98 | 15.7397 | N | 0
2025-04-27 | 06 | 2031-04-27 06:00 | 12.34 | 16.2127 | N | 0
2025-04-27 | 07 | 2031-04-27 07:00 | 13.08 | 17.1849 | N | 0
2025-04-27 | 08 | 2031-04-27 08:00 | 14.59 | 19.1688 | N | 0
2025-04-27 | 09 | 2031-04-27 09:00 | 15.47 | 20.3249 | N | 0
2025-04-27 | 10 | 2031-04-27 10:00 | 15.78 | 20.7322 | N | 0
2025-04-27 | 11 | 2031-04-27 11:00 | 16.09 | 21.1395 | N | 0
2025-04-27 | 12 | 2031-04-27 12:00 | 16.4 | 21.5468 | N | 0
2025-04-27 | 13 | 2031-04-27 13:00 | 16.36 | 21.4943 | N | 0
2025-04-27 | 14 | 2031-04-27 14:00 | 16.12 | 21.1789 | N | 0
2025-04-27 | 15 | 2031-04-27 15:00 | 16.22 | 21.3103 | N | 0
2025-04-27 | 16 | 2031-04-27 16:00 | 17.14 | 22.519 | N | 0
2025-04-27 | 17 | 2031-04-27 17:00 | 18.24 | 23.9643 | N | 0
2025-04-27 | 18 | 2031-04-27 18:00 | 18.21 | 23.9248 | N | 0
2025-04-27 | 19 | 2031-04-27 19:00 | 17.84 | 23.4387 | N | 0
2025-04-27 | 20 | 2031-04-27 20:00 | 18.25 | 23.9774 | N | 0
2025-04-27 | 21 | 2031-04-27 21:00 | 18.24 | 23.9643 | N | 0
2025-04-27 | 22 | 2031-04-27 22:00 | 16.83 | 22.1118 | N | 0
2025-04-27 | 23 | 2031-04-27 23:00 | 14.88 | 19.5498 | N | 0
2025-04-28 | 00 | 2031-04-28 | 13.17 | 17.3031 | N | 0
2025-04-28 | 01 | 2031-04-28 01:00 | 11.88 | 15.6083 | N | 0
2025-04-28 | 02 | 2031-04-28 02:00 | 11.3 | 14.8463 | N | 0
2025-04-28 | 03 | 2031-04-28 03:00 | 10.95 | 14.3864 | N | 0
2025-04-28 | 04 | 2031-04-28 04:00 | 11.27 | 14.8069 | N | 0
2025-04-28 | 05 | 2031-04-28 05:00 | 12.55 | 16.4886 | N | 0
2025-04-28 | 06 | 2031-04-28 06:00 | 14.15 | 18.5907 | N | 0
2025-04-28 | 07 | 2031-04-28 07:00 | 16.67 | 21.9015 | N | 0
2025-04-28 | 08 | 2031-04-28 08:00 | 16.38 | 21.5205 | N | 0
2025-04-28 | 09 | 2031-04-28 09:00 | 16.46 | 21.6256 | N | 0
2025-04-28 | 10 | 2031-04-28 10:00 | 16.73 | 21.9804 | N | 0
2025-04-28 | 11 | 2031-04-28 11:00 | 16.84 | 22.1249 | N | 0
2025-04-28 | 12 | 2031-04-28 12:00 | 17.09 | 22.4534 | N | 0
2025-04-28 | 13 | 2031-04-28 13:00 | 16.79 | 22.0592 | N | 0
2025-04-28 | 14 | 2031-04-28 14:00 | 16.61 | 21.8227 | N | 0
2025-04-28 | 15 | 2031-04-28 15:00 | 16.93 | 22.2431 | N | 0
2025-04-28 | 16 | 2031-04-28 16:00 | 17.43 | 22.9001 | N | 0
2025-04-28 | 17 | 2031-04-28 17:00 | 18.21 | 23.9248 | N | 0
2025-04-28 | 18 | 2031-04-28 18:00 | 17.91 | 23.5307 | N | 0
2025-04-28 | 19 | 2031-04-28 19:00 | 17.63 | 23.1628 | N | 0
2025-04-28 | 20 | 2031-04-28 20:00 | 18.42 | 24.2007 | N | 0
2025-04-28 | 21 | 2031-04-28 21:00 | 18.08 | 23.754 | N | 0
2025-04-28 | 22 | 2031-04-28 22:00 | 16.96 | 22.2826 | N | 0
2025-04-28 | 23 | 2031-04-28 23:00 | 14.66 | 19.2607 | N | 0
2025-04-29 | 00 | 2031-04-29 | 13.51 | 17.7498 | N | 0
2025-04-29 | 01 | 2031-04-29 01:00 | 12.27 | 16.1207 | N | 0
2025-04-29 | 02 | 2031-04-29 02:00 | 11.34 | 14.8988 | N | 0
2025-04-29 | 03 | 2031-04-29 03:00 | 11.22 | 14.7412 | N | 0
2025-04-29 | 04 | 2031-04-29 04:00 | 11.31 | 14.8594 | N | 0
2025-04-29 | 05 | 2031-04-29 05:00 | 12.01 | 15.7791 | N | 0
2025-04-29 | 06 | 2031-04-29 06:00 | 13.63 | 17.9075 | N | 0
2025-04-29 | 07 | 2031-04-29 07:00 | 16.11 | 21.1658 | N | 0
2025-04-29 | 08 | 2031-04-29 08:00 | 16.42 | 21.5731 | N | 0
2025-04-29 | 09 | 2031-04-29 09:00 | 16.65 | 21.8753 | N | 0
2025-04-29 | 10 | 2031-04-29 10:00 | 16.93 | 22.2431 | N | 0
2025-04-29 | 11 | 2031-04-29 11:00 | 17.02 | 22.3614 | N | 0
2025-04-29 | 12 | 2031-04-29 12:00 | 17.34 | 22.7818 | N | 0
2025-04-29 | 13 | 2031-04-29 13:00 | 17.53 | 23.0314 | N | 0
2025-04-29 | 14 | 2031-04-29 14:00 | 17.32 | 22.7555 | N | 0
2025-04-29 | 15 | 2031-04-29 15:00 | 17.27 | 22.6898 | N | 0
2025-04-29 | 16 | 2031-04-29 16:00 | 17.93 | 23.557 | N | 0
2025-04-29 | 17 | 2031-04-29 17:00 | 18.62 | 24.4635 | N | 0
2025-04-29 | 18 | 2031-04-29 18:00 | 18.91 | 24.8445 | N | 0
2025-04-29 | 19 | 2031-04-29 19:00 | 18.19 | 23.8986 | N | 0
2025-04-29 | 20 | 2031-04-29 20:00 | 17.86 | 23.465 | N | 0
2025-04-29 | 21 | 2031-04-29 21:00 | 18.01 | 23.6621 | N | 0
2025-04-29 | 22 | 2031-04-29 22:00 | 15.27 | 20.0622 | N | 0
2025-04-29 | 23 | 2031-04-29 23:00 | 13.47 | 17.6973 | N | 0
2025-04-30 | 00 | 2031-04-30 | 14.4 | 18.9191 | N | 0
2025-04-30 | 01 | 2031-04-30 01:00 | 12.54 | 16.4754 | N | 0
2025-04-30 | 02 | 2031-04-30 02:00 | 12 | 15.766 | N | 0
2025-04-30 | 03 | 2031-04-30 03:00 | 11.52 | 15.1353 | N | 0
2025-04-30 | 04 | 2031-04-30 04:00 | 11.72 | 15.3981 | N | 0
2025-04-30 | 05 | 2031-04-30 05:00 | 12.78 | 16.7907 | N | 0
2025-04-30 | 06 | 2031-04-30 06:00 | 14.52 | 19.0768 | N | 0
2025-04-30 | 07 | 2031-04-30 07:00 | 16.62 | 21.8359 | N | 0
2025-04-30 | 08 | 2031-04-30 08:00 | 17.26 | 22.6767 | N | 0
2025-04-30 | 09 | 2031-04-30 09:00 | 17.19 | 22.5847 | N | 0
2025-04-30 | 10 | 2031-04-30 10:00 | 17.15 | 22.5322 | N | 0
2025-04-30 | 11 | 2031-04-30 11:00 | 17.08 | 22.4402 | N | 0
2025-04-30 | 12 | 2031-04-30 12:00 | 17.48 | 22.9657 | N | 0
2025-04-30 | 13 | 2031-04-30 13:00 | 17.14 | 22.519 | N | 0
2025-04-30 | 14 | 2031-04-30 14:00 | 17 | 22.3351 | N | 0
2025-04-30 | 15 | 2031-04-30 15:00 | 16.88 | 22.1774 | N | 0
2025-04-30 | 16 | 2031-04-30 16:00 | 17.32 | 22.7555 | N | 0
2025-04-30 | 17 | 2031-04-30 17:00 | 18.19 | 23.8986 | N | 0
2025-04-30 | 18 | 2031-04-30 18:00 | 17.8 | 23.3862 | N | 0
2025-04-30 | 19 | 2031-04-30 19:00 | 18.16 | 23.8591 | N | 0
2025-04-30 | 20 | 2031-04-30 20:00 | 18.74 | 24.6212 | N | 0
2025-04-30 | 21 | 2031-04-30 21:00 | 18.65 | 24.5029 | N | 0
2025-04-30 | 22 | 2031-04-30 22:00 | 17.48 | 22.9657 | N | 0
2025-04-30 | 23 | 2031-04-30 23:00 | 15.51 | 20.3775 | N | 0
2025-05-01 | 00 | 2031-05-01 | 14.18 | 18.6301 | N | 0
2025-05-01 | 01 | 2031-05-01 01:00 | 12.92 | 16.9747 | N | 0
2025-05-01 | 02 | 2031-05-01 02:00 | 12.18 | 16.0024 | N | 0
2025-05-01 | 03 | 2031-05-01 03:00 | 11.71 | 15.3849 | N | 0
2025-05-01 | 04 | 2031-05-01 04:00 | 11.91 | 15.6477 | N | 0
2025-05-01 | 05 | 2031-05-01 05:00 | 12.81 | 16.8302 | N | 0
2025-05-01 | 06 | 2031-05-01 06:00 | 14.77 | 19.4053 | N | 0
2025-05-01 | 07 | 2031-05-01 07:00 | 16.71 | 21.9541 | N | 0
2025-05-01 | 08 | 2031-05-01 08:00 | 16.73 | 21.9804 | N | 0
2025-05-01 | 09 | 2031-05-01 09:00 | 16.59 | 21.7964 | N | 0
2025-05-01 | 10 | 2031-05-01 10:00 | 16.84 | 22.1249 | N | 0
2025-05-01 | 11 | 2031-05-01 11:00 | 17.56 | 23.0709 | N | 0
2025-05-01 | 12 | 2031-05-01 12:00 | 17.66 | 23.2022 | N | 0
2025-05-01 | 13 | 2031-05-01 13:00 | 18.06 | 23.7278 | N | 0
2025-05-01 | 14 | 2031-05-01 14:00 | 17.98 | 23.6227 | N | 0
2025-05-01 | 15 | 2031-05-01 15:00 | 18.21 | 23.9248 | N | 0
2025-05-01 | 16 | 2031-05-01 16:00 | 19.06 | 25.0416 | N | 0
2025-05-01 | 17 | 2031-05-01 17:00 | 19.89 | 26.1321 | N | 0
2025-05-01 | 18 | 2031-05-01 18:00 | 19.5 | 25.6197 | N | 0
2025-05-01 | 19 | 2031-05-01 19:00 | 19.48 | 25.5934 | N | 0
2025-05-01 | 20 | 2031-05-01 20:00 | 19.16 | 25.173 | N | 0
2025-05-01 | 21 | 2031-05-01 21:00 | 18.77 | 24.6606 | N | 0
2025-05-01 | 22 | 2031-05-01 22:00 | 16.88 | 22.1774 | N | 0
2025-05-01 | 23 | 2031-05-01 23:00 | 15.44 | 20.2855 | N | 0
2025-05-02 | 00 | 2031-05-02 | 13.98 | 18.3673 | N | 0
2025-05-02 | 01 | 2031-05-02 01:00 | 12.76 | 16.7645 | N | 0
2025-05-02 | 02 | 2031-05-02 02:00 | 11.91 | 15.6477 | N | 0
2025-05-02 | 03 | 2031-05-02 03:00 | 11.37 | 14.9382 | N | 0
2025-05-02 | 04 | 2031-05-02 04:00 | 11.53 | 15.1485 | N | 0
2025-05-02 | 05 | 2031-05-02 05:00 | 12.56 | 16.5017 | N | 0
2025-05-02 | 06 | 2031-05-02 06:00 | 14.01 | 18.4068 | N | 0
2025-05-02 | 07 | 2031-05-02 07:00 | 15.97 | 20.9819 | N | 0
2025-05-02 | 08 | 2031-05-02 08:00 | 16.55 | 21.7439 | N | 0
2025-05-02 | 09 | 2031-05-02 09:00 | 16.54 | 21.7307 | N | 0
2025-05-02 | 10 | 2031-05-02 10:00 | 16.95 | 22.2694 | N | 0
2025-05-02 | 11 | 2031-05-02 11:00 | 16.75 | 22.0066 | N | 0
2025-05-02 | 12 | 2031-05-02 12:00 | 16.61 | 21.8227 | N | 0
2025-05-02 | 13 | 2031-05-02 13:00 | 16.57 | 21.7702 | N | 0
2025-05-02 | 14 | 2031-05-02 14:00 | 16.45 | 21.6125 | N | 0
2025-05-02 | 15 | 2031-05-02 15:00 | 16.32 | 21.4417 | N | 0
2025-05-02 | 16 | 2031-05-02 16:00 | 16.83 | 22.1118 | N | 0
2025-05-02 | 17 | 2031-05-02 17:00 | 17.48 | 22.9657 | N | 0
2025-05-02 | 18 | 2031-05-02 18:00 | 17.3 | 22.7293 | N | 0
2025-05-02 | 19 | 2031-05-02 19:00 | 16.74 | 21.9935 | N | 0
2025-05-02 | 20 | 2031-05-02 20:00 | 17.47 | 22.9526 | N | 0
2025-05-02 | 21 | 2031-05-02 21:00 | 17.38 | 22.8344 | N | 0
2025-05-02 | 22 | 2031-05-02 22:00 | 16.6 | 21.8096 | N | 0
2025-05-02 | 23 | 2031-05-02 23:00 | 14.9 | 19.5761 | N | 0
2025-05-03 | 00 | 2031-05-03 | 13.7 | 17.9995 | N | 0
2025-05-03 | 01 | 2031-05-03 01:00 | 12.23 | 16.0681 | N | 0
2025-05-03 | 02 | 2031-05-03 02:00 | 11.18 | 14.6886 | N | 0
2025-05-03 | 03 | 2031-05-03 03:00 | 10.91 | 14.3339 | N | 0
2025-05-03 | 04 | 2031-05-03 04:00 | 10.64 | 13.9791 | N | 0
2025-05-03 | 05 | 2031-05-03 05:00 | 10.95 | 14.3864 | N | 0
2025-05-03 | 06 | 2031-05-03 06:00 | 11.39 | 14.9645 | N | 0
2025-05-03 | 07 | 2031-05-03 07:00 | 13.12 | 17.2374 | N | 0
2025-05-03 | 08 | 2031-05-03 08:00 | 14.93 | 19.6155 | N | 0
2025-05-03 | 09 | 2031-05-03 09:00 | 16.07 | 21.1132 | N | 0
2025-05-03 | 10 | 2031-05-03 10:00 | 16.54 | 21.7307 | N | 0
2025-05-03 | 11 | 2031-05-03 11:00 | 17.06 | 22.4139 | N | 0
2025-05-03 | 12 | 2031-05-03 12:00 | 16.96 | 22.2826 | N | 0
2025-05-03 | 13 | 2031-05-03 13:00 | 16.35 | 21.4811 | N | 0
2025-05-03 | 14 | 2031-05-03 14:00 | 16.15 | 21.2184 | N | 0
2025-05-03 | 15 | 2031-05-03 15:00 | 16.54 | 21.7307 | N | 0
2025-05-03 | 16 | 2031-05-03 16:00 | 16.94 | 22.2563 | N | 0
2025-05-03 | 17 | 2031-05-03 17:00 | 17.5 | 22.992 | N | 0
2025-05-03 | 18 | 2031-05-03 18:00 | 17.45 | 22.9263 | N | 0
2025-05-03 | 19 | 2031-05-03 19:00 | 17.01 | 22.3482 | N | 0
2025-05-03 | 20 | 2031-05-03 20:00 | 17.21 | 22.611 | N | 0
2025-05-03 | 21 | 2031-05-03 21:00 | 17.6 | 23.1234 | N | 0
2025-05-03 | 22 | 2031-05-03 22:00 | 16.29 | 21.4023 | N | 0
2025-05-03 | 23 | 2031-05-03 23:00 | 14.8 | 19.4447 | N | 0
2025-05-04 | 00 | 2031-05-04 | 13.61 | 17.8812 | N | 0
2025-05-04 | 01 | 2031-05-04 01:00 | 12.37 | 16.2521 | N | 0
2025-05-04 | 02 | 2031-05-04 02:00 | 11.8 | 15.5032 | N | 0
2025-05-04 | 03 | 2031-05-04 03:00 | 11.2 | 14.7149 | N | 0
2025-05-04 | 04 | 2031-05-04 04:00 | 11.05 | 14.5178 | N | 0
2025-05-04 | 05 | 2031-05-04 05:00 | 11.11 | 14.5966 | N | 0
2025-05-04 | 06 | 2031-05-04 06:00 | 11.68 | 15.3455 | N | 0
2025-05-04 | 07 | 2031-05-04 07:00 | 12.72 | 16.7119 | N | 0
2025-05-04 | 08 | 2031-05-04 08:00 | 14 | 18.3936 | N | 0
2025-05-04 | 09 | 2031-05-04 09:00 | 15.21 | 19.9834 | N | 0
2025-05-04 | 10 | 2031-05-04 10:00 | 15.74 | 20.6797 | N | 0
2025-05-04 | 11 | 2031-05-04 11:00 | 16.2 | 21.284 | N | 0
2025-05-04 | 12 | 2031-05-04 12:00 | 16.41 | 21.5599 | N | 0
2025-05-04 | 13 | 2031-05-04 13:00 | 16.35 | 21.4811 | N | 0
2025-05-04 | 14 | 2031-05-04 14:00 | 16.62 | 21.8359 | N | 0
2025-05-04 | 15 | 2031-05-04 15:00 | 16.84 | 22.1249 | N | 0
2025-05-04 | 16 | 2031-05-04 16:00 | 18.12 | 23.8066 | N | 0
2025-05-04 | 17 | 2031-05-04 17:00 | 19.2 | 25.2255 | N | 0
2025-05-04 | 18 | 2031-05-04 18:00 | 18.66 | 24.5161 | N | 0
2025-05-04 | 19 | 2031-05-04 19:00 | 18.56 | 24.3847 | N | 0
2025-05-04 | 20 | 2031-05-04 20:00 | 18.4 | 24.1745 | N | 0
2025-05-04 | 21 | 2031-05-04 21:00 | 18.04 | 23.7015 | N | 0
2025-05-04 | 22 | 2031-05-04 22:00 | 16.51 | 21.6913 | N | 0
2025-05-04 | 23 | 2031-05-04 23:00 | 14.27 | 18.7484 | N | 0
2025-05-05 | 00 | 2031-05-05 | 12.62 | 16.5805 | N | 0
2025-05-05 | 01 | 2031-05-05 01:00 | 11.49 | 15.0959 | N | 0
2025-05-05 | 02 | 2031-05-05 02:00 | 10.73 | 14.0974 | N | 0
2025-05-05 | 03 | 2031-05-05 03:00 | 10.51 | 13.8084 | N | 0
2025-05-05 | 04 | 2031-05-05 04:00 | 10.77 | 14.1499 | N | 0
2025-05-05 | 05 | 2031-05-05 05:00 | 11.7 | 15.3718 | N | 0
2025-05-05 | 06 | 2031-05-05 06:00 | 13.57 | 17.8287 | N | 0
2025-05-05 | 07 | 2031-05-05 07:00 | 15.61 | 20.5089 | N | 0
2025-05-05 | 08 | 2031-05-05 08:00 | 16.24 | 21.3366 | N | 0
2025-05-05 | 09 | 2031-05-05 09:00 | 16.44 | 21.5994 | N | 0
2025-05-05 | 10 | 2031-05-05 10:00 | 17.08 | 22.4402 | N | 0
2025-05-05 | 11 | 2031-05-05 11:00 | 17.58 | 23.0971 | N | 0
2025-05-05 | 12 | 2031-05-05 12:00 | 17.64 | 23.176 | N | 0
2025-05-05 | 13 | 2031-05-05 13:00 | 17.63 | 23.1628 | N | 0
2025-05-05 | 14 | 2031-05-05 14:00 | 17.42 | 22.8869 | N | 0
2025-05-05 | 15 | 2031-05-05 15:00 | 17.71 | 23.2679 | N | 0
2025-05-05 | 16 | 2031-05-05 16:00 | 18.34 | 24.0956 | N | 0
2025-05-05 | 17 | 2031-05-05 17:00 | 19.33 | 25.3963 | N | 0
2025-05-05 | 18 | 2031-05-05 18:00 | 18.9 | 24.8314 | N | 0
2025-05-05 | 19 | 2031-05-05 19:00 | 18.51 | 24.319 | N | 0
2025-05-05 | 20 | 2031-05-05 20:00 | 18.75 | 24.6343 | N | 0
2025-05-05 | 21 | 2031-05-05 21:00 | 18.36 | 24.1219 | N | 0
2025-05-05 | 22 | 2031-05-05 22:00 | 17.05 | 22.4008 | N | 0
2025-05-05 | 23 | 2031-05-05 23:00 | 15.1 | 19.8388 | N | 0
2025-05-06 | 00 | 2031-05-06 | 13.51 | 17.7498 | N | 0
2025-05-06 | 01 | 2031-05-06 01:00 | 11.91 | 15.6477 | N | 0
2025-05-06 | 02 | 2031-05-06 02:00 | 11.23 | 14.7543 | N | 0
2025-05-06 | 03 | 2031-05-06 03:00 | 10.81 | 14.2025 | N | 0
2025-05-06 | 04 | 2031-05-06 04:00 | 10.86 | 14.2682 | N | 0
2025-05-06 | 05 | 2031-05-06 05:00 | 11.52 | 15.1353 | N | 0
2025-05-06 | 06 | 2031-05-06 06:00 | 13.78 | 18.1046 | N | 0
2025-05-06 | 07 | 2031-05-06 07:00 | 15.76 | 20.706 | N | 0
2025-05-06 | 08 | 2031-05-06 08:00 | 17.25 | 22.6636 | N | 0
2025-05-06 | 09 | 2031-05-06 09:00 | 17.08 | 22.4402 | N | 0
2025-05-06 | 10 | 2031-05-06 10:00 | 17.19 | 22.5847 | N | 0
2025-05-06 | 11 | 2031-05-06 11:00 | 17.33 | 22.7687 | N | 0
2025-05-06 | 12 | 2031-05-06 12:00 | 17.7 | 23.2548 | N | 0
2025-05-06 | 13 | 2031-05-06 13:00 | 17.47 | 22.9526 | N | 0
2025-05-06 | 14 | 2031-05-06 14:00 | 17.44 | 22.9132 | N | 0
2025-05-06 | 15 | 2031-05-06 15:00 | 17.18 | 22.5716 | N | 0
2025-05-06 | 16 | 2031-05-06 16:00 | 17.74 | 23.3073 | N | 0
2025-05-06 | 17 | 2031-05-06 17:00 | 18.47 | 24.2664 | N | 0
2025-05-06 | 18 | 2031-05-06 18:00 | 18.19 | 23.8986 | N | 0
2025-05-06 | 19 | 2031-05-06 19:00 | 17.96 | 23.5964 | N | 0
2025-05-06 | 20 | 2031-05-06 20:00 | 18.55 | 24.3715 | N | 0
2025-05-06 | 21 | 2031-05-06 21:00 | 18.43 | 24.2139 | N | 0
2025-05-06 | 22 | 2031-05-06 22:00 | 16.99 | 22.322 | N | 0
2025-05-06 | 23 | 2031-05-06 23:00 | 14.89 | 19.5629 | N | 0
2025-05-07 | 00 | 2031-05-07 | 13.33 | 17.5134 | N | 0
2025-05-07 | 01 | 2031-05-07 01:00 | 12.06 | 15.8448 | N | 0
2025-05-07 | 02 | 2031-05-07 02:00 | 11.23 | 14.7543 | N | 0
2025-05-07 | 03 | 2031-05-07 03:00 | 11.13 | 14.6229 | N | 0
2025-05-07 | 04 | 2031-05-07 04:00 | 10.88 | 14.2945 | N | 0
2025-05-07 | 05 | 2031-05-07 05:00 | 11.69 | 15.3587 | N | 0
2025-05-07 | 06 | 2031-05-07 06:00 | 13.82 | 18.1571 | N | 0
2025-05-07 | 07 | 2031-05-07 07:00 | 16.04 | 21.0738 | N | 0
2025-05-07 | 08 | 2031-05-07 08:00 | 16.73 | 21.9804 | N | 0
2025-05-07 | 09 | 2031-05-07 09:00 | 17.05 | 22.4008 | N | 0
2025-05-07 | 10 | 2031-05-07 10:00 | 17.39 | 22.8475 | N | 0
2025-05-07 | 11 | 2031-05-07 11:00 | 17.88 | 23.4913 | N | 0
2025-05-07 | 12 | 2031-05-07 12:00 | 17.83 | 23.4256 | N | 0
2025-05-07 | 13 | 2031-05-07 13:00 | 17.88 | 23.4913 | N | 0
2025-05-07 | 14 | 2031-05-07 14:00 | 17.96 | 23.5964 | N | 0
2025-05-07 | 15 | 2031-05-07 15:00 | 18.25 | 23.9774 | N | 0
2025-05-07 | 16 | 2031-05-07 16:00 | 18.55 | 24.3715 | N | 0
2025-05-07 | 17 | 2031-05-07 17:00 | 19.34 | 25.4095 | N | 0
2025-05-07 | 18 | 2031-05-07 18:00 | 18.89 | 24.8182 | N | 0
2025-05-07 | 19 | 2031-05-07 19:00 | 19.05 | 25.0285 | N | 0
2025-05-07 | 20 | 2031-05-07 20:00 | 19.15 | 25.1598 | N | 0
2025-05-07 | 21 | 2031-05-07 21:00 | 19.09 | 25.081 | N | 0
2025-05-07 | 22 | 2031-05-07 22:00 | 17.58 | 23.0971 | N | 0
2025-05-07 | 23 | 2031-05-07 23:00 | 15.41 | 20.2461 | N | 0
2025-05-08 | 00 | 2031-05-08 | 13.7 | 17.9995 | N | 0
2025-05-08 | 01 | 2031-05-08 01:00 | 12.39 | 16.2784 | N | 0
2025-05-08 | 02 | 2031-05-08 02:00 | 11.43 | 15.0171 | N | 0
2025-05-08 | 03 | 2031-05-08 03:00 | 11.16 | 14.6623 | N | 0
2025-05-08 | 04 | 2031-05-08 04:00 | 11.03 | 14.4915 | N | 0
2025-05-08 | 05 | 2031-05-08 05:00 | 12.18 | 16.0024 | N | 0
2025-05-08 | 06 | 2031-05-08 06:00 | 13.81 | 18.144 | N | 0
2025-05-08 | 07 | 2031-05-08 07:00 | 16.16 | 21.2315 | N | 0
2025-05-08 | 08 | 2031-05-08 08:00 | 16.95 | 22.2694 | N | 0
2025-05-08 | 09 | 2031-05-08 09:00 | 17.77 | 23.3468 | N | 0
2025-05-08 | 10 | 2031-05-08 10:00 | 18.17 | 23.8723 | N | 0
2025-05-08 | 11 | 2031-05-08 11:00 | 18.1 | 23.7803 | N | 0
2025-05-08 | 12 | 2031-05-08 12:00 | 18.24 | 23.9643 | N | 0
2025-05-08 | 13 | 2031-05-08 13:00 | 18.12 | 23.8066 | N | 0
2025-05-08 | 14 | 2031-05-08 14:00 | 17.62 | 23.1497 | N | 0
2025-05-08 | 15 | 2031-05-08 15:00 | 17.23 | 22.6373 | N | 0
2025-05-08 | 16 | 2031-05-08 16:00 | 15.97 | 20.9819 | N | 0
2025-05-08 | 17 | 2031-05-08 17:00 | 18.39 | 24.1613 | N | 0
2025-05-08 | 18 | 2031-05-08 18:00 | 18 | 23.6489 | N | 0
2025-05-08 | 19 | 2031-05-08 19:00 | 18.39 | 24.1613 | N | 0
2025-05-08 | 20 | 2031-05-08 20:00 | 18.76 | 24.6474 | N | 0
2025-05-08 | 21 | 2031-05-08 21:00 | 18.66 | 24.5161 | N | 0
2025-05-08 | 22 | 2031-05-08 22:00 | 17.7 | 23.2548 | N | 0
2025-05-08 | 23 | 2031-05-08 23:00 | 15.41 | 20.2461 | N | 0
2025-05-09 | 00 | 2031-05-09 | 13.8 | 18.1309 | N | 0
2025-05-09 | 01 | 2031-05-09 01:00 | 12.57 | 16.5148 | N | 0
2025-05-09 | 02 | 2031-05-09 02:00 | 11.95 | 15.7003 | N | 0
2025-05-09 | 03 | 2031-05-09 03:00 | 11.63 | 15.2798 | N | 0
2025-05-09 | 04 | 2031-05-09 04:00 | 11.67 | 15.3324 | N | 0
2025-05-09 | 05 | 2031-05-09 05:00 | 12.82 | 16.8433 | N | 0
2025-05-09 | 06 | 2031-05-09 06:00 | 14.78 | 19.4184 | N | 0
2025-05-09 | 07 | 2031-05-09 07:00 | 16.79 | 22.0592 | N | 0
2025-05-09 | 08 | 2031-05-09 08:00 | 16.97 | 22.2957 | N | 0
2025-05-09 | 09 | 2031-05-09 09:00 | 16.97 | 22.2957 | N | 0
2025-05-09 | 10 | 2031-05-09 10:00 | 17.01 | 22.3482 | N | 0
2025-05-09 | 11 | 2031-05-09 11:00 | 17 | 22.3351 | N | 0
2025-05-09 | 12 | 2031-05-09 12:00 | 17.08 | 22.4402 | N | 0
2025-05-09 | 13 | 2031-05-09 13:00 | 17.02 | 22.3614 | N | 0
2025-05-09 | 14 | 2031-05-09 14:00 | 16.2 | 21.284 | N | 0
2025-05-09 | 15 | 2031-05-09 15:00 | 16.45 | 21.6125 | N | 0
2025-05-09 | 16 | 2031-05-09 16:00 | 16.6 | 21.8096 | N | 0
2025-05-09 | 17 | 2031-05-09 17:00 | 17.15 | 22.5322 | N | 0
2025-05-09 | 18 | 2031-05-09 18:00 | 17.02 | 22.3614 | N | 0
2025-05-09 | 19 | 2031-05-09 19:00 | 16.98 | 22.3088 | N | 0
2025-05-09 | 20 | 2031-05-09 20:00 | 17.2 | 22.5979 | N | 0
2025-05-09 | 21 | 2031-05-09 21:00 | 17.42 | 22.8869 | N | 0
2025-05-09 | 22 | 2031-05-09 22:00 | 16.6 | 21.8096 | N | 0
2025-05-09 | 23 | 2031-05-09 23:00 | 15.32 | 20.1279 | N | 0
2025-05-10 | 00 | 2031-05-10 | 13.8 | 18.1309 | N | 0
2025-05-10 | 01 | 2031-05-10 01:00 | 12.38 | 16.2652 | N | 0
2025-05-10 | 02 | 2031-05-10 02:00 | 11.61 | 15.2536 | N | 0
2025-05-10 | 03 | 2031-05-10 03:00 | 11.23 | 14.7543 | N | 0
2025-05-10 | 04 | 2031-05-10 04:00 | 11.18 | 14.6886 | N | 0
2025-05-10 | 05 | 2031-05-10 05:00 | 11.29 | 14.8331 | N | 0
2025-05-10 | 06 | 2031-05-10 06:00 | 11.62 | 15.2667 | N | 0
2025-05-10 | 07 | 2031-05-10 07:00 | 13.1 | 17.2112 | N | 0
2025-05-10 | 08 | 2031-05-10 08:00 | 14.69 | 19.3002 | N | 0
2025-05-10 | 09 | 2031-05-10 09:00 | 15.4 | 20.233 | N | 0
2025-05-10 | 10 | 2031-05-10 10:00 | 15.95 | 20.9556 | N | 0
2025-05-10 | 11 | 2031-05-10 11:00 | 15.97 | 20.9819 | N | 0
2025-05-10 | 12 | 2031-05-10 12:00 | 15.88 | 20.8636 | N | 0
2025-05-10 | 13 | 2031-05-10 13:00 | 15.56 | 20.4432 | N | 0
2025-05-10 | 14 | 2031-05-10 14:00 | 15.62 | 20.522 | N | 0
2025-05-10 | 15 | 2031-05-10 15:00 | 15.29 | 20.0885 | N | 0
2025-05-10 | 16 | 2031-05-10 16:00 | 15.95 | 20.9556 | N | 0
2025-05-10 | 17 | 2031-05-10 17:00 | 16.65 | 21.8753 | N | 0
2025-05-10 | 18 | 2031-05-10 18:00 | 16.73 | 21.9804 | N | 0
2025-05-10 | 19 | 2031-05-10 19:00 | 16.27 | 21.376 | N | 0
2025-05-10 | 20 | 2031-05-10 20:00 | 16.51 | 21.6913 | N | 0
2025-05-10 | 21 | 2031-05-10 21:00 | 16.77 | 22.0329 | N | 0
2025-05-10 | 22 | 2031-05-10 22:00 | 15.76 | 20.706 | N | 0
2025-05-10 | 23 | 2031-05-10 23:00 | 14.57 | 19.1425 | N | 0
2025-05-11 | 00 | 2031-05-11 | 13.23 | 17.382 | N | 0
2025-05-11 | 01 | 2031-05-11 01:00 | 11.98 | 15.7397 | N | 0
2025-05-11 | 02 | 2031-05-11 02:00 | 11.22 | 14.7412 | N | 0
2025-05-11 | 03 | 2031-05-11 03:00 | 10.83 | 14.2288 | N | 0
2025-05-11 | 04 | 2031-05-11 04:00 | 10.69 | 14.0448 | N | 0
2025-05-11 | 05 | 2031-05-11 05:00 | 10.79 | 14.1762 | N | 0
2025-05-11 | 06 | 2031-05-11 06:00 | 11.2 | 14.7149 | N | 0
2025-05-11 | 07 | 2031-05-11 07:00 | 12.41 | 16.3046 | N | 0
2025-05-11 | 08 | 2031-05-11 08:00 | 14.19 | 18.6432 | N | 0
2025-05-11 | 09 | 2031-05-11 09:00 | 14.9 | 19.5761 | N | 0
2025-05-11 | 10 | 2031-05-11 10:00 | 15.31 | 20.1147 | N | 0
2025-05-11 | 11 | 2031-05-11 11:00 | 15.5 | 20.3644 | N | 0
2025-05-11 | 12 | 2031-05-11 12:00 | 15.75 | 20.6928 | N | 0
2025-05-11 | 13 | 2031-05-11 13:00 | 15.64 | 20.5483 | N | 0
2025-05-11 | 14 | 2031-05-11 14:00 | 15.2 | 19.9702 | N | 0
2025-05-11 | 15 | 2031-05-11 15:00 | 15.63 | 20.5352 | N | 0
2025-05-11 | 16 | 2031-05-11 16:00 | 16.6 | 21.8096 | N | 0
2025-05-11 | 17 | 2031-05-11 17:00 | 17.41 | 22.8738 | N | 0
2025-05-11 | 18 | 2031-05-11 18:00 | 17.49 | 22.9789 | N | 0
2025-05-11 | 19 | 2031-05-11 19:00 | 17.72 | 23.2811 | N | 0
2025-05-11 | 20 | 2031-05-11 20:00 | 17.93 | 23.557 | N | 0
2025-05-11 | 21 | 2031-05-11 21:00 | 18.18 | 23.8854 | N | 0
2025-05-11 | 22 | 2031-05-11 22:00 | 17.09 | 22.4534 | N | 0
2025-05-11 | 23 | 2031-05-11 23:00 | 14.87 | 19.5366 | N | 0
2025-05-12 | 00 | 2031-05-12 | 13.14 | 17.2637 | N | 0
2025-05-12 | 01 | 2031-05-12 01:00 | 11.9 | 15.6346 | N | 0
2025-05-12 | 02 | 2031-05-12 02:00 | 11.34 | 14.8988 | N | 0
2025-05-12 | 03 | 2031-05-12 03:00 | 10.98 | 14.4259 | N | 0
2025-05-12 | 04 | 2031-05-12 04:00 | 11.23 | 14.7543 | N | 0
2025-05-12 | 05 | 2031-05-12 05:00 | 12.12 | 15.9236 | N | 0
2025-05-12 | 06 | 2031-05-12 06:00 | 14.06 | 18.4724 | N | 0
2025-05-12 | 07 | 2031-05-12 07:00 | 16.23 | 21.3235 | N | 0
2025-05-12 | 08 | 2031-05-12 08:00 | 16.71 | 21.9541 | N | 0
2025-05-12 | 09 | 2031-05-12 09:00 | 16.88 | 22.1774 | N | 0
2025-05-12 | 10 | 2031-05-12 10:00 | 16.97 | 22.2957 | N | 0
2025-05-12 | 11 | 2031-05-12 11:00 | 17.25 | 22.6636 | N | 0
2025-05-12 | 12 | 2031-05-12 12:00 | 17.04 | 22.3877 | N | 0
2025-05-12 | 13 | 2031-05-12 13:00 | 17.18 | 22.5716 | N | 0
2025-05-12 | 14 | 2031-05-12 14:00 | 16.81 | 22.0855 | N | 0
2025-05-12 | 15 | 2031-05-12 15:00 | 17.13 | 22.5059 | N | 0
2025-05-12 | 16 | 2031-05-12 16:00 | 17.9 | 23.5176 | N | 0
2025-05-12 | 17 | 2031-05-12 17:00 | 18.58 | 24.411 | N | 0
2025-05-12 | 18 | 2031-05-12 18:00 | 18.27 | 24.0037 | N | 0
2025-05-12 | 19 | 2031-05-12 19:00 | 18.05 | 23.7146 | N | 0
2025-05-12 | 20 | 2031-05-12 20:00 | 17.93 | 23.557 | N | 0
2025-05-12 | 21 | 2031-05-12 21:00 | 18.11 | 23.7935 | N | 0
2025-05-12 | 22 | 2031-05-12 22:00 | 17.03 | 22.3745 | N | 0
2025-05-12 | 23 | 2031-05-12 23:00 | 14.74 | 19.3659 | N | 0
2025-05-13 | 00 | 2031-05-13 | 13.14 | 17.2637 | N | 0
2025-05-13 | 01 | 2031-05-13 01:00 | 12.1 | 15.8973 | N | 0
2025-05-13 | 02 | 2031-05-13 02:00 | 11.36 | 14.9251 | N | 0
2025-05-13 | 03 | 2031-05-13 03:00 | 11.03 | 14.4915 | N | 0
2025-05-13 | 04 | 2031-05-13 04:00 | 11.03 | 14.4915 | N | 0
2025-05-13 | 05 | 2031-05-13 05:00 | 11.61 | 15.2536 | N | 0
2025-05-13 | 06 | 2031-05-13 06:00 | 13.64 | 17.9206 | N | 0
2025-05-13 | 07 | 2031-05-13 07:00 | 15.77 | 20.7191 | N | 0
2025-05-13 | 08 | 2031-05-13 08:00 | 16.42 | 21.5731 | N | 0
2025-05-13 | 09 | 2031-05-13 09:00 | 16.83 | 22.1118 | N | 0
2025-05-13 | 10 | 2031-05-13 10:00 | 17.32 | 22.7555 | N | 0
2025-05-13 | 11 | 2031-05-13 11:00 | 17.96 | 23.5964 | N | 0
2025-05-13 | 12 | 2031-05-13 12:00 | 18.04 | 23.7015 | N | 0
2025-05-13 | 13 | 2031-05-13 13:00 | 18.42 | 24.2007 | N | 0
2025-05-13 | 14 | 2031-05-13 14:00 | 18.53 | 24.3453 | N | 0
2025-05-13 | 15 | 2031-05-13 15:00 | 18.53 | 24.3453 | N | 0
2025-05-13 | 16 | 2031-05-13 16:00 | 19.43 | 25.5277 | N | 0
2025-05-13 | 17 | 2031-05-13 17:00 | 19.7 | 25.8824 | N | 0
2025-05-13 | 18 | 2031-05-13 18:00 | 20 | 26.2766 | N | 0
2025-05-13 | 19 | 2031-05-13 19:00 | 18.9 | 24.8314 | N | 0
2025-05-13 | 20 | 2031-05-13 20:00 | 19.09 | 25.081 | N | 0
2025-05-13 | 21 | 2031-05-13 21:00 | 18.78 | 24.6737 | N | 0
2025-05-13 | 22 | 2031-05-13 22:00 | 17.55 | 23.0577 | N | 0
2025-05-13 | 23 | 2031-05-13 23:00 | 15.53 | 20.4038 | N | 0
2025-05-14 | 00 | 2031-05-14 | 13.81 | 18.144 | N | 0
2025-05-14 | 01 | 2031-05-14 01:00 | 12.51 | 16.436 | N | 0
2025-05-14 | 02 | 2031-05-14 02:00 | 11.94 | 15.6871 | N | 0
2025-05-14 | 03 | 2031-05-14 03:00 | 11.68 | 15.3455 | N | 0
2025-05-14 | 04 | 2031-05-14 04:00 | 11.35 | 14.912 | N | 0
2025-05-14 | 05 | 2031-05-14 05:00 | 11.9 | 15.6346 | N | 0
2025-05-14 | 06 | 2031-05-14 06:00 | 14.05 | 18.4593 | N | 0
2025-05-14 | 07 | 2031-05-14 07:00 | 16.99 | 22.322 | N | 0
2025-05-14 | 08 | 2031-05-14 08:00 | 17.48 | 22.9657 | N | 0
2025-05-14 | 09 | 2031-05-14 09:00 | 17.77 | 23.3468 | N | 0
2025-05-14 | 10 | 2031-05-14 10:00 | 18.05 | 23.7146 | N | 0
2025-05-14 | 11 | 2031-05-14 11:00 | 18.69 | 24.5555 | N | 0
2025-05-14 | 12 | 2031-05-14 12:00 | 18.82 | 24.7263 | N | 0
2025-05-14 | 13 | 2031-05-14 13:00 | 18.84 | 24.7526 | N | 0
2025-05-14 | 14 | 2031-05-14 14:00 | 19.08 | 25.0679 | N | 0
2025-05-14 | 15 | 2031-05-14 15:00 | 19.16 | 25.173 | N | 0
2025-05-14 | 16 | 2031-05-14 16:00 | 19.04 | 25.0153 | N | 0
2025-05-14 | 17 | 2031-05-14 17:00 | 19.51 | 25.6328 | N | 0
2025-05-14 | 18 | 2031-05-14 18:00 | 19.56 | 25.6985 | N | 0
2025-05-14 | 19 | 2031-05-14 19:00 | 19.02 | 24.989 | N | 0
2025-05-14 | 20 | 2031-05-14 20:00 | 18.75 | 24.6343 | N | 0
2025-05-14 | 21 | 2031-05-14 21:00 | 18.75 | 24.6343 | N | 0
2025-05-14 | 22 | 2031-05-14 22:00 | 17.57 | 23.084 | N | 0
2025-05-14 | 23 | 2031-05-14 23:00 | 15.84 | 20.8111 | N | 0
2025-05-15 | 00 | 2031-05-15 | 13.75 | 18.0652 | N | 0
2025-05-15 | 01 | 2031-05-15 01:00 | 12.5 | 16.4229 | N | 0
2025-05-15 | 02 | 2031-05-15 02:00 | 11.67 | 15.3324 | N | 0
2025-05-15 | 03 | 2031-05-15 03:00 | 11.21 | 14.728 | N | 0
2025-05-15 | 04 | 2031-05-15 04:00 | 11.26 | 14.7937 | N | 0
2025-05-15 | 05 | 2031-05-15 05:00 | 11.63 | 15.2798 | N | 0
2025-05-15 | 06 | 2031-05-15 06:00 | 14.02 | 18.4199 | N | 0
2025-05-15 | 07 | 2031-05-15 07:00 | 16.19 | 21.2709 | N | 0
2025-05-15 | 08 | 2031-05-15 08:00 | 16.98 | 22.3088 | N | 0
2025-05-15 | 09 | 2031-05-15 09:00 | 17.32 | 22.7555 | N | 0
2025-05-15 | 10 | 2031-05-15 10:00 | 17.64 | 23.176 | N | 0
2025-05-15 | 11 | 2031-05-15 11:00 | 18.02 | 23.6752 | N | 0
2025-05-15 | 12 | 2031-05-15 12:00 | 18.25 | 23.9774 | N | 0
2025-05-15 | 13 | 2031-05-15 13:00 | 18.71 | 24.5818 | N | 0
2025-05-15 | 14 | 2031-05-15 14:00 | 19.36 | 25.4357 | N | 0
2025-05-15 | 15 | 2031-05-15 15:00 | 19.17 | 25.1861 | N | 0
2025-05-15 | 16 | 2031-05-15 16:00 | 19.78 | 25.9876 | N | 0
2025-05-15 | 17 | 2031-05-15 17:00 | 21.01 | 27.6036 | N | 0
2025-05-15 | 18 | 2031-05-15 18:00 | 20.68 | 27.17 | N | 0
2025-05-15 | 19 | 2031-05-15 19:00 | 19.72 | 25.9087 | N | 0
2025-05-15 | 20 | 2031-05-15 20:00 | 19.81 | 26.027 | N | 0
2025-05-15 | 21 | 2031-05-15 21:00 | 20.16 | 26.4868 | N | 0
2025-05-15 | 22 | 2031-05-15 22:00 | 19.32 | 25.3832 | N | 0
2025-05-15 | 23 | 2031-05-15 23:00 | 16.46 | 21.6256 | N | 0
2025-05-16 | 00 | 2031-05-16 | 14.67 | 19.2739 | N | 0
2025-05-16 | 01 | 2031-05-16 01:00 | 12.86 | 16.8959 | N | 0
2025-05-16 | 02 | 2031-05-16 02:00 | 12.07 | 15.8579 | N | 0
2025-05-16 | 03 | 2031-05-16 03:00 | 11.36 | 14.9251 | N | 0
2025-05-16 | 04 | 2031-05-16 04:00 | 11.03 | 14.4915 | N | 0
2025-05-16 | 05 | 2031-05-16 05:00 | 11.56 | 15.1879 | N | 0
2025-05-16 | 06 | 2031-05-16 06:00 | 13.32 | 17.5002 | N | 0
2025-05-16 | 07 | 2031-05-16 07:00 | 15.77 | 20.7191 | N | 0
2025-05-16 | 08 | 2031-05-16 08:00 | 16.72 | 21.9672 | N | 0
2025-05-16 | 09 | 2031-05-16 09:00 | 17.7 | 23.2548 | N | 0
2025-05-16 | 10 | 2031-05-16 10:00 | 18.8 | 24.7 | N | 0
2025-05-16 | 11 | 2031-05-16 11:00 | 18.97 | 24.9234 | N | 0
2025-05-16 | 12 | 2031-05-16 12:00 | 19.31 | 25.3701 | N | 0
2025-05-16 | 13 | 2031-05-16 13:00 | 19.82 | 26.0401 | N | 0
2025-05-16 | 14 | 2031-05-16 14:00 | 20.17 | 26.4999 | N | 0
2025-05-16 | 15 | 2031-05-16 15:00 | 20.51 | 26.9466 | N | 0
2025-05-16 | 16 | 2031-05-16 16:00 | 20.95 | 27.5247 | N | 0
2025-05-16 | 17 | 2031-05-16 17:00 | 21.53 | 28.2868 | N | 0
2025-05-16 | 18 | 2031-05-16 18:00 | 21.91 | 28.786 | N | 0
2025-05-16 | 19 | 2031-05-16 19:00 | 20.94 | 27.5116 | N | 0
2025-05-16 | 20 | 2031-05-16 20:00 | 20.22 | 26.5656 | N | 0
2025-05-16 | 21 | 2031-05-16 21:00 | 20.23 | 26.5788 | N | 0
2025-05-16 | 22 | 2031-05-16 22:00 | 19.38 | 25.462 | N | 0
2025-05-16 | 23 | 2031-05-16 23:00 | 17.42 | 22.8869 | N | 0
2025-05-17 | 00 | 2031-05-17 | 15.64 | 20.5483 | N | 0
2025-05-17 | 01 | 2031-05-17 01:00 | 13.67 | 17.9601 | N | 0
2025-05-17 | 02 | 2031-05-17 02:00 | 12.22 | 16.055 | N | 0
2025-05-17 | 03 | 2031-05-17 03:00 | 11.72 | 15.3981 | N | 0
2025-05-17 | 04 | 2031-05-17 04:00 | 11.25 | 14.7806 | N | 0
2025-05-17 | 05 | 2031-05-17 05:00 | 10.99 | 14.439 | N | 0
2025-05-17 | 06 | 2031-05-17 06:00 | 11.39 | 14.9645 | N | 0
2025-05-17 | 07 | 2031-05-17 07:00 | 12.8 | 16.817 | N | 0
2025-05-17 | 08 | 2031-05-17 08:00 | 14.77 | 19.4053 | N | 0
2025-05-17 | 09 | 2031-05-17 09:00 | 16.01 | 21.0344 | N | 0
2025-05-17 | 10 | 2031-05-17 10:00 | 16.75 | 22.0066 | N | 0
2025-05-17 | 11 | 2031-05-17 11:00 | 17 | 22.3351 | N | 0
2025-05-17 | 12 | 2031-05-17 12:00 | 17.74 | 23.3073 | N | 0
2025-05-17 | 13 | 2031-05-17 13:00 | 17.83 | 23.4256 | N | 0
2025-05-17 | 14 | 2031-05-17 14:00 | 18.04 | 23.7015 | N | 0
2025-05-17 | 15 | 2031-05-17 15:00 | 17.84 | 23.4387 | N | 0
2025-05-17 | 16 | 2031-05-17 16:00 | 17.9 | 23.5176 | N | 0
2025-05-17 | 17 | 2031-05-17 17:00 | 18 | 23.6489 | N | 0
2025-05-17 | 18 | 2031-05-17 18:00 | 17.88 | 23.4913 | N | 0
2025-05-17 | 19 | 2031-05-17 19:00 | 16.97 | 22.2957 | N | 0
2025-05-17 | 20 | 2031-05-17 20:00 | 16.93 | 22.2431 | N | 0
2025-05-17 | 21 | 2031-05-17 21:00 | 17.03 | 22.3745 | N | 0
2025-05-17 | 22 | 2031-05-17 22:00 | 16.11 | 21.1658 | N | 0
2025-05-17 | 23 | 2031-05-17 23:00 | 14.68 | 19.287 | N | 0
2025-05-18 | 00 | 2031-05-18 | 13.08 | 17.1849 | N | 0
2025-05-18 | 01 | 2031-05-18 01:00 | 12.18 | 16.0024 | N | 0
2025-05-18 | 02 | 2031-05-18 02:00 | 11.22 | 14.7412 | N | 0
2025-05-18 | 03 | 2031-05-18 03:00 | 10.66 | 14.0054 | N | 0
2025-05-18 | 04 | 2031-05-18 04:00 | 10.49 | 13.7821 | N | 0
2025-05-18 | 05 | 2031-05-18 05:00 | 10.56 | 13.874 | N | 0
2025-05-18 | 06 | 2031-05-18 06:00 | 10.99 | 14.439 | N | 0
2025-05-18 | 07 | 2031-05-18 07:00 | 12.01 | 15.7791 | N | 0
2025-05-18 | 08 | 2031-05-18 08:00 | 13.22 | 17.3688 | N | 0
2025-05-18 | 09 | 2031-05-18 09:00 | 14.88 | 19.5498 | N | 0
2025-05-18 | 10 | 2031-05-18 10:00 | 15.35 | 20.1673 | N | 0
2025-05-18 | 11 | 2031-05-18 11:00 | 16.14 | 21.2052 | N | 0
2025-05-18 | 12 | 2031-05-18 12:00 | 16.17 | 21.2446 | N | 0
2025-05-18 | 13 | 2031-05-18 13:00 | 16.2 | 21.284 | N | 0
2025-05-18 | 14 | 2031-05-18 14:00 | 15.95 | 20.9556 | N | 0
2025-05-18 | 15 | 2031-05-18 15:00 | 15.98 | 20.995 | N | 0
2025-05-18 | 16 | 2031-05-18 16:00 | 16.78 | 22.0461 | N | 0
2025-05-18 | 17 | 2031-05-18 17:00 | 17.34 | 22.7818 | N | 0
2025-05-18 | 18 | 2031-05-18 18:00 | 17.41 | 22.8738 | N | 0
2025-05-18 | 19 | 2031-05-18 19:00 | 17.05 | 22.4008 | N | 0
2025-05-18 | 20 | 2031-05-18 20:00 | 16.4 | 21.5468 | N | 0
2025-05-18 | 21 | 2031-05-18 21:00 | 16.52 | 21.7045 | N | 0
2025-05-18 | 22 | 2031-05-18 22:00 | 15.58 | 20.4695 | N | 0
2025-05-18 | 23 | 2031-05-18 23:00 | 14.38 | 18.8929 | N | 0
2025-05-19 | 00 | 2031-05-19 | 13.02 | 17.1061 | N | 0
2025-05-19 | 01 | 2031-05-19 01:00 | 12.09 | 15.8842 | N | 0
2025-05-19 | 02 | 2031-05-19 02:00 | 11.08 | 14.5572 | N | 0
2025-05-19 | 03 | 2031-05-19 03:00 | 10.66 | 14.0054 | N | 0
2025-05-19 | 04 | 2031-05-19 04:00 | 10.54 | 13.8478 | N | 0
2025-05-19 | 05 | 2031-05-19 05:00 | 10.63 | 13.966 | N | 0
2025-05-19 | 06 | 2031-05-19 06:00 | 11.33 | 14.8857 | N | 0
2025-05-19 | 07 | 2031-05-19 07:00 | 12.53 | 16.4623 | N | 0
2025-05-19 | 08 | 2031-05-19 08:00 | 13.85 | 18.1965 | N | 0
2025-05-19 | 09 | 2031-05-19 09:00 | 15.05 | 19.7731 | N | 0
2025-05-19 | 10 | 2031-05-19 10:00 | 16.02 | 21.0476 | N | 0
2025-05-19 | 11 | 2031-05-19 11:00 | 16.54 | 21.7307 | N | 0
2025-05-19 | 12 | 2031-05-19 12:00 | 17.03 | 22.3745 | N | 0
2025-05-19 | 13 | 2031-05-19 13:00 | 16.8 | 22.0723 | N | 0
2025-05-19 | 14 | 2031-05-19 14:00 | 16.92 | 22.23 | N | 0
2025-05-19 | 15 | 2031-05-19 15:00 | 16.75 | 22.0066 | N | 0
2025-05-19 | 16 | 2031-05-19 16:00 | 18.04 | 23.7015 | N | 0
2025-05-19 | 17 | 2031-05-19 17:00 | 18.87 | 24.792 | N | 0
2025-05-19 | 18 | 2031-05-19 18:00 | 18.9 | 24.8314 | N | 0
2025-05-19 | 19 | 2031-05-19 19:00 | 18.36 | 24.1219 | N | 0
2025-05-19 | 20 | 2031-05-19 20:00 | 18.37 | 24.1351 | N | 0
2025-05-19 | 21 | 2031-05-19 21:00 | 18.3 | 24.0431 | N | 0
2025-05-19 | 22 | 2031-05-19 22:00 | 16.95 | 22.2694 | N | 0
2025-05-19 | 23 | 2031-05-19 23:00 | 14.95 | 19.6418 | N | 0
2025-05-20 | 00 | 2031-05-20 | 13.17 | 17.3031 | N | 0
2025-05-20 | 01 | 2031-05-20 01:00 | 11.72 | 15.3981 | N | 0
2025-05-20 | 02 | 2031-05-20 02:00 | 11.19 | 14.7018 | N | 0
2025-05-20 | 03 | 2031-05-20 03:00 | 10.96 | 14.3996 | N | 0
2025-05-20 | 04 | 2031-05-20 04:00 | 11.09 | 14.5704 | N | 0
2025-05-20 | 05 | 2031-05-20 05:00 | 11.63 | 15.2798 | N | 0
2025-05-20 | 06 | 2031-05-20 06:00 | 13.81 | 18.144 | N | 0
2025-05-20 | 07 | 2031-05-20 07:00 | 15.81 | 20.7716 | N | 0
2025-05-20 | 08 | 2031-05-20 08:00 | 16.51 | 21.6913 | N | 0
2025-05-20 | 09 | 2031-05-20 09:00 | 16.84 | 22.1249 | N | 0
2025-05-20 | 10 | 2031-05-20 10:00 | 17.05 | 22.4008 | N | 0
2025-05-20 | 11 | 2031-05-20 11:00 | 17.23 | 22.6373 | N | 0
2025-05-20 | 12 | 2031-05-20 12:00 | 17.14 | 22.519 | N | 0
2025-05-20 | 13 | 2031-05-20 13:00 | 17.33 | 22.7687 | N | 0
2025-05-20 | 14 | 2031-05-20 14:00 | 16.93 | 22.2431 | N | 0
2025-05-20 | 15 | 2031-05-20 15:00 | 16.86 | 22.1512 | N | 0
2025-05-20 | 16 | 2031-05-20 16:00 | 17.57 | 23.084 | N | 0
2025-05-20 | 17 | 2031-05-20 17:00 | 18.29 | 24.0299 | N | 0
2025-05-20 | 18 | 2031-05-20 18:00 | 18.3 | 24.0431 | N | 0
2025-05-20 | 19 | 2031-05-20 19:00 | 17.68 | 23.2285 | N | 0
2025-05-20 | 20 | 2031-05-20 20:00 | 18.17 | 23.8723 | N | 0
2025-05-20 | 21 | 2031-05-20 21:00 | 18.19 | 23.8986 | N | 0
2025-05-20 | 22 | 2031-05-20 22:00 | 17.02 | 22.3614 | N | 0
2025-05-20 | 23 | 2031-05-20 23:00 | 15.02 | 19.7337 | N | 0
2025-05-21 | 00 | 2031-05-21 | 13.77 | 18.0914 | N | 0
2025-05-21 | 01 | 2031-05-21 01:00 | 12.54 | 16.4754 | N | 0
2025-05-21 | 02 | 2031-05-21 02:00 | 11.62 | 15.2667 | N | 0
2025-05-21 | 03 | 2031-05-21 03:00 | 11.26 | 14.7937 | N | 0
2025-05-21 | 04 | 2031-05-21 04:00 | 11.35 | 14.912 | N | 0
2025-05-21 | 05 | 2031-05-21 05:00 | 12.09 | 15.8842 | N | 0
2025-05-21 | 06 | 2031-05-21 06:00 | 13.91 | 18.2754 | N | 0
2025-05-21 | 07 | 2031-05-21 07:00 | 16.13 | 21.1921 | N | 0
2025-05-21 | 08 | 2031-05-21 08:00 | 16.58 | 21.7833 | N | 0
2025-05-21 | 09 | 2031-05-21 09:00 | 16.75 | 22.0066 | N | 0
2025-05-21 | 10 | 2031-05-21 10:00 | 17.38 | 22.8344 | N | 0
2025-05-21 | 11 | 2031-05-21 11:00 | 17.83 | 23.4256 | N | 0
2025-05-21 | 12 | 2031-05-21 12:00 | 18 | 23.6489 | N | 0
2025-05-21 | 13 | 2031-05-21 13:00 | 18.27 | 24.0037 | N | 0
2025-05-21 | 14 | 2031-05-21 14:00 | 18.38 | 24.1482 | N | 0
2025-05-21 | 15 | 2031-05-21 15:00 | 18.41 | 24.1876 | N | 0
2025-05-21 | 16 | 2031-05-21 16:00 | 19.39 | 25.4752 | N | 0
2025-05-21 | 17 | 2031-05-21 17:00 | 20.48 | 26.9072 | N | 0
2025-05-21 | 18 | 2031-05-21 18:00 | 20.33 | 26.7102 | N | 0
2025-05-21 | 19 | 2031-05-21 19:00 | 19.44 | 25.5409 | N | 0
2025-05-21 | 20 | 2031-05-21 20:00 | 19.29 | 25.3438 | N | 0
2025-05-21 | 21 | 2031-05-21 21:00 | 19.4 | 25.4883 | N | 0
2025-05-21 | 22 | 2031-05-21 22:00 | 17.79 | 23.373 | N | 0
2025-05-21 | 23 | 2031-05-21 23:00 | 15.62 | 20.522 | N | 0
2025-05-22 | 00 | 2031-05-22 | 14.22 | 18.6827 | N | 0
2025-05-22 | 01 | 2031-05-22 01:00 | 9.94 | 13.0595 | N | 0
2025-05-22 | 02 | 2031-05-22 02:00 | 9.35 | 12.2843 | N | 0
2025-05-22 | 03 | 2031-05-22 03:00 | 14.32 | 18.814 | N | 0
2025-05-22 | 04 | 2031-05-22 04:00 | 12.33 | 16.1995 | N | 0
2025-05-22 | 05 | 2031-05-22 05:00 | 12.89 | 16.9353 | N | 0
2025-05-22 | 06 | 2031-05-22 06:00 | 14.8 | 19.4447 | N | 0
2025-05-22 | 07 | 2031-05-22 07:00 | 17.08 | 22.4402 | N | 0
2025-05-22 | 08 | 2031-05-22 08:00 | 17.72 | 23.2811 | N | 0
2025-05-22 | 09 | 2031-05-22 09:00 | 18.11 | 23.7935 | N | 0
2025-05-22 | 10 | 2031-05-22 10:00 | 18.97 | 24.9234 | N | 0
2025-05-22 | 11 | 2031-05-22 11:00 | 18.94 | 24.8839 | N | 0
2025-05-22 | 12 | 2031-05-22 12:00 | 19.2 | 25.2255 | N | 0
2025-05-22 | 13 | 2031-05-22 13:00 | 19.06 | 25.0416 | N | 0
2025-05-22 | 14 | 2031-05-22 14:00 | 19.01 | 24.9759 | N | 0
2025-05-22 | 15 | 2031-05-22 15:00 | 19.49 | 25.6065 | N | 0
2025-05-22 | 16 | 2031-05-22 16:00 | 20.32 | 26.697 | N | 0
2025-05-22 | 17 | 2031-05-22 17:00 | 20.95 | 27.5247 | N | 0
2025-05-22 | 18 | 2031-05-22 18:00 | 20.65 | 27.1306 | N | 0
2025-05-22 | 19 | 2031-05-22 19:00 | 19.7 | 25.8824 | N | 0
2025-05-22 | 20 | 2031-05-22 20:00 | 19.57 | 25.7116 | N | 0
2025-05-22 | 21 | 2031-05-22 21:00 | 19.41 | 25.5014 | N | 0
2025-05-22 | 22 | 2031-05-22 22:00 | 18.3 | 24.0431 | N | 0
2025-05-22 | 23 | 2031-05-22 23:00 | 16.04 | 21.0738 | N | 0
2025-05-23 | 00 | 2031-05-23 | 14.37 | 18.8797 | N | 0
2025-05-23 | 01 | 2031-05-23 01:00 | 13 | 17.0798 | N | 0
2025-05-23 | 02 | 2031-05-23 02:00 | 12.47 | 16.3835 | N | 0
2025-05-23 | 03 | 2031-05-23 03:00 | 12.04 | 15.8185 | N | 0
2025-05-23 | 04 | 2031-05-23 04:00 | 11.93 | 15.674 | N | 0
2025-05-23 | 05 | 2031-05-23 05:00 | 12.41 | 16.3046 | N | 0
2025-05-23 | 06 | 2031-05-23 06:00 | 14.36 | 18.8666 | N | 0
2025-05-23 | 07 | 2031-05-23 07:00 | 16.45 | 21.6125 | N | 0
2025-05-23 | 08 | 2031-05-23 08:00 | 17.14 | 22.519 | N | 0
2025-05-23 | 09 | 2031-05-23 09:00 | 17.7 | 23.2548 | N | 0
2025-05-23 | 10 | 2031-05-23 10:00 | 17.92 | 23.5438 | N | 0
2025-05-23 | 11 | 2031-05-23 11:00 | 17.92 | 23.5438 | N | 0
2025-05-23 | 12 | 2031-05-23 12:00 | 17.9 | 23.5176 | N | 0
2025-05-23 | 13 | 2031-05-23 13:00 | 17.92 | 23.5438 | N | 0
2025-05-23 | 14 | 2031-05-23 14:00 | 17.66 | 23.2022 | N | 0
2025-05-23 | 15 | 2031-05-23 15:00 | 17.84 | 23.4387 | N | 0
2025-05-23 | 16 | 2031-05-23 16:00 | 18.46 | 24.2533 | N | 0
2025-05-23 | 17 | 2031-05-23 17:00 | 18.84 | 24.7526 | N | 0
2025-05-23 | 18 | 2031-05-23 18:00 | 18.88 | 24.8051 | N | 0
2025-05-23 | 19 | 2031-05-23 19:00 | 17.83 | 23.4256 | N | 0
2025-05-23 | 20 | 2031-05-23 20:00 | 17.97 | 23.6095 | N | 0
2025-05-23 | 21 | 2031-05-23 21:00 | 18.01 | 23.6621 | N | 0
2025-05-23 | 22 | 2031-05-23 22:00 | 17.21 | 22.611 | N | 0
2025-05-23 | 23 | 2031-05-23 23:00 | 15.89 | 20.8768 | N | 0
2025-05-24 | 00 | 2031-05-24 | 14.62 | 19.2082 | N | 0
2025-05-24 | 01 | 2031-05-24 01:00 | 13.21 | 17.3557 | N | 0
2025-05-24 | 02 | 2031-05-24 02:00 | 12.42 | 16.3178 | N | 0
2025-05-24 | 03 | 2031-05-24 03:00 | 11.86 | 15.582 | N | 0
2025-05-24 | 04 | 2031-05-24 04:00 | 11.7 | 15.3718 | N | 0
2025-05-24 | 05 | 2031-05-24 05:00 | 11.84 | 15.5557 | N | 0
2025-05-24 | 06 | 2031-05-24 06:00 | 12.5 | 16.4229 | N | 0
2025-05-24 | 07 | 2031-05-24 07:00 | 13.97 | 18.3542 | N | 0
2025-05-24 | 08 | 2031-05-24 08:00 | 15.29 | 20.0885 | N | 0
2025-05-24 | 09 | 2031-05-24 09:00 | 16.38 | 21.5205 | N | 0
2025-05-24 | 10 | 2031-05-24 10:00 | 16.95 | 22.2694 | N | 0
2025-05-24 | 11 | 2031-05-24 11:00 | 17.43 | 22.9001 | N | 0
2025-05-24 | 12 | 2031-05-24 12:00 | 17.45 | 22.9263 | N | 0
2025-05-24 | 13 | 2031-05-24 13:00 | 17.36 | 22.8081 | N | 0
2025-05-24 | 14 | 2031-05-24 14:00 | 16.96 | 22.2826 | N | 0
2025-05-24 | 15 | 2031-05-24 15:00 | 17.2 | 22.5979 | N | 0
2025-05-24 | 16 | 2031-05-24 16:00 | 17.38 | 22.8344 | N | 0
2025-05-24 | 17 | 2031-05-24 17:00 | 17.71 | 23.2679 | N | 0
2025-05-24 | 18 | 2031-05-24 18:00 | 17.82 | 23.4124 | N | 0
2025-05-24 | 19 | 2031-05-24 19:00 | 17.03 | 22.3745 | N | 0
2025-05-24 | 20 | 2031-05-24 20:00 | 16.96 | 22.2826 | N | 0
2025-05-24 | 21 | 2031-05-24 21:00 | 17.31 | 22.7424 | N | 0
2025-05-24 | 22 | 2031-05-24 22:00 | 16.55 | 21.7439 | N | 0
2025-05-24 | 23 | 2031-05-24 23:00 | 15.25 | 20.0359 | N | 0
2025-05-25 | 00 | 2031-05-25 | 13.92 | 18.2885 | N | 0
2025-05-25 | 01 | 2031-05-25 01:00 | 12.65 | 16.6199 | N | 0
2025-05-25 | 02 | 2031-05-25 02:00 | 11.89 | 15.6214 | N | 0
2025-05-25 | 03 | 2031-05-25 03:00 | 11.49 | 15.0959 | N | 0
2025-05-25 | 04 | 2031-05-25 04:00 | 11.32 | 14.8726 | N | 0
2025-05-25 | 05 | 2031-05-25 05:00 | 11.32 | 14.8726 | N | 0
2025-05-25 | 06 | 2031-05-25 06:00 | 11.64 | 15.293 | N | 0
2025-05-25 | 07 | 2031-05-25 07:00 | 12.96 | 17.0272 | N | 0
2025-05-25 | 08 | 2031-05-25 08:00 | 14.07 | 18.4856 | N | 0
2025-05-25 | 09 | 2031-05-25 09:00 | 15.21 | 19.9834 | N | 0
2025-05-25 | 10 | 2031-05-25 10:00 | 15.93 | 20.9293 | N | 0
2025-05-25 | 11 | 2031-05-25 11:00 | 16.99 | 22.322 | N | 0
2025-05-25 | 12 | 2031-05-25 12:00 | 17.23 | 22.6373 | N | 0
2025-05-25 | 13 | 2031-05-25 13:00 | 17.5 | 22.992 | N | 0
2025-05-25 | 14 | 2031-05-25 14:00 | 17.41 | 22.8738 | N | 0
2025-05-25 | 15 | 2031-05-25 15:00 | 17.67 | 23.2154 | N | 0
2025-05-25 | 16 | 2031-05-25 16:00 | 18.3 | 24.0431 | N | 0
2025-05-25 | 17 | 2031-05-25 17:00 | 19.35 | 25.4226 | N | 0
2025-05-25 | 18 | 2031-05-25 18:00 | 19.2 | 25.2255 | N | 0
2025-05-25 | 19 | 2031-05-25 19:00 | 18.82 | 24.7263 | N | 0
2025-05-25 | 20 | 2031-05-25 20:00 | 18.48 | 24.2796 | N | 0
2025-05-25 | 21 | 2031-05-25 21:00 | 18.09 | 23.7672 | N | 0
2025-05-25 | 22 | 2031-05-25 22:00 | 17.07 | 22.4271 | N | 0
2025-05-25 | 23 | 2031-05-25 23:00 | 14.94 | 19.6286 | N | 0
2025-05-26 | 00 | 2031-05-26 | 13.1 | 17.2112 | N | 0
2025-05-26 | 01 | 2031-05-26 01:00 | 12 | 15.766 | N | 0
2025-05-26 | 02 | 2031-05-26 02:00 | 11.37 | 14.9382 | N | 0
2025-05-26 | 03 | 2031-05-26 03:00 | 11.23 | 14.7543 | N | 0
2025-05-26 | 04 | 2031-05-26 04:00 | 11.35 | 14.912 | N | 0
2025-05-26 | 05 | 2031-05-26 05:00 | 11.92 | 15.6609 | N | 0
2025-05-26 | 06 | 2031-05-26 06:00 | 13.67 | 17.9601 | N | 0
2025-05-26 | 07 | 2031-05-26 07:00 | 15.68 | 20.6009 | N | 0
2025-05-26 | 08 | 2031-05-26 08:00 | 16.4 | 21.5468 | N | 0
2025-05-26 | 09 | 2031-05-26 09:00 | 16.74 | 21.9935 | N | 0
2025-05-26 | 10 | 2031-05-26 10:00 | 17.32 | 22.7555 | N | 0
2025-05-26 | 11 | 2031-05-26 11:00 | 17.46 | 22.9395 | N | 0
2025-05-26 | 12 | 2031-05-26 12:00 | 17.7 | 23.2548 | N | 0
2025-05-26 | 13 | 2031-05-26 13:00 | 17.55 | 23.0577 | N | 0
2025-05-26 | 14 | 2031-05-26 14:00 | 18.26 | 23.9905 | N | 0
2025-05-26 | 15 | 2031-05-26 15:00 | 17.88 | 23.4913 | N | 0
2025-05-26 | 16 | 2031-05-26 16:00 | 18.78 | 24.6737 | N | 0
2025-05-26 | 17 | 2031-05-26 17:00 | 19.82 | 26.0401 | N | 0
2025-05-26 | 18 | 2031-05-26 18:00 | 19.65 | 25.8168 | N | 0
2025-05-26 | 19 | 2031-05-26 19:00 | 18.64 | 24.4898 | N | 0
2025-05-26 | 20 | 2031-05-26 20:00 | 18.45 | 24.2402 | N | 0
2025-05-26 | 21 | 2031-05-26 21:00 | 18.57 | 24.3978 | N | 0
2025-05-26 | 22 | 2031-05-26 22:00 | 17.78 | 23.3599 | N | 0
2025-05-26 | 23 | 2031-05-26 23:00 | 15.78 | 20.7322 | N | 0
2025-05-27 | 00 | 2031-05-27 | 13.62 | 17.8944 | N | 0
2025-05-27 | 01 | 2031-05-27 01:00 | 12.33 | 16.1995 | N | 0
2025-05-27 | 02 | 2031-05-27 02:00 | 11.57 | 15.201 | N | 0
2025-05-27 | 03 | 2031-05-27 03:00 | 11.33 | 14.8857 | N | 0
2025-05-27 | 04 | 2031-05-27 04:00 | 11.31 | 14.8594 | N | 0
2025-05-27 | 05 | 2031-05-27 05:00 | 11.97 | 15.7265 | N | 0
2025-05-27 | 06 | 2031-05-27 06:00 | 13.94 | 18.3148 | N | 0
2025-05-27 | 07 | 2031-05-27 07:00 | 16.08 | 21.1264 | N | 0
2025-05-27 | 08 | 2031-05-27 08:00 | 16.63 | 21.849 | N | 0
2025-05-27 | 09 | 2031-05-27 09:00 | 17.51 | 23.0052 | N | 0
2025-05-27 | 10 | 2031-05-27 10:00 | 17.89 | 23.5044 | N | 0
2025-05-27 | 11 | 2031-05-27 11:00 | 18.2 | 23.9117 | N | 0
2025-05-27 | 12 | 2031-05-27 12:00 | 18.33 | 24.0825 | N | 0
2025-05-27 | 13 | 2031-05-27 13:00 | 18.56 | 24.3847 | N | 0
2025-05-27 | 14 | 2031-05-27 14:00 | 18.6 | 24.4372 | N | 0
2025-05-27 | 15 | 2031-05-27 15:00 | 18.95 | 24.8971 | N | 0
2025-05-27 | 16 | 2031-05-27 16:00 | 19.53 | 25.6591 | N | 0
2025-05-27 | 17 | 2031-05-27 17:00 | 20.32 | 26.697 | N | 0
2025-05-27 | 18 | 2031-05-27 18:00 | 20.22 | 26.5656 | N | 0
2025-05-27 | 19 | 2031-05-27 19:00 | 19.39 | 25.4752 | N | 0
2025-05-27 | 20 | 2031-05-27 20:00 | 18.86 | 24.7788 | N | 0
2025-05-27 | 21 | 2031-05-27 21:00 | 19.29 | 25.3438 | N | 0
2025-05-27 | 22 | 2031-05-27 22:00 | 18.36 | 24.1219 | N | 0
2025-05-27 | 23 | 2031-05-27 23:00 | 15.89 | 20.8768 | N | 0
2025-05-28 | 00 | 2031-05-28 | 14.06 | 18.4724 | N | 0
2025-05-28 | 01 | 2031-05-28 01:00 | 12.48 | 16.3966 | N | 0
2025-05-28 | 02 | 2031-05-28 02:00 | 11.73 | 15.4112 | N | 0
2025-05-28 | 03 | 2031-05-28 03:00 | 11.32 | 14.8726 | N | 0
2025-05-28 | 04 | 2031-05-28 04:00 | 11.26 | 14.7937 | N | 0
2025-05-28 | 05 | 2031-05-28 05:00 | 11.77 | 15.4638 | N | 0
2025-05-28 | 06 | 2031-05-28 06:00 | 13.97 | 18.3542 | N | 0
2025-05-28 | 07 | 2031-05-28 07:00 | 16.5 | 21.6782 | N | 0
2025-05-28 | 08 | 2031-05-28 08:00 | 17.01 | 22.3482 | N | 0
2025-05-28 | 09 | 2031-05-28 09:00 | 17.67 | 23.2154 | N | 0
2025-05-28 | 10 | 2031-05-28 10:00 | 18.45 | 24.2402 | N | 0
2025-05-28 | 11 | 2031-05-28 11:00 | 19.03 | 25.0022 | N | 0
2025-05-28 | 12 | 2031-05-28 12:00 | 19.02 | 24.989 | N | 0
2025-05-28 | 13 | 2031-05-28 13:00 | 19.11 | 25.1073 | N | 0
2025-05-28 | 14 | 2031-05-28 14:00 | 19.38 | 25.462 | N | 0
2025-05-28 | 15 | 2031-05-28 15:00 | 18.88 | 24.8051 | N | 0
2025-05-28 | 16 | 2031-05-28 16:00 | 18.99 | 24.9496 | N | 0
2025-05-28 | 17 | 2031-05-28 17:00 | 19.61 | 25.7642 | N | 0
2025-05-28 | 18 | 2031-05-28 18:00 | 19.5 | 25.6197 | N | 0
2025-05-28 | 19 | 2031-05-28 19:00 | 18.93 | 24.8708 | N | 0
2025-05-28 | 20 | 2031-05-28 20:00 | 19.42 | 25.5146 | N | 0
2025-05-28 | 21 | 2031-05-28 21:00 | 18.9 | 24.8314 | N | 0
2025-05-28 | 22 | 2031-05-28 22:00 | 17.69 | 23.2416 | N | 0
2025-05-28 | 23 | 2031-05-28 23:00 | 15.41 | 20.2461 | N | 0
2025-05-29 | 00 | 2031-05-29 | 13.87 | 18.2228 | N | 0
2025-05-29 | 01 | 2031-05-29 01:00 | 12.6 | 16.5543 | N | 0
2025-05-29 | 02 | 2031-05-29 02:00 | 11.88 | 15.6083 | N | 0
2025-05-29 | 03 | 2031-05-29 03:00 | 11.42 | 15.0039 | N | 0
2025-05-29 | 04 | 2031-05-29 04:00 | 11.57 | 15.201 | N | 0
2025-05-29 | 05 | 2031-05-29 05:00 | 12.14 | 15.9499 | N | 0
2025-05-29 | 06 | 2031-05-29 06:00 | 14.47 | 19.0111 | N | 0
2025-05-29 | 07 | 2031-05-29 07:00 | 16.17 | 21.2446 | N | 0
2025-05-29 | 08 | 2031-05-29 08:00 | 17.15 | 22.5322 | N | 0
2025-05-29 | 09 | 2031-05-29 09:00 | 17.69 | 23.2416 | N | 0
2025-05-29 | 10 | 2031-05-29 10:00 | 18.28 | 24.0168 | N | 0
2025-05-29 | 11 | 2031-05-29 11:00 | 18.26 | 23.9905 | N | 0
2025-05-29 | 12 | 2031-05-29 12:00 | 18.39 | 24.1613 | N | 0
2025-05-29 | 13 | 2031-05-29 13:00 | 18.27 | 24.0037 | N | 0
2025-05-29 | 14 | 2031-05-29 14:00 | 18.32 | 24.0694 | N | 0
2025-05-29 | 15 | 2031-05-29 15:00 | 17.99 | 23.6358 | N | 0
2025-05-29 | 16 | 2031-05-29 16:00 | 18.42 | 24.2007 | N | 0
2025-05-29 | 17 | 2031-05-29 17:00 | 19.01 | 24.9759 | N | 0
2025-05-29 | 18 | 2031-05-29 18:00 | 18.72 | 24.5949 | N | 0
2025-05-29 | 19 | 2031-05-29 19:00 | 18.56 | 24.3847 | N | 0
2025-05-29 | 20 | 2031-05-29 20:00 | 18.72 | 24.5949 | N | 0
2025-05-29 | 21 | 2031-05-29 21:00 | 18.61 | 24.4504 | N | 0
2025-05-29 | 22 | 2031-05-29 22:00 | 17.52 | 23.0183 | N | 0
2025-05-29 | 23 | 2031-05-29 23:00 | 15.7 | 20.6271 | N | 0
2025-05-30 | 00 | 2031-05-30 | 14.04 | 18.4462 | N | 0
2025-05-30 | 01 | 2031-05-30 01:00 | 12.61 | 16.5674 | N | 0
2025-05-30 | 02 | 2031-05-30 02:00 | 11.91 | 15.6477 | N | 0
2025-05-30 | 03 | 2031-05-30 03:00 | 11.45 | 15.0434 | N | 0
2025-05-30 | 04 | 2031-05-30 04:00 | 11.3 | 14.8463 | N | 0
2025-05-30 | 05 | 2031-05-30 05:00 | 12.11 | 15.9105 | N | 0
2025-05-30 | 06 | 2031-05-30 06:00 | 13.62 | 17.8944 | N | 0
2025-05-30 | 07 | 2031-05-30 07:00 | 15.56 | 20.4432 | N | 0
2025-05-30 | 08 | 2031-05-30 08:00 | 16.61 | 21.8227 | N | 0
2025-05-30 | 09 | 2031-05-30 09:00 | 17.17 | 22.5585 | N | 0
2025-05-30 | 10 | 2031-05-30 10:00 | 17.98 | 23.6227 | N | 0
2025-05-30 | 11 | 2031-05-30 11:00 | 18.13 | 23.8197 | N | 0
2025-05-30 | 12 | 2031-05-30 12:00 | 18.34 | 24.0956 | N | 0
2025-05-30 | 13 | 2031-05-30 13:00 | 18.14 | 23.8329 | N | 0
2025-05-30 | 14 | 2031-05-30 14:00 | 18.25 | 23.9774 | N | 0
2025-05-30 | 15 | 2031-05-30 15:00 | 18.6 | 24.4372 | N | 0
2025-05-30 | 16 | 2031-05-30 16:00 | 18.5 | 24.3059 | N | 0
2025-05-30 | 17 | 2031-05-30 17:00 | 19.18 | 25.1993 | N | 0
2025-05-30 | 18 | 2031-05-30 18:00 | 19.17 | 25.1861 | N | 0
2025-05-30 | 19 | 2031-05-30 19:00 | 18.55 | 24.3715 | N | 0
2025-05-30 | 20 | 2031-05-30 20:00 | 17.98 | 23.6227 | N | 0
2025-05-30 | 21 | 2031-05-30 21:00 | 17.82 | 23.4124 | N | 0
2025-05-30 | 22 | 2031-05-30 22:00 | 17.2 | 22.5979 | N | 0
2025-05-30 | 23 | 2031-05-30 23:00 | 15.68 | 20.6009 | N | 0
2025-05-31 | 00 | 2031-05-31 | 13.98 | 18.3673 | N | 0
2025-05-31 | 01 | 2031-05-31 01:00 | 12.82 | 16.8433 | N | 0
2025-05-31 | 02 | 2031-05-31 02:00 | 11.82 | 15.5295 | N | 0
2025-05-31 | 03 | 2031-05-31 03:00 | 11.35 | 14.912 | N | 0
2025-05-31 | 04 | 2031-05-31 04:00 | 11.06 | 14.531 | N | 0
2025-05-31 | 05 | 2031-05-31 05:00 | 10.97 | 14.4127 | N | 0
2025-05-31 | 06 | 2031-05-31 06:00 | 11.31 | 14.8594 | N | 0
2025-05-31 | 07 | 2031-05-31 07:00 | 12.76 | 16.7645 | N | 0
2025-05-31 | 08 | 2031-05-31 08:00 | 14.29 | 18.7746 | N | 0
2025-05-31 | 09 | 2031-05-31 09:00 | 15.67 | 20.5877 | N | 0
2025-05-31 | 10 | 2031-05-31 10:00 | 16.3 | 21.4154 | N | 0
2025-05-31 | 11 | 2031-05-31 11:00 | 16.91 | 22.2169 | N | 0
2025-05-31 | 12 | 2031-05-31 12:00 | 16.86 | 22.1512 | N | 0
2025-05-31 | 13 | 2031-05-31 13:00 | 16.81 | 22.0855 | N | 0
2025-05-31 | 14 | 2031-05-31 14:00 | 16.53 | 21.7176 | N | 0
2025-05-31 | 15 | 2031-05-31 15:00 | 16.64 | 21.8621 | N | 0
2025-05-31 | 16 | 2031-05-31 16:00 | 17.09 | 22.4534 | N | 0
2025-05-31 | 17 | 2031-05-31 17:00 | 17.15 | 22.5322 | N | 0
2025-05-31 | 18 | 2031-05-31 18:00 | 17.5 | 22.992 | N | 0
2025-05-31 | 19 | 2031-05-31 19:00 | 17.23 | 22.6373 | N | 0
2025-05-31 | 20 | 2031-05-31 20:00 | 16.9 | 22.2037 | N | 0
2025-05-31 | 21 | 2031-05-31 21:00 | 16.91 | 22.2169 | N | 0
2025-05-31 | 22 | 2031-05-31 22:00 | 16.1 | 21.1527 | N | 0
2025-05-31 | 23 | 2031-05-31 23:00 | 14.68 | 19.287 | N | 0
2025-06-01 | 00 | 2031-06-01 | 10.65 | 13.9923 | N | 0
2025-06-01 | 01 | 2031-06-01 01:00 | 0 | 0 | N | 0
2025-06-01 | 02 | 2031-06-01 02:00 | 0 | 0 | N | 0
2025-06-01 | 03 | 2031-06-01 03:00 | 0 | 0 | N | 0
2025-06-01 | 04 | 2031-06-01 04:00 | 0 | 0 | N | 0
2025-06-01 | 05 | 2031-06-01 05:00 | 0 | 0 | N | 0
2025-06-01 | 06 | 2031-06-01 06:00 | 0 | 0 | N | 0
2025-06-01 | 07 | 2031-06-01 07:00 | 0 | 0 | N | 0
2025-06-01 | 08 | 2031-06-01 08:00 | 0 | 0 | N | 0
2025-06-01 | 09 | 2031-06-01 09:00 | 0 | 0 | N | 0
2025-06-01 | 10 | 2031-06-01 10:00 | 0 | 0 | N | 0
2025-06-01 | 11 | 2031-06-01 11:00 | 0 | 0 | N | 0
2025-06-01 | 12 | 2031-06-01 12:00 | 0 | 0 | N | 0
2025-06-01 | 13 | 2031-06-01 13:00 | 0 | 0 | N | 0
2025-06-01 | 14 | 2031-06-01 14:00 | 0 | 0 | N | 0
2025-06-01 | 15 | 2031-06-01 15:00 | 0 | 0 | N | 0
2025-06-01 | 16 | 2031-06-01 16:00 | 0 | 0 | N | 0
2025-06-01 | 17 | 2031-06-01 17:00 | 0 | 0 | N | 0
2025-06-01 | 18 | 2031-06-01 18:00 | 0 | 0 | N | 0
2025-06-01 | 19 | 2031-06-01 19:00 | 0 | 0 | N | 0
2025-06-01 | 20 | 2031-06-01 20:00 | 0 | 0 | N | 0
2025-06-01 | 21 | 2031-06-01 21:00 | 0 | 0 | N | 0
2025-06-01 | 22 | 2031-06-01 22:00 | 0 | 0 | N | 0
2025-06-01 | 23 | 2031-06-01 23:00 | 0 | 0 | N | 0
2025-06-02 | 00 | 2031-06-02 | 0 | 0 | N | 0
2025-06-02 | 01 | 2031-06-02 01:00 | 0 | 0 | N | 0
2025-06-02 | 02 | 2031-06-02 02:00 | 0 | 0 | N | 0
2025-06-02 | 03 | 2031-06-02 03:00 | 0 | 0 | N | 0
2025-06-02 | 04 | 2031-06-02 04:00 | 0 | 0 | N | 0
2025-06-02 | 05 | 2031-06-02 05:00 | 0 | 0 | N | 0
2025-06-02 | 06 | 2031-06-02 06:00 | 0 | 0 | N | 0
2025-06-02 | 07 | 2031-06-02 07:00 | 0 | 0 | N | 0
2025-06-02 | 08 | 2031-06-02 08:00 | 0 | 0 | N | 0
2025-06-02 | 09 | 2031-06-02 09:00 | 0 | 0 | N | 0
2025-06-02 | 10 | 2031-06-02 10:00 | 0 | 0 | N | 0
2025-06-02 | 11 | 2031-06-02 11:00 | 0 | 0 | N | 0
2025-06-02 | 12 | 2031-06-02 12:00 | 0 | 0 | N | 0
2025-06-02 | 13 | 2031-06-02 13:00 | 0 | 0 | N | 0
2025-06-02 | 14 | 2031-06-02 14:00 | 0 | 0 | N | 0
2025-06-02 | 15 | 2031-06-02 15:00 | 0 | 0 | N | 0
2025-06-02 | 16 | 2031-06-02 16:00 | 0 | 0 | N | 0
2025-06-02 | 17 | 2031-06-02 17:00 | 0 | 0 | N | 0
2025-06-02 | 18 | 2031-06-02 18:00 | 0 | 0 | N | 0
2025-06-02 | 19 | 2031-06-02 19:00 | 0 | 0 | N | 0
2025-06-02 | 20 | 2031-06-02 20:00 | 0 | 0 | N | 0
2025-06-02 | 21 | 2031-06-02 21:00 | 0 | 0 | N | 0
2025-06-02 | 22 | 2031-06-02 22:00 | 0 | 0 | N | 0
2025-06-02 | 23 | 2031-06-02 23:00 | 0 | 0 | N | 0
2025-06-03 | 00 | 2031-06-03 | 0 | 0 | N | 0
2025-06-03 | 01 | 2031-06-03 01:00 | 0 | 0 | N | 0
2025-06-03 | 02 | 2031-06-03 02:00 | 0 | 0 | N | 0
2025-06-03 | 03 | 2031-06-03 03:00 | 0 | 0 | N | 0
2025-06-03 | 04 | 2031-06-03 04:00 | 0 | 0 | N | 0
2025-06-03 | 05 | 2031-06-03 05:00 | 0 | 0 | N | 0
2025-06-03 | 06 | 2031-06-03 06:00 | 0 | 0 | N | 0
2025-06-03 | 07 | 2031-06-03 07:00 | 0 | 0 | N | 0
2025-06-03 | 08 | 2031-06-03 08:00 | 0 | 0 | N | 0
2025-06-03 | 09 | 2031-06-03 09:00 | 0 | 0 | N | 0
2025-06-03 | 10 | 2031-06-03 10:00 | 0 | 0 | N | 0
2025-06-03 | 11 | 2031-06-03 11:00 | 0 | 0 | N | 0
2025-06-03 | 12 | 2031-06-03 12:00 | 0 | 0 | N | 0
2025-06-03 | 13 | 2031-06-03 13:00 | 0 | 0 | N | 0
2025-06-03 | 14 | 2031-06-03 14:00 | 0 | 0 | N | 0
2025-06-03 | 15 | 2031-06-03 15:00 | 0 | 0 | N | 0
2025-06-03 | 16 | 2031-06-03 16:00 | 0 | 0 | N | 0
2025-06-03 | 17 | 2031-06-03 17:00 | 0 | 0 | N | 0
2025-06-03 | 18 | 2031-06-03 18:00 | 0 | 0 | N | 0
2025-06-03 | 19 | 2031-06-03 19:00 | 0 | 0 | N | 0
2025-06-03 | 20 | 2031-06-03 20:00 | 0 | 0 | N | 0
2025-06-03 | 21 | 2031-06-03 21:00 | 0 | 0 | N | 0
2025-06-03 | 22 | 2031-06-03 22:00 | 0 | 0 | N | 0
2025-06-03 | 23 | 2031-06-03 23:00 | 0 | 0 | N | 0
2025-06-04 | 00 | 2031-06-04 | 0 | 0 | N | 0
2025-06-04 | 01 | 2031-06-04 01:00 | 0 | 0 | N | 0
2025-06-04 | 02 | 2031-06-04 02:00 | 0 | 0 | N | 0
2025-06-04 | 03 | 2031-06-04 03:00 | 0 | 0 | N | 0
2025-06-04 | 04 | 2031-06-04 04:00 | 0 | 0 | N | 0
2025-06-04 | 05 | 2031-06-04 05:00 | 0 | 0 | N | 0
2025-06-04 | 06 | 2031-06-04 06:00 | 0 | 0 | N | 0
2025-06-04 | 07 | 2031-06-04 07:00 | 0 | 0 | N | 0
2025-06-04 | 08 | 2031-06-04 08:00 | 0 | 0 | N | 0
2025-06-04 | 09 | 2031-06-04 09:00 | 0 | 0 | N | 0
2025-06-04 | 10 | 2031-06-04 10:00 | 0 | 0 | N | 0
2025-06-04 | 11 | 2031-06-04 11:00 | 0 | 0 | N | 0
2025-06-04 | 12 | 2031-06-04 12:00 | 0 | 0 | N | 0
2025-06-04 | 13 | 2031-06-04 13:00 | 0 | 0 | N | 0
2025-06-04 | 14 | 2031-06-04 14:00 | 0 | 0 | N | 0
2025-06-04 | 15 | 2031-06-04 15:00 | 0 | 0 | N | 0
2025-06-04 | 16 | 2031-06-04 16:00 | 0 | 0 | N | 0
2025-06-04 | 17 | 2031-06-04 17:00 | 0 | 0 | N | 0
2025-06-04 | 18 | 2031-06-04 18:00 | 0 | 0 | N | 0
2025-06-04 | 19 | 2031-06-04 19:00 | 0 | 0 | N | 0
2025-06-04 | 20 | 2031-06-04 20:00 | 0 | 0 | N | 0
2025-06-04 | 21 | 2031-06-04 21:00 | 0 | 0 | N | 0
2025-06-04 | 22 | 2031-06-04 22:00 | 0 | 0 | N | 0
2025-06-04 | 23 | 2031-06-04 23:00 | 0 | 0 | N | 0
2025-06-05 | 00 | 2031-06-05 | 0 | 0 | N | 0
2025-06-05 | 01 | 2031-06-05 01:00 | 0 | 0 | N | 0
2025-06-05 | 02 | 2031-06-05 02:00 | 0 | 0 | N | 0
2025-06-05 | 03 | 2031-06-05 03:00 | 0 | 0 | N | 0
2025-06-05 | 04 | 2031-06-05 04:00 | 0 | 0 | N | 0
2025-06-05 | 05 | 2031-06-05 05:00 | 0 | 0 | N | 0
2025-06-05 | 06 | 2031-06-05 06:00 | 0 | 0 | N | 0
2025-06-05 | 07 | 2031-06-05 07:00 | 0 | 0 | N | 0
2025-06-05 | 08 | 2031-06-05 08:00 | 0 | 0 | N | 0
2025-06-05 | 09 | 2031-06-05 09:00 | 0 | 0 | N | 0
2025-06-05 | 10 | 2031-06-05 10:00 | 0 | 0 | N | 0
2025-06-05 | 11 | 2031-06-05 11:00 | 0 | 0 | N | 0
2025-06-05 | 12 | 2031-06-05 12:00 | 0 | 0 | N | 0
2025-06-05 | 13 | 2031-06-05 13:00 | 0 | 0 | N | 0
2025-06-05 | 14 | 2031-06-05 14:00 | 0 | 0 | N | 0
2025-06-05 | 15 | 2031-06-05 15:00 | 0 | 0 | N | 0
2025-06-05 | 16 | 2031-06-05 16:00 | 0 | 0 | N | 0
2025-06-05 | 17 | 2031-06-05 17:00 | 0 | 0 | N | 0
2025-06-05 | 18 | 2031-06-05 18:00 | 0 | 0 | N | 0
2025-06-05 | 19 | 2031-06-05 19:00 | 0 | 0 | N | 0
2025-06-05 | 20 | 2031-06-05 20:00 | 0 | 0 | N | 0
2025-06-05 | 21 | 2031-06-05 21:00 | 0 | 0 | N | 0
2025-06-05 | 22 | 2031-06-05 22:00 | 0 | 0 | N | 0
2025-06-05 | 23 | 2031-06-05 23:00 | 0 | 0 | N | 0
2025-06-06 | 00 | 2031-06-06 | 0 | 0 | N | 0
2025-06-06 | 01 | 2031-06-06 01:00 | 0 | 0 | N | 0
2025-06-06 | 02 | 2031-06-06 02:00 | 0 | 0 | N | 0
2025-06-06 | 03 | 2031-06-06 03:00 | 0 | 0 | N | 0
2025-06-06 | 04 | 2031-06-06 04:00 | 0 | 0 | N | 0
2025-06-06 | 05 | 2031-06-06 05:00 | 0 | 0 | N | 0
2025-06-06 | 06 | 2031-06-06 06:00 | 0 | 0 | N | 0
2025-06-06 | 07 | 2031-06-06 07:00 | 0 | 0 | N | 0
2025-06-06 | 08 | 2031-06-06 08:00 | 0 | 0 | N | 0
2025-06-06 | 09 | 2031-06-06 09:00 | 0 | 0 | N | 0
2025-06-06 | 10 | 2031-06-06 10:00 | 0 | 0 | N | 0
2025-06-06 | 11 | 2031-06-06 11:00 | 0 | 0 | N | 0
2025-06-06 | 12 | 2031-06-06 12:00 | 0 | 0 | N | 0
2025-06-06 | 13 | 2031-06-06 13:00 | 0 | 0 | N | 0
2025-06-06 | 14 | 2031-06-06 14:00 | 0 | 0 | N | 0
2025-06-06 | 15 | 2031-06-06 15:00 | 0 | 0 | N | 0
2025-06-06 | 16 | 2031-06-06 16:00 | 0 | 0 | N | 0
2025-06-06 | 17 | 2031-06-06 17:00 | 0 | 0 | N | 0
2025-06-06 | 18 | 2031-06-06 18:00 | 0 | 0 | N | 0
2025-06-06 | 19 | 2031-06-06 19:00 | 0 | 0 | N | 0
2025-06-06 | 20 | 2031-06-06 20:00 | 0 | 0 | N | 0
2025-06-06 | 21 | 2031-06-06 21:00 | 0 | 0 | N | 0
2025-06-06 | 22 | 2031-06-06 22:00 | 0 | 0 | N | 0
2025-06-06 | 23 | 2031-06-06 23:00 | 0 | 0 | N | 0
2025-06-07 | 00 | 2031-06-07 | 0 | 0 | N | 0
2025-06-07 | 01 | 2031-06-07 01:00 | 0 | 0 | N | 0
2025-06-07 | 02 | 2031-06-07 02:00 | 0 | 0 | N | 0
2025-06-07 | 03 | 2031-06-07 03:00 | 0 | 0 | N | 0
2025-06-07 | 04 | 2031-06-07 04:00 | 0 | 0 | N | 0
2025-06-07 | 05 | 2031-06-07 05:00 | 0 | 0 | N | 0
2025-06-07 | 06 | 2031-06-07 06:00 | 0 | 0 | N | 0
2025-06-07 | 07 | 2031-06-07 07:00 | 0 | 0 | N | 0
2025-06-07 | 08 | 2031-06-07 08:00 | 0 | 0 | N | 0
2025-06-07 | 09 | 2031-06-07 09:00 | 0 | 0 | N | 0
2025-06-07 | 10 | 2031-06-07 10:00 | 0 | 0 | N | 0
2025-06-07 | 11 | 2031-06-07 11:00 | 0 | 0 | N | 0
2025-06-07 | 12 | 2031-06-07 12:00 | 0 | 0 | N | 0
2025-06-07 | 13 | 2031-06-07 13:00 | 0 | 0 | N | 0
2025-06-07 | 14 | 2031-06-07 14:00 | 0 | 0 | N | 0
2025-06-07 | 15 | 2031-06-07 15:00 | 0 | 0 | N | 0
2025-06-07 | 16 | 2031-06-07 16:00 | 0 | 0 | N | 0
2025-06-07 | 17 | 2031-06-07 17:00 | 0 | 0 | N | 0
2025-06-07 | 18 | 2031-06-07 18:00 | 0 | 0 | N | 0
2025-06-07 | 19 | 2031-06-07 19:00 | 0 | 0 | N | 0
2025-06-07 | 20 | 2031-06-07 20:00 | 0 | 0 | N | 0
2025-06-07 | 21 | 2031-06-07 21:00 | 0 | 0 | N | 0
2025-06-07 | 22 | 2031-06-07 22:00 | 0 | 0 | N | 0
2025-06-07 | 23 | 2031-06-07 23:00 | 0 | 0 | N | 0
2025-06-08 | 00 | 2031-06-08 | 0 | 0 | N | 0
2025-06-08 | 01 | 2031-06-08 01:00 | 0 | 0 | N | 0
2025-06-08 | 02 | 2031-06-08 02:00 | 0 | 0 | N | 0
2025-06-08 | 03 | 2031-06-08 03:00 | 0 | 0 | N | 0
2025-06-08 | 04 | 2031-06-08 04:00 | 0 | 0 | N | 0
2025-06-08 | 05 | 2031-06-08 05:00 | 0 | 0 | N | 0
2025-06-08 | 06 | 2031-06-08 06:00 | 0 | 0 | N | 0
2025-06-08 | 07 | 2031-06-08 07:00 | 0 | 0 | N | 0
2025-06-08 | 08 | 2031-06-08 08:00 | 0 | 0 | N | 0
2025-06-08 | 09 | 2031-06-08 09:00 | 0 | 0 | N | 0
2025-06-08 | 10 | 2031-06-08 10:00 | 0 | 0 | N | 0
2025-06-08 | 11 | 2031-06-08 11:00 | 0 | 0 | N | 0
2025-06-08 | 12 | 2031-06-08 12:00 | 0 | 0 | N | 0
2025-06-08 | 13 | 2031-06-08 13:00 | 0 | 0 | N | 0
2025-06-08 | 14 | 2031-06-08 14:00 | 0 | 0 | N | 0
2025-06-08 | 15 | 2031-06-08 15:00 | 0 | 0 | N | 0
2025-06-08 | 16 | 2031-06-08 16:00 | 0 | 0 | N | 0
2025-06-08 | 17 | 2031-06-08 17:00 | 0 | 0 | N | 0
2025-06-08 | 18 | 2031-06-08 18:00 | 0 | 0 | N | 0
2025-06-08 | 19 | 2031-06-08 19:00 | 0 | 0 | N | 0
2025-06-08 | 20 | 2031-06-08 20:00 | 0 | 0 | N | 0
2025-06-08 | 21 | 2031-06-08 21:00 | 0 | 0 | N | 0
2025-06-08 | 22 | 2031-06-08 22:00 | 0 | 0 | N | 0
2025-06-08 | 23 | 2031-06-08 23:00 | 0 | 0 | N | 0
2025-06-09 | 00 | 2031-06-09 | 0 | 0 | N | 0
2025-06-09 | 01 | 2031-06-09 01:00 | 0 | 0 | N | 0
2025-06-09 | 02 | 2031-06-09 02:00 | 0 | 0 | N | 0
2025-06-09 | 03 | 2031-06-09 03:00 | 0 | 0 | N | 0
2025-06-09 | 04 | 2031-06-09 04:00 | 0 | 0 | N | 0
2025-06-09 | 05 | 2031-06-09 05:00 | 0 | 0 | N | 0
2025-06-09 | 06 | 2031-06-09 06:00 | 0 | 0 | N | 0
2025-06-09 | 07 | 2031-06-09 07:00 | 0 | 0 | N | 0
2025-06-09 | 08 | 2031-06-09 08:00 | 0 | 0 | N | 0
2025-06-09 | 09 | 2031-06-09 09:00 | 0 | 0 | N | 0
2025-06-09 | 10 | 2031-06-09 10:00 | 0 | 0 | N | 0
2025-06-09 | 11 | 2031-06-09 11:00 | 0 | 0 | N | 0
2025-06-09 | 12 | 2031-06-09 12:00 | 0 | 0 | N | 0
2025-06-09 | 13 | 2031-06-09 13:00 | 0 | 0 | N | 0
2025-06-09 | 14 | 2031-06-09 14:00 | 0 | 0 | N | 0
2025-06-09 | 15 | 2031-06-09 15:00 | 0 | 0 | N | 0
2025-06-09 | 16 | 2031-06-09 16:00 | 0 | 0 | N | 0
2025-06-09 | 17 | 2031-06-09 17:00 | 0 | 0 | N | 0
2025-06-09 | 18 | 2031-06-09 18:00 | 0 | 0 | N | 0
2025-06-09 | 19 | 2031-06-09 19:00 | 0 | 0 | N | 0
2025-06-09 | 20 | 2031-06-09 20:00 | 0 | 0 | N | 0
2025-06-09 | 21 | 2031-06-09 21:00 | 0 | 0 | N | 0
2025-06-09 | 22 | 2031-06-09 22:00 | 0 | 0 | N | 0
2025-06-09 | 23 | 2031-06-09 23:00 | 0 | 0 | N | 0
2025-06-10 | 00 | 2031-06-10 | 0 | 0 | N | 0
2025-06-10 | 01 | 2031-06-10 01:00 | 0 | 0 | N | 0
2025-06-10 | 02 | 2031-06-10 02:00 | 0 | 0 | N | 0
2025-06-10 | 03 | 2031-06-10 03:00 | 0 | 0 | N | 0
2025-06-10 | 04 | 2031-06-10 04:00 | 0 | 0 | N | 0
2025-06-10 | 05 | 2031-06-10 05:00 | 0 | 0 | N | 0
2025-06-10 | 06 | 2031-06-10 06:00 | 0 | 0 | N | 0
2025-06-10 | 07 | 2031-06-10 07:00 | 0 | 0 | N | 0
2025-06-10 | 08 | 2031-06-10 08:00 | 0 | 0 | N | 0
2025-06-10 | 09 | 2031-06-10 09:00 | 0 | 0 | N | 0
2025-06-10 | 10 | 2031-06-10 10:00 | 0 | 0 | N | 0
2025-06-10 | 11 | 2031-06-10 11:00 | 0 | 0 | N | 0
2025-06-10 | 12 | 2031-06-10 12:00 | 0 | 0 | N | 0
2025-06-10 | 13 | 2031-06-10 13:00 | 0 | 0 | N | 0
2025-06-10 | 14 | 2031-06-10 14:00 | 0 | 0 | N | 0
2025-06-10 | 15 | 2031-06-10 15:00 | 0 | 0 | N | 0
2025-06-10 | 16 | 2031-06-10 16:00 | 0 | 0 | N | 0
2025-06-10 | 17 | 2031-06-10 17:00 | 0 | 0 | N | 0
2025-06-10 | 18 | 2031-06-10 18:00 | 0 | 0 | N | 0
2025-06-10 | 19 | 2031-06-10 19:00 | 0 | 0 | N | 0
2025-06-10 | 20 | 2031-06-10 20:00 | 0 | 0 | N | 0
2025-06-10 | 21 | 2031-06-10 21:00 | 0 | 0 | N | 0
2025-06-10 | 22 | 2031-06-10 22:00 | 0 | 0 | N | 0
2025-06-10 | 23 | 2031-06-10 23:00 | 0 | 0 | N | 0
2025-06-11 | 00 | 2031-06-11 | 0 | 0 | N | 0
2025-06-11 | 01 | 2031-06-11 01:00 | 0 | 0 | N | 0
2025-06-11 | 02 | 2031-06-11 02:00 | 0 | 0 | N | 0
2025-06-11 | 03 | 2031-06-11 03:00 | 0 | 0 | N | 0
2025-06-11 | 04 | 2031-06-11 04:00 | 0 | 0 | N | 0
2025-06-11 | 05 | 2031-06-11 05:00 | 0 | 0 | N | 0
2025-06-11 | 06 | 2031-06-11 06:00 | 0 | 0 | N | 0
2025-06-11 | 07 | 2031-06-11 07:00 | 0 | 0 | N | 0
2025-06-11 | 08 | 2031-06-11 08:00 | 0 | 0 | N | 0
2025-06-11 | 09 | 2031-06-11 09:00 | 0 | 0 | N | 0
2025-06-11 | 10 | 2031-06-11 10:00 | 0 | 0 | N | 0
2025-06-11 | 11 | 2031-06-11 11:00 | 0 | 0 | N | 0
2025-06-11 | 12 | 2031-06-11 12:00 | 0 | 0 | N | 0
2025-06-11 | 13 | 2031-06-11 13:00 | 0 | 0 | N | 0
2025-06-11 | 14 | 2031-06-11 14:00 | 0 | 0 | N | 0
2025-06-11 | 15 | 2031-06-11 15:00 | 0 | 0 | N | 0
2025-06-11 | 16 | 2031-06-11 16:00 | 0 | 0 | N | 0
2025-06-11 | 17 | 2031-06-11 17:00 | 0 | 0 | N | 0
2025-06-11 | 18 | 2031-06-11 18:00 | 0 | 0 | N | 0
2025-06-11 | 19 | 2031-06-11 19:00 | 0 | 0 | N | 0
2025-06-11 | 20 | 2031-06-11 20:00 | 0 | 0 | N | 0
2025-06-11 | 21 | 2031-06-11 21:00 | 0 | 0 | N | 0
2025-06-11 | 22 | 2031-06-11 22:00 | 0 | 0 | N | 0
2025-06-11 | 23 | 2031-06-11 23:00 | 0 | 0 | N | 0
2025-06-12 | 00 | 2031-06-12 | 0 | 0 | N | 0
2025-06-12 | 01 | 2031-06-12 01:00 | 0 | 0 | N | 0
2025-06-12 | 02 | 2031-06-12 02:00 | 0 | 0 | N | 0
2025-06-12 | 03 | 2031-06-12 03:00 | 0 | 0 | N | 0
2025-06-12 | 04 | 2031-06-12 04:00 | 0 | 0 | N | 0
2025-06-12 | 05 | 2031-06-12 05:00 | 0 | 0 | N | 0
2025-06-12 | 06 | 2031-06-12 06:00 | 0 | 0 | N | 0
2025-06-12 | 07 | 2031-06-12 07:00 | 0 | 0 | N | 0
2025-06-12 | 08 | 2031-06-12 08:00 | 0 | 0 | N | 0
2025-06-12 | 09 | 2031-06-12 09:00 | 0 | 0 | N | 0
2025-06-12 | 10 | 2031-06-12 10:00 | 0 | 0 | N | 0
2025-06-12 | 11 | 2031-06-12 11:00 | 0 | 0 | N | 0
2025-06-12 | 12 | 2031-06-12 12:00 | 0 | 0 | N | 0
2025-06-12 | 13 | 2031-06-12 13:00 | 0 | 0 | N | 0
2025-06-12 | 14 | 2031-06-12 14:00 | 0 | 0 | N | 0
2025-06-12 | 15 | 2031-06-12 15:00 | 0 | 0 | N | 0
2025-06-12 | 16 | 2031-06-12 16:00 | 0 | 0 | N | 0
2025-06-12 | 17 | 2031-06-12 17:00 | 0 | 0 | N | 0
2025-06-12 | 18 | 2031-06-12 18:00 | 0 | 0 | N | 0
2025-06-12 | 19 | 2031-06-12 19:00 | 0 | 0 | N | 0
2025-06-12 | 20 | 2031-06-12 20:00 | 0 | 0 | N | 0
2025-06-12 | 21 | 2031-06-12 21:00 | 0 | 0 | N | 0
2025-06-12 | 22 | 2031-06-12 22:00 | 0 | 0 | N | 0
2025-06-12 | 23 | 2031-06-12 23:00 | 0 | 0 | N | 0
2025-06-13 | 00 | 2031-06-13 | 0 | 0 | N | 0
2025-06-13 | 01 | 2031-06-13 01:00 | 0 | 0 | N | 0
2025-06-13 | 02 | 2031-06-13 02:00 | 0 | 0 | N | 0
2025-06-13 | 03 | 2031-06-13 03:00 | 0 | 0 | N | 0
2025-06-13 | 04 | 2031-06-13 04:00 | 0 | 0 | N | 0
2025-06-13 | 05 | 2031-06-13 05:00 | 0 | 0 | N | 0
2025-06-13 | 06 | 2031-06-13 06:00 | 0 | 0 | N | 0
2025-06-13 | 07 | 2031-06-13 07:00 | 0 | 0 | N | 0
2025-06-13 | 08 | 2031-06-13 08:00 | 0 | 0 | N | 0
2025-06-13 | 09 | 2031-06-13 09:00 | 0 | 0 | N | 0
2025-06-13 | 10 | 2031-06-13 10:00 | 0 | 0 | N | 0
2025-06-13 | 11 | 2031-06-13 11:00 | 0 | 0 | N | 0
2025-06-13 | 12 | 2031-06-13 12:00 | 0 | 0 | N | 0
2025-06-13 | 13 | 2031-06-13 13:00 | 0 | 0 | N | 0
2025-06-13 | 14 | 2031-06-13 14:00 | 0 | 0 | N | 0
2025-06-13 | 15 | 2031-06-13 15:00 | 0 | 0 | N | 0
2025-06-13 | 16 | 2031-06-13 16:00 | 0 | 0 | N | 0
2025-06-13 | 17 | 2031-06-13 17:00 | 0 | 0 | N | 0
2025-06-13 | 18 | 2031-06-13 18:00 | 0 | 0 | N | 0
2025-06-13 | 19 | 2031-06-13 19:00 | 0 | 0 | N | 0
2025-06-13 | 20 | 2031-06-13 20:00 | 0 | 0 | N | 0
2025-06-13 | 21 | 2031-06-13 21:00 | 0 | 0 | N | 0
2025-06-13 | 22 | 2031-06-13 22:00 | 0 | 0 | N | 0
2025-06-13 | 23 | 2031-06-13 23:00 | 0 | 0 | N | 0
2025-06-14 | 00 | 2031-06-14 | 0 | 0 | N | 0
2025-06-14 | 01 | 2031-06-14 01:00 | 0 | 0 | N | 0
2025-06-14 | 02 | 2031-06-14 02:00 | 0 | 0 | N | 0
2025-06-14 | 03 | 2031-06-14 03:00 | 0 | 0 | N | 0
2025-06-14 | 04 | 2031-06-14 04:00 | 0 | 0 | N | 0
2025-06-14 | 05 | 2031-06-14 05:00 | 0 | 0 | N | 0
2025-06-14 | 06 | 2031-06-14 06:00 | 0 | 0 | N | 0
2025-06-14 | 07 | 2031-06-14 07:00 | 0 | 0 | N | 0
2025-06-14 | 08 | 2031-06-14 08:00 | 0 | 0 | N | 0
2025-06-14 | 09 | 2031-06-14 09:00 | 0 | 0 | N | 0
2025-06-14 | 10 | 2031-06-14 10:00 | 0 | 0 | N | 0
2025-06-14 | 11 | 2031-06-14 11:00 | 0 | 0 | N | 0
2025-06-14 | 12 | 2031-06-14 12:00 | 0 | 0 | N | 0
2025-06-14 | 13 | 2031-06-14 13:00 | 0 | 0 | N | 0
2025-06-14 | 14 | 2031-06-14 14:00 | 0 | 0 | N | 0
2025-06-14 | 15 | 2031-06-14 15:00 | 0 | 0 | N | 0
2025-06-14 | 16 | 2031-06-14 16:00 | 0 | 0 | N | 0
2025-06-14 | 17 | 2031-06-14 17:00 | 0 | 0 | N | 0
2025-06-14 | 18 | 2031-06-14 18:00 | 0 | 0 | N | 0
2025-06-14 | 19 | 2031-06-14 19:00 | 0 | 0 | N | 0
2025-06-14 | 20 | 2031-06-14 20:00 | 0 | 0 | N | 0
2025-06-14 | 21 | 2031-06-14 21:00 | 0 | 0 | N | 0
2025-06-14 | 22 | 2031-06-14 22:00 | 0 | 0 | N | 0
2025-06-14 | 23 | 2031-06-14 23:00 | 0 | 0 | N | 0
2025-06-15 | 00 | 2031-06-15 | 0 | 0 | N | 0
2025-06-15 | 01 | 2031-06-15 01:00 | 0 | 0 | N | 0
2025-06-15 | 02 | 2031-06-15 02:00 | 0 | 0 | N | 0
2025-06-15 | 03 | 2031-06-15 03:00 | 0 | 0 | N | 0
2025-06-15 | 04 | 2031-06-15 04:00 | 0 | 0 | N | 0
2025-06-15 | 05 | 2031-06-15 05:00 | 0 | 0 | N | 0
2025-06-15 | 06 | 2031-06-15 06:00 | 0 | 0 | N | 0
2025-06-15 | 07 | 2031-06-15 07:00 | 0 | 0 | N | 0
2025-06-15 | 08 | 2031-06-15 08:00 | 0 | 0 | N | 0
2025-06-15 | 09 | 2031-06-15 09:00 | 0 | 0 | N | 0
2025-06-15 | 10 | 2031-06-15 10:00 | 0 | 0 | N | 0
2025-06-15 | 11 | 2031-06-15 11:00 | 0 | 0 | N | 0
2025-06-15 | 12 | 2031-06-15 12:00 | 0 | 0 | N | 0
2025-06-15 | 13 | 2031-06-15 13:00 | 0 | 0 | N | 0
2025-06-15 | 14 | 2031-06-15 14:00 | 0 | 0 | N | 0
2025-06-15 | 15 | 2031-06-15 15:00 | 0 | 0 | N | 0
2025-06-15 | 16 | 2031-06-15 16:00 | 0 | 0 | N | 0
2025-06-15 | 17 | 2031-06-15 17:00 | 0 | 0 | N | 0
2025-06-15 | 18 | 2031-06-15 18:00 | 0 | 0 | N | 0
2025-06-15 | 19 | 2031-06-15 19:00 | 0 | 0 | N | 0
2025-06-15 | 20 | 2031-06-15 20:00 | 0 | 0 | N | 0
2025-06-15 | 21 | 2031-06-15 21:00 | 0 | 0 | N | 0
2025-06-15 | 22 | 2031-06-15 22:00 | 0 | 0 | N | 0
2025-06-15 | 23 | 2031-06-15 23:00 | 0 | 0 | N | 0
2025-06-16 | 00 | 2031-06-16 | 0 | 0 | N | 0
2025-06-16 | 01 | 2031-06-16 01:00 | 0 | 0 | N | 0
2025-06-16 | 02 | 2031-06-16 02:00 | 0 | 0 | N | 0
2025-06-16 | 03 | 2031-06-16 03:00 | 0 | 0 | N | 0
2025-06-16 | 04 | 2031-06-16 04:00 | 0 | 0 | N | 0
2025-06-16 | 05 | 2031-06-16 05:00 | 0 | 0 | N | 0
2025-06-16 | 06 | 2031-06-16 06:00 | 0 | 0 | N | 0
2025-06-16 | 07 | 2031-06-16 07:00 | 0 | 0 | N | 0
2025-06-16 | 08 | 2031-06-16 08:00 | 0 | 0 | N | 0
2025-06-16 | 09 | 2031-06-16 09:00 | 0 | 0 | N | 0
2025-06-16 | 10 | 2031-06-16 10:00 | 0 | 0 | N | 0
2025-06-16 | 11 | 2031-06-16 11:00 | 0 | 0 | N | 0
2025-06-16 | 12 | 2031-06-16 12:00 | 0 | 0 | N | 0
2025-06-16 | 13 | 2031-06-16 13:00 | 0 | 0 | N | 0
2025-06-16 | 14 | 2031-06-16 14:00 | 0 | 0 | N | 0
2025-06-16 | 15 | 2031-06-16 15:00 | 0 | 0 | N | 0
2025-06-16 | 16 | 2031-06-16 16:00 | 0 | 0 | N | 0
2025-06-16 | 17 | 2031-06-16 17:00 | 0 | 0 | N | 0
2025-06-16 | 18 | 2031-06-16 18:00 | 0 | 0 | N | 0
2025-06-16 | 19 | 2031-06-16 19:00 | 0 | 0 | N | 0
2025-06-16 | 20 | 2031-06-16 20:00 | 0 | 0 | N | 0
2025-06-16 | 21 | 2031-06-16 21:00 | 0 | 0 | N | 0
2025-06-16 | 22 | 2031-06-16 22:00 | 0 | 0 | N | 0
2025-06-16 | 23 | 2031-06-16 23:00 | 0 | 0 | N | 0
2025-06-17 | 00 | 2031-06-17 | 0 | 0 | N | 0
2025-06-17 | 01 | 2031-06-17 01:00 | 0 | 0 | N | 0
2025-06-17 | 02 | 2031-06-17 02:00 | 0 | 0 | N | 0
2025-06-17 | 03 | 2031-06-17 03:00 | 0 | 0 | N | 0
2025-06-17 | 04 | 2031-06-17 04:00 | 0 | 0 | N | 0
2025-06-17 | 05 | 2031-06-17 05:00 | 0 | 0 | N | 0
2025-06-17 | 06 | 2031-06-17 06:00 | 0 | 0 | N | 0
2025-06-17 | 07 | 2031-06-17 07:00 | 0 | 0 | N | 0
2025-06-17 | 08 | 2031-06-17 08:00 | 0 | 0 | N | 0
2025-06-17 | 09 | 2031-06-17 09:00 | 0 | 0 | N | 0
2025-06-17 | 10 | 2031-06-17 10:00 | 0 | 0 | N | 0
2025-06-17 | 11 | 2031-06-17 11:00 | 0 | 0 | N | 0
2025-06-17 | 12 | 2031-06-17 12:00 | 0 | 0 | N | 0
2025-06-17 | 13 | 2031-06-17 13:00 | 0 | 0 | N | 0
2025-06-17 | 14 | 2031-06-17 14:00 | 0 | 0 | N | 0
2025-06-17 | 15 | 2031-06-17 15:00 | 0 | 0 | N | 0
2025-06-17 | 16 | 2031-06-17 16:00 | 0 | 0 | N | 0
2025-06-17 | 17 | 2031-06-17 17:00 | 0 | 0 | N | 0
2025-06-17 | 18 | 2031-06-17 18:00 | 0 | 0 | N | 0
2025-06-17 | 19 | 2031-06-17 19:00 | 0 | 0 | N | 0
2025-06-17 | 20 | 2031-06-17 20:00 | 0 | 0 | N | 0
2025-06-17 | 21 | 2031-06-17 21:00 | 0 | 0 | N | 0
2025-06-17 | 22 | 2031-06-17 22:00 | 0 | 0 | N | 0
2025-06-17 | 23 | 2031-06-17 23:00 | 0 | 0 | N | 0
2025-06-18 | 00 | 2031-06-18 | 0 | 0 | N | 0
2025-06-18 | 01 | 2031-06-18 01:00 | 0 | 0 | N | 0
2025-06-18 | 02 | 2031-06-18 02:00 | 0 | 0 | N | 0
2025-06-18 | 03 | 2031-06-18 03:00 | 0 | 0 | N | 0
2025-06-18 | 04 | 2031-06-18 04:00 | 0 | 0 | N | 0
2025-06-18 | 05 | 2031-06-18 05:00 | 0 | 0 | N | 0
2025-06-18 | 06 | 2031-06-18 06:00 | 0 | 0 | N | 0
2025-06-18 | 07 | 2031-06-18 07:00 | 0 | 0 | N | 0
2025-06-18 | 08 | 2031-06-18 08:00 | 0 | 0 | N | 0
2025-06-18 | 09 | 2031-06-18 09:00 | 0 | 0 | N | 0
2025-06-18 | 10 | 2031-06-18 10:00 | 0 | 0 | N | 0
2025-06-18 | 11 | 2031-06-18 11:00 | 0 | 0 | N | 0
2025-06-18 | 12 | 2031-06-18 12:00 | 0 | 0 | N | 0
2025-06-18 | 13 | 2031-06-18 13:00 | 0 | 0 | N | 0
2025-06-18 | 14 | 2031-06-18 14:00 | 0 | 0 | N | 0
2025-06-18 | 15 | 2031-06-18 15:00 | 0 | 0 | N | 0
2025-06-18 | 16 | 2031-06-18 16:00 | 0 | 0 | N | 0
2025-06-18 | 17 | 2031-06-18 17:00 | 0 | 0 | N | 0
2025-06-18 | 18 | 2031-06-18 18:00 | 0 | 0 | N | 0
2025-06-18 | 19 | 2031-06-18 19:00 | 0 | 0 | N | 0
2025-06-18 | 20 | 2031-06-18 20:00 | 0 | 0 | N | 0
2025-06-18 | 21 | 2031-06-18 21:00 | 0 | 0 | N | 0
2025-06-18 | 22 | 2031-06-18 22:00 | 0 | 0 | N | 0
2025-06-18 | 23 | 2031-06-18 23:00 | 0 | 0 | N | 0
2025-06-19 | 00 | 2031-06-19 | 0 | 0 | N | 0
2025-06-19 | 01 | 2031-06-19 01:00 | 0 | 0 | N | 0
2025-06-19 | 02 | 2031-06-19 02:00 | 0 | 0 | N | 0
2025-06-19 | 03 | 2031-06-19 03:00 | 0 | 0 | N | 0
2025-06-19 | 04 | 2031-06-19 04:00 | 0 | 0 | N | 0
2025-06-19 | 05 | 2031-06-19 05:00 | 0 | 0 | N | 0
2025-06-19 | 06 | 2031-06-19 06:00 | 0 | 0 | N | 0
2025-06-19 | 07 | 2031-06-19 07:00 | 0 | 0 | N | 0
2025-06-19 | 08 | 2031-06-19 08:00 | 0 | 0 | N | 0
2025-06-19 | 09 | 2031-06-19 09:00 | 0 | 0 | N | 0
2025-06-19 | 10 | 2031-06-19 10:00 | 0 | 0 | N | 0
2025-06-19 | 11 | 2031-06-19 11:00 | 0 | 0 | N | 0
2025-06-19 | 12 | 2031-06-19 12:00 | 0 | 0 | N | 0
2025-06-19 | 13 | 2031-06-19 13:00 | 0 | 0 | N | 0
2025-06-19 | 14 | 2031-06-19 14:00 | 0 | 0 | N | 0
2025-06-19 | 15 | 2031-06-19 15:00 | 0 | 0 | N | 0
2025-06-19 | 16 | 2031-06-19 16:00 | 0 | 0 | N | 0
2025-06-19 | 17 | 2031-06-19 17:00 | 0 | 0 | N | 0
2025-06-19 | 18 | 2031-06-19 18:00 | 0 | 0 | N | 0
2025-06-19 | 19 | 2031-06-19 19:00 | 0 | 0 | N | 0
2025-06-19 | 20 | 2031-06-19 20:00 | 0 | 0 | N | 0
2025-06-19 | 21 | 2031-06-19 21:00 | 0 | 0 | N | 0
2025-06-19 | 22 | 2031-06-19 22:00 | 0 | 0 | N | 0
2025-06-19 | 23 | 2031-06-19 23:00 | 0 | 0 | N | 0
2025-06-20 | 00 | 2031-06-20 | 0 | 0 | N | 0
2025-06-20 | 01 | 2031-06-20 01:00 | 0 | 0 | N | 0
2025-06-20 | 02 | 2031-06-20 02:00 | 0 | 0 | N | 0
2025-06-20 | 03 | 2031-06-20 03:00 | 0 | 0 | N | 0
2025-06-20 | 04 | 2031-06-20 04:00 | 0 | 0 | N | 0
2025-06-20 | 05 | 2031-06-20 05:00 | 0 | 0 | N | 0
2025-06-20 | 06 | 2031-06-20 06:00 | 0 | 0 | N | 0
2025-06-20 | 07 | 2031-06-20 07:00 | 0 | 0 | N | 0
2025-06-20 | 08 | 2031-06-20 08:00 | 0 | 0 | N | 0
2025-06-20 | 09 | 2031-06-20 09:00 | 0 | 0 | N | 0
2025-06-20 | 10 | 2031-06-20 10:00 | 0 | 0 | N | 0
2025-06-20 | 11 | 2031-06-20 11:00 | 0 | 0 | N | 0
2025-06-20 | 12 | 2031-06-20 12:00 | 0 | 0 | N | 0
2025-06-20 | 13 | 2031-06-20 13:00 | 0 | 0 | N | 0
2025-06-20 | 14 | 2031-06-20 14:00 | 0 | 0 | N | 0
2025-06-20 | 15 | 2031-06-20 15:00 | 0 | 0 | N | 0
2025-06-20 | 16 | 2031-06-20 16:00 | 0 | 0 | N | 0
2025-06-20 | 17 | 2031-06-20 17:00 | 0 | 0 | N | 0
2025-06-20 | 18 | 2031-06-20 18:00 | 0 | 0 | N | 0
2025-06-20 | 19 | 2031-06-20 19:00 | 0 | 0 | N | 0
2025-06-20 | 20 | 2031-06-20 20:00 | 0 | 0 | N | 0
2025-06-20 | 21 | 2031-06-20 21:00 | 0 | 0 | N | 0
2025-06-20 | 22 | 2031-06-20 22:00 | 0 | 0 | N | 0
2025-06-20 | 23 | 2031-06-20 23:00 | 0 | 0 | N | 0
2025-06-21 | 00 | 2031-06-21 | 0 | 0 | N | 0
2025-06-21 | 01 | 2031-06-21 01:00 | 0 | 0 | N | 0
2025-06-21 | 02 | 2031-06-21 02:00 | 0 | 0 | N | 0
2025-06-21 | 03 | 2031-06-21 03:00 | 0 | 0 | N | 0
2025-06-21 | 04 | 2031-06-21 04:00 | 0 | 0 | N | 0
2025-06-21 | 05 | 2031-06-21 05:00 | 0 | 0 | N | 0
2025-06-21 | 06 | 2031-06-21 06:00 | 0 | 0 | N | 0
2025-06-21 | 07 | 2031-06-21 07:00 | 0 | 0 | N | 0
2025-06-21 | 08 | 2031-06-21 08:00 | 0 | 0 | N | 0
2025-06-21 | 09 | 2031-06-21 09:00 | 0 | 0 | N | 0
2025-06-21 | 10 | 2031-06-21 10:00 | 0 | 0 | N | 0
2025-06-21 | 11 | 2031-06-21 11:00 | 0 | 0 | N | 0
2025-06-21 | 12 | 2031-06-21 12:00 | 0 | 0 | N | 0
2025-06-21 | 13 | 2031-06-21 13:00 | 0 | 0 | N | 0
2025-06-21 | 14 | 2031-06-21 14:00 | 0 | 0 | N | 0
2025-06-21 | 15 | 2031-06-21 15:00 | 0 | 0 | N | 0
2025-06-21 | 16 | 2031-06-21 16:00 | 0 | 0 | N | 0
2025-06-21 | 17 | 2031-06-21 17:00 | 0 | 0 | N | 0
2025-06-21 | 18 | 2031-06-21 18:00 | 0 | 0 | N | 0
2025-06-21 | 19 | 2031-06-21 19:00 | 0 | 0 | N | 0
2025-06-21 | 20 | 2031-06-21 20:00 | 0 | 0 | N | 0
2025-06-21 | 21 | 2031-06-21 21:00 | 0 | 0 | N | 0
2025-06-21 | 22 | 2031-06-21 22:00 | 0 | 0 | N | 0
2025-06-21 | 23 | 2031-06-21 23:00 | 0 | 0 | N | 0
2025-06-22 | 00 | 2031-06-22 | 0.62 | 0.81457 | N | 0
2025-06-22 | 01 | 2031-06-22 01:00 | 0.48 | 0.63064 | N | 0
2025-06-22 | 02 | 2031-06-22 02:00 | 0.36 | 0.47298 | N | 0
2025-06-22 | 03 | 2031-06-22 03:00 | 0.54 | 0.70947 | N | 0
2025-06-22 | 04 | 2031-06-22 04:00 | 0.75 | 0.98537 | N | 0
2025-06-22 | 05 | 2031-06-22 05:00 | 0.96 | 1.2613 | N | 0
2025-06-22 | 06 | 2031-06-22 06:00 | 1.08 | 1.4189 | N | 0
2025-06-22 | 07 | 2031-06-22 07:00 | 1.21 | 1.5897 | N | 0
2025-06-22 | 08 | 2031-06-22 08:00 | 4 | 5.2553 | N | 0
2025-06-22 | 09 | 2031-06-22 09:00 | 4.15 | 5.4524 | N | 0
2025-06-22 | 10 | 2031-06-22 10:00 | 4.16 | 5.4655 | N | 0
2025-06-22 | 11 | 2031-06-22 11:00 | 4.78 | 6.2801 | N | 0
2025-06-22 | 12 | 2031-06-22 12:00 | 5.16 | 6.7794 | N | 0
2025-06-22 | 13 | 2031-06-22 13:00 | 5.76 | 7.5677 | N | 0
2025-06-22 | 14 | 2031-06-22 14:00 | 6.23 | 8.1852 | N | 0
2025-06-22 | 15 | 2031-06-22 15:00 | 6.93 | 9.1048 | N | 0
2025-06-22 | 16 | 2031-06-22 16:00 | 6.99 | 9.1837 | N | 0
2025-06-22 | 17 | 2031-06-22 17:00 | 7.08 | 9.3019 | N | 0
2025-06-22 | 18 | 2031-06-22 18:00 | 7.26 | 9.5384 | N | 0
2025-06-22 | 19 | 2031-06-22 19:00 | 7.5 | 9.8537 | N | 0
2025-06-22 | 20 | 2031-06-22 20:00 | 7.74 | 10.169 | N | 0
2025-06-22 | 21 | 2031-06-22 21:00 | 8.13 | 10.6814 | N | 0
2025-06-22 | 22 | 2031-06-22 22:00 | 7.46 | 9.8012 | N | 0
2025-06-22 | 23 | 2031-06-22 23:00 | 7 | 9.1968 | N | 0
2025-06-23 | 00 | 2031-06-23 | 6.74 | 8.8552 | N | 0
2025-06-23 | 01 | 2031-06-23 01:00 | 6.7 | 8.8027 | N | 0
2025-06-23 | 02 | 2031-06-23 02:00 | 6.07 | 7.9749 | N | 0
2025-06-23 | 03 | 2031-06-23 03:00 | 5.44 | 7.1472 | N | 0
2025-06-23 | 04 | 2031-06-23 04:00 | 5.27 | 6.9239 | N | 0
2025-06-23 | 05 | 2031-06-23 05:00 | 5 | 6.5691 | N | 0
2025-06-23 | 06 | 2031-06-23 06:00 | 4.69 | 6.1619 | N | 0
2025-06-23 | 07 | 2031-06-23 07:00 | 4.46 | 5.8597 | N | 0
2025-06-23 | 08 | 2031-06-23 08:00 | 4.59 | 6.0305 | N | 0
2025-06-23 | 09 | 2031-06-23 09:00 | 5.15 | 6.7662 | N | 0
2025-06-23 | 10 | 2031-06-23 10:00 | 5.49 | 7.2129 | N | 0
2025-06-23 | 11 | 2031-06-23 11:00 | 7.22 | 9.4859 | N | 0
2025-06-23 | 12 | 2031-06-23 12:00 | 7.97 | 10.4712 | N | 0
2025-06-23 | 13 | 2031-06-23 13:00 | 8.38 | 11.0099 | N | 0
2025-06-23 | 14 | 2031-06-23 14:00 | 9 | 11.8245 | N | 0
2025-06-23 | 15 | 2031-06-23 15:00 | 9.57 | 12.5734 | N | 0
2025-06-23 | 16 | 2031-06-23 16:00 | 9.25 | 12.1529 | N | 0
2025-06-23 | 17 | 2031-06-23 17:00 | 10.21 | 13.4142 | N | 0
2025-06-23 | 18 | 2031-06-23 18:00 | 9.99 | 13.1252 | N | 0
2025-06-23 | 19 | 2031-06-23 19:00 | 9.97 | 13.0989 | N | 0
2025-06-23 | 20 | 2031-06-23 20:00 | 9.89 | 12.9938 | N | 0
2025-06-23 | 21 | 2031-06-23 21:00 | 9.38 | 12.3237 | N | 0
2025-06-23 | 22 | 2031-06-23 22:00 | 9.25 | 12.1529 | N | 0
2025-06-23 | 23 | 2031-06-23 23:00 | 8.45 | 11.1019 | N | 0
2025-06-24 | 00 | 2031-06-24 | 7.81 | 10.261 | N | 0
2025-06-24 | 01 | 2031-06-24 01:00 | 7.34 | 9.6435 | N | 0
2025-06-24 | 02 | 2031-06-24 02:00 | 6.59 | 8.6581 | N | 0
2025-06-24 | 03 | 2031-06-24 03:00 | 6.14 | 8.0669 | N | 0
2025-06-24 | 04 | 2031-06-24 04:00 | 5.86 | 7.699 | N | 0
2025-06-24 | 05 | 2031-06-24 05:00 | 5.62 | 7.3837 | N | 0
2025-06-24 | 06 | 2031-06-24 06:00 | 5.34 | 7.0159 | N | 0
2025-06-24 | 07 | 2031-06-24 07:00 | 5.26 | 6.9107 | N | 0
2025-06-24 | 08 | 2031-06-24 08:00 | 5.2 | 6.8319 | N | 0
2025-06-24 | 09 | 2031-06-24 09:00 | 5.5 | 7.2261 | N | 0
2025-06-24 | 10 | 2031-06-24 10:00 | 5.69 | 7.4757 | N | 0
2025-06-24 | 11 | 2031-06-24 11:00 | 7.22 | 9.4859 | N | 0
2025-06-24 | 12 | 2031-06-24 12:00 | 7.72 | 10.1428 | N | 0
2025-06-24 | 13 | 2031-06-24 13:00 | 8.14 | 10.6946 | N | 0
2025-06-24 | 14 | 2031-06-24 14:00 | 9.26 | 12.1661 | N | 0
2025-06-24 | 15 | 2031-06-24 15:00 | 9.42 | 12.3763 | N | 0
2025-06-24 | 16 | 2031-06-24 16:00 | 9.87 | 12.9675 | N | 0
2025-06-24 | 17 | 2031-06-24 17:00 | 10.17 | 13.3616 | N | 0
2025-06-24 | 18 | 2031-06-24 18:00 | 10.46 | 13.7427 | N | 0
2025-06-24 | 19 | 2031-06-24 19:00 | 10.39 | 13.6507 | N | 0
2025-06-24 | 20 | 2031-06-24 20:00 | 10.11 | 13.2828 | N | 0
2025-06-24 | 21 | 2031-06-24 21:00 | 10.18 | 13.3748 | N | 0
2025-06-24 | 22 | 2031-06-24 22:00 | 9.89 | 12.9938 | N | 0
2025-06-24 | 23 | 2031-06-24 23:00 | 9.72 | 12.7704 | N | 0
2025-06-25 | 00 | 2031-06-25 | 9.02 | 11.8507 | N | 0
2025-06-25 | 01 | 2031-06-25 01:00 | 8.24 | 10.826 | N | 0
2025-06-25 | 02 | 2031-06-25 02:00 | 7.46 | 9.8012 | N | 0
2025-06-25 | 03 | 2031-06-25 03:00 | 6.76 | 8.8815 | N | 0
2025-06-25 | 04 | 2031-06-25 04:00 | 6.46 | 8.4873 | N | 0
2025-06-25 | 05 | 2031-06-25 05:00 | 6.06 | 7.9618 | N | 0
2025-06-25 | 06 | 2031-06-25 06:00 | 5.76 | 7.5677 | N | 0
2025-06-25 | 07 | 2031-06-25 07:00 | 5.79 | 7.6071 | N | 0
2025-06-25 | 08 | 2031-06-25 08:00 | 5.66 | 7.4363 | N | 0
2025-06-25 | 09 | 2031-06-25 09:00 | 6.04 | 7.9355 | N | 0
2025-06-25 | 10 | 2031-06-25 10:00 | 6.78 | 8.9078 | N | 0
2025-06-25 | 11 | 2031-06-25 11:00 | 7.49 | 9.8406 | N | 0
2025-06-25 | 12 | 2031-06-25 12:00 | 8.23 | 10.8128 | N | 0
2025-06-25 | 13 | 2031-06-25 13:00 | 8.43 | 11.0756 | N | 0
2025-06-25 | 14 | 2031-06-25 14:00 | 9.17 | 12.0478 | N | 0
2025-06-25 | 15 | 2031-06-25 15:00 | 9.6 | 12.6128 | N | 0
2025-06-25 | 16 | 2031-06-25 16:00 | 9.64 | 12.6653 | N | 0
2025-06-25 | 17 | 2031-06-25 17:00 | 10.2 | 13.4011 | N | 0
2025-06-25 | 18 | 2031-06-25 18:00 | 9.97 | 13.0989 | N | 0
2025-06-25 | 19 | 2031-06-25 19:00 | 10.07 | 13.2303 | N | 0
2025-06-25 | 20 | 2031-06-25 20:00 | 9.72 | 12.7704 | N | 0
2025-06-25 | 21 | 2031-06-25 21:00 | 9.64 | 12.6653 | N | 0
2025-06-25 | 22 | 2031-06-25 22:00 | 8.99 | 11.8113 | N | 0
2025-06-25 | 23 | 2031-06-25 23:00 | 8.98 | 11.7982 | N | 0
2025-06-26 | 00 | 2031-06-26 | 7.61 | 9.9982 | N | 0
2025-06-26 | 01 | 2031-06-26 01:00 | 7.67 | 10.0771 | N | 0
2025-06-26 | 02 | 2031-06-26 02:00 | 6.59 | 8.6581 | N | 0
2025-06-26 | 03 | 2031-06-26 03:00 | 6.2 | 8.1457 | N | 0
2025-06-26 | 04 | 2031-06-26 04:00 | 5.81 | 7.6334 | N | 0
2025-06-26 | 05 | 2031-06-26 05:00 | 5.42 | 7.121 | N | 0
2025-06-26 | 06 | 2031-06-26 06:00 | 5.34 | 7.0159 | N | 0
2025-06-26 | 07 | 2031-06-26 07:00 | 5.37 | 7.0553 | N | 0
2025-06-26 | 08 | 2031-06-26 08:00 | 5.27 | 6.9239 | N | 0
2025-06-26 | 09 | 2031-06-26 09:00 | 5.7 | 7.4888 | N | 0
2025-06-26 | 10 | 2031-06-26 10:00 | 6.36 | 8.356 | N | 0
2025-06-26 | 11 | 2031-06-26 11:00 | 7.35 | 9.6566 | N | 0
2025-06-26 | 12 | 2031-06-26 12:00 | 8 | 10.5106 | N | 0
2025-06-26 | 13 | 2031-06-26 13:00 | 8.46 | 11.115 | N | 0
2025-06-26 | 14 | 2031-06-26 14:00 | 8.74 | 11.4829 | N | 0
2025-06-26 | 15 | 2031-06-26 15:00 | 8.97 | 11.7851 | N | 0
2025-06-26 | 16 | 2031-06-26 16:00 | 8.77 | 11.5223 | N | 0
2025-06-26 | 17 | 2031-06-26 17:00 | 8.7 | 11.4303 | N | 0
2025-06-26 | 18 | 2031-06-26 18:00 | 8.33 | 10.9442 | N | 0
2025-06-26 | 19 | 2031-06-26 19:00 | 21.14 | 27.7744 | N | 0
2025-06-26 | 20 | 2031-06-26 20:00 | 21.63 | 28.4181 | N | 0
2025-06-26 | 21 | 2031-06-26 21:00 | 22.1 | 29.0356 | N | 0
2025-06-26 | 22 | 2031-06-26 22:00 | 21.52 | 28.2736 | N | 0
2025-06-26 | 23 | 2031-06-26 23:00 | 20.93 | 27.4985 | N | 0
2025-06-27 | 00 | 2031-06-27 | 20.97 | 27.551 | N | 0
2025-06-27 | 01 | 2031-06-27 01:00 | 21 | 27.5904 | N | 0
2025-06-27 | 02 | 2031-06-27 02:00 | 20.28 | 26.6445 | N | 0
2025-06-27 | 03 | 2031-06-27 03:00 | 17.87 | 23.4781 | N | 0
2025-06-27 | 04 | 2031-06-27 04:00 | 15.67 | 20.5877 | N | 0
2025-06-27 | 05 | 2031-06-27 05:00 | 14.03 | 18.433 | N | 0
2025-06-27 | 06 | 2031-06-27 06:00 | 12.98 | 17.0535 | N | 0
2025-06-27 | 07 | 2031-06-27 07:00 | 12.36 | 16.2389 | N | 0
2025-06-27 | 08 | 2031-06-27 08:00 | 12.24 | 16.0813 | N | 0
2025-06-27 | 09 | 2031-06-27 09:00 | 12.7 | 16.6856 | N | 0
2025-06-27 | 10 | 2031-06-27 10:00 | 14.74 | 19.3659 | N | 0
2025-06-27 | 11 | 2031-06-27 11:00 | 16.55 | 21.7439 | N | 0
2025-06-27 | 12 | 2031-06-27 12:00 | 18.41 | 24.1876 | N | 0
2025-06-27 | 13 | 2031-06-27 13:00 | 19.24 | 25.2781 | N | 0
2025-06-27 | 14 | 2031-06-27 14:00 | 20.08 | 26.3817 | N | 0
2025-06-27 | 15 | 2031-06-27 15:00 | 20.34 | 26.7233 | N | 0
2025-06-27 | 16 | 2031-06-27 16:00 | 20.82 | 27.3539 | N | 0
2025-06-27 | 17 | 2031-06-27 17:00 | 20.54 | 26.9861 | N | 0
2025-06-27 | 18 | 2031-06-27 18:00 | 20.71 | 27.2094 | N | 0
2025-06-27 | 19 | 2031-06-27 19:00 | 21.66 | 28.4576 | N | 0
2025-06-27 | 20 | 2031-06-27 20:00 | 23.87 | 31.3611 | N | 0
2025-06-27 | 21 | 2031-06-27 21:00 | 24.9 | 32.7144 | N | 0
2025-06-27 | 22 | 2031-06-27 22:00 | 25.37 | 33.3319 | N | 0
2025-06-27 | 23 | 2031-06-27 23:00 | 24.8 | 32.583 | N | 0
2025-06-28 | 00 | 2031-06-28 | 23.69 | 31.1246 | N | 0
2025-06-28 | 01 | 2031-06-28 01:00 | 23.06 | 30.2969 | N | 0
2025-06-28 | 02 | 2031-06-28 02:00 | 22.6 | 29.6926 | N | 0
2025-06-28 | 03 | 2031-06-28 03:00 | 20.54 | 26.9861 | N | 0
2025-06-28 | 04 | 2031-06-28 04:00 | 18.29 | 24.0299 | N | 0
2025-06-28 | 05 | 2031-06-28 05:00 | 16.04 | 21.0738 | N | 0
2025-06-28 | 06 | 2031-06-28 06:00 | 14.67 | 19.2739 | N | 0
2025-06-28 | 07 | 2031-06-28 07:00 | 14.01 | 18.4068 | N | 0
2025-06-28 | 08 | 2031-06-28 08:00 | 13.52 | 17.763 | N | 0
2025-06-28 | 09 | 2031-06-28 09:00 | 13.22 | 17.3688 | N | 0
2025-06-28 | 10 | 2031-06-28 10:00 | 13.98 | 18.3673 | N | 0
2025-06-28 | 11 | 2031-06-28 11:00 | 16.49 | 21.6651 | N | 0
2025-06-28 | 12 | 2031-06-28 12:00 | 20.77 | 27.2882 | N | 0
2025-06-28 | 13 | 2031-06-28 13:00 | 23.46 | 30.8224 | N | 0
2025-06-28 | 14 | 2031-06-28 14:00 | 25.05 | 32.9114 | N | 0
2025-06-28 | 15 | 2031-06-28 15:00 | 26.59 | 34.9347 | N | 0
2025-06-28 | 16 | 2031-06-28 16:00 | 27.65 | 36.3274 | N | 0
2025-06-28 | 17 | 2031-06-28 17:00 | 27.95 | 36.7215 | N | 0
2025-06-28 | 18 | 2031-06-28 18:00 | 27.73 | 36.4325 | N | 0
2025-06-28 | 19 | 2031-06-28 19:00 | 27.8 | 36.5245 | N | 0
2025-06-28 | 20 | 2031-06-28 20:00 | 27.85 | 36.5902 | N | 0
2025-06-28 | 21 | 2031-06-28 21:00 | 27.6 | 36.2617 | N | 0
2025-06-28 | 22 | 2031-06-28 22:00 | 26.47 | 34.7771 | N | 0
2025-06-28 | 23 | 2031-06-28 23:00 | 25.12 | 33.0034 | N | 0
2025-06-29 | 00 | 2031-06-29 | 22.8 | 29.9553 | N | 0
2025-06-29 | 01 | 2031-06-29 01:00 | 20.97 | 27.551 | N | 0
2025-06-29 | 02 | 2031-06-29 02:00 | 20.28 | 26.6445 | N | 0
2025-06-29 | 03 | 2031-06-29 03:00 | 18.68 | 24.5423 | N | 0
2025-06-29 | 04 | 2031-06-29 04:00 | 16.32 | 21.4417 | N | 0
2025-06-29 | 05 | 2031-06-29 05:00 | 14.47 | 19.0111 | N | 0
2025-06-29 | 06 | 2031-06-29 06:00 | 13.28 | 17.4477 | N | 0
2025-06-29 | 07 | 2031-06-29 07:00 | 12.44 | 16.344 | N | 0
2025-06-29 | 08 | 2031-06-29 08:00 | 11.89 | 15.6214 | N | 0
2025-06-29 | 09 | 2031-06-29 09:00 | 11.86 | 15.582 | N | 0
2025-06-29 | 10 | 2031-06-29 10:00 | 12.29 | 16.147 | N | 0
2025-06-29 | 11 | 2031-06-29 11:00 | 14.31 | 18.8009 | N | 0
2025-06-29 | 12 | 2031-06-29 12:00 | 16.83 | 22.1118 | N | 0
2025-06-29 | 13 | 2031-06-29 13:00 | 19.11 | 25.1073 | N | 0
2025-06-29 | 14 | 2031-06-29 14:00 | 20.73 | 27.2357 | N | 0
2025-06-29 | 15 | 2031-06-29 15:00 | 21.78 | 28.6152 | N | 0
2025-06-29 | 16 | 2031-06-29 16:00 | 22.17 | 29.1276 | N | 0
2025-06-29 | 17 | 2031-06-29 17:00 | 22.47 | 29.5218 | N | 0
2025-06-29 | 18 | 2031-06-29 18:00 | 22.91 | 30.0998 | N | 0
2025-06-29 | 19 | 2031-06-29 19:00 | 24.39 | 32.0443 | N | 0
2025-06-29 | 20 | 2031-06-29 20:00 | 26.29 | 34.5406 | N | 0
2025-06-29 | 21 | 2031-06-29 21:00 | 27.26 | 35.815 | N | 0
2025-06-29 | 22 | 2031-06-29 22:00 | 27.2 | 35.7362 | N | 0
2025-06-29 | 23 | 2031-06-29 23:00 | 26.7 | 35.0793 | N | 0
2025-06-30 | 00 | 2031-06-30 | 24.96 | 32.7932 | N | 0
2025-06-30 | 01 | 2031-06-30 01:00 | 23.28 | 30.586 | N | 0
2025-06-30 | 02 | 2031-06-30 02:00 | 22.16 | 29.1145 | N | 0
2025-06-30 | 03 | 2031-06-30 03:00 | 19.72 | 25.9087 | N | 0
2025-06-30 | 04 | 2031-06-30 04:00 | 17.16 | 22.5453 | N | 0
2025-06-30 | 05 | 2031-06-30 05:00 | 15.31 | 20.1147 | N | 0
2025-06-30 | 06 | 2031-06-30 06:00 | 14.02 | 18.4199 | N | 0
2025-06-30 | 07 | 2031-06-30 07:00 | 13.1 | 17.2112 | N | 0
2025-06-30 | 08 | 2031-06-30 08:00 | 12.53 | 16.4623 | N | 0
2025-06-30 | 09 | 2031-06-30 09:00 | 12.69 | 16.6725 | N | 0
2025-06-30 | 10 | 2031-06-30 10:00 | 14.66 | 19.2607 | N | 0
2025-06-30 | 11 | 2031-06-30 11:00 | 17.2 | 22.5979 | N | 0
2025-06-30 | 12 | 2031-06-30 12:00 | 20.03 | 26.316 | N | 0
2025-06-30 | 13 | 2031-06-30 13:00 | 22.39 | 29.4166 | N | 0
2025-06-30 | 14 | 2031-06-30 14:00 | 24.81 | 32.5961 | N | 0
2025-06-30 | 15 | 2031-06-30 15:00 | 25.56 | 33.5815 | N | 0
2025-06-30 | 16 | 2031-06-30 16:00 | 26.68 | 35.053 | N | 0
2025-06-30 | 17 | 2031-06-30 17:00 | 27.51 | 36.1435 | N | 0
2025-06-30 | 18 | 2031-06-30 18:00 | 27.19 | 35.723 | N | 0
2025-06-30 | 19 | 2031-06-30 19:00 | 26.03 | 34.199 | N | 0
2025-06-30 | 20 | 2031-06-30 20:00 | 25.74 | 33.818 | N | 0
2025-06-30 | 21 | 2031-06-30 21:00 | 25.94 | 34.0807 | N | 0
2025-06-30 | 22 | 2031-06-30 22:00 | 25.89 | 34.0151 | N | 0
2025-06-30 | 23 | 2031-06-30 23:00 | 25.18 | 33.0822 | N | 0
2025-07-01 | 00 | 2031-07-01 | 23.71 | 31.1509 | N | 0
2025-07-01 | 01 | 2031-07-01 01:00 | 23.44 | 30.7962 | N | 0
2025-07-01 | 02 | 2031-07-01 02:00 | 22.24 | 29.2196 | N | 0
2025-07-01 | 03 | 2031-07-01 03:00 | 20.24 | 26.5919 | N | 0
2025-07-01 | 04 | 2031-07-01 04:00 | 18.09 | 23.7672 | N | 0
2025-07-01 | 05 | 2031-07-01 05:00 | 16.48 | 21.6519 | N | 0
2025-07-01 | 06 | 2031-07-01 06:00 | 15.12 | 19.8651 | N | 0
2025-07-01 | 07 | 2031-07-01 07:00 | 14.16 | 18.6038 | N | 0
2025-07-01 | 08 | 2031-07-01 08:00 | 13.92 | 18.2885 | N | 0
2025-07-01 | 09 | 2031-07-01 09:00 | 13.92 | 18.2885 | N | 0
2025-07-01 | 10 | 2031-07-01 10:00 | 14.93 | 19.6155 | N | 0
2025-07-01 | 11 | 2031-07-01 11:00 | 16.49 | 21.6651 | N | 0
2025-07-01 | 12 | 2031-07-01 12:00 | 19.57 | 25.7116 | N | 0
2025-07-01 | 13 | 2031-07-01 13:00 | 22.34 | 29.351 | N | 0
2025-07-01 | 14 | 2031-07-01 14:00 | 25.01 | 32.8589 | N | 0
2025-07-01 | 15 | 2031-07-01 15:00 | 26.21 | 34.4355 | N | 0
2025-07-01 | 16 | 2031-07-01 16:00 | 27.8 | 36.5245 | N | 0
2025-07-01 | 17 | 2031-07-01 17:00 | 29.7 | 39.0207 | Y | 1.8407 | 1
2025-07-01 | 18 | 2031-07-01 18:00 | 30.85 | 40.5316 | Y | 3.3516 | 2
2025-07-01 | 19 | 2031-07-01 19:00 | 31.28 | 41.0966 | Y | 3.9166 | 3
2025-07-01 | 20 | 2031-07-01 20:00 | 31.8 | 41.7798 | Y | 4.5998 | 4
2025-07-01 | 21 | 2031-07-01 21:00 | 32.24 | 42.3579 | Y | 5.1779 | 5
2025-07-01 | 22 | 2031-07-01 22:00 | 31.76 | 41.7272 | Y | 4.5472 | 6
2025-07-01 | 23 | 2031-07-01 23:00 | 31.14 | 40.9127 | Y | 3.7327 | 7
2025-07-02 | 00 | 2031-07-02 | 29.3 | 38.4952 | Y | 1.3152 | 8 | 8
2025-07-02 | 01 | 2031-07-02 01:00 | 26.63 | 34.9873 | N | 0
2025-07-02 | 02 | 2031-07-02 02:00 | 24.27 | 31.8866 | N | 0
2025-07-02 | 03 | 2031-07-02 03:00 | 22.55 | 29.6269 | N | 0
2025-07-02 | 04 | 2031-07-02 04:00 | 19.85 | 26.0795 | N | 0
2025-07-02 | 05 | 2031-07-02 05:00 | 17.02 | 22.3614 | N | 0
2025-07-02 | 06 | 2031-07-02 06:00 | 15.36 | 20.1804 | N | 0
2025-07-02 | 07 | 2031-07-02 07:00 | 14.05 | 18.4593 | N | 0
2025-07-02 | 08 | 2031-07-02 08:00 | 13.41 | 17.6185 | N | 0
2025-07-02 | 09 | 2031-07-02 09:00 | 13.55 | 17.8024 | N | 0
2025-07-02 | 10 | 2031-07-02 10:00 | 15.38 | 20.2067 | N | 0
2025-07-02 | 11 | 2031-07-02 11:00 | 18.84 | 24.7526 | N | 0
2025-07-02 | 12 | 2031-07-02 12:00 | 21.83 | 28.6809 | N | 0
2025-07-02 | 13 | 2031-07-02 13:00 | 24.27 | 31.8866 | N | 0
2025-07-02 | 14 | 2031-07-02 14:00 | 26.32 | 34.58 | N | 0
2025-07-02 | 15 | 2031-07-02 15:00 | 27.08 | 35.5785 | N | 0
2025-07-02 | 16 | 2031-07-02 16:00 | 28.43 | 37.3522 | Y | 0.17218 | 1
2025-07-02 | 17 | 2031-07-02 17:00 | 28.91 | 37.9828 | Y | 0.80282 | 2
2025-07-02 | 18 | 2031-07-02 18:00 | 29.62 | 38.9156 | Y | 1.7356 | 3
2025-07-02 | 19 | 2031-07-02 19:00 | 30.7 | 40.3346 | Y | 3.1546 | 4
2025-07-02 | 20 | 2031-07-02 20:00 | 31.45 | 41.3199 | Y | 4.1399 | 5
2025-07-02 | 21 | 2031-07-02 21:00 | 32.11 | 42.1871 | Y | 5.0071 | 6
2025-07-02 | 22 | 2031-07-02 22:00 | 29.31 | 38.5084 | Y | 1.3284 | 7
2025-07-02 | 23 | 2031-07-02 23:00 | 28.6 | 37.5755 | Y | 0.39553 | 8 | 8
2025-07-03 | 00 | 2031-07-03 | 27.41 | 36.0121 | N | 0
2025-07-03 | 01 | 2031-07-03 01:00 | 26.16 | 34.3698 | N | 0
2025-07-03 | 02 | 2031-07-03 02:00 | 24.75 | 32.5173 | N | 0
2025-07-03 | 03 | 2031-07-03 03:00 | 22.06 | 28.9831 | N | 0
2025-07-03 | 04 | 2031-07-03 04:00 | 19.08 | 25.0679 | N | 0
2025-07-03 | 05 | 2031-07-03 05:00 | 16.84 | 22.1249 | N | 0
2025-07-03 | 06 | 2031-07-03 06:00 | 15.52 | 20.3906 | N | 0
2025-07-03 | 07 | 2031-07-03 07:00 | 14.58 | 19.1556 | N | 0
2025-07-03 | 08 | 2031-07-03 08:00 | 14.11 | 18.5381 | N | 0
2025-07-03 | 09 | 2031-07-03 09:00 | 14.49 | 19.0374 | N | 0
2025-07-03 | 10 | 2031-07-03 10:00 | 16.24 | 21.3366 | N | 0
2025-07-03 | 11 | 2031-07-03 11:00 | 18.33 | 24.0825 | N | 0
2025-07-03 | 12 | 2031-07-03 12:00 | 18.46 | 24.2533 | N | 0
2025-07-03 | 13 | 2031-07-03 13:00 | 20.61 | 27.078 | N | 0
2025-07-03 | 14 | 2031-07-03 14:00 | 23.87 | 31.3611 | N | 0
2025-07-03 | 15 | 2031-07-03 15:00 | 24.92 | 32.7406 | N | 0
2025-07-03 | 16 | 2031-07-03 16:00 | 26.13 | 34.3304 | N | 0
2025-07-03 | 17 | 2031-07-03 17:00 | 26.35 | 34.6194 | N | 0
2025-07-03 | 18 | 2031-07-03 18:00 | 26.57 | 34.9085 | N | 0
2025-07-03 | 19 | 2031-07-03 19:00 | 27.83 | 36.5639 | N | 0
2025-07-03 | 20 | 2031-07-03 20:00 | 28.43 | 37.3522 | Y | 0.17218 | 1
2025-07-03 | 21 | 2031-07-03 21:00 | 28.92 | 37.996 | Y | 0.81596 | 2
2025-07-03 | 22 | 2031-07-03 22:00 | 28.69 | 37.6938 | Y | 0.51378 | 3 | 3
2025-07-03 | 23 | 2031-07-03 23:00 | 27.74 | 36.4456 | N | 0
2025-07-04 | 00 | 2031-07-04 | 25.32 | 33.2662 | N | 0
2025-07-04 | 01 | 2031-07-04 01:00 | 23.76 | 31.2166 | N | 0
2025-07-04 | 02 | 2031-07-04 02:00 | 22.37 | 29.3904 | N | 0
2025-07-04 | 03 | 2031-07-04 03:00 | 19.86 | 26.0927 | N | 0
2025-07-04 | 04 | 2031-07-04 04:00 | 16.99 | 22.322 | N | 0
2025-07-04 | 05 | 2031-07-04 05:00 | 14.97 | 19.668 | N | 0
2025-07-04 | 06 | 2031-07-04 06:00 | 13.61 | 17.8812 | N | 0
2025-07-04 | 07 | 2031-07-04 07:00 | 12.58 | 16.528 | N | 0
2025-07-04 | 08 | 2031-07-04 08:00 | 12.23 | 16.0681 | N | 0
2025-07-04 | 09 | 2031-07-04 09:00 | 12.4 | 16.2915 | N | 0
2025-07-04 | 10 | 2031-07-04 10:00 | 14.38 | 18.8929 | N | 0
2025-07-04 | 11 | 2031-07-04 11:00 | 17.07 | 22.4271 | N | 0
2025-07-04 | 12 | 2031-07-04 12:00 | 19.14 | 25.1467 | N | 0
2025-07-04 | 13 | 2031-07-04 13:00 | 21.03 | 27.6298 | N | 0
2025-07-04 | 14 | 2031-07-04 14:00 | 22.53 | 29.6006 | N | 0
2025-07-04 | 15 | 2031-07-04 15:00 | 23.25 | 30.5465 | N | 0
2025-07-04 | 16 | 2031-07-04 16:00 | 23.65 | 31.0721 | N | 0
2025-07-04 | 17 | 2031-07-04 17:00 | 24.4 | 32.0574 | N | 0
2025-07-04 | 18 | 2031-07-04 18:00 | 25.28 | 33.2136 | N | 0
2025-07-04 | 19 | 2031-07-04 19:00 | 25.4 | 33.3713 | N | 0
2025-07-04 | 20 | 2031-07-04 20:00 | 26.33 | 34.5931 | N | 0
2025-07-04 | 21 | 2031-07-04 21:00 | 27.46 | 36.0778 | N | 0
2025-07-04 | 22 | 2031-07-04 22:00 | 27.03 | 35.5128 | N | 0
2025-07-04 | 23 | 2031-07-04 23:00 | 25.64 | 33.6866 | N | 0
2025-07-05 | 00 | 2031-07-05 | 24.16 | 31.7421 | N | 0
2025-07-05 | 01 | 2031-07-05 01:00 | 22.87 | 30.0473 | N | 0
2025-07-05 | 02 | 2031-07-05 02:00 | 21.77 | 28.6021 | N | 0
2025-07-05 | 03 | 2031-07-05 03:00 | 19.2 | 25.2255 | N | 0
2025-07-05 | 04 | 2031-07-05 04:00 | 17.03 | 22.3745 | N | 0
2025-07-05 | 05 | 2031-07-05 05:00 | 14.67 | 19.2739 | N | 0
2025-07-05 | 06 | 2031-07-05 06:00 | 13.3 | 17.4739 | N | 0
2025-07-05 | 07 | 2031-07-05 07:00 | 12.49 | 16.4097 | N | 0
2025-07-05 | 08 | 2031-07-05 08:00 | 11.94 | 15.6871 | N | 0
2025-07-05 | 09 | 2031-07-05 09:00 | 11.76 | 15.4506 | N | 0
2025-07-05 | 10 | 2031-07-05 10:00 | 12.42 | 16.3178 | N | 0
2025-07-05 | 11 | 2031-07-05 11:00 | 14.32 | 18.814 | N | 0
2025-07-05 | 12 | 2031-07-05 12:00 | 17.66 | 23.2022 | N | 0
2025-07-05 | 13 | 2031-07-05 13:00 | 20.45 | 26.8678 | N | 0
2025-07-05 | 14 | 2031-07-05 14:00 | 22.8 | 29.9553 | N | 0
2025-07-05 | 15 | 2031-07-05 15:00 | 24.08 | 31.637 | N | 0
2025-07-05 | 16 | 2031-07-05 16:00 | 24.72 | 32.4779 | N | 0
2025-07-05 | 17 | 2031-07-05 17:00 | 25.43 | 33.4107 | N | 0
2025-07-05 | 18 | 2031-07-05 18:00 | 26.26 | 34.5012 | N | 0
2025-07-05 | 19 | 2031-07-05 19:00 | 27.57 | 36.2223 | N | 0
2025-07-05 | 20 | 2031-07-05 20:00 | 28.67 | 37.6675 | Y | 0.4875 | 1
2025-07-05 | 21 | 2031-07-05 21:00 | 29.51 | 38.7711 | Y | 1.5911 | 2
2025-07-05 | 22 | 2031-07-05 22:00 | 29.3 | 38.4952 | Y | 1.3152 | 3
2025-07-05 | 23 | 2031-07-05 23:00 | 28.61 | 37.5887 | Y | 0.40867 | 4 | 4
2025-07-06 | 00 | 2031-07-06 | 26.71 | 35.0924 | N | 0
2025-07-06 | 01 | 2031-07-06 01:00 | 25.8 | 33.8968 | N | 0
2025-07-06 | 02 | 2031-07-06 02:00 | 24.68 | 32.4253 | N | 0
2025-07-06 | 03 | 2031-07-06 03:00 | 22.71 | 29.8371 | N | 0
2025-07-06 | 04 | 2031-07-06 04:00 | 20.49 | 26.9204 | N | 0
2025-07-06 | 05 | 2031-07-06 05:00 | 18.09 | 23.7672 | N | 0
2025-07-06 | 06 | 2031-07-06 06:00 | 16.43 | 21.5862 | N | 0
2025-07-06 | 07 | 2031-07-06 07:00 | 15.07 | 19.7994 | N | 0
2025-07-06 | 08 | 2031-07-06 08:00 | 14.55 | 19.1162 | N | 0
2025-07-06 | 09 | 2031-07-06 09:00 | 13.97 | 18.3542 | N | 0
2025-07-06 | 10 | 2031-07-06 10:00 | 14.33 | 18.8272 | N | 0
2025-07-06 | 11 | 2031-07-06 11:00 | 17.31 | 22.7424 | N | 0
2025-07-06 | 12 | 2031-07-06 12:00 | 21.39 | 28.1028 | N | 0
2025-07-06 | 13 | 2031-07-06 13:00 | 25.22 | 33.1348 | N | 0
2025-07-06 | 14 | 2031-07-06 14:00 | 27.88 | 36.6296 | N | 0
2025-07-06 | 15 | 2031-07-06 15:00 | 29.97 | 39.3755 | Y | 2.1955 | 1
2025-07-06 | 16 | 2031-07-06 16:00 | 31.27 | 41.0835 | Y | 3.9035 | 2
2025-07-06 | 17 | 2031-07-06 17:00 | 32.32 | 42.463 | Y | 5.283 | 3
2025-07-06 | 18 | 2031-07-06 18:00 | 33.44 | 43.9345 | Y | 6.7545 | 4
2025-07-06 | 19 | 2031-07-06 19:00 | 34.6 | 45.4585 | Y | 8.2785 | 5
2025-07-06 | 20 | 2031-07-06 20:00 | 35.7 | 46.9037 | Y | 9.7237 | 6
2025-07-06 | 21 | 2031-07-06 21:00 | 36.36 | 47.7709 | Y | 10.5909 | 7
2025-07-06 | 22 | 2031-07-06 22:00 | 36.19 | 47.5475 | Y | 10.3675 | 8
2025-07-06 | 23 | 2031-07-06 23:00 | 35.38 | 46.4833 | Y | 9.3033 | 9
2025-07-07 | 00 | 2031-07-07 | 33.88 | 44.5126 | Y | 7.3326 | 10
2025-07-07 | 01 | 2031-07-07 01:00 | 32.18 | 42.279 | Y | 5.099 | 11
2025-07-07 | 02 | 2031-07-07 02:00 | 30.37 | 39.901 | Y | 2.721 | 12 | 12
2025-07-07 | 03 | 2031-07-07 03:00 | 27.45 | 36.0646 | N | 0
2025-07-07 | 04 | 2031-07-07 04:00 | 23.54 | 30.9276 | N | 0
2025-07-07 | 05 | 2031-07-07 05:00 | 20.88 | 27.4328 | N | 0
2025-07-07 | 06 | 2031-07-07 06:00 | 19.09 | 25.081 | N | 0
2025-07-07 | 07 | 2031-07-07 07:00 | 18.65 | 24.5029 | N | 0
2025-07-07 | 08 | 2031-07-07 08:00 | 17.86 | 23.465 | N | 0
2025-07-07 | 09 | 2031-07-07 09:00 | 18.09 | 23.7672 | N | 0
2025-07-07 | 10 | 2031-07-07 10:00 | 20.21 | 26.5525 | N | 0
2025-07-07 | 11 | 2031-07-07 11:00 | 24.05 | 31.5976 | N | 0
2025-07-07 | 12 | 2031-07-07 12:00 | 27.24 | 35.7887 | N | 0
2025-07-07 | 13 | 2031-07-07 13:00 | 29.62 | 38.9156 | Y | 1.7356 | 1
2025-07-07 | 14 | 2031-07-07 14:00 | 31.9 | 41.9112 | Y | 4.7312 | 2
2025-07-07 | 15 | 2031-07-07 15:00 | 32.81 | 43.1068 | Y | 5.9268 | 3
2025-07-07 | 16 | 2031-07-07 16:00 | 33.4 | 43.8819 | Y | 6.7019 | 4
2025-07-07 | 17 | 2031-07-07 17:00 | 33.17 | 43.5797 | Y | 6.3997 | 5
2025-07-07 | 18 | 2031-07-07 18:00 | 33.61 | 44.1578 | Y | 6.9778 | 6
2025-07-07 | 19 | 2031-07-07 19:00 | 34.35 | 45.1301 | Y | 7.9501 | 7
2025-07-07 | 20 | 2031-07-07 20:00 | 34.55 | 45.3928 | Y | 8.2128 | 8
2025-07-07 | 21 | 2031-07-07 21:00 | 35.15 | 46.1811 | Y | 9.0011 | 9
2025-07-07 | 22 | 2031-07-07 22:00 | 33.28 | 43.7243 | Y | 6.5443 | 10
2025-07-07 | 23 | 2031-07-07 23:00 | 30.94 | 40.6499 | Y | 3.4699 | 11
2025-07-08 | 00 | 2031-07-08 | 29.67 | 38.9813 | Y | 1.8013 | 12
2025-07-08 | 01 | 2031-07-08 01:00 | 28.68 | 37.6806 | Y | 0.50064 | 13 | 13
2025-07-08 | 02 | 2031-07-08 02:00 | 27.05 | 35.5391 | N | 0
2025-07-08 | 03 | 2031-07-08 03:00 | 23.71 | 31.1509 | N | 0
2025-07-08 | 04 | 2031-07-08 04:00 | 20.79 | 27.3145 | N | 0
2025-07-08 | 05 | 2031-07-08 05:00 | 18.52 | 24.3321 | N | 0
2025-07-08 | 06 | 2031-07-08 06:00 | 17.19 | 22.5847 | N | 0
2025-07-08 | 07 | 2031-07-08 07:00 | 16.07 | 21.1132 | N | 0
2025-07-08 | 08 | 2031-07-08 08:00 | 15.44 | 20.2855 | N | 0
2025-07-08 | 09 | 2031-07-08 09:00 | 15.81 | 20.7716 | N | 0
2025-07-08 | 10 | 2031-07-08 10:00 | 17.53 | 23.0314 | N | 0
2025-07-08 | 11 | 2031-07-08 11:00 | 20.31 | 26.6839 | N | 0
2025-07-08 | 12 | 2031-07-08 12:00 | 21.73 | 28.5495 | N | 0
2025-07-08 | 13 | 2031-07-08 13:00 | 23.73 | 31.1772 | N | 0
2025-07-08 | 14 | 2031-07-08 14:00 | 24.29 | 31.9129 | N | 0
2025-07-08 | 15 | 2031-07-08 15:00 | 25.09 | 32.964 | N | 0
2025-07-08 | 16 | 2031-07-08 16:00 | 25.92 | 34.0545 | N | 0
2025-07-08 | 17 | 2031-07-08 17:00 | 27.96 | 36.7347 | N | 0
2025-07-08 | 18 | 2031-07-08 18:00 | 28.14 | 36.9712 | N | 0
2025-07-08 | 19 | 2031-07-08 19:00 | 29.91 | 39.2966 | Y | 2.1166 | 1
2025-07-08 | 20 | 2031-07-08 20:00 | 30.19 | 39.6645 | Y | 2.4845 | 2
2025-07-08 | 21 | 2031-07-08 21:00 | 31.42 | 41.2805 | Y | 4.1005 | 3
2025-07-08 | 22 | 2031-07-08 22:00 | 31.38 | 41.228 | Y | 4.048 | 4
2025-07-08 | 23 | 2031-07-08 23:00 | 29.92 | 39.3098 | Y | 2.1298 | 5
2025-07-09 | 00 | 2031-07-09 | 28.37 | 37.2734 | Y | 0.093351 | 6 | 6
2025-07-09 | 01 | 2031-07-09 01:00 | 26.74 | 35.1318 | N | 0
2025-07-09 | 02 | 2031-07-09 02:00 | 25.46 | 33.4501 | N | 0
2025-07-09 | 03 | 2031-07-09 03:00 | 22.24 | 29.2196 | N | 0
2025-07-09 | 04 | 2031-07-09 04:00 | 19.36 | 25.4357 | N | 0
2025-07-09 | 05 | 2031-07-09 05:00 | 17.04 | 22.3877 | N | 0
2025-07-09 | 06 | 2031-07-09 06:00 | 15.49 | 20.3512 | N | 0
2025-07-09 | 07 | 2031-07-09 07:00 | 14.55 | 19.1162 | N | 0
2025-07-09 | 08 | 2031-07-09 08:00 | 13.84 | 18.1834 | N | 0
2025-07-09 | 09 | 2031-07-09 09:00 | 14.2 | 18.6564 | N | 0
2025-07-09 | 10 | 2031-07-09 10:00 | 16.45 | 21.6125 | N | 0
2025-07-09 | 11 | 2031-07-09 11:00 | 18.55 | 24.3715 | N | 0
2025-07-09 | 12 | 2031-07-09 12:00 | 20.34 | 26.7233 | N | 0
2025-07-09 | 13 | 2031-07-09 13:00 | 21.23 | 27.8926 | N | 0
2025-07-09 | 14 | 2031-07-09 14:00 | 24.37 | 32.018 | N | 0
2025-07-09 | 15 | 2031-07-09 15:00 | 27.11 | 35.6179 | N | 0
2025-07-09 | 16 | 2031-07-09 16:00 | 28.12 | 36.9449 | N | 0
2025-07-09 | 17 | 2031-07-09 17:00 | 28.96 | 38.0485 | Y | 0.86851 | 1
2025-07-09 | 18 | 2031-07-09 18:00 | 28.45 | 37.3785 | Y | 0.19846 | 2
2025-07-09 | 19 | 2031-07-09 19:00 | 28.4 | 37.3128 | Y | 0.13277 | 3
2025-07-09 | 20 | 2031-07-09 20:00 | 30.72 | 40.3609 | Y | 3.1809 | 4
2025-07-09 | 21 | 2031-07-09 21:00 | 31.64 | 41.5696 | Y | 4.3896 | 5
2025-07-09 | 22 | 2031-07-09 22:00 | 31.09 | 40.847 | Y | 3.667 | 6
2025-07-09 | 23 | 2031-07-09 23:00 | 28.54 | 37.4967 | Y | 0.3167 | 7 | 7
2025-07-10 | 00 | 2031-07-10 | 26.84 | 35.2632 | N | 0
2025-07-10 | 01 | 2031-07-10 01:00 | 26.27 | 34.5143 | N | 0
2025-07-10 | 02 | 2031-07-10 02:00 | 25.16 | 33.056 | N | 0
2025-07-10 | 03 | 2031-07-10 03:00 | 22.12 | 29.0619 | N | 0
2025-07-10 | 04 | 2031-07-10 04:00 | 19.18 | 25.1993 | N | 0
2025-07-10 | 05 | 2031-07-10 05:00 | 17.15 | 22.5322 | N | 0
2025-07-10 | 06 | 2031-07-10 06:00 | 15.58 | 20.4695 | N | 0
2025-07-10 | 07 | 2031-07-10 07:00 | 14.45 | 18.9848 | N | 0
2025-07-10 | 08 | 2031-07-10 08:00 | 13.92 | 18.2885 | N | 0
2025-07-10 | 09 | 2031-07-10 09:00 | 14.24 | 18.7089 | N | 0
2025-07-10 | 10 | 2031-07-10 10:00 | 16.69 | 21.9278 | N | 0
2025-07-10 | 11 | 2031-07-10 11:00 | 18.45 | 24.2402 | N | 0
2025-07-10 | 12 | 2031-07-10 12:00 | 21.95 | 28.8386 | N | 0
2025-07-10 | 13 | 2031-07-10 13:00 | 25.03 | 32.8852 | N | 0
2025-07-10 | 14 | 2031-07-10 14:00 | 27.92 | 36.6821 | N | 0
2025-07-10 | 15 | 2031-07-10 15:00 | 28.23 | 37.0894 | N | 0
2025-07-10 | 16 | 2031-07-10 16:00 | 29.22 | 38.3901 | Y | 1.2101 | 1
2025-07-10 | 17 | 2031-07-10 17:00 | 30.49 | 40.0587 | Y | 2.8787 | 2
2025-07-10 | 18 | 2031-07-10 18:00 | 30.91 | 40.6105 | Y | 3.4305 | 3
2025-07-10 | 19 | 2031-07-10 19:00 | 31.11 | 40.8732 | Y | 3.6932 | 4
2025-07-10 | 20 | 2031-07-10 20:00 | 31.38 | 41.228 | Y | 4.048 | 5
2025-07-10 | 21 | 2031-07-10 21:00 | 31.95 | 41.9769 | Y | 4.7969 | 6
2025-07-10 | 22 | 2031-07-10 22:00 | 32.16 | 42.2528 | Y | 5.0728 | 7
2025-07-10 | 23 | 2031-07-10 23:00 | 31.82 | 41.8061 | Y | 4.6261 | 8
2025-07-11 | 00 | 2031-07-11 | 30.84 | 40.5185 | Y | 3.3385 | 9
2025-07-11 | 01 | 2031-07-11 01:00 | 29.11 | 38.2456 | Y | 1.0656 | 10 | 10
2025-07-11 | 02 | 2031-07-11 02:00 | 27.5 | 36.1303 | N | 0
2025-07-11 | 03 | 2031-07-11 03:00 | 24.43 | 32.0969 | N | 0
2025-07-11 | 04 | 2031-07-11 04:00 | 21.1 | 27.7218 | N | 0
2025-07-11 | 05 | 2031-07-11 05:00 | 18.84 | 24.7526 | N | 0
2025-07-11 | 06 | 2031-07-11 06:00 | 17.13 | 22.5059 | N | 0
2025-07-11 | 07 | 2031-07-11 07:00 | 15.92 | 20.9162 | N | 0
2025-07-11 | 08 | 2031-07-11 08:00 | 15.18 | 19.9439 | N | 0
2025-07-11 | 09 | 2031-07-11 09:00 | 15.19 | 19.9571 | N | 0
2025-07-11 | 10 | 2031-07-11 10:00 | 16.99 | 22.322 | N | 0
2025-07-11 | 11 | 2031-07-11 11:00 | 19.28 | 25.3306 | N | 0
2025-07-11 | 12 | 2031-07-11 12:00 | 21.69 | 28.497 | N | 0
2025-07-11 | 13 | 2031-07-11 13:00 | 24.58 | 32.2939 | N | 0
2025-07-11 | 14 | 2031-07-11 14:00 | 27.75 | 36.4588 | N | 0
2025-07-11 | 15 | 2031-07-11 15:00 | 28.83 | 37.8777 | Y | 0.69771 | 1
2025-07-11 | 16 | 2031-07-11 16:00 | 29.69 | 39.0076 | Y | 1.8276 | 2
2025-07-11 | 17 | 2031-07-11 17:00 | 30.59 | 40.1901 | Y | 3.0101 | 3
2025-07-11 | 18 | 2031-07-11 18:00 | 31.62 | 41.5433 | Y | 4.3633 | 4
2025-07-11 | 19 | 2031-07-11 19:00 | 32.58 | 42.8046 | Y | 5.6246 | 5
2025-07-11 | 20 | 2031-07-11 20:00 | 33.71 | 44.2892 | Y | 7.1092 | 6
2025-07-11 | 21 | 2031-07-11 21:00 | 33.79 | 44.3943 | Y | 7.2143 | 7
2025-07-11 | 22 | 2031-07-11 22:00 | 33.03 | 43.3958 | Y | 6.2158 | 8
2025-07-11 | 23 | 2031-07-11 23:00 | 31.91 | 41.9243 | Y | 4.7443 | 9
2025-07-12 | 00 | 2031-07-12 | 30.54 | 40.1244 | Y | 2.9444 | 10
2025-07-12 | 01 | 2031-07-12 01:00 | 29.2 | 38.3638 | Y | 1.1838 | 11 | 11
2025-07-12 | 02 | 2031-07-12 02:00 | 28 | 36.7872 | N | 0
2025-07-12 | 03 | 2031-07-12 03:00 | 25.5 | 33.5027 | N | 0
2025-07-12 | 04 | 2031-07-12 04:00 | 22.68 | 29.7977 | N | 0
2025-07-12 | 05 | 2031-07-12 05:00 | 20.32 | 26.697 | N | 0
2025-07-12 | 06 | 2031-07-12 06:00 | 18.41 | 24.1876 | N | 0
2025-07-12 | 07 | 2031-07-12 07:00 | 16.94 | 22.2563 | N | 0
2025-07-12 | 08 | 2031-07-12 08:00 | 16.24 | 21.3366 | N | 0
2025-07-12 | 09 | 2031-07-12 09:00 | 15.85 | 20.8242 | N | 0
2025-07-12 | 10 | 2031-07-12 10:00 | 16.34 | 21.468 | N | 0
2025-07-12 | 11 | 2031-07-12 11:00 | 18.38 | 24.1482 | N | 0
2025-07-12 | 12 | 2031-07-12 12:00 | 21.9 | 28.7729 | N | 0
2025-07-12 | 13 | 2031-07-12 13:00 | 26.27 | 34.5143 | N | 0
2025-07-12 | 14 | 2031-07-12 14:00 | 29.22 | 38.3901 | Y | 1.2101 | 1
2025-07-12 | 15 | 2031-07-12 15:00 | 31.03 | 40.7681 | Y | 3.5881 | 2
2025-07-12 | 16 | 2031-07-12 16:00 | 31.44 | 41.3068 | Y | 4.1268 | 3
2025-07-12 | 17 | 2031-07-12 17:00 | 31.69 | 41.6353 | Y | 4.4553 | 4
2025-07-12 | 18 | 2031-07-12 18:00 | 32.23 | 42.3447 | Y | 5.1647 | 5
2025-07-12 | 19 | 2031-07-12 19:00 | 32.47 | 42.6601 | Y | 5.4801 | 6
2025-07-12 | 20 | 2031-07-12 20:00 | 33.1 | 43.4878 | Y | 6.3078 | 7
2025-07-12 | 21 | 2031-07-12 21:00 | 33.86 | 44.4863 | Y | 7.3063 | 8
2025-07-12 | 22 | 2031-07-12 22:00 | 33.67 | 44.2366 | Y | 7.0566 | 9
2025-07-12 | 23 | 2031-07-12 23:00 | 33.24 | 43.6717 | Y | 6.4917 | 10
2025-07-13 | 00 | 2031-07-13 | 31.24 | 41.044 | Y | 3.864 | 11
2025-07-13 | 01 | 2031-07-13 01:00 | 29.89 | 39.2704 | Y | 2.0904 | 12
2025-07-13 | 02 | 2031-07-13 02:00 | 28.81 | 37.8514 | Y | 0.67144 | 13 | 13
2025-07-13 | 03 | 2031-07-13 03:00 | 26.8 | 35.2106 | N | 0
2025-07-13 | 04 | 2031-07-13 04:00 | 24.23 | 31.8341 | N | 0
2025-07-13 | 05 | 2031-07-13 05:00 | 22.02 | 28.9305 | N | 0
2025-07-13 | 06 | 2031-07-13 06:00 | 20.33 | 26.7102 | N | 0
2025-07-13 | 07 | 2031-07-13 07:00 | 19.08 | 25.0679 | N | 0
2025-07-13 | 08 | 2031-07-13 08:00 | 18.18 | 23.8854 | N | 0
2025-07-13 | 09 | 2031-07-13 09:00 | 17.35 | 22.7949 | N | 0
2025-07-13 | 10 | 2031-07-13 10:00 | 17.21 | 22.611 | N | 0
2025-07-13 | 11 | 2031-07-13 11:00 | 19.17 | 25.1861 | N | 0
2025-07-13 | 12 | 2031-07-13 12:00 | 23.23 | 30.5203 | N | 0
2025-07-13 | 13 | 2031-07-13 13:00 | 27.96 | 36.7347 | N | 0
2025-07-13 | 14 | 2031-07-13 14:00 | 29.32 | 38.5215 | Y | 1.3415 | 1 | 1
2025-07-13 | 15 | 2031-07-13 15:00 | 27.54 | 36.1829 | N | 0
2025-07-13 | 16 | 2031-07-13 16:00 | 27.65 | 36.3274 | N | 0
2025-07-13 | 17 | 2031-07-13 17:00 | 29.75 | 39.0864 | Y | 1.9064 | 1
2025-07-13 | 18 | 2031-07-13 18:00 | 31.18 | 40.9652 | Y | 3.7852 | 2
2025-07-13 | 19 | 2031-07-13 19:00 | 32.79 | 43.0805 | Y | 5.9005 | 3
2025-07-13 | 20 | 2031-07-13 20:00 | 34.7 | 45.5899 | Y | 8.4099 | 4
2025-07-13 | 21 | 2031-07-13 21:00 | 35.24 | 46.2994 | Y | 9.1194 | 5
2025-07-13 | 22 | 2031-07-13 22:00 | 34.67 | 45.5505 | Y | 8.3705 | 6
2025-07-13 | 23 | 2031-07-13 23:00 | 34.69 | 45.5768 | Y | 8.3968 | 7
2025-07-14 | 00 | 2031-07-14 | 32.87 | 43.1856 | Y | 6.0056 | 8
2025-07-14 | 01 | 2031-07-14 01:00 | 31.13 | 40.8995 | Y | 3.7195 | 9
2025-07-14 | 02 | 2031-07-14 02:00 | 28.64 | 37.6281 | Y | 0.44809 | 10 | 10
2025-07-14 | 03 | 2031-07-14 03:00 | 25.24 | 33.1611 | N | 0
2025-07-14 | 04 | 2031-07-14 04:00 | 21.94 | 28.8254 | N | 0
2025-07-14 | 05 | 2031-07-14 05:00 | 18.99 | 24.9496 | N | 0
2025-07-14 | 06 | 2031-07-14 06:00 | 17.44 | 22.9132 | N | 0
2025-07-14 | 07 | 2031-07-14 07:00 | 16.3 | 21.4154 | N | 0
2025-07-14 | 08 | 2031-07-14 08:00 | 15.32 | 20.1279 | N | 0
2025-07-14 | 09 | 2031-07-14 09:00 | 15.66 | 20.5746 | N | 0
2025-07-14 | 10 | 2031-07-14 10:00 | 17.39 | 22.8475 | N | 0
2025-07-14 | 11 | 2031-07-14 11:00 | 19.59 | 25.7379 | N | 0
2025-07-14 | 12 | 2031-07-14 12:00 | 21.63 | 28.4181 | N | 0
2025-07-14 | 13 | 2031-07-14 13:00 | 23.74 | 31.1903 | N | 0
2025-07-14 | 14 | 2031-07-14 14:00 | 26.04 | 34.2121 | N | 0
2025-07-14 | 15 | 2031-07-14 15:00 | 26.99 | 35.4603 | N | 0
2025-07-14 | 16 | 2031-07-14 16:00 | 28.88 | 37.9434 | Y | 0.7634 | 1
2025-07-14 | 17 | 2031-07-14 17:00 | 29.98 | 39.3886 | Y | 2.2086 | 2
2025-07-14 | 18 | 2031-07-14 18:00 | 31.12 | 40.8864 | Y | 3.7064 | 3
2025-07-14 | 19 | 2031-07-14 19:00 | 32.1 | 42.1739 | Y | 4.9939 | 4
2025-07-14 | 20 | 2031-07-14 20:00 | 33.3 | 43.7505 | Y | 6.5705 | 5
2025-07-14 | 21 | 2031-07-14 21:00 | 34.11 | 44.8147 | Y | 7.6347 | 6
2025-07-14 | 22 | 2031-07-14 22:00 | 34.06 | 44.749 | Y | 7.569 | 7
2025-07-14 | 23 | 2031-07-14 23:00 | 32.38 | 42.5418 | Y | 5.3618 | 8
2025-07-15 | 00 | 2031-07-15 | 31.04 | 40.7813 | Y | 3.6013 | 9
2025-07-15 | 01 | 2031-07-15 01:00 | 29.17 | 38.3244 | Y | 1.1444 | 10 | 10
2025-07-15 | 02 | 2031-07-15 02:00 | 27.38 | 35.9727 | N | 0
2025-07-15 | 03 | 2031-07-15 03:00 | 24.38 | 32.0312 | N | 0
2025-07-15 | 04 | 2031-07-15 04:00 | 20.86 | 27.4065 | N | 0
2025-07-15 | 05 | 2031-07-15 05:00 | 18.46 | 24.2533 | N | 0
2025-07-15 | 06 | 2031-07-15 06:00 | 16.6 | 21.8096 | N | 0
2025-07-15 | 07 | 2031-07-15 07:00 | 15.37 | 20.1936 | N | 0
2025-07-15 | 08 | 2031-07-15 08:00 | 14.49 | 19.0374 | N | 0
2025-07-15 | 09 | 2031-07-15 09:00 | 14.36 | 18.8666 | N | 0
2025-07-15 | 10 | 2031-07-15 10:00 | 16.5 | 21.6782 | N | 0
2025-07-15 | 11 | 2031-07-15 11:00 | 20.19 | 26.5262 | N | 0
2025-07-15 | 12 | 2031-07-15 12:00 | 23.14 | 30.402 | N | 0
2025-07-15 | 13 | 2031-07-15 13:00 | 26.03 | 34.199 | N | 0
2025-07-15 | 14 | 2031-07-15 14:00 | 28.59 | 37.5624 | Y | 0.38239 | 1
2025-07-15 | 15 | 2031-07-15 15:00 | 29.85 | 39.2178 | Y | 2.0378 | 2
2025-07-15 | 16 | 2031-07-15 16:00 | 30.91 | 40.6105 | Y | 3.4305 | 3
2025-07-15 | 17 | 2031-07-15 17:00 | 31.69 | 41.6353 | Y | 4.4553 | 4
2025-07-15 | 18 | 2031-07-15 18:00 | 32.71 | 42.9754 | Y | 5.7954 | 5
2025-07-15 | 19 | 2031-07-15 19:00 | 33.82 | 44.4337 | Y | 7.2537 | 6
2025-07-15 | 20 | 2031-07-15 20:00 | 35.43 | 46.549 | Y | 9.369 | 7
2025-07-15 | 21 | 2031-07-15 21:00 | 35.26 | 46.3256 | Y | 9.1456 | 8
2025-07-15 | 22 | 2031-07-15 22:00 | 35.1 | 46.1154 | Y | 8.9354 | 9
2025-07-15 | 23 | 2031-07-15 23:00 | 33.96 | 44.6177 | Y | 7.4377 | 10
2025-07-16 | 00 | 2031-07-16 | 32.66 | 42.9097 | Y | 5.7297 | 11
2025-07-16 | 01 | 2031-07-16 01:00 | 31.26 | 41.0703 | Y | 3.8903 | 12
2025-07-16 | 02 | 2031-07-16 02:00 | 29.13 | 38.2719 | Y | 1.0919 | 13 | 13
2025-07-16 | 03 | 2031-07-16 03:00 | 25.76 | 33.8443 | N | 0
2025-07-16 | 04 | 2031-07-16 04:00 | 22.52 | 29.5874 | N | 0
2025-07-16 | 05 | 2031-07-16 05:00 | 20.01 | 26.2897 | N | 0
2025-07-16 | 06 | 2031-07-16 06:00 | 17.92 | 23.5438 | N | 0
2025-07-16 | 07 | 2031-07-16 07:00 | 16.35 | 21.4811 | N | 0
2025-07-16 | 08 | 2031-07-16 08:00 | 15.55 | 20.4301 | N | 0
2025-07-16 | 09 | 2031-07-16 09:00 | 15.36 | 20.1804 | N | 0
2025-07-16 | 10 | 2031-07-16 10:00 | 17.63 | 23.1628 | N | 0
2025-07-16 | 11 | 2031-07-16 11:00 | 21.35 | 28.0503 | N | 0
2025-07-16 | 12 | 2031-07-16 12:00 | 24.64 | 32.3728 | N | 0
2025-07-16 | 13 | 2031-07-16 13:00 | 27.58 | 36.2354 | N | 0
2025-07-16 | 14 | 2031-07-16 14:00 | 30.26 | 39.7565 | Y | 2.5765 | 1
2025-07-16 | 15 | 2031-07-16 15:00 | 31.83 | 41.8192 | Y | 4.6392 | 2
2025-07-16 | 16 | 2031-07-16 16:00 | 32.75 | 43.0279 | Y | 5.8479 | 3
2025-07-16 | 17 | 2031-07-16 17:00 | 33 | 43.3564 | Y | 6.1764 | 4
2025-07-16 | 18 | 2031-07-16 18:00 | 33.94 | 44.5914 | Y | 7.4114 | 5
2025-07-16 | 19 | 2031-07-16 19:00 | 35.36 | 46.457 | Y | 9.277 | 6
2025-07-16 | 20 | 2031-07-16 20:00 | 36.34 | 47.7446 | Y | 10.5646 | 7
2025-07-16 | 21 | 2031-07-16 21:00 | 36.06 | 47.3767 | Y | 10.1967 | 8
2025-07-16 | 22 | 2031-07-16 22:00 | 35.95 | 47.2322 | Y | 10.0522 | 9
2025-07-16 | 23 | 2031-07-16 23:00 | 34.75 | 45.6556 | Y | 8.4756 | 10
2025-07-17 | 00 | 2031-07-17 | 33.73 | 44.3155 | Y | 7.1355 | 11
2025-07-17 | 01 | 2031-07-17 01:00 | 33 | 43.3564 | Y | 6.1764 | 12
2025-07-17 | 02 | 2031-07-17 02:00 | 31.76 | 41.7272 | Y | 4.5472 | 13
2025-07-17 | 03 | 2031-07-17 03:00 | 28.62 | 37.6018 | Y | 0.42181 | 14 | 14
2025-07-17 | 04 | 2031-07-17 04:00 | 25.65 | 33.6997 | N | 0
2025-07-17 | 05 | 2031-07-17 05:00 | 23.59 | 30.9932 | N | 0
2025-07-17 | 06 | 2031-07-17 06:00 | 21.66 | 28.4576 | N | 0
2025-07-17 | 07 | 2031-07-17 07:00 | 19.89 | 26.1321 | N | 0
2025-07-17 | 08 | 2031-07-17 08:00 | 19.67 | 25.843 | N | 0
2025-07-17 | 09 | 2031-07-17 09:00 | 19.6 | 25.7511 | N | 0
2025-07-17 | 10 | 2031-07-17 10:00 | 21.53 | 28.2868 | N | 0
2025-07-17 | 11 | 2031-07-17 11:00 | 23.86 | 31.348 | N | 0
2025-07-17 | 12 | 2031-07-17 12:00 | 25.37 | 33.3319 | N | 0
2025-07-17 | 13 | 2031-07-17 13:00 | 29.6 | 38.8894 | Y | 1.7094 | 1
2025-07-17 | 14 | 2031-07-17 14:00 | 31.24 | 41.044 | Y | 3.864 | 2
2025-07-17 | 15 | 2031-07-17 15:00 | 31.82 | 41.8061 | Y | 4.6261 | 3
2025-07-17 | 16 | 2031-07-17 16:00 | 32.27 | 42.3973 | Y | 5.2173 | 4
2025-07-17 | 17 | 2031-07-17 17:00 | 31.87 | 41.8718 | Y | 4.6918 | 5
2025-07-17 | 18 | 2031-07-17 18:00 | 31.51 | 41.3988 | Y | 4.2188 | 6
2025-07-17 | 19 | 2031-07-17 19:00 | 31.43 | 41.2937 | Y | 4.1137 | 7
2025-07-17 | 20 | 2031-07-17 20:00 | 31.74 | 41.701 | Y | 4.521 | 8
2025-07-17 | 21 | 2031-07-17 21:00 | 31.06 | 40.8076 | Y | 3.6276 | 9
2025-07-17 | 22 | 2031-07-17 22:00 | 29.36 | 38.574 | Y | 1.394 | 10 | 10
2025-07-17 | 23 | 2031-07-17 23:00 | 26.81 | 35.2238 | N | 0
2025-07-18 | 00 | 2031-07-18 | 24.94 | 32.7669 | N | 0
2025-07-18 | 01 | 2031-07-18 01:00 | 23.96 | 31.4794 | N | 0
2025-07-18 | 02 | 2031-07-18 02:00 | 22.02 | 28.9305 | N | 0
2025-07-18 | 03 | 2031-07-18 03:00 | 19.46 | 25.5671 | N | 0
2025-07-18 | 04 | 2031-07-18 04:00 | 17.16 | 22.5453 | N | 0
2025-07-18 | 05 | 2031-07-18 05:00 | 15.19 | 19.9571 | N | 0
2025-07-18 | 06 | 2031-07-18 06:00 | 13.73 | 18.0389 | N | 0
2025-07-18 | 07 | 2031-07-18 07:00 | 12.71 | 16.6988 | N | 0
2025-07-18 | 08 | 2031-07-18 08:00 | 12.27 | 16.1207 | N | 0
2025-07-18 | 09 | 2031-07-18 09:00 | 12.35 | 16.2258 | N | 0
2025-07-18 | 10 | 2031-07-18 10:00 | 13.92 | 18.2885 | N | 0
2025-07-18 | 11 | 2031-07-18 11:00 | 16.23 | 21.3235 | N | 0
2025-07-18 | 12 | 2031-07-18 12:00 | 18.54 | 24.3584 | N | 0
2025-07-18 | 13 | 2031-07-18 13:00 | 19.92 | 26.1715 | N | 0
2025-07-18 | 14 | 2031-07-18 14:00 | 21.72 | 28.5364 | N | 0
2025-07-18 | 15 | 2031-07-18 15:00 | 22.01 | 28.9174 | N | 0
2025-07-18 | 16 | 2031-07-18 16:00 | 22.26 | 29.2459 | N | 0
2025-07-18 | 17 | 2031-07-18 17:00 | 22.58 | 29.6663 | N | 0
2025-07-18 | 18 | 2031-07-18 18:00 | 22.9 | 30.0867 | N | 0
2025-07-18 | 19 | 2031-07-18 19:00 | 23.53 | 30.9144 | N | 0
2025-07-18 | 20 | 2031-07-18 20:00 | 24.05 | 31.5976 | N | 0
2025-07-18 | 21 | 2031-07-18 21:00 | 24.81 | 32.5961 | N | 0
2025-07-18 | 22 | 2031-07-18 22:00 | 24.25 | 31.8604 | N | 0
2025-07-18 | 23 | 2031-07-18 23:00 | 23.22 | 30.5071 | N | 0
2025-07-19 | 00 | 2031-07-19 | 22.13 | 29.0751 | N | 0
2025-07-19 | 01 | 2031-07-19 01:00 | 21.05 | 27.6561 | N | 0
2025-07-19 | 02 | 2031-07-19 02:00 | 20.03 | 26.316 | N | 0
2025-07-19 | 03 | 2031-07-19 03:00 | 17.71 | 23.2679 | N | 0
2025-07-19 | 04 | 2031-07-19 04:00 | 15.65 | 20.5614 | N | 0
2025-07-19 | 05 | 2031-07-19 05:00 | 14.05 | 18.4593 | N | 0
2025-07-19 | 06 | 2031-07-19 06:00 | 12.95 | 17.0141 | N | 0
2025-07-19 | 07 | 2031-07-19 07:00 | 11.98 | 15.7397 | N | 0
2025-07-19 | 08 | 2031-07-19 08:00 | 11.72 | 15.3981 | N | 0
2025-07-19 | 09 | 2031-07-19 09:00 | 11.66 | 15.3193 | N | 0
2025-07-19 | 10 | 2031-07-19 10:00 | 11.95 | 15.7003 | N | 0
2025-07-19 | 11 | 2031-07-19 11:00 | 13.99 | 18.3805 | N | 0
2025-07-19 | 12 | 2031-07-19 12:00 | 16.53 | 21.7176 | N | 0
2025-07-19 | 13 | 2031-07-19 13:00 | 18.09 | 23.7672 | N | 0
2025-07-19 | 14 | 2031-07-19 14:00 | 20.1 | 26.408 | N | 0
2025-07-19 | 15 | 2031-07-19 15:00 | 21.05 | 27.6561 | N | 0
2025-07-19 | 16 | 2031-07-19 16:00 | 21.66 | 28.4576 | N | 0
2025-07-19 | 17 | 2031-07-19 17:00 | 22.39 | 29.4166 | N | 0
2025-07-19 | 18 | 2031-07-19 18:00 | 22.58 | 29.6663 | N | 0
2025-07-19 | 19 | 2031-07-19 19:00 | 23.79 | 31.256 | N | 0
2025-07-19 | 20 | 2031-07-19 20:00 | 24.85 | 32.6487 | N | 0
2025-07-19 | 21 | 2031-07-19 21:00 | 25.02 | 32.872 | N | 0
2025-07-19 | 22 | 2031-07-19 22:00 | 24.29 | 31.9129 | N | 0
2025-07-19 | 23 | 2031-07-19 23:00 | 23.27 | 30.5728 | N | 0
2025-07-20 | 00 | 2031-07-20 | 22.01 | 28.9174 | N | 0
2025-07-20 | 01 | 2031-07-20 01:00 | 21.92 | 28.7991 | N | 0
2025-07-20 | 02 | 2031-07-20 02:00 | 20.99 | 27.5773 | N | 0
2025-07-20 | 03 | 2031-07-20 03:00 | 19.31 | 25.3701 | N | 0
2025-07-20 | 04 | 2031-07-20 04:00 | 17.64 | 23.176 | N | 0
2025-07-20 | 05 | 2031-07-20 05:00 | 15.82 | 20.7848 | N | 0
2025-07-20 | 06 | 2031-07-20 06:00 | 14.63 | 19.2213 | N | 0
2025-07-20 | 07 | 2031-07-20 07:00 | 13.78 | 18.1046 | N | 0
2025-07-20 | 08 | 2031-07-20 08:00 | 13.24 | 17.3951 | N | 0
2025-07-20 | 09 | 2031-07-20 09:00 | 13.05 | 17.1455 | N | 0
2025-07-20 | 10 | 2031-07-20 10:00 | 13.02 | 17.1061 | N | 0
2025-07-20 | 11 | 2031-07-20 11:00 | 14.49 | 19.0374 | N | 0
2025-07-20 | 12 | 2031-07-20 12:00 | 16.91 | 22.2169 | N | 0
2025-07-20 | 13 | 2031-07-20 13:00 | 19.71 | 25.8956 | N | 0
2025-07-20 | 14 | 2031-07-20 14:00 | 21.89 | 28.7597 | N | 0
2025-07-20 | 15 | 2031-07-20 15:00 | 24.12 | 31.6896 | N | 0
2025-07-20 | 16 | 2031-07-20 16:00 | 25.63 | 33.6735 | N | 0
2025-07-20 | 17 | 2031-07-20 17:00 | 27 | 35.4734 | N | 0
2025-07-20 | 18 | 2031-07-20 18:00 | 28.24 | 37.1026 | N | 0
2025-07-20 | 19 | 2031-07-20 19:00 | 28.99 | 38.0879 | Y | 0.90793 | 1
2025-07-20 | 20 | 2031-07-20 20:00 | 30.55 | 40.1375 | Y | 2.9575 | 2
2025-07-20 | 21 | 2031-07-20 21:00 | 31.58 | 41.4907 | Y | 4.3107 | 3
2025-07-20 | 22 | 2031-07-20 22:00 | 31.57 | 41.4776 | Y | 4.2976 | 4
2025-07-20 | 23 | 2031-07-20 23:00 | 30.51 | 40.0849 | Y | 2.9049 | 5
2025-07-21 | 00 | 2031-07-21 | 28.81 | 37.8514 | Y | 0.67144 | 6 | 6
2025-07-21 | 01 | 2031-07-21 01:00 | 26.44 | 34.7377 | N | 0
2025-07-21 | 02 | 2031-07-21 02:00 | 24.56 | 32.2677 | N | 0
2025-07-21 | 03 | 2031-07-21 03:00 | 21.13 | 27.7612 | N | 0
2025-07-21 | 04 | 2031-07-21 04:00 | 18.55 | 24.3715 | N | 0
2025-07-21 | 05 | 2031-07-21 05:00 | 16.22 | 21.3103 | N | 0
2025-07-21 | 06 | 2031-07-21 06:00 | 14.8 | 19.4447 | N | 0
2025-07-21 | 07 | 2031-07-21 07:00 | 13.83 | 18.1703 | N | 0
2025-07-21 | 08 | 2031-07-21 08:00 | 13.19 | 17.3294 | N | 0
2025-07-21 | 09 | 2031-07-21 09:00 | 13.18 | 17.3163 | N | 0
2025-07-21 | 10 | 2031-07-21 10:00 | 14.79 | 19.4315 | N | 0
2025-07-21 | 11 | 2031-07-21 11:00 | 17.57 | 23.084 | N | 0
2025-07-21 | 12 | 2031-07-21 12:00 | 19.47 | 25.5803 | N | 0
2025-07-21 | 13 | 2031-07-21 13:00 | 21.46 | 28.1948 | N | 0
2025-07-21 | 14 | 2031-07-21 14:00 | 22.44 | 29.4823 | N | 0
2025-07-21 | 15 | 2031-07-21 15:00 | 23.15 | 30.4152 | N | 0
2025-07-21 | 16 | 2031-07-21 16:00 | 23.12 | 30.3757 | N | 0
2025-07-21 | 17 | 2031-07-21 17:00 | 23.6 | 31.0064 | N | 0
2025-07-21 | 18 | 2031-07-21 18:00 | 24.02 | 31.5582 | N | 0
2025-07-21 | 19 | 2031-07-21 19:00 | 24.9 | 32.7144 | N | 0
2025-07-21 | 20 | 2031-07-21 20:00 | 26.37 | 34.6457 | N | 0
2025-07-21 | 21 | 2031-07-21 21:00 | 27.35 | 35.9332 | N | 0
2025-07-21 | 22 | 2031-07-21 22:00 | 27.51 | 36.1435 | N | 0
2025-07-21 | 23 | 2031-07-21 23:00 | 26.19 | 34.4092 | N | 0
2025-07-22 | 00 | 2031-07-22 | 24.42 | 32.0837 | N | 0
2025-07-22 | 01 | 2031-07-22 01:00 | 23.04 | 30.2706 | N | 0
2025-07-22 | 02 | 2031-07-22 02:00 | 21.65 | 28.4444 | N | 0
2025-07-22 | 03 | 2031-07-22 03:00 | 19.02 | 24.989 | N | 0
2025-07-22 | 04 | 2031-07-22 04:00 | 16.37 | 21.5074 | N | 0
2025-07-22 | 05 | 2031-07-22 05:00 | 14.54 | 19.1031 | N | 0
2025-07-22 | 06 | 2031-07-22 06:00 | 13.26 | 17.4214 | N | 0
2025-07-22 | 07 | 2031-07-22 07:00 | 12.46 | 16.3703 | N | 0
2025-07-22 | 08 | 2031-07-22 08:00 | 11.96 | 15.7134 | N | 0
2025-07-22 | 09 | 2031-07-22 09:00 | 12.25 | 16.0944 | N | 0
2025-07-22 | 10 | 2031-07-22 10:00 | 13.79 | 18.1177 | N | 0
2025-07-22 | 11 | 2031-07-22 11:00 | 16.48 | 21.6519 | N | 0
2025-07-22 | 12 | 2031-07-22 12:00 | 18.36 | 24.1219 | N | 0
2025-07-22 | 13 | 2031-07-22 13:00 | 19.95 | 26.2109 | N | 0
2025-07-22 | 14 | 2031-07-22 14:00 | 21.13 | 27.7612 | N | 0
2025-07-22 | 15 | 2031-07-22 15:00 | 21.61 | 28.3919 | N | 0
2025-07-22 | 16 | 2031-07-22 16:00 | 22.36 | 29.3772 | N | 0
2025-07-22 | 17 | 2031-07-22 17:00 | 22.84 | 30.0079 | N | 0
2025-07-22 | 18 | 2031-07-22 18:00 | 23.25 | 30.5465 | N | 0
2025-07-22 | 19 | 2031-07-22 19:00 | 24.76 | 32.5304 | N | 0
2025-07-22 | 20 | 2031-07-22 20:00 | 26.14 | 34.3435 | N | 0
2025-07-22 | 21 | 2031-07-22 21:00 | 27.01 | 35.4865 | N | 0
2025-07-22 | 22 | 2031-07-22 22:00 | 26.97 | 35.434 | N | 0
2025-07-22 | 23 | 2031-07-22 23:00 | 25.83 | 33.9362 | N | 0
2025-07-23 | 00 | 2031-07-23 | 24.35 | 31.9918 | N | 0
2025-07-23 | 01 | 2031-07-23 01:00 | 23.14 | 30.402 | N | 0
2025-07-23 | 02 | 2031-07-23 02:00 | 21.53 | 28.2868 | N | 0
2025-07-23 | 03 | 2031-07-23 03:00 | 18.68 | 24.5423 | N | 0
2025-07-23 | 04 | 2031-07-23 04:00 | 16.23 | 21.3235 | N | 0
2025-07-23 | 05 | 2031-07-23 05:00 | 14.42 | 18.9454 | N | 0
2025-07-23 | 06 | 2031-07-23 06:00 | 13.15 | 17.2769 | N | 0
2025-07-23 | 07 | 2031-07-23 07:00 | 12.34 | 16.2127 | N | 0
2025-07-23 | 08 | 2031-07-23 08:00 | 12.08 | 15.8711 | N | 0
2025-07-23 | 09 | 2031-07-23 09:00 | 12.34 | 16.2127 | N | 0
2025-07-23 | 10 | 2031-07-23 10:00 | 14.03 | 18.433 | N | 0
2025-07-23 | 11 | 2031-07-23 11:00 | 16.59 | 21.7964 | N | 0
2025-07-23 | 12 | 2031-07-23 12:00 | 18.95 | 24.8971 | N | 0
2025-07-23 | 13 | 2031-07-23 13:00 | 20.65 | 27.1306 | N | 0
2025-07-23 | 14 | 2031-07-23 14:00 | 22.25 | 29.2327 | N | 0
2025-07-23 | 15 | 2031-07-23 15:00 | 23.24 | 30.5334 | N | 0
2025-07-23 | 16 | 2031-07-23 16:00 | 24.16 | 31.7421 | N | 0
2025-07-23 | 17 | 2031-07-23 17:00 | 25.17 | 33.0691 | N | 0
2025-07-23 | 18 | 2031-07-23 18:00 | 25.67 | 33.726 | N | 0
2025-07-23 | 19 | 2031-07-23 19:00 | 27.06 | 35.5522 | N | 0
2025-07-23 | 20 | 2031-07-23 20:00 | 28.98 | 38.0748 | Y | 0.89479 | 1
2025-07-23 | 21 | 2031-07-23 21:00 | 29.87 | 39.2441 | Y | 2.0641 | 2
2025-07-23 | 22 | 2031-07-23 22:00 | 29.87 | 39.2441 | Y | 2.0641 | 3 | 3
2025-07-23 | 23 | 2031-07-23 23:00 | 28 | 36.7872 | N | 0
2025-07-24 | 00 | 2031-07-24 | 26.64 | 35.0004 | N | 0
2025-07-24 | 01 | 2031-07-24 01:00 | 25.73 | 33.8048 | N | 0
2025-07-24 | 02 | 2031-07-24 02:00 | 23.7 | 31.1378 | N | 0
2025-07-24 | 03 | 2031-07-24 03:00 | 20.73 | 27.2357 | N | 0
2025-07-24 | 04 | 2031-07-24 04:00 | 17.77 | 23.3468 | N | 0
2025-07-24 | 05 | 2031-07-24 05:00 | 15.74 | 20.6797 | N | 0
2025-07-24 | 06 | 2031-07-24 06:00 | 14.19 | 18.6432 | N | 0
2025-07-24 | 07 | 2031-07-24 07:00 | 13.3 | 17.4739 | N | 0
2025-07-24 | 08 | 2031-07-24 08:00 | 12.71 | 16.6988 | N | 0
2025-07-24 | 09 | 2031-07-24 09:00 | 13.06 | 17.1586 | N | 0
2025-07-24 | 10 | 2031-07-24 10:00 | 15.11 | 19.852 | N | 0
2025-07-24 | 11 | 2031-07-24 11:00 | 17.72 | 23.2811 | N | 0
2025-07-24 | 12 | 2031-07-24 12:00 | 20.82 | 27.3539 | N | 0
2025-07-24 | 13 | 2031-07-24 13:00 | 22.95 | 30.1524 | N | 0
2025-07-24 | 14 | 2031-07-24 14:00 | 26.62 | 34.9741 | N | 0
2025-07-24 | 15 | 2031-07-24 15:00 | 28.06 | 36.8661 | N | 0
2025-07-24 | 16 | 2031-07-24 16:00 | 29.99 | 39.4018 | Y | 2.2218 | 1
2025-07-24 | 17 | 2031-07-24 17:00 | 31.49 | 41.3725 | Y | 4.1925 | 2
2025-07-24 | 18 | 2031-07-24 18:00 | 33.01 | 43.3695 | Y | 6.1895 | 3
2025-07-24 | 19 | 2031-07-24 19:00 | 34 | 44.6702 | Y | 7.4902 | 4
2025-07-24 | 20 | 2031-07-24 20:00 | 35.51 | 46.6541 | Y | 9.4741 | 5
2025-07-24 | 21 | 2031-07-24 21:00 | 36.46 | 47.9022 | Y | 10.7222 | 6
2025-07-24 | 22 | 2031-07-24 22:00 | 36.55 | 48.0205 | Y | 10.8405 | 7
2025-07-24 | 23 | 2031-07-24 23:00 | 34.5 | 45.3271 | Y | 8.1471 | 8
2025-07-25 | 00 | 2031-07-25 | 33.45 | 43.9476 | Y | 6.7676 | 9
2025-07-25 | 01 | 2031-07-25 01:00 | 31.38 | 41.228 | Y | 4.048 | 10
2025-07-25 | 02 | 2031-07-25 02:00 | 29.08 | 38.2062 | Y | 1.0262 | 11 | 11
2025-07-25 | 03 | 2031-07-25 03:00 | 25.88 | 34.0019 | N | 0
2025-07-25 | 04 | 2031-07-25 04:00 | 23.03 | 30.2575 | N | 0
2025-07-25 | 05 | 2031-07-25 05:00 | 20.9 | 27.459 | N | 0
2025-07-25 | 06 | 2031-07-25 06:00 | 19.25 | 25.2912 | N | 0
2025-07-25 | 07 | 2031-07-25 07:00 | 18.1 | 23.7803 | N | 0
2025-07-25 | 08 | 2031-07-25 08:00 | 17.33 | 22.7687 | N | 0
2025-07-25 | 09 | 2031-07-25 09:00 | 17.24 | 22.6504 | N | 0
2025-07-25 | 10 | 2031-07-25 10:00 | 18.49 | 24.2927 | N | 0
2025-07-25 | 11 | 2031-07-25 11:00 | 20.99 | 27.5773 | N | 0
2025-07-25 | 12 | 2031-07-25 12:00 | 22.84 | 30.0079 | N | 0
2025-07-25 | 13 | 2031-07-25 13:00 | 24.06 | 31.6107 | N | 0
2025-07-25 | 14 | 2031-07-25 14:00 | 27.44 | 36.0515 | N | 0
2025-07-25 | 15 | 2031-07-25 15:00 | 28.36 | 37.2602 | Y | 0.080213 | 1
2025-07-25 | 16 | 2031-07-25 16:00 | 29.16 | 38.3113 | Y | 1.1313 | 2
2025-07-25 | 17 | 2031-07-25 17:00 | 30.39 | 39.9273 | Y | 2.7473 | 3
2025-07-25 | 18 | 2031-07-25 18:00 | 31.87 | 41.8718 | Y | 4.6918 | 4
2025-07-25 | 19 | 2031-07-25 19:00 | 33.24 | 43.6717 | Y | 6.4917 | 5
2025-07-25 | 20 | 2031-07-25 20:00 | 33.73 | 44.3155 | Y | 7.1355 | 6
2025-07-25 | 21 | 2031-07-25 21:00 | 35.17 | 46.2074 | Y | 9.0274 | 7
2025-07-25 | 22 | 2031-07-25 22:00 | 34.76 | 45.6687 | Y | 8.4887 | 8
2025-07-25 | 23 | 2031-07-25 23:00 | 33.46 | 43.9607 | Y | 6.7807 | 9
2025-07-26 | 00 | 2031-07-26 | 31.62 | 41.5433 | Y | 4.3633 | 10
2025-07-26 | 01 | 2031-07-26 01:00 | 30.45 | 40.0061 | Y | 2.8261 | 11
2025-07-26 | 02 | 2031-07-26 02:00 | 28.36 | 37.2602 | Y | 0.080213 | 12 | 12
2025-07-26 | 03 | 2031-07-26 03:00 | 25.37 | 33.3319 | N | 0
2025-07-26 | 04 | 2031-07-26 04:00 | 22.51 | 29.5743 | N | 0
2025-07-26 | 05 | 2031-07-26 05:00 | 20.19 | 26.5262 | N | 0
2025-07-26 | 06 | 2031-07-26 06:00 | 17.84 | 23.4387 | N | 0
2025-07-26 | 07 | 2031-07-26 07:00 | 16.48 | 21.6519 | N | 0
2025-07-26 | 08 | 2031-07-26 08:00 | 15.53 | 20.4038 | N | 0
2025-07-26 | 09 | 2031-07-26 09:00 | 14.94 | 19.6286 | N | 0
2025-07-26 | 10 | 2031-07-26 10:00 | 15 | 19.7074 | N | 0
2025-07-26 | 11 | 2031-07-26 11:00 | 17.63 | 23.1628 | N | 0
2025-07-26 | 12 | 2031-07-26 12:00 | 21.38 | 28.0897 | N | 0
2025-07-26 | 13 | 2031-07-26 13:00 | 24.21 | 31.8078 | N | 0
2025-07-26 | 14 | 2031-07-26 14:00 | 24.32 | 31.9523 | N | 0
2025-07-26 | 15 | 2031-07-26 15:00 | 26.08 | 34.2647 | N | 0
2025-07-26 | 16 | 2031-07-26 16:00 | 28.5 | 37.4441 | Y | 0.26415 | 1
2025-07-26 | 17 | 2031-07-26 17:00 | 29.45 | 38.6923 | Y | 1.5123 | 2
2025-07-26 | 18 | 2031-07-26 18:00 | 29.25 | 38.4295 | Y | 1.2495 | 3
2025-07-26 | 19 | 2031-07-26 19:00 | 30.06 | 39.4937 | Y | 2.3137 | 4
2025-07-26 | 20 | 2031-07-26 20:00 | 29.64 | 38.9419 | Y | 1.7619 | 5
2025-07-26 | 21 | 2031-07-26 21:00 | 28.93 | 38.0091 | Y | 0.8291 | 6
2025-07-26 | 22 | 2031-07-26 22:00 | 28.4 | 37.3128 | Y | 0.13277 | 7 | 7
2025-07-26 | 23 | 2031-07-26 23:00 | 26.98 | 35.4471 | N | 0
2025-07-27 | 00 | 2031-07-27 | 26.55 | 34.8822 | N | 0
2025-07-27 | 01 | 2031-07-27 01:00 | 25.65 | 33.6997 | N | 0
2025-07-27 | 02 | 2031-07-27 02:00 | 24.71 | 32.4647 | N | 0
2025-07-27 | 03 | 2031-07-27 03:00 | 22.47 | 29.5218 | N | 0
2025-07-27 | 04 | 2031-07-27 04:00 | 20.45 | 26.8678 | N | 0
2025-07-27 | 05 | 2031-07-27 05:00 | 18.52 | 24.3321 | N | 0
2025-07-27 | 06 | 2031-07-27 06:00 | 17.06 | 22.4139 | N | 0
2025-07-27 | 07 | 2031-07-27 07:00 | 16.09 | 21.1395 | N | 0
2025-07-27 | 08 | 2031-07-27 08:00 | 15.74 | 20.6797 | N | 0
2025-07-27 | 09 | 2031-07-27 09:00 | 15.43 | 20.2724 | N | 0
2025-07-27 | 10 | 2031-07-27 10:00 | 15.88 | 20.8636 | N | 0
2025-07-27 | 11 | 2031-07-27 11:00 | 17.58 | 23.0971 | N | 0
2025-07-27 | 12 | 2031-07-27 12:00 | 22.11 | 29.0488 | N | 0
2025-07-27 | 13 | 2031-07-27 13:00 | 25.92 | 34.0545 | N | 0
2025-07-27 | 14 | 2031-07-27 14:00 | 27.33 | 35.907 | N | 0
2025-07-27 | 15 | 2031-07-27 15:00 | 29.54 | 38.8105 | Y | 1.6305 | 1
2025-07-27 | 16 | 2031-07-27 16:00 | 31.2 | 40.9915 | Y | 3.8115 | 2
2025-07-27 | 17 | 2031-07-27 17:00 | 32.97 | 43.317 | Y | 6.137 | 3
2025-07-27 | 18 | 2031-07-27 18:00 | 33.17 | 43.5797 | Y | 6.3997 | 4
2025-07-27 | 19 | 2031-07-27 19:00 | 33.94 | 44.5914 | Y | 7.4114 | 5
2025-07-27 | 20 | 2031-07-27 20:00 | 35.14 | 46.168 | Y | 8.988 | 6
2025-07-27 | 21 | 2031-07-27 21:00 | 36.83 | 48.3884 | Y | 11.2084 | 7
2025-07-27 | 22 | 2031-07-27 22:00 | 36.97 | 48.5723 | Y | 11.3923 | 8
2025-07-27 | 23 | 2031-07-27 23:00 | 35.87 | 47.1271 | Y | 9.9471 | 9
2025-07-28 | 00 | 2031-07-28 | 33.95 | 44.6045 | Y | 7.4245 | 10
2025-07-28 | 01 | 2031-07-28 01:00 | 32.47 | 42.6601 | Y | 5.4801 | 11
2025-07-28 | 02 | 2031-07-28 02:00 | 29.78 | 39.1259 | Y | 1.9459 | 12 | 12
2025-07-28 | 03 | 2031-07-28 03:00 | 26.46 | 34.7639 | N | 0
2025-07-28 | 04 | 2031-07-28 04:00 | 23.22 | 30.5071 | N | 0
2025-07-28 | 05 | 2031-07-28 05:00 | 20.47 | 26.8941 | N | 0
2025-07-28 | 06 | 2031-07-28 06:00 | 18.57 | 24.3978 | N | 0
2025-07-28 | 07 | 2031-07-28 07:00 | 17.33 | 22.7687 | N | 0
2025-07-28 | 08 | 2031-07-28 08:00 | 16.39 | 21.5337 | N | 0
2025-07-28 | 09 | 2031-07-28 09:00 | 15.88 | 20.8636 | N | 0
2025-07-28 | 10 | 2031-07-28 10:00 | 17.79 | 23.373 | N | 0
2025-07-28 | 11 | 2031-07-28 11:00 | 21.53 | 28.2868 | N | 0
2025-07-28 | 12 | 2031-07-28 12:00 | 24.96 | 32.7932 | N | 0
2025-07-28 | 13 | 2031-07-28 13:00 | 28.02 | 36.8135 | N | 0
2025-07-28 | 14 | 2031-07-28 14:00 | 30.62 | 40.2295 | Y | 3.0495 | 1
2025-07-28 | 15 | 2031-07-28 15:00 | 32.1 | 42.1739 | Y | 4.9939 | 2
2025-07-28 | 16 | 2031-07-28 16:00 | 32.5 | 42.6995 | Y | 5.5195 | 3
2025-07-28 | 17 | 2031-07-28 17:00 | 33.38 | 43.8556 | Y | 6.6756 | 4
2025-07-28 | 18 | 2031-07-28 18:00 | 34.04 | 44.7228 | Y | 7.5428 | 5
2025-07-28 | 19 | 2031-07-28 19:00 | 35.45 | 46.5753 | Y | 9.3953 | 6
2025-07-28 | 20 | 2031-07-28 20:00 | 37.14 | 48.7956 | Y | 11.6156 | 7
2025-07-28 | 21 | 2031-07-28 21:00 | 36.84 | 48.4015 | Y | 11.2215 | 8
2025-07-28 | 22 | 2031-07-28 22:00 | 36.51 | 47.9679 | Y | 10.7879 | 9
2025-07-28 | 23 | 2031-07-28 23:00 | 35.16 | 46.1943 | Y | 9.0143 | 10
2025-07-29 | 00 | 2031-07-29 | 34.67 | 45.5505 | Y | 8.3705 | 11
2025-07-29 | 01 | 2031-07-29 01:00 | 33.38 | 43.8556 | Y | 6.6756 | 12
2025-07-29 | 02 | 2031-07-29 02:00 | 31.62 | 41.5433 | Y | 4.3633 | 13 | 13
2025-07-29 | 03 | 2031-07-29 03:00 | 27.98 | 36.761 | N | 0
2025-07-29 | 04 | 2031-07-29 04:00 | 25.2 | 33.1085 | N | 0
2025-07-29 | 05 | 2031-07-29 05:00 | 22.7 | 29.8239 | N | 0
2025-07-29 | 06 | 2031-07-29 06:00 | 20.34 | 26.7233 | N | 0
2025-07-29 | 07 | 2031-07-29 07:00 | 18.97 | 24.9234 | N | 0
2025-07-29 | 08 | 2031-07-29 08:00 | 17.85 | 23.4519 | N | 0
2025-07-29 | 09 | 2031-07-29 09:00 | 17.23 | 22.6373 | N | 0
2025-07-29 | 10 | 2031-07-29 10:00 | 18.78 | 24.6737 | N | 0
2025-07-29 | 11 | 2031-07-29 11:00 | 22.65 | 29.7582 | N | 0
2025-07-29 | 12 | 2031-07-29 12:00 | 25.96 | 34.107 | N | 0
2025-07-29 | 13 | 2031-07-29 13:00 | 28.93 | 38.0091 | Y | 0.8291 | 1
2025-07-29 | 14 | 2031-07-29 14:00 | 31.27 | 41.0835 | Y | 3.9035 | 2
2025-07-29 | 15 | 2031-07-29 15:00 | 32.21 | 42.3185 | Y | 5.1385 | 3
2025-07-29 | 16 | 2031-07-29 16:00 | 33.47 | 43.9739 | Y | 6.7939 | 4
2025-07-29 | 17 | 2031-07-29 17:00 | 34.32 | 45.0906 | Y | 7.9106 | 5
2025-07-29 | 18 | 2031-07-29 18:00 | 34.95 | 45.9184 | Y | 8.7384 | 6
2025-07-29 | 19 | 2031-07-29 19:00 | 35.59 | 46.7592 | Y | 9.5792 | 7
2025-07-29 | 20 | 2031-07-29 20:00 | 36.37 | 47.784 | Y | 10.604 | 8
2025-07-29 | 21 | 2031-07-29 21:00 | 36.65 | 48.1519 | Y | 10.9719 | 9
2025-07-29 | 22 | 2031-07-29 22:00 | 36.5 | 47.9548 | Y | 10.7748 | 10
2025-07-29 | 23 | 2031-07-29 23:00 | 35.56 | 46.7198 | Y | 9.5398 | 11
2025-07-30 | 00 | 2031-07-30 | 34.05 | 44.7359 | Y | 7.5559 | 12
2025-07-30 | 01 | 2031-07-30 01:00 | 33.44 | 43.9345 | Y | 6.7545 | 13
2025-07-30 | 02 | 2031-07-30 02:00 | 30.96 | 40.6762 | Y | 3.4962 | 14 | 14
2025-07-30 | 03 | 2031-07-30 03:00 | 27.22 | 35.7624 | N | 0
2025-07-30 | 04 | 2031-07-30 04:00 | 24.16 | 31.7421 | N | 0
2025-07-30 | 05 | 2031-07-30 05:00 | 21.3 | 27.9846 | N | 0
2025-07-30 | 06 | 2031-07-30 06:00 | 18.86 | 24.7788 | N | 0
2025-07-30 | 07 | 2031-07-30 07:00 | 17.35 | 22.7949 | N | 0
2025-07-30 | 08 | 2031-07-30 08:00 | 16.38 | 21.5205 | N | 0
2025-07-30 | 09 | 2031-07-30 09:00 | 16.34 | 21.468 | N | 0
2025-07-30 | 10 | 2031-07-30 10:00 | 17.98 | 23.6227 | N | 0
2025-07-30 | 11 | 2031-07-30 11:00 | 20.13 | 26.4474 | N | 0
2025-07-30 | 12 | 2031-07-30 12:00 | 24.26 | 31.8735 | N | 0
2025-07-30 | 13 | 2031-07-30 13:00 | 26.35 | 34.6194 | N | 0
2025-07-30 | 14 | 2031-07-30 14:00 | 29.06 | 38.1799 | Y | 0.99989 | 1
2025-07-30 | 15 | 2031-07-30 15:00 | 31.1 | 40.8601 | Y | 3.6801 | 2
2025-07-30 | 16 | 2031-07-30 16:00 | 33 | 43.3564 | Y | 6.1764 | 3
2025-07-30 | 17 | 2031-07-30 17:00 | 33.52 | 44.0396 | Y | 6.8596 | 4
2025-07-30 | 18 | 2031-07-30 18:00 | 32.79 | 43.0805 | Y | 5.9005 | 5
2025-07-30 | 19 | 2031-07-30 19:00 | 33.3 | 43.7505 | Y | 6.5705 | 6
2025-07-30 | 20 | 2031-07-30 20:00 | 33.32 | 43.7768 | Y | 6.5968 | 7
2025-07-30 | 21 | 2031-07-30 21:00 | 35.01 | 45.9972 | Y | 8.8172 | 8
2025-07-30 | 22 | 2031-07-30 22:00 | 35.19 | 46.2337 | Y | 9.0537 | 9
2025-07-30 | 23 | 2031-07-30 23:00 | 32.65 | 42.8965 | Y | 5.7165 | 10
2025-07-31 | 00 | 2031-07-31 | 30.87 | 40.5579 | Y | 3.3779 | 11
2025-07-31 | 01 | 2031-07-31 01:00 | 29.86 | 39.231 | Y | 2.051 | 12 | 12
2025-07-31 | 02 | 2031-07-31 02:00 | 27.04 | 35.526 | N | 0
2025-07-31 | 03 | 2031-07-31 03:00 | 24.06 | 31.6107 | N | 0
2025-07-31 | 04 | 2031-07-31 04:00 | 21.08 | 27.6955 | N | 0
2025-07-31 | 05 | 2031-07-31 05:00 | 18.81 | 24.7131 | N | 0
2025-07-31 | 06 | 2031-07-31 06:00 | 16.84 | 22.1249 | N | 0
2025-07-31 | 07 | 2031-07-31 07:00 | 15.64 | 20.5483 | N | 0
2025-07-31 | 08 | 2031-07-31 08:00 | 14.93 | 19.6155 | N | 0
2025-07-31 | 09 | 2031-07-31 09:00 | 15.08 | 19.8126 | N | 0
2025-07-31 | 10 | 2031-07-31 10:00 | 16.92 | 22.23 | N | 0
2025-07-31 | 11 | 2031-07-31 11:00 | 18.54 | 24.3584 | N | 0
2025-07-31 | 12 | 2031-07-31 12:00 | 21.08 | 27.6955 | N | 0
2025-07-31 | 13 | 2031-07-31 13:00 | 21.61 | 28.3919 | N | 0
2025-07-31 | 14 | 2031-07-31 14:00 | 21.4 | 28.116 | N | 0
2025-07-31 | 15 | 2031-07-31 15:00 | 21.84 | 28.694 | N | 0
2025-07-31 | 16 | 2031-07-31 16:00 | 22.71 | 29.8371 | N | 0
2025-07-31 | 17 | 2031-07-31 17:00 | 23.02 | 30.2444 | N | 0
2025-07-31 | 18 | 2031-07-31 18:00 | 22.81 | 29.9685 | N | 0
2025-07-31 | 19 | 2031-07-31 19:00 | 23.63 | 31.0458 | N | 0
2025-07-31 | 20 | 2031-07-31 20:00 | 26.02 | 34.1859 | N | 0
2025-07-31 | 21 | 2031-07-31 21:00 | 26.82 | 35.2369 | N | 0
2025-07-31 | 22 | 2031-07-31 22:00 | 26.41 | 34.6982 | N | 0
2025-07-31 | 23 | 2031-07-31 23:00 | 24.82 | 32.6093 | N | 0
2025-08-01 | 00 | 2031-08-01 | 23.21 | 30.494 | N | 0
2025-08-01 | 01 | 2031-08-01 01:00 | 22.79 | 29.9422 | N | 0
2025-08-01 | 02 | 2031-08-01 02:00 | 21.42 | 28.1422 | N | 0
2025-08-01 | 03 | 2031-08-01 03:00 | 19.11 | 25.1073 | N | 0
2025-08-01 | 04 | 2031-08-01 04:00 | 16.54 | 21.7307 | N | 0
2025-08-01 | 05 | 2031-08-01 05:00 | 14.72 | 19.3396 | N | 0
2025-08-01 | 06 | 2031-08-01 06:00 | 13.46 | 17.6841 | N | 0
2025-08-01 | 07 | 2031-08-01 07:00 | 12.59 | 16.5411 | N | 0
2025-08-01 | 08 | 2031-08-01 08:00 | 12.35 | 16.2258 | N | 0
2025-08-01 | 09 | 2031-08-01 09:00 | 12.68 | 16.6594 | N | 0
2025-08-01 | 10 | 2031-08-01 10:00 | 14.12 | 18.5513 | N | 0
2025-08-01 | 11 | 2031-08-01 11:00 | 16.26 | 21.3629 | N | 0
2025-08-01 | 12 | 2031-08-01 12:00 | 18.12 | 23.8066 | N | 0
2025-08-01 | 13 | 2031-08-01 13:00 | 20.41 | 26.8153 | N | 0
2025-08-01 | 14 | 2031-08-01 14:00 | 21.01 | 27.6036 | N | 0
2025-08-01 | 15 | 2031-08-01 15:00 | 21.89 | 28.7597 | N | 0
2025-08-01 | 16 | 2031-08-01 16:00 | 22.27 | 29.259 | N | 0
2025-08-01 | 17 | 2031-08-01 17:00 | 23.41 | 30.7568 | N | 0
2025-08-01 | 18 | 2031-08-01 18:00 | 23.83 | 31.3086 | N | 0
2025-08-01 | 19 | 2031-08-01 19:00 | 24.74 | 32.5041 | N | 0
2025-08-01 | 20 | 2031-08-01 20:00 | 24.99 | 32.8326 | N | 0
2025-08-01 | 21 | 2031-08-01 21:00 | 26.19 | 34.4092 | N | 0
2025-08-01 | 22 | 2031-08-01 22:00 | 25.81 | 33.9099 | N | 0
2025-08-01 | 23 | 2031-08-01 23:00 | 24.75 | 32.5173 | N | 0
2025-08-02 | 00 | 2031-08-02 | 22.95 | 30.1524 | N | 0
2025-08-02 | 01 | 2031-08-02 01:00 | 21.8 | 28.6415 | N | 0
2025-08-02 | 02 | 2031-08-02 02:00 | 20.52 | 26.9598 | N | 0
2025-08-02 | 03 | 2031-08-02 03:00 | 18.53 | 24.3453 | N | 0
2025-08-02 | 04 | 2031-08-02 04:00 | 16.29 | 21.4023 | N | 0
2025-08-02 | 05 | 2031-08-02 05:00 | 14.69 | 19.3002 | N | 0
2025-08-02 | 06 | 2031-08-02 06:00 | 13.37 | 17.5659 | N | 0
2025-08-02 | 07 | 2031-08-02 07:00 | 12.48 | 16.3966 | N | 0
2025-08-02 | 08 | 2031-08-02 08:00 | 11.84 | 15.5557 | N | 0
2025-08-02 | 09 | 2031-08-02 09:00 | 11.67 | 15.3324 | N | 0
2025-08-02 | 10 | 2031-08-02 10:00 | 11.76 | 15.4506 | N | 0
2025-08-02 | 11 | 2031-08-02 11:00 | 13.68 | 17.9732 | N | 0
2025-08-02 | 12 | 2031-08-02 12:00 | 16.11 | 21.1658 | N | 0
2025-08-02 | 13 | 2031-08-02 13:00 | 18.34 | 24.0956 | N | 0
2025-08-02 | 14 | 2031-08-02 14:00 | 20.48 | 26.9072 | N | 0
2025-08-02 | 15 | 2031-08-02 15:00 | 22.01 | 28.9174 | N | 0
2025-08-02 | 16 | 2031-08-02 16:00 | 23.01 | 30.2312 | N | 0
2025-08-02 | 17 | 2031-08-02 17:00 | 23.53 | 30.9144 | N | 0
2025-08-02 | 18 | 2031-08-02 18:00 | 24.09 | 31.6502 | N | 0
2025-08-02 | 19 | 2031-08-02 19:00 | 24.61 | 32.3334 | N | 0
2025-08-02 | 20 | 2031-08-02 20:00 | 25.48 | 33.4764 | N | 0
2025-08-02 | 21 | 2031-08-02 21:00 | 25.81 | 33.9099 | N | 0
2025-08-02 | 22 | 2031-08-02 22:00 | 25.61 | 33.6472 | N | 0
2025-08-02 | 23 | 2031-08-02 23:00 | 24.38 | 32.0312 | N | 0
2025-08-03 | 00 | 2031-08-03 | 22.71 | 29.8371 | N | 0
2025-08-03 | 01 | 2031-08-03 01:00 | 21.67 | 28.4707 | N | 0
2025-08-03 | 02 | 2031-08-03 02:00 | 20.2 | 26.5394 | N | 0
2025-08-03 | 03 | 2031-08-03 03:00 | 18.56 | 24.3847 | N | 0
2025-08-03 | 04 | 2031-08-03 04:00 | 16.29 | 21.4023 | N | 0
2025-08-03 | 05 | 2031-08-03 05:00 | 14.82 | 19.471 | N | 0
2025-08-03 | 06 | 2031-08-03 06:00 | 13.24 | 17.3951 | N | 0
2025-08-03 | 07 | 2031-08-03 07:00 | 12.49 | 16.4097 | N | 0
2025-08-03 | 08 | 2031-08-03 08:00 | 12.1 | 15.8973 | N | 0
2025-08-03 | 09 | 2031-08-03 09:00 | 11.64 | 15.293 | N | 0
2025-08-03 | 10 | 2031-08-03 10:00 | 11.6 | 15.2404 | N | 0
2025-08-03 | 11 | 2031-08-03 11:00 | 12.84 | 16.8696 | N | 0
2025-08-03 | 12 | 2031-08-03 12:00 | 15.1 | 19.8388 | N | 0
2025-08-03 | 13 | 2031-08-03 13:00 | 17.54 | 23.0446 | N | 0
2025-08-03 | 14 | 2031-08-03 14:00 | 19.33 | 25.3963 | N | 0
2025-08-03 | 15 | 2031-08-03 15:00 | 21.93 | 28.8123 | N | 0
2025-08-03 | 16 | 2031-08-03 16:00 | 23.54 | 30.9276 | N | 0
2025-08-03 | 17 | 2031-08-03 17:00 | 24.5 | 32.1888 | N | 0
2025-08-03 | 18 | 2031-08-03 18:00 | 25.59 | 33.6209 | N | 0
2025-08-03 | 19 | 2031-08-03 19:00 | 26.54 | 34.869 | N | 0
2025-08-03 | 20 | 2031-08-03 20:00 | 27.19 | 35.723 | N | 0
2025-08-03 | 21 | 2031-08-03 21:00 | 27.97 | 36.7478 | N | 0
2025-08-03 | 22 | 2031-08-03 22:00 | 27.86 | 36.6033 | N | 0
2025-08-03 | 23 | 2031-08-03 23:00 | 26.2 | 34.4223 | N | 0
2025-08-04 | 00 | 2031-08-04 | 24.43 | 32.0969 | N | 0
2025-08-04 | 01 | 2031-08-04 01:00 | 23.91 | 31.4137 | N | 0
2025-08-04 | 02 | 2031-08-04 02:00 | 22.04 | 28.9568 | N | 0
2025-08-04 | 03 | 2031-08-04 03:00 | 19.64 | 25.8036 | N | 0
2025-08-04 | 04 | 2031-08-04 04:00 | 17.18 | 22.5716 | N | 0
2025-08-04 | 05 | 2031-08-04 05:00 | 15.36 | 20.1804 | N | 0
2025-08-04 | 06 | 2031-08-04 06:00 | 14.02 | 18.4199 | N | 0
2025-08-04 | 07 | 2031-08-04 07:00 | 12.97 | 17.0404 | N | 0
2025-08-04 | 08 | 2031-08-04 08:00 | 12.51 | 16.436 | N | 0
2025-08-04 | 09 | 2031-08-04 09:00 | 12.31 | 16.1732 | N | 0
2025-08-04 | 10 | 2031-08-04 10:00 | 12.7 | 16.6856 | N | 0
2025-08-04 | 11 | 2031-08-04 11:00 | 14.68 | 19.287 | N | 0
2025-08-04 | 12 | 2031-08-04 12:00 | 17.27 | 22.6898 | N | 0
2025-08-04 | 13 | 2031-08-04 13:00 | 20.67 | 27.1569 | N | 0
2025-08-04 | 14 | 2031-08-04 14:00 | 23.94 | 31.4531 | N | 0
2025-08-04 | 15 | 2031-08-04 15:00 | 25.99 | 34.1464 | N | 0
2025-08-04 | 16 | 2031-08-04 16:00 | 27.64 | 36.3143 | N | 0
2025-08-04 | 17 | 2031-08-04 17:00 | 28.03 | 36.8266 | N | 0
2025-08-04 | 18 | 2031-08-04 18:00 | 29.4 | 38.6266 | Y | 1.4466 | 1
2025-08-04 | 19 | 2031-08-04 19:00 | 30.55 | 40.1375 | Y | 2.9575 | 2
2025-08-04 | 20 | 2031-08-04 20:00 | 31.94 | 41.9637 | Y | 4.7837 | 3
2025-08-04 | 21 | 2031-08-04 21:00 | 32.88 | 43.1987 | Y | 6.0187 | 4
2025-08-04 | 22 | 2031-08-04 22:00 | 31.67 | 41.609 | Y | 4.429 | 5
2025-08-04 | 23 | 2031-08-04 23:00 | 29.6 | 38.8894 | Y | 1.7094 | 6 | 6
2025-08-05 | 00 | 2031-08-05 | 28.08 | 36.8923 | N | 0
2025-08-05 | 01 | 2031-08-05 01:00 | 27.18 | 35.7099 | N | 0
2025-08-05 | 02 | 2031-08-05 02:00 | 24.75 | 32.5173 | N | 0
2025-08-05 | 03 | 2031-08-05 03:00 | 21.68 | 28.4838 | N | 0
2025-08-05 | 04 | 2031-08-05 04:00 | 18.86 | 24.7788 | N | 0
2025-08-05 | 05 | 2031-08-05 05:00 | 16.66 | 21.8884 | N | 0
2025-08-05 | 06 | 2031-08-05 06:00 | 15.11 | 19.852 | N | 0
2025-08-05 | 07 | 2031-08-05 07:00 | 14.24 | 18.7089 | N | 0
2025-08-05 | 08 | 2031-08-05 08:00 | 13.87 | 18.2228 | N | 0
2025-08-05 | 09 | 2031-08-05 09:00 | 14.11 | 18.5381 | N | 0
2025-08-05 | 10 | 2031-08-05 10:00 | 15.14 | 19.8914 | N | 0
2025-08-05 | 11 | 2031-08-05 11:00 | 17.23 | 22.6373 | N | 0
2025-08-05 | 12 | 2031-08-05 12:00 | 20.2 | 26.5394 | N | 0
2025-08-05 | 13 | 2031-08-05 13:00 | 22.63 | 29.732 | N | 0
2025-08-05 | 14 | 2031-08-05 14:00 | 25.27 | 33.2005 | N | 0
2025-08-05 | 15 | 2031-08-05 15:00 | 26.91 | 35.3552 | N | 0
2025-08-05 | 16 | 2031-08-05 16:00 | 27.84 | 36.577 | N | 0
2025-08-05 | 17 | 2031-08-05 17:00 | 28.98 | 38.0748 | Y | 0.89479 | 1
2025-08-05 | 18 | 2031-08-05 18:00 | 29.53 | 38.7974 | Y | 1.6174 | 2
2025-08-05 | 19 | 2031-08-05 19:00 | 30.96 | 40.6762 | Y | 3.4962 | 3
2025-08-05 | 20 | 2031-08-05 20:00 | 32.3 | 42.4367 | Y | 5.2567 | 4
2025-08-05 | 21 | 2031-08-05 21:00 | 32.83 | 43.133 | Y | 5.953 | 5
2025-08-05 | 22 | 2031-08-05 22:00 | 32.49 | 42.6863 | Y | 5.5063 | 6
2025-08-05 | 23 | 2031-08-05 23:00 | 31.21 | 41.0046 | Y | 3.8246 | 7
2025-08-06 | 00 | 2031-08-06 | 28.54 | 37.4967 | Y | 0.3167 | 8 | 8
2025-08-06 | 01 | 2031-08-06 01:00 | 27.28 | 35.8413 | N | 0
2025-08-06 | 02 | 2031-08-06 02:00 | 25.19 | 33.0954 | N | 0
2025-08-06 | 03 | 2031-08-06 03:00 | 22.14 | 29.0882 | N | 0
2025-08-06 | 04 | 2031-08-06 04:00 | 19.43 | 25.5277 | N | 0
2025-08-06 | 05 | 2031-08-06 05:00 | 17.01 | 22.3482 | N | 0
2025-08-06 | 06 | 2031-08-06 06:00 | 15.34 | 20.1541 | N | 0
2025-08-06 | 07 | 2031-08-06 07:00 | 14.34 | 18.8403 | N | 0
2025-08-06 | 08 | 2031-08-06 08:00 | 13.79 | 18.1177 | N | 0
2025-08-06 | 09 | 2031-08-06 09:00 | 14.14 | 18.5776 | N | 0
2025-08-06 | 10 | 2031-08-06 10:00 | 15.79 | 20.7454 | N | 0
2025-08-06 | 11 | 2031-08-06 11:00 | 17.76 | 23.3336 | N | 0
2025-08-06 | 12 | 2031-08-06 12:00 | 19.6 | 25.7511 | N | 0
2025-08-06 | 13 | 2031-08-06 13:00 | 21.42 | 28.1422 | N | 0
2025-08-06 | 14 | 2031-08-06 14:00 | 22.85 | 30.021 | N | 0
2025-08-06 | 15 | 2031-08-06 15:00 | 24.25 | 31.8604 | N | 0
2025-08-06 | 16 | 2031-08-06 16:00 | 27.13 | 35.6442 | N | 0
2025-08-06 | 17 | 2031-08-06 17:00 | 28.36 | 37.2602 | Y | 0.080213 | 1
2025-08-06 | 18 | 2031-08-06 18:00 | 29.01 | 38.1142 | Y | 0.9342 | 2
2025-08-06 | 19 | 2031-08-06 19:00 | 30.17 | 39.6382 | Y | 2.4582 | 3
2025-08-06 | 20 | 2031-08-06 20:00 | 32.01 | 42.0557 | Y | 4.8757 | 4
2025-08-06 | 21 | 2031-08-06 21:00 | 32.52 | 42.7257 | Y | 5.5457 | 5
2025-08-06 | 22 | 2031-08-06 22:00 | 32.23 | 42.3447 | Y | 5.1647 | 6
2025-08-06 | 23 | 2031-08-06 23:00 | 29.97 | 39.3755 | Y | 2.1955 | 7 | 7
2025-08-07 | 00 | 2031-08-07 | 28.29 | 37.1682 | N | 0
2025-08-07 | 01 | 2031-08-07 01:00 | 28.14 | 36.9712 | N | 0
2025-08-07 | 02 | 2031-08-07 02:00 | 25.89 | 34.0151 | N | 0
2025-08-07 | 03 | 2031-08-07 03:00 | 22.95 | 30.1524 | N | 0
2025-08-07 | 04 | 2031-08-07 04:00 | 20.4 | 26.8021 | N | 0
2025-08-07 | 05 | 2031-08-07 05:00 | 17.96 | 23.5964 | N | 0
2025-08-07 | 06 | 2031-08-07 06:00 | 16.27 | 21.376 | N | 0
2025-08-07 | 07 | 2031-08-07 07:00 | 15.45 | 20.2987 | N | 0
2025-08-07 | 08 | 2031-08-07 08:00 | 14.79 | 19.4315 | N | 0
2025-08-07 | 09 | 2031-08-07 09:00 | 15.2 | 19.9702 | N | 0
2025-08-07 | 10 | 2031-08-07 10:00 | 16.55 | 21.7439 | N | 0
2025-08-07 | 11 | 2031-08-07 11:00 | 19.62 | 25.7773 | N | 0
2025-08-07 | 12 | 2031-08-07 12:00 | 22.38 | 29.4035 | N | 0
2025-08-07 | 13 | 2031-08-07 13:00 | 24.88 | 32.6881 | N | 0
2025-08-07 | 14 | 2031-08-07 14:00 | 27.77 | 36.4851 | N | 0
2025-08-07 | 15 | 2031-08-07 15:00 | 28.86 | 37.9171 | Y | 0.73713 | 1
2025-08-07 | 16 | 2031-08-07 16:00 | 29.93 | 39.3229 | Y | 2.1429 | 2
2025-08-07 | 17 | 2031-08-07 17:00 | 30.87 | 40.5579 | Y | 3.3779 | 3
2025-08-07 | 18 | 2031-08-07 18:00 | 31.34 | 41.1754 | Y | 3.9954 | 4
2025-08-07 | 19 | 2031-08-07 19:00 | 32.07 | 42.1345 | Y | 4.9545 | 5
2025-08-07 | 20 | 2031-08-07 20:00 | 32.24 | 42.3579 | Y | 5.1779 | 6
2025-08-07 | 21 | 2031-08-07 21:00 | 32.33 | 42.4761 | Y | 5.2961 | 7
2025-08-07 | 22 | 2031-08-07 22:00 | 31.01 | 40.7419 | Y | 3.5619 | 8
2025-08-07 | 23 | 2031-08-07 23:00 | 29.52 | 38.7843 | Y | 1.6043 | 9 | 9
2025-08-08 | 00 | 2031-08-08 | 28.2 | 37.05 | N | 0
2025-08-08 | 01 | 2031-08-08 01:00 | 27.47 | 36.0909 | N | 0
2025-08-08 | 02 | 2031-08-08 02:00 | 25.17 | 33.0691 | N | 0
2025-08-08 | 03 | 2031-08-08 03:00 | 22.4 | 29.4298 | N | 0
2025-08-08 | 04 | 2031-08-08 04:00 | 19.71 | 25.8956 | N | 0
2025-08-08 | 05 | 2031-08-08 05:00 | 17.26 | 22.6767 | N | 0
2025-08-08 | 06 | 2031-08-08 06:00 | 15.58 | 20.4695 | N | 0
2025-08-08 | 07 | 2031-08-08 07:00 | 14.64 | 19.2345 | N | 0
2025-08-08 | 08 | 2031-08-08 08:00 | 14.1 | 18.525 | N | 0
2025-08-08 | 09 | 2031-08-08 09:00 | 14.11 | 18.5381 | N | 0
2025-08-08 | 10 | 2031-08-08 10:00 | 15.92 | 20.9162 | N | 0
2025-08-08 | 11 | 2031-08-08 11:00 | 19.02 | 24.989 | N | 0
2025-08-08 | 12 | 2031-08-08 12:00 | 22.03 | 28.9437 | N | 0
2025-08-08 | 13 | 2031-08-08 13:00 | 24.68 | 32.4253 | N | 0
2025-08-08 | 14 | 2031-08-08 14:00 | 27.15 | 35.6705 | N | 0
2025-08-08 | 15 | 2031-08-08 15:00 | 28.03 | 36.8266 | N | 0
2025-08-08 | 16 | 2031-08-08 16:00 | 29.62 | 38.9156 | Y | 1.7356 | 1
2025-08-08 | 17 | 2031-08-08 17:00 | 30.58 | 40.1769 | Y | 2.9969 | 2
2025-08-08 | 18 | 2031-08-08 18:00 | 31.24 | 41.044 | Y | 3.864 | 3
2025-08-08 | 19 | 2031-08-08 19:00 | 32.05 | 42.1082 | Y | 4.9282 | 4
2025-08-08 | 20 | 2031-08-08 20:00 | 31.47 | 41.3462 | Y | 4.1662 | 5
2025-08-08 | 21 | 2031-08-08 21:00 | 30.03 | 39.4543 | Y | 2.2743 | 6
2025-08-08 | 22 | 2031-08-08 22:00 | 28.79 | 37.8252 | Y | 0.64516 | 7 | 7
2025-08-08 | 23 | 2031-08-08 23:00 | 27.74 | 36.4456 | N | 0
2025-08-09 | 00 | 2031-08-09 | 27.05 | 35.5391 | N | 0
2025-08-09 | 01 | 2031-08-09 01:00 | 26.55 | 34.8822 | N | 0
2025-08-09 | 02 | 2031-08-09 02:00 | 25.1 | 32.9771 | N | 0
2025-08-09 | 03 | 2031-08-09 03:00 | 23.02 | 30.2444 | N | 0
2025-08-09 | 04 | 2031-08-09 04:00 | 20.68 | 27.17 | N | 0
2025-08-09 | 05 | 2031-08-09 05:00 | 18.35 | 24.1088 | N | 0
2025-08-09 | 06 | 2031-08-09 06:00 | 16.42 | 21.5731 | N | 0
2025-08-09 | 07 | 2031-08-09 07:00 | 15.2 | 19.9702 | N | 0
2025-08-09 | 08 | 2031-08-09 08:00 | 14.4 | 18.9191 | N | 0
2025-08-09 | 09 | 2031-08-09 09:00 | 13.95 | 18.3279 | N | 0
2025-08-09 | 10 | 2031-08-09 10:00 | 14.27 | 18.7484 | N | 0
2025-08-09 | 11 | 2031-08-09 11:00 | 16.65 | 21.8753 | N | 0
2025-08-09 | 12 | 2031-08-09 12:00 | 19.99 | 26.2635 | N | 0
2025-08-09 | 13 | 2031-08-09 13:00 | 21.99 | 28.8911 | N | 0
2025-08-09 | 14 | 2031-08-09 14:00 | 26.87 | 35.3026 | N | 0
2025-08-09 | 15 | 2031-08-09 15:00 | 28.75 | 37.7726 | Y | 0.59261 | 1
2025-08-09 | 16 | 2031-08-09 16:00 | 29.77 | 39.1127 | Y | 1.9327 | 2
2025-08-09 | 17 | 2031-08-09 17:00 | 30.88 | 40.5711 | Y | 3.3911 | 3
2025-08-09 | 18 | 2031-08-09 18:00 | 31.65 | 41.5827 | Y | 4.4027 | 4
2025-08-09 | 19 | 2031-08-09 19:00 | 32.88 | 43.1987 | Y | 6.0187 | 5
2025-08-09 | 20 | 2031-08-09 20:00 | 33.4 | 43.8819 | Y | 6.7019 | 6
2025-08-09 | 21 | 2031-08-09 21:00 | 34.05 | 44.7359 | Y | 7.5559 | 7
2025-08-09 | 22 | 2031-08-09 22:00 | 33.52 | 44.0396 | Y | 6.8596 | 8
2025-08-09 | 23 | 2031-08-09 23:00 | 31.86 | 41.8586 | Y | 4.6786 | 9
2025-08-10 | 00 | 2031-08-10 | 30.21 | 39.6908 | Y | 2.5108 | 10
2025-08-10 | 01 | 2031-08-10 01:00 | 29.16 | 38.3113 | Y | 1.1313 | 11 | 11
2025-08-10 | 02 | 2031-08-10 02:00 | 27.32 | 35.8938 | N | 0
2025-08-10 | 03 | 2031-08-10 03:00 | 24.91 | 32.7275 | N | 0
2025-08-10 | 04 | 2031-08-10 04:00 | 22.42 | 29.4561 | N | 0
2025-08-10 | 05 | 2031-08-10 05:00 | 20 | 26.2766 | N | 0
2025-08-10 | 06 | 2031-08-10 06:00 | 18.34 | 24.0956 | N | 0
2025-08-10 | 07 | 2031-08-10 07:00 | 16.73 | 21.9804 | N | 0
2025-08-10 | 08 | 2031-08-10 08:00 | 15.74 | 20.6797 | N | 0
2025-08-10 | 09 | 2031-08-10 09:00 | 14.96 | 19.6549 | N | 0
2025-08-10 | 10 | 2031-08-10 10:00 | 14.88 | 19.5498 | N | 0
2025-08-10 | 11 | 2031-08-10 11:00 | 17.39 | 22.8475 | N | 0
2025-08-10 | 12 | 2031-08-10 12:00 | 21.45 | 28.1816 | N | 0
2025-08-10 | 13 | 2031-08-10 13:00 | 25.57 | 33.5946 | N | 0
2025-08-10 | 14 | 2031-08-10 14:00 | 28.67 | 37.6675 | Y | 0.4875 | 1
2025-08-10 | 15 | 2031-08-10 15:00 | 30.77 | 40.4265 | Y | 3.2465 | 2
2025-08-10 | 16 | 2031-08-10 16:00 | 32.4 | 42.5681 | Y | 5.3881 | 3
2025-08-10 | 17 | 2031-08-10 17:00 | 33.24 | 43.6717 | Y | 6.4917 | 4
2025-08-10 | 18 | 2031-08-10 18:00 | 33.9 | 44.5388 | Y | 7.3588 | 5
2025-08-10 | 19 | 2031-08-10 19:00 | 35.19 | 46.2337 | Y | 9.0537 | 6
2025-08-10 | 20 | 2031-08-10 20:00 | 36.05 | 47.3636 | Y | 10.1836 | 7
2025-08-10 | 21 | 2031-08-10 21:00 | 36.31 | 47.7052 | Y | 10.5252 | 8
2025-08-10 | 22 | 2031-08-10 22:00 | 36.03 | 47.3373 | Y | 10.1573 | 9
2025-08-10 | 23 | 2031-08-10 23:00 | 35.54 | 46.6935 | Y | 9.5135 | 10
2025-08-11 | 00 | 2031-08-11 | 32.87 | 43.1856 | Y | 6.0056 | 11
2025-08-11 | 01 | 2031-08-11 01:00 | 32.34 | 42.4893 | Y | 5.3093 | 12
2025-08-11 | 02 | 2031-08-11 02:00 | 29.57 | 38.8499 | Y | 1.6699 | 13 | 13
2025-08-11 | 03 | 2031-08-11 03:00 | 26.22 | 34.4486 | N | 0
2025-08-11 | 04 | 2031-08-11 04:00 | 22.88 | 30.0604 | N | 0
2025-08-11 | 05 | 2031-08-11 05:00 | 20.48 | 26.9072 | N | 0
2025-08-11 | 06 | 2031-08-11 06:00 | 18.43 | 24.2139 | N | 0
2025-08-11 | 07 | 2031-08-11 07:00 | 16.96 | 22.2826 | N | 0
2025-08-11 | 08 | 2031-08-11 08:00 | 15.87 | 20.8505 | N | 0
2025-08-11 | 09 | 2031-08-11 09:00 | 16.05 | 21.087 | N | 0
2025-08-11 | 10 | 2031-08-11 10:00 | 17.25 | 22.6636 | N | 0
2025-08-11 | 11 | 2031-08-11 11:00 | 21.07 | 27.6824 | N | 0
2025-08-11 | 12 | 2031-08-11 12:00 | 24.72 | 32.4779 | N | 0
2025-08-11 | 13 | 2031-08-11 13:00 | 28.18 | 37.0237 | N | 0
2025-08-11 | 14 | 2031-08-11 14:00 | 30.95 | 40.663 | Y | 3.483 | 1
2025-08-11 | 15 | 2031-08-11 15:00 | 32.25 | 42.371 | Y | 5.191 | 2
2025-08-11 | 16 | 2031-08-11 16:00 | 33.26 | 43.698 | Y | 6.518 | 3
2025-08-11 | 17 | 2031-08-11 17:00 | 33.97 | 44.6308 | Y | 7.4508 | 4
2025-08-11 | 18 | 2031-08-11 18:00 | 34.97 | 45.9446 | Y | 8.7646 | 5
2025-08-11 | 19 | 2031-08-11 19:00 | 36.28 | 47.6657 | Y | 10.4857 | 6
2025-08-11 | 20 | 2031-08-11 20:00 | 36.29 | 47.6789 | Y | 10.4989 | 7
2025-08-11 | 21 | 2031-08-11 21:00 | 36.72 | 48.2438 | Y | 11.0638 | 8
2025-08-11 | 22 | 2031-08-11 22:00 | 36.43 | 47.8628 | Y | 10.6828 | 9
2025-08-11 | 23 | 2031-08-11 23:00 | 35.29 | 46.3651 | Y | 9.1851 | 10
2025-08-12 | 00 | 2031-08-12 | 33.7 | 44.2761 | Y | 7.0961 | 11
2025-08-12 | 01 | 2031-08-12 01:00 | 32.71 | 42.9754 | Y | 5.7954 | 12
2025-08-12 | 02 | 2031-08-12 02:00 | 30.47 | 40.0324 | Y | 2.8524 | 13 | 13
2025-08-12 | 03 | 2031-08-12 03:00 | 26.99 | 35.4603 | N | 0
2025-08-12 | 04 | 2031-08-12 04:00 | 23.78 | 31.2429 | N | 0
2025-08-12 | 05 | 2031-08-12 05:00 | 21.13 | 27.7612 | N | 0
2025-08-12 | 06 | 2031-08-12 06:00 | 18.77 | 24.6606 | N | 0
2025-08-12 | 07 | 2031-08-12 07:00 | 17.44 | 22.9132 | N | 0
2025-08-12 | 08 | 2031-08-12 08:00 | 16.7 | 21.941 | N | 0
2025-08-12 | 09 | 2031-08-12 09:00 | 16.88 | 22.1774 | N | 0
2025-08-12 | 10 | 2031-08-12 10:00 | 18.54 | 24.3584 | N | 0
2025-08-12 | 11 | 2031-08-12 11:00 | 21.42 | 28.1422 | N | 0
2025-08-12 | 12 | 2031-08-12 12:00 | 25.28 | 33.2136 | N | 0
2025-08-12 | 13 | 2031-08-12 13:00 | 28.54 | 37.4967 | Y | 0.3167 | 1
2025-08-12 | 14 | 2031-08-12 14:00 | 31.21 | 41.0046 | Y | 3.8246 | 2
2025-08-12 | 15 | 2031-08-12 15:00 | 33.23 | 43.6586 | Y | 6.4786 | 3
2025-08-12 | 16 | 2031-08-12 16:00 | 34.48 | 45.3009 | Y | 8.1209 | 4
2025-08-12 | 17 | 2031-08-12 17:00 | 36.27 | 47.6526 | Y | 10.4726 | 5
2025-08-12 | 18 | 2031-08-12 18:00 | 37.24 | 48.927 | Y | 11.747 | 6
2025-08-12 | 19 | 2031-08-12 19:00 | 37.6 | 49.4 | Y | 12.22 | 7
2025-08-12 | 20 | 2031-08-12 20:00 | 35.93 | 47.2059 | Y | 10.0259 | 8
2025-08-12 | 21 | 2031-08-12 21:00 | 35.9 | 47.1665 | Y | 9.9865 | 9
2025-08-12 | 22 | 2031-08-12 22:00 | 34.74 | 45.6424 | Y | 8.4624 | 10
2025-08-12 | 23 | 2031-08-12 23:00 | 32.95 | 43.2907 | Y | 6.1107 | 11
2025-08-13 | 00 | 2031-08-13 | 31.78 | 41.7535 | Y | 4.5735 | 12
2025-08-13 | 01 | 2031-08-13 01:00 | 31.38 | 41.228 | Y | 4.048 | 13
2025-08-13 | 02 | 2031-08-13 02:00 | 29.1 | 38.2324 | Y | 1.0524 | 14 | 14
2025-08-13 | 03 | 2031-08-13 03:00 | 25.66 | 33.7129 | N | 0
2025-08-13 | 04 | 2031-08-13 04:00 | 22.93 | 30.1261 | N | 0
2025-08-13 | 05 | 2031-08-13 05:00 | 20.23 | 26.5788 | N | 0
2025-08-13 | 06 | 2031-08-13 06:00 | 18.58 | 24.411 | N | 0
2025-08-13 | 07 | 2031-08-13 07:00 | 17.71 | 23.2679 | N | 0
2025-08-13 | 08 | 2031-08-13 08:00 | 17.2 | 22.5979 | N | 0
2025-08-13 | 09 | 2031-08-13 09:00 | 17.31 | 22.7424 | N | 0
2025-08-13 | 10 | 2031-08-13 10:00 | 18.81 | 24.7131 | N | 0
2025-08-13 | 11 | 2031-08-13 11:00 | 21.42 | 28.1422 | N | 0
2025-08-13 | 12 | 2031-08-13 12:00 | 23.86 | 31.348 | N | 0
2025-08-13 | 13 | 2031-08-13 13:00 | 26.7 | 35.0793 | N | 0
2025-08-13 | 14 | 2031-08-13 14:00 | 28.11 | 36.9318 | N | 0
2025-08-13 | 15 | 2031-08-13 15:00 | 28.77 | 37.7989 | Y | 0.61888 | 1
2025-08-13 | 16 | 2031-08-13 16:00 | 31.7 | 41.6484 | Y | 4.4684 | 2
2025-08-13 | 17 | 2031-08-13 17:00 | 32.17 | 42.2659 | Y | 5.0859 | 3
2025-08-13 | 18 | 2031-08-13 18:00 | 33.65 | 44.2104 | Y | 7.0304 | 4
2025-08-13 | 19 | 2031-08-13 19:00 | 34.62 | 45.4848 | Y | 8.3048 | 5
2025-08-13 | 20 | 2031-08-13 20:00 | 35.59 | 46.7592 | Y | 9.5792 | 6
2025-08-13 | 21 | 2031-08-13 21:00 | 35.43 | 46.549 | Y | 9.369 | 7
2025-08-13 | 22 | 2031-08-13 22:00 | 34.25 | 44.9987 | Y | 7.8187 | 8
2025-08-13 | 23 | 2031-08-13 23:00 | 32.73 | 43.0016 | Y | 5.8216 | 9
2025-08-14 | 00 | 2031-08-14 | 31.46 | 41.3331 | Y | 4.1531 | 10
2025-08-14 | 01 | 2031-08-14 01:00 | 30.6 | 40.2032 | Y | 3.0232 | 11 | 11
2025-08-14 | 02 | 2031-08-14 02:00 | 27.95 | 36.7215 | N | 0
2025-08-14 | 03 | 2031-08-14 03:00 | 24.72 | 32.4779 | N | 0
2025-08-14 | 04 | 2031-08-14 04:00 | 21.85 | 28.7072 | N | 0
2025-08-14 | 05 | 2031-08-14 05:00 | 19.71 | 25.8956 | N | 0
2025-08-14 | 06 | 2031-08-14 06:00 | 17.54 | 23.0446 | N | 0
2025-08-14 | 07 | 2031-08-14 07:00 | 16.21 | 21.2972 | N | 0
2025-08-14 | 08 | 2031-08-14 08:00 | 15.59 | 20.4826 | N | 0
2025-08-14 | 09 | 2031-08-14 09:00 | 15.52 | 20.3906 | N | 0
2025-08-14 | 10 | 2031-08-14 10:00 | 16.87 | 22.1643 | N | 0
2025-08-14 | 11 | 2031-08-14 11:00 | 20.12 | 26.4343 | N | 0
2025-08-14 | 12 | 2031-08-14 12:00 | 22.84 | 30.0079 | N | 0
2025-08-14 | 13 | 2031-08-14 13:00 | 25.97 | 34.1202 | N | 0
2025-08-14 | 14 | 2031-08-14 14:00 | 27.34 | 35.9201 | N | 0
2025-08-14 | 15 | 2031-08-14 15:00 | 28.68 | 37.6806 | Y | 0.50064 | 1
2025-08-14 | 16 | 2031-08-14 16:00 | 30.09 | 39.5331 | Y | 2.3531 | 2
2025-08-14 | 17 | 2031-08-14 17:00 | 30.23 | 39.7171 | Y | 2.5371 | 3
2025-08-14 | 18 | 2031-08-14 18:00 | 31.31 | 41.136 | Y | 3.956 | 4
2025-08-14 | 19 | 2031-08-14 19:00 | 31.94 | 41.9637 | Y | 4.7837 | 5
2025-08-14 | 20 | 2031-08-14 20:00 | 32.84 | 43.1462 | Y | 5.9662 | 6
2025-08-14 | 21 | 2031-08-14 21:00 | 33.02 | 43.3827 | Y | 6.2027 | 7
2025-08-14 | 22 | 2031-08-14 22:00 | 33.23 | 43.6586 | Y | 6.4786 | 8
2025-08-14 | 23 | 2031-08-14 23:00 | 31.6 | 41.517 | Y | 4.337 | 9
2025-08-15 | 00 | 2031-08-15 | 30.18 | 39.6514 | Y | 2.4714 | 10
2025-08-15 | 01 | 2031-08-15 01:00 | 28.76 | 37.7857 | Y | 0.60574 | 11 | 11
2025-08-15 | 02 | 2031-08-15 02:00 | 26.33 | 34.5931 | N | 0
2025-08-15 | 03 | 2031-08-15 03:00 | 23.48 | 30.8487 | N | 0
2025-08-15 | 04 | 2031-08-15 04:00 | 20.35 | 26.7364 | N | 0
2025-08-15 | 05 | 2031-08-15 05:00 | 17.93 | 23.557 | N | 0
2025-08-15 | 06 | 2031-08-15 06:00 | 16.3 | 21.4154 | N | 0
2025-08-15 | 07 | 2031-08-15 07:00 | 14.92 | 19.6023 | N | 0
2025-08-15 | 08 | 2031-08-15 08:00 | 14.11 | 18.5381 | N | 0
2025-08-15 | 09 | 2031-08-15 09:00 | 14.13 | 18.5644 | N | 0
2025-08-15 | 10 | 2031-08-15 10:00 | 15.85 | 20.8242 | N | 0
2025-08-15 | 11 | 2031-08-15 11:00 | 18.75 | 24.6343 | N | 0
2025-08-15 | 12 | 2031-08-15 12:00 | 21.65 | 28.4444 | N | 0
2025-08-15 | 13 | 2031-08-15 13:00 | 24.53 | 32.2282 | N | 0
2025-08-15 | 14 | 2031-08-15 14:00 | 26.93 | 35.3814 | N | 0
2025-08-15 | 15 | 2031-08-15 15:00 | 28.37 | 37.2734 | Y | 0.093351 | 1
2025-08-15 | 16 | 2031-08-15 16:00 | 29.54 | 38.8105 | Y | 1.6305 | 2
2025-08-15 | 17 | 2031-08-15 17:00 | 30.51 | 40.0849 | Y | 2.9049 | 3
2025-08-15 | 18 | 2031-08-15 18:00 | 31.19 | 40.9784 | Y | 3.7984 | 4
2025-08-15 | 19 | 2031-08-15 19:00 | 31.28 | 41.0966 | Y | 3.9166 | 5
2025-08-15 | 20 | 2031-08-15 20:00 | 32 | 42.0426 | Y | 4.8626 | 6
2025-08-15 | 21 | 2031-08-15 21:00 | 32.71 | 42.9754 | Y | 5.7954 | 7
2025-08-15 | 22 | 2031-08-15 22:00 | 32.45 | 42.6338 | Y | 5.4538 | 8
2025-08-15 | 23 | 2031-08-15 23:00 | 30.73 | 40.374 | Y | 3.194 | 9 | 9
2025-08-16 | 00 | 2031-08-16 | 28.15 | 36.9843 | N | 0
2025-08-16 | 01 | 2031-08-16 01:00 | 27.23 | 35.7756 | N | 0
2025-08-16 | 02 | 2031-08-16 02:00 | 25.05 | 32.9114 | N | 0
2025-08-16 | 03 | 2031-08-16 03:00 | 22.5 | 29.5612 | N | 0
2025-08-16 | 04 | 2031-08-16 04:00 | 20.11 | 26.4211 | N | 0
2025-08-16 | 05 | 2031-08-16 05:00 | 17.39 | 22.8475 | N | 0
2025-08-16 | 06 | 2031-08-16 06:00 | 15.75 | 20.6928 | N | 0
2025-08-16 | 07 | 2031-08-16 07:00 | 14.67 | 19.2739 | N | 0
2025-08-16 | 08 | 2031-08-16 08:00 | 14.09 | 18.5119 | N | 0
2025-08-16 | 09 | 2031-08-16 09:00 | 13.7 | 17.9995 | N | 0
2025-08-16 | 10 | 2031-08-16 10:00 | 13.86 | 18.2097 | N | 0
2025-08-16 | 11 | 2031-08-16 11:00 | 16.4 | 21.5468 | N | 0
2025-08-16 | 12 | 2031-08-16 12:00 | 20.4 | 26.8021 | N | 0
2025-08-16 | 13 | 2031-08-16 13:00 | 24.05 | 31.5976 | N | 0
2025-08-16 | 14 | 2031-08-16 14:00 | 26.73 | 35.1187 | N | 0
2025-08-16 | 15 | 2031-08-16 15:00 | 28.77 | 37.7989 | Y | 0.61888 | 1
2025-08-16 | 16 | 2031-08-16 16:00 | 30.58 | 40.1769 | Y | 2.9969 | 2
2025-08-16 | 17 | 2031-08-16 17:00 | 31.31 | 41.136 | Y | 3.956 | 3
2025-08-16 | 18 | 2031-08-16 18:00 | 31.69 | 41.6353 | Y | 4.4553 | 4
2025-08-16 | 19 | 2031-08-16 19:00 | 32.44 | 42.6206 | Y | 5.4406 | 5
2025-08-16 | 20 | 2031-08-16 20:00 | 32.43 | 42.6075 | Y | 5.4275 | 6
2025-08-16 | 21 | 2031-08-16 21:00 | 32.76 | 43.0411 | Y | 5.8611 | 7
2025-08-16 | 22 | 2031-08-16 22:00 | 32.92 | 43.2513 | Y | 6.0713 | 8
2025-08-16 | 23 | 2031-08-16 23:00 | 31.18 | 40.9652 | Y | 3.7852 | 9
2025-08-17 | 00 | 2031-08-17 | 29.55 | 38.8237 | Y | 1.6437 | 10
2025-08-17 | 01 | 2031-08-17 01:00 | 28.57 | 37.5361 | Y | 0.35612 | 11 | 11
2025-08-17 | 02 | 2031-08-17 02:00 | 26.74 | 35.1318 | N | 0
2025-08-17 | 03 | 2031-08-17 03:00 | 24.33 | 31.9655 | N | 0
2025-08-17 | 04 | 2031-08-17 04:00 | 21.5 | 28.2473 | N | 0
2025-08-17 | 05 | 2031-08-17 05:00 | 19.43 | 25.5277 | N | 0
2025-08-17 | 06 | 2031-08-17 06:00 | 17.36 | 22.8081 | N | 0
2025-08-17 | 07 | 2031-08-17 07:00 | 16.25 | 21.3497 | N | 0
2025-08-17 | 08 | 2031-08-17 08:00 | 15.66 | 20.5746 | N | 0
2025-08-17 | 09 | 2031-08-17 09:00 | 15.59 | 20.4826 | N | 0
2025-08-17 | 10 | 2031-08-17 10:00 | 15.51 | 20.3775 | N | 0
2025-08-17 | 11 | 2031-08-17 11:00 | 16.87 | 22.1643 | N | 0
2025-08-17 | 12 | 2031-08-17 12:00 | 19.22 | 25.2518 | N | 0
2025-08-17 | 13 | 2031-08-17 13:00 | 22.48 | 29.5349 | N | 0
2025-08-17 | 14 | 2031-08-17 14:00 | 23.8 | 31.2691 | N | 0
2025-08-17 | 15 | 2031-08-17 15:00 | 24.15 | 31.729 | N | 0
2025-08-17 | 16 | 2031-08-17 16:00 | 25.14 | 33.0297 | N | 0
2025-08-17 | 17 | 2031-08-17 17:00 | 25.2 | 33.1085 | N | 0
2025-08-17 | 18 | 2031-08-17 18:00 | 25.06 | 32.9246 | N | 0
2025-08-17 | 19 | 2031-08-17 19:00 | 25.14 | 33.0297 | N | 0
2025-08-17 | 20 | 2031-08-17 20:00 | 27.84 | 36.577 | N | 0
2025-08-17 | 21 | 2031-08-17 21:00 | 29.18 | 38.3376 | Y | 1.1576 | 1
2025-08-17 | 22 | 2031-08-17 22:00 | 29.14 | 38.285 | Y | 1.105 | 2 | 2
2025-08-17 | 23 | 2031-08-17 23:00 | 28 | 36.7872 | N | 0
2025-08-18 | 00 | 2031-08-18 | 25.52 | 33.5289 | N | 0
2025-08-18 | 01 | 2031-08-18 01:00 | 24.6 | 32.3202 | N | 0
2025-08-18 | 02 | 2031-08-18 02:00 | 21.73 | 28.5495 | N | 0
2025-08-18 | 03 | 2031-08-18 03:00 | 19.01 | 24.9759 | N | 0
2025-08-18 | 04 | 2031-08-18 04:00 | 16.15 | 21.2184 | N | 0
2025-08-18 | 05 | 2031-08-18 05:00 | 14.41 | 18.9323 | N | 0
2025-08-18 | 06 | 2031-08-18 06:00 | 13.01 | 17.0929 | N | 0
2025-08-18 | 07 | 2031-08-18 07:00 | 12.38 | 16.2652 | N | 0
2025-08-18 | 08 | 2031-08-18 08:00 | 11.96 | 15.7134 | N | 0
2025-08-18 | 09 | 2031-08-18 09:00 | 12.41 | 16.3046 | N | 0
2025-08-18 | 10 | 2031-08-18 10:00 | 13.21 | 17.3557 | N | 0
2025-08-18 | 11 | 2031-08-18 11:00 | 15.51 | 20.3775 | N | 0
2025-08-18 | 12 | 2031-08-18 12:00 | 17.46 | 22.9395 | N | 0
2025-08-18 | 13 | 2031-08-18 13:00 | 18.43 | 24.2139 | N | 0
2025-08-18 | 14 | 2031-08-18 14:00 | 19.89 | 26.1321 | N | 0
2025-08-18 | 15 | 2031-08-18 15:00 | 20.84 | 27.3802 | N | 0
2025-08-18 | 16 | 2031-08-18 16:00 | 21.35 | 28.0503 | N | 0
2025-08-18 | 17 | 2031-08-18 17:00 | 21.63 | 28.4181 | N | 0
2025-08-18 | 18 | 2031-08-18 18:00 | 22.12 | 29.0619 | N | 0
2025-08-18 | 19 | 2031-08-18 19:00 | 22.98 | 30.1918 | N | 0
2025-08-18 | 20 | 2031-08-18 20:00 | 23.98 | 31.5056 | N | 0
2025-08-18 | 21 | 2031-08-18 21:00 | 24.82 | 32.6093 | N | 0
2025-08-18 | 22 | 2031-08-18 22:00 | 24.02 | 31.5582 | N | 0
2025-08-18 | 23 | 2031-08-18 23:00 | 22.58 | 29.6663 | N | 0
2025-08-19 | 00 | 2031-08-19 | 21.66 | 28.4576 | N | 0
2025-08-19 | 01 | 2031-08-19 01:00 | 21.29 | 27.9714 | N | 0
2025-08-19 | 02 | 2031-08-19 02:00 | 19.33 | 25.3963 | N | 0
2025-08-19 | 03 | 2031-08-19 03:00 | 17.23 | 22.6373 | N | 0
2025-08-19 | 04 | 2031-08-19 04:00 | 15.27 | 20.0622 | N | 0
2025-08-19 | 05 | 2031-08-19 05:00 | 13.73 | 18.0389 | N | 0
2025-08-19 | 06 | 2031-08-19 06:00 | 12.77 | 16.7776 | N | 0
2025-08-19 | 07 | 2031-08-19 07:00 | 12.14 | 15.9499 | N | 0
2025-08-19 | 08 | 2031-08-19 08:00 | 11.98 | 15.7397 | N | 0
2025-08-19 | 09 | 2031-08-19 09:00 | 12.54 | 16.4754 | N | 0
2025-08-19 | 10 | 2031-08-19 10:00 | 13.94 | 18.3148 | N | 0
2025-08-19 | 11 | 2031-08-19 11:00 | 15.71 | 20.6403 | N | 0
2025-08-19 | 12 | 2031-08-19 12:00 | 17.37 | 22.8212 | N | 0
2025-08-19 | 13 | 2031-08-19 13:00 | 18.39 | 24.1613 | N | 0
2025-08-19 | 14 | 2031-08-19 14:00 | 18.97 | 24.9234 | N | 0
2025-08-19 | 15 | 2031-08-19 15:00 | 19.85 | 26.0795 | N | 0
2025-08-19 | 16 | 2031-08-19 16:00 | 20.67 | 27.1569 | N | 0
2025-08-19 | 17 | 2031-08-19 17:00 | 20.72 | 27.2226 | N | 0
2025-08-19 | 18 | 2031-08-19 18:00 | 21.04 | 27.643 | N | 0
2025-08-19 | 19 | 2031-08-19 19:00 | 20.81 | 27.3408 | N | 0
2025-08-19 | 20 | 2031-08-19 20:00 | 22.06 | 28.9831 | N | 0
2025-08-19 | 21 | 2031-08-19 21:00 | 22.64 | 29.7451 | N | 0
2025-08-19 | 22 | 2031-08-19 22:00 | 22.28 | 29.2721 | N | 0
2025-08-19 | 23 | 2031-08-19 23:00 | 21.45 | 28.1816 | N | 0
2025-08-20 | 00 | 2031-08-20 | 21.39 | 28.1028 | N | 0
2025-08-20 | 01 | 2031-08-20 01:00 | 21 | 27.5904 | N | 0
2025-08-20 | 02 | 2031-08-20 02:00 | 19.55 | 25.6854 | N | 0
2025-08-20 | 03 | 2031-08-20 03:00 | 17.23 | 22.6373 | N | 0
2025-08-20 | 04 | 2031-08-20 04:00 | 15.36 | 20.1804 | N | 0
2025-08-20 | 05 | 2031-08-20 05:00 | 14.11 | 18.5381 | N | 0
2025-08-20 | 06 | 2031-08-20 06:00 | 13.15 | 17.2769 | N | 0
2025-08-20 | 07 | 2031-08-20 07:00 | 12.62 | 16.5805 | N | 0
2025-08-20 | 08 | 2031-08-20 08:00 | 12.37 | 16.2521 | N | 0
2025-08-20 | 09 | 2031-08-20 09:00 | 13.12 | 17.2374 | N | 0
2025-08-20 | 10 | 2031-08-20 10:00 | 14.77 | 19.4053 | N | 0
2025-08-20 | 11 | 2031-08-20 11:00 | 16.72 | 21.9672 | N | 0
2025-08-20 | 12 | 2031-08-20 12:00 | 17.81 | 23.3993 | N | 0
2025-08-20 | 13 | 2031-08-20 13:00 | 18.67 | 24.5292 | N | 0
2025-08-20 | 14 | 2031-08-20 14:00 | 19.7 | 25.8824 | N | 0
2025-08-20 | 15 | 2031-08-20 15:00 | 20.34 | 26.7233 | N | 0
2025-08-20 | 16 | 2031-08-20 16:00 | 20.69 | 27.1831 | N | 0
2025-08-20 | 17 | 2031-08-20 17:00 | 21.62 | 28.405 | N | 0
2025-08-20 | 18 | 2031-08-20 18:00 | 21.52 | 28.2736 | N | 0
2025-08-20 | 19 | 2031-08-20 19:00 | 20.56 | 27.0123 | N | 0
2025-08-20 | 20 | 2031-08-20 20:00 | 21.17 | 27.8138 | N | 0
2025-08-20 | 21 | 2031-08-20 21:00 | 22.56 | 29.64 | N | 0
2025-08-20 | 22 | 2031-08-20 22:00 | 22.01 | 28.9174 | N | 0
2025-08-20 | 23 | 2031-08-20 23:00 | 21.05 | 27.6561 | N | 0
2025-08-21 | 00 | 2031-08-21 | 21.07 | 27.6824 | N | 0
2025-08-21 | 01 | 2031-08-21 01:00 | 20.68 | 27.17 | N | 0
2025-08-21 | 02 | 2031-08-21 02:00 | 19.44 | 25.5409 | N | 0
2025-08-21 | 03 | 2031-08-21 03:00 | 17.19 | 22.5847 | N | 0
2025-08-21 | 04 | 2031-08-21 04:00 | 15.33 | 20.141 | N | 0
2025-08-21 | 05 | 2031-08-21 05:00 | 13.98 | 18.3673 | N | 0
2025-08-21 | 06 | 2031-08-21 06:00 | 12.75 | 16.7513 | N | 0
2025-08-21 | 07 | 2031-08-21 07:00 | 12.13 | 15.9368 | N | 0
2025-08-21 | 08 | 2031-08-21 08:00 | 11.85 | 15.5689 | N | 0
2025-08-21 | 09 | 2031-08-21 09:00 | 12.42 | 16.3178 | N | 0
2025-08-21 | 10 | 2031-08-21 10:00 | 13.86 | 18.2097 | N | 0
2025-08-21 | 11 | 2031-08-21 11:00 | 15.72 | 20.6534 | N | 0
2025-08-21 | 12 | 2031-08-21 12:00 | 17.62 | 23.1497 | N | 0
2025-08-21 | 13 | 2031-08-21 13:00 | 19.19 | 25.2124 | N | 0
2025-08-21 | 14 | 2031-08-21 14:00 | 20.34 | 26.7233 | N | 0
2025-08-21 | 15 | 2031-08-21 15:00 | 20.71 | 27.2094 | N | 0
2025-08-21 | 16 | 2031-08-21 16:00 | 20.26 | 26.6182 | N | 0
2025-08-21 | 17 | 2031-08-21 17:00 | 20.53 | 26.9729 | N | 0
2025-08-21 | 18 | 2031-08-21 18:00 | 21.62 | 28.405 | N | 0
2025-08-21 | 19 | 2031-08-21 19:00 | 22.62 | 29.7188 | N | 0
2025-08-21 | 20 | 2031-08-21 20:00 | 24.31 | 31.9392 | N | 0
2025-08-21 | 21 | 2031-08-21 21:00 | 25.26 | 33.1873 | N | 0
2025-08-21 | 22 | 2031-08-21 22:00 | 25.46 | 33.4501 | N | 0
2025-08-21 | 23 | 2031-08-21 23:00 | 24.77 | 32.5436 | N | 0
2025-08-22 | 00 | 2031-08-22 | 23.4 | 30.7436 | N | 0
2025-08-22 | 01 | 2031-08-22 01:00 | 22.73 | 29.8634 | N | 0
2025-08-22 | 02 | 2031-08-22 02:00 | 20.78 | 27.3014 | N | 0
2025-08-22 | 03 | 2031-08-22 03:00 | 18.42 | 24.2007 | N | 0
2025-08-22 | 04 | 2031-08-22 04:00 | 16.17 | 21.2446 | N | 0
2025-08-22 | 05 | 2031-08-22 05:00 | 14.45 | 18.9848 | N | 0
2025-08-22 | 06 | 2031-08-22 06:00 | 13.21 | 17.3557 | N | 0
2025-08-22 | 07 | 2031-08-22 07:00 | 12.62 | 16.5805 | N | 0
2025-08-22 | 08 | 2031-08-22 08:00 | 12.29 | 16.147 | N | 0
2025-08-22 | 09 | 2031-08-22 09:00 | 12.71 | 16.6988 | N | 0
2025-08-22 | 10 | 2031-08-22 10:00 | 14.34 | 18.8403 | N | 0
2025-08-22 | 11 | 2031-08-22 11:00 | 17.17 | 22.5585 | N | 0
2025-08-22 | 12 | 2031-08-22 12:00 | 19.66 | 25.8299 | N | 0
2025-08-22 | 13 | 2031-08-22 13:00 | 21.91 | 28.786 | N | 0
2025-08-22 | 14 | 2031-08-22 14:00 | 24.24 | 31.8472 | N | 0
2025-08-22 | 15 | 2031-08-22 15:00 | 25.27 | 33.2005 | N | 0
2025-08-22 | 16 | 2031-08-22 16:00 | 26.03 | 34.199 | N | 0
2025-08-22 | 17 | 2031-08-22 17:00 | 26.93 | 35.3814 | N | 0
2025-08-22 | 18 | 2031-08-22 18:00 | 27.32 | 35.8938 | N | 0
2025-08-22 | 19 | 2031-08-22 19:00 | 27.84 | 36.577 | N | 0
2025-08-22 | 20 | 2031-08-22 20:00 | 28.49 | 37.431 | Y | 0.25101 | 1
2025-08-22 | 21 | 2031-08-22 21:00 | 28.61 | 37.5887 | Y | 0.40867 | 2
2025-08-22 | 22 | 2031-08-22 22:00 | 28.3 | 37.1814 | Y | 0.001383 | 3 | 3
2025-08-22 | 23 | 2031-08-22 23:00 | 26.75 | 35.1449 | N | 0
2025-08-23 | 00 | 2031-08-23 | 25.14 | 33.0297 | N | 0
2025-08-23 | 01 | 2031-08-23 01:00 | 24.67 | 32.4122 | N | 0
2025-08-23 | 02 | 2031-08-23 02:00 | 22.53 | 29.6006 | N | 0
2025-08-23 | 03 | 2031-08-23 03:00 | 20.37 | 26.7627 | N | 0
2025-08-23 | 04 | 2031-08-23 04:00 | 17.71 | 23.2679 | N | 0
2025-08-23 | 05 | 2031-08-23 05:00 | 15.83 | 20.7979 | N | 0
2025-08-23 | 06 | 2031-08-23 06:00 | 14.59 | 19.1688 | N | 0
2025-08-23 | 07 | 2031-08-23 07:00 | 13.58 | 17.8418 | N | 0
2025-08-23 | 08 | 2031-08-23 08:00 | 12.67 | 16.6462 | N | 0
2025-08-23 | 09 | 2031-08-23 09:00 | 12.48 | 16.3966 | N | 0
2025-08-23 | 10 | 2031-08-23 10:00 | 12.58 | 16.528 | N | 0
2025-08-23 | 11 | 2031-08-23 11:00 | 14.67 | 19.2739 | N | 0
2025-08-23 | 12 | 2031-08-23 12:00 | 18.32 | 24.0694 | N | 0
2025-08-23 | 13 | 2031-08-23 13:00 | 19.96 | 26.224 | N | 0
2025-08-23 | 14 | 2031-08-23 14:00 | 21.79 | 28.6284 | N | 0
2025-08-23 | 15 | 2031-08-23 15:00 | 24.18 | 31.7684 | N | 0
2025-08-23 | 16 | 2031-08-23 16:00 | 24.77 | 32.5436 | N | 0
2025-08-23 | 17 | 2031-08-23 17:00 | 25.32 | 33.2662 | N | 0
2025-08-23 | 18 | 2031-08-23 18:00 | 25.31 | 33.253 | N | 0
2025-08-23 | 19 | 2031-08-23 19:00 | 24.86 | 32.6618 | N | 0
2025-08-23 | 20 | 2031-08-23 20:00 | 24.95 | 32.7801 | N | 0
2025-08-23 | 21 | 2031-08-23 21:00 | 26.38 | 34.6588 | N | 0
2025-08-23 | 22 | 2031-08-23 22:00 | 25.52 | 33.5289 | N | 0
2025-08-23 | 23 | 2031-08-23 23:00 | 24.89 | 32.7012 | N | 0
2025-08-24 | 00 | 2031-08-24 | 24.08 | 31.637 | N | 0
2025-08-24 | 01 | 2031-08-24 01:00 | 23.59 | 30.9932 | N | 0
2025-08-24 | 02 | 2031-08-24 02:00 | 22.3 | 29.2984 | N | 0
2025-08-24 | 03 | 2031-08-24 03:00 | 20.87 | 27.4196 | N | 0
2025-08-24 | 04 | 2031-08-24 04:00 | 18.71 | 24.5818 | N | 0
2025-08-24 | 05 | 2031-08-24 05:00 | 16.75 | 22.0066 | N | 0
2025-08-24 | 06 | 2031-08-24 06:00 | 15.49 | 20.3512 | N | 0
2025-08-24 | 07 | 2031-08-24 07:00 | 14.4 | 18.9191 | N | 0
2025-08-24 | 08 | 2031-08-24 08:00 | 13.61 | 17.8812 | N | 0
2025-08-24 | 09 | 2031-08-24 09:00 | 12.9 | 16.9484 | N | 0
2025-08-24 | 10 | 2031-08-24 10:00 | 12.76 | 16.7645 | N | 0
2025-08-24 | 11 | 2031-08-24 11:00 | 15.18 | 19.9439 | N | 0
2025-08-24 | 12 | 2031-08-24 12:00 | 17.59 | 23.1103 | N | 0
2025-08-24 | 13 | 2031-08-24 13:00 | 20.05 | 26.3423 | N | 0
2025-08-24 | 14 | 2031-08-24 14:00 | 21.88 | 28.7466 | N | 0
2025-08-24 | 15 | 2031-08-24 15:00 | 24.14 | 31.7159 | N | 0
2025-08-24 | 16 | 2031-08-24 16:00 | 25.95 | 34.0939 | N | 0
2025-08-24 | 17 | 2031-08-24 17:00 | 26.24 | 34.4749 | N | 0
2025-08-24 | 18 | 2031-08-24 18:00 | 26.69 | 35.0661 | N | 0
2025-08-24 | 19 | 2031-08-24 19:00 | 27.52 | 36.1566 | N | 0
2025-08-24 | 20 | 2031-08-24 20:00 | 28.24 | 37.1026 | N | 0
2025-08-24 | 21 | 2031-08-24 21:00 | 28.88 | 37.9434 | Y | 0.7634 | 1
2025-08-24 | 22 | 2031-08-24 22:00 | 28.35 | 37.2471 | Y | 0.067074 | 2 | 2
2025-08-24 | 23 | 2031-08-24 23:00 | 26.65 | 35.0136 | N | 0
2025-08-25 | 00 | 2031-08-25 | 25.41 | 33.3844 | N | 0
2025-08-25 | 01 | 2031-08-25 01:00 | 24.61 | 32.3334 | N | 0
2025-08-25 | 02 | 2031-08-25 02:00 | 21.95 | 28.8386 | N | 0
2025-08-25 | 03 | 2031-08-25 03:00 | 18.99 | 24.9496 | N | 0
2025-08-25 | 04 | 2031-08-25 04:00 | 16.52 | 21.7045 | N | 0
2025-08-25 | 05 | 2031-08-25 05:00 | 14.65 | 19.2476 | N | 0
2025-08-25 | 06 | 2031-08-25 06:00 | 13.36 | 17.5528 | N | 0
2025-08-25 | 07 | 2031-08-25 07:00 | 12.87 | 16.909 | N | 0
2025-08-25 | 08 | 2031-08-25 08:00 | 12.36 | 16.2389 | N | 0
2025-08-25 | 09 | 2031-08-25 09:00 | 12.47 | 16.3835 | N | 0
2025-08-25 | 10 | 2031-08-25 10:00 | 13.59 | 17.8549 | N | 0
2025-08-25 | 11 | 2031-08-25 11:00 | 16.27 | 21.376 | N | 0
2025-08-25 | 12 | 2031-08-25 12:00 | 18.14 | 23.8329 | N | 0
2025-08-25 | 13 | 2031-08-25 13:00 | 19.61 | 25.7642 | N | 0
2025-08-25 | 14 | 2031-08-25 14:00 | 21.43 | 28.1554 | N | 0
2025-08-25 | 15 | 2031-08-25 15:00 | 22 | 28.9043 | N | 0
2025-08-25 | 16 | 2031-08-25 16:00 | 22.06 | 28.9831 | N | 0
2025-08-25 | 17 | 2031-08-25 17:00 | 21.83 | 28.6809 | N | 0
2025-08-25 | 18 | 2031-08-25 18:00 | 21.03 | 27.6298 | N | 0
2025-08-25 | 19 | 2031-08-25 19:00 | 21.8 | 28.6415 | N | 0
2025-08-25 | 20 | 2031-08-25 20:00 | 22.38 | 29.4035 | N | 0
2025-08-25 | 21 | 2031-08-25 21:00 | 23.18 | 30.4546 | N | 0
2025-08-25 | 22 | 2031-08-25 22:00 | 22.07 | 28.9962 | N | 0
2025-08-25 | 23 | 2031-08-25 23:00 | 21.21 | 27.8663 | N | 0
2025-08-26 | 00 | 2031-08-26 | 20.71 | 27.2094 | N | 0
2025-08-26 | 01 | 2031-08-26 01:00 | 20.22 | 26.5656 | N | 0
2025-08-26 | 02 | 2031-08-26 02:00 | 18.33 | 24.0825 | N | 0
2025-08-26 | 03 | 2031-08-26 03:00 | 16.23 | 21.3235 | N | 0
2025-08-26 | 04 | 2031-08-26 04:00 | 14.57 | 19.1425 | N | 0
2025-08-26 | 05 | 2031-08-26 05:00 | 13.03 | 17.1192 | N | 0
2025-08-26 | 06 | 2031-08-26 06:00 | 11.8 | 15.5032 | N | 0
2025-08-26 | 07 | 2031-08-26 07:00 | 11.43 | 15.0171 | N | 0
2025-08-26 | 08 | 2031-08-26 08:00 | 11.3 | 14.8463 | N | 0
2025-08-26 | 09 | 2031-08-26 09:00 | 11.72 | 15.3981 | N | 0
2025-08-26 | 10 | 2031-08-26 10:00 | 12.89 | 16.9353 | N | 0
2025-08-26 | 11 | 2031-08-26 11:00 | 14.69 | 19.3002 | N | 0
2025-08-26 | 12 | 2031-08-26 12:00 | 16.1 | 21.1527 | N | 0
2025-08-26 | 13 | 2031-08-26 13:00 | 17.14 | 22.519 | N | 0
2025-08-26 | 14 | 2031-08-26 14:00 | 18.44 | 24.227 | N | 0
2025-08-26 | 15 | 2031-08-26 15:00 | 18.92 | 24.8577 | N | 0
2025-08-26 | 16 | 2031-08-26 16:00 | 19.43 | 25.5277 | N | 0
2025-08-26 | 17 | 2031-08-26 17:00 | 19.62 | 25.7773 | N | 0
2025-08-26 | 18 | 2031-08-26 18:00 | 19.84 | 26.0664 | N | 0
2025-08-26 | 19 | 2031-08-26 19:00 | 20.14 | 26.4605 | N | 0
2025-08-26 | 20 | 2031-08-26 20:00 | 20.45 | 26.8678 | N | 0
2025-08-26 | 21 | 2031-08-26 21:00 | 21.35 | 28.0503 | N | 0
2025-08-26 | 22 | 2031-08-26 22:00 | 20.61 | 27.078 | N | 0
2025-08-26 | 23 | 2031-08-26 23:00 | 19.77 | 25.9744 | N | 0
2025-08-27 | 00 | 2031-08-27 | 19.87 | 26.1058 | N | 0
2025-08-27 | 01 | 2031-08-27 01:00 | 19.47 | 25.5803 | N | 0
2025-08-27 | 02 | 2031-08-27 02:00 | 17.83 | 23.4256 | N | 0
2025-08-27 | 03 | 2031-08-27 03:00 | 15.93 | 20.9293 | N | 0
2025-08-27 | 04 | 2031-08-27 04:00 | 14.21 | 18.6695 | N | 0
2025-08-27 | 05 | 2031-08-27 05:00 | 12.92 | 16.9747 | N | 0
2025-08-27 | 06 | 2031-08-27 06:00 | 11.87 | 15.5952 | N | 0
2025-08-27 | 07 | 2031-08-27 07:00 | 11.4 | 14.9777 | N | 0
2025-08-27 | 08 | 2031-08-27 08:00 | 11.14 | 14.6361 | N | 0
2025-08-27 | 09 | 2031-08-27 09:00 | 11.85 | 15.5689 | N | 0
2025-08-27 | 10 | 2031-08-27 10:00 | 13.02 | 17.1061 | N | 0
2025-08-27 | 11 | 2031-08-27 11:00 | 14.77 | 19.4053 | N | 0
2025-08-27 | 12 | 2031-08-27 12:00 | 16.55 | 21.7439 | N | 0
2025-08-27 | 13 | 2031-08-27 13:00 | 17.33 | 22.7687 | N | 0
2025-08-27 | 14 | 2031-08-27 14:00 | 18.71 | 24.5818 | N | 0
2025-08-27 | 15 | 2031-08-27 15:00 | 19.27 | 25.3175 | N | 0
2025-08-27 | 16 | 2031-08-27 16:00 | 19.71 | 25.8956 | N | 0
2025-08-27 | 17 | 2031-08-27 17:00 | 19.77 | 25.9744 | N | 0
2025-08-27 | 18 | 2031-08-27 18:00 | 20.49 | 26.9204 | N | 0
2025-08-27 | 19 | 2031-08-27 19:00 | 20.06 | 26.3554 | N | 0
2025-08-27 | 20 | 2031-08-27 20:00 | 21.36 | 28.0634 | N | 0
2025-08-27 | 21 | 2031-08-27 21:00 | 22.6 | 29.6926 | N | 0
2025-08-27 | 22 | 2031-08-27 22:00 | 22.47 | 29.5218 | N | 0
2025-08-27 | 23 | 2031-08-27 23:00 | 21 | 27.5904 | N | 0
2025-08-28 | 00 | 2031-08-28 | 20.41 | 26.8153 | N | 0
2025-08-28 | 01 | 2031-08-28 01:00 | 19.78 | 25.9876 | N | 0
2025-08-28 | 02 | 2031-08-28 02:00 | 17.81 | 23.3993 | N | 0
2025-08-28 | 03 | 2031-08-28 03:00 | 15.8 | 20.7585 | N | 0
2025-08-28 | 04 | 2031-08-28 04:00 | 14.1 | 18.525 | N | 0
2025-08-28 | 05 | 2031-08-28 05:00 | 12.87 | 16.909 | N | 0
2025-08-28 | 06 | 2031-08-28 06:00 | 12.14 | 15.9499 | N | 0
2025-08-28 | 07 | 2031-08-28 07:00 | 11.58 | 15.2141 | N | 0
2025-08-28 | 08 | 2031-08-28 08:00 | 11.39 | 14.9645 | N | 0
2025-08-28 | 09 | 2031-08-28 09:00 | 11.83 | 15.5426 | N | 0
2025-08-28 | 10 | 2031-08-28 10:00 | 13.25 | 17.4082 | N | 0
2025-08-28 | 11 | 2031-08-28 11:00 | 14.89 | 19.5629 | N | 0
2025-08-28 | 12 | 2031-08-28 12:00 | 16.36 | 21.4943 | N | 0
2025-08-28 | 13 | 2031-08-28 13:00 | 16.93 | 22.2431 | N | 0
2025-08-28 | 14 | 2031-08-28 14:00 | 17.93 | 23.557 | N | 0
2025-08-28 | 15 | 2031-08-28 15:00 | 18.65 | 24.5029 | N | 0
2025-08-28 | 16 | 2031-08-28 16:00 | 18.96 | 24.9102 | N | 0
2025-08-28 | 17 | 2031-08-28 17:00 | 18.92 | 24.8577 | N | 0
2025-08-28 | 18 | 2031-08-28 18:00 | 18.81 | 24.7131 | N | 0
2025-08-28 | 19 | 2031-08-28 19:00 | 18.97 | 24.9234 | N | 0
2025-08-28 | 20 | 2031-08-28 20:00 | 19.14 | 25.1467 | N | 0
2025-08-28 | 21 | 2031-08-28 21:00 | 19.91 | 26.1584 | N | 0
2025-08-28 | 22 | 2031-08-28 22:00 | 20 | 26.2766 | N | 0
2025-08-28 | 23 | 2031-08-28 23:00 | 18.96 | 24.9102 | N | 0
2025-08-29 | 00 | 2031-08-29 | 19.31 | 25.3701 | N | 0
2025-08-29 | 01 | 2031-08-29 01:00 | 18.63 | 24.4766 | N | 0
2025-08-29 | 02 | 2031-08-29 02:00 | 17.46 | 22.9395 | N | 0
2025-08-29 | 03 | 2031-08-29 03:00 | 15.44 | 20.2855 | N | 0
2025-08-29 | 04 | 2031-08-29 04:00 | 13.71 | 18.0126 | N | 0
2025-08-29 | 05 | 2031-08-29 05:00 | 12.79 | 16.8039 | N | 0
2025-08-29 | 06 | 2031-08-29 06:00 | 11.68 | 15.3455 | N | 0
2025-08-29 | 07 | 2031-08-29 07:00 | 11.18 | 14.6886 | N | 0
2025-08-29 | 08 | 2031-08-29 08:00 | 11 | 14.4521 | N | 0
2025-08-29 | 09 | 2031-08-29 09:00 | 11.51 | 15.1222 | N | 0
2025-08-29 | 10 | 2031-08-29 10:00 | 12.79 | 16.8039 | N | 0
2025-08-29 | 11 | 2031-08-29 11:00 | 14.8 | 19.4447 | N | 0
2025-08-29 | 12 | 2031-08-29 12:00 | 15.86 | 20.8373 | N | 0
2025-08-29 | 13 | 2031-08-29 13:00 | 16.85 | 22.138 | N | 0
2025-08-29 | 14 | 2031-08-29 14:00 | 17.14 | 22.519 | N | 0
2025-08-29 | 15 | 2031-08-29 15:00 | 17.5 | 22.992 | N | 0
2025-08-29 | 16 | 2031-08-29 16:00 | 17.41 | 22.8738 | N | 0
2025-08-29 | 17 | 2031-08-29 17:00 | 17.46 | 22.9395 | N | 0
2025-08-29 | 18 | 2031-08-29 18:00 | 17.61 | 23.1365 | N | 0
2025-08-29 | 19 | 2031-08-29 19:00 | 17.65 | 23.1891 | N | 0
2025-08-29 | 20 | 2031-08-29 20:00 | 18.53 | 24.3453 | N | 0
2025-08-29 | 21 | 2031-08-29 21:00 | 18.89 | 24.8182 | N | 0
2025-08-29 | 22 | 2031-08-29 22:00 | 18.7 | 24.5686 | N | 0
2025-08-29 | 23 | 2031-08-29 23:00 | 17.98 | 23.6227 | N | 0
2025-08-30 | 00 | 2031-08-30 | 17.69 | 23.2416 | N | 0
2025-08-30 | 01 | 2031-08-30 01:00 | 17.33 | 22.7687 | N | 0
2025-08-30 | 02 | 2031-08-30 02:00 | 16.11 | 21.1658 | N | 0
2025-08-30 | 03 | 2031-08-30 03:00 | 14.7 | 19.3133 | N | 0
2025-08-30 | 04 | 2031-08-30 04:00 | 13.52 | 17.763 | N | 0
2025-08-30 | 05 | 2031-08-30 05:00 | 12.38 | 16.2652 | N | 0
2025-08-30 | 06 | 2031-08-30 06:00 | 11.46 | 15.0565 | N | 0
2025-08-30 | 07 | 2031-08-30 07:00 | 11.09 | 14.5704 | N | 0
2025-08-30 | 08 | 2031-08-30 08:00 | 10.81 | 14.2025 | N | 0
2025-08-30 | 09 | 2031-08-30 09:00 | 10.78 | 14.1631 | N | 0
2025-08-30 | 10 | 2031-08-30 10:00 | 11.02 | 14.4784 | N | 0
2025-08-30 | 11 | 2031-08-30 11:00 | 12.24 | 16.0813 | N | 0
2025-08-30 | 12 | 2031-08-30 12:00 | 13.94 | 18.3148 | N | 0
2025-08-30 | 13 | 2031-08-30 13:00 | 15.14 | 19.8914 | N | 0
2025-08-30 | 14 | 2031-08-30 14:00 | 16.01 | 21.0344 | N | 0
2025-08-30 | 15 | 2031-08-30 15:00 | 16.72 | 21.9672 | N | 0
2025-08-30 | 16 | 2031-08-30 16:00 | 17 | 22.3351 | N | 0
2025-08-30 | 17 | 2031-08-30 17:00 | 17.06 | 22.4139 | N | 0
2025-08-30 | 18 | 2031-08-30 18:00 | 17.29 | 22.7161 | N | 0
2025-08-30 | 19 | 2031-08-30 19:00 | 17.62 | 23.1497 | N | 0
2025-08-30 | 20 | 2031-08-30 20:00 | 18.94 | 24.8839 | N | 0
2025-08-30 | 21 | 2031-08-30 21:00 | 19.2 | 25.2255 | N | 0
2025-08-30 | 22 | 2031-08-30 22:00 | 19.09 | 25.081 | N | 0
2025-08-30 | 23 | 2031-08-30 23:00 | 18.09 | 23.7672 | N | 0
2025-08-31 | 00 | 2031-08-31 | 17.5 | 22.992 | N | 0
2025-08-31 | 01 | 2031-08-31 01:00 | 16.98 | 22.3088 | N | 0
2025-08-31 | 02 | 2031-08-31 02:00 | 16.01 | 21.0344 | N | 0
2025-08-31 | 03 | 2031-08-31 03:00 | 14.66 | 19.2607 | N | 0
2025-08-31 | 04 | 2031-08-31 04:00 | 13.37 | 17.5659 | N | 0
2025-08-31 | 05 | 2031-08-31 05:00 | 12.4 | 16.2915 | N | 0
2025-08-31 | 06 | 2031-08-31 06:00 | 11.54 | 15.1616 | N | 0
2025-08-31 | 07 | 2031-08-31 07:00 | 11 | 14.4521 | N | 0
2025-08-31 | 08 | 2031-08-31 08:00 | 10.62 | 13.9529 | N | 0
2025-08-31 | 09 | 2031-08-31 09:00 | 10.57 | 13.8872 | N | 0
2025-08-31 | 10 | 2031-08-31 10:00 | 10.71 | 14.0711 | N | 0
2025-08-31 | 11 | 2031-08-31 11:00 | 11.98 | 15.7397 | N | 0
2025-08-31 | 12 | 2031-08-31 12:00 | 13.64 | 17.9206 | N | 0
2025-08-31 | 13 | 2031-08-31 13:00 | 15.07 | 19.7994 | N | 0
2025-08-31 | 14 | 2031-08-31 14:00 | 16.28 | 21.3891 | N | 0
2025-08-31 | 15 | 2031-08-31 15:00 | 17.35 | 22.7949 | N | 0
2025-08-31 | 16 | 2031-08-31 16:00 | 18.02 | 23.6752 | N | 0
2025-08-31 | 17 | 2031-08-31 17:00 | 18.38 | 24.1482 | N | 0
2025-08-31 | 18 | 2031-08-31 18:00 | 18.94 | 24.8839 | N | 0
2025-08-31 | 19 | 2031-08-31 19:00 | 19.47 | 25.5803 | N | 0
2025-08-31 | 20 | 2031-08-31 20:00 | 21.04 | 27.643 | N | 0
2025-08-31 | 21 | 2031-08-31 21:00 | 21.27 | 27.9452 | N | 0
2025-08-31 | 22 | 2031-08-31 22:00 | 20.93 | 27.4985 | N | 0
2025-08-31 | 23 | 2031-08-31 23:00 | 20.27 | 26.6313 | N | 0
2025-09-01 | 00 | 2031-09-01 | 19.26 | 25.3044 | N | 0
2025-09-01 | 01 | 2031-09-01 01:00 | 18.64 | 24.4898 | N | 0
2025-09-01 | 02 | 2031-09-01 02:00 | 17.2 | 22.5979 | N | 0
2025-09-01 | 03 | 2031-09-01 03:00 | 15.56 | 20.4432 | N | 0
2025-09-01 | 04 | 2031-09-01 04:00 | 14.1 | 18.525 | N | 0
2025-09-01 | 05 | 2031-09-01 05:00 | 12.71 | 16.6988 | N | 0
2025-09-01 | 06 | 2031-09-01 06:00 | 11.72 | 15.3981 | N | 0
2025-09-01 | 07 | 2031-09-01 07:00 | 11.17 | 14.6755 | N | 0
2025-09-01 | 08 | 2031-09-01 08:00 | 10.87 | 14.2813 | N | 0
2025-09-01 | 09 | 2031-09-01 09:00 | 10.92 | 14.347 | N | 0
2025-09-01 | 10 | 2031-09-01 10:00 | 11.18 | 14.6886 | N | 0
2025-09-01 | 11 | 2031-09-01 11:00 | 12.51 | 16.436 | N | 0
2025-09-01 | 12 | 2031-09-01 12:00 | 14.39 | 18.906 | N | 0
2025-09-01 | 13 | 2031-09-01 13:00 | 16.5 | 21.6782 | N | 0
2025-09-01 | 14 | 2031-09-01 14:00 | 18.42 | 24.2007 | N | 0
2025-09-01 | 15 | 2031-09-01 15:00 | 20.25 | 26.6051 | N | 0
2025-09-01 | 16 | 2031-09-01 16:00 | 20.96 | 27.5379 | N | 0
2025-09-01 | 17 | 2031-09-01 17:00 | 21.71 | 28.5232 | N | 0
2025-09-01 | 18 | 2031-09-01 18:00 | 22.49 | 29.548 | N | 0
2025-09-01 | 19 | 2031-09-01 19:00 | 23.42 | 30.7699 | N | 0
2025-09-01 | 20 | 2031-09-01 20:00 | 25.25 | 33.1742 | N | 0
2025-09-01 | 21 | 2031-09-01 21:00 | 25.98 | 34.1333 | N | 0
2025-09-01 | 22 | 2031-09-01 22:00 | 25.38 | 33.345 | N | 0
2025-09-01 | 23 | 2031-09-01 23:00 | 24.05 | 31.5976 | N | 0
2025-09-02 | 00 | 2031-09-02 | 22.82 | 29.9816 | N | 0
2025-09-02 | 01 | 2031-09-02 01:00 | 21.68 | 28.4838 | N | 0
2025-09-02 | 02 | 2031-09-02 02:00 | 19 | 24.9628 | N | 0
2025-09-02 | 03 | 2031-09-02 03:00 | 16.45 | 21.6125 | N | 0
2025-09-02 | 04 | 2031-09-02 04:00 | 14.09 | 18.5119 | N | 0
2025-09-02 | 05 | 2031-09-02 05:00 | 12.6 | 16.5543 | N | 0
2025-09-02 | 06 | 2031-09-02 06:00 | 11.71 | 15.3849 | N | 0
2025-09-02 | 07 | 2031-09-02 07:00 | 11.06 | 14.531 | N | 0
2025-09-02 | 08 | 2031-09-02 08:00 | 10.93 | 14.3602 | N | 0
2025-09-02 | 09 | 2031-09-02 09:00 | 11.85 | 15.5689 | N | 0
2025-09-02 | 10 | 2031-09-02 10:00 | 13.74 | 18.052 | N | 0
2025-09-02 | 11 | 2031-09-02 11:00 | 15.64 | 20.5483 | N | 0
2025-09-02 | 12 | 2031-09-02 12:00 | 16.29 | 21.4023 | N | 0
2025-09-02 | 13 | 2031-09-02 13:00 | 16.86 | 22.1512 | N | 0
2025-09-02 | 14 | 2031-09-02 14:00 | 18.3 | 24.0431 | N | 0
2025-09-02 | 15 | 2031-09-02 15:00 | 19.37 | 25.4489 | N | 0
2025-09-02 | 16 | 2031-09-02 16:00 | 20.39 | 26.789 | N | 0
2025-09-02 | 17 | 2031-09-02 17:00 | 21.44 | 28.1685 | N | 0
2025-09-02 | 18 | 2031-09-02 18:00 | 22.03 | 28.9437 | N | 0
2025-09-02 | 19 | 2031-09-02 19:00 | 22.85 | 30.021 | N | 0
2025-09-02 | 20 | 2031-09-02 20:00 | 24.2 | 31.7947 | N | 0
2025-09-02 | 21 | 2031-09-02 21:00 | 25.42 | 33.3976 | N | 0
2025-09-02 | 22 | 2031-09-02 22:00 | 25.28 | 33.2136 | N | 0
2025-09-02 | 23 | 2031-09-02 23:00 | 23.68 | 31.1115 | N | 0
2025-09-03 | 00 | 2031-09-03 | 22.58 | 29.6663 | N | 0
2025-09-03 | 01 | 2031-09-03 01:00 | 22.01 | 28.9174 | N | 0
2025-09-03 | 02 | 2031-09-03 02:00 | 19.59 | 25.7379 | N | 0
2025-09-03 | 03 | 2031-09-03 03:00 | 16.89 | 22.1906 | N | 0
2025-09-03 | 04 | 2031-09-03 04:00 | 14.63 | 19.2213 | N | 0
2025-09-03 | 05 | 2031-09-03 05:00 | 13.16 | 17.29 | N | 0
2025-09-03 | 06 | 2031-09-03 06:00 | 12.17 | 15.9893 | N | 0
2025-09-03 | 07 | 2031-09-03 07:00 | 11.63 | 15.2798 | N | 0
2025-09-03 | 08 | 2031-09-03 08:00 | 11.34 | 14.8988 | N | 0
2025-09-03 | 09 | 2031-09-03 09:00 | 12.06 | 15.8448 | N | 0
2025-09-03 | 10 | 2031-09-03 10:00 | 13.82 | 18.1571 | N | 0
2025-09-03 | 11 | 2031-09-03 11:00 | 16.05 | 21.087 | N | 0
2025-09-03 | 12 | 2031-09-03 12:00 | 17.42 | 22.8869 | N | 0
2025-09-03 | 13 | 2031-09-03 13:00 | 18.98 | 24.9365 | N | 0
2025-09-03 | 14 | 2031-09-03 14:00 | 20.03 | 26.316 | N | 0
2025-09-03 | 15 | 2031-09-03 15:00 | 20.96 | 27.5379 | N | 0
2025-09-03 | 16 | 2031-09-03 16:00 | 21.53 | 28.2868 | N | 0
2025-09-03 | 17 | 2031-09-03 17:00 | 22.38 | 29.4035 | N | 0
2025-09-03 | 18 | 2031-09-03 18:00 | 23.11 | 30.3626 | N | 0
2025-09-03 | 19 | 2031-09-03 19:00 | 23.85 | 31.3348 | N | 0
2025-09-03 | 20 | 2031-09-03 20:00 | 25.18 | 33.0822 | N | 0
2025-09-03 | 21 | 2031-09-03 21:00 | 26.07 | 34.2515 | N | 0
2025-09-03 | 22 | 2031-09-03 22:00 | 25.73 | 33.8048 | N | 0
2025-09-03 | 23 | 2031-09-03 23:00 | 24.04 | 31.5845 | N | 0
2025-09-04 | 00 | 2031-09-04 | 23.68 | 31.1115 | N | 0
2025-09-04 | 01 | 2031-09-04 01:00 | 22.65 | 29.7582 | N | 0
2025-09-04 | 02 | 2031-09-04 02:00 | 20.21 | 26.5525 | N | 0
2025-09-04 | 03 | 2031-09-04 03:00 | 18.01 | 23.6621 | N | 0
2025-09-04 | 04 | 2031-09-04 04:00 | 15.9 | 20.8899 | N | 0
2025-09-04 | 05 | 2031-09-04 05:00 | 14.23 | 18.6958 | N | 0
2025-09-04 | 06 | 2031-09-04 06:00 | 12.96 | 17.0272 | N | 0
2025-09-04 | 07 | 2031-09-04 07:00 | 12.43 | 16.3309 | N | 0
2025-09-04 | 08 | 2031-09-04 08:00 | 11.94 | 15.6871 | N | 0
2025-09-04 | 09 | 2031-09-04 09:00 | 12.69 | 16.6725 | N | 0
2025-09-04 | 10 | 2031-09-04 10:00 | 15.09 | 19.8257 | N | 0
2025-09-04 | 11 | 2031-09-04 11:00 | 17.36 | 22.8081 | N | 0
2025-09-04 | 12 | 2031-09-04 12:00 | 18.27 | 24.0037 | N | 0
2025-09-04 | 13 | 2031-09-04 13:00 | 18.37 | 24.1351 | N | 0
2025-09-04 | 14 | 2031-09-04 14:00 | 18.8 | 24.7 | N | 0
2025-09-04 | 15 | 2031-09-04 15:00 | 18.87 | 24.792 | N | 0
2025-09-04 | 16 | 2031-09-04 16:00 | 18.99 | 24.9496 | N | 0
2025-09-04 | 17 | 2031-09-04 17:00 | 18.64 | 24.4898 | N | 0
2025-09-04 | 18 | 2031-09-04 18:00 | 18.71 | 24.5818 | N | 0
2025-09-04 | 19 | 2031-09-04 19:00 | 19.24 | 25.2781 | N | 0
2025-09-04 | 20 | 2031-09-04 20:00 | 20.62 | 27.0912 | N | 0
2025-09-04 | 21 | 2031-09-04 21:00 | 21.19 | 27.8401 | N | 0
2025-09-04 | 22 | 2031-09-04 22:00 | 20.89 | 27.4459 | N | 0
2025-09-04 | 23 | 2031-09-04 23:00 | 19.53 | 25.6591 | N | 0
2025-09-05 | 00 | 2031-09-05 | 19.55 | 25.6854 | N | 0
2025-09-05 | 01 | 2031-09-05 01:00 | 18.8 | 24.7 | N | 0
2025-09-05 | 02 | 2031-09-05 02:00 | 17.45 | 22.9263 | N | 0
2025-09-05 | 03 | 2031-09-05 03:00 | 15.22 | 19.9965 | N | 0
2025-09-05 | 04 | 2031-09-05 04:00 | 13.63 | 17.9075 | N | 0
2025-09-05 | 05 | 2031-09-05 05:00 | 12.41 | 16.3046 | N | 0
2025-09-05 | 06 | 2031-09-05 06:00 | 11.65 | 15.3061 | N | 0
2025-09-05 | 07 | 2031-09-05 07:00 | 11.3 | 14.8463 | N | 0
2025-09-05 | 08 | 2031-09-05 08:00 | 11.08 | 14.5572 | N | 0
2025-09-05 | 09 | 2031-09-05 09:00 | 11.73 | 15.4112 | N | 0
2025-09-05 | 10 | 2031-09-05 10:00 | 13.84 | 18.1834 | N | 0
2025-09-05 | 11 | 2031-09-05 11:00 | 15.96 | 20.9687 | N | 0
2025-09-05 | 12 | 2031-09-05 12:00 | 16.36 | 21.4943 | N | 0
2025-09-05 | 13 | 2031-09-05 13:00 | 17.25 | 22.6636 | N | 0
2025-09-05 | 14 | 2031-09-05 14:00 | 18.05 | 23.7146 | N | 0
2025-09-05 | 15 | 2031-09-05 15:00 | 18.6 | 24.4372 | N | 0
2025-09-05 | 16 | 2031-09-05 16:00 | 18.64 | 24.4898 | N | 0
2025-09-05 | 17 | 2031-09-05 17:00 | 18.92 | 24.8577 | N | 0
2025-09-05 | 18 | 2031-09-05 18:00 | 19.15 | 25.1598 | N | 0
2025-09-05 | 19 | 2031-09-05 19:00 | 18.94 | 24.8839 | N | 0
2025-09-05 | 20 | 2031-09-05 20:00 | 19.67 | 25.843 | N | 0
2025-09-05 | 21 | 2031-09-05 21:00 | 20.03 | 26.316 | N | 0
2025-09-05 | 22 | 2031-09-05 22:00 | 19.82 | 26.0401 | N | 0
2025-09-05 | 23 | 2031-09-05 23:00 | 18.89 | 24.8182 | N | 0
2025-09-06 | 00 | 2031-09-06 | 18.92 | 24.8577 | N | 0
2025-09-06 | 01 | 2031-09-06 01:00 | 18.4 | 24.1745 | N | 0
2025-09-06 | 02 | 2031-09-06 02:00 | 16.97 | 22.2957 | N | 0
2025-09-06 | 03 | 2031-09-06 03:00 | 15.23 | 20.0096 | N | 0
2025-09-06 | 04 | 2031-09-06 04:00 | 13.52 | 17.763 | N | 0
2025-09-06 | 05 | 2031-09-06 05:00 | 12.28 | 16.1338 | N | 0
2025-09-06 | 06 | 2031-09-06 06:00 | 11.43 | 15.0171 | N | 0
2025-09-06 | 07 | 2031-09-06 07:00 | 11.08 | 14.5572 | N | 0
2025-09-06 | 08 | 2031-09-06 08:00 | 10.78 | 14.1631 | N | 0
2025-09-06 | 09 | 2031-09-06 09:00 | 10.82 | 14.2156 | N | 0
2025-09-06 | 10 | 2031-09-06 10:00 | 11.3 | 14.8463 | N | 0
2025-09-06 | 11 | 2031-09-06 11:00 | 12.77 | 16.7776 | N | 0
2025-09-06 | 12 | 2031-09-06 12:00 | 14.33 | 18.8272 | N | 0
2025-09-06 | 13 | 2031-09-06 13:00 | 15.38 | 20.2067 | N | 0
2025-09-06 | 14 | 2031-09-06 14:00 | 16.1 | 21.1527 | N | 0
2025-09-06 | 15 | 2031-09-06 15:00 | 16.71 | 21.9541 | N | 0
2025-09-06 | 16 | 2031-09-06 16:00 | 16.67 | 21.9015 | N | 0
2025-09-06 | 17 | 2031-09-06 17:00 | 17.06 | 22.4139 | N | 0
2025-09-06 | 18 | 2031-09-06 18:00 | 17.31 | 22.7424 | N | 0
2025-09-06 | 19 | 2031-09-06 19:00 | 17.51 | 23.0052 | N | 0
2025-09-06 | 20 | 2031-09-06 20:00 | 18 | 23.6489 | N | 0
2025-09-06 | 21 | 2031-09-06 21:00 | 18.5 | 24.3059 | N | 0
2025-09-06 | 22 | 2031-09-06 22:00 | 18.01 | 23.6621 | N | 0
2025-09-06 | 23 | 2031-09-06 23:00 | 17.29 | 22.7161 | N | 0
2025-09-07 | 00 | 2031-09-07 | 17.25 | 22.6636 | N | 0
2025-09-07 | 01 | 2031-09-07 01:00 | 16.7 | 21.941 | N | 0
2025-09-07 | 02 | 2031-09-07 02:00 | 15.68 | 20.6009 | N | 0
2025-09-07 | 03 | 2031-09-07 03:00 | 14.57 | 19.1425 | N | 0
2025-09-07 | 04 | 2031-09-07 04:00 | 13.25 | 17.4082 | N | 0
2025-09-07 | 05 | 2031-09-07 05:00 | 12.17 | 15.9893 | N | 0
2025-09-07 | 06 | 2031-09-07 06:00 | 11.41 | 14.9908 | N | 0
2025-09-07 | 07 | 2031-09-07 07:00 | 10.91 | 14.3339 | N | 0
2025-09-07 | 08 | 2031-09-07 08:00 | 10.62 | 13.9529 | N | 0
2025-09-07 | 09 | 2031-09-07 09:00 | 10.6 | 13.9266 | N | 0
2025-09-07 | 10 | 2031-09-07 10:00 | 10.75 | 14.1237 | N | 0
2025-09-07 | 11 | 2031-09-07 11:00 | 12.28 | 16.1338 | N | 0
2025-09-07 | 12 | 2031-09-07 12:00 | 13.65 | 17.9338 | N | 0
2025-09-07 | 13 | 2031-09-07 13:00 | 14.93 | 19.6155 | N | 0
2025-09-07 | 14 | 2031-09-07 14:00 | 16.25 | 21.3497 | N | 0
2025-09-07 | 15 | 2031-09-07 15:00 | 16.84 | 22.1249 | N | 0
2025-09-07 | 16 | 2031-09-07 16:00 | 17.11 | 22.4796 | N | 0
2025-09-07 | 17 | 2031-09-07 17:00 | 17.52 | 23.0183 | N | 0
2025-09-07 | 18 | 2031-09-07 18:00 | 17.8 | 23.3862 | N | 0
2025-09-07 | 19 | 2031-09-07 19:00 | 18.24 | 23.9643 | N | 0
2025-09-07 | 20 | 2031-09-07 20:00 | 19.29 | 25.3438 | N | 0
2025-09-07 | 21 | 2031-09-07 21:00 | 20.16 | 26.4868 | N | 0
2025-09-07 | 22 | 2031-09-07 22:00 | 19.88 | 26.1189 | N | 0
2025-09-07 | 23 | 2031-09-07 23:00 | 18.85 | 24.7657 | N | 0
2025-09-08 | 00 | 2031-09-08 | 18.8 | 24.7 | N | 0
2025-09-08 | 01 | 2031-09-08 01:00 | 18.23 | 23.9511 | N | 0
2025-09-08 | 02 | 2031-09-08 02:00 | 16.38 | 21.5205 | N | 0
2025-09-08 | 03 | 2031-09-08 03:00 | 14.39 | 18.906 | N | 0
2025-09-08 | 04 | 2031-09-08 04:00 | 12.71 | 16.6988 | N | 0
2025-09-08 | 05 | 2031-09-08 05:00 | 11.76 | 15.4506 | N | 0
2025-09-08 | 06 | 2031-09-08 06:00 | 11.02 | 14.4784 | N | 0
2025-09-08 | 07 | 2031-09-08 07:00 | 10.7 | 14.058 | N | 0
2025-09-08 | 08 | 2031-09-08 08:00 | 10.66 | 14.0054 | N | 0
2025-09-08 | 09 | 2031-09-08 09:00 | 11.48 | 15.0828 | N | 0
2025-09-08 | 10 | 2031-09-08 10:00 | 13.37 | 17.5659 | N | 0
2025-09-08 | 11 | 2031-09-08 11:00 | 15.41 | 20.2461 | N | 0
2025-09-08 | 12 | 2031-09-08 12:00 | 15.56 | 20.4432 | N | 0
2025-09-08 | 13 | 2031-09-08 13:00 | 16.11 | 21.1658 | N | 0
2025-09-08 | 14 | 2031-09-08 14:00 | 16.53 | 21.7176 | N | 0
2025-09-08 | 15 | 2031-09-08 15:00 | 16.91 | 22.2169 | N | 0
2025-09-08 | 16 | 2031-09-08 16:00 | 16.79 | 22.0592 | N | 0
2025-09-08 | 17 | 2031-09-08 17:00 | 16.81 | 22.0855 | N | 0
2025-09-08 | 18 | 2031-09-08 18:00 | 16.84 | 22.1249 | N | 0
2025-09-08 | 19 | 2031-09-08 19:00 | 17.23 | 22.6373 | N | 0
2025-09-08 | 20 | 2031-09-08 20:00 | 18.53 | 24.3453 | N | 0
2025-09-08 | 21 | 2031-09-08 21:00 | 19.14 | 25.1467 | N | 0
2025-09-08 | 22 | 2031-09-08 22:00 | 19.02 | 24.989 | N | 0
2025-09-08 | 23 | 2031-09-08 23:00 | 18.59 | 24.4241 | N | 0
2025-09-09 | 00 | 2031-09-09 | 18.75 | 24.6343 | N | 0
2025-09-09 | 01 | 2031-09-09 01:00 | 18.47 | 24.2664 | N | 0
2025-09-09 | 02 | 2031-09-09 02:00 | 16.51 | 21.6913 | N | 0
2025-09-09 | 03 | 2031-09-09 03:00 | 14.56 | 19.1294 | N | 0
2025-09-09 | 04 | 2031-09-09 04:00 | 13.06 | 17.1586 | N | 0
2025-09-09 | 05 | 2031-09-09 05:00 | 11.84 | 15.5557 | N | 0
2025-09-09 | 06 | 2031-09-09 06:00 | 11.33 | 14.8857 | N | 0
2025-09-09 | 07 | 2031-09-09 07:00 | 10.92 | 14.347 | N | 0
2025-09-09 | 08 | 2031-09-09 08:00 | 10.81 | 14.2025 | N | 0
2025-09-09 | 09 | 2031-09-09 09:00 | 11.73 | 15.4112 | N | 0
2025-09-09 | 10 | 2031-09-09 10:00 | 13.71 | 18.0126 | N | 0
2025-09-09 | 11 | 2031-09-09 11:00 | 15.22 | 19.9965 | N | 0
2025-09-09 | 12 | 2031-09-09 12:00 | 15.77 | 20.7191 | N | 0
2025-09-09 | 13 | 2031-09-09 13:00 | 16.08 | 21.1264 | N | 0
2025-09-09 | 14 | 2031-09-09 14:00 | 16.56 | 21.757 | N | 0
2025-09-09 | 15 | 2031-09-09 15:00 | 16.8 | 22.0723 | N | 0
2025-09-09 | 16 | 2031-09-09 16:00 | 17.09 | 22.4534 | N | 0
2025-09-09 | 17 | 2031-09-09 17:00 | 17.37 | 22.8212 | N | 0
2025-09-09 | 18 | 2031-09-09 18:00 | 17.74 | 23.3073 | N | 0
2025-09-09 | 19 | 2031-09-09 19:00 | 18.26 | 23.9905 | N | 0
2025-09-09 | 20 | 2031-09-09 20:00 | 19.43 | 25.5277 | N | 0
2025-09-09 | 21 | 2031-09-09 21:00 | 20.16 | 26.4868 | N | 0
2025-09-09 | 22 | 2031-09-09 22:00 | 19.68 | 25.8562 | N | 0
2025-09-09 | 23 | 2031-09-09 23:00 | 19.03 | 25.0022 | N | 0
2025-09-10 | 00 | 2031-09-10 | 19.43 | 25.5277 | N | 0
2025-09-10 | 01 | 2031-09-10 01:00 | 18.64 | 24.4898 | N | 0
2025-09-10 | 02 | 2031-09-10 02:00 | 16.71 | 21.9541 | N | 0
2025-09-10 | 03 | 2031-09-10 03:00 | 15.04 | 19.76 | N | 0
2025-09-10 | 04 | 2031-09-10 04:00 | 13.01 | 17.0929 | N | 0
2025-09-10 | 05 | 2031-09-10 05:00 | 12.08 | 15.8711 | N | 0
2025-09-10 | 06 | 2031-09-10 06:00 | 11.4 | 14.9777 | N | 0
2025-09-10 | 07 | 2031-09-10 07:00 | 10.84 | 14.2419 | N | 0
2025-09-10 | 08 | 2031-09-10 08:00 | 10.83 | 14.2288 | N | 0
2025-09-10 | 09 | 2031-09-10 09:00 | 11.73 | 15.4112 | N | 0
2025-09-10 | 10 | 2031-09-10 10:00 | 13.82 | 18.1571 | N | 0
2025-09-10 | 11 | 2031-09-10 11:00 | 15.78 | 20.7322 | N | 0
2025-09-10 | 12 | 2031-09-10 12:00 | 16.26 | 21.3629 | N | 0
2025-09-10 | 13 | 2031-09-10 13:00 | 16.84 | 22.1249 | N | 0
2025-09-10 | 14 | 2031-09-10 14:00 | 17.75 | 23.3205 | N | 0
2025-09-10 | 15 | 2031-09-10 15:00 | 18.53 | 24.3453 | N | 0
2025-09-10 | 16 | 2031-09-10 16:00 | 19 | 24.9628 | N | 0
2025-09-10 | 17 | 2031-09-10 17:00 | 19.45 | 25.554 | N | 0
2025-09-10 | 18 | 2031-09-10 18:00 | 19.94 | 26.1978 | N | 0
2025-09-10 | 19 | 2031-09-10 19:00 | 20.72 | 27.2226 | N | 0
2025-09-10 | 20 | 2031-09-10 20:00 | 21.83 | 28.6809 | N | 0
2025-09-10 | 21 | 2031-09-10 21:00 | 22.6 | 29.6926 | N | 0
2025-09-10 | 22 | 2031-09-10 22:00 | 22.27 | 29.259 | N | 0
2025-09-10 | 23 | 2031-09-10 23:00 | 20.98 | 27.5641 | N | 0
2025-09-11 | 00 | 2031-09-11 | 20.85 | 27.3934 | N | 0
2025-09-11 | 01 | 2031-09-11 01:00 | 20.1 | 26.408 | N | 0
2025-09-11 | 02 | 2031-09-11 02:00 | 18.32 | 24.0694 | N | 0
2025-09-11 | 03 | 2031-09-11 03:00 | 15.98 | 20.995 | N | 0
2025-09-11 | 04 | 2031-09-11 04:00 | 13.9 | 18.2622 | N | 0
2025-09-11 | 05 | 2031-09-11 05:00 | 12.71 | 16.6988 | N | 0
2025-09-11 | 06 | 2031-09-11 06:00 | 11.82 | 15.5295 | N | 0
2025-09-11 | 07 | 2031-09-11 07:00 | 11.31 | 14.8594 | N | 0
2025-09-11 | 08 | 2031-09-11 08:00 | 11.17 | 14.6755 | N | 0
2025-09-11 | 09 | 2031-09-11 09:00 | 11.95 | 15.7003 | N | 0
2025-09-11 | 10 | 2031-09-11 10:00 | 14.16 | 18.6038 | N | 0
2025-09-11 | 11 | 2031-09-11 11:00 | 16.08 | 21.1264 | N | 0
2025-09-11 | 12 | 2031-09-11 12:00 | 16.64 | 21.8621 | N | 0
2025-09-11 | 13 | 2031-09-11 13:00 | 18.16 | 23.8591 | N | 0
2025-09-11 | 14 | 2031-09-11 14:00 | 19.07 | 25.0547 | N | 0
2025-09-11 | 15 | 2031-09-11 15:00 | 19.86 | 26.0927 | N | 0
2025-09-11 | 16 | 2031-09-11 16:00 | 20.65 | 27.1306 | N | 0
2025-09-11 | 17 | 2031-09-11 17:00 | 20.9 | 27.459 | N | 0
2025-09-11 | 18 | 2031-09-11 18:00 | 21.32 | 28.0109 | N | 0
2025-09-11 | 19 | 2031-09-11 19:00 | 21.75 | 28.5758 | N | 0
2025-09-11 | 20 | 2031-09-11 20:00 | 22.9 | 30.0867 | N | 0
2025-09-11 | 21 | 2031-09-11 21:00 | 23.33 | 30.6516 | N | 0
2025-09-11 | 22 | 2031-09-11 22:00 | 22.51 | 29.5743 | N | 0
2025-09-11 | 23 | 2031-09-11 23:00 | 21.78 | 28.6152 | N | 0
2025-09-12 | 00 | 2031-09-12 | 21.85 | 28.7072 | N | 0
2025-09-12 | 01 | 2031-09-12 01:00 | 20.85 | 27.3934 | N | 0
2025-09-12 | 02 | 2031-09-12 02:00 | 18.88 | 24.8051 | N | 0
2025-09-12 | 03 | 2031-09-12 03:00 | 16.58 | 21.7833 | N | 0
2025-09-12 | 04 | 2031-09-12 04:00 | 14.65 | 19.2476 | N | 0
2025-09-12 | 05 | 2031-09-12 05:00 | 12.95 | 17.0141 | N | 0
2025-09-12 | 06 | 2031-09-12 06:00 | 12.21 | 16.0419 | N | 0
2025-09-12 | 07 | 2031-09-12 07:00 | 11.54 | 15.1616 | N | 0
2025-09-12 | 08 | 2031-09-12 08:00 | 11.31 | 14.8594 | N | 0
2025-09-12 | 09 | 2031-09-12 09:00 | 11.93 | 15.674 | N | 0
2025-09-12 | 10 | 2031-09-12 10:00 | 13.69 | 17.9863 | N | 0
2025-09-12 | 11 | 2031-09-12 11:00 | 16.43 | 21.5862 | N | 0
2025-09-12 | 12 | 2031-09-12 12:00 | 17.02 | 22.3614 | N | 0
2025-09-12 | 13 | 2031-09-12 13:00 | 18.18 | 23.8854 | N | 0
2025-09-12 | 14 | 2031-09-12 14:00 | 19.34 | 25.4095 | N | 0
2025-09-12 | 15 | 2031-09-12 15:00 | 19.57 | 25.7116 | N | 0
2025-09-12 | 16 | 2031-09-12 16:00 | 20.3 | 26.6707 | N | 0
2025-09-12 | 17 | 2031-09-12 17:00 | 20.14 | 26.4605 | N | 0
2025-09-12 | 18 | 2031-09-12 18:00 | 20.68 | 27.17 | N | 0
2025-09-12 | 19 | 2031-09-12 19:00 | 21.35 | 28.0503 | N | 0
2025-09-12 | 20 | 2031-09-12 20:00 | 21.89 | 28.7597 | N | 0
2025-09-12 | 21 | 2031-09-12 21:00 | 22.49 | 29.548 | N | 0
2025-09-12 | 22 | 2031-09-12 22:00 | 21.67 | 28.4707 | N | 0
2025-09-12 | 23 | 2031-09-12 23:00 | 20.78 | 27.3014 | N | 0
2025-09-13 | 00 | 2031-09-13 | 20.64 | 27.1174 | N | 0
2025-09-13 | 01 | 2031-09-13 01:00 | 19.49 | 25.6065 | N | 0
2025-09-13 | 02 | 2031-09-13 02:00 | 18.03 | 23.6884 | N | 0
2025-09-13 | 03 | 2031-09-13 03:00 | 16.01 | 21.0344 | N | 0
2025-09-13 | 04 | 2031-09-13 04:00 | 14.33 | 18.8272 | N | 0
2025-09-13 | 05 | 2031-09-13 05:00 | 12.91 | 16.9615 | N | 0
2025-09-13 | 06 | 2031-09-13 06:00 | 11.88 | 15.6083 | N | 0
2025-09-13 | 07 | 2031-09-13 07:00 | 11.47 | 15.0696 | N | 0
2025-09-13 | 08 | 2031-09-13 08:00 | 11.12 | 14.6098 | N | 0
2025-09-13 | 09 | 2031-09-13 09:00 | 11.12 | 14.6098 | N | 0
2025-09-13 | 10 | 2031-09-13 10:00 | 11.64 | 15.293 | N | 0
2025-09-13 | 11 | 2031-09-13 11:00 | 13.09 | 17.198 | N | 0
2025-09-13 | 12 | 2031-09-13 12:00 | 14.66 | 19.2607 | N | 0
2025-09-13 | 13 | 2031-09-13 13:00 | 16.07 | 21.1132 | N | 0
2025-09-13 | 14 | 2031-09-13 14:00 | 17.12 | 22.4928 | N | 0
2025-09-13 | 15 | 2031-09-13 15:00 | 17.83 | 23.4256 | N | 0
2025-09-13 | 16 | 2031-09-13 16:00 | 17.88 | 23.4913 | N | 0
2025-09-13 | 17 | 2031-09-13 17:00 | 17.96 | 23.5964 | N | 0
2025-09-13 | 18 | 2031-09-13 18:00 | 17.79 | 23.373 | N | 0
2025-09-13 | 19 | 2031-09-13 19:00 | 18.37 | 24.1351 | N | 0
2025-09-13 | 20 | 2031-09-13 20:00 | 18.87 | 24.792 | N | 0
2025-09-13 | 21 | 2031-09-13 21:00 | 19.81 | 26.027 | N | 0
2025-09-13 | 22 | 2031-09-13 22:00 | 19.54 | 25.6722 | N | 0
2025-09-13 | 23 | 2031-09-13 23:00 | 19.03 | 25.0022 | N | 0
2025-09-14 | 00 | 2031-09-14 | 19.08 | 25.0679 | N | 0
2025-09-14 | 01 | 2031-09-14 01:00 | 18.39 | 24.1613 | N | 0
2025-09-14 | 02 | 2031-09-14 02:00 | 17.05 | 22.4008 | N | 0
2025-09-14 | 03 | 2031-09-14 03:00 | 15.59 | 20.4826 | N | 0
2025-09-14 | 04 | 2031-09-14 04:00 | 14.13 | 18.5644 | N | 0
2025-09-14 | 05 | 2031-09-14 05:00 | 12.83 | 16.8564 | N | 0
2025-09-14 | 06 | 2031-09-14 06:00 | 11.91 | 15.6477 | N | 0
2025-09-14 | 07 | 2031-09-14 07:00 | 11.27 | 14.8069 | N | 0
2025-09-14 | 08 | 2031-09-14 08:00 | 10.87 | 14.2813 | N | 0
2025-09-14 | 09 | 2031-09-14 09:00 | 10.7 | 14.058 | N | 0
2025-09-14 | 10 | 2031-09-14 10:00 | 11.02 | 14.4784 | N | 0
2025-09-14 | 11 | 2031-09-14 11:00 | 12.31 | 16.1732 | N | 0
2025-09-14 | 12 | 2031-09-14 12:00 | 14.01 | 18.4068 | N | 0
2025-09-14 | 13 | 2031-09-14 13:00 | 16.29 | 21.4023 | N | 0
2025-09-14 | 14 | 2031-09-14 14:00 | 18.13 | 23.8197 | N | 0
2025-09-14 | 15 | 2031-09-14 15:00 | 20.16 | 26.4868 | N | 0
2025-09-14 | 16 | 2031-09-14 16:00 | 21.65 | 28.4444 | N | 0
2025-09-14 | 17 | 2031-09-14 17:00 | 22.41 | 29.4429 | N | 0
2025-09-14 | 18 | 2031-09-14 18:00 | 22.97 | 30.1787 | N | 0
2025-09-14 | 19 | 2031-09-14 19:00 | 23.28 | 30.586 | N | 0
2025-09-14 | 20 | 2031-09-14 20:00 | 24.15 | 31.729 | N | 0
2025-09-14 | 21 | 2031-09-14 21:00 | 25.33 | 33.2793 | N | 0
2025-09-14 | 22 | 2031-09-14 22:00 | 25.43 | 33.4107 | N | 0
2025-09-14 | 23 | 2031-09-14 23:00 | 23.92 | 31.4268 | N | 0
2025-09-15 | 00 | 2031-09-15 | 23.59 | 30.9932 | N | 0
2025-09-15 | 01 | 2031-09-15 01:00 | 22.15 | 29.1013 | N | 0
2025-09-15 | 02 | 2031-09-15 02:00 | 19.8 | 26.0138 | N | 0
2025-09-15 | 03 | 2031-09-15 03:00 | 16.79 | 22.0592 | N | 0
2025-09-15 | 04 | 2031-09-15 04:00 | 14.48 | 19.0243 | N | 0
2025-09-15 | 05 | 2031-09-15 05:00 | 12.75 | 16.7513 | N | 0
2025-09-15 | 06 | 2031-09-15 06:00 | 12.05 | 15.8316 | N | 0
2025-09-15 | 07 | 2031-09-15 07:00 | 11.36 | 14.9251 | N | 0
2025-09-15 | 08 | 2031-09-15 08:00 | 11.36 | 14.9251 | N | 0
2025-09-15 | 09 | 2031-09-15 09:00 | 11.8 | 15.5032 | N | 0
2025-09-15 | 10 | 2031-09-15 10:00 | 13.54 | 17.7893 | N | 0
2025-09-15 | 11 | 2031-09-15 11:00 | 15.99 | 21.0081 | N | 0
2025-09-15 | 12 | 2031-09-15 12:00 | 16.91 | 22.2169 | N | 0
2025-09-15 | 13 | 2031-09-15 13:00 | 17.8 | 23.3862 | N | 0
2025-09-15 | 14 | 2031-09-15 14:00 | 19.32 | 25.3832 | N | 0
2025-09-15 | 15 | 2031-09-15 15:00 | 20.15 | 26.4737 | N | 0
2025-09-15 | 16 | 2031-09-15 16:00 | 20.76 | 27.2751 | N | 0
2025-09-15 | 17 | 2031-09-15 17:00 | 21.67 | 28.4707 | N | 0
2025-09-15 | 18 | 2031-09-15 18:00 | 21.88 | 28.7466 | N | 0
2025-09-15 | 19 | 2031-09-15 19:00 | 22.82 | 29.9816 | N | 0
2025-09-15 | 20 | 2031-09-15 20:00 | 24.21 | 31.8078 | N | 0
2025-09-15 | 21 | 2031-09-15 21:00 | 24.62 | 32.3465 | N | 0
2025-09-15 | 22 | 2031-09-15 22:00 | 24.06 | 31.6107 | N | 0
2025-09-15 | 23 | 2031-09-15 23:00 | 22.66 | 29.7714 | N | 0
2025-09-16 | 00 | 2031-09-16 | 22.1 | 29.0356 | N | 0
2025-09-16 | 01 | 2031-09-16 01:00 | 21.11 | 27.7349 | N | 0
2025-09-16 | 02 | 2031-09-16 02:00 | 18.8 | 24.7 | N | 0
2025-09-16 | 03 | 2031-09-16 03:00 | 16.07 | 21.1132 | N | 0
2025-09-16 | 04 | 2031-09-16 04:00 | 14.16 | 18.6038 | N | 0
2025-09-16 | 05 | 2031-09-16 05:00 | 12.8 | 16.817 | N | 0
2025-09-16 | 06 | 2031-09-16 06:00 | 11.91 | 15.6477 | N | 0
2025-09-16 | 07 | 2031-09-16 07:00 | 11.41 | 14.9908 | N | 0
2025-09-16 | 08 | 2031-09-16 08:00 | 11.16 | 14.6623 | N | 0
2025-09-16 | 09 | 2031-09-16 09:00 | 11.93 | 15.674 | N | 0
2025-09-16 | 10 | 2031-09-16 10:00 | 13.79 | 18.1177 | N | 0
2025-09-16 | 11 | 2031-09-16 11:00 | 15.99 | 21.0081 | N | 0
2025-09-16 | 12 | 2031-09-16 12:00 | 17.1 | 22.4665 | N | 0
2025-09-16 | 13 | 2031-09-16 13:00 | 18.25 | 23.9774 | N | 0
2025-09-16 | 14 | 2031-09-16 14:00 | 19.79 | 26.0007 | N | 0
2025-09-16 | 15 | 2031-09-16 15:00 | 20.98 | 27.5641 | N | 0
2025-09-16 | 16 | 2031-09-16 16:00 | 21.37 | 28.0765 | N | 0
2025-09-16 | 17 | 2031-09-16 17:00 | 21.8 | 28.6415 | N | 0
2025-09-16 | 18 | 2031-09-16 18:00 | 22.46 | 29.5086 | N | 0
2025-09-16 | 19 | 2031-09-16 19:00 | 23.01 | 30.2312 | N | 0
2025-09-16 | 20 | 2031-09-16 20:00 | 24.4 | 32.0574 | N | 0
2025-09-16 | 21 | 2031-09-16 21:00 | 24.9 | 32.7144 | N | 0
2025-09-16 | 22 | 2031-09-16 22:00 | 24.48 | 32.1626 | N | 0
2025-09-16 | 23 | 2031-09-16 23:00 | 22.96 | 30.1655 | N | 0
2025-09-17 | 00 | 2031-09-17 | 22.72 | 29.8502 | N | 0
2025-09-17 | 01 | 2031-09-17 01:00 | 21.16 | 27.8006 | N | 0
2025-09-17 | 02 | 2031-09-17 02:00 | 19.07 | 25.0547 | N | 0
2025-09-17 | 03 | 2031-09-17 03:00 | 16.42 | 21.5731 | N | 0
2025-09-17 | 04 | 2031-09-17 04:00 | 14.36 | 18.8666 | N | 0
2025-09-17 | 05 | 2031-09-17 05:00 | 12.77 | 16.7776 | N | 0
2025-09-17 | 06 | 2031-09-17 06:00 | 11.95 | 15.7003 | N | 0
2025-09-17 | 07 | 2031-09-17 07:00 | 11.33 | 14.8857 | N | 0
2025-09-17 | 08 | 2031-09-17 08:00 | 11.32 | 14.8726 | N | 0
2025-09-17 | 09 | 2031-09-17 09:00 | 12.22 | 16.055 | N | 0
2025-09-17 | 10 | 2031-09-17 10:00 | 14.19 | 18.6432 | N | 0
2025-09-17 | 11 | 2031-09-17 11:00 | 16.03 | 21.0607 | N | 0
2025-09-17 | 12 | 2031-09-17 12:00 | 17.02 | 22.3614 | N | 0
2025-09-17 | 13 | 2031-09-17 13:00 | 18.02 | 23.6752 | N | 0
2025-09-17 | 14 | 2031-09-17 14:00 | 19.28 | 25.3306 | N | 0
2025-09-17 | 15 | 2031-09-17 15:00 | 20.69 | 27.1831 | N | 0
2025-09-17 | 16 | 2031-09-17 16:00 | 21.73 | 28.5495 | N | 0
2025-09-17 | 17 | 2031-09-17 17:00 | 22.49 | 29.548 | N | 0
2025-09-17 | 18 | 2031-09-17 18:00 | 22.96 | 30.1655 | N | 0
2025-09-17 | 19 | 2031-09-17 19:00 | 23.93 | 31.4399 | N | 0
2025-09-17 | 20 | 2031-09-17 20:00 | 24.3 | 31.9261 | N | 0
2025-09-17 | 21 | 2031-09-17 21:00 | 24.62 | 32.3465 | N | 0
2025-09-17 | 22 | 2031-09-17 22:00 | 23.76 | 31.2166 | N | 0
2025-09-17 | 23 | 2031-09-17 23:00 | 22.43 | 29.4692 | N | 0
2025-09-18 | 00 | 2031-09-18 | 22.52 | 29.5874 | N | 0
2025-09-18 | 01 | 2031-09-18 01:00 | 21.4 | 28.116 | N | 0
2025-09-18 | 02 | 2031-09-18 02:00 | 19.1 | 25.0941 | N | 0
2025-09-18 | 03 | 2031-09-18 03:00 | 16.91 | 22.2169 | N | 0
2025-09-18 | 04 | 2031-09-18 04:00 | 14.5 | 19.0505 | N | 0
2025-09-18 | 05 | 2031-09-18 05:00 | 13.02 | 17.1061 | N | 0
2025-09-18 | 06 | 2031-09-18 06:00 | 12.06 | 15.8448 | N | 0
2025-09-18 | 07 | 2031-09-18 07:00 | 11.47 | 15.0696 | N | 0
2025-09-18 | 08 | 2031-09-18 08:00 | 11.27 | 14.8069 | N | 0
2025-09-18 | 09 | 2031-09-18 09:00 | 12.16 | 15.9762 | N | 0
2025-09-18 | 10 | 2031-09-18 10:00 | 14.32 | 18.814 | N | 0
2025-09-18 | 11 | 2031-09-18 11:00 | 16.55 | 21.7439 | N | 0
2025-09-18 | 12 | 2031-09-18 12:00 | 17.5 | 22.992 | N | 0
2025-09-18 | 13 | 2031-09-18 13:00 | 18.95 | 24.8971 | N | 0
2025-09-18 | 14 | 2031-09-18 14:00 | 20.07 | 26.3686 | N | 0
2025-09-18 | 15 | 2031-09-18 15:00 | 21.04 | 27.643 | N | 0
2025-09-18 | 16 | 2031-09-18 16:00 | 21.74 | 28.5627 | N | 0
2025-09-18 | 17 | 2031-09-18 17:00 | 23.14 | 30.402 | N | 0
2025-09-18 | 18 | 2031-09-18 18:00 | 23.96 | 31.4794 | N | 0
2025-09-18 | 19 | 2031-09-18 19:00 | 24.71 | 32.4647 | N | 0
2025-09-18 | 20 | 2031-09-18 20:00 | 25.64 | 33.6866 | N | 0
2025-09-18 | 21 | 2031-09-18 21:00 | 25.9 | 34.0282 | N | 0
2025-09-18 | 22 | 2031-09-18 22:00 | 25.76 | 33.8443 | N | 0
2025-09-18 | 23 | 2031-09-18 23:00 | 24.61 | 32.3334 | N | 0
2025-09-19 | 00 | 2031-09-19 | 24.37 | 32.018 | N | 0
2025-09-19 | 01 | 2031-09-19 01:00 | 23.36 | 30.6911 | N | 0
2025-09-19 | 02 | 2031-09-19 02:00 | 21.03 | 27.6298 | N | 0
2025-09-19 | 03 | 2031-09-19 03:00 | 18.29 | 24.0299 | N | 0
2025-09-19 | 04 | 2031-09-19 04:00 | 15.92 | 20.9162 | N | 0
2025-09-19 | 05 | 2031-09-19 05:00 | 14.06 | 18.4724 | N | 0
2025-09-19 | 06 | 2031-09-19 06:00 | 12.91 | 16.9615 | N | 0
2025-09-19 | 07 | 2031-09-19 07:00 | 12.1 | 15.8973 | N | 0
2025-09-19 | 08 | 2031-09-19 08:00 | 11.75 | 15.4375 | N | 0
2025-09-19 | 09 | 2031-09-19 09:00 | 12.28 | 16.1338 | N | 0
2025-09-19 | 10 | 2031-09-19 10:00 | 14.14 | 18.5776 | N | 0
2025-09-19 | 11 | 2031-09-19 11:00 | 16.03 | 21.0607 | N | 0
2025-09-19 | 12 | 2031-09-19 12:00 | 17.13 | 22.5059 | N | 0
2025-09-19 | 13 | 2031-09-19 13:00 | 17.96 | 23.5964 | N | 0
2025-09-19 | 14 | 2031-09-19 14:00 | 18.77 | 24.6606 | N | 0
2025-09-19 | 15 | 2031-09-19 15:00 | 19.67 | 25.843 | N | 0
2025-09-19 | 16 | 2031-09-19 16:00 | 19.99 | 26.2635 | N | 0
2025-09-19 | 17 | 2031-09-19 17:00 | 20.35 | 26.7364 | N | 0
2025-09-19 | 18 | 2031-09-19 18:00 | 20.31 | 26.6839 | N | 0
2025-09-19 | 19 | 2031-09-19 19:00 | 20.71 | 27.2094 | N | 0
2025-09-19 | 20 | 2031-09-19 20:00 | 21.38 | 28.0897 | N | 0
2025-09-19 | 21 | 2031-09-19 21:00 | 21.66 | 28.4576 | N | 0
2025-09-19 | 22 | 2031-09-19 22:00 | 21.13 | 27.7612 | N | 0
2025-09-19 | 23 | 2031-09-19 23:00 | 19.66 | 25.8299 | N | 0
2025-09-20 | 00 | 2031-09-20 | 19.54 | 25.6722 | N | 0
2025-09-20 | 01 | 2031-09-20 01:00 | 18.48 | 24.2796 | N | 0
2025-09-20 | 02 | 2031-09-20 02:00 | 17.21 | 22.611 | N | 0
2025-09-20 | 03 | 2031-09-20 03:00 | 15.29 | 20.0885 | N | 0
2025-09-20 | 04 | 2031-09-20 04:00 | 13.66 | 17.9469 | N | 0
2025-09-20 | 05 | 2031-09-20 05:00 | 12.38 | 16.2652 | N | 0
2025-09-20 | 06 | 2031-09-20 06:00 | 11.65 | 15.3061 | N | 0
2025-09-20 | 07 | 2031-09-20 07:00 | 11.08 | 14.5572 | N | 0
2025-09-20 | 08 | 2031-09-20 08:00 | 10.69 | 14.0448 | N | 0
2025-09-20 | 09 | 2031-09-20 09:00 | 11 | 14.4521 | N | 0
2025-09-20 | 10 | 2031-09-20 10:00 | 11.44 | 15.0302 | N | 0
2025-09-20 | 11 | 2031-09-20 11:00 | 12.61 | 16.5674 | N | 0
2025-09-20 | 12 | 2031-09-20 12:00 | 14.12 | 18.5513 | N | 0
2025-09-20 | 13 | 2031-09-20 13:00 | 15.38 | 20.2067 | N | 0
2025-09-20 | 14 | 2031-09-20 14:00 | 16.5 | 21.6782 | N | 0
2025-09-20 | 15 | 2031-09-20 15:00 | 16.88 | 22.1774 | N | 0
2025-09-20 | 16 | 2031-09-20 16:00 | 17.06 | 22.4139 | N | 0
2025-09-20 | 17 | 2031-09-20 17:00 | 16.95 | 22.2694 | N | 0
2025-09-20 | 18 | 2031-09-20 18:00 | 16.87 | 22.1643 | N | 0
2025-09-20 | 19 | 2031-09-20 19:00 | 17.04 | 22.3877 | N | 0
2025-09-20 | 20 | 2031-09-20 20:00 | 17.8 | 23.3862 | N | 0
2025-09-20 | 21 | 2031-09-20 21:00 | 18.16 | 23.8591 | N | 0
2025-09-20 | 22 | 2031-09-20 22:00 | 17.94 | 23.5701 | N | 0
2025-09-20 | 23 | 2031-09-20 23:00 | 17.18 | 22.5716 | N | 0
2025-09-21 | 00 | 2031-09-21 | 17.15 | 22.5322 | N | 0
2025-09-21 | 01 | 2031-09-21 01:00 | 16.43 | 21.5862 | N | 0
2025-09-21 | 02 | 2031-09-21 02:00 | 15.4 | 20.233 | N | 0
2025-09-21 | 03 | 2031-09-21 03:00 | 14.01 | 18.4068 | N | 0
2025-09-21 | 04 | 2031-09-21 04:00 | 12.8 | 16.817 | N | 0
2025-09-21 | 05 | 2031-09-21 05:00 | 11.79 | 15.4901 | N | 0
2025-09-21 | 06 | 2031-09-21 06:00 | 10.96 | 14.3996 | N | 0
2025-09-21 | 07 | 2031-09-21 07:00 | 10.52 | 13.8215 | N | 0
2025-09-21 | 08 | 2031-09-21 08:00 | 10.37 | 13.6244 | N | 0
2025-09-21 | 09 | 2031-09-21 09:00 | 10.4 | 13.6638 | N | 0
2025-09-21 | 10 | 2031-09-21 10:00 | 10.8 | 14.1894 | N | 0
2025-09-21 | 11 | 2031-09-21 11:00 | 11.93 | 15.674 | N | 0
2025-09-21 | 12 | 2031-09-21 12:00 | 13.47 | 17.6973 | N | 0
2025-09-21 | 13 | 2031-09-21 13:00 | 14.86 | 19.5235 | N | 0
2025-09-21 | 14 | 2031-09-21 14:00 | 16.09 | 21.1395 | N | 0
2025-09-21 | 15 | 2031-09-21 15:00 | 17.23 | 22.6373 | N | 0
2025-09-21 | 16 | 2031-09-21 16:00 | 18.08 | 23.754 | N | 0
2025-09-21 | 17 | 2031-09-21 17:00 | 18.67 | 24.5292 | N | 0
2025-09-21 | 18 | 2031-09-21 18:00 | 19.61 | 25.7642 | N | 0
2025-09-21 | 19 | 2031-09-21 19:00 | 20.83 | 27.3671 | N | 0
2025-09-21 | 20 | 2031-09-21 20:00 | 21.67 | 28.4707 | N | 0
2025-09-21 | 21 | 2031-09-21 21:00 | 22.63 | 29.732 | N | 0
2025-09-21 | 22 | 2031-09-21 22:00 | 22.15 | 29.1013 | N | 0
2025-09-21 | 23 | 2031-09-21 23:00 | 21.6 | 28.3787 | N | 0
2025-09-22 | 00 | 2031-09-22 | 21.72 | 28.5364 | N | 0
2025-09-22 | 01 | 2031-09-22 01:00 | 20.65 | 27.1306 | N | 0
2025-09-22 | 02 | 2031-09-22 02:00 | 19.11 | 25.1073 | N | 0
2025-09-22 | 03 | 2031-09-22 03:00 | 16.32 | 21.4417 | N | 0
2025-09-22 | 04 | 2031-09-22 04:00 | 14.35 | 18.8535 | N | 0
2025-09-22 | 05 | 2031-09-22 05:00 | 12.86 | 16.8959 | N | 0
2025-09-22 | 06 | 2031-09-22 06:00 | 12.04 | 15.8185 | N | 0
2025-09-22 | 07 | 2031-09-22 07:00 | 11.54 | 15.1616 | N | 0
2025-09-22 | 08 | 2031-09-22 08:00 | 11.4 | 14.9777 | N | 0
2025-09-22 | 09 | 2031-09-22 09:00 | 12.23 | 16.0681 | N | 0
2025-09-22 | 10 | 2031-09-22 10:00 | 14.25 | 18.7221 | N | 0
2025-09-22 | 11 | 2031-09-22 11:00 | 16.42 | 21.5731 | N | 0
2025-09-22 | 12 | 2031-09-22 12:00 | 17.35 | 22.7949 | N | 0
2025-09-22 | 13 | 2031-09-22 13:00 | 18.34 | 24.0956 | N | 0
2025-09-22 | 14 | 2031-09-22 14:00 | 18.92 | 24.8577 | N | 0
2025-09-22 | 15 | 2031-09-22 15:00 | 19.18 | 25.1993 | N | 0
2025-09-22 | 16 | 2031-09-22 16:00 | 19.64 | 25.8036 | N | 0
2025-09-22 | 17 | 2031-09-22 17:00 | 20.44 | 26.8547 | N | 0
2025-09-22 | 18 | 2031-09-22 18:00 | 20.72 | 27.2226 | N | 0
2025-09-22 | 19 | 2031-09-22 19:00 | 20.87 | 27.4196 | N | 0
2025-09-22 | 20 | 2031-09-22 20:00 | 22.77 | 29.9159 | N | 0
2025-09-22 | 21 | 2031-09-22 21:00 | 23.92 | 31.4268 | N | 0
2025-09-22 | 22 | 2031-09-22 22:00 | 23.24 | 30.5334 | N | 0
2025-09-22 | 23 | 2031-09-22 23:00 | 22.61 | 29.7057 | N | 0
2025-09-23 | 00 | 2031-09-23 | 22.58 | 29.6663 | N | 0
2025-09-23 | 01 | 2031-09-23 01:00 | 21.52 | 28.2736 | N | 0
2025-09-23 | 02 | 2031-09-23 02:00 | 19.32 | 25.3832 | N | 0
2025-09-23 | 03 | 2031-09-23 03:00 | 17.34 | 22.7818 | N | 0
2025-09-23 | 04 | 2031-09-23 04:00 | 15.13 | 19.8782 | N | 0
2025-09-23 | 05 | 2031-09-23 05:00 | 13.69 | 17.9863 | N | 0
2025-09-23 | 06 | 2031-09-23 06:00 | 12.86 | 16.8959 | N | 0
2025-09-23 | 07 | 2031-09-23 07:00 | 12.28 | 16.1338 | N | 0
2025-09-23 | 08 | 2031-09-23 08:00 | 12.15 | 15.963 | N | 0
2025-09-23 | 09 | 2031-09-23 09:00 | 13.08 | 17.1849 | N | 0
2025-09-23 | 10 | 2031-09-23 10:00 | 14.97 | 19.668 | N | 0
2025-09-23 | 11 | 2031-09-23 11:00 | 17.63 | 23.1628 | N | 0
2025-09-23 | 12 | 2031-09-23 12:00 | 18.23 | 23.9511 | N | 0
2025-09-23 | 13 | 2031-09-23 13:00 | 18.95 | 24.8971 | N | 0
2025-09-23 | 14 | 2031-09-23 14:00 | 19.94 | 26.1978 | N | 0
2025-09-23 | 15 | 2031-09-23 15:00 | 20.9 | 27.459 | N | 0
2025-09-23 | 16 | 2031-09-23 16:00 | 22.19 | 29.1539 | N | 0
2025-09-23 | 17 | 2031-09-23 17:00 | 23.26 | 30.5597 | N | 0
2025-09-23 | 18 | 2031-09-23 18:00 | 24.13 | 31.7027 | N | 0
2025-09-23 | 19 | 2031-09-23 19:00 | 24.67 | 32.4122 | N | 0
2025-09-23 | 20 | 2031-09-23 20:00 | 25.44 | 33.4238 | N | 0
2025-09-23 | 21 | 2031-09-23 21:00 | 25.71 | 33.7786 | N | 0
2025-09-23 | 22 | 2031-09-23 22:00 | 24.82 | 32.6093 | N | 0
2025-09-23 | 23 | 2031-09-23 23:00 | 24.44 | 32.11 | N | 0
2025-09-24 | 00 | 2031-09-24 | 24.04 | 31.5845 | N | 0
2025-09-24 | 01 | 2031-09-24 01:00 | 22.93 | 30.1261 | N | 0
2025-09-24 | 02 | 2031-09-24 02:00 | 20.7 | 27.1963 | N | 0
2025-09-24 | 03 | 2031-09-24 03:00 | 17.88 | 23.4913 | N | 0
2025-09-24 | 04 | 2031-09-24 04:00 | 16.16 | 21.2315 | N | 0
2025-09-24 | 05 | 2031-09-24 05:00 | 14.17 | 18.617 | N | 0
2025-09-24 | 06 | 2031-09-24 06:00 | 13.1 | 17.2112 | N | 0
2025-09-24 | 07 | 2031-09-24 07:00 | 12.42 | 16.3178 | N | 0
2025-09-24 | 08 | 2031-09-24 08:00 | 12.22 | 16.055 | N | 0
2025-09-24 | 09 | 2031-09-24 09:00 | 13.26 | 17.4214 | N | 0
2025-09-24 | 10 | 2031-09-24 10:00 | 15.41 | 20.2461 | N | 0
2025-09-24 | 11 | 2031-09-24 11:00 | 17.56 | 23.0709 | N | 0
2025-09-24 | 12 | 2031-09-24 12:00 | 18.17 | 23.8723 | N | 0
2025-09-24 | 13 | 2031-09-24 13:00 | 19.16 | 25.173 | N | 0
2025-09-24 | 14 | 2031-09-24 14:00 | 19.91 | 26.1584 | N | 0
2025-09-24 | 15 | 2031-09-24 15:00 | 20.63 | 27.1043 | N | 0
2025-09-24 | 16 | 2031-09-24 16:00 | 21.41 | 28.1291 | N | 0
2025-09-24 | 17 | 2031-09-24 17:00 | 23.2 | 30.4809 | N | 0
2025-09-24 | 18 | 2031-09-24 18:00 | 22.88 | 30.0604 | N | 0
2025-09-24 | 19 | 2031-09-24 19:00 | 22.04 | 28.9568 | N | 0
2025-09-24 | 20 | 2031-09-24 20:00 | 22.45 | 29.4955 | N | 0
2025-09-24 | 21 | 2031-09-24 21:00 | 23.04 | 30.2706 | N | 0
2025-09-24 | 22 | 2031-09-24 22:00 | 22.79 | 29.9422 | N | 0
2025-09-24 | 23 | 2031-09-24 23:00 | 22.54 | 29.6137 | N | 0
2025-09-25 | 00 | 2031-09-25 | 22.53 | 29.6006 | N | 0
2025-09-25 | 01 | 2031-09-25 01:00 | 21.51 | 28.2605 | N | 0
2025-09-25 | 02 | 2031-09-25 02:00 | 19.52 | 25.646 | N | 0
2025-09-25 | 03 | 2031-09-25 03:00 | 17.35 | 22.7949 | N | 0
2025-09-25 | 04 | 2031-09-25 04:00 | 15.34 | 20.1541 | N | 0
2025-09-25 | 05 | 2031-09-25 05:00 | 13.76 | 18.0783 | N | 0
2025-09-25 | 06 | 2031-09-25 06:00 | 12.87 | 16.909 | N | 0
2025-09-25 | 07 | 2031-09-25 07:00 | 12.3 | 16.1601 | N | 0
2025-09-25 | 08 | 2031-09-25 08:00 | 11.95 | 15.7003 | N | 0
2025-09-25 | 09 | 2031-09-25 09:00 | 13.02 | 17.1061 | N | 0
2025-09-25 | 10 | 2031-09-25 10:00 | 15.12 | 19.8651 | N | 0
2025-09-25 | 11 | 2031-09-25 11:00 | 17.57 | 23.084 | N | 0
2025-09-25 | 12 | 2031-09-25 12:00 | 18.16 | 23.8591 | N | 0
2025-09-25 | 13 | 2031-09-25 13:00 | 18.51 | 24.319 | N | 0
2025-09-25 | 14 | 2031-09-25 14:00 | 19.13 | 25.1336 | N | 0
2025-09-25 | 15 | 2031-09-25 15:00 | 19.75 | 25.9481 | N | 0
2025-09-25 | 16 | 2031-09-25 16:00 | 19.74 | 25.935 | N | 0
2025-09-25 | 17 | 2031-09-25 17:00 | 19.8 | 26.0138 | N | 0
2025-09-25 | 18 | 2031-09-25 18:00 | 19.97 | 26.2372 | N | 0
2025-09-25 | 19 | 2031-09-25 19:00 | 20.24 | 26.5919 | N | 0
2025-09-25 | 20 | 2031-09-25 20:00 | 20.99 | 27.5773 | N | 0
2025-09-25 | 21 | 2031-09-25 21:00 | 21.14 | 27.7744 | N | 0
2025-09-25 | 22 | 2031-09-25 22:00 | 21.1 | 27.7218 | N | 0
2025-09-25 | 23 | 2031-09-25 23:00 | 21.22 | 27.8795 | N | 0
2025-09-26 | 00 | 2031-09-26 | 20.88 | 27.4328 | N | 0
2025-09-26 | 01 | 2031-09-26 01:00 | 20.08 | 26.3817 | N | 0
2025-09-26 | 02 | 2031-09-26 02:00 | 18.71 | 24.5818 | N | 0
2025-09-26 | 03 | 2031-09-26 03:00 | 16.43 | 21.5862 | N | 0
2025-09-26 | 04 | 2031-09-26 04:00 | 14.48 | 19.0243 | N | 0
2025-09-26 | 05 | 2031-09-26 05:00 | 13.04 | 17.1323 | N | 0
2025-09-26 | 06 | 2031-09-26 06:00 | 12.24 | 16.0813 | N | 0
2025-09-26 | 07 | 2031-09-26 07:00 | 11.8 | 15.5032 | N | 0
2025-09-26 | 08 | 2031-09-26 08:00 | 11.44 | 15.0302 | N | 0
2025-09-26 | 09 | 2031-09-26 09:00 | 12.39 | 16.2784 | N | 0
2025-09-26 | 10 | 2031-09-26 10:00 | 14.32 | 18.814 | N | 0
2025-09-26 | 11 | 2031-09-26 11:00 | 15.72 | 20.6534 | N | 0
2025-09-26 | 12 | 2031-09-26 12:00 | 17.63 | 23.1628 | N | 0
2025-09-26 | 13 | 2031-09-26 13:00 | 18.86 | 24.7788 | N | 0
2025-09-26 | 14 | 2031-09-26 14:00 | 19.84 | 26.0664 | N | 0
2025-09-26 | 15 | 2031-09-26 15:00 | 20.43 | 26.8415 | N | 0
2025-09-26 | 16 | 2031-09-26 16:00 | 20.66 | 27.1437 | N | 0
2025-09-26 | 17 | 2031-09-26 17:00 | 21.05 | 27.6561 | N | 0
2025-09-26 | 18 | 2031-09-26 18:00 | 21.79 | 28.6284 | N | 0
2025-09-26 | 19 | 2031-09-26 19:00 | 22.18 | 29.1407 | N | 0
2025-09-26 | 20 | 2031-09-26 20:00 | 22.33 | 29.3378 | N | 0
2025-09-26 | 21 | 2031-09-26 21:00 | 22.84 | 30.0079 | N | 0
2025-09-26 | 22 | 2031-09-26 22:00 | 22.04 | 28.9568 | N | 0
2025-09-26 | 23 | 2031-09-26 23:00 | 20.92 | 27.4853 | N | 0
2025-09-27 | 00 | 2031-09-27 | 20.8 | 27.3277 | N | 0
2025-09-27 | 01 | 2031-09-27 01:00 | 19.83 | 26.0532 | N | 0
2025-09-27 | 02 | 2031-09-27 02:00 | 18.51 | 24.319 | N | 0
2025-09-27 | 03 | 2031-09-27 03:00 | 16.17 | 21.2446 | N | 0
2025-09-27 | 04 | 2031-09-27 04:00 | 14.67 | 19.2739 | N | 0
2025-09-27 | 05 | 2031-09-27 05:00 | 13.15 | 17.2769 | N | 0
2025-09-27 | 06 | 2031-09-27 06:00 | 12.18 | 16.0024 | N | 0
2025-09-27 | 07 | 2031-09-27 07:00 | 11.42 | 15.0039 | N | 0
2025-09-27 | 08 | 2031-09-27 08:00 | 11.09 | 14.5704 | N | 0
2025-09-27 | 09 | 2031-09-27 09:00 | 11.14 | 14.6361 | N | 0
2025-09-27 | 10 | 2031-09-27 10:00 | 11.57 | 15.201 | N | 0
2025-09-27 | 11 | 2031-09-27 11:00 | 12.96 | 17.0272 | N | 0
2025-09-27 | 12 | 2031-09-27 12:00 | 14.58 | 19.1556 | N | 0
2025-09-27 | 13 | 2031-09-27 13:00 | 16.37 | 21.5074 | N | 0
2025-09-27 | 14 | 2031-09-27 14:00 | 17.99 | 23.6358 | N | 0
2025-09-27 | 15 | 2031-09-27 15:00 | 19.5 | 25.6197 | N | 0
2025-09-27 | 16 | 2031-09-27 16:00 | 19.9 | 26.1452 | N | 0
2025-09-27 | 17 | 2031-09-27 17:00 | 19.61 | 25.7642 | N | 0
2025-09-27 | 18 | 2031-09-27 18:00 | 19.94 | 26.1978 | N | 0
2025-09-27 | 19 | 2031-09-27 19:00 | 20 | 26.2766 | N | 0
2025-09-27 | 20 | 2031-09-27 20:00 | 20.42 | 26.8284 | N | 0
2025-09-27 | 21 | 2031-09-27 21:00 | 21.22 | 27.8795 | N | 0
2025-09-27 | 22 | 2031-09-27 22:00 | 20.92 | 27.4853 | N | 0
2025-09-27 | 23 | 2031-09-27 23:00 | 20.17 | 26.4999 | N | 0
2025-09-28 | 00 | 2031-09-28 | 19.74 | 25.935 | N | 0
2025-09-28 | 01 | 2031-09-28 01:00 | 18.94 | 24.8839 | N | 0
2025-09-28 | 02 | 2031-09-28 02:00 | 17.51 | 23.0052 | N | 0
2025-09-28 | 03 | 2031-09-28 03:00 | 15.58 | 20.4695 | N | 0
2025-09-28 | 04 | 2031-09-28 04:00 | 14 | 18.3936 | N | 0
2025-09-28 | 05 | 2031-09-28 05:00 | 12.59 | 16.5411 | N | 0
2025-09-28 | 06 | 2031-09-28 06:00 | 11.59 | 15.2273 | N | 0
2025-09-28 | 07 | 2031-09-28 07:00 | 11.09 | 14.5704 | N | 0
2025-09-28 | 08 | 2031-09-28 08:00 | 10.76 | 14.1368 | N | 0
2025-09-28 | 09 | 2031-09-28 09:00 | 10.72 | 14.0843 | N | 0
2025-09-28 | 10 | 2031-09-28 10:00 | 11.06 | 14.531 | N | 0
2025-09-28 | 11 | 2031-09-28 11:00 | 12.21 | 16.0419 | N | 0
2025-09-28 | 12 | 2031-09-28 12:00 | 14.03 | 18.433 | N | 0
2025-09-28 | 13 | 2031-09-28 13:00 | 16.46 | 21.6256 | N | 0
2025-09-28 | 14 | 2031-09-28 14:00 | 17.87 | 23.4781 | N | 0
2025-09-28 | 15 | 2031-09-28 15:00 | 19.38 | 25.462 | N | 0
2025-09-28 | 16 | 2031-09-28 16:00 | 20.28 | 26.6445 | N | 0
2025-09-28 | 17 | 2031-09-28 17:00 | 21.35 | 28.0503 | N | 0
2025-09-28 | 18 | 2031-09-28 18:00 | 21.97 | 28.8648 | N | 0
2025-09-28 | 19 | 2031-09-28 19:00 | 22.57 | 29.6531 | N | 0
2025-09-28 | 20 | 2031-09-28 20:00 | 23.82 | 31.2954 | N | 0
2025-09-28 | 21 | 2031-09-28 21:00 | 24.6 | 32.3202 | N | 0
2025-09-28 | 22 | 2031-09-28 22:00 | 23.92 | 31.4268 | N | 0
2025-09-28 | 23 | 2031-09-28 23:00 | 22.68 | 29.7977 | N | 0
2025-09-29 | 00 | 2031-09-29 | 22.4 | 29.4298 | N | 0
2025-09-29 | 01 | 2031-09-29 01:00 | 20.2 | 26.5394 | N | 0
2025-09-29 | 02 | 2031-09-29 02:00 | 18.14 | 23.8329 | N | 0
2025-09-29 | 03 | 2031-09-29 03:00 | 15.69 | 20.614 | N | 0
2025-09-29 | 04 | 2031-09-29 04:00 | 13.76 | 18.0783 | N | 0
2025-09-29 | 05 | 2031-09-29 05:00 | 12.32 | 16.1864 | N | 0
2025-09-29 | 06 | 2031-09-29 06:00 | 11.44 | 15.0302 | N | 0
2025-09-29 | 07 | 2031-09-29 07:00 | 10.91 | 14.3339 | N | 0
2025-09-29 | 08 | 2031-09-29 08:00 | 10.73 | 14.0974 | N | 0
2025-09-29 | 09 | 2031-09-29 09:00 | 11.57 | 15.201 | N | 0
2025-09-29 | 10 | 2031-09-29 10:00 | 13.27 | 17.4345 | N | 0
2025-09-29 | 11 | 2031-09-29 11:00 | 15.13 | 19.8782 | N | 0
2025-09-29 | 12 | 2031-09-29 12:00 | 15.72 | 20.6534 | N | 0
2025-09-29 | 13 | 2031-09-29 13:00 | 16.86 | 22.1512 | N | 0
2025-09-29 | 14 | 2031-09-29 14:00 | 18.13 | 23.8197 | N | 0
2025-09-29 | 15 | 2031-09-29 15:00 | 18.93 | 24.8708 | N | 0
2025-09-29 | 16 | 2031-09-29 16:00 | 19.65 | 25.8168 | N | 0
2025-09-29 | 17 | 2031-09-29 17:00 | 20.18 | 26.5131 | N | 0
2025-09-29 | 18 | 2031-09-29 18:00 | 21.28 | 27.9583 | N | 0
2025-09-29 | 19 | 2031-09-29 19:00 | 21.96 | 28.8517 | N | 0
2025-09-29 | 20 | 2031-09-29 20:00 | 23.54 | 30.9276 | N | 0
2025-09-29 | 21 | 2031-09-29 21:00 | 24.29 | 31.9129 | N | 0
2025-09-29 | 22 | 2031-09-29 22:00 | 23.71 | 31.1509 | N | 0
2025-09-29 | 23 | 2031-09-29 23:00 | 21.93 | 28.8123 | N | 0
2025-09-30 | 00 | 2031-09-30 | 21.29 | 27.9714 | N | 0
2025-09-30 | 01 | 2031-09-30 01:00 | 19.82 | 26.0401 | N | 0
2025-09-30 | 02 | 2031-09-30 02:00 | 17.69 | 23.2416 | N | 0
2025-09-30 | 03 | 2031-09-30 03:00 | 15.55 | 20.4301 | N | 0
2025-09-30 | 04 | 2031-09-30 04:00 | 13.44 | 17.6579 | N | 0
2025-09-30 | 05 | 2031-09-30 05:00 | 12.08 | 15.8711 | N | 0
2025-09-30 | 06 | 2031-09-30 06:00 | 11.31 | 14.8594 | N | 0
2025-09-30 | 07 | 2031-09-30 07:00 | 11.05 | 14.5178 | N | 0
2025-09-30 | 08 | 2031-09-30 08:00 | 10.9 | 14.3207 | N | 0
2025-09-30 | 09 | 2031-09-30 09:00 | 11.59 | 15.2273 | N | 0
2025-09-30 | 10 | 2031-09-30 10:00 | 13.8 | 18.1309 | N | 0
2025-09-30 | 11 | 2031-09-30 11:00 | 15.66 | 20.5746 | N | 0
2025-09-30 | 12 | 2031-09-30 12:00 | 16.32 | 21.4417 | N | 0
2025-09-30 | 13 | 2031-09-30 13:00 | 17.07 | 22.4271 | N | 0
2025-09-30 | 14 | 2031-09-30 14:00 | 17.7 | 23.2548 | N | 0
2025-09-30 | 15 | 2031-09-30 15:00 | 18.76 | 24.6474 | N | 0
2025-09-30 | 16 | 2031-09-30 16:00 | 19.34 | 25.4095 | N | 0
2025-09-30 | 17 | 2031-09-30 17:00 | 20.06 | 26.3554 | N | 0
2025-09-30 | 18 | 2031-09-30 18:00 | 20.66 | 27.1437 | N | 0
2025-09-30 | 19 | 2031-09-30 19:00 | 21.99 | 28.8911 | N | 0
2025-09-30 | 20 | 2031-09-30 20:00 | 23.06 | 30.2969 | N | 0
2025-09-30 | 21 | 2031-09-30 21:00 | 23.21 | 30.494 | N | 0
2025-09-30 | 22 | 2031-09-30 22:00 | 22.92 | 30.113 | N | 0
2025-09-30 | 23 | 2031-09-30 23:00 | 21.41 | 28.1291 | N | 0
2025-10-01 | 00 | 2031-10-01 | 20.74 | 27.2488 | N | 0
2025-10-01 | 01 | 2031-10-01 01:00 | 19.56 | 25.6985 | N | 0
2025-10-01 | 02 | 2031-10-01 02:00 | 17.39 | 22.8475 | N | 0
2025-10-01 | 03 | 2031-10-01 03:00 | 15.2 | 19.9702 | N | 0
2025-10-01 | 04 | 2031-10-01 04:00 | 13.46 | 17.6841 | N | 0
2025-10-01 | 05 | 2031-10-01 05:00 | 12.18 | 16.0024 | N | 0
2025-10-01 | 06 | 2031-10-01 06:00 | 11.4 | 14.9777 | N | 0
2025-10-01 | 07 | 2031-10-01 07:00 | 11 | 14.4521 | N | 0
2025-10-01 | 08 | 2031-10-01 08:00 | 10.88 | 14.2945 | N | 0
2025-10-01 | 09 | 2031-10-01 09:00 | 11.84 | 15.5557 | N | 0
2025-10-01 | 10 | 2031-10-01 10:00 | 13.73 | 18.0389 | N | 0
2025-10-01 | 11 | 2031-10-01 11:00 | 15.66 | 20.5746 | N | 0
2025-10-01 | 12 | 2031-10-01 12:00 | 16.15 | 21.2184 | N | 0
2025-10-01 | 13 | 2031-10-01 13:00 | 16.41 | 21.5599 | N | 0
2025-10-01 | 14 | 2031-10-01 14:00 | 16.98 | 22.3088 | N | 0
2025-10-01 | 15 | 2031-10-01 15:00 | 17.39 | 22.8475 | N | 0
2025-10-01 | 16 | 2031-10-01 16:00 | 17.57 | 23.084 | N | 0
2025-10-01 | 17 | 2031-10-01 17:00 | 17.59 | 23.1103 | N | 0
2025-10-01 | 18 | 2031-10-01 18:00 | 17.72 | 23.2811 | N | 0
2025-10-01 | 19 | 2031-10-01 19:00 | 18.34 | 24.0956 | N | 0
2025-10-01 | 20 | 2031-10-01 20:00 | 18.86 | 24.7788 | N | 0
2025-10-01 | 21 | 2031-10-01 21:00 | 19.49 | 25.6065 | N | 0
2025-10-01 | 22 | 2031-10-01 22:00 | 19.25 | 25.2912 | N | 0
2025-10-01 | 23 | 2031-10-01 23:00 | 19.29 | 25.3438 | N | 0
2025-10-02 | 00 | 2031-10-02 | 19.16 | 25.173 | N | 0
2025-10-02 | 01 | 2031-10-02 01:00 | 18 | 23.6489 | N | 0
2025-10-02 | 02 | 2031-10-02 02:00 | 16.39 | 21.5337 | N | 0
2025-10-02 | 03 | 2031-10-02 03:00 | 14.37 | 18.8797 | N | 0
2025-10-02 | 04 | 2031-10-02 04:00 | 12.93 | 16.9878 | N | 0
2025-10-02 | 05 | 2031-10-02 05:00 | 11.7 | 15.3718 | N | 0
2025-10-02 | 06 | 2031-10-02 06:00 | 11.03 | 14.4915 | N | 0
2025-10-02 | 07 | 2031-10-02 07:00 | 10.65 | 13.9923 | N | 0
2025-10-02 | 08 | 2031-10-02 08:00 | 10.73 | 14.0974 | N | 0
2025-10-02 | 09 | 2031-10-02 09:00 | 11.58 | 15.2141 | N | 0
2025-10-02 | 10 | 2031-10-02 10:00 | 13.68 | 17.9732 | N | 0
2025-10-02 | 11 | 2031-10-02 11:00 | 15.8 | 20.7585 | N | 0
2025-10-02 | 12 | 2031-10-02 12:00 | 16.08 | 21.1264 | N | 0
2025-10-02 | 13 | 2031-10-02 13:00 | 16.44 | 21.5994 | N | 0
2025-10-02 | 14 | 2031-10-02 14:00 | 16.64 | 21.8621 | N | 0
2025-10-02 | 15 | 2031-10-02 15:00 | 16.94 | 22.2563 | N | 0
2025-10-02 | 16 | 2031-10-02 16:00 | 17.09 | 22.4534 | N | 0
2025-10-02 | 17 | 2031-10-02 17:00 | 17.56 | 23.0709 | N | 0
2025-10-02 | 18 | 2031-10-02 18:00 | 17.56 | 23.0709 | N | 0
2025-10-02 | 19 | 2031-10-02 19:00 | 17.94 | 23.5701 | N | 0
2025-10-02 | 20 | 2031-10-02 20:00 | 18.36 | 24.1219 | N | 0
2025-10-02 | 21 | 2031-10-02 21:00 | 18.94 | 24.8839 | N | 0
2025-10-02 | 22 | 2031-10-02 22:00 | 18.67 | 24.5292 | N | 0
2025-10-02 | 23 | 2031-10-02 23:00 | 18.84 | 24.7526 | N | 0
2025-10-03 | 00 | 2031-10-03 | 18.67 | 24.5292 | N | 0
2025-10-03 | 01 | 2031-10-03 01:00 | 18.2 | 23.9117 | N | 0
2025-10-03 | 02 | 2031-10-03 02:00 | 16.21 | 21.2972 | N | 0
2025-10-03 | 03 | 2031-10-03 03:00 | 14.64 | 19.2345 | N | 0
2025-10-03 | 04 | 2031-10-03 04:00 | 12.88 | 16.9221 | N | 0
2025-10-03 | 05 | 2031-10-03 05:00 | 12.12 | 15.9236 | N | 0
2025-10-03 | 06 | 2031-10-03 06:00 | 11.21 | 14.728 | N | 0
2025-10-03 | 07 | 2031-10-03 07:00 | 10.86 | 14.2682 | N | 0
2025-10-03 | 08 | 2031-10-03 08:00 | 10.75 | 14.1237 | N | 0
2025-10-03 | 09 | 2031-10-03 09:00 | 11.64 | 15.293 | N | 0
2025-10-03 | 10 | 2031-10-03 10:00 | 13.71 | 18.0126 | N | 0
2025-10-03 | 11 | 2031-10-03 11:00 | 15.24 | 20.0228 | N | 0
2025-10-03 | 12 | 2031-10-03 12:00 | 15.81 | 20.7716 | N | 0
2025-10-03 | 13 | 2031-10-03 13:00 | 16.27 | 21.376 | N | 0
2025-10-03 | 14 | 2031-10-03 14:00 | 16.96 | 22.2826 | N | 0
2025-10-03 | 15 | 2031-10-03 15:00 | 17.49 | 22.9789 | N | 0
2025-10-03 | 16 | 2031-10-03 16:00 | 17.72 | 23.2811 | N | 0
2025-10-03 | 17 | 2031-10-03 17:00 | 18.08 | 23.754 | N | 0
2025-10-03 | 18 | 2031-10-03 18:00 | 18.08 | 23.754 | N | 0
2025-10-03 | 19 | 2031-10-03 19:00 | 18.66 | 24.5161 | N | 0
2025-10-03 | 20 | 2031-10-03 20:00 | 19.56 | 25.6985 | N | 0
2025-10-03 | 21 | 2031-10-03 21:00 | 19.77 | 25.9744 | N | 0
2025-10-03 | 22 | 2031-10-03 22:00 | 19.62 | 25.7773 | N | 0
2025-10-03 | 23 | 2031-10-03 23:00 | 19.16 | 25.173 | N | 0
2025-10-04 | 00 | 2031-10-04 | 19.02 | 24.989 | N | 0
2025-10-04 | 01 | 2031-10-04 01:00 | 17.82 | 23.4124 | N | 0
2025-10-04 | 02 | 2031-10-04 02:00 | 16.75 | 22.0066 | N | 0
2025-10-04 | 03 | 2031-10-04 03:00 | 15.02 | 19.7337 | N | 0
2025-10-04 | 04 | 2031-10-04 04:00 | 13.34 | 17.5265 | N | 0
2025-10-04 | 05 | 2031-10-04 05:00 | 12.23 | 16.0681 | N | 0
2025-10-04 | 06 | 2031-10-04 06:00 | 11.55 | 15.1747 | N | 0
2025-10-04 | 07 | 2031-10-04 07:00 | 10.9 | 14.3207 | N | 0
2025-10-04 | 08 | 2031-10-04 08:00 | 10.6 | 13.9266 | N | 0
2025-10-04 | 09 | 2031-10-04 09:00 | 10.69 | 14.0448 | N | 0
2025-10-04 | 10 | 2031-10-04 10:00 | 11.33 | 14.8857 | N | 0
2025-10-04 | 11 | 2031-10-04 11:00 | 12.57 | 16.5148 | N | 0
2025-10-04 | 12 | 2031-10-04 12:00 | 14.21 | 18.6695 | N | 0
2025-10-04 | 13 | 2031-10-04 13:00 | 15.76 | 20.706 | N | 0
2025-10-04 | 14 | 2031-10-04 14:00 | 17.31 | 22.7424 | N | 0
2025-10-04 | 15 | 2031-10-04 15:00 | 18.57 | 24.3978 | N | 0
2025-10-04 | 16 | 2031-10-04 16:00 | 19.22 | 25.2518 | N | 0
2025-10-04 | 17 | 2031-10-04 17:00 | 20.1 | 26.408 | N | 0
2025-10-04 | 18 | 2031-10-04 18:00 | 20.78 | 27.3014 | N | 0
2025-10-04 | 19 | 2031-10-04 19:00 | 21.32 | 28.0109 | N | 0
2025-10-04 | 20 | 2031-10-04 20:00 | 22.08 | 29.0094 | N | 0
2025-10-04 | 21 | 2031-10-04 21:00 | 22.36 | 29.3772 | N | 0
2025-10-04 | 22 | 2031-10-04 22:00 | 21.93 | 28.8123 | N | 0
2025-10-04 | 23 | 2031-10-04 23:00 | 20.81 | 27.3408 | N | 0
2025-10-05 | 00 | 2031-10-05 | 20.36 | 26.7496 | N | 0
2025-10-05 | 01 | 2031-10-05 01:00 | 19.11 | 25.1073 | N | 0
2025-10-05 | 02 | 2031-10-05 02:00 | 17.97 | 23.6095 | N | 0
2025-10-05 | 03 | 2031-10-05 03:00 | 16.15 | 21.2184 | N | 0
2025-10-05 | 04 | 2031-10-05 04:00 | 14.31 | 18.8009 | N | 0
2025-10-05 | 05 | 2031-10-05 05:00 | 12.69 | 16.6725 | N | 0
2025-10-05 | 06 | 2031-10-05 06:00 | 11.8 | 15.5032 | N | 0
2025-10-05 | 07 | 2031-10-05 07:00 | 11.17 | 14.6755 | N | 0
2025-10-05 | 08 | 2031-10-05 08:00 | 10.75 | 14.1237 | N | 0
2025-10-05 | 09 | 2031-10-05 09:00 | 10.61 | 13.9397 | N | 0
2025-10-05 | 10 | 2031-10-05 10:00 | 11.07 | 14.5441 | N | 0
2025-10-05 | 11 | 2031-10-05 11:00 | 12.06 | 15.8448 | N | 0
2025-10-05 | 12 | 2031-10-05 12:00 | 14.05 | 18.4593 | N | 0
2025-10-05 | 13 | 2031-10-05 13:00 | 16.07 | 21.1132 | N | 0
2025-10-05 | 14 | 2031-10-05 14:00 | 18.02 | 23.6752 | N | 0
2025-10-05 | 15 | 2031-10-05 15:00 | 19.72 | 25.9087 | N | 0
2025-10-05 | 16 | 2031-10-05 16:00 | 20.91 | 27.4722 | N | 0
2025-10-05 | 17 | 2031-10-05 17:00 | 21.7 | 28.5101 | N | 0
2025-10-05 | 18 | 2031-10-05 18:00 | 23.09 | 30.3363 | N | 0
2025-10-05 | 19 | 2031-10-05 19:00 | 24.2 | 31.7947 | N | 0
2025-10-05 | 20 | 2031-10-05 20:00 | 25.25 | 33.1742 | N | 0
2025-10-05 | 21 | 2031-10-05 21:00 | 25.61 | 33.6472 | N | 0
2025-10-05 | 22 | 2031-10-05 22:00 | 24.59 | 32.3071 | N | 0
2025-10-05 | 23 | 2031-10-05 23:00 | 23.75 | 31.2035 | N | 0
2025-10-06 | 00 | 2031-10-06 | 22.9 | 30.0867 | N | 0
2025-10-06 | 01 | 2031-10-06 01:00 | 20.88 | 27.4328 | N | 0
2025-10-06 | 02 | 2031-10-06 02:00 | 18.68 | 24.5423 | N | 0
2025-10-06 | 03 | 2031-10-06 03:00 | 15.98 | 20.995 | N | 0
2025-10-06 | 04 | 2031-10-06 04:00 | 13.94 | 18.3148 | N | 0
2025-10-06 | 05 | 2031-10-06 05:00 | 12.4 | 16.2915 | N | 0
2025-10-06 | 06 | 2031-10-06 06:00 | 11.61 | 15.2536 | N | 0
2025-10-06 | 07 | 2031-10-06 07:00 | 10.92 | 14.347 | N | 0
2025-10-06 | 08 | 2031-10-06 08:00 | 10.8 | 14.1894 | N | 0
2025-10-06 | 09 | 2031-10-06 09:00 | 11.43 | 15.0171 | N | 0
2025-10-06 | 10 | 2031-10-06 10:00 | 13.52 | 17.763 | N | 0
2025-10-06 | 11 | 2031-10-06 11:00 | 15.12 | 19.8651 | N | 0
2025-10-06 | 12 | 2031-10-06 12:00 | 16.1 | 21.1527 | N | 0
2025-10-06 | 13 | 2031-10-06 13:00 | 17.24 | 22.6504 | N | 0
2025-10-06 | 14 | 2031-10-06 14:00 | 18.92 | 24.8577 | N | 0
2025-10-06 | 15 | 2031-10-06 15:00 | 19.47 | 25.5803 | N | 0
2025-10-06 | 16 | 2031-10-06 16:00 | 20.2 | 26.5394 | N | 0
2025-10-06 | 17 | 2031-10-06 17:00 | 21.45 | 28.1816 | N | 0
2025-10-06 | 18 | 2031-10-06 18:00 | 22.35 | 29.3641 | N | 0
2025-10-06 | 19 | 2031-10-06 19:00 | 23.65 | 31.0721 | N | 0
2025-10-06 | 20 | 2031-10-06 20:00 | 24.77 | 32.5436 | N | 0
2025-10-06 | 21 | 2031-10-06 21:00 | 25.13 | 33.0165 | N | 0
2025-10-06 | 22 | 2031-10-06 22:00 | 24.4 | 32.0574 | N | 0
2025-10-06 | 23 | 2031-10-06 23:00 | 23.58 | 30.9801 | N | 0
2025-10-07 | 00 | 2031-10-07 | 22.79 | 29.9422 | N | 0
2025-10-07 | 01 | 2031-10-07 01:00 | 21.6 | 28.3787 | N | 0
2025-10-07 | 02 | 2031-10-07 02:00 | 19.69 | 25.8693 | N | 0
2025-10-07 | 03 | 2031-10-07 03:00 | 17.28 | 22.703 | N | 0
2025-10-07 | 04 | 2031-10-07 04:00 | 15.11 | 19.852 | N | 0
2025-10-07 | 05 | 2031-10-07 05:00 | 13.2 | 17.3426 | N | 0
2025-10-07 | 06 | 2031-10-07 06:00 | 12.19 | 16.0156 | N | 0
2025-10-07 | 07 | 2031-10-07 07:00 | 11.47 | 15.0696 | N | 0
2025-10-07 | 08 | 2031-10-07 08:00 | 11.16 | 14.6623 | N | 0
2025-10-07 | 09 | 2031-10-07 09:00 | 12.14 | 15.9499 | N | 0
2025-10-07 | 10 | 2031-10-07 10:00 | 14.2 | 18.6564 | N | 0
2025-10-07 | 11 | 2031-10-07 11:00 | 16.8 | 22.0723 | N | 0
2025-10-07 | 12 | 2031-10-07 12:00 | 17.52 | 23.0183 | N | 0
2025-10-07 | 13 | 2031-10-07 13:00 | 18.16 | 23.8591 | N | 0
2025-10-07 | 14 | 2031-10-07 14:00 | 19.03 | 25.0022 | N | 0
2025-10-07 | 15 | 2031-10-07 15:00 | 19.53 | 25.6591 | N | 0
2025-10-07 | 16 | 2031-10-07 16:00 | 19.95 | 26.2109 | N | 0
2025-10-07 | 17 | 2031-10-07 17:00 | 20.06 | 26.3554 | N | 0
2025-10-07 | 18 | 2031-10-07 18:00 | 19.78 | 25.9876 | N | 0
2025-10-07 | 19 | 2031-10-07 19:00 | 19.38 | 25.462 | N | 0
2025-10-07 | 20 | 2031-10-07 20:00 | 20.37 | 26.7627 | N | 0
2025-10-07 | 21 | 2031-10-07 21:00 | 21.07 | 27.6824 | N | 0
2025-10-07 | 22 | 2031-10-07 22:00 | 20.89 | 27.4459 | N | 0
2025-10-07 | 23 | 2031-10-07 23:00 | 20.38 | 26.7759 | N | 0
2025-10-08 | 00 | 2031-10-08 | 19.88 | 26.1189 | N | 0
2025-10-08 | 01 | 2031-10-08 01:00 | 18.45 | 24.2402 | N | 0
2025-10-08 | 02 | 2031-10-08 02:00 | 16.94 | 22.2563 | N | 0
2025-10-08 | 03 | 2031-10-08 03:00 | 15.44 | 20.2855 | N | 0
2025-10-08 | 04 | 2031-10-08 04:00 | 13.52 | 17.763 | N | 0
2025-10-08 | 05 | 2031-10-08 05:00 | 12.25 | 16.0944 | N | 0
2025-10-08 | 06 | 2031-10-08 06:00 | 11.62 | 15.2667 | N | 0
2025-10-08 | 07 | 2031-10-08 07:00 | 10.8 | 14.1894 | N | 0
2025-10-08 | 08 | 2031-10-08 08:00 | 10.81 | 14.2025 | N | 0
2025-10-08 | 09 | 2031-10-08 09:00 | 11.67 | 15.3324 | N | 0
2025-10-08 | 10 | 2031-10-08 10:00 | 14.04 | 18.4462 | N | 0
2025-10-08 | 11 | 2031-10-08 11:00 | 15.9 | 20.8899 | N | 0
2025-10-08 | 12 | 2031-10-08 12:00 | 16.3 | 21.4154 | N | 0
2025-10-08 | 13 | 2031-10-08 13:00 | 16.52 | 21.7045 | N | 0
2025-10-08 | 14 | 2031-10-08 14:00 | 16.7 | 21.941 | N | 0
2025-10-08 | 15 | 2031-10-08 15:00 | 16.83 | 22.1118 | N | 0
2025-10-08 | 16 | 2031-10-08 16:00 | 17.08 | 22.4402 | N | 0
2025-10-08 | 17 | 2031-10-08 17:00 | 17.36 | 22.8081 | N | 0
2025-10-08 | 18 | 2031-10-08 18:00 | 17.15 | 22.5322 | N | 0
2025-10-08 | 19 | 2031-10-08 19:00 | 17.5 | 22.992 | N | 0
2025-10-08 | 20 | 2031-10-08 20:00 | 18.12 | 23.8066 | N | 0
2025-10-08 | 21 | 2031-10-08 21:00 | 18.77 | 24.6606 | N | 0
2025-10-08 | 22 | 2031-10-08 22:00 | 18.45 | 24.2402 | N | 0
2025-10-08 | 23 | 2031-10-08 23:00 | 18.57 | 24.3978 | N | 0
2025-10-09 | 00 | 2031-10-09 | 18.55 | 24.3715 | N | 0
2025-10-09 | 01 | 2031-10-09 01:00 | 17.7 | 23.2548 | N | 0
2025-10-09 | 02 | 2031-10-09 02:00 | 16.37 | 21.5074 | N | 0
2025-10-09 | 03 | 2031-10-09 03:00 | 14.72 | 19.3396 | N | 0
2025-10-09 | 04 | 2031-10-09 04:00 | 12.84 | 16.8696 | N | 0
2025-10-09 | 05 | 2031-10-09 05:00 | 11.66 | 15.3193 | N | 0
2025-10-09 | 06 | 2031-10-09 06:00 | 11.13 | 14.6229 | N | 0
2025-10-09 | 07 | 2031-10-09 07:00 | 10.69 | 14.0448 | N | 0
2025-10-09 | 08 | 2031-10-09 08:00 | 10.9 | 14.3207 | N | 0
2025-10-09 | 09 | 2031-10-09 09:00 | 11.87 | 15.5952 | N | 0
2025-10-09 | 10 | 2031-10-09 10:00 | 14.68 | 19.287 | N | 0
2025-10-09 | 11 | 2031-10-09 11:00 | 15.83 | 20.7979 | N | 0
2025-10-09 | 12 | 2031-10-09 12:00 | 16.5 | 21.6782 | N | 0
2025-10-09 | 13 | 2031-10-09 13:00 | 16.67 | 21.9015 | N | 0
2025-10-09 | 14 | 2031-10-09 14:00 | 16.88 | 22.1774 | N | 0
2025-10-09 | 15 | 2031-10-09 15:00 | 17.25 | 22.6636 | N | 0
2025-10-09 | 16 | 2031-10-09 16:00 | 16.8 | 22.0723 | N | 0
2025-10-09 | 17 | 2031-10-09 17:00 | 16.92 | 22.23 | N | 0
2025-10-09 | 18 | 2031-10-09 18:00 | 16.71 | 21.9541 | N | 0
2025-10-09 | 19 | 2031-10-09 19:00 | 16.95 | 22.2694 | N | 0
2025-10-09 | 20 | 2031-10-09 20:00 | 17.62 | 23.1497 | N | 0
2025-10-09 | 21 | 2031-10-09 21:00 | 18.11 | 23.7935 | N | 0
2025-10-09 | 22 | 2031-10-09 22:00 | 18.34 | 24.0956 | N | 0
2025-10-09 | 23 | 2031-10-09 23:00 | 18.93 | 24.8708 | N | 0
2025-10-10 | 00 | 2031-10-10 | 18.68 | 24.5423 | N | 0
2025-10-10 | 01 | 2031-10-10 01:00 | 18.33 | 24.0825 | N | 0
2025-10-10 | 02 | 2031-10-10 02:00 | 16.91 | 22.2169 | N | 0
2025-10-10 | 03 | 2031-10-10 03:00 | 14.85 | 19.5104 | N | 0
2025-10-10 | 04 | 2031-10-10 04:00 | 13.51 | 17.7498 | N | 0
2025-10-10 | 05 | 2031-10-10 05:00 | 12.44 | 16.344 | N | 0
2025-10-10 | 06 | 2031-10-10 06:00 | 11.85 | 15.5689 | N | 0
2025-10-10 | 07 | 2031-10-10 07:00 | 11.49 | 15.0959 | N | 0
2025-10-10 | 08 | 2031-10-10 08:00 | 11.42 | 15.0039 | N | 0
2025-10-10 | 09 | 2031-10-10 09:00 | 12.29 | 16.147 | N | 0
2025-10-10 | 10 | 2031-10-10 10:00 | 15.14 | 19.8914 | N | 0
2025-10-10 | 11 | 2031-10-10 11:00 | 16.43 | 21.5862 | N | 0
2025-10-10 | 12 | 2031-10-10 12:00 | 17.15 | 22.5322 | N | 0
2025-10-10 | 13 | 2031-10-10 13:00 | 17.22 | 22.6241 | N | 0
2025-10-10 | 14 | 2031-10-10 14:00 | 17.65 | 23.1891 | N | 0
2025-10-10 | 15 | 2031-10-10 15:00 | 17.58 | 23.0971 | N | 0
2025-10-10 | 16 | 2031-10-10 16:00 | 17.17 | 22.5585 | N | 0
2025-10-10 | 17 | 2031-10-10 17:00 | 16.99 | 22.322 | N | 0
2025-10-10 | 18 | 2031-10-10 18:00 | 16.64 | 21.8621 | N | 0
2025-10-10 | 19 | 2031-10-10 19:00 | 16.67 | 21.9015 | N | 0
2025-10-10 | 20 | 2031-10-10 20:00 | 17.03 | 22.3745 | N | 0
2025-10-10 | 21 | 2031-10-10 21:00 | 17.68 | 23.2285 | N | 0
2025-10-10 | 22 | 2031-10-10 22:00 | 17.34 | 22.7818 | N | 0
2025-10-10 | 23 | 2031-10-10 23:00 | 17.98 | 23.6227 | N | 0
2025-10-11 | 00 | 2031-10-11 | 17.88 | 23.4913 | N | 0
2025-10-11 | 01 | 2031-10-11 01:00 | 17.34 | 22.7818 | N | 0
2025-10-11 | 02 | 2031-10-11 02:00 | 16.19 | 21.2709 | N | 0
2025-10-11 | 03 | 2031-10-11 03:00 | 14.43 | 18.9586 | N | 0
2025-10-11 | 04 | 2031-10-11 04:00 | 13.32 | 17.5002 | N | 0
2025-10-11 | 05 | 2031-10-11 05:00 | 12.1 | 15.8973 | N | 0
2025-10-11 | 06 | 2031-10-11 06:00 | 11.35 | 14.912 | N | 0
2025-10-11 | 07 | 2031-10-11 07:00 | 10.89 | 14.3076 | N | 0
2025-10-11 | 08 | 2031-10-11 08:00 | 10.56 | 13.874 | N | 0
2025-10-11 | 09 | 2031-10-11 09:00 | 10.64 | 13.9791 | N | 0
2025-10-11 | 10 | 2031-10-11 10:00 | 11.23 | 14.7543 | N | 0
2025-10-11 | 11 | 2031-10-11 11:00 | 12.69 | 16.6725 | N | 0
2025-10-11 | 12 | 2031-10-11 12:00 | 14.23 | 18.6958 | N | 0
2025-10-11 | 13 | 2031-10-11 13:00 | 15.78 | 20.7322 | N | 0
2025-10-11 | 14 | 2031-10-11 14:00 | 16.96 | 22.2826 | N | 0
2025-10-11 | 15 | 2031-10-11 15:00 | 17.9 | 23.5176 | N | 0
2025-10-11 | 16 | 2031-10-11 16:00 | 17.69 | 23.2416 | N | 0
2025-10-11 | 17 | 2031-10-11 17:00 | 17.72 | 23.2811 | N | 0
2025-10-11 | 18 | 2031-10-11 18:00 | 17.4 | 22.8606 | N | 0
2025-10-11 | 19 | 2031-10-11 19:00 | 17.42 | 22.8869 | N | 0
2025-10-11 | 20 | 2031-10-11 20:00 | 17.68 | 23.2285 | N | 0
2025-10-11 | 21 | 2031-10-11 21:00 | 17.81 | 23.3993 | N | 0
2025-10-11 | 22 | 2031-10-11 22:00 | 17.64 | 23.176 | N | 0
2025-10-11 | 23 | 2031-10-11 23:00 | 17.22 | 22.6241 | N | 0
2025-10-12 | 00 | 2031-10-12 | 17.05 | 22.4008 | N | 0
2025-10-12 | 01 | 2031-10-12 01:00 | 15.92 | 20.9162 | N | 0
2025-10-12 | 02 | 2031-10-12 02:00 | 15.36 | 20.1804 | N | 0
2025-10-12 | 03 | 2031-10-12 03:00 | 14.16 | 18.6038 | N | 0
2025-10-12 | 04 | 2031-10-12 04:00 | 12.79 | 16.8039 | N | 0
2025-10-12 | 05 | 2031-10-12 05:00 | 11.75 | 15.4375 | N | 0
2025-10-12 | 06 | 2031-10-12 06:00 | 11.21 | 14.728 | N | 0
2025-10-12 | 07 | 2031-10-12 07:00 | 10.68 | 14.0317 | N | 0
2025-10-12 | 08 | 2031-10-12 08:00 | 10.41 | 13.677 | N | 0
2025-10-12 | 09 | 2031-10-12 09:00 | 10.62 | 13.9529 | N | 0
2025-10-12 | 10 | 2031-10-12 10:00 | 11.07 | 14.5441 | N | 0
2025-10-12 | 11 | 2031-10-12 11:00 | 12.1 | 15.8973 | N | 0
2025-10-12 | 12 | 2031-10-12 12:00 | 13.53 | 17.7761 | N | 0
2025-10-12 | 13 | 2031-10-12 13:00 | 14.72 | 19.3396 | N | 0
2025-10-12 | 14 | 2031-10-12 14:00 | 16.29 | 21.4023 | N | 0
2025-10-12 | 15 | 2031-10-12 15:00 | 16.76 | 22.0198 | N | 0
2025-10-12 | 16 | 2031-10-12 16:00 | 16.95 | 22.2694 | N | 0
2025-10-12 | 17 | 2031-10-12 17:00 | 17.06 | 22.4139 | N | 0
2025-10-12 | 18 | 2031-10-12 18:00 | 16.88 | 22.1774 | N | 0
2025-10-12 | 19 | 2031-10-12 19:00 | 17.31 | 22.7424 | N | 0
2025-10-12 | 20 | 2031-10-12 20:00 | 17.45 | 22.9263 | N | 0
2025-10-12 | 21 | 2031-10-12 21:00 | 17.45 | 22.9263 | N | 0
2025-10-12 | 22 | 2031-10-12 22:00 | 16.71 | 21.9541 | N | 0
2025-10-12 | 23 | 2031-10-12 23:00 | 16.69 | 21.9278 | N | 0
2025-10-13 | 00 | 2031-10-13 | 16.48 | 21.6519 | N | 0
2025-10-13 | 01 | 2031-10-13 01:00 | 15.78 | 20.7322 | N | 0
2025-10-13 | 02 | 2031-10-13 02:00 | 15.26 | 20.049 | N | 0
2025-10-13 | 03 | 2031-10-13 03:00 | 14.19 | 18.6432 | N | 0
2025-10-13 | 04 | 2031-10-13 04:00 | 12.7 | 16.6856 | N | 0
2025-10-13 | 05 | 2031-10-13 05:00 | 11.78 | 15.4769 | N | 0
2025-10-13 | 06 | 2031-10-13 06:00 | 11 | 14.4521 | N | 0
2025-10-13 | 07 | 2031-10-13 07:00 | 10.53 | 13.8346 | N | 0
2025-10-13 | 08 | 2031-10-13 08:00 | 10.38 | 13.6376 | N | 0
2025-10-13 | 09 | 2031-10-13 09:00 | 10.48 | 13.7689 | N | 0
2025-10-13 | 10 | 2031-10-13 10:00 | 11.22 | 14.7412 | N | 0
2025-10-13 | 11 | 2031-10-13 11:00 | 12.12 | 15.9236 | N | 0
2025-10-13 | 12 | 2031-10-13 12:00 | 13.67 | 17.9601 | N | 0
2025-10-13 | 13 | 2031-10-13 13:00 | 15.07 | 19.7994 | N | 0
2025-10-13 | 14 | 2031-10-13 14:00 | 16.66 | 21.8884 | N | 0
2025-10-13 | 15 | 2031-10-13 15:00 | 17.41 | 22.8738 | N | 0
2025-10-13 | 16 | 2031-10-13 16:00 | 18.03 | 23.6884 | N | 0
2025-10-13 | 17 | 2031-10-13 17:00 | 18.19 | 23.8986 | N | 0
2025-10-13 | 18 | 2031-10-13 18:00 | 17.96 | 23.5964 | N | 0
2025-10-13 | 19 | 2031-10-13 19:00 | 18.34 | 24.0956 | N | 0
2025-10-13 | 20 | 2031-10-13 20:00 | 18.98 | 24.9365 | N | 0
2025-10-13 | 21 | 2031-10-13 21:00 | 18.96 | 24.9102 | N | 0
2025-10-13 | 22 | 2031-10-13 22:00 | 18.67 | 24.5292 | N | 0
2025-10-13 | 23 | 2031-10-13 23:00 | 18.74 | 24.6212 | N | 0
2025-10-14 | 00 | 2031-10-14 | 18.36 | 24.1219 | N | 0
2025-10-14 | 01 | 2031-10-14 01:00 | 17.23 | 22.6373 | N | 0
2025-10-14 | 02 | 2031-10-14 02:00 | 15.72 | 20.6534 | N | 0
2025-10-14 | 03 | 2031-10-14 03:00 | 13.64 | 17.9206 | N | 0
2025-10-14 | 04 | 2031-10-14 04:00 | 12.18 | 16.0024 | N | 0
2025-10-14 | 05 | 2031-10-14 05:00 | 11.08 | 14.5572 | N | 0
2025-10-14 | 06 | 2031-10-14 06:00 | 10.49 | 13.7821 | N | 0
2025-10-14 | 07 | 2031-10-14 07:00 | 10.29 | 13.5193 | N | 0
2025-10-14 | 08 | 2031-10-14 08:00 | 10.35 | 13.5981 | N | 0
2025-10-14 | 09 | 2031-10-14 09:00 | 11.35 | 14.912 | N | 0
2025-10-14 | 10 | 2031-10-14 10:00 | 13.13 | 17.2506 | N | 0
2025-10-14 | 11 | 2031-10-14 11:00 | 15.32 | 20.1279 | N | 0
2025-10-14 | 12 | 2031-10-14 12:00 | 15.79 | 20.7454 | N | 0
2025-10-14 | 13 | 2031-10-14 13:00 | 16.26 | 21.3629 | N | 0
2025-10-14 | 14 | 2031-10-14 14:00 | 16.32 | 21.4417 | N | 0
2025-10-14 | 15 | 2031-10-14 15:00 | 16.56 | 21.757 | N | 0
2025-10-14 | 16 | 2031-10-14 16:00 | 16.77 | 22.0329 | N | 0
2025-10-14 | 17 | 2031-10-14 17:00 | 17.12 | 22.4928 | N | 0
2025-10-14 | 18 | 2031-10-14 18:00 | 17.36 | 22.8081 | N | 0
2025-10-14 | 19 | 2031-10-14 19:00 | 17.69 | 23.2416 | N | 0
2025-10-14 | 20 | 2031-10-14 20:00 | 18.5 | 24.3059 | N | 0
2025-10-14 | 21 | 2031-10-14 21:00 | 18.97 | 24.9234 | N | 0
2025-10-14 | 22 | 2031-10-14 22:00 | 19.09 | 25.081 | N | 0
2025-10-14 | 23 | 2031-10-14 23:00 | 19.05 | 25.0285 | N | 0
2025-10-15 | 00 | 2031-10-15 | 18.89 | 24.8182 | N | 0
2025-10-15 | 01 | 2031-10-15 01:00 | 17.7 | 23.2548 | N | 0
2025-10-15 | 02 | 2031-10-15 02:00 | 16.32 | 21.4417 | N | 0
2025-10-15 | 03 | 2031-10-15 03:00 | 14.3 | 18.7878 | N | 0
2025-10-15 | 04 | 2031-10-15 04:00 | 12.8 | 16.817 | N | 0
2025-10-15 | 05 | 2031-10-15 05:00 | 11.61 | 15.2536 | N | 0
2025-10-15 | 06 | 2031-10-15 06:00 | 10.95 | 14.3864 | N | 0
2025-10-15 | 07 | 2031-10-15 07:00 | 10.59 | 13.9135 | N | 0
2025-10-15 | 08 | 2031-10-15 08:00 | 10.49 | 13.7821 | N | 0
2025-10-15 | 09 | 2031-10-15 09:00 | 11.43 | 15.0171 | N | 0
2025-10-15 | 10 | 2031-10-15 10:00 | 13.51 | 17.7498 | N | 0
2025-10-15 | 11 | 2031-10-15 11:00 | 15.32 | 20.1279 | N | 0
2025-10-15 | 12 | 2031-10-15 12:00 | 15.75 | 20.6928 | N | 0
2025-10-15 | 13 | 2031-10-15 13:00 | 16.14 | 21.2052 | N | 0
2025-10-15 | 14 | 2031-10-15 14:00 | 16.54 | 21.7307 | N | 0
2025-10-15 | 15 | 2031-10-15 15:00 | 16.58 | 21.7833 | N | 0
2025-10-15 | 16 | 2031-10-15 16:00 | 16.68 | 21.9147 | N | 0
2025-10-15 | 17 | 2031-10-15 17:00 | 16.34 | 21.468 | N | 0
2025-10-15 | 18 | 2031-10-15 18:00 | 16.27 | 21.376 | N | 0
2025-10-15 | 19 | 2031-10-15 19:00 | 16.65 | 21.8753 | N | 0
2025-10-15 | 20 | 2031-10-15 20:00 | 17.83 | 23.4256 | N | 0
2025-10-15 | 21 | 2031-10-15 21:00 | 18.4 | 24.1745 | N | 0
2025-10-15 | 22 | 2031-10-15 22:00 | 18.46 | 24.2533 | N | 0
2025-10-15 | 23 | 2031-10-15 23:00 | 18.8 | 24.7 | N | 0
2025-10-16 | 00 | 2031-10-16 | 18.3 | 24.0431 | N | 0
2025-10-16 | 01 | 2031-10-16 01:00 | 17.76 | 23.3336 | N | 0
2025-10-16 | 02 | 2031-10-16 02:00 | 16.3 | 21.4154 | N | 0
2025-10-16 | 03 | 2031-10-16 03:00 | 14.63 | 19.2213 | N | 0
2025-10-16 | 04 | 2031-10-16 04:00 | 12.91 | 16.9615 | N | 0
2025-10-16 | 05 | 2031-10-16 05:00 | 11.79 | 15.4901 | N | 0
2025-10-16 | 06 | 2031-10-16 06:00 | 11.13 | 14.6229 | N | 0
2025-10-16 | 07 | 2031-10-16 07:00 | 10.97 | 14.4127 | N | 0
2025-10-16 | 08 | 2031-10-16 08:00 | 11.03 | 14.4915 | N | 0
2025-10-16 | 09 | 2031-10-16 09:00 | 12.18 | 16.0024 | N | 0
2025-10-16 | 10 | 2031-10-16 10:00 | 14.26 | 18.7352 | N | 0
2025-10-16 | 11 | 2031-10-16 11:00 | 16.05 | 21.087 | N | 0
2025-10-16 | 12 | 2031-10-16 12:00 | 16.55 | 21.7439 | N | 0
2025-10-16 | 13 | 2031-10-16 13:00 | 16.68 | 21.9147 | N | 0
2025-10-16 | 14 | 2031-10-16 14:00 | 16.78 | 22.0461 | N | 0
2025-10-16 | 15 | 2031-10-16 15:00 | 16.76 | 22.0198 | N | 0
2025-10-16 | 16 | 2031-10-16 16:00 | 16.79 | 22.0592 | N | 0
2025-10-16 | 17 | 2031-10-16 17:00 | 16.73 | 21.9804 | N | 0
2025-10-16 | 18 | 2031-10-16 18:00 | 16.85 | 22.138 | N | 0
2025-10-16 | 19 | 2031-10-16 19:00 | 17.05 | 22.4008 | N | 0
2025-10-16 | 20 | 2031-10-16 20:00 | 17.97 | 23.6095 | N | 0
2025-10-16 | 21 | 2031-10-16 21:00 | 18.16 | 23.8591 | N | 0
2025-10-16 | 22 | 2031-10-16 22:00 | 18.3 | 24.0431 | N | 0
2025-10-16 | 23 | 2031-10-16 23:00 | 18.85 | 24.7657 | N | 0
2025-10-17 | 00 | 2031-10-17 | 18.82 | 24.7263 | N | 0
2025-10-17 | 01 | 2031-10-17 01:00 | 17.88 | 23.4913 | N | 0
2025-10-17 | 02 | 2031-10-17 02:00 | 16.78 | 22.0461 | N | 0
2025-10-17 | 03 | 2031-10-17 03:00 | 14.93 | 19.6155 | N | 0
2025-10-17 | 04 | 2031-10-17 04:00 | 13.45 | 17.671 | N | 0
2025-10-17 | 05 | 2031-10-17 05:00 | 12.31 | 16.1732 | N | 0
2025-10-17 | 06 | 2031-10-17 06:00 | 11.62 | 15.2667 | N | 0
2025-10-17 | 07 | 2031-10-17 07:00 | 11.09 | 14.5704 | N | 0
2025-10-17 | 08 | 2031-10-17 08:00 | 11.14 | 14.6361 | N | 0
2025-10-17 | 09 | 2031-10-17 09:00 | 12.22 | 16.055 | N | 0
2025-10-17 | 10 | 2031-10-17 10:00 | 14.3 | 18.7878 | N | 0
2025-10-17 | 11 | 2031-10-17 11:00 | 16.06 | 21.1001 | N | 0
2025-10-17 | 12 | 2031-10-17 12:00 | 16.72 | 21.9672 | N | 0
2025-10-17 | 13 | 2031-10-17 13:00 | 17.2 | 22.5979 | N | 0
2025-10-17 | 14 | 2031-10-17 14:00 | 17.62 | 23.1497 | N | 0
2025-10-17 | 15 | 2031-10-17 15:00 | 17.75 | 23.3205 | N | 0
2025-10-17 | 16 | 2031-10-17 16:00 | 17.64 | 23.176 | N | 0
2025-10-17 | 17 | 2031-10-17 17:00 | 17.76 | 23.3336 | N | 0
2025-10-17 | 18 | 2031-10-17 18:00 | 17.76 | 23.3336 | N | 0
2025-10-17 | 19 | 2031-10-17 19:00 | 17.67 | 23.2154 | N | 0
2025-10-17 | 20 | 2031-10-17 20:00 | 18.14 | 23.8329 | N | 0
2025-10-17 | 21 | 2031-10-17 21:00 | 18.72 | 24.5949 | N | 0
2025-10-17 | 22 | 2031-10-17 22:00 | 18.69 | 24.5555 | N | 0
2025-10-17 | 23 | 2031-10-17 23:00 | 18.64 | 24.4898 | N | 0
2025-10-18 | 00 | 2031-10-18 | 18.24 | 23.9643 | N | 0
2025-10-18 | 01 | 2031-10-18 01:00 | 17.48 | 22.9657 | N | 0
2025-10-18 | 02 | 2031-10-18 02:00 | 16.39 | 21.5337 | N | 0
2025-10-18 | 03 | 2031-10-18 03:00 | 14.7 | 19.3133 | N | 0
2025-10-18 | 04 | 2031-10-18 04:00 | 13.25 | 17.4082 | N | 0
2025-10-18 | 05 | 2031-10-18 05:00 | 12.17 | 15.9893 | N | 0
2025-10-18 | 06 | 2031-10-18 06:00 | 11.49 | 15.0959 | N | 0
2025-10-18 | 07 | 2031-10-18 07:00 | 11.08 | 14.5572 | N | 0
2025-10-18 | 08 | 2031-10-18 08:00 | 10.75 | 14.1237 | N | 0
2025-10-18 | 09 | 2031-10-18 09:00 | 11.09 | 14.5704 | N | 0
2025-10-18 | 10 | 2031-10-18 10:00 | 11.8 | 15.5032 | N | 0
2025-10-18 | 11 | 2031-10-18 11:00 | 12.83 | 16.8564 | N | 0
2025-10-18 | 12 | 2031-10-18 12:00 | 14.59 | 19.1688 | N | 0
2025-10-18 | 13 | 2031-10-18 13:00 | 15.43 | 20.2724 | N | 0
2025-10-18 | 14 | 2031-10-18 14:00 | 15.66 | 20.5746 | N | 0
2025-10-18 | 15 | 2031-10-18 15:00 | 16.12 | 21.1789 | N | 0
2025-10-18 | 16 | 2031-10-18 16:00 | 16.22 | 21.3103 | N | 0
2025-10-18 | 17 | 2031-10-18 17:00 | 15.98 | 20.995 | N | 0
2025-10-18 | 18 | 2031-10-18 18:00 | 15.93 | 20.9293 | N | 0
2025-10-18 | 19 | 2031-10-18 19:00 | 15.96 | 20.9687 | N | 0
2025-10-18 | 20 | 2031-10-18 20:00 | 16.77 | 22.0329 | N | 0
2025-10-18 | 21 | 2031-10-18 21:00 | 17.53 | 23.0314 | N | 0
2025-10-18 | 22 | 2031-10-18 22:00 | 17.67 | 23.2154 | N | 0
2025-10-18 | 23 | 2031-10-18 23:00 | 17.36 | 22.8081 | N | 0
2025-10-19 | 00 | 2031-10-19 | 17.19 | 22.5847 | N | 0
2025-10-19 | 01 | 2031-10-19 01:00 | 16.04 | 21.0738 | N | 0
2025-10-19 | 02 | 2031-10-19 02:00 | 15.47 | 20.3249 | N | 0
2025-10-19 | 03 | 2031-10-19 03:00 | 13.87 | 18.2228 | N | 0
2025-10-19 | 04 | 2031-10-19 04:00 | 12.88 | 16.9221 | N | 0
2025-10-19 | 05 | 2031-10-19 05:00 | 11.68 | 15.3455 | N | 0
2025-10-19 | 06 | 2031-10-19 06:00 | 11.03 | 14.4915 | N | 0
2025-10-19 | 07 | 2031-10-19 07:00 | 10.36 | 13.6113 | N | 0
2025-10-19 | 08 | 2031-10-19 08:00 | 10.21 | 13.4142 | N | 0
2025-10-19 | 09 | 2031-10-19 09:00 | 10.26 | 13.4799 | N | 0
2025-10-19 | 10 | 2031-10-19 10:00 | 10.67 | 14.0186 | N | 0
2025-10-19 | 11 | 2031-10-19 11:00 | 11.63 | 15.2798 | N | 0
2025-10-19 | 12 | 2031-10-19 12:00 | 13.17 | 17.3031 | N | 0
2025-10-19 | 13 | 2031-10-19 13:00 | 14.91 | 19.5892 | N | 0
2025-10-19 | 14 | 2031-10-19 14:00 | 15.66 | 20.5746 | N | 0
2025-10-19 | 15 | 2031-10-19 15:00 | 16.42 | 21.5731 | N | 0
2025-10-19 | 16 | 2031-10-19 16:00 | 17.08 | 22.4402 | N | 0
2025-10-19 | 17 | 2031-10-19 17:00 | 17.46 | 22.9395 | N | 0
2025-10-19 | 18 | 2031-10-19 18:00 | 17.62 | 23.1497 | N | 0
2025-10-19 | 19 | 2031-10-19 19:00 | 17.86 | 23.465 | N | 0
2025-10-19 | 20 | 2031-10-19 20:00 | 19.77 | 25.9744 | N | 0
2025-10-19 | 21 | 2031-10-19 21:00 | 20.38 | 26.7759 | N | 0
2025-10-19 | 22 | 2031-10-19 22:00 | 19.57 | 25.7116 | N | 0
2025-10-19 | 23 | 2031-10-19 23:00 | 19.48 | 25.5934 | N | 0
2025-10-20 | 00 | 2031-10-20 | 18.64 | 24.4898 | N | 0
2025-10-20 | 01 | 2031-10-20 01:00 | 17.72 | 23.2811 | N | 0
2025-10-20 | 02 | 2031-10-20 02:00 | 16.2 | 21.284 | N | 0
2025-10-20 | 03 | 2031-10-20 03:00 | 14.38 | 18.8929 | N | 0
2025-10-20 | 04 | 2031-10-20 04:00 | 12.64 | 16.6068 | N | 0
2025-10-20 | 05 | 2031-10-20 05:00 | 11.53 | 15.1485 | N | 0
2025-10-20 | 06 | 2031-10-20 06:00 | 10.79 | 14.1762 | N | 0
2025-10-20 | 07 | 2031-10-20 07:00 | 10.26 | 13.4799 | N | 0
2025-10-20 | 08 | 2031-10-20 08:00 | 10.33 | 13.5719 | N | 0
2025-10-20 | 09 | 2031-10-20 09:00 | 11.15 | 14.6492 | N | 0
2025-10-20 | 10 | 2031-10-20 10:00 | 13.41 | 17.6185 | N | 0
2025-10-20 | 11 | 2031-10-20 11:00 | 15.72 | 20.6534 | N | 0
2025-10-20 | 12 | 2031-10-20 12:00 | 15.99 | 21.0081 | N | 0
2025-10-20 | 13 | 2031-10-20 13:00 | 16.36 | 21.4943 | N | 0
2025-10-20 | 14 | 2031-10-20 14:00 | 16.97 | 22.2957 | N | 0
2025-10-20 | 15 | 2031-10-20 15:00 | 17.06 | 22.4139 | N | 0
2025-10-20 | 16 | 2031-10-20 16:00 | 17.11 | 22.4796 | N | 0
2025-10-20 | 17 | 2031-10-20 17:00 | 17.32 | 22.7555 | N | 0
2025-10-20 | 18 | 2031-10-20 18:00 | 17.09 | 22.4534 | N | 0
2025-10-20 | 19 | 2031-10-20 19:00 | 17.23 | 22.6373 | N | 0
2025-10-20 | 20 | 2031-10-20 20:00 | 18.26 | 23.9905 | N | 0
2025-10-20 | 21 | 2031-10-20 21:00 | 18.63 | 24.4766 | N | 0
2025-10-20 | 22 | 2031-10-20 22:00 | 18.78 | 24.6737 | N | 0
2025-10-20 | 23 | 2031-10-20 23:00 | 18.99 | 24.9496 | N | 0
2025-10-21 | 00 | 2031-10-21 | 18.76 | 24.6474 | N | 0
2025-10-21 | 01 | 2031-10-21 01:00 | 17.71 | 23.2679 | N | 0
2025-10-21 | 02 | 2031-10-21 02:00 | 16.48 | 21.6519 | N | 0
2025-10-21 | 03 | 2031-10-21 03:00 | 14.69 | 19.3002 | N | 0
2025-10-21 | 04 | 2031-10-21 04:00 | 13.28 | 17.4477 | N | 0
2025-10-21 | 05 | 2031-10-21 05:00 | 12.14 | 15.9499 | N | 0
2025-10-21 | 06 | 2031-10-21 06:00 | 11.46 | 15.0565 | N | 0
2025-10-21 | 07 | 2031-10-21 07:00 | 11.05 | 14.5178 | N | 0
2025-10-21 | 08 | 2031-10-21 08:00 | 11.41 | 14.9908 | N | 0
2025-10-21 | 09 | 2031-10-21 09:00 | 12.25 | 16.0944 | N | 0
2025-10-21 | 10 | 2031-10-21 10:00 | 14.46 | 18.998 | N | 0
2025-10-21 | 11 | 2031-10-21 11:00 | 16.02 | 21.0476 | N | 0
2025-10-21 | 12 | 2031-10-21 12:00 | 16.34 | 21.468 | N | 0
2025-10-21 | 13 | 2031-10-21 13:00 | 16.3 | 21.4154 | N | 0
2025-10-21 | 14 | 2031-10-21 14:00 | 16.73 | 21.9804 | N | 0
2025-10-21 | 15 | 2031-10-21 15:00 | 17.07 | 22.4271 | N | 0
2025-10-21 | 16 | 2031-10-21 16:00 | 16.89 | 22.1906 | N | 0
2025-10-21 | 17 | 2031-10-21 17:00 | 17.05 | 22.4008 | N | 0
2025-10-21 | 18 | 2031-10-21 18:00 | 16.9 | 22.2037 | N | 0
2025-10-21 | 19 | 2031-10-21 19:00 | 16.7 | 21.941 | N | 0
2025-10-21 | 20 | 2031-10-21 20:00 | 17.81 | 23.3993 | N | 0
2025-10-21 | 21 | 2031-10-21 21:00 | 18.43 | 24.2139 | N | 0
2025-10-21 | 22 | 2031-10-21 22:00 | 18.66 | 24.5161 | N | 0
2025-10-21 | 23 | 2031-10-21 23:00 | 18.4 | 24.1745 | N | 0
2025-10-22 | 00 | 2031-10-22 | 17.91 | 23.5307 | N | 0
2025-10-22 | 01 | 2031-10-22 01:00 | 17.44 | 22.9132 | N | 0
2025-10-22 | 02 | 2031-10-22 02:00 | 16.04 | 21.0738 | N | 0
2025-10-22 | 03 | 2031-10-22 03:00 | 14.12 | 18.5513 | N | 0
2025-10-22 | 04 | 2031-10-22 04:00 | 12.79 | 16.8039 | N | 0
2025-10-22 | 05 | 2031-10-22 05:00 | 11.81 | 15.5163 | N | 0
2025-10-22 | 06 | 2031-10-22 06:00 | 11.22 | 14.7412 | N | 0
2025-10-22 | 07 | 2031-10-22 07:00 | 10.86 | 14.2682 | N | 0
2025-10-22 | 08 | 2031-10-22 08:00 | 10.93 | 14.3602 | N | 0
2025-10-22 | 09 | 2031-10-22 09:00 | 12.02 | 15.7922 | N | 0
2025-10-22 | 10 | 2031-10-22 10:00 | 13.9 | 18.2622 | N | 0
2025-10-22 | 11 | 2031-10-22 11:00 | 15.9 | 20.8899 | N | 0
2025-10-22 | 12 | 2031-10-22 12:00 | 16.07 | 21.1132 | N | 0
2025-10-22 | 13 | 2031-10-22 13:00 | 16.62 | 21.8359 | N | 0
2025-10-22 | 14 | 2031-10-22 14:00 | 16.7 | 21.941 | N | 0
2025-10-22 | 15 | 2031-10-22 15:00 | 16.63 | 21.849 | N | 0
2025-10-22 | 16 | 2031-10-22 16:00 | 16.44 | 21.5994 | N | 0
2025-10-22 | 17 | 2031-10-22 17:00 | 16.5 | 21.6782 | N | 0
2025-10-22 | 18 | 2031-10-22 18:00 | 16.55 | 21.7439 | N | 0
2025-10-22 | 19 | 2031-10-22 19:00 | 17.18 | 22.5716 | N | 0
2025-10-22 | 20 | 2031-10-22 20:00 | 18.34 | 24.0956 | N | 0
2025-10-22 | 21 | 2031-10-22 21:00 | 19.23 | 25.2649 | N | 0
2025-10-22 | 22 | 2031-10-22 22:00 | 18.88 | 24.8051 | N | 0
2025-10-22 | 23 | 2031-10-22 23:00 | 18.82 | 24.7263 | N | 0
2025-10-23 | 00 | 2031-10-23 | 18.54 | 24.3584 | N | 0
2025-10-23 | 01 | 2031-10-23 01:00 | 17.73 | 23.2942 | N | 0
2025-10-23 | 02 | 2031-10-23 02:00 | 16.41 | 21.5599 | N | 0
2025-10-23 | 03 | 2031-10-23 03:00 | 14.57 | 19.1425 | N | 0
2025-10-23 | 04 | 2031-10-23 04:00 | 13.27 | 17.4345 | N | 0
2025-10-23 | 05 | 2031-10-23 05:00 | 12.26 | 16.1076 | N | 0
2025-10-23 | 06 | 2031-10-23 06:00 | 11.58 | 15.2141 | N | 0
2025-10-23 | 07 | 2031-10-23 07:00 | 11.38 | 14.9514 | N | 0
2025-10-23 | 08 | 2031-10-23 08:00 | 11.27 | 14.8069 | N | 0
2025-10-23 | 09 | 2031-10-23 09:00 | 12.54 | 16.4754 | N | 0
2025-10-23 | 10 | 2031-10-23 10:00 | 14.45 | 18.9848 | N | 0
2025-10-23 | 11 | 2031-10-23 11:00 | 16.3 | 21.4154 | N | 0
2025-10-23 | 12 | 2031-10-23 12:00 | 16.46 | 21.6256 | N | 0
2025-10-23 | 13 | 2031-10-23 13:00 | 16.71 | 21.9541 | N | 0
2025-10-23 | 14 | 2031-10-23 14:00 | 16.73 | 21.9804 | N | 0
2025-10-23 | 15 | 2031-10-23 15:00 | 16.97 | 22.2957 | N | 0
2025-10-23 | 16 | 2031-10-23 16:00 | 16.93 | 22.2431 | N | 0
2025-10-23 | 17 | 2031-10-23 17:00 | 16.71 | 21.9541 | N | 0
2025-10-23 | 18 | 2031-10-23 18:00 | 17.09 | 22.4534 | N | 0
2025-10-23 | 19 | 2031-10-23 19:00 | 17.08 | 22.4402 | N | 0
2025-10-23 | 20 | 2031-10-23 20:00 | 18.17 | 23.8723 | N | 0
2025-10-23 | 21 | 2031-10-23 21:00 | 18.98 | 24.9365 | N | 0
2025-10-23 | 22 | 2031-10-23 22:00 | 18.88 | 24.8051 | N | 0
2025-10-23 | 23 | 2031-10-23 23:00 | 18.68 | 24.5423 | N | 0
2025-10-24 | 00 | 2031-10-24 | 18.43 | 24.2139 | N | 0
2025-10-24 | 01 | 2031-10-24 01:00 | 17.69 | 23.2416 | N | 0
2025-10-24 | 02 | 2031-10-24 02:00 | 16.6 | 21.8096 | N | 0
2025-10-24 | 03 | 2031-10-24 03:00 | 14.64 | 19.2345 | N | 0
2025-10-24 | 04 | 2031-10-24 04:00 | 13.37 | 17.5659 | N | 0
2025-10-24 | 05 | 2031-10-24 05:00 | 12.42 | 16.3178 | N | 0
2025-10-24 | 06 | 2031-10-24 06:00 | 11.85 | 15.5689 | N | 0
2025-10-24 | 07 | 2031-10-24 07:00 | 11.37 | 14.9382 | N | 0
2025-10-24 | 08 | 2031-10-24 08:00 | 11.44 | 15.0302 | N | 0
2025-10-24 | 09 | 2031-10-24 09:00 | 12.34 | 16.2127 | N | 0
2025-10-24 | 10 | 2031-10-24 10:00 | 14.03 | 18.433 | N | 0
2025-10-24 | 11 | 2031-10-24 11:00 | 15.6 | 20.4957 | N | 0
2025-10-24 | 12 | 2031-10-24 12:00 | 16.6 | 21.8096 | N | 0
2025-10-24 | 13 | 2031-10-24 13:00 | 16.82 | 22.0986 | N | 0
2025-10-24 | 14 | 2031-10-24 14:00 | 17.1 | 22.4665 | N | 0
2025-10-24 | 15 | 2031-10-24 15:00 | 17.21 | 22.611 | N | 0
2025-10-24 | 16 | 2031-10-24 16:00 | 17.48 | 22.9657 | N | 0
2025-10-24 | 17 | 2031-10-24 17:00 | 17.09 | 22.4534 | N | 0
2025-10-24 | 18 | 2031-10-24 18:00 | 17.15 | 22.5322 | N | 0
2025-10-24 | 19 | 2031-10-24 19:00 | 17.06 | 22.4139 | N | 0
2025-10-24 | 20 | 2031-10-24 20:00 | 17.83 | 23.4256 | N | 0
2025-10-24 | 21 | 2031-10-24 21:00 | 17.99 | 23.6358 | N | 0
2025-10-24 | 22 | 2031-10-24 22:00 | 18.27 | 24.0037 | N | 0
2025-10-24 | 23 | 2031-10-24 23:00 | 18.41 | 24.1876 | N | 0
2025-10-25 | 00 | 2031-10-25 | 17.93 | 23.557 | N | 0
2025-10-25 | 01 | 2031-10-25 01:00 | 17.09 | 22.4534 | N | 0
2025-10-25 | 02 | 2031-10-25 02:00 | 16.47 | 21.6388 | N | 0
2025-10-25 | 03 | 2031-10-25 03:00 | 15.06 | 19.7863 | N | 0
2025-10-25 | 04 | 2031-10-25 04:00 | 13.97 | 18.3542 | N | 0
2025-10-25 | 05 | 2031-10-25 05:00 | 13.01 | 17.0929 | N | 0
2025-10-25 | 06 | 2031-10-25 06:00 | 12.33 | 16.1995 | N | 0
2025-10-25 | 07 | 2031-10-25 07:00 | 11.83 | 15.5426 | N | 0
2025-10-25 | 08 | 2031-10-25 08:00 | 11.7 | 15.3718 | N | 0
2025-10-25 | 09 | 2031-10-25 09:00 | 11.82 | 15.5295 | N | 0
2025-10-25 | 10 | 2031-10-25 10:00 | 12.46 | 16.3703 | N | 0
2025-10-25 | 11 | 2031-10-25 11:00 | 13.86 | 18.2097 | N | 0
2025-10-25 | 12 | 2031-10-25 12:00 | 15.42 | 20.2593 | N | 0
2025-10-25 | 13 | 2031-10-25 13:00 | 16.47 | 21.6388 | N | 0
2025-10-25 | 14 | 2031-10-25 14:00 | 16.8 | 22.0723 | N | 0
2025-10-25 | 15 | 2031-10-25 15:00 | 16.98 | 22.3088 | N | 0
2025-10-25 | 16 | 2031-10-25 16:00 | 17.34 | 22.7818 | N | 0
2025-10-25 | 17 | 2031-10-25 17:00 | 17.7 | 23.2548 | N | 0
2025-10-25 | 18 | 2031-10-25 18:00 | 17.23 | 22.6373 | N | 0
2025-10-25 | 19 | 2031-10-25 19:00 | 17.02 | 22.3614 | N | 0
2025-10-25 | 20 | 2031-10-25 20:00 | 17.86 | 23.465 | N | 0
2025-10-25 | 21 | 2031-10-25 21:00 | 18.43 | 24.2139 | N | 0
2025-10-25 | 22 | 2031-10-25 22:00 | 18.73 | 24.608 | N | 0
2025-10-25 | 23 | 2031-10-25 23:00 | 18.53 | 24.3453 | N | 0
2025-10-26 | 00 | 2031-10-26 | 18.12 | 23.8066 | N | 0
2025-10-26 | 01 | 2031-10-26 01:00 | 17.43 | 22.9001 | N | 0
2025-10-26 | 02 | 2031-10-26 02:00 | 16.44 | 21.5994 | N | 0
2025-10-26 | 03 | 2031-10-26 03:00 | 15.41 | 20.2461 | N | 0
2025-10-26 | 04 | 2031-10-26 04:00 | 14.17 | 18.617 | N | 0
2025-10-26 | 05 | 2031-10-26 05:00 | 13.04 | 17.1323 | N | 0
2025-10-26 | 06 | 2031-10-26 06:00 | 12.3 | 16.1601 | N | 0
2025-10-26 | 07 | 2031-10-26 07:00 | 12.13 | 15.9368 | N | 0
2025-10-26 | 08 | 2031-10-26 08:00 | 12.04 | 15.8185 | N | 0
2025-10-26 | 09 | 2031-10-26 09:00 | 12.21 | 16.0419 | N | 0
2025-10-26 | 10 | 2031-10-26 10:00 | 12.64 | 16.6068 | N | 0
2025-10-26 | 11 | 2031-10-26 11:00 | 13.87 | 18.2228 | N | 0
2025-10-26 | 12 | 2031-10-26 12:00 | 15.05 | 19.7731 | N | 0
2025-10-26 | 13 | 2031-10-26 13:00 | 16.28 | 21.3891 | N | 0
2025-10-26 | 14 | 2031-10-26 14:00 | 16.52 | 21.7045 | N | 0
2025-10-26 | 15 | 2031-10-26 15:00 | 17.11 | 22.4796 | N | 0
2025-10-26 | 16 | 2031-10-26 16:00 | 17.25 | 22.6636 | N | 0
2025-10-26 | 17 | 2031-10-26 17:00 | 17.69 | 23.2416 | N | 0
2025-10-26 | 18 | 2031-10-26 18:00 | 17.52 | 23.0183 | N | 0
2025-10-26 | 19 | 2031-10-26 19:00 | 17.69 | 23.2416 | N | 0
2025-10-26 | 20 | 2031-10-26 20:00 | 19.11 | 25.1073 | N | 0
2025-10-26 | 21 | 2031-10-26 21:00 | 19.98 | 26.2503 | N | 0
2025-10-26 | 22 | 2031-10-26 22:00 | 20.34 | 26.7233 | N | 0
2025-10-26 | 23 | 2031-10-26 23:00 | 20.06 | 26.3554 | N | 0
2025-10-27 | 00 | 2031-10-27 | 19.28 | 25.3306 | N | 0
2025-10-27 | 01 | 2031-10-27 01:00 | 18.82 | 24.7263 | N | 0
2025-10-27 | 02 | 2031-10-27 02:00 | 17.39 | 22.8475 | N | 0
2025-10-27 | 03 | 2031-10-27 03:00 | 15.61 | 20.5089 | N | 0
2025-10-27 | 04 | 2031-10-27 04:00 | 14.02 | 18.4199 | N | 0
2025-10-27 | 05 | 2031-10-27 05:00 | 12.9 | 16.9484 | N | 0
2025-10-27 | 06 | 2031-10-27 06:00 | 12.23 | 16.0681 | N | 0
2025-10-27 | 07 | 2031-10-27 07:00 | 11.97 | 15.7265 | N | 0
2025-10-27 | 08 | 2031-10-27 08:00 | 12.28 | 16.1338 | N | 0
2025-10-27 | 09 | 2031-10-27 09:00 | 13.28 | 17.4477 | N | 0
2025-10-27 | 10 | 2031-10-27 10:00 | 15.5 | 20.3644 | N | 0
2025-10-27 | 11 | 2031-10-27 11:00 | 17.32 | 22.7555 | N | 0
2025-10-27 | 12 | 2031-10-27 12:00 | 17.65 | 23.1891 | N | 0
2025-10-27 | 13 | 2031-10-27 13:00 | 17.54 | 23.0446 | N | 0
2025-10-27 | 14 | 2031-10-27 14:00 | 17.6 | 23.1234 | N | 0
2025-10-27 | 15 | 2031-10-27 15:00 | 17.89 | 23.5044 | N | 0
2025-10-27 | 16 | 2031-10-27 16:00 | 17.85 | 23.4519 | N | 0
2025-10-27 | 17 | 2031-10-27 17:00 | 17.88 | 23.4913 | N | 0
2025-10-27 | 18 | 2031-10-27 18:00 | 17.6 | 23.1234 | N | 0
2025-10-27 | 19 | 2031-10-27 19:00 | 17.37 | 22.8212 | N | 0
2025-10-27 | 20 | 2031-10-27 20:00 | 18.74 | 24.6212 | N | 0
2025-10-27 | 21 | 2031-10-27 21:00 | 19.47 | 25.5803 | N | 0
2025-10-27 | 22 | 2031-10-27 22:00 | 19.85 | 26.0795 | N | 0
2025-10-27 | 23 | 2031-10-27 23:00 | 20.01 | 26.2897 | N | 0
2025-10-28 | 00 | 2031-10-28 | 19.68 | 25.8562 | N | 0
2025-10-28 | 01 | 2031-10-28 01:00 | 18.73 | 24.608 | N | 0
2025-10-28 | 02 | 2031-10-28 02:00 | 17.55 | 23.0577 | N | 0
2025-10-28 | 03 | 2031-10-28 03:00 | 15.61 | 20.5089 | N | 0
2025-10-28 | 04 | 2031-10-28 04:00 | 14.31 | 18.8009 | N | 0
2025-10-28 | 05 | 2031-10-28 05:00 | 13.51 | 17.7498 | N | 0
2025-10-28 | 06 | 2031-10-28 06:00 | 12.87 | 16.909 | N | 0
2025-10-28 | 07 | 2031-10-28 07:00 | 12.43 | 16.3309 | N | 0
2025-10-28 | 08 | 2031-10-28 08:00 | 12.31 | 16.1732 | N | 0
2025-10-28 | 09 | 2031-10-28 09:00 | 13.24 | 17.3951 | N | 0
2025-10-28 | 10 | 2031-10-28 10:00 | 15.45 | 20.2987 | N | 0
2025-10-28 | 11 | 2031-10-28 11:00 | 17.19 | 22.5847 | N | 0
2025-10-28 | 12 | 2031-10-28 12:00 | 17.54 | 23.0446 | N | 0
2025-10-28 | 13 | 2031-10-28 13:00 | 17.58 | 23.0971 | N | 0
2025-10-28 | 14 | 2031-10-28 14:00 | 17.61 | 23.1365 | N | 0
2025-10-28 | 15 | 2031-10-28 15:00 | 17.83 | 23.4256 | N | 0
2025-10-28 | 16 | 2031-10-28 16:00 | 17.66 | 23.2022 | N | 0
2025-10-28 | 17 | 2031-10-28 17:00 | 17.82 | 23.4124 | N | 0
2025-10-28 | 18 | 2031-10-28 18:00 | 17.22 | 22.6241 | N | 0
2025-10-28 | 19 | 2031-10-28 19:00 | 17.15 | 22.5322 | N | 0
2025-10-28 | 20 | 2031-10-28 20:00 | 18.23 | 23.9511 | N | 0
2025-10-28 | 21 | 2031-10-28 21:00 | 19.01 | 24.9759 | N | 0
2025-10-28 | 22 | 2031-10-28 22:00 | 19.45 | 25.554 | N | 0
2025-10-28 | 23 | 2031-10-28 23:00 | 19.37 | 25.4489 | N | 0
2025-10-29 | 00 | 2031-10-29 | 19.15 | 25.1598 | N | 0
2025-10-29 | 01 | 2031-10-29 01:00 | 18.64 | 24.4898 | N | 0
2025-10-29 | 02 | 2031-10-29 02:00 | 17.26 | 22.6767 | N | 0
2025-10-29 | 03 | 2031-10-29 03:00 | 15.25 | 20.0359 | N | 0
2025-10-29 | 04 | 2031-10-29 04:00 | 13.95 | 18.3279 | N | 0
2025-10-29 | 05 | 2031-10-29 05:00 | 12.77 | 16.7776 | N | 0
2025-10-29 | 06 | 2031-10-29 06:00 | 12.19 | 16.0156 | N | 0
2025-10-29 | 07 | 2031-10-29 07:00 | 11.85 | 15.5689 | N | 0
2025-10-29 | 08 | 2031-10-29 08:00 | 12.09 | 15.8842 | N | 0
2025-10-29 | 09 | 2031-10-29 09:00 | 13.2 | 17.3426 | N | 0
2025-10-29 | 10 | 2031-10-29 10:00 | 15.57 | 20.4563 | N | 0
2025-10-29 | 11 | 2031-10-29 11:00 | 17.31 | 22.7424 | N | 0
2025-10-29 | 12 | 2031-10-29 12:00 | 17.46 | 22.9395 | N | 0
2025-10-29 | 13 | 2031-10-29 13:00 | 17.58 | 23.0971 | N | 0
2025-10-29 | 14 | 2031-10-29 14:00 | 17.68 | 23.2285 | N | 0
2025-10-29 | 15 | 2031-10-29 15:00 | 17.42 | 22.8869 | N | 0
2025-10-29 | 16 | 2031-10-29 16:00 | 17.43 | 22.9001 | N | 0
2025-10-29 | 17 | 2031-10-29 17:00 | 17.54 | 23.0446 | N | 0
2025-10-29 | 18 | 2031-10-29 18:00 | 17.07 | 22.4271 | N | 0
2025-10-29 | 19 | 2031-10-29 19:00 | 17.43 | 22.9001 | N | 0
2025-10-29 | 20 | 2031-10-29 20:00 | 18.11 | 23.7935 | N | 0
2025-10-29 | 21 | 2031-10-29 21:00 | 18.89 | 24.8182 | N | 0
2025-10-29 | 22 | 2031-10-29 22:00 | 19.39 | 25.4752 | N | 0
2025-10-29 | 23 | 2031-10-29 23:00 | 19.63 | 25.7905 | N | 0
2025-10-30 | 00 | 2031-10-30 | 19.33 | 25.3963 | N | 0
2025-10-30 | 01 | 2031-10-30 01:00 | 18.51 | 24.319 | N | 0
2025-10-30 | 02 | 2031-10-30 02:00 | 17.31 | 22.7424 | N | 0
2025-10-30 | 03 | 2031-10-30 03:00 | 15.72 | 20.6534 | N | 0
2025-10-30 | 04 | 2031-10-30 04:00 | 13.9 | 18.2622 | N | 0
2025-10-30 | 05 | 2031-10-30 05:00 | 12.8 | 16.817 | N | 0
2025-10-30 | 06 | 2031-10-30 06:00 | 12.03 | 15.8054 | N | 0
2025-10-30 | 07 | 2031-10-30 07:00 | 11.71 | 15.3849 | N | 0
2025-10-30 | 08 | 2031-10-30 08:00 | 11.72 | 15.3981 | N | 0
2025-10-30 | 09 | 2031-10-30 09:00 | 12.83 | 16.8564 | N | 0
2025-10-30 | 10 | 2031-10-30 10:00 | 14.74 | 19.3659 | N | 0
2025-10-30 | 11 | 2031-10-30 11:00 | 16.86 | 22.1512 | N | 0
2025-10-30 | 12 | 2031-10-30 12:00 | 17.49 | 22.9789 | N | 0
2025-10-30 | 13 | 2031-10-30 13:00 | 18.26 | 23.9905 | N | 0
2025-10-30 | 14 | 2031-10-30 14:00 | 18.55 | 24.3715 | N | 0
2025-10-30 | 15 | 2031-10-30 15:00 | 18.64 | 24.4898 | N | 0
2025-10-30 | 16 | 2031-10-30 16:00 | 18.92 | 24.8577 | N | 0
2025-10-30 | 17 | 2031-10-30 17:00 | 18.52 | 24.3321 | N | 0
2025-10-30 | 18 | 2031-10-30 18:00 | 18.57 | 24.3978 | N | 0
2025-10-30 | 19 | 2031-10-30 19:00 | 19.21 | 25.2387 | N | 0
2025-10-30 | 20 | 2031-10-30 20:00 | 20.23 | 26.5788 | N | 0
2025-10-30 | 21 | 2031-10-30 21:00 | 20.98 | 27.5641 | N | 0
2025-10-30 | 22 | 2031-10-30 22:00 | 20.65 | 27.1306 | N | 0
2025-10-30 | 23 | 2031-10-30 23:00 | 20.21 | 26.5525 | N | 0
2025-10-31 | 00 | 2031-10-31 | 20.18 | 26.5131 | N | 0
2025-10-31 | 01 | 2031-10-31 01:00 | 19.54 | 25.6722 | N | 0
2025-10-31 | 02 | 2031-10-31 02:00 | 17.68 | 23.2285 | N | 0
2025-10-31 | 03 | 2031-10-31 03:00 | 15.73 | 20.6665 | N | 0
2025-10-31 | 04 | 2031-10-31 04:00 | 14.47 | 19.0111 | N | 0
2025-10-31 | 05 | 2031-10-31 05:00 | 13.24 | 17.3951 | N | 0
2025-10-31 | 06 | 2031-10-31 06:00 | 12.58 | 16.528 | N | 0
2025-10-31 | 07 | 2031-10-31 07:00 | 12.14 | 15.9499 | N | 0
2025-10-31 | 08 | 2031-10-31 08:00 | 12.21 | 16.0419 | N | 0
2025-10-31 | 09 | 2031-10-31 09:00 | 13.19 | 17.3294 | N | 0
2025-10-31 | 10 | 2031-10-31 10:00 | 15.4 | 20.233 | N | 0
2025-10-31 | 11 | 2031-10-31 11:00 | 17.32 | 22.7555 | N | 0
2025-10-31 | 12 | 2031-10-31 12:00 | 17.89 | 23.5044 | N | 0
2025-10-31 | 13 | 2031-10-31 13:00 | 18.63 | 24.4766 | N | 0
2025-10-31 | 14 | 2031-10-31 14:00 | 18.9 | 24.8314 | N | 0
2025-10-31 | 15 | 2031-10-31 15:00 | 18.72 | 24.5949 | N | 0
2025-10-31 | 16 | 2031-10-31 16:00 | 18.67 | 24.5292 | N | 0
2025-10-31 | 17 | 2031-10-31 17:00 | 18.52 | 24.3321 | N | 0
2025-10-31 | 18 | 2031-10-31 18:00 | 18.74 | 24.6212 | N | 0
2025-10-31 | 19 | 2031-10-31 19:00 | 19.36 | 25.4357 | N | 0
2025-10-31 | 20 | 2031-10-31 20:00 | 20.49 | 26.9204 | N | 0
2025-10-31 | 21 | 2031-10-31 21:00 | 20.37 | 26.7627 | N | 0
2025-10-31 | 22 | 2031-10-31 22:00 | 18.84 | 24.7526 | N | 0
2025-10-31 | 23 | 2031-10-31 23:00 | 18.49 | 24.2927 | N | 0
2025-11-01 | 00 | 2031-11-01 | 18.48 | 24.2796 | N | 0
2025-11-01 | 01 | 2031-11-01 01:00 | 17.53 | 23.0314 | N | 0
2025-11-01 | 02 | 2031-11-01 02:00 | 16.99 | 22.322 | N | 0
2025-11-01 | 03 | 2031-11-01 03:00 | 15.7 | 20.6271 | N | 0
2025-11-01 | 04 | 2031-11-01 04:00 | 14.66 | 19.2607 | N | 0
2025-11-01 | 05 | 2031-11-01 05:00 | 13.34 | 17.5265 | N | 0
2025-11-01 | 06 | 2031-11-01 06:00 | 12.83 | 16.8564 | N | 0
2025-11-01 | 07 | 2031-11-01 07:00 | 12.3 | 16.1601 | N | 0
2025-11-01 | 08 | 2031-11-01 08:00 | 11.9 | 15.6346 | N | 0
2025-11-01 | 09 | 2031-11-01 09:00 | 12.02 | 15.7922 | N | 0
2025-11-01 | 10 | 2031-11-01 10:00 | 12.79 | 16.8039 | N | 0
2025-11-01 | 11 | 2031-11-01 11:00 | 13.89 | 18.2491 | N | 0
2025-11-01 | 12 | 2031-11-01 12:00 | 15.39 | 20.2198 | N | 0
2025-11-01 | 13 | 2031-11-01 13:00 | 16.39 | 21.5337 | N | 0
2025-11-01 | 14 | 2031-11-01 14:00 | 17.43 | 22.9001 | N | 0
2025-11-01 | 15 | 2031-11-01 15:00 | 17.62 | 23.1497 | N | 0
2025-11-01 | 16 | 2031-11-01 16:00 | 17.8 | 23.3862 | N | 0
2025-11-01 | 17 | 2031-11-01 17:00 | 18.24 | 23.9643 | N | 0
2025-11-01 | 18 | 2031-11-01 18:00 | 17.95 | 23.5832 | N | 0
2025-11-01 | 19 | 2031-11-01 19:00 | 17.99 | 23.6358 | N | 0
2025-11-01 | 20 | 2031-11-01 20:00 | 18.71 | 24.5818 | N | 0
2025-11-01 | 21 | 2031-11-01 21:00 | 19.42 | 25.5146 | N | 0
2025-11-01 | 22 | 2031-11-01 22:00 | 19.75 | 25.9481 | N | 0
2025-11-01 | 23 | 2031-11-01 23:00 | 19.67 | 25.843 | N | 0
2025-11-02 | 00 | 2031-11-02 | 18.84 | 24.7526 | N | 0
2025-11-02 | 01 | 2031-11-02 01:00 | 17.64 | 23.176 | N | 0
2025-11-02 | 02 | 2031-11-02 02:00 | 16.92 | 22.23 | N | 0
2025-11-02 | 03 | 2031-11-02 03:00 | 15.82 | 20.7848 | N | 0
2025-11-02 | 04 | 2031-11-02 04:00 | 15.21 | 19.9834 | N | 0
2025-11-02 | 06 | 2031-11-02 05:00 | 13.43 | 17.6447 | N | 0
2025-11-02 | 07 | 2031-11-02 06:00 | 12.88 | 16.9221 | N | 0
2025-11-02 | 08 | 2031-11-02 07:00 | 12.43 | 16.3309 | N | 0
2025-11-02 | 09 | 2031-11-02 08:00 | 12.61 | 16.5674 | N | 0
2025-11-02 | 10 | 2031-11-02 09:00 | 12.78 | 16.7907 | N | 0
2025-11-02 | 11 | 2031-11-02 10:00 | 13.54 | 17.7893 | N | 0
2025-11-02 | 12 | 2031-11-02 11:00 | 14.93 | 19.6155 | N | 0
2025-11-02 | 13 | 2031-11-02 12:00 | 16.04 | 21.0738 | N | 0
2025-11-02 | 14 | 2031-11-02 13:00 | 16.48 | 21.6519 | N | 0
2025-11-02 | 15 | 2031-11-02 14:00 | 16.82 | 22.0986 | N | 0
2025-11-02 | 16 | 2031-11-02 15:00 | 17.33 | 22.7687 | N | 0
2025-11-02 | 17 | 2031-11-02 16:00 | 17.51 | 23.0052 | N | 0
2025-11-02 | 18 | 2031-11-02 17:00 | 17.5 | 22.992 | N | 0
2025-11-02 | 19 | 2031-11-02 18:00 | 17.71 | 23.2679 | N | 0
2025-11-02 | 20 | 2031-11-02 19:00 | 18.25 | 23.9774 | N | 0
2025-11-02 | 21 | 2031-11-02 20:00 | 20.86 | 27.4065 | N | 0
2025-11-02 | 22 | 2031-11-02 21:00 | 21.67 | 28.4707 | N | 0
2025-11-02 | 23 | 2031-11-02 22:00 | 21.33 | 28.024 | N | 0
2025-11-03 | 00 | 2031-11-02 23:00 | 19.91 | 26.1584 | N | 0
2025-11-03 | 01 | 2031-11-03 | 19.16 | 25.173 | N | 0
2025-11-03 | 02 | 2031-11-03 01:00 | 18.24 | 23.9643 | N | 0
2025-11-03 | 03 | 2031-11-03 02:00 | 16.5 | 21.6782 | N | 0
2025-11-03 | 04 | 2031-11-03 03:00 | 14.9 | 19.5761 | N | 0
2025-11-03 | 05 | 2031-11-03 04:00 | 13.45 | 17.671 | N | 0
2025-11-03 | 06 | 2031-11-03 05:00 | 12.62 | 16.5805 | N | 0
2025-11-03 | 07 | 2031-11-03 06:00 | 12.11 | 15.9105 | N | 0
2025-11-03 | 08 | 2031-11-03 07:00 | 11.84 | 15.5557 | N | 0
2025-11-03 | 09 | 2031-11-03 08:00 | 11.98 | 15.7397 | N | 0
2025-11-03 | 10 | 2031-11-03 09:00 | 13.19 | 17.3294 | N | 0
2025-11-03 | 11 | 2031-11-03 10:00 | 15.12 | 19.8651 | N | 0
2025-11-03 | 12 | 2031-11-03 11:00 | 16.74 | 21.9935 | N | 0
2025-11-03 | 13 | 2031-11-03 12:00 | 17.33 | 22.7687 | N | 0
2025-11-03 | 14 | 2031-11-03 13:00 | 17.59 | 23.1103 | N | 0
2025-11-03 | 15 | 2031-11-03 14:00 | 18.17 | 23.8723 | N | 0
2025-11-03 | 16 | 2031-11-03 15:00 | 18.71 | 24.5818 | N | 0
2025-11-03 | 17 | 2031-11-03 16:00 | 18.91 | 24.8445 | N | 0
2025-11-03 | 18 | 2031-11-03 17:00 | 18.74 | 24.6212 | N | 0
2025-11-03 | 19 | 2031-11-03 18:00 | 18.44 | 24.227 | N | 0
2025-11-03 | 20 | 2031-11-03 19:00 | 18.6 | 24.4372 | N | 0
2025-11-03 | 21 | 2031-11-03 20:00 | 20.29 | 26.6576 | N | 0
2025-11-03 | 22 | 2031-11-03 21:00 | 21.51 | 28.2605 | N | 0
2025-11-03 | 23 | 2031-11-03 22:00 | 21 | 27.5904 | N | 0
2025-11-04 | 00 | 2031-11-03 23:00 | 20.11 | 26.4211 | N | 0
2025-11-04 | 01 | 2031-11-04 | 19.71 | 25.8956 | N | 0
2025-11-04 | 02 | 2031-11-04 01:00 | 18.61 | 24.4504 | N | 0
2025-11-04 | 03 | 2031-11-04 02:00 | 16.91 | 22.2169 | N | 0
2025-11-04 | 04 | 2031-11-04 03:00 | 15.3 | 20.1016 | N | 0
2025-11-04 | 05 | 2031-11-04 04:00 | 13.86 | 18.2097 | N | 0
2025-11-04 | 06 | 2031-11-04 05:00 | 12.85 | 16.8827 | N | 0
2025-11-04 | 07 | 2031-11-04 06:00 | 12.29 | 16.147 | N | 0
2025-11-04 | 08 | 2031-11-04 07:00 | 12 | 15.766 | N | 0
2025-11-04 | 09 | 2031-11-04 08:00 | 12.18 | 16.0024 | N | 0
2025-11-04 | 10 | 2031-11-04 09:00 | 13.57 | 17.8287 | N | 0
2025-11-04 | 11 | 2031-11-04 10:00 | 15.73 | 20.6665 | N | 0
2025-11-04 | 12 | 2031-11-04 11:00 | 17.29 | 22.7161 | N | 0
2025-11-04 | 13 | 2031-11-04 12:00 | 17.28 | 22.703 | N | 0
2025-11-04 | 14 | 2031-11-04 13:00 | 17.35 | 22.7949 | N | 0
2025-11-04 | 15 | 2031-11-04 14:00 | 17.54 | 23.0446 | N | 0
2025-11-04 | 16 | 2031-11-04 15:00 | 17.77 | 23.3468 | N | 0
2025-11-04 | 17 | 2031-11-04 16:00 | 17.86 | 23.465 | N | 0
2025-11-04 | 18 | 2031-11-04 17:00 | 17.58 | 23.0971 | N | 0
2025-11-04 | 19 | 2031-11-04 18:00 | 17.28 | 22.703 | N | 0
2025-11-04 | 20 | 2031-11-04 19:00 | 17.15 | 22.5322 | N | 0
2025-11-04 | 21 | 2031-11-04 20:00 | 19.31 | 25.3701 | N | 0
2025-11-04 | 22 | 2031-11-04 21:00 | 20.44 | 26.8547 | N | 0
2025-11-04 | 23 | 2031-11-04 22:00 | 20.13 | 26.4474 | N | 0
2025-11-05 | 00 | 2031-11-04 23:00 | 19.33 | 25.3963 | N | 0
2025-11-05 | 01 | 2031-11-05 | 19.06 | 25.0416 | N | 0
2025-11-05 | 02 | 2031-11-05 01:00 | 18.33 | 24.0825 | N | 0
2025-11-05 | 03 | 2031-11-05 02:00 | 16.84 | 22.1249 | N | 0
2025-11-05 | 04 | 2031-11-05 03:00 | 15.12 | 19.8651 | N | 0
2025-11-05 | 05 | 2031-11-05 04:00 | 13.67 | 17.9601 | N | 0
2025-11-05 | 06 | 2031-11-05 05:00 | 12.78 | 16.7907 | N | 0
2025-11-05 | 07 | 2031-11-05 06:00 | 12.03 | 15.8054 | N | 0
2025-11-05 | 08 | 2031-11-05 07:00 | 11.96 | 15.7134 | N | 0
2025-11-05 | 09 | 2031-11-05 08:00 | 12.05 | 15.8316 | N | 0
2025-11-05 | 10 | 2031-11-05 09:00 | 13.18 | 17.3163 | N | 0
2025-11-05 | 11 | 2031-11-05 10:00 | 15.56 | 20.4432 | N | 0
2025-11-05 | 12 | 2031-11-05 11:00 | 17.06 | 22.4139 | N | 0
2025-11-05 | 13 | 2031-11-05 12:00 | 18 | 23.6489 | N | 0
2025-11-05 | 14 | 2031-11-05 13:00 | 18.17 | 23.8723 | N | 0
2025-11-05 | 15 | 2031-11-05 14:00 | 18.84 | 24.7526 | N | 0
2025-11-05 | 16 | 2031-11-05 15:00 | 19.16 | 25.173 | N | 0
2025-11-05 | 17 | 2031-11-05 16:00 | 19.42 | 25.5146 | N | 0
2025-11-05 | 18 | 2031-11-05 17:00 | 19.14 | 25.1467 | N | 0
2025-11-05 | 19 | 2031-11-05 18:00 | 19.01 | 24.9759 | N | 0
2025-11-05 | 20 | 2031-11-05 19:00 | 19.8 | 26.0138 | N | 0
2025-11-05 | 21 | 2031-11-05 20:00 | 20.53 | 26.9729 | N | 0
2025-11-05 | 22 | 2031-11-05 21:00 | 21.7 | 28.5101 | N | 0
2025-11-05 | 23 | 2031-11-05 22:00 | 21.15 | 27.7875 | N | 0
2025-11-06 | 00 | 2031-11-05 23:00 | 20.46 | 26.881 | N | 0
2025-11-06 | 01 | 2031-11-06 | 19.82 | 26.0401 | N | 0
2025-11-06 | 02 | 2031-11-06 01:00 | 18.89 | 24.8182 | N | 0
2025-11-06 | 03 | 2031-11-06 02:00 | 17.19 | 22.5847 | N | 0
2025-11-06 | 04 | 2031-11-06 03:00 | 15.57 | 20.4563 | N | 0
2025-11-06 | 05 | 2031-11-06 04:00 | 14.09 | 18.5119 | N | 0
2025-11-06 | 06 | 2031-11-06 05:00 | 13.17 | 17.3031 | N | 0
2025-11-06 | 07 | 2031-11-06 06:00 | 12.64 | 16.6068 | N | 0
2025-11-06 | 08 | 2031-11-06 07:00 | 12.46 | 16.3703 | N | 0
2025-11-06 | 09 | 2031-11-06 08:00 | 12.55 | 16.4886 | N | 0
2025-11-06 | 10 | 2031-11-06 09:00 | 13.81 | 18.144 | N | 0
2025-11-06 | 11 | 2031-11-06 10:00 | 16.45 | 21.6125 | N | 0
2025-11-06 | 12 | 2031-11-06 11:00 | 17.71 | 23.2679 | N | 0
2025-11-06 | 13 | 2031-11-06 12:00 | 17.64 | 23.176 | N | 0
2025-11-06 | 14 | 2031-11-06 13:00 | 17.82 | 23.4124 | N | 0
2025-11-06 | 15 | 2031-11-06 14:00 | 18.21 | 23.9248 | N | 0
2025-11-06 | 16 | 2031-11-06 15:00 | 18.36 | 24.1219 | N | 0
2025-11-06 | 17 | 2031-11-06 16:00 | 18.02 | 23.6752 | N | 0
2025-11-06 | 18 | 2031-11-06 17:00 | 18.38 | 24.1482 | N | 0
2025-11-06 | 19 | 2031-11-06 18:00 | 18.5 | 24.3059 | N | 0
2025-11-06 | 20 | 2031-11-06 19:00 | 19.17 | 25.1861 | N | 0
2025-11-06 | 21 | 2031-11-06 20:00 | 20.31 | 26.6839 | N | 0
2025-11-06 | 22 | 2031-11-06 21:00 | 21.5 | 28.2473 | N | 0
2025-11-06 | 23 | 2031-11-06 22:00 | 20.97 | 27.551 | N | 0
2025-11-07 | 00 | 2031-11-06 23:00 | 20.48 | 26.9072 | N | 0
2025-11-07 | 01 | 2031-11-07 | 20.28 | 26.6445 | N | 0
2025-11-07 | 02 | 2031-11-07 01:00 | 19.61 | 25.7642 | N | 0
2025-11-07 | 03 | 2031-11-07 02:00 | 17.93 | 23.557 | N | 0
2025-11-07 | 04 | 2031-11-07 03:00 | 16.2 | 21.284 | N | 0
2025-11-07 | 05 | 2031-11-07 04:00 | 14.8 | 19.4447 | N | 0
2025-11-07 | 06 | 2031-11-07 05:00 | 13.85 | 18.1965 | N | 0
2025-11-07 | 07 | 2031-11-07 06:00 | 13.38 | 17.579 | N | 0
2025-11-07 | 08 | 2031-11-07 07:00 | 12.99 | 17.0666 | N | 0
2025-11-07 | 09 | 2031-11-07 08:00 | 12.95 | 17.0141 | N | 0
2025-11-07 | 10 | 2031-11-07 09:00 | 14.08 | 18.4987 | N | 0
2025-11-07 | 11 | 2031-11-07 10:00 | 16.72 | 21.9672 | N | 0
2025-11-07 | 12 | 2031-11-07 11:00 | 17.68 | 23.2285 | N | 0
2025-11-07 | 13 | 2031-11-07 12:00 | 18.28 | 24.0168 | N | 0
2025-11-07 | 14 | 2031-11-07 13:00 | 18.57 | 24.3978 | N | 0
2025-11-07 | 15 | 2031-11-07 14:00 | 18.97 | 24.9234 | N | 0
2025-11-07 | 16 | 2031-11-07 15:00 | 19.6 | 25.7511 | N | 0
2025-11-07 | 17 | 2031-11-07 16:00 | 19.34 | 25.4095 | N | 0
2025-11-07 | 18 | 2031-11-07 17:00 | 19.65 | 25.8168 | N | 0
2025-11-07 | 19 | 2031-11-07 18:00 | 18.89 | 24.8182 | N | 0
2025-11-07 | 20 | 2031-11-07 19:00 | 19.28 | 25.3306 | N | 0
2025-11-07 | 21 | 2031-11-07 20:00 | 20.29 | 26.6576 | N | 0
2025-11-07 | 22 | 2031-11-07 21:00 | 20.69 | 27.1831 | N | 0
2025-11-07 | 23 | 2031-11-07 22:00 | 20.17 | 26.4999 | N | 0
2025-11-08 | 00 | 2031-11-07 23:00 | 19.35 | 25.4226 | N | 0
2025-11-08 | 01 | 2031-11-08 | 18.81 | 24.7131 | N | 0
2025-11-08 | 02 | 2031-11-08 01:00 | 18.09 | 23.7672 | N | 0
2025-11-08 | 03 | 2031-11-08 02:00 | 17.07 | 22.4271 | N | 0
2025-11-08 | 04 | 2031-11-08 03:00 | 15.57 | 20.4563 | N | 0
2025-11-08 | 05 | 2031-11-08 04:00 | 14.24 | 18.7089 | N | 0
2025-11-08 | 06 | 2031-11-08 05:00 | 13.29 | 17.4608 | N | 0
2025-11-08 | 07 | 2031-11-08 06:00 | 12.54 | 16.4754 | N | 0
2025-11-08 | 08 | 2031-11-08 07:00 | 12.22 | 16.055 | N | 0
2025-11-08 | 09 | 2031-11-08 08:00 | 12.03 | 15.8054 | N | 0
2025-11-08 | 10 | 2031-11-08 09:00 | 12.41 | 16.3046 | N | 0
2025-11-08 | 11 | 2031-11-08 10:00 | 13.32 | 17.5002 | N | 0
2025-11-08 | 12 | 2031-11-08 11:00 | 14.7 | 19.3133 | N | 0
2025-11-08 | 13 | 2031-11-08 12:00 | 16 | 21.0213 | N | 0
2025-11-08 | 14 | 2031-11-08 13:00 | 16.75 | 22.0066 | N | 0
2025-11-08 | 15 | 2031-11-08 14:00 | 17.22 | 22.6241 | N | 0
2025-11-08 | 16 | 2031-11-08 15:00 | 17.56 | 23.0709 | N | 0
2025-11-08 | 17 | 2031-11-08 16:00 | 17.51 | 23.0052 | N | 0
2025-11-08 | 18 | 2031-11-08 17:00 | 17.47 | 22.9526 | N | 0
2025-11-08 | 19 | 2031-11-08 18:00 | 17.43 | 22.9001 | N | 0
2025-11-08 | 20 | 2031-11-08 19:00 | 18.44 | 24.227 | N | 0
2025-11-08 | 21 | 2031-11-08 20:00 | 19.69 | 25.8693 | N | 0
2025-11-08 | 22 | 2031-11-08 21:00 | 20.83 | 27.3671 | N | 0
2025-11-08 | 23 | 2031-11-08 22:00 | 20.58 | 27.0386 | N | 0
2025-11-09 | 00 | 2031-11-08 23:00 | 19.64 | 25.8036 | N | 0
2025-11-09 | 01 | 2031-11-09 | 18.96 | 24.9102 | N | 0
2025-11-09 | 02 | 2031-11-09 01:00 | 18.34 | 24.0956 | N | 0
2025-11-09 | 03 | 2031-11-09 02:00 | 17.34 | 22.7818 | N | 0
2025-11-09 | 04 | 2031-11-09 03:00 | 15.8 | 20.7585 | N | 0
2025-11-09 | 05 | 2031-11-09 04:00 | 14.79 | 19.4315 | N | 0
2025-11-09 | 06 | 2031-11-09 05:00 | 13.78 | 18.1046 | N | 0
2025-11-09 | 07 | 2031-11-09 06:00 | 12.97 | 17.0404 | N | 0
2025-11-09 | 08 | 2031-11-09 07:00 | 12.83 | 16.8564 | N | 0
2025-11-09 | 09 | 2031-11-09 08:00 | 12.75 | 16.7513 | N | 0
2025-11-09 | 10 | 2031-11-09 09:00 | 12.99 | 17.0666 | N | 0
2025-11-09 | 11 | 2031-11-09 10:00 | 13.8 | 18.1309 | N | 0
2025-11-09 | 12 | 2031-11-09 11:00 | 15.11 | 19.852 | N | 0
2025-11-09 | 13 | 2031-11-09 12:00 | 16.78 | 22.0461 | N | 0
2025-11-09 | 14 | 2031-11-09 13:00 | 18.4 | 24.1745 | N | 0
2025-11-09 | 15 | 2031-11-09 14:00 | 19.39 | 25.4752 | N | 0
2025-11-09 | 16 | 2031-11-09 15:00 | 20.65 | 27.1306 | N | 0
2025-11-09 | 17 | 2031-11-09 16:00 | 21.47 | 28.2079 | N | 0
2025-11-09 | 18 | 2031-11-09 17:00 | 21.43 | 28.1554 | N | 0
2025-11-09 | 19 | 2031-11-09 18:00 | 21.5 | 28.2473 | N | 0
2025-11-09 | 20 | 2031-11-09 19:00 | 22.25 | 29.2327 | N | 0
2025-11-09 | 21 | 2031-11-09 20:00 | 23.48 | 30.8487 | N | 0
2025-11-09 | 22 | 2031-11-09 21:00 | 15.98 | 20.995 | N | 0
2025-11-09 | 23 | 2031-11-09 22:00 | 15.5 | 20.3644 | N | 0
2025-11-10 | 00 | 2031-11-09 23:00 | 25.69 | 33.7523 | N | 0
2025-11-10 | 01 | 2031-11-10 | 23.39 | 30.7305 | N | 0
2025-11-10 | 02 | 2031-11-10 01:00 | 21.03 | 27.6298 | N | 0
2025-11-10 | 03 | 2031-11-10 02:00 | 19.25 | 25.2912 | N | 0
2025-11-10 | 04 | 2031-11-10 03:00 | 17.12 | 22.4928 | N | 0
2025-11-10 | 05 | 2031-11-10 04:00 | 15.47 | 20.3249 | N | 0
2025-11-10 | 06 | 2031-11-10 05:00 | 14.48 | 19.0243 | N | 0
2025-11-10 | 07 | 2031-11-10 06:00 | 14.02 | 18.4199 | N | 0
2025-11-10 | 08 | 2031-11-10 07:00 | 13.72 | 18.0257 | N | 0
2025-11-10 | 09 | 2031-11-10 08:00 | 13.82 | 18.1571 | N | 0
2025-11-10 | 10 | 2031-11-10 09:00 | 15.14 | 19.8914 | N | 0
2025-11-10 | 11 | 2031-11-10 10:00 | 17.22 | 22.6241 | N | 0
2025-11-10 | 12 | 2031-11-10 11:00 | 19.14 | 25.1467 | N | 0
2025-11-10 | 13 | 2031-11-10 12:00 | 19.88 | 26.1189 | N | 0
2025-11-10 | 14 | 2031-11-10 13:00 | 20.29 | 26.6576 | N | 0
2025-11-10 | 15 | 2031-11-10 14:00 | 20.96 | 27.5379 | N | 0
2025-11-10 | 16 | 2031-11-10 15:00 | 20.95 | 27.5247 | N | 0
2025-11-10 | 17 | 2031-11-10 16:00 | 21.29 | 27.9714 | N | 0
2025-11-10 | 18 | 2031-11-10 17:00 | 21.22 | 27.8795 | N | 0
2025-11-10 | 19 | 2031-11-10 18:00 | 20.86 | 27.4065 | N | 0
2025-11-10 | 20 | 2031-11-10 19:00 | 21.31 | 27.9977 | N | 0
2025-11-10 | 21 | 2031-11-10 20:00 | 22.93 | 30.1261 | N | 0
2025-11-10 | 22 | 2031-11-10 21:00 | 24.48 | 32.1626 | N | 0
2025-11-10 | 23 | 2031-11-10 22:00 | 24.19 | 31.7815 | N | 0
2025-11-11 | 00 | 2031-11-10 23:00 | 22.85 | 30.021 | N | 0
2025-11-11 | 01 | 2031-11-11 | 22.63 | 29.732 | N | 0
2025-11-11 | 02 | 2031-11-11 01:00 | 21.4 | 28.116 | N | 0
2025-11-11 | 03 | 2031-11-11 02:00 | 19.77 | 25.9744 | N | 0
2025-11-11 | 04 | 2031-11-11 03:00 | 17.94 | 23.5701 | N | 0
2025-11-11 | 05 | 2031-11-11 04:00 | 16.35 | 21.4811 | N | 0
2025-11-11 | 06 | 2031-11-11 05:00 | 15.38 | 20.2067 | N | 0
2025-11-11 | 07 | 2031-11-11 06:00 | 14.74 | 19.3659 | N | 0
2025-11-11 | 08 | 2031-11-11 07:00 | 14.29 | 18.7746 | N | 0
2025-11-11 | 09 | 2031-11-11 08:00 | 14.48 | 19.0243 | N | 0
2025-11-11 | 10 | 2031-11-11 09:00 | 15.63 | 20.5352 | N | 0
2025-11-11 | 11 | 2031-11-11 10:00 | 17.59 | 23.1103 | N | 0
2025-11-11 | 12 | 2031-11-11 11:00 | 19.59 | 25.7379 | N | 0
2025-11-11 | 13 | 2031-11-11 12:00 | 20.29 | 26.6576 | N | 0
2025-11-11 | 14 | 2031-11-11 13:00 | 20.22 | 26.5656 | N | 0
2025-11-11 | 15 | 2031-11-11 14:00 | 19.86 | 26.0927 | N | 0
2025-11-11 | 16 | 2031-11-11 15:00 | 20.33 | 26.7102 | N | 0
2025-11-11 | 17 | 2031-11-11 16:00 | 20.41 | 26.8153 | N | 0
2025-11-11 | 18 | 2031-11-11 17:00 | 20.62 | 27.0912 | N | 0
2025-11-11 | 19 | 2031-11-11 18:00 | 20.78 | 27.3014 | N | 0
2025-11-11 | 20 | 2031-11-11 19:00 | 20.68 | 27.17 | N | 0
2025-11-11 | 21 | 2031-11-11 20:00 | 22.67 | 29.7845 | N | 0
2025-11-11 | 22 | 2031-11-11 21:00 | 23.8 | 31.2691 | N | 0
2025-11-11 | 23 | 2031-11-11 22:00 | 22.79 | 29.9422 | N | 0
2025-11-12 | 00 | 2031-11-11 23:00 | 21.92 | 28.7991 | N | 0
2025-11-12 | 01 | 2031-11-12 | 21.53 | 28.2868 | N | 0
2025-11-12 | 02 | 2031-11-12 01:00 | 20.58 | 27.0386 | N | 0
2025-11-12 | 03 | 2031-11-12 02:00 | 19.03 | 25.0022 | N | 0
2025-11-12 | 04 | 2031-11-12 03:00 | 17.12 | 22.4928 | N | 0
2025-11-12 | 05 | 2031-11-12 04:00 | 15.57 | 20.4563 | N | 0
2025-11-12 | 06 | 2031-11-12 05:00 | 14.48 | 19.0243 | N | 0
2025-11-12 | 07 | 2031-11-12 06:00 | 13.9 | 18.2622 | N | 0
2025-11-12 | 08 | 2031-11-12 07:00 | 13.69 | 17.9863 | N | 0
2025-11-12 | 09 | 2031-11-12 08:00 | 13.59 | 17.8549 | N | 0
2025-11-12 | 10 | 2031-11-12 09:00 | 14.87 | 19.5366 | N | 0
2025-11-12 | 11 | 2031-11-12 10:00 | 16.96 | 22.2826 | N | 0
2025-11-12 | 12 | 2031-11-12 11:00 | 18.77 | 24.6606 | N | 0
2025-11-12 | 13 | 2031-11-12 12:00 | 19.7 | 25.8824 | N | 0
2025-11-12 | 14 | 2031-11-12 13:00 | 19.81 | 26.027 | N | 0
2025-11-12 | 15 | 2031-11-12 14:00 | 19.98 | 26.2503 | N | 0
2025-11-12 | 16 | 2031-11-12 15:00 | 20.1 | 26.408 | N | 0
2025-11-12 | 17 | 2031-11-12 16:00 | 20.28 | 26.6445 | N | 0
2025-11-12 | 18 | 2031-11-12 17:00 | 20 | 26.2766 | N | 0
2025-11-12 | 19 | 2031-11-12 18:00 | 19.91 | 26.1584 | N | 0
2025-11-12 | 20 | 2031-11-12 19:00 | 20.3 | 26.6707 | N | 0
2025-11-12 | 21 | 2031-11-12 20:00 | 21.76 | 28.5889 | N | 0
2025-11-12 | 22 | 2031-11-12 21:00 | 22.7 | 29.8239 | N | 0
2025-11-12 | 23 | 2031-11-12 22:00 | 22.25 | 29.2327 | N | 0
2025-11-13 | 00 | 2031-11-12 23:00 | 21.42 | 28.1422 | N | 0
2025-11-13 | 01 | 2031-11-13 | 20.81 | 27.3408 | N | 0
2025-11-13 | 02 | 2031-11-13 01:00 | 20.15 | 26.4737 | N | 0
2025-11-13 | 03 | 2031-11-13 02:00 | 18.22 | 23.938 | N | 0
2025-11-13 | 04 | 2031-11-13 03:00 | 16.52 | 21.7045 | N | 0
2025-11-13 | 05 | 2031-11-13 04:00 | 14.98 | 19.6812 | N | 0
2025-11-13 | 06 | 2031-11-13 05:00 | 13.93 | 18.3016 | N | 0
2025-11-13 | 07 | 2031-11-13 06:00 | 13.39 | 17.5922 | N | 0
2025-11-13 | 08 | 2031-11-13 07:00 | 13.04 | 17.1323 | N | 0
2025-11-13 | 09 | 2031-11-13 08:00 | 13.24 | 17.3951 | N | 0
2025-11-13 | 10 | 2031-11-13 09:00 | 14.26 | 18.7352 | N | 0
2025-11-13 | 11 | 2031-11-13 10:00 | 16.39 | 21.5337 | N | 0
2025-11-13 | 12 | 2031-11-13 11:00 | 18.58 | 24.411 | N | 0
2025-11-13 | 13 | 2031-11-13 12:00 | 18.65 | 24.5029 | N | 0
2025-11-13 | 14 | 2031-11-13 13:00 | 18.44 | 24.227 | N | 0
2025-11-13 | 15 | 2031-11-13 14:00 | 18.61 | 24.4504 | N | 0
2025-11-13 | 16 | 2031-11-13 15:00 | 19.4 | 25.4883 | N | 0
2025-11-13 | 17 | 2031-11-13 16:00 | 18.99 | 24.9496 | N | 0
2025-11-13 | 18 | 2031-11-13 17:00 | 19.04 | 25.0153 | N | 0
2025-11-13 | 19 | 2031-11-13 18:00 | 19.01 | 24.9759 | N | 0
2025-11-13 | 20 | 2031-11-13 19:00 | 19.84 | 26.0664 | N | 0
2025-11-13 | 21 | 2031-11-13 20:00 | 21.41 | 28.1291 | N | 0
2025-11-13 | 22 | 2031-11-13 21:00 | 22.37 | 29.3904 | N | 0
2025-11-13 | 23 | 2031-11-13 22:00 | 21.85 | 28.7072 | N | 0
2025-11-14 | 00 | 2031-11-13 23:00 | 21.11 | 27.7349 | N | 0
2025-11-14 | 01 | 2031-11-14 | 20.68 | 27.17 | N | 0
2025-11-14 | 02 | 2031-11-14 01:00 | 20.23 | 26.5788 | N | 0
2025-11-14 | 03 | 2031-11-14 02:00 | 18.54 | 24.3584 | N | 0
2025-11-14 | 04 | 2031-11-14 03:00 | 16.57 | 21.7702 | N | 0
2025-11-14 | 05 | 2031-11-14 04:00 | 15 | 19.7074 | N | 0
2025-11-14 | 06 | 2031-11-14 05:00 | 14.2 | 18.6564 | N | 0
2025-11-14 | 07 | 2031-11-14 06:00 | 13.71 | 18.0126 | N | 0
2025-11-14 | 08 | 2031-11-14 07:00 | 13.32 | 17.5002 | N | 0
2025-11-14 | 09 | 2031-11-14 08:00 | 13.36 | 17.5528 | N | 0
2025-11-14 | 10 | 2031-11-14 09:00 | 14.57 | 19.1425 | N | 0
2025-11-14 | 11 | 2031-11-14 10:00 | 16.53 | 21.7176 | N | 0
2025-11-14 | 12 | 2031-11-14 11:00 | 17.79 | 23.373 | N | 0
2025-11-14 | 13 | 2031-11-14 12:00 | 18.34 | 24.0956 | N | 0
2025-11-14 | 14 | 2031-11-14 13:00 | 18.54 | 24.3584 | N | 0
2025-11-14 | 15 | 2031-11-14 14:00 | 18.74 | 24.6212 | N | 0
2025-11-14 | 16 | 2031-11-14 15:00 | 19.11 | 25.1073 | N | 0
2025-11-14 | 17 | 2031-11-14 16:00 | 19.12 | 25.1204 | N | 0
2025-11-14 | 18 | 2031-11-14 17:00 | 18.85 | 24.7657 | N | 0
2025-11-14 | 19 | 2031-11-14 18:00 | 18.55 | 24.3715 | N | 0
2025-11-14 | 20 | 2031-11-14 19:00 | 18.44 | 24.227 | N | 0
2025-11-14 | 21 | 2031-11-14 20:00 | 20.42 | 26.8284 | N | 0
2025-11-14 | 22 | 2031-11-14 21:00 | 21.81 | 28.6546 | N | 0
2025-11-14 | 23 | 2031-11-14 22:00 | 21.25 | 27.9189 | N | 0
2025-11-15 | 00 | 2031-11-14 23:00 | 20.68 | 27.17 | N | 0
2025-11-15 | 01 | 2031-11-15 | 20.24 | 26.5919 | N | 0
2025-11-15 | 02 | 2031-11-15 01:00 | 19.85 | 26.0795 | N | 0
2025-11-15 | 03 | 2031-11-15 02:00 | 18.48 | 24.2796 | N | 0
2025-11-15 | 04 | 2031-11-15 03:00 | 16.95 | 22.2694 | N | 0
2025-11-15 | 05 | 2031-11-15 04:00 | 15.71 | 20.6403 | N | 0
2025-11-15 | 06 | 2031-11-15 05:00 | 14.91 | 19.5892 | N | 0
2025-11-15 | 07 | 2031-11-15 06:00 | 13.89 | 18.2491 | N | 0
2025-11-15 | 08 | 2031-11-15 07:00 | 13.54 | 17.7893 | N | 0
2025-11-15 | 09 | 2031-11-15 08:00 | 13.66 | 17.9469 | N | 0
2025-11-15 | 10 | 2031-11-15 09:00 | 13.73 | 18.0389 | N | 0
2025-11-15 | 11 | 2031-11-15 10:00 | 14.71 | 19.3264 | N | 0
2025-11-15 | 12 | 2031-11-15 11:00 | 16.37 | 21.5074 | N | 0
2025-11-15 | 13 | 2031-11-15 12:00 | 17.68 | 23.2285 | N | 0
2025-11-15 | 14 | 2031-11-15 13:00 | 18.29 | 24.0299 | N | 0
2025-11-15 | 15 | 2031-11-15 14:00 | 18.49 | 24.2927 | N | 0
2025-11-15 | 16 | 2031-11-15 15:00 | 19.87 | 26.1058 | N | 0
2025-11-15 | 17 | 2031-11-15 16:00 | 20.55 | 26.9992 | N | 0
2025-11-15 | 18 | 2031-11-15 17:00 | 20.15 | 26.4737 | N | 0
2025-11-15 | 19 | 2031-11-15 18:00 | 20.13 | 26.4474 | N | 0
2025-11-15 | 20 | 2031-11-15 19:00 | 20.74 | 27.2488 | N | 0
2025-11-15 | 21 | 2031-11-15 20:00 | 21.39 | 28.1028 | N | 0
2025-11-15 | 22 | 2031-11-15 21:00 | 21.89 | 28.7597 | N | 0
2025-11-15 | 23 | 2031-11-15 22:00 | 21.31 | 27.9977 | N | 0
2025-11-16 | 00 | 2031-11-15 23:00 | 19.94 | 26.1978 | N | 0
2025-11-16 | 01 | 2031-11-16 | 19.19 | 25.2124 | N | 0
2025-11-16 | 02 | 2031-11-16 01:00 | 18.45 | 24.2402 | N | 0
2025-11-16 | 03 | 2031-11-16 02:00 | 17.46 | 22.9395 | N | 0
2025-11-16 | 04 | 2031-11-16 03:00 | 15.96 | 20.9687 | N | 0
2025-11-16 | 05 | 2031-11-16 04:00 | 14.6 | 19.1819 | N | 0
2025-11-16 | 06 | 2031-11-16 05:00 | 13.58 | 17.8418 | N | 0
2025-11-16 | 07 | 2031-11-16 06:00 | 13.03 | 17.1192 | N | 0
2025-11-16 | 08 | 2031-11-16 07:00 | 12.74 | 16.7382 | N | 0
2025-11-16 | 09 | 2031-11-16 08:00 | 12.41 | 16.3046 | N | 0
2025-11-16 | 10 | 2031-11-16 09:00 | 12.8 | 16.817 | N | 0
2025-11-16 | 11 | 2031-11-16 10:00 | 13.59 | 17.8549 | N | 0
2025-11-16 | 12 | 2031-11-16 11:00 | 14.95 | 19.6418 | N | 0
2025-11-16 | 13 | 2031-11-16 12:00 | 16.49 | 21.6651 | N | 0
2025-11-16 | 14 | 2031-11-16 13:00 | 18.17 | 23.8723 | N | 0
2025-11-16 | 15 | 2031-11-16 14:00 | 19.39 | 25.4752 | N | 0
2025-11-16 | 16 | 2031-11-16 15:00 | 19.84 | 26.0664 | N | 0
2025-11-16 | 17 | 2031-11-16 16:00 | 20.29 | 26.6576 | N | 0
2025-11-16 | 18 | 2031-11-16 17:00 | 20.49 | 26.9204 | N | 0
2025-11-16 | 19 | 2031-11-16 18:00 | 20.58 | 27.0386 | N | 0
2025-11-16 | 20 | 2031-11-16 19:00 | 21.59 | 28.3656 | N | 0
2025-11-16 | 21 | 2031-11-16 20:00 | 22.95 | 30.1524 | N | 0
2025-11-16 | 22 | 2031-11-16 21:00 | 24.2 | 31.7947 | N | 0
2025-11-16 | 23 | 2031-11-16 22:00 | 23.47 | 30.8356 | N | 0
2025-11-17 | 00 | 2031-11-16 23:00 | 22.32 | 29.3247 | N | 0
2025-11-17 | 01 | 2031-11-17 | 22.04 | 28.9568 | N | 0
2025-11-17 | 02 | 2031-11-17 01:00 | 20.43 | 26.8415 | N | 0
2025-11-17 | 03 | 2031-11-17 02:00 | 19.08 | 25.0679 | N | 0
2025-11-17 | 04 | 2031-11-17 03:00 | 17.17 | 22.5585 | N | 0
2025-11-17 | 05 | 2031-11-17 04:00 | 15.63 | 20.5352 | N | 0
2025-11-17 | 06 | 2031-11-17 05:00 | 14.29 | 18.7746 | N | 0
2025-11-17 | 07 | 2031-11-17 06:00 | 13.82 | 18.1571 | N | 0
2025-11-17 | 08 | 2031-11-17 07:00 | 13.47 | 17.6973 | N | 0
2025-11-17 | 09 | 2031-11-17 08:00 | 13.79 | 18.1177 | N | 0
2025-11-17 | 10 | 2031-11-17 09:00 | 14.94 | 19.6286 | N | 0
2025-11-17 | 11 | 2031-11-17 10:00 | 16.99 | 22.322 | N | 0
2025-11-17 | 12 | 2031-11-17 11:00 | 18.84 | 24.7526 | N | 0
2025-11-17 | 13 | 2031-11-17 12:00 | 19.03 | 25.0022 | N | 0
2025-11-17 | 14 | 2031-11-17 13:00 | 19.18 | 25.1993 | N | 0
2025-11-17 | 15 | 2031-11-17 14:00 | 19.73 | 25.9219 | N | 0
2025-11-17 | 16 | 2031-11-17 15:00 | 20.08 | 26.3817 | N | 0
2025-11-17 | 17 | 2031-11-17 16:00 | 20.42 | 26.8284 | N | 0
2025-11-17 | 18 | 2031-11-17 17:00 | 20.45 | 26.8678 | N | 0
2025-11-17 | 19 | 2031-11-17 18:00 | 20.29 | 26.6576 | N | 0
2025-11-17 | 20 | 2031-11-17 19:00 | 20.8 | 27.3277 | N | 0
2025-11-17 | 21 | 2031-11-17 20:00 | 22.79 | 29.9422 | N | 0
2025-11-17 | 22 | 2031-11-17 21:00 | 23.73 | 31.1772 | N | 0
2025-11-17 | 23 | 2031-11-17 22:00 | 23.13 | 30.3889 | N | 0
2025-11-18 | 00 | 2031-11-17 23:00 | 22.19 | 29.1539 | N | 0
2025-11-18 | 01 | 2031-11-18 | 21.73 | 28.5495 | N | 0
2025-11-18 | 02 | 2031-11-18 01:00 | 20.78 | 27.3014 | N | 0
2025-11-18 | 03 | 2031-11-18 02:00 | 19.06 | 25.0416 | N | 0
2025-11-18 | 04 | 2031-11-18 03:00 | 16.94 | 22.2563 | N | 0
2025-11-18 | 05 | 2031-11-18 04:00 | 15.74 | 20.6797 | N | 0
2025-11-18 | 06 | 2031-11-18 05:00 | 14.57 | 19.1425 | N | 0
2025-11-18 | 07 | 2031-11-18 06:00 | 13.99 | 18.3805 | N | 0
2025-11-18 | 08 | 2031-11-18 07:00 | 13.64 | 17.9206 | N | 0
2025-11-18 | 09 | 2031-11-18 08:00 | 13.77 | 18.0914 | N | 0
2025-11-18 | 10 | 2031-11-18 09:00 | 14.8 | 19.4447 | N | 0
2025-11-18 | 11 | 2031-11-18 10:00 | 16.76 | 22.0198 | N | 0
2025-11-18 | 12 | 2031-11-18 11:00 | 18.76 | 24.6474 | N | 0
2025-11-18 | 13 | 2031-11-18 12:00 | 18.9 | 24.8314 | N | 0
2025-11-18 | 14 | 2031-11-18 13:00 | 19.3 | 25.3569 | N | 0
2025-11-18 | 15 | 2031-11-18 14:00 | 19.49 | 25.6065 | N | 0
2025-11-18 | 16 | 2031-11-18 15:00 | 19.75 | 25.9481 | N | 0
2025-11-18 | 17 | 2031-11-18 16:00 | 19.44 | 25.5409 | N | 0
2025-11-18 | 18 | 2031-11-18 17:00 | 19.71 | 25.8956 | N | 0
2025-11-18 | 19 | 2031-11-18 18:00 | 19.37 | 25.4489 | N | 0
2025-11-18 | 20 | 2031-11-18 19:00 | 19.92 | 26.1715 | N | 0
2025-11-18 | 21 | 2031-11-18 20:00 | 21.91 | 28.786 | N | 0
2025-11-18 | 22 | 2031-11-18 21:00 | 22.96 | 30.1655 | N | 0
2025-11-18 | 23 | 2031-11-18 22:00 | 22.91 | 30.0998 | N | 0
2025-11-19 | 00 | 2031-11-18 23:00 | 22.4 | 29.4298 | N | 0
2025-11-19 | 01 | 2031-11-19 | 21.79 | 28.6284 | N | 0
2025-11-19 | 02 | 2031-11-19 01:00 | 20.91 | 27.4722 | N | 0
2025-11-19 | 03 | 2031-11-19 02:00 | 19.19 | 25.2124 | N | 0
2025-11-19 | 04 | 2031-11-19 03:00 | 17.36 | 22.8081 | N | 0
2025-11-19 | 05 | 2031-11-19 04:00 | 15.8 | 20.7585 | N | 0
2025-11-19 | 06 | 2031-11-19 05:00 | 14.96 | 19.6549 | N | 0
2025-11-19 | 07 | 2031-11-19 06:00 | 14.41 | 18.9323 | N | 0
2025-11-19 | 08 | 2031-11-19 07:00 | 14.07 | 18.4856 | N | 0
2025-11-19 | 09 | 2031-11-19 08:00 | 14.12 | 18.5513 | N | 0
2025-11-19 | 10 | 2031-11-19 09:00 | 15.41 | 20.2461 | N | 0
2025-11-19 | 11 | 2031-11-19 10:00 | 17.3 | 22.7293 | N | 0
2025-11-19 | 12 | 2031-11-19 11:00 | 19.16 | 25.173 | N | 0
2025-11-19 | 13 | 2031-11-19 12:00 | 19.25 | 25.2912 | N | 0
2025-11-19 | 14 | 2031-11-19 13:00 | 19.2 | 25.2255 | N | 0
2025-11-19 | 15 | 2031-11-19 14:00 | 18.93 | 24.8708 | N | 0
2025-11-19 | 16 | 2031-11-19 15:00 | 19.38 | 25.462 | N | 0
2025-11-19 | 17 | 2031-11-19 16:00 | 19.26 | 25.3044 | N | 0
2025-11-19 | 18 | 2031-11-19 17:00 | 18.86 | 24.7788 | N | 0
2025-11-19 | 19 | 2031-11-19 18:00 | 18.83 | 24.7394 | N | 0
2025-11-19 | 20 | 2031-11-19 19:00 | 19.09 | 25.081 | N | 0
2025-11-19 | 21 | 2031-11-19 20:00 | 21.34 | 28.0371 | N | 0
2025-11-19 | 22 | 2031-11-19 21:00 | 22.56 | 29.64 | N | 0
2025-11-19 | 23 | 2031-11-19 22:00 | 22.07 | 28.9962 | N | 0
2025-11-20 | 00 | 2031-11-19 23:00 | 21.74 | 28.5627 | N | 0
2025-11-20 | 01 | 2031-11-20 | 21.28 | 27.9583 | N | 0
2025-11-20 | 02 | 2031-11-20 01:00 | 20.46 | 26.881 | N | 0
2025-11-20 | 03 | 2031-11-20 02:00 | 18.97 | 24.9234 | N | 0
2025-11-20 | 04 | 2031-11-20 03:00 | 17.14 | 22.519 | N | 0
2025-11-20 | 05 | 2031-11-20 04:00 | 15.67 | 20.5877 | N | 0
2025-11-20 | 06 | 2031-11-20 05:00 | 14.45 | 18.9848 | N | 0
2025-11-20 | 07 | 2031-11-20 06:00 | 13.94 | 18.3148 | N | 0
2025-11-20 | 08 | 2031-11-20 07:00 | 13.81 | 18.144 | N | 0
2025-11-20 | 09 | 2031-11-20 08:00 | 14.04 | 18.4462 | N | 0
2025-11-20 | 10 | 2031-11-20 09:00 | 15.21 | 19.9834 | N | 0
2025-11-20 | 11 | 2031-11-20 10:00 | 17.88 | 23.4913 | N | 0
2025-11-20 | 12 | 2031-11-20 11:00 | 19.35 | 25.4226 | N | 0
2025-11-20 | 13 | 2031-11-20 12:00 | 19.53 | 25.6591 | N | 0
2025-11-20 | 14 | 2031-11-20 13:00 | 19.22 | 25.2518 | N | 0
2025-11-20 | 15 | 2031-11-20 14:00 | 19.4 | 25.4883 | N | 0
2025-11-20 | 16 | 2031-11-20 15:00 | 19.22 | 25.2518 | N | 0
2025-11-20 | 17 | 2031-11-20 16:00 | 19.19 | 25.2124 | N | 0
2025-11-20 | 18 | 2031-11-20 17:00 | 18.81 | 24.7131 | N | 0
2025-11-20 | 19 | 2031-11-20 18:00 | 18.69 | 24.5555 | N | 0
2025-11-20 | 20 | 2031-11-20 19:00 | 19.37 | 25.4489 | N | 0
2025-11-20 | 21 | 2031-11-20 20:00 | 21.17 | 27.8138 | N | 0
2025-11-20 | 22 | 2031-11-20 21:00 | 22.64 | 29.7451 | N | 0
2025-11-20 | 23 | 2031-11-20 22:00 | 21.8 | 28.6415 | N | 0
2025-11-21 | 00 | 2031-11-20 23:00 | 21.46 | 28.1948 | N | 0
2025-11-21 | 01 | 2031-11-21 | 21.08 | 27.6955 | N | 0
2025-11-21 | 02 | 2031-11-21 01:00 | 20.62 | 27.0912 | N | 0
2025-11-21 | 03 | 2031-11-21 02:00 | 18.52 | 24.3321 | N | 0
2025-11-21 | 04 | 2031-11-21 03:00 | 16.9 | 22.2037 | N | 0
2025-11-21 | 05 | 2031-11-21 04:00 | 15.31 | 20.1147 | N | 0
2025-11-21 | 06 | 2031-11-21 05:00 | 14.48 | 19.0243 | N | 0
2025-11-21 | 07 | 2031-11-21 06:00 | 13.69 | 17.9863 | N | 0
2025-11-21 | 08 | 2031-11-21 07:00 | 13.03 | 17.1192 | N | 0
2025-11-21 | 09 | 2031-11-21 08:00 | 13.06 | 17.1586 | N | 0
2025-11-21 | 10 | 2031-11-21 09:00 | 14.24 | 18.7089 | N | 0
2025-11-21 | 11 | 2031-11-21 10:00 | 16.49 | 21.6651 | N | 0
2025-11-21 | 12 | 2031-11-21 11:00 | 17.99 | 23.6358 | N | 0
2025-11-21 | 13 | 2031-11-21 12:00 | 18.7 | 24.5686 | N | 0
2025-11-21 | 14 | 2031-11-21 13:00 | 19.03 | 25.0022 | N | 0
2025-11-21 | 15 | 2031-11-21 14:00 | 19.14 | 25.1467 | N | 0
2025-11-21 | 16 | 2031-11-21 15:00 | 19.32 | 25.3832 | N | 0
2025-11-21 | 17 | 2031-11-21 16:00 | 19.25 | 25.2912 | N | 0
2025-11-21 | 18 | 2031-11-21 17:00 | 19.68 | 25.8562 | N | 0
2025-11-21 | 19 | 2031-11-21 18:00 | 18.75 | 24.6343 | N | 0
2025-11-21 | 20 | 2031-11-21 19:00 | 19.01 | 24.9759 | N | 0
2025-11-21 | 21 | 2031-11-21 20:00 | 20.21 | 26.5525 | N | 0
2025-11-21 | 22 | 2031-11-21 21:00 | 21.19 | 27.8401 | N | 0
2025-11-21 | 23 | 2031-11-21 22:00 | 20.67 | 27.1569 | N | 0
2025-11-22 | 00 | 2031-11-21 23:00 | 20.48 | 26.9072 | N | 0
2025-11-22 | 01 | 2031-11-22 | 19.98 | 26.2503 | N | 0
2025-11-22 | 02 | 2031-11-22 01:00 | 19.76 | 25.9613 | N | 0
2025-11-22 | 03 | 2031-11-22 02:00 | 18.48 | 24.2796 | N | 0
2025-11-22 | 04 | 2031-11-22 03:00 | 17.15 | 22.5322 | N | 0
2025-11-22 | 05 | 2031-11-22 04:00 | 15.84 | 20.8111 | N | 0
2025-11-22 | 06 | 2031-11-22 05:00 | 14.45 | 18.9848 | N | 0
2025-11-22 | 07 | 2031-11-22 06:00 | 13.96 | 18.3411 | N | 0
2025-11-22 | 08 | 2031-11-22 07:00 | 13.54 | 17.7893 | N | 0
2025-11-22 | 09 | 2031-11-22 08:00 | 13.31 | 17.4871 | N | 0
2025-11-22 | 10 | 2031-11-22 09:00 | 13.47 | 17.6973 | N | 0
2025-11-22 | 11 | 2031-11-22 10:00 | 14.53 | 19.0899 | N | 0
2025-11-22 | 12 | 2031-11-22 11:00 | 15.92 | 20.9162 | N | 0
2025-11-22 | 13 | 2031-11-22 12:00 | 17.09 | 22.4534 | N | 0
2025-11-22 | 14 | 2031-11-22 13:00 | 18.2 | 23.9117 | N | 0
2025-11-22 | 15 | 2031-11-22 14:00 | 18.33 | 24.0825 | N | 0
2025-11-22 | 16 | 2031-11-22 15:00 | 19.15 | 25.1598 | N | 0
2025-11-22 | 17 | 2031-11-22 16:00 | 19.31 | 25.3701 | N | 0
2025-11-22 | 18 | 2031-11-22 17:00 | 19.62 | 25.7773 | N | 0
2025-11-22 | 19 | 2031-11-22 18:00 | 19.42 | 25.5146 | N | 0
2025-11-22 | 20 | 2031-11-22 19:00 | 20.34 | 26.7233 | N | 0
2025-11-22 | 21 | 2031-11-22 20:00 | 21.52 | 28.2736 | N | 0
2025-11-22 | 22 | 2031-11-22 21:00 | 22.24 | 29.2196 | N | 0
2025-11-22 | 23 | 2031-11-22 22:00 | 21.63 | 28.4181 | N | 0
2025-11-23 | 00 | 2031-11-22 23:00 | 20.51 | 26.9466 | N | 0
2025-11-23 | 01 | 2031-11-23 | 20.06 | 26.3554 | N | 0
2025-11-23 | 02 | 2031-11-23 01:00 | 19.34 | 25.4095 | N | 0
2025-11-23 | 03 | 2031-11-23 02:00 | 18.42 | 24.2007 | N | 0
2025-11-23 | 04 | 2031-11-23 03:00 | 17.02 | 22.3614 | N | 0
2025-11-23 | 05 | 2031-11-23 04:00 | 15.67 | 20.5877 | N | 0
2025-11-23 | 06 | 2031-11-23 05:00 | 14.74 | 19.3659 | N | 0
2025-11-23 | 07 | 2031-11-23 06:00 | 13.97 | 18.3542 | N | 0
2025-11-23 | 08 | 2031-11-23 07:00 | 13.51 | 17.7498 | N | 0
2025-11-23 | 09 | 2031-11-23 08:00 | 13.14 | 17.2637 | N | 0
2025-11-23 | 10 | 2031-11-23 09:00 | 13.24 | 17.3951 | N | 0
2025-11-23 | 11 | 2031-11-23 10:00 | 14.08 | 18.4987 | N | 0
2025-11-23 | 12 | 2031-11-23 11:00 | 14.99 | 19.6943 | N | 0
2025-11-23 | 13 | 2031-11-23 12:00 | 16.56 | 21.757 | N | 0
2025-11-23 | 14 | 2031-11-23 13:00 | 17.75 | 23.3205 | N | 0
2025-11-23 | 15 | 2031-11-23 14:00 | 18.49 | 24.2927 | N | 0
2025-11-23 | 16 | 2031-11-23 15:00 | 18.58 | 24.411 | N | 0
2025-11-23 | 17 | 2031-11-23 16:00 | 19.25 | 25.2912 | N | 0
2025-11-23 | 18 | 2031-11-23 17:00 | 19.69 | 25.8693 | N | 0
2025-11-23 | 19 | 2031-11-23 18:00 | 19.65 | 25.8168 | N | 0
2025-11-23 | 20 | 2031-11-23 19:00 | 20.6 | 27.0649 | N | 0
2025-11-23 | 21 | 2031-11-23 20:00 | 23.07 | 30.3101 | N | 0
2025-11-23 | 22 | 2031-11-23 21:00 | 23.78 | 31.2429 | N | 0
2025-11-23 | 23 | 2031-11-23 22:00 | 22.82 | 29.9816 | N | 0
2025-11-24 | 00 | 2031-11-23 23:00 | 21.82 | 28.6678 | N | 0
2025-11-24 | 01 | 2031-11-24 | 21.39 | 28.1028 | N | 0
2025-11-24 | 02 | 2031-11-24 01:00 | 19.95 | 26.2109 | N | 0
2025-11-24 | 03 | 2031-11-24 02:00 | 18.2 | 23.9117 | N | 0
2025-11-24 | 04 | 2031-11-24 03:00 | 16.26 | 21.3629 | N | 0
2025-11-24 | 05 | 2031-11-24 04:00 | 14.63 | 19.2213 | N | 0
2025-11-24 | 06 | 2031-11-24 05:00 | 13.61 | 17.8812 | N | 0
2025-11-24 | 07 | 2031-11-24 06:00 | 13.17 | 17.3031 | N | 0
2025-11-24 | 08 | 2031-11-24 07:00 | 12.95 | 17.0141 | N | 0
2025-11-24 | 09 | 2031-11-24 08:00 | 13.34 | 17.5265 | N | 0
2025-11-24 | 10 | 2031-11-24 09:00 | 14.65 | 19.2476 | N | 0
2025-11-24 | 11 | 2031-11-24 10:00 | 16.85 | 22.138 | N | 0
2025-11-24 | 12 | 2031-11-24 11:00 | 18.54 | 24.3584 | N | 0
2025-11-24 | 13 | 2031-11-24 12:00 | 18.66 | 24.5161 | N | 0
2025-11-24 | 14 | 2031-11-24 13:00 | 18.61 | 24.4504 | N | 0
2025-11-24 | 15 | 2031-11-24 14:00 | 18.68 | 24.5423 | N | 0
2025-11-24 | 16 | 2031-11-24 15:00 | 18.58 | 24.411 | N | 0
2025-11-24 | 17 | 2031-11-24 16:00 | 18.71 | 24.5818 | N | 0
2025-11-24 | 18 | 2031-11-24 17:00 | 18.6 | 24.4372 | N | 0
2025-11-24 | 19 | 2031-11-24 18:00 | 18.32 | 24.0694 | N | 0
2025-11-24 | 20 | 2031-11-24 19:00 | 19.41 | 25.5014 | N | 0
2025-11-24 | 21 | 2031-11-24 20:00 | 21.99 | 28.8911 | N | 0
2025-11-24 | 22 | 2031-11-24 21:00 | 23.14 | 30.402 | N | 0
2025-11-24 | 23 | 2031-11-24 22:00 | 22.04 | 28.9568 | N | 0
2025-11-25 | 00 | 2031-11-24 23:00 | 21.22 | 27.8795 | N | 0
2025-11-25 | 01 | 2031-11-25 | 20.78 | 27.3014 | N | 0
2025-11-25 | 02 | 2031-11-25 01:00 | 20.09 | 26.3948 | N | 0
2025-11-25 | 03 | 2031-11-25 02:00 | 18.4 | 24.1745 | N | 0
2025-11-25 | 04 | 2031-11-25 03:00 | 16.33 | 21.4548 | N | 0
2025-11-25 | 05 | 2031-11-25 04:00 | 14.75 | 19.379 | N | 0
2025-11-25 | 06 | 2031-11-25 05:00 | 13.61 | 17.8812 | N | 0
2025-11-25 | 07 | 2031-11-25 06:00 | 13.19 | 17.3294 | N | 0
2025-11-25 | 08 | 2031-11-25 07:00 | 12.83 | 16.8564 | N | 0
2025-11-25 | 09 | 2031-11-25 08:00 | 13 | 17.0798 | N | 0
2025-11-25 | 10 | 2031-11-25 09:00 | 14.08 | 18.4987 | N | 0
2025-11-25 | 11 | 2031-11-25 10:00 | 16.68 | 21.9147 | N | 0
2025-11-25 | 12 | 2031-11-25 11:00 | 18.01 | 23.6621 | N | 0
2025-11-25 | 13 | 2031-11-25 12:00 | 18.5 | 24.3059 | N | 0
2025-11-25 | 14 | 2031-11-25 13:00 | 18.61 | 24.4504 | N | 0
2025-11-25 | 15 | 2031-11-25 14:00 | 18.86 | 24.7788 | N | 0
2025-11-25 | 16 | 2031-11-25 15:00 | 18.92 | 24.8577 | N | 0
2025-11-25 | 17 | 2031-11-25 16:00 | 19.12 | 25.1204 | N | 0
2025-11-25 | 18 | 2031-11-25 17:00 | 19.32 | 25.3832 | N | 0
2025-11-25 | 19 | 2031-11-25 18:00 | 19.2 | 25.2255 | N | 0
2025-11-25 | 20 | 2031-11-25 19:00 | 19.77 | 25.9744 | N | 0
2025-11-25 | 21 | 2031-11-25 20:00 | 21.87 | 28.7335 | N | 0
2025-11-25 | 22 | 2031-11-25 21:00 | 22.54 | 29.6137 | N | 0
2025-11-25 | 23 | 2031-11-25 22:00 | 21.8 | 28.6415 | N | 0
2025-11-26 | 00 | 2031-11-25 23:00 | 20.7 | 27.1963 | N | 0
2025-11-26 | 01 | 2031-11-26 | 20.54 | 26.9861 | N | 0
2025-11-26 | 02 | 2031-11-26 01:00 | 19.72 | 25.9087 | N | 0
2025-11-26 | 03 | 2031-11-26 02:00 | 18 | 23.6489 | N | 0
2025-11-26 | 04 | 2031-11-26 03:00 | 15.91 | 20.903 | N | 0
2025-11-26 | 05 | 2031-11-26 04:00 | 14.58 | 19.1556 | N | 0
2025-11-26 | 06 | 2031-11-26 05:00 | 13.17 | 17.3031 | N | 0
2025-11-26 | 07 | 2031-11-26 06:00 | 12.85 | 16.8827 | N | 0
2025-11-26 | 08 | 2031-11-26 07:00 | 12.32 | 16.1864 | N | 0
2025-11-26 | 09 | 2031-11-26 08:00 | 12.5 | 16.4229 | N | 0
2025-11-26 | 10 | 2031-11-26 09:00 | 13.75 | 18.0652 | N | 0
2025-11-26 | 11 | 2031-11-26 10:00 | 16.03 | 21.0607 | N | 0
2025-11-26 | 12 | 2031-11-26 11:00 | 17.56 | 23.0709 | N | 0
2025-11-26 | 13 | 2031-11-26 12:00 | 17.85 | 23.4519 | N | 0
2025-11-26 | 14 | 2031-11-26 13:00 | 18.15 | 23.846 | N | 0
2025-11-26 | 15 | 2031-11-26 14:00 | 18.58 | 24.411 | N | 0
2025-11-26 | 16 | 2031-11-26 15:00 | 18.98 | 24.9365 | N | 0
2025-11-26 | 17 | 2031-11-26 16:00 | 19.12 | 25.1204 | N | 0
2025-11-26 | 18 | 2031-11-26 17:00 | 19.24 | 25.2781 | N | 0
2025-11-26 | 19 | 2031-11-26 18:00 | 19.41 | 25.5014 | N | 0
2025-11-26 | 20 | 2031-11-26 19:00 | 20.37 | 26.7627 | N | 0
2025-11-26 | 21 | 2031-11-26 20:00 | 21.24 | 27.9057 | N | 0
2025-11-26 | 22 | 2031-11-26 21:00 | 14.52 | 19.0768 | N | 0
2025-11-26 | 23 | 2031-11-26 22:00 | 24.8 | 32.583 | N | 0
2025-11-27 | 00 | 2031-11-26 23:00 | 21.75 | 28.5758 | N | 0
2025-11-27 | 01 | 2031-11-27 | 21.5 | 28.2473 | N | 0
2025-11-27 | 02 | 2031-11-27 01:00 | 20.53 | 26.9729 | N | 0
2025-11-27 | 03 | 2031-11-27 02:00 | 19.01 | 24.9759 | N | 0
2025-11-27 | 04 | 2031-11-27 03:00 | 17.09 | 22.4534 | N | 0
2025-11-27 | 05 | 2031-11-27 04:00 | 15.81 | 20.7716 | N | 0
2025-11-27 | 06 | 2031-11-27 05:00 | 14.94 | 19.6286 | N | 0
2025-11-27 | 07 | 2031-11-27 06:00 | 14.45 | 18.9848 | N | 0
2025-11-27 | 08 | 2031-11-27 07:00 | 14.12 | 18.5513 | N | 0
2025-11-27 | 09 | 2031-11-27 08:00 | 14.16 | 18.6038 | N | 0
2025-11-27 | 10 | 2031-11-27 09:00 | 15.47 | 20.3249 | N | 0
2025-11-27 | 11 | 2031-11-27 10:00 | 17.49 | 22.9789 | N | 0
2025-11-27 | 12 | 2031-11-27 11:00 | 19.64 | 25.8036 | N | 0
2025-11-27 | 13 | 2031-11-27 12:00 | 20.03 | 26.316 | N | 0
2025-11-27 | 14 | 2031-11-27 13:00 | 20.5 | 26.9335 | N | 0
2025-11-27 | 15 | 2031-11-27 14:00 | 20.86 | 27.4065 | N | 0
2025-11-27 | 16 | 2031-11-27 15:00 | 20.72 | 27.2226 | N | 0
2025-11-27 | 17 | 2031-11-27 16:00 | 20.75 | 27.262 | N | 0
2025-11-27 | 18 | 2031-11-27 17:00 | 20.67 | 27.1569 | N | 0
2025-11-27 | 19 | 2031-11-27 18:00 | 21.01 | 27.6036 | N | 0
2025-11-27 | 20 | 2031-11-27 19:00 | 21.72 | 28.5364 | N | 0
2025-11-27 | 21 | 2031-11-27 20:00 | 23.82 | 31.2954 | N | 0
2025-11-27 | 22 | 2031-11-27 21:00 | 24.05 | 31.5976 | N | 0
2025-11-27 | 23 | 2031-11-27 22:00 | 23.51 | 30.8881 | N | 0
2025-11-28 | 00 | 2031-11-27 23:00 | 22.82 | 29.9816 | N | 0
2025-11-28 | 01 | 2031-11-28 | 22.74 | 29.8765 | N | 0
2025-11-28 | 02 | 2031-11-28 01:00 | 21.8 | 28.6415 | N | 0
2025-11-28 | 03 | 2031-11-28 02:00 | 20.14 | 26.4605 | N | 0
2025-11-28 | 04 | 2031-11-28 03:00 | 17.84 | 23.4387 | N | 0
2025-11-28 | 05 | 2031-11-28 04:00 | 16.46 | 21.6256 | N | 0
2025-11-28 | 06 | 2031-11-28 05:00 | 15.48 | 20.3381 | N | 0
2025-11-28 | 07 | 2031-11-28 06:00 | 15.02 | 19.7337 | N | 0
2025-11-28 | 08 | 2031-11-28 07:00 | 14.56 | 19.1294 | N | 0
2025-11-28 | 09 | 2031-11-28 08:00 | 14.74 | 19.3659 | N | 0
2025-11-28 | 10 | 2031-11-28 09:00 | 15.65 | 20.5614 | N | 0
2025-11-28 | 11 | 2031-11-28 10:00 | 18.49 | 24.2927 | N | 0
2025-11-28 | 12 | 2031-11-28 11:00 | 19.57 | 25.7116 | N | 0
2025-11-28 | 13 | 2031-11-28 12:00 | 20.52 | 26.9598 | N | 0
2025-11-28 | 14 | 2031-11-28 13:00 | 20.79 | 27.3145 | N | 0
2025-11-28 | 15 | 2031-11-28 14:00 | 21.1 | 27.7218 | N | 0
2025-11-28 | 16 | 2031-11-28 15:00 | 21.86 | 28.7203 | N | 0
2025-11-28 | 17 | 2031-11-28 16:00 | 22.01 | 28.9174 | N | 0
2025-11-28 | 18 | 2031-11-28 17:00 | 21.89 | 28.7597 | N | 0
2025-11-28 | 19 | 2031-11-28 18:00 | 21.37 | 28.0765 | N | 0
2025-11-28 | 20 | 2031-11-28 19:00 | 21.6 | 28.3787 | N | 0
2025-11-28 | 21 | 2031-11-28 20:00 | 23.31 | 30.6254 | N | 0
2025-11-28 | 22 | 2031-11-28 21:00 | 23.92 | 31.4268 | N | 0
2025-11-28 | 23 | 2031-11-28 22:00 | 23.56 | 30.9538 | N | 0
2025-11-29 | 00 | 2031-11-28 23:00 | 22.74 | 29.8765 | N | 0
2025-11-29 | 01 | 2031-11-29 | 22.17 | 29.1276 | N | 0
2025-11-29 | 02 | 2031-11-29 01:00 | 21.65 | 28.4444 | N | 0
2025-11-29 | 03 | 2031-11-29 02:00 | 19.96 | 26.224 | N | 0
2025-11-29 | 04 | 2031-11-29 03:00 | 18.57 | 24.3978 | N | 0
2025-11-29 | 05 | 2031-11-29 04:00 | 16.93 | 22.2431 | N | 0
2025-11-29 | 06 | 2031-11-29 05:00 | 15.81 | 20.7716 | N | 0
2025-11-29 | 07 | 2031-11-29 06:00 | 14.99 | 19.6943 | N | 0
2025-11-29 | 08 | 2031-11-29 07:00 | 14.59 | 19.1688 | N | 0
2025-11-29 | 09 | 2031-11-29 08:00 | 14.6 | 19.1819 | N | 0
2025-11-29 | 10 | 2031-11-29 09:00 | 14.99 | 19.6943 | N | 0
2025-11-29 | 11 | 2031-11-29 10:00 | 15.95 | 20.9556 | N | 0
2025-11-29 | 12 | 2031-11-29 11:00 | 17.44 | 22.9132 | N | 0
2025-11-29 | 13 | 2031-11-29 12:00 | 18.54 | 24.3584 | N | 0
2025-11-29 | 14 | 2031-11-29 13:00 | 19.36 | 25.4357 | N | 0
2025-11-29 | 15 | 2031-11-29 14:00 | 19.75 | 25.9481 | N | 0
2025-11-29 | 16 | 2031-11-29 15:00 | 19.8 | 26.0138 | N | 0
2025-11-29 | 17 | 2031-11-29 16:00 | 20.2 | 26.5394 | N | 0
2025-11-29 | 18 | 2031-11-29 17:00 | 20.16 | 26.4868 | N | 0
2025-11-29 | 19 | 2031-11-29 18:00 | 20.14 | 26.4605 | N | 0
2025-11-29 | 20 | 2031-11-29 19:00 | 20.9 | 27.459 | N | 0
2025-11-29 | 21 | 2031-11-29 20:00 | 22.35 | 29.3641 | N | 0
2025-11-29 | 22 | 2031-11-29 21:00 | 23.22 | 30.5071 | N | 0
2025-11-29 | 23 | 2031-11-29 22:00 | 22.52 | 29.5874 | N | 0
2025-11-30 | 00 | 2031-11-29 23:00 | 21.69 | 28.497 | N | 0
2025-11-30 | 01 | 2031-11-30 | 21.05 | 27.6561 | N | 0
2025-11-30 | 02 | 2031-11-30 01:00 | 20.52 | 26.9598 | N | 0
2025-11-30 | 03 | 2031-11-30 02:00 | 19.33 | 25.3963 | N | 0
2025-11-30 | 04 | 2031-11-30 03:00 | 17.86 | 23.465 | N | 0
2025-11-30 | 05 | 2031-11-30 04:00 | 16.35 | 21.4811 | N | 0
2025-11-30 | 06 | 2031-11-30 05:00 | 15.16 | 19.9177 | N | 0
2025-11-30 | 07 | 2031-11-30 06:00 | 14.53 | 19.0899 | N | 0
2025-11-30 | 08 | 2031-11-30 07:00 | 14.21 | 18.6695 | N | 0
2025-11-30 | 09 | 2031-11-30 08:00 | 14.12 | 18.5513 | N | 0
2025-11-30 | 10 | 2031-11-30 09:00 | 14.34 | 18.8403 | N | 0
2025-11-30 | 11 | 2031-11-30 10:00 | 15.22 | 19.9965 | N | 0
2025-11-30 | 12 | 2031-11-30 11:00 | 16.43 | 21.5862 | N | 0
2025-11-30 | 13 | 2031-11-30 12:00 | 17.69 | 23.2416 | N | 0
2025-11-30 | 14 | 2031-11-30 13:00 | 19.1 | 25.0941 | N | 0
2025-11-30 | 15 | 2031-11-30 14:00 | 20.24 | 26.5919 | N | 0
2025-11-30 | 16 | 2031-11-30 15:00 | 20.81 | 27.3408 | N | 0
2025-11-30 | 17 | 2031-11-30 16:00 | 21.61 | 28.3919 | N | 0
2025-11-30 | 18 | 2031-11-30 17:00 | 21.53 | 28.2868 | N | 0
2025-11-30 | 19 | 2031-11-30 18:00 | 22.04 | 28.9568 | N | 0
2025-11-30 | 20 | 2031-11-30 19:00 | 22.47 | 29.5218 | N | 0
2025-11-30 | 21 | 2031-11-30 20:00 | 24.57 | 32.2808 | N | 0
2025-11-30 | 22 | 2031-11-30 21:00 | 25.07 | 32.9377 | N | 0
2025-11-30 | 23 | 2031-11-30 22:00 | 24.59 | 32.3071 | N | 0
2026-12-01 | 00 | 2031-11-30 23:00 | 23.46 | 30.8224 | N | 0
2026-12-01 | 01 | 2031-12-01 | 22.57 | 29.6531 | N | 0
2026-12-01 | 02 | 2031-12-01 01:00 | 21.36 | 28.0634 | N | 0
2026-12-01 | 03 | 2031-12-01 02:00 | 19.89 | 26.1321 | N | 0
2026-12-01 | 04 | 2031-12-01 03:00 | 17.69 | 23.2416 | N | 0
2026-12-01 | 05 | 2031-12-01 04:00 | 16.25 | 21.3497 | N | 0
2026-12-01 | 06 | 2031-12-01 05:00 | 15.26 | 20.049 | N | 0
2026-12-01 | 07 | 2031-12-01 06:00 | 14.6 | 19.1819 | N | 0
2026-12-01 | 08 | 2031-12-01 07:00 | 14.47 | 19.0111 | N | 0
2026-12-01 | 09 | 2031-12-01 08:00 | 14.68 | 19.287 | N | 0
2026-12-01 | 10 | 2031-12-01 09:00 | 16.23 | 21.3235 | N | 0
2026-12-01 | 11 | 2031-12-01 10:00 | 18.57 | 24.3978 | N | 0
2026-12-01 | 12 | 2031-12-01 11:00 | 20.44 | 26.8547 | N | 0
2026-12-01 | 13 | 2031-12-01 12:00 | 20.65 | 27.1306 | N | 0
2026-12-01 | 14 | 2031-12-01 13:00 | 20.3 | 26.6707 | N | 0
2026-12-01 | 15 | 2031-12-01 14:00 | 20.42 | 26.8284 | N | 0
2026-12-01 | 16 | 2031-12-01 15:00 | 20.77 | 27.2882 | N | 0
2026-12-01 | 17 | 2031-12-01 16:00 | 20.86 | 27.4065 | N | 0
2026-12-01 | 18 | 2031-12-01 17:00 | 20.89 | 27.4459 | N | 0
2026-12-01 | 19 | 2031-12-01 18:00 | 20.97 | 27.551 | N | 0
2026-12-01 | 20 | 2031-12-01 19:00 | 21.7 | 28.5101 | N | 0
2026-12-01 | 21 | 2031-12-01 20:00 | 24.14 | 31.7159 | N | 0
2026-12-01 | 22 | 2031-12-01 21:00 | 25.31 | 33.253 | N | 0
2026-12-01 | 23 | 2031-12-01 22:00 | 24.58 | 32.2939 | N | 0
2026-12-02 | 00 | 2031-12-01 23:00 | 23.94 | 31.4531 | N | 0
2026-12-02 | 01 | 2031-12-02 | 23.56 | 30.9538 | N | 0
2026-12-02 | 02 | 2031-12-02 01:00 | 22.39 | 29.4166 | N | 0
2026-12-02 | 03 | 2031-12-02 02:00 | 20.74 | 27.2488 | N | 0
2026-12-02 | 04 | 2031-12-02 03:00 | 18.91 | 24.8445 | N | 0
2026-12-02 | 05 | 2031-12-02 04:00 | 17.15 | 22.5322 | N | 0
2026-12-02 | 06 | 2031-12-02 05:00 | 16.04 | 21.0738 | N | 0
2026-12-02 | 07 | 2031-12-02 06:00 | 15.44 | 20.2855 | N | 0
2026-12-02 | 08 | 2031-12-02 07:00 | 15.08 | 19.8126 | N | 0
2026-12-02 | 09 | 2031-12-02 08:00 | 15.05 | 19.7731 | N | 0
2026-12-02 | 10 | 2031-12-02 09:00 | 16.01 | 21.0344 | N | 0
2026-12-02 | 11 | 2031-12-02 10:00 | 18.32 | 24.0694 | N | 0
2026-12-02 | 12 | 2031-12-02 11:00 | 20.13 | 26.4474 | N | 0
2026-12-02 | 13 | 2031-12-02 12:00 | 20.62 | 27.0912 | N | 0
2026-12-02 | 14 | 2031-12-02 13:00 | 20.7 | 27.1963 | N | 0
2026-12-02 | 15 | 2031-12-02 14:00 | 20.77 | 27.2882 | N | 0
2026-12-02 | 16 | 2031-12-02 15:00 | 20.4 | 26.8021 | N | 0
2026-12-02 | 17 | 2031-12-02 16:00 | 20.21 | 26.5525 | N | 0
2026-12-02 | 18 | 2031-12-02 17:00 | 20.2 | 26.5394 | N | 0
2026-12-02 | 19 | 2031-12-02 18:00 | 20.14 | 26.4605 | N | 0
2026-12-02 | 20 | 2031-12-02 19:00 | 21.19 | 27.8401 | N | 0
2026-12-02 | 21 | 2031-12-02 20:00 | 23.5 | 30.875 | N | 0
2026-12-02 | 22 | 2031-12-02 21:00 | 24.81 | 32.5961 | N | 0
2026-12-02 | 23 | 2031-12-02 22:00 | 24.23 | 31.8341 | N | 0
2026-12-03 | 00 | 2031-12-02 23:00 | 23.83 | 31.3086 | N | 0
2026-12-03 | 01 | 2031-12-03 | 23.42 | 30.7699 | N | 0
2026-12-03 | 02 | 2031-12-03 01:00 | 22.46 | 29.5086 | N | 0
2026-12-03 | 03 | 2031-12-03 02:00 | 20.73 | 27.2357 | N | 0
2026-12-03 | 04 | 2031-12-03 03:00 | 18.99 | 24.9496 | N | 0
2026-12-03 | 05 | 2031-12-03 04:00 | 17.41 | 22.8738 | N | 0
2026-12-03 | 06 | 2031-12-03 05:00 | 16.27 | 21.376 | N | 0
2026-12-03 | 07 | 2031-12-03 06:00 | 15.88 | 20.8636 | N | 0
2026-12-03 | 08 | 2031-12-03 07:00 | 15.73 | 20.6665 | N | 0
2026-12-03 | 09 | 2031-12-03 08:00 | 15.91 | 20.903 | N | 0
2026-12-03 | 10 | 2031-12-03 09:00 | 17.19 | 22.5847 | N | 0
2026-12-03 | 11 | 2031-12-03 10:00 | 19.48 | 25.5934 | N | 0
2026-12-03 | 12 | 2031-12-03 11:00 | 21.37 | 28.0765 | N | 0
2026-12-03 | 13 | 2031-12-03 12:00 | 21.67 | 28.4707 | N | 0
2026-12-03 | 14 | 2031-12-03 13:00 | 21.85 | 28.7072 | N | 0
2026-12-03 | 15 | 2031-12-03 14:00 | 21.8 | 28.6415 | N | 0
2026-12-03 | 16 | 2031-12-03 15:00 | 21.86 | 28.7203 | N | 0
2026-12-03 | 17 | 2031-12-03 16:00 | 22.39 | 29.4166 | N | 0
2026-12-03 | 18 | 2031-12-03 17:00 | 21.88 | 28.7466 | N | 0
2026-12-03 | 19 | 2031-12-03 18:00 | 22.02 | 28.9305 | N | 0
2026-12-03 | 20 | 2031-12-03 19:00 | 22.71 | 29.8371 | N | 0
2026-12-03 | 21 | 2031-12-03 20:00 | 24.52 | 32.2151 | N | 0
2026-12-03 | 22 | 2031-12-03 21:00 | 25.01 | 32.8589 | N | 0
2026-12-03 | 23 | 2031-12-03 22:00 | 24.52 | 32.2151 | N | 0
2026-12-04 | 00 | 2031-12-03 23:00 | 23.77 | 31.2297 | N | 0
2026-12-04 | 01 | 2031-12-04 | 23.25 | 30.5465 | N | 0
2026-12-04 | 02 | 2031-12-04 01:00 | 22.47 | 29.5218 | N | 0
2026-12-04 | 03 | 2031-12-04 02:00 | 20.82 | 27.3539 | N | 0
2026-12-04 | 04 | 2031-12-04 03:00 | 18.99 | 24.9496 | N | 0
2026-12-04 | 05 | 2031-12-04 04:00 | 17.03 | 22.3745 | N | 0
2026-12-04 | 06 | 2031-12-04 05:00 | 15.94 | 20.9424 | N | 0
2026-12-04 | 07 | 2031-12-04 06:00 | 15.31 | 20.1147 | N | 0
2026-12-04 | 08 | 2031-12-04 07:00 | 15.03 | 19.7469 | N | 0
2026-12-04 | 09 | 2031-12-04 08:00 | 15.34 | 20.1541 | N | 0
2026-12-04 | 10 | 2031-12-04 09:00 | 16.49 | 21.6651 | N | 0
2026-12-04 | 11 | 2031-12-04 10:00 | 18.95 | 24.8971 | N | 0
2026-12-04 | 12 | 2031-12-04 11:00 | 21 | 27.5904 | N | 0
2026-12-04 | 13 | 2031-12-04 12:00 | 21.12 | 27.7481 | N | 0
2026-12-04 | 14 | 2031-12-04 13:00 | 21.28 | 27.9583 | N | 0
2026-12-04 | 15 | 2031-12-04 14:00 | 21.4 | 28.116 | N | 0
2026-12-04 | 16 | 2031-12-04 15:00 | 21.86 | 28.7203 | N | 0
2026-12-04 | 17 | 2031-12-04 16:00 | 22.15 | 29.1013 | N | 0
2026-12-04 | 18 | 2031-12-04 17:00 | 22.38 | 29.4035 | N | 0
2026-12-04 | 19 | 2031-12-04 18:00 | 22.33 | 29.3378 | N | 0
2026-12-04 | 20 | 2031-12-04 19:00 | 23.24 | 30.5334 | N | 0
2026-12-04 | 21 | 2031-12-04 20:00 | 25.31 | 33.253 | N | 0
2026-12-04 | 22 | 2031-12-04 21:00 | 26.44 | 34.7377 | N | 0
2026-12-04 | 23 | 2031-12-04 22:00 | 25.7 | 33.7654 | N | 0
2026-12-05 | 00 | 2031-12-04 23:00 | 25.31 | 33.253 | N | 0
2026-12-05 | 01 | 2031-12-05 | 25.01 | 32.8589 | N | 0
2026-12-05 | 02 | 2031-12-05 01:00 | 24.49 | 32.1757 | N | 0
2026-12-05 | 03 | 2031-12-05 02:00 | 22.62 | 29.7188 | N | 0
2026-12-05 | 04 | 2031-12-05 03:00 | 20.62 | 27.0912 | N | 0
2026-12-05 | 05 | 2031-12-05 04:00 | 19.36 | 25.4357 | N | 0
2026-12-05 | 06 | 2031-12-05 05:00 | 18.17 | 23.8723 | N | 0
2026-12-05 | 07 | 2031-12-05 06:00 | 17.71 | 23.2679 | N | 0
2026-12-05 | 08 | 2031-12-05 07:00 | 17.25 | 22.6636 | N | 0
2026-12-05 | 09 | 2031-12-05 08:00 | 17.32 | 22.7555 | N | 0
2026-12-05 | 10 | 2031-12-05 09:00 | 18.17 | 23.8723 | N | 0
2026-12-05 | 11 | 2031-12-05 10:00 | 20.68 | 27.17 | N | 0
2026-12-05 | 12 | 2031-12-05 11:00 | 22.2 | 29.167 | N | 0
2026-12-05 | 13 | 2031-12-05 12:00 | 22.65 | 29.7582 | N | 0
2026-12-05 | 14 | 2031-12-05 13:00 | 22.56 | 29.64 | N | 0
2026-12-05 | 15 | 2031-12-05 14:00 | 22.89 | 30.0736 | N | 0
2026-12-05 | 16 | 2031-12-05 15:00 | 23 | 30.2181 | N | 0
2026-12-05 | 17 | 2031-12-05 16:00 | 22.78 | 29.929 | N | 0
2026-12-05 | 18 | 2031-12-05 17:00 | 22.38 | 29.4035 | N | 0
2026-12-05 | 19 | 2031-12-05 18:00 | 22.18 | 29.1407 | N | 0
2026-12-05 | 20 | 2031-12-05 19:00 | 22.58 | 29.6663 | N | 0
2026-12-05 | 21 | 2031-12-05 20:00 | 24.13 | 31.7027 | N | 0
2026-12-05 | 22 | 2031-12-05 21:00 | 25.03 | 32.8852 | N | 0
2026-12-05 | 23 | 2031-12-05 22:00 | 24.18 | 31.7684 | N | 0
2026-12-06 | 00 | 2031-12-05 23:00 | 23.56 | 30.9538 | N | 0
2026-12-06 | 01 | 2031-12-06 | 23.01 | 30.2312 | N | 0
2026-12-06 | 02 | 2031-12-06 01:00 | 22.62 | 29.7188 | N | 0
2026-12-06 | 03 | 2031-12-06 02:00 | 20.91 | 27.4722 | N | 0
2026-12-06 | 04 | 2031-12-06 03:00 | 19.41 | 25.5014 | N | 0
2026-12-06 | 05 | 2031-12-06 04:00 | 17.9 | 23.5176 | N | 0
2026-12-06 | 06 | 2031-12-06 05:00 | 16.64 | 21.8621 | N | 0
2026-12-06 | 07 | 2031-12-06 06:00 | 15.87 | 20.8505 | N | 0
2026-12-06 | 08 | 2031-12-06 07:00 | 15.21 | 19.9834 | N | 0
2026-12-06 | 09 | 2031-12-06 08:00 | 15.01 | 19.7206 | N | 0
2026-12-06 | 10 | 2031-12-06 09:00 | 15.41 | 20.2461 | N | 0
2026-12-06 | 11 | 2031-12-06 10:00 | 16.29 | 21.4023 | N | 0
2026-12-06 | 12 | 2031-12-06 11:00 | 17.46 | 22.9395 | N | 0
2026-12-06 | 13 | 2031-12-06 12:00 | 19.04 | 25.0153 | N | 0
2026-12-06 | 14 | 2031-12-06 13:00 | 20.36 | 26.7496 | N | 0
2026-12-06 | 15 | 2031-12-06 14:00 | 21 | 27.5904 | N | 0
2026-12-06 | 16 | 2031-12-06 15:00 | 21.64 | 28.4313 | N | 0
2026-12-06 | 17 | 2031-12-06 16:00 | 21.77 | 28.6021 | N | 0
2026-12-06 | 18 | 2031-12-06 17:00 | 21.9 | 28.7729 | N | 0
2026-12-06 | 19 | 2031-12-06 18:00 | 21.66 | 28.4576 | N | 0
2026-12-06 | 20 | 2031-12-06 19:00 | 22.14 | 29.0882 | N | 0
2026-12-06 | 21 | 2031-12-06 20:00 | 23.29 | 30.5991 | N | 0
2026-12-06 | 22 | 2031-12-06 21:00 | 23.95 | 31.4662 | N | 0
2026-12-06 | 23 | 2031-12-06 22:00 | 23.42 | 30.7699 | N | 0
2026-12-07 | 00 | 2031-12-06 23:00 | 22.63 | 29.732 | N | 0
2026-12-07 | 01 | 2031-12-07 | 21.7 | 28.5101 | N | 0
2026-12-07 | 02 | 2031-12-07 01:00 | 20.95 | 27.5247 | N | 0
2026-12-07 | 03 | 2031-12-07 02:00 | 19.73 | 25.9219 | N | 0
2026-12-07 | 04 | 2031-12-07 03:00 | 18.29 | 24.0299 | N | 0
2026-12-07 | 05 | 2031-12-07 04:00 | 16.83 | 22.1118 | N | 0
2026-12-07 | 06 | 2031-12-07 05:00 | 15.77 | 20.7191 | N | 0
2026-12-07 | 07 | 2031-12-07 06:00 | 15.14 | 19.8914 | N | 0
2026-12-07 | 08 | 2031-12-07 07:00 | 14.71 | 19.3264 | N | 0
2026-12-07 | 09 | 2031-12-07 08:00 | 14.58 | 19.1556 | N | 0
2026-12-07 | 10 | 2031-12-07 09:00 | 14.76 | 19.3921 | N | 0
2026-12-07 | 11 | 2031-12-07 10:00 | 15.54 | 20.4169 | N | 0
2026-12-07 | 12 | 2031-12-07 11:00 | 16.62 | 21.8359 | N | 0
2026-12-07 | 13 | 2031-12-07 12:00 | 18.18 | 23.8854 | N | 0
2026-12-07 | 14 | 2031-12-07 13:00 | 19.47 | 25.5803 | N | 0
2026-12-07 | 15 | 2031-12-07 14:00 | 20.26 | 26.6182 | N | 0
2026-12-07 | 16 | 2031-12-07 15:00 | 21.38 | 28.0897 | N | 0
2026-12-07 | 17 | 2031-12-07 16:00 | 21.48 | 28.2211 | N | 0
2026-12-07 | 18 | 2031-12-07 17:00 | 21.82 | 28.6678 | N | 0
2026-12-07 | 19 | 2031-12-07 18:00 | 22.12 | 29.0619 | N | 0
2026-12-07 | 20 | 2031-12-07 19:00 | 22.69 | 29.8108 | N | 0
2026-12-07 | 21 | 2031-12-07 20:00 | 25.31 | 33.253 | N | 0
2026-12-07 | 22 | 2031-12-07 21:00 | 26.79 | 35.1975 | N | 0
2026-12-07 | 23 | 2031-12-07 22:00 | 25.92 | 34.0545 | N | 0
2026-12-08 | 00 | 2031-12-07 23:00 | 24.85 | 32.6487 | N | 0
2026-12-08 | 01 | 2031-12-08 | 24.53 | 32.2282 | N | 0
2026-12-08 | 02 | 2031-12-08 01:00 | 23.05 | 30.2838 | N | 0
2026-12-08 | 03 | 2031-12-08 02:00 | 21.15 | 27.7875 | N | 0
2026-12-08 | 04 | 2031-12-08 03:00 | 19.23 | 25.2649 | N | 0
2026-12-08 | 05 | 2031-12-08 04:00 | 17.69 | 23.2416 | N | 0
2026-12-08 | 06 | 2031-12-08 05:00 | 16.77 | 22.0329 | N | 0
2026-12-08 | 07 | 2031-12-08 06:00 | 16.33 | 21.4548 | N | 0
2026-12-08 | 08 | 2031-12-08 07:00 | 16.32 | 21.4417 | N | 0
2026-12-08 | 09 | 2031-12-08 08:00 | 16.65 | 21.8753 | N | 0
2026-12-08 | 10 | 2031-12-08 09:00 | 17.97 | 23.6095 | N | 0
2026-12-08 | 11 | 2031-12-08 10:00 | 20.08 | 26.3817 | N | 0
2026-12-08 | 12 | 2031-12-08 11:00 | 21.82 | 28.6678 | N | 0
2026-12-08 | 13 | 2031-12-08 12:00 | 22.42 | 29.4561 | N | 0
2026-12-08 | 14 | 2031-12-08 13:00 | 22.34 | 29.351 | N | 0
2026-12-08 | 15 | 2031-12-08 14:00 | 22.27 | 29.259 | N | 0
2026-12-08 | 16 | 2031-12-08 15:00 | 22.26 | 29.2459 | N | 0
2026-12-08 | 17 | 2031-12-08 16:00 | 21.94 | 28.8254 | N | 0
2026-12-08 | 18 | 2031-12-08 17:00 | 22.06 | 28.9831 | N | 0
2026-12-08 | 19 | 2031-12-08 18:00 | 21.91 | 28.786 | N | 0
2026-12-08 | 20 | 2031-12-08 19:00 | 22.5 | 29.5612 | N | 0
2026-12-08 | 21 | 2031-12-08 20:00 | 25.54 | 33.5552 | N | 0
2026-12-08 | 22 | 2031-12-08 21:00 | 26.81 | 35.2238 | N | 0
2026-12-08 | 23 | 2031-12-08 22:00 | 26.22 | 34.4486 | N | 0
2026-12-09 | 00 | 2031-12-08 23:00 | 25.5 | 33.5027 | N | 0
2026-12-09 | 01 | 2031-12-09 | 25.08 | 32.9509 | N | 0
2026-12-09 | 02 | 2031-12-09 01:00 | 24.31 | 31.9392 | N | 0
2026-12-09 | 03 | 2031-12-09 02:00 | 22.8 | 29.9553 | N | 0
2026-12-09 | 04 | 2031-12-09 03:00 | 20.42 | 26.8284 | N | 0
2026-12-09 | 05 | 2031-12-09 04:00 | 18.83 | 24.7394 | N | 0
2026-12-09 | 06 | 2031-12-09 05:00 | 17.71 | 23.2679 | N | 0
2026-12-09 | 07 | 2031-12-09 06:00 | 17.25 | 22.6636 | N | 0
2026-12-09 | 08 | 2031-12-09 07:00 | 16.79 | 22.0592 | N | 0
2026-12-09 | 09 | 2031-12-09 08:00 | 16.64 | 21.8621 | N | 0
2026-12-09 | 10 | 2031-12-09 09:00 | 17.74 | 23.3073 | N | 0
2026-12-09 | 11 | 2031-12-09 10:00 | 20 | 26.2766 | N | 0
2026-12-09 | 12 | 2031-12-09 11:00 | 21.35 | 28.0503 | N | 0
2026-12-09 | 13 | 2031-12-09 12:00 | 21.83 | 28.6809 | N | 0
2026-12-09 | 14 | 2031-12-09 13:00 | 22.39 | 29.4166 | N | 0
2026-12-09 | 15 | 2031-12-09 14:00 | 22.51 | 29.5743 | N | 0
2026-12-09 | 16 | 2031-12-09 15:00 | 22.34 | 29.351 | N | 0
2026-12-09 | 17 | 2031-12-09 16:00 | 22.78 | 29.929 | N | 0
2026-12-09 | 18 | 2031-12-09 17:00 | 23.07 | 30.3101 | N | 0
2026-12-09 | 19 | 2031-12-09 18:00 | 23.14 | 30.402 | N | 0
2026-12-09 | 20 | 2031-12-09 19:00 | 23.38 | 30.7173 | N | 0
2026-12-09 | 21 | 2031-12-09 20:00 | 25.98 | 34.1333 | N | 0
2026-12-09 | 22 | 2031-12-09 21:00 | 26.75 | 35.1449 | N | 0
2026-12-09 | 23 | 2031-12-09 22:00 | 25.67 | 33.726 | N | 0
2026-12-10 | 00 | 2031-12-09 23:00 | 25.3 | 33.2399 | N | 0
2026-12-10 | 01 | 2031-12-10 | 24.19 | 31.7815 | N | 0
2026-12-10 | 02 | 2031-12-10 01:00 | 23.01 | 30.2312 | N | 0
2026-12-10 | 03 | 2031-12-10 02:00 | 21.22 | 27.8795 | N | 0
2026-12-10 | 04 | 2031-12-10 03:00 | 18.87 | 24.792 | N | 0
2026-12-10 | 05 | 2031-12-10 04:00 | 17.26 | 22.6767 | N | 0
2026-12-10 | 06 | 2031-12-10 05:00 | 15.82 | 20.7848 | N | 0
2026-12-10 | 07 | 2031-12-10 06:00 | 15.34 | 20.1541 | N | 0
2026-12-10 | 08 | 2031-12-10 07:00 | 14.94 | 19.6286 | N | 0
2026-12-10 | 09 | 2031-12-10 08:00 | 15 | 19.7074 | N | 0
2026-12-10 | 10 | 2031-12-10 09:00 | 16.3 | 21.4154 | N | 0
2026-12-10 | 11 | 2031-12-10 10:00 | 18.5 | 24.3059 | N | 0
2026-12-10 | 12 | 2031-12-10 11:00 | 19.69 | 25.8693 | N | 0
2026-12-10 | 13 | 2031-12-10 12:00 | 20.4 | 26.8021 | N | 0
2026-12-10 | 14 | 2031-12-10 13:00 | 20.97 | 27.551 | N | 0
2026-12-10 | 15 | 2031-12-10 14:00 | 21.82 | 28.6678 | N | 0
2026-12-10 | 16 | 2031-12-10 15:00 | 22.49 | 29.548 | N | 0
2026-12-10 | 17 | 2031-12-10 16:00 | 22.34 | 29.351 | N | 0
2026-12-10 | 18 | 2031-12-10 17:00 | 22.34 | 29.351 | N | 0
2026-12-10 | 19 | 2031-12-10 18:00 | 22.16 | 29.1145 | N | 0
2026-12-10 | 20 | 2031-12-10 19:00 | 22.24 | 29.2196 | N | 0
2026-12-10 | 21 | 2031-12-10 20:00 | 24.31 | 31.9392 | N | 0
2026-12-10 | 22 | 2031-12-10 21:00 | 25.44 | 33.4238 | N | 0
2026-12-10 | 23 | 2031-12-10 22:00 | 24.77 | 32.5436 | N | 0
2026-12-11 | 00 | 2031-12-10 23:00 | 24.12 | 31.6896 | N | 0
2026-12-11 | 01 | 2031-12-11 | 23.94 | 31.4531 | N | 0
2026-12-11 | 02 | 2031-12-11 01:00 | 22.99 | 30.2049 | N | 0
2026-12-11 | 03 | 2031-12-11 02:00 | 21.19 | 27.8401 | N | 0
2026-12-11 | 04 | 2031-12-11 03:00 | 19.34 | 25.4095 | N | 0
2026-12-11 | 05 | 2031-12-11 04:00 | 18.08 | 23.754 | N | 0
2026-12-11 | 06 | 2031-12-11 05:00 | 17.01 | 22.3482 | N | 0
2026-12-11 | 07 | 2031-12-11 06:00 | 16.25 | 21.3497 | N | 0
2026-12-11 | 08 | 2031-12-11 07:00 | 16.09 | 21.1395 | N | 0
2026-12-11 | 09 | 2031-12-11 08:00 | 16.77 | 22.0329 | N | 0
2026-12-11 | 10 | 2031-12-11 09:00 | 17.73 | 23.2942 | N | 0
2026-12-11 | 11 | 2031-12-11 10:00 | 20.2 | 26.5394 | N | 0
2026-12-11 | 12 | 2031-12-11 11:00 | 21.83 | 28.6809 | N | 0
2026-12-11 | 13 | 2031-12-11 12:00 | 22.36 | 29.3772 | N | 0
2026-12-11 | 14 | 2031-12-11 13:00 | 22.37 | 29.3904 | N | 0
2026-12-11 | 15 | 2031-12-11 14:00 | 22.73 | 29.8634 | N | 0
2026-12-11 | 16 | 2031-12-11 15:00 | 22.74 | 29.8765 | N | 0
2026-12-11 | 17 | 2031-12-11 16:00 | 22.42 | 29.4561 | N | 0
2026-12-11 | 18 | 2031-12-11 17:00 | 22.86 | 30.0341 | N | 0
2026-12-11 | 19 | 2031-12-11 18:00 | 22.52 | 29.5874 | N | 0
2026-12-11 | 20 | 2031-12-11 19:00 | 23.29 | 30.5991 | N | 0
2026-12-11 | 21 | 2031-12-11 20:00 | 25.2 | 33.1085 | N | 0
2026-12-11 | 22 | 2031-12-11 21:00 | 26.71 | 35.0924 | N | 0
2026-12-11 | 23 | 2031-12-11 22:00 | 26.17 | 34.3829 | N | 0
2026-12-12 | 00 | 2031-12-11 23:00 | 25.96 | 34.107 | N | 0
2026-12-12 | 01 | 2031-12-12 | 25.47 | 33.4632 | N | 0
2026-12-12 | 02 | 2031-12-12 01:00 | 24.85 | 32.6487 | N | 0
2026-12-12 | 03 | 2031-12-12 02:00 | 23 | 30.2181 | N | 0
2026-12-12 | 04 | 2031-12-12 03:00 | 21.14 | 27.7744 | N | 0
2026-12-12 | 05 | 2031-12-12 04:00 | 19.4 | 25.4883 | N | 0
2026-12-12 | 06 | 2031-12-12 05:00 | 18.36 | 24.1219 | N | 0
2026-12-12 | 07 | 2031-12-12 06:00 | 17.64 | 23.176 | N | 0
2026-12-12 | 08 | 2031-12-12 07:00 | 17.04 | 22.3877 | N | 0
2026-12-12 | 09 | 2031-12-12 08:00 | 17.23 | 22.6373 | N | 0
2026-12-12 | 10 | 2031-12-12 09:00 | 18.14 | 23.8329 | N | 0
2026-12-12 | 11 | 2031-12-12 10:00 | 20.6 | 27.0649 | N | 0
2026-12-12 | 12 | 2031-12-12 11:00 | 22.21 | 29.1802 | N | 0
2026-12-12 | 13 | 2031-12-12 12:00 | 22.61 | 29.7057 | N | 0
2026-12-12 | 14 | 2031-12-12 13:00 | 23.14 | 30.402 | N | 0
2026-12-12 | 15 | 2031-12-12 14:00 | 22.87 | 30.0473 | N | 0
2026-12-12 | 16 | 2031-12-12 15:00 | 22.84 | 30.0079 | N | 0
2026-12-12 | 17 | 2031-12-12 16:00 | 22.96 | 30.1655 | N | 0
2026-12-12 | 18 | 2031-12-12 17:00 | 23.12 | 30.3757 | N | 0
2026-12-12 | 19 | 2031-12-12 18:00 | 22.74 | 29.8765 | N | 0
2026-12-12 | 20 | 2031-12-12 19:00 | 22.92 | 30.113 | N | 0
2026-12-12 | 21 | 2031-12-12 20:00 | 24.39 | 32.0443 | N | 0
2026-12-12 | 22 | 2031-12-12 21:00 | 24.88 | 32.6881 | N | 0
2026-12-12 | 23 | 2031-12-12 22:00 | 24.53 | 32.2282 | N | 0
2026-12-13 | 00 | 2031-12-12 23:00 | 23.79 | 31.256 | N | 0
2026-12-13 | 01 | 2031-12-13 | 23.34 | 30.6648 | N | 0
2026-12-13 | 02 | 2031-12-13 01:00 | 22.86 | 30.0341 | N | 0
2026-12-13 | 03 | 2031-12-13 02:00 | 21.57 | 28.3393 | N | 0
2026-12-13 | 04 | 2031-12-13 03:00 | 19.95 | 26.2109 | N | 0
2026-12-13 | 05 | 2031-12-13 04:00 | 18.08 | 23.754 | N | 0
2026-12-13 | 06 | 2031-12-13 05:00 | 17.04 | 22.3877 | N | 0
2026-12-13 | 07 | 2031-12-13 06:00 | 15.98 | 20.995 | N | 0
2026-12-13 | 08 | 2031-12-13 07:00 | 15.59 | 20.4826 | N | 0
2026-12-13 | 09 | 2031-12-13 08:00 | 15.27 | 20.0622 | N | 0
2026-12-13 | 10 | 2031-12-13 09:00 | 15.7 | 20.6271 | N | 0
2026-12-13 | 11 | 2031-12-13 10:00 | 16.57 | 21.7702 | N | 0
2026-12-13 | 12 | 2031-12-13 11:00 | 17.76 | 23.3336 | N | 0
2026-12-13 | 13 | 2031-12-13 12:00 | 19.12 | 25.1204 | N | 0
2026-12-13 | 14 | 2031-12-13 13:00 | 20.57 | 27.0255 | N | 0
2026-12-13 | 15 | 2031-12-13 14:00 | 21.26 | 27.932 | N | 0
2026-12-13 | 16 | 2031-12-13 15:00 | 21.72 | 28.5364 | N | 0
2026-12-13 | 17 | 2031-12-13 16:00 | 22.08 | 29.0094 | N | 0
2026-12-13 | 18 | 2031-12-13 17:00 | 21.42 | 28.1422 | N | 0
2026-12-13 | 19 | 2031-12-13 18:00 | 21.62 | 28.405 | N | 0
2026-12-13 | 20 | 2031-12-13 19:00 | 22.35 | 29.3641 | N | 0
2026-12-13 | 21 | 2031-12-13 20:00 | 24.27 | 31.8866 | N | 0
2026-12-13 | 22 | 2031-12-13 21:00 | 24.98 | 32.8195 | N | 0
2026-12-13 | 23 | 2031-12-13 22:00 | 24.59 | 32.3071 | N | 0
2026-12-14 | 00 | 2031-12-13 23:00 | 23.46 | 30.8224 | N | 0
2026-12-14 | 01 | 2031-12-14 | 22.9 | 30.0867 | N | 0
2026-12-14 | 02 | 2031-12-14 01:00 | 22.19 | 29.1539 | N | 0
2026-12-14 | 03 | 2031-12-14 02:00 | 21.09 | 27.7087 | N | 0
2026-12-14 | 04 | 2031-12-14 03:00 | 20.11 | 26.4211 | N | 0
2026-12-14 | 05 | 2031-12-14 04:00 | 18.78 | 24.6737 | N | 0
2026-12-14 | 06 | 2031-12-14 05:00 | 17.51 | 23.0052 | N | 0
2026-12-14 | 07 | 2031-12-14 06:00 | 16.76 | 22.0198 | N | 0
2026-12-14 | 08 | 2031-12-14 07:00 | 16.28 | 21.3891 | N | 0
2026-12-14 | 09 | 2031-12-14 08:00 | 16.32 | 21.4417 | N | 0
2026-12-14 | 10 | 2031-12-14 09:00 | 16.85 | 22.138 | N | 0
2026-12-14 | 11 | 2031-12-14 10:00 | 17.29 | 22.7161 | N | 0
2026-12-14 | 12 | 2031-12-14 11:00 | 18.76 | 24.6474 | N | 0
2026-12-14 | 13 | 2031-12-14 12:00 | 20.41 | 26.8153 | N | 0
2026-12-14 | 14 | 2031-12-14 13:00 | 21.22 | 27.8795 | N | 0
2026-12-14 | 15 | 2031-12-14 14:00 | 22.33 | 29.3378 | N | 0
2026-12-14 | 16 | 2031-12-14 15:00 | 22.65 | 29.7582 | N | 0
2026-12-14 | 17 | 2031-12-14 16:00 | 22.83 | 29.9947 | N | 0
2026-12-14 | 18 | 2031-12-14 17:00 | 23.08 | 30.3232 | N | 0
2026-12-14 | 19 | 2031-12-14 18:00 | 22.97 | 30.1787 | N | 0
2026-12-14 | 20 | 2031-12-14 19:00 | 24.07 | 31.6239 | N | 0
2026-12-14 | 21 | 2031-12-14 20:00 | 26.64 | 35.0004 | N | 0
2026-12-14 | 22 | 2031-12-14 21:00 | 27.91 | 36.669 | N | 0
2026-12-14 | 23 | 2031-12-14 22:00 | 27.68 | 36.3668 | N | 0
2026-12-15 | 00 | 2031-12-14 23:00 | 26.67 | 35.0398 | N | 0
2026-12-15 | 01 | 2031-12-15 | 25.88 | 34.0019 | N | 0
2026-12-15 | 02 | 2031-12-15 01:00 | 25.08 | 32.9509 | N | 0
2026-12-15 | 03 | 2031-12-15 02:00 | 22.67 | 29.7845 | N | 0
2026-12-15 | 04 | 2031-12-15 03:00 | 20.73 | 27.2357 | N | 0
2026-12-15 | 05 | 2031-12-15 04:00 | 19.04 | 25.0153 | N | 0
2026-12-15 | 06 | 2031-12-15 05:00 | 17.71 | 23.2679 | N | 0
2026-12-15 | 07 | 2031-12-15 06:00 | 17.2 | 22.5979 | N | 0
2026-12-15 | 08 | 2031-12-15 07:00 | 16.92 | 22.23 | N | 0
2026-12-15 | 09 | 2031-12-15 08:00 | 17.02 | 22.3614 | N | 0
2026-12-15 | 10 | 2031-12-15 09:00 | 17.98 | 23.6227 | N | 0
2026-12-15 | 11 | 2031-12-15 10:00 | 19.95 | 26.2109 | N | 0
2026-12-15 | 12 | 2031-12-15 11:00 | 22 | 28.9043 | N | 0
2026-12-15 | 13 | 2031-12-15 12:00 | 22.22 | 29.1933 | N | 0
2026-12-15 | 14 | 2031-12-15 13:00 | 22.77 | 29.9159 | N | 0
2026-12-15 | 15 | 2031-12-15 14:00 | 22.91 | 30.0998 | N | 0
2026-12-15 | 16 | 2031-12-15 15:00 | 23.49 | 30.8619 | N | 0
2026-12-15 | 17 | 2031-12-15 16:00 | 23.28 | 30.586 | N | 0
2026-12-15 | 18 | 2031-12-15 17:00 | 23.48 | 30.8487 | N | 0
2026-12-15 | 19 | 2031-12-15 18:00 | 23.47 | 30.8356 | N | 0
2026-12-15 | 20 | 2031-12-15 19:00 | 23.9 | 31.4005 | N | 0
2026-12-15 | 21 | 2031-12-15 20:00 | 25.95 | 34.0939 | N | 0
2026-12-15 | 22 | 2031-12-15 21:00 | 27.01 | 35.4865 | N | 0
2026-12-15 | 23 | 2031-12-15 22:00 | 26.72 | 35.1055 | N | 0
2026-12-16 | 00 | 2031-12-15 23:00 | 26.08 | 34.2647 | N | 0
2026-12-16 | 01 | 2031-12-16 | 25.13 | 33.0165 | N | 0
2026-12-16 | 02 | 2031-12-16 01:00 | 24.51 | 32.202 | N | 0
2026-12-16 | 03 | 2031-12-16 02:00 | 22.97 | 30.1787 | N | 0
2026-12-16 | 04 | 2031-12-16 03:00 | 19.96 | 26.224 | N | 0
2026-12-16 | 05 | 2031-12-16 04:00 | 18.24 | 23.9643 | N | 0
2026-12-16 | 06 | 2031-12-16 05:00 | 17.26 | 22.6767 | N | 0
2026-12-16 | 07 | 2031-12-16 06:00 | 16.63 | 21.849 | N | 0
2026-12-16 | 08 | 2031-12-16 07:00 | 16.29 | 21.4023 | N | 0
2026-12-16 | 09 | 2031-12-16 08:00 | 16.37 | 21.5074 | N | 0
2026-12-16 | 10 | 2031-12-16 09:00 | 17.32 | 22.7555 | N | 0
2026-12-16 | 11 | 2031-12-16 10:00 | 19.52 | 25.646 | N | 0
2026-12-16 | 12 | 2031-12-16 11:00 | 21.21 | 27.8663 | N | 0
2026-12-16 | 13 | 2031-12-16 12:00 | 21.96 | 28.8517 | N | 0
2026-12-16 | 14 | 2031-12-16 13:00 | 22.05 | 28.9699 | N | 0
2026-12-16 | 15 | 2031-12-16 14:00 | 22.43 | 29.4692 | N | 0
2026-12-16 | 16 | 2031-12-16 15:00 | 22.81 | 29.9685 | N | 0
2026-12-16 | 17 | 2031-12-16 16:00 | 22.92 | 30.113 | N | 0
2026-12-16 | 18 | 2031-12-16 17:00 | 23.1 | 30.3495 | N | 0
2026-12-16 | 19 | 2031-12-16 18:00 | 23.14 | 30.402 | N | 0
2026-12-16 | 20 | 2031-12-16 19:00 | 23.41 | 30.7568 | N | 0
2026-12-16 | 21 | 2031-12-16 20:00 | 25.32 | 33.2662 | N | 0
2026-12-16 | 22 | 2031-12-16 21:00 | 26.21 | 34.4355 | N | 0
2026-12-16 | 23 | 2031-12-16 22:00 | 25.65 | 33.6997 | N | 0
2026-12-17 | 00 | 2031-12-16 23:00 | 24.94 | 32.7669 | N | 0
2026-12-17 | 01 | 2031-12-17 | 24.21 | 31.8078 | N | 0
2026-12-17 | 02 | 2031-12-17 01:00 | 23.35 | 30.6779 | N | 0
2026-12-17 | 03 | 2031-12-17 02:00 | 21.63 | 28.4181 | N | 0
2026-12-17 | 04 | 2031-12-17 03:00 | 19.41 | 25.5014 | N | 0
2026-12-17 | 05 | 2031-12-17 04:00 | 17.35 | 22.7949 | N | 0
2026-12-17 | 06 | 2031-12-17 05:00 | 16.31 | 21.4286 | N | 0
2026-12-17 | 07 | 2031-12-17 06:00 | 15.81 | 20.7716 | N | 0
2026-12-17 | 08 | 2031-12-17 07:00 | 15.45 | 20.2987 | N | 0
2026-12-17 | 09 | 2031-12-17 08:00 | 15.42 | 20.2593 | N | 0
2026-12-17 | 10 | 2031-12-17 09:00 | 16.58 | 21.7833 | N | 0
2026-12-17 | 11 | 2031-12-17 10:00 | 18.65 | 24.5029 | N | 0
2026-12-17 | 12 | 2031-12-17 11:00 | 20.09 | 26.3948 | N | 0
2026-12-17 | 13 | 2031-12-17 12:00 | 20.32 | 26.697 | N | 0
2026-12-17 | 14 | 2031-12-17 13:00 | 20.69 | 27.1831 | N | 0
2026-12-17 | 15 | 2031-12-17 14:00 | 20.93 | 27.4985 | N | 0
2026-12-17 | 16 | 2031-12-17 15:00 | 21.15 | 27.7875 | N | 0
2026-12-17 | 17 | 2031-12-17 16:00 | 21.55 | 28.313 | N | 0
2026-12-17 | 18 | 2031-12-17 17:00 | 21.46 | 28.1948 | N | 0
2026-12-17 | 19 | 2031-12-17 18:00 | 21.32 | 28.0109 | N | 0
2026-12-17 | 20 | 2031-12-17 19:00 | 22.14 | 29.0882 | N | 0
2026-12-17 | 21 | 2031-12-17 20:00 | 23.74 | 31.1903 | N | 0
2026-12-17 | 22 | 2031-12-17 21:00 | 24.6 | 32.3202 | N | 0
2026-12-17 | 23 | 2031-12-17 22:00 | 24.26 | 31.8735 | N | 0
2026-12-18 | 00 | 2031-12-17 23:00 | 23.74 | 31.1903 | N | 0
2026-12-18 | 01 | 2031-12-18 | 23.09 | 30.3363 | N | 0
2026-12-18 | 02 | 2031-12-18 01:00 | 22.12 | 29.0619 | N | 0
2026-12-18 | 03 | 2031-12-18 02:00 | 20.79 | 27.3145 | N | 0
2026-12-18 | 04 | 2031-12-18 03:00 | 18.59 | 24.4241 | N | 0
2026-12-18 | 05 | 2031-12-18 04:00 | 16.92 | 22.23 | N | 0
2026-12-18 | 06 | 2031-12-18 05:00 | 16.05 | 21.087 | N | 0
2026-12-18 | 07 | 2031-12-18 06:00 | 15.35 | 20.1673 | N | 0
2026-12-18 | 08 | 2031-12-18 07:00 | 14.74 | 19.3659 | N | 0
2026-12-18 | 09 | 2031-12-18 08:00 | 14.93 | 19.6155 | N | 0
2026-12-18 | 10 | 2031-12-18 09:00 | 16.12 | 21.1789 | N | 0
2026-12-18 | 11 | 2031-12-18 10:00 | 18.03 | 23.6884 | N | 0
2026-12-18 | 12 | 2031-12-18 11:00 | 19.72 | 25.9087 | N | 0
2026-12-18 | 13 | 2031-12-18 12:00 | 20.05 | 26.3423 | N | 0
2026-12-18 | 14 | 2031-12-18 13:00 | 20.2 | 26.5394 | N | 0
2026-12-18 | 15 | 2031-12-18 14:00 | 20.79 | 27.3145 | N | 0
2026-12-18 | 16 | 2031-12-18 15:00 | 20.54 | 26.9861 | N | 0
2026-12-18 | 17 | 2031-12-18 16:00 | 20.33 | 26.7102 | N | 0
2026-12-18 | 18 | 2031-12-18 17:00 | 20.23 | 26.5788 | N | 0
2026-12-18 | 19 | 2031-12-18 18:00 | 20.16 | 26.4868 | N | 0
2026-12-18 | 20 | 2031-12-18 19:00 | 20.71 | 27.2094 | N | 0
2026-12-18 | 21 | 2031-12-18 20:00 | 23.1 | 30.3495 | N | 0
2026-12-18 | 22 | 2031-12-18 21:00 | 23.61 | 31.0195 | N | 0
2026-12-18 | 23 | 2031-12-18 22:00 | 23.11 | 30.3626 | N | 0
2026-12-19 | 00 | 2031-12-18 23:00 | 22.47 | 29.5218 | N | 0
2026-12-19 | 01 | 2031-12-19 | 22.15 | 29.1013 | N | 0
2026-12-19 | 02 | 2031-12-19 01:00 | 21.81 | 28.6546 | N | 0
2026-12-19 | 03 | 2031-12-19 02:00 | 19.92 | 26.1715 | N | 0
2026-12-19 | 04 | 2031-12-19 03:00 | 17.72 | 23.2811 | N | 0
2026-12-19 | 05 | 2031-12-19 04:00 | 15.87 | 20.8505 | N | 0
2026-12-19 | 06 | 2031-12-19 05:00 | 14.68 | 19.287 | N | 0
2026-12-19 | 07 | 2031-12-19 06:00 | 14 | 18.3936 | N | 0
2026-12-19 | 08 | 2031-12-19 07:00 | 13.54 | 17.7893 | N | 0
2026-12-19 | 09 | 2031-12-19 08:00 | 13.66 | 17.9469 | N | 0
2026-12-19 | 10 | 2031-12-19 09:00 | 14.47 | 19.0111 | N | 0
2026-12-19 | 11 | 2031-12-19 10:00 | 16.61 | 21.8227 | N | 0
2026-12-19 | 12 | 2031-12-19 11:00 | 18.7 | 24.5686 | N | 0
2026-12-19 | 13 | 2031-12-19 12:00 | 19.71 | 25.8956 | N | 0
2026-12-19 | 14 | 2031-12-19 13:00 | 20.09 | 26.3948 | N | 0
2026-12-19 | 15 | 2031-12-19 14:00 | 20.74 | 27.2488 | N | 0
2026-12-19 | 16 | 2031-12-19 15:00 | 21.47 | 28.2079 | N | 0
2026-12-19 | 17 | 2031-12-19 16:00 | 21.59 | 28.3656 | N | 0
2026-12-19 | 18 | 2031-12-19 17:00 | 21.86 | 28.7203 | N | 0
2026-12-19 | 19 | 2031-12-19 18:00 | 22.07 | 28.9962 | N | 0
2026-12-19 | 20 | 2031-12-19 19:00 | 22.67 | 29.7845 | N | 0
2026-12-19 | 21 | 2031-12-19 20:00 | 24.66 | 32.399 | N | 0
2026-12-19 | 22 | 2031-12-19 21:00 | 25.34 | 33.2924 | N | 0
2026-12-19 | 23 | 2031-12-19 22:00 | 24.81 | 32.5961 | N | 0
2026-12-20 | 00 | 2031-12-19 23:00 | 24.11 | 31.6764 | N | 0
2026-12-20 | 01 | 2031-12-20 | 23.66 | 31.0852 | N | 0
2026-12-20 | 02 | 2031-12-20 01:00 | 23.28 | 30.586 | N | 0
2026-12-20 | 03 | 2031-12-20 02:00 | 21.96 | 28.8517 | N | 0
2026-12-20 | 04 | 2031-12-20 03:00 | 19.9 | 26.1452 | N | 0
2026-12-20 | 05 | 2031-12-20 04:00 | 18.54 | 24.3584 | N | 0
2026-12-20 | 06 | 2031-12-20 05:00 | 17.26 | 22.6767 | N | 0
2026-12-20 | 07 | 2031-12-20 06:00 | 16.62 | 21.8359 | N | 0
2026-12-20 | 08 | 2031-12-20 07:00 | 16.11 | 21.1658 | N | 0
2026-12-20 | 09 | 2031-12-20 08:00 | 15.6 | 20.4957 | N | 0
2026-12-20 | 10 | 2031-12-20 09:00 | 15.98 | 20.995 | N | 0
2026-12-20 | 11 | 2031-12-20 10:00 | 16.64 | 21.8621 | N | 0
2026-12-20 | 12 | 2031-12-20 11:00 | 17.75 | 23.3205 | N | 0
2026-12-20 | 13 | 2031-12-20 12:00 | 19.66 | 25.8299 | N | 0
2026-12-20 | 14 | 2031-12-20 13:00 | 21.39 | 28.1028 | N | 0
2026-12-20 | 15 | 2031-12-20 14:00 | 22.5 | 29.5612 | N | 0
2026-12-20 | 16 | 2031-12-20 15:00 | 22.82 | 29.9816 | N | 0
2026-12-20 | 17 | 2031-12-20 16:00 | 22.6 | 29.6926 | N | 0
2026-12-20 | 18 | 2031-12-20 17:00 | 22.71 | 29.8371 | N | 0
2026-12-20 | 19 | 2031-12-20 18:00 | 22.59 | 29.6794 | N | 0
2026-12-20 | 20 | 2031-12-20 19:00 | 22.71 | 29.8371 | N | 0
2026-12-20 | 21 | 2031-12-20 20:00 | 24 | 31.5319 | N | 0
2026-12-20 | 22 | 2031-12-20 21:00 | 24.43 | 32.0969 | N | 0
2026-12-20 | 23 | 2031-12-20 22:00 | 23.57 | 30.967 | N | 0
2026-12-21 | 00 | 2031-12-20 23:00 | 22.83 | 29.9947 | N | 0
2026-12-21 | 01 | 2031-12-21 | 22.14 | 29.0882 | N | 0
2026-12-21 | 02 | 2031-12-21 01:00 | 21.44 | 28.1685 | N | 0
2026-12-21 | 03 | 2031-12-21 02:00 | 20.18 | 26.5131 | N | 0
2026-12-21 | 04 | 2031-12-21 03:00 | 18.79 | 24.6869 | N | 0
2026-12-21 | 05 | 2031-12-21 04:00 | 17.16 | 22.5453 | N | 0
2026-12-21 | 06 | 2031-12-21 05:00 | 16.06 | 21.1001 | N | 0
2026-12-21 | 07 | 2031-12-21 06:00 | 15.31 | 20.1147 | N | 0
2026-12-21 | 08 | 2031-12-21 07:00 | 15.13 | 19.8782 | N | 0
2026-12-21 | 09 | 2031-12-21 08:00 | 15.18 | 19.9439 | N | 0
2026-12-21 | 10 | 2031-12-21 09:00 | 15.65 | 20.5614 | N | 0
2026-12-21 | 11 | 2031-12-21 10:00 | 16.39 | 21.5337 | N | 0
2026-12-21 | 12 | 2031-12-21 11:00 | 17.25 | 22.6636 | N | 0
2026-12-21 | 13 | 2031-12-21 12:00 | 18.58 | 24.411 | N | 0
2026-12-21 | 14 | 2031-12-21 13:00 | 19.77 | 25.9744 | N | 0
2026-12-21 | 15 | 2031-12-21 14:00 | 20.17 | 26.4999 | N | 0
2026-12-21 | 16 | 2031-12-21 15:00 | 21.3 | 27.9846 | N | 0
2026-12-21 | 17 | 2031-12-21 16:00 | 22.08 | 29.0094 | N | 0
2026-12-21 | 18 | 2031-12-21 17:00 | 22.17 | 29.1276 | N | 0
2026-12-21 | 19 | 2031-12-21 18:00 | 22.34 | 29.351 | N | 0
2026-12-21 | 20 | 2031-12-21 19:00 | 22.95 | 30.1524 | N | 0
2026-12-21 | 21 | 2031-12-21 20:00 | 24.95 | 32.7801 | N | 0
2026-12-21 | 22 | 2031-12-21 21:00 | 25.63 | 33.6735 | N | 0
2026-12-21 | 23 | 2031-12-21 22:00 | 25.02 | 32.872 | N | 0
2026-12-22 | 00 | 2031-12-21 23:00 | 24.49 | 32.1757 | N | 0
2026-12-22 | 01 | 2031-12-22 | 23.75 | 31.2035 | N | 0
2026-12-22 | 02 | 2031-12-22 01:00 | 22.72 | 29.8502 | N | 0
2026-12-22 | 03 | 2031-12-22 02:00 | 21.42 | 28.1422 | N | 0
2026-12-22 | 04 | 2031-12-22 03:00 | 19.36 | 25.4357 | N | 0
2026-12-22 | 05 | 2031-12-22 04:00 | 17.66 | 23.2022 | N | 0
2026-12-22 | 06 | 2031-12-22 05:00 | 16.42 | 21.5731 | N | 0
2026-12-22 | 07 | 2031-12-22 06:00 | 15.84 | 20.8111 | N | 0
2026-12-22 | 08 | 2031-12-22 07:00 | 15.27 | 20.0622 | N | 0
2026-12-22 | 09 | 2031-12-22 08:00 | 15.37 | 20.1936 | N | 0
2026-12-22 | 10 | 2031-12-22 09:00 | 16.2 | 21.284 | N | 0
2026-12-22 | 11 | 2031-12-22 10:00 | 17.98 | 23.6227 | N | 0
2026-12-22 | 12 | 2031-12-22 11:00 | 19.59 | 25.7379 | N | 0
2026-12-22 | 13 | 2031-12-22 12:00 | 20.61 | 27.078 | N | 0
2026-12-22 | 14 | 2031-12-22 13:00 | 20.89 | 27.4459 | N | 0
2026-12-22 | 15 | 2031-12-22 14:00 | 21.36 | 28.0634 | N | 0
2026-12-22 | 16 | 2031-12-22 15:00 | 21.86 | 28.7203 | N | 0
2026-12-22 | 17 | 2031-12-22 16:00 | 21.59 | 28.3656 | N | 0
2026-12-22 | 18 | 2031-12-22 17:00 | 22.14 | 29.0882 | N | 0
2026-12-22 | 19 | 2031-12-22 18:00 | 22.14 | 29.0882 | N | 0
2026-12-22 | 20 | 2031-12-22 19:00 | 22.42 | 29.4561 | N | 0
2026-12-22 | 21 | 2031-12-22 20:00 | 24.06 | 31.6107 | N | 0
2026-12-22 | 22 | 2031-12-22 21:00 | 24.93 | 32.7538 | N | 0
2026-12-22 | 23 | 2031-12-22 22:00 | 24.49 | 32.1757 | N | 0
2026-12-23 | 00 | 2031-12-22 23:00 | 23.46 | 30.8224 | N | 0
2026-12-23 | 01 | 2031-12-23 | 22.91 | 30.0998 | N | 0
2026-12-23 | 02 | 2031-12-23 01:00 | 21.88 | 28.7466 | N | 0
2026-12-23 | 03 | 2031-12-23 02:00 | 20.59 | 27.0518 | N | 0
2026-12-23 | 04 | 2031-12-23 03:00 | 18.73 | 24.608 | N | 0
2026-12-23 | 05 | 2031-12-23 04:00 | 17.1 | 22.4665 | N | 0
2026-12-23 | 06 | 2031-12-23 05:00 | 15.63 | 20.5352 | N | 0
2026-12-23 | 07 | 2031-12-23 06:00 | 15.01 | 19.7206 | N | 0
2026-12-23 | 08 | 2031-12-23 07:00 | 14.46 | 18.998 | N | 0
2026-12-23 | 09 | 2031-12-23 08:00 | 14.47 | 19.0111 | N | 0
2026-12-23 | 10 | 2031-12-23 09:00 | 15.43 | 20.2724 | N | 0
2026-12-23 | 11 | 2031-12-23 10:00 | 17 | 22.3351 | N | 0
2026-12-23 | 12 | 2031-12-23 11:00 | 18.29 | 24.0299 | N | 0
2026-12-23 | 13 | 2031-12-23 12:00 | 19.86 | 26.0927 | N | 0
2026-12-23 | 14 | 2031-12-23 13:00 | 20.3 | 26.6707 | N | 0
2026-12-23 | 15 | 2031-12-23 14:00 | 21.2 | 27.8532 | N | 0
2026-12-23 | 16 | 2031-12-23 15:00 | 22.03 | 28.9437 | N | 0
2026-12-23 | 17 | 2031-12-23 16:00 | 22.04 | 28.9568 | N | 0
2026-12-23 | 18 | 2031-12-23 17:00 | 22.33 | 29.3378 | N | 0
2026-12-23 | 19 | 2031-12-23 18:00 | 22.29 | 29.2853 | N | 0
2026-12-23 | 20 | 2031-12-23 19:00 | 22.47 | 29.5218 | N | 0
2026-12-23 | 21 | 2031-12-23 20:00 | 23.57 | 30.967 | N | 0
2026-12-23 | 22 | 2031-12-23 21:00 | 24.13 | 31.7027 | N | 0
2026-12-23 | 23 | 2031-12-23 22:00 | 23.72 | 31.164 | N | 0
2026-12-24 | 00 | 2031-12-23 23:00 | 22.84 | 30.0079 | N | 0
2026-12-24 | 01 | 2031-12-24 | 22.64 | 29.7451 | N | 0
2026-12-24 | 02 | 2031-12-24 01:00 | 22.01 | 28.9174 | N | 0
2026-12-24 | 03 | 2031-12-24 02:00 | 20.56 | 27.0123 | N | 0
2026-12-24 | 04 | 2031-12-24 03:00 | 18.84 | 24.7526 | N | 0
2026-12-24 | 05 | 2031-12-24 04:00 | 17.18 | 22.5716 | N | 0
2026-12-24 | 06 | 2031-12-24 05:00 | 15.78 | 20.7322 | N | 0
2026-12-24 | 07 | 2031-12-24 06:00 | 14.99 | 19.6943 | N | 0
2026-12-24 | 08 | 2031-12-24 07:00 | 14.66 | 19.2607 | N | 0
2026-12-24 | 09 | 2031-12-24 08:00 | 14.51 | 19.0637 | N | 0
2026-12-24 | 10 | 2031-12-24 09:00 | 15.41 | 20.2461 | N | 0
2026-12-24 | 11 | 2031-12-24 10:00 | 16.89 | 22.1906 | N | 0
2026-12-24 | 12 | 2031-12-24 11:00 | 18.24 | 23.9643 | N | 0
2026-12-24 | 13 | 2031-12-24 12:00 | 19.32 | 25.3832 | N | 0
2026-12-24 | 14 | 2031-12-24 13:00 | 20.22 | 26.5656 | N | 0
2026-12-24 | 15 | 2031-12-24 14:00 | 20.82 | 27.3539 | N | 0
2026-12-24 | 16 | 2031-12-24 15:00 | 21.41 | 28.1291 | N | 0
2026-12-24 | 17 | 2031-12-24 16:00 | 21.47 | 28.2079 | N | 0
2026-12-24 | 18 | 2031-12-24 17:00 | 21.19 | 27.8401 | N | 0
2026-12-24 | 19 | 2031-12-24 18:00 | 20.93 | 27.4985 | N | 0
2026-12-24 | 20 | 2031-12-24 19:00 | 21.31 | 27.9977 | N | 0
2026-12-24 | 21 | 2031-12-24 20:00 | 23.07 | 30.3101 | N | 0
2026-12-24 | 22 | 2031-12-24 21:00 | 23.32 | 30.6385 | N | 0
2026-12-24 | 23 | 2031-12-24 22:00 | 22.55 | 29.6269 | N | 0
2026-12-25 | 00 | 2031-12-24 23:00 | 21.79 | 28.6284 | N | 0
2026-12-25 | 01 | 2031-12-25 | 21.18 | 27.8269 | N | 0
2026-12-25 | 02 | 2031-12-25 01:00 | 21.03 | 27.6298 | N | 0
2026-12-25 | 03 | 2031-12-25 02:00 | 19.86 | 26.0927 | N | 0
2026-12-25 | 04 | 2031-12-25 03:00 | 18.51 | 24.319 | N | 0
2026-12-25 | 05 | 2031-12-25 04:00 | 17.19 | 22.5847 | N | 0
2026-12-25 | 06 | 2031-12-25 05:00 | 15.98 | 20.995 | N | 0
2026-12-25 | 07 | 2031-12-25 06:00 | 15 | 19.7074 | N | 0
2026-12-25 | 08 | 2031-12-25 07:00 | 14.41 | 18.9323 | N | 0
2026-12-25 | 09 | 2031-12-25 08:00 | 14.23 | 18.6958 | N | 0
2026-12-25 | 10 | 2031-12-25 09:00 | 14.43 | 18.9586 | N | 0
2026-12-25 | 11 | 2031-12-25 10:00 | 15.44 | 20.2855 | N | 0
2026-12-25 | 12 | 2031-12-25 11:00 | 16.73 | 21.9804 | N | 0
2026-12-25 | 13 | 2031-12-25 12:00 | 18.85 | 24.7657 | N | 0
2026-12-25 | 14 | 2031-12-25 13:00 | 20.09 | 26.3948 | N | 0
2026-12-25 | 15 | 2031-12-25 14:00 | 20.91 | 27.4722 | N | 0
2026-12-25 | 16 | 2031-12-25 15:00 | 21.11 | 27.7349 | N | 0
2026-12-25 | 17 | 2031-12-25 16:00 | 20.81 | 27.3408 | N | 0
2026-12-25 | 18 | 2031-12-25 17:00 | 21 | 27.5904 | N | 0
2026-12-25 | 19 | 2031-12-25 18:00 | 21.04 | 27.643 | N | 0
2026-12-25 | 20 | 2031-12-25 19:00 | 21.32 | 28.0109 | N | 0
2026-12-25 | 21 | 2031-12-25 20:00 | 22.95 | 30.1524 | N | 0
2026-12-25 | 22 | 2031-12-25 21:00 | 23.09 | 30.3363 | N | 0
2026-12-25 | 23 | 2031-12-25 22:00 | 21.73 | 28.5495 | N | 0
2026-12-26 | 00 | 2031-12-25 23:00 | 20.67 | 27.1569 | N | 0
2026-12-26 | 01 | 2031-12-26 | 20.67 | 27.1569 | N | 0
2026-12-26 | 02 | 2031-12-26 01:00 | 20.71 | 27.2094 | N | 0
2026-12-26 | 03 | 2031-12-26 02:00 | 20.43 | 26.8415 | N | 0
2026-12-26 | 04 | 2031-12-26 03:00 | 19.37 | 25.4489 | N | 0
2026-12-26 | 05 | 2031-12-26 04:00 | 18.28 | 24.0168 | N | 0
2026-12-26 | 06 | 2031-12-26 05:00 | 17.09 | 22.4534 | N | 0
2026-12-26 | 07 | 2031-12-26 06:00 | 16.5 | 21.6782 | N | 0
2026-12-26 | 08 | 2031-12-26 07:00 | 16.23 | 21.3235 | N | 0
2026-12-26 | 09 | 2031-12-26 08:00 | 16.21 | 21.2972 | N | 0
2026-12-26 | 10 | 2031-12-26 09:00 | 16.65 | 21.8753 | N | 0
2026-12-26 | 11 | 2031-12-26 10:00 | 17.43 | 22.9001 | N | 0
2026-12-26 | 12 | 2031-12-26 11:00 | 18.38 | 24.1482 | N | 0
2026-12-26 | 13 | 2031-12-26 12:00 | 19.61 | 25.7642 | N | 0
2026-12-26 | 14 | 2031-12-26 13:00 | 21.11 | 27.7349 | N | 0
2026-12-26 | 15 | 2031-12-26 14:00 | 23.1 | 30.3495 | N | 0
2026-12-26 | 16 | 2031-12-26 15:00 | 24.39 | 32.0443 | N | 0
2026-12-26 | 17 | 2031-12-26 16:00 | 24.5 | 32.1888 | N | 0
2026-12-26 | 18 | 2031-12-26 17:00 | 24.3 | 31.9261 | N | 0
2026-12-26 | 19 | 2031-12-26 18:00 | 24.24 | 31.8472 | N | 0
2026-12-26 | 20 | 2031-12-26 19:00 | 24.35 | 31.9918 | N | 0
2026-12-26 | 21 | 2031-12-26 20:00 | 25.28 | 33.2136 | N | 0
2026-12-26 | 22 | 2031-12-26 21:00 | 25.93 | 34.0676 | N | 0
2026-12-26 | 23 | 2031-12-26 22:00 | 25.26 | 33.1873 | N | 0
2026-12-27 | 00 | 2031-12-26 23:00 | 24.64 | 32.3728 | N | 0
2026-12-27 | 01 | 2031-12-27 | 23.8 | 31.2691 | N | 0
2026-12-27 | 02 | 2031-12-27 01:00 | 23.43 | 30.783 | N | 0
2026-12-27 | 03 | 2031-12-27 02:00 | 22.4 | 29.4298 | N | 0
2026-12-27 | 04 | 2031-12-27 03:00 | 20.6 | 27.0649 | N | 0
2026-12-27 | 05 | 2031-12-27 04:00 | 19.21 | 25.2387 | N | 0
2026-12-27 | 06 | 2031-12-27 05:00 | 17.73 | 23.2942 | N | 0
2026-12-27 | 07 | 2031-12-27 06:00 | 17.03 | 22.3745 | N | 0
2026-12-27 | 08 | 2031-12-27 07:00 | 16.42 | 21.5731 | N | 0
2026-12-27 | 09 | 2031-12-27 08:00 | 16.28 | 21.3891 | N | 0
2026-12-27 | 10 | 2031-12-27 09:00 | 16.77 | 22.0329 | N | 0
2026-12-27 | 11 | 2031-12-27 10:00 | 17.42 | 22.8869 | N | 0
2026-12-27 | 12 | 2031-12-27 11:00 | 18.15 | 23.846 | N | 0
2026-12-27 | 13 | 2031-12-27 12:00 | 19.95 | 26.2109 | N | 0
2026-12-27 | 14 | 2031-12-27 13:00 | 20.77 | 27.2882 | N | 0
2026-12-27 | 15 | 2031-12-27 14:00 | 22.01 | 28.9174 | N | 0
2026-12-27 | 16 | 2031-12-27 15:00 | 22.74 | 29.8765 | N | 0
2026-12-27 | 17 | 2031-12-27 16:00 | 23.12 | 30.3757 | N | 0
2026-12-27 | 18 | 2031-12-27 17:00 | 22.78 | 29.929 | N | 0
2026-12-27 | 19 | 2031-12-27 18:00 | 22.6 | 29.6926 | N | 0
2026-12-27 | 20 | 2031-12-27 19:00 | 22.75 | 29.8896 | N | 0
2026-12-27 | 21 | 2031-12-27 20:00 | 24.28 | 31.8998 | N | 0
2026-12-27 | 22 | 2031-12-27 21:00 | 24.92 | 32.7406 | N | 0
2026-12-27 | 23 | 2031-12-27 22:00 | 24.7 | 32.4516 | N | 0
2026-12-28 | 00 | 2031-12-27 23:00 | 23.68 | 31.1115 | N | 0
2026-12-28 | 01 | 2031-12-28 | 23.44 | 30.7962 | N | 0
2026-12-28 | 02 | 2031-12-28 01:00 | 22.53 | 29.6006 | N | 0
2026-12-28 | 03 | 2031-12-28 02:00 | 21.16 | 27.8006 | N | 0
2026-12-28 | 04 | 2031-12-28 03:00 | 19.87 | 26.1058 | N | 0
2026-12-28 | 05 | 2031-12-28 04:00 | 18.52 | 24.3321 | N | 0
2026-12-28 | 06 | 2031-12-28 05:00 | 17.4 | 22.8606 | N | 0
2026-12-28 | 07 | 2031-12-28 06:00 | 16.62 | 21.8359 | N | 0
2026-12-28 | 08 | 2031-12-28 07:00 | 16 | 21.0213 | N | 0
2026-12-28 | 09 | 2031-12-28 08:00 | 15.76 | 20.706 | N | 0
2026-12-28 | 10 | 2031-12-28 09:00 | 16 | 21.0213 | N | 0
2026-12-28 | 11 | 2031-12-28 10:00 | 16.38 | 21.5205 | N | 0
2026-12-28 | 12 | 2031-12-28 11:00 | 17.29 | 22.7161 | N | 0
2026-12-28 | 13 | 2031-12-28 12:00 | 18.52 | 24.3321 | N | 0
2026-12-28 | 14 | 2031-12-28 13:00 | 19.85 | 26.0795 | N | 0
2026-12-28 | 15 | 2031-12-28 14:00 | 20.6 | 27.0649 | N | 0
2026-12-28 | 16 | 2031-12-28 15:00 | 21.03 | 27.6298 | N | 0
2026-12-28 | 17 | 2031-12-28 16:00 | 21.71 | 28.5232 | N | 0
2026-12-28 | 18 | 2031-12-28 17:00 | 22.19 | 29.1539 | N | 0
2026-12-28 | 19 | 2031-12-28 18:00 | 22.73 | 29.8634 | N | 0
2026-12-28 | 20 | 2031-12-28 19:00 | 23.29 | 30.5991 | N | 0
2026-12-28 | 21 | 2031-12-28 20:00 | 25.22 | 33.1348 | N | 0
2026-12-28 | 22 | 2031-12-28 21:00 | 25.93 | 34.0676 | N | 0
2026-12-28 | 23 | 2031-12-28 22:00 | 24.73 | 32.491 | N | 0
2026-12-29 | 00 | 2031-12-28 23:00 | 23.85 | 31.3348 | N | 0
2026-12-29 | 01 | 2031-12-29 | 22.7 | 29.8239 | N | 0
2026-12-29 | 02 | 2031-12-29 01:00 | 21.87 | 28.7335 | N | 0
2026-12-29 | 03 | 2031-12-29 02:00 | 20.25 | 26.6051 | N | 0
2026-12-29 | 04 | 2031-12-29 03:00 | 18.47 | 24.2664 | N | 0
2026-12-29 | 05 | 2031-12-29 04:00 | 16.92 | 22.23 | N | 0
2026-12-29 | 06 | 2031-12-29 05:00 | 15.64 | 20.5483 | N | 0
2026-12-29 | 07 | 2031-12-29 06:00 | 15.08 | 19.8126 | N | 0
2026-12-29 | 08 | 2031-12-29 07:00 | 14.62 | 19.2082 | N | 0
2026-12-29 | 09 | 2031-12-29 08:00 | 14.26 | 18.7352 | N | 0
2026-12-29 | 10 | 2031-12-29 09:00 | 14.78 | 19.4184 | N | 0
2026-12-29 | 11 | 2031-12-29 10:00 | 15.85 | 20.8242 | N | 0
2026-12-29 | 12 | 2031-12-29 11:00 | 16.95 | 22.2694 | N | 0
2026-12-29 | 13 | 2031-12-29 12:00 | 18.13 | 23.8197 | N | 0
2026-12-29 | 14 | 2031-12-29 13:00 | 19.87 | 26.1058 | N | 0
2026-12-29 | 15 | 2031-12-29 14:00 | 21.42 | 28.1422 | N | 0
2026-12-29 | 16 | 2031-12-29 15:00 | 21.76 | 28.5889 | N | 0
2026-12-29 | 17 | 2031-12-29 16:00 | 22.69 | 29.8108 | N | 0
2026-12-29 | 18 | 2031-12-29 17:00 | 22.72 | 29.8502 | N | 0
2026-12-29 | 19 | 2031-12-29 18:00 | 22.4 | 29.4298 | N | 0
2026-12-29 | 20 | 2031-12-29 19:00 | 22.62 | 29.7188 | N | 0
2026-12-29 | 21 | 2031-12-29 20:00 | 24.61 | 32.3334 | N | 0
2026-12-29 | 22 | 2031-12-29 21:00 | 25.93 | 34.0676 | N | 0
2026-12-29 | 23 | 2031-12-29 22:00 | 25.49 | 33.4895 | N | 0
2026-12-30 | 00 | 2031-12-29 23:00 | 24.62 | 32.3465 | N | 0
2026-12-30 | 01 | 2031-12-30 | 24.29 | 31.9129 | N | 0
2026-12-30 | 02 | 2031-12-30 01:00 | 23.68 | 31.1115 | N | 0
2026-12-30 | 03 | 2031-12-30 02:00 | 22.12 | 29.0619 | N | 0
2026-12-30 | 04 | 2031-12-30 03:00 | 20.14 | 26.4605 | N | 0
2026-12-30 | 05 | 2031-12-30 04:00 | 19 | 24.9628 | N | 0
2026-12-30 | 06 | 2031-12-30 05:00 | 17.92 | 23.5438 | N | 0
2026-12-30 | 07 | 2031-12-30 06:00 | 17.14 | 22.519 | N | 0
2026-12-30 | 08 | 2031-12-30 07:00 | 16.65 | 21.8753 | N | 0
2026-12-30 | 09 | 2031-12-30 08:00 | 16.38 | 21.5205 | N | 0
2026-12-30 | 10 | 2031-12-30 09:00 | 16.89 | 22.1906 | N | 0
2026-12-30 | 11 | 2031-12-30 10:00 | 17.97 | 23.6095 | N | 0
2026-12-30 | 12 | 2031-12-30 11:00 | 19.28 | 25.3306 | N | 0
2026-12-30 | 13 | 2031-12-30 12:00 | 20.07 | 26.3686 | N | 0
2026-12-30 | 14 | 2031-12-30 13:00 | 20.78 | 27.3014 | N | 0
2026-12-30 | 15 | 2031-12-30 14:00 | 21.71 | 28.5232 | N | 0
2026-12-30 | 16 | 2031-12-30 15:00 | 21.87 | 28.7335 | N | 0
2026-12-30 | 17 | 2031-12-30 16:00 | 22.12 | 29.0619 | N | 0
2026-12-30 | 18 | 2031-12-30 17:00 | 21.87 | 28.7335 | N | 0
2026-12-30 | 19 | 2031-12-30 18:00 | 22.04 | 28.9568 | N | 0
2026-12-30 | 20 | 2031-12-30 19:00 | 22.66 | 29.7714 | N | 0
2026-12-30 | 21 | 2031-12-30 20:00 | 24.88 | 32.6881 | N | 0
2026-12-30 | 22 | 2031-12-30 21:00 | 26.14 | 34.3435 | N | 0
2026-12-30 | 23 | 2031-12-30 22:00 | 25.94 | 34.0807 | N | 0
2026-12-31 | 00 | 2031-12-30 23:00 | 24.69 | 32.4385 | N | 0
2026-12-31 | 01 | 2031-12-31 | 24.35 | 31.9918 | N | 0
2026-12-31 | 02 | 2031-12-31 01:00 | 23.66 | 31.0852 | N | 0
2026-12-31 | 03 | 2031-12-31 02:00 | 22.44 | 29.4823 | N | 0
2026-12-31 | 04 | 2031-12-31 03:00 | 20.69 | 27.1831 | N | 0
2026-12-31 | 05 | 2031-12-31 04:00 | 18.92 | 24.8577 | N | 0
2026-12-31 | 06 | 2031-12-31 05:00 | 17.76 | 23.3336 | N | 0
2026-12-31 | 07 | 2031-12-31 06:00 | 17.06 | 22.4139 | N | 0
2026-12-31 | 08 | 2031-12-31 07:00 | 16.72 | 21.9672 | N | 0
2026-12-31 | 09 | 2031-12-31 08:00 | 16.67 | 21.9015 | N | 0
2026-12-31 | 10 | 2031-12-31 09:00 | 16.6 | 21.8096 | N | 0
2026-12-31 | 11 | 2031-12-31 10:00 | 17.61 | 23.1365 | N | 0
2026-12-31 | 12 | 2031-12-31 11:00 | 18.63 | 24.4766 | N | 0
2026-12-31 | 13 | 2031-12-31 12:00 | 19.8 | 26.0138 | N | 0
2026-12-31 | 14 | 2031-12-31 13:00 | 20.7 | 27.1963 | N | 0
2026-12-31 | 15 | 2031-12-31 14:00 | 21.58 | 28.3524 | N | 0
2026-12-31 | 16 | 2031-12-31 15:00 | 21.56 | 28.3262 | N | 0
2026-12-31 | 17 | 2031-12-31 16:00 | 22.24 | 29.2196 | N | 0
2026-12-31 | 18 | 2031-12-31 17:00 | 22.31 | 29.3115 | N | 0
2026-12-31 | 19 | 2031-12-31 18:00 | 22.45 | 29.4955 | N | 0
2026-12-31 | 20 | 2031-12-31 19:00 | 23.23 | 30.5203 | N | 0
2026-12-31 | 21 | 2031-12-31 20:00 | 24.61 | 32.3334 | N | 0
2026-12-31 | 22 | 2031-12-31 21:00 | 25.29 | 33.2268 | N | 0
2026-12-31 | 23 | 2031-12-31 22:00 | 25.06 | 32.9246 | N | 0
Formulas:
Date-Time = [Date-Time, row above] + TIME(1,0,0)

## Bowmanville Forecast
Hourly Load (MVA)
Total load | 206926.1025 |  | 216100.2139 | 225681.0613 | 235686.6777 | 246135.895 | Exceeds N-1 (MW) |  |  |  | BOWMANVILLE
Date-Time | BOWMANVILLE 2031 (MVA) | Load Shape | 2032 | 2033 | 2034 | 2035 | 2032 | 2033 | 2034 | 2035 | MW Exceeding planning capacity |  |  |  |  | Load CAGR
2031-01-01 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0 |  | 2032 | 2033 | 2034 | 2035 | 4.434%
2031-01-01 01:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0 | avg | 4.954 | 5.2118 | 5.2104 | 5.1454
2031-01-01 02:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0 | max | 13.1311 | 15.1897 | 17.3395 | 19.5846
2031-01-01 03:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0 | median | 4.9193 | 4.3827 | 3.7907 | 3.1988
2031-01-01 04:00 | 18.4987 | 0.00894% | 19.3189 | 20.1754 | 21.0699 | 22.004 | 0 | 0 | 0 | 0
2031-01-01 05:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0 | Annual Hours Exceeding Planning Capacity After BESS Deployment
2031-01-01 06:00 | 18.1046 | 0.008749% | 18.9072 | 19.7455 | 20.6209 | 21.5352 | 0 | 0 | 0 | 0 | MW BESS Size | 2032 | 2033 | 2034 | 2035
2031-01-01 07:00 | 18.5644 | 0.008972% | 19.3875 | 20.247 | 21.1447 | 22.0821 | 0 | 0 | 0 | 0 | 1 | 421 | 522 | 699 | 977
2031-01-01 08:00 | 19.3921 | 0.009372% | 20.2519 | 21.1498 | 22.0874 | 23.0667 | 0 | 0 | 0 | 0 | 2 | 364 | 449 | 567 | 769
2031-01-01 09:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0 | 3 | 312 | 390 | 485 | 643
2031-01-01 10:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0 | 4 | 273 | 338 | 427 | 530
2031-01-01 11:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0 | 5 | 239 | 295 | 372 | 458
2031-01-01 12:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0 | 6 | 181 | 266 | 321 | 409
2031-01-01 13:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0 | 7 | 140 | 221 | 284 | 357
2031-01-01 14:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0 | 8 | 95 | 170 | 255 | 312
2031-01-01 15:00 | 26.0532 | 0.01259% | 27.2083 | 28.4146 | 29.6744 | 30.99 | 0 | 0 | 0 | 0 | 9 | 66 | 130 | 209 | 277
2031-01-01 16:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0 | 10 | 49 | 90 | 165 | 251
2031-01-01 17:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0 | 11 | 27 | 64 | 123 | 202
2031-01-01 18:00 | 30.5597 | 0.01477% | 31.9146 | 33.3295 | 34.8072 | 36.3503 | 0 | 0 | 0 | 0 | 12 | 7 | 48 | 89 | 162
2031-01-01 19:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0 | 13 | 1 | 26 | 64 | 123
2031-01-01 20:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0 | 14 | 0 | 7 | 48 | 89
2031-01-01 21:00 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0 | 15 | 0 | 1 | 28 | 65
2031-01-01 22:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 8 | 49
2031-01-01 23:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 28
2031-01-02 | 22.8606 | 0.01105% | 23.8742 | 24.9326 | 26.038 | 27.1924 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 11
2031-01-02 01:00 | 21.0476 | 0.01017% | 21.9807 | 22.9552 | 23.9729 | 25.0358 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 2
2031-01-02 02:00 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0
2031-01-02 03:00 | 19.0899 | 0.009225% | 19.9363 | 20.8202 | 21.7433 | 22.7072 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0
2031-01-02 04:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0
2031-01-02 05:00 | 18.7221 | 0.009048% | 19.5521 | 20.419 | 21.3242 | 22.2697 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0
2031-01-02 06:00 | 19.668 | 0.009505% | 20.54 | 21.4507 | 22.4017 | 23.3949 | 0 | 0 | 0 | 0 | BESS MW needed | 13 | 15 | 17 | 19
2031-01-02 07:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-01-02 08:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-01-02 09:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0 | Year | Min MW BESS
2031-01-02 10:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0 | 2032 | 13
2031-01-02 11:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0 | 2033 | 15
2031-01-02 12:00 | 26.4474 | 0.01278% | 27.6199 | 28.8445 | 30.1233 | 31.4588 | 0 | 0 | 0 | 0 | 2034 | 17
2031-01-02 13:00 | 27.4328 | 0.01326% | 28.649 | 29.9192 | 31.2456 | 32.6309 | 0 | 0 | 0 | 0 | 2035 | 19
2031-01-02 14:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-01-02 15:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-01-02 16:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-01-02 17:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-01-02 18:00 | 32.1757 | 0.01555% | 33.6022 | 35.092 | 36.6478 | 38.2726 | 0 | 0 | 0 | 1.1453
2031-01-02 19:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-01-02 20:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-01-02 21:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-01-02 22:00 | 28.6152 | 0.01383% | 29.8839 | 31.2088 | 32.5924 | 34.0374 | 0 | 0 | 0 | 0
2031-01-02 23:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-01-03 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-01-03 01:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-01-03 02:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-01-03 03:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-01-03 04:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-01-03 05:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-01-03 06:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-01-03 07:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-01-03 08:00 | 24.7394 | 0.01196% | 25.8362 | 26.9817 | 28.1779 | 29.4272 | 0 | 0 | 0 | 0
2031-01-03 09:00 | 26.1715 | 0.01265% | 27.3318 | 28.5436 | 29.8091 | 31.1306 | 0 | 0 | 0 | 0
2031-01-03 10:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-01-03 11:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-01-03 12:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-01-03 13:00 | 28.313 | 0.01368% | 29.5683 | 30.8792 | 32.2482 | 33.678 | 0 | 0 | 0 | 0
2031-01-03 14:00 | 28.6152 | 0.01383% | 29.8839 | 31.2088 | 32.5924 | 34.0374 | 0 | 0 | 0 | 0
2031-01-03 15:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-01-03 16:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-01-03 17:00 | 30.2706 | 0.01463% | 31.6127 | 33.0142 | 34.4779 | 36.0065 | 0 | 0 | 0 | 0
2031-01-03 18:00 | 32.2545 | 0.01559% | 33.6845 | 35.1779 | 36.7376 | 38.3663 | 0 | 0 | 0 | 1.2297
2031-01-03 19:00 | 31.9129 | 0.01542% | 33.3278 | 34.8054 | 36.3485 | 37.96 | 0 | 0 | 0 | 0.86401
2031-01-03 20:00 | 30.9407 | 0.01495% | 32.3125 | 33.745 | 35.2411 | 36.8035 | 0 | 0 | 0 | 0
2031-01-03 21:00 | 30.7173 | 0.01484% | 32.0792 | 33.5014 | 34.9867 | 36.5379 | 0 | 0 | 0 | 0
2031-01-03 22:00 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-01-03 23:00 | 28.1554 | 0.01361% | 29.4036 | 30.7073 | 32.0687 | 33.4904 | 0 | 0 | 0 | 0
2031-01-04 | 26.0532 | 0.01259% | 27.2083 | 28.4146 | 29.6744 | 30.99 | 0 | 0 | 0 | 0
2031-01-04 01:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-01-04 02:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-01-04 03:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-01-04 04:00 | 21.2578 | 0.01027% | 22.2002 | 23.1845 | 24.2124 | 25.2858 | 0 | 0 | 0 | 0
2031-01-04 05:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-01-04 06:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-01-04 07:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-01-04 08:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-01-04 09:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-01-04 10:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-01-04 11:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-01-04 12:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-01-04 13:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-01-04 14:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-01-04 15:00 | 30.1393 | 0.01457% | 31.4755 | 32.871 | 34.3283 | 35.8503 | 0 | 0 | 0 | 0
2031-01-04 16:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-01-04 17:00 | 31.7421 | 0.01534% | 33.1494 | 34.6191 | 36.154 | 37.7568 | 0 | 0 | 0 | 0.68116
2031-01-04 18:00 | 33.634 | 0.01625% | 35.1252 | 36.6825 | 38.3088 | 40.0073 | 0 | 0 | 1.1779 | 2.7065
2031-01-04 19:00 | 33.1216 | 0.01601% | 34.5901 | 36.1237 | 37.7252 | 39.3978 | 0 | 0 | 0.65269 | 2.158
2031-01-04 20:00 | 32.5304 | 0.01572% | 33.9727 | 35.4789 | 37.0518 | 38.6945 | 0 | 0 | 0.046635 | 1.5251
2031-01-04 21:00 | 31.2297 | 0.01509% | 32.6143 | 34.0603 | 35.5703 | 37.1474 | 0 | 0 | 0 | 0.13262
2031-01-04 22:00 | 29.9028 | 0.01445% | 31.2285 | 32.613 | 34.0589 | 35.5689 | 0 | 0 | 0 | 0
2031-01-04 23:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-01-05 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-01-05 01:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-01-05 02:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-01-05 03:00 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-01-05 04:00 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-01-05 05:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-01-05 06:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-01-05 07:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-01-05 08:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-01-05 09:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-01-05 10:00 | 25.9613 | 0.01255% | 27.1123 | 28.3143 | 29.5696 | 30.8806 | 0 | 0 | 0 | 0
2031-01-05 11:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-01-05 12:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-01-05 13:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-01-05 14:00 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-01-05 15:00 | 30.2444 | 0.01462% | 31.5853 | 32.9856 | 34.448 | 35.9753 | 0 | 0 | 0 | 0
2031-01-05 16:00 | 30.7962 | 0.01488% | 32.1615 | 33.5874 | 35.0765 | 36.6316 | 0 | 0 | 0 | 0
2031-01-05 17:00 | 33.2136 | 0.01605% | 34.6861 | 36.224 | 37.83 | 39.5072 | 0 | 0 | 0.74697 | 2.2564
2031-01-05 18:00 | 35.6705 | 0.01724% | 37.2519 | 38.9035 | 40.6283 | 42.4296 | 0.22674 | 1.7132 | 3.2655 | 4.8866
2031-01-05 19:00 | 34.6588 | 0.01675% | 36.1954 | 37.8002 | 39.476 | 41.2262 | 0 | 0.72015 | 2.2284 | 3.8036
2031-01-05 20:00 | 32.9509 | 0.01592% | 34.4117 | 35.9374 | 37.5307 | 39.1946 | 0 | 0 | 0.47761 | 1.9751
2031-01-05 21:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-01-05 22:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-01-05 23:00 | 27.6693 | 0.01337% | 28.896 | 30.1771 | 31.515 | 32.9122 | 0 | 0 | 0 | 0
2031-01-06 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-01-06 01:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-01-06 02:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-01-06 03:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-01-06 04:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-01-06 05:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-01-06 06:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-01-06 07:00 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-01-06 08:00 | 28.3393 | 0.0137% | 29.5957 | 30.9079 | 32.2782 | 33.7092 | 0 | 0 | 0 | 0
2031-01-06 09:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-01-06 10:00 | 29.9947 | 0.0145% | 31.3246 | 32.7133 | 34.1637 | 35.6783 | 0 | 0 | 0 | 0
2031-01-06 11:00 | 30.5991 | 0.01479% | 31.9557 | 33.3725 | 34.8521 | 36.3972 | 0 | 0 | 0 | 0
2031-01-06 12:00 | 31.256 | 0.0151% | 32.6418 | 34.0889 | 35.6003 | 37.1786 | 0 | 0 | 0 | 0.16075
2031-01-06 13:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-01-06 14:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-01-06 15:00 | 29.9685 | 0.01448% | 31.2971 | 32.6847 | 34.1338 | 35.6471 | 0 | 0 | 0 | 0
2031-01-06 16:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-01-06 17:00 | 32.5436 | 0.01573% | 33.9864 | 35.4932 | 37.0668 | 38.7101 | 0 | 0 | 0.060103 | 1.5391
2031-01-06 18:00 | 35.342 | 0.01708% | 36.9089 | 38.5453 | 40.2542 | 42.0389 | 0 | 1.3908 | 2.9288 | 4.535
2031-01-06 19:00 | 34.9085 | 0.01687% | 36.4561 | 38.0724 | 39.7604 | 41.5232 | 0 | 0.96518 | 2.4843 | 4.0708
2031-01-06 20:00 | 33.9099 | 0.01639% | 35.4134 | 36.9834 | 38.6231 | 40.3354 | 0 | 0 | 1.4608 | 3.0019
2031-01-06 21:00 | 32.5698 | 0.01574% | 34.0138 | 35.5218 | 37.0967 | 38.7414 | 0 | 0 | 0.087038 | 1.5673
2031-01-06 22:00 | 31.5188 | 0.01523% | 32.9162 | 34.3755 | 35.8996 | 37.4912 | 0 | 0 | 0 | 0.44206
2031-01-06 23:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-01-07 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-01-07 01:00 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-01-07 02:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-01-07 03:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-01-07 04:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-01-07 05:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-01-07 06:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-01-07 07:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-01-07 08:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-01-07 09:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-01-07 10:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-01-07 11:00 | 30.1393 | 0.01457% | 31.4755 | 32.871 | 34.3283 | 35.8503 | 0 | 0 | 0 | 0
2031-01-07 12:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-01-07 13:00 | 30.6122 | 0.01479% | 31.9694 | 33.3868 | 34.867 | 36.4129 | 0 | 0 | 0 | 0
2031-01-07 14:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-01-07 15:00 | 30.2181 | 0.0146% | 31.5578 | 32.9569 | 34.4181 | 35.944 | 0 | 0 | 0 | 0
2031-01-07 16:00 | 31.0852 | 0.01502% | 32.4634 | 33.9027 | 35.4057 | 36.9755 | 0 | 0 | 0 | 0
2031-01-07 17:00 | 33.5684 | 0.01622% | 35.0566 | 36.6109 | 38.234 | 39.9291 | 0 | 0 | 1.1106 | 2.6362
2031-01-07 18:00 | 35.3289 | 0.01707% | 36.8952 | 38.531 | 40.2392 | 42.0232 | 0 | 1.3779 | 2.9153 | 4.5209
2031-01-07 19:00 | 34.5537 | 0.0167% | 36.0857 | 37.6855 | 39.3563 | 41.1012 | 0 | 0.61698 | 2.1207 | 3.6911
2031-01-07 20:00 | 33.3319 | 0.01611% | 34.8096 | 36.3529 | 37.9646 | 39.6478 | 0 | 0 | 0.86818 | 2.383
2031-01-07 21:00 | 32.8983 | 0.0159% | 34.3569 | 35.8801 | 37.4708 | 39.1321 | 0 | 0 | 0.42374 | 1.9189
2031-01-07 22:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-01-07 23:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-01-08 | 26.8941 | 0.013% | 28.0865 | 29.3317 | 30.6321 | 31.9902 | 0 | 0 | 0 | 0
2031-01-08 01:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-01-08 02:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-01-08 03:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-01-08 04:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-01-08 05:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-01-08 06:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-01-08 07:00 | 28.694 | 0.01387% | 29.9662 | 31.2948 | 32.6822 | 34.1312 | 0 | 0 | 0 | 0
2031-01-08 08:00 | 31.0852 | 0.01502% | 32.4634 | 33.9027 | 35.4057 | 36.9755 | 0 | 0 | 0 | 0
2031-01-08 09:00 | 31.8472 | 0.01539% | 33.2592 | 34.7337 | 36.2737 | 37.8819 | 0 | 0 | 0 | 0.79368
2031-01-08 10:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-01-08 11:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-01-08 12:00 | 31.4662 | 0.01521% | 32.8613 | 34.3182 | 35.8397 | 37.4287 | 0 | 0 | 0 | 0.3858
2031-01-08 13:00 | 31.5319 | 0.01524% | 32.9299 | 34.3898 | 35.9145 | 37.5068 | 0 | 0 | 0 | 0.45612
2031-01-08 14:00 | 31.1378 | 0.01505% | 32.5183 | 33.96 | 35.4656 | 37.038 | 0 | 0 | 0 | 0.034169
2031-01-08 15:00 | 30.5728 | 0.01477% | 31.9283 | 33.3438 | 34.8221 | 36.366 | 0 | 0 | 0 | 0
2031-01-08 16:00 | 31.0721 | 0.01502% | 32.4497 | 33.8883 | 35.3908 | 36.9598 | 0 | 0 | 0 | 0
2031-01-08 17:00 | 34.4749 | 0.01666% | 36.0033 | 37.5996 | 39.2665 | 41.0074 | 0 | 0.5396 | 2.0399 | 3.6067
2031-01-08 18:00 | 36.2617 | 0.01752% | 37.8694 | 39.5483 | 41.3017 | 43.1328 | 0.78243 | 2.2935 | 3.8715 | 5.5195
2031-01-08 19:00 | 36.196 | 0.01749% | 37.8008 | 39.4767 | 41.2269 | 43.0547 | 0.72069 | 2.229 | 3.8042 | 5.4492
2031-01-08 20:00 | 34.4092 | 0.01663% | 35.9347 | 37.5279 | 39.1917 | 40.9293 | 0 | 0.47512 | 1.9726 | 3.5364
2031-01-08 21:00 | 34.107 | 0.01648% | 35.6192 | 37.1983 | 38.8475 | 40.5699 | 0 | 0.17851 | 1.6628 | 3.2129
2031-01-08 22:00 | 32.6749 | 0.01579% | 34.1236 | 35.6365 | 37.2164 | 38.8664 | 0 | 0 | 0.19478 | 1.6798
2031-01-08 23:00 | 30.2706 | 0.01463% | 31.6127 | 33.0142 | 34.4779 | 36.0065 | 0 | 0 | 0 | 0
2031-01-09 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-01-09 01:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-01-09 02:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-01-09 03:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-01-09 04:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-01-09 05:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-01-09 06:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-01-09 07:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-01-09 08:00 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-01-09 09:00 | 31.2954 | 0.01512% | 32.6829 | 34.1319 | 35.6452 | 37.2255 | 0 | 0 | 0 | 0.20295
2031-01-09 10:00 | 30.9276 | 0.01495% | 32.2987 | 33.7307 | 35.2262 | 36.7879 | 0 | 0 | 0 | 0
2031-01-09 11:00 | 30.8619 | 0.01491% | 32.2301 | 33.6591 | 35.1513 | 36.7098 | 0 | 0 | 0 | 0
2031-01-09 12:00 | 30.8093 | 0.01489% | 32.1752 | 33.6017 | 35.0915 | 36.6473 | 0 | 0 | 0 | 0
2031-01-09 13:00 | 30.7173 | 0.01484% | 32.0792 | 33.5014 | 34.9867 | 36.5379 | 0 | 0 | 0 | 0
2031-01-09 14:00 | 30.7305 | 0.01485% | 32.0929 | 33.5158 | 35.0017 | 36.5535 | 0 | 0 | 0 | 0
2031-01-09 15:00 | 30.6122 | 0.01479% | 31.9694 | 33.3868 | 34.867 | 36.4129 | 0 | 0 | 0 | 0
2031-01-09 16:00 | 30.4546 | 0.01472% | 31.8048 | 33.2149 | 34.6874 | 36.2253 | 0 | 0 | 0 | 0
2031-01-09 17:00 | 33.5552 | 0.01622% | 35.0429 | 36.5965 | 38.219 | 39.9135 | 0 | 0 | 1.0971 | 2.6221
2031-01-09 18:00 | 35.3552 | 0.01709% | 36.9226 | 38.5596 | 40.2692 | 42.0545 | 0 | 1.4036 | 2.9422 | 4.5491
2031-01-09 19:00 | 35.053 | 0.01694% | 36.6071 | 38.23 | 39.925 | 41.6951 | 0 | 1.107 | 2.6325 | 4.2256
2031-01-09 20:00 | 34.4223 | 0.01664% | 35.9485 | 37.5422 | 39.2067 | 40.9449 | 0 | 0.48802 | 1.986 | 3.5504
2031-01-09 21:00 | 34.0019 | 0.01643% | 35.5094 | 37.0837 | 38.7278 | 40.4448 | 0 | 0.075342 | 1.555 | 3.1004
2031-01-09 22:00 | 32.3071 | 0.01561% | 33.7394 | 35.2353 | 36.7974 | 38.4288 | 0 | 0 | 0 | 1.286
2031-01-09 23:00 | 30.2049 | 0.0146% | 31.5441 | 32.9426 | 34.4031 | 35.9284 | 0 | 0 | 0 | 0
2031-01-10 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-01-10 01:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-01-10 02:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-01-10 03:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-01-10 04:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-01-10 05:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-01-10 06:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-01-10 07:00 | 26.8941 | 0.013% | 28.0865 | 29.3317 | 30.6321 | 31.9902 | 0 | 0 | 0 | 0
2031-01-10 08:00 | 30.2575 | 0.01462% | 31.599 | 32.9999 | 34.463 | 35.9909 | 0 | 0 | 0 | 0
2031-01-10 09:00 | 31.5188 | 0.01523% | 32.9162 | 34.3755 | 35.8996 | 37.4912 | 0 | 0 | 0 | 0.44206
2031-01-10 10:00 | 31.3743 | 0.01516% | 32.7652 | 34.2179 | 35.735 | 37.3193 | 0 | 0 | 0 | 0.28734
2031-01-10 11:00 | 31.3217 | 0.01514% | 32.7104 | 34.1606 | 35.6751 | 37.2568 | 0 | 0 | 0 | 0.23108
2031-01-10 12:00 | 30.9013 | 0.01493% | 32.2713 | 33.702 | 35.1962 | 36.7567 | 0 | 0 | 0 | 0
2031-01-10 13:00 | 30.3232 | 0.01465% | 31.6676 | 33.0716 | 34.5378 | 36.069 | 0 | 0 | 0 | 0
2031-01-10 14:00 | 29.2853 | 0.01415% | 30.5836 | 31.9396 | 33.3556 | 34.8344 | 0 | 0 | 0 | 0
2031-01-10 15:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-01-10 16:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-01-10 17:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-01-10 18:00 | 33.0297 | 0.01596% | 34.4941 | 36.0234 | 37.6205 | 39.2884 | 0 | 0 | 0.55842 | 2.0595
2031-01-10 19:00 | 32.7801 | 0.01584% | 34.2334 | 35.7511 | 37.3361 | 38.9914 | 0 | 0 | 0.30253 | 1.7923
2031-01-10 20:00 | 31.3348 | 0.01514% | 32.7241 | 34.1749 | 35.6901 | 37.2724 | 0 | 0 | 0 | 0.24514
2031-01-10 21:00 | 31.0458 | 0.015% | 32.4222 | 33.8597 | 35.3608 | 36.9286 | 0 | 0 | 0 | 0
2031-01-10 22:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-01-10 23:00 | 28.6152 | 0.01383% | 29.8839 | 31.2088 | 32.5924 | 34.0374 | 0 | 0 | 0 | 0
2031-01-11 | 25.7905 | 0.01246% | 26.9339 | 28.128 | 29.3751 | 30.6774 | 0 | 0 | 0 | 0
2031-01-11 01:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-01-11 02:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-01-11 03:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-01-11 04:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-01-11 05:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-01-11 06:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-01-11 07:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-01-11 08:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-01-11 09:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-01-11 10:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-01-11 11:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-01-11 12:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-01-11 13:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-01-11 14:00 | 28.1291 | 0.01359% | 29.3762 | 30.6786 | 32.0387 | 33.4592 | 0 | 0 | 0 | 0
2031-01-11 15:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-01-11 16:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-01-11 17:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-01-11 18:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-01-11 19:00 | 31.6502 | 0.0153% | 33.0534 | 34.5188 | 36.0492 | 37.6475 | 0 | 0 | 0 | 0.58271
2031-01-11 20:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-01-11 21:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-01-11 22:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-01-11 23:00 | 26.1846 | 0.01265% | 27.3455 | 28.5579 | 29.824 | 31.1463 | 0 | 0 | 0 | 0
2031-01-12 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-01-12 01:00 | 22.6898 | 0.01097% | 23.6958 | 24.7464 | 25.8435 | 26.9893 | 0 | 0 | 0 | 0
2031-01-12 02:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-01-12 03:00 | 20.3249 | 0.009822% | 21.2261 | 22.1671 | 23.1499 | 24.1763 | 0 | 0 | 0 | 0
2031-01-12 04:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-01-12 05:00 | 19.7206 | 0.00953% | 20.5949 | 21.508 | 22.4615 | 23.4574 | 0 | 0 | 0 | 0
2031-01-12 06:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-01-12 07:00 | 20.6403 | 0.009975% | 21.5554 | 22.511 | 23.509 | 24.5513 | 0 | 0 | 0 | 0
2031-01-12 08:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-01-12 09:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-01-12 10:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-01-12 11:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-01-12 12:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-01-12 13:00 | 28.3787 | 0.01371% | 29.6369 | 30.9509 | 32.3231 | 33.7561 | 0 | 0 | 0 | 0
2031-01-12 14:00 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-01-12 15:00 | 28.7729 | 0.0139% | 30.0485 | 31.3807 | 32.772 | 34.225 | 0 | 0 | 0 | 0
2031-01-12 16:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-01-12 17:00 | 31.9261 | 0.01543% | 33.3415 | 34.8197 | 36.3635 | 37.9756 | 0 | 0 | 0 | 0.87807
2031-01-12 18:00 | 33.4632 | 0.01617% | 34.9468 | 36.4962 | 38.1143 | 39.8041 | 0 | 0 | 1.0029 | 2.5237
2031-01-12 19:00 | 32.6749 | 0.01579% | 34.1236 | 35.6365 | 37.2164 | 38.8664 | 0 | 0 | 0.19478 | 1.6798
2031-01-12 20:00 | 30.9407 | 0.01495% | 32.3125 | 33.745 | 35.2411 | 36.8035 | 0 | 0 | 0 | 0
2031-01-12 21:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-01-12 22:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-01-12 23:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-01-13 | 23.7278 | 0.01147% | 24.7797 | 25.8784 | 27.0257 | 28.2239 | 0 | 0 | 0 | 0
2031-01-13 01:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-01-13 02:00 | 20.0753 | 0.009702% | 20.9654 | 21.8949 | 22.8656 | 23.8793 | 0 | 0 | 0 | 0
2031-01-13 03:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-01-13 04:00 | 18.8535 | 0.009111% | 19.6893 | 20.5623 | 21.4739 | 22.4259 | 0 | 0 | 0 | 0
2031-01-13 05:00 | 19.2082 | 0.009283% | 20.0598 | 20.9491 | 21.8779 | 22.8479 | 0 | 0 | 0 | 0
2031-01-13 06:00 | 20.4301 | 0.009873% | 21.3358 | 22.2818 | 23.2696 | 24.3013 | 0 | 0 | 0 | 0
2031-01-13 07:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-01-13 08:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-01-13 09:00 | 27.5773 | 0.01333% | 28.7999 | 30.0768 | 31.4102 | 32.8028 | 0 | 0 | 0 | 0
2031-01-13 10:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-01-13 11:00 | 27.8926 | 0.01348% | 29.1292 | 30.4207 | 31.7694 | 33.1779 | 0 | 0 | 0 | 0
2031-01-13 12:00 | 28.2999 | 0.01368% | 29.5546 | 30.8649 | 32.2333 | 33.6624 | 0 | 0 | 0 | 0
2031-01-13 13:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-01-13 14:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-01-13 15:00 | 29.2721 | 0.01415% | 30.5699 | 31.9252 | 33.3406 | 34.8188 | 0 | 0 | 0 | 0
2031-01-13 16:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-01-13 17:00 | 31.7553 | 0.01535% | 33.1631 | 34.6334 | 36.1689 | 37.7725 | 0 | 0 | 0 | 0.69523
2031-01-13 18:00 | 33.5946 | 0.01624% | 35.0841 | 36.6395 | 38.2639 | 39.9604 | 0 | 0 | 1.1375 | 2.6643
2031-01-13 19:00 | 33.8574 | 0.01636% | 35.3585 | 36.9261 | 38.5632 | 40.2729 | 0 | 0 | 1.4069 | 2.9456
2031-01-13 20:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-01-13 21:00 | 31.256 | 0.0151% | 32.6418 | 34.0889 | 35.6003 | 37.1786 | 0 | 0 | 0 | 0.16075
2031-01-13 22:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-01-13 23:00 | 27.8138 | 0.01344% | 29.0469 | 30.3347 | 31.6796 | 33.0841 | 0 | 0 | 0 | 0
2031-01-14 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-01-14 01:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-01-14 02:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-01-14 03:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-01-14 04:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-01-14 05:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-01-14 06:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-01-14 07:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-01-14 08:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0
2031-01-14 09:00 | 30.0473 | 0.01452% | 31.3794 | 32.7707 | 34.2235 | 35.7409 | 0 | 0 | 0 | 0
2031-01-14 10:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-01-14 11:00 | 30.3232 | 0.01465% | 31.6676 | 33.0716 | 34.5378 | 36.069 | 0 | 0 | 0 | 0
2031-01-14 12:00 | 29.9028 | 0.01445% | 31.2285 | 32.613 | 34.0589 | 35.5689 | 0 | 0 | 0 | 0
2031-01-14 13:00 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-01-14 14:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-01-14 15:00 | 29.1802 | 0.0141% | 30.4739 | 31.8249 | 33.2359 | 34.7094 | 0 | 0 | 0 | 0
2031-01-14 16:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-01-14 17:00 | 31.1903 | 0.01507% | 32.5731 | 34.0173 | 35.5254 | 37.1005 | 0 | 0 | 0 | 0.090429
2031-01-14 18:00 | 34.8822 | 0.01686% | 36.4287 | 38.0438 | 39.7304 | 41.4919 | 0 | 0.93939 | 2.4574 | 4.0427
2031-01-14 19:00 | 34.3304 | 0.01659% | 35.8524 | 37.4419 | 39.1019 | 40.8355 | 0 | 0.39775 | 1.8917 | 3.452
2031-01-14 20:00 | 32.8983 | 0.0159% | 34.3569 | 35.8801 | 37.4708 | 39.1321 | 0 | 0 | 0.42374 | 1.9189
2031-01-14 21:00 | 32.3465 | 0.01563% | 33.7806 | 35.2782 | 36.8423 | 38.4757 | 0 | 0 | 0 | 1.3282
2031-01-14 22:00 | 31.4794 | 0.01521% | 32.875 | 34.3325 | 35.8547 | 37.4443 | 0 | 0 | 0 | 0.39986
2031-01-14 23:00 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-01-15 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-01-15 01:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-01-15 02:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-01-15 03:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-01-15 04:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-01-15 05:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-01-15 06:00 | 23.7803 | 0.01149% | 24.8346 | 25.9357 | 27.0855 | 28.2864 | 0 | 0 | 0 | 0
2031-01-15 07:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-01-15 08:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-01-15 09:00 | 30.2575 | 0.01462% | 31.599 | 32.9999 | 34.463 | 35.9909 | 0 | 0 | 0 | 0
2031-01-15 10:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-01-15 11:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-01-15 12:00 | 31.0589 | 0.01501% | 32.4359 | 33.874 | 35.3758 | 36.9442 | 0 | 0 | 0 | 0
2031-01-15 13:00 | 31.1772 | 0.01507% | 32.5594 | 34.003 | 35.5105 | 37.0848 | 0 | 0 | 0 | 0.076364
2031-01-15 14:00 | 30.586 | 0.01478% | 31.942 | 33.3581 | 34.8371 | 36.3816 | 0 | 0 | 0 | 0
2031-01-15 15:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-01-15 16:00 | 30.783 | 0.01488% | 32.1478 | 33.5731 | 35.0616 | 36.616 | 0 | 0 | 0 | 0
2031-01-15 17:00 | 32.399 | 0.01566% | 33.8355 | 35.3356 | 36.9022 | 38.5382 | 0 | 0 | 0 | 1.3844
2031-01-15 18:00 | 34.3566 | 0.0166% | 35.8799 | 37.4706 | 39.1319 | 40.8668 | 0 | 0.42354 | 1.9187 | 3.4801
2031-01-15 19:00 | 34.1202 | 0.01649% | 35.6329 | 37.2127 | 38.8625 | 40.5855 | 0 | 0.19141 | 1.6763 | 3.2269
2031-01-15 20:00 | 32.6355 | 0.01577% | 34.0824 | 35.5935 | 37.1715 | 38.8195 | 0 | 0 | 0.15438 | 1.6376
2031-01-15 21:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-01-15 22:00 | 31.2823 | 0.01512% | 32.6692 | 34.1176 | 35.6302 | 37.2099 | 0 | 0 | 0 | 0.18888
2031-01-15 23:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-01-16 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-01-16 01:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-01-16 02:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-01-16 03:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-01-16 04:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-01-16 05:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-01-16 06:00 | 23.1365 | 0.01118% | 24.1623 | 25.2335 | 26.3523 | 27.5206 | 0 | 0 | 0 | 0
2031-01-16 07:00 | 25.6985 | 0.01242% | 26.8379 | 28.0277 | 29.2703 | 30.568 | 0 | 0 | 0 | 0
2031-01-16 08:00 | 29.0488 | 0.01404% | 30.3367 | 31.6816 | 33.0863 | 34.5531 | 0 | 0 | 0 | 0
2031-01-16 09:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-01-16 10:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-01-16 11:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-01-16 12:00 | 30.4677 | 0.01472% | 31.8185 | 33.2292 | 34.7024 | 36.2409 | 0 | 0 | 0 | 0
2031-01-16 13:00 | 30.2049 | 0.0146% | 31.5441 | 32.9426 | 34.4031 | 35.9284 | 0 | 0 | 0 | 0
2031-01-16 14:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-01-16 15:00 | 30.6648 | 0.01482% | 32.0243 | 33.4441 | 34.9269 | 36.4754 | 0 | 0 | 0 | 0
2031-01-16 16:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-01-16 17:00 | 31.0589 | 0.01501% | 32.4359 | 33.874 | 35.3758 | 36.9442 | 0 | 0 | 0 | 0
2031-01-16 18:00 | 33.9756 | 0.01642% | 35.482 | 37.0551 | 38.6979 | 40.4136 | 0 | 0.04955 | 1.5281 | 3.0722
2031-01-16 19:00 | 33.4632 | 0.01617% | 34.9468 | 36.4962 | 38.1143 | 39.8041 | 0 | 0 | 1.0029 | 2.5237
2031-01-16 20:00 | 32.2677 | 0.01559% | 33.6983 | 35.1923 | 36.7525 | 38.382 | 0 | 0 | 0 | 1.2438
2031-01-16 21:00 | 31.9523 | 0.01544% | 33.369 | 34.8484 | 36.3934 | 38.0069 | 0 | 0 | 0 | 0.9062
2031-01-16 22:00 | 30.6385 | 0.01481% | 31.9969 | 33.4155 | 34.8969 | 36.4441 | 0 | 0 | 0 | 0
2031-01-16 23:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0
2031-01-17 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-01-17 01:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-01-17 02:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-01-17 03:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-01-17 04:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-01-17 05:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-01-17 06:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-01-17 07:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-01-17 08:00 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-01-17 09:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-01-17 10:00 | 28.0897 | 0.01357% | 29.335 | 30.6356 | 31.9939 | 33.4123 | 0 | 0 | 0 | 0
2031-01-17 11:00 | 28.3393 | 0.0137% | 29.5957 | 30.9079 | 32.2782 | 33.7092 | 0 | 0 | 0 | 0
2031-01-17 12:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-01-17 13:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-01-17 14:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-01-17 15:00 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-01-17 16:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-01-17 17:00 | 30.2444 | 0.01462% | 31.5853 | 32.9856 | 34.448 | 35.9753 | 0 | 0 | 0 | 0
2031-01-17 18:00 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-01-17 19:00 | 31.6239 | 0.01528% | 33.0259 | 34.4901 | 36.0193 | 37.6162 | 0 | 0 | 0 | 0.55458
2031-01-17 20:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-01-17 21:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-01-17 22:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-01-17 23:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-01-18 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-01-18 01:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-01-18 02:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-01-18 03:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-01-18 04:00 | 19.3264 | 0.00934% | 20.1833 | 21.0781 | 22.0126 | 22.9885 | 0 | 0 | 0 | 0
2031-01-18 05:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-01-18 06:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-01-18 07:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-01-18 08:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-01-18 09:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-01-18 10:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-01-18 11:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-01-18 12:00 | 28.2079 | 0.01363% | 29.4585 | 30.7646 | 32.1285 | 33.553 | 0 | 0 | 0 | 0
2031-01-18 13:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-01-18 14:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-01-18 15:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-01-18 16:00 | 28.694 | 0.01387% | 29.9662 | 31.2948 | 32.6822 | 34.1312 | 0 | 0 | 0 | 0
2031-01-18 17:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-01-18 18:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-01-18 19:00 | 31.9261 | 0.01543% | 33.3415 | 34.8197 | 36.3635 | 37.9756 | 0 | 0 | 0 | 0.87807
2031-01-18 20:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-01-18 21:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-01-18 22:00 | 28.6021 | 0.01382% | 29.8702 | 31.1945 | 32.5775 | 34.0218 | 0 | 0 | 0 | 0
2031-01-18 23:00 | 26.7759 | 0.01294% | 27.963 | 29.2027 | 30.4974 | 31.8495 | 0 | 0 | 0 | 0
2031-01-19 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-01-19 01:00 | 23.938 | 0.01157% | 24.9993 | 26.1076 | 27.2651 | 28.4739 | 0 | 0 | 0 | 0
2031-01-19 02:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-01-19 03:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-01-19 04:00 | 21.2446 | 0.01027% | 22.1865 | 23.1702 | 24.1974 | 25.2702 | 0 | 0 | 0 | 0
2031-01-19 05:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-01-19 06:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-01-19 07:00 | 22.4665 | 0.01086% | 23.4625 | 24.5028 | 25.5891 | 26.7236 | 0 | 0 | 0 | 0
2031-01-19 08:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-01-19 09:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-01-19 10:00 | 27.4853 | 0.01328% | 28.7039 | 29.9765 | 31.3055 | 32.6934 | 0 | 0 | 0 | 0
2031-01-19 11:00 | 29.3115 | 0.01417% | 30.6111 | 31.9682 | 33.3855 | 34.8657 | 0 | 0 | 0 | 0
2031-01-19 12:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-01-19 13:00 | 30.3889 | 0.01469% | 31.7362 | 33.1432 | 34.6126 | 36.1472 | 0 | 0 | 0 | 0
2031-01-19 14:00 | 30.5334 | 0.01476% | 31.8871 | 33.3008 | 34.7772 | 36.3191 | 0 | 0 | 0 | 0
2031-01-19 15:00 | 30.7436 | 0.01486% | 32.1066 | 33.5301 | 35.0167 | 36.5691 | 0 | 0 | 0 | 0
2031-01-19 16:00 | 31.5582 | 0.01525% | 32.9573 | 34.4185 | 35.9445 | 37.5381 | 0 | 0 | 0 | 0.48425
2031-01-19 17:00 | 33.6209 | 0.01625% | 35.1115 | 36.6682 | 38.2939 | 39.9916 | 0 | 0 | 1.1645 | 2.6925
2031-01-19 18:00 | 35.4734 | 0.01714% | 37.0461 | 38.6886 | 40.4038 | 42.1952 | 0.041512 | 1.5197 | 3.0635 | 4.6756
2031-01-19 19:00 | 35.0924 | 0.01696% | 36.6482 | 38.273 | 39.9699 | 41.7419 | 0 | 1.1457 | 2.6729 | 4.2677
2031-01-19 20:00 | 33.6735 | 0.01627% | 35.1664 | 36.7255 | 38.3537 | 40.0541 | 0 | 0 | 1.2183 | 2.7487
2031-01-19 21:00 | 32.3596 | 0.01564% | 33.7943 | 35.2926 | 36.8573 | 38.4914 | 0 | 0 | 0 | 1.3422
2031-01-19 22:00 | 31.1772 | 0.01507% | 32.5594 | 34.003 | 35.5105 | 37.0848 | 0 | 0 | 0 | 0.076364
2031-01-19 23:00 | 28.8254 | 0.01393% | 30.1034 | 31.438 | 32.8319 | 34.2875 | 0 | 0 | 0 | 0
2031-01-20 | 26.3686 | 0.01274% | 27.5376 | 28.7585 | 30.0335 | 31.3651 | 0 | 0 | 0 | 0
2031-01-20 01:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-01-20 02:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-01-20 03:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-01-20 04:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-01-20 05:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-01-20 06:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-01-20 07:00 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-01-20 08:00 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-01-20 09:00 | 30.783 | 0.01488% | 32.1478 | 33.5731 | 35.0616 | 36.616 | 0 | 0 | 0 | 0
2031-01-20 10:00 | 30.7699 | 0.01487% | 32.1341 | 33.5588 | 35.0466 | 36.6004 | 0 | 0 | 0 | 0
2031-01-20 11:00 | 31.2429 | 0.0151% | 32.628 | 34.0746 | 35.5853 | 37.163 | 0 | 0 | 0 | 0.14669
2031-01-20 12:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-01-20 13:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-01-20 14:00 | 31.348 | 0.01515% | 32.7378 | 34.1892 | 35.705 | 37.288 | 0 | 0 | 0 | 0.25921
2031-01-20 15:00 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-01-20 16:00 | 32.4253 | 0.01567% | 33.8629 | 35.3642 | 36.9321 | 38.5695 | 0 | 0 | 0 | 1.4125
2031-01-20 17:00 | 34.1727 | 0.01651% | 35.6878 | 37.27 | 38.9224 | 40.648 | 0 | 0.24299 | 1.7301 | 3.2832
2031-01-20 18:00 | 36.4982 | 0.01764% | 38.1163 | 39.8062 | 41.5711 | 43.4141 | 1.0047 | 2.5256 | 4.114 | 5.7727
2031-01-20 19:00 | 36.4851 | 0.01763% | 38.1026 | 39.7919 | 41.5561 | 43.3985 | 0.99236 | 2.5127 | 4.1005 | 5.7586
2031-01-20 20:00 | 35.6573 | 0.01723% | 37.2382 | 38.8892 | 40.6133 | 42.4139 | 0.21439 | 1.7003 | 3.252 | 4.8725
2031-01-20 21:00 | 35.1449 | 0.01698% | 36.7031 | 38.3303 | 40.0297 | 41.8045 | 0 | 1.1973 | 2.7268 | 4.324
2031-01-20 22:00 | 34.2121 | 0.01653% | 35.7289 | 37.313 | 38.9673 | 40.6949 | 0 | 0.28168 | 1.7705 | 3.3254
2031-01-20 23:00 | 31.7159 | 0.01533% | 33.122 | 34.5904 | 36.124 | 37.7256 | 0 | 0 | 0 | 0.65303
2031-01-21 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-01-21 01:00 | 26.9466 | 0.01302% | 28.1413 | 29.389 | 30.692 | 32.0527 | 0 | 0 | 0 | 0
2031-01-21 02:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-01-21 03:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-01-21 04:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-01-21 05:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-01-21 06:00 | 25.6328 | 0.01239% | 26.7693 | 27.9561 | 29.1955 | 30.4899 | 0 | 0 | 0 | 0
2031-01-21 07:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-01-21 08:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-01-21 09:00 | 32.4516 | 0.01568% | 33.8903 | 35.3929 | 36.962 | 38.6007 | 0 | 0 | 0 | 1.4407
2031-01-21 10:00 | 32.2545 | 0.01559% | 33.6845 | 35.1779 | 36.7376 | 38.3663 | 0 | 0 | 0 | 1.2297
2031-01-21 11:00 | 32.0706 | 0.0155% | 33.4924 | 34.9773 | 36.5281 | 38.1475 | 0 | 0 | 0 | 1.0328
2031-01-21 12:00 | 32.3859 | 0.01565% | 33.8217 | 35.3212 | 36.8872 | 38.5226 | 0 | 0 | 0 | 1.3703
2031-01-21 13:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-01-21 14:00 | 32.5567 | 0.01573% | 34.0001 | 35.5075 | 37.0817 | 38.7258 | 0 | 0 | 0.07357 | 1.5532
2031-01-21 15:00 | 32.7275 | 0.01582% | 34.1785 | 35.6938 | 37.2763 | 38.9289 | 0 | 0 | 0.24865 | 1.736
2031-01-21 16:00 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-01-21 17:00 | 35.2106 | 0.01702% | 36.7717 | 38.402 | 40.1046 | 41.8826 | 0 | 1.2618 | 2.7941 | 4.3943
2031-01-21 18:00 | 37.4441 | 0.0181% | 39.1042 | 40.8379 | 42.6485 | 44.5393 | 1.8938 | 3.4541 | 5.0836 | 6.7854
2031-01-21 19:00 | 36.8135 | 0.01779% | 38.4456 | 40.1501 | 41.9302 | 43.7892 | 1.3011 | 2.8351 | 4.4372 | 6.1103
2031-01-21 20:00 | 35.8281 | 0.01731% | 37.4166 | 39.0755 | 40.8079 | 42.6171 | 0.37493 | 1.8679 | 3.4271 | 5.0554
2031-01-21 21:00 | 35.1318 | 0.01698% | 36.6894 | 38.316 | 40.0148 | 41.7888 | 0 | 1.1844 | 2.7133 | 4.3099
2031-01-21 22:00 | 34.1727 | 0.01651% | 35.6878 | 37.27 | 38.9224 | 40.648 | 0 | 0.24299 | 1.7301 | 3.2832
2031-01-21 23:00 | 32.0706 | 0.0155% | 33.4924 | 34.9773 | 36.5281 | 38.1475 | 0 | 0 | 0 | 1.0328
2031-01-22 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-01-22 01:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-01-22 02:00 | 26.2897 | 0.0127% | 27.4553 | 28.6725 | 29.9437 | 31.2713 | 0 | 0 | 0 | 0
2031-01-22 03:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-01-22 04:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-01-22 05:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-01-22 06:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-01-22 07:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-01-22 08:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-01-22 09:00 | 33.6078 | 0.01624% | 35.0978 | 36.6538 | 38.2789 | 39.976 | 0 | 0 | 1.151 | 2.6784
2031-01-22 10:00 | 33.7654 | 0.01632% | 35.2624 | 36.8258 | 38.4585 | 40.1635 | 0 | 0 | 1.3126 | 2.8472
2031-01-22 11:00 | 33.726 | 0.0163% | 35.2213 | 36.7828 | 38.4136 | 40.1166 | 0 | 0 | 1.2722 | 2.805
2031-01-22 12:00 | 34.672 | 0.01676% | 36.2092 | 37.8145 | 39.491 | 41.2419 | 0 | 0.73305 | 2.2419 | 3.8177
2031-01-22 13:00 | 34.7639 | 0.0168% | 36.3052 | 37.9148 | 39.5958 | 41.3512 | 0 | 0.82332 | 2.3362 | 3.9161
2031-01-22 14:00 | 34.7902 | 0.01681% | 36.3326 | 37.9435 | 39.6257 | 41.3825 | 0 | 0.84911 | 2.3631 | 3.9443
2031-01-22 15:00 | 34.2384 | 0.01655% | 35.7564 | 37.3416 | 38.9972 | 40.7261 | 0 | 0.30747 | 1.7975 | 3.3535
2031-01-22 16:00 | 34.488 | 0.01667% | 36.0171 | 37.6139 | 39.2815 | 41.0231 | 0 | 0.5525 | 2.0534 | 3.6208
2031-01-22 17:00 | 36.0121 | 0.0174% | 37.6087 | 39.2761 | 41.0174 | 42.8359 | 0.54781 | 2.0485 | 3.6156 | 5.2523
2031-01-22 18:00 | 37.6675 | 0.0182% | 39.3375 | 41.0815 | 42.9029 | 44.805 | 2.1037 | 3.6734 | 5.3126 | 7.0245
2031-01-22 19:00 | 37.6281 | 0.01818% | 39.2963 | 41.0385 | 42.858 | 44.7581 | 2.0667 | 3.6347 | 5.2722 | 6.9823
2031-01-22 20:00 | 36.3537 | 0.01757% | 37.9654 | 39.6486 | 41.4065 | 43.2422 | 0.86888 | 2.3838 | 3.9658 | 5.618
2031-01-22 21:00 | 35.2501 | 0.01704% | 36.8129 | 38.445 | 40.1494 | 41.9295 | 0 | 1.3005 | 2.8345 | 4.4365
2031-01-22 22:00 | 33.9494 | 0.01641% | 35.4545 | 37.0264 | 38.668 | 40.3823 | 0 | 0.023757 | 1.5012 | 3.0441
2031-01-22 23:00 | 32.018 | 0.01547% | 33.4376 | 34.92 | 36.4682 | 38.085 | 0 | 0 | 0 | 0.97653
2031-01-23 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-01-23 01:00 | 26.4343 | 0.01277% | 27.6062 | 28.8302 | 30.1083 | 31.4432 | 0 | 0 | 0 | 0
2031-01-23 02:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-01-23 03:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-01-23 04:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-01-23 05:00 | 23.938 | 0.01157% | 24.9993 | 26.1076 | 27.2651 | 28.4739 | 0 | 0 | 0 | 0
2031-01-23 06:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-01-23 07:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-01-23 08:00 | 29.8896 | 0.01444% | 31.2148 | 32.5987 | 34.044 | 35.5533 | 0 | 0 | 0 | 0
2031-01-23 09:00 | 30.9407 | 0.01495% | 32.3125 | 33.745 | 35.2411 | 36.8035 | 0 | 0 | 0 | 0
2031-01-23 10:00 | 31.637 | 0.01529% | 33.0397 | 34.5045 | 36.0342 | 37.6318 | 0 | 0 | 0 | 0.56864
2031-01-23 11:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-01-23 12:00 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-01-23 13:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-01-23 14:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-01-23 15:00 | 31.7684 | 0.01535% | 33.1769 | 34.6478 | 36.1839 | 37.7881 | 0 | 0 | 0 | 0.70929
2031-01-23 16:00 | 31.5056 | 0.01523% | 32.9024 | 34.3612 | 35.8846 | 37.4755 | 0 | 0 | 0 | 0.42799
2031-01-23 17:00 | 32.1363 | 0.01553% | 33.561 | 35.049 | 36.6029 | 38.2257 | 0 | 0 | 0 | 1.1031
2031-01-23 18:00 | 34.7114 | 0.01677% | 36.2503 | 37.8575 | 39.5359 | 41.2887 | 0 | 0.77174 | 2.2823 | 3.8599
2031-01-23 19:00 | 34.0151 | 0.01644% | 35.5231 | 37.098 | 38.7428 | 40.4605 | 0 | 0.088238 | 1.5685 | 3.1144
2031-01-23 20:00 | 33.2793 | 0.01608% | 34.7548 | 36.2956 | 37.9048 | 39.5853 | 0 | 0 | 0.81431 | 2.3268
2031-01-23 21:00 | 32.6224 | 0.01577% | 34.0687 | 35.5792 | 37.1566 | 38.8039 | 0 | 0 | 0.14091 | 1.6235
2031-01-23 22:00 | 31.1378 | 0.01505% | 32.5183 | 33.96 | 35.4656 | 37.038 | 0 | 0 | 0 | 0.034169
2031-01-23 23:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-01-24 | 27.0518 | 0.01307% | 28.2511 | 29.5036 | 30.8117 | 32.1777 | 0 | 0 | 0 | 0
2031-01-24 01:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-01-24 02:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-01-24 03:00 | 22.9526 | 0.01109% | 23.9702 | 25.0329 | 26.1428 | 27.3018 | 0 | 0 | 0 | 0
2031-01-24 04:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-01-24 05:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-01-24 06:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-01-24 07:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-01-24 08:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-01-24 09:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-01-24 10:00 | 31.4925 | 0.01522% | 32.8887 | 34.3469 | 35.8696 | 37.4599 | 0 | 0 | 0 | 0.41393
2031-01-24 11:00 | 30.9407 | 0.01495% | 32.3125 | 33.745 | 35.2411 | 36.8035 | 0 | 0 | 0 | 0
2031-01-24 12:00 | 30.7305 | 0.01485% | 32.0929 | 33.5158 | 35.0017 | 36.5535 | 0 | 0 | 0 | 0
2031-01-24 13:00 | 29.9159 | 0.01446% | 31.2422 | 32.6274 | 34.0739 | 35.5846 | 0 | 0 | 0 | 0
2031-01-24 14:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-01-24 15:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-01-24 16:00 | 28.8123 | 0.01392% | 30.0897 | 31.4237 | 32.8169 | 34.2718 | 0 | 0 | 0 | 0
2031-01-24 17:00 | 30.8619 | 0.01491% | 32.2301 | 33.6591 | 35.1513 | 36.7098 | 0 | 0 | 0 | 0
2031-01-24 18:00 | 32.3728 | 0.01564% | 33.808 | 35.3069 | 36.8722 | 38.507 | 0 | 0 | 0 | 1.3563
2031-01-24 19:00 | 32.6487 | 0.01578% | 34.0962 | 35.6078 | 37.1865 | 38.8352 | 0 | 0 | 0.16785 | 1.6516
2031-01-24 20:00 | 31.7684 | 0.01535% | 33.1769 | 34.6478 | 36.1839 | 37.7881 | 0 | 0 | 0 | 0.70929
2031-01-24 21:00 | 31.1378 | 0.01505% | 32.5183 | 33.96 | 35.4656 | 37.038 | 0 | 0 | 0 | 0.034169
2031-01-24 22:00 | 31.0458 | 0.015% | 32.4222 | 33.8597 | 35.3608 | 36.9286 | 0 | 0 | 0 | 0
2031-01-24 23:00 | 29.1933 | 0.01411% | 30.4876 | 31.8393 | 33.2509 | 34.725 | 0 | 0 | 0 | 0
2031-01-25 | 27.1437 | 0.01312% | 28.3471 | 29.6039 | 30.9164 | 32.2871 | 0 | 0 | 0 | 0
2031-01-25 01:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-01-25 02:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-01-25 03:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-01-25 04:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-01-25 05:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-01-25 06:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-01-25 07:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-01-25 08:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-01-25 09:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-01-25 10:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-01-25 11:00 | 30.3889 | 0.01469% | 31.7362 | 33.1432 | 34.6126 | 36.1472 | 0 | 0 | 0 | 0
2031-01-25 12:00 | 31.6502 | 0.0153% | 33.0534 | 34.5188 | 36.0492 | 37.6475 | 0 | 0 | 0 | 0.58271
2031-01-25 13:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-01-25 14:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-01-25 15:00 | 30.8881 | 0.01493% | 32.2576 | 33.6877 | 35.1813 | 36.741 | 0 | 0 | 0 | 0
2031-01-25 16:00 | 30.9144 | 0.01494% | 32.285 | 33.7164 | 35.2112 | 36.7723 | 0 | 0 | 0 | 0
2031-01-25 17:00 | 32.1494 | 0.01554% | 33.5748 | 35.0633 | 36.6178 | 38.2413 | 0 | 0 | 0 | 1.1172
2031-01-25 18:00 | 33.1216 | 0.01601% | 34.5901 | 36.1237 | 37.7252 | 39.3978 | 0 | 0 | 0.65269 | 2.158
2031-01-25 19:00 | 32.6618 | 0.01578% | 34.1099 | 35.6221 | 37.2015 | 38.8508 | 0 | 0 | 0.18131 | 1.6657
2031-01-25 20:00 | 31.3086 | 0.01513% | 32.6966 | 34.1462 | 35.6601 | 37.2411 | 0 | 0 | 0 | 0.21701
2031-01-25 21:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-01-25 22:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-01-25 23:00 | 26.9992 | 0.01305% | 28.1962 | 29.4463 | 30.7518 | 32.1152 | 0 | 0 | 0 | 0
2031-01-26 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-01-26 01:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-01-26 02:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-01-26 03:00 | 21.4943 | 0.01039% | 22.4472 | 23.4424 | 24.4817 | 25.5671 | 0 | 0 | 0 | 0
2031-01-26 04:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-01-26 05:00 | 20.8111 | 0.01006% | 21.7337 | 22.6973 | 23.7036 | 24.7545 | 0 | 0 | 0 | 0
2031-01-26 06:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-01-26 07:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-01-26 08:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-01-26 09:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-01-26 10:00 | 25.3569 | 0.01225% | 26.4811 | 27.6552 | 28.8813 | 30.1617 | 0 | 0 | 0 | 0
2031-01-26 11:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-01-26 12:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-01-26 13:00 | 28.5889 | 0.01382% | 29.8564 | 31.1801 | 32.5625 | 34.0062 | 0 | 0 | 0 | 0
2031-01-26 14:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-01-26 15:00 | 29.1539 | 0.01409% | 30.4464 | 31.7963 | 33.206 | 34.6782 | 0 | 0 | 0 | 0
2031-01-26 16:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-01-26 17:00 | 31.8341 | 0.01538% | 33.2455 | 34.7194 | 36.2587 | 37.8662 | 0 | 0 | 0 | 0.77962
2031-01-26 18:00 | 34.0676 | 0.01646% | 35.578 | 37.1554 | 38.8026 | 40.523 | 0 | 0.13982 | 1.6224 | 3.1707
2031-01-26 19:00 | 33.9099 | 0.01639% | 35.4134 | 36.9834 | 38.6231 | 40.3354 | 0 | 0 | 1.4608 | 3.0019
2031-01-26 20:00 | 32.583 | 0.01575% | 34.0276 | 35.5362 | 37.1117 | 38.757 | 0 | 0 | 0.10051 | 1.5813
2031-01-26 21:00 | 31.3611 | 0.01516% | 32.7515 | 34.2036 | 35.72 | 37.3036 | 0 | 0 | 0 | 0.27328
2031-01-26 22:00 | 30.113 | 0.01455% | 31.448 | 32.8423 | 34.2984 | 35.819 | 0 | 0 | 0 | 0
2031-01-26 23:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-01-27 | 25.0547 | 0.01211% | 26.1655 | 27.3256 | 28.5371 | 29.8023 | 0 | 0 | 0 | 0
2031-01-27 01:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-01-27 02:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-01-27 03:00 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-01-27 04:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-01-27 05:00 | 21.1001 | 0.0102% | 22.0356 | 23.0125 | 24.0328 | 25.0983 | 0 | 0 | 0 | 0
2031-01-27 06:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-01-27 07:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-01-27 08:00 | 28.0371 | 0.01355% | 29.2802 | 30.5783 | 31.934 | 33.3498 | 0 | 0 | 0 | 0
2031-01-27 09:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-01-27 10:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-01-27 11:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-01-27 12:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-01-27 13:00 | 30.0473 | 0.01452% | 31.3794 | 32.7707 | 34.2235 | 35.7409 | 0 | 0 | 0 | 0
2031-01-27 14:00 | 29.4955 | 0.01425% | 30.8032 | 32.1688 | 33.595 | 35.0845 | 0 | 0 | 0 | 0
2031-01-27 15:00 | 29.3641 | 0.01419% | 30.666 | 32.0255 | 33.4454 | 34.9282 | 0 | 0 | 0 | 0
2031-01-27 16:00 | 29.8634 | 0.01443% | 31.1873 | 32.57 | 34.014 | 35.5221 | 0 | 0 | 0 | 0
2031-01-27 17:00 | 32.5698 | 0.01574% | 34.0138 | 35.5218 | 37.0967 | 38.7414 | 0 | 0 | 0.087038 | 1.5673
2031-01-27 18:00 | 34.672 | 0.01676% | 36.2092 | 37.8145 | 39.491 | 41.2419 | 0 | 0.73305 | 2.2419 | 3.8177
2031-01-27 19:00 | 34.6194 | 0.01673% | 36.1543 | 37.7572 | 39.4312 | 41.1793 | 0 | 0.68146 | 2.188 | 3.7614
2031-01-27 20:00 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-01-27 21:00 | 31.9918 | 0.01546% | 33.4101 | 34.8914 | 36.4383 | 38.0538 | 0 | 0 | 0 | 0.9484
2031-01-27 22:00 | 30.5597 | 0.01477% | 31.9146 | 33.3295 | 34.8072 | 36.3503 | 0 | 0 | 0 | 0
2031-01-27 23:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-01-28 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-01-28 01:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-01-28 02:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-01-28 03:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-01-28 04:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-01-28 05:00 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-01-28 06:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-01-28 07:00 | 26.0007 | 0.01257% | 27.1534 | 28.3573 | 29.6145 | 30.9275 | 0 | 0 | 0 | 0
2031-01-28 08:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-01-28 09:00 | 29.2853 | 0.01415% | 30.5836 | 31.9396 | 33.3556 | 34.8344 | 0 | 0 | 0 | 0
2031-01-28 10:00 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-01-28 11:00 | 30.0736 | 0.01453% | 31.4069 | 32.7993 | 34.2535 | 35.7721 | 0 | 0 | 0 | 0
2031-01-28 12:00 | 30.6911 | 0.01483% | 32.0518 | 33.4728 | 34.9568 | 36.5066 | 0 | 0 | 0 | 0
2031-01-28 13:00 | 30.6648 | 0.01482% | 32.0243 | 33.4441 | 34.9269 | 36.4754 | 0 | 0 | 0 | 0
2031-01-28 14:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-01-28 15:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-01-28 16:00 | 30.9801 | 0.01497% | 32.3536 | 33.788 | 35.286 | 36.8504 | 0 | 0 | 0 | 0
2031-01-28 17:00 | 32.6749 | 0.01579% | 34.1236 | 35.6365 | 37.2164 | 38.8664 | 0 | 0 | 0.19478 | 1.6798
2031-01-28 18:00 | 34.8953 | 0.01686% | 36.4424 | 38.0581 | 39.7454 | 41.5075 | 0 | 0.95228 | 2.4709 | 4.0568
2031-01-28 19:00 | 34.3041 | 0.01658% | 35.825 | 37.4133 | 39.072 | 40.8043 | 0 | 0.37195 | 1.8648 | 3.4238
2031-01-28 20:00 | 32.399 | 0.01566% | 33.8355 | 35.3356 | 36.9022 | 38.5382 | 0 | 0 | 0 | 1.3844
2031-01-28 21:00 | 32.5304 | 0.01572% | 33.9727 | 35.4789 | 37.0518 | 38.6945 | 0 | 0 | 0.046635 | 1.5251
2031-01-28 22:00 | 30.7699 | 0.01487% | 32.1341 | 33.5588 | 35.0466 | 36.6004 | 0 | 0 | 0 | 0
2031-01-28 23:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-01-29 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-01-29 01:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-01-29 02:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-01-29 03:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-01-29 04:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-01-29 05:00 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-01-29 06:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-01-29 07:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-01-29 08:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-01-29 09:00 | 27.6824 | 0.01338% | 28.9097 | 30.1914 | 31.53 | 32.9278 | 0 | 0 | 0 | 0
2031-01-29 10:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-01-29 11:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-01-29 12:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-01-29 13:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-01-29 14:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-01-29 15:00 | 29.9553 | 0.01448% | 31.2834 | 32.6704 | 34.1188 | 35.6315 | 0 | 0 | 0 | 0
2031-01-29 16:00 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-01-29 17:00 | 31.8866 | 0.01541% | 33.3004 | 34.7767 | 36.3186 | 37.9288 | 0 | 0 | 0 | 0.83588
2031-01-29 18:00 | 34.7639 | 0.0168% | 36.3052 | 37.9148 | 39.5958 | 41.3512 | 0 | 0.82332 | 2.3362 | 3.9161
2031-01-29 19:00 | 34.4223 | 0.01664% | 35.9485 | 37.5422 | 39.2067 | 40.9449 | 0 | 0.48802 | 1.986 | 3.5504
2031-01-29 20:00 | 33.6866 | 0.01628% | 35.1801 | 36.7398 | 38.3687 | 40.0698 | 0 | 0 | 1.2318 | 2.7628
2031-01-29 21:00 | 32.6749 | 0.01579% | 34.1236 | 35.6365 | 37.2164 | 38.8664 | 0 | 0 | 0.19478 | 1.6798
2031-01-29 22:00 | 32.1757 | 0.01555% | 33.6022 | 35.092 | 36.6478 | 38.2726 | 0 | 0 | 0 | 1.1453
2031-01-29 23:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-01-30 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-01-30 01:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-01-30 02:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-01-30 03:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-01-30 04:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-01-30 05:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-01-30 06:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-01-30 07:00 | 26.2635 | 0.01269% | 27.4279 | 28.6439 | 29.9138 | 31.24 | 0 | 0 | 0 | 0
2031-01-30 08:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-01-30 09:00 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-01-30 10:00 | 30.2575 | 0.01462% | 31.599 | 32.9999 | 34.463 | 35.9909 | 0 | 0 | 0 | 0
2031-01-30 11:00 | 30.1655 | 0.01458% | 31.5029 | 32.8996 | 34.3582 | 35.8815 | 0 | 0 | 0 | 0
2031-01-30 12:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-01-30 13:00 | 29.9028 | 0.01445% | 31.2285 | 32.613 | 34.0589 | 35.5689 | 0 | 0 | 0 | 0
2031-01-30 14:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-01-30 15:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-01-30 16:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-01-30 17:00 | 31.3086 | 0.01513% | 32.6966 | 34.1462 | 35.6601 | 37.2411 | 0 | 0 | 0 | 0.21701
2031-01-30 18:00 | 32.583 | 0.01575% | 34.0276 | 35.5362 | 37.1117 | 38.757 | 0 | 0 | 0.10051 | 1.5813
2031-01-30 19:00 | 33.1348 | 0.01601% | 34.6038 | 36.138 | 37.7402 | 39.4134 | 0 | 0 | 0.66616 | 2.1721
2031-01-30 20:00 | 31.9655 | 0.01545% | 33.3827 | 34.8627 | 36.4083 | 38.0225 | 0 | 0 | 0 | 0.92027
2031-01-30 21:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-01-30 22:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-01-30 23:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0
2031-01-31 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-01-31 01:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-01-31 02:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-01-31 03:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-01-31 04:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-01-31 05:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-01-31 06:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-01-31 07:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-01-31 08:00 | 27.9583 | 0.01351% | 29.1978 | 30.4923 | 31.8442 | 33.256 | 0 | 0 | 0 | 0
2031-01-31 09:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-01-31 10:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0
2031-01-31 11:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-01-31 12:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-01-31 13:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-01-31 14:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-01-31 15:00 | 28.6021 | 0.01382% | 29.8702 | 31.1945 | 32.5775 | 34.0218 | 0 | 0 | 0 | 0
2031-01-31 16:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-01-31 17:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-01-31 18:00 | 30.6779 | 0.01483% | 32.038 | 33.4585 | 34.9418 | 36.491 | 0 | 0 | 0 | 0
2031-01-31 19:00 | 30.7173 | 0.01484% | 32.0792 | 33.5014 | 34.9867 | 36.5379 | 0 | 0 | 0 | 0
2031-01-31 20:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-01-31 21:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-01-31 22:00 | 28.7729 | 0.0139% | 30.0485 | 31.3807 | 32.772 | 34.225 | 0 | 0 | 0 | 0
2031-01-31 23:00 | 27.3277 | 0.01321% | 28.5392 | 29.8045 | 31.1259 | 32.5059 | 0 | 0 | 0 | 0
2031-02-01 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-02-01 01:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-02-01 02:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-02-01 03:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-02-01 04:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-02-01 05:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-02-01 06:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-02-01 07:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-02-01 08:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-02-01 09:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-02-01 10:00 | 29.167 | 0.0141% | 30.4601 | 31.8106 | 33.2209 | 34.6938 | 0 | 0 | 0 | 0
2031-02-01 11:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-02-01 12:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-02-01 13:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-02-01 14:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-02-01 15:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-02-01 16:00 | 29.9947 | 0.0145% | 31.3246 | 32.7133 | 34.1637 | 35.6783 | 0 | 0 | 0 | 0
2031-02-01 17:00 | 30.8487 | 0.01491% | 32.2164 | 33.6447 | 35.1364 | 36.6942 | 0 | 0 | 0 | 0
2031-02-01 18:00 | 33.3581 | 0.01612% | 34.8371 | 36.3816 | 37.9946 | 39.6791 | 0 | 0 | 0.89512 | 2.4112
2031-02-01 19:00 | 33.634 | 0.01625% | 35.1252 | 36.6825 | 38.3088 | 40.0073 | 0 | 0 | 1.1779 | 2.7065
2031-02-01 20:00 | 32.7012 | 0.0158% | 34.151 | 35.6651 | 37.2464 | 38.8977 | 0 | 0 | 0.22172 | 1.7079
2031-02-01 21:00 | 32.4253 | 0.01567% | 33.8629 | 35.3642 | 36.9321 | 38.5695 | 0 | 0 | 0 | 1.4125
2031-02-01 22:00 | 31.3611 | 0.01516% | 32.7515 | 34.2036 | 35.72 | 37.3036 | 0 | 0 | 0 | 0.27328
2031-02-01 23:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-02-02 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-02-02 01:00 | 26.6051 | 0.01286% | 27.7846 | 29.0164 | 30.3029 | 31.6464 | 0 | 0 | 0 | 0
2031-02-02 02:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-02-02 03:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-02-02 04:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-02-02 05:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-02-02 06:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-02-02 07:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-02-02 08:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-02-02 09:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-02-02 10:00 | 29.2984 | 0.01416% | 30.5974 | 31.9539 | 33.3706 | 34.8501 | 0 | 0 | 0 | 0
2031-02-02 11:00 | 30.5071 | 0.01474% | 31.8597 | 33.2722 | 34.7473 | 36.2878 | 0 | 0 | 0 | 0
2031-02-02 12:00 | 31.5056 | 0.01523% | 32.9024 | 34.3612 | 35.8846 | 37.4755 | 0 | 0 | 0 | 0.42799
2031-02-02 13:00 | 32.0706 | 0.0155% | 33.4924 | 34.9773 | 36.5281 | 38.1475 | 0 | 0 | 0 | 1.0328
2031-02-02 14:00 | 32.2545 | 0.01559% | 33.6845 | 35.1779 | 36.7376 | 38.3663 | 0 | 0 | 0 | 1.2297
2031-02-02 15:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-02-02 16:00 | 32.4779 | 0.0157% | 33.9178 | 35.4215 | 36.992 | 38.632 | 0 | 0 | 0 | 1.4688
2031-02-02 17:00 | 34.5931 | 0.01672% | 36.1268 | 37.7285 | 39.4012 | 41.1481 | 0 | 0.65567 | 2.1611 | 3.7333
2031-02-02 18:00 | 35.6311 | 0.01722% | 37.2108 | 38.8605 | 40.5834 | 42.3827 | 0.1897 | 1.6745 | 3.2251 | 4.8444
2031-02-02 19:00 | 35.7756 | 0.01729% | 37.3617 | 39.0181 | 40.748 | 42.5546 | 0.32553 | 1.8163 | 3.3732 | 4.9991
2031-02-02 20:00 | 34.3304 | 0.01659% | 35.8524 | 37.4419 | 39.1019 | 40.8355 | 0 | 0.39775 | 1.8917 | 3.452
2031-02-02 21:00 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-02-02 22:00 | 31.1246 | 0.01504% | 32.5045 | 33.9456 | 35.4506 | 37.0223 | 0 | 0 | 0 | 0.020104
2031-02-02 23:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-02-03 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-02-03 01:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-02-03 02:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-02-03 03:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-02-03 04:00 | 20.7979 | 0.01005% | 21.72 | 22.683 | 23.6886 | 24.7389 | 0 | 0 | 0 | 0
2031-02-03 05:00 | 20.8899 | 0.0101% | 21.8161 | 22.7833 | 23.7934 | 24.8483 | 0 | 0 | 0 | 0
2031-02-03 06:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-02-03 07:00 | 25.3175 | 0.01224% | 26.44 | 27.6122 | 28.8364 | 30.1148 | 0 | 0 | 0 | 0
2031-02-03 08:00 | 28.024 | 0.01354% | 29.2664 | 30.564 | 31.919 | 33.3342 | 0 | 0 | 0 | 0
2031-02-03 09:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-02-03 10:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-02-03 11:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-02-03 12:00 | 30.0341 | 0.01451% | 31.3657 | 32.7563 | 34.2086 | 35.7252 | 0 | 0 | 0 | 0
2031-02-03 13:00 | 29.9028 | 0.01445% | 31.2285 | 32.613 | 34.0589 | 35.5689 | 0 | 0 | 0 | 0
2031-02-03 14:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-02-03 15:00 | 29.0488 | 0.01404% | 30.3367 | 31.6816 | 33.0863 | 34.5531 | 0 | 0 | 0 | 0
2031-02-03 16:00 | 29.6531 | 0.01433% | 30.9678 | 32.3408 | 33.7746 | 35.272 | 0 | 0 | 0 | 0
2031-02-03 17:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-02-03 18:00 | 32.9246 | 0.01591% | 34.3843 | 35.9087 | 37.5007 | 39.1634 | 0 | 0 | 0.45067 | 1.947
2031-02-03 19:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-02-03 20:00 | 31.0064 | 0.01498% | 32.3811 | 33.8167 | 35.3159 | 36.8817 | 0 | 0 | 0 | 0
2031-02-03 21:00 | 30.4414 | 0.01471% | 31.7911 | 33.2005 | 34.6725 | 36.2097 | 0 | 0 | 0 | 0
2031-02-03 22:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-02-03 23:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-02-04 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-02-04 01:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-02-04 02:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-02-04 03:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-02-04 04:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-02-04 05:00 | 20.2067 | 0.009765% | 21.1026 | 22.0382 | 23.0152 | 24.0356 | 0 | 0 | 0 | 0
2031-02-04 06:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-02-04 07:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-02-04 08:00 | 27.1174 | 0.0131% | 28.3197 | 29.5753 | 30.8865 | 32.2558 | 0 | 0 | 0 | 0
2031-02-04 09:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-02-04 10:00 | 28.1685 | 0.01361% | 29.4174 | 30.7216 | 32.0836 | 33.5061 | 0 | 0 | 0 | 0
2031-02-04 11:00 | 28.8648 | 0.01395% | 30.1446 | 31.481 | 32.8768 | 34.3344 | 0 | 0 | 0 | 0
2031-02-04 12:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-02-04 13:00 | 29.167 | 0.0141% | 30.4601 | 31.8106 | 33.2209 | 34.6938 | 0 | 0 | 0 | 0
2031-02-04 14:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-02-04 15:00 | 28.313 | 0.01368% | 29.5683 | 30.8792 | 32.2482 | 33.678 | 0 | 0 | 0 | 0
2031-02-04 16:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-02-04 17:00 | 30.6122 | 0.01479% | 31.9694 | 33.3868 | 34.867 | 36.4129 | 0 | 0 | 0 | 0
2031-02-04 18:00 | 33.2793 | 0.01608% | 34.7548 | 36.2956 | 37.9048 | 39.5853 | 0 | 0 | 0.81431 | 2.3268
2031-02-04 19:00 | 33.9888 | 0.01643% | 35.4957 | 37.0694 | 38.7129 | 40.4292 | 0 | 0.062446 | 1.5416 | 3.0863
2031-02-04 20:00 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-02-04 21:00 | 32.4385 | 0.01568% | 33.8766 | 35.3786 | 36.9471 | 38.5851 | 0 | 0 | 0 | 1.4266
2031-02-04 22:00 | 31.5451 | 0.01524% | 32.9436 | 34.4042 | 35.9295 | 37.5224 | 0 | 0 | 0 | 0.47019
2031-02-04 23:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-02-05 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-02-05 01:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-02-05 02:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-02-05 03:00 | 23.1365 | 0.01118% | 24.1623 | 25.2335 | 26.3523 | 27.5206 | 0 | 0 | 0 | 0
2031-02-05 04:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-02-05 05:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-02-05 06:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-02-05 07:00 | 27.0518 | 0.01307% | 28.2511 | 29.5036 | 30.8117 | 32.1777 | 0 | 0 | 0 | 0
2031-02-05 08:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-02-05 09:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-02-05 10:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-02-05 11:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-02-05 12:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-02-05 13:00 | 29.1407 | 0.01408% | 30.4327 | 31.7819 | 33.191 | 34.6625 | 0 | 0 | 0 | 0
2031-02-05 14:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-02-05 15:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-02-05 16:00 | 29.4955 | 0.01425% | 30.8032 | 32.1688 | 33.595 | 35.0845 | 0 | 0 | 0 | 0
2031-02-05 17:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-02-05 18:00 | 33.0691 | 0.01598% | 34.5352 | 36.0663 | 37.6654 | 39.3353 | 0 | 0 | 0.59882 | 2.1017
2031-02-05 19:00 | 33.4764 | 0.01618% | 34.9606 | 36.5105 | 38.1293 | 39.8197 | 0 | 0 | 1.0163 | 2.5377
2031-02-05 20:00 | 33.1742 | 0.01603% | 34.645 | 36.181 | 37.7851 | 39.4603 | 0 | 0 | 0.70656 | 2.2143
2031-02-05 21:00 | 32.6224 | 0.01577% | 34.0687 | 35.5792 | 37.1566 | 38.8039 | 0 | 0 | 0.14091 | 1.6235
2031-02-05 22:00 | 31.4794 | 0.01521% | 32.875 | 34.3325 | 35.8547 | 37.4443 | 0 | 0 | 0 | 0.39986
2031-02-05 23:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-02-06 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-02-06 01:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-02-06 02:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-02-06 03:00 | 22.8606 | 0.01105% | 23.8742 | 24.9326 | 26.038 | 27.1924 | 0 | 0 | 0 | 0
2031-02-06 04:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-02-06 05:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-02-06 06:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-02-06 07:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-02-06 08:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-02-06 09:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-02-06 10:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-02-06 11:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-02-06 12:00 | 31.0327 | 0.015% | 32.4085 | 33.8453 | 35.3459 | 36.9129 | 0 | 0 | 0 | 0
2031-02-06 13:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-02-06 14:00 | 30.9801 | 0.01497% | 32.3536 | 33.788 | 35.286 | 36.8504 | 0 | 0 | 0 | 0
2031-02-06 15:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-02-06 16:00 | 30.8356 | 0.0149% | 32.2027 | 33.6304 | 35.1214 | 36.6785 | 0 | 0 | 0 | 0
2031-02-06 17:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-02-06 18:00 | 33.3844 | 0.01613% | 34.8645 | 36.4102 | 38.0245 | 39.7103 | 0 | 0 | 0.92205 | 2.4393
2031-02-06 19:00 | 33.7391 | 0.0163% | 35.235 | 36.7971 | 38.4285 | 40.1323 | 0 | 0 | 1.2857 | 2.819
2031-02-06 20:00 | 32.5173 | 0.01571% | 33.9589 | 35.4645 | 37.0369 | 38.6789 | 0 | 0 | 0.033167 | 1.511
2031-02-06 21:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-02-06 22:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-02-06 23:00 | 27.9057 | 0.01349% | 29.143 | 30.435 | 31.7844 | 33.1935 | 0 | 0 | 0 | 0
2031-02-07 | 25.9219 | 0.01253% | 27.0711 | 28.2713 | 29.5247 | 30.8337 | 0 | 0 | 0 | 0
2031-02-07 01:00 | 24.0562 | 0.01163% | 25.1228 | 26.2366 | 27.3998 | 28.6146 | 0 | 0 | 0 | 0
2031-02-07 02:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-02-07 03:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-02-07 04:00 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-02-07 05:00 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-02-07 06:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-02-07 07:00 | 26.3291 | 0.01272% | 27.4965 | 28.7155 | 29.9886 | 31.3182 | 0 | 0 | 0 | 0
2031-02-07 08:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-02-07 09:00 | 29.3115 | 0.01417% | 30.6111 | 31.9682 | 33.3855 | 34.8657 | 0 | 0 | 0 | 0
2031-02-07 10:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-02-07 11:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-02-07 12:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-02-07 13:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-02-07 14:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-02-07 15:00 | 29.2721 | 0.01415% | 30.5699 | 31.9252 | 33.3406 | 34.8188 | 0 | 0 | 0 | 0
2031-02-07 16:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-02-07 17:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-02-07 18:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-02-07 19:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-02-07 20:00 | 31.4925 | 0.01522% | 32.8887 | 34.3469 | 35.8696 | 37.4599 | 0 | 0 | 0 | 0.41393
2031-02-07 21:00 | 31.1246 | 0.01504% | 32.5045 | 33.9456 | 35.4506 | 37.0223 | 0 | 0 | 0 | 0.020104
2031-02-07 22:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-02-07 23:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-02-08 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-02-08 01:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-02-08 02:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-02-08 03:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-02-08 04:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-02-08 05:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-02-08 06:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-02-08 07:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-02-08 08:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-02-08 09:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-02-08 10:00 | 27.4328 | 0.01326% | 28.649 | 29.9192 | 31.2456 | 32.6309 | 0 | 0 | 0 | 0
2031-02-08 11:00 | 28.1685 | 0.01361% | 29.4174 | 30.7216 | 32.0836 | 33.5061 | 0 | 0 | 0 | 0
2031-02-08 12:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-02-08 13:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-02-08 14:00 | 29.8896 | 0.01444% | 31.2148 | 32.5987 | 34.044 | 35.5533 | 0 | 0 | 0 | 0
2031-02-08 15:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-02-08 16:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-02-08 17:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-02-08 18:00 | 32.5173 | 0.01571% | 33.9589 | 35.4645 | 37.0369 | 38.6789 | 0 | 0 | 0.033167 | 1.511
2031-02-08 19:00 | 32.7012 | 0.0158% | 34.151 | 35.6651 | 37.2464 | 38.8977 | 0 | 0 | 0.22172 | 1.7079
2031-02-08 20:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-02-08 21:00 | 30.4677 | 0.01472% | 31.8185 | 33.2292 | 34.7024 | 36.2409 | 0 | 0 | 0 | 0
2031-02-08 22:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-02-08 23:00 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-02-09 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-02-09 01:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-02-09 02:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-02-09 03:00 | 21.3366 | 0.01031% | 22.2826 | 23.2705 | 24.3022 | 25.3796 | 0 | 0 | 0 | 0
2031-02-09 04:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-02-09 05:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-02-09 06:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-02-09 07:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-02-09 08:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-02-09 09:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-02-09 10:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-02-09 11:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-02-09 12:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-02-09 13:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-02-09 14:00 | 29.1145 | 0.01407% | 30.4053 | 31.7533 | 33.1611 | 34.6313 | 0 | 0 | 0 | 0
2031-02-09 15:00 | 29.0225 | 0.01403% | 30.3092 | 31.653 | 33.0563 | 34.5219 | 0 | 0 | 0 | 0
2031-02-09 16:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-02-09 17:00 | 31.5713 | 0.01526% | 32.9711 | 34.4328 | 35.9594 | 37.5537 | 0 | 0 | 0 | 0.49832
2031-02-09 18:00 | 33.9362 | 0.0164% | 35.4408 | 37.0121 | 38.653 | 40.3667 | 0 | 0.010861 | 1.4877 | 3.03
2031-02-09 19:00 | 34.2121 | 0.01653% | 35.7289 | 37.313 | 38.9673 | 40.6949 | 0 | 0.28168 | 1.7705 | 3.3254
2031-02-09 20:00 | 32.4516 | 0.01568% | 33.8903 | 35.3929 | 36.962 | 38.6007 | 0 | 0 | 0 | 1.4407
2031-02-09 21:00 | 31.2429 | 0.0151% | 32.628 | 34.0746 | 35.5853 | 37.163 | 0 | 0 | 0 | 0.14669
2031-02-09 22:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-02-09 23:00 | 26.9992 | 0.01305% | 28.1962 | 29.4463 | 30.7518 | 32.1152 | 0 | 0 | 0 | 0
2031-02-10 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-02-10 01:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-02-10 02:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-02-10 03:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-02-10 04:00 | 20.6271 | 0.009968% | 21.5416 | 22.4967 | 23.4941 | 24.5357 | 0 | 0 | 0 | 0
2031-02-10 05:00 | 20.7979 | 0.01005% | 21.72 | 22.683 | 23.6886 | 24.7389 | 0 | 0 | 0 | 0
2031-02-10 06:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-02-10 07:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-02-10 08:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-02-10 09:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-02-10 10:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-02-10 11:00 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-02-10 12:00 | 29.4692 | 0.01424% | 30.7757 | 32.1402 | 33.5651 | 35.0532 | 0 | 0 | 0 | 0
2031-02-10 13:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-02-10 14:00 | 29.4429 | 0.01423% | 30.7483 | 32.1115 | 33.5352 | 35.022 | 0 | 0 | 0 | 0
2031-02-10 15:00 | 29.3247 | 0.01417% | 30.6248 | 31.9826 | 33.4005 | 34.8813 | 0 | 0 | 0 | 0
2031-02-10 16:00 | 29.7977 | 0.0144% | 31.1187 | 32.4984 | 33.9392 | 35.4439 | 0 | 0 | 0 | 0
2031-02-10 17:00 | 31.256 | 0.0151% | 32.6418 | 34.0889 | 35.6003 | 37.1786 | 0 | 0 | 0 | 0.16075
2031-02-10 18:00 | 33.0954 | 0.01599% | 34.5627 | 36.095 | 37.6953 | 39.3665 | 0 | 0 | 0.62576 | 2.1299
2031-02-10 19:00 | 33.5946 | 0.01624% | 35.0841 | 36.6395 | 38.2639 | 39.9604 | 0 | 0 | 1.1375 | 2.6643
2031-02-10 20:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-02-10 21:00 | 31.6239 | 0.01528% | 33.0259 | 34.4901 | 36.0193 | 37.6162 | 0 | 0 | 0 | 0.55458
2031-02-10 22:00 | 30.6911 | 0.01483% | 32.0518 | 33.4728 | 34.9568 | 36.5066 | 0 | 0 | 0 | 0
2031-02-10 23:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-02-11 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-02-11 01:00 | 23.938 | 0.01157% | 24.9993 | 26.1076 | 27.2651 | 28.4739 | 0 | 0 | 0 | 0
2031-02-11 02:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-02-11 03:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-02-11 04:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-02-11 05:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-02-11 06:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-02-11 07:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-02-11 08:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-02-11 09:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-02-11 10:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-02-11 11:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-02-11 12:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-02-11 13:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-02-11 14:00 | 29.3115 | 0.01417% | 30.6111 | 31.9682 | 33.3855 | 34.8657 | 0 | 0 | 0 | 0
2031-02-11 15:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-02-11 16:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-02-11 17:00 | 30.6516 | 0.01481% | 32.0106 | 33.4298 | 34.9119 | 36.4597 | 0 | 0 | 0 | 0
2031-02-11 18:00 | 32.9509 | 0.01592% | 34.4117 | 35.9374 | 37.5307 | 39.1946 | 0 | 0 | 0.47761 | 1.9751
2031-02-11 19:00 | 33.5027 | 0.01619% | 34.988 | 36.5392 | 38.1592 | 39.851 | 0 | 0 | 1.0433 | 2.5659
2031-02-11 20:00 | 32.2414 | 0.01558% | 33.6708 | 35.1636 | 36.7226 | 38.3507 | 0 | 0 | 0 | 1.2156
2031-02-11 21:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-02-11 22:00 | 30.4809 | 0.01473% | 31.8322 | 33.2435 | 34.7174 | 36.2566 | 0 | 0 | 0 | 0
2031-02-11 23:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-02-12 | 26.2635 | 0.01269% | 27.4279 | 28.6439 | 29.9138 | 31.24 | 0 | 0 | 0 | 0
2031-02-12 01:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-02-12 02:00 | 22.7293 | 0.01098% | 23.737 | 24.7893 | 25.8884 | 27.0362 | 0 | 0 | 0 | 0
2031-02-12 03:00 | 21.849 | 0.01056% | 22.8177 | 23.8293 | 24.8858 | 25.9891 | 0 | 0 | 0 | 0
2031-02-12 04:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-02-12 05:00 | 22.1906 | 0.01072% | 23.1744 | 24.2019 | 25.2748 | 26.3954 | 0 | 0 | 0 | 0
2031-02-12 06:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-02-12 07:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-02-12 08:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-02-12 09:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-02-12 10:00 | 30.875 | 0.01492% | 32.2438 | 33.6734 | 35.1663 | 36.7254 | 0 | 0 | 0 | 0
2031-02-12 11:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-02-12 12:00 | 30.2049 | 0.0146% | 31.5441 | 32.9426 | 34.4031 | 35.9284 | 0 | 0 | 0 | 0
2031-02-12 13:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-02-12 14:00 | 30.3232 | 0.01465% | 31.6676 | 33.0716 | 34.5378 | 36.069 | 0 | 0 | 0 | 0
2031-02-12 15:00 | 30.6648 | 0.01482% | 32.0243 | 33.4441 | 34.9269 | 36.4754 | 0 | 0 | 0 | 0
2031-02-12 16:00 | 31.637 | 0.01529% | 33.0397 | 34.5045 | 36.0342 | 37.6318 | 0 | 0 | 0 | 0.56864
2031-02-12 17:00 | 33.1216 | 0.01601% | 34.5901 | 36.1237 | 37.7252 | 39.3978 | 0 | 0 | 0.65269 | 2.158
2031-02-12 18:00 | 34.7114 | 0.01677% | 36.2503 | 37.8575 | 39.5359 | 41.2887 | 0 | 0.77174 | 2.2823 | 3.8599
2031-02-12 19:00 | 34.5274 | 0.01669% | 36.0582 | 37.6569 | 39.3264 | 41.0699 | 0 | 0.59119 | 2.0938 | 3.663
2031-02-12 20:00 | 33.4632 | 0.01617% | 34.9468 | 36.4962 | 38.1143 | 39.8041 | 0 | 0 | 1.0029 | 2.5237
2031-02-12 21:00 | 32.8589 | 0.01588% | 34.3157 | 35.8371 | 37.4259 | 39.0852 | 0 | 0 | 0.38333 | 1.8767
2031-02-12 22:00 | 31.7421 | 0.01534% | 33.1494 | 34.6191 | 36.154 | 37.7568 | 0 | 0 | 0 | 0.68116
2031-02-12 23:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-02-13 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-02-13 01:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-02-13 02:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-02-13 03:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-02-13 04:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-02-13 05:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-02-13 06:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-02-13 07:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-02-13 08:00 | 26.789 | 0.01295% | 27.9767 | 29.217 | 30.5124 | 31.8652 | 0 | 0 | 0 | 0
2031-02-13 09:00 | 27.9977 | 0.01353% | 29.239 | 30.5353 | 31.8891 | 33.3029 | 0 | 0 | 0 | 0
2031-02-13 10:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-02-13 11:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-02-13 12:00 | 31.0327 | 0.015% | 32.4085 | 33.8453 | 35.3459 | 36.9129 | 0 | 0 | 0 | 0
2031-02-13 13:00 | 31.729 | 0.01533% | 33.1357 | 34.6048 | 36.139 | 37.7412 | 0 | 0 | 0 | 0.6671
2031-02-13 14:00 | 31.821 | 0.01538% | 33.2317 | 34.7051 | 36.2437 | 37.8506 | 0 | 0 | 0 | 0.76555
2031-02-13 15:00 | 30.7436 | 0.01486% | 32.1066 | 33.5301 | 35.0167 | 36.5691 | 0 | 0 | 0 | 0
2031-02-13 16:00 | 30.494 | 0.01474% | 31.8459 | 33.2578 | 34.7323 | 36.2722 | 0 | 0 | 0 | 0
2031-02-13 17:00 | 31.164 | 0.01506% | 32.5457 | 33.9886 | 35.4955 | 37.0692 | 0 | 0 | 0 | 0.062299
2031-02-13 18:00 | 32.6881 | 0.0158% | 34.1373 | 35.6508 | 37.2314 | 38.8821 | 0 | 0 | 0.20825 | 1.6938
2031-02-13 19:00 | 33.5946 | 0.01624% | 35.0841 | 36.6395 | 38.2639 | 39.9604 | 0 | 0 | 1.1375 | 2.6643
2031-02-13 20:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-02-13 21:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-02-13 22:00 | 30.5597 | 0.01477% | 31.9146 | 33.3295 | 34.8072 | 36.3503 | 0 | 0 | 0 | 0
2031-02-13 23:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-02-14 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-02-14 01:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-02-14 02:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-02-14 03:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-02-14 04:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-02-14 05:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-02-14 06:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-02-14 07:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-02-14 08:00 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-02-14 09:00 | 29.6794 | 0.01434% | 30.9953 | 32.3694 | 33.8045 | 35.3033 | 0 | 0 | 0 | 0
2031-02-14 10:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-02-14 11:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-02-14 12:00 | 29.1933 | 0.01411% | 30.4876 | 31.8393 | 33.2509 | 34.725 | 0 | 0 | 0 | 0
2031-02-14 13:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-02-14 14:00 | 29.7977 | 0.0144% | 31.1187 | 32.4984 | 33.9392 | 35.4439 | 0 | 0 | 0 | 0
2031-02-14 15:00 | 29.7057 | 0.01436% | 31.0227 | 32.3981 | 33.8345 | 35.3345 | 0 | 0 | 0 | 0
2031-02-14 16:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-02-14 17:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-02-14 18:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-02-14 19:00 | 31.3348 | 0.01514% | 32.7241 | 34.1749 | 35.6901 | 37.2724 | 0 | 0 | 0 | 0.24514
2031-02-14 20:00 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-02-14 21:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-02-14 22:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-02-14 23:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-02-15 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-02-15 01:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-02-15 02:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-02-15 03:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-02-15 04:00 | 21.3497 | 0.01032% | 22.2963 | 23.2848 | 24.3171 | 25.3952 | 0 | 0 | 0 | 0
2031-02-15 05:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-02-15 06:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-02-15 07:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-02-15 08:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-02-15 09:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-02-15 10:00 | 27.9846 | 0.01352% | 29.2253 | 30.521 | 31.8741 | 33.2873 | 0 | 0 | 0 | 0
2031-02-15 11:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-02-15 12:00 | 29.4955 | 0.01425% | 30.8032 | 32.1688 | 33.595 | 35.0845 | 0 | 0 | 0 | 0
2031-02-15 13:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-02-15 14:00 | 30.1787 | 0.01458% | 31.5166 | 32.9139 | 34.3732 | 35.8971 | 0 | 0 | 0 | 0
2031-02-15 15:00 | 30.2181 | 0.0146% | 31.5578 | 32.9569 | 34.4181 | 35.944 | 0 | 0 | 0 | 0
2031-02-15 16:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-02-15 17:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-02-15 18:00 | 32.9246 | 0.01591% | 34.3843 | 35.9087 | 37.5007 | 39.1634 | 0 | 0 | 0.45067 | 1.947
2031-02-15 19:00 | 32.9771 | 0.01594% | 34.4392 | 35.966 | 37.5606 | 39.2259 | 0 | 0 | 0.50454 | 2.0033
2031-02-15 20:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-02-15 21:00 | 30.9276 | 0.01495% | 32.2987 | 33.7307 | 35.2262 | 36.7879 | 0 | 0 | 0 | 0
2031-02-15 22:00 | 29.167 | 0.0141% | 30.4601 | 31.8106 | 33.2209 | 34.6938 | 0 | 0 | 0 | 0
2031-02-15 23:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-02-16 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-02-16 01:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-02-16 02:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-02-16 03:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-02-16 04:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-02-16 05:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-02-16 06:00 | 21.7176 | 0.0105% | 22.6805 | 23.686 | 24.7361 | 25.8328 | 0 | 0 | 0 | 0
2031-02-16 07:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-02-16 08:00 | 23.7803 | 0.01149% | 24.8346 | 25.9357 | 27.0855 | 28.2864 | 0 | 0 | 0 | 0
2031-02-16 09:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-02-16 10:00 | 27.8926 | 0.01348% | 29.1292 | 30.4207 | 31.7694 | 33.1779 | 0 | 0 | 0 | 0
2031-02-16 11:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-02-16 12:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-02-16 13:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-02-16 14:00 | 31.5188 | 0.01523% | 32.9162 | 34.3755 | 35.8996 | 37.4912 | 0 | 0 | 0 | 0.44206
2031-02-16 15:00 | 31.0589 | 0.01501% | 32.4359 | 33.874 | 35.3758 | 36.9442 | 0 | 0 | 0 | 0
2031-02-16 16:00 | 30.8619 | 0.01491% | 32.2301 | 33.6591 | 35.1513 | 36.7098 | 0 | 0 | 0 | 0
2031-02-16 17:00 | 32.1363 | 0.01553% | 33.561 | 35.049 | 36.6029 | 38.2257 | 0 | 0 | 0 | 1.1031
2031-02-16 18:00 | 34.0019 | 0.01643% | 35.5094 | 37.0837 | 38.7278 | 40.4448 | 0 | 0.075342 | 1.555 | 3.1004
2031-02-16 19:00 | 34.199 | 0.01653% | 35.7152 | 37.2986 | 38.9523 | 40.6793 | 0 | 0.26878 | 1.7571 | 3.3113
2031-02-16 20:00 | 32.9114 | 0.0159% | 34.3706 | 35.8944 | 37.4858 | 39.1477 | 0 | 0 | 0.43721 | 1.933
2031-02-16 21:00 | 31.8472 | 0.01539% | 33.2592 | 34.7337 | 36.2737 | 37.8819 | 0 | 0 | 0 | 0.79368
2031-02-16 22:00 | 29.9685 | 0.01448% | 31.2971 | 32.6847 | 34.1338 | 35.6471 | 0 | 0 | 0 | 0
2031-02-16 23:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-02-17 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-02-17 01:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-02-17 02:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-02-17 03:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-02-17 04:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-02-17 05:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-02-17 06:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-02-17 07:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-02-17 08:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-02-17 09:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-02-17 10:00 | 26.7496 | 0.01293% | 27.9355 | 29.174 | 30.4675 | 31.8183 | 0 | 0 | 0 | 0
2031-02-17 11:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-02-17 12:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-02-17 13:00 | 30.8487 | 0.01491% | 32.2164 | 33.6447 | 35.1364 | 36.6942 | 0 | 0 | 0 | 0
2031-02-17 14:00 | 30.9144 | 0.01494% | 32.285 | 33.7164 | 35.2112 | 36.7723 | 0 | 0 | 0 | 0
2031-02-17 15:00 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-02-17 16:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-02-17 17:00 | 32.8852 | 0.01589% | 34.3431 | 35.8657 | 37.4559 | 39.1165 | 0 | 0 | 0.41027 | 1.9048
2031-02-17 18:00 | 34.3961 | 0.01662% | 35.921 | 37.5136 | 39.1768 | 40.9137 | 0 | 0.46223 | 1.9591 | 3.5223
2031-02-17 19:00 | 34.5143 | 0.01668% | 36.0445 | 37.6425 | 39.3114 | 41.0543 | 0 | 0.57829 | 2.0803 | 3.6489
2031-02-17 20:00 | 33.4107 | 0.01615% | 34.892 | 36.4389 | 38.0544 | 39.7416 | 0 | 0 | 0.94899 | 2.4674
2031-02-17 21:00 | 32.7801 | 0.01584% | 34.2334 | 35.7511 | 37.3361 | 38.9914 | 0 | 0 | 0.30253 | 1.7923
2031-02-17 22:00 | 31.6896 | 0.01531% | 33.0945 | 34.5618 | 36.0941 | 37.6943 | 0 | 0 | 0 | 0.6249
2031-02-17 23:00 | 29.9553 | 0.01448% | 31.2834 | 32.6704 | 34.1188 | 35.6315 | 0 | 0 | 0 | 0
2031-02-18 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-02-18 01:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-02-18 02:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-02-18 03:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-02-18 04:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-02-18 05:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-02-18 06:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-02-18 07:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-02-18 08:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-02-18 09:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-02-18 10:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-02-18 11:00 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-02-18 12:00 | 31.5451 | 0.01524% | 32.9436 | 34.4042 | 35.9295 | 37.5224 | 0 | 0 | 0 | 0.47019
2031-02-18 13:00 | 31.4662 | 0.01521% | 32.8613 | 34.3182 | 35.8397 | 37.4287 | 0 | 0 | 0 | 0.3858
2031-02-18 14:00 | 31.1772 | 0.01507% | 32.5594 | 34.003 | 35.5105 | 37.0848 | 0 | 0 | 0 | 0.076364
2031-02-18 15:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-02-18 16:00 | 31.6764 | 0.01531% | 33.0808 | 34.5475 | 36.0791 | 37.6787 | 0 | 0 | 0 | 0.61084
2031-02-18 17:00 | 32.5041 | 0.01571% | 33.9452 | 35.4502 | 37.0219 | 38.6633 | 0 | 0 | 0.019699 | 1.4969
2031-02-18 18:00 | 34.1727 | 0.01651% | 35.6878 | 37.27 | 38.9224 | 40.648 | 0 | 0.24299 | 1.7301 | 3.2832
2031-02-18 19:00 | 34.488 | 0.01667% | 36.0171 | 37.6139 | 39.2815 | 41.0231 | 0 | 0.5525 | 2.0534 | 3.6208
2031-02-18 20:00 | 34.2253 | 0.01654% | 35.7427 | 37.3273 | 38.9822 | 40.7105 | 0 | 0.29458 | 1.784 | 3.3395
2031-02-18 21:00 | 33.4632 | 0.01617% | 34.9468 | 36.4962 | 38.1143 | 39.8041 | 0 | 0 | 1.0029 | 2.5237
2031-02-18 22:00 | 31.9655 | 0.01545% | 33.3827 | 34.8627 | 36.4083 | 38.0225 | 0 | 0 | 0 | 0.92027
2031-02-18 23:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-02-19 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-02-19 01:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-02-19 02:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-02-19 03:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-02-19 04:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-02-19 05:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-02-19 06:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-02-19 07:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-02-19 08:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-02-19 09:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-02-19 10:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-02-19 11:00 | 30.7436 | 0.01486% | 32.1066 | 33.5301 | 35.0167 | 36.5691 | 0 | 0 | 0 | 0
2031-02-19 12:00 | 30.7042 | 0.01484% | 32.0655 | 33.4871 | 34.9718 | 36.5222 | 0 | 0 | 0 | 0
2031-02-19 13:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-02-19 14:00 | 30.2444 | 0.01462% | 31.5853 | 32.9856 | 34.448 | 35.9753 | 0 | 0 | 0 | 0
2031-02-19 15:00 | 30.6779 | 0.01483% | 32.038 | 33.4585 | 34.9418 | 36.491 | 0 | 0 | 0 | 0
2031-02-19 16:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-02-19 17:00 | 32.491 | 0.0157% | 33.9315 | 35.4359 | 37.0069 | 38.6476 | 0 | 0 | 0.0062307 | 1.4829
2031-02-19 18:00 | 34.0019 | 0.01643% | 35.5094 | 37.0837 | 38.7278 | 40.4448 | 0 | 0.075342 | 1.555 | 3.1004
2031-02-19 19:00 | 34.5406 | 0.01669% | 36.0719 | 37.6712 | 39.3414 | 41.0856 | 0 | 0.60409 | 2.1072 | 3.677
2031-02-19 20:00 | 34.1596 | 0.01651% | 35.674 | 37.2557 | 38.9074 | 40.6324 | 0 | 0.2301 | 1.7167 | 3.2691
2031-02-19 21:00 | 33.5158 | 0.0162% | 35.0017 | 36.5535 | 38.1741 | 39.8666 | 0 | 0 | 1.0567 | 2.5799
2031-02-19 22:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-02-19 23:00 | 30.4283 | 0.0147% | 31.7773 | 33.1862 | 34.6575 | 36.1941 | 0 | 0 | 0 | 0
2031-02-20 | 27.6824 | 0.01338% | 28.9097 | 30.1914 | 31.53 | 32.9278 | 0 | 0 | 0 | 0
2031-02-20 01:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-02-20 02:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-02-20 03:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-02-20 04:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-02-20 05:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-02-20 06:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-02-20 07:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-02-20 08:00 | 30.6385 | 0.01481% | 31.9969 | 33.4155 | 34.8969 | 36.4441 | 0 | 0 | 0 | 0
2031-02-20 09:00 | 31.0589 | 0.01501% | 32.4359 | 33.874 | 35.3758 | 36.9442 | 0 | 0 | 0 | 0
2031-02-20 10:00 | 31.4005 | 0.01517% | 32.7927 | 34.2466 | 35.7649 | 37.3505 | 0 | 0 | 0 | 0.31547
2031-02-20 11:00 | 31.5713 | 0.01526% | 32.9711 | 34.4328 | 35.9594 | 37.5537 | 0 | 0 | 0 | 0.49832
2031-02-20 12:00 | 32.1626 | 0.01554% | 33.5885 | 35.0776 | 36.6328 | 38.2569 | 0 | 0 | 0 | 1.1312
2031-02-20 13:00 | 31.8604 | 0.0154% | 33.2729 | 34.7481 | 36.2886 | 37.8975 | 0 | 0 | 0 | 0.80775
2031-02-20 14:00 | 31.4137 | 0.01518% | 32.8064 | 34.2609 | 35.7798 | 37.3662 | 0 | 0 | 0 | 0.32954
2031-02-20 15:00 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-02-20 16:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-02-20 17:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-02-20 18:00 | 34.5669 | 0.0167% | 36.0994 | 37.6999 | 39.3713 | 41.1168 | 0 | 0.62988 | 2.1342 | 3.7051
2031-02-20 19:00 | 34.3698 | 0.01661% | 35.8936 | 37.4849 | 39.1468 | 40.8824 | 0 | 0.43644 | 1.9321 | 3.4942
2031-02-20 20:00 | 34.0282 | 0.01644% | 35.5368 | 37.1124 | 38.7578 | 40.4761 | 0 | 0.10113 | 1.582 | 3.1285
2031-02-20 21:00 | 33.4764 | 0.01618% | 34.9606 | 36.5105 | 38.1293 | 39.8197 | 0 | 0 | 1.0163 | 2.5377
2031-02-20 22:00 | 32.3596 | 0.01564% | 33.7943 | 35.2926 | 36.8573 | 38.4914 | 0 | 0 | 0 | 1.3422
2031-02-20 23:00 | 30.3889 | 0.01469% | 31.7362 | 33.1432 | 34.6126 | 36.1472 | 0 | 0 | 0 | 0
2031-02-21 | 27.932 | 0.0135% | 29.1704 | 30.4637 | 31.8143 | 33.2248 | 0 | 0 | 0 | 0
2031-02-21 01:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-02-21 02:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-02-21 03:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-02-21 04:00 | 23.846 | 0.01152% | 24.9032 | 26.0073 | 27.1604 | 28.3645 | 0 | 0 | 0 | 0
2031-02-21 05:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-02-21 06:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-02-21 07:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-02-21 08:00 | 30.7568 | 0.01486% | 32.1204 | 33.5444 | 35.0316 | 36.5848 | 0 | 0 | 0 | 0
2031-02-21 09:00 | 32.0706 | 0.0155% | 33.4924 | 34.9773 | 36.5281 | 38.1475 | 0 | 0 | 0 | 1.0328
2031-02-21 10:00 | 32.5567 | 0.01573% | 34.0001 | 35.5075 | 37.0817 | 38.7258 | 0 | 0 | 0.07357 | 1.5532
2031-02-21 11:00 | 32.2939 | 0.01561% | 33.7257 | 35.2209 | 36.7825 | 38.4132 | 0 | 0 | 0 | 1.2719
2031-02-21 12:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-02-21 13:00 | 31.3217 | 0.01514% | 32.7104 | 34.1606 | 35.6751 | 37.2568 | 0 | 0 | 0 | 0.23108
2031-02-21 14:00 | 31.2954 | 0.01512% | 32.6829 | 34.1319 | 35.6452 | 37.2255 | 0 | 0 | 0 | 0.20295
2031-02-21 15:00 | 29.9685 | 0.01448% | 31.2971 | 32.6847 | 34.1338 | 35.6471 | 0 | 0 | 0 | 0
2031-02-21 16:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-02-21 17:00 | 30.8619 | 0.01491% | 32.2301 | 33.6591 | 35.1513 | 36.7098 | 0 | 0 | 0 | 0
2031-02-21 18:00 | 32.1494 | 0.01554% | 33.5748 | 35.0633 | 36.6178 | 38.2413 | 0 | 0 | 0 | 1.1172
2031-02-21 19:00 | 32.6618 | 0.01578% | 34.1099 | 35.6221 | 37.2015 | 38.8508 | 0 | 0 | 0.18131 | 1.6657
2031-02-21 20:00 | 32.9246 | 0.01591% | 34.3843 | 35.9087 | 37.5007 | 39.1634 | 0 | 0 | 0.45067 | 1.947
2031-02-21 21:00 | 32.018 | 0.01547% | 33.4376 | 34.92 | 36.4682 | 38.085 | 0 | 0 | 0 | 0.97653
2031-02-21 22:00 | 31.348 | 0.01515% | 32.7378 | 34.1892 | 35.705 | 37.288 | 0 | 0 | 0 | 0.25921
2031-02-21 23:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-02-22 | 27.4853 | 0.01328% | 28.7039 | 29.9765 | 31.3055 | 32.6934 | 0 | 0 | 0 | 0
2031-02-22 01:00 | 25.5671 | 0.01236% | 26.7007 | 27.8844 | 29.1207 | 30.4118 | 0 | 0 | 0 | 0
2031-02-22 02:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-02-22 03:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-02-22 04:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-02-22 05:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-02-22 06:00 | 23.2154 | 0.01122% | 24.2446 | 25.3195 | 26.4421 | 27.6144 | 0 | 0 | 0 | 0
2031-02-22 07:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-02-22 08:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-02-22 09:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-02-22 10:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-02-22 11:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-02-22 12:00 | 30.3889 | 0.01469% | 31.7362 | 33.1432 | 34.6126 | 36.1472 | 0 | 0 | 0 | 0
2031-02-22 13:00 | 30.7042 | 0.01484% | 32.0655 | 33.4871 | 34.9718 | 36.5222 | 0 | 0 | 0 | 0
2031-02-22 14:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-02-22 15:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-02-22 16:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-02-22 17:00 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-02-22 18:00 | 32.0969 | 0.01551% | 33.5199 | 35.006 | 36.558 | 38.1788 | 0 | 0 | 0 | 1.0609
2031-02-22 19:00 | 32.6749 | 0.01579% | 34.1236 | 35.6365 | 37.2164 | 38.8664 | 0 | 0 | 0.19478 | 1.6798
2031-02-22 20:00 | 31.8341 | 0.01538% | 33.2455 | 34.7194 | 36.2587 | 37.8662 | 0 | 0 | 0 | 0.77962
2031-02-22 21:00 | 30.7305 | 0.01485% | 32.0929 | 33.5158 | 35.0017 | 36.5535 | 0 | 0 | 0 | 0
2031-02-22 22:00 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-02-22 23:00 | 27.9189 | 0.01349% | 29.1567 | 30.4493 | 31.7993 | 33.2091 | 0 | 0 | 0 | 0
2031-02-23 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-02-23 01:00 | 23.7278 | 0.01147% | 24.7797 | 25.8784 | 27.0257 | 28.2239 | 0 | 0 | 0 | 0
2031-02-23 02:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-02-23 03:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-02-23 04:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-02-23 05:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-02-23 06:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-02-23 07:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-02-23 08:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-02-23 09:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-02-23 10:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-02-23 11:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-02-23 12:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-02-23 13:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-02-23 14:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-02-23 15:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-02-23 16:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-02-23 17:00 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-02-23 18:00 | 32.2545 | 0.01559% | 33.6845 | 35.1779 | 36.7376 | 38.3663 | 0 | 0 | 0 | 1.2297
2031-02-23 19:00 | 32.4647 | 0.01569% | 33.9041 | 35.4072 | 36.977 | 38.6164 | 0 | 0 | 0 | 1.4547
2031-02-23 20:00 | 31.5845 | 0.01526% | 32.9848 | 34.4472 | 35.9744 | 37.5693 | 0 | 0 | 0 | 0.51238
2031-02-23 21:00 | 30.494 | 0.01474% | 31.8459 | 33.2578 | 34.7323 | 36.2722 | 0 | 0 | 0 | 0
2031-02-23 22:00 | 28.9043 | 0.01397% | 30.1857 | 31.524 | 32.9216 | 34.3812 | 0 | 0 | 0 | 0
2031-02-23 23:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-02-24 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-02-24 01:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-02-24 02:00 | 20.2724 | 0.009797% | 21.1712 | 22.1098 | 23.09 | 24.1137 | 0 | 0 | 0 | 0
2031-02-24 03:00 | 19.6023 | 0.009473% | 20.4714 | 21.379 | 22.3269 | 23.3167 | 0 | 0 | 0 | 0
2031-02-24 04:00 | 19.3527 | 0.009352% | 20.2107 | 21.1068 | 22.0425 | 23.0198 | 0 | 0 | 0 | 0
2031-02-24 05:00 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-02-24 06:00 | 20.9687 | 0.01013% | 21.8984 | 22.8692 | 23.8832 | 24.942 | 0 | 0 | 0 | 0
2031-02-24 07:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-02-24 08:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-02-24 09:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-02-24 10:00 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-02-24 11:00 | 27.9057 | 0.01349% | 29.143 | 30.435 | 31.7844 | 33.1935 | 0 | 0 | 0 | 0
2031-02-24 12:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-02-24 13:00 | 28.6546 | 0.01385% | 29.925 | 31.2518 | 32.6373 | 34.0843 | 0 | 0 | 0 | 0
2031-02-24 14:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-02-24 15:00 | 27.9452 | 0.0135% | 29.1841 | 30.478 | 31.8292 | 33.2404 | 0 | 0 | 0 | 0
2031-02-24 16:00 | 27.9583 | 0.01351% | 29.1978 | 30.4923 | 31.8442 | 33.256 | 0 | 0 | 0 | 0
2031-02-24 17:00 | 29.1933 | 0.01411% | 30.4876 | 31.8393 | 33.2509 | 34.725 | 0 | 0 | 0 | 0
2031-02-24 18:00 | 30.6516 | 0.01481% | 32.0106 | 33.4298 | 34.9119 | 36.4597 | 0 | 0 | 0 | 0
2031-02-24 19:00 | 30.9144 | 0.01494% | 32.285 | 33.7164 | 35.2112 | 36.7723 | 0 | 0 | 0 | 0
2031-02-24 20:00 | 30.5203 | 0.01475% | 31.8734 | 33.2865 | 34.7623 | 36.3035 | 0 | 0 | 0 | 0
2031-02-24 21:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-02-24 22:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-02-24 23:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-02-25 | 23.7409 | 0.01147% | 24.7935 | 25.8927 | 27.0406 | 28.2395 | 0 | 0 | 0 | 0
2031-02-25 01:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-02-25 02:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-02-25 03:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-02-25 04:00 | 19.3264 | 0.00934% | 20.1833 | 21.0781 | 22.0126 | 22.9885 | 0 | 0 | 0 | 0
2031-02-25 05:00 | 19.5104 | 0.009429% | 20.3754 | 21.2787 | 22.2221 | 23.2073 | 0 | 0 | 0 | 0
2031-02-25 06:00 | 20.8899 | 0.0101% | 21.8161 | 22.7833 | 23.7934 | 24.8483 | 0 | 0 | 0 | 0
2031-02-25 07:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-02-25 08:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-02-25 09:00 | 26.8941 | 0.013% | 28.0865 | 29.3317 | 30.6321 | 31.9902 | 0 | 0 | 0 | 0
2031-02-25 10:00 | 27.262 | 0.01317% | 28.4706 | 29.7329 | 31.0511 | 32.4278 | 0 | 0 | 0 | 0
2031-02-25 11:00 | 27.5773 | 0.01333% | 28.7999 | 30.0768 | 31.4102 | 32.8028 | 0 | 0 | 0 | 0
2031-02-25 12:00 | 27.2226 | 0.01316% | 28.4295 | 29.6899 | 31.0062 | 32.3809 | 0 | 0 | 0 | 0
2031-02-25 13:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-02-25 14:00 | 26.8415 | 0.01297% | 28.0316 | 29.2744 | 30.5722 | 31.9277 | 0 | 0 | 0 | 0
2031-02-25 15:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-02-25 16:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-02-25 17:00 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-02-25 18:00 | 30.2706 | 0.01463% | 31.6127 | 33.0142 | 34.4779 | 36.0065 | 0 | 0 | 0 | 0
2031-02-25 19:00 | 30.7436 | 0.01486% | 32.1066 | 33.5301 | 35.0167 | 36.5691 | 0 | 0 | 0 | 0
2031-02-25 20:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-02-25 21:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-02-25 22:00 | 27.9714 | 0.01352% | 29.2116 | 30.5067 | 31.8592 | 33.2717 | 0 | 0 | 0 | 0
2031-02-25 23:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-02-26 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-02-26 01:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-02-26 02:00 | 20.2724 | 0.009797% | 21.1712 | 22.1098 | 23.09 | 24.1137 | 0 | 0 | 0 | 0
2031-02-26 03:00 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-02-26 04:00 | 19.1031 | 0.009232% | 19.95 | 20.8345 | 21.7582 | 22.7229 | 0 | 0 | 0 | 0
2031-02-26 05:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-02-26 06:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-02-26 07:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-02-26 08:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-02-26 09:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-02-26 10:00 | 26.0007 | 0.01257% | 27.1534 | 28.3573 | 29.6145 | 30.9275 | 0 | 0 | 0 | 0
2031-02-26 11:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-02-26 12:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-02-26 13:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-02-26 14:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-02-26 15:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-02-26 16:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-02-26 17:00 | 27.4196 | 0.01325% | 28.6353 | 29.9048 | 31.2307 | 32.6153 | 0 | 0 | 0 | 0
2031-02-26 18:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-02-26 19:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-02-26 20:00 | 29.2721 | 0.01415% | 30.5699 | 31.9252 | 33.3406 | 34.8188 | 0 | 0 | 0 | 0
2031-02-26 21:00 | 29.0094 | 0.01402% | 30.2955 | 31.6387 | 33.0414 | 34.5063 | 0 | 0 | 0 | 0
2031-02-26 22:00 | 28.313 | 0.01368% | 29.5683 | 30.8792 | 32.2482 | 33.678 | 0 | 0 | 0 | 0
2031-02-26 23:00 | 27.0123 | 0.01305% | 28.2099 | 29.4606 | 30.7668 | 32.1308 | 0 | 0 | 0 | 0
2031-02-27 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-02-27 01:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-02-27 02:00 | 20.1673 | 0.009746% | 21.0614 | 21.9952 | 22.9703 | 23.9887 | 0 | 0 | 0 | 0
2031-02-27 03:00 | 19.379 | 0.009365% | 20.2382 | 21.1354 | 22.0725 | 23.0511 | 0 | 0 | 0 | 0
2031-02-27 04:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-02-27 05:00 | 19.4184 | 0.009384% | 20.2793 | 21.1784 | 22.1174 | 23.0979 | 0 | 0 | 0 | 0
2031-02-27 06:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0
2031-02-27 07:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-02-27 08:00 | 26.4343 | 0.01277% | 27.6062 | 28.8302 | 30.1083 | 31.4432 | 0 | 0 | 0 | 0
2031-02-27 09:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-02-27 10:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-02-27 11:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-02-27 12:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-02-27 13:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-02-27 14:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-02-27 15:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-02-27 16:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-02-27 17:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-02-27 18:00 | 29.3641 | 0.01419% | 30.666 | 32.0255 | 33.4454 | 34.9282 | 0 | 0 | 0 | 0
2031-02-27 19:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-02-27 20:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-02-27 21:00 | 28.9437 | 0.01399% | 30.2269 | 31.567 | 32.9665 | 34.4281 | 0 | 0 | 0 | 0
2031-02-27 22:00 | 27.7875 | 0.01343% | 29.0195 | 30.306 | 31.6497 | 33.0529 | 0 | 0 | 0 | 0
2031-02-27 23:00 | 26.2372 | 0.01268% | 27.4004 | 28.6152 | 29.8839 | 31.2088 | 0 | 0 | 0 | 0
2031-02-28 | 23.5307 | 0.01137% | 24.5739 | 25.6634 | 26.8012 | 27.9895 | 0 | 0 | 0 | 0
2031-02-28 01:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-02-28 02:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-02-28 03:00 | 20.0228 | 0.009676% | 20.9105 | 21.8375 | 22.8057 | 23.8168 | 0 | 0 | 0 | 0
2031-02-28 04:00 | 19.668 | 0.009505% | 20.54 | 21.4507 | 22.4017 | 23.3949 | 0 | 0 | 0 | 0
2031-02-28 05:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-02-28 06:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-02-28 07:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-02-28 08:00 | 26.0532 | 0.01259% | 27.2083 | 28.4146 | 29.6744 | 30.99 | 0 | 0 | 0 | 0
2031-02-28 09:00 | 26.4999 | 0.01281% | 27.6748 | 28.9018 | 30.1832 | 31.5213 | 0 | 0 | 0 | 0
2031-02-28 10:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-02-28 11:00 | 28.2736 | 0.01366% | 29.5271 | 30.8362 | 32.2034 | 33.6311 | 0 | 0 | 0 | 0
2031-02-28 12:00 | 28.694 | 0.01387% | 29.9662 | 31.2948 | 32.6822 | 34.1312 | 0 | 0 | 0 | 0
2031-02-28 13:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-02-28 14:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-02-28 15:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-02-28 16:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-02-28 17:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-02-28 18:00 | 31.2954 | 0.01512% | 32.6829 | 34.1319 | 35.6452 | 37.2255 | 0 | 0 | 0 | 0.20295
2031-02-28 19:00 | 30.875 | 0.01492% | 32.2438 | 33.6734 | 35.1663 | 36.7254 | 0 | 0 | 0 | 0
2031-02-28 20:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-02-28 21:00 | 29.5349 | 0.01427% | 30.8443 | 32.2118 | 33.6399 | 35.1314 | 0 | 0 | 0 | 0
2031-02-28 22:00 | 27.9452 | 0.0135% | 29.1841 | 30.478 | 31.8292 | 33.2404 | 0 | 0 | 0 | 0
2031-02-28 23:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-03-01 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-03-01 01:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-03-01 02:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-03-01 03:00 | 19.7469 | 0.009543% | 20.6223 | 21.5366 | 22.4915 | 23.4886 | 0 | 0 | 0 | 0
2031-03-01 04:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-03-01 05:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-03-01 06:00 | 20.1279 | 0.009727% | 21.0202 | 21.9522 | 22.9254 | 23.9418 | 0 | 0 | 0 | 0
2031-03-01 07:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-03-01 08:00 | 23.2942 | 0.01126% | 24.327 | 25.4055 | 26.5319 | 27.7081 | 0 | 0 | 0 | 0
2031-03-01 09:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-03-01 10:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-03-01 11:00 | 28.2211 | 0.01364% | 29.4723 | 30.7789 | 32.1435 | 33.5686 | 0 | 0 | 0 | 0
2031-03-01 12:00 | 28.5627 | 0.0138% | 29.829 | 31.1515 | 32.5326 | 33.9749 | 0 | 0 | 0 | 0
2031-03-01 13:00 | 29.0356 | 0.01403% | 30.3229 | 31.6673 | 33.0713 | 34.5375 | 0 | 0 | 0 | 0
2031-03-01 14:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-03-01 15:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-03-01 16:00 | 28.1816 | 0.01362% | 29.4311 | 30.7359 | 32.0986 | 33.5217 | 0 | 0 | 0 | 0
2031-03-01 17:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-03-01 18:00 | 31.9655 | 0.01545% | 33.3827 | 34.8627 | 36.4083 | 38.0225 | 0 | 0 | 0 | 0.92027
2031-03-01 19:00 | 32.7669 | 0.01584% | 34.2196 | 35.7368 | 37.3212 | 38.9758 | 0 | 0 | 0.28906 | 1.7782
2031-03-01 20:00 | 32.3859 | 0.01565% | 33.8217 | 35.3212 | 36.8872 | 38.5226 | 0 | 0 | 0 | 1.3703
2031-03-01 21:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-03-01 22:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-03-01 23:00 | 29.3247 | 0.01417% | 30.6248 | 31.9826 | 33.4005 | 34.8813 | 0 | 0 | 0 | 0
2031-03-02 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-03-02 01:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-03-02 02:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-03-02 03:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-03-02 04:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-03-02 05:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-03-02 06:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-03-02 07:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-03-02 08:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-03-02 09:00 | 27.6693 | 0.01337% | 28.896 | 30.1771 | 31.515 | 32.9122 | 0 | 0 | 0 | 0
2031-03-02 10:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-03-02 11:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-03-02 12:00 | 29.9947 | 0.0145% | 31.3246 | 32.7133 | 34.1637 | 35.6783 | 0 | 0 | 0 | 0
2031-03-02 13:00 | 30.4809 | 0.01473% | 31.8322 | 33.2435 | 34.7174 | 36.2566 | 0 | 0 | 0 | 0
2031-03-02 14:00 | 30.2575 | 0.01462% | 31.599 | 32.9999 | 34.463 | 35.9909 | 0 | 0 | 0 | 0
2031-03-02 15:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-03-02 16:00 | 30.875 | 0.01492% | 32.2438 | 33.6734 | 35.1663 | 36.7254 | 0 | 0 | 0 | 0
2031-03-02 17:00 | 32.7012 | 0.0158% | 34.151 | 35.6651 | 37.2464 | 38.8977 | 0 | 0 | 0.22172 | 1.7079
2031-03-02 18:00 | 33.8443 | 0.01636% | 35.3447 | 36.9118 | 38.5483 | 40.2573 | 0 | 0 | 1.3934 | 2.9316
2031-03-02 19:00 | 33.9099 | 0.01639% | 35.4134 | 36.9834 | 38.6231 | 40.3354 | 0 | 0 | 1.4608 | 3.0019
2031-03-02 20:00 | 33.9231 | 0.01639% | 35.4271 | 36.9977 | 38.638 | 40.3511 | 0 | 0 | 1.4742 | 3.016
2031-03-02 21:00 | 32.4647 | 0.01569% | 33.9041 | 35.4072 | 36.977 | 38.6164 | 0 | 0 | 0 | 1.4547
2031-03-02 22:00 | 30.6779 | 0.01483% | 32.038 | 33.4585 | 34.9418 | 36.491 | 0 | 0 | 0 | 0
2031-03-02 23:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-03-03 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-03-03 01:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-03-03 02:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-03-03 03:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-03-03 04:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-03-03 05:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-03-03 06:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-03-03 07:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-03-03 08:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-03-03 09:00 | 29.4692 | 0.01424% | 30.7757 | 32.1402 | 33.5651 | 35.0532 | 0 | 0 | 0 | 0
2031-03-03 10:00 | 28.9437 | 0.01399% | 30.2269 | 31.567 | 32.9665 | 34.4281 | 0 | 0 | 0 | 0
2031-03-03 11:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-03-03 12:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-03-03 13:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-03-03 14:00 | 28.1685 | 0.01361% | 29.4174 | 30.7216 | 32.0836 | 33.5061 | 0 | 0 | 0 | 0
2031-03-03 15:00 | 27.4196 | 0.01325% | 28.6353 | 29.9048 | 31.2307 | 32.6153 | 0 | 0 | 0 | 0
2031-03-03 16:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-03-03 17:00 | 30.0736 | 0.01453% | 31.4069 | 32.7993 | 34.2535 | 35.7721 | 0 | 0 | 0 | 0
2031-03-03 18:00 | 31.0984 | 0.01503% | 32.4771 | 33.917 | 35.4207 | 36.9911 | 0 | 0 | 0 | 0
2031-03-03 19:00 | 31.637 | 0.01529% | 33.0397 | 34.5045 | 36.0342 | 37.6318 | 0 | 0 | 0 | 0.56864
2031-03-03 20:00 | 31.2035 | 0.01508% | 32.5869 | 34.0316 | 35.5404 | 37.1161 | 0 | 0 | 0 | 0.10449
2031-03-03 21:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-03-03 22:00 | 29.2064 | 0.01411% | 30.5013 | 31.8536 | 33.2658 | 34.7407 | 0 | 0 | 0 | 0
2031-03-03 23:00 | 27.3671 | 0.01323% | 28.5804 | 29.8475 | 31.1708 | 32.5528 | 0 | 0 | 0 | 0
2031-03-04 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-03-04 01:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-03-04 02:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-03-04 03:00 | 20.3118 | 0.009816% | 21.2123 | 22.1528 | 23.1349 | 24.1606 | 0 | 0 | 0 | 0
2031-03-04 04:00 | 19.76 | 0.009549% | 20.6361 | 21.551 | 22.5064 | 23.5043 | 0 | 0 | 0 | 0
2031-03-04 05:00 | 20.141 | 0.009733% | 21.034 | 21.9665 | 22.9404 | 23.9575 | 0 | 0 | 0 | 0
2031-03-04 06:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-03-04 07:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-03-04 08:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-03-04 09:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-03-04 10:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-03-04 11:00 | 27.3802 | 0.01323% | 28.5941 | 29.8618 | 31.1858 | 32.5684 | 0 | 0 | 0 | 0
2031-03-04 12:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-03-04 13:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-03-04 14:00 | 27.8926 | 0.01348% | 29.1292 | 30.4207 | 31.7694 | 33.1779 | 0 | 0 | 0 | 0
2031-03-04 15:00 | 28.024 | 0.01354% | 29.2664 | 30.564 | 31.919 | 33.3342 | 0 | 0 | 0 | 0
2031-03-04 16:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-03-04 17:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-03-04 18:00 | 30.9407 | 0.01495% | 32.3125 | 33.745 | 35.2411 | 36.8035 | 0 | 0 | 0 | 0
2031-03-04 19:00 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-03-04 20:00 | 29.7057 | 0.01436% | 31.0227 | 32.3981 | 33.8345 | 35.3345 | 0 | 0 | 0 | 0
2031-03-04 21:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-03-04 22:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-03-04 23:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-03-05 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-03-05 01:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-03-05 02:00 | 19.9308 | 0.009632% | 20.8144 | 21.7372 | 22.701 | 23.7074 | 0 | 0 | 0 | 0
2031-03-05 03:00 | 19.2345 | 0.009295% | 20.0872 | 20.9778 | 21.9079 | 22.8791 | 0 | 0 | 0 | 0
2031-03-05 04:00 | 18.8535 | 0.009111% | 19.6893 | 20.5623 | 21.4739 | 22.4259 | 0 | 0 | 0 | 0
2031-03-05 05:00 | 18.906 | 0.009137% | 19.7442 | 20.6196 | 21.5337 | 22.4885 | 0 | 0 | 0 | 0
2031-03-05 06:00 | 19.8388 | 0.009587% | 20.7184 | 21.6369 | 22.5962 | 23.598 | 0 | 0 | 0 | 0
2031-03-05 07:00 | 23.2942 | 0.01126% | 24.327 | 25.4055 | 26.5319 | 27.7081 | 0 | 0 | 0 | 0
2031-03-05 08:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-03-05 09:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-03-05 10:00 | 27.6693 | 0.01337% | 28.896 | 30.1771 | 31.515 | 32.9122 | 0 | 0 | 0 | 0
2031-03-05 11:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-03-05 12:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-03-05 13:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-03-05 14:00 | 28.6021 | 0.01382% | 29.8702 | 31.1945 | 32.5775 | 34.0218 | 0 | 0 | 0 | 0
2031-03-05 15:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-03-05 16:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-03-05 17:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-03-05 18:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-03-05 19:00 | 29.3247 | 0.01417% | 30.6248 | 31.9826 | 33.4005 | 34.8813 | 0 | 0 | 0 | 0
2031-03-05 20:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-03-05 21:00 | 28.2342 | 0.01364% | 29.486 | 30.7932 | 32.1585 | 33.5842 | 0 | 0 | 0 | 0
2031-03-05 22:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-03-05 23:00 | 25.7379 | 0.01244% | 26.879 | 28.0707 | 29.3152 | 30.6149 | 0 | 0 | 0 | 0
2031-03-06 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-03-06 01:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-03-06 02:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-03-06 03:00 | 19.379 | 0.009365% | 20.2382 | 21.1354 | 22.0725 | 23.0511 | 0 | 0 | 0 | 0
2031-03-06 04:00 | 18.8666 | 0.009118% | 19.7031 | 20.5766 | 21.4889 | 22.4416 | 0 | 0 | 0 | 0
2031-03-06 05:00 | 19.1819 | 0.00927% | 20.0323 | 20.9205 | 21.848 | 22.8166 | 0 | 0 | 0 | 0
2031-03-06 06:00 | 20.8373 | 0.01007% | 21.7612 | 22.726 | 23.7335 | 24.7857 | 0 | 0 | 0 | 0
2031-03-06 07:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-03-06 08:00 | 26.3029 | 0.01271% | 27.469 | 28.6869 | 29.9587 | 31.2869 | 0 | 0 | 0 | 0
2031-03-06 09:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-03-06 10:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-06 11:00 | 27.8269 | 0.01345% | 29.0606 | 30.349 | 31.6946 | 33.0998 | 0 | 0 | 0 | 0
2031-03-06 12:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-03-06 13:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-03-06 14:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-03-06 15:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-03-06 16:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-03-06 17:00 | 30.3232 | 0.01465% | 31.6676 | 33.0716 | 34.5378 | 36.069 | 0 | 0 | 0 | 0
2031-03-06 18:00 | 31.4662 | 0.01521% | 32.8613 | 34.3182 | 35.8397 | 37.4287 | 0 | 0 | 0 | 0.3858
2031-03-06 19:00 | 31.4531 | 0.0152% | 32.8476 | 34.3039 | 35.8247 | 37.413 | 0 | 0 | 0 | 0.37173
2031-03-06 20:00 | 31.5713 | 0.01526% | 32.9711 | 34.4328 | 35.9594 | 37.5537 | 0 | 0 | 0 | 0.49832
2031-03-06 21:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-03-06 22:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-03-06 23:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-03-07 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-03-07 01:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-03-07 02:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-03-07 03:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-03-07 04:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-03-07 05:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-03-07 06:00 | 21.3629 | 0.01032% | 22.31 | 23.2991 | 24.3321 | 25.4109 | 0 | 0 | 0 | 0
2031-03-07 07:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-03-07 08:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-03-07 09:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-03-07 10:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-07 11:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-03-07 12:00 | 28.2079 | 0.01363% | 29.4585 | 30.7646 | 32.1285 | 33.553 | 0 | 0 | 0 | 0
2031-03-07 13:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-07 14:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-03-07 15:00 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-03-07 16:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-03-07 17:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-03-07 18:00 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-03-07 19:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-03-07 20:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-03-07 21:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-03-07 22:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-03-07 23:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-03-08 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-03-08 01:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-03-08 02:00 | 21.2052 | 0.01025% | 22.1454 | 23.1272 | 24.1525 | 25.2233 | 0 | 0 | 0 | 0
2031-03-08 03:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-03-08 04:00 | 20.0096 | 0.00967% | 20.8968 | 21.8232 | 22.7908 | 23.8012 | 0 | 0 | 0 | 0
2031-03-08 05:00 | 20.1673 | 0.009746% | 21.0614 | 21.9952 | 22.9703 | 23.9887 | 0 | 0 | 0 | 0
2031-03-08 06:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-03-08 07:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-03-08 08:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-03-08 09:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-03-08 10:00 | 25.3569 | 0.01225% | 26.4811 | 27.6552 | 28.8813 | 30.1617 | 0 | 0 | 0 | 0
2031-03-08 11:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-03-08 12:00 | 26.6051 | 0.01286% | 27.7846 | 29.0164 | 30.3029 | 31.6464 | 0 | 0 | 0 | 0
2031-03-08 13:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-03-08 14:00 | 26.3948 | 0.01276% | 27.5651 | 28.7872 | 30.0634 | 31.3963 | 0 | 0 | 0 | 0
2031-03-08 15:00 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-03-08 16:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-03-08 17:00 | 26.7496 | 0.01293% | 27.9355 | 29.174 | 30.4675 | 31.8183 | 0 | 0 | 0 | 0
2031-03-08 18:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-03-08 19:00 | 28.8648 | 0.01395% | 30.1446 | 31.481 | 32.8768 | 34.3344 | 0 | 0 | 0 | 0
2031-03-08 20:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-03-08 21:00 | 28.2999 | 0.01368% | 29.5546 | 30.8649 | 32.2333 | 33.6624 | 0 | 0 | 0 | 0
2031-03-08 22:00 | 27.262 | 0.01317% | 28.4706 | 29.7329 | 31.0511 | 32.4278 | 0 | 0 | 0 | 0
2031-03-08 23:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-03-09 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-03-09 01:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-03-09 02:00 | 21.0081 | 0.01015% | 21.9395 | 22.9122 | 23.9281 | 24.9889 | 0 | 0 | 0 | 0
2031-03-09 03:00 | 20.2198 | 0.009772% | 21.1163 | 22.0525 | 23.0302 | 24.0512 | 0 | 0 | 0 | 0
2031-03-09 04:00 | 19.6812 | 0.009511% | 20.5537 | 21.465 | 22.4166 | 23.4105 | 0 | 0 | 0 | 0
2031-03-09 05:00 | 19.668 | 0.009505% | 20.54 | 21.4507 | 22.4017 | 23.3949 | 0 | 0 | 0 | 0
2031-03-09 06:00 | 19.7994 | 0.009568% | 20.6772 | 21.594 | 22.5513 | 23.5511 | 0 | 0 | 0 | 0
2031-03-09 07:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-03-09 08:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-03-09 09:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-03-09 10:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-03-09 11:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-03-09 12:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-03-09 13:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-03-09 14:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-03-09 15:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-03-09 16:00 | 26.9466 | 0.01302% | 28.1413 | 29.389 | 30.692 | 32.0527 | 0 | 0 | 0 | 0
2031-03-09 17:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-03-09 18:00 | 27.7612 | 0.01342% | 28.992 | 30.2774 | 31.6197 | 33.0216 | 0 | 0 | 0 | 0
2031-03-09 19:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-03-09 20:00 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-03-09 21:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-03-09 22:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-03-09 23:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-03-10 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-03-10 01:00 | 18.998 | 0.009181% | 19.8403 | 20.7199 | 21.6385 | 22.5978 | 0 | 0 | 0 | 0
2031-03-10 02:00 | 18.0652 | 0.00873% | 18.8661 | 19.7025 | 20.576 | 21.4883 | 0 | 0 | 0 | 0
2031-03-10 03:00 | 17.8681 | 0.008635% | 18.6603 | 19.4876 | 20.3516 | 21.2539 | 0 | 0 | 0 | 0
2031-03-10 04:00 | 17.9601 | 0.008679% | 18.7563 | 19.5879 | 20.4563 | 21.3632 | 0 | 0 | 0 | 0
2031-03-10 05:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-03-10 06:00 | 21.1001 | 0.0102% | 22.0356 | 23.0125 | 24.0328 | 25.0983 | 0 | 0 | 0 | 0
2031-03-10 07:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-03-10 08:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-03-10 09:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-03-10 10:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-03-10 11:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-03-10 12:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-03-10 13:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-03-10 14:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-03-10 15:00 | 23.5832 | 0.0114% | 24.6288 | 25.7207 | 26.8611 | 28.052 | 0 | 0 | 0 | 0
2031-03-10 16:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-03-10 17:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-03-10 18:00 | 25.4226 | 0.01229% | 26.5497 | 27.7268 | 28.9561 | 30.2399 | 0 | 0 | 0 | 0
2031-03-10 19:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-03-10 20:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-03-10 21:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-03-10 22:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-03-10 23:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-03-11 | 20.0359 | 0.009683% | 20.9242 | 21.8519 | 22.8207 | 23.8324 | 0 | 0 | 0 | 0
2031-03-11 01:00 | 18.7352 | 0.009054% | 19.5658 | 20.4333 | 21.3392 | 22.2853 | 0 | 0 | 0 | 0
2031-03-11 02:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-03-11 03:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-03-11 04:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-03-11 05:00 | 19.0899 | 0.009225% | 19.9363 | 20.8202 | 21.7433 | 22.7072 | 0 | 0 | 0 | 0
2031-03-11 06:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-03-11 07:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-03-11 08:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-03-11 09:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-03-11 10:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-03-11 11:00 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-03-11 12:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-03-11 13:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-03-11 14:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-03-11 15:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-03-11 16:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-03-11 17:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-03-11 18:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-03-11 19:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-03-11 20:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-03-11 21:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-03-11 22:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-03-11 23:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-03-12 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-03-12 01:00 | 19.9045 | 0.009619% | 20.787 | 21.7086 | 22.671 | 23.6762 | 0 | 0 | 0 | 0
2031-03-12 02:00 | 19.2213 | 0.009289% | 20.0735 | 20.9635 | 21.8929 | 22.8635 | 0 | 0 | 0 | 0
2031-03-12 03:00 | 19.0768 | 0.009219% | 19.9226 | 20.8059 | 21.7283 | 22.6916 | 0 | 0 | 0 | 0
2031-03-12 04:00 | 19.5892 | 0.009467% | 20.4577 | 21.3647 | 22.3119 | 23.3011 | 0 | 0 | 0 | 0
2031-03-12 05:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-03-12 06:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-03-12 07:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-03-12 08:00 | 26.5262 | 0.01282% | 27.7023 | 28.9305 | 30.2131 | 31.5526 | 0 | 0 | 0 | 0
2031-03-12 09:00 | 26.9466 | 0.01302% | 28.1413 | 29.389 | 30.692 | 32.0527 | 0 | 0 | 0 | 0
2031-03-12 10:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-12 11:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-03-12 12:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-03-12 13:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-03-12 14:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-03-12 15:00 | 27.9452 | 0.0135% | 29.1841 | 30.478 | 31.8292 | 33.2404 | 0 | 0 | 0 | 0
2031-03-12 16:00 | 28.5889 | 0.01382% | 29.8564 | 31.1801 | 32.5625 | 34.0062 | 0 | 0 | 0 | 0
2031-03-12 17:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-03-12 18:00 | 29.1145 | 0.01407% | 30.4053 | 31.7533 | 33.1611 | 34.6313 | 0 | 0 | 0 | 0
2031-03-12 19:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-03-12 20:00 | 29.0356 | 0.01403% | 30.3229 | 31.6673 | 33.0713 | 34.5375 | 0 | 0 | 0 | 0
2031-03-12 21:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-03-12 22:00 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-03-12 23:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-03-13 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-03-13 01:00 | 20.9424 | 0.01012% | 21.8709 | 22.8406 | 23.8532 | 24.9108 | 0 | 0 | 0 | 0
2031-03-13 02:00 | 20.0753 | 0.009702% | 20.9654 | 21.8949 | 22.8656 | 23.8793 | 0 | 0 | 0 | 0
2031-03-13 03:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-03-13 04:00 | 20.0359 | 0.009683% | 20.9242 | 21.8519 | 22.8207 | 23.8324 | 0 | 0 | 0 | 0
2031-03-13 05:00 | 21.1921 | 0.01024% | 22.1316 | 23.1128 | 24.1376 | 25.2077 | 0 | 0 | 0 | 0
2031-03-13 06:00 | 23.3599 | 0.01129% | 24.3956 | 25.4771 | 26.6067 | 27.7863 | 0 | 0 | 0 | 0
2031-03-13 07:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-03-13 08:00 | 26.3423 | 0.01273% | 27.5102 | 28.7298 | 30.0036 | 31.3338 | 0 | 0 | 0 | 0
2031-03-13 09:00 | 26.3291 | 0.01272% | 27.4965 | 28.7155 | 29.9886 | 31.3182 | 0 | 0 | 0 | 0
2031-03-13 10:00 | 25.6722 | 0.01241% | 26.8104 | 27.9991 | 29.2404 | 30.5368 | 0 | 0 | 0 | 0
2031-03-13 11:00 | 26.0532 | 0.01259% | 27.2083 | 28.4146 | 29.6744 | 30.99 | 0 | 0 | 0 | 0
2031-03-13 12:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-03-13 13:00 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-03-13 14:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-03-13 15:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-03-13 16:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-03-13 17:00 | 26.2503 | 0.01269% | 27.4141 | 28.6295 | 29.8988 | 31.2244 | 0 | 0 | 0 | 0
2031-03-13 18:00 | 26.224 | 0.01267% | 27.3867 | 28.6009 | 29.8689 | 31.1932 | 0 | 0 | 0 | 0
2031-03-13 19:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-03-13 20:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-03-13 21:00 | 27.2751 | 0.01318% | 28.4844 | 29.7472 | 31.0661 | 32.4434 | 0 | 0 | 0 | 0
2031-03-13 22:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-03-13 23:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-03-14 | 21.4286 | 0.01036% | 22.3786 | 23.3708 | 24.4069 | 25.489 | 0 | 0 | 0 | 0
2031-03-14 01:00 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-03-14 02:00 | 19.379 | 0.009365% | 20.2382 | 21.1354 | 22.0725 | 23.0511 | 0 | 0 | 0 | 0
2031-03-14 03:00 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-03-14 04:00 | 18.9717 | 0.009168% | 19.8128 | 20.6912 | 21.6086 | 22.5666 | 0 | 0 | 0 | 0
2031-03-14 05:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-03-14 06:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-03-14 07:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-03-14 08:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-03-14 09:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-03-14 10:00 | 25.2387 | 0.0122% | 26.3576 | 27.5262 | 28.7466 | 30.0211 | 0 | 0 | 0 | 0
2031-03-14 11:00 | 25.2518 | 0.0122% | 26.3714 | 27.5405 | 28.7615 | 30.0367 | 0 | 0 | 0 | 0
2031-03-14 12:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-03-14 13:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-03-14 14:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-03-14 15:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-03-14 16:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-03-14 17:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-03-14 18:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-03-14 19:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-03-14 20:00 | 25.2387 | 0.0122% | 26.3576 | 27.5262 | 28.7466 | 30.0211 | 0 | 0 | 0 | 0
2031-03-14 21:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-03-14 22:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-03-14 23:00 | 21.2052 | 0.01025% | 22.1454 | 23.1272 | 24.1525 | 25.2233 | 0 | 0 | 0 | 0
2031-03-15 | 19.6418 | 0.009492% | 20.5126 | 21.422 | 22.3718 | 23.3636 | 0 | 0 | 0 | 0
2031-03-15 01:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-03-15 02:00 | 17.2769 | 0.008349% | 18.0428 | 18.8428 | 19.6782 | 20.5506 | 0 | 0 | 0 | 0
2031-03-15 03:00 | 16.4229 | 0.007937% | 17.151 | 17.9114 | 18.7055 | 19.5348 | 0 | 0 | 0 | 0
2031-03-15 04:00 | 16.4886 | 0.007968% | 17.2196 | 17.983 | 18.7803 | 19.6129 | 0 | 0 | 0 | 0
2031-03-15 05:00 | 16.7382 | 0.008089% | 17.4803 | 18.2553 | 19.0646 | 19.9099 | 0 | 0 | 0 | 0
2031-03-15 06:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-03-15 07:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-03-15 08:00 | 20.614 | 0.009962% | 21.5279 | 22.4824 | 23.4791 | 24.5201 | 0 | 0 | 0 | 0
2031-03-15 09:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-03-15 10:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-03-15 11:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-03-15 12:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-03-15 13:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-03-15 14:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-03-15 15:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-03-15 16:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-03-15 17:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-03-15 18:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-03-15 19:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-03-15 20:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-03-15 21:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-03-15 22:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-03-15 23:00 | 20.5614 | 0.009937% | 21.473 | 22.425 | 23.4193 | 24.4576 | 0 | 0 | 0 | 0
2031-03-16 | 18.814 | 0.009092% | 19.6482 | 20.5193 | 21.429 | 22.3791 | 0 | 0 | 0 | 0
2031-03-16 01:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-03-16 02:00 | 16.4886 | 0.007968% | 17.2196 | 17.983 | 18.7803 | 19.6129 | 0 | 0 | 0 | 0
2031-03-16 03:00 | 15.8579 | 0.007664% | 16.561 | 17.2952 | 18.062 | 18.8628 | 0 | 0 | 0 | 0
2031-03-16 04:00 | 15.6346 | 0.007556% | 16.3277 | 17.0516 | 17.8076 | 18.5971 | 0 | 0 | 0 | 0
2031-03-16 05:00 | 15.9762 | 0.007721% | 16.6845 | 17.4242 | 18.1967 | 19.0034 | 0 | 0 | 0 | 0
2031-03-16 06:00 | 16.1207 | 0.007791% | 16.8354 | 17.5818 | 18.3613 | 19.1754 | 0 | 0 | 0 | 0
2031-03-16 07:00 | 17.7104 | 0.008559% | 18.4956 | 19.3156 | 20.172 | 21.0663 | 0 | 0 | 0 | 0
2031-03-16 08:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-03-16 09:00 | 21.3366 | 0.01031% | 22.2826 | 23.2705 | 24.3022 | 25.3796 | 0 | 0 | 0 | 0
2031-03-16 10:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-03-16 11:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-03-16 12:00 | 24.6869 | 0.01193% | 25.7814 | 26.9244 | 28.1181 | 29.3647 | 0 | 0 | 0 | 0
2031-03-16 13:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-03-16 14:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-03-16 15:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-03-16 16:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-03-16 17:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-03-16 18:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-03-16 19:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-03-16 20:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-03-16 21:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-03-16 22:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-03-16 23:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-03-17 | 18.4856 | 0.008933% | 19.3051 | 20.161 | 21.0549 | 21.9884 | 0 | 0 | 0 | 0
2031-03-17 01:00 | 17.1455 | 0.008286% | 17.9056 | 18.6995 | 19.5285 | 20.3943 | 0 | 0 | 0 | 0
2031-03-17 02:00 | 16.6856 | 0.008064% | 17.4254 | 18.198 | 19.0048 | 19.8473 | 0 | 0 | 0 | 0
2031-03-17 03:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-03-17 04:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-03-17 05:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-03-17 06:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-03-17 07:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-03-17 08:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-03-17 09:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-03-17 10:00 | 25.554 | 0.01235% | 26.6869 | 27.8701 | 29.1057 | 30.3961 | 0 | 0 | 0 | 0
2031-03-17 11:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-03-17 12:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-03-17 13:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-03-17 14:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-03-17 15:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-03-17 16:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-03-17 17:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-03-17 18:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-03-17 19:00 | 26.7364 | 0.01292% | 27.9218 | 29.1597 | 30.4525 | 31.8026 | 0 | 0 | 0 | 0
2031-03-17 20:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-03-17 21:00 | 26.3423 | 0.01273% | 27.5102 | 28.7298 | 30.0036 | 31.3338 | 0 | 0 | 0 | 0
2031-03-17 22:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-03-17 23:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-03-18 | 20.8242 | 0.01006% | 21.7474 | 22.7116 | 23.7185 | 24.7701 | 0 | 0 | 0 | 0
2031-03-18 01:00 | 19.5104 | 0.009429% | 20.3754 | 21.2787 | 22.2221 | 23.2073 | 0 | 0 | 0 | 0
2031-03-18 02:00 | 18.8272 | 0.009099% | 19.6619 | 20.5336 | 21.444 | 22.3947 | 0 | 0 | 0 | 0
2031-03-18 03:00 | 18.4462 | 0.008914% | 19.264 | 20.1181 | 21.01 | 21.9415 | 0 | 0 | 0 | 0
2031-03-18 04:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-03-18 05:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-03-18 06:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-03-18 07:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-03-18 08:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-03-18 09:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-03-18 10:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-03-18 11:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-03-18 12:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-03-18 13:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-03-18 14:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-03-18 15:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-03-18 16:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-03-18 17:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-03-18 18:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-03-18 19:00 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-03-18 20:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-03-18 21:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-03-18 22:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-03-18 23:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-03-19 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-03-19 01:00 | 17.8944 | 0.008648% | 18.6877 | 19.5162 | 20.3815 | 21.2851 | 0 | 0 | 0 | 0
2031-03-19 02:00 | 17.2637 | 0.008343% | 18.0291 | 18.8284 | 19.6632 | 20.535 | 0 | 0 | 0 | 0
2031-03-19 03:00 | 16.8696 | 0.008152% | 17.6175 | 18.3986 | 19.2143 | 20.0661 | 0 | 0 | 0 | 0
2031-03-19 04:00 | 17.382 | 0.0084% | 18.1526 | 18.9574 | 19.7979 | 20.6756 | 0 | 0 | 0 | 0
2031-03-19 05:00 | 18.3805 | 0.008883% | 19.1954 | 20.0464 | 20.9352 | 21.8633 | 0 | 0 | 0 | 0
2031-03-19 06:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-03-19 07:00 | 23.846 | 0.01152% | 24.9032 | 26.0073 | 27.1604 | 28.3645 | 0 | 0 | 0 | 0
2031-03-19 08:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-03-19 09:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-03-19 10:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-03-19 11:00 | 23.938 | 0.01157% | 24.9993 | 26.1076 | 27.2651 | 28.4739 | 0 | 0 | 0 | 0
2031-03-19 12:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-03-19 13:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-03-19 14:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-03-19 15:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-03-19 16:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-03-19 17:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-03-19 18:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-03-19 19:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-03-19 20:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-03-19 21:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-03-19 22:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-03-19 23:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-03-20 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-03-20 01:00 | 16.909 | 0.008172% | 17.6587 | 18.4416 | 19.2592 | 20.113 | 0 | 0 | 0 | 0
2031-03-20 02:00 | 16.2258 | 0.007841% | 16.9452 | 17.6964 | 18.481 | 19.3004 | 0 | 0 | 0 | 0
2031-03-20 03:00 | 15.7265 | 0.0076% | 16.4238 | 17.1519 | 17.9124 | 18.7065 | 0 | 0 | 0 | 0
2031-03-20 04:00 | 15.674 | 0.007575% | 16.3689 | 17.0946 | 17.8525 | 18.644 | 0 | 0 | 0 | 0
2031-03-20 05:00 | 16.7251 | 0.008083% | 17.4666 | 18.2409 | 19.0497 | 19.8942 | 0 | 0 | 0 | 0
2031-03-20 06:00 | 19.5235 | 0.009435% | 20.3891 | 21.293 | 22.2371 | 23.223 | 0 | 0 | 0 | 0
2031-03-20 07:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-03-20 08:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-03-20 09:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-03-20 10:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-03-20 11:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-03-20 12:00 | 24.9628 | 0.01206% | 26.0695 | 27.2253 | 28.4323 | 29.6929 | 0 | 0 | 0 | 0
2031-03-20 13:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-03-20 14:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-03-20 15:00 | 25.3044 | 0.01223% | 26.4262 | 27.5978 | 28.8214 | 30.0992 | 0 | 0 | 0 | 0
2031-03-20 16:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-03-20 17:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-03-20 18:00 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-03-20 19:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-03-20 20:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-03-20 21:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-03-20 22:00 | 26.3686 | 0.01274% | 27.5376 | 28.7585 | 30.0335 | 31.3651 | 0 | 0 | 0 | 0
2031-03-20 23:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-03-21 | 20.9819 | 0.01014% | 21.9121 | 22.8836 | 23.8981 | 24.9577 | 0 | 0 | 0 | 0
2031-03-21 01:00 | 19.6023 | 0.009473% | 20.4714 | 21.379 | 22.3269 | 23.3167 | 0 | 0 | 0 | 0
2031-03-21 02:00 | 19.1031 | 0.009232% | 19.95 | 20.8345 | 21.7582 | 22.7229 | 0 | 0 | 0 | 0
2031-03-21 03:00 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-03-21 04:00 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-03-21 05:00 | 19.6549 | 0.009499% | 20.5263 | 21.4363 | 22.3867 | 23.3792 | 0 | 0 | 0 | 0
2031-03-21 06:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-03-21 07:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-03-21 08:00 | 25.7248 | 0.01243% | 26.8653 | 28.0564 | 29.3003 | 30.5993 | 0 | 0 | 0 | 0
2031-03-21 09:00 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-03-21 10:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-03-21 11:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-03-21 12:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-03-21 13:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-03-21 14:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-03-21 15:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-03-21 16:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-03-21 17:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-03-21 18:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-03-21 19:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-03-21 20:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-03-21 21:00 | 25.7905 | 0.01246% | 26.9339 | 28.128 | 29.3751 | 30.6774 | 0 | 0 | 0 | 0
2031-03-21 22:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-03-21 23:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-03-22 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-03-22 01:00 | 19.0374 | 0.0092% | 19.8814 | 20.7629 | 21.6834 | 22.6447 | 0 | 0 | 0 | 0
2031-03-22 02:00 | 17.6841 | 0.008546% | 18.4682 | 19.287 | 20.1421 | 21.0351 | 0 | 0 | 0 | 0
2031-03-22 03:00 | 17.579 | 0.008495% | 18.3584 | 19.1723 | 20.0223 | 20.91 | 0 | 0 | 0 | 0
2031-03-22 04:00 | 17.3557 | 0.008387% | 18.1252 | 18.9287 | 19.768 | 20.6444 | 0 | 0 | 0 | 0
2031-03-22 05:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-03-22 06:00 | 18.2754 | 0.008832% | 19.0856 | 19.9318 | 20.8155 | 21.7383 | 0 | 0 | 0 | 0
2031-03-22 07:00 | 19.7863 | 0.009562% | 20.6635 | 21.5796 | 22.5364 | 23.5355 | 0 | 0 | 0 | 0
2031-03-22 08:00 | 21.9935 | 0.01063% | 22.9686 | 23.9869 | 25.0504 | 26.161 | 0 | 0 | 0 | 0
2031-03-22 09:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-03-22 10:00 | 25.554 | 0.01235% | 26.6869 | 27.8701 | 29.1057 | 30.3961 | 0 | 0 | 0 | 0
2031-03-22 11:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-03-22 12:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-03-22 13:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-03-22 14:00 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-03-22 15:00 | 25.6328 | 0.01239% | 26.7693 | 27.9561 | 29.1955 | 30.4899 | 0 | 0 | 0 | 0
2031-03-22 16:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-03-22 17:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-03-22 18:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-03-22 19:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-03-22 20:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-03-22 21:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-03-22 22:00 | 25.9876 | 0.01256% | 27.1397 | 28.343 | 29.5996 | 30.9119 | 0 | 0 | 0 | 0
2031-03-22 23:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-03-23 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-03-23 01:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-03-23 02:00 | 20.3906 | 0.009854% | 21.2947 | 22.2388 | 23.2247 | 24.2544 | 0 | 0 | 0 | 0
2031-03-23 03:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-03-23 04:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-03-23 05:00 | 20.0228 | 0.009676% | 20.9105 | 21.8375 | 22.8057 | 23.8168 | 0 | 0 | 0 | 0
2031-03-23 06:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-03-23 07:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-03-23 08:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-03-23 09:00 | 24.5686 | 0.01187% | 25.6579 | 26.7954 | 27.9834 | 29.224 | 0 | 0 | 0 | 0
2031-03-23 10:00 | 25.2387 | 0.0122% | 26.3576 | 27.5262 | 28.7466 | 30.0211 | 0 | 0 | 0 | 0
2031-03-23 11:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-03-23 12:00 | 26.3029 | 0.01271% | 27.469 | 28.6869 | 29.9587 | 31.2869 | 0 | 0 | 0 | 0
2031-03-23 13:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-03-23 14:00 | 26.2372 | 0.01268% | 27.4004 | 28.6152 | 29.8839 | 31.2088 | 0 | 0 | 0 | 0
2031-03-23 15:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-03-23 16:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-03-23 17:00 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-03-23 18:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-03-23 19:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-03-23 20:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-03-23 21:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-03-23 22:00 | 26.1846 | 0.01265% | 27.3455 | 28.5579 | 29.824 | 31.1463 | 0 | 0 | 0 | 0
2031-03-23 23:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-03-24 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-03-24 01:00 | 19.9439 | 0.009638% | 20.8282 | 21.7516 | 22.7159 | 23.7231 | 0 | 0 | 0 | 0
2031-03-24 02:00 | 19.0505 | 0.009206% | 19.8951 | 20.7772 | 21.6984 | 22.6604 | 0 | 0 | 0 | 0
2031-03-24 03:00 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-03-24 04:00 | 18.9717 | 0.009168% | 19.8128 | 20.6912 | 21.6086 | 22.5666 | 0 | 0 | 0 | 0
2031-03-24 05:00 | 19.9439 | 0.009638% | 20.8282 | 21.7516 | 22.7159 | 23.7231 | 0 | 0 | 0 | 0
2031-03-24 06:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-03-24 07:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-03-24 08:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-03-24 09:00 | 25.6854 | 0.01241% | 26.8241 | 28.0134 | 29.2554 | 30.5524 | 0 | 0 | 0 | 0
2031-03-24 10:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-03-24 11:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-03-24 12:00 | 26.6051 | 0.01286% | 27.7846 | 29.0164 | 30.3029 | 31.6464 | 0 | 0 | 0 | 0
2031-03-24 13:00 | 26.7759 | 0.01294% | 27.963 | 29.2027 | 30.4974 | 31.8495 | 0 | 0 | 0 | 0
2031-03-24 14:00 | 26.789 | 0.01295% | 27.9767 | 29.217 | 30.5124 | 31.8652 | 0 | 0 | 0 | 0
2031-03-24 15:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-03-24 16:00 | 29.1145 | 0.01407% | 30.4053 | 31.7533 | 33.1611 | 34.6313 | 0 | 0 | 0 | 0
2031-03-24 17:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-03-24 18:00 | 29.0094 | 0.01402% | 30.2955 | 31.6387 | 33.0414 | 34.5063 | 0 | 0 | 0 | 0
2031-03-24 19:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-03-24 20:00 | 28.2342 | 0.01364% | 29.486 | 30.7932 | 32.1585 | 33.5842 | 0 | 0 | 0 | 0
2031-03-24 21:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-03-24 22:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-03-24 23:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-03-25 | 20.6009 | 0.009956% | 21.5142 | 22.468 | 23.4642 | 24.5044 | 0 | 0 | 0 | 0
2031-03-25 01:00 | 19.4841 | 0.009416% | 20.3479 | 21.2501 | 22.1922 | 23.1761 | 0 | 0 | 0 | 0
2031-03-25 02:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0
2031-03-25 03:00 | 18.1703 | 0.008781% | 18.9758 | 19.8171 | 20.6957 | 21.6133 | 0 | 0 | 0 | 0
2031-03-25 04:00 | 18.433 | 0.008908% | 19.2503 | 20.1037 | 20.995 | 21.9259 | 0 | 0 | 0 | 0
2031-03-25 05:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-03-25 06:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-03-25 07:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-03-25 08:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-03-25 09:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-03-25 10:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-03-25 11:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-03-25 12:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-03-25 13:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-03-25 14:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-03-25 15:00 | 27.0123 | 0.01305% | 28.2099 | 29.4606 | 30.7668 | 32.1308 | 0 | 0 | 0 | 0
2031-03-25 16:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-03-25 17:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-03-25 18:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-03-25 19:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-03-25 20:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-03-25 21:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-03-25 22:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-03-25 23:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-03-26 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-03-26 01:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-03-26 02:00 | 18.998 | 0.009181% | 19.8403 | 20.7199 | 21.6385 | 22.5978 | 0 | 0 | 0 | 0
2031-03-26 03:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-03-26 04:00 | 19.0768 | 0.009219% | 19.9226 | 20.8059 | 21.7283 | 22.6916 | 0 | 0 | 0 | 0
2031-03-26 05:00 | 20.8242 | 0.01006% | 21.7474 | 22.7116 | 23.7185 | 24.7701 | 0 | 0 | 0 | 0
2031-03-26 06:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-03-26 07:00 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-03-26 08:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-03-26 09:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-03-26 10:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-03-26 11:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-03-26 12:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-03-26 13:00 | 26.7759 | 0.01294% | 27.963 | 29.2027 | 30.4974 | 31.8495 | 0 | 0 | 0 | 0
2031-03-26 14:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0
2031-03-26 15:00 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-03-26 16:00 | 27.3277 | 0.01321% | 28.5392 | 29.8045 | 31.1259 | 32.5059 | 0 | 0 | 0 | 0
2031-03-26 17:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-03-26 18:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-03-26 19:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-03-26 20:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-03-26 21:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-03-26 22:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-03-26 23:00 | 24.2664 | 0.01173% | 25.3423 | 26.4658 | 27.6392 | 28.8646 | 0 | 0 | 0 | 0
2031-03-27 | 21.9278 | 0.0106% | 22.9 | 23.9153 | 24.9756 | 26.0829 | 0 | 0 | 0 | 0
2031-03-27 01:00 | 20.7191 | 0.01001% | 21.6377 | 22.597 | 23.5988 | 24.6451 | 0 | 0 | 0 | 0
2031-03-27 02:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-03-27 03:00 | 19.379 | 0.009365% | 20.2382 | 21.1354 | 22.0725 | 23.0511 | 0 | 0 | 0 | 0
2031-03-27 04:00 | 20.0359 | 0.009683% | 20.9242 | 21.8519 | 22.8207 | 23.8324 | 0 | 0 | 0 | 0
2031-03-27 05:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-03-27 06:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-03-27 07:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-03-27 08:00 | 26.9992 | 0.01305% | 28.1962 | 29.4463 | 30.7518 | 32.1152 | 0 | 0 | 0 | 0
2031-03-27 09:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-03-27 10:00 | 26.3423 | 0.01273% | 27.5102 | 28.7298 | 30.0036 | 31.3338 | 0 | 0 | 0 | 0
2031-03-27 11:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-03-27 12:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-03-27 13:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-03-27 14:00 | 25.5934 | 0.01237% | 26.7281 | 27.9131 | 29.1506 | 30.443 | 0 | 0 | 0 | 0
2031-03-27 15:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-03-27 16:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-03-27 17:00 | 26.3029 | 0.01271% | 27.469 | 28.6869 | 29.9587 | 31.2869 | 0 | 0 | 0 | 0
2031-03-27 18:00 | 26.3291 | 0.01272% | 27.4965 | 28.7155 | 29.9886 | 31.3182 | 0 | 0 | 0 | 0
2031-03-27 19:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-03-27 20:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-03-27 21:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-03-27 22:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-03-27 23:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-03-28 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-03-28 01:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-03-28 02:00 | 18.3411 | 0.008864% | 19.1542 | 20.0034 | 20.8903 | 21.8165 | 0 | 0 | 0 | 0
2031-03-28 03:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-03-28 04:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-03-28 05:00 | 19.5235 | 0.009435% | 20.3891 | 21.293 | 22.2371 | 23.223 | 0 | 0 | 0 | 0
2031-03-28 06:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-03-28 07:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-03-28 08:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-03-28 09:00 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-03-28 10:00 | 27.2751 | 0.01318% | 28.4844 | 29.7472 | 31.0661 | 32.4434 | 0 | 0 | 0 | 0
2031-03-28 11:00 | 27.262 | 0.01317% | 28.4706 | 29.7329 | 31.0511 | 32.4278 | 0 | 0 | 0 | 0
2031-03-28 12:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-03-28 13:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-03-28 14:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-03-28 15:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-03-28 16:00 | 27.4196 | 0.01325% | 28.6353 | 29.9048 | 31.2307 | 32.6153 | 0 | 0 | 0 | 0
2031-03-28 17:00 | 28.3787 | 0.01371% | 29.6369 | 30.9509 | 32.3231 | 33.7561 | 0 | 0 | 0 | 0
2031-03-28 18:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-03-28 19:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-03-28 20:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-03-28 21:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-03-28 22:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-03-28 23:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-03-29 | 21.5468 | 0.01041% | 22.5021 | 23.4997 | 24.5416 | 25.6296 | 0 | 0 | 0 | 0
2031-03-29 01:00 | 19.9045 | 0.009619% | 20.787 | 21.7086 | 22.671 | 23.6762 | 0 | 0 | 0 | 0
2031-03-29 02:00 | 18.7484 | 0.00906% | 19.5796 | 20.4476 | 21.3542 | 22.3009 | 0 | 0 | 0 | 0
2031-03-29 03:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-03-29 04:00 | 18.0652 | 0.00873% | 18.8661 | 19.7025 | 20.576 | 21.4883 | 0 | 0 | 0 | 0
2031-03-29 05:00 | 18.1965 | 0.008794% | 19.0033 | 19.8458 | 20.7257 | 21.6445 | 0 | 0 | 0 | 0
2031-03-29 06:00 | 19.0768 | 0.009219% | 19.9226 | 20.8059 | 21.7283 | 22.6916 | 0 | 0 | 0 | 0
2031-03-29 07:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-03-29 08:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-03-29 09:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-03-29 10:00 | 26.2503 | 0.01269% | 27.4141 | 28.6295 | 29.8988 | 31.2244 | 0 | 0 | 0 | 0
2031-03-29 11:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-29 12:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-03-29 13:00 | 28.1816 | 0.01362% | 29.4311 | 30.7359 | 32.0986 | 33.5217 | 0 | 0 | 0 | 0
2031-03-29 14:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-03-29 15:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-03-29 16:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-03-29 17:00 | 29.9028 | 0.01445% | 31.2285 | 32.613 | 34.0589 | 35.5689 | 0 | 0 | 0 | 0
2031-03-29 18:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-03-29 19:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-03-29 20:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-03-29 21:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-03-29 22:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-03-29 23:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-03-30 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-03-30 01:00 | 20.4957 | 0.009905% | 21.4044 | 22.3534 | 23.3444 | 24.3794 | 0 | 0 | 0 | 0
2031-03-30 02:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-03-30 03:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-03-30 04:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-03-30 05:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0
2031-03-30 06:00 | 19.0505 | 0.009206% | 19.8951 | 20.7772 | 21.6984 | 22.6604 | 0 | 0 | 0 | 0
2031-03-30 07:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-03-30 08:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-03-30 09:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-03-30 10:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-03-30 11:00 | 27.8926 | 0.01348% | 29.1292 | 30.4207 | 31.7694 | 33.1779 | 0 | 0 | 0 | 0
2031-03-30 12:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-03-30 13:00 | 28.8648 | 0.01395% | 30.1446 | 31.481 | 32.8768 | 34.3344 | 0 | 0 | 0 | 0
2031-03-30 14:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-03-30 15:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-03-30 16:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-03-30 17:00 | 30.6911 | 0.01483% | 32.0518 | 33.4728 | 34.9568 | 36.5066 | 0 | 0 | 0 | 0
2031-03-30 18:00 | 29.7977 | 0.0144% | 31.1187 | 32.4984 | 33.9392 | 35.4439 | 0 | 0 | 0 | 0
2031-03-30 19:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-03-30 20:00 | 27.7875 | 0.01343% | 29.0195 | 30.306 | 31.6497 | 33.0529 | 0 | 0 | 0 | 0
2031-03-30 21:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-03-30 22:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-03-30 23:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-03-31 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-03-31 01:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-03-31 02:00 | 17.1586 | 0.008292% | 17.9193 | 18.7138 | 19.5435 | 20.41 | 0 | 0 | 0 | 0
2031-03-31 03:00 | 16.5017 | 0.007975% | 17.2333 | 17.9974 | 18.7953 | 19.6286 | 0 | 0 | 0 | 0
2031-03-31 04:00 | 16.528 | 0.007987% | 17.2608 | 18.026 | 18.8252 | 19.6598 | 0 | 0 | 0 | 0
2031-03-31 05:00 | 17.8287 | 0.008616% | 18.6191 | 19.4446 | 20.3067 | 21.207 | 0 | 0 | 0 | 0
2031-03-31 06:00 | 19.9571 | 0.009645% | 20.8419 | 21.7659 | 22.7309 | 23.7387 | 0 | 0 | 0 | 0
2031-03-31 07:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-03-31 08:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-03-31 09:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-03-31 10:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-03-31 11:00 | 25.3569 | 0.01225% | 26.4811 | 27.6552 | 28.8813 | 30.1617 | 0 | 0 | 0 | 0
2031-03-31 12:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-03-31 13:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-03-31 14:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-03-31 15:00 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-03-31 16:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-03-31 17:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-03-31 18:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-03-31 19:00 | 27.7087 | 0.01339% | 28.9371 | 30.2201 | 31.5599 | 32.9591 | 0 | 0 | 0 | 0
2031-03-31 20:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-03-31 21:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-03-31 22:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-03-31 23:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-04-01 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-04-01 01:00 | 19.5104 | 0.009429% | 20.3754 | 21.2787 | 22.2221 | 23.2073 | 0 | 0 | 0 | 0
2031-04-01 02:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-04-01 03:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-04-01 04:00 | 18.0783 | 0.008737% | 18.8798 | 19.7168 | 20.591 | 21.5039 | 0 | 0 | 0 | 0
2031-04-01 05:00 | 19.7206 | 0.00953% | 20.5949 | 21.508 | 22.4615 | 23.4574 | 0 | 0 | 0 | 0
2031-04-01 06:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-04-01 07:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-04-01 08:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-04-01 09:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-04-01 10:00 | 25.4226 | 0.01229% | 26.5497 | 27.7268 | 28.9561 | 30.2399 | 0 | 0 | 0 | 0
2031-04-01 11:00 | 25.6854 | 0.01241% | 26.8241 | 28.0134 | 29.2554 | 30.5524 | 0 | 0 | 0 | 0
2031-04-01 12:00 | 25.6985 | 0.01242% | 26.8379 | 28.0277 | 29.2703 | 30.568 | 0 | 0 | 0 | 0
2031-04-01 13:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-04-01 14:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-04-01 15:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-04-01 16:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-04-01 17:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-04-01 18:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-04-01 19:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-04-01 20:00 | 27.932 | 0.0135% | 29.1704 | 30.4637 | 31.8143 | 33.2248 | 0 | 0 | 0 | 0
2031-04-01 21:00 | 27.8006 | 0.01344% | 29.0332 | 30.3204 | 31.6646 | 33.0685 | 0 | 0 | 0 | 0
2031-04-01 22:00 | 25.6722 | 0.01241% | 26.8104 | 27.9991 | 29.2404 | 30.5368 | 0 | 0 | 0 | 0
2031-04-01 23:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-04-02 | 20.8768 | 0.01009% | 21.8023 | 22.7689 | 23.7784 | 24.8326 | 0 | 0 | 0 | 0
2031-04-02 01:00 | 19.7994 | 0.009568% | 20.6772 | 21.594 | 22.5513 | 23.5511 | 0 | 0 | 0 | 0
2031-04-02 02:00 | 19.0505 | 0.009206% | 19.8951 | 20.7772 | 21.6984 | 22.6604 | 0 | 0 | 0 | 0
2031-04-02 03:00 | 19.3396 | 0.009346% | 20.197 | 21.0924 | 22.0276 | 23.0042 | 0 | 0 | 0 | 0
2031-04-02 04:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-04-02 05:00 | 20.3644 | 0.009841% | 21.2672 | 22.2101 | 23.1948 | 24.2231 | 0 | 0 | 0 | 0
2031-04-02 06:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-04-02 07:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-04-02 08:00 | 27.8663 | 0.01347% | 29.1018 | 30.392 | 31.7395 | 33.1466 | 0 | 0 | 0 | 0
2031-04-02 09:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-04-02 10:00 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-04-02 11:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-04-02 12:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-04-02 13:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-04-02 14:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-04-02 15:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-04-02 16:00 | 31.4399 | 0.01519% | 32.8338 | 34.2895 | 35.8098 | 37.3974 | 0 | 0 | 0 | 0.35767
2031-04-02 17:00 | 32.4647 | 0.01569% | 33.9041 | 35.4072 | 36.977 | 38.6164 | 0 | 0 | 0 | 1.4547
2031-04-02 18:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-04-02 19:00 | 31.1378 | 0.01505% | 32.5183 | 33.96 | 35.4656 | 37.038 | 0 | 0 | 0 | 0.034169
2031-04-02 20:00 | 30.4283 | 0.0147% | 31.7773 | 33.1862 | 34.6575 | 36.1941 | 0 | 0 | 0 | 0
2031-04-02 21:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-04-02 22:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-04-02 23:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-04-03 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-04-03 01:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-04-03 02:00 | 18.6301 | 0.009003% | 19.4561 | 20.3187 | 21.2195 | 22.1603 | 0 | 0 | 0 | 0
2031-04-03 03:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-04-03 04:00 | 18.3016 | 0.008845% | 19.1131 | 19.9604 | 20.8454 | 21.7696 | 0 | 0 | 0 | 0
2031-04-03 05:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-04-03 06:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-04-03 07:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-04-03 08:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-04-03 09:00 | 25.5934 | 0.01237% | 26.7281 | 27.9131 | 29.1506 | 30.443 | 0 | 0 | 0 | 0
2031-04-03 10:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-04-03 11:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-04-03 12:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-04-03 13:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-04-03 14:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-04-03 15:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-04-03 16:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-04-03 17:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-04-03 18:00 | 25.0547 | 0.01211% | 26.1655 | 27.3256 | 28.5371 | 29.8023 | 0 | 0 | 0 | 0
2031-04-03 19:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-04-03 20:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-04-03 21:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-04-03 22:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-04-03 23:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-04-04 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-04-04 01:00 | 17.3688 | 0.008394% | 18.1389 | 18.9431 | 19.7829 | 20.66 | 0 | 0 | 0 | 0
2031-04-04 02:00 | 16.9353 | 0.008184% | 17.6861 | 18.4702 | 19.2891 | 20.1443 | 0 | 0 | 0 | 0
2031-04-04 03:00 | 16.4491 | 0.007949% | 17.1784 | 17.94 | 18.7354 | 19.566 | 0 | 0 | 0 | 0
2031-04-04 04:00 | 17.001 | 0.008216% | 17.7547 | 18.5419 | 19.3639 | 20.2224 | 0 | 0 | 0 | 0
2031-04-04 05:00 | 18.4987 | 0.00894% | 19.3189 | 20.1754 | 21.0699 | 22.004 | 0 | 0 | 0 | 0
2031-04-04 06:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-04-04 07:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-04-04 08:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-04-04 09:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-04-04 10:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-04-04 11:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-04-04 12:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-04-04 13:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-04-04 14:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-04-04 15:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-04-04 16:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-04-04 17:00 | 24.608 | 0.01189% | 25.699 | 26.8384 | 28.0283 | 29.2709 | 0 | 0 | 0 | 0
2031-04-04 18:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-04-04 19:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-04-04 20:00 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-04-04 21:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-04-04 22:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-04-04 23:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-04-05 | 19.5892 | 0.009467% | 20.4577 | 21.3647 | 22.3119 | 23.3011 | 0 | 0 | 0 | 0
2031-04-05 01:00 | 18.0783 | 0.008737% | 18.8798 | 19.7168 | 20.591 | 21.5039 | 0 | 0 | 0 | 0
2031-04-05 02:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-04-05 03:00 | 16.6856 | 0.008064% | 17.4254 | 18.198 | 19.0048 | 19.8473 | 0 | 0 | 0 | 0
2031-04-05 04:00 | 16.344 | 0.007898% | 17.0687 | 17.8254 | 18.6157 | 19.441 | 0 | 0 | 0 | 0
2031-04-05 05:00 | 16.7776 | 0.008108% | 17.5214 | 18.2983 | 19.1095 | 19.9567 | 0 | 0 | 0 | 0
2031-04-05 06:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-04-05 07:00 | 19.4841 | 0.009416% | 20.3479 | 21.2501 | 22.1922 | 23.1761 | 0 | 0 | 0 | 0
2031-04-05 08:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-04-05 09:00 | 23.6884 | 0.01145% | 24.7386 | 25.8354 | 26.9808 | 28.177 | 0 | 0 | 0 | 0
2031-04-05 10:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-04-05 11:00 | 25.7511 | 0.01244% | 26.8927 | 28.085 | 29.3302 | 30.6306 | 0 | 0 | 0 | 0
2031-04-05 12:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-04-05 13:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-04-05 14:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-04-05 15:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-04-05 16:00 | 25.8299 | 0.01248% | 26.9751 | 28.171 | 29.42 | 30.7243 | 0 | 0 | 0 | 0
2031-04-05 17:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-04-05 18:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-04-05 19:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-04-05 20:00 | 25.3569 | 0.01225% | 26.4811 | 27.6552 | 28.8813 | 30.1617 | 0 | 0 | 0 | 0
2031-04-05 21:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-04-05 22:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-04-05 23:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-04-06 | 19.9308 | 0.009632% | 20.8144 | 21.7372 | 22.701 | 23.7074 | 0 | 0 | 0 | 0
2031-04-06 01:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-04-06 02:00 | 17.5396 | 0.008476% | 18.3173 | 19.1293 | 19.9775 | 20.8632 | 0 | 0 | 0 | 0
2031-04-06 03:00 | 17.0535 | 0.008241% | 17.8096 | 18.5992 | 19.4238 | 20.2849 | 0 | 0 | 0 | 0
2031-04-06 04:00 | 16.7251 | 0.008083% | 17.4666 | 18.2409 | 19.0497 | 19.8942 | 0 | 0 | 0 | 0
2031-04-06 05:00 | 17.1455 | 0.008286% | 17.9056 | 18.6995 | 19.5285 | 20.3943 | 0 | 0 | 0 | 0
2031-04-06 06:00 | 18.1834 | 0.008787% | 18.9896 | 19.8315 | 20.7107 | 21.6289 | 0 | 0 | 0 | 0
2031-04-06 07:00 | 19.4184 | 0.009384% | 20.2793 | 21.1784 | 22.1174 | 23.0979 | 0 | 0 | 0 | 0
2031-04-06 08:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-04-06 09:00 | 22.6898 | 0.01097% | 23.6958 | 24.7464 | 25.8435 | 26.9893 | 0 | 0 | 0 | 0
2031-04-06 10:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-04-06 11:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-04-06 12:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-04-06 13:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-04-06 14:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-04-06 15:00 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-04-06 16:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-04-06 17:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-04-06 18:00 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-04-06 19:00 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-04-06 20:00 | 27.1174 | 0.0131% | 28.3197 | 29.5753 | 30.8865 | 32.2558 | 0 | 0 | 0 | 0
2031-04-06 21:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-04-06 22:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-04-06 23:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-04-07 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0
2031-04-07 01:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-04-07 02:00 | 17.5922 | 0.008502% | 18.3721 | 19.1867 | 20.0373 | 20.9257 | 0 | 0 | 0 | 0
2031-04-07 03:00 | 17.1586 | 0.008292% | 17.9193 | 18.7138 | 19.5435 | 20.41 | 0 | 0 | 0 | 0
2031-04-07 04:00 | 17.7367 | 0.008572% | 18.5231 | 19.3443 | 20.2019 | 21.0976 | 0 | 0 | 0 | 0
2031-04-07 05:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-04-07 06:00 | 22.1643 | 0.01071% | 23.147 | 24.1732 | 25.2449 | 26.3642 | 0 | 0 | 0 | 0
2031-04-07 07:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-04-07 08:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-04-07 09:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-04-07 10:00 | 24.7394 | 0.01196% | 25.8362 | 26.9817 | 28.1779 | 29.4272 | 0 | 0 | 0 | 0
2031-04-07 11:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-04-07 12:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-04-07 13:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-04-07 14:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-04-07 15:00 | 24.2664 | 0.01173% | 25.3423 | 26.4658 | 27.6392 | 28.8646 | 0 | 0 | 0 | 0
2031-04-07 16:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-04-07 17:00 | 27.6167 | 0.01335% | 28.8411 | 30.1198 | 31.4551 | 32.8497 | 0 | 0 | 0 | 0
2031-04-07 18:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-04-07 19:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-04-07 20:00 | 27.262 | 0.01317% | 28.4706 | 29.7329 | 31.0511 | 32.4278 | 0 | 0 | 0 | 0
2031-04-07 21:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-04-07 22:00 | 25.0941 | 0.01213% | 26.2067 | 27.3686 | 28.582 | 29.8492 | 0 | 0 | 0 | 0
2031-04-07 23:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-04-08 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-04-08 01:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-04-08 02:00 | 19.3921 | 0.009372% | 20.2519 | 21.1498 | 22.0874 | 23.0667 | 0 | 0 | 0 | 0
2031-04-08 03:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-04-08 04:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-04-08 05:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-04-08 06:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-04-08 07:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-04-08 08:00 | 27.8532 | 0.01346% | 29.0881 | 30.3777 | 31.7245 | 33.131 | 0 | 0 | 0 | 0
2031-04-08 09:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-04-08 10:00 | 28.3393 | 0.0137% | 29.5957 | 30.9079 | 32.2782 | 33.7092 | 0 | 0 | 0 | 0
2031-04-08 11:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-04-08 12:00 | 28.8648 | 0.01395% | 30.1446 | 31.481 | 32.8768 | 34.3344 | 0 | 0 | 0 | 0
2031-04-08 13:00 | 27.9714 | 0.01352% | 29.2116 | 30.5067 | 31.8592 | 33.2717 | 0 | 0 | 0 | 0
2031-04-08 14:00 | 27.1174 | 0.0131% | 28.3197 | 29.5753 | 30.8865 | 32.2558 | 0 | 0 | 0 | 0
2031-04-08 15:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-04-08 16:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-04-08 17:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-04-08 18:00 | 28.8123 | 0.01392% | 30.0897 | 31.4237 | 32.8169 | 34.2718 | 0 | 0 | 0 | 0
2031-04-08 19:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-04-08 20:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-04-08 21:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-04-08 22:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-04-08 23:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-04-09 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-04-09 01:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-04-09 02:00 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-04-09 03:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-04-09 04:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-04-09 05:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-04-09 06:00 | 24.9628 | 0.01206% | 26.0695 | 27.2253 | 28.4323 | 29.6929 | 0 | 0 | 0 | 0
2031-04-09 07:00 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-04-09 08:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-04-09 09:00 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-04-09 10:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-04-09 11:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-04-09 12:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-04-09 13:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-04-09 14:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-04-09 15:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-04-09 16:00 | 26.3291 | 0.01272% | 27.4965 | 28.7155 | 29.9886 | 31.3182 | 0 | 0 | 0 | 0
2031-04-09 17:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-04-09 18:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-04-09 19:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-04-09 20:00 | 28.0897 | 0.01357% | 29.335 | 30.6356 | 31.9939 | 33.4123 | 0 | 0 | 0 | 0
2031-04-09 21:00 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-04-09 22:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-04-09 23:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-04-10 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-04-10 01:00 | 19.8126 | 0.009575% | 20.6909 | 21.6083 | 22.5663 | 23.5668 | 0 | 0 | 0 | 0
2031-04-10 02:00 | 19.1556 | 0.009257% | 20.0049 | 20.8918 | 21.8181 | 22.7854 | 0 | 0 | 0 | 0
2031-04-10 03:00 | 18.7878 | 0.009079% | 19.6207 | 20.4906 | 21.3991 | 22.3478 | 0 | 0 | 0 | 0
2031-04-10 04:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-04-10 05:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-04-10 06:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-04-10 07:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-04-10 08:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-04-10 09:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-04-10 10:00 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-04-10 11:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-04-10 12:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-04-10 13:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-04-10 14:00 | 26.4343 | 0.01277% | 27.6062 | 28.8302 | 30.1083 | 31.4432 | 0 | 0 | 0 | 0
2031-04-10 15:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-04-10 16:00 | 28.1948 | 0.01363% | 29.4448 | 30.7503 | 32.1136 | 33.5373 | 0 | 0 | 0 | 0
2031-04-10 17:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-04-10 18:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-04-10 19:00 | 27.932 | 0.0135% | 29.1704 | 30.4637 | 31.8143 | 33.2248 | 0 | 0 | 0 | 0
2031-04-10 20:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-04-10 21:00 | 28.0371 | 0.01355% | 29.2802 | 30.5783 | 31.934 | 33.3498 | 0 | 0 | 0 | 0
2031-04-10 22:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-04-10 23:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-04-11 | 20.8373 | 0.01007% | 21.7612 | 22.726 | 23.7335 | 24.7857 | 0 | 0 | 0 | 0
2031-04-11 01:00 | 19.471 | 0.00941% | 20.3342 | 21.2357 | 22.1772 | 23.1604 | 0 | 0 | 0 | 0
2031-04-11 02:00 | 18.6564 | 0.009016% | 19.4835 | 20.3473 | 21.2494 | 22.1915 | 0 | 0 | 0 | 0
2031-04-11 03:00 | 18.3279 | 0.008857% | 19.1405 | 19.9891 | 20.8753 | 21.8008 | 0 | 0 | 0 | 0
2031-04-11 04:00 | 18.3673 | 0.008876% | 19.1817 | 20.0321 | 20.9202 | 21.8477 | 0 | 0 | 0 | 0
2031-04-11 05:00 | 19.1951 | 0.009276% | 20.0461 | 20.9348 | 21.863 | 22.8323 | 0 | 0 | 0 | 0
2031-04-11 06:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-04-11 07:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-04-11 08:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-04-11 09:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-04-11 10:00 | 26.7364 | 0.01292% | 27.9218 | 29.1597 | 30.4525 | 31.8026 | 0 | 0 | 0 | 0
2031-04-11 11:00 | 26.8941 | 0.013% | 28.0865 | 29.3317 | 30.6321 | 31.9902 | 0 | 0 | 0 | 0
2031-04-11 12:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-04-11 13:00 | 26.7496 | 0.01293% | 27.9355 | 29.174 | 30.4675 | 31.8183 | 0 | 0 | 0 | 0
2031-04-11 14:00 | 26.6313 | 0.01287% | 27.812 | 29.0451 | 30.3328 | 31.6776 | 0 | 0 | 0 | 0
2031-04-11 15:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-04-11 16:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-04-11 17:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-04-11 18:00 | 26.6839 | 0.0129% | 27.8669 | 29.1024 | 30.3927 | 31.7401 | 0 | 0 | 0 | 0
2031-04-11 19:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-04-11 20:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-04-11 21:00 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-04-11 22:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-04-11 23:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-04-12 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-04-12 01:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-04-12 02:00 | 18.0783 | 0.008737% | 18.8798 | 19.7168 | 20.591 | 21.5039 | 0 | 0 | 0 | 0
2031-04-12 03:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-04-12 04:00 | 17.0535 | 0.008241% | 17.8096 | 18.5992 | 19.4238 | 20.2849 | 0 | 0 | 0 | 0
2031-04-12 05:00 | 17.579 | 0.008495% | 18.3584 | 19.1723 | 20.0223 | 20.91 | 0 | 0 | 0 | 0
2031-04-12 06:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-04-12 07:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-04-12 08:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-04-12 09:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-04-12 10:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-04-12 11:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-04-12 12:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-04-12 13:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-04-12 14:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-04-12 15:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-04-12 16:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-04-12 17:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-04-12 18:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-04-12 19:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-04-12 20:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-04-12 21:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-04-12 22:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-04-12 23:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-04-13 | 19.7337 | 0.009537% | 20.6086 | 21.5223 | 22.4765 | 23.473 | 0 | 0 | 0 | 0
2031-04-13 01:00 | 18.6827 | 0.009029% | 19.511 | 20.376 | 21.2794 | 22.2228 | 0 | 0 | 0 | 0
2031-04-13 02:00 | 17.6447 | 0.008527% | 18.427 | 19.244 | 20.0972 | 20.9882 | 0 | 0 | 0 | 0
2031-04-13 03:00 | 17.1455 | 0.008286% | 17.9056 | 18.6995 | 19.5285 | 20.3943 | 0 | 0 | 0 | 0
2031-04-13 04:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-04-13 05:00 | 17.3426 | 0.008381% | 18.1114 | 18.9144 | 19.753 | 20.6287 | 0 | 0 | 0 | 0
2031-04-13 06:00 | 18.0257 | 0.008711% | 18.8249 | 19.6595 | 20.5311 | 21.4414 | 0 | 0 | 0 | 0
2031-04-13 07:00 | 19.5366 | 0.009441% | 20.4028 | 21.3074 | 22.252 | 23.2386 | 0 | 0 | 0 | 0
2031-04-13 08:00 | 20.7454 | 0.01003% | 21.6651 | 22.6257 | 23.6288 | 24.6763 | 0 | 0 | 0 | 0
2031-04-13 09:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-04-13 10:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-04-13 11:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-04-13 12:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-04-13 13:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-04-13 14:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-04-13 15:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-04-13 16:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-04-13 17:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-04-13 18:00 | 24.8445 | 0.01201% | 25.946 | 27.0963 | 28.2977 | 29.5522 | 0 | 0 | 0 | 0
2031-04-13 19:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-04-13 20:00 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-04-13 21:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-04-13 22:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-04-13 23:00 | 20.3118 | 0.009816% | 21.2123 | 22.1528 | 23.1349 | 24.1606 | 0 | 0 | 0 | 0
2031-04-14 | 17.9075 | 0.008654% | 18.7014 | 19.5306 | 20.3965 | 21.3007 | 0 | 0 | 0 | 0
2031-04-14 01:00 | 16.6068 | 0.008025% | 17.3431 | 18.112 | 18.915 | 19.7536 | 0 | 0 | 0 | 0
2031-04-14 02:00 | 16.0419 | 0.007752% | 16.7531 | 17.4958 | 18.2715 | 19.0816 | 0 | 0 | 0 | 0
2031-04-14 03:00 | 15.6214 | 0.007549% | 16.314 | 17.0373 | 17.7927 | 18.5815 | 0 | 0 | 0 | 0
2031-04-14 04:00 | 15.8579 | 0.007664% | 16.561 | 17.2952 | 18.062 | 18.8628 | 0 | 0 | 0 | 0
2031-04-14 05:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-04-14 06:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-04-14 07:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-04-14 08:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-04-14 09:00 | 23.7803 | 0.01149% | 24.8346 | 25.9357 | 27.0855 | 28.2864 | 0 | 0 | 0 | 0
2031-04-14 10:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-04-14 11:00 | 23.5307 | 0.01137% | 24.5739 | 25.6634 | 26.8012 | 27.9895 | 0 | 0 | 0 | 0
2031-04-14 12:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-04-14 13:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-04-14 14:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-04-14 15:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-04-14 16:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-04-14 17:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-04-14 18:00 | 24.7394 | 0.01196% | 25.8362 | 26.9817 | 28.1779 | 29.4272 | 0 | 0 | 0 | 0
2031-04-14 19:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-04-14 20:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-04-14 21:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-04-14 22:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-04-14 23:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-04-15 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-04-15 01:00 | 16.4491 | 0.007949% | 17.1784 | 17.94 | 18.7354 | 19.566 | 0 | 0 | 0 | 0
2031-04-15 02:00 | 15.8711 | 0.00767% | 16.5747 | 17.3096 | 18.077 | 18.8784 | 0 | 0 | 0 | 0
2031-04-15 03:00 | 15.4901 | 0.007486% | 16.1768 | 16.894 | 17.643 | 18.4252 | 0 | 0 | 0 | 0
2031-04-15 04:00 | 15.6871 | 0.007581% | 16.3826 | 17.1089 | 17.8675 | 18.6596 | 0 | 0 | 0 | 0
2031-04-15 05:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-04-15 06:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-04-15 07:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-04-15 08:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-04-15 09:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-04-15 10:00 | 24.6869 | 0.01193% | 25.7814 | 26.9244 | 28.1181 | 29.3647 | 0 | 0 | 0 | 0
2031-04-15 11:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-04-15 12:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-04-15 13:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-04-15 14:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-04-15 15:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-04-15 16:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-04-15 17:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-04-15 18:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-04-15 19:00 | 26.2372 | 0.01268% | 27.4004 | 28.6152 | 29.8839 | 31.2088 | 0 | 0 | 0 | 0
2031-04-15 20:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-04-15 21:00 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-04-15 22:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-04-15 23:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-04-16 | 19.7469 | 0.009543% | 20.6223 | 21.5366 | 22.4915 | 23.4886 | 0 | 0 | 0 | 0
2031-04-16 01:00 | 18.3805 | 0.008883% | 19.1954 | 20.0464 | 20.9352 | 21.8633 | 0 | 0 | 0 | 0
2031-04-16 02:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-04-16 03:00 | 17.4477 | 0.008432% | 18.2212 | 19.029 | 19.8727 | 20.7538 | 0 | 0 | 0 | 0
2031-04-16 04:00 | 17.6447 | 0.008527% | 18.427 | 19.244 | 20.0972 | 20.9882 | 0 | 0 | 0 | 0
2031-04-16 05:00 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-04-16 06:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-04-16 07:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-04-16 08:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-04-16 09:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-04-16 10:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-04-16 11:00 | 26.5262 | 0.01282% | 27.7023 | 28.9305 | 30.2131 | 31.5526 | 0 | 0 | 0 | 0
2031-04-16 12:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-04-16 13:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-04-16 14:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-04-16 15:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-04-16 16:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-04-16 17:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-04-16 18:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-04-16 19:00 | 26.3686 | 0.01274% | 27.5376 | 28.7585 | 30.0335 | 31.3651 | 0 | 0 | 0 | 0
2031-04-16 20:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-04-16 21:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-04-16 22:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-04-16 23:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-04-17 | 20.5089 | 0.009911% | 21.4181 | 22.3677 | 23.3594 | 24.395 | 0 | 0 | 0 | 0
2031-04-17 01:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-04-17 02:00 | 18.5907 | 0.008984% | 19.4149 | 20.2757 | 21.1746 | 22.1134 | 0 | 0 | 0 | 0
2031-04-17 03:00 | 18.2754 | 0.008832% | 19.0856 | 19.9318 | 20.8155 | 21.7383 | 0 | 0 | 0 | 0
2031-04-17 04:00 | 18.5644 | 0.008972% | 19.3875 | 20.247 | 21.1447 | 22.0821 | 0 | 0 | 0 | 0
2031-04-17 05:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-04-17 06:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-04-17 07:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-04-17 08:00 | 24.6869 | 0.01193% | 25.7814 | 26.9244 | 28.1181 | 29.3647 | 0 | 0 | 0 | 0
2031-04-17 09:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-04-17 10:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-04-17 11:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-04-17 12:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-04-17 13:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-04-17 14:00 | 23.5832 | 0.0114% | 24.6288 | 25.7207 | 26.8611 | 28.052 | 0 | 0 | 0 | 0
2031-04-17 15:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-04-17 16:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-04-17 17:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-04-17 18:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-04-17 19:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-04-17 20:00 | 24.6869 | 0.01193% | 25.7814 | 26.9244 | 28.1181 | 29.3647 | 0 | 0 | 0 | 0
2031-04-17 21:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-04-17 22:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-04-17 23:00 | 21.4286 | 0.01036% | 22.3786 | 23.3708 | 24.4069 | 25.489 | 0 | 0 | 0 | 0
2031-04-18 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-04-18 01:00 | 18.0914 | 0.008743% | 18.8935 | 19.7312 | 20.606 | 21.5195 | 0 | 0 | 0 | 0
2031-04-18 02:00 | 17.3163 | 0.008368% | 18.084 | 18.8858 | 19.7231 | 20.5975 | 0 | 0 | 0 | 0
2031-04-18 03:00 | 16.8302 | 0.008133% | 17.5763 | 18.3556 | 19.1694 | 20.0193 | 0 | 0 | 0 | 0
2031-04-18 04:00 | 16.6462 | 0.008045% | 17.3842 | 18.155 | 18.9599 | 19.8005 | 0 | 0 | 0 | 0
2031-04-18 05:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-04-18 06:00 | 18.0257 | 0.008711% | 18.8249 | 19.6595 | 20.5311 | 21.4414 | 0 | 0 | 0 | 0
2031-04-18 07:00 | 20.0228 | 0.009676% | 20.9105 | 21.8375 | 22.8057 | 23.8168 | 0 | 0 | 0 | 0
2031-04-18 08:00 | 21.2052 | 0.01025% | 22.1454 | 23.1272 | 24.1525 | 25.2233 | 0 | 0 | 0 | 0
2031-04-18 09:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-04-18 10:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-04-18 11:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-04-18 12:00 | 25.6328 | 0.01239% | 26.7693 | 27.9561 | 29.1955 | 30.4899 | 0 | 0 | 0 | 0
2031-04-18 13:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-04-18 14:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-04-18 15:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-04-18 16:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-04-18 17:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-04-18 18:00 | 22.8606 | 0.01105% | 23.8742 | 24.9326 | 26.038 | 27.1924 | 0 | 0 | 0 | 0
2031-04-18 19:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-04-18 20:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-04-18 21:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-04-18 22:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-04-18 23:00 | 19.6549 | 0.009499% | 20.5263 | 21.4363 | 22.3867 | 23.3792 | 0 | 0 | 0 | 0
2031-04-19 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-04-19 01:00 | 16.4229 | 0.007937% | 17.151 | 17.9114 | 18.7055 | 19.5348 | 0 | 0 | 0 | 0
2031-04-19 02:00 | 15.5952 | 0.007537% | 16.2866 | 17.0086 | 17.7627 | 18.5502 | 0 | 0 | 0 | 0
2031-04-19 03:00 | 14.9645 | 0.007232% | 15.628 | 16.3208 | 17.0444 | 17.8001 | 0 | 0 | 0 | 0
2031-04-19 04:00 | 14.5966 | 0.007054% | 15.2438 | 15.9196 | 16.6254 | 17.3625 | 0 | 0 | 0 | 0
2031-04-19 05:00 | 14.728 | 0.007118% | 15.381 | 16.0629 | 16.7751 | 17.5188 | 0 | 0 | 0 | 0
2031-04-19 06:00 | 15.3455 | 0.007416% | 16.0259 | 16.7364 | 17.4784 | 18.2533 | 0 | 0 | 0 | 0
2031-04-19 07:00 | 17.001 | 0.008216% | 17.7547 | 18.5419 | 19.3639 | 20.2224 | 0 | 0 | 0 | 0
2031-04-19 08:00 | 19.0505 | 0.009206% | 19.8951 | 20.7772 | 21.6984 | 22.6604 | 0 | 0 | 0 | 0
2031-04-19 09:00 | 20.6009 | 0.009956% | 21.5142 | 22.468 | 23.4642 | 24.5044 | 0 | 0 | 0 | 0
2031-04-19 10:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-04-19 11:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-04-19 12:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-04-19 13:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-04-19 14:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-04-19 15:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-04-19 16:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-04-19 17:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-04-19 18:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-04-19 19:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-04-19 20:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-04-19 21:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-04-19 22:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-04-19 23:00 | 20.0753 | 0.009702% | 20.9654 | 21.8949 | 22.8656 | 23.8793 | 0 | 0 | 0 | 0
2031-04-20 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-04-20 01:00 | 16.6725 | 0.008057% | 17.4117 | 18.1836 | 18.9898 | 19.8317 | 0 | 0 | 0 | 0
2031-04-20 02:00 | 15.8842 | 0.007676% | 16.5884 | 17.3239 | 18.0919 | 18.8941 | 0 | 0 | 0 | 0
2031-04-20 03:00 | 15.4506 | 0.007467% | 16.1356 | 16.851 | 17.5981 | 18.3783 | 0 | 0 | 0 | 0
2031-04-20 04:00 | 15.6609 | 0.007568% | 16.3552 | 17.0803 | 17.8375 | 18.6284 | 0 | 0 | 0 | 0
2031-04-20 05:00 | 16.0813 | 0.007772% | 16.7942 | 17.5388 | 18.3164 | 19.1285 | 0 | 0 | 0 | 0
2031-04-20 06:00 | 16.3309 | 0.007892% | 17.0549 | 17.8111 | 18.6007 | 19.4254 | 0 | 0 | 0 | 0
2031-04-20 07:00 | 18.236 | 0.008813% | 19.0445 | 19.8888 | 20.7706 | 21.6914 | 0 | 0 | 0 | 0
2031-04-20 08:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-04-20 09:00 | 21.1395 | 0.01022% | 22.0767 | 23.0555 | 24.0777 | 25.1452 | 0 | 0 | 0 | 0
2031-04-20 10:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-04-20 11:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-04-20 12:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-04-20 13:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-04-20 14:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-04-20 15:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-04-20 16:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-04-20 17:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-04-20 18:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-04-20 19:00 | 21.757 | 0.01051% | 22.7216 | 23.729 | 24.781 | 25.8797 | 0 | 0 | 0 | 0
2031-04-20 20:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-04-20 21:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-04-20 22:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-04-20 23:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-04-21 | 18.236 | 0.008813% | 19.0445 | 19.8888 | 20.7706 | 21.6914 | 0 | 0 | 0 | 0
2031-04-21 01:00 | 17.0535 | 0.008241% | 17.8096 | 18.5992 | 19.4238 | 20.2849 | 0 | 0 | 0 | 0
2031-04-21 02:00 | 16.147 | 0.007803% | 16.8628 | 17.6105 | 18.3912 | 19.2066 | 0 | 0 | 0 | 0
2031-04-21 03:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-04-21 04:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-04-21 05:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-04-21 06:00 | 18.7615 | 0.009067% | 19.5933 | 20.462 | 21.3691 | 22.3165 | 0 | 0 | 0 | 0
2031-04-21 07:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-04-21 08:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-04-21 09:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-04-21 10:00 | 26.2372 | 0.01268% | 27.4004 | 28.6152 | 29.8839 | 31.2088 | 0 | 0 | 0 | 0
2031-04-21 11:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-04-21 12:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-04-21 13:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-04-21 14:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-04-21 15:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-04-21 16:00 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-04-21 17:00 | 27.9977 | 0.01353% | 29.239 | 30.5353 | 31.8891 | 33.3029 | 0 | 0 | 0 | 0
2031-04-21 18:00 | 26.3029 | 0.01271% | 27.469 | 28.6869 | 29.9587 | 31.2869 | 0 | 0 | 0 | 0
2031-04-21 19:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-04-21 20:00 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-04-21 21:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-04-21 22:00 | 23.3599 | 0.01129% | 24.3956 | 25.4771 | 26.6067 | 27.7863 | 0 | 0 | 0 | 0
2031-04-21 23:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-04-22 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-04-22 01:00 | 16.9353 | 0.008184% | 17.6861 | 18.4702 | 19.2891 | 20.1443 | 0 | 0 | 0 | 0
2031-04-22 02:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-04-22 03:00 | 15.6214 | 0.007549% | 16.314 | 17.0373 | 17.7927 | 18.5815 | 0 | 0 | 0 | 0
2031-04-22 04:00 | 15.963 | 0.007714% | 16.6708 | 17.4099 | 18.1817 | 18.9878 | 0 | 0 | 0 | 0
2031-04-22 05:00 | 17.1455 | 0.008286% | 17.9056 | 18.6995 | 19.5285 | 20.3943 | 0 | 0 | 0 | 0
2031-04-22 06:00 | 19.7206 | 0.00953% | 20.5949 | 21.508 | 22.4615 | 23.4574 | 0 | 0 | 0 | 0
2031-04-22 07:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-04-22 08:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-04-22 09:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-04-22 10:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-04-22 11:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-04-22 12:00 | 24.1088 | 0.01165% | 25.1776 | 26.2939 | 27.4596 | 28.6771 | 0 | 0 | 0 | 0
2031-04-22 13:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-04-22 14:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-04-22 15:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-04-22 16:00 | 23.7409 | 0.01147% | 24.7935 | 25.8927 | 27.0406 | 28.2395 | 0 | 0 | 0 | 0
2031-04-22 17:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-04-22 18:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-04-22 19:00 | 24.1088 | 0.01165% | 25.1776 | 26.2939 | 27.4596 | 28.6771 | 0 | 0 | 0 | 0
2031-04-22 20:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-04-22 21:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-04-22 22:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-04-22 23:00 | 20.4169 | 0.009867% | 21.3221 | 22.2674 | 23.2547 | 24.2857 | 0 | 0 | 0 | 0
2031-04-23 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-04-23 01:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-04-23 02:00 | 16.5017 | 0.007975% | 17.2333 | 17.9974 | 18.7953 | 19.6286 | 0 | 0 | 0 | 0
2031-04-23 03:00 | 16.1076 | 0.007784% | 16.8217 | 17.5675 | 18.3463 | 19.1597 | 0 | 0 | 0 | 0
2031-04-23 04:00 | 16.2915 | 0.007873% | 17.0138 | 17.7681 | 18.5558 | 19.3785 | 0 | 0 | 0 | 0
2031-04-23 05:00 | 18.0126 | 0.008705% | 18.8112 | 19.6452 | 20.5162 | 21.4258 | 0 | 0 | 0 | 0
2031-04-23 06:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-04-23 07:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-04-23 08:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-04-23 09:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-04-23 10:00 | 23.5832 | 0.0114% | 24.6288 | 25.7207 | 26.8611 | 28.052 | 0 | 0 | 0 | 0
2031-04-23 11:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-04-23 12:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-04-23 13:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-04-23 14:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-04-23 15:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-04-23 16:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-04-23 17:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-04-23 18:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-04-23 19:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-04-23 20:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-04-23 21:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-04-23 22:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-04-23 23:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-04-24 | 18.3016 | 0.008845% | 19.1131 | 19.9604 | 20.8454 | 21.7696 | 0 | 0 | 0 | 0
2031-04-24 01:00 | 16.6594 | 0.008051% | 17.398 | 18.1693 | 18.9748 | 19.8161 | 0 | 0 | 0 | 0
2031-04-24 02:00 | 15.8054 | 0.007638% | 16.5061 | 17.2379 | 18.0022 | 18.8003 | 0 | 0 | 0 | 0
2031-04-24 03:00 | 15.4112 | 0.007448% | 16.0945 | 16.808 | 17.5532 | 18.3314 | 0 | 0 | 0 | 0
2031-04-24 04:00 | 15.5426 | 0.007511% | 16.2317 | 16.9513 | 17.7029 | 18.4877 | 0 | 0 | 0 | 0
2031-04-24 05:00 | 16.5937 | 0.008019% | 17.3294 | 18.0977 | 18.9 | 19.738 | 0 | 0 | 0 | 0
2031-04-24 06:00 | 19.2345 | 0.009295% | 20.0872 | 20.9778 | 21.9079 | 22.8791 | 0 | 0 | 0 | 0
2031-04-24 07:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-04-24 08:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-04-24 09:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-04-24 10:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-04-24 11:00 | 23.5307 | 0.01137% | 24.5739 | 25.6634 | 26.8012 | 27.9895 | 0 | 0 | 0 | 0
2031-04-24 12:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-04-24 13:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-04-24 14:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-04-24 15:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-04-24 16:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-04-24 17:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-04-24 18:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-04-24 19:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-04-24 20:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-04-24 21:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-04-24 22:00 | 21.9278 | 0.0106% | 22.9 | 23.9153 | 24.9756 | 26.0829 | 0 | 0 | 0 | 0
2031-04-24 23:00 | 19.3527 | 0.009352% | 20.2107 | 21.1068 | 22.0425 | 23.0198 | 0 | 0 | 0 | 0
2031-04-25 | 17.579 | 0.008495% | 18.3584 | 19.1723 | 20.0223 | 20.91 | 0 | 0 | 0 | 0
2031-04-25 01:00 | 16.0287 | 0.007746% | 16.7394 | 17.4815 | 18.2565 | 19.066 | 0 | 0 | 0 | 0
2031-04-25 02:00 | 14.9382 | 0.007219% | 15.6005 | 16.2922 | 17.0145 | 17.7688 | 0 | 0 | 0 | 0
2031-04-25 03:00 | 14.5047 | 0.00701% | 15.1477 | 15.8193 | 16.5207 | 17.2531 | 0 | 0 | 0 | 0
2031-04-25 04:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-04-25 05:00 | 15.7791 | 0.007625% | 16.4787 | 17.2093 | 17.9722 | 18.769 | 0 | 0 | 0 | 0
2031-04-25 06:00 | 18.0257 | 0.008711% | 18.8249 | 19.6595 | 20.5311 | 21.4414 | 0 | 0 | 0 | 0
2031-04-25 07:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-04-25 08:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-04-25 09:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-04-25 10:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-04-25 11:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-04-25 12:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-04-25 13:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-04-25 14:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-04-25 15:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-04-25 16:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-04-25 17:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-04-25 18:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-04-25 19:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-04-25 20:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-04-25 21:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-04-25 22:00 | 21.8884 | 0.01058% | 22.8588 | 23.8723 | 24.9307 | 26.036 | 0 | 0 | 0 | 0
2031-04-25 23:00 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0
2031-04-26 | 17.5134 | 0.008464% | 18.2898 | 19.1007 | 19.9475 | 20.8319 | 0 | 0 | 0 | 0
2031-04-26 01:00 | 16.0944 | 0.007778% | 16.808 | 17.5531 | 18.3314 | 19.1441 | 0 | 0 | 0 | 0
2031-04-26 02:00 | 14.8726 | 0.007187% | 15.5319 | 16.2205 | 16.9397 | 17.6907 | 0 | 0 | 0 | 0
2031-04-26 03:00 | 14.347 | 0.006933% | 14.9831 | 15.6474 | 16.3411 | 17.0656 | 0 | 0 | 0 | 0
2031-04-26 04:00 | 14.1631 | 0.006845% | 14.791 | 15.4468 | 16.1316 | 16.8468 | 0 | 0 | 0 | 0
2031-04-26 05:00 | 14.439 | 0.006978% | 15.0791 | 15.7477 | 16.4459 | 17.175 | 0 | 0 | 0 | 0
2031-04-26 06:00 | 14.8331 | 0.007168% | 15.4908 | 16.1776 | 16.8948 | 17.6438 | 0 | 0 | 0 | 0
2031-04-26 07:00 | 17.579 | 0.008495% | 18.3584 | 19.1723 | 20.0223 | 20.91 | 0 | 0 | 0 | 0
2031-04-26 08:00 | 19.4053 | 0.009378% | 20.2656 | 21.1641 | 22.1024 | 23.0823 | 0 | 0 | 0 | 0
2031-04-26 09:00 | 20.9424 | 0.01012% | 21.8709 | 22.8406 | 23.8532 | 24.9108 | 0 | 0 | 0 | 0
2031-04-26 10:00 | 21.849 | 0.01056% | 22.8177 | 23.8293 | 24.8858 | 25.9891 | 0 | 0 | 0 | 0
2031-04-26 11:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-04-26 12:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-04-26 13:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-04-26 14:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-04-26 15:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-04-26 16:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-04-26 17:00 | 23.6884 | 0.01145% | 24.7386 | 25.8354 | 26.9808 | 28.177 | 0 | 0 | 0 | 0
2031-04-26 18:00 | 23.7278 | 0.01147% | 24.7797 | 25.8784 | 27.0257 | 28.2239 | 0 | 0 | 0 | 0
2031-04-26 19:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-04-26 20:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-04-26 21:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-04-26 22:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-04-26 23:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-04-27 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-04-27 01:00 | 17.0666 | 0.008248% | 17.8233 | 18.6135 | 19.4387 | 20.3006 | 0 | 0 | 0 | 0
2031-04-27 02:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-04-27 03:00 | 15.4244 | 0.007454% | 16.1082 | 16.8224 | 17.5682 | 18.3471 | 0 | 0 | 0 | 0
2031-04-27 04:00 | 15.2141 | 0.007352% | 15.8887 | 16.5931 | 17.3288 | 18.097 | 0 | 0 | 0 | 0
2031-04-27 05:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-04-27 06:00 | 16.2127 | 0.007835% | 16.9315 | 17.6821 | 18.4661 | 19.2847 | 0 | 0 | 0 | 0
2031-04-27 07:00 | 17.1849 | 0.008305% | 17.9468 | 18.7425 | 19.5734 | 20.4412 | 0 | 0 | 0 | 0
2031-04-27 08:00 | 19.1688 | 0.009264% | 20.0186 | 20.9062 | 21.833 | 22.801 | 0 | 0 | 0 | 0
2031-04-27 09:00 | 20.3249 | 0.009822% | 21.2261 | 22.1671 | 23.1499 | 24.1763 | 0 | 0 | 0 | 0
2031-04-27 10:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-04-27 11:00 | 21.1395 | 0.01022% | 22.0767 | 23.0555 | 24.0777 | 25.1452 | 0 | 0 | 0 | 0
2031-04-27 12:00 | 21.5468 | 0.01041% | 22.5021 | 23.4997 | 24.5416 | 25.6296 | 0 | 0 | 0 | 0
2031-04-27 13:00 | 21.4943 | 0.01039% | 22.4472 | 23.4424 | 24.4817 | 25.5671 | 0 | 0 | 0 | 0
2031-04-27 14:00 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-04-27 15:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-04-27 16:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-04-27 17:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-04-27 18:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-04-27 19:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-04-27 20:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-04-27 21:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-04-27 22:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-04-27 23:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-04-28 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-04-28 01:00 | 15.6083 | 0.007543% | 16.3003 | 17.023 | 17.7777 | 18.5659 | 0 | 0 | 0 | 0
2031-04-28 02:00 | 14.8463 | 0.007175% | 15.5045 | 16.1919 | 16.9098 | 17.6595 | 0 | 0 | 0 | 0
2031-04-28 03:00 | 14.3864 | 0.006952% | 15.0243 | 15.6904 | 16.386 | 17.1125 | 0 | 0 | 0 | 0
2031-04-28 04:00 | 14.8069 | 0.007156% | 15.4633 | 16.1489 | 16.8649 | 17.6126 | 0 | 0 | 0 | 0
2031-04-28 05:00 | 16.4886 | 0.007968% | 17.2196 | 17.983 | 18.7803 | 19.6129 | 0 | 0 | 0 | 0
2031-04-28 06:00 | 18.5907 | 0.008984% | 19.4149 | 20.2757 | 21.1746 | 22.1134 | 0 | 0 | 0 | 0
2031-04-28 07:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-04-28 08:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-04-28 09:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-04-28 10:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-04-28 11:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-04-28 12:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-04-28 13:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-04-28 14:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-04-28 15:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-04-28 16:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-04-28 17:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-04-28 18:00 | 23.5307 | 0.01137% | 24.5739 | 25.6634 | 26.8012 | 27.9895 | 0 | 0 | 0 | 0
2031-04-28 19:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-04-28 20:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-04-28 21:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-04-28 22:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-04-28 23:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-04-29 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-04-29 01:00 | 16.1207 | 0.007791% | 16.8354 | 17.5818 | 18.3613 | 19.1754 | 0 | 0 | 0 | 0
2031-04-29 02:00 | 14.8988 | 0.0072% | 15.5594 | 16.2492 | 16.9696 | 17.722 | 0 | 0 | 0 | 0
2031-04-29 03:00 | 14.7412 | 0.007124% | 15.3947 | 16.0773 | 16.79 | 17.5344 | 0 | 0 | 0 | 0
2031-04-29 04:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-04-29 05:00 | 15.7791 | 0.007625% | 16.4787 | 17.2093 | 17.9722 | 18.769 | 0 | 0 | 0 | 0
2031-04-29 06:00 | 17.9075 | 0.008654% | 18.7014 | 19.5306 | 20.3965 | 21.3007 | 0 | 0 | 0 | 0
2031-04-29 07:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-04-29 08:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-04-29 09:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-04-29 10:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-04-29 11:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-04-29 12:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-04-29 13:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-04-29 14:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-04-29 15:00 | 22.6898 | 0.01097% | 23.6958 | 24.7464 | 25.8435 | 26.9893 | 0 | 0 | 0 | 0
2031-04-29 16:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-04-29 17:00 | 24.4635 | 0.01182% | 25.5481 | 26.6808 | 27.8637 | 29.099 | 0 | 0 | 0 | 0
2031-04-29 18:00 | 24.8445 | 0.01201% | 25.946 | 27.0963 | 28.2977 | 29.5522 | 0 | 0 | 0 | 0
2031-04-29 19:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-04-29 20:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-04-29 21:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-04-29 22:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-04-29 23:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-04-30 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-04-30 01:00 | 16.4754 | 0.007962% | 17.2059 | 17.9687 | 18.7653 | 19.5973 | 0 | 0 | 0 | 0
2031-04-30 02:00 | 15.766 | 0.007619% | 16.4649 | 17.1949 | 17.9573 | 18.7534 | 0 | 0 | 0 | 0
2031-04-30 03:00 | 15.1353 | 0.007314% | 15.8063 | 16.5071 | 17.239 | 18.0033 | 0 | 0 | 0 | 0
2031-04-30 04:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-04-30 05:00 | 16.7907 | 0.008114% | 17.5352 | 18.3126 | 19.1245 | 19.9724 | 0 | 0 | 0 | 0
2031-04-30 06:00 | 19.0768 | 0.009219% | 19.9226 | 20.8059 | 21.7283 | 22.6916 | 0 | 0 | 0 | 0
2031-04-30 07:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-04-30 08:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-04-30 09:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-04-30 10:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-04-30 11:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-04-30 12:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-04-30 13:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-04-30 14:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-04-30 15:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-04-30 16:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-04-30 17:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-04-30 18:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-04-30 19:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-04-30 20:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-04-30 21:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-04-30 22:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-04-30 23:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-05-01 | 18.6301 | 0.009003% | 19.4561 | 20.3187 | 21.2195 | 22.1603 | 0 | 0 | 0 | 0
2031-05-01 01:00 | 16.9747 | 0.008203% | 17.7273 | 18.5132 | 19.334 | 20.1912 | 0 | 0 | 0 | 0
2031-05-01 02:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-05-01 03:00 | 15.3849 | 0.007435% | 16.067 | 16.7794 | 17.5233 | 18.3002 | 0 | 0 | 0 | 0
2031-05-01 04:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-05-01 05:00 | 16.8302 | 0.008133% | 17.5763 | 18.3556 | 19.1694 | 20.0193 | 0 | 0 | 0 | 0
2031-05-01 06:00 | 19.4053 | 0.009378% | 20.2656 | 21.1641 | 22.1024 | 23.0823 | 0 | 0 | 0 | 0
2031-05-01 07:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-05-01 08:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-05-01 09:00 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-05-01 10:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-05-01 11:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-05-01 12:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-05-01 13:00 | 23.7278 | 0.01147% | 24.7797 | 25.8784 | 27.0257 | 28.2239 | 0 | 0 | 0 | 0
2031-05-01 14:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-05-01 15:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-05-01 16:00 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-05-01 17:00 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-05-01 18:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-05-01 19:00 | 25.5934 | 0.01237% | 26.7281 | 27.9131 | 29.1506 | 30.443 | 0 | 0 | 0 | 0
2031-05-01 20:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-05-01 21:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-05-01 22:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-05-01 23:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-05-02 | 18.3673 | 0.008876% | 19.1817 | 20.0321 | 20.9202 | 21.8477 | 0 | 0 | 0 | 0
2031-05-02 01:00 | 16.7645 | 0.008102% | 17.5077 | 18.2839 | 19.0946 | 19.9411 | 0 | 0 | 0 | 0
2031-05-02 02:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-05-02 03:00 | 14.9382 | 0.007219% | 15.6005 | 16.2922 | 17.0145 | 17.7688 | 0 | 0 | 0 | 0
2031-05-02 04:00 | 15.1485 | 0.007321% | 15.8201 | 16.5215 | 17.2539 | 18.0189 | 0 | 0 | 0 | 0
2031-05-02 05:00 | 16.5017 | 0.007975% | 17.2333 | 17.9974 | 18.7953 | 19.6286 | 0 | 0 | 0 | 0
2031-05-02 06:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-05-02 07:00 | 20.9819 | 0.01014% | 21.9121 | 22.8836 | 23.8981 | 24.9577 | 0 | 0 | 0 | 0
2031-05-02 08:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-05-02 09:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-05-02 10:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-05-02 11:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-05-02 12:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-05-02 13:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-05-02 14:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-05-02 15:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-05-02 16:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-05-02 17:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-05-02 18:00 | 22.7293 | 0.01098% | 23.737 | 24.7893 | 25.8884 | 27.0362 | 0 | 0 | 0 | 0
2031-05-02 19:00 | 21.9935 | 0.01063% | 22.9686 | 23.9869 | 25.0504 | 26.161 | 0 | 0 | 0 | 0
2031-05-02 20:00 | 22.9526 | 0.01109% | 23.9702 | 25.0329 | 26.1428 | 27.3018 | 0 | 0 | 0 | 0
2031-05-02 21:00 | 22.8344 | 0.01104% | 23.8467 | 24.904 | 26.0081 | 27.1612 | 0 | 0 | 0 | 0
2031-05-02 22:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-05-02 23:00 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-05-03 | 17.9995 | 0.008699% | 18.7975 | 19.6309 | 20.5012 | 21.4101 | 0 | 0 | 0 | 0
2031-05-03 01:00 | 16.0681 | 0.007765% | 16.7805 | 17.5245 | 18.3014 | 19.1128 | 0 | 0 | 0 | 0
2031-05-03 02:00 | 14.6886 | 0.007098% | 15.3398 | 16.0199 | 16.7302 | 17.4719 | 0 | 0 | 0 | 0
2031-05-03 03:00 | 14.3339 | 0.006927% | 14.9694 | 15.633 | 16.3261 | 17.05 | 0 | 0 | 0 | 0
2031-05-03 04:00 | 13.9791 | 0.006756% | 14.5989 | 15.2462 | 15.9221 | 16.628 | 0 | 0 | 0 | 0
2031-05-03 05:00 | 14.3864 | 0.006952% | 15.0243 | 15.6904 | 16.386 | 17.1125 | 0 | 0 | 0 | 0
2031-05-03 06:00 | 14.9645 | 0.007232% | 15.628 | 16.3208 | 17.0444 | 17.8001 | 0 | 0 | 0 | 0
2031-05-03 07:00 | 17.2374 | 0.00833% | 18.0017 | 18.7998 | 19.6333 | 20.5037 | 0 | 0 | 0 | 0
2031-05-03 08:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-05-03 09:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-05-03 10:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-05-03 11:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-05-03 12:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-05-03 13:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-05-03 14:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-05-03 15:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-05-03 16:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-05-03 17:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-05-03 18:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-05-03 19:00 | 22.3482 | 0.0108% | 23.3391 | 24.3738 | 25.4544 | 26.5829 | 0 | 0 | 0 | 0
2031-05-03 20:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-05-03 21:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-05-03 22:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-05-03 23:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-05-04 | 17.8812 | 0.008641% | 18.674 | 19.5019 | 20.3665 | 21.2695 | 0 | 0 | 0 | 0
2031-05-04 01:00 | 16.2521 | 0.007854% | 16.9726 | 17.7251 | 18.5109 | 19.3316 | 0 | 0 | 0 | 0
2031-05-04 02:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-05-04 03:00 | 14.7149 | 0.007111% | 15.3673 | 16.0486 | 16.7601 | 17.5032 | 0 | 0 | 0 | 0
2031-05-04 04:00 | 14.5178 | 0.007016% | 15.1615 | 15.8337 | 16.5356 | 17.2688 | 0 | 0 | 0 | 0
2031-05-04 05:00 | 14.5966 | 0.007054% | 15.2438 | 15.9196 | 16.6254 | 17.3625 | 0 | 0 | 0 | 0
2031-05-04 06:00 | 15.3455 | 0.007416% | 16.0259 | 16.7364 | 17.4784 | 18.2533 | 0 | 0 | 0 | 0
2031-05-04 07:00 | 16.7119 | 0.008076% | 17.4528 | 18.2266 | 19.0347 | 19.8786 | 0 | 0 | 0 | 0
2031-05-04 08:00 | 18.3936 | 0.008889% | 19.2091 | 20.0607 | 20.9501 | 21.879 | 0 | 0 | 0 | 0
2031-05-04 09:00 | 19.9834 | 0.009657% | 20.8693 | 21.7946 | 22.7608 | 23.7699 | 0 | 0 | 0 | 0
2031-05-04 10:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-05-04 11:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-05-04 12:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-05-04 13:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-05-04 14:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-05-04 15:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-05-04 16:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-05-04 17:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-05-04 18:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-05-04 19:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-05-04 20:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-05-04 21:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-05-04 22:00 | 21.6913 | 0.01048% | 22.653 | 23.6573 | 24.7062 | 25.8016 | 0 | 0 | 0 | 0
2031-05-04 23:00 | 18.7484 | 0.00906% | 19.5796 | 20.4476 | 21.3542 | 22.3009 | 0 | 0 | 0 | 0
2031-05-05 | 16.5805 | 0.008013% | 17.3156 | 18.0833 | 18.8851 | 19.7223 | 0 | 0 | 0 | 0
2031-05-05 01:00 | 15.0959 | 0.007295% | 15.7652 | 16.4641 | 17.1941 | 17.9564 | 0 | 0 | 0 | 0
2031-05-05 02:00 | 14.0974 | 0.006813% | 14.7224 | 15.3751 | 16.0568 | 16.7687 | 0 | 0 | 0 | 0
2031-05-05 03:00 | 13.8084 | 0.006673% | 14.4205 | 15.0599 | 15.7276 | 16.4249 | 0 | 0 | 0 | 0
2031-05-05 04:00 | 14.1499 | 0.006838% | 14.7773 | 15.4324 | 16.1166 | 16.8312 | 0 | 0 | 0 | 0
2031-05-05 05:00 | 15.3718 | 0.007429% | 16.0533 | 16.765 | 17.5083 | 18.2846 | 0 | 0 | 0 | 0
2031-05-05 06:00 | 17.8287 | 0.008616% | 18.6191 | 19.4446 | 20.3067 | 21.207 | 0 | 0 | 0 | 0
2031-05-05 07:00 | 20.5089 | 0.009911% | 21.4181 | 22.3677 | 23.3594 | 24.395 | 0 | 0 | 0 | 0
2031-05-05 08:00 | 21.3366 | 0.01031% | 22.2826 | 23.2705 | 24.3022 | 25.3796 | 0 | 0 | 0 | 0
2031-05-05 09:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-05-05 10:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-05-05 11:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-05-05 12:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-05-05 13:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-05-05 14:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-05-05 15:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-05-05 16:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-05-05 17:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-05-05 18:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-05-05 19:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-05-05 20:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-05-05 21:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-05-05 22:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-05-05 23:00 | 19.8388 | 0.009587% | 20.7184 | 21.6369 | 22.5962 | 23.598 | 0 | 0 | 0 | 0
2031-05-06 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-05-06 01:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-05-06 02:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-05-06 03:00 | 14.2025 | 0.006864% | 14.8322 | 15.4898 | 16.1765 | 16.8937 | 0 | 0 | 0 | 0
2031-05-06 04:00 | 14.2682 | 0.006895% | 14.9008 | 15.5614 | 16.2513 | 16.9718 | 0 | 0 | 0 | 0
2031-05-06 05:00 | 15.1353 | 0.007314% | 15.8063 | 16.5071 | 17.239 | 18.0033 | 0 | 0 | 0 | 0
2031-05-06 06:00 | 18.1046 | 0.008749% | 18.9072 | 19.7455 | 20.6209 | 21.5352 | 0 | 0 | 0 | 0
2031-05-06 07:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-05-06 08:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-05-06 09:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-05-06 10:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-05-06 11:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-05-06 12:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-05-06 13:00 | 22.9526 | 0.01109% | 23.9702 | 25.0329 | 26.1428 | 27.3018 | 0 | 0 | 0 | 0
2031-05-06 14:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-05-06 15:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-05-06 16:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-05-06 17:00 | 24.2664 | 0.01173% | 25.3423 | 26.4658 | 27.6392 | 28.8646 | 0 | 0 | 0 | 0
2031-05-06 18:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-05-06 19:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-05-06 20:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-05-06 21:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-05-06 22:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-05-06 23:00 | 19.5629 | 0.009454% | 20.4303 | 21.336 | 22.282 | 23.2698 | 0 | 0 | 0 | 0
2031-05-07 | 17.5134 | 0.008464% | 18.2898 | 19.1007 | 19.9475 | 20.8319 | 0 | 0 | 0 | 0
2031-05-07 01:00 | 15.8448 | 0.007657% | 16.5473 | 17.2809 | 18.047 | 18.8472 | 0 | 0 | 0 | 0
2031-05-07 02:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-05-07 03:00 | 14.6229 | 0.007067% | 15.2712 | 15.9483 | 16.6554 | 17.3938 | 0 | 0 | 0 | 0
2031-05-07 04:00 | 14.2945 | 0.006908% | 14.9282 | 15.5901 | 16.2813 | 17.0031 | 0 | 0 | 0 | 0
2031-05-07 05:00 | 15.3587 | 0.007422% | 16.0396 | 16.7507 | 17.4934 | 18.2689 | 0 | 0 | 0 | 0
2031-05-07 06:00 | 18.1571 | 0.008775% | 18.9621 | 19.8028 | 20.6808 | 21.5977 | 0 | 0 | 0 | 0
2031-05-07 07:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-05-07 08:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-05-07 09:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-05-07 10:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-05-07 11:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-05-07 12:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-05-07 13:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-05-07 14:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-05-07 15:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-05-07 16:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-05-07 17:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-05-07 18:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-05-07 19:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-05-07 20:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-05-07 21:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-05-07 22:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-05-07 23:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-05-08 | 17.9995 | 0.008699% | 18.7975 | 19.6309 | 20.5012 | 21.4101 | 0 | 0 | 0 | 0
2031-05-08 01:00 | 16.2784 | 0.007867% | 17.0001 | 17.7538 | 18.5409 | 19.3629 | 0 | 0 | 0 | 0
2031-05-08 02:00 | 15.0171 | 0.007257% | 15.6829 | 16.3782 | 17.1043 | 17.8626 | 0 | 0 | 0 | 0
2031-05-08 03:00 | 14.6623 | 0.007086% | 15.3124 | 15.9913 | 16.7003 | 17.4407 | 0 | 0 | 0 | 0
2031-05-08 04:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-05-08 05:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-05-08 06:00 | 18.144 | 0.008768% | 18.9484 | 19.7885 | 20.6658 | 21.582 | 0 | 0 | 0 | 0
2031-05-08 07:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-05-08 08:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-05-08 09:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-05-08 10:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-05-08 11:00 | 23.7803 | 0.01149% | 24.8346 | 25.9357 | 27.0855 | 28.2864 | 0 | 0 | 0 | 0
2031-05-08 12:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-05-08 13:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-05-08 14:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-05-08 15:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-05-08 16:00 | 20.9819 | 0.01014% | 21.9121 | 22.8836 | 23.8981 | 24.9577 | 0 | 0 | 0 | 0
2031-05-08 17:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-05-08 18:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-05-08 19:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-05-08 20:00 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-05-08 21:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-05-08 22:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-05-08 23:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-05-09 | 18.1309 | 0.008762% | 18.9347 | 19.7742 | 20.6509 | 21.5664 | 0 | 0 | 0 | 0
2031-05-09 01:00 | 16.5148 | 0.007981% | 17.247 | 18.0117 | 18.8102 | 19.6442 | 0 | 0 | 0 | 0
2031-05-09 02:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-05-09 03:00 | 15.2798 | 0.007384% | 15.9573 | 16.6647 | 17.4036 | 18.1752 | 0 | 0 | 0 | 0
2031-05-09 04:00 | 15.3324 | 0.00741% | 16.0122 | 16.7221 | 17.4634 | 18.2377 | 0 | 0 | 0 | 0
2031-05-09 05:00 | 16.8433 | 0.00814% | 17.59 | 18.3699 | 19.1843 | 20.0349 | 0 | 0 | 0 | 0
2031-05-09 06:00 | 19.4184 | 0.009384% | 20.2793 | 21.1784 | 22.1174 | 23.0979 | 0 | 0 | 0 | 0
2031-05-09 07:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-05-09 08:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-05-09 09:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-05-09 10:00 | 22.3482 | 0.0108% | 23.3391 | 24.3738 | 25.4544 | 26.5829 | 0 | 0 | 0 | 0
2031-05-09 11:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-05-09 12:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-05-09 13:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-05-09 14:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-05-09 15:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-05-09 16:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-05-09 17:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-05-09 18:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-05-09 19:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-05-09 20:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-05-09 21:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-05-09 22:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-05-09 23:00 | 20.1279 | 0.009727% | 21.0202 | 21.9522 | 22.9254 | 23.9418 | 0 | 0 | 0 | 0
2031-05-10 | 18.1309 | 0.008762% | 18.9347 | 19.7742 | 20.6509 | 21.5664 | 0 | 0 | 0 | 0
2031-05-10 01:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-05-10 02:00 | 15.2536 | 0.007372% | 15.9298 | 16.6361 | 17.3737 | 18.1439 | 0 | 0 | 0 | 0
2031-05-10 03:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-05-10 04:00 | 14.6886 | 0.007098% | 15.3398 | 16.0199 | 16.7302 | 17.4719 | 0 | 0 | 0 | 0
2031-05-10 05:00 | 14.8331 | 0.007168% | 15.4908 | 16.1776 | 16.8948 | 17.6438 | 0 | 0 | 0 | 0
2031-05-10 06:00 | 15.2667 | 0.007378% | 15.9436 | 16.6504 | 17.3886 | 18.1595 | 0 | 0 | 0 | 0
2031-05-10 07:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-05-10 08:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-05-10 09:00 | 20.233 | 0.009778% | 21.13 | 22.0668 | 23.0452 | 24.0669 | 0 | 0 | 0 | 0
2031-05-10 10:00 | 20.9556 | 0.01013% | 21.8847 | 22.8549 | 23.8682 | 24.9264 | 0 | 0 | 0 | 0
2031-05-10 11:00 | 20.9819 | 0.01014% | 21.9121 | 22.8836 | 23.8981 | 24.9577 | 0 | 0 | 0 | 0
2031-05-10 12:00 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-05-10 13:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-05-10 14:00 | 20.522 | 0.009918% | 21.4319 | 22.3821 | 23.3744 | 24.4107 | 0 | 0 | 0 | 0
2031-05-10 15:00 | 20.0885 | 0.009708% | 20.9791 | 21.9092 | 22.8805 | 23.895 | 0 | 0 | 0 | 0
2031-05-10 16:00 | 20.9556 | 0.01013% | 21.8847 | 22.8549 | 23.8682 | 24.9264 | 0 | 0 | 0 | 0
2031-05-10 17:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-05-10 18:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-05-10 19:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-05-10 20:00 | 21.6913 | 0.01048% | 22.653 | 23.6573 | 24.7062 | 25.8016 | 0 | 0 | 0 | 0
2031-05-10 21:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-05-10 22:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-05-10 23:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-05-11 | 17.382 | 0.0084% | 18.1526 | 18.9574 | 19.7979 | 20.6756 | 0 | 0 | 0 | 0
2031-05-11 01:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-05-11 02:00 | 14.7412 | 0.007124% | 15.3947 | 16.0773 | 16.79 | 17.5344 | 0 | 0 | 0 | 0
2031-05-11 03:00 | 14.2288 | 0.006876% | 14.8596 | 15.5184 | 16.2064 | 16.9249 | 0 | 0 | 0 | 0
2031-05-11 04:00 | 14.0448 | 0.006787% | 14.6675 | 15.3178 | 15.9969 | 16.7062 | 0 | 0 | 0 | 0
2031-05-11 05:00 | 14.1762 | 0.006851% | 14.8047 | 15.4611 | 16.1466 | 16.8624 | 0 | 0 | 0 | 0
2031-05-11 06:00 | 14.7149 | 0.007111% | 15.3673 | 16.0486 | 16.7601 | 17.5032 | 0 | 0 | 0 | 0
2031-05-11 07:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-05-11 08:00 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-05-11 09:00 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-05-11 10:00 | 20.1147 | 0.009721% | 21.0065 | 21.9379 | 22.9105 | 23.9262 | 0 | 0 | 0 | 0
2031-05-11 11:00 | 20.3644 | 0.009841% | 21.2672 | 22.2101 | 23.1948 | 24.2231 | 0 | 0 | 0 | 0
2031-05-11 12:00 | 20.6928 | 0.01% | 21.6102 | 22.5683 | 23.5689 | 24.6138 | 0 | 0 | 0 | 0
2031-05-11 13:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-05-11 14:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-05-11 15:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0
2031-05-11 16:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-05-11 17:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-05-11 18:00 | 22.9789 | 0.0111% | 23.9977 | 25.0616 | 26.1727 | 27.3331 | 0 | 0 | 0 | 0
2031-05-11 19:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-05-11 20:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-05-11 21:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-05-11 22:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-05-11 23:00 | 19.5366 | 0.009441% | 20.4028 | 21.3074 | 22.252 | 23.2386 | 0 | 0 | 0 | 0
2031-05-12 | 17.2637 | 0.008343% | 18.0291 | 18.8284 | 19.6632 | 20.535 | 0 | 0 | 0 | 0
2031-05-12 01:00 | 15.6346 | 0.007556% | 16.3277 | 17.0516 | 17.8076 | 18.5971 | 0 | 0 | 0 | 0
2031-05-12 02:00 | 14.8988 | 0.0072% | 15.5594 | 16.2492 | 16.9696 | 17.722 | 0 | 0 | 0 | 0
2031-05-12 03:00 | 14.4259 | 0.006971% | 15.0654 | 15.7334 | 16.4309 | 17.1594 | 0 | 0 | 0 | 0
2031-05-12 04:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-05-12 05:00 | 15.9236 | 0.007695% | 16.6296 | 17.3669 | 18.1368 | 18.9409 | 0 | 0 | 0 | 0
2031-05-12 06:00 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-05-12 07:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-05-12 08:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-05-12 09:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-05-12 10:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-05-12 11:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-05-12 12:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-05-12 13:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-05-12 14:00 | 22.0855 | 0.01067% | 23.0646 | 24.0872 | 25.1551 | 26.2704 | 0 | 0 | 0 | 0
2031-05-12 15:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-05-12 16:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-05-12 17:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-05-12 18:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-05-12 19:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-05-12 20:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-05-12 21:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-05-12 22:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-05-12 23:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-05-13 | 17.2637 | 0.008343% | 18.0291 | 18.8284 | 19.6632 | 20.535 | 0 | 0 | 0 | 0
2031-05-13 01:00 | 15.8973 | 0.007683% | 16.6022 | 17.3382 | 18.1069 | 18.9097 | 0 | 0 | 0 | 0
2031-05-13 02:00 | 14.9251 | 0.007213% | 15.5868 | 16.2779 | 16.9995 | 17.7532 | 0 | 0 | 0 | 0
2031-05-13 03:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-05-13 04:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-05-13 05:00 | 15.2536 | 0.007372% | 15.9298 | 16.6361 | 17.3737 | 18.1439 | 0 | 0 | 0 | 0
2031-05-13 06:00 | 17.9206 | 0.00866% | 18.7152 | 19.5449 | 20.4114 | 21.3164 | 0 | 0 | 0 | 0
2031-05-13 07:00 | 20.7191 | 0.01001% | 21.6377 | 22.597 | 23.5988 | 24.6451 | 0 | 0 | 0 | 0
2031-05-13 08:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-05-13 09:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-05-13 10:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-05-13 11:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-05-13 12:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-05-13 13:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-05-13 14:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-05-13 15:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-05-13 16:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-05-13 17:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0
2031-05-13 18:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-05-13 19:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-05-13 20:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-05-13 21:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-05-13 22:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-05-13 23:00 | 20.4038 | 0.00986% | 21.3084 | 22.2531 | 23.2397 | 24.27 | 0 | 0 | 0 | 0
2031-05-14 | 18.144 | 0.008768% | 18.9484 | 19.7885 | 20.6658 | 21.582 | 0 | 0 | 0 | 0
2031-05-14 01:00 | 16.436 | 0.007943% | 17.1647 | 17.9257 | 18.7204 | 19.5504 | 0 | 0 | 0 | 0
2031-05-14 02:00 | 15.6871 | 0.007581% | 16.3826 | 17.1089 | 17.8675 | 18.6596 | 0 | 0 | 0 | 0
2031-05-14 03:00 | 15.3455 | 0.007416% | 16.0259 | 16.7364 | 17.4784 | 18.2533 | 0 | 0 | 0 | 0
2031-05-14 04:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-05-14 05:00 | 15.6346 | 0.007556% | 16.3277 | 17.0516 | 17.8076 | 18.5971 | 0 | 0 | 0 | 0
2031-05-14 06:00 | 18.4593 | 0.008921% | 19.2777 | 20.1324 | 21.025 | 21.9571 | 0 | 0 | 0 | 0
2031-05-14 07:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-05-14 08:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-05-14 09:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-05-14 10:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-05-14 11:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-05-14 12:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-05-14 13:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-05-14 14:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-05-14 15:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-05-14 16:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-05-14 17:00 | 25.6328 | 0.01239% | 26.7693 | 27.9561 | 29.1955 | 30.4899 | 0 | 0 | 0 | 0
2031-05-14 18:00 | 25.6985 | 0.01242% | 26.8379 | 28.0277 | 29.2703 | 30.568 | 0 | 0 | 0 | 0
2031-05-14 19:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-05-14 20:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-05-14 21:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-05-14 22:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-05-14 23:00 | 20.8111 | 0.01006% | 21.7337 | 22.6973 | 23.7036 | 24.7545 | 0 | 0 | 0 | 0
2031-05-15 | 18.0652 | 0.00873% | 18.8661 | 19.7025 | 20.576 | 21.4883 | 0 | 0 | 0 | 0
2031-05-15 01:00 | 16.4229 | 0.007937% | 17.151 | 17.9114 | 18.7055 | 19.5348 | 0 | 0 | 0 | 0
2031-05-15 02:00 | 15.3324 | 0.00741% | 16.0122 | 16.7221 | 17.4634 | 18.2377 | 0 | 0 | 0 | 0
2031-05-15 03:00 | 14.728 | 0.007118% | 15.381 | 16.0629 | 16.7751 | 17.5188 | 0 | 0 | 0 | 0
2031-05-15 04:00 | 14.7937 | 0.007149% | 15.4496 | 16.1346 | 16.8499 | 17.5969 | 0 | 0 | 0 | 0
2031-05-15 05:00 | 15.2798 | 0.007384% | 15.9573 | 16.6647 | 17.4036 | 18.1752 | 0 | 0 | 0 | 0
2031-05-15 06:00 | 18.4199 | 0.008902% | 19.2365 | 20.0894 | 20.9801 | 21.9102 | 0 | 0 | 0 | 0
2031-05-15 07:00 | 21.2709 | 0.01028% | 22.214 | 23.1988 | 24.2273 | 25.3015 | 0 | 0 | 0 | 0
2031-05-15 08:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-05-15 09:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-05-15 10:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-05-15 11:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-05-15 12:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-05-15 13:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-05-15 14:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-05-15 15:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-05-15 16:00 | 25.9876 | 0.01256% | 27.1397 | 28.343 | 29.5996 | 30.9119 | 0 | 0 | 0 | 0
2031-05-15 17:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-05-15 18:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-05-15 19:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-05-15 20:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-05-15 21:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-05-15 22:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-05-15 23:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-05-16 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-05-16 01:00 | 16.8959 | 0.008165% | 17.6449 | 18.4272 | 19.2442 | 20.0974 | 0 | 0 | 0 | 0
2031-05-16 02:00 | 15.8579 | 0.007664% | 16.561 | 17.2952 | 18.062 | 18.8628 | 0 | 0 | 0 | 0
2031-05-16 03:00 | 14.9251 | 0.007213% | 15.5868 | 16.2779 | 16.9995 | 17.7532 | 0 | 0 | 0 | 0
2031-05-16 04:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-05-16 05:00 | 15.1879 | 0.00734% | 15.8612 | 16.5644 | 17.2988 | 18.0658 | 0 | 0 | 0 | 0
2031-05-16 06:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-05-16 07:00 | 20.7191 | 0.01001% | 21.6377 | 22.597 | 23.5988 | 24.6451 | 0 | 0 | 0 | 0
2031-05-16 08:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-05-16 09:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-05-16 10:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-05-16 11:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-05-16 12:00 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-05-16 13:00 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-05-16 14:00 | 26.4999 | 0.01281% | 27.6748 | 28.9018 | 30.1832 | 31.5213 | 0 | 0 | 0 | 0
2031-05-16 15:00 | 26.9466 | 0.01302% | 28.1413 | 29.389 | 30.692 | 32.0527 | 0 | 0 | 0 | 0
2031-05-16 16:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-05-16 17:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-05-16 18:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-05-16 19:00 | 27.5116 | 0.0133% | 28.7313 | 30.0051 | 31.3354 | 32.7247 | 0 | 0 | 0 | 0
2031-05-16 20:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-05-16 21:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-05-16 22:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-05-16 23:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-05-17 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-05-17 01:00 | 17.9601 | 0.008679% | 18.7563 | 19.5879 | 20.4563 | 21.3632 | 0 | 0 | 0 | 0
2031-05-17 02:00 | 16.055 | 0.007759% | 16.7668 | 17.5102 | 18.2865 | 19.0972 | 0 | 0 | 0 | 0
2031-05-17 03:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-05-17 04:00 | 14.7806 | 0.007143% | 15.4359 | 16.1202 | 16.8349 | 17.5813 | 0 | 0 | 0 | 0
2031-05-17 05:00 | 14.439 | 0.006978% | 15.0791 | 15.7477 | 16.4459 | 17.175 | 0 | 0 | 0 | 0
2031-05-17 06:00 | 14.9645 | 0.007232% | 15.628 | 16.3208 | 17.0444 | 17.8001 | 0 | 0 | 0 | 0
2031-05-17 07:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-05-17 08:00 | 19.4053 | 0.009378% | 20.2656 | 21.1641 | 22.1024 | 23.0823 | 0 | 0 | 0 | 0
2031-05-17 09:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-05-17 10:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-05-17 11:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-05-17 12:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-05-17 13:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-05-17 14:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-05-17 15:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-05-17 16:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-05-17 17:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-05-17 18:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-05-17 19:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-05-17 20:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-05-17 21:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-05-17 22:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-05-17 23:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-05-18 | 17.1849 | 0.008305% | 17.9468 | 18.7425 | 19.5734 | 20.4412 | 0 | 0 | 0 | 0
2031-05-18 01:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-05-18 02:00 | 14.7412 | 0.007124% | 15.3947 | 16.0773 | 16.79 | 17.5344 | 0 | 0 | 0 | 0
2031-05-18 03:00 | 14.0054 | 0.006768% | 14.6264 | 15.2748 | 15.952 | 16.6593 | 0 | 0 | 0 | 0
2031-05-18 04:00 | 13.7821 | 0.00666% | 14.3931 | 15.0312 | 15.6976 | 16.3936 | 0 | 0 | 0 | 0
2031-05-18 05:00 | 13.874 | 0.006705% | 14.4892 | 15.1315 | 15.8024 | 16.503 | 0 | 0 | 0 | 0
2031-05-18 06:00 | 14.439 | 0.006978% | 15.0791 | 15.7477 | 16.4459 | 17.175 | 0 | 0 | 0 | 0
2031-05-18 07:00 | 15.7791 | 0.007625% | 16.4787 | 17.2093 | 17.9722 | 18.769 | 0 | 0 | 0 | 0
2031-05-18 08:00 | 17.3688 | 0.008394% | 18.1389 | 18.9431 | 19.7829 | 20.66 | 0 | 0 | 0 | 0
2031-05-18 09:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-05-18 10:00 | 20.1673 | 0.009746% | 21.0614 | 21.9952 | 22.9703 | 23.9887 | 0 | 0 | 0 | 0
2031-05-18 11:00 | 21.2052 | 0.01025% | 22.1454 | 23.1272 | 24.1525 | 25.2233 | 0 | 0 | 0 | 0
2031-05-18 12:00 | 21.2446 | 0.01027% | 22.1865 | 23.1702 | 24.1974 | 25.2702 | 0 | 0 | 0 | 0
2031-05-18 13:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-05-18 14:00 | 20.9556 | 0.01013% | 21.8847 | 22.8549 | 23.8682 | 24.9264 | 0 | 0 | 0 | 0
2031-05-18 15:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-05-18 16:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-05-18 17:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-05-18 18:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-05-18 19:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-05-18 20:00 | 21.5468 | 0.01041% | 22.5021 | 23.4997 | 24.5416 | 25.6296 | 0 | 0 | 0 | 0
2031-05-18 21:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-05-18 22:00 | 20.4695 | 0.009892% | 21.377 | 22.3247 | 23.3145 | 24.3482 | 0 | 0 | 0 | 0
2031-05-18 23:00 | 18.8929 | 0.00913% | 19.7305 | 20.6052 | 21.5188 | 22.4728 | 0 | 0 | 0 | 0
2031-05-19 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-05-19 01:00 | 15.8842 | 0.007676% | 16.5884 | 17.3239 | 18.0919 | 18.8941 | 0 | 0 | 0 | 0
2031-05-19 02:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-05-19 03:00 | 14.0054 | 0.006768% | 14.6264 | 15.2748 | 15.952 | 16.6593 | 0 | 0 | 0 | 0
2031-05-19 04:00 | 13.8478 | 0.006692% | 14.4617 | 15.1029 | 15.7725 | 16.4717 | 0 | 0 | 0 | 0
2031-05-19 05:00 | 13.966 | 0.006749% | 14.5852 | 15.2318 | 15.9071 | 16.6124 | 0 | 0 | 0 | 0
2031-05-19 06:00 | 14.8857 | 0.007194% | 15.5457 | 16.2349 | 16.9546 | 17.7063 | 0 | 0 | 0 | 0
2031-05-19 07:00 | 16.4623 | 0.007956% | 17.1921 | 17.9544 | 18.7504 | 19.5817 | 0 | 0 | 0 | 0
2031-05-19 08:00 | 18.1965 | 0.008794% | 19.0033 | 19.8458 | 20.7257 | 21.6445 | 0 | 0 | 0 | 0
2031-05-19 09:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-05-19 10:00 | 21.0476 | 0.01017% | 21.9807 | 22.9552 | 23.9729 | 25.0358 | 0 | 0 | 0 | 0
2031-05-19 11:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-05-19 12:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-05-19 13:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-05-19 14:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-05-19 15:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-05-19 16:00 | 23.7015 | 0.01145% | 24.7523 | 25.8497 | 26.9957 | 28.1926 | 0 | 0 | 0 | 0
2031-05-19 17:00 | 24.792 | 0.01198% | 25.8911 | 27.039 | 28.2378 | 29.4897 | 0 | 0 | 0 | 0
2031-05-19 18:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-05-19 19:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-05-19 20:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-05-19 21:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-05-19 22:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-05-19 23:00 | 19.6418 | 0.009492% | 20.5126 | 21.422 | 22.3718 | 23.3636 | 0 | 0 | 0 | 0
2031-05-20 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-05-20 01:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-05-20 02:00 | 14.7018 | 0.007105% | 15.3536 | 16.0343 | 16.7451 | 17.4875 | 0 | 0 | 0 | 0
2031-05-20 03:00 | 14.3996 | 0.006959% | 15.038 | 15.7047 | 16.401 | 17.1281 | 0 | 0 | 0 | 0
2031-05-20 04:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-05-20 05:00 | 15.2798 | 0.007384% | 15.9573 | 16.6647 | 17.4036 | 18.1752 | 0 | 0 | 0 | 0
2031-05-20 06:00 | 18.144 | 0.008768% | 18.9484 | 19.7885 | 20.6658 | 21.582 | 0 | 0 | 0 | 0
2031-05-20 07:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-05-20 08:00 | 21.6913 | 0.01048% | 22.653 | 23.6573 | 24.7062 | 25.8016 | 0 | 0 | 0 | 0
2031-05-20 09:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-05-20 10:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-05-20 11:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-05-20 12:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-05-20 13:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-05-20 14:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-05-20 15:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-05-20 16:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-05-20 17:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-05-20 18:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-05-20 19:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-05-20 20:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-05-20 21:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-05-20 22:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-05-20 23:00 | 19.7337 | 0.009537% | 20.6086 | 21.5223 | 22.4765 | 23.473 | 0 | 0 | 0 | 0
2031-05-21 | 18.0914 | 0.008743% | 18.8935 | 19.7312 | 20.606 | 21.5195 | 0 | 0 | 0 | 0
2031-05-21 01:00 | 16.4754 | 0.007962% | 17.2059 | 17.9687 | 18.7653 | 19.5973 | 0 | 0 | 0 | 0
2031-05-21 02:00 | 15.2667 | 0.007378% | 15.9436 | 16.6504 | 17.3886 | 18.1595 | 0 | 0 | 0 | 0
2031-05-21 03:00 | 14.7937 | 0.007149% | 15.4496 | 16.1346 | 16.8499 | 17.5969 | 0 | 0 | 0 | 0
2031-05-21 04:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-05-21 05:00 | 15.8842 | 0.007676% | 16.5884 | 17.3239 | 18.0919 | 18.8941 | 0 | 0 | 0 | 0
2031-05-21 06:00 | 18.2754 | 0.008832% | 19.0856 | 19.9318 | 20.8155 | 21.7383 | 0 | 0 | 0 | 0
2031-05-21 07:00 | 21.1921 | 0.01024% | 22.1316 | 23.1128 | 24.1376 | 25.2077 | 0 | 0 | 0 | 0
2031-05-21 08:00 | 21.7833 | 0.01053% | 22.7491 | 23.7576 | 24.8109 | 25.9109 | 0 | 0 | 0 | 0
2031-05-21 09:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-05-21 10:00 | 22.8344 | 0.01104% | 23.8467 | 24.904 | 26.0081 | 27.1612 | 0 | 0 | 0 | 0
2031-05-21 11:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-05-21 12:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-05-21 13:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-05-21 14:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-05-21 15:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-05-21 16:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-05-21 17:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-05-21 18:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-05-21 19:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-05-21 20:00 | 25.3438 | 0.01225% | 26.4674 | 27.6408 | 28.8663 | 30.1461 | 0 | 0 | 0 | 0
2031-05-21 21:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-05-21 22:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-05-21 23:00 | 20.522 | 0.009918% | 21.4319 | 22.3821 | 23.3744 | 24.4107 | 0 | 0 | 0 | 0
2031-05-22 | 18.6827 | 0.009029% | 19.511 | 20.376 | 21.2794 | 22.2228 | 0 | 0 | 0 | 0
2031-05-22 01:00 | 13.0595 | 0.006311% | 13.6385 | 14.2431 | 14.8746 | 15.5341 | 0 | 0 | 0 | 0
2031-05-22 02:00 | 12.2843 | 0.005937% | 12.8289 | 13.3977 | 13.9917 | 14.612 | 0 | 0 | 0 | 0
2031-05-22 03:00 | 18.814 | 0.009092% | 19.6482 | 20.5193 | 21.429 | 22.3791 | 0 | 0 | 0 | 0
2031-05-22 04:00 | 16.1995 | 0.007829% | 16.9177 | 17.6678 | 18.4511 | 19.2691 | 0 | 0 | 0 | 0
2031-05-22 05:00 | 16.9353 | 0.008184% | 17.6861 | 18.4702 | 19.2891 | 20.1443 | 0 | 0 | 0 | 0
2031-05-22 06:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-05-22 07:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-05-22 08:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-05-22 09:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-05-22 10:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-05-22 11:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-05-22 12:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-05-22 13:00 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-05-22 14:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-05-22 15:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-05-22 16:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-05-22 17:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-05-22 18:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-05-22 19:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0
2031-05-22 20:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-05-22 21:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-05-22 22:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-05-22 23:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-05-23 | 18.8797 | 0.009124% | 19.7168 | 20.5909 | 21.5038 | 22.4572 | 0 | 0 | 0 | 0
2031-05-23 01:00 | 17.0798 | 0.008254% | 17.837 | 18.6278 | 19.4537 | 20.3162 | 0 | 0 | 0 | 0
2031-05-23 02:00 | 16.3835 | 0.007918% | 17.1098 | 17.8684 | 18.6606 | 19.4879 | 0 | 0 | 0 | 0
2031-05-23 03:00 | 15.8185 | 0.007645% | 16.5198 | 17.2522 | 18.0171 | 18.8159 | 0 | 0 | 0 | 0
2031-05-23 04:00 | 15.674 | 0.007575% | 16.3689 | 17.0946 | 17.8525 | 18.644 | 0 | 0 | 0 | 0
2031-05-23 05:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-05-23 06:00 | 18.8666 | 0.009118% | 19.7031 | 20.5766 | 21.4889 | 22.4416 | 0 | 0 | 0 | 0
2031-05-23 07:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-05-23 08:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-05-23 09:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-05-23 10:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-05-23 11:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-05-23 12:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-05-23 13:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-05-23 14:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-05-23 15:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-05-23 16:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-05-23 17:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-05-23 18:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-05-23 19:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-05-23 20:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-05-23 21:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-05-23 22:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-05-23 23:00 | 20.8768 | 0.01009% | 21.8023 | 22.7689 | 23.7784 | 24.8326 | 0 | 0 | 0 | 0
2031-05-24 | 19.2082 | 0.009283% | 20.0598 | 20.9491 | 21.8779 | 22.8479 | 0 | 0 | 0 | 0
2031-05-24 01:00 | 17.3557 | 0.008387% | 18.1252 | 18.9287 | 19.768 | 20.6444 | 0 | 0 | 0 | 0
2031-05-24 02:00 | 16.3178 | 0.007886% | 17.0412 | 17.7967 | 18.5858 | 19.4098 | 0 | 0 | 0 | 0
2031-05-24 03:00 | 15.582 | 0.00753% | 16.2729 | 16.9943 | 17.7478 | 18.5346 | 0 | 0 | 0 | 0
2031-05-24 04:00 | 15.3718 | 0.007429% | 16.0533 | 16.765 | 17.5083 | 18.2846 | 0 | 0 | 0 | 0
2031-05-24 05:00 | 15.5557 | 0.007518% | 16.2454 | 16.9657 | 17.7178 | 18.5034 | 0 | 0 | 0 | 0
2031-05-24 06:00 | 16.4229 | 0.007937% | 17.151 | 17.9114 | 18.7055 | 19.5348 | 0 | 0 | 0 | 0
2031-05-24 07:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-05-24 08:00 | 20.0885 | 0.009708% | 20.9791 | 21.9092 | 22.8805 | 23.895 | 0 | 0 | 0 | 0
2031-05-24 09:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-05-24 10:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-05-24 11:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-05-24 12:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-05-24 13:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-05-24 14:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-05-24 15:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-05-24 16:00 | 22.8344 | 0.01104% | 23.8467 | 24.904 | 26.0081 | 27.1612 | 0 | 0 | 0 | 0
2031-05-24 17:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-05-24 18:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-05-24 19:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-05-24 20:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-05-24 21:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-05-24 22:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-05-24 23:00 | 20.0359 | 0.009683% | 20.9242 | 21.8519 | 22.8207 | 23.8324 | 0 | 0 | 0 | 0
2031-05-25 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-05-25 01:00 | 16.6199 | 0.008032% | 17.3568 | 18.1263 | 18.9299 | 19.7692 | 0 | 0 | 0 | 0
2031-05-25 02:00 | 15.6214 | 0.007549% | 16.314 | 17.0373 | 17.7927 | 18.5815 | 0 | 0 | 0 | 0
2031-05-25 03:00 | 15.0959 | 0.007295% | 15.7652 | 16.4641 | 17.1941 | 17.9564 | 0 | 0 | 0 | 0
2031-05-25 04:00 | 14.8726 | 0.007187% | 15.5319 | 16.2205 | 16.9397 | 17.6907 | 0 | 0 | 0 | 0
2031-05-25 05:00 | 14.8726 | 0.007187% | 15.5319 | 16.2205 | 16.9397 | 17.6907 | 0 | 0 | 0 | 0
2031-05-25 06:00 | 15.293 | 0.007391% | 15.971 | 16.6791 | 17.4185 | 18.1908 | 0 | 0 | 0 | 0
2031-05-25 07:00 | 17.0272 | 0.008229% | 17.7821 | 18.5705 | 19.3938 | 20.2537 | 0 | 0 | 0 | 0
2031-05-25 08:00 | 18.4856 | 0.008933% | 19.3051 | 20.161 | 21.0549 | 21.9884 | 0 | 0 | 0 | 0
2031-05-25 09:00 | 19.9834 | 0.009657% | 20.8693 | 21.7946 | 22.7608 | 23.7699 | 0 | 0 | 0 | 0
2031-05-25 10:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-05-25 11:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-05-25 12:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-05-25 13:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-05-25 14:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-05-25 15:00 | 23.2154 | 0.01122% | 24.2446 | 25.3195 | 26.4421 | 27.6144 | 0 | 0 | 0 | 0
2031-05-25 16:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-05-25 17:00 | 25.4226 | 0.01229% | 26.5497 | 27.7268 | 28.9561 | 30.2399 | 0 | 0 | 0 | 0
2031-05-25 18:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-05-25 19:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-05-25 20:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-05-25 21:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-05-25 22:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-05-25 23:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-05-26 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-05-26 01:00 | 15.766 | 0.007619% | 16.4649 | 17.1949 | 17.9573 | 18.7534 | 0 | 0 | 0 | 0
2031-05-26 02:00 | 14.9382 | 0.007219% | 15.6005 | 16.2922 | 17.0145 | 17.7688 | 0 | 0 | 0 | 0
2031-05-26 03:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-05-26 04:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-05-26 05:00 | 15.6609 | 0.007568% | 16.3552 | 17.0803 | 17.8375 | 18.6284 | 0 | 0 | 0 | 0
2031-05-26 06:00 | 17.9601 | 0.008679% | 18.7563 | 19.5879 | 20.4563 | 21.3632 | 0 | 0 | 0 | 0
2031-05-26 07:00 | 20.6009 | 0.009956% | 21.5142 | 22.468 | 23.4642 | 24.5044 | 0 | 0 | 0 | 0
2031-05-26 08:00 | 21.5468 | 0.01041% | 22.5021 | 23.4997 | 24.5416 | 25.6296 | 0 | 0 | 0 | 0
2031-05-26 09:00 | 21.9935 | 0.01063% | 22.9686 | 23.9869 | 25.0504 | 26.161 | 0 | 0 | 0 | 0
2031-05-26 10:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-05-26 11:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-05-26 12:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-05-26 13:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-05-26 14:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-05-26 15:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-05-26 16:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-05-26 17:00 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-05-26 18:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-05-26 19:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-05-26 20:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-05-26 21:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-05-26 22:00 | 23.3599 | 0.01129% | 24.3956 | 25.4771 | 26.6067 | 27.7863 | 0 | 0 | 0 | 0
2031-05-26 23:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-05-27 | 17.8944 | 0.008648% | 18.6877 | 19.5162 | 20.3815 | 21.2851 | 0 | 0 | 0 | 0
2031-05-27 01:00 | 16.1995 | 0.007829% | 16.9177 | 17.6678 | 18.4511 | 19.2691 | 0 | 0 | 0 | 0
2031-05-27 02:00 | 15.201 | 0.007346% | 15.875 | 16.5788 | 17.3138 | 18.0814 | 0 | 0 | 0 | 0
2031-05-27 03:00 | 14.8857 | 0.007194% | 15.5457 | 16.2349 | 16.9546 | 17.7063 | 0 | 0 | 0 | 0
2031-05-27 04:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-05-27 05:00 | 15.7265 | 0.0076% | 16.4238 | 17.1519 | 17.9124 | 18.7065 | 0 | 0 | 0 | 0
2031-05-27 06:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-05-27 07:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-05-27 08:00 | 21.849 | 0.01056% | 22.8177 | 23.8293 | 24.8858 | 25.9891 | 0 | 0 | 0 | 0
2031-05-27 09:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-05-27 10:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-05-27 11:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-05-27 12:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-05-27 13:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-05-27 14:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-05-27 15:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-05-27 16:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-05-27 17:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-05-27 18:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-05-27 19:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-05-27 20:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-05-27 21:00 | 25.3438 | 0.01225% | 26.4674 | 27.6408 | 28.8663 | 30.1461 | 0 | 0 | 0 | 0
2031-05-27 22:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-05-27 23:00 | 20.8768 | 0.01009% | 21.8023 | 22.7689 | 23.7784 | 24.8326 | 0 | 0 | 0 | 0
2031-05-28 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-05-28 01:00 | 16.3966 | 0.007924% | 17.1235 | 17.8827 | 18.6756 | 19.5035 | 0 | 0 | 0 | 0
2031-05-28 02:00 | 15.4112 | 0.007448% | 16.0945 | 16.808 | 17.5532 | 18.3314 | 0 | 0 | 0 | 0
2031-05-28 03:00 | 14.8726 | 0.007187% | 15.5319 | 16.2205 | 16.9397 | 17.6907 | 0 | 0 | 0 | 0
2031-05-28 04:00 | 14.7937 | 0.007149% | 15.4496 | 16.1346 | 16.8499 | 17.5969 | 0 | 0 | 0 | 0
2031-05-28 05:00 | 15.4638 | 0.007473% | 16.1494 | 16.8654 | 17.6131 | 18.394 | 0 | 0 | 0 | 0
2031-05-28 06:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-05-28 07:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-05-28 08:00 | 22.3482 | 0.0108% | 23.3391 | 24.3738 | 25.4544 | 26.5829 | 0 | 0 | 0 | 0
2031-05-28 09:00 | 23.2154 | 0.01122% | 24.2446 | 25.3195 | 26.4421 | 27.6144 | 0 | 0 | 0 | 0
2031-05-28 10:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-05-28 11:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-05-28 12:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-05-28 13:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-05-28 14:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-05-28 15:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-05-28 16:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-05-28 17:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-05-28 18:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-05-28 19:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-05-28 20:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-05-28 21:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-05-28 22:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-05-28 23:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-05-29 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-05-29 01:00 | 16.5543 | 0.008% | 17.2882 | 18.0547 | 18.8551 | 19.6911 | 0 | 0 | 0 | 0
2031-05-29 02:00 | 15.6083 | 0.007543% | 16.3003 | 17.023 | 17.7777 | 18.5659 | 0 | 0 | 0 | 0
2031-05-29 03:00 | 15.0039 | 0.007251% | 15.6691 | 16.3638 | 17.0893 | 17.847 | 0 | 0 | 0 | 0
2031-05-29 04:00 | 15.201 | 0.007346% | 15.875 | 16.5788 | 17.3138 | 18.0814 | 0 | 0 | 0 | 0
2031-05-29 05:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-05-29 06:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-05-29 07:00 | 21.2446 | 0.01027% | 22.1865 | 23.1702 | 24.1974 | 25.2702 | 0 | 0 | 0 | 0
2031-05-29 08:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-05-29 09:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-05-29 10:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-05-29 11:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-05-29 12:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-05-29 13:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-05-29 14:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-05-29 15:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-05-29 16:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-05-29 17:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-05-29 18:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-05-29 19:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-05-29 20:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-05-29 21:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-05-29 22:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-05-29 23:00 | 20.6271 | 0.009968% | 21.5416 | 22.4967 | 23.4941 | 24.5357 | 0 | 0 | 0 | 0
2031-05-30 | 18.4462 | 0.008914% | 19.264 | 20.1181 | 21.01 | 21.9415 | 0 | 0 | 0 | 0
2031-05-30 01:00 | 16.5674 | 0.008006% | 17.3019 | 18.069 | 18.8701 | 19.7067 | 0 | 0 | 0 | 0
2031-05-30 02:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-05-30 03:00 | 15.0434 | 0.00727% | 15.7103 | 16.4068 | 17.1342 | 17.8939 | 0 | 0 | 0 | 0
2031-05-30 04:00 | 14.8463 | 0.007175% | 15.5045 | 16.1919 | 16.9098 | 17.6595 | 0 | 0 | 0 | 0
2031-05-30 05:00 | 15.9105 | 0.007689% | 16.6159 | 17.3525 | 18.1219 | 18.9253 | 0 | 0 | 0 | 0
2031-05-30 06:00 | 17.8944 | 0.008648% | 18.6877 | 19.5162 | 20.3815 | 21.2851 | 0 | 0 | 0 | 0
2031-05-30 07:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-05-30 08:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-05-30 09:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-05-30 10:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-05-30 11:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-05-30 12:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-05-30 13:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-05-30 14:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-05-30 15:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-05-30 16:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-05-30 17:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-05-30 18:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-05-30 19:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-05-30 20:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-05-30 21:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-05-30 22:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-05-30 23:00 | 20.6009 | 0.009956% | 21.5142 | 22.468 | 23.4642 | 24.5044 | 0 | 0 | 0 | 0
2031-05-31 | 18.3673 | 0.008876% | 19.1817 | 20.0321 | 20.9202 | 21.8477 | 0 | 0 | 0 | 0
2031-05-31 01:00 | 16.8433 | 0.00814% | 17.59 | 18.3699 | 19.1843 | 20.0349 | 0 | 0 | 0 | 0
2031-05-31 02:00 | 15.5295 | 0.007505% | 16.218 | 16.937 | 17.6879 | 18.4721 | 0 | 0 | 0 | 0
2031-05-31 03:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-05-31 04:00 | 14.531 | 0.007022% | 15.1752 | 15.848 | 16.5506 | 17.2844 | 0 | 0 | 0 | 0
2031-05-31 05:00 | 14.4127 | 0.006965% | 15.0517 | 15.719 | 16.4159 | 17.1437 | 0 | 0 | 0 | 0
2031-05-31 06:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-05-31 07:00 | 16.7645 | 0.008102% | 17.5077 | 18.2839 | 19.0946 | 19.9411 | 0 | 0 | 0 | 0
2031-05-31 08:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-05-31 09:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-05-31 10:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-05-31 11:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-05-31 12:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-05-31 13:00 | 22.0855 | 0.01067% | 23.0646 | 24.0872 | 25.1551 | 26.2704 | 0 | 0 | 0 | 0
2031-05-31 14:00 | 21.7176 | 0.0105% | 22.6805 | 23.686 | 24.7361 | 25.8328 | 0 | 0 | 0 | 0
2031-05-31 15:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-05-31 16:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-05-31 17:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-05-31 18:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-05-31 19:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-05-31 20:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-05-31 21:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-05-31 22:00 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-05-31 23:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-06-01 | 13.9923 | 0.006762% | 14.6126 | 15.2605 | 15.9371 | 16.6436 | 0 | 0 | 0 | 0
2031-06-01 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-01 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-02 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-03 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-04 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-05 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-06 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-07 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-08 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-09 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-10 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-11 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-12 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-13 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-14 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-15 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-16 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-17 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-18 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-19 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-20 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 01:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 02:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 03:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 04:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 05:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 06:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 07:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 08:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 09:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 10:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 11:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 12:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 13:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 14:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 15:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 16:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 17:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 18:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 19:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 20:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 21:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 22:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-21 23:00 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2031-06-22 | 0.81457 | 0.0003937% | 0.85069 | 0.8884 | 0.92779 | 0.96893 | 0 | 0 | 0 | 0
2031-06-22 01:00 | 0.63064 | 0.0003048% | 0.6586 | 0.6878 | 0.71829 | 0.75014 | 0 | 0 | 0 | 0
2031-06-22 02:00 | 0.47298 | 0.0002286% | 0.49395 | 0.51585 | 0.53872 | 0.5626 | 0 | 0 | 0 | 0
2031-06-22 03:00 | 0.70947 | 0.0003429% | 0.74092 | 0.77377 | 0.80808 | 0.8439 | 0 | 0 | 0 | 0
2031-06-22 04:00 | 0.98537 | 0.0004762% | 1.0291 | 1.0747 | 1.1223 | 1.1721 | 0 | 0 | 0 | 0
2031-06-22 05:00 | 1.2613 | 0.0006095% | 1.3172 | 1.3756 | 1.4366 | 1.5003 | 0 | 0 | 0 | 0
2031-06-22 06:00 | 1.4189 | 0.0006857% | 1.4818 | 1.5475 | 1.6162 | 1.6878 | 0 | 0 | 0 | 0
2031-06-22 07:00 | 1.5897 | 0.0007683% | 1.6602 | 1.7338 | 1.8107 | 1.891 | 0 | 0 | 0 | 0
2031-06-22 08:00 | 5.2553 | 0.00254% | 5.4883 | 5.7316 | 5.9858 | 6.2511 | 0 | 0 | 0 | 0
2031-06-22 09:00 | 5.4524 | 0.002635% | 5.6941 | 5.9466 | 6.2102 | 6.4856 | 0 | 0 | 0 | 0
2031-06-22 10:00 | 5.4655 | 0.002641% | 5.7078 | 5.9609 | 6.2252 | 6.5012 | 0 | 0 | 0 | 0
2031-06-22 11:00 | 6.2801 | 0.003035% | 6.5585 | 6.8493 | 7.153 | 7.4701 | 0 | 0 | 0 | 0
2031-06-22 12:00 | 6.7794 | 0.003276% | 7.0799 | 7.3938 | 7.7216 | 8.064 | 0 | 0 | 0 | 0
2031-06-22 13:00 | 7.5677 | 0.003657% | 7.9032 | 8.2536 | 8.6195 | 9.0016 | 0 | 0 | 0 | 0
2031-06-22 14:00 | 8.1852 | 0.003956% | 8.5481 | 8.927 | 9.3228 | 9.7361 | 0 | 0 | 0 | 0
2031-06-22 15:00 | 9.1048 | 0.0044% | 9.5085 | 9.9301 | 10.3703 | 10.8301 | 0 | 0 | 0 | 0
2031-06-22 16:00 | 9.1837 | 0.004438% | 9.5908 | 10.016 | 10.4601 | 10.9239 | 0 | 0 | 0 | 0
2031-06-22 17:00 | 9.3019 | 0.004495% | 9.7143 | 10.145 | 10.5948 | 11.0645 | 0 | 0 | 0 | 0
2031-06-22 18:00 | 9.5384 | 0.00461% | 9.9613 | 10.4029 | 10.8641 | 11.3458 | 0 | 0 | 0 | 0
2031-06-22 19:00 | 9.8537 | 0.004762% | 10.2906 | 10.7468 | 11.2233 | 11.7209 | 0 | 0 | 0 | 0
2031-06-22 20:00 | 10.169 | 0.004914% | 10.6199 | 11.0907 | 11.5824 | 12.0959 | 0 | 0 | 0 | 0
2031-06-22 21:00 | 10.6814 | 0.005162% | 11.155 | 11.6496 | 12.166 | 12.7054 | 0 | 0 | 0 | 0
2031-06-22 22:00 | 9.8012 | 0.004737% | 10.2357 | 10.6895 | 11.1634 | 11.6584 | 0 | 0 | 0 | 0
2031-06-22 23:00 | 9.1968 | 0.004444% | 9.6046 | 10.0304 | 10.4751 | 10.9395 | 0 | 0 | 0 | 0
2031-06-23 | 8.8552 | 0.004279% | 9.2478 | 9.6578 | 10.086 | 10.5332 | 0 | 0 | 0 | 0
2031-06-23 01:00 | 8.8027 | 0.004254% | 9.1929 | 9.6005 | 10.0261 | 10.4706 | 0 | 0 | 0 | 0
2031-06-23 02:00 | 7.9749 | 0.003854% | 8.3285 | 8.6978 | 9.0834 | 9.4861 | 0 | 0 | 0 | 0
2031-06-23 03:00 | 7.1472 | 0.003454% | 7.4641 | 7.795 | 8.1406 | 8.5015 | 0 | 0 | 0 | 0
2031-06-23 04:00 | 6.9239 | 0.003346% | 7.2309 | 7.5514 | 7.8862 | 8.2359 | 0 | 0 | 0 | 0
2031-06-23 05:00 | 6.5691 | 0.003175% | 6.8604 | 7.1646 | 7.4822 | 7.8139 | 0 | 0 | 0 | 0
2031-06-23 06:00 | 6.1619 | 0.002978% | 6.435 | 6.7203 | 7.0183 | 7.3295 | 0 | 0 | 0 | 0
2031-06-23 07:00 | 5.8597 | 0.002832% | 6.1195 | 6.3908 | 6.6741 | 6.97 | 0 | 0 | 0 | 0
2031-06-23 08:00 | 6.0305 | 0.002914% | 6.2978 | 6.5771 | 6.8687 | 7.1732 | 0 | 0 | 0 | 0
2031-06-23 09:00 | 6.7662 | 0.00327% | 7.0662 | 7.3795 | 7.7067 | 8.0483 | 0 | 0 | 0 | 0
2031-06-23 10:00 | 7.2129 | 0.003486% | 7.5327 | 7.8667 | 8.2154 | 8.5797 | 0 | 0 | 0 | 0
2031-06-23 11:00 | 9.4859 | 0.004584% | 9.9064 | 10.3456 | 10.8043 | 11.2833 | 0 | 0 | 0 | 0
2031-06-23 12:00 | 10.4712 | 0.00506% | 10.9355 | 11.4203 | 11.9266 | 12.4554 | 0 | 0 | 0 | 0
2031-06-23 13:00 | 11.0099 | 0.005321% | 11.498 | 12.0078 | 12.5402 | 13.0961 | 0 | 0 | 0 | 0
2031-06-23 14:00 | 11.8245 | 0.005714% | 12.3487 | 12.8962 | 13.4679 | 14.0651 | 0 | 0 | 0 | 0
2031-06-23 15:00 | 12.5734 | 0.006076% | 13.1308 | 13.7129 | 14.3209 | 14.9558 | 0 | 0 | 0 | 0
2031-06-23 16:00 | 12.1529 | 0.005873% | 12.6917 | 13.2544 | 13.8421 | 14.4557 | 0 | 0 | 0 | 0
2031-06-23 17:00 | 13.4142 | 0.006483% | 14.0089 | 14.63 | 15.2786 | 15.956 | 0 | 0 | 0 | 0
2031-06-23 18:00 | 13.1252 | 0.006343% | 13.7071 | 14.3148 | 14.9494 | 15.6122 | 0 | 0 | 0 | 0
2031-06-23 19:00 | 13.0989 | 0.00633% | 13.6796 | 14.2861 | 14.9195 | 15.581 | 0 | 0 | 0 | 0
2031-06-23 20:00 | 12.9938 | 0.006279% | 13.5699 | 14.1715 | 14.7998 | 15.4559 | 0 | 0 | 0 | 0
2031-06-23 21:00 | 12.3237 | 0.005956% | 12.8701 | 13.4407 | 14.0366 | 14.6589 | 0 | 0 | 0 | 0
2031-06-23 22:00 | 12.1529 | 0.005873% | 12.6917 | 13.2544 | 13.8421 | 14.4557 | 0 | 0 | 0 | 0
2031-06-23 23:00 | 11.1019 | 0.005365% | 11.5941 | 12.1081 | 12.6449 | 13.2055 | 0 | 0 | 0 | 0
2031-06-24 | 10.261 | 0.004959% | 10.7159 | 11.191 | 11.6872 | 12.2053 | 0 | 0 | 0 | 0
2031-06-24 01:00 | 9.6435 | 0.00466% | 10.0711 | 10.5176 | 10.9839 | 11.4708 | 0 | 0 | 0 | 0
2031-06-24 02:00 | 8.6581 | 0.004184% | 9.042 | 9.4429 | 9.8615 | 10.2987 | 0 | 0 | 0 | 0
2031-06-24 03:00 | 8.0669 | 0.003898% | 8.4246 | 8.7981 | 9.1881 | 9.5955 | 0 | 0 | 0 | 0
2031-06-24 04:00 | 7.699 | 0.003721% | 8.0404 | 8.3969 | 8.7691 | 9.1579 | 0 | 0 | 0 | 0
2031-06-24 05:00 | 7.3837 | 0.003568% | 7.7111 | 8.053 | 8.41 | 8.7828 | 0 | 0 | 0 | 0
2031-06-24 06:00 | 7.0159 | 0.003391% | 7.3269 | 7.6517 | 7.991 | 8.3453 | 0 | 0 | 0 | 0
2031-06-24 07:00 | 6.9107 | 0.00334% | 7.2171 | 7.5371 | 7.8713 | 8.2202 | 0 | 0 | 0 | 0
2031-06-24 08:00 | 6.8319 | 0.003302% | 7.1348 | 7.4511 | 7.7815 | 8.1265 | 0 | 0 | 0 | 0
2031-06-24 09:00 | 7.2261 | 0.003492% | 7.5464 | 7.881 | 8.2304 | 8.5953 | 0 | 0 | 0 | 0
2031-06-24 10:00 | 7.4757 | 0.003613% | 7.8071 | 8.1533 | 8.5147 | 8.8922 | 0 | 0 | 0 | 0
2031-06-24 11:00 | 9.4859 | 0.004584% | 9.9064 | 10.3456 | 10.8043 | 11.2833 | 0 | 0 | 0 | 0
2031-06-24 12:00 | 10.1428 | 0.004902% | 10.5924 | 11.0621 | 11.5525 | 12.0647 | 0 | 0 | 0 | 0
2031-06-24 13:00 | 10.6946 | 0.005168% | 11.1687 | 11.6639 | 12.181 | 12.7211 | 0 | 0 | 0 | 0
2031-06-24 14:00 | 12.1661 | 0.005879% | 12.7054 | 13.2687 | 13.857 | 14.4714 | 0 | 0 | 0 | 0
2031-06-24 15:00 | 12.3763 | 0.005981% | 12.925 | 13.498 | 14.0965 | 14.7214 | 0 | 0 | 0 | 0
2031-06-24 16:00 | 12.9675 | 0.006267% | 13.5424 | 14.1428 | 14.7698 | 15.4247 | 0 | 0 | 0 | 0
2031-06-24 17:00 | 13.3616 | 0.006457% | 13.954 | 14.5727 | 15.2188 | 15.8935 | 0 | 0 | 0 | 0
2031-06-24 18:00 | 13.7427 | 0.006641% | 14.3519 | 14.9882 | 15.6527 | 16.3467 | 0 | 0 | 0 | 0
2031-06-24 19:00 | 13.6507 | 0.006597% | 14.2559 | 14.8879 | 15.548 | 16.2373 | 0 | 0 | 0 | 0
2031-06-24 20:00 | 13.2828 | 0.006419% | 13.8717 | 14.4867 | 15.129 | 15.7997 | 0 | 0 | 0 | 0
2031-06-24 21:00 | 13.3748 | 0.006464% | 13.9678 | 14.587 | 15.2337 | 15.9091 | 0 | 0 | 0 | 0
2031-06-24 22:00 | 12.9938 | 0.006279% | 13.5699 | 14.1715 | 14.7998 | 15.4559 | 0 | 0 | 0 | 0
2031-06-24 23:00 | 12.7704 | 0.006171% | 13.3366 | 13.9279 | 14.5454 | 15.1903 | 0 | 0 | 0 | 0
2031-06-25 | 11.8507 | 0.005727% | 12.3761 | 12.9248 | 13.4979 | 14.0963 | 0 | 0 | 0 | 0
2031-06-25 01:00 | 10.826 | 0.005232% | 11.3059 | 11.8072 | 12.3307 | 12.8773 | 0 | 0 | 0 | 0
2031-06-25 02:00 | 9.8012 | 0.004737% | 10.2357 | 10.6895 | 11.1634 | 11.6584 | 0 | 0 | 0 | 0
2031-06-25 03:00 | 8.8815 | 0.004292% | 9.2753 | 9.6865 | 10.1159 | 10.5644 | 0 | 0 | 0 | 0
2031-06-25 04:00 | 8.4873 | 0.004102% | 8.8636 | 9.2566 | 9.667 | 10.0956 | 0 | 0 | 0 | 0
2031-06-25 05:00 | 7.9618 | 0.003848% | 8.3148 | 8.6834 | 9.0684 | 9.4705 | 0 | 0 | 0 | 0
2031-06-25 06:00 | 7.5677 | 0.003657% | 7.9032 | 8.2536 | 8.6195 | 9.0016 | 0 | 0 | 0 | 0
2031-06-25 07:00 | 7.6071 | 0.003676% | 7.9443 | 8.2965 | 8.6644 | 9.0485 | 0 | 0 | 0 | 0
2031-06-25 08:00 | 7.4363 | 0.003594% | 7.766 | 8.1103 | 8.4698 | 8.8454 | 0 | 0 | 0 | 0
2031-06-25 09:00 | 7.9355 | 0.003835% | 8.2874 | 8.6548 | 9.0385 | 9.4392 | 0 | 0 | 0 | 0
2031-06-25 10:00 | 8.9078 | 0.004305% | 9.3027 | 9.7151 | 10.1459 | 10.5957 | 0 | 0 | 0 | 0
2031-06-25 11:00 | 9.8406 | 0.004756% | 10.2769 | 10.7325 | 11.2083 | 11.7052 | 0 | 0 | 0 | 0
2031-06-25 12:00 | 10.8128 | 0.005225% | 11.2922 | 11.7929 | 12.3157 | 12.8617 | 0 | 0 | 0 | 0
2031-06-25 13:00 | 11.0756 | 0.005352% | 11.5666 | 12.0794 | 12.615 | 13.1743 | 0 | 0 | 0 | 0
2031-06-25 14:00 | 12.0478 | 0.005822% | 12.582 | 13.1398 | 13.7223 | 14.3307 | 0 | 0 | 0 | 0
2031-06-25 15:00 | 12.6128 | 0.006095% | 13.172 | 13.7559 | 14.3658 | 15.0027 | 0 | 0 | 0 | 0
2031-06-25 16:00 | 12.6653 | 0.006121% | 13.2268 | 13.8133 | 14.4257 | 15.0652 | 0 | 0 | 0 | 0
2031-06-25 17:00 | 13.4011 | 0.006476% | 13.9952 | 14.6157 | 15.2637 | 15.9404 | 0 | 0 | 0 | 0
2031-06-25 18:00 | 13.0989 | 0.00633% | 13.6796 | 14.2861 | 14.9195 | 15.581 | 0 | 0 | 0 | 0
2031-06-25 19:00 | 13.2303 | 0.006394% | 13.8168 | 14.4294 | 15.0691 | 15.7372 | 0 | 0 | 0 | 0
2031-06-25 20:00 | 12.7704 | 0.006171% | 13.3366 | 13.9279 | 14.5454 | 15.1903 | 0 | 0 | 0 | 0
2031-06-25 21:00 | 12.6653 | 0.006121% | 13.2268 | 13.8133 | 14.4257 | 15.0652 | 0 | 0 | 0 | 0
2031-06-25 22:00 | 11.8113 | 0.005708% | 12.335 | 12.8819 | 13.453 | 14.0494 | 0 | 0 | 0 | 0
2031-06-25 23:00 | 11.7982 | 0.005702% | 12.3213 | 12.8675 | 13.438 | 14.0338 | 0 | 0 | 0 | 0
2031-06-26 | 9.9982 | 0.004832% | 10.4415 | 10.9044 | 11.3879 | 11.8928 | 0 | 0 | 0 | 0
2031-06-26 01:00 | 10.0771 | 0.00487% | 10.5238 | 10.9904 | 11.4777 | 11.9865 | 0 | 0 | 0 | 0
2031-06-26 02:00 | 8.6581 | 0.004184% | 9.042 | 9.4429 | 9.8615 | 10.2987 | 0 | 0 | 0 | 0
2031-06-26 03:00 | 8.1457 | 0.003937% | 8.5069 | 8.884 | 9.2779 | 9.6893 | 0 | 0 | 0 | 0
2031-06-26 04:00 | 7.6334 | 0.003689% | 7.9718 | 8.3252 | 8.6943 | 9.0798 | 0 | 0 | 0 | 0
2031-06-26 05:00 | 7.121 | 0.003441% | 7.4367 | 7.7664 | 8.1107 | 8.4703 | 0 | 0 | 0 | 0
2031-06-26 06:00 | 7.0159 | 0.003391% | 7.3269 | 7.6517 | 7.991 | 8.3453 | 0 | 0 | 0 | 0
2031-06-26 07:00 | 7.0553 | 0.00341% | 7.3681 | 7.6947 | 8.0359 | 8.3921 | 0 | 0 | 0 | 0
2031-06-26 08:00 | 6.9239 | 0.003346% | 7.2309 | 7.5514 | 7.8862 | 8.2359 | 0 | 0 | 0 | 0
2031-06-26 09:00 | 7.4888 | 0.003619% | 7.8208 | 8.1676 | 8.5297 | 8.9079 | 0 | 0 | 0 | 0
2031-06-26 10:00 | 8.356 | 0.004038% | 8.7264 | 9.1133 | 9.5173 | 9.9393 | 0 | 0 | 0 | 0
2031-06-26 11:00 | 9.6566 | 0.004667% | 10.0848 | 10.5319 | 10.9988 | 11.4865 | 0 | 0 | 0 | 0
2031-06-26 12:00 | 10.5106 | 0.005079% | 10.9766 | 11.4633 | 11.9715 | 12.5023 | 0 | 0 | 0 | 0
2031-06-26 13:00 | 11.115 | 0.005371% | 11.6078 | 12.1224 | 12.6599 | 13.2211 | 0 | 0 | 0 | 0
2031-06-26 14:00 | 11.4829 | 0.005549% | 11.992 | 12.5236 | 13.0789 | 13.6587 | 0 | 0 | 0 | 0
2031-06-26 15:00 | 11.7851 | 0.005695% | 12.3075 | 12.8532 | 13.4231 | 14.0182 | 0 | 0 | 0 | 0
2031-06-26 16:00 | 11.5223 | 0.005568% | 12.0331 | 12.5666 | 13.1238 | 13.7056 | 0 | 0 | 0 | 0
2031-06-26 17:00 | 11.4303 | 0.005524% | 11.9371 | 12.4663 | 13.019 | 13.5962 | 0 | 0 | 0 | 0
2031-06-26 18:00 | 10.9442 | 0.005289% | 11.4294 | 11.9361 | 12.4653 | 13.018 | 0 | 0 | 0 | 0
2031-06-26 19:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-06-26 20:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-06-26 21:00 | 29.0356 | 0.01403% | 30.3229 | 31.6673 | 33.0713 | 34.5375 | 0 | 0 | 0 | 0
2031-06-26 22:00 | 28.2736 | 0.01366% | 29.5271 | 30.8362 | 32.2034 | 33.6311 | 0 | 0 | 0 | 0
2031-06-26 23:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-06-27 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-06-27 01:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-06-27 02:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-06-27 03:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-06-27 04:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-06-27 05:00 | 18.433 | 0.008908% | 19.2503 | 20.1037 | 20.995 | 21.9259 | 0 | 0 | 0 | 0
2031-06-27 06:00 | 17.0535 | 0.008241% | 17.8096 | 18.5992 | 19.4238 | 20.2849 | 0 | 0 | 0 | 0
2031-06-27 07:00 | 16.2389 | 0.007848% | 16.9589 | 17.7108 | 18.496 | 19.316 | 0 | 0 | 0 | 0
2031-06-27 08:00 | 16.0813 | 0.007772% | 16.7942 | 17.5388 | 18.3164 | 19.1285 | 0 | 0 | 0 | 0
2031-06-27 09:00 | 16.6856 | 0.008064% | 17.4254 | 18.198 | 19.0048 | 19.8473 | 0 | 0 | 0 | 0
2031-06-27 10:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-06-27 11:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-06-27 12:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-06-27 13:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-06-27 14:00 | 26.3817 | 0.01275% | 27.5513 | 28.7728 | 30.0485 | 31.3807 | 0 | 0 | 0 | 0
2031-06-27 15:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-06-27 16:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-06-27 17:00 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-06-27 18:00 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-06-27 19:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-06-27 20:00 | 31.3611 | 0.01516% | 32.7515 | 34.2036 | 35.72 | 37.3036 | 0 | 0 | 0 | 0.27328
2031-06-27 21:00 | 32.7144 | 0.01581% | 34.1648 | 35.6795 | 37.2613 | 38.9133 | 0 | 0 | 0.23519 | 1.722
2031-06-27 22:00 | 33.3319 | 0.01611% | 34.8096 | 36.3529 | 37.9646 | 39.6478 | 0 | 0 | 0.86818 | 2.383
2031-06-27 23:00 | 32.583 | 0.01575% | 34.0276 | 35.5362 | 37.1117 | 38.757 | 0 | 0 | 0.10051 | 1.5813
2031-06-28 | 31.1246 | 0.01504% | 32.5045 | 33.9456 | 35.4506 | 37.0223 | 0 | 0 | 0 | 0.020104
2031-06-28 01:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-06-28 02:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-06-28 03:00 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-06-28 04:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-06-28 05:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-06-28 06:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-06-28 07:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-06-28 08:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-06-28 09:00 | 17.3688 | 0.008394% | 18.1389 | 18.9431 | 19.7829 | 20.66 | 0 | 0 | 0 | 0
2031-06-28 10:00 | 18.3673 | 0.008876% | 19.1817 | 20.0321 | 20.9202 | 21.8477 | 0 | 0 | 0 | 0
2031-06-28 11:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-06-28 12:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-06-28 13:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-06-28 14:00 | 32.9114 | 0.0159% | 34.3706 | 35.8944 | 37.4858 | 39.1477 | 0 | 0 | 0.43721 | 1.933
2031-06-28 15:00 | 34.9347 | 0.01688% | 36.4836 | 38.1011 | 39.7903 | 41.5544 | 0 | 0.99097 | 2.5113 | 4.099
2031-06-28 16:00 | 36.3274 | 0.01756% | 37.938 | 39.62 | 41.3765 | 43.211 | 0.84418 | 2.358 | 3.9389 | 5.5899
2031-06-28 17:00 | 36.7215 | 0.01775% | 38.3496 | 40.0498 | 41.8255 | 43.6798 | 1.2146 | 2.7449 | 4.3429 | 6.0118
2031-06-28 18:00 | 36.4325 | 0.01761% | 38.0477 | 39.7346 | 41.4962 | 43.336 | 0.94297 | 2.4611 | 4.0466 | 5.7024
2031-06-28 19:00 | 36.5245 | 0.01765% | 38.1438 | 39.8349 | 41.601 | 43.4454 | 1.0294 | 2.5514 | 4.1409 | 5.8008
2031-06-28 20:00 | 36.5902 | 0.01768% | 38.2124 | 39.9065 | 41.6758 | 43.5235 | 1.0912 | 2.6159 | 4.2082 | 5.8712
2031-06-28 21:00 | 36.2617 | 0.01752% | 37.8694 | 39.5483 | 41.3017 | 43.1328 | 0.78243 | 2.2935 | 3.8715 | 5.5195
2031-06-28 22:00 | 34.7771 | 0.01681% | 36.3189 | 37.9291 | 39.6107 | 41.3669 | 0 | 0.83622 | 2.3497 | 3.9302
2031-06-28 23:00 | 33.0034 | 0.01595% | 34.4666 | 35.9947 | 37.5905 | 39.2571 | 0 | 0 | 0.53148 | 2.0314
2031-06-29 | 29.9553 | 0.01448% | 31.2834 | 32.6704 | 34.1188 | 35.6315 | 0 | 0 | 0 | 0
2031-06-29 01:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-06-29 02:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-06-29 03:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-06-29 04:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-06-29 05:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-06-29 06:00 | 17.4477 | 0.008432% | 18.2212 | 19.029 | 19.8727 | 20.7538 | 0 | 0 | 0 | 0
2031-06-29 07:00 | 16.344 | 0.007898% | 17.0687 | 17.8254 | 18.6157 | 19.441 | 0 | 0 | 0 | 0
2031-06-29 08:00 | 15.6214 | 0.007549% | 16.314 | 17.0373 | 17.7927 | 18.5815 | 0 | 0 | 0 | 0
2031-06-29 09:00 | 15.582 | 0.00753% | 16.2729 | 16.9943 | 17.7478 | 18.5346 | 0 | 0 | 0 | 0
2031-06-29 10:00 | 16.147 | 0.007803% | 16.8628 | 17.6105 | 18.3912 | 19.2066 | 0 | 0 | 0 | 0
2031-06-29 11:00 | 18.8009 | 0.009086% | 19.6344 | 20.5049 | 21.414 | 22.3634 | 0 | 0 | 0 | 0
2031-06-29 12:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-06-29 13:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-06-29 14:00 | 27.2357 | 0.01316% | 28.4432 | 29.7042 | 31.0212 | 32.3965 | 0 | 0 | 0 | 0
2031-06-29 15:00 | 28.6152 | 0.01383% | 29.8839 | 31.2088 | 32.5924 | 34.0374 | 0 | 0 | 0 | 0
2031-06-29 16:00 | 29.1276 | 0.01408% | 30.419 | 31.7676 | 33.176 | 34.6469 | 0 | 0 | 0 | 0
2031-06-29 17:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-06-29 18:00 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-06-29 19:00 | 32.0443 | 0.01549% | 33.465 | 34.9487 | 36.4981 | 38.1163 | 0 | 0 | 0 | 1.0047
2031-06-29 20:00 | 34.5406 | 0.01669% | 36.0719 | 37.6712 | 39.3414 | 41.0856 | 0 | 0.60409 | 2.1072 | 3.677
2031-06-29 21:00 | 35.815 | 0.01731% | 37.4029 | 39.0611 | 40.7929 | 42.6015 | 0.36258 | 1.855 | 3.4136 | 5.0413
2031-06-29 22:00 | 35.7362 | 0.01727% | 37.3205 | 38.9752 | 40.7031 | 42.5077 | 0.28849 | 1.7776 | 3.3328 | 4.9569
2031-06-29 23:00 | 35.0793 | 0.01695% | 36.6345 | 38.2587 | 39.9549 | 41.7263 | 0 | 1.1328 | 2.6594 | 4.2537
2031-06-30 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-06-30 01:00 | 30.586 | 0.01478% | 31.942 | 33.3581 | 34.8371 | 36.3816 | 0 | 0 | 0 | 0
2031-06-30 02:00 | 29.1145 | 0.01407% | 30.4053 | 31.7533 | 33.1611 | 34.6313 | 0 | 0 | 0 | 0
2031-06-30 03:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-06-30 04:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-06-30 05:00 | 20.1147 | 0.009721% | 21.0065 | 21.9379 | 22.9105 | 23.9262 | 0 | 0 | 0 | 0
2031-06-30 06:00 | 18.4199 | 0.008902% | 19.2365 | 20.0894 | 20.9801 | 21.9102 | 0 | 0 | 0 | 0
2031-06-30 07:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-06-30 08:00 | 16.4623 | 0.007956% | 17.1921 | 17.9544 | 18.7504 | 19.5817 | 0 | 0 | 0 | 0
2031-06-30 09:00 | 16.6725 | 0.008057% | 17.4117 | 18.1836 | 18.9898 | 19.8317 | 0 | 0 | 0 | 0
2031-06-30 10:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-06-30 11:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-06-30 12:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-06-30 13:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-06-30 14:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-06-30 15:00 | 33.5815 | 0.01623% | 35.0703 | 36.6252 | 38.249 | 39.9447 | 0 | 0 | 1.1241 | 2.6503
2031-06-30 16:00 | 35.053 | 0.01694% | 36.6071 | 38.23 | 39.925 | 41.6951 | 0 | 1.107 | 2.6325 | 4.2256
2031-06-30 17:00 | 36.1435 | 0.01747% | 37.7459 | 39.4194 | 41.167 | 42.9922 | 0.6713 | 2.1774 | 3.7503 | 5.393
2031-06-30 18:00 | 35.723 | 0.01726% | 37.3068 | 38.9608 | 40.6882 | 42.4921 | 0.27614 | 1.7647 | 3.3193 | 4.9429
2031-06-30 19:00 | 34.199 | 0.01653% | 35.7152 | 37.2986 | 38.9523 | 40.6793 | 0 | 0.26878 | 1.7571 | 3.3113
2031-06-30 20:00 | 33.818 | 0.01634% | 35.3173 | 36.8831 | 38.5183 | 40.226 | 0 | 0 | 1.3665 | 2.9034
2031-06-30 21:00 | 34.0807 | 0.01647% | 35.5917 | 37.1697 | 38.8176 | 40.5386 | 0 | 0.15272 | 1.6359 | 3.1847
2031-06-30 22:00 | 34.0151 | 0.01644% | 35.5231 | 37.098 | 38.7428 | 40.4605 | 0 | 0.088238 | 1.5685 | 3.1144
2031-06-30 23:00 | 33.0822 | 0.01599% | 34.5489 | 36.0807 | 37.6803 | 39.3509 | 0 | 0 | 0.61229 | 2.1158
2031-07-01 | 31.1509 | 0.01505% | 32.532 | 33.9743 | 35.4806 | 37.0536 | 0 | 0 | 0 | 0.048234
2031-07-01 01:00 | 30.7962 | 0.01488% | 32.1615 | 33.5874 | 35.0765 | 36.6316 | 0 | 0 | 0 | 0
2031-07-01 02:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-07-01 03:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-07-01 04:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-07-01 05:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-07-01 06:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-07-01 07:00 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-07-01 08:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-07-01 09:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-07-01 10:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-07-01 11:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-07-01 12:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-07-01 13:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-07-01 14:00 | 32.8589 | 0.01588% | 34.3157 | 35.8371 | 37.4259 | 39.0852 | 0 | 0 | 0.38333 | 1.8767
2031-07-01 15:00 | 34.4355 | 0.01664% | 35.9622 | 37.5566 | 39.2217 | 40.9606 | 0 | 0.50092 | 1.9995 | 3.5645
2031-07-01 16:00 | 36.5245 | 0.01765% | 38.1438 | 39.8349 | 41.601 | 43.4454 | 1.0294 | 2.5514 | 4.1409 | 5.8008
2031-07-01 17:00 | 39.0207 | 0.01886% | 40.7507 | 42.5574 | 44.4442 | 46.4147 | 3.3757 | 5.0017 | 6.6998 | 8.4732
2031-07-01 18:00 | 40.5316 | 0.01959% | 42.3286 | 44.2053 | 46.1651 | 48.2119 | 4.7958 | 6.4847 | 8.2486 | 10.0907
2031-07-01 19:00 | 41.0966 | 0.01986% | 42.9186 | 44.8214 | 46.8086 | 48.8839 | 5.3268 | 7.0393 | 8.8277 | 10.6955
2031-07-01 20:00 | 41.7798 | 0.02019% | 43.6321 | 45.5665 | 47.5867 | 49.6965 | 5.9689 | 7.7099 | 9.5281 | 11.4269
2031-07-01 21:00 | 42.3579 | 0.02047% | 44.2358 | 46.197 | 48.2452 | 50.3841 | 6.5122 | 8.2773 | 10.1207 | 12.0457
2031-07-01 22:00 | 41.7272 | 0.02017% | 43.5772 | 45.5092 | 47.5269 | 49.634 | 5.9195 | 7.6583 | 9.4742 | 11.3706
2031-07-01 23:00 | 40.9127 | 0.01977% | 42.7265 | 44.6208 | 46.5991 | 48.6651 | 5.1539 | 6.8587 | 8.6392 | 10.4986
2031-07-02 | 38.4952 | 0.0186% | 40.2019 | 41.9843 | 43.8456 | 45.7896 | 2.8817 | 4.4858 | 6.1611 | 7.9106
2031-07-02 01:00 | 34.9873 | 0.01691% | 36.5385 | 38.1584 | 39.8502 | 41.6169 | 0 | 1.0426 | 2.5651 | 4.1552
2031-07-02 02:00 | 31.8866 | 0.01541% | 33.3004 | 34.7767 | 36.3186 | 37.9288 | 0 | 0 | 0 | 0.83588
2031-07-02 03:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-07-02 04:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-07-02 05:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-07-02 06:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-07-02 07:00 | 18.4593 | 0.008921% | 19.2777 | 20.1324 | 21.025 | 21.9571 | 0 | 0 | 0 | 0
2031-07-02 08:00 | 17.6185 | 0.008514% | 18.3996 | 19.2153 | 20.0672 | 20.9569 | 0 | 0 | 0 | 0
2031-07-02 09:00 | 17.8024 | 0.008603% | 18.5917 | 19.4159 | 20.2767 | 21.1757 | 0 | 0 | 0 | 0
2031-07-02 10:00 | 20.2067 | 0.009765% | 21.1026 | 22.0382 | 23.0152 | 24.0356 | 0 | 0 | 0 | 0
2031-07-02 11:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-07-02 12:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-07-02 13:00 | 31.8866 | 0.01541% | 33.3004 | 34.7767 | 36.3186 | 37.9288 | 0 | 0 | 0 | 0.83588
2031-07-02 14:00 | 34.58 | 0.01671% | 36.1131 | 37.7142 | 39.3863 | 41.1325 | 0 | 0.64277 | 2.1476 | 3.7192
2031-07-02 15:00 | 35.5785 | 0.01719% | 37.1559 | 38.8032 | 40.5236 | 42.3202 | 0.1403 | 1.6229 | 3.1712 | 4.7882
2031-07-02 16:00 | 37.3522 | 0.01805% | 39.0082 | 40.7376 | 42.5437 | 44.4299 | 1.8074 | 3.3639 | 4.9894 | 6.6869
2031-07-02 17:00 | 37.9828 | 0.01836% | 39.6668 | 41.4254 | 43.262 | 45.1801 | 2.4001 | 3.9829 | 5.6358 | 7.3621
2031-07-02 18:00 | 38.9156 | 0.01881% | 40.641 | 42.4428 | 44.3245 | 46.2896 | 3.2769 | 4.8985 | 6.5921 | 8.3607
2031-07-02 19:00 | 40.3346 | 0.01949% | 42.1228 | 43.9903 | 45.9407 | 47.9774 | 4.6105 | 6.2913 | 8.0466 | 9.8797
2031-07-02 20:00 | 41.3199 | 0.01997% | 43.1519 | 45.065 | 47.063 | 49.1495 | 5.5367 | 7.2585 | 9.0567 | 10.9346
2031-07-02 21:00 | 42.1871 | 0.02039% | 44.0574 | 46.0107 | 48.0506 | 50.181 | 6.3517 | 8.1097 | 9.9456 | 11.8629
2031-07-02 22:00 | 38.5084 | 0.01861% | 40.2156 | 41.9986 | 43.8606 | 45.8052 | 2.8941 | 4.4987 | 6.1746 | 7.9247
2031-07-02 23:00 | 37.5755 | 0.01816% | 39.2415 | 40.9812 | 42.7981 | 44.6956 | 2.0173 | 3.5831 | 5.2183 | 6.926
2031-07-03 | 36.0121 | 0.0174% | 37.6087 | 39.2761 | 41.0174 | 42.8359 | 0.54781 | 2.0485 | 3.6156 | 5.2523
2031-07-03 01:00 | 34.3698 | 0.01661% | 35.8936 | 37.4849 | 39.1468 | 40.8824 | 0 | 0.43644 | 1.9321 | 3.4942
2031-07-03 02:00 | 32.5173 | 0.01571% | 33.9589 | 35.4645 | 37.0369 | 38.6789 | 0 | 0 | 0.033167 | 1.511
2031-07-03 03:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-07-03 04:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-07-03 05:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-07-03 06:00 | 20.3906 | 0.009854% | 21.2947 | 22.2388 | 23.2247 | 24.2544 | 0 | 0 | 0 | 0
2031-07-03 07:00 | 19.1556 | 0.009257% | 20.0049 | 20.8918 | 21.8181 | 22.7854 | 0 | 0 | 0 | 0
2031-07-03 08:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-07-03 09:00 | 19.0374 | 0.0092% | 19.8814 | 20.7629 | 21.6834 | 22.6447 | 0 | 0 | 0 | 0
2031-07-03 10:00 | 21.3366 | 0.01031% | 22.2826 | 23.2705 | 24.3022 | 25.3796 | 0 | 0 | 0 | 0
2031-07-03 11:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-07-03 12:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-07-03 13:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-07-03 14:00 | 31.3611 | 0.01516% | 32.7515 | 34.2036 | 35.72 | 37.3036 | 0 | 0 | 0 | 0.27328
2031-07-03 15:00 | 32.7406 | 0.01582% | 34.1922 | 35.7081 | 37.2912 | 38.9446 | 0 | 0 | 0.26212 | 1.7501
2031-07-03 16:00 | 34.3304 | 0.01659% | 35.8524 | 37.4419 | 39.1019 | 40.8355 | 0 | 0.39775 | 1.8917 | 3.452
2031-07-03 17:00 | 34.6194 | 0.01673% | 36.1543 | 37.7572 | 39.4312 | 41.1793 | 0 | 0.68146 | 2.188 | 3.7614
2031-07-03 18:00 | 34.9085 | 0.01687% | 36.4561 | 38.0724 | 39.7604 | 41.5232 | 0 | 0.96518 | 2.4843 | 4.0708
2031-07-03 19:00 | 36.5639 | 0.01767% | 38.185 | 39.8779 | 41.6459 | 43.4923 | 1.0665 | 2.5901 | 4.1813 | 5.843
2031-07-03 20:00 | 37.3522 | 0.01805% | 39.0082 | 40.7376 | 42.5437 | 44.4299 | 1.8074 | 3.3639 | 4.9894 | 6.6869
2031-07-03 21:00 | 37.996 | 0.01836% | 39.6805 | 41.4398 | 43.277 | 45.1957 | 2.4125 | 3.9958 | 5.6493 | 7.3761
2031-07-03 22:00 | 37.6938 | 0.01822% | 39.3649 | 41.1102 | 42.9328 | 44.8363 | 2.1284 | 3.6992 | 5.3395 | 7.0526
2031-07-03 23:00 | 36.4456 | 0.01761% | 38.0615 | 39.7489 | 41.5112 | 43.3516 | 0.95532 | 2.474 | 4.0601 | 5.7164
2031-07-04 | 33.2662 | 0.01608% | 34.741 | 36.2813 | 37.8898 | 39.5697 | 0 | 0 | 0.80084 | 2.3127
2031-07-04 01:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-07-04 02:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-07-04 03:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-07-04 04:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-07-04 05:00 | 19.668 | 0.009505% | 20.54 | 21.4507 | 22.4017 | 23.3949 | 0 | 0 | 0 | 0
2031-07-04 06:00 | 17.8812 | 0.008641% | 18.674 | 19.5019 | 20.3665 | 21.2695 | 0 | 0 | 0 | 0
2031-07-04 07:00 | 16.528 | 0.007987% | 17.2608 | 18.026 | 18.8252 | 19.6598 | 0 | 0 | 0 | 0
2031-07-04 08:00 | 16.0681 | 0.007765% | 16.7805 | 17.5245 | 18.3014 | 19.1128 | 0 | 0 | 0 | 0
2031-07-04 09:00 | 16.2915 | 0.007873% | 17.0138 | 17.7681 | 18.5558 | 19.3785 | 0 | 0 | 0 | 0
2031-07-04 10:00 | 18.8929 | 0.00913% | 19.7305 | 20.6052 | 21.5188 | 22.4728 | 0 | 0 | 0 | 0
2031-07-04 11:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-07-04 12:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-07-04 13:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-07-04 14:00 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-07-04 15:00 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-07-04 16:00 | 31.0721 | 0.01502% | 32.4497 | 33.8883 | 35.3908 | 36.9598 | 0 | 0 | 0 | 0
2031-07-04 17:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-07-04 18:00 | 33.2136 | 0.01605% | 34.6861 | 36.224 | 37.83 | 39.5072 | 0 | 0 | 0.74697 | 2.2564
2031-07-04 19:00 | 33.3713 | 0.01613% | 34.8508 | 36.3959 | 38.0095 | 39.6947 | 0 | 0 | 0.90858 | 2.4252
2031-07-04 20:00 | 34.5931 | 0.01672% | 36.1268 | 37.7285 | 39.4012 | 41.1481 | 0 | 0.65567 | 2.1611 | 3.7333
2031-07-04 21:00 | 36.0778 | 0.01744% | 37.6773 | 39.3477 | 41.0922 | 42.914 | 0.60955 | 2.1129 | 3.683 | 5.3226
2031-07-04 22:00 | 35.5128 | 0.01716% | 37.0873 | 38.7316 | 40.4487 | 42.242 | 0.078559 | 1.5584 | 3.1039 | 4.7178
2031-07-04 23:00 | 33.6866 | 0.01628% | 35.1801 | 36.7398 | 38.3687 | 40.0698 | 0 | 0 | 1.2318 | 2.7628
2031-07-05 | 31.7421 | 0.01534% | 33.1494 | 34.6191 | 36.154 | 37.7568 | 0 | 0 | 0 | 0.68116
2031-07-05 01:00 | 30.0473 | 0.01452% | 31.3794 | 32.7707 | 34.2235 | 35.7409 | 0 | 0 | 0 | 0
2031-07-05 02:00 | 28.6021 | 0.01382% | 29.8702 | 31.1945 | 32.5775 | 34.0218 | 0 | 0 | 0 | 0
2031-07-05 03:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-07-05 04:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-07-05 05:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-07-05 06:00 | 17.4739 | 0.008445% | 18.2486 | 19.0577 | 19.9026 | 20.785 | 0 | 0 | 0 | 0
2031-07-05 07:00 | 16.4097 | 0.00793% | 17.1373 | 17.897 | 18.6905 | 19.5192 | 0 | 0 | 0 | 0
2031-07-05 08:00 | 15.6871 | 0.007581% | 16.3826 | 17.1089 | 17.8675 | 18.6596 | 0 | 0 | 0 | 0
2031-07-05 09:00 | 15.4506 | 0.007467% | 16.1356 | 16.851 | 17.5981 | 18.3783 | 0 | 0 | 0 | 0
2031-07-05 10:00 | 16.3178 | 0.007886% | 17.0412 | 17.7967 | 18.5858 | 19.4098 | 0 | 0 | 0 | 0
2031-07-05 11:00 | 18.814 | 0.009092% | 19.6482 | 20.5193 | 21.429 | 22.3791 | 0 | 0 | 0 | 0
2031-07-05 12:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-07-05 13:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-07-05 14:00 | 29.9553 | 0.01448% | 31.2834 | 32.6704 | 34.1188 | 35.6315 | 0 | 0 | 0 | 0
2031-07-05 15:00 | 31.637 | 0.01529% | 33.0397 | 34.5045 | 36.0342 | 37.6318 | 0 | 0 | 0 | 0.56864
2031-07-05 16:00 | 32.4779 | 0.0157% | 33.9178 | 35.4215 | 36.992 | 38.632 | 0 | 0 | 0 | 1.4688
2031-07-05 17:00 | 33.4107 | 0.01615% | 34.892 | 36.4389 | 38.0544 | 39.7416 | 0 | 0 | 0.94899 | 2.4674
2031-07-05 18:00 | 34.5012 | 0.01667% | 36.0308 | 37.6282 | 39.2965 | 41.0387 | 0 | 0.5654 | 2.0668 | 3.6348
2031-07-05 19:00 | 36.2223 | 0.0175% | 37.8282 | 39.5053 | 41.2568 | 43.0859 | 0.74539 | 2.2548 | 3.8311 | 5.4773
2031-07-05 20:00 | 37.6675 | 0.0182% | 39.3375 | 41.0815 | 42.9029 | 44.805 | 2.1037 | 3.6734 | 5.3126 | 7.0245
2031-07-05 21:00 | 38.7711 | 0.01874% | 40.49 | 42.2852 | 44.1599 | 46.1177 | 3.141 | 4.7567 | 6.4439 | 8.206
2031-07-05 22:00 | 38.4952 | 0.0186% | 40.2019 | 41.9843 | 43.8456 | 45.7896 | 2.8817 | 4.4858 | 6.1611 | 7.9106
2031-07-05 23:00 | 37.5887 | 0.01817% | 39.2552 | 40.9956 | 42.8131 | 44.7112 | 2.0297 | 3.596 | 5.2318 | 6.9401
2031-07-06 | 35.0924 | 0.01696% | 36.6482 | 38.273 | 39.9699 | 41.7419 | 0 | 1.1457 | 2.6729 | 4.2677
2031-07-06 01:00 | 33.8968 | 0.01638% | 35.3996 | 36.9691 | 38.6081 | 40.3198 | 0 | 0 | 1.4473 | 2.9878
2031-07-06 02:00 | 32.4253 | 0.01567% | 33.8629 | 35.3642 | 36.9321 | 38.5695 | 0 | 0 | 0 | 1.4125
2031-07-06 03:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-07-06 04:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-07-06 05:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-07-06 06:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-07-06 07:00 | 19.7994 | 0.009568% | 20.6772 | 21.594 | 22.5513 | 23.5511 | 0 | 0 | 0 | 0
2031-07-06 08:00 | 19.1162 | 0.009238% | 19.9637 | 20.8488 | 21.7732 | 22.7385 | 0 | 0 | 0 | 0
2031-07-06 09:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-07-06 10:00 | 18.8272 | 0.009099% | 19.6619 | 20.5336 | 21.444 | 22.3947 | 0 | 0 | 0 | 0
2031-07-06 11:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-07-06 12:00 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0
2031-07-06 13:00 | 33.1348 | 0.01601% | 34.6038 | 36.138 | 37.7402 | 39.4134 | 0 | 0 | 0.66616 | 2.1721
2031-07-06 14:00 | 36.6296 | 0.0177% | 38.2536 | 39.9495 | 41.7207 | 43.5704 | 1.1282 | 2.6546 | 4.2486 | 5.9134
2031-07-06 15:00 | 39.3755 | 0.01903% | 41.1212 | 42.9443 | 44.8483 | 46.8366 | 3.7091 | 5.3499 | 7.0634 | 8.853
2031-07-06 16:00 | 41.0835 | 0.01985% | 42.9049 | 44.8071 | 46.7936 | 48.8682 | 5.3144 | 7.0264 | 8.8143 | 10.6814
2031-07-06 17:00 | 42.463 | 0.02052% | 44.3456 | 46.3117 | 48.3649 | 50.5092 | 6.611 | 8.3805 | 10.2284 | 12.1582
2031-07-06 18:00 | 43.9345 | 0.02123% | 45.8823 | 47.9165 | 50.0409 | 52.2595 | 7.9941 | 9.8249 | 11.7368 | 13.7335
2031-07-06 19:00 | 45.4585 | 0.02197% | 47.4739 | 49.5787 | 51.7768 | 54.0723 | 9.4265 | 11.3208 | 13.2991 | 15.3651
2031-07-06 20:00 | 46.9037 | 0.02267% | 48.9832 | 51.1549 | 53.4229 | 55.7914 | 10.7849 | 12.7394 | 14.7806 | 16.9122
2031-07-06 21:00 | 47.7709 | 0.02309% | 49.8888 | 52.1006 | 54.4105 | 56.8228 | 11.5999 | 13.5905 | 15.6695 | 17.8405
2031-07-06 22:00 | 47.5475 | 0.02298% | 49.6555 | 51.857 | 54.1561 | 56.5571 | 11.39 | 13.3713 | 15.4405 | 17.6014
2031-07-06 23:00 | 46.4833 | 0.02246% | 48.5441 | 50.6964 | 52.944 | 55.2913 | 10.3897 | 12.3267 | 14.3496 | 16.4621
2031-07-07 | 44.5126 | 0.02151% | 46.486 | 48.547 | 50.6993 | 52.9471 | 8.5374 | 10.3923 | 12.3294 | 14.3524
2031-07-07 01:00 | 42.279 | 0.02043% | 44.1535 | 46.111 | 48.1554 | 50.2904 | 6.4381 | 8.1999 | 10.0399 | 11.9613
2031-07-07 02:00 | 39.901 | 0.01928% | 41.67 | 43.5175 | 45.4468 | 47.4617 | 4.203 | 5.8657 | 7.6022 | 9.4156
2031-07-07 03:00 | 36.0646 | 0.01743% | 37.6636 | 39.3334 | 41.0772 | 42.8984 | 0.5972 | 2.1 | 3.6695 | 5.3086
2031-07-07 04:00 | 30.9276 | 0.01495% | 32.2987 | 33.7307 | 35.2262 | 36.7879 | 0 | 0 | 0 | 0
2031-07-07 05:00 | 27.4328 | 0.01326% | 28.649 | 29.9192 | 31.2456 | 32.6309 | 0 | 0 | 0 | 0
2031-07-07 06:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-07-07 07:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-07-07 08:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-07-07 09:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-07-07 10:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-07-07 11:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-07-07 12:00 | 35.7887 | 0.0173% | 37.3754 | 39.0325 | 40.763 | 42.5702 | 0.33788 | 1.8292 | 3.3867 | 5.0132
2031-07-07 13:00 | 38.9156 | 0.01881% | 40.641 | 42.4428 | 44.3245 | 46.2896 | 3.2769 | 4.8985 | 6.5921 | 8.3607
2031-07-07 14:00 | 41.9112 | 0.02025% | 43.7693 | 45.7098 | 47.7364 | 49.8528 | 6.0924 | 7.8388 | 9.6627 | 11.5675
2031-07-07 15:00 | 43.1068 | 0.02083% | 45.0179 | 47.0138 | 49.0981 | 51.2749 | 7.2161 | 9.0124 | 10.8883 | 12.8474
2031-07-07 16:00 | 43.8819 | 0.02121% | 45.8274 | 47.8592 | 49.981 | 52.197 | 7.9447 | 9.7733 | 11.6829 | 13.6773
2031-07-07 17:00 | 43.5797 | 0.02106% | 45.5119 | 47.5296 | 49.6369 | 51.8375 | 7.6607 | 9.4767 | 11.3732 | 13.3538
2031-07-07 18:00 | 44.1578 | 0.02134% | 46.1156 | 48.1601 | 50.2953 | 52.5251 | 8.204 | 10.0441 | 11.9658 | 13.9726
2031-07-07 19:00 | 45.1301 | 0.02181% | 47.1309 | 49.2205 | 51.4027 | 53.6816 | 9.1178 | 10.9984 | 12.9624 | 15.0134
2031-07-07 20:00 | 45.3928 | 0.02194% | 47.4053 | 49.507 | 51.7019 | 53.9942 | 9.3648 | 11.2563 | 13.2318 | 15.2947
2031-07-07 21:00 | 46.1811 | 0.02232% | 48.2286 | 50.3668 | 52.5998 | 54.9318 | 10.1057 | 12.0301 | 14.0398 | 16.1387
2031-07-07 22:00 | 43.7243 | 0.02113% | 45.6628 | 47.6872 | 49.8015 | 52.0094 | 7.7965 | 9.6185 | 11.5213 | 13.5085
2031-07-07 23:00 | 40.6499 | 0.01964% | 42.4521 | 44.3342 | 46.2998 | 48.3525 | 4.9069 | 6.6008 | 8.3698 | 10.2173
2031-07-08 | 38.9813 | 0.01884% | 40.7096 | 42.5144 | 44.3993 | 46.3678 | 3.3386 | 4.963 | 6.6594 | 8.431
2031-07-08 01:00 | 37.6806 | 0.01821% | 39.3512 | 41.0959 | 42.9179 | 44.8206 | 2.1161 | 3.6863 | 5.3261 | 7.0386
2031-07-08 02:00 | 35.5391 | 0.01717% | 37.1147 | 38.7602 | 40.4787 | 42.2733 | 0.10326 | 1.5842 | 3.1308 | 4.746
2031-07-08 03:00 | 31.1509 | 0.01505% | 32.532 | 33.9743 | 35.4806 | 37.0536 | 0 | 0 | 0 | 0.048234
2031-07-08 04:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-07-08 05:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-07-08 06:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-07-08 07:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-07-08 08:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-07-08 09:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-07-08 10:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-07-08 11:00 | 26.6839 | 0.0129% | 27.8669 | 29.1024 | 30.3927 | 31.7401 | 0 | 0 | 0 | 0
2031-07-08 12:00 | 28.5495 | 0.0138% | 29.8153 | 31.1371 | 32.5176 | 33.9593 | 0 | 0 | 0 | 0
2031-07-08 13:00 | 31.1772 | 0.01507% | 32.5594 | 34.003 | 35.5105 | 37.0848 | 0 | 0 | 0 | 0.076364
2031-07-08 14:00 | 31.9129 | 0.01542% | 33.3278 | 34.8054 | 36.3485 | 37.96 | 0 | 0 | 0 | 0.86401
2031-07-08 15:00 | 32.964 | 0.01593% | 34.4255 | 35.9517 | 37.5456 | 39.2102 | 0 | 0 | 0.49108 | 1.9892
2031-07-08 16:00 | 34.0545 | 0.01646% | 35.5643 | 37.141 | 38.7877 | 40.5073 | 0 | 0.12693 | 1.6089 | 3.1566
2031-07-08 17:00 | 36.7347 | 0.01775% | 38.3633 | 40.0642 | 41.8404 | 43.6954 | 1.227 | 2.7577 | 4.3564 | 6.0259
2031-07-08 18:00 | 36.9712 | 0.01787% | 38.6103 | 40.3221 | 42.1098 | 43.9767 | 1.4493 | 2.9899 | 4.5988 | 6.2791
2031-07-08 19:00 | 39.2966 | 0.01899% | 41.0389 | 42.8583 | 44.7585 | 46.7429 | 3.635 | 5.2725 | 6.9826 | 8.7686
2031-07-08 20:00 | 39.6645 | 0.01917% | 41.4231 | 43.2596 | 45.1775 | 47.1804 | 3.9808 | 5.6336 | 7.3597 | 9.1624
2031-07-08 21:00 | 41.2805 | 0.01995% | 43.1107 | 45.022 | 47.0181 | 49.1027 | 5.4996 | 7.2198 | 9.0163 | 10.8924
2031-07-08 22:00 | 41.228 | 0.01992% | 43.0558 | 44.9647 | 46.9582 | 49.0401 | 5.4502 | 7.1682 | 8.9624 | 10.8361
2031-07-08 23:00 | 39.3098 | 0.019% | 41.0526 | 42.8727 | 44.7734 | 46.7585 | 3.6473 | 5.2854 | 6.9961 | 8.7826
2031-07-09 | 37.2734 | 0.01801% | 38.9259 | 40.6517 | 42.454 | 44.3362 | 1.7333 | 3.2865 | 4.9086 | 6.6025
2031-07-09 01:00 | 35.1318 | 0.01698% | 36.6894 | 38.316 | 40.0148 | 41.7888 | 0 | 1.1844 | 2.7133 | 4.3099
2031-07-09 02:00 | 33.4501 | 0.01617% | 34.9331 | 36.4819 | 38.0993 | 39.7885 | 0 | 0 | 0.98939 | 2.5096
2031-07-09 03:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-07-09 04:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-07-09 05:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-07-09 06:00 | 20.3512 | 0.009835% | 21.2535 | 22.1958 | 23.1798 | 24.2075 | 0 | 0 | 0 | 0
2031-07-09 07:00 | 19.1162 | 0.009238% | 19.9637 | 20.8488 | 21.7732 | 22.7385 | 0 | 0 | 0 | 0
2031-07-09 08:00 | 18.1834 | 0.008787% | 18.9896 | 19.8315 | 20.7107 | 21.6289 | 0 | 0 | 0 | 0
2031-07-09 09:00 | 18.6564 | 0.009016% | 19.4835 | 20.3473 | 21.2494 | 22.1915 | 0 | 0 | 0 | 0
2031-07-09 10:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-07-09 11:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-07-09 12:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-07-09 13:00 | 27.8926 | 0.01348% | 29.1292 | 30.4207 | 31.7694 | 33.1779 | 0 | 0 | 0 | 0
2031-07-09 14:00 | 32.018 | 0.01547% | 33.4376 | 34.92 | 36.4682 | 38.085 | 0 | 0 | 0 | 0.97653
2031-07-09 15:00 | 35.6179 | 0.01721% | 37.1971 | 38.8462 | 40.5684 | 42.3671 | 0.17735 | 1.6616 | 3.2116 | 4.8304
2031-07-09 16:00 | 36.9449 | 0.01785% | 38.5829 | 40.2934 | 42.0798 | 43.9455 | 1.4246 | 2.9641 | 4.5719 | 6.2509
2031-07-09 17:00 | 38.0485 | 0.01839% | 39.7354 | 41.4971 | 43.3369 | 45.2582 | 2.4619 | 4.0474 | 5.7032 | 7.4324
2031-07-09 18:00 | 37.3785 | 0.01806% | 39.0356 | 40.7663 | 42.5737 | 44.4612 | 1.8321 | 3.3897 | 5.0163 | 6.7151
2031-07-09 19:00 | 37.3128 | 0.01803% | 38.967 | 40.6946 | 42.4989 | 44.383 | 1.7703 | 3.3252 | 4.949 | 6.6447
2031-07-09 20:00 | 40.3609 | 0.0195% | 42.1503 | 44.019 | 45.9706 | 48.0087 | 4.6352 | 6.3171 | 8.0735 | 9.9078
2031-07-09 21:00 | 41.5696 | 0.02009% | 43.4126 | 45.3373 | 47.3473 | 49.4465 | 5.7713 | 7.5035 | 9.3126 | 11.2018
2031-07-09 22:00 | 40.847 | 0.01974% | 42.6579 | 44.5492 | 46.5243 | 48.5869 | 5.0921 | 6.7943 | 8.5718 | 10.4282
2031-07-09 23:00 | 37.4967 | 0.01812% | 39.1591 | 40.8953 | 42.7084 | 44.6018 | 1.9432 | 3.5057 | 5.1375 | 6.8417
2031-07-10 | 35.2632 | 0.01704% | 36.8266 | 38.4593 | 40.1644 | 41.9451 | 0 | 1.3134 | 2.848 | 4.4506
2031-07-10 01:00 | 34.5143 | 0.01668% | 36.0445 | 37.6425 | 39.3114 | 41.0543 | 0 | 0.57829 | 2.0803 | 3.6489
2031-07-10 02:00 | 33.056 | 0.01597% | 34.5215 | 36.052 | 37.6504 | 39.3196 | 0 | 0 | 0.58535 | 2.0877
2031-07-10 03:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-07-10 04:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-07-10 05:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-07-10 06:00 | 20.4695 | 0.009892% | 21.377 | 22.3247 | 23.3145 | 24.3482 | 0 | 0 | 0 | 0
2031-07-10 07:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-07-10 08:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-07-10 09:00 | 18.7089 | 0.009041% | 19.5384 | 20.4046 | 21.3093 | 22.254 | 0 | 0 | 0 | 0
2031-07-10 10:00 | 21.9278 | 0.0106% | 22.9 | 23.9153 | 24.9756 | 26.0829 | 0 | 0 | 0 | 0
2031-07-10 11:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-07-10 12:00 | 28.8386 | 0.01394% | 30.1171 | 31.4524 | 32.8468 | 34.3031 | 0 | 0 | 0 | 0
2031-07-10 13:00 | 32.8852 | 0.01589% | 34.3431 | 35.8657 | 37.4559 | 39.1165 | 0 | 0 | 0.41027 | 1.9048
2031-07-10 14:00 | 36.6821 | 0.01773% | 38.3084 | 40.0068 | 41.7806 | 43.6329 | 1.1776 | 2.7062 | 4.3025 | 5.9696
2031-07-10 15:00 | 37.0894 | 0.01792% | 38.7338 | 40.4511 | 42.2445 | 44.1174 | 1.5604 | 3.1059 | 4.72 | 6.4056
2031-07-10 16:00 | 38.3901 | 0.01855% | 40.0921 | 41.8696 | 43.7259 | 45.6645 | 2.7829 | 4.3827 | 6.0533 | 7.7981
2031-07-10 17:00 | 40.0587 | 0.01936% | 41.8347 | 43.6894 | 45.6264 | 47.6493 | 4.3512 | 6.0205 | 7.7638 | 9.5843
2031-07-10 18:00 | 40.6105 | 0.01963% | 42.411 | 44.2913 | 46.2549 | 48.3056 | 4.8699 | 6.5621 | 8.3294 | 10.1751
2031-07-10 19:00 | 40.8732 | 0.01975% | 42.6854 | 44.5778 | 46.5542 | 48.6182 | 5.1168 | 6.82 | 8.5988 | 10.4564
2031-07-10 20:00 | 41.228 | 0.01992% | 43.0558 | 44.9647 | 46.9582 | 49.0401 | 5.4502 | 7.1682 | 8.9624 | 10.8361
2031-07-10 21:00 | 41.9769 | 0.02029% | 43.8379 | 45.7815 | 47.8112 | 49.9309 | 6.1541 | 7.9033 | 9.7301 | 11.6378
2031-07-10 22:00 | 42.2528 | 0.02042% | 44.1261 | 46.0824 | 48.1255 | 50.2591 | 6.4134 | 8.1741 | 10.0129 | 11.9332
2031-07-10 23:00 | 41.8061 | 0.0202% | 43.6595 | 45.5952 | 47.6167 | 49.7278 | 5.9936 | 7.7357 | 9.555 | 11.455
2031-07-11 | 40.5185 | 0.01958% | 42.3149 | 44.1909 | 46.1502 | 48.1962 | 4.7834 | 6.4719 | 8.2351 | 10.0766
2031-07-11 01:00 | 38.2456 | 0.01848% | 39.9412 | 41.712 | 43.5613 | 45.4926 | 2.6471 | 4.2408 | 5.9052 | 7.6434
2031-07-11 02:00 | 36.1303 | 0.01746% | 37.7322 | 39.405 | 41.1521 | 42.9765 | 0.65895 | 2.1645 | 3.7369 | 5.3789
2031-07-11 03:00 | 32.0969 | 0.01551% | 33.5199 | 35.006 | 36.558 | 38.1788 | 0 | 0 | 0 | 1.0609
2031-07-11 04:00 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-07-11 05:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-07-11 06:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-07-11 07:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-07-11 08:00 | 19.9439 | 0.009638% | 20.8282 | 21.7516 | 22.7159 | 23.7231 | 0 | 0 | 0 | 0
2031-07-11 09:00 | 19.9571 | 0.009645% | 20.8419 | 21.7659 | 22.7309 | 23.7387 | 0 | 0 | 0 | 0
2031-07-11 10:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-07-11 11:00 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-07-11 12:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-07-11 13:00 | 32.2939 | 0.01561% | 33.7257 | 35.2209 | 36.7825 | 38.4132 | 0 | 0 | 0 | 1.2719
2031-07-11 14:00 | 36.4588 | 0.01762% | 38.0752 | 39.7633 | 41.5262 | 43.3672 | 0.96767 | 2.4869 | 4.0736 | 5.7305
2031-07-11 15:00 | 37.8777 | 0.0183% | 39.557 | 41.3108 | 43.1423 | 45.055 | 2.3013 | 3.8797 | 5.5281 | 7.2495
2031-07-11 16:00 | 39.0076 | 0.01885% | 40.737 | 42.5431 | 44.4293 | 46.399 | 3.3633 | 4.9888 | 6.6863 | 8.4591
2031-07-11 17:00 | 40.1901 | 0.01942% | 41.9719 | 43.8327 | 45.7761 | 47.8055 | 4.4747 | 6.1494 | 7.8984 | 9.725
2031-07-11 18:00 | 41.5433 | 0.02008% | 43.3851 | 45.3086 | 47.3174 | 49.4152 | 5.7466 | 7.4778 | 9.2856 | 11.1737
2031-07-11 19:00 | 42.8046 | 0.02069% | 44.7023 | 46.6842 | 48.754 | 50.9155 | 6.9321 | 8.7158 | 10.5786 | 12.5239
2031-07-11 20:00 | 44.2892 | 0.0214% | 46.2528 | 48.3034 | 50.4449 | 52.6814 | 8.3275 | 10.1731 | 12.1004 | 14.1133
2031-07-11 21:00 | 44.3943 | 0.02145% | 46.3625 | 48.418 | 50.5647 | 52.8064 | 8.4263 | 10.2762 | 12.2082 | 14.2258
2031-07-11 22:00 | 43.3958 | 0.02097% | 45.3198 | 47.329 | 49.4274 | 51.6187 | 7.4878 | 9.2961 | 11.1846 | 13.1569
2031-07-11 23:00 | 41.9243 | 0.02026% | 43.783 | 45.7242 | 47.7514 | 49.8684 | 6.1047 | 7.8517 | 9.6762 | 11.5816
2031-07-12 | 40.1244 | 0.01939% | 41.9033 | 43.7611 | 45.7012 | 47.7274 | 4.413 | 6.085 | 7.8311 | 9.6547
2031-07-12 01:00 | 38.3638 | 0.01854% | 40.0647 | 41.841 | 43.696 | 45.6333 | 2.7582 | 4.3569 | 6.0264 | 7.7699
2031-07-12 02:00 | 36.7872 | 0.01778% | 38.4182 | 40.1215 | 41.9003 | 43.7579 | 1.2764 | 2.8093 | 4.4102 | 6.0821
2031-07-12 03:00 | 33.5027 | 0.01619% | 34.988 | 36.5392 | 38.1592 | 39.851 | 0 | 0 | 1.0433 | 2.5659
2031-07-12 04:00 | 29.7977 | 0.0144% | 31.1187 | 32.4984 | 33.9392 | 35.4439 | 0 | 0 | 0 | 0
2031-07-12 05:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-07-12 06:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-07-12 07:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-07-12 08:00 | 21.3366 | 0.01031% | 22.2826 | 23.2705 | 24.3022 | 25.3796 | 0 | 0 | 0 | 0
2031-07-12 09:00 | 20.8242 | 0.01006% | 21.7474 | 22.7116 | 23.7185 | 24.7701 | 0 | 0 | 0 | 0
2031-07-12 10:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-07-12 11:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-07-12 12:00 | 28.7729 | 0.0139% | 30.0485 | 31.3807 | 32.772 | 34.225 | 0 | 0 | 0 | 0
2031-07-12 13:00 | 34.5143 | 0.01668% | 36.0445 | 37.6425 | 39.3114 | 41.0543 | 0 | 0.57829 | 2.0803 | 3.6489
2031-07-12 14:00 | 38.3901 | 0.01855% | 40.0921 | 41.8696 | 43.7259 | 45.6645 | 2.7829 | 4.3827 | 6.0533 | 7.7981
2031-07-12 15:00 | 40.7681 | 0.0197% | 42.5756 | 44.4632 | 46.4345 | 48.4932 | 5.018 | 6.7169 | 8.491 | 10.3439
2031-07-12 16:00 | 41.3068 | 0.01996% | 43.1382 | 45.0507 | 47.048 | 49.1339 | 5.5243 | 7.2456 | 9.0432 | 10.9205
2031-07-12 17:00 | 41.6353 | 0.02012% | 43.4812 | 45.4089 | 47.4221 | 49.5246 | 5.8331 | 7.568 | 9.3799 | 11.2721
2031-07-12 18:00 | 42.3447 | 0.02046% | 44.2221 | 46.1827 | 48.2302 | 50.3685 | 6.4999 | 8.2644 | 10.1072 | 12.0317
2031-07-12 19:00 | 42.6601 | 0.02062% | 44.5514 | 46.5266 | 48.5894 | 50.7436 | 6.7963 | 8.5739 | 10.4304 | 12.3692
2031-07-12 20:00 | 43.4878 | 0.02102% | 45.4158 | 47.4293 | 49.5321 | 51.7281 | 7.5742 | 9.3864 | 11.2789 | 13.2553
2031-07-12 21:00 | 44.4863 | 0.0215% | 46.4586 | 48.5183 | 50.6694 | 52.9158 | 8.5127 | 10.3665 | 12.3025 | 14.3243
2031-07-12 22:00 | 44.2366 | 0.02138% | 46.1979 | 48.2461 | 50.3851 | 52.6189 | 8.2781 | 10.1215 | 12.0466 | 14.057
2031-07-12 23:00 | 43.6717 | 0.0211% | 45.6079 | 47.6299 | 49.7416 | 51.9469 | 7.7471 | 9.5669 | 11.4675 | 13.4522
2031-07-13 | 41.044 | 0.01984% | 42.8637 | 44.7641 | 46.7487 | 48.8214 | 5.2774 | 6.9877 | 8.7739 | 10.6392
2031-07-13 01:00 | 39.2704 | 0.01898% | 41.0114 | 42.8297 | 44.7285 | 46.7116 | 3.6103 | 5.2467 | 6.9557 | 8.7404
2031-07-13 02:00 | 37.8514 | 0.01829% | 39.5296 | 41.2821 | 43.1124 | 45.0238 | 2.2766 | 3.8539 | 5.5012 | 7.2214
2031-07-13 03:00 | 35.2106 | 0.01702% | 36.7717 | 38.402 | 40.1046 | 41.8826 | 0 | 1.2618 | 2.7941 | 4.3943
2031-07-13 04:00 | 31.8341 | 0.01538% | 33.2455 | 34.7194 | 36.2587 | 37.8662 | 0 | 0 | 0 | 0.77962
2031-07-13 05:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-07-13 06:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-07-13 07:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-07-13 08:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-07-13 09:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-07-13 10:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-07-13 11:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-07-13 12:00 | 30.5203 | 0.01475% | 31.8734 | 33.2865 | 34.7623 | 36.3035 | 0 | 0 | 0 | 0
2031-07-13 13:00 | 36.7347 | 0.01775% | 38.3633 | 40.0642 | 41.8404 | 43.6954 | 1.227 | 2.7577 | 4.3564 | 6.0259
2031-07-13 14:00 | 38.5215 | 0.01862% | 40.2293 | 42.0129 | 43.8756 | 45.8208 | 2.9064 | 4.5116 | 6.188 | 7.9387
2031-07-13 15:00 | 36.1829 | 0.01749% | 37.787 | 39.4623 | 41.2119 | 43.0391 | 0.70834 | 2.2161 | 3.7907 | 5.4351
2031-07-13 16:00 | 36.3274 | 0.01756% | 37.938 | 39.62 | 41.3765 | 43.211 | 0.84418 | 2.358 | 3.9389 | 5.5899
2031-07-13 17:00 | 39.0864 | 0.01889% | 40.8193 | 42.6291 | 44.519 | 46.4928 | 3.4374 | 5.0662 | 6.7671 | 8.5435
2031-07-13 18:00 | 40.9652 | 0.0198% | 42.7814 | 44.6781 | 46.659 | 48.7276 | 5.2033 | 6.9103 | 8.6931 | 10.5548
2031-07-13 19:00 | 43.0805 | 0.02082% | 44.9905 | 46.9851 | 49.0682 | 51.2437 | 7.1914 | 8.9866 | 10.8614 | 12.8193
2031-07-13 20:00 | 45.5899 | 0.02203% | 47.6111 | 49.722 | 51.9264 | 54.2286 | 9.55 | 11.4498 | 13.4338 | 15.5057
2031-07-13 21:00 | 46.2994 | 0.02237% | 48.3521 | 50.4958 | 52.7345 | 55.0725 | 10.2168 | 12.1462 | 14.161 | 16.2652
2031-07-13 22:00 | 45.5505 | 0.02201% | 47.57 | 49.679 | 51.8815 | 54.1817 | 9.513 | 11.4111 | 13.3934 | 15.4635
2031-07-13 23:00 | 45.5768 | 0.02203% | 47.5974 | 49.7077 | 51.9115 | 54.213 | 9.5377 | 11.4369 | 13.4203 | 15.4917
2031-07-14 | 43.1856 | 0.02087% | 45.1002 | 47.0998 | 49.1879 | 51.3687 | 7.2902 | 9.0898 | 10.9691 | 12.9318
2031-07-14 01:00 | 40.8995 | 0.01977% | 42.7128 | 44.6065 | 46.5841 | 48.6494 | 5.1415 | 6.8458 | 8.6257 | 10.4845
2031-07-14 02:00 | 37.6281 | 0.01818% | 39.2963 | 41.0385 | 42.858 | 44.7581 | 2.0667 | 3.6347 | 5.2722 | 6.9823
2031-07-14 03:00 | 33.1611 | 0.01603% | 34.6313 | 36.1667 | 37.7701 | 39.4447 | 0 | 0 | 0.6931 | 2.2002
2031-07-14 04:00 | 28.8254 | 0.01393% | 30.1034 | 31.438 | 32.8319 | 34.2875 | 0 | 0 | 0 | 0
2031-07-14 05:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-07-14 06:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-07-14 07:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-07-14 08:00 | 20.1279 | 0.009727% | 21.0202 | 21.9522 | 22.9254 | 23.9418 | 0 | 0 | 0 | 0
2031-07-14 09:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-07-14 10:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-07-14 11:00 | 25.7379 | 0.01244% | 26.879 | 28.0707 | 29.3152 | 30.6149 | 0 | 0 | 0 | 0
2031-07-14 12:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-07-14 13:00 | 31.1903 | 0.01507% | 32.5731 | 34.0173 | 35.5254 | 37.1005 | 0 | 0 | 0 | 0.090429
2031-07-14 14:00 | 34.2121 | 0.01653% | 35.7289 | 37.313 | 38.9673 | 40.6949 | 0 | 0.28168 | 1.7705 | 3.3254
2031-07-14 15:00 | 35.4603 | 0.01714% | 37.0324 | 38.6742 | 40.3889 | 42.1795 | 0.029164 | 1.5068 | 3.05 | 4.6616
2031-07-14 16:00 | 37.9434 | 0.01834% | 39.6256 | 41.3824 | 43.2171 | 45.1332 | 2.3631 | 3.9442 | 5.5954 | 7.3199
2031-07-14 17:00 | 39.3886 | 0.01904% | 41.1349 | 42.9586 | 44.8632 | 46.8522 | 3.7214 | 5.3628 | 7.0769 | 8.867
2031-07-14 18:00 | 40.8864 | 0.01976% | 42.6991 | 44.5922 | 46.5692 | 48.6338 | 5.1292 | 6.8329 | 8.6122 | 10.4704
2031-07-14 19:00 | 42.1739 | 0.02038% | 44.0437 | 45.9964 | 48.0357 | 50.1653 | 6.3394 | 8.0968 | 9.9321 | 11.8488
2031-07-14 20:00 | 43.7505 | 0.02114% | 45.6902 | 47.7159 | 49.8314 | 52.0407 | 7.8212 | 9.6443 | 11.5483 | 13.5366
2031-07-14 21:00 | 44.8147 | 0.02166% | 46.8016 | 48.8766 | 51.0435 | 53.3065 | 8.8214 | 10.6889 | 12.6392 | 14.6759
2031-07-14 22:00 | 44.749 | 0.02163% | 46.733 | 48.8049 | 50.9687 | 53.2284 | 8.7597 | 10.6244 | 12.5718 | 14.6056
2031-07-14 23:00 | 42.5418 | 0.02056% | 44.4279 | 46.3976 | 48.4547 | 50.6029 | 6.6851 | 8.4579 | 10.3092 | 12.2426
2031-07-15 | 40.7813 | 0.01971% | 42.5893 | 44.4775 | 46.4494 | 48.5088 | 5.0304 | 6.7298 | 8.5045 | 10.3579
2031-07-15 01:00 | 38.3244 | 0.01852% | 40.0235 | 41.798 | 43.6511 | 45.5864 | 2.7212 | 4.3182 | 5.986 | 7.7278
2031-07-15 02:00 | 35.9727 | 0.01738% | 37.5675 | 39.2331 | 40.9725 | 42.789 | 0.51076 | 2.0098 | 3.5752 | 5.2101
2031-07-15 03:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-07-15 04:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-07-15 05:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-07-15 06:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-07-15 07:00 | 20.1936 | 0.009759% | 21.0888 | 22.0238 | 23.0003 | 24.02 | 0 | 0 | 0 | 0
2031-07-15 08:00 | 19.0374 | 0.0092% | 19.8814 | 20.7629 | 21.6834 | 22.6447 | 0 | 0 | 0 | 0
2031-07-15 09:00 | 18.8666 | 0.009118% | 19.7031 | 20.5766 | 21.4889 | 22.4416 | 0 | 0 | 0 | 0
2031-07-15 10:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-07-15 11:00 | 26.5262 | 0.01282% | 27.7023 | 28.9305 | 30.2131 | 31.5526 | 0 | 0 | 0 | 0
2031-07-15 12:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-07-15 13:00 | 34.199 | 0.01653% | 35.7152 | 37.2986 | 38.9523 | 40.6793 | 0 | 0.26878 | 1.7571 | 3.3113
2031-07-15 14:00 | 37.5624 | 0.01815% | 39.2277 | 40.9669 | 42.7832 | 44.68 | 2.005 | 3.5702 | 5.2049 | 6.912
2031-07-15 15:00 | 39.2178 | 0.01895% | 40.9565 | 42.7724 | 44.6687 | 46.6491 | 3.5609 | 5.1951 | 6.9018 | 8.6842
2031-07-15 16:00 | 40.6105 | 0.01963% | 42.411 | 44.2913 | 46.2549 | 48.3056 | 4.8699 | 6.5621 | 8.3294 | 10.1751
2031-07-15 17:00 | 41.6353 | 0.02012% | 43.4812 | 45.4089 | 47.4221 | 49.5246 | 5.8331 | 7.568 | 9.3799 | 11.2721
2031-07-15 18:00 | 42.9754 | 0.02077% | 44.8807 | 46.8705 | 48.9485 | 51.1186 | 7.0926 | 8.8834 | 10.7537 | 12.7068
2031-07-15 19:00 | 44.4337 | 0.02147% | 46.4037 | 48.461 | 50.6095 | 52.8533 | 8.4633 | 10.3149 | 12.2486 | 14.268
2031-07-15 20:00 | 46.549 | 0.0225% | 48.6127 | 50.768 | 53.0188 | 55.3694 | 10.4515 | 12.3912 | 14.4169 | 16.5325
2031-07-15 21:00 | 46.3256 | 0.02239% | 48.3795 | 50.5244 | 52.7644 | 55.1037 | 10.2415 | 12.172 | 14.188 | 16.2934
2031-07-15 22:00 | 46.1154 | 0.02229% | 48.16 | 50.2951 | 52.525 | 54.8537 | 10.044 | 11.9656 | 13.9725 | 16.0683
2031-07-15 23:00 | 44.6177 | 0.02156% | 46.5958 | 48.6616 | 50.8191 | 53.0721 | 8.6362 | 10.4955 | 12.4371 | 14.4649
2031-07-16 | 42.9097 | 0.02074% | 44.8121 | 46.7988 | 48.8737 | 51.0405 | 7.0309 | 8.819 | 10.6863 | 12.6365
2031-07-16 01:00 | 41.0703 | 0.01985% | 42.8912 | 44.7928 | 46.7787 | 48.8526 | 5.3021 | 7.0135 | 8.8008 | 10.6673
2031-07-16 02:00 | 38.2719 | 0.0185% | 39.9687 | 41.7407 | 43.5913 | 45.5239 | 2.6718 | 4.2666 | 5.9321 | 7.6715
2031-07-16 03:00 | 33.8443 | 0.01636% | 35.3447 | 36.9118 | 38.5483 | 40.2573 | 0 | 0 | 1.3934 | 2.9316
2031-07-16 04:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-07-16 05:00 | 26.2897 | 0.0127% | 27.4553 | 28.6725 | 29.9437 | 31.2713 | 0 | 0 | 0 | 0
2031-07-16 06:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-07-16 07:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-07-16 08:00 | 20.4301 | 0.009873% | 21.3358 | 22.2818 | 23.2696 | 24.3013 | 0 | 0 | 0 | 0
2031-07-16 09:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-07-16 10:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-07-16 11:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-07-16 12:00 | 32.3728 | 0.01564% | 33.808 | 35.3069 | 36.8722 | 38.507 | 0 | 0 | 0 | 1.3563
2031-07-16 13:00 | 36.2354 | 0.01751% | 37.8419 | 39.5197 | 41.2718 | 43.1016 | 0.75774 | 2.2677 | 3.8446 | 5.4914
2031-07-16 14:00 | 39.7565 | 0.01921% | 41.5191 | 43.3599 | 45.2822 | 47.2898 | 4.0672 | 5.7239 | 7.454 | 9.2608
2031-07-16 15:00 | 41.8192 | 0.02021% | 43.6733 | 45.6095 | 47.6316 | 49.7434 | 6.0059 | 7.7486 | 9.5685 | 11.4691
2031-07-16 16:00 | 43.0279 | 0.02079% | 44.9356 | 46.9278 | 49.0084 | 51.1812 | 7.142 | 8.935 | 10.8075 | 12.763
2031-07-16 17:00 | 43.3564 | 0.02095% | 45.2786 | 47.286 | 49.3825 | 51.5719 | 7.4507 | 9.2574 | 11.1442 | 13.1147
2031-07-16 18:00 | 44.5914 | 0.02155% | 46.5684 | 48.633 | 50.7891 | 53.0409 | 8.6115 | 10.4697 | 12.4102 | 14.4368
2031-07-16 19:00 | 46.457 | 0.02245% | 48.5167 | 50.6677 | 52.9141 | 55.26 | 10.365 | 12.3009 | 14.3227 | 16.434
2031-07-16 20:00 | 47.7446 | 0.02307% | 49.8613 | 52.072 | 54.3806 | 56.7915 | 11.5752 | 13.5648 | 15.6425 | 17.8124
2031-07-16 21:00 | 47.3767 | 0.0229% | 49.4772 | 51.6707 | 53.9616 | 56.354 | 11.2294 | 13.2037 | 15.2654 | 17.4186
2031-07-16 22:00 | 47.2322 | 0.02283% | 49.3262 | 51.5131 | 53.797 | 56.1821 | 11.0936 | 13.0618 | 15.1173 | 17.2639
2031-07-16 23:00 | 45.6556 | 0.02206% | 47.6797 | 49.7936 | 52.0012 | 54.3067 | 9.6118 | 11.5143 | 13.5011 | 15.576
2031-07-17 | 44.3155 | 0.02142% | 46.2802 | 48.3321 | 50.4749 | 52.7127 | 8.3522 | 10.1989 | 12.1274 | 14.1414
2031-07-17 01:00 | 43.3564 | 0.02095% | 45.2786 | 47.286 | 49.3825 | 51.5719 | 7.4507 | 9.2574 | 11.1442 | 13.1147
2031-07-17 02:00 | 41.7272 | 0.02017% | 43.5772 | 45.5092 | 47.5269 | 49.634 | 5.9195 | 7.6583 | 9.4742 | 11.3706
2031-07-17 03:00 | 37.6018 | 0.01817% | 39.2689 | 41.0099 | 42.8281 | 44.7269 | 2.042 | 3.6089 | 5.2453 | 6.9542
2031-07-17 04:00 | 33.6997 | 0.01629% | 35.1938 | 36.7541 | 38.3836 | 40.0854 | 0 | 0 | 1.2453 | 2.7769
2031-07-17 05:00 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-07-17 06:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-07-17 07:00 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-07-17 08:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-07-17 09:00 | 25.7511 | 0.01244% | 26.8927 | 28.085 | 29.3302 | 30.6306 | 0 | 0 | 0 | 0
2031-07-17 10:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-07-17 11:00 | 31.348 | 0.01515% | 32.7378 | 34.1892 | 35.705 | 37.288 | 0 | 0 | 0 | 0.25921
2031-07-17 12:00 | 33.3319 | 0.01611% | 34.8096 | 36.3529 | 37.9646 | 39.6478 | 0 | 0 | 0.86818 | 2.383
2031-07-17 13:00 | 38.8894 | 0.01879% | 40.6135 | 42.4141 | 44.2946 | 46.2584 | 3.2522 | 4.8727 | 6.5651 | 8.3325
2031-07-17 14:00 | 41.044 | 0.01984% | 42.8637 | 44.7641 | 46.7487 | 48.8214 | 5.2774 | 6.9877 | 8.7739 | 10.6392
2031-07-17 15:00 | 41.8061 | 0.0202% | 43.6595 | 45.5952 | 47.6167 | 49.7278 | 5.9936 | 7.7357 | 9.555 | 11.455
2031-07-17 16:00 | 42.3973 | 0.02049% | 44.277 | 46.24 | 48.2901 | 50.431 | 6.5493 | 8.316 | 10.1611 | 12.0879
2031-07-17 17:00 | 41.8718 | 0.02024% | 43.7281 | 45.6668 | 47.6915 | 49.8059 | 6.0553 | 7.8002 | 9.6223 | 11.5253
2031-07-17 18:00 | 41.3988 | 0.02001% | 43.2342 | 45.151 | 47.1528 | 49.2433 | 5.6108 | 7.3359 | 9.1375 | 11.019
2031-07-17 19:00 | 41.2937 | 0.01996% | 43.1244 | 45.0364 | 47.0331 | 49.1183 | 5.512 | 7.2327 | 9.0298 | 10.9065
2031-07-17 20:00 | 41.701 | 0.02015% | 43.5498 | 45.4806 | 47.497 | 49.6027 | 5.8948 | 7.6325 | 9.4473 | 11.3425
2031-07-17 21:00 | 40.8076 | 0.01972% | 42.6168 | 44.5062 | 46.4794 | 48.5401 | 5.0551 | 6.7556 | 8.5314 | 10.386
2031-07-17 22:00 | 38.574 | 0.01864% | 40.2842 | 42.0702 | 43.9354 | 45.8833 | 2.9558 | 4.5632 | 6.2419 | 7.995
2031-07-17 23:00 | 35.2238 | 0.01702% | 36.7854 | 38.4163 | 40.1195 | 41.8982 | 0 | 1.2747 | 2.8076 | 4.4084
2031-07-18 | 32.7669 | 0.01584% | 34.2196 | 35.7368 | 37.3212 | 38.9758 | 0 | 0 | 0.28906 | 1.7782
2031-07-18 01:00 | 31.4794 | 0.01521% | 32.875 | 34.3325 | 35.8547 | 37.4443 | 0 | 0 | 0 | 0.39986
2031-07-18 02:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-07-18 03:00 | 25.5671 | 0.01236% | 26.7007 | 27.8844 | 29.1207 | 30.4118 | 0 | 0 | 0 | 0
2031-07-18 04:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-07-18 05:00 | 19.9571 | 0.009645% | 20.8419 | 21.7659 | 22.7309 | 23.7387 | 0 | 0 | 0 | 0
2031-07-18 06:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-07-18 07:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-07-18 08:00 | 16.1207 | 0.007791% | 16.8354 | 17.5818 | 18.3613 | 19.1754 | 0 | 0 | 0 | 0
2031-07-18 09:00 | 16.2258 | 0.007841% | 16.9452 | 17.6964 | 18.481 | 19.3004 | 0 | 0 | 0 | 0
2031-07-18 10:00 | 18.2885 | 0.008838% | 19.0993 | 19.9461 | 20.8304 | 21.7539 | 0 | 0 | 0 | 0
2031-07-18 11:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-07-18 12:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-07-18 13:00 | 26.1715 | 0.01265% | 27.3318 | 28.5436 | 29.8091 | 31.1306 | 0 | 0 | 0 | 0
2031-07-18 14:00 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-07-18 15:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-07-18 16:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-07-18 17:00 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-07-18 18:00 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-07-18 19:00 | 30.9144 | 0.01494% | 32.285 | 33.7164 | 35.2112 | 36.7723 | 0 | 0 | 0 | 0
2031-07-18 20:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-07-18 21:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-07-18 22:00 | 31.8604 | 0.0154% | 33.2729 | 34.7481 | 36.2886 | 37.8975 | 0 | 0 | 0 | 0.80775
2031-07-18 23:00 | 30.5071 | 0.01474% | 31.8597 | 33.2722 | 34.7473 | 36.2878 | 0 | 0 | 0 | 0
2031-07-19 | 29.0751 | 0.01405% | 30.3641 | 31.7103 | 33.1162 | 34.5844 | 0 | 0 | 0 | 0
2031-07-19 01:00 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-07-19 02:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-07-19 03:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-07-19 04:00 | 20.5614 | 0.009937% | 21.473 | 22.425 | 23.4193 | 24.4576 | 0 | 0 | 0 | 0
2031-07-19 05:00 | 18.4593 | 0.008921% | 19.2777 | 20.1324 | 21.025 | 21.9571 | 0 | 0 | 0 | 0
2031-07-19 06:00 | 17.0141 | 0.008222% | 17.7684 | 18.5562 | 19.3789 | 20.238 | 0 | 0 | 0 | 0
2031-07-19 07:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-07-19 08:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-07-19 09:00 | 15.3193 | 0.007403% | 15.9984 | 16.7077 | 17.4485 | 18.2221 | 0 | 0 | 0 | 0
2031-07-19 10:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-07-19 11:00 | 18.3805 | 0.008883% | 19.1954 | 20.0464 | 20.9352 | 21.8633 | 0 | 0 | 0 | 0
2031-07-19 12:00 | 21.7176 | 0.0105% | 22.6805 | 23.686 | 24.7361 | 25.8328 | 0 | 0 | 0 | 0
2031-07-19 13:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-07-19 14:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-07-19 15:00 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-07-19 16:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-07-19 17:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-07-19 18:00 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-07-19 19:00 | 31.256 | 0.0151% | 32.6418 | 34.0889 | 35.6003 | 37.1786 | 0 | 0 | 0 | 0.16075
2031-07-19 20:00 | 32.6487 | 0.01578% | 34.0962 | 35.6078 | 37.1865 | 38.8352 | 0 | 0 | 0.16785 | 1.6516
2031-07-19 21:00 | 32.872 | 0.01589% | 34.3294 | 35.8514 | 37.4409 | 39.1008 | 0 | 0 | 0.3968 | 1.8908
2031-07-19 22:00 | 31.9129 | 0.01542% | 33.3278 | 34.8054 | 36.3485 | 37.96 | 0 | 0 | 0 | 0.86401
2031-07-19 23:00 | 30.5728 | 0.01477% | 31.9283 | 33.3438 | 34.8221 | 36.366 | 0 | 0 | 0 | 0
2031-07-20 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-07-20 01:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-07-20 02:00 | 27.5773 | 0.01333% | 28.7999 | 30.0768 | 31.4102 | 32.8028 | 0 | 0 | 0 | 0
2031-07-20 03:00 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-07-20 04:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-07-20 05:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-07-20 06:00 | 19.2213 | 0.009289% | 20.0735 | 20.9635 | 21.8929 | 22.8635 | 0 | 0 | 0 | 0
2031-07-20 07:00 | 18.1046 | 0.008749% | 18.9072 | 19.7455 | 20.6209 | 21.5352 | 0 | 0 | 0 | 0
2031-07-20 08:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-07-20 09:00 | 17.1455 | 0.008286% | 17.9056 | 18.6995 | 19.5285 | 20.3943 | 0 | 0 | 0 | 0
2031-07-20 10:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-07-20 11:00 | 19.0374 | 0.0092% | 19.8814 | 20.7629 | 21.6834 | 22.6447 | 0 | 0 | 0 | 0
2031-07-20 12:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-07-20 13:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-07-20 14:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-07-20 15:00 | 31.6896 | 0.01531% | 33.0945 | 34.5618 | 36.0941 | 37.6943 | 0 | 0 | 0 | 0.6249
2031-07-20 16:00 | 33.6735 | 0.01627% | 35.1664 | 36.7255 | 38.3537 | 40.0541 | 0 | 0 | 1.2183 | 2.7487
2031-07-20 17:00 | 35.4734 | 0.01714% | 37.0461 | 38.6886 | 40.4038 | 42.1952 | 0.041512 | 1.5197 | 3.0635 | 4.6756
2031-07-20 18:00 | 37.1026 | 0.01793% | 38.7475 | 40.4654 | 42.2594 | 44.133 | 1.5728 | 3.1188 | 4.7335 | 6.4197
2031-07-20 19:00 | 38.0879 | 0.01841% | 39.7766 | 41.5401 | 43.3818 | 45.3051 | 2.4989 | 4.0861 | 5.7436 | 7.4746
2031-07-20 20:00 | 40.1375 | 0.0194% | 41.917 | 43.7754 | 45.7162 | 47.743 | 4.4253 | 6.0979 | 7.8446 | 9.6687
2031-07-20 21:00 | 41.4907 | 0.02005% | 43.3302 | 45.2513 | 47.2575 | 49.3527 | 5.6972 | 7.4262 | 9.2318 | 11.1174
2031-07-20 22:00 | 41.4776 | 0.02004% | 43.3165 | 45.237 | 47.2426 | 49.3371 | 5.6849 | 7.4133 | 9.2183 | 11.1034
2031-07-20 23:00 | 40.0849 | 0.01937% | 41.8621 | 43.7181 | 45.6563 | 47.6805 | 4.3759 | 6.0463 | 7.7907 | 9.6125
2031-07-21 | 37.8514 | 0.01829% | 39.5296 | 41.2821 | 43.1124 | 45.0238 | 2.2766 | 3.8539 | 5.5012 | 7.2214
2031-07-21 01:00 | 34.7377 | 0.01679% | 36.2778 | 37.8861 | 39.5658 | 41.32 | 0 | 0.79753 | 2.3092 | 3.888
2031-07-21 02:00 | 32.2677 | 0.01559% | 33.6983 | 35.1923 | 36.7525 | 38.382 | 0 | 0 | 0 | 1.2438
2031-07-21 03:00 | 27.7612 | 0.01342% | 28.992 | 30.2774 | 31.6197 | 33.0216 | 0 | 0 | 0 | 0
2031-07-21 04:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-07-21 05:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-07-21 06:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-07-21 07:00 | 18.1703 | 0.008781% | 18.9758 | 19.8171 | 20.6957 | 21.6133 | 0 | 0 | 0 | 0
2031-07-21 08:00 | 17.3294 | 0.008375% | 18.0977 | 18.9001 | 19.738 | 20.6131 | 0 | 0 | 0 | 0
2031-07-21 09:00 | 17.3163 | 0.008368% | 18.084 | 18.8858 | 19.7231 | 20.5975 | 0 | 0 | 0 | 0
2031-07-21 10:00 | 19.4315 | 0.009391% | 20.293 | 21.1927 | 22.1323 | 23.1136 | 0 | 0 | 0 | 0
2031-07-21 11:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-07-21 12:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-07-21 13:00 | 28.1948 | 0.01363% | 29.4448 | 30.7503 | 32.1136 | 33.5373 | 0 | 0 | 0 | 0
2031-07-21 14:00 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-07-21 15:00 | 30.4152 | 0.0147% | 31.7636 | 33.1719 | 34.6426 | 36.1784 | 0 | 0 | 0 | 0
2031-07-21 16:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-07-21 17:00 | 31.0064 | 0.01498% | 32.3811 | 33.8167 | 35.3159 | 36.8817 | 0 | 0 | 0 | 0
2031-07-21 18:00 | 31.5582 | 0.01525% | 32.9573 | 34.4185 | 35.9445 | 37.5381 | 0 | 0 | 0 | 0.48425
2031-07-21 19:00 | 32.7144 | 0.01581% | 34.1648 | 35.6795 | 37.2613 | 38.9133 | 0 | 0 | 0.23519 | 1.722
2031-07-21 20:00 | 34.6457 | 0.01674% | 36.1817 | 37.7858 | 39.4611 | 41.2106 | 0 | 0.70726 | 2.215 | 3.7895
2031-07-21 21:00 | 35.9332 | 0.01737% | 37.5264 | 39.1901 | 40.9276 | 42.7421 | 0.47372 | 1.9711 | 3.5348 | 5.1679
2031-07-21 22:00 | 36.1435 | 0.01747% | 37.7459 | 39.4194 | 41.167 | 42.9922 | 0.6713 | 2.1774 | 3.7503 | 5.393
2031-07-21 23:00 | 34.4092 | 0.01663% | 35.9347 | 37.5279 | 39.1917 | 40.9293 | 0 | 0.47512 | 1.9726 | 3.5364
2031-07-22 | 32.0837 | 0.0155% | 33.5062 | 34.9917 | 36.543 | 38.1632 | 0 | 0 | 0 | 1.0469
2031-07-22 01:00 | 30.2706 | 0.01463% | 31.6127 | 33.0142 | 34.4779 | 36.0065 | 0 | 0 | 0 | 0
2031-07-22 02:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-07-22 03:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-07-22 04:00 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-07-22 05:00 | 19.1031 | 0.009232% | 19.95 | 20.8345 | 21.7582 | 22.7229 | 0 | 0 | 0 | 0
2031-07-22 06:00 | 17.4214 | 0.008419% | 18.1938 | 19.0004 | 19.8428 | 20.7225 | 0 | 0 | 0 | 0
2031-07-22 07:00 | 16.3703 | 0.007911% | 17.0961 | 17.8541 | 18.6456 | 19.4723 | 0 | 0 | 0 | 0
2031-07-22 08:00 | 15.7134 | 0.007594% | 16.4101 | 17.1376 | 17.8974 | 18.6909 | 0 | 0 | 0 | 0
2031-07-22 09:00 | 16.0944 | 0.007778% | 16.808 | 17.5531 | 18.3314 | 19.1441 | 0 | 0 | 0 | 0
2031-07-22 10:00 | 18.1177 | 0.008756% | 18.921 | 19.7598 | 20.6359 | 21.5508 | 0 | 0 | 0 | 0
2031-07-22 11:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-07-22 12:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-07-22 13:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-07-22 14:00 | 27.7612 | 0.01342% | 28.992 | 30.2774 | 31.6197 | 33.0216 | 0 | 0 | 0 | 0
2031-07-22 15:00 | 28.3919 | 0.01372% | 29.6506 | 30.9652 | 32.338 | 33.7717 | 0 | 0 | 0 | 0
2031-07-22 16:00 | 29.3772 | 0.0142% | 30.6797 | 32.0399 | 33.4604 | 34.9438 | 0 | 0 | 0 | 0
2031-07-22 17:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-07-22 18:00 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-07-22 19:00 | 32.5304 | 0.01572% | 33.9727 | 35.4789 | 37.0518 | 38.6945 | 0 | 0 | 0.046635 | 1.5251
2031-07-22 20:00 | 34.3435 | 0.0166% | 35.8661 | 37.4563 | 39.1169 | 40.8512 | 0 | 0.41064 | 1.9052 | 3.466
2031-07-22 21:00 | 35.4865 | 0.01715% | 37.0598 | 38.7029 | 40.4188 | 42.2108 | 0.053861 | 1.5326 | 3.0769 | 4.6897
2031-07-22 22:00 | 35.434 | 0.01712% | 37.005 | 38.6456 | 40.3589 | 42.1483 | 0.0044663 | 1.481 | 3.0231 | 4.6334
2031-07-22 23:00 | 33.9362 | 0.0164% | 35.4408 | 37.0121 | 38.653 | 40.3667 | 0 | 0.010861 | 1.4877 | 3.03
2031-07-23 | 31.9918 | 0.01546% | 33.4101 | 34.8914 | 36.4383 | 38.0538 | 0 | 0 | 0 | 0.9484
2031-07-23 01:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-07-23 02:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-07-23 03:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-07-23 04:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-07-23 05:00 | 18.9454 | 0.009156% | 19.7854 | 20.6626 | 21.5786 | 22.5353 | 0 | 0 | 0 | 0
2031-07-23 06:00 | 17.2769 | 0.008349% | 18.0428 | 18.8428 | 19.6782 | 20.5506 | 0 | 0 | 0 | 0
2031-07-23 07:00 | 16.2127 | 0.007835% | 16.9315 | 17.6821 | 18.4661 | 19.2847 | 0 | 0 | 0 | 0
2031-07-23 08:00 | 15.8711 | 0.00767% | 16.5747 | 17.3096 | 18.077 | 18.8784 | 0 | 0 | 0 | 0
2031-07-23 09:00 | 16.2127 | 0.007835% | 16.9315 | 17.6821 | 18.4661 | 19.2847 | 0 | 0 | 0 | 0
2031-07-23 10:00 | 18.433 | 0.008908% | 19.2503 | 20.1037 | 20.995 | 21.9259 | 0 | 0 | 0 | 0
2031-07-23 11:00 | 21.7964 | 0.01053% | 22.7628 | 23.772 | 24.8259 | 25.9266 | 0 | 0 | 0 | 0
2031-07-23 12:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-07-23 13:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-07-23 14:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-07-23 15:00 | 30.5334 | 0.01476% | 31.8871 | 33.3008 | 34.7772 | 36.3191 | 0 | 0 | 0 | 0
2031-07-23 16:00 | 31.7421 | 0.01534% | 33.1494 | 34.6191 | 36.154 | 37.7568 | 0 | 0 | 0 | 0.68116
2031-07-23 17:00 | 33.0691 | 0.01598% | 34.5352 | 36.0663 | 37.6654 | 39.3353 | 0 | 0 | 0.59882 | 2.1017
2031-07-23 18:00 | 33.726 | 0.0163% | 35.2213 | 36.7828 | 38.4136 | 40.1166 | 0 | 0 | 1.2722 | 2.805
2031-07-23 19:00 | 35.5522 | 0.01718% | 37.1284 | 38.7745 | 40.4936 | 42.2889 | 0.1156 | 1.5971 | 3.1443 | 4.76
2031-07-23 20:00 | 38.0748 | 0.0184% | 39.7628 | 41.5257 | 43.3668 | 45.2895 | 2.4866 | 4.0732 | 5.7301 | 7.4605
2031-07-23 21:00 | 39.2441 | 0.01897% | 40.984 | 42.801 | 44.6986 | 46.6803 | 3.5856 | 5.2209 | 6.9288 | 8.7123
2031-07-23 22:00 | 39.2441 | 0.01897% | 40.984 | 42.801 | 44.6986 | 46.6803 | 3.5856 | 5.2209 | 6.9288 | 8.7123
2031-07-23 23:00 | 36.7872 | 0.01778% | 38.4182 | 40.1215 | 41.9003 | 43.7579 | 1.2764 | 2.8093 | 4.4102 | 6.0821
2031-07-24 | 35.0004 | 0.01691% | 36.5522 | 38.1727 | 39.8651 | 41.6325 | 0 | 1.0555 | 2.5786 | 4.1693
2031-07-24 01:00 | 33.8048 | 0.01634% | 35.3036 | 36.8688 | 38.5034 | 40.2104 | 0 | 0 | 1.353 | 2.8894
2031-07-24 02:00 | 31.1378 | 0.01505% | 32.5183 | 33.96 | 35.4656 | 37.038 | 0 | 0 | 0 | 0.034169
2031-07-24 03:00 | 27.2357 | 0.01316% | 28.4432 | 29.7042 | 31.0212 | 32.3965 | 0 | 0 | 0 | 0
2031-07-24 04:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-07-24 05:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-07-24 06:00 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-07-24 07:00 | 17.4739 | 0.008445% | 18.2486 | 19.0577 | 19.9026 | 20.785 | 0 | 0 | 0 | 0
2031-07-24 08:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-07-24 09:00 | 17.1586 | 0.008292% | 17.9193 | 18.7138 | 19.5435 | 20.41 | 0 | 0 | 0 | 0
2031-07-24 10:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-07-24 11:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-07-24 12:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-07-24 13:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-07-24 14:00 | 34.9741 | 0.0169% | 36.5247 | 38.1441 | 39.8352 | 41.6013 | 0 | 1.0297 | 2.5517 | 4.1412
2031-07-24 15:00 | 36.8661 | 0.01782% | 38.5005 | 40.2075 | 41.9901 | 43.8517 | 1.3505 | 2.8867 | 4.4911 | 6.1665
2031-07-24 16:00 | 39.4018 | 0.01904% | 41.1486 | 42.973 | 44.8782 | 46.8679 | 3.7338 | 5.3757 | 7.0904 | 8.8811
2031-07-24 17:00 | 41.3725 | 0.01999% | 43.2068 | 45.1223 | 47.1228 | 49.212 | 5.5861 | 7.3101 | 9.1106 | 10.9908
2031-07-24 18:00 | 43.3695 | 0.02096% | 45.2923 | 47.3004 | 49.3974 | 51.5875 | 7.4631 | 9.2703 | 11.1577 | 13.1287
2031-07-24 19:00 | 44.6702 | 0.02159% | 46.6507 | 48.7189 | 50.8789 | 53.1346 | 8.6856 | 10.547 | 12.491 | 14.5212
2031-07-24 20:00 | 46.6541 | 0.02255% | 48.7225 | 50.8826 | 53.1385 | 55.4944 | 10.5503 | 12.4944 | 14.5247 | 16.645
2031-07-24 21:00 | 47.9022 | 0.02315% | 50.026 | 52.2439 | 54.5601 | 56.9791 | 11.7234 | 13.7195 | 15.8041 | 17.9812
2031-07-24 22:00 | 48.0205 | 0.02321% | 50.1495 | 52.3729 | 54.6948 | 57.1197 | 11.8345 | 13.8356 | 15.9253 | 18.1078
2031-07-24 23:00 | 45.3271 | 0.0219% | 47.3367 | 49.4354 | 51.6271 | 53.916 | 9.303 | 11.1919 | 13.1644 | 15.2244
2031-07-25 | 43.9476 | 0.02124% | 45.896 | 47.9308 | 50.0559 | 52.2751 | 8.0064 | 9.8378 | 11.7503 | 13.7476
2031-07-25 01:00 | 41.228 | 0.01992% | 43.0558 | 44.9647 | 46.9582 | 49.0401 | 5.4502 | 7.1682 | 8.9624 | 10.8361
2031-07-25 02:00 | 38.2062 | 0.01846% | 39.9 | 41.669 | 43.5164 | 45.4457 | 2.61 | 4.2021 | 5.8648 | 7.6012
2031-07-25 03:00 | 34.0019 | 0.01643% | 35.5094 | 37.0837 | 38.7278 | 40.4448 | 0 | 0.075342 | 1.555 | 3.1004
2031-07-25 04:00 | 30.2575 | 0.01462% | 31.599 | 32.9999 | 34.463 | 35.9909 | 0 | 0 | 0 | 0
2031-07-25 05:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-07-25 06:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-07-25 07:00 | 23.7803 | 0.01149% | 24.8346 | 25.9357 | 27.0855 | 28.2864 | 0 | 0 | 0 | 0
2031-07-25 08:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-07-25 09:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-07-25 10:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-07-25 11:00 | 27.5773 | 0.01333% | 28.7999 | 30.0768 | 31.4102 | 32.8028 | 0 | 0 | 0 | 0
2031-07-25 12:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-07-25 13:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-07-25 14:00 | 36.0515 | 0.01742% | 37.6498 | 39.3191 | 41.0623 | 42.8828 | 0.58486 | 2.0871 | 3.656 | 5.2945
2031-07-25 15:00 | 37.2602 | 0.01801% | 38.9122 | 40.6373 | 42.439 | 44.3205 | 1.7209 | 3.2736 | 4.8951 | 6.5885
2031-07-25 16:00 | 38.3113 | 0.01851% | 40.0098 | 41.7837 | 43.6361 | 45.5708 | 2.7088 | 4.3053 | 5.9725 | 7.7137
2031-07-25 17:00 | 39.9273 | 0.0193% | 41.6975 | 43.5461 | 45.4768 | 47.493 | 4.2277 | 5.8915 | 7.6291 | 9.4437
2031-07-25 18:00 | 41.8718 | 0.02024% | 43.7281 | 45.6668 | 47.6915 | 49.8059 | 6.0553 | 7.8002 | 9.6223 | 11.5253
2031-07-25 19:00 | 43.6717 | 0.0211% | 45.6079 | 47.6299 | 49.7416 | 51.9469 | 7.7471 | 9.5669 | 11.4675 | 13.4522
2031-07-25 20:00 | 44.3155 | 0.02142% | 46.2802 | 48.3321 | 50.4749 | 52.7127 | 8.3522 | 10.1989 | 12.1274 | 14.1414
2031-07-25 21:00 | 46.2074 | 0.02233% | 48.256 | 50.3954 | 52.6297 | 54.9631 | 10.1304 | 12.0559 | 14.0668 | 16.1668
2031-07-25 22:00 | 45.6687 | 0.02207% | 47.6935 | 49.808 | 52.0162 | 54.3223 | 9.6241 | 11.5272 | 13.5146 | 15.5901
2031-07-25 23:00 | 43.9607 | 0.02124% | 45.9098 | 47.9452 | 50.0708 | 52.2907 | 8.0188 | 9.8507 | 11.7637 | 13.7617
2031-07-26 | 41.5433 | 0.02008% | 43.3851 | 45.3086 | 47.3174 | 49.4152 | 5.7466 | 7.4778 | 9.2856 | 11.1737
2031-07-26 01:00 | 40.0061 | 0.01933% | 41.7798 | 43.6321 | 45.5666 | 47.5868 | 4.3018 | 5.9689 | 7.7099 | 9.5281
2031-07-26 02:00 | 37.2602 | 0.01801% | 38.9122 | 40.6373 | 42.439 | 44.3205 | 1.7209 | 3.2736 | 4.8951 | 6.5885
2031-07-26 03:00 | 33.3319 | 0.01611% | 34.8096 | 36.3529 | 37.9646 | 39.6478 | 0 | 0 | 0.86818 | 2.383
2031-07-26 04:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-07-26 05:00 | 26.5262 | 0.01282% | 27.7023 | 28.9305 | 30.2131 | 31.5526 | 0 | 0 | 0 | 0
2031-07-26 06:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-07-26 07:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-07-26 08:00 | 20.4038 | 0.00986% | 21.3084 | 22.2531 | 23.2397 | 24.27 | 0 | 0 | 0 | 0
2031-07-26 09:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-07-26 10:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-07-26 11:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-07-26 12:00 | 28.0897 | 0.01357% | 29.335 | 30.6356 | 31.9939 | 33.4123 | 0 | 0 | 0 | 0
2031-07-26 13:00 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-07-26 14:00 | 31.9523 | 0.01544% | 33.369 | 34.8484 | 36.3934 | 38.0069 | 0 | 0 | 0 | 0.9062
2031-07-26 15:00 | 34.2647 | 0.01656% | 35.7838 | 37.3703 | 39.0271 | 40.7574 | 0 | 0.33327 | 1.8244 | 3.3817
2031-07-26 16:00 | 37.4441 | 0.0181% | 39.1042 | 40.8379 | 42.6485 | 44.5393 | 1.8938 | 3.4541 | 5.0836 | 6.7854
2031-07-26 17:00 | 38.6923 | 0.0187% | 40.4077 | 42.1992 | 44.0701 | 46.024 | 3.0669 | 4.6793 | 6.3631 | 8.1216
2031-07-26 18:00 | 38.4295 | 0.01857% | 40.1333 | 41.9126 | 43.7708 | 45.7114 | 2.82 | 4.4214 | 6.0937 | 7.8403
2031-07-26 19:00 | 39.4937 | 0.01909% | 41.2447 | 43.0733 | 44.9829 | 46.9773 | 3.8202 | 5.4659 | 7.1846 | 8.9795
2031-07-26 20:00 | 38.9419 | 0.01882% | 40.6684 | 42.4715 | 44.3544 | 46.3209 | 3.3016 | 4.9243 | 6.619 | 8.3888
2031-07-26 21:00 | 38.0091 | 0.01837% | 39.6942 | 41.4541 | 43.292 | 45.2113 | 2.4248 | 4.0087 | 5.6628 | 7.3902
2031-07-26 22:00 | 37.3128 | 0.01803% | 38.967 | 40.6946 | 42.4989 | 44.383 | 1.7703 | 3.3252 | 4.949 | 6.6447
2031-07-26 23:00 | 35.4471 | 0.01713% | 37.0187 | 38.6599 | 40.3739 | 42.1639 | 0.016815 | 1.4939 | 3.0365 | 4.6475
2031-07-27 | 34.8822 | 0.01686% | 36.4287 | 38.0438 | 39.7304 | 41.4919 | 0 | 0.93939 | 2.4574 | 4.0427
2031-07-27 01:00 | 33.6997 | 0.01629% | 35.1938 | 36.7541 | 38.3836 | 40.0854 | 0 | 0 | 1.2453 | 2.7769
2031-07-27 02:00 | 32.4647 | 0.01569% | 33.9041 | 35.4072 | 36.977 | 38.6164 | 0 | 0 | 0 | 1.4547
2031-07-27 03:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-07-27 04:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-07-27 05:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-07-27 06:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-07-27 07:00 | 21.1395 | 0.01022% | 22.0767 | 23.0555 | 24.0777 | 25.1452 | 0 | 0 | 0 | 0
2031-07-27 08:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-07-27 09:00 | 20.2724 | 0.009797% | 21.1712 | 22.1098 | 23.09 | 24.1137 | 0 | 0 | 0 | 0
2031-07-27 10:00 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-07-27 11:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-07-27 12:00 | 29.0488 | 0.01404% | 30.3367 | 31.6816 | 33.0863 | 34.5531 | 0 | 0 | 0 | 0
2031-07-27 13:00 | 34.0545 | 0.01646% | 35.5643 | 37.141 | 38.7877 | 40.5073 | 0 | 0.12693 | 1.6089 | 3.1566
2031-07-27 14:00 | 35.907 | 0.01735% | 37.4989 | 39.1614 | 40.8977 | 42.7109 | 0.44902 | 1.9453 | 3.5079 | 5.1398
2031-07-27 15:00 | 38.8105 | 0.01876% | 40.5312 | 42.3282 | 44.2048 | 46.1646 | 3.1781 | 4.7953 | 6.4843 | 8.2482
2031-07-27 16:00 | 40.9915 | 0.01981% | 42.8089 | 44.7068 | 46.6889 | 48.7588 | 5.228 | 6.9361 | 8.72 | 10.583
2031-07-27 17:00 | 43.317 | 0.02093% | 45.2374 | 47.243 | 49.3376 | 51.525 | 7.4137 | 9.2187 | 11.1038 | 13.0725
2031-07-27 18:00 | 43.5797 | 0.02106% | 45.5119 | 47.5296 | 49.6369 | 51.8375 | 7.6607 | 9.4767 | 11.3732 | 13.3538
2031-07-27 19:00 | 44.5914 | 0.02155% | 46.5684 | 48.633 | 50.7891 | 53.0409 | 8.6115 | 10.4697 | 12.4102 | 14.4368
2031-07-27 20:00 | 46.168 | 0.02231% | 48.2148 | 50.3525 | 52.5848 | 54.9162 | 10.0934 | 12.0172 | 14.0264 | 16.1246
2031-07-27 21:00 | 48.3884 | 0.02338% | 50.5337 | 52.7741 | 55.1138 | 57.5573 | 12.1803 | 14.1967 | 16.3024 | 18.5016
2031-07-27 22:00 | 48.5723 | 0.02347% | 50.7257 | 52.9747 | 55.3233 | 57.7761 | 12.3532 | 14.3772 | 16.491 | 18.6985
2031-07-27 23:00 | 47.1271 | 0.02277% | 49.2165 | 51.3985 | 53.6772 | 56.057 | 10.9948 | 12.9586 | 15.0095 | 17.1513
2031-07-28 | 44.6045 | 0.02156% | 46.5821 | 48.6473 | 50.8041 | 53.0565 | 8.6239 | 10.4826 | 12.4237 | 14.4508
2031-07-28 01:00 | 42.6601 | 0.02062% | 44.5514 | 46.5266 | 48.5894 | 50.7436 | 6.7963 | 8.5739 | 10.4304 | 12.3692
2031-07-28 02:00 | 39.1259 | 0.01891% | 40.8605 | 42.6721 | 44.5639 | 46.5397 | 3.4745 | 5.1049 | 6.8075 | 8.5857
2031-07-28 03:00 | 34.7639 | 0.0168% | 36.3052 | 37.9148 | 39.5958 | 41.3512 | 0 | 0.82332 | 2.3362 | 3.9161
2031-07-28 04:00 | 30.5071 | 0.01474% | 31.8597 | 33.2722 | 34.7473 | 36.2878 | 0 | 0 | 0 | 0
2031-07-28 05:00 | 26.8941 | 0.013% | 28.0865 | 29.3317 | 30.6321 | 31.9902 | 0 | 0 | 0 | 0
2031-07-28 06:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-07-28 07:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-07-28 08:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-07-28 09:00 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-07-28 10:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-07-28 11:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-07-28 12:00 | 32.7932 | 0.01585% | 34.2471 | 35.7654 | 37.3511 | 39.0071 | 0 | 0 | 0.31599 | 1.8064
2031-07-28 13:00 | 36.8135 | 0.01779% | 38.4456 | 40.1501 | 41.9302 | 43.7892 | 1.3011 | 2.8351 | 4.4372 | 6.1103
2031-07-28 14:00 | 40.2295 | 0.01944% | 42.013 | 43.8757 | 45.8209 | 47.8524 | 4.5117 | 6.1881 | 7.9389 | 9.7672
2031-07-28 15:00 | 42.1739 | 0.02038% | 44.0437 | 45.9964 | 48.0357 | 50.1653 | 6.3394 | 8.0968 | 9.9321 | 11.8488
2031-07-28 16:00 | 42.6995 | 0.02064% | 44.5926 | 46.5696 | 48.6342 | 50.7905 | 6.8333 | 8.6126 | 10.4708 | 12.4114
2031-07-28 17:00 | 43.8556 | 0.02119% | 45.8 | 47.8305 | 49.9511 | 52.1657 | 7.92 | 9.7475 | 11.656 | 13.6491
2031-07-28 18:00 | 44.7228 | 0.02161% | 46.7056 | 48.7763 | 50.9388 | 53.1971 | 8.735 | 10.5986 | 12.5449 | 14.5774
2031-07-28 19:00 | 46.5753 | 0.02251% | 48.6402 | 50.7967 | 53.0487 | 55.4007 | 10.4762 | 12.417 | 14.4439 | 16.5606
2031-07-28 20:00 | 48.7956 | 0.02358% | 50.959 | 53.2183 | 55.5777 | 58.0418 | 12.5631 | 14.5965 | 16.72 | 18.9376
2031-07-28 21:00 | 48.4015 | 0.02339% | 50.5474 | 52.7884 | 55.1288 | 57.5729 | 12.1926 | 14.2096 | 16.3159 | 18.5156
2031-07-28 22:00 | 47.9679 | 0.02318% | 50.0946 | 52.3155 | 54.635 | 57.0572 | 11.7851 | 13.784 | 15.8715 | 18.0515
2031-07-28 23:00 | 46.1943 | 0.02232% | 48.2423 | 50.3811 | 52.6148 | 54.9475 | 10.1181 | 12.043 | 14.0533 | 16.1527
2031-07-29 | 45.5505 | 0.02201% | 47.57 | 49.679 | 51.8815 | 54.1817 | 9.513 | 11.4111 | 13.3934 | 15.4635
2031-07-29 01:00 | 43.8556 | 0.02119% | 45.8 | 47.8305 | 49.9511 | 52.1657 | 7.92 | 9.7475 | 11.656 | 13.6491
2031-07-29 02:00 | 41.5433 | 0.02008% | 43.3851 | 45.3086 | 47.3174 | 49.4152 | 5.7466 | 7.4778 | 9.2856 | 11.1737
2031-07-29 03:00 | 36.761 | 0.01777% | 38.3908 | 40.0928 | 41.8703 | 43.7267 | 1.2517 | 2.7835 | 4.3833 | 6.054
2031-07-29 04:00 | 33.1085 | 0.016% | 34.5764 | 36.1093 | 37.7102 | 39.3821 | 0 | 0 | 0.63922 | 2.1439
2031-07-29 05:00 | 29.8239 | 0.01441% | 31.1462 | 32.5271 | 33.9692 | 35.4752 | 0 | 0 | 0 | 0
2031-07-29 06:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-07-29 07:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-07-29 08:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-07-29 09:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-07-29 10:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-07-29 11:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-07-29 12:00 | 34.107 | 0.01648% | 35.6192 | 37.1983 | 38.8475 | 40.5699 | 0 | 0.17851 | 1.6628 | 3.2129
2031-07-29 13:00 | 38.0091 | 0.01837% | 39.6942 | 41.4541 | 43.292 | 45.2113 | 2.4248 | 4.0087 | 5.6628 | 7.3902
2031-07-29 14:00 | 41.0835 | 0.01985% | 42.9049 | 44.8071 | 46.7936 | 48.8682 | 5.3144 | 7.0264 | 8.8143 | 10.6814
2031-07-29 15:00 | 42.3185 | 0.02045% | 44.1947 | 46.154 | 48.2003 | 50.3373 | 6.4752 | 8.2386 | 10.0803 | 12.0035
2031-07-29 16:00 | 43.9739 | 0.02125% | 45.9235 | 47.9595 | 50.0858 | 52.3064 | 8.0311 | 9.8636 | 11.7772 | 13.7757
2031-07-29 17:00 | 45.0906 | 0.02179% | 47.0897 | 49.1775 | 51.3578 | 53.6347 | 9.0808 | 10.9597 | 12.922 | 14.9713
2031-07-29 18:00 | 45.9184 | 0.02219% | 47.9542 | 50.0802 | 52.3005 | 54.6193 | 9.8587 | 11.7722 | 13.7705 | 15.8574
2031-07-29 19:00 | 46.7592 | 0.0226% | 48.8323 | 50.9973 | 53.2582 | 55.6195 | 10.6491 | 12.5975 | 14.6324 | 16.7575
2031-07-29 20:00 | 47.784 | 0.02309% | 49.9025 | 52.1149 | 54.4255 | 56.8384 | 11.6123 | 13.6034 | 15.6829 | 17.8546
2031-07-29 21:00 | 48.1519 | 0.02327% | 50.2867 | 52.5162 | 54.8445 | 57.276 | 11.958 | 13.9645 | 16.06 | 18.2484
2031-07-29 22:00 | 47.9548 | 0.02317% | 50.0809 | 52.3012 | 54.62 | 57.0416 | 11.7728 | 13.7711 | 15.858 | 18.0374
2031-07-29 23:00 | 46.7198 | 0.02258% | 48.7911 | 50.9543 | 53.2134 | 55.5726 | 10.612 | 12.5589 | 14.592 | 16.7153
2031-07-30 | 44.7359 | 0.02162% | 46.7193 | 48.7906 | 50.9537 | 53.2128 | 8.7474 | 10.6115 | 12.5584 | 14.5915
2031-07-30 01:00 | 43.9345 | 0.02123% | 45.8823 | 47.9165 | 50.0409 | 52.2595 | 7.9941 | 9.8249 | 11.7368 | 13.7335
2031-07-30 02:00 | 40.6762 | 0.01966% | 42.4796 | 44.3629 | 46.3297 | 48.3838 | 4.9316 | 6.6266 | 8.3968 | 10.2454
2031-07-30 03:00 | 35.7624 | 0.01728% | 37.348 | 39.0038 | 40.7331 | 42.539 | 0.31318 | 1.8034 | 3.3597 | 4.9851
2031-07-30 04:00 | 31.7421 | 0.01534% | 33.1494 | 34.6191 | 36.154 | 37.7568 | 0 | 0 | 0 | 0.68116
2031-07-30 05:00 | 27.9846 | 0.01352% | 29.2253 | 30.521 | 31.8741 | 33.2873 | 0 | 0 | 0 | 0
2031-07-30 06:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-07-30 07:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-07-30 08:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-07-30 09:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-07-30 10:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-07-30 11:00 | 26.4474 | 0.01278% | 27.6199 | 28.8445 | 30.1233 | 31.4588 | 0 | 0 | 0 | 0
2031-07-30 12:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-07-30 13:00 | 34.6194 | 0.01673% | 36.1543 | 37.7572 | 39.4312 | 41.1793 | 0 | 0.68146 | 2.188 | 3.7614
2031-07-30 14:00 | 38.1799 | 0.01845% | 39.8726 | 41.6404 | 43.4865 | 45.4145 | 2.5853 | 4.1763 | 5.8379 | 7.573
2031-07-30 15:00 | 40.8601 | 0.01975% | 42.6716 | 44.5635 | 46.5392 | 48.6026 | 5.1045 | 6.8072 | 8.5853 | 10.4423
2031-07-30 16:00 | 43.3564 | 0.02095% | 45.2786 | 47.286 | 49.3825 | 51.5719 | 7.4507 | 9.2574 | 11.1442 | 13.1147
2031-07-30 17:00 | 44.0396 | 0.02128% | 45.9921 | 48.0311 | 50.1606 | 52.3845 | 8.0929 | 9.928 | 11.8446 | 13.846
2031-07-30 18:00 | 43.0805 | 0.02082% | 44.9905 | 46.9851 | 49.0682 | 51.2437 | 7.1914 | 8.9866 | 10.8614 | 12.8193
2031-07-30 19:00 | 43.7505 | 0.02114% | 45.6902 | 47.7159 | 49.8314 | 52.0407 | 7.8212 | 9.6443 | 11.5483 | 13.5366
2031-07-30 20:00 | 43.7768 | 0.02116% | 45.7177 | 47.7446 | 49.8613 | 52.0719 | 7.8459 | 9.6701 | 11.5752 | 13.5647
2031-07-30 21:00 | 45.9972 | 0.02223% | 48.0365 | 50.1662 | 52.3903 | 54.713 | 9.9328 | 11.8496 | 13.8513 | 15.9417
2031-07-30 22:00 | 46.2337 | 0.02234% | 48.2834 | 50.4241 | 52.6597 | 54.9943 | 10.1551 | 12.0817 | 14.0937 | 16.1949
2031-07-30 23:00 | 42.8965 | 0.02073% | 44.7984 | 46.7845 | 48.8587 | 51.0249 | 7.0185 | 8.8061 | 10.6728 | 12.6224
2031-07-31 | 40.5579 | 0.0196% | 42.3561 | 44.2339 | 46.1951 | 48.2431 | 4.8205 | 6.5105 | 8.2755 | 10.1188
2031-07-31 01:00 | 39.231 | 0.01896% | 40.9703 | 42.7867 | 44.6837 | 46.6647 | 3.5732 | 5.208 | 6.9153 | 8.6982
2031-07-31 02:00 | 35.526 | 0.01717% | 37.101 | 38.7459 | 40.4637 | 42.2577 | 0.090907 | 1.5713 | 3.1173 | 4.7319
2031-07-31 03:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-07-31 04:00 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-07-31 05:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-07-31 06:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-07-31 07:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-07-31 08:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-07-31 09:00 | 19.8126 | 0.009575% | 20.6909 | 21.6083 | 22.5663 | 23.5668 | 0 | 0 | 0 | 0
2031-07-31 10:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-07-31 11:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-07-31 12:00 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-07-31 13:00 | 28.3919 | 0.01372% | 29.6506 | 30.9652 | 32.338 | 33.7717 | 0 | 0 | 0 | 0
2031-07-31 14:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-07-31 15:00 | 28.694 | 0.01387% | 29.9662 | 31.2948 | 32.6822 | 34.1312 | 0 | 0 | 0 | 0
2031-07-31 16:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-07-31 17:00 | 30.2444 | 0.01462% | 31.5853 | 32.9856 | 34.448 | 35.9753 | 0 | 0 | 0 | 0
2031-07-31 18:00 | 29.9685 | 0.01448% | 31.2971 | 32.6847 | 34.1338 | 35.6471 | 0 | 0 | 0 | 0
2031-07-31 19:00 | 31.0458 | 0.015% | 32.4222 | 33.8597 | 35.3608 | 36.9286 | 0 | 0 | 0 | 0
2031-07-31 20:00 | 34.1859 | 0.01652% | 35.7015 | 37.2843 | 38.9373 | 40.6636 | 0 | 0.25589 | 1.7436 | 3.2973
2031-07-31 21:00 | 35.2369 | 0.01703% | 36.7992 | 38.4306 | 40.1345 | 41.9138 | 0 | 1.2876 | 2.821 | 4.4225
2031-07-31 22:00 | 34.6982 | 0.01677% | 36.2366 | 37.8432 | 39.5209 | 41.2731 | 0 | 0.75884 | 2.2688 | 3.8458
2031-07-31 23:00 | 32.6093 | 0.01576% | 34.055 | 35.5648 | 37.1416 | 38.7883 | 0 | 0 | 0.12744 | 1.6095
2031-08-01 | 30.494 | 0.01474% | 31.8459 | 33.2578 | 34.7323 | 36.2722 | 0 | 0 | 0 | 0
2031-08-01 01:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-08-01 02:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-08-01 03:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-08-01 04:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-08-01 05:00 | 19.3396 | 0.009346% | 20.197 | 21.0924 | 22.0276 | 23.0042 | 0 | 0 | 0 | 0
2031-08-01 06:00 | 17.6841 | 0.008546% | 18.4682 | 19.287 | 20.1421 | 21.0351 | 0 | 0 | 0 | 0
2031-08-01 07:00 | 16.5411 | 0.007994% | 17.2745 | 18.0403 | 18.8402 | 19.6754 | 0 | 0 | 0 | 0
2031-08-01 08:00 | 16.2258 | 0.007841% | 16.9452 | 17.6964 | 18.481 | 19.3004 | 0 | 0 | 0 | 0
2031-08-01 09:00 | 16.6594 | 0.008051% | 17.398 | 18.1693 | 18.9748 | 19.8161 | 0 | 0 | 0 | 0
2031-08-01 10:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-08-01 11:00 | 21.3629 | 0.01032% | 22.31 | 23.2991 | 24.3321 | 25.4109 | 0 | 0 | 0 | 0
2031-08-01 12:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-08-01 13:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-08-01 14:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-08-01 15:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-08-01 16:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-08-01 17:00 | 30.7568 | 0.01486% | 32.1204 | 33.5444 | 35.0316 | 36.5848 | 0 | 0 | 0 | 0
2031-08-01 18:00 | 31.3086 | 0.01513% | 32.6966 | 34.1462 | 35.6601 | 37.2411 | 0 | 0 | 0 | 0.21701
2031-08-01 19:00 | 32.5041 | 0.01571% | 33.9452 | 35.4502 | 37.0219 | 38.6633 | 0 | 0 | 0.019699 | 1.4969
2031-08-01 20:00 | 32.8326 | 0.01587% | 34.2882 | 35.8084 | 37.396 | 39.054 | 0 | 0 | 0.3564 | 1.8486
2031-08-01 21:00 | 34.4092 | 0.01663% | 35.9347 | 37.5279 | 39.1917 | 40.9293 | 0 | 0.47512 | 1.9726 | 3.5364
2031-08-01 22:00 | 33.9099 | 0.01639% | 35.4134 | 36.9834 | 38.6231 | 40.3354 | 0 | 0 | 1.4608 | 3.0019
2031-08-01 23:00 | 32.5173 | 0.01571% | 33.9589 | 35.4645 | 37.0369 | 38.6789 | 0 | 0 | 0.033167 | 1.511
2031-08-02 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-08-02 01:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-08-02 02:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-08-02 03:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-08-02 04:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-08-02 05:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-08-02 06:00 | 17.5659 | 0.008489% | 18.3447 | 19.158 | 20.0074 | 20.8944 | 0 | 0 | 0 | 0
2031-08-02 07:00 | 16.3966 | 0.007924% | 17.1235 | 17.8827 | 18.6756 | 19.5035 | 0 | 0 | 0 | 0
2031-08-02 08:00 | 15.5557 | 0.007518% | 16.2454 | 16.9657 | 17.7178 | 18.5034 | 0 | 0 | 0 | 0
2031-08-02 09:00 | 15.3324 | 0.00741% | 16.0122 | 16.7221 | 17.4634 | 18.2377 | 0 | 0 | 0 | 0
2031-08-02 10:00 | 15.4506 | 0.007467% | 16.1356 | 16.851 | 17.5981 | 18.3783 | 0 | 0 | 0 | 0
2031-08-02 11:00 | 17.9732 | 0.008686% | 18.77 | 19.6022 | 20.4713 | 21.3789 | 0 | 0 | 0 | 0
2031-08-02 12:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-08-02 13:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-08-02 14:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-08-02 15:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-08-02 16:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-08-02 17:00 | 30.9144 | 0.01494% | 32.285 | 33.7164 | 35.2112 | 36.7723 | 0 | 0 | 0 | 0
2031-08-02 18:00 | 31.6502 | 0.0153% | 33.0534 | 34.5188 | 36.0492 | 37.6475 | 0 | 0 | 0 | 0.58271
2031-08-02 19:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-08-02 20:00 | 33.4764 | 0.01618% | 34.9606 | 36.5105 | 38.1293 | 39.8197 | 0 | 0 | 1.0163 | 2.5377
2031-08-02 21:00 | 33.9099 | 0.01639% | 35.4134 | 36.9834 | 38.6231 | 40.3354 | 0 | 0 | 1.4608 | 3.0019
2031-08-02 22:00 | 33.6472 | 0.01626% | 35.1389 | 36.6968 | 38.3238 | 40.0229 | 0 | 0 | 1.1914 | 2.7206
2031-08-02 23:00 | 32.0312 | 0.01548% | 33.4513 | 34.9343 | 36.4832 | 38.1007 | 0 | 0 | 0 | 0.99059
2031-08-03 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-08-03 01:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-08-03 02:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-08-03 03:00 | 24.3847 | 0.01178% | 25.4658 | 26.5948 | 27.7739 | 29.0053 | 0 | 0 | 0 | 0
2031-08-03 04:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-08-03 05:00 | 19.471 | 0.00941% | 20.3342 | 21.2357 | 22.1772 | 23.1604 | 0 | 0 | 0 | 0
2031-08-03 06:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-08-03 07:00 | 16.4097 | 0.00793% | 17.1373 | 17.897 | 18.6905 | 19.5192 | 0 | 0 | 0 | 0
2031-08-03 08:00 | 15.8973 | 0.007683% | 16.6022 | 17.3382 | 18.1069 | 18.9097 | 0 | 0 | 0 | 0
2031-08-03 09:00 | 15.293 | 0.007391% | 15.971 | 16.6791 | 17.4185 | 18.1908 | 0 | 0 | 0 | 0
2031-08-03 10:00 | 15.2404 | 0.007365% | 15.9161 | 16.6218 | 17.3587 | 18.1283 | 0 | 0 | 0 | 0
2031-08-03 11:00 | 16.8696 | 0.008152% | 17.6175 | 18.3986 | 19.2143 | 20.0661 | 0 | 0 | 0 | 0
2031-08-03 12:00 | 19.8388 | 0.009587% | 20.7184 | 21.6369 | 22.5962 | 23.598 | 0 | 0 | 0 | 0
2031-08-03 13:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-08-03 14:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-08-03 15:00 | 28.8123 | 0.01392% | 30.0897 | 31.4237 | 32.8169 | 34.2718 | 0 | 0 | 0 | 0
2031-08-03 16:00 | 30.9276 | 0.01495% | 32.2987 | 33.7307 | 35.2262 | 36.7879 | 0 | 0 | 0 | 0
2031-08-03 17:00 | 32.1888 | 0.01556% | 33.6159 | 35.1063 | 36.6627 | 38.2882 | 0 | 0 | 0 | 1.1594
2031-08-03 18:00 | 33.6209 | 0.01625% | 35.1115 | 36.6682 | 38.2939 | 39.9916 | 0 | 0 | 1.1645 | 2.6925
2031-08-03 19:00 | 34.869 | 0.01685% | 36.415 | 38.0294 | 39.7155 | 41.4763 | 0 | 0.92649 | 2.4439 | 4.0286
2031-08-03 20:00 | 35.723 | 0.01726% | 37.3068 | 38.9608 | 40.6882 | 42.4921 | 0.27614 | 1.7647 | 3.3193 | 4.9429
2031-08-03 21:00 | 36.7478 | 0.01776% | 38.377 | 40.0785 | 41.8554 | 43.7111 | 1.2393 | 2.7706 | 4.3698 | 6.0399
2031-08-03 22:00 | 36.6033 | 0.01769% | 38.2261 | 39.9209 | 41.6908 | 43.5391 | 1.1035 | 2.6288 | 4.2217 | 5.8852
2031-08-03 23:00 | 34.4223 | 0.01664% | 35.9485 | 37.5422 | 39.2067 | 40.9449 | 0 | 0.48802 | 1.986 | 3.5504
2031-08-04 | 32.0969 | 0.01551% | 33.5199 | 35.006 | 36.558 | 38.1788 | 0 | 0 | 0 | 1.0609
2031-08-04 01:00 | 31.4137 | 0.01518% | 32.8064 | 34.2609 | 35.7798 | 37.3662 | 0 | 0 | 0 | 0.32954
2031-08-04 02:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-08-04 03:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-08-04 04:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-08-04 05:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-08-04 06:00 | 18.4199 | 0.008902% | 19.2365 | 20.0894 | 20.9801 | 21.9102 | 0 | 0 | 0 | 0
2031-08-04 07:00 | 17.0404 | 0.008235% | 17.7959 | 18.5848 | 19.4088 | 20.2693 | 0 | 0 | 0 | 0
2031-08-04 08:00 | 16.436 | 0.007943% | 17.1647 | 17.9257 | 18.7204 | 19.5504 | 0 | 0 | 0 | 0
2031-08-04 09:00 | 16.1732 | 0.007816% | 16.8903 | 17.6391 | 18.4212 | 19.2379 | 0 | 0 | 0 | 0
2031-08-04 10:00 | 16.6856 | 0.008064% | 17.4254 | 18.198 | 19.0048 | 19.8473 | 0 | 0 | 0 | 0
2031-08-04 11:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-08-04 12:00 | 22.6898 | 0.01097% | 23.6958 | 24.7464 | 25.8435 | 26.9893 | 0 | 0 | 0 | 0
2031-08-04 13:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-08-04 14:00 | 31.4531 | 0.0152% | 32.8476 | 34.3039 | 35.8247 | 37.413 | 0 | 0 | 0 | 0.37173
2031-08-04 15:00 | 34.1464 | 0.0165% | 35.6603 | 37.2413 | 38.8924 | 40.6167 | 0 | 0.2172 | 1.7032 | 3.2551
2031-08-04 16:00 | 36.3143 | 0.01755% | 37.9243 | 39.6056 | 41.3616 | 43.1953 | 0.83183 | 2.3451 | 3.9254 | 5.5758
2031-08-04 17:00 | 36.8266 | 0.0178% | 38.4594 | 40.1645 | 41.9452 | 43.8048 | 1.3134 | 2.848 | 4.4507 | 6.1243
2031-08-04 18:00 | 38.6266 | 0.01867% | 40.3391 | 42.1276 | 43.9953 | 45.9458 | 3.0052 | 4.6148 | 6.2958 | 8.0512
2031-08-04 19:00 | 40.1375 | 0.0194% | 41.917 | 43.7754 | 45.7162 | 47.743 | 4.4253 | 6.0979 | 7.8446 | 9.6687
2031-08-04 20:00 | 41.9637 | 0.02028% | 43.8242 | 45.7671 | 47.7962 | 49.9153 | 6.1418 | 7.8904 | 9.7166 | 11.6238
2031-08-04 21:00 | 43.1987 | 0.02088% | 45.1139 | 47.1141 | 49.2029 | 51.3843 | 7.3026 | 9.1027 | 10.9826 | 12.9459
2031-08-04 22:00 | 41.609 | 0.02011% | 43.4537 | 45.3803 | 47.3922 | 49.4933 | 5.8084 | 7.5422 | 9.353 | 11.244
2031-08-04 23:00 | 38.8894 | 0.01879% | 40.6135 | 42.4141 | 44.2946 | 46.2584 | 3.2522 | 4.8727 | 6.5651 | 8.3325
2031-08-05 | 36.8923 | 0.01783% | 38.528 | 40.2361 | 42.02 | 43.883 | 1.3752 | 2.9125 | 4.518 | 6.1947
2031-08-05 01:00 | 35.7099 | 0.01726% | 37.2931 | 38.9465 | 40.6732 | 42.4765 | 0.26379 | 1.7518 | 3.3059 | 4.9288
2031-08-05 02:00 | 32.5173 | 0.01571% | 33.9589 | 35.4645 | 37.0369 | 38.6789 | 0 | 0 | 0.033167 | 1.511
2031-08-05 03:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-08-05 04:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-08-05 05:00 | 21.8884 | 0.01058% | 22.8588 | 23.8723 | 24.9307 | 26.036 | 0 | 0 | 0 | 0
2031-08-05 06:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-08-05 07:00 | 18.7089 | 0.009041% | 19.5384 | 20.4046 | 21.3093 | 22.254 | 0 | 0 | 0 | 0
2031-08-05 08:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-08-05 09:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-08-05 10:00 | 19.8914 | 0.009613% | 20.7733 | 21.6943 | 22.6561 | 23.6605 | 0 | 0 | 0 | 0
2031-08-05 11:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-08-05 12:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-08-05 13:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-08-05 14:00 | 33.2005 | 0.01604% | 34.6724 | 36.2096 | 37.815 | 39.4915 | 0 | 0 | 0.7335 | 2.2424
2031-08-05 15:00 | 35.3552 | 0.01709% | 36.9226 | 38.5596 | 40.2692 | 42.0545 | 0 | 1.4036 | 2.9422 | 4.5491
2031-08-05 16:00 | 36.577 | 0.01768% | 38.1987 | 39.8922 | 41.6608 | 43.5079 | 1.0788 | 2.603 | 4.1948 | 5.8571
2031-08-05 17:00 | 38.0748 | 0.0184% | 39.7628 | 41.5257 | 43.3668 | 45.2895 | 2.4866 | 4.0732 | 5.7301 | 7.4605
2031-08-05 18:00 | 38.7974 | 0.01875% | 40.5175 | 42.3138 | 44.1898 | 46.149 | 3.1657 | 4.7825 | 6.4708 | 8.2341
2031-08-05 19:00 | 40.6762 | 0.01966% | 42.4796 | 44.3629 | 46.3297 | 48.3838 | 4.9316 | 6.6266 | 8.3968 | 10.2454
2031-08-05 20:00 | 42.4367 | 0.02051% | 44.3181 | 46.283 | 48.335 | 50.4779 | 6.5863 | 8.3547 | 10.2015 | 12.1301
2031-08-05 21:00 | 43.133 | 0.02084% | 45.0453 | 47.0424 | 49.1281 | 51.3062 | 7.2408 | 9.0382 | 10.9153 | 12.8756
2031-08-05 22:00 | 42.6863 | 0.02063% | 44.5788 | 46.5552 | 48.6193 | 50.7748 | 6.821 | 8.5997 | 10.4574 | 12.3973
2031-08-05 23:00 | 41.0046 | 0.01982% | 42.8226 | 44.7211 | 46.7038 | 48.7745 | 5.2403 | 6.949 | 8.7335 | 10.597
2031-08-06 | 37.4967 | 0.01812% | 39.1591 | 40.8953 | 42.7084 | 44.6018 | 1.9432 | 3.5057 | 5.1375 | 6.8417
2031-08-06 01:00 | 35.8413 | 0.01732% | 37.4303 | 39.0898 | 40.8228 | 42.6327 | 0.38728 | 1.8808 | 3.4406 | 5.0695
2031-08-06 02:00 | 33.0954 | 0.01599% | 34.5627 | 36.095 | 37.6953 | 39.3665 | 0 | 0 | 0.62576 | 2.1299
2031-08-06 03:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-08-06 04:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-08-06 05:00 | 22.3482 | 0.0108% | 23.3391 | 24.3738 | 25.4544 | 26.5829 | 0 | 0 | 0 | 0
2031-08-06 06:00 | 20.1541 | 0.00974% | 21.0477 | 21.9808 | 22.9554 | 23.9731 | 0 | 0 | 0 | 0
2031-08-06 07:00 | 18.8403 | 0.009105% | 19.6756 | 20.5479 | 21.4589 | 22.4103 | 0 | 0 | 0 | 0
2031-08-06 08:00 | 18.1177 | 0.008756% | 18.921 | 19.7598 | 20.6359 | 21.5508 | 0 | 0 | 0 | 0
2031-08-06 09:00 | 18.5776 | 0.008978% | 19.4012 | 20.2613 | 21.1596 | 22.0978 | 0 | 0 | 0 | 0
2031-08-06 10:00 | 20.7454 | 0.01003% | 21.6651 | 22.6257 | 23.6288 | 24.6763 | 0 | 0 | 0 | 0
2031-08-06 11:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-08-06 12:00 | 25.7511 | 0.01244% | 26.8927 | 28.085 | 29.3302 | 30.6306 | 0 | 0 | 0 | 0
2031-08-06 13:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-08-06 14:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-08-06 15:00 | 31.8604 | 0.0154% | 33.2729 | 34.7481 | 36.2886 | 37.8975 | 0 | 0 | 0 | 0.80775
2031-08-06 16:00 | 35.6442 | 0.01723% | 37.2245 | 38.8749 | 40.5984 | 42.3983 | 0.20205 | 1.6874 | 3.2385 | 4.8585
2031-08-06 17:00 | 37.2602 | 0.01801% | 38.9122 | 40.6373 | 42.439 | 44.3205 | 1.7209 | 3.2736 | 4.8951 | 6.5885
2031-08-06 18:00 | 38.1142 | 0.01842% | 39.804 | 41.5687 | 43.4117 | 45.3363 | 2.5236 | 4.1118 | 5.7705 | 7.5027
2031-08-06 19:00 | 39.6382 | 0.01916% | 41.3956 | 43.2309 | 45.1475 | 47.1492 | 3.9561 | 5.6078 | 7.3328 | 9.1343
2031-08-06 20:00 | 42.0557 | 0.02032% | 43.9202 | 45.8675 | 47.901 | 50.0247 | 6.2282 | 7.9807 | 9.8109 | 11.7222
2031-08-06 21:00 | 42.7257 | 0.02065% | 44.62 | 46.5982 | 48.6642 | 50.8217 | 6.858 | 8.6384 | 10.4978 | 12.4395
2031-08-06 22:00 | 42.3447 | 0.02046% | 44.2221 | 46.1827 | 48.2302 | 50.3685 | 6.4999 | 8.2644 | 10.1072 | 12.0317
2031-08-06 23:00 | 39.3755 | 0.01903% | 41.1212 | 42.9443 | 44.8483 | 46.8366 | 3.7091 | 5.3499 | 7.0634 | 8.853
2031-08-07 | 37.1682 | 0.01796% | 38.8161 | 40.537 | 42.3342 | 44.2111 | 1.6345 | 3.1833 | 4.8008 | 6.49
2031-08-07 01:00 | 36.9712 | 0.01787% | 38.6103 | 40.3221 | 42.1098 | 43.9767 | 1.4493 | 2.9899 | 4.5988 | 6.2791
2031-08-07 02:00 | 34.0151 | 0.01644% | 35.5231 | 37.098 | 38.7428 | 40.4605 | 0 | 0.088238 | 1.5685 | 3.1144
2031-08-07 03:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-08-07 04:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-08-07 05:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-08-07 06:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-08-07 07:00 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-08-07 08:00 | 19.4315 | 0.009391% | 20.293 | 21.1927 | 22.1323 | 23.1136 | 0 | 0 | 0 | 0
2031-08-07 09:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-08-07 10:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-08-07 11:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-08-07 12:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-08-07 13:00 | 32.6881 | 0.0158% | 34.1373 | 35.6508 | 37.2314 | 38.8821 | 0 | 0 | 0.20825 | 1.6938
2031-08-07 14:00 | 36.4851 | 0.01763% | 38.1026 | 39.7919 | 41.5561 | 43.3985 | 0.99236 | 2.5127 | 4.1005 | 5.7586
2031-08-07 15:00 | 37.9171 | 0.01832% | 39.5982 | 41.3538 | 43.1872 | 45.1019 | 2.3384 | 3.9184 | 5.5685 | 7.2917
2031-08-07 16:00 | 39.3229 | 0.019% | 41.0663 | 42.887 | 44.7884 | 46.7741 | 3.6597 | 5.2983 | 7.0096 | 8.7967
2031-08-07 17:00 | 40.5579 | 0.0196% | 42.3561 | 44.2339 | 46.1951 | 48.2431 | 4.8205 | 6.5105 | 8.2755 | 10.1188
2031-08-07 18:00 | 41.1754 | 0.0199% | 43.0009 | 44.9074 | 46.8984 | 48.9776 | 5.4009 | 7.1167 | 8.9085 | 10.7799
2031-08-07 19:00 | 42.1345 | 0.02036% | 44.0026 | 45.9534 | 47.9908 | 50.1185 | 6.3023 | 8.0581 | 9.8917 | 11.8066
2031-08-07 20:00 | 42.3579 | 0.02047% | 44.2358 | 46.197 | 48.2452 | 50.3841 | 6.5122 | 8.2773 | 10.1207 | 12.0457
2031-08-07 21:00 | 42.4761 | 0.02053% | 44.3593 | 46.326 | 48.3799 | 50.5248 | 6.6234 | 8.3934 | 10.2419 | 12.1723
2031-08-07 22:00 | 40.7419 | 0.01969% | 42.5482 | 44.4345 | 46.4046 | 48.4619 | 4.9933 | 6.6911 | 8.4641 | 10.3157
2031-08-07 23:00 | 38.7843 | 0.01874% | 40.5038 | 42.2995 | 44.1749 | 46.1334 | 3.1534 | 4.7696 | 6.4574 | 8.22
2031-08-08 | 37.05 | 0.0179% | 38.6926 | 40.4081 | 42.1996 | 44.0705 | 1.5234 | 3.0673 | 4.6796 | 6.3634
2031-08-08 01:00 | 36.0909 | 0.01744% | 37.691 | 39.362 | 41.1072 | 42.9297 | 0.6219 | 2.1258 | 3.6964 | 5.3367
2031-08-08 02:00 | 33.0691 | 0.01598% | 34.5352 | 36.0663 | 37.6654 | 39.3353 | 0 | 0 | 0.59882 | 2.1017
2031-08-08 03:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-08-08 04:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-08-08 05:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-08-08 06:00 | 20.4695 | 0.009892% | 21.377 | 22.3247 | 23.3145 | 24.3482 | 0 | 0 | 0 | 0
2031-08-08 07:00 | 19.2345 | 0.009295% | 20.0872 | 20.9778 | 21.9079 | 22.8791 | 0 | 0 | 0 | 0
2031-08-08 08:00 | 18.525 | 0.008952% | 19.3463 | 20.204 | 21.0998 | 22.0352 | 0 | 0 | 0 | 0
2031-08-08 09:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-08-08 10:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-08-08 11:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-08-08 12:00 | 28.9437 | 0.01399% | 30.2269 | 31.567 | 32.9665 | 34.4281 | 0 | 0 | 0 | 0
2031-08-08 13:00 | 32.4253 | 0.01567% | 33.8629 | 35.3642 | 36.9321 | 38.5695 | 0 | 0 | 0 | 1.4125
2031-08-08 14:00 | 35.6705 | 0.01724% | 37.2519 | 38.9035 | 40.6283 | 42.4296 | 0.22674 | 1.7132 | 3.2655 | 4.8866
2031-08-08 15:00 | 36.8266 | 0.0178% | 38.4594 | 40.1645 | 41.9452 | 43.8048 | 1.3134 | 2.848 | 4.4507 | 6.1243
2031-08-08 16:00 | 38.9156 | 0.01881% | 40.641 | 42.4428 | 44.3245 | 46.2896 | 3.2769 | 4.8985 | 6.5921 | 8.3607
2031-08-08 17:00 | 40.1769 | 0.01942% | 41.9582 | 43.8184 | 45.7611 | 47.7899 | 4.4624 | 6.1366 | 7.885 | 9.7109
2031-08-08 18:00 | 41.044 | 0.01984% | 42.8637 | 44.7641 | 46.7487 | 48.8214 | 5.2774 | 6.9877 | 8.7739 | 10.6392
2031-08-08 19:00 | 42.1082 | 0.02035% | 43.9751 | 45.9248 | 47.9609 | 50.0872 | 6.2776 | 8.0323 | 9.8648 | 11.7785
2031-08-08 20:00 | 41.3462 | 0.01998% | 43.1793 | 45.0937 | 47.0929 | 49.1808 | 5.5614 | 7.2843 | 9.0836 | 10.9627
2031-08-08 21:00 | 39.4543 | 0.01907% | 41.2035 | 43.0303 | 44.938 | 46.9304 | 3.7832 | 5.4273 | 7.1442 | 8.9373
2031-08-08 22:00 | 37.8252 | 0.01828% | 39.5021 | 41.2535 | 43.0825 | 44.9925 | 2.2519 | 3.8281 | 5.4742 | 7.1933
2031-08-08 23:00 | 36.4456 | 0.01761% | 38.0615 | 39.7489 | 41.5112 | 43.3516 | 0.95532 | 2.474 | 4.0601 | 5.7164
2031-08-09 | 35.5391 | 0.01717% | 37.1147 | 38.7602 | 40.4787 | 42.2733 | 0.10326 | 1.5842 | 3.1308 | 4.746
2031-08-09 01:00 | 34.8822 | 0.01686% | 36.4287 | 38.0438 | 39.7304 | 41.4919 | 0 | 0.93939 | 2.4574 | 4.0427
2031-08-09 02:00 | 32.9771 | 0.01594% | 34.4392 | 35.966 | 37.5606 | 39.2259 | 0 | 0 | 0.50454 | 2.0033
2031-08-09 03:00 | 30.2444 | 0.01462% | 31.5853 | 32.9856 | 34.448 | 35.9753 | 0 | 0 | 0 | 0
2031-08-09 04:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-08-09 05:00 | 24.1088 | 0.01165% | 25.1776 | 26.2939 | 27.4596 | 28.6771 | 0 | 0 | 0 | 0
2031-08-09 06:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-08-09 07:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-08-09 08:00 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-08-09 09:00 | 18.3279 | 0.008857% | 19.1405 | 19.9891 | 20.8753 | 21.8008 | 0 | 0 | 0 | 0
2031-08-09 10:00 | 18.7484 | 0.00906% | 19.5796 | 20.4476 | 21.3542 | 22.3009 | 0 | 0 | 0 | 0
2031-08-09 11:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-08-09 12:00 | 26.2635 | 0.01269% | 27.4279 | 28.6439 | 29.9138 | 31.24 | 0 | 0 | 0 | 0
2031-08-09 13:00 | 28.8911 | 0.01396% | 30.172 | 31.5097 | 32.9067 | 34.3656 | 0 | 0 | 0 | 0
2031-08-09 14:00 | 35.3026 | 0.01706% | 36.8678 | 38.5023 | 40.2093 | 41.992 | 0 | 1.3521 | 2.8884 | 4.4928
2031-08-09 15:00 | 37.7726 | 0.01825% | 39.4473 | 41.1962 | 43.0226 | 44.93 | 2.2025 | 3.7765 | 5.4203 | 7.137
2031-08-09 16:00 | 39.1127 | 0.0189% | 40.8468 | 42.6577 | 44.549 | 46.5241 | 3.4621 | 5.092 | 6.7941 | 8.5717
2031-08-09 17:00 | 40.5711 | 0.01961% | 42.3698 | 44.2483 | 46.21 | 48.2588 | 4.8328 | 6.5234 | 8.289 | 10.1329
2031-08-09 18:00 | 41.5827 | 0.0201% | 43.4263 | 45.3516 | 47.3623 | 49.4621 | 5.7837 | 7.5164 | 9.326 | 11.2159
2031-08-09 19:00 | 43.1987 | 0.02088% | 45.1139 | 47.1141 | 49.2029 | 51.3843 | 7.3026 | 9.1027 | 10.9826 | 12.9459
2031-08-09 20:00 | 43.8819 | 0.02121% | 45.8274 | 47.8592 | 49.981 | 52.197 | 7.9447 | 9.7733 | 11.6829 | 13.6773
2031-08-09 21:00 | 44.7359 | 0.02162% | 46.7193 | 48.7906 | 50.9537 | 53.2128 | 8.7474 | 10.6115 | 12.5584 | 14.5915
2031-08-09 22:00 | 44.0396 | 0.02128% | 45.9921 | 48.0311 | 50.1606 | 52.3845 | 8.0929 | 9.928 | 11.8446 | 13.846
2031-08-09 23:00 | 41.8586 | 0.02023% | 43.7144 | 45.6525 | 47.6765 | 49.7903 | 6.043 | 7.7873 | 9.6089 | 11.5113
2031-08-10 | 39.6908 | 0.01918% | 41.4505 | 43.2882 | 45.2074 | 47.2117 | 4.0054 | 5.6594 | 7.3867 | 9.1905
2031-08-10 01:00 | 38.3113 | 0.01851% | 40.0098 | 41.7837 | 43.6361 | 45.5708 | 2.7088 | 4.3053 | 5.9725 | 7.7137
2031-08-10 02:00 | 35.8938 | 0.01735% | 37.4852 | 39.1471 | 40.8827 | 42.6952 | 0.43667 | 1.9324 | 3.4944 | 5.1257
2031-08-10 03:00 | 32.7275 | 0.01582% | 34.1785 | 35.6938 | 37.2763 | 38.9289 | 0 | 0 | 0.24865 | 1.736
2031-08-10 04:00 | 29.4561 | 0.01424% | 30.762 | 32.1258 | 33.5502 | 35.0376 | 0 | 0 | 0 | 0
2031-08-10 05:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-08-10 06:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-08-10 07:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-08-10 08:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-08-10 09:00 | 19.6549 | 0.009499% | 20.5263 | 21.4363 | 22.3867 | 23.3792 | 0 | 0 | 0 | 0
2031-08-10 10:00 | 19.5498 | 0.009448% | 20.4165 | 21.3217 | 22.267 | 23.2542 | 0 | 0 | 0 | 0
2031-08-10 11:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-08-10 12:00 | 28.1816 | 0.01362% | 29.4311 | 30.7359 | 32.0986 | 33.5217 | 0 | 0 | 0 | 0
2031-08-10 13:00 | 33.5946 | 0.01624% | 35.0841 | 36.6395 | 38.2639 | 39.9604 | 0 | 0 | 1.1375 | 2.6643
2031-08-10 14:00 | 37.6675 | 0.0182% | 39.3375 | 41.0815 | 42.9029 | 44.805 | 2.1037 | 3.6734 | 5.3126 | 7.0245
2031-08-10 15:00 | 40.4265 | 0.01954% | 42.2189 | 44.0906 | 46.0454 | 48.0868 | 4.697 | 6.3816 | 8.1409 | 9.9782
2031-08-10 16:00 | 42.5681 | 0.02057% | 44.4553 | 46.4263 | 48.4846 | 50.6342 | 6.7098 | 8.4837 | 10.3361 | 12.2708
2031-08-10 17:00 | 43.6717 | 0.0211% | 45.6079 | 47.6299 | 49.7416 | 51.9469 | 7.7471 | 9.5669 | 11.4675 | 13.4522
2031-08-10 18:00 | 44.5388 | 0.02152% | 46.5135 | 48.5757 | 50.7293 | 52.9784 | 8.5621 | 10.4181 | 12.3563 | 14.3805
2031-08-10 19:00 | 46.2337 | 0.02234% | 48.2834 | 50.4241 | 52.6597 | 54.9943 | 10.1551 | 12.0817 | 14.0937 | 16.1949
2031-08-10 20:00 | 47.3636 | 0.02289% | 49.4634 | 51.6564 | 53.9466 | 56.3383 | 11.2171 | 13.1908 | 15.2519 | 17.4045
2031-08-10 21:00 | 47.7052 | 0.02305% | 49.8202 | 52.029 | 54.3357 | 56.7447 | 11.5382 | 13.5261 | 15.6021 | 17.7702
2031-08-10 22:00 | 47.3373 | 0.02288% | 49.436 | 51.6278 | 53.9167 | 56.3071 | 11.1924 | 13.165 | 15.225 | 17.3764
2031-08-10 23:00 | 46.6935 | 0.02257% | 48.7637 | 50.9256 | 53.1834 | 55.5413 | 10.5873 | 12.5331 | 14.5651 | 16.6872
2031-08-11 | 43.1856 | 0.02087% | 45.1002 | 47.0998 | 49.1879 | 51.3687 | 7.2902 | 9.0898 | 10.9691 | 12.9318
2031-08-11 01:00 | 42.4893 | 0.02053% | 44.373 | 46.3403 | 48.3948 | 50.5404 | 6.6357 | 8.4063 | 10.2553 | 12.1864
2031-08-11 02:00 | 38.8499 | 0.01877% | 40.5724 | 42.3712 | 44.2497 | 46.2115 | 3.2151 | 4.834 | 6.5247 | 8.2904
2031-08-11 03:00 | 34.4486 | 0.01665% | 35.9759 | 37.5709 | 39.2366 | 40.9762 | 0 | 0.51381 | 2.013 | 3.5786
2031-08-11 04:00 | 30.0604 | 0.01453% | 31.3932 | 32.785 | 34.2385 | 35.7565 | 0 | 0 | 0 | 0
2031-08-11 05:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-08-11 06:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-08-11 07:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-08-11 08:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-08-11 09:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-08-11 10:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-08-11 11:00 | 27.6824 | 0.01338% | 28.9097 | 30.1914 | 31.53 | 32.9278 | 0 | 0 | 0 | 0
2031-08-11 12:00 | 32.4779 | 0.0157% | 33.9178 | 35.4215 | 36.992 | 38.632 | 0 | 0 | 0 | 1.4688
2031-08-11 13:00 | 37.0237 | 0.01789% | 38.6652 | 40.3794 | 42.1696 | 44.0392 | 1.4987 | 3.0415 | 4.6527 | 6.3353
2031-08-11 14:00 | 40.663 | 0.01965% | 42.4658 | 44.3486 | 46.3148 | 48.3681 | 4.9193 | 6.6137 | 8.3833 | 10.2313
2031-08-11 15:00 | 42.371 | 0.02048% | 44.2495 | 46.2114 | 48.2601 | 50.3998 | 6.5246 | 8.2902 | 10.1341 | 12.0598
2031-08-11 16:00 | 43.698 | 0.02112% | 45.6353 | 47.6586 | 49.7715 | 51.9782 | 7.7718 | 9.5927 | 11.4944 | 13.4804
2031-08-11 17:00 | 44.6308 | 0.02157% | 46.6095 | 48.676 | 50.834 | 53.0878 | 8.6486 | 10.5084 | 12.4506 | 14.479
2031-08-11 18:00 | 45.9446 | 0.0222% | 47.9816 | 50.1089 | 52.3305 | 54.6505 | 9.8834 | 11.798 | 13.7974 | 15.8855
2031-08-11 19:00 | 47.6657 | 0.02304% | 49.779 | 51.986 | 54.2908 | 56.6978 | 11.5011 | 13.4874 | 15.5617 | 17.728
2031-08-11 20:00 | 47.6789 | 0.02304% | 49.7927 | 52.0003 | 54.3058 | 56.7134 | 11.5135 | 13.5003 | 15.5752 | 17.7421
2031-08-11 21:00 | 48.2438 | 0.02331% | 50.3827 | 52.6165 | 54.9492 | 57.3854 | 12.0445 | 14.0548 | 16.1543 | 18.3469
2031-08-11 22:00 | 47.8628 | 0.02313% | 49.9848 | 52.2009 | 54.5153 | 56.9322 | 11.6863 | 13.6808 | 15.7637 | 17.939
2031-08-11 23:00 | 46.3651 | 0.02241% | 48.4207 | 50.5674 | 52.8093 | 55.1506 | 10.2786 | 12.2107 | 14.2284 | 16.3356
2031-08-12 | 44.2761 | 0.0214% | 46.2391 | 48.2891 | 50.43 | 52.6658 | 8.3151 | 10.1602 | 12.087 | 14.0992
2031-08-12 01:00 | 42.9754 | 0.02077% | 44.8807 | 46.8705 | 48.9485 | 51.1186 | 7.0926 | 8.8834 | 10.7537 | 12.7068
2031-08-12 02:00 | 40.0324 | 0.01935% | 41.8072 | 43.6608 | 45.5965 | 47.618 | 4.3265 | 5.9947 | 7.7368 | 9.5562
2031-08-12 03:00 | 35.4603 | 0.01714% | 37.0324 | 38.6742 | 40.3889 | 42.1795 | 0.029164 | 1.5068 | 3.05 | 4.6616
2031-08-12 04:00 | 31.2429 | 0.0151% | 32.628 | 34.0746 | 35.5853 | 37.163 | 0 | 0 | 0 | 0.14669
2031-08-12 05:00 | 27.7612 | 0.01342% | 28.992 | 30.2774 | 31.6197 | 33.0216 | 0 | 0 | 0 | 0
2031-08-12 06:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-08-12 07:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-08-12 08:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-08-12 09:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-08-12 10:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-08-12 11:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-08-12 12:00 | 33.2136 | 0.01605% | 34.6861 | 36.224 | 37.83 | 39.5072 | 0 | 0 | 0.74697 | 2.2564
2031-08-12 13:00 | 37.4967 | 0.01812% | 39.1591 | 40.8953 | 42.7084 | 44.6018 | 1.9432 | 3.5057 | 5.1375 | 6.8417
2031-08-12 14:00 | 41.0046 | 0.01982% | 42.8226 | 44.7211 | 46.7038 | 48.7745 | 5.2403 | 6.949 | 8.7335 | 10.597
2031-08-12 15:00 | 43.6586 | 0.0211% | 45.5942 | 47.6156 | 49.7266 | 51.9313 | 7.7348 | 9.554 | 11.454 | 13.4382
2031-08-12 16:00 | 45.3009 | 0.02189% | 47.3093 | 49.4067 | 51.5972 | 53.8848 | 9.2783 | 11.1661 | 13.1375 | 15.1963
2031-08-12 17:00 | 47.6526 | 0.02303% | 49.7653 | 51.9716 | 54.2758 | 56.6822 | 11.4888 | 13.4745 | 15.5482 | 17.7139
2031-08-12 18:00 | 48.927 | 0.02364% | 51.0962 | 53.3616 | 55.7274 | 58.1981 | 12.6866 | 14.7254 | 16.8546 | 19.0782
2031-08-12 19:00 | 49.4 | 0.02387% | 51.5902 | 53.8774 | 56.2661 | 58.7607 | 13.1311 | 15.1897 | 17.3395 | 19.5846
2031-08-12 20:00 | 47.2059 | 0.02281% | 49.2988 | 51.4845 | 53.767 | 56.1508 | 11.0689 | 13.036 | 15.0903 | 17.2357
2031-08-12 21:00 | 47.1665 | 0.02279% | 49.2576 | 51.4415 | 53.7221 | 56.1039 | 11.0319 | 12.9973 | 15.0499 | 17.1935
2031-08-12 22:00 | 45.6424 | 0.02206% | 47.666 | 49.7793 | 51.9863 | 54.2911 | 9.5994 | 11.5014 | 13.4876 | 15.562
2031-08-12 23:00 | 43.2907 | 0.02092% | 45.21 | 47.2144 | 49.3076 | 51.4937 | 7.389 | 9.1929 | 11.0769 | 13.0443
2031-08-13 | 41.7535 | 0.02018% | 43.6047 | 45.5379 | 47.5568 | 49.6653 | 5.9442 | 7.6841 | 9.5011 | 11.3987
2031-08-13 01:00 | 41.228 | 0.01992% | 43.0558 | 44.9647 | 46.9582 | 49.0401 | 5.4502 | 7.1682 | 8.9624 | 10.8361
2031-08-13 02:00 | 38.2324 | 0.01848% | 39.9275 | 41.6977 | 43.5464 | 45.477 | 2.6347 | 4.2279 | 5.8917 | 7.6293
2031-08-13 03:00 | 33.7129 | 0.01629% | 35.2075 | 36.7685 | 38.3986 | 40.101 | 0 | 0 | 1.2587 | 2.7909
2031-08-13 04:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-08-13 05:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-08-13 06:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-08-13 07:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-08-13 08:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-08-13 09:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-08-13 10:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-08-13 11:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-08-13 12:00 | 31.348 | 0.01515% | 32.7378 | 34.1892 | 35.705 | 37.288 | 0 | 0 | 0 | 0.25921
2031-08-13 13:00 | 35.0793 | 0.01695% | 36.6345 | 38.2587 | 39.9549 | 41.7263 | 0 | 1.1328 | 2.6594 | 4.2537
2031-08-13 14:00 | 36.9318 | 0.01785% | 38.5691 | 40.2791 | 42.0649 | 43.9298 | 1.4122 | 2.9512 | 4.5584 | 6.2369
2031-08-13 15:00 | 37.7989 | 0.01827% | 39.4747 | 41.2248 | 43.0525 | 44.9613 | 2.2272 | 3.8023 | 5.4473 | 7.1651
2031-08-13 16:00 | 41.6484 | 0.02013% | 43.4949 | 45.4232 | 47.4371 | 49.5402 | 5.8454 | 7.5809 | 9.3934 | 11.2862
2031-08-13 17:00 | 42.2659 | 0.02043% | 44.1398 | 46.0967 | 48.1404 | 50.2747 | 6.4258 | 8.187 | 10.0264 | 11.9473
2031-08-13 18:00 | 44.2104 | 0.02137% | 46.1704 | 48.2174 | 50.3552 | 52.5877 | 8.2534 | 10.0957 | 12.0196 | 14.0289
2031-08-13 19:00 | 45.4848 | 0.02198% | 47.5014 | 49.6073 | 51.8067 | 54.1036 | 9.4512 | 11.3466 | 13.326 | 15.3932
2031-08-13 20:00 | 46.7592 | 0.0226% | 48.8323 | 50.9973 | 53.2582 | 55.6195 | 10.6491 | 12.5975 | 14.6324 | 16.7575
2031-08-13 21:00 | 46.549 | 0.0225% | 48.6127 | 50.768 | 53.0188 | 55.3694 | 10.4515 | 12.3912 | 14.4169 | 16.5325
2031-08-13 22:00 | 44.9987 | 0.02175% | 46.9937 | 49.0772 | 51.253 | 53.5253 | 8.9943 | 10.8695 | 12.8277 | 14.8728
2031-08-13 23:00 | 43.0016 | 0.02078% | 44.9081 | 46.8991 | 48.9784 | 51.1499 | 7.1173 | 8.9092 | 10.7806 | 12.7349
2031-08-14 | 41.3331 | 0.01997% | 43.1656 | 45.0794 | 47.078 | 49.1652 | 5.549 | 7.2714 | 9.0702 | 10.9486
2031-08-14 01:00 | 40.2032 | 0.01943% | 41.9856 | 43.847 | 45.791 | 47.8212 | 4.487 | 6.1623 | 7.9119 | 9.7391
2031-08-14 02:00 | 36.7215 | 0.01775% | 38.3496 | 40.0498 | 41.8255 | 43.6798 | 1.2146 | 2.7449 | 4.3429 | 6.0118
2031-08-14 03:00 | 32.4779 | 0.0157% | 33.9178 | 35.4215 | 36.992 | 38.632 | 0 | 0 | 0 | 1.4688
2031-08-14 04:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-08-14 05:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-08-14 06:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-08-14 07:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-08-14 08:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-08-14 09:00 | 20.3906 | 0.009854% | 21.2947 | 22.2388 | 23.2247 | 24.2544 | 0 | 0 | 0 | 0
2031-08-14 10:00 | 22.1643 | 0.01071% | 23.147 | 24.1732 | 25.2449 | 26.3642 | 0 | 0 | 0 | 0
2031-08-14 11:00 | 26.4343 | 0.01277% | 27.6062 | 28.8302 | 30.1083 | 31.4432 | 0 | 0 | 0 | 0
2031-08-14 12:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-08-14 13:00 | 34.1202 | 0.01649% | 35.6329 | 37.2127 | 38.8625 | 40.5855 | 0 | 0.19141 | 1.6763 | 3.2269
2031-08-14 14:00 | 35.9201 | 0.01736% | 37.5126 | 39.1758 | 40.9126 | 42.7265 | 0.46137 | 1.9582 | 3.5214 | 5.1538
2031-08-14 15:00 | 37.6806 | 0.01821% | 39.3512 | 41.0959 | 42.9179 | 44.8206 | 2.1161 | 3.6863 | 5.3261 | 7.0386
2031-08-14 16:00 | 39.5331 | 0.0191% | 41.2858 | 43.1163 | 45.0278 | 47.0242 | 3.8573 | 5.5046 | 7.225 | 9.0217
2031-08-14 17:00 | 39.7171 | 0.01919% | 41.4779 | 43.3169 | 45.2373 | 47.2429 | 4.0301 | 5.6852 | 7.4136 | 9.2186
2031-08-14 18:00 | 41.136 | 0.01988% | 42.9598 | 44.8644 | 46.8535 | 48.9307 | 5.3638 | 7.078 | 8.8681 | 10.7377
2031-08-14 19:00 | 41.9637 | 0.02028% | 43.8242 | 45.7671 | 47.7962 | 49.9153 | 6.1418 | 7.8904 | 9.7166 | 11.6238
2031-08-14 20:00 | 43.1462 | 0.02085% | 45.0591 | 47.0568 | 49.143 | 51.3218 | 7.2532 | 9.0511 | 10.9287 | 12.8896
2031-08-14 21:00 | 43.3827 | 0.02097% | 45.306 | 47.3147 | 49.4124 | 51.6031 | 7.4754 | 9.2832 | 11.1712 | 13.1428
2031-08-14 22:00 | 43.6586 | 0.0211% | 45.5942 | 47.6156 | 49.7266 | 51.9313 | 7.7348 | 9.554 | 11.454 | 13.4382
2031-08-14 23:00 | 41.517 | 0.02006% | 43.3577 | 45.28 | 47.2875 | 49.384 | 5.7219 | 7.452 | 9.2587 | 11.1456
2031-08-15 | 39.6514 | 0.01916% | 41.4093 | 43.2452 | 45.1625 | 47.1648 | 3.9684 | 5.6207 | 7.3463 | 9.1483
2031-08-15 01:00 | 37.7857 | 0.01826% | 39.461 | 41.2105 | 43.0376 | 44.9456 | 2.2149 | 3.7894 | 5.4338 | 7.1511
2031-08-15 02:00 | 34.5931 | 0.01672% | 36.1268 | 37.7285 | 39.4012 | 41.1481 | 0 | 0.65567 | 2.1611 | 3.7333
2031-08-15 03:00 | 30.8487 | 0.01491% | 32.2164 | 33.6447 | 35.1364 | 36.6942 | 0 | 0 | 0 | 0
2031-08-15 04:00 | 26.7364 | 0.01292% | 27.9218 | 29.1597 | 30.4525 | 31.8026 | 0 | 0 | 0 | 0
2031-08-15 05:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-08-15 06:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-08-15 07:00 | 19.6023 | 0.009473% | 20.4714 | 21.379 | 22.3269 | 23.3167 | 0 | 0 | 0 | 0
2031-08-15 08:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-08-15 09:00 | 18.5644 | 0.008972% | 19.3875 | 20.247 | 21.1447 | 22.0821 | 0 | 0 | 0 | 0
2031-08-15 10:00 | 20.8242 | 0.01006% | 21.7474 | 22.7116 | 23.7185 | 24.7701 | 0 | 0 | 0 | 0
2031-08-15 11:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-08-15 12:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-08-15 13:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-08-15 14:00 | 35.3814 | 0.0171% | 36.9501 | 38.5883 | 40.2991 | 42.0858 | 0 | 1.4294 | 2.9692 | 4.5772
2031-08-15 15:00 | 37.2734 | 0.01801% | 38.9259 | 40.6517 | 42.454 | 44.3362 | 1.7333 | 3.2865 | 4.9086 | 6.6025
2031-08-15 16:00 | 38.8105 | 0.01876% | 40.5312 | 42.3282 | 44.2048 | 46.1646 | 3.1781 | 4.7953 | 6.4843 | 8.2482
2031-08-15 17:00 | 40.0849 | 0.01937% | 41.8621 | 43.7181 | 45.6563 | 47.6805 | 4.3759 | 6.0463 | 7.7907 | 9.6125
2031-08-15 18:00 | 40.9784 | 0.0198% | 42.7951 | 44.6925 | 46.6739 | 48.7432 | 5.2156 | 6.9232 | 8.7065 | 10.5689
2031-08-15 19:00 | 41.0966 | 0.01986% | 42.9186 | 44.8214 | 46.8086 | 48.8839 | 5.3268 | 7.0393 | 8.8277 | 10.6955
2031-08-15 20:00 | 42.0426 | 0.02032% | 43.9065 | 45.8531 | 47.886 | 50.0091 | 6.2159 | 7.9678 | 9.7974 | 11.7082
2031-08-15 21:00 | 42.9754 | 0.02077% | 44.8807 | 46.8705 | 48.9485 | 51.1186 | 7.0926 | 8.8834 | 10.7537 | 12.7068
2031-08-15 22:00 | 42.6338 | 0.0206% | 44.524 | 46.4979 | 48.5594 | 50.7123 | 6.7716 | 8.5481 | 10.4035 | 12.3411
2031-08-15 23:00 | 40.374 | 0.01951% | 42.164 | 44.0333 | 45.9856 | 48.0243 | 4.6476 | 6.33 | 8.087 | 9.9219
2031-08-16 | 36.9843 | 0.01787% | 38.624 | 40.3364 | 42.1247 | 43.9924 | 1.4616 | 3.0028 | 4.6123 | 6.2931
2031-08-16 01:00 | 35.7756 | 0.01729% | 37.3617 | 39.0181 | 40.748 | 42.5546 | 0.32553 | 1.8163 | 3.3732 | 4.9991
2031-08-16 02:00 | 32.9114 | 0.0159% | 34.3706 | 35.8944 | 37.4858 | 39.1477 | 0 | 0 | 0.43721 | 1.933
2031-08-16 03:00 | 29.5612 | 0.01429% | 30.8718 | 32.2405 | 33.6699 | 35.1626 | 0 | 0 | 0 | 0
2031-08-16 04:00 | 26.4211 | 0.01277% | 27.5925 | 28.8158 | 30.0934 | 31.4276 | 0 | 0 | 0 | 0
2031-08-16 05:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-08-16 06:00 | 20.6928 | 0.01% | 21.6102 | 22.5683 | 23.5689 | 24.6138 | 0 | 0 | 0 | 0
2031-08-16 07:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-08-16 08:00 | 18.5119 | 0.008946% | 19.3326 | 20.1897 | 21.0848 | 22.0196 | 0 | 0 | 0 | 0
2031-08-16 09:00 | 17.9995 | 0.008699% | 18.7975 | 19.6309 | 20.5012 | 21.4101 | 0 | 0 | 0 | 0
2031-08-16 10:00 | 18.2097 | 0.0088% | 19.017 | 19.8601 | 20.7406 | 21.6602 | 0 | 0 | 0 | 0
2031-08-16 11:00 | 21.5468 | 0.01041% | 22.5021 | 23.4997 | 24.5416 | 25.6296 | 0 | 0 | 0 | 0
2031-08-16 12:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-08-16 13:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-08-16 14:00 | 35.1187 | 0.01697% | 36.6757 | 38.3017 | 39.9998 | 41.7732 | 0 | 1.1715 | 2.6998 | 4.2959
2031-08-16 15:00 | 37.7989 | 0.01827% | 39.4747 | 41.2248 | 43.0525 | 44.9613 | 2.2272 | 3.8023 | 5.4473 | 7.1651
2031-08-16 16:00 | 40.1769 | 0.01942% | 41.9582 | 43.8184 | 45.7611 | 47.7899 | 4.4624 | 6.1366 | 7.885 | 9.7109
2031-08-16 17:00 | 41.136 | 0.01988% | 42.9598 | 44.8644 | 46.8535 | 48.9307 | 5.3638 | 7.078 | 8.8681 | 10.7377
2031-08-16 18:00 | 41.6353 | 0.02012% | 43.4812 | 45.4089 | 47.4221 | 49.5246 | 5.8331 | 7.568 | 9.3799 | 11.2721
2031-08-16 19:00 | 42.6206 | 0.0206% | 44.5102 | 46.4836 | 48.5445 | 50.6967 | 6.7592 | 8.5352 | 10.39 | 12.327
2031-08-16 20:00 | 42.6075 | 0.02059% | 44.4965 | 46.4693 | 48.5295 | 50.6811 | 6.7469 | 8.5223 | 10.3765 | 12.313
2031-08-16 21:00 | 43.0411 | 0.0208% | 44.9493 | 46.9421 | 49.0233 | 51.1968 | 7.1544 | 8.9479 | 10.821 | 12.7771
2031-08-16 22:00 | 43.2513 | 0.0209% | 45.1688 | 47.1714 | 49.2628 | 51.4468 | 7.3519 | 9.1543 | 11.0365 | 13.0021
2031-08-16 23:00 | 40.9652 | 0.0198% | 42.7814 | 44.6781 | 46.659 | 48.7276 | 5.2033 | 6.9103 | 8.6931 | 10.5548
2031-08-17 | 38.8237 | 0.01876% | 40.5449 | 42.3425 | 44.2198 | 46.1802 | 3.1904 | 4.8082 | 6.4978 | 8.2622
2031-08-17 01:00 | 37.5361 | 0.01814% | 39.2003 | 40.9382 | 42.7532 | 44.6487 | 1.9803 | 3.5444 | 5.1779 | 6.8838
2031-08-17 02:00 | 35.1318 | 0.01698% | 36.6894 | 38.316 | 40.0148 | 41.7888 | 0 | 1.1844 | 2.7133 | 4.3099
2031-08-17 03:00 | 31.9655 | 0.01545% | 33.3827 | 34.8627 | 36.4083 | 38.0225 | 0 | 0 | 0 | 0.92027
2031-08-17 04:00 | 28.2473 | 0.01365% | 29.4997 | 30.8076 | 32.1734 | 33.5998 | 0 | 0 | 0 | 0
2031-08-17 05:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-08-17 06:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-08-17 07:00 | 21.3497 | 0.01032% | 22.2963 | 23.2848 | 24.3171 | 25.3952 | 0 | 0 | 0 | 0
2031-08-17 08:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-08-17 09:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-08-17 10:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-08-17 11:00 | 22.1643 | 0.01071% | 23.147 | 24.1732 | 25.2449 | 26.3642 | 0 | 0 | 0 | 0
2031-08-17 12:00 | 25.2518 | 0.0122% | 26.3714 | 27.5405 | 28.7615 | 30.0367 | 0 | 0 | 0 | 0
2031-08-17 13:00 | 29.5349 | 0.01427% | 30.8443 | 32.2118 | 33.6399 | 35.1314 | 0 | 0 | 0 | 0
2031-08-17 14:00 | 31.2691 | 0.01511% | 32.6555 | 34.1033 | 35.6152 | 37.1942 | 0 | 0 | 0 | 0.17482
2031-08-17 15:00 | 31.729 | 0.01533% | 33.1357 | 34.6048 | 36.139 | 37.7412 | 0 | 0 | 0 | 0.6671
2031-08-17 16:00 | 33.0297 | 0.01596% | 34.4941 | 36.0234 | 37.6205 | 39.2884 | 0 | 0 | 0.55842 | 2.0595
2031-08-17 17:00 | 33.1085 | 0.016% | 34.5764 | 36.1093 | 37.7102 | 39.3821 | 0 | 0 | 0.63922 | 2.1439
2031-08-17 18:00 | 32.9246 | 0.01591% | 34.3843 | 35.9087 | 37.5007 | 39.1634 | 0 | 0 | 0.45067 | 1.947
2031-08-17 19:00 | 33.0297 | 0.01596% | 34.4941 | 36.0234 | 37.6205 | 39.2884 | 0 | 0 | 0.55842 | 2.0595
2031-08-17 20:00 | 36.577 | 0.01768% | 38.1987 | 39.8922 | 41.6608 | 43.5079 | 1.0788 | 2.603 | 4.1948 | 5.8571
2031-08-17 21:00 | 38.3376 | 0.01853% | 40.0373 | 41.8123 | 43.6661 | 45.602 | 2.7335 | 4.3311 | 5.9995 | 7.7418
2031-08-17 22:00 | 38.285 | 0.0185% | 39.9824 | 41.755 | 43.6062 | 45.5395 | 2.6841 | 4.2795 | 5.9456 | 7.6856
2031-08-17 23:00 | 36.7872 | 0.01778% | 38.4182 | 40.1215 | 41.9003 | 43.7579 | 1.2764 | 2.8093 | 4.4102 | 6.0821
2031-08-18 | 33.5289 | 0.0162% | 35.0154 | 36.5679 | 38.1891 | 39.8822 | 0 | 0 | 1.0702 | 2.594
2031-08-18 01:00 | 32.3202 | 0.01562% | 33.7531 | 35.2496 | 36.8124 | 38.4445 | 0 | 0 | 0 | 1.3
2031-08-18 02:00 | 28.5495 | 0.0138% | 29.8153 | 31.1371 | 32.5176 | 33.9593 | 0 | 0 | 0 | 0
2031-08-18 03:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-08-18 04:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-08-18 05:00 | 18.9323 | 0.009149% | 19.7717 | 20.6482 | 21.5637 | 22.5197 | 0 | 0 | 0 | 0
2031-08-18 06:00 | 17.0929 | 0.00826% | 17.8507 | 18.6422 | 19.4687 | 20.3318 | 0 | 0 | 0 | 0
2031-08-18 07:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-08-18 08:00 | 15.7134 | 0.007594% | 16.4101 | 17.1376 | 17.8974 | 18.6909 | 0 | 0 | 0 | 0
2031-08-18 09:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-08-18 10:00 | 17.3557 | 0.008387% | 18.1252 | 18.9287 | 19.768 | 20.6444 | 0 | 0 | 0 | 0
2031-08-18 11:00 | 20.3775 | 0.009848% | 21.2809 | 22.2244 | 23.2098 | 24.2388 | 0 | 0 | 0 | 0
2031-08-18 12:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-08-18 13:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-08-18 14:00 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-08-18 15:00 | 27.3802 | 0.01323% | 28.5941 | 29.8618 | 31.1858 | 32.5684 | 0 | 0 | 0 | 0
2031-08-18 16:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-08-18 17:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-08-18 18:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-08-18 19:00 | 30.1918 | 0.01459% | 31.5304 | 32.9283 | 34.3882 | 35.9128 | 0 | 0 | 0 | 0
2031-08-18 20:00 | 31.5056 | 0.01523% | 32.9024 | 34.3612 | 35.8846 | 37.4755 | 0 | 0 | 0 | 0.42799
2031-08-18 21:00 | 32.6093 | 0.01576% | 34.055 | 35.5648 | 37.1416 | 38.7883 | 0 | 0 | 0.12744 | 1.6095
2031-08-18 22:00 | 31.5582 | 0.01525% | 32.9573 | 34.4185 | 35.9445 | 37.5381 | 0 | 0 | 0 | 0.48425
2031-08-18 23:00 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-08-19 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-08-19 01:00 | 27.9714 | 0.01352% | 29.2116 | 30.5067 | 31.8592 | 33.2717 | 0 | 0 | 0 | 0
2031-08-19 02:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-08-19 03:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-08-19 04:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-08-19 05:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-08-19 06:00 | 16.7776 | 0.008108% | 17.5214 | 18.2983 | 19.1095 | 19.9567 | 0 | 0 | 0 | 0
2031-08-19 07:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-08-19 08:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-08-19 09:00 | 16.4754 | 0.007962% | 17.2059 | 17.9687 | 18.7653 | 19.5973 | 0 | 0 | 0 | 0
2031-08-19 10:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-08-19 11:00 | 20.6403 | 0.009975% | 21.5554 | 22.511 | 23.509 | 24.5513 | 0 | 0 | 0 | 0
2031-08-19 12:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-08-19 13:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-08-19 14:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-08-19 15:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-08-19 16:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-08-19 17:00 | 27.2226 | 0.01316% | 28.4295 | 29.6899 | 31.0062 | 32.3809 | 0 | 0 | 0 | 0
2031-08-19 18:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-08-19 19:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-08-19 20:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-08-19 21:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-08-19 22:00 | 29.2721 | 0.01415% | 30.5699 | 31.9252 | 33.3406 | 34.8188 | 0 | 0 | 0 | 0
2031-08-19 23:00 | 28.1816 | 0.01362% | 29.4311 | 30.7359 | 32.0986 | 33.5217 | 0 | 0 | 0 | 0
2031-08-20 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0
2031-08-20 01:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-08-20 02:00 | 25.6854 | 0.01241% | 26.8241 | 28.0134 | 29.2554 | 30.5524 | 0 | 0 | 0 | 0
2031-08-20 03:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-08-20 04:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-08-20 05:00 | 18.5381 | 0.008959% | 19.36 | 20.2184 | 21.1147 | 22.0509 | 0 | 0 | 0 | 0
2031-08-20 06:00 | 17.2769 | 0.008349% | 18.0428 | 18.8428 | 19.6782 | 20.5506 | 0 | 0 | 0 | 0
2031-08-20 07:00 | 16.5805 | 0.008013% | 17.3156 | 18.0833 | 18.8851 | 19.7223 | 0 | 0 | 0 | 0
2031-08-20 08:00 | 16.2521 | 0.007854% | 16.9726 | 17.7251 | 18.5109 | 19.3316 | 0 | 0 | 0 | 0
2031-08-20 09:00 | 17.2374 | 0.00833% | 18.0017 | 18.7998 | 19.6333 | 20.5037 | 0 | 0 | 0 | 0
2031-08-20 10:00 | 19.4053 | 0.009378% | 20.2656 | 21.1641 | 22.1024 | 23.0823 | 0 | 0 | 0 | 0
2031-08-20 11:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-08-20 12:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-08-20 13:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-08-20 14:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0
2031-08-20 15:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-08-20 16:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-08-20 17:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-08-20 18:00 | 28.2736 | 0.01366% | 29.5271 | 30.8362 | 32.2034 | 33.6311 | 0 | 0 | 0 | 0
2031-08-20 19:00 | 27.0123 | 0.01305% | 28.2099 | 29.4606 | 30.7668 | 32.1308 | 0 | 0 | 0 | 0
2031-08-20 20:00 | 27.8138 | 0.01344% | 29.0469 | 30.3347 | 31.6796 | 33.0841 | 0 | 0 | 0 | 0
2031-08-20 21:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-08-20 22:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-08-20 23:00 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-08-21 | 27.6824 | 0.01338% | 28.9097 | 30.1914 | 31.53 | 32.9278 | 0 | 0 | 0 | 0
2031-08-21 01:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-08-21 02:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-08-21 03:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-08-21 04:00 | 20.141 | 0.009733% | 21.034 | 21.9665 | 22.9404 | 23.9575 | 0 | 0 | 0 | 0
2031-08-21 05:00 | 18.3673 | 0.008876% | 19.1817 | 20.0321 | 20.9202 | 21.8477 | 0 | 0 | 0 | 0
2031-08-21 06:00 | 16.7513 | 0.008095% | 17.494 | 18.2696 | 19.0796 | 19.9255 | 0 | 0 | 0 | 0
2031-08-21 07:00 | 15.9368 | 0.007702% | 16.6433 | 17.3812 | 18.1518 | 18.9566 | 0 | 0 | 0 | 0
2031-08-21 08:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-08-21 09:00 | 16.3178 | 0.007886% | 17.0412 | 17.7967 | 18.5858 | 19.4098 | 0 | 0 | 0 | 0
2031-08-21 10:00 | 18.2097 | 0.0088% | 19.017 | 19.8601 | 20.7406 | 21.6602 | 0 | 0 | 0 | 0
2031-08-21 11:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-08-21 12:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-08-21 13:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-08-21 14:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-08-21 15:00 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-08-21 16:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-08-21 17:00 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-08-21 18:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-08-21 19:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-08-21 20:00 | 31.9392 | 0.01544% | 33.3552 | 34.834 | 36.3784 | 37.9913 | 0 | 0 | 0 | 0.89214
2031-08-21 21:00 | 33.1873 | 0.01604% | 34.6587 | 36.1953 | 37.8 | 39.4759 | 0 | 0 | 0.72003 | 2.2283
2031-08-21 22:00 | 33.4501 | 0.01617% | 34.9331 | 36.4819 | 38.0993 | 39.7885 | 0 | 0 | 0.98939 | 2.5096
2031-08-21 23:00 | 32.5436 | 0.01573% | 33.9864 | 35.4932 | 37.0668 | 38.7101 | 0 | 0 | 0.060103 | 1.5391
2031-08-22 | 30.7436 | 0.01486% | 32.1066 | 33.5301 | 35.0167 | 36.5691 | 0 | 0 | 0 | 0
2031-08-22 01:00 | 29.8634 | 0.01443% | 31.1873 | 32.57 | 34.014 | 35.5221 | 0 | 0 | 0 | 0
2031-08-22 02:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-08-22 03:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-08-22 04:00 | 21.2446 | 0.01027% | 22.1865 | 23.1702 | 24.1974 | 25.2702 | 0 | 0 | 0 | 0
2031-08-22 05:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-08-22 06:00 | 17.3557 | 0.008387% | 18.1252 | 18.9287 | 19.768 | 20.6444 | 0 | 0 | 0 | 0
2031-08-22 07:00 | 16.5805 | 0.008013% | 17.3156 | 18.0833 | 18.8851 | 19.7223 | 0 | 0 | 0 | 0
2031-08-22 08:00 | 16.147 | 0.007803% | 16.8628 | 17.6105 | 18.3912 | 19.2066 | 0 | 0 | 0 | 0
2031-08-22 09:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-08-22 10:00 | 18.8403 | 0.009105% | 19.6756 | 20.5479 | 21.4589 | 22.4103 | 0 | 0 | 0 | 0
2031-08-22 11:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-08-22 12:00 | 25.8299 | 0.01248% | 26.9751 | 28.171 | 29.42 | 30.7243 | 0 | 0 | 0 | 0
2031-08-22 13:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-08-22 14:00 | 31.8472 | 0.01539% | 33.2592 | 34.7337 | 36.2737 | 37.8819 | 0 | 0 | 0 | 0.79368
2031-08-22 15:00 | 33.2005 | 0.01604% | 34.6724 | 36.2096 | 37.815 | 39.4915 | 0 | 0 | 0.7335 | 2.2424
2031-08-22 16:00 | 34.199 | 0.01653% | 35.7152 | 37.2986 | 38.9523 | 40.6793 | 0 | 0.26878 | 1.7571 | 3.3113
2031-08-22 17:00 | 35.3814 | 0.0171% | 36.9501 | 38.5883 | 40.2991 | 42.0858 | 0 | 1.4294 | 2.9692 | 4.5772
2031-08-22 18:00 | 35.8938 | 0.01735% | 37.4852 | 39.1471 | 40.8827 | 42.6952 | 0.43667 | 1.9324 | 3.4944 | 5.1257
2031-08-22 19:00 | 36.577 | 0.01768% | 38.1987 | 39.8922 | 41.6608 | 43.5079 | 1.0788 | 2.603 | 4.1948 | 5.8571
2031-08-22 20:00 | 37.431 | 0.01809% | 39.0905 | 40.8236 | 42.6335 | 44.5237 | 1.8815 | 3.4412 | 5.0702 | 6.7713
2031-08-22 21:00 | 37.5887 | 0.01817% | 39.2552 | 40.9956 | 42.8131 | 44.7112 | 2.0297 | 3.596 | 5.2318 | 6.9401
2031-08-22 22:00 | 37.1814 | 0.01797% | 38.8298 | 40.5514 | 42.3492 | 44.2268 | 1.6468 | 3.1962 | 4.8143 | 6.5041
2031-08-22 23:00 | 35.1449 | 0.01698% | 36.7031 | 38.3303 | 40.0297 | 41.8045 | 0 | 1.1973 | 2.7268 | 4.324
2031-08-23 | 33.0297 | 0.01596% | 34.4941 | 36.0234 | 37.6205 | 39.2884 | 0 | 0 | 0.55842 | 2.0595
2031-08-23 01:00 | 32.4122 | 0.01566% | 33.8492 | 35.3499 | 36.9171 | 38.5539 | 0 | 0 | 0 | 1.3985
2031-08-23 02:00 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-08-23 03:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-08-23 04:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-08-23 05:00 | 20.7979 | 0.01005% | 21.72 | 22.683 | 23.6886 | 24.7389 | 0 | 0 | 0 | 0
2031-08-23 06:00 | 19.1688 | 0.009264% | 20.0186 | 20.9062 | 21.833 | 22.801 | 0 | 0 | 0 | 0
2031-08-23 07:00 | 17.8418 | 0.008622% | 18.6328 | 19.4589 | 20.3216 | 21.2226 | 0 | 0 | 0 | 0
2031-08-23 08:00 | 16.6462 | 0.008045% | 17.3842 | 18.155 | 18.9599 | 19.8005 | 0 | 0 | 0 | 0
2031-08-23 09:00 | 16.3966 | 0.007924% | 17.1235 | 17.8827 | 18.6756 | 19.5035 | 0 | 0 | 0 | 0
2031-08-23 10:00 | 16.528 | 0.007987% | 17.2608 | 18.026 | 18.8252 | 19.6598 | 0 | 0 | 0 | 0
2031-08-23 11:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-08-23 12:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-08-23 13:00 | 26.224 | 0.01267% | 27.3867 | 28.6009 | 29.8689 | 31.1932 | 0 | 0 | 0 | 0
2031-08-23 14:00 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-08-23 15:00 | 31.7684 | 0.01535% | 33.1769 | 34.6478 | 36.1839 | 37.7881 | 0 | 0 | 0 | 0.70929
2031-08-23 16:00 | 32.5436 | 0.01573% | 33.9864 | 35.4932 | 37.0668 | 38.7101 | 0 | 0 | 0.060103 | 1.5391
2031-08-23 17:00 | 33.2662 | 0.01608% | 34.741 | 36.2813 | 37.8898 | 39.5697 | 0 | 0 | 0.80084 | 2.3127
2031-08-23 18:00 | 33.253 | 0.01607% | 34.7273 | 36.267 | 37.8749 | 39.554 | 0 | 0 | 0.78737 | 2.2986
2031-08-23 19:00 | 32.6618 | 0.01578% | 34.1099 | 35.6221 | 37.2015 | 38.8508 | 0 | 0 | 0.18131 | 1.6657
2031-08-23 20:00 | 32.7801 | 0.01584% | 34.2334 | 35.7511 | 37.3361 | 38.9914 | 0 | 0 | 0.30253 | 1.7923
2031-08-23 21:00 | 34.6588 | 0.01675% | 36.1954 | 37.8002 | 39.476 | 41.2262 | 0 | 0.72015 | 2.2284 | 3.8036
2031-08-23 22:00 | 33.5289 | 0.0162% | 35.0154 | 36.5679 | 38.1891 | 39.8822 | 0 | 0 | 1.0702 | 2.594
2031-08-23 23:00 | 32.7012 | 0.0158% | 34.151 | 35.6651 | 37.2464 | 38.8977 | 0 | 0 | 0.22172 | 1.7079
2031-08-24 | 31.637 | 0.01529% | 33.0397 | 34.5045 | 36.0342 | 37.6318 | 0 | 0 | 0 | 0.56864
2031-08-24 01:00 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-08-24 02:00 | 29.2984 | 0.01416% | 30.5974 | 31.9539 | 33.3706 | 34.8501 | 0 | 0 | 0 | 0
2031-08-24 03:00 | 27.4196 | 0.01325% | 28.6353 | 29.9048 | 31.2307 | 32.6153 | 0 | 0 | 0 | 0
2031-08-24 04:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-08-24 05:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-08-24 06:00 | 20.3512 | 0.009835% | 21.2535 | 22.1958 | 23.1798 | 24.2075 | 0 | 0 | 0 | 0
2031-08-24 07:00 | 18.9191 | 0.009143% | 19.7579 | 20.6339 | 21.5487 | 22.5041 | 0 | 0 | 0 | 0
2031-08-24 08:00 | 17.8812 | 0.008641% | 18.674 | 19.5019 | 20.3665 | 21.2695 | 0 | 0 | 0 | 0
2031-08-24 09:00 | 16.9484 | 0.008191% | 17.6998 | 18.4845 | 19.3041 | 20.1599 | 0 | 0 | 0 | 0
2031-08-24 10:00 | 16.7645 | 0.008102% | 17.5077 | 18.2839 | 19.0946 | 19.9411 | 0 | 0 | 0 | 0
2031-08-24 11:00 | 19.9439 | 0.009638% | 20.8282 | 21.7516 | 22.7159 | 23.7231 | 0 | 0 | 0 | 0
2031-08-24 12:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-08-24 13:00 | 26.3423 | 0.01273% | 27.5102 | 28.7298 | 30.0036 | 31.3338 | 0 | 0 | 0 | 0
2031-08-24 14:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-08-24 15:00 | 31.7159 | 0.01533% | 33.122 | 34.5904 | 36.124 | 37.7256 | 0 | 0 | 0 | 0.65303
2031-08-24 16:00 | 34.0939 | 0.01648% | 35.6054 | 37.184 | 38.8326 | 40.5542 | 0 | 0.16562 | 1.6493 | 3.1988
2031-08-24 17:00 | 34.4749 | 0.01666% | 36.0033 | 37.5996 | 39.2665 | 41.0074 | 0 | 0.5396 | 2.0399 | 3.6067
2031-08-24 18:00 | 35.0661 | 0.01695% | 36.6208 | 38.2444 | 39.9399 | 41.7107 | 0 | 1.1199 | 2.6459 | 4.2396
2031-08-24 19:00 | 36.1566 | 0.01747% | 37.7596 | 39.4337 | 41.182 | 43.0078 | 0.68365 | 2.1903 | 3.7638 | 5.407
2031-08-24 20:00 | 37.1026 | 0.01793% | 38.7475 | 40.4654 | 42.2594 | 44.133 | 1.5728 | 3.1188 | 4.7335 | 6.4197
2031-08-24 21:00 | 37.9434 | 0.01834% | 39.6256 | 41.3824 | 43.2171 | 45.1332 | 2.3631 | 3.9442 | 5.5954 | 7.3199
2031-08-24 22:00 | 37.2471 | 0.018% | 38.8984 | 40.623 | 42.424 | 44.3049 | 1.7086 | 3.2607 | 4.8816 | 6.5744
2031-08-24 23:00 | 35.0136 | 0.01692% | 36.5659 | 38.1871 | 39.8801 | 41.6482 | 0 | 1.0683 | 2.5921 | 4.1834
2031-08-25 | 33.3844 | 0.01613% | 34.8645 | 36.4102 | 38.0245 | 39.7103 | 0 | 0 | 0.92205 | 2.4393
2031-08-25 01:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-08-25 02:00 | 28.8386 | 0.01394% | 30.1171 | 31.4524 | 32.8468 | 34.3031 | 0 | 0 | 0 | 0
2031-08-25 03:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-08-25 04:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-08-25 05:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-08-25 06:00 | 17.5528 | 0.008483% | 18.331 | 19.1437 | 19.9924 | 20.8788 | 0 | 0 | 0 | 0
2031-08-25 07:00 | 16.909 | 0.008172% | 17.6587 | 18.4416 | 19.2592 | 20.113 | 0 | 0 | 0 | 0
2031-08-25 08:00 | 16.2389 | 0.007848% | 16.9589 | 17.7108 | 18.496 | 19.316 | 0 | 0 | 0 | 0
2031-08-25 09:00 | 16.3835 | 0.007918% | 17.1098 | 17.8684 | 18.6606 | 19.4879 | 0 | 0 | 0 | 0
2031-08-25 10:00 | 17.8549 | 0.008629% | 18.6465 | 19.4732 | 20.3366 | 21.2382 | 0 | 0 | 0 | 0
2031-08-25 11:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-08-25 12:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-08-25 13:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-08-25 14:00 | 28.1554 | 0.01361% | 29.4036 | 30.7073 | 32.0687 | 33.4904 | 0 | 0 | 0 | 0
2031-08-25 15:00 | 28.9043 | 0.01397% | 30.1857 | 31.524 | 32.9216 | 34.3812 | 0 | 0 | 0 | 0
2031-08-25 16:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-08-25 17:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-08-25 18:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-08-25 19:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-08-25 20:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-08-25 21:00 | 30.4546 | 0.01472% | 31.8048 | 33.2149 | 34.6874 | 36.2253 | 0 | 0 | 0 | 0
2031-08-25 22:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-08-25 23:00 | 27.8663 | 0.01347% | 29.1018 | 30.392 | 31.7395 | 33.1466 | 0 | 0 | 0 | 0
2031-08-26 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-08-26 01:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-08-26 02:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-08-26 03:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-08-26 04:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-08-26 05:00 | 17.1192 | 0.008273% | 17.8782 | 18.6708 | 19.4986 | 20.3631 | 0 | 0 | 0 | 0
2031-08-26 06:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-08-26 07:00 | 15.0171 | 0.007257% | 15.6829 | 16.3782 | 17.1043 | 17.8626 | 0 | 0 | 0 | 0
2031-08-26 08:00 | 14.8463 | 0.007175% | 15.5045 | 16.1919 | 16.9098 | 17.6595 | 0 | 0 | 0 | 0
2031-08-26 09:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-08-26 10:00 | 16.9353 | 0.008184% | 17.6861 | 18.4702 | 19.2891 | 20.1443 | 0 | 0 | 0 | 0
2031-08-26 11:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-08-26 12:00 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-08-26 13:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-08-26 14:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-08-26 15:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-08-26 16:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-08-26 17:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-08-26 18:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-08-26 19:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-08-26 20:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-08-26 21:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-08-26 22:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-08-26 23:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-08-27 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-08-27 01:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-08-27 02:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-08-27 03:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-08-27 04:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0
2031-08-27 05:00 | 16.9747 | 0.008203% | 17.7273 | 18.5132 | 19.334 | 20.1912 | 0 | 0 | 0 | 0
2031-08-27 06:00 | 15.5952 | 0.007537% | 16.2866 | 17.0086 | 17.7627 | 18.5502 | 0 | 0 | 0 | 0
2031-08-27 07:00 | 14.9777 | 0.007238% | 15.6417 | 16.3352 | 17.0594 | 17.8157 | 0 | 0 | 0 | 0
2031-08-27 08:00 | 14.6361 | 0.007073% | 15.285 | 15.9626 | 16.6703 | 17.4094 | 0 | 0 | 0 | 0
2031-08-27 09:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-08-27 10:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-08-27 11:00 | 19.4053 | 0.009378% | 20.2656 | 21.1641 | 22.1024 | 23.0823 | 0 | 0 | 0 | 0
2031-08-27 12:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-08-27 13:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-08-27 14:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-08-27 15:00 | 25.3175 | 0.01224% | 26.44 | 27.6122 | 28.8364 | 30.1148 | 0 | 0 | 0 | 0
2031-08-27 16:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-08-27 17:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-08-27 18:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-08-27 19:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-08-27 20:00 | 28.0634 | 0.01356% | 29.3076 | 30.607 | 31.9639 | 33.3811 | 0 | 0 | 0 | 0
2031-08-27 21:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-08-27 22:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-08-27 23:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-08-28 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-08-28 01:00 | 25.9876 | 0.01256% | 27.1397 | 28.343 | 29.5996 | 30.9119 | 0 | 0 | 0 | 0
2031-08-28 02:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-08-28 03:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-08-28 04:00 | 18.525 | 0.008952% | 19.3463 | 20.204 | 21.0998 | 22.0352 | 0 | 0 | 0 | 0
2031-08-28 05:00 | 16.909 | 0.008172% | 17.6587 | 18.4416 | 19.2592 | 20.113 | 0 | 0 | 0 | 0
2031-08-28 06:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-08-28 07:00 | 15.2141 | 0.007352% | 15.8887 | 16.5931 | 17.3288 | 18.097 | 0 | 0 | 0 | 0
2031-08-28 08:00 | 14.9645 | 0.007232% | 15.628 | 16.3208 | 17.0444 | 17.8001 | 0 | 0 | 0 | 0
2031-08-28 09:00 | 15.5426 | 0.007511% | 16.2317 | 16.9513 | 17.7029 | 18.4877 | 0 | 0 | 0 | 0
2031-08-28 10:00 | 17.4082 | 0.008413% | 18.18 | 18.9861 | 19.8278 | 20.7069 | 0 | 0 | 0 | 0
2031-08-28 11:00 | 19.5629 | 0.009454% | 20.4303 | 21.336 | 22.282 | 23.2698 | 0 | 0 | 0 | 0
2031-08-28 12:00 | 21.4943 | 0.01039% | 22.4472 | 23.4424 | 24.4817 | 25.5671 | 0 | 0 | 0 | 0
2031-08-28 13:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-08-28 14:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-08-28 15:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-08-28 16:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-08-28 17:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-08-28 18:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-08-28 19:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-08-28 20:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-08-28 21:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-08-28 22:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-08-28 23:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-08-29 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-08-29 01:00 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-08-29 02:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-08-29 03:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-08-29 04:00 | 18.0126 | 0.008705% | 18.8112 | 19.6452 | 20.5162 | 21.4258 | 0 | 0 | 0 | 0
2031-08-29 05:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-08-29 06:00 | 15.3455 | 0.007416% | 16.0259 | 16.7364 | 17.4784 | 18.2533 | 0 | 0 | 0 | 0
2031-08-29 07:00 | 14.6886 | 0.007098% | 15.3398 | 16.0199 | 16.7302 | 17.4719 | 0 | 0 | 0 | 0
2031-08-29 08:00 | 14.4521 | 0.006984% | 15.0929 | 15.762 | 16.4608 | 17.1906 | 0 | 0 | 0 | 0
2031-08-29 09:00 | 15.1222 | 0.007308% | 15.7926 | 16.4928 | 17.224 | 17.9876 | 0 | 0 | 0 | 0
2031-08-29 10:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-08-29 11:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-08-29 12:00 | 20.8373 | 0.01007% | 21.7612 | 22.726 | 23.7335 | 24.7857 | 0 | 0 | 0 | 0
2031-08-29 13:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-08-29 14:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-08-29 15:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-08-29 16:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-08-29 17:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-08-29 18:00 | 23.1365 | 0.01118% | 24.1623 | 25.2335 | 26.3523 | 27.5206 | 0 | 0 | 0 | 0
2031-08-29 19:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-08-29 20:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-08-29 21:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-08-29 22:00 | 24.5686 | 0.01187% | 25.6579 | 26.7954 | 27.9834 | 29.224 | 0 | 0 | 0 | 0
2031-08-29 23:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-08-30 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-08-30 01:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-08-30 02:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-08-30 03:00 | 19.3133 | 0.009333% | 20.1696 | 21.0638 | 21.9976 | 22.9729 | 0 | 0 | 0 | 0
2031-08-30 04:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-08-30 05:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-08-30 06:00 | 15.0565 | 0.007276% | 15.724 | 16.4211 | 17.1492 | 17.9095 | 0 | 0 | 0 | 0
2031-08-30 07:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-08-30 08:00 | 14.2025 | 0.006864% | 14.8322 | 15.4898 | 16.1765 | 16.8937 | 0 | 0 | 0 | 0
2031-08-30 09:00 | 14.1631 | 0.006845% | 14.791 | 15.4468 | 16.1316 | 16.8468 | 0 | 0 | 0 | 0
2031-08-30 10:00 | 14.4784 | 0.006997% | 15.1203 | 15.7907 | 16.4908 | 17.2219 | 0 | 0 | 0 | 0
2031-08-30 11:00 | 16.0813 | 0.007772% | 16.7942 | 17.5388 | 18.3164 | 19.1285 | 0 | 0 | 0 | 0
2031-08-30 12:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-08-30 13:00 | 19.8914 | 0.009613% | 20.7733 | 21.6943 | 22.6561 | 23.6605 | 0 | 0 | 0 | 0
2031-08-30 14:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-08-30 15:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-08-30 16:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-08-30 17:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-08-30 18:00 | 22.7161 | 0.01098% | 23.7232 | 24.775 | 25.8734 | 27.0205 | 0 | 0 | 0 | 0
2031-08-30 19:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-08-30 20:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-08-30 21:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-08-30 22:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-08-30 23:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-08-31 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-08-31 01:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-08-31 02:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-08-31 03:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-08-31 04:00 | 17.5659 | 0.008489% | 18.3447 | 19.158 | 20.0074 | 20.8944 | 0 | 0 | 0 | 0
2031-08-31 05:00 | 16.2915 | 0.007873% | 17.0138 | 17.7681 | 18.5558 | 19.3785 | 0 | 0 | 0 | 0
2031-08-31 06:00 | 15.1616 | 0.007327% | 15.8338 | 16.5358 | 17.2689 | 18.0345 | 0 | 0 | 0 | 0
2031-08-31 07:00 | 14.4521 | 0.006984% | 15.0929 | 15.762 | 16.4608 | 17.1906 | 0 | 0 | 0 | 0
2031-08-31 08:00 | 13.9529 | 0.006743% | 14.5715 | 15.2175 | 15.8922 | 16.5968 | 0 | 0 | 0 | 0
2031-08-31 09:00 | 13.8872 | 0.006711% | 14.5029 | 15.1459 | 15.8174 | 16.5186 | 0 | 0 | 0 | 0
2031-08-31 10:00 | 14.0711 | 0.0068% | 14.695 | 15.3465 | 16.0269 | 16.7374 | 0 | 0 | 0 | 0
2031-08-31 11:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-08-31 12:00 | 17.9206 | 0.00866% | 18.7152 | 19.5449 | 20.4114 | 21.3164 | 0 | 0 | 0 | 0
2031-08-31 13:00 | 19.7994 | 0.009568% | 20.6772 | 21.594 | 22.5513 | 23.5511 | 0 | 0 | 0 | 0
2031-08-31 14:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-08-31 15:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-08-31 16:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-08-31 17:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-08-31 18:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-08-31 19:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-08-31 20:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-08-31 21:00 | 27.9452 | 0.0135% | 29.1841 | 30.478 | 31.8292 | 33.2404 | 0 | 0 | 0 | 0
2031-08-31 22:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-08-31 23:00 | 26.6313 | 0.01287% | 27.812 | 29.0451 | 30.3328 | 31.6776 | 0 | 0 | 0 | 0
2031-09-01 | 25.3044 | 0.01223% | 26.4262 | 27.5978 | 28.8214 | 30.0992 | 0 | 0 | 0 | 0
2031-09-01 01:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-09-01 02:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-09-01 03:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-09-01 04:00 | 18.525 | 0.008952% | 19.3463 | 20.204 | 21.0998 | 22.0352 | 0 | 0 | 0 | 0
2031-09-01 05:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-09-01 06:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-09-01 07:00 | 14.6755 | 0.007092% | 15.3261 | 16.0056 | 16.7152 | 17.4563 | 0 | 0 | 0 | 0
2031-09-01 08:00 | 14.2813 | 0.006902% | 14.9145 | 15.5757 | 16.2663 | 16.9875 | 0 | 0 | 0 | 0
2031-09-01 09:00 | 14.347 | 0.006933% | 14.9831 | 15.6474 | 16.3411 | 17.0656 | 0 | 0 | 0 | 0
2031-09-01 10:00 | 14.6886 | 0.007098% | 15.3398 | 16.0199 | 16.7302 | 17.4719 | 0 | 0 | 0 | 0
2031-09-01 11:00 | 16.436 | 0.007943% | 17.1647 | 17.9257 | 18.7204 | 19.5504 | 0 | 0 | 0 | 0
2031-09-01 12:00 | 18.906 | 0.009137% | 19.7442 | 20.6196 | 21.5337 | 22.4885 | 0 | 0 | 0 | 0
2031-09-01 13:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-09-01 14:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-09-01 15:00 | 26.6051 | 0.01286% | 27.7846 | 29.0164 | 30.3029 | 31.6464 | 0 | 0 | 0 | 0
2031-09-01 16:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-09-01 17:00 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-09-01 18:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-09-01 19:00 | 30.7699 | 0.01487% | 32.1341 | 33.5588 | 35.0466 | 36.6004 | 0 | 0 | 0 | 0
2031-09-01 20:00 | 33.1742 | 0.01603% | 34.645 | 36.181 | 37.7851 | 39.4603 | 0 | 0 | 0.70656 | 2.2143
2031-09-01 21:00 | 34.1333 | 0.0165% | 35.6466 | 37.227 | 38.8775 | 40.6011 | 0 | 0.2043 | 1.6897 | 3.241
2031-09-01 22:00 | 33.345 | 0.01611% | 34.8234 | 36.3673 | 37.9796 | 39.6634 | 0 | 0 | 0.88165 | 2.3971
2031-09-01 23:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-09-02 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-09-02 01:00 | 28.4838 | 0.01377% | 29.7467 | 31.0655 | 32.4428 | 33.8811 | 0 | 0 | 0 | 0
2031-09-02 02:00 | 24.9628 | 0.01206% | 26.0695 | 27.2253 | 28.4323 | 29.6929 | 0 | 0 | 0 | 0
2031-09-02 03:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-09-02 04:00 | 18.5119 | 0.008946% | 19.3326 | 20.1897 | 21.0848 | 22.0196 | 0 | 0 | 0 | 0
2031-09-02 05:00 | 16.5543 | 0.008% | 17.2882 | 18.0547 | 18.8551 | 19.6911 | 0 | 0 | 0 | 0
2031-09-02 06:00 | 15.3849 | 0.007435% | 16.067 | 16.7794 | 17.5233 | 18.3002 | 0 | 0 | 0 | 0
2031-09-02 07:00 | 14.531 | 0.007022% | 15.1752 | 15.848 | 16.5506 | 17.2844 | 0 | 0 | 0 | 0
2031-09-02 08:00 | 14.3602 | 0.00694% | 14.9968 | 15.6617 | 16.3561 | 17.0812 | 0 | 0 | 0 | 0
2031-09-02 09:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-09-02 10:00 | 18.052 | 0.008724% | 18.8524 | 19.6882 | 20.5611 | 21.4726 | 0 | 0 | 0 | 0
2031-09-02 11:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-09-02 12:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-09-02 13:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-09-02 14:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-09-02 15:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-09-02 16:00 | 26.789 | 0.01295% | 27.9767 | 29.217 | 30.5124 | 31.8652 | 0 | 0 | 0 | 0
2031-09-02 17:00 | 28.1685 | 0.01361% | 29.4174 | 30.7216 | 32.0836 | 33.5061 | 0 | 0 | 0 | 0
2031-09-02 18:00 | 28.9437 | 0.01399% | 30.2269 | 31.567 | 32.9665 | 34.4281 | 0 | 0 | 0 | 0
2031-09-02 19:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-09-02 20:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-09-02 21:00 | 33.3976 | 0.01614% | 34.8782 | 36.4246 | 38.0395 | 39.726 | 0 | 0 | 0.93552 | 2.4534
2031-09-02 22:00 | 33.2136 | 0.01605% | 34.6861 | 36.224 | 37.83 | 39.5072 | 0 | 0 | 0.74697 | 2.2564
2031-09-02 23:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-09-03 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-09-03 01:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-09-03 02:00 | 25.7379 | 0.01244% | 26.879 | 28.0707 | 29.3152 | 30.6149 | 0 | 0 | 0 | 0
2031-09-03 03:00 | 22.1906 | 0.01072% | 23.1744 | 24.2019 | 25.2748 | 26.3954 | 0 | 0 | 0 | 0
2031-09-03 04:00 | 19.2213 | 0.009289% | 20.0735 | 20.9635 | 21.8929 | 22.8635 | 0 | 0 | 0 | 0
2031-09-03 05:00 | 17.29 | 0.008356% | 18.0566 | 18.8571 | 19.6931 | 20.5662 | 0 | 0 | 0 | 0
2031-09-03 06:00 | 15.9893 | 0.007727% | 16.6982 | 17.4385 | 18.2117 | 19.0191 | 0 | 0 | 0 | 0
2031-09-03 07:00 | 15.2798 | 0.007384% | 15.9573 | 16.6647 | 17.4036 | 18.1752 | 0 | 0 | 0 | 0
2031-09-03 08:00 | 14.8988 | 0.0072% | 15.5594 | 16.2492 | 16.9696 | 17.722 | 0 | 0 | 0 | 0
2031-09-03 09:00 | 15.8448 | 0.007657% | 16.5473 | 17.2809 | 18.047 | 18.8472 | 0 | 0 | 0 | 0
2031-09-03 10:00 | 18.1571 | 0.008775% | 18.9621 | 19.8028 | 20.6808 | 21.5977 | 0 | 0 | 0 | 0
2031-09-03 11:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-09-03 12:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-09-03 13:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-09-03 14:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-09-03 15:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-09-03 16:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-09-03 17:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-09-03 18:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-09-03 19:00 | 31.3348 | 0.01514% | 32.7241 | 34.1749 | 35.6901 | 37.2724 | 0 | 0 | 0 | 0.24514
2031-09-03 20:00 | 33.0822 | 0.01599% | 34.5489 | 36.0807 | 37.6803 | 39.3509 | 0 | 0 | 0.61229 | 2.1158
2031-09-03 21:00 | 34.2515 | 0.01655% | 35.7701 | 37.356 | 39.0122 | 40.7418 | 0 | 0.32037 | 1.8109 | 3.3676
2031-09-03 22:00 | 33.8048 | 0.01634% | 35.3036 | 36.8688 | 38.5034 | 40.2104 | 0 | 0 | 1.353 | 2.8894
2031-09-03 23:00 | 31.5845 | 0.01526% | 32.9848 | 34.4472 | 35.9744 | 37.5693 | 0 | 0 | 0 | 0.51238
2031-09-04 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-09-04 01:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-09-04 02:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-09-04 03:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-09-04 04:00 | 20.8899 | 0.0101% | 21.8161 | 22.7833 | 23.7934 | 24.8483 | 0 | 0 | 0 | 0
2031-09-04 05:00 | 18.6958 | 0.009035% | 19.5247 | 20.3903 | 21.2943 | 22.2384 | 0 | 0 | 0 | 0
2031-09-04 06:00 | 17.0272 | 0.008229% | 17.7821 | 18.5705 | 19.3938 | 20.2537 | 0 | 0 | 0 | 0
2031-09-04 07:00 | 16.3309 | 0.007892% | 17.0549 | 17.8111 | 18.6007 | 19.4254 | 0 | 0 | 0 | 0
2031-09-04 08:00 | 15.6871 | 0.007581% | 16.3826 | 17.1089 | 17.8675 | 18.6596 | 0 | 0 | 0 | 0
2031-09-04 09:00 | 16.6725 | 0.008057% | 17.4117 | 18.1836 | 18.9898 | 19.8317 | 0 | 0 | 0 | 0
2031-09-04 10:00 | 19.8257 | 0.009581% | 20.7047 | 21.6226 | 22.5813 | 23.5824 | 0 | 0 | 0 | 0
2031-09-04 11:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-09-04 12:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-09-04 13:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-09-04 14:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-09-04 15:00 | 24.792 | 0.01198% | 25.8911 | 27.039 | 28.2378 | 29.4897 | 0 | 0 | 0 | 0
2031-09-04 16:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-09-04 17:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-09-04 18:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-09-04 19:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-09-04 20:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-09-04 21:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-09-04 22:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-09-04 23:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-09-05 | 25.6854 | 0.01241% | 26.8241 | 28.0134 | 29.2554 | 30.5524 | 0 | 0 | 0 | 0
2031-09-05 01:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-09-05 02:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-09-05 03:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-09-05 04:00 | 17.9075 | 0.008654% | 18.7014 | 19.5306 | 20.3965 | 21.3007 | 0 | 0 | 0 | 0
2031-09-05 05:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-09-05 06:00 | 15.3061 | 0.007397% | 15.9847 | 16.6934 | 17.4335 | 18.2064 | 0 | 0 | 0 | 0
2031-09-05 07:00 | 14.8463 | 0.007175% | 15.5045 | 16.1919 | 16.9098 | 17.6595 | 0 | 0 | 0 | 0
2031-09-05 08:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-09-05 09:00 | 15.4112 | 0.007448% | 16.0945 | 16.808 | 17.5532 | 18.3314 | 0 | 0 | 0 | 0
2031-09-05 10:00 | 18.1834 | 0.008787% | 18.9896 | 19.8315 | 20.7107 | 21.6289 | 0 | 0 | 0 | 0
2031-09-05 11:00 | 20.9687 | 0.01013% | 21.8984 | 22.8692 | 23.8832 | 24.942 | 0 | 0 | 0 | 0
2031-09-05 12:00 | 21.4943 | 0.01039% | 22.4472 | 23.4424 | 24.4817 | 25.5671 | 0 | 0 | 0 | 0
2031-09-05 13:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-09-05 14:00 | 23.7146 | 0.01146% | 24.766 | 25.864 | 27.0107 | 28.2082 | 0 | 0 | 0 | 0
2031-09-05 15:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-09-05 16:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-09-05 17:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-09-05 18:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-09-05 19:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-09-05 20:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-09-05 21:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-09-05 22:00 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-09-05 23:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-09-06 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-09-06 01:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-09-06 02:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-09-06 03:00 | 20.0096 | 0.00967% | 20.8968 | 21.8232 | 22.7908 | 23.8012 | 0 | 0 | 0 | 0
2031-09-06 04:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-09-06 05:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-09-06 06:00 | 15.0171 | 0.007257% | 15.6829 | 16.3782 | 17.1043 | 17.8626 | 0 | 0 | 0 | 0
2031-09-06 07:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-09-06 08:00 | 14.1631 | 0.006845% | 14.791 | 15.4468 | 16.1316 | 16.8468 | 0 | 0 | 0 | 0
2031-09-06 09:00 | 14.2156 | 0.00687% | 14.8459 | 15.5041 | 16.1915 | 16.9093 | 0 | 0 | 0 | 0
2031-09-06 10:00 | 14.8463 | 0.007175% | 15.5045 | 16.1919 | 16.9098 | 17.6595 | 0 | 0 | 0 | 0
2031-09-06 11:00 | 16.7776 | 0.008108% | 17.5214 | 18.2983 | 19.1095 | 19.9567 | 0 | 0 | 0 | 0
2031-09-06 12:00 | 18.8272 | 0.009099% | 19.6619 | 20.5336 | 21.444 | 22.3947 | 0 | 0 | 0 | 0
2031-09-06 13:00 | 20.2067 | 0.009765% | 21.1026 | 22.0382 | 23.0152 | 24.0356 | 0 | 0 | 0 | 0
2031-09-06 14:00 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-09-06 15:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-09-06 16:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-09-06 17:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-09-06 18:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-09-06 19:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-09-06 20:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-09-06 21:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-09-06 22:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-09-06 23:00 | 22.7161 | 0.01098% | 23.7232 | 24.775 | 25.8734 | 27.0205 | 0 | 0 | 0 | 0
2031-09-07 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-09-07 01:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-09-07 02:00 | 20.6009 | 0.009956% | 21.5142 | 22.468 | 23.4642 | 24.5044 | 0 | 0 | 0 | 0
2031-09-07 03:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-09-07 04:00 | 17.4082 | 0.008413% | 18.18 | 18.9861 | 19.8278 | 20.7069 | 0 | 0 | 0 | 0
2031-09-07 05:00 | 15.9893 | 0.007727% | 16.6982 | 17.4385 | 18.2117 | 19.0191 | 0 | 0 | 0 | 0
2031-09-07 06:00 | 14.9908 | 0.007245% | 15.6554 | 16.3495 | 17.0744 | 17.8314 | 0 | 0 | 0 | 0
2031-09-07 07:00 | 14.3339 | 0.006927% | 14.9694 | 15.633 | 16.3261 | 17.05 | 0 | 0 | 0 | 0
2031-09-07 08:00 | 13.9529 | 0.006743% | 14.5715 | 15.2175 | 15.8922 | 16.5968 | 0 | 0 | 0 | 0
2031-09-07 09:00 | 13.9266 | 0.00673% | 14.544 | 15.1888 | 15.8622 | 16.5655 | 0 | 0 | 0 | 0
2031-09-07 10:00 | 14.1237 | 0.006825% | 14.7498 | 15.4038 | 16.0867 | 16.7999 | 0 | 0 | 0 | 0
2031-09-07 11:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-09-07 12:00 | 17.9338 | 0.008667% | 18.7289 | 19.5592 | 20.4264 | 21.332 | 0 | 0 | 0 | 0
2031-09-07 13:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-09-07 14:00 | 21.3497 | 0.01032% | 22.2963 | 23.2848 | 24.3171 | 25.3952 | 0 | 0 | 0 | 0
2031-09-07 15:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-09-07 16:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-09-07 17:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-09-07 18:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-09-07 19:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-09-07 20:00 | 25.3438 | 0.01225% | 26.4674 | 27.6408 | 28.8663 | 30.1461 | 0 | 0 | 0 | 0
2031-09-07 21:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-09-07 22:00 | 26.1189 | 0.01262% | 27.2769 | 28.4863 | 29.7492 | 31.0681 | 0 | 0 | 0 | 0
2031-09-07 23:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-09-08 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-09-08 01:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-09-08 02:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-09-08 03:00 | 18.906 | 0.009137% | 19.7442 | 20.6196 | 21.5337 | 22.4885 | 0 | 0 | 0 | 0
2031-09-08 04:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-09-08 05:00 | 15.4506 | 0.007467% | 16.1356 | 16.851 | 17.5981 | 18.3783 | 0 | 0 | 0 | 0
2031-09-08 06:00 | 14.4784 | 0.006997% | 15.1203 | 15.7907 | 16.4908 | 17.2219 | 0 | 0 | 0 | 0
2031-09-08 07:00 | 14.058 | 0.006794% | 14.6812 | 15.3321 | 16.0119 | 16.7218 | 0 | 0 | 0 | 0
2031-09-08 08:00 | 14.0054 | 0.006768% | 14.6264 | 15.2748 | 15.952 | 16.6593 | 0 | 0 | 0 | 0
2031-09-08 09:00 | 15.0828 | 0.007289% | 15.7515 | 16.4498 | 17.1791 | 17.9408 | 0 | 0 | 0 | 0
2031-09-08 10:00 | 17.5659 | 0.008489% | 18.3447 | 19.158 | 20.0074 | 20.8944 | 0 | 0 | 0 | 0
2031-09-08 11:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-09-08 12:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-09-08 13:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-09-08 14:00 | 21.7176 | 0.0105% | 22.6805 | 23.686 | 24.7361 | 25.8328 | 0 | 0 | 0 | 0
2031-09-08 15:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-09-08 16:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-09-08 17:00 | 22.0855 | 0.01067% | 23.0646 | 24.0872 | 25.1551 | 26.2704 | 0 | 0 | 0 | 0
2031-09-08 18:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-09-08 19:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-09-08 20:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-09-08 21:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-09-08 22:00 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-09-08 23:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-09-09 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-09-09 01:00 | 24.2664 | 0.01173% | 25.3423 | 26.4658 | 27.6392 | 28.8646 | 0 | 0 | 0 | 0
2031-09-09 02:00 | 21.6913 | 0.01048% | 22.653 | 23.6573 | 24.7062 | 25.8016 | 0 | 0 | 0 | 0
2031-09-09 03:00 | 19.1294 | 0.009245% | 19.9775 | 20.8632 | 21.7881 | 22.7541 | 0 | 0 | 0 | 0
2031-09-09 04:00 | 17.1586 | 0.008292% | 17.9193 | 18.7138 | 19.5435 | 20.41 | 0 | 0 | 0 | 0
2031-09-09 05:00 | 15.5557 | 0.007518% | 16.2454 | 16.9657 | 17.7178 | 18.5034 | 0 | 0 | 0 | 0
2031-09-09 06:00 | 14.8857 | 0.007194% | 15.5457 | 16.2349 | 16.9546 | 17.7063 | 0 | 0 | 0 | 0
2031-09-09 07:00 | 14.347 | 0.006933% | 14.9831 | 15.6474 | 16.3411 | 17.0656 | 0 | 0 | 0 | 0
2031-09-09 08:00 | 14.2025 | 0.006864% | 14.8322 | 15.4898 | 16.1765 | 16.8937 | 0 | 0 | 0 | 0
2031-09-09 09:00 | 15.4112 | 0.007448% | 16.0945 | 16.808 | 17.5532 | 18.3314 | 0 | 0 | 0 | 0
2031-09-09 10:00 | 18.0126 | 0.008705% | 18.8112 | 19.6452 | 20.5162 | 21.4258 | 0 | 0 | 0 | 0
2031-09-09 11:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-09-09 12:00 | 20.7191 | 0.01001% | 21.6377 | 22.597 | 23.5988 | 24.6451 | 0 | 0 | 0 | 0
2031-09-09 13:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-09-09 14:00 | 21.757 | 0.01051% | 22.7216 | 23.729 | 24.781 | 25.8797 | 0 | 0 | 0 | 0
2031-09-09 15:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-09-09 16:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-09-09 17:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-09-09 18:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-09-09 19:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-09-09 20:00 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-09-09 21:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-09-09 22:00 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-09-09 23:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-09-10 | 25.5277 | 0.01234% | 26.6595 | 27.8414 | 29.0758 | 30.3649 | 0 | 0 | 0 | 0
2031-09-10 01:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-09-10 02:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-09-10 03:00 | 19.76 | 0.009549% | 20.6361 | 21.551 | 22.5064 | 23.5043 | 0 | 0 | 0 | 0
2031-09-10 04:00 | 17.0929 | 0.00826% | 17.8507 | 18.6422 | 19.4687 | 20.3318 | 0 | 0 | 0 | 0
2031-09-10 05:00 | 15.8711 | 0.00767% | 16.5747 | 17.3096 | 18.077 | 18.8784 | 0 | 0 | 0 | 0
2031-09-10 06:00 | 14.9777 | 0.007238% | 15.6417 | 16.3352 | 17.0594 | 17.8157 | 0 | 0 | 0 | 0
2031-09-10 07:00 | 14.2419 | 0.006883% | 14.8733 | 15.5327 | 16.2214 | 16.9406 | 0 | 0 | 0 | 0
2031-09-10 08:00 | 14.2288 | 0.006876% | 14.8596 | 15.5184 | 16.2064 | 16.9249 | 0 | 0 | 0 | 0
2031-09-10 09:00 | 15.4112 | 0.007448% | 16.0945 | 16.808 | 17.5532 | 18.3314 | 0 | 0 | 0 | 0
2031-09-10 10:00 | 18.1571 | 0.008775% | 18.9621 | 19.8028 | 20.6808 | 21.5977 | 0 | 0 | 0 | 0
2031-09-10 11:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-09-10 12:00 | 21.3629 | 0.01032% | 22.31 | 23.2991 | 24.3321 | 25.4109 | 0 | 0 | 0 | 0
2031-09-10 13:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-09-10 14:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-09-10 15:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-09-10 16:00 | 24.9628 | 0.01206% | 26.0695 | 27.2253 | 28.4323 | 29.6929 | 0 | 0 | 0 | 0
2031-09-10 17:00 | 25.554 | 0.01235% | 26.6869 | 27.8701 | 29.1057 | 30.3961 | 0 | 0 | 0 | 0
2031-09-10 18:00 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-09-10 19:00 | 27.2226 | 0.01316% | 28.4295 | 29.6899 | 31.0062 | 32.3809 | 0 | 0 | 0 | 0
2031-09-10 20:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-09-10 21:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-09-10 22:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-09-10 23:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-09-11 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-09-11 01:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-09-11 02:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-09-11 03:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-09-11 04:00 | 18.2622 | 0.008825% | 19.0719 | 19.9175 | 20.8005 | 21.7227 | 0 | 0 | 0 | 0
2031-09-11 05:00 | 16.6988 | 0.00807% | 17.4391 | 18.2123 | 19.0197 | 19.863 | 0 | 0 | 0 | 0
2031-09-11 06:00 | 15.5295 | 0.007505% | 16.218 | 16.937 | 17.6879 | 18.4721 | 0 | 0 | 0 | 0
2031-09-11 07:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-09-11 08:00 | 14.6755 | 0.007092% | 15.3261 | 16.0056 | 16.7152 | 17.4563 | 0 | 0 | 0 | 0
2031-09-11 09:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-09-11 10:00 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-09-11 11:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-09-11 12:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-09-11 13:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-09-11 14:00 | 25.0547 | 0.01211% | 26.1655 | 27.3256 | 28.5371 | 29.8023 | 0 | 0 | 0 | 0
2031-09-11 15:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-09-11 16:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-09-11 17:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-09-11 18:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-09-11 19:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-09-11 20:00 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-09-11 21:00 | 30.6516 | 0.01481% | 32.0106 | 33.4298 | 34.9119 | 36.4597 | 0 | 0 | 0 | 0
2031-09-11 22:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-09-11 23:00 | 28.6152 | 0.01383% | 29.8839 | 31.2088 | 32.5924 | 34.0374 | 0 | 0 | 0 | 0
2031-09-12 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-09-12 01:00 | 27.3934 | 0.01324% | 28.6078 | 29.8762 | 31.2007 | 32.584 | 0 | 0 | 0 | 0
2031-09-12 02:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-09-12 03:00 | 21.7833 | 0.01053% | 22.7491 | 23.7576 | 24.8109 | 25.9109 | 0 | 0 | 0 | 0
2031-09-12 04:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-09-12 05:00 | 17.0141 | 0.008222% | 17.7684 | 18.5562 | 19.3789 | 20.238 | 0 | 0 | 0 | 0
2031-09-12 06:00 | 16.0419 | 0.007752% | 16.7531 | 17.4958 | 18.2715 | 19.0816 | 0 | 0 | 0 | 0
2031-09-12 07:00 | 15.1616 | 0.007327% | 15.8338 | 16.5358 | 17.2689 | 18.0345 | 0 | 0 | 0 | 0
2031-09-12 08:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-09-12 09:00 | 15.674 | 0.007575% | 16.3689 | 17.0946 | 17.8525 | 18.644 | 0 | 0 | 0 | 0
2031-09-12 10:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-09-12 11:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-09-12 12:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-09-12 13:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-09-12 14:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-09-12 15:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-09-12 16:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-09-12 17:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-09-12 18:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-09-12 19:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-09-12 20:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-09-12 21:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-09-12 22:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-09-12 23:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-09-13 | 27.1174 | 0.0131% | 28.3197 | 29.5753 | 30.8865 | 32.2558 | 0 | 0 | 0 | 0
2031-09-13 01:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-09-13 02:00 | 23.6884 | 0.01145% | 24.7386 | 25.8354 | 26.9808 | 28.177 | 0 | 0 | 0 | 0
2031-09-13 03:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-09-13 04:00 | 18.8272 | 0.009099% | 19.6619 | 20.5336 | 21.444 | 22.3947 | 0 | 0 | 0 | 0
2031-09-13 05:00 | 16.9615 | 0.008197% | 17.7135 | 18.4989 | 19.319 | 20.1755 | 0 | 0 | 0 | 0
2031-09-13 06:00 | 15.6083 | 0.007543% | 16.3003 | 17.023 | 17.7777 | 18.5659 | 0 | 0 | 0 | 0
2031-09-13 07:00 | 15.0696 | 0.007283% | 15.7377 | 16.4355 | 17.1641 | 17.9251 | 0 | 0 | 0 | 0
2031-09-13 08:00 | 14.6098 | 0.00706% | 15.2575 | 15.934 | 16.6404 | 17.3782 | 0 | 0 | 0 | 0
2031-09-13 09:00 | 14.6098 | 0.00706% | 15.2575 | 15.934 | 16.6404 | 17.3782 | 0 | 0 | 0 | 0
2031-09-13 10:00 | 15.293 | 0.007391% | 15.971 | 16.6791 | 17.4185 | 18.1908 | 0 | 0 | 0 | 0
2031-09-13 11:00 | 17.198 | 0.008311% | 17.9605 | 18.7568 | 19.5884 | 20.4568 | 0 | 0 | 0 | 0
2031-09-13 12:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-09-13 13:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-09-13 14:00 | 22.4928 | 0.01087% | 23.49 | 24.5314 | 25.619 | 26.7549 | 0 | 0 | 0 | 0
2031-09-13 15:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-09-13 16:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-09-13 17:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-09-13 18:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-09-13 19:00 | 24.1351 | 0.01166% | 25.2051 | 26.3226 | 27.4896 | 28.7083 | 0 | 0 | 0 | 0
2031-09-13 20:00 | 24.792 | 0.01198% | 25.8911 | 27.039 | 28.2378 | 29.4897 | 0 | 0 | 0 | 0
2031-09-13 21:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-09-13 22:00 | 25.6722 | 0.01241% | 26.8104 | 27.9991 | 29.2404 | 30.5368 | 0 | 0 | 0 | 0
2031-09-13 23:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-09-14 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-09-14 01:00 | 24.1613 | 0.01168% | 25.2325 | 26.3512 | 27.5195 | 28.7396 | 0 | 0 | 0 | 0
2031-09-14 02:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-09-14 03:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-09-14 04:00 | 18.5644 | 0.008972% | 19.3875 | 20.247 | 21.1447 | 22.0821 | 0 | 0 | 0 | 0
2031-09-14 05:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-09-14 06:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-09-14 07:00 | 14.8069 | 0.007156% | 15.4633 | 16.1489 | 16.8649 | 17.6126 | 0 | 0 | 0 | 0
2031-09-14 08:00 | 14.2813 | 0.006902% | 14.9145 | 15.5757 | 16.2663 | 16.9875 | 0 | 0 | 0 | 0
2031-09-14 09:00 | 14.058 | 0.006794% | 14.6812 | 15.3321 | 16.0119 | 16.7218 | 0 | 0 | 0 | 0
2031-09-14 10:00 | 14.4784 | 0.006997% | 15.1203 | 15.7907 | 16.4908 | 17.2219 | 0 | 0 | 0 | 0
2031-09-14 11:00 | 16.1732 | 0.007816% | 16.8903 | 17.6391 | 18.4212 | 19.2379 | 0 | 0 | 0 | 0
2031-09-14 12:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-09-14 13:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-09-14 14:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-09-14 15:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-09-14 16:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-09-14 17:00 | 29.4429 | 0.01423% | 30.7483 | 32.1115 | 33.5352 | 35.022 | 0 | 0 | 0 | 0
2031-09-14 18:00 | 30.1787 | 0.01458% | 31.5166 | 32.9139 | 34.3732 | 35.8971 | 0 | 0 | 0 | 0
2031-09-14 19:00 | 30.586 | 0.01478% | 31.942 | 33.3581 | 34.8371 | 36.3816 | 0 | 0 | 0 | 0
2031-09-14 20:00 | 31.729 | 0.01533% | 33.1357 | 34.6048 | 36.139 | 37.7412 | 0 | 0 | 0 | 0.6671
2031-09-14 21:00 | 33.2793 | 0.01608% | 34.7548 | 36.2956 | 37.9048 | 39.5853 | 0 | 0 | 0.81431 | 2.3268
2031-09-14 22:00 | 33.4107 | 0.01615% | 34.892 | 36.4389 | 38.0544 | 39.7416 | 0 | 0 | 0.94899 | 2.4674
2031-09-14 23:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-09-15 | 30.9932 | 0.01498% | 32.3673 | 33.8023 | 35.301 | 36.8661 | 0 | 0 | 0 | 0
2031-09-15 01:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-09-15 02:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-09-15 03:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-09-15 04:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-09-15 05:00 | 16.7513 | 0.008095% | 17.494 | 18.2696 | 19.0796 | 19.9255 | 0 | 0 | 0 | 0
2031-09-15 06:00 | 15.8316 | 0.007651% | 16.5335 | 17.2666 | 18.0321 | 18.8315 | 0 | 0 | 0 | 0
2031-09-15 07:00 | 14.9251 | 0.007213% | 15.5868 | 16.2779 | 16.9995 | 17.7532 | 0 | 0 | 0 | 0
2031-09-15 08:00 | 14.9251 | 0.007213% | 15.5868 | 16.2779 | 16.9995 | 17.7532 | 0 | 0 | 0 | 0
2031-09-15 09:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-09-15 10:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-09-15 11:00 | 21.0081 | 0.01015% | 21.9395 | 22.9122 | 23.9281 | 24.9889 | 0 | 0 | 0 | 0
2031-09-15 12:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-09-15 13:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-09-15 14:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-09-15 15:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-09-15 16:00 | 27.2751 | 0.01318% | 28.4844 | 29.7472 | 31.0661 | 32.4434 | 0 | 0 | 0 | 0
2031-09-15 17:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-09-15 18:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-09-15 19:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-09-15 20:00 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-09-15 21:00 | 32.3465 | 0.01563% | 33.7806 | 35.2782 | 36.8423 | 38.4757 | 0 | 0 | 0 | 1.3282
2031-09-15 22:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-09-15 23:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-09-16 | 29.0356 | 0.01403% | 30.3229 | 31.6673 | 33.0713 | 34.5375 | 0 | 0 | 0 | 0
2031-09-16 01:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-09-16 02:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-09-16 03:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-09-16 04:00 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-09-16 05:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-09-16 06:00 | 15.6477 | 0.007562% | 16.3415 | 17.066 | 17.8226 | 18.6127 | 0 | 0 | 0 | 0
2031-09-16 07:00 | 14.9908 | 0.007245% | 15.6554 | 16.3495 | 17.0744 | 17.8314 | 0 | 0 | 0 | 0
2031-09-16 08:00 | 14.6623 | 0.007086% | 15.3124 | 15.9913 | 16.7003 | 17.4407 | 0 | 0 | 0 | 0
2031-09-16 09:00 | 15.674 | 0.007575% | 16.3689 | 17.0946 | 17.8525 | 18.644 | 0 | 0 | 0 | 0
2031-09-16 10:00 | 18.1177 | 0.008756% | 18.921 | 19.7598 | 20.6359 | 21.5508 | 0 | 0 | 0 | 0
2031-09-16 11:00 | 21.0081 | 0.01015% | 21.9395 | 22.9122 | 23.9281 | 24.9889 | 0 | 0 | 0 | 0
2031-09-16 12:00 | 22.4665 | 0.01086% | 23.4625 | 24.5028 | 25.5891 | 26.7236 | 0 | 0 | 0 | 0
2031-09-16 13:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-09-16 14:00 | 26.0007 | 0.01257% | 27.1534 | 28.3573 | 29.6145 | 30.9275 | 0 | 0 | 0 | 0
2031-09-16 15:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-09-16 16:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-09-16 17:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-09-16 18:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-09-16 19:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-09-16 20:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-09-16 21:00 | 32.7144 | 0.01581% | 34.1648 | 35.6795 | 37.2613 | 38.9133 | 0 | 0 | 0.23519 | 1.722
2031-09-16 22:00 | 32.1626 | 0.01554% | 33.5885 | 35.0776 | 36.6328 | 38.2569 | 0 | 0 | 0 | 1.1312
2031-09-16 23:00 | 30.1655 | 0.01458% | 31.5029 | 32.8996 | 34.3582 | 35.8815 | 0 | 0 | 0 | 0
2031-09-17 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-09-17 01:00 | 27.8006 | 0.01344% | 29.0332 | 30.3204 | 31.6646 | 33.0685 | 0 | 0 | 0 | 0
2031-09-17 02:00 | 25.0547 | 0.01211% | 26.1655 | 27.3256 | 28.5371 | 29.8023 | 0 | 0 | 0 | 0
2031-09-17 03:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-09-17 04:00 | 18.8666 | 0.009118% | 19.7031 | 20.5766 | 21.4889 | 22.4416 | 0 | 0 | 0 | 0
2031-09-17 05:00 | 16.7776 | 0.008108% | 17.5214 | 18.2983 | 19.1095 | 19.9567 | 0 | 0 | 0 | 0
2031-09-17 06:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-09-17 07:00 | 14.8857 | 0.007194% | 15.5457 | 16.2349 | 16.9546 | 17.7063 | 0 | 0 | 0 | 0
2031-09-17 08:00 | 14.8726 | 0.007187% | 15.5319 | 16.2205 | 16.9397 | 17.6907 | 0 | 0 | 0 | 0
2031-09-17 09:00 | 16.055 | 0.007759% | 16.7668 | 17.5102 | 18.2865 | 19.0972 | 0 | 0 | 0 | 0
2031-09-17 10:00 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-09-17 11:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-09-17 12:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-09-17 13:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-09-17 14:00 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-09-17 15:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-09-17 16:00 | 28.5495 | 0.0138% | 29.8153 | 31.1371 | 32.5176 | 33.9593 | 0 | 0 | 0 | 0
2031-09-17 17:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-09-17 18:00 | 30.1655 | 0.01458% | 31.5029 | 32.8996 | 34.3582 | 35.8815 | 0 | 0 | 0 | 0
2031-09-17 19:00 | 31.4399 | 0.01519% | 32.8338 | 34.2895 | 35.8098 | 37.3974 | 0 | 0 | 0 | 0.35767
2031-09-17 20:00 | 31.9261 | 0.01543% | 33.3415 | 34.8197 | 36.3635 | 37.9756 | 0 | 0 | 0 | 0.87807
2031-09-17 21:00 | 32.3465 | 0.01563% | 33.7806 | 35.2782 | 36.8423 | 38.4757 | 0 | 0 | 0 | 1.3282
2031-09-17 22:00 | 31.2166 | 0.01509% | 32.6006 | 34.0459 | 35.5554 | 37.1317 | 0 | 0 | 0 | 0.11856
2031-09-17 23:00 | 29.4692 | 0.01424% | 30.7757 | 32.1402 | 33.5651 | 35.0532 | 0 | 0 | 0 | 0
2031-09-18 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-09-18 01:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-09-18 02:00 | 25.0941 | 0.01213% | 26.2067 | 27.3686 | 28.582 | 29.8492 | 0 | 0 | 0 | 0
2031-09-18 03:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-09-18 04:00 | 19.0505 | 0.009206% | 19.8951 | 20.7772 | 21.6984 | 22.6604 | 0 | 0 | 0 | 0
2031-09-18 05:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-09-18 06:00 | 15.8448 | 0.007657% | 16.5473 | 17.2809 | 18.047 | 18.8472 | 0 | 0 | 0 | 0
2031-09-18 07:00 | 15.0696 | 0.007283% | 15.7377 | 16.4355 | 17.1641 | 17.9251 | 0 | 0 | 0 | 0
2031-09-18 08:00 | 14.8069 | 0.007156% | 15.4633 | 16.1489 | 16.8649 | 17.6126 | 0 | 0 | 0 | 0
2031-09-18 09:00 | 15.9762 | 0.007721% | 16.6845 | 17.4242 | 18.1967 | 19.0034 | 0 | 0 | 0 | 0
2031-09-18 10:00 | 18.814 | 0.009092% | 19.6482 | 20.5193 | 21.429 | 22.3791 | 0 | 0 | 0 | 0
2031-09-18 11:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-09-18 12:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-09-18 13:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-09-18 14:00 | 26.3686 | 0.01274% | 27.5376 | 28.7585 | 30.0335 | 31.3651 | 0 | 0 | 0 | 0
2031-09-18 15:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-09-18 16:00 | 28.5627 | 0.0138% | 29.829 | 31.1515 | 32.5326 | 33.9749 | 0 | 0 | 0 | 0
2031-09-18 17:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-09-18 18:00 | 31.4794 | 0.01521% | 32.875 | 34.3325 | 35.8547 | 37.4443 | 0 | 0 | 0 | 0.39986
2031-09-18 19:00 | 32.4647 | 0.01569% | 33.9041 | 35.4072 | 36.977 | 38.6164 | 0 | 0 | 0 | 1.4547
2031-09-18 20:00 | 33.6866 | 0.01628% | 35.1801 | 36.7398 | 38.3687 | 40.0698 | 0 | 0 | 1.2318 | 2.7628
2031-09-18 21:00 | 34.0282 | 0.01644% | 35.5368 | 37.1124 | 38.7578 | 40.4761 | 0 | 0.10113 | 1.582 | 3.1285
2031-09-18 22:00 | 33.8443 | 0.01636% | 35.3447 | 36.9118 | 38.5483 | 40.2573 | 0 | 0 | 1.3934 | 2.9316
2031-09-18 23:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-09-19 | 32.018 | 0.01547% | 33.4376 | 34.92 | 36.4682 | 38.085 | 0 | 0 | 0 | 0.97653
2031-09-19 01:00 | 30.6911 | 0.01483% | 32.0518 | 33.4728 | 34.9568 | 36.5066 | 0 | 0 | 0 | 0
2031-09-19 02:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-09-19 03:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-09-19 04:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-09-19 05:00 | 18.4724 | 0.008927% | 19.2914 | 20.1467 | 21.0399 | 21.9727 | 0 | 0 | 0 | 0
2031-09-19 06:00 | 16.9615 | 0.008197% | 17.7135 | 18.4989 | 19.319 | 20.1755 | 0 | 0 | 0 | 0
2031-09-19 07:00 | 15.8973 | 0.007683% | 16.6022 | 17.3382 | 18.1069 | 18.9097 | 0 | 0 | 0 | 0
2031-09-19 08:00 | 15.4375 | 0.00746% | 16.1219 | 16.8367 | 17.5832 | 18.3627 | 0 | 0 | 0 | 0
2031-09-19 09:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-09-19 10:00 | 18.5776 | 0.008978% | 19.4012 | 20.2613 | 21.1596 | 22.0978 | 0 | 0 | 0 | 0
2031-09-19 11:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-09-19 12:00 | 22.5059 | 0.01088% | 23.5037 | 24.5457 | 25.634 | 26.7705 | 0 | 0 | 0 | 0
2031-09-19 13:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-09-19 14:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-09-19 15:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-09-19 16:00 | 26.2635 | 0.01269% | 27.4279 | 28.6439 | 29.9138 | 31.24 | 0 | 0 | 0 | 0
2031-09-19 17:00 | 26.7364 | 0.01292% | 27.9218 | 29.1597 | 30.4525 | 31.8026 | 0 | 0 | 0 | 0
2031-09-19 18:00 | 26.6839 | 0.0129% | 27.8669 | 29.1024 | 30.3927 | 31.7401 | 0 | 0 | 0 | 0
2031-09-19 19:00 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-09-19 20:00 | 28.0897 | 0.01357% | 29.335 | 30.6356 | 31.9939 | 33.4123 | 0 | 0 | 0 | 0
2031-09-19 21:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-09-19 22:00 | 27.7612 | 0.01342% | 28.992 | 30.2774 | 31.6197 | 33.0216 | 0 | 0 | 0 | 0
2031-09-19 23:00 | 25.8299 | 0.01248% | 26.9751 | 28.171 | 29.42 | 30.7243 | 0 | 0 | 0 | 0
2031-09-20 | 25.6722 | 0.01241% | 26.8104 | 27.9991 | 29.2404 | 30.5368 | 0 | 0 | 0 | 0
2031-09-20 01:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-09-20 02:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-09-20 03:00 | 20.0885 | 0.009708% | 20.9791 | 21.9092 | 22.8805 | 23.895 | 0 | 0 | 0 | 0
2031-09-20 04:00 | 17.9469 | 0.008673% | 18.7426 | 19.5736 | 20.4413 | 21.3476 | 0 | 0 | 0 | 0
2031-09-20 05:00 | 16.2652 | 0.00786% | 16.9863 | 17.7394 | 18.5259 | 19.3473 | 0 | 0 | 0 | 0
2031-09-20 06:00 | 15.3061 | 0.007397% | 15.9847 | 16.6934 | 17.4335 | 18.2064 | 0 | 0 | 0 | 0
2031-09-20 07:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-09-20 08:00 | 14.0448 | 0.006787% | 14.6675 | 15.3178 | 15.9969 | 16.7062 | 0 | 0 | 0 | 0
2031-09-20 09:00 | 14.4521 | 0.006984% | 15.0929 | 15.762 | 16.4608 | 17.1906 | 0 | 0 | 0 | 0
2031-09-20 10:00 | 15.0302 | 0.007264% | 15.6966 | 16.3925 | 17.1193 | 17.8782 | 0 | 0 | 0 | 0
2031-09-20 11:00 | 16.5674 | 0.008006% | 17.3019 | 18.069 | 18.8701 | 19.7067 | 0 | 0 | 0 | 0
2031-09-20 12:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-09-20 13:00 | 20.2067 | 0.009765% | 21.1026 | 22.0382 | 23.0152 | 24.0356 | 0 | 0 | 0 | 0
2031-09-20 14:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-09-20 15:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-09-20 16:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-09-20 17:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-09-20 18:00 | 22.1643 | 0.01071% | 23.147 | 24.1732 | 25.2449 | 26.3642 | 0 | 0 | 0 | 0
2031-09-20 19:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-09-20 20:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-09-20 21:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-09-20 22:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-09-20 23:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-09-21 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-09-21 01:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-09-21 02:00 | 20.233 | 0.009778% | 21.13 | 22.0668 | 23.0452 | 24.0669 | 0 | 0 | 0 | 0
2031-09-21 03:00 | 18.4068 | 0.008895% | 19.2228 | 20.0751 | 20.9651 | 21.8946 | 0 | 0 | 0 | 0
2031-09-21 04:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-09-21 05:00 | 15.4901 | 0.007486% | 16.1768 | 16.894 | 17.643 | 18.4252 | 0 | 0 | 0 | 0
2031-09-21 06:00 | 14.3996 | 0.006959% | 15.038 | 15.7047 | 16.401 | 17.1281 | 0 | 0 | 0 | 0
2031-09-21 07:00 | 13.8215 | 0.006679% | 14.4343 | 15.0742 | 15.7425 | 16.4405 | 0 | 0 | 0 | 0
2031-09-21 08:00 | 13.6244 | 0.006584% | 14.2285 | 14.8593 | 15.5181 | 16.2061 | 0 | 0 | 0 | 0
2031-09-21 09:00 | 13.6638 | 0.006603% | 14.2696 | 14.9023 | 15.563 | 16.2529 | 0 | 0 | 0 | 0
2031-09-21 10:00 | 14.1894 | 0.006857% | 14.8184 | 15.4754 | 16.1615 | 16.8781 | 0 | 0 | 0 | 0
2031-09-21 11:00 | 15.674 | 0.007575% | 16.3689 | 17.0946 | 17.8525 | 18.644 | 0 | 0 | 0 | 0
2031-09-21 12:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-09-21 13:00 | 19.5235 | 0.009435% | 20.3891 | 21.293 | 22.2371 | 23.223 | 0 | 0 | 0 | 0
2031-09-21 14:00 | 21.1395 | 0.01022% | 22.0767 | 23.0555 | 24.0777 | 25.1452 | 0 | 0 | 0 | 0
2031-09-21 15:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-09-21 16:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-09-21 17:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-09-21 18:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-09-21 19:00 | 27.3671 | 0.01323% | 28.5804 | 29.8475 | 31.1708 | 32.5528 | 0 | 0 | 0 | 0
2031-09-21 20:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-09-21 21:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-09-21 22:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-09-21 23:00 | 28.3787 | 0.01371% | 29.6369 | 30.9509 | 32.3231 | 33.7561 | 0 | 0 | 0 | 0
2031-09-22 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-09-22 01:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-09-22 02:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-09-22 03:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-09-22 04:00 | 18.8535 | 0.009111% | 19.6893 | 20.5623 | 21.4739 | 22.4259 | 0 | 0 | 0 | 0
2031-09-22 05:00 | 16.8959 | 0.008165% | 17.6449 | 18.4272 | 19.2442 | 20.0974 | 0 | 0 | 0 | 0
2031-09-22 06:00 | 15.8185 | 0.007645% | 16.5198 | 17.2522 | 18.0171 | 18.8159 | 0 | 0 | 0 | 0
2031-09-22 07:00 | 15.1616 | 0.007327% | 15.8338 | 16.5358 | 17.2689 | 18.0345 | 0 | 0 | 0 | 0
2031-09-22 08:00 | 14.9777 | 0.007238% | 15.6417 | 16.3352 | 17.0594 | 17.8157 | 0 | 0 | 0 | 0
2031-09-22 09:00 | 16.0681 | 0.007765% | 16.7805 | 17.5245 | 18.3014 | 19.1128 | 0 | 0 | 0 | 0
2031-09-22 10:00 | 18.7221 | 0.009048% | 19.5521 | 20.419 | 21.3242 | 22.2697 | 0 | 0 | 0 | 0
2031-09-22 11:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-09-22 12:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-09-22 13:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-09-22 14:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-09-22 15:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-09-22 16:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-09-22 17:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-09-22 18:00 | 27.2226 | 0.01316% | 28.4295 | 29.6899 | 31.0062 | 32.3809 | 0 | 0 | 0 | 0
2031-09-22 19:00 | 27.4196 | 0.01325% | 28.6353 | 29.9048 | 31.2307 | 32.6153 | 0 | 0 | 0 | 0
2031-09-22 20:00 | 29.9159 | 0.01446% | 31.2422 | 32.6274 | 34.0739 | 35.5846 | 0 | 0 | 0 | 0
2031-09-22 21:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-09-22 22:00 | 30.5334 | 0.01476% | 31.8871 | 33.3008 | 34.7772 | 36.3191 | 0 | 0 | 0 | 0
2031-09-22 23:00 | 29.7057 | 0.01436% | 31.0227 | 32.3981 | 33.8345 | 35.3345 | 0 | 0 | 0 | 0
2031-09-23 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-09-23 01:00 | 28.2736 | 0.01366% | 29.5271 | 30.8362 | 32.2034 | 33.6311 | 0 | 0 | 0 | 0
2031-09-23 02:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-09-23 03:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-09-23 04:00 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0
2031-09-23 05:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-09-23 06:00 | 16.8959 | 0.008165% | 17.6449 | 18.4272 | 19.2442 | 20.0974 | 0 | 0 | 0 | 0
2031-09-23 07:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-09-23 08:00 | 15.963 | 0.007714% | 16.6708 | 17.4099 | 18.1817 | 18.9878 | 0 | 0 | 0 | 0
2031-09-23 09:00 | 17.1849 | 0.008305% | 17.9468 | 18.7425 | 19.5734 | 20.4412 | 0 | 0 | 0 | 0
2031-09-23 10:00 | 19.668 | 0.009505% | 20.54 | 21.4507 | 22.4017 | 23.3949 | 0 | 0 | 0 | 0
2031-09-23 11:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-09-23 12:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-09-23 13:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-09-23 14:00 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-09-23 15:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-09-23 16:00 | 29.1539 | 0.01409% | 30.4464 | 31.7963 | 33.206 | 34.6782 | 0 | 0 | 0 | 0
2031-09-23 17:00 | 30.5597 | 0.01477% | 31.9146 | 33.3295 | 34.8072 | 36.3503 | 0 | 0 | 0 | 0
2031-09-23 18:00 | 31.7027 | 0.01532% | 33.1083 | 34.5761 | 36.1091 | 37.71 | 0 | 0 | 0 | 0.63897
2031-09-23 19:00 | 32.4122 | 0.01566% | 33.8492 | 35.3499 | 36.9171 | 38.5539 | 0 | 0 | 0 | 1.3985
2031-09-23 20:00 | 33.4238 | 0.01615% | 34.9057 | 36.4532 | 38.0694 | 39.7572 | 0 | 0 | 0.96245 | 2.4815
2031-09-23 21:00 | 33.7786 | 0.01632% | 35.2761 | 36.8401 | 38.4734 | 40.1792 | 0 | 0 | 1.3261 | 2.8612
2031-09-23 22:00 | 32.6093 | 0.01576% | 34.055 | 35.5648 | 37.1416 | 38.7883 | 0 | 0 | 0.12744 | 1.6095
2031-09-23 23:00 | 32.11 | 0.01552% | 33.5336 | 35.0203 | 36.573 | 38.1944 | 0 | 0 | 0 | 1.075
2031-09-24 | 31.5845 | 0.01526% | 32.9848 | 34.4472 | 35.9744 | 37.5693 | 0 | 0 | 0 | 0.51238
2031-09-24 01:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-09-24 02:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-09-24 03:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-09-24 04:00 | 21.2315 | 0.01026% | 22.1728 | 23.1558 | 24.1824 | 25.2546 | 0 | 0 | 0 | 0
2031-09-24 05:00 | 18.617 | 0.008997% | 19.4424 | 20.3043 | 21.2045 | 22.1446 | 0 | 0 | 0 | 0
2031-09-24 06:00 | 17.2112 | 0.008318% | 17.9742 | 18.7711 | 19.6033 | 20.4725 | 0 | 0 | 0 | 0
2031-09-24 07:00 | 16.3178 | 0.007886% | 17.0412 | 17.7967 | 18.5858 | 19.4098 | 0 | 0 | 0 | 0
2031-09-24 08:00 | 16.055 | 0.007759% | 16.7668 | 17.5102 | 18.2865 | 19.0972 | 0 | 0 | 0 | 0
2031-09-24 09:00 | 17.4214 | 0.008419% | 18.1938 | 19.0004 | 19.8428 | 20.7225 | 0 | 0 | 0 | 0
2031-09-24 10:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-09-24 11:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-09-24 12:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-09-24 13:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-09-24 14:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-09-24 15:00 | 27.1043 | 0.0131% | 28.306 | 29.5609 | 30.8715 | 32.2402 | 0 | 0 | 0 | 0
2031-09-24 16:00 | 28.1291 | 0.01359% | 29.3762 | 30.6786 | 32.0387 | 33.4592 | 0 | 0 | 0 | 0
2031-09-24 17:00 | 30.4809 | 0.01473% | 31.8322 | 33.2435 | 34.7174 | 36.2566 | 0 | 0 | 0 | 0
2031-09-24 18:00 | 30.0604 | 0.01453% | 31.3932 | 32.785 | 34.2385 | 35.7565 | 0 | 0 | 0 | 0
2031-09-24 19:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-09-24 20:00 | 29.4955 | 0.01425% | 30.8032 | 32.1688 | 33.595 | 35.0845 | 0 | 0 | 0 | 0
2031-09-24 21:00 | 30.2706 | 0.01463% | 31.6127 | 33.0142 | 34.4779 | 36.0065 | 0 | 0 | 0 | 0
2031-09-24 22:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-09-24 23:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-09-25 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-09-25 01:00 | 28.2605 | 0.01366% | 29.5134 | 30.8219 | 32.1884 | 33.6155 | 0 | 0 | 0 | 0
2031-09-25 02:00 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-09-25 03:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-09-25 04:00 | 20.1541 | 0.00974% | 21.0477 | 21.9808 | 22.9554 | 23.9731 | 0 | 0 | 0 | 0
2031-09-25 05:00 | 18.0783 | 0.008737% | 18.8798 | 19.7168 | 20.591 | 21.5039 | 0 | 0 | 0 | 0
2031-09-25 06:00 | 16.909 | 0.008172% | 17.6587 | 18.4416 | 19.2592 | 20.113 | 0 | 0 | 0 | 0
2031-09-25 07:00 | 16.1601 | 0.00781% | 16.8766 | 17.6248 | 18.4062 | 19.2222 | 0 | 0 | 0 | 0
2031-09-25 08:00 | 15.7003 | 0.007587% | 16.3963 | 17.1233 | 17.8824 | 18.6753 | 0 | 0 | 0 | 0
2031-09-25 09:00 | 17.1061 | 0.008267% | 17.8645 | 18.6565 | 19.4836 | 20.3474 | 0 | 0 | 0 | 0
2031-09-25 10:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-09-25 11:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-09-25 12:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-09-25 13:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-09-25 14:00 | 25.1336 | 0.01215% | 26.2479 | 27.4116 | 28.6269 | 29.896 | 0 | 0 | 0 | 0
2031-09-25 15:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-09-25 16:00 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-09-25 17:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-09-25 18:00 | 26.2372 | 0.01268% | 27.4004 | 28.6152 | 29.8839 | 31.2088 | 0 | 0 | 0 | 0
2031-09-25 19:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-09-25 20:00 | 27.5773 | 0.01333% | 28.7999 | 30.0768 | 31.4102 | 32.8028 | 0 | 0 | 0 | 0
2031-09-25 21:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-09-25 22:00 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-09-25 23:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-09-26 | 27.4328 | 0.01326% | 28.649 | 29.9192 | 31.2456 | 32.6309 | 0 | 0 | 0 | 0
2031-09-26 01:00 | 26.3817 | 0.01275% | 27.5513 | 28.7728 | 30.0485 | 31.3807 | 0 | 0 | 0 | 0
2031-09-26 02:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-09-26 03:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-09-26 04:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-09-26 05:00 | 17.1323 | 0.008279% | 17.8919 | 18.6851 | 19.5136 | 20.3787 | 0 | 0 | 0 | 0
2031-09-26 06:00 | 16.0813 | 0.007772% | 16.7942 | 17.5388 | 18.3164 | 19.1285 | 0 | 0 | 0 | 0
2031-09-26 07:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-09-26 08:00 | 15.0302 | 0.007264% | 15.6966 | 16.3925 | 17.1193 | 17.8782 | 0 | 0 | 0 | 0
2031-09-26 09:00 | 16.2784 | 0.007867% | 17.0001 | 17.7538 | 18.5409 | 19.3629 | 0 | 0 | 0 | 0
2031-09-26 10:00 | 18.814 | 0.009092% | 19.6482 | 20.5193 | 21.429 | 22.3791 | 0 | 0 | 0 | 0
2031-09-26 11:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-09-26 12:00 | 23.1628 | 0.01119% | 24.1897 | 25.2622 | 26.3822 | 27.5519 | 0 | 0 | 0 | 0
2031-09-26 13:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-09-26 14:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-09-26 15:00 | 26.8415 | 0.01297% | 28.0316 | 29.2744 | 30.5722 | 31.9277 | 0 | 0 | 0 | 0
2031-09-26 16:00 | 27.1437 | 0.01312% | 28.3471 | 29.6039 | 30.9164 | 32.2871 | 0 | 0 | 0 | 0
2031-09-26 17:00 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-09-26 18:00 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-09-26 19:00 | 29.1407 | 0.01408% | 30.4327 | 31.7819 | 33.191 | 34.6625 | 0 | 0 | 0 | 0
2031-09-26 20:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-09-26 21:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-09-26 22:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-09-26 23:00 | 27.4853 | 0.01328% | 28.7039 | 29.9765 | 31.3055 | 32.6934 | 0 | 0 | 0 | 0
2031-09-27 | 27.3277 | 0.01321% | 28.5392 | 29.8045 | 31.1259 | 32.5059 | 0 | 0 | 0 | 0
2031-09-27 01:00 | 26.0532 | 0.01259% | 27.2083 | 28.4146 | 29.6744 | 30.99 | 0 | 0 | 0 | 0
2031-09-27 02:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-09-27 03:00 | 21.2446 | 0.01027% | 22.1865 | 23.1702 | 24.1974 | 25.2702 | 0 | 0 | 0 | 0
2031-09-27 04:00 | 19.2739 | 0.009314% | 20.1284 | 21.0208 | 21.9528 | 22.926 | 0 | 0 | 0 | 0
2031-09-27 05:00 | 17.2769 | 0.008349% | 18.0428 | 18.8428 | 19.6782 | 20.5506 | 0 | 0 | 0 | 0
2031-09-27 06:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-09-27 07:00 | 15.0039 | 0.007251% | 15.6691 | 16.3638 | 17.0893 | 17.847 | 0 | 0 | 0 | 0
2031-09-27 08:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-09-27 09:00 | 14.6361 | 0.007073% | 15.285 | 15.9626 | 16.6703 | 17.4094 | 0 | 0 | 0 | 0
2031-09-27 10:00 | 15.201 | 0.007346% | 15.875 | 16.5788 | 17.3138 | 18.0814 | 0 | 0 | 0 | 0
2031-09-27 11:00 | 17.0272 | 0.008229% | 17.7821 | 18.5705 | 19.3938 | 20.2537 | 0 | 0 | 0 | 0
2031-09-27 12:00 | 19.1556 | 0.009257% | 20.0049 | 20.8918 | 21.8181 | 22.7854 | 0 | 0 | 0 | 0
2031-09-27 13:00 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-09-27 14:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-09-27 15:00 | 25.6197 | 0.01238% | 26.7555 | 27.9417 | 29.1805 | 30.4743 | 0 | 0 | 0 | 0
2031-09-27 16:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-09-27 17:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-09-27 18:00 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-09-27 19:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-09-27 20:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-09-27 21:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-09-27 22:00 | 27.4853 | 0.01328% | 28.7039 | 29.9765 | 31.3055 | 32.6934 | 0 | 0 | 0 | 0
2031-09-27 23:00 | 26.4999 | 0.01281% | 27.6748 | 28.9018 | 30.1832 | 31.5213 | 0 | 0 | 0 | 0
2031-09-28 | 25.935 | 0.01253% | 27.0848 | 28.2856 | 29.5397 | 30.8493 | 0 | 0 | 0 | 0
2031-09-28 01:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-09-28 02:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-09-28 03:00 | 20.4695 | 0.009892% | 21.377 | 22.3247 | 23.3145 | 24.3482 | 0 | 0 | 0 | 0
2031-09-28 04:00 | 18.3936 | 0.008889% | 19.2091 | 20.0607 | 20.9501 | 21.879 | 0 | 0 | 0 | 0
2031-09-28 05:00 | 16.5411 | 0.007994% | 17.2745 | 18.0403 | 18.8402 | 19.6754 | 0 | 0 | 0 | 0
2031-09-28 06:00 | 15.2273 | 0.007359% | 15.9024 | 16.6074 | 17.3437 | 18.1127 | 0 | 0 | 0 | 0
2031-09-28 07:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-09-28 08:00 | 14.1368 | 0.006832% | 14.7636 | 15.4181 | 16.1017 | 16.8155 | 0 | 0 | 0 | 0
2031-09-28 09:00 | 14.0843 | 0.006806% | 14.7087 | 15.3608 | 16.0418 | 16.753 | 0 | 0 | 0 | 0
2031-09-28 10:00 | 14.531 | 0.007022% | 15.1752 | 15.848 | 16.5506 | 17.2844 | 0 | 0 | 0 | 0
2031-09-28 11:00 | 16.0419 | 0.007752% | 16.7531 | 17.4958 | 18.2715 | 19.0816 | 0 | 0 | 0 | 0
2031-09-28 12:00 | 18.433 | 0.008908% | 19.2503 | 20.1037 | 20.995 | 21.9259 | 0 | 0 | 0 | 0
2031-09-28 13:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-09-28 14:00 | 23.4781 | 0.01135% | 24.519 | 25.6061 | 26.7414 | 27.9269 | 0 | 0 | 0 | 0
2031-09-28 15:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-09-28 16:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-09-28 17:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-09-28 18:00 | 28.8648 | 0.01395% | 30.1446 | 31.481 | 32.8768 | 34.3344 | 0 | 0 | 0 | 0
2031-09-28 19:00 | 29.6531 | 0.01433% | 30.9678 | 32.3408 | 33.7746 | 35.272 | 0 | 0 | 0 | 0
2031-09-28 20:00 | 31.2954 | 0.01512% | 32.6829 | 34.1319 | 35.6452 | 37.2255 | 0 | 0 | 0 | 0.20295
2031-09-28 21:00 | 32.3202 | 0.01562% | 33.7531 | 35.2496 | 36.8124 | 38.4445 | 0 | 0 | 0 | 1.3
2031-09-28 22:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-09-28 23:00 | 29.7977 | 0.0144% | 31.1187 | 32.4984 | 33.9392 | 35.4439 | 0 | 0 | 0 | 0
2031-09-29 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-09-29 01:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-09-29 02:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-09-29 03:00 | 20.614 | 0.009962% | 21.5279 | 22.4824 | 23.4791 | 24.5201 | 0 | 0 | 0 | 0
2031-09-29 04:00 | 18.0783 | 0.008737% | 18.8798 | 19.7168 | 20.591 | 21.5039 | 0 | 0 | 0 | 0
2031-09-29 05:00 | 16.1864 | 0.007822% | 16.904 | 17.6535 | 18.4361 | 19.2535 | 0 | 0 | 0 | 0
2031-09-29 06:00 | 15.0302 | 0.007264% | 15.6966 | 16.3925 | 17.1193 | 17.8782 | 0 | 0 | 0 | 0
2031-09-29 07:00 | 14.3339 | 0.006927% | 14.9694 | 15.633 | 16.3261 | 17.05 | 0 | 0 | 0 | 0
2031-09-29 08:00 | 14.0974 | 0.006813% | 14.7224 | 15.3751 | 16.0568 | 16.7687 | 0 | 0 | 0 | 0
2031-09-29 09:00 | 15.201 | 0.007346% | 15.875 | 16.5788 | 17.3138 | 18.0814 | 0 | 0 | 0 | 0
2031-09-29 10:00 | 17.4345 | 0.008425% | 18.2075 | 19.0147 | 19.8577 | 20.7381 | 0 | 0 | 0 | 0
2031-09-29 11:00 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0
2031-09-29 12:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-09-29 13:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-09-29 14:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-09-29 15:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-09-29 16:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-09-29 17:00 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-09-29 18:00 | 27.9583 | 0.01351% | 29.1978 | 30.4923 | 31.8442 | 33.256 | 0 | 0 | 0 | 0
2031-09-29 19:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-09-29 20:00 | 30.9276 | 0.01495% | 32.2987 | 33.7307 | 35.2262 | 36.7879 | 0 | 0 | 0 | 0
2031-09-29 21:00 | 31.9129 | 0.01542% | 33.3278 | 34.8054 | 36.3485 | 37.96 | 0 | 0 | 0 | 0.86401
2031-09-29 22:00 | 31.1509 | 0.01505% | 32.532 | 33.9743 | 35.4806 | 37.0536 | 0 | 0 | 0 | 0.048234
2031-09-29 23:00 | 28.8123 | 0.01392% | 30.0897 | 31.4237 | 32.8169 | 34.2718 | 0 | 0 | 0 | 0
2031-09-30 | 27.9714 | 0.01352% | 29.2116 | 30.5067 | 31.8592 | 33.2717 | 0 | 0 | 0 | 0
2031-09-30 01:00 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-09-30 02:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-09-30 03:00 | 20.4301 | 0.009873% | 21.3358 | 22.2818 | 23.2696 | 24.3013 | 0 | 0 | 0 | 0
2031-09-30 04:00 | 17.6579 | 0.008533% | 18.4407 | 19.2583 | 20.1121 | 21.0038 | 0 | 0 | 0 | 0
2031-09-30 05:00 | 15.8711 | 0.00767% | 16.5747 | 17.3096 | 18.077 | 18.8784 | 0 | 0 | 0 | 0
2031-09-30 06:00 | 14.8594 | 0.007181% | 15.5182 | 16.2062 | 16.9247 | 17.6751 | 0 | 0 | 0 | 0
2031-09-30 07:00 | 14.5178 | 0.007016% | 15.1615 | 15.8337 | 16.5356 | 17.2688 | 0 | 0 | 0 | 0
2031-09-30 08:00 | 14.3207 | 0.006921% | 14.9557 | 15.6187 | 16.3112 | 17.0343 | 0 | 0 | 0 | 0
2031-09-30 09:00 | 15.2273 | 0.007359% | 15.9024 | 16.6074 | 17.3437 | 18.1127 | 0 | 0 | 0 | 0
2031-09-30 10:00 | 18.1309 | 0.008762% | 18.9347 | 19.7742 | 20.6509 | 21.5664 | 0 | 0 | 0 | 0
2031-09-30 11:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-09-30 12:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-09-30 13:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-09-30 14:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-09-30 15:00 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-09-30 16:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-09-30 17:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-09-30 18:00 | 27.1437 | 0.01312% | 28.3471 | 29.6039 | 30.9164 | 32.2871 | 0 | 0 | 0 | 0
2031-09-30 19:00 | 28.8911 | 0.01396% | 30.172 | 31.5097 | 32.9067 | 34.3656 | 0 | 0 | 0 | 0
2031-09-30 20:00 | 30.2969 | 0.01464% | 31.6401 | 33.0429 | 34.5079 | 36.0378 | 0 | 0 | 0 | 0
2031-09-30 21:00 | 30.494 | 0.01474% | 31.8459 | 33.2578 | 34.7323 | 36.2722 | 0 | 0 | 0 | 0
2031-09-30 22:00 | 30.113 | 0.01455% | 31.448 | 32.8423 | 34.2984 | 35.819 | 0 | 0 | 0 | 0
2031-09-30 23:00 | 28.1291 | 0.01359% | 29.3762 | 30.6786 | 32.0387 | 33.4592 | 0 | 0 | 0 | 0
2031-10-01 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-10-01 01:00 | 25.6985 | 0.01242% | 26.8379 | 28.0277 | 29.2703 | 30.568 | 0 | 0 | 0 | 0
2031-10-01 02:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-10-01 03:00 | 19.9702 | 0.009651% | 20.8556 | 21.7802 | 22.7459 | 23.7543 | 0 | 0 | 0 | 0
2031-10-01 04:00 | 17.6841 | 0.008546% | 18.4682 | 19.287 | 20.1421 | 21.0351 | 0 | 0 | 0 | 0
2031-10-01 05:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-10-01 06:00 | 14.9777 | 0.007238% | 15.6417 | 16.3352 | 17.0594 | 17.8157 | 0 | 0 | 0 | 0
2031-10-01 07:00 | 14.4521 | 0.006984% | 15.0929 | 15.762 | 16.4608 | 17.1906 | 0 | 0 | 0 | 0
2031-10-01 08:00 | 14.2945 | 0.006908% | 14.9282 | 15.5901 | 16.2813 | 17.0031 | 0 | 0 | 0 | 0
2031-10-01 09:00 | 15.5557 | 0.007518% | 16.2454 | 16.9657 | 17.7178 | 18.5034 | 0 | 0 | 0 | 0
2031-10-01 10:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-10-01 11:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-10-01 12:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-10-01 13:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-10-01 14:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-10-01 15:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-10-01 16:00 | 23.084 | 0.01116% | 24.1074 | 25.1762 | 26.2924 | 27.4581 | 0 | 0 | 0 | 0
2031-10-01 17:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-10-01 18:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-10-01 19:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-10-01 20:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-10-01 21:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-10-01 22:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-10-01 23:00 | 25.3438 | 0.01225% | 26.4674 | 27.6408 | 28.8663 | 30.1461 | 0 | 0 | 0 | 0
2031-10-02 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-10-02 01:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-10-02 02:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-10-02 03:00 | 18.8797 | 0.009124% | 19.7168 | 20.5909 | 21.5038 | 22.4572 | 0 | 0 | 0 | 0
2031-10-02 04:00 | 16.9878 | 0.00821% | 17.741 | 18.5275 | 19.3489 | 20.2068 | 0 | 0 | 0 | 0
2031-10-02 05:00 | 15.3718 | 0.007429% | 16.0533 | 16.765 | 17.5083 | 18.2846 | 0 | 0 | 0 | 0
2031-10-02 06:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-10-02 07:00 | 13.9923 | 0.006762% | 14.6126 | 15.2605 | 15.9371 | 16.6436 | 0 | 0 | 0 | 0
2031-10-02 08:00 | 14.0974 | 0.006813% | 14.7224 | 15.3751 | 16.0568 | 16.7687 | 0 | 0 | 0 | 0
2031-10-02 09:00 | 15.2141 | 0.007352% | 15.8887 | 16.5931 | 17.3288 | 18.097 | 0 | 0 | 0 | 0
2031-10-02 10:00 | 17.9732 | 0.008686% | 18.77 | 19.6022 | 20.4713 | 21.3789 | 0 | 0 | 0 | 0
2031-10-02 11:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-10-02 12:00 | 21.1264 | 0.01021% | 22.063 | 23.0412 | 24.0627 | 25.1296 | 0 | 0 | 0 | 0
2031-10-02 13:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-10-02 14:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-10-02 15:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-10-02 16:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-10-02 17:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-10-02 18:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-10-02 19:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-10-02 20:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-10-02 21:00 | 24.8839 | 0.01203% | 25.9872 | 27.1393 | 28.3425 | 29.5991 | 0 | 0 | 0 | 0
2031-10-02 22:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-10-02 23:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-10-03 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-10-03 01:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-10-03 02:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-10-03 03:00 | 19.2345 | 0.009295% | 20.0872 | 20.9778 | 21.9079 | 22.8791 | 0 | 0 | 0 | 0
2031-10-03 04:00 | 16.9221 | 0.008178% | 17.6724 | 18.4559 | 19.2741 | 20.1286 | 0 | 0 | 0 | 0
2031-10-03 05:00 | 15.9236 | 0.007695% | 16.6296 | 17.3669 | 18.1368 | 18.9409 | 0 | 0 | 0 | 0
2031-10-03 06:00 | 14.728 | 0.007118% | 15.381 | 16.0629 | 16.7751 | 17.5188 | 0 | 0 | 0 | 0
2031-10-03 07:00 | 14.2682 | 0.006895% | 14.9008 | 15.5614 | 16.2513 | 16.9718 | 0 | 0 | 0 | 0
2031-10-03 08:00 | 14.1237 | 0.006825% | 14.7498 | 15.4038 | 16.0867 | 16.7999 | 0 | 0 | 0 | 0
2031-10-03 09:00 | 15.293 | 0.007391% | 15.971 | 16.6791 | 17.4185 | 18.1908 | 0 | 0 | 0 | 0
2031-10-03 10:00 | 18.0126 | 0.008705% | 18.8112 | 19.6452 | 20.5162 | 21.4258 | 0 | 0 | 0 | 0
2031-10-03 11:00 | 20.0228 | 0.009676% | 20.9105 | 21.8375 | 22.8057 | 23.8168 | 0 | 0 | 0 | 0
2031-10-03 12:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-10-03 13:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-10-03 14:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-10-03 15:00 | 22.9789 | 0.0111% | 23.9977 | 25.0616 | 26.1727 | 27.3331 | 0 | 0 | 0 | 0
2031-10-03 16:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-10-03 17:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-10-03 18:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-10-03 19:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-10-03 20:00 | 25.6985 | 0.01242% | 26.8379 | 28.0277 | 29.2703 | 30.568 | 0 | 0 | 0 | 0
2031-10-03 21:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-10-03 22:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-10-03 23:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-10-04 | 24.989 | 0.01208% | 26.0969 | 27.2539 | 28.4623 | 29.7241 | 0 | 0 | 0 | 0
2031-10-04 01:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-10-04 02:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-10-04 03:00 | 19.7337 | 0.009537% | 20.6086 | 21.5223 | 22.4765 | 23.473 | 0 | 0 | 0 | 0
2031-10-04 04:00 | 17.5265 | 0.00847% | 18.3035 | 19.115 | 19.9625 | 20.8475 | 0 | 0 | 0 | 0
2031-10-04 05:00 | 16.0681 | 0.007765% | 16.7805 | 17.5245 | 18.3014 | 19.1128 | 0 | 0 | 0 | 0
2031-10-04 06:00 | 15.1747 | 0.007333% | 15.8475 | 16.5501 | 17.2839 | 18.0501 | 0 | 0 | 0 | 0
2031-10-04 07:00 | 14.3207 | 0.006921% | 14.9557 | 15.6187 | 16.3112 | 17.0343 | 0 | 0 | 0 | 0
2031-10-04 08:00 | 13.9266 | 0.00673% | 14.544 | 15.1888 | 15.8622 | 16.5655 | 0 | 0 | 0 | 0
2031-10-04 09:00 | 14.0448 | 0.006787% | 14.6675 | 15.3178 | 15.9969 | 16.7062 | 0 | 0 | 0 | 0
2031-10-04 10:00 | 14.8857 | 0.007194% | 15.5457 | 16.2349 | 16.9546 | 17.7063 | 0 | 0 | 0 | 0
2031-10-04 11:00 | 16.5148 | 0.007981% | 17.247 | 18.0117 | 18.8102 | 19.6442 | 0 | 0 | 0 | 0
2031-10-04 12:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0
2031-10-04 13:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-10-04 14:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-10-04 15:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-10-04 16:00 | 25.2518 | 0.0122% | 26.3714 | 27.5405 | 28.7615 | 30.0367 | 0 | 0 | 0 | 0
2031-10-04 17:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-10-04 18:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-10-04 19:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-10-04 20:00 | 29.0094 | 0.01402% | 30.2955 | 31.6387 | 33.0414 | 34.5063 | 0 | 0 | 0 | 0
2031-10-04 21:00 | 29.3772 | 0.0142% | 30.6797 | 32.0399 | 33.4604 | 34.9438 | 0 | 0 | 0 | 0
2031-10-04 22:00 | 28.8123 | 0.01392% | 30.0897 | 31.4237 | 32.8169 | 34.2718 | 0 | 0 | 0 | 0
2031-10-04 23:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-10-05 | 26.7496 | 0.01293% | 27.9355 | 29.174 | 30.4675 | 31.8183 | 0 | 0 | 0 | 0
2031-10-05 01:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-10-05 02:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-10-05 03:00 | 21.2184 | 0.01025% | 22.1591 | 23.1415 | 24.1675 | 25.239 | 0 | 0 | 0 | 0
2031-10-05 04:00 | 18.8009 | 0.009086% | 19.6344 | 20.5049 | 21.414 | 22.3634 | 0 | 0 | 0 | 0
2031-10-05 05:00 | 16.6725 | 0.008057% | 17.4117 | 18.1836 | 18.9898 | 19.8317 | 0 | 0 | 0 | 0
2031-10-05 06:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-10-05 07:00 | 14.6755 | 0.007092% | 15.3261 | 16.0056 | 16.7152 | 17.4563 | 0 | 0 | 0 | 0
2031-10-05 08:00 | 14.1237 | 0.006825% | 14.7498 | 15.4038 | 16.0867 | 16.7999 | 0 | 0 | 0 | 0
2031-10-05 09:00 | 13.9397 | 0.006737% | 14.5578 | 15.2032 | 15.8772 | 16.5811 | 0 | 0 | 0 | 0
2031-10-05 10:00 | 14.5441 | 0.007029% | 15.1889 | 15.8623 | 16.5656 | 17.3 | 0 | 0 | 0 | 0
2031-10-05 11:00 | 15.8448 | 0.007657% | 16.5473 | 17.2809 | 18.047 | 18.8472 | 0 | 0 | 0 | 0
2031-10-05 12:00 | 18.4593 | 0.008921% | 19.2777 | 20.1324 | 21.025 | 21.9571 | 0 | 0 | 0 | 0
2031-10-05 13:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-10-05 14:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-10-05 15:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-10-05 16:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-10-05 17:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-10-05 18:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-10-05 19:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-10-05 20:00 | 33.1742 | 0.01603% | 34.645 | 36.181 | 37.7851 | 39.4603 | 0 | 0 | 0.70656 | 2.2143
2031-10-05 21:00 | 33.6472 | 0.01626% | 35.1389 | 36.6968 | 38.3238 | 40.0229 | 0 | 0 | 1.1914 | 2.7206
2031-10-05 22:00 | 32.3071 | 0.01561% | 33.7394 | 35.2353 | 36.7974 | 38.4288 | 0 | 0 | 0 | 1.286
2031-10-05 23:00 | 31.2035 | 0.01508% | 32.5869 | 34.0316 | 35.5404 | 37.1161 | 0 | 0 | 0 | 0.10449
2031-10-06 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-10-06 01:00 | 27.4328 | 0.01326% | 28.649 | 29.9192 | 31.2456 | 32.6309 | 0 | 0 | 0 | 0
2031-10-06 02:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-10-06 03:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-10-06 04:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-10-06 05:00 | 16.2915 | 0.007873% | 17.0138 | 17.7681 | 18.5558 | 19.3785 | 0 | 0 | 0 | 0
2031-10-06 06:00 | 15.2536 | 0.007372% | 15.9298 | 16.6361 | 17.3737 | 18.1439 | 0 | 0 | 0 | 0
2031-10-06 07:00 | 14.347 | 0.006933% | 14.9831 | 15.6474 | 16.3411 | 17.0656 | 0 | 0 | 0 | 0
2031-10-06 08:00 | 14.1894 | 0.006857% | 14.8184 | 15.4754 | 16.1615 | 16.8781 | 0 | 0 | 0 | 0
2031-10-06 09:00 | 15.0171 | 0.007257% | 15.6829 | 16.3782 | 17.1043 | 17.8626 | 0 | 0 | 0 | 0
2031-10-06 10:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-10-06 11:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-10-06 12:00 | 21.1527 | 0.01022% | 22.0905 | 23.0699 | 24.0927 | 25.1608 | 0 | 0 | 0 | 0
2031-10-06 13:00 | 22.6504 | 0.01095% | 23.6546 | 24.7034 | 25.7986 | 26.9424 | 0 | 0 | 0 | 0
2031-10-06 14:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-10-06 15:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-10-06 16:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-10-06 17:00 | 28.1816 | 0.01362% | 29.4311 | 30.7359 | 32.0986 | 33.5217 | 0 | 0 | 0 | 0
2031-10-06 18:00 | 29.3641 | 0.01419% | 30.666 | 32.0255 | 33.4454 | 34.9282 | 0 | 0 | 0 | 0
2031-10-06 19:00 | 31.0721 | 0.01502% | 32.4497 | 33.8883 | 35.3908 | 36.9598 | 0 | 0 | 0 | 0
2031-10-06 20:00 | 32.5436 | 0.01573% | 33.9864 | 35.4932 | 37.0668 | 38.7101 | 0 | 0 | 0.060103 | 1.5391
2031-10-06 21:00 | 33.0165 | 0.01596% | 34.4803 | 36.009 | 37.6055 | 39.2727 | 0 | 0 | 0.54495 | 2.0455
2031-10-06 22:00 | 32.0574 | 0.01549% | 33.4787 | 34.963 | 36.5131 | 38.1319 | 0 | 0 | 0 | 1.0187
2031-10-06 23:00 | 30.9801 | 0.01497% | 32.3536 | 33.788 | 35.286 | 36.8504 | 0 | 0 | 0 | 0
2031-10-07 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-10-07 01:00 | 28.3787 | 0.01371% | 29.6369 | 30.9509 | 32.3231 | 33.7561 | 0 | 0 | 0 | 0
2031-10-07 02:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-10-07 03:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-10-07 04:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-10-07 05:00 | 17.3426 | 0.008381% | 18.1114 | 18.9144 | 19.753 | 20.6287 | 0 | 0 | 0 | 0
2031-10-07 06:00 | 16.0156 | 0.00774% | 16.7256 | 17.4672 | 18.2416 | 19.0503 | 0 | 0 | 0 | 0
2031-10-07 07:00 | 15.0696 | 0.007283% | 15.7377 | 16.4355 | 17.1641 | 17.9251 | 0 | 0 | 0 | 0
2031-10-07 08:00 | 14.6623 | 0.007086% | 15.3124 | 15.9913 | 16.7003 | 17.4407 | 0 | 0 | 0 | 0
2031-10-07 09:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-10-07 10:00 | 18.6564 | 0.009016% | 19.4835 | 20.3473 | 21.2494 | 22.1915 | 0 | 0 | 0 | 0
2031-10-07 11:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-10-07 12:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-10-07 13:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-10-07 14:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-10-07 15:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-10-07 16:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-10-07 17:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-10-07 18:00 | 25.9876 | 0.01256% | 27.1397 | 28.343 | 29.5996 | 30.9119 | 0 | 0 | 0 | 0
2031-10-07 19:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-10-07 20:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-10-07 21:00 | 27.6824 | 0.01338% | 28.9097 | 30.1914 | 31.53 | 32.9278 | 0 | 0 | 0 | 0
2031-10-07 22:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-10-07 23:00 | 26.7759 | 0.01294% | 27.963 | 29.2027 | 30.4974 | 31.8495 | 0 | 0 | 0 | 0
2031-10-08 | 26.1189 | 0.01262% | 27.2769 | 28.4863 | 29.7492 | 31.0681 | 0 | 0 | 0 | 0
2031-10-08 01:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-10-08 02:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-10-08 03:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-10-08 04:00 | 17.763 | 0.008584% | 18.5505 | 19.3729 | 20.2318 | 21.1288 | 0 | 0 | 0 | 0
2031-10-08 05:00 | 16.0944 | 0.007778% | 16.808 | 17.5531 | 18.3314 | 19.1441 | 0 | 0 | 0 | 0
2031-10-08 06:00 | 15.2667 | 0.007378% | 15.9436 | 16.6504 | 17.3886 | 18.1595 | 0 | 0 | 0 | 0
2031-10-08 07:00 | 14.1894 | 0.006857% | 14.8184 | 15.4754 | 16.1615 | 16.8781 | 0 | 0 | 0 | 0
2031-10-08 08:00 | 14.2025 | 0.006864% | 14.8322 | 15.4898 | 16.1765 | 16.8937 | 0 | 0 | 0 | 0
2031-10-08 09:00 | 15.3324 | 0.00741% | 16.0122 | 16.7221 | 17.4634 | 18.2377 | 0 | 0 | 0 | 0
2031-10-08 10:00 | 18.4462 | 0.008914% | 19.264 | 20.1181 | 21.01 | 21.9415 | 0 | 0 | 0 | 0
2031-10-08 11:00 | 20.8899 | 0.0101% | 21.8161 | 22.7833 | 23.7934 | 24.8483 | 0 | 0 | 0 | 0
2031-10-08 12:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-10-08 13:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-10-08 14:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-10-08 15:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-10-08 16:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-10-08 17:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-10-08 18:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-10-08 19:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-10-08 20:00 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-10-08 21:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-10-08 22:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-10-08 23:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-10-09 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-10-09 01:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-10-09 02:00 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-10-09 03:00 | 19.3396 | 0.009346% | 20.197 | 21.0924 | 22.0276 | 23.0042 | 0 | 0 | 0 | 0
2031-10-09 04:00 | 16.8696 | 0.008152% | 17.6175 | 18.3986 | 19.2143 | 20.0661 | 0 | 0 | 0 | 0
2031-10-09 05:00 | 15.3193 | 0.007403% | 15.9984 | 16.7077 | 17.4485 | 18.2221 | 0 | 0 | 0 | 0
2031-10-09 06:00 | 14.6229 | 0.007067% | 15.2712 | 15.9483 | 16.6554 | 17.3938 | 0 | 0 | 0 | 0
2031-10-09 07:00 | 14.0448 | 0.006787% | 14.6675 | 15.3178 | 15.9969 | 16.7062 | 0 | 0 | 0 | 0
2031-10-09 08:00 | 14.3207 | 0.006921% | 14.9557 | 15.6187 | 16.3112 | 17.0343 | 0 | 0 | 0 | 0
2031-10-09 09:00 | 15.5952 | 0.007537% | 16.2866 | 17.0086 | 17.7627 | 18.5502 | 0 | 0 | 0 | 0
2031-10-09 10:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-10-09 11:00 | 20.7979 | 0.01005% | 21.72 | 22.683 | 23.6886 | 24.7389 | 0 | 0 | 0 | 0
2031-10-09 12:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-10-09 13:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-10-09 14:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-10-09 15:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-10-09 16:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-10-09 17:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-10-09 18:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-10-09 19:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-10-09 20:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-10-09 21:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-10-09 22:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-10-09 23:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-10-10 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-10-10 01:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-10-10 02:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-10-10 03:00 | 19.5104 | 0.009429% | 20.3754 | 21.2787 | 22.2221 | 23.2073 | 0 | 0 | 0 | 0
2031-10-10 04:00 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-10-10 05:00 | 16.344 | 0.007898% | 17.0687 | 17.8254 | 18.6157 | 19.441 | 0 | 0 | 0 | 0
2031-10-10 06:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-10-10 07:00 | 15.0959 | 0.007295% | 15.7652 | 16.4641 | 17.1941 | 17.9564 | 0 | 0 | 0 | 0
2031-10-10 08:00 | 15.0039 | 0.007251% | 15.6691 | 16.3638 | 17.0893 | 17.847 | 0 | 0 | 0 | 0
2031-10-10 09:00 | 16.147 | 0.007803% | 16.8628 | 17.6105 | 18.3912 | 19.2066 | 0 | 0 | 0 | 0
2031-10-10 10:00 | 19.8914 | 0.009613% | 20.7733 | 21.6943 | 22.6561 | 23.6605 | 0 | 0 | 0 | 0
2031-10-10 11:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-10-10 12:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-10-10 13:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-10-10 14:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-10-10 15:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-10-10 16:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-10-10 17:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-10-10 18:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-10-10 19:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-10-10 20:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-10-10 21:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-10-10 22:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-10-10 23:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-10-11 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-10-11 01:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-10-11 02:00 | 21.2709 | 0.01028% | 22.214 | 23.1988 | 24.2273 | 25.3015 | 0 | 0 | 0 | 0
2031-10-11 03:00 | 18.9586 | 0.009162% | 19.7991 | 20.6769 | 21.5936 | 22.551 | 0 | 0 | 0 | 0
2031-10-11 04:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-10-11 05:00 | 15.8973 | 0.007683% | 16.6022 | 17.3382 | 18.1069 | 18.9097 | 0 | 0 | 0 | 0
2031-10-11 06:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-10-11 07:00 | 14.3076 | 0.006914% | 14.9419 | 15.6044 | 16.2962 | 17.0187 | 0 | 0 | 0 | 0
2031-10-11 08:00 | 13.874 | 0.006705% | 14.4892 | 15.1315 | 15.8024 | 16.503 | 0 | 0 | 0 | 0
2031-10-11 09:00 | 13.9791 | 0.006756% | 14.5989 | 15.2462 | 15.9221 | 16.628 | 0 | 0 | 0 | 0
2031-10-11 10:00 | 14.7543 | 0.00713% | 15.4084 | 16.0916 | 16.805 | 17.5501 | 0 | 0 | 0 | 0
2031-10-11 11:00 | 16.6725 | 0.008057% | 17.4117 | 18.1836 | 18.9898 | 19.8317 | 0 | 0 | 0 | 0
2031-10-11 12:00 | 18.6958 | 0.009035% | 19.5247 | 20.3903 | 21.2943 | 22.2384 | 0 | 0 | 0 | 0
2031-10-11 13:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-10-11 14:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-10-11 15:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-10-11 16:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-10-11 17:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-10-11 18:00 | 22.8606 | 0.01105% | 23.8742 | 24.9326 | 26.038 | 27.1924 | 0 | 0 | 0 | 0
2031-10-11 19:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-10-11 20:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-10-11 21:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-10-11 22:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-10-11 23:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-10-12 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-10-12 01:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-10-12 02:00 | 20.1804 | 0.009752% | 21.0751 | 22.0095 | 22.9853 | 24.0044 | 0 | 0 | 0 | 0
2031-10-12 03:00 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-10-12 04:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-10-12 05:00 | 15.4375 | 0.00746% | 16.1219 | 16.8367 | 17.5832 | 18.3627 | 0 | 0 | 0 | 0
2031-10-12 06:00 | 14.728 | 0.007118% | 15.381 | 16.0629 | 16.7751 | 17.5188 | 0 | 0 | 0 | 0
2031-10-12 07:00 | 14.0317 | 0.006781% | 14.6538 | 15.3035 | 15.982 | 16.6905 | 0 | 0 | 0 | 0
2031-10-12 08:00 | 13.677 | 0.00661% | 14.2833 | 14.9166 | 15.5779 | 16.2686 | 0 | 0 | 0 | 0
2031-10-12 09:00 | 13.9529 | 0.006743% | 14.5715 | 15.2175 | 15.8922 | 16.5968 | 0 | 0 | 0 | 0
2031-10-12 10:00 | 14.5441 | 0.007029% | 15.1889 | 15.8623 | 16.5656 | 17.3 | 0 | 0 | 0 | 0
2031-10-12 11:00 | 15.8973 | 0.007683% | 16.6022 | 17.3382 | 18.1069 | 18.9097 | 0 | 0 | 0 | 0
2031-10-12 12:00 | 17.7761 | 0.008591% | 18.5642 | 19.3873 | 20.2468 | 21.1445 | 0 | 0 | 0 | 0
2031-10-12 13:00 | 19.3396 | 0.009346% | 20.197 | 21.0924 | 22.0276 | 23.0042 | 0 | 0 | 0 | 0
2031-10-12 14:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-10-12 15:00 | 22.0198 | 0.01064% | 22.996 | 24.0156 | 25.0803 | 26.1922 | 0 | 0 | 0 | 0
2031-10-12 16:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-10-12 17:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-10-12 18:00 | 22.1774 | 0.01072% | 23.1607 | 24.1875 | 25.2599 | 26.3798 | 0 | 0 | 0 | 0
2031-10-12 19:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-10-12 20:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-10-12 21:00 | 22.9263 | 0.01108% | 23.9428 | 25.0043 | 26.1129 | 27.2706 | 0 | 0 | 0 | 0
2031-10-12 22:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-10-12 23:00 | 21.9278 | 0.0106% | 22.9 | 23.9153 | 24.9756 | 26.0829 | 0 | 0 | 0 | 0
2031-10-13 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-10-13 01:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-10-13 02:00 | 20.049 | 0.009689% | 20.9379 | 21.8662 | 22.8357 | 23.8481 | 0 | 0 | 0 | 0
2031-10-13 03:00 | 18.6432 | 0.00901% | 19.4698 | 20.333 | 21.2345 | 22.1759 | 0 | 0 | 0 | 0
2031-10-13 04:00 | 16.6856 | 0.008064% | 17.4254 | 18.198 | 19.0048 | 19.8473 | 0 | 0 | 0 | 0
2031-10-13 05:00 | 15.4769 | 0.007479% | 16.1631 | 16.8797 | 17.628 | 18.4096 | 0 | 0 | 0 | 0
2031-10-13 06:00 | 14.4521 | 0.006984% | 15.0929 | 15.762 | 16.4608 | 17.1906 | 0 | 0 | 0 | 0
2031-10-13 07:00 | 13.8346 | 0.006686% | 14.448 | 15.0885 | 15.7575 | 16.4561 | 0 | 0 | 0 | 0
2031-10-13 08:00 | 13.6376 | 0.006591% | 14.2422 | 14.8736 | 15.533 | 16.2217 | 0 | 0 | 0 | 0
2031-10-13 09:00 | 13.7689 | 0.006654% | 14.3794 | 15.0169 | 15.6827 | 16.378 | 0 | 0 | 0 | 0
2031-10-13 10:00 | 14.7412 | 0.007124% | 15.3947 | 16.0773 | 16.79 | 17.5344 | 0 | 0 | 0 | 0
2031-10-13 11:00 | 15.9236 | 0.007695% | 16.6296 | 17.3669 | 18.1368 | 18.9409 | 0 | 0 | 0 | 0
2031-10-13 12:00 | 17.9601 | 0.008679% | 18.7563 | 19.5879 | 20.4563 | 21.3632 | 0 | 0 | 0 | 0
2031-10-13 13:00 | 19.7994 | 0.009568% | 20.6772 | 21.594 | 22.5513 | 23.5511 | 0 | 0 | 0 | 0
2031-10-13 14:00 | 21.8884 | 0.01058% | 22.8588 | 23.8723 | 24.9307 | 26.036 | 0 | 0 | 0 | 0
2031-10-13 15:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-10-13 16:00 | 23.6884 | 0.01145% | 24.7386 | 25.8354 | 26.9808 | 28.177 | 0 | 0 | 0 | 0
2031-10-13 17:00 | 23.8986 | 0.01155% | 24.9581 | 26.0646 | 27.2202 | 28.427 | 0 | 0 | 0 | 0
2031-10-13 18:00 | 23.5964 | 0.0114% | 24.6425 | 25.7351 | 26.876 | 28.0676 | 0 | 0 | 0 | 0
2031-10-13 19:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-10-13 20:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-10-13 21:00 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-10-13 22:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-10-13 23:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-10-14 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-10-14 01:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-10-14 02:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-10-14 03:00 | 17.9206 | 0.00866% | 18.7152 | 19.5449 | 20.4114 | 21.3164 | 0 | 0 | 0 | 0
2031-10-14 04:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-10-14 05:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-10-14 06:00 | 13.7821 | 0.00666% | 14.3931 | 15.0312 | 15.6976 | 16.3936 | 0 | 0 | 0 | 0
2031-10-14 07:00 | 13.5193 | 0.006533% | 14.1187 | 14.7446 | 15.3984 | 16.081 | 0 | 0 | 0 | 0
2031-10-14 08:00 | 13.5981 | 0.006571% | 14.201 | 14.8306 | 15.4881 | 16.1748 | 0 | 0 | 0 | 0
2031-10-14 09:00 | 14.912 | 0.007206% | 15.5731 | 16.2635 | 16.9846 | 17.7376 | 0 | 0 | 0 | 0
2031-10-14 10:00 | 17.2506 | 0.008337% | 18.0154 | 18.8141 | 19.6482 | 20.5193 | 0 | 0 | 0 | 0
2031-10-14 11:00 | 20.1279 | 0.009727% | 21.0202 | 21.9522 | 22.9254 | 23.9418 | 0 | 0 | 0 | 0
2031-10-14 12:00 | 20.7454 | 0.01003% | 21.6651 | 22.6257 | 23.6288 | 24.6763 | 0 | 0 | 0 | 0
2031-10-14 13:00 | 21.3629 | 0.01032% | 22.31 | 23.2991 | 24.3321 | 25.4109 | 0 | 0 | 0 | 0
2031-10-14 14:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-10-14 15:00 | 21.757 | 0.01051% | 22.7216 | 23.729 | 24.781 | 25.8797 | 0 | 0 | 0 | 0
2031-10-14 16:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-10-14 17:00 | 22.4928 | 0.01087% | 23.49 | 24.5314 | 25.619 | 26.7549 | 0 | 0 | 0 | 0
2031-10-14 18:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-10-14 19:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-10-14 20:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-10-14 21:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-10-14 22:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-10-14 23:00 | 25.0285 | 0.0121% | 26.1381 | 27.2969 | 28.5072 | 29.771 | 0 | 0 | 0 | 0
2031-10-15 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-10-15 01:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-10-15 02:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-10-15 03:00 | 18.7878 | 0.009079% | 19.6207 | 20.4906 | 21.3991 | 22.3478 | 0 | 0 | 0 | 0
2031-10-15 04:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-10-15 05:00 | 15.2536 | 0.007372% | 15.9298 | 16.6361 | 17.3737 | 18.1439 | 0 | 0 | 0 | 0
2031-10-15 06:00 | 14.3864 | 0.006952% | 15.0243 | 15.6904 | 16.386 | 17.1125 | 0 | 0 | 0 | 0
2031-10-15 07:00 | 13.9135 | 0.006724% | 14.5303 | 15.1745 | 15.8473 | 16.5499 | 0 | 0 | 0 | 0
2031-10-15 08:00 | 13.7821 | 0.00666% | 14.3931 | 15.0312 | 15.6976 | 16.3936 | 0 | 0 | 0 | 0
2031-10-15 09:00 | 15.0171 | 0.007257% | 15.6829 | 16.3782 | 17.1043 | 17.8626 | 0 | 0 | 0 | 0
2031-10-15 10:00 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-10-15 11:00 | 20.1279 | 0.009727% | 21.0202 | 21.9522 | 22.9254 | 23.9418 | 0 | 0 | 0 | 0
2031-10-15 12:00 | 20.6928 | 0.01% | 21.6102 | 22.5683 | 23.5689 | 24.6138 | 0 | 0 | 0 | 0
2031-10-15 13:00 | 21.2052 | 0.01025% | 22.1454 | 23.1272 | 24.1525 | 25.2233 | 0 | 0 | 0 | 0
2031-10-15 14:00 | 21.7307 | 0.0105% | 22.6942 | 23.7003 | 24.7511 | 25.8484 | 0 | 0 | 0 | 0
2031-10-15 15:00 | 21.7833 | 0.01053% | 22.7491 | 23.7576 | 24.8109 | 25.9109 | 0 | 0 | 0 | 0
2031-10-15 16:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-10-15 17:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-10-15 18:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-10-15 19:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-10-15 20:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-10-15 21:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-10-15 22:00 | 24.2533 | 0.01172% | 25.3286 | 26.4515 | 27.6243 | 28.849 | 0 | 0 | 0 | 0
2031-10-15 23:00 | 24.7 | 0.01194% | 25.7951 | 26.9387 | 28.133 | 29.3803 | 0 | 0 | 0 | 0
2031-10-16 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-10-16 01:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-10-16 02:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-10-16 03:00 | 19.2213 | 0.009289% | 20.0735 | 20.9635 | 21.8929 | 22.8635 | 0 | 0 | 0 | 0
2031-10-16 04:00 | 16.9615 | 0.008197% | 17.7135 | 18.4989 | 19.319 | 20.1755 | 0 | 0 | 0 | 0
2031-10-16 05:00 | 15.4901 | 0.007486% | 16.1768 | 16.894 | 17.643 | 18.4252 | 0 | 0 | 0 | 0
2031-10-16 06:00 | 14.6229 | 0.007067% | 15.2712 | 15.9483 | 16.6554 | 17.3938 | 0 | 0 | 0 | 0
2031-10-16 07:00 | 14.4127 | 0.006965% | 15.0517 | 15.719 | 16.4159 | 17.1437 | 0 | 0 | 0 | 0
2031-10-16 08:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-10-16 09:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-10-16 10:00 | 18.7352 | 0.009054% | 19.5658 | 20.4333 | 21.3392 | 22.2853 | 0 | 0 | 0 | 0
2031-10-16 11:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-10-16 12:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-10-16 13:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-10-16 14:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-10-16 15:00 | 22.0198 | 0.01064% | 22.996 | 24.0156 | 25.0803 | 26.1922 | 0 | 0 | 0 | 0
2031-10-16 16:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-10-16 17:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-10-16 18:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-10-16 19:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-10-16 20:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-10-16 21:00 | 23.8591 | 0.01153% | 24.9169 | 26.0216 | 27.1753 | 28.3801 | 0 | 0 | 0 | 0
2031-10-16 22:00 | 24.0431 | 0.01162% | 25.109 | 26.2223 | 27.3848 | 28.5989 | 0 | 0 | 0 | 0
2031-10-16 23:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-10-17 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-10-17 01:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-10-17 02:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-10-17 03:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-10-17 04:00 | 17.671 | 0.00854% | 18.4545 | 19.2726 | 20.1271 | 21.0194 | 0 | 0 | 0 | 0
2031-10-17 05:00 | 16.1732 | 0.007816% | 16.8903 | 17.6391 | 18.4212 | 19.2379 | 0 | 0 | 0 | 0
2031-10-17 06:00 | 15.2667 | 0.007378% | 15.9436 | 16.6504 | 17.3886 | 18.1595 | 0 | 0 | 0 | 0
2031-10-17 07:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-10-17 08:00 | 14.6361 | 0.007073% | 15.285 | 15.9626 | 16.6703 | 17.4094 | 0 | 0 | 0 | 0
2031-10-17 09:00 | 16.055 | 0.007759% | 16.7668 | 17.5102 | 18.2865 | 19.0972 | 0 | 0 | 0 | 0
2031-10-17 10:00 | 18.7878 | 0.009079% | 19.6207 | 20.4906 | 21.3991 | 22.3478 | 0 | 0 | 0 | 0
2031-10-17 11:00 | 21.1001 | 0.0102% | 22.0356 | 23.0125 | 24.0328 | 25.0983 | 0 | 0 | 0 | 0
2031-10-17 12:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-10-17 13:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-10-17 14:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-10-17 15:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-10-17 16:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-10-17 17:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-10-17 18:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-10-17 19:00 | 23.2154 | 0.01122% | 24.2446 | 25.3195 | 26.4421 | 27.6144 | 0 | 0 | 0 | 0
2031-10-17 20:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-10-17 21:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-10-17 22:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-10-17 23:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-10-18 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-10-18 01:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-10-18 02:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-10-18 03:00 | 19.3133 | 0.009333% | 20.1696 | 21.0638 | 21.9976 | 22.9729 | 0 | 0 | 0 | 0
2031-10-18 04:00 | 17.4082 | 0.008413% | 18.18 | 18.9861 | 19.8278 | 20.7069 | 0 | 0 | 0 | 0
2031-10-18 05:00 | 15.9893 | 0.007727% | 16.6982 | 17.4385 | 18.2117 | 19.0191 | 0 | 0 | 0 | 0
2031-10-18 06:00 | 15.0959 | 0.007295% | 15.7652 | 16.4641 | 17.1941 | 17.9564 | 0 | 0 | 0 | 0
2031-10-18 07:00 | 14.5572 | 0.007035% | 15.2026 | 15.8766 | 16.5805 | 17.3156 | 0 | 0 | 0 | 0
2031-10-18 08:00 | 14.1237 | 0.006825% | 14.7498 | 15.4038 | 16.0867 | 16.7999 | 0 | 0 | 0 | 0
2031-10-18 09:00 | 14.5704 | 0.007041% | 15.2164 | 15.891 | 16.5955 | 17.3313 | 0 | 0 | 0 | 0
2031-10-18 10:00 | 15.5032 | 0.007492% | 16.1905 | 16.9083 | 17.658 | 18.4408 | 0 | 0 | 0 | 0
2031-10-18 11:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-10-18 12:00 | 19.1688 | 0.009264% | 20.0186 | 20.9062 | 21.833 | 22.801 | 0 | 0 | 0 | 0
2031-10-18 13:00 | 20.2724 | 0.009797% | 21.1712 | 22.1098 | 23.09 | 24.1137 | 0 | 0 | 0 | 0
2031-10-18 14:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-10-18 15:00 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-10-18 16:00 | 21.3103 | 0.0103% | 22.2551 | 23.2418 | 24.2722 | 25.3483 | 0 | 0 | 0 | 0
2031-10-18 17:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-10-18 18:00 | 20.9293 | 0.01011% | 21.8572 | 22.8263 | 23.8383 | 24.8951 | 0 | 0 | 0 | 0
2031-10-18 19:00 | 20.9687 | 0.01013% | 21.8984 | 22.8692 | 23.8832 | 24.942 | 0 | 0 | 0 | 0
2031-10-18 20:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-10-18 21:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-10-18 22:00 | 23.2154 | 0.01122% | 24.2446 | 25.3195 | 26.4421 | 27.6144 | 0 | 0 | 0 | 0
2031-10-18 23:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-10-19 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-10-19 01:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-10-19 02:00 | 20.3249 | 0.009822% | 21.2261 | 22.1671 | 23.1499 | 24.1763 | 0 | 0 | 0 | 0
2031-10-19 03:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-10-19 04:00 | 16.9221 | 0.008178% | 17.6724 | 18.4559 | 19.2741 | 20.1286 | 0 | 0 | 0 | 0
2031-10-19 05:00 | 15.3455 | 0.007416% | 16.0259 | 16.7364 | 17.4784 | 18.2533 | 0 | 0 | 0 | 0
2031-10-19 06:00 | 14.4915 | 0.007003% | 15.134 | 15.805 | 16.5057 | 17.2375 | 0 | 0 | 0 | 0
2031-10-19 07:00 | 13.6113 | 0.006578% | 14.2147 | 14.8449 | 15.5031 | 16.1904 | 0 | 0 | 0 | 0
2031-10-19 08:00 | 13.4142 | 0.006483% | 14.0089 | 14.63 | 15.2786 | 15.956 | 0 | 0 | 0 | 0
2031-10-19 09:00 | 13.4799 | 0.006514% | 14.0775 | 14.7017 | 15.3535 | 16.0342 | 0 | 0 | 0 | 0
2031-10-19 10:00 | 14.0186 | 0.006775% | 14.6401 | 15.2892 | 15.967 | 16.6749 | 0 | 0 | 0 | 0
2031-10-19 11:00 | 15.2798 | 0.007384% | 15.9573 | 16.6647 | 17.4036 | 18.1752 | 0 | 0 | 0 | 0
2031-10-19 12:00 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-10-19 13:00 | 19.5892 | 0.009467% | 20.4577 | 21.3647 | 22.3119 | 23.3011 | 0 | 0 | 0 | 0
2031-10-19 14:00 | 20.5746 | 0.009943% | 21.4868 | 22.4394 | 23.4342 | 24.4732 | 0 | 0 | 0 | 0
2031-10-19 15:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-10-19 16:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-10-19 17:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-10-19 18:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-10-19 19:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-10-19 20:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-10-19 21:00 | 26.7759 | 0.01294% | 27.963 | 29.2027 | 30.4974 | 31.8495 | 0 | 0 | 0 | 0
2031-10-19 22:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-10-19 23:00 | 25.5934 | 0.01237% | 26.7281 | 27.9131 | 29.1506 | 30.443 | 0 | 0 | 0 | 0
2031-10-20 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-10-20 01:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-10-20 02:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-10-20 03:00 | 18.8929 | 0.00913% | 19.7305 | 20.6052 | 21.5188 | 22.4728 | 0 | 0 | 0 | 0
2031-10-20 04:00 | 16.6068 | 0.008025% | 17.3431 | 18.112 | 18.915 | 19.7536 | 0 | 0 | 0 | 0
2031-10-20 05:00 | 15.1485 | 0.007321% | 15.8201 | 16.5215 | 17.2539 | 18.0189 | 0 | 0 | 0 | 0
2031-10-20 06:00 | 14.1762 | 0.006851% | 14.8047 | 15.4611 | 16.1466 | 16.8624 | 0 | 0 | 0 | 0
2031-10-20 07:00 | 13.4799 | 0.006514% | 14.0775 | 14.7017 | 15.3535 | 16.0342 | 0 | 0 | 0 | 0
2031-10-20 08:00 | 13.5719 | 0.006559% | 14.1736 | 14.802 | 15.4582 | 16.1436 | 0 | 0 | 0 | 0
2031-10-20 09:00 | 14.6492 | 0.007079% | 15.2987 | 15.9769 | 16.6853 | 17.425 | 0 | 0 | 0 | 0
2031-10-20 10:00 | 17.6185 | 0.008514% | 18.3996 | 19.2153 | 20.0672 | 20.9569 | 0 | 0 | 0 | 0
2031-10-20 11:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-10-20 12:00 | 21.0081 | 0.01015% | 21.9395 | 22.9122 | 23.9281 | 24.9889 | 0 | 0 | 0 | 0
2031-10-20 13:00 | 21.4943 | 0.01039% | 22.4472 | 23.4424 | 24.4817 | 25.5671 | 0 | 0 | 0 | 0
2031-10-20 14:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-10-20 15:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-10-20 16:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-10-20 17:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-10-20 18:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-10-20 19:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-10-20 20:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-10-20 21:00 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-10-20 22:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-10-20 23:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-10-21 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-10-21 01:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-10-21 02:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-10-21 03:00 | 19.3002 | 0.009327% | 20.1558 | 21.0494 | 21.9827 | 22.9573 | 0 | 0 | 0 | 0
2031-10-21 04:00 | 17.4477 | 0.008432% | 18.2212 | 19.029 | 19.8727 | 20.7538 | 0 | 0 | 0 | 0
2031-10-21 05:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-10-21 06:00 | 15.0565 | 0.007276% | 15.724 | 16.4211 | 17.1492 | 17.9095 | 0 | 0 | 0 | 0
2031-10-21 07:00 | 14.5178 | 0.007016% | 15.1615 | 15.8337 | 16.5356 | 17.2688 | 0 | 0 | 0 | 0
2031-10-21 08:00 | 14.9908 | 0.007245% | 15.6554 | 16.3495 | 17.0744 | 17.8314 | 0 | 0 | 0 | 0
2031-10-21 09:00 | 16.0944 | 0.007778% | 16.808 | 17.5531 | 18.3314 | 19.1441 | 0 | 0 | 0 | 0
2031-10-21 10:00 | 18.998 | 0.009181% | 19.8403 | 20.7199 | 21.6385 | 22.5978 | 0 | 0 | 0 | 0
2031-10-21 11:00 | 21.0476 | 0.01017% | 21.9807 | 22.9552 | 23.9729 | 25.0358 | 0 | 0 | 0 | 0
2031-10-21 12:00 | 21.468 | 0.01037% | 22.4198 | 23.4138 | 24.4518 | 25.5359 | 0 | 0 | 0 | 0
2031-10-21 13:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-10-21 14:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-10-21 15:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-10-21 16:00 | 22.1906 | 0.01072% | 23.1744 | 24.2019 | 25.2748 | 26.3954 | 0 | 0 | 0 | 0
2031-10-21 17:00 | 22.4008 | 0.01083% | 23.3939 | 24.4311 | 25.5143 | 26.6455 | 0 | 0 | 0 | 0
2031-10-21 18:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-10-21 19:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-10-21 20:00 | 23.3993 | 0.01131% | 24.4367 | 25.5201 | 26.6516 | 27.8332 | 0 | 0 | 0 | 0
2031-10-21 21:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-10-21 22:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-10-21 23:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-10-22 | 23.5307 | 0.01137% | 24.5739 | 25.6634 | 26.8012 | 27.9895 | 0 | 0 | 0 | 0
2031-10-22 01:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-10-22 02:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-10-22 03:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-10-22 04:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-10-22 05:00 | 15.5163 | 0.007498% | 16.2042 | 16.9227 | 17.6729 | 18.4565 | 0 | 0 | 0 | 0
2031-10-22 06:00 | 14.7412 | 0.007124% | 15.3947 | 16.0773 | 16.79 | 17.5344 | 0 | 0 | 0 | 0
2031-10-22 07:00 | 14.2682 | 0.006895% | 14.9008 | 15.5614 | 16.2513 | 16.9718 | 0 | 0 | 0 | 0
2031-10-22 08:00 | 14.3602 | 0.00694% | 14.9968 | 15.6617 | 16.3561 | 17.0812 | 0 | 0 | 0 | 0
2031-10-22 09:00 | 15.7922 | 0.007632% | 16.4924 | 17.2236 | 17.9872 | 18.7847 | 0 | 0 | 0 | 0
2031-10-22 10:00 | 18.2622 | 0.008825% | 19.0719 | 19.9175 | 20.8005 | 21.7227 | 0 | 0 | 0 | 0
2031-10-22 11:00 | 20.8899 | 0.0101% | 21.8161 | 22.7833 | 23.7934 | 24.8483 | 0 | 0 | 0 | 0
2031-10-22 12:00 | 21.1132 | 0.0102% | 22.0493 | 23.0269 | 24.0478 | 25.1139 | 0 | 0 | 0 | 0
2031-10-22 13:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-10-22 14:00 | 21.941 | 0.0106% | 22.9137 | 23.9296 | 24.9905 | 26.0985 | 0 | 0 | 0 | 0
2031-10-22 15:00 | 21.849 | 0.01056% | 22.8177 | 23.8293 | 24.8858 | 25.9891 | 0 | 0 | 0 | 0
2031-10-22 16:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-10-22 17:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-10-22 18:00 | 21.7439 | 0.01051% | 22.7079 | 23.7147 | 24.7661 | 25.8641 | 0 | 0 | 0 | 0
2031-10-22 19:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-10-22 20:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-10-22 21:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-10-22 22:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-10-22 23:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-10-23 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-10-23 01:00 | 23.2942 | 0.01126% | 24.327 | 25.4055 | 26.5319 | 27.7081 | 0 | 0 | 0 | 0
2031-10-23 02:00 | 21.5599 | 0.01042% | 22.5158 | 23.5141 | 24.5566 | 25.6453 | 0 | 0 | 0 | 0
2031-10-23 03:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-10-23 04:00 | 17.4345 | 0.008425% | 18.2075 | 19.0147 | 19.8577 | 20.7381 | 0 | 0 | 0 | 0
2031-10-23 05:00 | 16.1076 | 0.007784% | 16.8217 | 17.5675 | 18.3463 | 19.1597 | 0 | 0 | 0 | 0
2031-10-23 06:00 | 15.2141 | 0.007352% | 15.8887 | 16.5931 | 17.3288 | 18.097 | 0 | 0 | 0 | 0
2031-10-23 07:00 | 14.9514 | 0.007225% | 15.6143 | 16.3065 | 17.0295 | 17.7845 | 0 | 0 | 0 | 0
2031-10-23 08:00 | 14.8069 | 0.007156% | 15.4633 | 16.1489 | 16.8649 | 17.6126 | 0 | 0 | 0 | 0
2031-10-23 09:00 | 16.4754 | 0.007962% | 17.2059 | 17.9687 | 18.7653 | 19.5973 | 0 | 0 | 0 | 0
2031-10-23 10:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-10-23 11:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-10-23 12:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-10-23 13:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-10-23 14:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-10-23 15:00 | 22.2957 | 0.01077% | 23.2842 | 24.3165 | 25.3946 | 26.5204 | 0 | 0 | 0 | 0
2031-10-23 16:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-10-23 17:00 | 21.9541 | 0.01061% | 22.9274 | 23.9439 | 25.0055 | 26.1141 | 0 | 0 | 0 | 0
2031-10-23 18:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-10-23 19:00 | 22.4402 | 0.01084% | 23.4351 | 24.4741 | 25.5592 | 26.6923 | 0 | 0 | 0 | 0
2031-10-23 20:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-10-23 21:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-10-23 22:00 | 24.8051 | 0.01199% | 25.9048 | 27.0533 | 28.2528 | 29.5053 | 0 | 0 | 0 | 0
2031-10-23 23:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-10-24 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-10-24 01:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-10-24 02:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-10-24 03:00 | 19.2345 | 0.009295% | 20.0872 | 20.9778 | 21.9079 | 22.8791 | 0 | 0 | 0 | 0
2031-10-24 04:00 | 17.5659 | 0.008489% | 18.3447 | 19.158 | 20.0074 | 20.8944 | 0 | 0 | 0 | 0
2031-10-24 05:00 | 16.3178 | 0.007886% | 17.0412 | 17.7967 | 18.5858 | 19.4098 | 0 | 0 | 0 | 0
2031-10-24 06:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-10-24 07:00 | 14.9382 | 0.007219% | 15.6005 | 16.2922 | 17.0145 | 17.7688 | 0 | 0 | 0 | 0
2031-10-24 08:00 | 15.0302 | 0.007264% | 15.6966 | 16.3925 | 17.1193 | 17.8782 | 0 | 0 | 0 | 0
2031-10-24 09:00 | 16.2127 | 0.007835% | 16.9315 | 17.6821 | 18.4661 | 19.2847 | 0 | 0 | 0 | 0
2031-10-24 10:00 | 18.433 | 0.008908% | 19.2503 | 20.1037 | 20.995 | 21.9259 | 0 | 0 | 0 | 0
2031-10-24 11:00 | 20.4957 | 0.009905% | 21.4044 | 22.3534 | 23.3444 | 24.3794 | 0 | 0 | 0 | 0
2031-10-24 12:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-10-24 13:00 | 22.0986 | 0.01068% | 23.0784 | 24.1015 | 25.1701 | 26.286 | 0 | 0 | 0 | 0
2031-10-24 14:00 | 22.4665 | 0.01086% | 23.4625 | 24.5028 | 25.5891 | 26.7236 | 0 | 0 | 0 | 0
2031-10-24 15:00 | 22.611 | 0.01093% | 23.6135 | 24.6604 | 25.7537 | 26.8955 | 0 | 0 | 0 | 0
2031-10-24 16:00 | 22.9657 | 0.0111% | 23.9839 | 25.0473 | 26.1577 | 27.3175 | 0 | 0 | 0 | 0
2031-10-24 17:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-10-24 18:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-10-24 19:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-10-24 20:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-10-24 21:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-10-24 22:00 | 24.0037 | 0.0116% | 25.0679 | 26.1793 | 27.3399 | 28.5521 | 0 | 0 | 0 | 0
2031-10-24 23:00 | 24.1876 | 0.01169% | 25.26 | 26.3799 | 27.5494 | 28.7708 | 0 | 0 | 0 | 0
2031-10-25 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-10-25 01:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-10-25 02:00 | 21.6388 | 0.01046% | 22.5981 | 23.6 | 24.6463 | 25.739 | 0 | 0 | 0 | 0
2031-10-25 03:00 | 19.7863 | 0.009562% | 20.6635 | 21.5796 | 22.5364 | 23.5355 | 0 | 0 | 0 | 0
2031-10-25 04:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-10-25 05:00 | 17.0929 | 0.00826% | 17.8507 | 18.6422 | 19.4687 | 20.3318 | 0 | 0 | 0 | 0
2031-10-25 06:00 | 16.1995 | 0.007829% | 16.9177 | 17.6678 | 18.4511 | 19.2691 | 0 | 0 | 0 | 0
2031-10-25 07:00 | 15.5426 | 0.007511% | 16.2317 | 16.9513 | 17.7029 | 18.4877 | 0 | 0 | 0 | 0
2031-10-25 08:00 | 15.3718 | 0.007429% | 16.0533 | 16.765 | 17.5083 | 18.2846 | 0 | 0 | 0 | 0
2031-10-25 09:00 | 15.5295 | 0.007505% | 16.218 | 16.937 | 17.6879 | 18.4721 | 0 | 0 | 0 | 0
2031-10-25 10:00 | 16.3703 | 0.007911% | 17.0961 | 17.8541 | 18.6456 | 19.4723 | 0 | 0 | 0 | 0
2031-10-25 11:00 | 18.2097 | 0.0088% | 19.017 | 19.8601 | 20.7406 | 21.6602 | 0 | 0 | 0 | 0
2031-10-25 12:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-10-25 13:00 | 21.6388 | 0.01046% | 22.5981 | 23.6 | 24.6463 | 25.739 | 0 | 0 | 0 | 0
2031-10-25 14:00 | 22.0723 | 0.01067% | 23.0509 | 24.0729 | 25.1402 | 26.2548 | 0 | 0 | 0 | 0
2031-10-25 15:00 | 22.3088 | 0.01078% | 23.2979 | 24.3308 | 25.4095 | 26.5361 | 0 | 0 | 0 | 0
2031-10-25 16:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-10-25 17:00 | 23.2548 | 0.01124% | 24.2858 | 25.3625 | 26.487 | 27.6613 | 0 | 0 | 0 | 0
2031-10-25 18:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-10-25 19:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-10-25 20:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-10-25 21:00 | 24.2139 | 0.0117% | 25.2874 | 26.4085 | 27.5794 | 28.8021 | 0 | 0 | 0 | 0
2031-10-25 22:00 | 24.608 | 0.01189% | 25.699 | 26.8384 | 28.0283 | 29.2709 | 0 | 0 | 0 | 0
2031-10-25 23:00 | 24.3453 | 0.01177% | 25.4246 | 26.5518 | 27.729 | 28.9584 | 0 | 0 | 0 | 0
2031-10-26 | 23.8066 | 0.0115% | 24.8621 | 25.9643 | 27.1155 | 28.3176 | 0 | 0 | 0 | 0
2031-10-26 01:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-10-26 02:00 | 21.5994 | 0.01044% | 22.557 | 23.557 | 24.6014 | 25.6922 | 0 | 0 | 0 | 0
2031-10-26 03:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-10-26 04:00 | 18.617 | 0.008997% | 19.4424 | 20.3043 | 21.2045 | 22.1446 | 0 | 0 | 0 | 0
2031-10-26 05:00 | 17.1323 | 0.008279% | 17.8919 | 18.6851 | 19.5136 | 20.3787 | 0 | 0 | 0 | 0
2031-10-26 06:00 | 16.1601 | 0.00781% | 16.8766 | 17.6248 | 18.4062 | 19.2222 | 0 | 0 | 0 | 0
2031-10-26 07:00 | 15.9368 | 0.007702% | 16.6433 | 17.3812 | 18.1518 | 18.9566 | 0 | 0 | 0 | 0
2031-10-26 08:00 | 15.8185 | 0.007645% | 16.5198 | 17.2522 | 18.0171 | 18.8159 | 0 | 0 | 0 | 0
2031-10-26 09:00 | 16.0419 | 0.007752% | 16.7531 | 17.4958 | 18.2715 | 19.0816 | 0 | 0 | 0 | 0
2031-10-26 10:00 | 16.6068 | 0.008025% | 17.3431 | 18.112 | 18.915 | 19.7536 | 0 | 0 | 0 | 0
2031-10-26 11:00 | 18.2228 | 0.008806% | 19.0307 | 19.8745 | 20.7556 | 21.6758 | 0 | 0 | 0 | 0
2031-10-26 12:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-10-26 13:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-10-26 14:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-10-26 15:00 | 22.4796 | 0.01086% | 23.4763 | 24.5171 | 25.6041 | 26.7392 | 0 | 0 | 0 | 0
2031-10-26 16:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-10-26 17:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-10-26 18:00 | 23.0183 | 0.01112% | 24.0388 | 25.1046 | 26.2176 | 27.38 | 0 | 0 | 0 | 0
2031-10-26 19:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-10-26 20:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-10-26 21:00 | 26.2503 | 0.01269% | 27.4141 | 28.6295 | 29.8988 | 31.2244 | 0 | 0 | 0 | 0
2031-10-26 22:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-10-26 23:00 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-10-27 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-10-27 01:00 | 24.7263 | 0.01195% | 25.8225 | 26.9674 | 28.163 | 29.4116 | 0 | 0 | 0 | 0
2031-10-27 02:00 | 22.8475 | 0.01104% | 23.8604 | 24.9183 | 26.0231 | 27.1768 | 0 | 0 | 0 | 0
2031-10-27 03:00 | 20.5089 | 0.009911% | 21.4181 | 22.3677 | 23.3594 | 24.395 | 0 | 0 | 0 | 0
2031-10-27 04:00 | 18.4199 | 0.008902% | 19.2365 | 20.0894 | 20.9801 | 21.9102 | 0 | 0 | 0 | 0
2031-10-27 05:00 | 16.9484 | 0.008191% | 17.6998 | 18.4845 | 19.3041 | 20.1599 | 0 | 0 | 0 | 0
2031-10-27 06:00 | 16.0681 | 0.007765% | 16.7805 | 17.5245 | 18.3014 | 19.1128 | 0 | 0 | 0 | 0
2031-10-27 07:00 | 15.7265 | 0.0076% | 16.4238 | 17.1519 | 17.9124 | 18.7065 | 0 | 0 | 0 | 0
2031-10-27 08:00 | 16.1338 | 0.007797% | 16.8491 | 17.5961 | 18.3763 | 19.191 | 0 | 0 | 0 | 0
2031-10-27 09:00 | 17.4477 | 0.008432% | 18.2212 | 19.029 | 19.8727 | 20.7538 | 0 | 0 | 0 | 0
2031-10-27 10:00 | 20.3644 | 0.009841% | 21.2672 | 22.2101 | 23.1948 | 24.2231 | 0 | 0 | 0 | 0
2031-10-27 11:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-10-27 12:00 | 23.1891 | 0.01121% | 24.2172 | 25.2909 | 26.4121 | 27.5831 | 0 | 0 | 0 | 0
2031-10-27 13:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-10-27 14:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-10-27 15:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-10-27 16:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-10-27 17:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-10-27 18:00 | 23.1234 | 0.01117% | 24.1486 | 25.2192 | 26.3373 | 27.505 | 0 | 0 | 0 | 0
2031-10-27 19:00 | 22.8212 | 0.01103% | 23.833 | 24.8896 | 25.9931 | 27.1455 | 0 | 0 | 0 | 0
2031-10-27 20:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-10-27 21:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-10-27 22:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-10-27 23:00 | 26.2897 | 0.0127% | 27.4553 | 28.6725 | 29.9437 | 31.2713 | 0 | 0 | 0 | 0
2031-10-28 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-10-28 01:00 | 24.608 | 0.01189% | 25.699 | 26.8384 | 28.0283 | 29.2709 | 0 | 0 | 0 | 0
2031-10-28 02:00 | 23.0577 | 0.01114% | 24.08 | 25.1476 | 26.2625 | 27.4268 | 0 | 0 | 0 | 0
2031-10-28 03:00 | 20.5089 | 0.009911% | 21.4181 | 22.3677 | 23.3594 | 24.395 | 0 | 0 | 0 | 0
2031-10-28 04:00 | 18.8009 | 0.009086% | 19.6344 | 20.5049 | 21.414 | 22.3634 | 0 | 0 | 0 | 0
2031-10-28 05:00 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-10-28 06:00 | 16.909 | 0.008172% | 17.6587 | 18.4416 | 19.2592 | 20.113 | 0 | 0 | 0 | 0
2031-10-28 07:00 | 16.3309 | 0.007892% | 17.0549 | 17.8111 | 18.6007 | 19.4254 | 0 | 0 | 0 | 0
2031-10-28 08:00 | 16.1732 | 0.007816% | 16.8903 | 17.6391 | 18.4212 | 19.2379 | 0 | 0 | 0 | 0
2031-10-28 09:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-10-28 10:00 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-10-28 11:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-10-28 12:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-10-28 13:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-10-28 14:00 | 23.1365 | 0.01118% | 24.1623 | 25.2335 | 26.3523 | 27.5206 | 0 | 0 | 0 | 0
2031-10-28 15:00 | 23.4256 | 0.01132% | 24.4642 | 25.5488 | 26.6815 | 27.8644 | 0 | 0 | 0 | 0
2031-10-28 16:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-10-28 17:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-10-28 18:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-10-28 19:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-10-28 20:00 | 23.9511 | 0.01157% | 25.013 | 26.122 | 27.2801 | 28.4895 | 0 | 0 | 0 | 0
2031-10-28 21:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-10-28 22:00 | 25.554 | 0.01235% | 26.6869 | 27.8701 | 29.1057 | 30.3961 | 0 | 0 | 0 | 0
2031-10-28 23:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-10-29 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-10-29 01:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-10-29 02:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-10-29 03:00 | 20.0359 | 0.009683% | 20.9242 | 21.8519 | 22.8207 | 23.8324 | 0 | 0 | 0 | 0
2031-10-29 04:00 | 18.3279 | 0.008857% | 19.1405 | 19.9891 | 20.8753 | 21.8008 | 0 | 0 | 0 | 0
2031-10-29 05:00 | 16.7776 | 0.008108% | 17.5214 | 18.2983 | 19.1095 | 19.9567 | 0 | 0 | 0 | 0
2031-10-29 06:00 | 16.0156 | 0.00774% | 16.7256 | 17.4672 | 18.2416 | 19.0503 | 0 | 0 | 0 | 0
2031-10-29 07:00 | 15.5689 | 0.007524% | 16.2591 | 16.98 | 17.7328 | 18.519 | 0 | 0 | 0 | 0
2031-10-29 08:00 | 15.8842 | 0.007676% | 16.5884 | 17.3239 | 18.0919 | 18.8941 | 0 | 0 | 0 | 0
2031-10-29 09:00 | 17.3426 | 0.008381% | 18.1114 | 18.9144 | 19.753 | 20.6287 | 0 | 0 | 0 | 0
2031-10-29 10:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-10-29 11:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-10-29 12:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-10-29 13:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-10-29 14:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-10-29 15:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-10-29 16:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-10-29 17:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-10-29 18:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-10-29 19:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-10-29 20:00 | 23.7935 | 0.0115% | 24.8483 | 25.95 | 27.1005 | 28.302 | 0 | 0 | 0 | 0
2031-10-29 21:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-10-29 22:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-10-29 23:00 | 25.7905 | 0.01246% | 26.9339 | 28.128 | 29.3751 | 30.6774 | 0 | 0 | 0 | 0
2031-10-30 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-10-30 01:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-10-30 02:00 | 22.7424 | 0.01099% | 23.7507 | 24.8037 | 25.9033 | 27.0518 | 0 | 0 | 0 | 0
2031-10-30 03:00 | 20.6534 | 0.009981% | 21.5691 | 22.5253 | 23.524 | 24.567 | 0 | 0 | 0 | 0
2031-10-30 04:00 | 18.2622 | 0.008825% | 19.0719 | 19.9175 | 20.8005 | 21.7227 | 0 | 0 | 0 | 0
2031-10-30 05:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-10-30 06:00 | 15.8054 | 0.007638% | 16.5061 | 17.2379 | 18.0022 | 18.8003 | 0 | 0 | 0 | 0
2031-10-30 07:00 | 15.3849 | 0.007435% | 16.067 | 16.7794 | 17.5233 | 18.3002 | 0 | 0 | 0 | 0
2031-10-30 08:00 | 15.3981 | 0.007441% | 16.0808 | 16.7937 | 17.5383 | 18.3158 | 0 | 0 | 0 | 0
2031-10-30 09:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-10-30 10:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-10-30 11:00 | 22.1512 | 0.0107% | 23.1332 | 24.1589 | 25.23 | 26.3485 | 0 | 0 | 0 | 0
2031-10-30 12:00 | 22.9789 | 0.0111% | 23.9977 | 25.0616 | 26.1727 | 27.3331 | 0 | 0 | 0 | 0
2031-10-30 13:00 | 23.9905 | 0.01159% | 25.0542 | 26.1649 | 27.325 | 28.5364 | 0 | 0 | 0 | 0
2031-10-30 14:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-10-30 15:00 | 24.4898 | 0.01184% | 25.5755 | 26.7094 | 27.8936 | 29.1303 | 0 | 0 | 0 | 0
2031-10-30 16:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-10-30 17:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-10-30 18:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-10-30 19:00 | 25.2387 | 0.0122% | 26.3576 | 27.5262 | 28.7466 | 30.0211 | 0 | 0 | 0 | 0
2031-10-30 20:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-10-30 21:00 | 27.5641 | 0.01332% | 28.7862 | 30.0625 | 31.3953 | 32.7872 | 0 | 0 | 0 | 0
2031-10-30 22:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-10-30 23:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-10-31 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-10-31 01:00 | 25.6722 | 0.01241% | 26.8104 | 27.9991 | 29.2404 | 30.5368 | 0 | 0 | 0 | 0
2031-10-31 02:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-10-31 03:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-10-31 04:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-10-31 05:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-10-31 06:00 | 16.528 | 0.007987% | 17.2608 | 18.026 | 18.8252 | 19.6598 | 0 | 0 | 0 | 0
2031-10-31 07:00 | 15.9499 | 0.007708% | 16.657 | 17.3955 | 18.1668 | 18.9722 | 0 | 0 | 0 | 0
2031-10-31 08:00 | 16.0419 | 0.007752% | 16.7531 | 17.4958 | 18.2715 | 19.0816 | 0 | 0 | 0 | 0
2031-10-31 09:00 | 17.3294 | 0.008375% | 18.0977 | 18.9001 | 19.738 | 20.6131 | 0 | 0 | 0 | 0
2031-10-31 10:00 | 20.233 | 0.009778% | 21.13 | 22.0668 | 23.0452 | 24.0669 | 0 | 0 | 0 | 0
2031-10-31 11:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-10-31 12:00 | 23.5044 | 0.01136% | 24.5465 | 25.6348 | 26.7713 | 27.9582 | 0 | 0 | 0 | 0
2031-10-31 13:00 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-10-31 14:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-10-31 15:00 | 24.5949 | 0.01189% | 25.6853 | 26.8241 | 28.0133 | 29.2553 | 0 | 0 | 0 | 0
2031-10-31 16:00 | 24.5292 | 0.01185% | 25.6167 | 26.7524 | 27.9385 | 29.1772 | 0 | 0 | 0 | 0
2031-10-31 17:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-10-31 18:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-10-31 19:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-10-31 20:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-10-31 21:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-10-31 22:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-10-31 23:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-11-01 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-11-01 01:00 | 23.0314 | 0.01113% | 24.0525 | 25.1189 | 26.2326 | 27.3956 | 0 | 0 | 0 | 0
2031-11-01 02:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-11-01 03:00 | 20.6271 | 0.009968% | 21.5416 | 22.4967 | 23.4941 | 24.5357 | 0 | 0 | 0 | 0
2031-11-01 04:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-11-01 05:00 | 17.5265 | 0.00847% | 18.3035 | 19.115 | 19.9625 | 20.8475 | 0 | 0 | 0 | 0
2031-11-01 06:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-11-01 07:00 | 16.1601 | 0.00781% | 16.8766 | 17.6248 | 18.4062 | 19.2222 | 0 | 0 | 0 | 0
2031-11-01 08:00 | 15.6346 | 0.007556% | 16.3277 | 17.0516 | 17.8076 | 18.5971 | 0 | 0 | 0 | 0
2031-11-01 09:00 | 15.7922 | 0.007632% | 16.4924 | 17.2236 | 17.9872 | 18.7847 | 0 | 0 | 0 | 0
2031-11-01 10:00 | 16.8039 | 0.008121% | 17.5489 | 18.3269 | 19.1394 | 19.988 | 0 | 0 | 0 | 0
2031-11-01 11:00 | 18.2491 | 0.008819% | 19.0582 | 19.9031 | 20.7855 | 21.7071 | 0 | 0 | 0 | 0
2031-11-01 12:00 | 20.2198 | 0.009772% | 21.1163 | 22.0525 | 23.0302 | 24.0512 | 0 | 0 | 0 | 0
2031-11-01 13:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-11-01 14:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-11-01 15:00 | 23.1497 | 0.01119% | 24.176 | 25.2479 | 26.3672 | 27.5362 | 0 | 0 | 0 | 0
2031-11-01 16:00 | 23.3862 | 0.0113% | 24.423 | 25.5058 | 26.6366 | 27.8175 | 0 | 0 | 0 | 0
2031-11-01 17:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-11-01 18:00 | 23.5832 | 0.0114% | 24.6288 | 25.7207 | 26.8611 | 28.052 | 0 | 0 | 0 | 0
2031-11-01 19:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-11-01 20:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-11-01 21:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-11-01 22:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-11-01 23:00 | 25.843 | 0.01249% | 26.9888 | 28.1853 | 29.4349 | 30.7399 | 0 | 0 | 0 | 0
2031-11-02 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-11-02 01:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-11-02 02:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-11-02 03:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-11-02 04:00 | 19.9834 | 0.009657% | 20.8693 | 21.7946 | 22.7608 | 23.7699 | 0 | 0 | 0 | 0
2031-11-02 05:00 | 17.6447 | 0.008527% | 18.427 | 19.244 | 20.0972 | 20.9882 | 0 | 0 | 0 | 0
2031-11-02 06:00 | 16.9221 | 0.008178% | 17.6724 | 18.4559 | 19.2741 | 20.1286 | 0 | 0 | 0 | 0
2031-11-02 07:00 | 16.3309 | 0.007892% | 17.0549 | 17.8111 | 18.6007 | 19.4254 | 0 | 0 | 0 | 0
2031-11-02 08:00 | 16.5674 | 0.008006% | 17.3019 | 18.069 | 18.8701 | 19.7067 | 0 | 0 | 0 | 0
2031-11-02 09:00 | 16.7907 | 0.008114% | 17.5352 | 18.3126 | 19.1245 | 19.9724 | 0 | 0 | 0 | 0
2031-11-02 10:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-11-02 11:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-11-02 12:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-11-02 13:00 | 21.6519 | 0.01046% | 22.6119 | 23.6144 | 24.6613 | 25.7547 | 0 | 0 | 0 | 0
2031-11-02 14:00 | 22.0986 | 0.01068% | 23.0784 | 24.1015 | 25.1701 | 26.286 | 0 | 0 | 0 | 0
2031-11-02 15:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-11-02 16:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-11-02 17:00 | 22.992 | 0.01111% | 24.0114 | 25.0759 | 26.1877 | 27.3487 | 0 | 0 | 0 | 0
2031-11-02 18:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-11-02 19:00 | 23.9774 | 0.01159% | 25.0404 | 26.1506 | 27.31 | 28.5208 | 0 | 0 | 0 | 0
2031-11-02 20:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-11-02 21:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-11-02 22:00 | 28.024 | 0.01354% | 29.2664 | 30.564 | 31.919 | 33.3342 | 0 | 0 | 0 | 0
2031-11-02 23:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-11-03 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-11-03 01:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-11-03 02:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-11-03 03:00 | 19.5761 | 0.00946% | 20.444 | 21.3504 | 22.2969 | 23.2855 | 0 | 0 | 0 | 0
2031-11-03 04:00 | 17.671 | 0.00854% | 18.4545 | 19.2726 | 20.1271 | 21.0194 | 0 | 0 | 0 | 0
2031-11-03 05:00 | 16.5805 | 0.008013% | 17.3156 | 18.0833 | 18.8851 | 19.7223 | 0 | 0 | 0 | 0
2031-11-03 06:00 | 15.9105 | 0.007689% | 16.6159 | 17.3525 | 18.1219 | 18.9253 | 0 | 0 | 0 | 0
2031-11-03 07:00 | 15.5557 | 0.007518% | 16.2454 | 16.9657 | 17.7178 | 18.5034 | 0 | 0 | 0 | 0
2031-11-03 08:00 | 15.7397 | 0.007606% | 16.4375 | 17.1663 | 17.9273 | 18.7221 | 0 | 0 | 0 | 0
2031-11-03 09:00 | 17.3294 | 0.008375% | 18.0977 | 18.9001 | 19.738 | 20.6131 | 0 | 0 | 0 | 0
2031-11-03 10:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-11-03 11:00 | 21.9935 | 0.01063% | 22.9686 | 23.9869 | 25.0504 | 26.161 | 0 | 0 | 0 | 0
2031-11-03 12:00 | 22.7687 | 0.011% | 23.7781 | 24.8323 | 25.9333 | 27.083 | 0 | 0 | 0 | 0
2031-11-03 13:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-11-03 14:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-11-03 15:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-11-03 16:00 | 24.8445 | 0.01201% | 25.946 | 27.0963 | 28.2977 | 29.5522 | 0 | 0 | 0 | 0
2031-11-03 17:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-11-03 18:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-11-03 19:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-11-03 20:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-03 21:00 | 28.2605 | 0.01366% | 29.5134 | 30.8219 | 32.1884 | 33.6155 | 0 | 0 | 0 | 0
2031-11-03 22:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-11-03 23:00 | 26.4211 | 0.01277% | 27.5925 | 28.8158 | 30.0934 | 31.4276 | 0 | 0 | 0 | 0
2031-11-04 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-11-04 01:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-11-04 02:00 | 22.2169 | 0.01074% | 23.2019 | 24.2305 | 25.3048 | 26.4267 | 0 | 0 | 0 | 0
2031-11-04 03:00 | 20.1016 | 0.009714% | 20.9928 | 21.9235 | 22.8955 | 23.9106 | 0 | 0 | 0 | 0
2031-11-04 04:00 | 18.2097 | 0.0088% | 19.017 | 19.8601 | 20.7406 | 21.6602 | 0 | 0 | 0 | 0
2031-11-04 05:00 | 16.8827 | 0.008159% | 17.6312 | 18.4129 | 19.2292 | 20.0818 | 0 | 0 | 0 | 0
2031-11-04 06:00 | 16.147 | 0.007803% | 16.8628 | 17.6105 | 18.3912 | 19.2066 | 0 | 0 | 0 | 0
2031-11-04 07:00 | 15.766 | 0.007619% | 16.4649 | 17.1949 | 17.9573 | 18.7534 | 0 | 0 | 0 | 0
2031-11-04 08:00 | 16.0024 | 0.007733% | 16.7119 | 17.4528 | 18.2266 | 19.0347 | 0 | 0 | 0 | 0
2031-11-04 09:00 | 17.8287 | 0.008616% | 18.6191 | 19.4446 | 20.3067 | 21.207 | 0 | 0 | 0 | 0
2031-11-04 10:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-11-04 11:00 | 22.7161 | 0.01098% | 23.7232 | 24.775 | 25.8734 | 27.0205 | 0 | 0 | 0 | 0
2031-11-04 12:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-11-04 13:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-11-04 14:00 | 23.0446 | 0.01114% | 24.0663 | 25.1332 | 26.2475 | 27.4112 | 0 | 0 | 0 | 0
2031-11-04 15:00 | 23.3468 | 0.01128% | 24.3818 | 25.4628 | 26.5917 | 27.7707 | 0 | 0 | 0 | 0
2031-11-04 16:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-11-04 17:00 | 23.0971 | 0.01116% | 24.1211 | 25.1906 | 26.3074 | 27.4737 | 0 | 0 | 0 | 0
2031-11-04 18:00 | 22.703 | 0.01097% | 23.7095 | 24.7607 | 25.8585 | 27.0049 | 0 | 0 | 0 | 0
2031-11-04 19:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-11-04 20:00 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-11-04 21:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-11-04 22:00 | 26.4474 | 0.01278% | 27.6199 | 28.8445 | 30.1233 | 31.4588 | 0 | 0 | 0 | 0
2031-11-04 23:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-11-05 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-11-05 01:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-11-05 02:00 | 22.1249 | 0.01069% | 23.1058 | 24.1302 | 25.2 | 26.3173 | 0 | 0 | 0 | 0
2031-11-05 03:00 | 19.8651 | 0.0096% | 20.7458 | 21.6656 | 22.6261 | 23.6293 | 0 | 0 | 0 | 0
2031-11-05 04:00 | 17.9601 | 0.008679% | 18.7563 | 19.5879 | 20.4563 | 21.3632 | 0 | 0 | 0 | 0
2031-11-05 05:00 | 16.7907 | 0.008114% | 17.5352 | 18.3126 | 19.1245 | 19.9724 | 0 | 0 | 0 | 0
2031-11-05 06:00 | 15.8054 | 0.007638% | 16.5061 | 17.2379 | 18.0022 | 18.8003 | 0 | 0 | 0 | 0
2031-11-05 07:00 | 15.7134 | 0.007594% | 16.4101 | 17.1376 | 17.8974 | 18.6909 | 0 | 0 | 0 | 0
2031-11-05 08:00 | 15.8316 | 0.007651% | 16.5335 | 17.2666 | 18.0321 | 18.8315 | 0 | 0 | 0 | 0
2031-11-05 09:00 | 17.3163 | 0.008368% | 18.084 | 18.8858 | 19.7231 | 20.5975 | 0 | 0 | 0 | 0
2031-11-05 10:00 | 20.4432 | 0.009879% | 21.3495 | 22.2961 | 23.2846 | 24.3169 | 0 | 0 | 0 | 0
2031-11-05 11:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-11-05 12:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-11-05 13:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-11-05 14:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-11-05 15:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-11-05 16:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-11-05 17:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-11-05 18:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-11-05 19:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-11-05 20:00 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-11-05 21:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-11-05 22:00 | 27.7875 | 0.01343% | 29.0195 | 30.306 | 31.6497 | 33.0529 | 0 | 0 | 0 | 0
2031-11-05 23:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-11-06 | 26.0401 | 0.01258% | 27.1946 | 28.4003 | 29.6594 | 30.9744 | 0 | 0 | 0 | 0
2031-11-06 01:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-11-06 02:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-11-06 03:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-11-06 04:00 | 18.5119 | 0.008946% | 19.3326 | 20.1897 | 21.0848 | 22.0196 | 0 | 0 | 0 | 0
2031-11-06 05:00 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-11-06 06:00 | 16.6068 | 0.008025% | 17.3431 | 18.112 | 18.915 | 19.7536 | 0 | 0 | 0 | 0
2031-11-06 07:00 | 16.3703 | 0.007911% | 17.0961 | 17.8541 | 18.6456 | 19.4723 | 0 | 0 | 0 | 0
2031-11-06 08:00 | 16.4886 | 0.007968% | 17.2196 | 17.983 | 18.7803 | 19.6129 | 0 | 0 | 0 | 0
2031-11-06 09:00 | 18.144 | 0.008768% | 18.9484 | 19.7885 | 20.6658 | 21.582 | 0 | 0 | 0 | 0
2031-11-06 10:00 | 21.6125 | 0.01044% | 22.5707 | 23.5714 | 24.6164 | 25.7078 | 0 | 0 | 0 | 0
2031-11-06 11:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-11-06 12:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-11-06 13:00 | 23.4124 | 0.01131% | 24.4504 | 25.5345 | 26.6665 | 27.8488 | 0 | 0 | 0 | 0
2031-11-06 14:00 | 23.9248 | 0.01156% | 24.9856 | 26.0933 | 27.2501 | 28.4583 | 0 | 0 | 0 | 0
2031-11-06 15:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-11-06 16:00 | 23.6752 | 0.01144% | 24.7249 | 25.821 | 26.9658 | 28.1614 | 0 | 0 | 0 | 0
2031-11-06 17:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-11-06 18:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-11-06 19:00 | 25.1861 | 0.01217% | 26.3027 | 27.4689 | 28.6867 | 29.9586 | 0 | 0 | 0 | 0
2031-11-06 20:00 | 26.6839 | 0.0129% | 27.8669 | 29.1024 | 30.3927 | 31.7401 | 0 | 0 | 0 | 0
2031-11-06 21:00 | 28.2473 | 0.01365% | 29.4997 | 30.8076 | 32.1734 | 33.5998 | 0 | 0 | 0 | 0
2031-11-06 22:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-11-06 23:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-11-07 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-11-07 01:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-11-07 02:00 | 23.557 | 0.01138% | 24.6014 | 25.6921 | 26.8311 | 28.0207 | 0 | 0 | 0 | 0
2031-11-07 03:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-11-07 04:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-11-07 05:00 | 18.1965 | 0.008794% | 19.0033 | 19.8458 | 20.7257 | 21.6445 | 0 | 0 | 0 | 0
2031-11-07 06:00 | 17.579 | 0.008495% | 18.3584 | 19.1723 | 20.0223 | 20.91 | 0 | 0 | 0 | 0
2031-11-07 07:00 | 17.0666 | 0.008248% | 17.8233 | 18.6135 | 19.4387 | 20.3006 | 0 | 0 | 0 | 0
2031-11-07 08:00 | 17.0141 | 0.008222% | 17.7684 | 18.5562 | 19.3789 | 20.238 | 0 | 0 | 0 | 0
2031-11-07 09:00 | 18.4987 | 0.00894% | 19.3189 | 20.1754 | 21.0699 | 22.004 | 0 | 0 | 0 | 0
2031-11-07 10:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-11-07 11:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-11-07 12:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-11-07 13:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-11-07 14:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-11-07 15:00 | 25.7511 | 0.01244% | 26.8927 | 28.085 | 29.3302 | 30.6306 | 0 | 0 | 0 | 0
2031-11-07 16:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-11-07 17:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-11-07 18:00 | 24.8182 | 0.01199% | 25.9186 | 27.0677 | 28.2677 | 29.521 | 0 | 0 | 0 | 0
2031-11-07 19:00 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-11-07 20:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-07 21:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-11-07 22:00 | 26.4999 | 0.01281% | 27.6748 | 28.9018 | 30.1832 | 31.5213 | 0 | 0 | 0 | 0
2031-11-07 23:00 | 25.4226 | 0.01229% | 26.5497 | 27.7268 | 28.9561 | 30.2399 | 0 | 0 | 0 | 0
2031-11-08 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-11-08 01:00 | 23.7672 | 0.01149% | 24.8209 | 25.9213 | 27.0706 | 28.2708 | 0 | 0 | 0 | 0
2031-11-08 02:00 | 22.4271 | 0.01084% | 23.4214 | 24.4598 | 25.5442 | 26.6767 | 0 | 0 | 0 | 0
2031-11-08 03:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-11-08 04:00 | 18.7089 | 0.009041% | 19.5384 | 20.4046 | 21.3093 | 22.254 | 0 | 0 | 0 | 0
2031-11-08 05:00 | 17.4608 | 0.008438% | 18.2349 | 19.0434 | 19.8877 | 20.7694 | 0 | 0 | 0 | 0
2031-11-08 06:00 | 16.4754 | 0.007962% | 17.2059 | 17.9687 | 18.7653 | 19.5973 | 0 | 0 | 0 | 0
2031-11-08 07:00 | 16.055 | 0.007759% | 16.7668 | 17.5102 | 18.2865 | 19.0972 | 0 | 0 | 0 | 0
2031-11-08 08:00 | 15.8054 | 0.007638% | 16.5061 | 17.2379 | 18.0022 | 18.8003 | 0 | 0 | 0 | 0
2031-11-08 09:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-11-08 10:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-11-08 11:00 | 19.3133 | 0.009333% | 20.1696 | 21.0638 | 21.9976 | 22.9729 | 0 | 0 | 0 | 0
2031-11-08 12:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-11-08 13:00 | 22.0066 | 0.01064% | 22.9823 | 24.0012 | 25.0653 | 26.1766 | 0 | 0 | 0 | 0
2031-11-08 14:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-11-08 15:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-11-08 16:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-11-08 17:00 | 22.9526 | 0.01109% | 23.9702 | 25.0329 | 26.1428 | 27.3018 | 0 | 0 | 0 | 0
2031-11-08 18:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-11-08 19:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-11-08 20:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-11-08 21:00 | 27.3671 | 0.01323% | 28.5804 | 29.8475 | 31.1708 | 32.5528 | 0 | 0 | 0 | 0
2031-11-08 22:00 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-11-08 23:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-11-09 | 24.9102 | 0.01204% | 26.0146 | 27.168 | 28.3725 | 29.6304 | 0 | 0 | 0 | 0
2031-11-09 01:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-11-09 02:00 | 22.7818 | 0.01101% | 23.7918 | 24.8467 | 25.9482 | 27.0987 | 0 | 0 | 0 | 0
2031-11-09 03:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-11-09 04:00 | 19.4315 | 0.009391% | 20.293 | 21.1927 | 22.1323 | 23.1136 | 0 | 0 | 0 | 0
2031-11-09 05:00 | 18.1046 | 0.008749% | 18.9072 | 19.7455 | 20.6209 | 21.5352 | 0 | 0 | 0 | 0
2031-11-09 06:00 | 17.0404 | 0.008235% | 17.7959 | 18.5848 | 19.4088 | 20.2693 | 0 | 0 | 0 | 0
2031-11-09 07:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-11-09 08:00 | 16.7513 | 0.008095% | 17.494 | 18.2696 | 19.0796 | 19.9255 | 0 | 0 | 0 | 0
2031-11-09 09:00 | 17.0666 | 0.008248% | 17.8233 | 18.6135 | 19.4387 | 20.3006 | 0 | 0 | 0 | 0
2031-11-09 10:00 | 18.1309 | 0.008762% | 18.9347 | 19.7742 | 20.6509 | 21.5664 | 0 | 0 | 0 | 0
2031-11-09 11:00 | 19.852 | 0.009594% | 20.7321 | 21.6513 | 22.6112 | 23.6137 | 0 | 0 | 0 | 0
2031-11-09 12:00 | 22.0461 | 0.01065% | 23.0235 | 24.0442 | 25.1102 | 26.2235 | 0 | 0 | 0 | 0
2031-11-09 13:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-11-09 14:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-11-09 15:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-11-09 16:00 | 28.2079 | 0.01363% | 29.4585 | 30.7646 | 32.1285 | 33.553 | 0 | 0 | 0 | 0
2031-11-09 17:00 | 28.1554 | 0.01361% | 29.4036 | 30.7073 | 32.0687 | 33.4904 | 0 | 0 | 0 | 0
2031-11-09 18:00 | 28.2473 | 0.01365% | 29.4997 | 30.8076 | 32.1734 | 33.5998 | 0 | 0 | 0 | 0
2031-11-09 19:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-11-09 20:00 | 30.8487 | 0.01491% | 32.2164 | 33.6447 | 35.1364 | 36.6942 | 0 | 0 | 0 | 0
2031-11-09 21:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-11-09 22:00 | 20.3644 | 0.009841% | 21.2672 | 22.2101 | 23.1948 | 24.2231 | 0 | 0 | 0 | 0
2031-11-09 23:00 | 33.7523 | 0.01631% | 35.2487 | 36.8115 | 38.4435 | 40.1479 | 0 | 0 | 1.2992 | 2.8331
2031-11-10 | 30.7305 | 0.01485% | 32.0929 | 33.5158 | 35.0017 | 36.5535 | 0 | 0 | 0 | 0
2031-11-10 01:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-11-10 02:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-11-10 03:00 | 22.4928 | 0.01087% | 23.49 | 24.5314 | 25.619 | 26.7549 | 0 | 0 | 0 | 0
2031-11-10 04:00 | 20.3249 | 0.009822% | 21.2261 | 22.1671 | 23.1499 | 24.1763 | 0 | 0 | 0 | 0
2031-11-10 05:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-11-10 06:00 | 18.4199 | 0.008902% | 19.2365 | 20.0894 | 20.9801 | 21.9102 | 0 | 0 | 0 | 0
2031-11-10 07:00 | 18.0257 | 0.008711% | 18.8249 | 19.6595 | 20.5311 | 21.4414 | 0 | 0 | 0 | 0
2031-11-10 08:00 | 18.1571 | 0.008775% | 18.9621 | 19.8028 | 20.6808 | 21.5977 | 0 | 0 | 0 | 0
2031-11-10 09:00 | 19.8914 | 0.009613% | 20.7733 | 21.6943 | 22.6561 | 23.6605 | 0 | 0 | 0 | 0
2031-11-10 10:00 | 22.6241 | 0.01093% | 23.6272 | 24.6747 | 25.7687 | 26.9111 | 0 | 0 | 0 | 0
2031-11-10 11:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-11-10 12:00 | 26.1189 | 0.01262% | 27.2769 | 28.4863 | 29.7492 | 31.0681 | 0 | 0 | 0 | 0
2031-11-10 13:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-10 14:00 | 27.5379 | 0.01331% | 28.7588 | 30.0338 | 31.3654 | 32.7559 | 0 | 0 | 0 | 0
2031-11-10 15:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-11-10 16:00 | 27.9714 | 0.01352% | 29.2116 | 30.5067 | 31.8592 | 33.2717 | 0 | 0 | 0 | 0
2031-11-10 17:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-11-10 18:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-11-10 19:00 | 27.9977 | 0.01353% | 29.239 | 30.5353 | 31.8891 | 33.3029 | 0 | 0 | 0 | 0
2031-11-10 20:00 | 30.1261 | 0.01456% | 31.4618 | 32.8566 | 34.3133 | 35.8346 | 0 | 0 | 0 | 0
2031-11-10 21:00 | 32.1626 | 0.01554% | 33.5885 | 35.0776 | 36.6328 | 38.2569 | 0 | 0 | 0 | 1.1312
2031-11-10 22:00 | 31.7815 | 0.01536% | 33.1906 | 34.6621 | 36.1988 | 37.8037 | 0 | 0 | 0 | 0.72336
2031-11-10 23:00 | 30.021 | 0.01451% | 31.352 | 32.742 | 34.1936 | 35.7096 | 0 | 0 | 0 | 0
2031-11-11 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-11-11 01:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-11-11 02:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-11-11 03:00 | 23.5701 | 0.01139% | 24.6151 | 25.7064 | 26.8461 | 28.0363 | 0 | 0 | 0 | 0
2031-11-11 04:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-11-11 05:00 | 20.2067 | 0.009765% | 21.1026 | 22.0382 | 23.0152 | 24.0356 | 0 | 0 | 0 | 0
2031-11-11 06:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-11-11 07:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-11-11 08:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-11-11 09:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0
2031-11-11 10:00 | 23.1103 | 0.01117% | 24.1349 | 25.2049 | 26.3224 | 27.4894 | 0 | 0 | 0 | 0
2031-11-11 11:00 | 25.7379 | 0.01244% | 26.879 | 28.0707 | 29.3152 | 30.6149 | 0 | 0 | 0 | 0
2031-11-11 12:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-11 13:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-11-11 14:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-11-11 15:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-11-11 16:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-11-11 17:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-11-11 18:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-11-11 19:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-11-11 20:00 | 29.7845 | 0.01439% | 31.105 | 32.4841 | 33.9243 | 35.4283 | 0 | 0 | 0 | 0
2031-11-11 21:00 | 31.2691 | 0.01511% | 32.6555 | 34.1033 | 35.6152 | 37.1942 | 0 | 0 | 0 | 0.17482
2031-11-11 22:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-11-11 23:00 | 28.7991 | 0.01392% | 30.076 | 31.4094 | 32.8019 | 34.2562 | 0 | 0 | 0 | 0
2031-11-12 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-11-12 01:00 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-11-12 02:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-11-12 03:00 | 22.4928 | 0.01087% | 23.49 | 24.5314 | 25.619 | 26.7549 | 0 | 0 | 0 | 0
2031-11-12 04:00 | 20.4563 | 0.009886% | 21.3633 | 22.3104 | 23.2995 | 24.3325 | 0 | 0 | 0 | 0
2031-11-12 05:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-11-12 06:00 | 18.2622 | 0.008825% | 19.0719 | 19.9175 | 20.8005 | 21.7227 | 0 | 0 | 0 | 0
2031-11-12 07:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-11-12 08:00 | 17.8549 | 0.008629% | 18.6465 | 19.4732 | 20.3366 | 21.2382 | 0 | 0 | 0 | 0
2031-11-12 09:00 | 19.5366 | 0.009441% | 20.4028 | 21.3074 | 22.252 | 23.2386 | 0 | 0 | 0 | 0
2031-11-12 10:00 | 22.2826 | 0.01077% | 23.2705 | 24.3022 | 25.3796 | 26.5048 | 0 | 0 | 0 | 0
2031-11-12 11:00 | 24.6606 | 0.01192% | 25.7539 | 26.8957 | 28.0881 | 29.3334 | 0 | 0 | 0 | 0
2031-11-12 12:00 | 25.8824 | 0.01251% | 27.03 | 28.2283 | 29.4798 | 30.7868 | 0 | 0 | 0 | 0
2031-11-12 13:00 | 26.027 | 0.01258% | 27.1809 | 28.3859 | 29.6444 | 30.9587 | 0 | 0 | 0 | 0
2031-11-12 14:00 | 26.2503 | 0.01269% | 27.4141 | 28.6295 | 29.8988 | 31.2244 | 0 | 0 | 0 | 0
2031-11-12 15:00 | 26.408 | 0.01276% | 27.5788 | 28.8015 | 30.0784 | 31.4119 | 0 | 0 | 0 | 0
2031-11-12 16:00 | 26.6445 | 0.01288% | 27.8258 | 29.0594 | 30.3478 | 31.6932 | 0 | 0 | 0 | 0
2031-11-12 17:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-11-12 18:00 | 26.1584 | 0.01264% | 27.3181 | 28.5292 | 29.7941 | 31.115 | 0 | 0 | 0 | 0
2031-11-12 19:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-11-12 20:00 | 28.5889 | 0.01382% | 29.8564 | 31.1801 | 32.5625 | 34.0062 | 0 | 0 | 0 | 0
2031-11-12 21:00 | 29.8239 | 0.01441% | 31.1462 | 32.5271 | 33.9692 | 35.4752 | 0 | 0 | 0 | 0
2031-11-12 22:00 | 29.2327 | 0.01413% | 30.5288 | 31.8822 | 33.2958 | 34.7719 | 0 | 0 | 0 | 0
2031-11-12 23:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-11-13 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-11-13 01:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-11-13 02:00 | 23.938 | 0.01157% | 24.9993 | 26.1076 | 27.2651 | 28.4739 | 0 | 0 | 0 | 0
2031-11-13 03:00 | 21.7045 | 0.01049% | 22.6667 | 23.6717 | 24.7212 | 25.8172 | 0 | 0 | 0 | 0
2031-11-13 04:00 | 19.6812 | 0.009511% | 20.5537 | 21.465 | 22.4166 | 23.4105 | 0 | 0 | 0 | 0
2031-11-13 05:00 | 18.3016 | 0.008845% | 19.1131 | 19.9604 | 20.8454 | 21.7696 | 0 | 0 | 0 | 0
2031-11-13 06:00 | 17.5922 | 0.008502% | 18.3721 | 19.1867 | 20.0373 | 20.9257 | 0 | 0 | 0 | 0
2031-11-13 07:00 | 17.1323 | 0.008279% | 17.8919 | 18.6851 | 19.5136 | 20.3787 | 0 | 0 | 0 | 0
2031-11-13 08:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-11-13 09:00 | 18.7352 | 0.009054% | 19.5658 | 20.4333 | 21.3392 | 22.2853 | 0 | 0 | 0 | 0
2031-11-13 10:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-11-13 11:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-11-13 12:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-11-13 13:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-11-13 14:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-11-13 15:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-11-13 16:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-11-13 17:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-11-13 18:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-11-13 19:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-11-13 20:00 | 28.1291 | 0.01359% | 29.3762 | 30.6786 | 32.0387 | 33.4592 | 0 | 0 | 0 | 0
2031-11-13 21:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-11-13 22:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-11-13 23:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-11-14 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-11-14 01:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-11-14 02:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-11-14 03:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-11-14 04:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-11-14 05:00 | 18.6564 | 0.009016% | 19.4835 | 20.3473 | 21.2494 | 22.1915 | 0 | 0 | 0 | 0
2031-11-14 06:00 | 18.0126 | 0.008705% | 18.8112 | 19.6452 | 20.5162 | 21.4258 | 0 | 0 | 0 | 0
2031-11-14 07:00 | 17.5002 | 0.008457% | 18.2761 | 19.0864 | 19.9326 | 20.8163 | 0 | 0 | 0 | 0
2031-11-14 08:00 | 17.5528 | 0.008483% | 18.331 | 19.1437 | 19.9924 | 20.8788 | 0 | 0 | 0 | 0
2031-11-14 09:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-11-14 10:00 | 21.7176 | 0.0105% | 22.6805 | 23.686 | 24.7361 | 25.8328 | 0 | 0 | 0 | 0
2031-11-14 11:00 | 23.373 | 0.0113% | 24.4093 | 25.4915 | 26.6216 | 27.8019 | 0 | 0 | 0 | 0
2031-11-14 12:00 | 24.0956 | 0.01164% | 25.1639 | 26.2796 | 27.4447 | 28.6614 | 0 | 0 | 0 | 0
2031-11-14 13:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-11-14 14:00 | 24.6212 | 0.0119% | 25.7128 | 26.8527 | 28.0433 | 29.2866 | 0 | 0 | 0 | 0
2031-11-14 15:00 | 25.1073 | 0.01213% | 26.2204 | 27.3829 | 28.5969 | 29.8648 | 0 | 0 | 0 | 0
2031-11-14 16:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-11-14 17:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-11-14 18:00 | 24.3715 | 0.01178% | 25.4521 | 26.5805 | 27.7589 | 28.9896 | 0 | 0 | 0 | 0
2031-11-14 19:00 | 24.227 | 0.01171% | 25.3011 | 26.4229 | 27.5943 | 28.8177 | 0 | 0 | 0 | 0
2031-11-14 20:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-11-14 21:00 | 28.6546 | 0.01385% | 29.925 | 31.2518 | 32.6373 | 34.0843 | 0 | 0 | 0 | 0
2031-11-14 22:00 | 27.9189 | 0.01349% | 29.1567 | 30.4493 | 31.7993 | 33.2091 | 0 | 0 | 0 | 0
2031-11-14 23:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-11-15 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-11-15 01:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-11-15 02:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-11-15 03:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-11-15 04:00 | 20.6403 | 0.009975% | 21.5554 | 22.511 | 23.509 | 24.5513 | 0 | 0 | 0 | 0
2031-11-15 05:00 | 19.5892 | 0.009467% | 20.4577 | 21.3647 | 22.3119 | 23.3011 | 0 | 0 | 0 | 0
2031-11-15 06:00 | 18.2491 | 0.008819% | 19.0582 | 19.9031 | 20.7855 | 21.7071 | 0 | 0 | 0 | 0
2031-11-15 07:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-11-15 08:00 | 17.9469 | 0.008673% | 18.7426 | 19.5736 | 20.4413 | 21.3476 | 0 | 0 | 0 | 0
2031-11-15 09:00 | 18.0389 | 0.008718% | 18.8386 | 19.6739 | 20.5461 | 21.457 | 0 | 0 | 0 | 0
2031-11-15 10:00 | 19.3264 | 0.00934% | 20.1833 | 21.0781 | 22.0126 | 22.9885 | 0 | 0 | 0 | 0
2031-11-15 11:00 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-11-15 12:00 | 23.2285 | 0.01123% | 24.2584 | 25.3339 | 26.457 | 27.63 | 0 | 0 | 0 | 0
2031-11-15 13:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-11-15 14:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-11-15 15:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-11-15 16:00 | 26.9992 | 0.01305% | 28.1962 | 29.4463 | 30.7518 | 32.1152 | 0 | 0 | 0 | 0
2031-11-15 17:00 | 26.4737 | 0.01279% | 27.6474 | 28.8731 | 30.1532 | 31.4901 | 0 | 0 | 0 | 0
2031-11-15 18:00 | 26.4474 | 0.01278% | 27.6199 | 28.8445 | 30.1233 | 31.4588 | 0 | 0 | 0 | 0
2031-11-15 19:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-11-15 20:00 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0
2031-11-15 21:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-11-15 22:00 | 27.9977 | 0.01353% | 29.239 | 30.5353 | 31.8891 | 33.3029 | 0 | 0 | 0 | 0
2031-11-15 23:00 | 26.1978 | 0.01266% | 27.3592 | 28.5722 | 29.839 | 31.1619 | 0 | 0 | 0 | 0
2031-11-16 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-11-16 01:00 | 24.2402 | 0.01171% | 25.3149 | 26.4372 | 27.6093 | 28.8334 | 0 | 0 | 0 | 0
2031-11-16 02:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-11-16 03:00 | 20.9687 | 0.01013% | 21.8984 | 22.8692 | 23.8832 | 24.942 | 0 | 0 | 0 | 0
2031-11-16 04:00 | 19.1819 | 0.00927% | 20.0323 | 20.9205 | 21.848 | 22.8166 | 0 | 0 | 0 | 0
2031-11-16 05:00 | 17.8418 | 0.008622% | 18.6328 | 19.4589 | 20.3216 | 21.2226 | 0 | 0 | 0 | 0
2031-11-16 06:00 | 17.1192 | 0.008273% | 17.8782 | 18.6708 | 19.4986 | 20.3631 | 0 | 0 | 0 | 0
2031-11-16 07:00 | 16.7382 | 0.008089% | 17.4803 | 18.2553 | 19.0646 | 19.9099 | 0 | 0 | 0 | 0
2031-11-16 08:00 | 16.3046 | 0.007879% | 17.0275 | 17.7824 | 18.5708 | 19.3941 | 0 | 0 | 0 | 0
2031-11-16 09:00 | 16.817 | 0.008127% | 17.5626 | 18.3412 | 19.1544 | 20.0036 | 0 | 0 | 0 | 0
2031-11-16 10:00 | 17.8549 | 0.008629% | 18.6465 | 19.4732 | 20.3366 | 21.2382 | 0 | 0 | 0 | 0
2031-11-16 11:00 | 19.6418 | 0.009492% | 20.5126 | 21.422 | 22.3718 | 23.3636 | 0 | 0 | 0 | 0
2031-11-16 12:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-11-16 13:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-11-16 14:00 | 25.4752 | 0.01231% | 26.6046 | 27.7841 | 29.0159 | 30.3024 | 0 | 0 | 0 | 0
2031-11-16 15:00 | 26.0664 | 0.0126% | 27.222 | 28.4289 | 29.6893 | 31.0056 | 0 | 0 | 0 | 0
2031-11-16 16:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-16 17:00 | 26.9204 | 0.01301% | 28.1139 | 29.3603 | 30.662 | 32.0214 | 0 | 0 | 0 | 0
2031-11-16 18:00 | 27.0386 | 0.01307% | 28.2374 | 29.4893 | 30.7967 | 32.1621 | 0 | 0 | 0 | 0
2031-11-16 19:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-11-16 20:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-11-16 21:00 | 31.7947 | 0.01537% | 33.2043 | 34.6764 | 36.2138 | 37.8194 | 0 | 0 | 0 | 0.73742
2031-11-16 22:00 | 30.8356 | 0.0149% | 32.2027 | 33.6304 | 35.1214 | 36.6785 | 0 | 0 | 0 | 0
2031-11-16 23:00 | 29.3247 | 0.01417% | 30.6248 | 31.9826 | 33.4005 | 34.8813 | 0 | 0 | 0 | 0
2031-11-17 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-11-17 01:00 | 26.8415 | 0.01297% | 28.0316 | 29.2744 | 30.5722 | 31.9277 | 0 | 0 | 0 | 0
2031-11-17 02:00 | 25.0679 | 0.01211% | 26.1793 | 27.3399 | 28.552 | 29.8179 | 0 | 0 | 0 | 0
2031-11-17 03:00 | 22.5585 | 0.0109% | 23.5586 | 24.6031 | 25.6938 | 26.833 | 0 | 0 | 0 | 0
2031-11-17 04:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0
2031-11-17 05:00 | 18.7746 | 0.009073% | 19.607 | 20.4763 | 21.3841 | 22.3322 | 0 | 0 | 0 | 0
2031-11-17 06:00 | 18.1571 | 0.008775% | 18.9621 | 19.8028 | 20.6808 | 21.5977 | 0 | 0 | 0 | 0
2031-11-17 07:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-11-17 08:00 | 18.1177 | 0.008756% | 18.921 | 19.7598 | 20.6359 | 21.5508 | 0 | 0 | 0 | 0
2031-11-17 09:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-11-17 10:00 | 22.322 | 0.01079% | 23.3116 | 24.3451 | 25.4245 | 26.5517 | 0 | 0 | 0 | 0
2031-11-17 11:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-11-17 12:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-11-17 13:00 | 25.1993 | 0.01218% | 26.3165 | 27.4832 | 28.7017 | 29.9742 | 0 | 0 | 0 | 0
2031-11-17 14:00 | 25.9219 | 0.01253% | 27.0711 | 28.2713 | 29.5247 | 30.8337 | 0 | 0 | 0 | 0
2031-11-17 15:00 | 26.3817 | 0.01275% | 27.5513 | 28.7728 | 30.0485 | 31.3807 | 0 | 0 | 0 | 0
2031-11-17 16:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-11-17 17:00 | 26.8678 | 0.01298% | 28.059 | 29.303 | 30.6022 | 31.9589 | 0 | 0 | 0 | 0
2031-11-17 18:00 | 26.6576 | 0.01288% | 27.8395 | 29.0737 | 30.3627 | 31.7089 | 0 | 0 | 0 | 0
2031-11-17 19:00 | 27.3277 | 0.01321% | 28.5392 | 29.8045 | 31.1259 | 32.5059 | 0 | 0 | 0 | 0
2031-11-17 20:00 | 29.9422 | 0.01447% | 31.2697 | 32.656 | 34.1038 | 35.6158 | 0 | 0 | 0 | 0
2031-11-17 21:00 | 31.1772 | 0.01507% | 32.5594 | 34.003 | 35.5105 | 37.0848 | 0 | 0 | 0 | 0.076364
2031-11-17 22:00 | 30.3889 | 0.01469% | 31.7362 | 33.1432 | 34.6126 | 36.1472 | 0 | 0 | 0 | 0
2031-11-17 23:00 | 29.1539 | 0.01409% | 30.4464 | 31.7963 | 33.206 | 34.6782 | 0 | 0 | 0 | 0
2031-11-18 | 28.5495 | 0.0138% | 29.8153 | 31.1371 | 32.5176 | 33.9593 | 0 | 0 | 0 | 0
2031-11-18 01:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-11-18 02:00 | 25.0416 | 0.0121% | 26.1518 | 27.3113 | 28.5221 | 29.7867 | 0 | 0 | 0 | 0
2031-11-18 03:00 | 22.2563 | 0.01076% | 23.243 | 24.2735 | 25.3497 | 26.4736 | 0 | 0 | 0 | 0
2031-11-18 04:00 | 20.6797 | 0.009994% | 21.5965 | 22.554 | 23.5539 | 24.5982 | 0 | 0 | 0 | 0
2031-11-18 05:00 | 19.1425 | 0.009251% | 19.9912 | 20.8775 | 21.8031 | 22.7698 | 0 | 0 | 0 | 0
2031-11-18 06:00 | 18.3805 | 0.008883% | 19.1954 | 20.0464 | 20.9352 | 21.8633 | 0 | 0 | 0 | 0
2031-11-18 07:00 | 17.9206 | 0.00866% | 18.7152 | 19.5449 | 20.4114 | 21.3164 | 0 | 0 | 0 | 0
2031-11-18 08:00 | 18.0914 | 0.008743% | 18.8935 | 19.7312 | 20.606 | 21.5195 | 0 | 0 | 0 | 0
2031-11-18 09:00 | 19.4447 | 0.009397% | 20.3068 | 21.2071 | 22.1473 | 23.1292 | 0 | 0 | 0 | 0
2031-11-18 10:00 | 22.0198 | 0.01064% | 22.996 | 24.0156 | 25.0803 | 26.1922 | 0 | 0 | 0 | 0
2031-11-18 11:00 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-11-18 12:00 | 24.8314 | 0.012% | 25.9323 | 27.082 | 28.2827 | 29.5366 | 0 | 0 | 0 | 0
2031-11-18 13:00 | 25.3569 | 0.01225% | 26.4811 | 27.6552 | 28.8813 | 30.1617 | 0 | 0 | 0 | 0
2031-11-18 14:00 | 25.6065 | 0.01237% | 26.7418 | 27.9274 | 29.1656 | 30.4586 | 0 | 0 | 0 | 0
2031-11-18 15:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-11-18 16:00 | 25.5409 | 0.01234% | 26.6732 | 27.8558 | 29.0908 | 30.3805 | 0 | 0 | 0 | 0
2031-11-18 17:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-11-18 18:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-11-18 19:00 | 26.1715 | 0.01265% | 27.3318 | 28.5436 | 29.8091 | 31.1306 | 0 | 0 | 0 | 0
2031-11-18 20:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-11-18 21:00 | 30.1655 | 0.01458% | 31.5029 | 32.8996 | 34.3582 | 35.8815 | 0 | 0 | 0 | 0
2031-11-18 22:00 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-11-18 23:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-11-19 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-11-19 01:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-11-19 02:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-11-19 03:00 | 22.8081 | 0.01102% | 23.8193 | 24.8753 | 25.9782 | 27.1299 | 0 | 0 | 0 | 0
2031-11-19 04:00 | 20.7585 | 0.01003% | 21.6788 | 22.64 | 23.6437 | 24.692 | 0 | 0 | 0 | 0
2031-11-19 05:00 | 19.6549 | 0.009499% | 20.5263 | 21.4363 | 22.3867 | 23.3792 | 0 | 0 | 0 | 0
2031-11-19 06:00 | 18.9323 | 0.009149% | 19.7717 | 20.6482 | 21.5637 | 22.5197 | 0 | 0 | 0 | 0
2031-11-19 07:00 | 18.4856 | 0.008933% | 19.3051 | 20.161 | 21.0549 | 21.9884 | 0 | 0 | 0 | 0
2031-11-19 08:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-11-19 09:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-11-19 10:00 | 22.7293 | 0.01098% | 23.737 | 24.7893 | 25.8884 | 27.0362 | 0 | 0 | 0 | 0
2031-11-19 11:00 | 25.173 | 0.01217% | 26.289 | 27.4546 | 28.6718 | 29.9429 | 0 | 0 | 0 | 0
2031-11-19 12:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-11-19 13:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-11-19 14:00 | 24.8708 | 0.01202% | 25.9734 | 27.125 | 28.3276 | 29.5835 | 0 | 0 | 0 | 0
2031-11-19 15:00 | 25.462 | 0.0123% | 26.5909 | 27.7698 | 29.001 | 30.2867 | 0 | 0 | 0 | 0
2031-11-19 16:00 | 25.3044 | 0.01223% | 26.4262 | 27.5978 | 28.8214 | 30.0992 | 0 | 0 | 0 | 0
2031-11-19 17:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-11-19 18:00 | 24.7394 | 0.01196% | 25.8362 | 26.9817 | 28.1779 | 29.4272 | 0 | 0 | 0 | 0
2031-11-19 19:00 | 25.081 | 0.01212% | 26.193 | 27.3543 | 28.567 | 29.8335 | 0 | 0 | 0 | 0
2031-11-19 20:00 | 28.0371 | 0.01355% | 29.2802 | 30.5783 | 31.934 | 33.3498 | 0 | 0 | 0 | 0
2031-11-19 21:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-11-19 22:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-11-19 23:00 | 28.5627 | 0.0138% | 29.829 | 31.1515 | 32.5326 | 33.9749 | 0 | 0 | 0 | 0
2031-11-20 | 27.9583 | 0.01351% | 29.1978 | 30.4923 | 31.8442 | 33.256 | 0 | 0 | 0 | 0
2031-11-20 01:00 | 26.881 | 0.01299% | 28.0727 | 29.3173 | 30.6171 | 31.9745 | 0 | 0 | 0 | 0
2031-11-20 02:00 | 24.9234 | 0.01204% | 26.0283 | 27.1823 | 28.3874 | 29.646 | 0 | 0 | 0 | 0
2031-11-20 03:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-11-20 04:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-11-20 05:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-11-20 06:00 | 18.3148 | 0.008851% | 19.1268 | 19.9748 | 20.8604 | 21.7852 | 0 | 0 | 0 | 0
2031-11-20 07:00 | 18.144 | 0.008768% | 18.9484 | 19.7885 | 20.6658 | 21.582 | 0 | 0 | 0 | 0
2031-11-20 08:00 | 18.4462 | 0.008914% | 19.264 | 20.1181 | 21.01 | 21.9415 | 0 | 0 | 0 | 0
2031-11-20 09:00 | 19.9834 | 0.009657% | 20.8693 | 21.7946 | 22.7608 | 23.7699 | 0 | 0 | 0 | 0
2031-11-20 10:00 | 23.4913 | 0.01135% | 24.5328 | 25.6204 | 26.7563 | 27.9426 | 0 | 0 | 0 | 0
2031-11-20 11:00 | 25.4226 | 0.01229% | 26.5497 | 27.7268 | 28.9561 | 30.2399 | 0 | 0 | 0 | 0
2031-11-20 12:00 | 25.6591 | 0.0124% | 26.7967 | 27.9847 | 29.2254 | 30.5212 | 0 | 0 | 0 | 0
2031-11-20 13:00 | 25.2518 | 0.0122% | 26.3714 | 27.5405 | 28.7615 | 30.0367 | 0 | 0 | 0 | 0
2031-11-20 14:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-11-20 15:00 | 25.2518 | 0.0122% | 26.3714 | 27.5405 | 28.7615 | 30.0367 | 0 | 0 | 0 | 0
2031-11-20 16:00 | 25.2124 | 0.01218% | 26.3302 | 27.4975 | 28.7167 | 29.9898 | 0 | 0 | 0 | 0
2031-11-20 17:00 | 24.7131 | 0.01194% | 25.8088 | 26.953 | 28.148 | 29.396 | 0 | 0 | 0 | 0
2031-11-20 18:00 | 24.5555 | 0.01187% | 25.6442 | 26.7811 | 27.9684 | 29.2084 | 0 | 0 | 0 | 0
2031-11-20 19:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-11-20 20:00 | 27.8138 | 0.01344% | 29.0469 | 30.3347 | 31.6796 | 33.0841 | 0 | 0 | 0 | 0
2031-11-20 21:00 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-11-20 22:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-11-20 23:00 | 28.1948 | 0.01363% | 29.4448 | 30.7503 | 32.1136 | 33.5373 | 0 | 0 | 0 | 0
2031-11-21 | 27.6955 | 0.01338% | 28.9234 | 30.2057 | 31.5449 | 32.9435 | 0 | 0 | 0 | 0
2031-11-21 01:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-11-21 02:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-11-21 03:00 | 22.2037 | 0.01073% | 23.1881 | 24.2162 | 25.2898 | 26.411 | 0 | 0 | 0 | 0
2031-11-21 04:00 | 20.1147 | 0.009721% | 21.0065 | 21.9379 | 22.9105 | 23.9262 | 0 | 0 | 0 | 0
2031-11-21 05:00 | 19.0243 | 0.009194% | 19.8677 | 20.7485 | 21.6684 | 22.6291 | 0 | 0 | 0 | 0
2031-11-21 06:00 | 17.9863 | 0.008692% | 18.7838 | 19.6165 | 20.4862 | 21.3945 | 0 | 0 | 0 | 0
2031-11-21 07:00 | 17.1192 | 0.008273% | 17.8782 | 18.6708 | 19.4986 | 20.3631 | 0 | 0 | 0 | 0
2031-11-21 08:00 | 17.1586 | 0.008292% | 17.9193 | 18.7138 | 19.5435 | 20.41 | 0 | 0 | 0 | 0
2031-11-21 09:00 | 18.7089 | 0.009041% | 19.5384 | 20.4046 | 21.3093 | 22.254 | 0 | 0 | 0 | 0
2031-11-21 10:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-11-21 11:00 | 23.6358 | 0.01142% | 24.6837 | 25.7781 | 26.9209 | 28.1145 | 0 | 0 | 0 | 0
2031-11-21 12:00 | 24.5686 | 0.01187% | 25.6579 | 26.7954 | 27.9834 | 29.224 | 0 | 0 | 0 | 0
2031-11-21 13:00 | 25.0022 | 0.01208% | 26.1107 | 27.2683 | 28.4772 | 29.7398 | 0 | 0 | 0 | 0
2031-11-21 14:00 | 25.1467 | 0.01215% | 26.2616 | 27.4259 | 28.6418 | 29.9117 | 0 | 0 | 0 | 0
2031-11-21 15:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-11-21 16:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-11-21 17:00 | 25.8562 | 0.0125% | 27.0025 | 28.1997 | 29.4499 | 30.7556 | 0 | 0 | 0 | 0
2031-11-21 18:00 | 24.6343 | 0.0119% | 25.7265 | 26.8671 | 28.0582 | 29.3022 | 0 | 0 | 0 | 0
2031-11-21 19:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-11-21 20:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-11-21 21:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-11-21 22:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-11-21 23:00 | 26.9072 | 0.013% | 28.1002 | 29.346 | 30.6471 | 32.0058 | 0 | 0 | 0 | 0
2031-11-22 | 26.2503 | 0.01269% | 27.4141 | 28.6295 | 29.8988 | 31.2244 | 0 | 0 | 0 | 0
2031-11-22 01:00 | 25.9613 | 0.01255% | 27.1123 | 28.3143 | 29.5696 | 30.8806 | 0 | 0 | 0 | 0
2031-11-22 02:00 | 24.2796 | 0.01173% | 25.356 | 26.4802 | 27.6542 | 28.8802 | 0 | 0 | 0 | 0
2031-11-22 03:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-11-22 04:00 | 20.8111 | 0.01006% | 21.7337 | 22.6973 | 23.7036 | 24.7545 | 0 | 0 | 0 | 0
2031-11-22 05:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-11-22 06:00 | 18.3411 | 0.008864% | 19.1542 | 20.0034 | 20.8903 | 21.8165 | 0 | 0 | 0 | 0
2031-11-22 07:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-11-22 08:00 | 17.4871 | 0.008451% | 18.2624 | 19.072 | 19.9176 | 20.8006 | 0 | 0 | 0 | 0
2031-11-22 09:00 | 17.6973 | 0.008552% | 18.4819 | 19.3013 | 20.157 | 21.0507 | 0 | 0 | 0 | 0
2031-11-22 10:00 | 19.0899 | 0.009225% | 19.9363 | 20.8202 | 21.7433 | 22.7072 | 0 | 0 | 0 | 0
2031-11-22 11:00 | 20.9162 | 0.01011% | 21.8435 | 22.8119 | 23.8233 | 24.8795 | 0 | 0 | 0 | 0
2031-11-22 12:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-11-22 13:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-11-22 14:00 | 24.0825 | 0.01164% | 25.1502 | 26.2652 | 27.4297 | 28.6458 | 0 | 0 | 0 | 0
2031-11-22 15:00 | 25.1598 | 0.01216% | 26.2753 | 27.4402 | 28.6568 | 29.9273 | 0 | 0 | 0 | 0
2031-11-22 16:00 | 25.3701 | 0.01226% | 26.4948 | 27.6695 | 28.8962 | 30.1773 | 0 | 0 | 0 | 0
2031-11-22 17:00 | 25.7773 | 0.01246% | 26.9202 | 28.1137 | 29.3601 | 30.6618 | 0 | 0 | 0 | 0
2031-11-22 18:00 | 25.5146 | 0.01233% | 26.6458 | 27.8271 | 29.0608 | 30.3493 | 0 | 0 | 0 | 0
2031-11-22 19:00 | 26.7233 | 0.01291% | 27.9081 | 29.1454 | 30.4376 | 31.787 | 0 | 0 | 0 | 0
2031-11-22 20:00 | 28.2736 | 0.01366% | 29.5271 | 30.8362 | 32.2034 | 33.6311 | 0 | 0 | 0 | 0
2031-11-22 21:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-11-22 22:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-11-22 23:00 | 26.9466 | 0.01302% | 28.1413 | 29.389 | 30.692 | 32.0527 | 0 | 0 | 0 | 0
2031-11-23 | 26.3554 | 0.01274% | 27.5239 | 28.7442 | 30.0186 | 31.3494 | 0 | 0 | 0 | 0
2031-11-23 01:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-11-23 02:00 | 24.2007 | 0.0117% | 25.2737 | 26.3942 | 27.5644 | 28.7865 | 0 | 0 | 0 | 0
2031-11-23 03:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-11-23 04:00 | 20.5877 | 0.009949% | 21.5005 | 22.4537 | 23.4492 | 24.4888 | 0 | 0 | 0 | 0
2031-11-23 05:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-11-23 06:00 | 18.3542 | 0.00887% | 19.1679 | 20.0178 | 20.9052 | 21.8321 | 0 | 0 | 0 | 0
2031-11-23 07:00 | 17.7498 | 0.008578% | 18.5368 | 19.3586 | 20.2169 | 21.1132 | 0 | 0 | 0 | 0
2031-11-23 08:00 | 17.2637 | 0.008343% | 18.0291 | 18.8284 | 19.6632 | 20.535 | 0 | 0 | 0 | 0
2031-11-23 09:00 | 17.3951 | 0.008406% | 18.1663 | 18.9717 | 19.8128 | 20.6913 | 0 | 0 | 0 | 0
2031-11-23 10:00 | 18.4987 | 0.00894% | 19.3189 | 20.1754 | 21.0699 | 22.004 | 0 | 0 | 0 | 0
2031-11-23 11:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-11-23 12:00 | 21.757 | 0.01051% | 22.7216 | 23.729 | 24.781 | 25.8797 | 0 | 0 | 0 | 0
2031-11-23 13:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-11-23 14:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-11-23 15:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-11-23 16:00 | 25.2912 | 0.01222% | 26.4125 | 27.5835 | 28.8064 | 30.0836 | 0 | 0 | 0 | 0
2031-11-23 17:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-11-23 18:00 | 25.8168 | 0.01248% | 26.9613 | 28.1567 | 29.405 | 30.7087 | 0 | 0 | 0 | 0
2031-11-23 19:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-11-23 20:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-11-23 21:00 | 31.2429 | 0.0151% | 32.628 | 34.0746 | 35.5853 | 37.163 | 0 | 0 | 0 | 0.14669
2031-11-23 22:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-11-23 23:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-11-24 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0
2031-11-24 01:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-11-24 02:00 | 23.9117 | 0.01156% | 24.9718 | 26.079 | 27.2352 | 28.4427 | 0 | 0 | 0 | 0
2031-11-24 03:00 | 21.3629 | 0.01032% | 22.31 | 23.2991 | 24.3321 | 25.4109 | 0 | 0 | 0 | 0
2031-11-24 04:00 | 19.2213 | 0.009289% | 20.0735 | 20.9635 | 21.8929 | 22.8635 | 0 | 0 | 0 | 0
2031-11-24 05:00 | 17.8812 | 0.008641% | 18.674 | 19.5019 | 20.3665 | 21.2695 | 0 | 0 | 0 | 0
2031-11-24 06:00 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-11-24 07:00 | 17.0141 | 0.008222% | 17.7684 | 18.5562 | 19.3789 | 20.238 | 0 | 0 | 0 | 0
2031-11-24 08:00 | 17.5265 | 0.00847% | 18.3035 | 19.115 | 19.9625 | 20.8475 | 0 | 0 | 0 | 0
2031-11-24 09:00 | 19.2476 | 0.009302% | 20.101 | 20.9921 | 21.9228 | 22.8948 | 0 | 0 | 0 | 0
2031-11-24 10:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-11-24 11:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-11-24 12:00 | 24.5161 | 0.01185% | 25.603 | 26.7381 | 27.9235 | 29.1615 | 0 | 0 | 0 | 0
2031-11-24 13:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-11-24 14:00 | 24.5423 | 0.01186% | 25.6304 | 26.7668 | 27.9535 | 29.1928 | 0 | 0 | 0 | 0
2031-11-24 15:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-11-24 16:00 | 24.5818 | 0.01188% | 25.6716 | 26.8097 | 27.9984 | 29.2397 | 0 | 0 | 0 | 0
2031-11-24 17:00 | 24.4372 | 0.01181% | 25.5207 | 26.6521 | 27.8338 | 29.0678 | 0 | 0 | 0 | 0
2031-11-24 18:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-11-24 19:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-11-24 20:00 | 28.8911 | 0.01396% | 30.172 | 31.5097 | 32.9067 | 34.3656 | 0 | 0 | 0 | 0
2031-11-24 21:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-11-24 22:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-11-24 23:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-11-25 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-11-25 01:00 | 26.3948 | 0.01276% | 27.5651 | 28.7872 | 30.0634 | 31.3963 | 0 | 0 | 0 | 0
2031-11-25 02:00 | 24.1745 | 0.01168% | 25.2462 | 26.3655 | 27.5345 | 28.7552 | 0 | 0 | 0 | 0
2031-11-25 03:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-11-25 04:00 | 19.379 | 0.009365% | 20.2382 | 21.1354 | 22.0725 | 23.0511 | 0 | 0 | 0 | 0
2031-11-25 05:00 | 17.8812 | 0.008641% | 18.674 | 19.5019 | 20.3665 | 21.2695 | 0 | 0 | 0 | 0
2031-11-25 06:00 | 17.3294 | 0.008375% | 18.0977 | 18.9001 | 19.738 | 20.6131 | 0 | 0 | 0 | 0
2031-11-25 07:00 | 16.8564 | 0.008146% | 17.6038 | 18.3842 | 19.1993 | 20.0505 | 0 | 0 | 0 | 0
2031-11-25 08:00 | 17.0798 | 0.008254% | 17.837 | 18.6278 | 19.4537 | 20.3162 | 0 | 0 | 0 | 0
2031-11-25 09:00 | 18.4987 | 0.00894% | 19.3189 | 20.1754 | 21.0699 | 22.004 | 0 | 0 | 0 | 0
2031-11-25 10:00 | 21.9147 | 0.01059% | 22.8863 | 23.9009 | 24.9606 | 26.0672 | 0 | 0 | 0 | 0
2031-11-25 11:00 | 23.6621 | 0.01144% | 24.7111 | 25.8067 | 26.9509 | 28.1457 | 0 | 0 | 0 | 0
2031-11-25 12:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-11-25 13:00 | 24.4504 | 0.01182% | 25.5344 | 26.6665 | 27.8487 | 29.0834 | 0 | 0 | 0 | 0
2031-11-25 14:00 | 24.7788 | 0.01197% | 25.8774 | 27.0247 | 28.2228 | 29.4741 | 0 | 0 | 0 | 0
2031-11-25 15:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-11-25 16:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-11-25 17:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-11-25 18:00 | 25.2255 | 0.01219% | 26.3439 | 27.5119 | 28.7316 | 30.0054 | 0 | 0 | 0 | 0
2031-11-25 19:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-11-25 20:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-11-25 21:00 | 29.6137 | 0.01431% | 30.9267 | 32.2978 | 33.7297 | 35.2251 | 0 | 0 | 0 | 0
2031-11-25 22:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-11-25 23:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-11-26 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-11-26 01:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-11-26 02:00 | 23.6489 | 0.01143% | 24.6974 | 25.7924 | 26.9359 | 28.1301 | 0 | 0 | 0 | 0
2031-11-26 03:00 | 20.903 | 0.0101% | 21.8298 | 22.7976 | 23.8083 | 24.8639 | 0 | 0 | 0 | 0
2031-11-26 04:00 | 19.1556 | 0.009257% | 20.0049 | 20.8918 | 21.8181 | 22.7854 | 0 | 0 | 0 | 0
2031-11-26 05:00 | 17.3031 | 0.008362% | 18.0703 | 18.8714 | 19.7081 | 20.5819 | 0 | 0 | 0 | 0
2031-11-26 06:00 | 16.8827 | 0.008159% | 17.6312 | 18.4129 | 19.2292 | 20.0818 | 0 | 0 | 0 | 0
2031-11-26 07:00 | 16.1864 | 0.007822% | 16.904 | 17.6535 | 18.4361 | 19.2535 | 0 | 0 | 0 | 0
2031-11-26 08:00 | 16.4229 | 0.007937% | 17.151 | 17.9114 | 18.7055 | 19.5348 | 0 | 0 | 0 | 0
2031-11-26 09:00 | 18.0652 | 0.00873% | 18.8661 | 19.7025 | 20.576 | 21.4883 | 0 | 0 | 0 | 0
2031-11-26 10:00 | 21.0607 | 0.01018% | 21.9944 | 22.9695 | 23.9879 | 25.0514 | 0 | 0 | 0 | 0
2031-11-26 11:00 | 23.0709 | 0.01115% | 24.0937 | 25.1619 | 26.2775 | 27.4425 | 0 | 0 | 0 | 0
2031-11-26 12:00 | 23.4519 | 0.01133% | 24.4916 | 25.5774 | 26.7114 | 27.8957 | 0 | 0 | 0 | 0
2031-11-26 13:00 | 23.846 | 0.01152% | 24.9032 | 26.0073 | 27.1604 | 28.3645 | 0 | 0 | 0 | 0
2031-11-26 14:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-11-26 15:00 | 24.9365 | 0.01205% | 26.0421 | 27.1966 | 28.4024 | 29.6616 | 0 | 0 | 0 | 0
2031-11-26 16:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-11-26 17:00 | 25.2781 | 0.01222% | 26.3988 | 27.5692 | 28.7915 | 30.068 | 0 | 0 | 0 | 0
2031-11-26 18:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-11-26 19:00 | 26.7627 | 0.01293% | 27.9492 | 29.1884 | 30.4825 | 31.8339 | 0 | 0 | 0 | 0
2031-11-26 20:00 | 27.9057 | 0.01349% | 29.143 | 30.435 | 31.7844 | 33.1935 | 0 | 0 | 0 | 0
2031-11-26 21:00 | 19.0768 | 0.009219% | 19.9226 | 20.8059 | 21.7283 | 22.6916 | 0 | 0 | 0 | 0
2031-11-26 22:00 | 32.583 | 0.01575% | 34.0276 | 35.5362 | 37.1117 | 38.757 | 0 | 0 | 0.10051 | 1.5813
2031-11-26 23:00 | 28.5758 | 0.01381% | 29.8427 | 31.1658 | 32.5475 | 33.9905 | 0 | 0 | 0 | 0
2031-11-27 | 28.2473 | 0.01365% | 29.4997 | 30.8076 | 32.1734 | 33.5998 | 0 | 0 | 0 | 0
2031-11-27 01:00 | 26.9729 | 0.01304% | 28.1688 | 29.4176 | 30.7219 | 32.0839 | 0 | 0 | 0 | 0
2031-11-27 02:00 | 24.9759 | 0.01207% | 26.0832 | 27.2396 | 28.4473 | 29.7085 | 0 | 0 | 0 | 0
2031-11-27 03:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-11-27 04:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-11-27 05:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-11-27 06:00 | 18.9848 | 0.009175% | 19.8265 | 20.7056 | 21.6235 | 22.5822 | 0 | 0 | 0 | 0
2031-11-27 07:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-11-27 08:00 | 18.6038 | 0.008991% | 19.4286 | 20.29 | 21.1896 | 22.129 | 0 | 0 | 0 | 0
2031-11-27 09:00 | 20.3249 | 0.009822% | 21.2261 | 22.1671 | 23.1499 | 24.1763 | 0 | 0 | 0 | 0
2031-11-27 10:00 | 22.9789 | 0.0111% | 23.9977 | 25.0616 | 26.1727 | 27.3331 | 0 | 0 | 0 | 0
2031-11-27 11:00 | 25.8036 | 0.01247% | 26.9476 | 28.1424 | 29.3901 | 30.6931 | 0 | 0 | 0 | 0
2031-11-27 12:00 | 26.316 | 0.01272% | 27.4827 | 28.7012 | 29.9737 | 31.3026 | 0 | 0 | 0 | 0
2031-11-27 13:00 | 26.9335 | 0.01302% | 28.1276 | 29.3747 | 30.677 | 32.0371 | 0 | 0 | 0 | 0
2031-11-27 14:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-11-27 15:00 | 27.2226 | 0.01316% | 28.4295 | 29.6899 | 31.0062 | 32.3809 | 0 | 0 | 0 | 0
2031-11-27 16:00 | 27.262 | 0.01317% | 28.4706 | 29.7329 | 31.0511 | 32.4278 | 0 | 0 | 0 | 0
2031-11-27 17:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-11-27 18:00 | 27.6036 | 0.01334% | 28.8274 | 30.1054 | 31.4402 | 32.8341 | 0 | 0 | 0 | 0
2031-11-27 19:00 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-11-27 20:00 | 31.2954 | 0.01512% | 32.6829 | 34.1319 | 35.6452 | 37.2255 | 0 | 0 | 0 | 0.20295
2031-11-27 21:00 | 31.5976 | 0.01527% | 32.9985 | 34.4615 | 35.9893 | 37.5849 | 0 | 0 | 0 | 0.52645
2031-11-27 22:00 | 30.8881 | 0.01493% | 32.2576 | 33.6877 | 35.1813 | 36.741 | 0 | 0 | 0 | 0
2031-11-27 23:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-11-28 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-11-28 01:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-11-28 02:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-11-28 03:00 | 23.4387 | 0.01133% | 24.4779 | 25.5631 | 26.6965 | 27.8801 | 0 | 0 | 0 | 0
2031-11-28 04:00 | 21.6256 | 0.01045% | 22.5844 | 23.5857 | 24.6314 | 25.7234 | 0 | 0 | 0 | 0
2031-11-28 05:00 | 20.3381 | 0.009829% | 21.2398 | 22.1814 | 23.1649 | 24.1919 | 0 | 0 | 0 | 0
2031-11-28 06:00 | 19.7337 | 0.009537% | 20.6086 | 21.5223 | 22.4765 | 23.473 | 0 | 0 | 0 | 0
2031-11-28 07:00 | 19.1294 | 0.009245% | 19.9775 | 20.8632 | 21.7881 | 22.7541 | 0 | 0 | 0 | 0
2031-11-28 08:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-11-28 09:00 | 20.5614 | 0.009937% | 21.473 | 22.425 | 23.4193 | 24.4576 | 0 | 0 | 0 | 0
2031-11-28 10:00 | 24.2927 | 0.01174% | 25.3697 | 26.4945 | 27.6691 | 28.8959 | 0 | 0 | 0 | 0
2031-11-28 11:00 | 25.7116 | 0.01243% | 26.8516 | 28.0421 | 29.2853 | 30.5837 | 0 | 0 | 0 | 0
2031-11-28 12:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-11-28 13:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-11-28 14:00 | 27.7218 | 0.0134% | 28.9509 | 30.2344 | 31.5749 | 32.9747 | 0 | 0 | 0 | 0
2031-11-28 15:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-11-28 16:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-11-28 17:00 | 28.7597 | 0.0139% | 30.0348 | 31.3664 | 32.757 | 34.2093 | 0 | 0 | 0 | 0
2031-11-28 18:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-11-28 19:00 | 28.3787 | 0.01371% | 29.6369 | 30.9509 | 32.3231 | 33.7561 | 0 | 0 | 0 | 0
2031-11-28 20:00 | 30.6254 | 0.0148% | 31.9832 | 33.4011 | 34.882 | 36.4285 | 0 | 0 | 0 | 0
2031-11-28 21:00 | 31.4268 | 0.01519% | 32.8201 | 34.2752 | 35.7948 | 37.3818 | 0 | 0 | 0 | 0.3436
2031-11-28 22:00 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-11-28 23:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-11-29 | 29.1276 | 0.01408% | 30.419 | 31.7676 | 33.176 | 34.6469 | 0 | 0 | 0 | 0
2031-11-29 01:00 | 28.4444 | 0.01375% | 29.7055 | 31.0225 | 32.3979 | 33.8343 | 0 | 0 | 0 | 0
2031-11-29 02:00 | 26.224 | 0.01267% | 27.3867 | 28.6009 | 29.8689 | 31.1932 | 0 | 0 | 0 | 0
2031-11-29 03:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-11-29 04:00 | 22.2431 | 0.01075% | 23.2293 | 24.2592 | 25.3347 | 26.4579 | 0 | 0 | 0 | 0
2031-11-29 05:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-11-29 06:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-11-29 07:00 | 19.1688 | 0.009264% | 20.0186 | 20.9062 | 21.833 | 22.801 | 0 | 0 | 0 | 0
2031-11-29 08:00 | 19.1819 | 0.00927% | 20.0323 | 20.9205 | 21.848 | 22.8166 | 0 | 0 | 0 | 0
2031-11-29 09:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-11-29 10:00 | 20.9556 | 0.01013% | 21.8847 | 22.8549 | 23.8682 | 24.9264 | 0 | 0 | 0 | 0
2031-11-29 11:00 | 22.9132 | 0.01107% | 23.9291 | 24.99 | 26.0979 | 27.2549 | 0 | 0 | 0 | 0
2031-11-29 12:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-11-29 13:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-11-29 14:00 | 25.9481 | 0.01254% | 27.0986 | 28.3 | 29.5547 | 30.865 | 0 | 0 | 0 | 0
2031-11-29 15:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-11-29 16:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-11-29 17:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-11-29 18:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-11-29 19:00 | 27.459 | 0.01327% | 28.6764 | 29.9478 | 31.2756 | 32.6622 | 0 | 0 | 0 | 0
2031-11-29 20:00 | 29.3641 | 0.01419% | 30.666 | 32.0255 | 33.4454 | 34.9282 | 0 | 0 | 0 | 0
2031-11-29 21:00 | 30.5071 | 0.01474% | 31.8597 | 33.2722 | 34.7473 | 36.2878 | 0 | 0 | 0 | 0
2031-11-29 22:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-11-29 23:00 | 28.497 | 0.01377% | 29.7604 | 31.0798 | 32.4578 | 33.8968 | 0 | 0 | 0 | 0
2031-11-30 | 27.6561 | 0.01337% | 28.8823 | 30.1628 | 31.5 | 32.8966 | 0 | 0 | 0 | 0
2031-11-30 01:00 | 26.9598 | 0.01303% | 28.1551 | 29.4033 | 30.7069 | 32.0683 | 0 | 0 | 0 | 0
2031-11-30 02:00 | 25.3963 | 0.01227% | 26.5223 | 27.6982 | 28.9262 | 30.2086 | 0 | 0 | 0 | 0
2031-11-30 03:00 | 23.465 | 0.01134% | 24.5053 | 25.5918 | 26.7264 | 27.9113 | 0 | 0 | 0 | 0
2031-11-30 04:00 | 21.4811 | 0.01038% | 22.4335 | 23.4281 | 24.4668 | 25.5515 | 0 | 0 | 0 | 0
2031-11-30 05:00 | 19.9177 | 0.009625% | 20.8007 | 21.7229 | 22.686 | 23.6918 | 0 | 0 | 0 | 0
2031-11-30 06:00 | 19.0899 | 0.009225% | 19.9363 | 20.8202 | 21.7433 | 22.7072 | 0 | 0 | 0 | 0
2031-11-30 07:00 | 18.6695 | 0.009022% | 19.4972 | 20.3617 | 21.2644 | 22.2072 | 0 | 0 | 0 | 0
2031-11-30 08:00 | 18.5513 | 0.008965% | 19.3738 | 20.2327 | 21.1297 | 22.0665 | 0 | 0 | 0 | 0
2031-11-30 09:00 | 18.8403 | 0.009105% | 19.6756 | 20.5479 | 21.4589 | 22.4103 | 0 | 0 | 0 | 0
2031-11-30 10:00 | 19.9965 | 0.009664% | 20.883 | 21.8089 | 22.7758 | 23.7856 | 0 | 0 | 0 | 0
2031-11-30 11:00 | 21.5862 | 0.01043% | 22.5433 | 23.5427 | 24.5865 | 25.6765 | 0 | 0 | 0 | 0
2031-11-30 12:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-11-30 13:00 | 25.0941 | 0.01213% | 26.2067 | 27.3686 | 28.582 | 29.8492 | 0 | 0 | 0 | 0
2031-11-30 14:00 | 26.5919 | 0.01285% | 27.7709 | 29.0021 | 30.2879 | 31.6307 | 0 | 0 | 0 | 0
2031-11-30 15:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-11-30 16:00 | 28.3919 | 0.01372% | 29.6506 | 30.9652 | 32.338 | 33.7717 | 0 | 0 | 0 | 0
2031-11-30 17:00 | 28.2868 | 0.01367% | 29.5409 | 30.8506 | 32.2183 | 33.6467 | 0 | 0 | 0 | 0
2031-11-30 18:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-11-30 19:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-11-30 20:00 | 32.2808 | 0.0156% | 33.712 | 35.2066 | 36.7675 | 38.3976 | 0 | 0 | 0 | 1.2578
2031-11-30 21:00 | 32.9377 | 0.01592% | 34.398 | 35.9231 | 37.5157 | 39.179 | 0 | 0 | 0.46414 | 1.9611
2031-11-30 22:00 | 32.3071 | 0.01561% | 33.7394 | 35.2353 | 36.7974 | 38.4288 | 0 | 0 | 0 | 1.286
2031-11-30 23:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-12-01 | 29.6531 | 0.01433% | 30.9678 | 32.3408 | 33.7746 | 35.272 | 0 | 0 | 0 | 0
2031-12-01 01:00 | 28.0634 | 0.01356% | 29.3076 | 30.607 | 31.9639 | 33.3811 | 0 | 0 | 0 | 0
2031-12-01 02:00 | 26.1321 | 0.01263% | 27.2906 | 28.5006 | 29.7642 | 31.0838 | 0 | 0 | 0 | 0
2031-12-01 03:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-12-01 04:00 | 21.3497 | 0.01032% | 22.2963 | 23.2848 | 24.3171 | 25.3952 | 0 | 0 | 0 | 0
2031-12-01 05:00 | 20.049 | 0.009689% | 20.9379 | 21.8662 | 22.8357 | 23.8481 | 0 | 0 | 0 | 0
2031-12-01 06:00 | 19.1819 | 0.00927% | 20.0323 | 20.9205 | 21.848 | 22.8166 | 0 | 0 | 0 | 0
2031-12-01 07:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-12-01 08:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-12-01 09:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-12-01 10:00 | 24.3978 | 0.01179% | 25.4795 | 26.6091 | 27.7889 | 29.0209 | 0 | 0 | 0 | 0
2031-12-01 11:00 | 26.8547 | 0.01298% | 28.0453 | 29.2887 | 30.5872 | 31.9433 | 0 | 0 | 0 | 0
2031-12-01 12:00 | 27.1306 | 0.01311% | 28.3334 | 29.5896 | 30.9015 | 32.2715 | 0 | 0 | 0 | 0
2031-12-01 13:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-12-01 14:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-12-01 15:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-12-01 16:00 | 27.4065 | 0.01324% | 28.6216 | 29.8905 | 31.2157 | 32.5997 | 0 | 0 | 0 | 0
2031-12-01 17:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-12-01 18:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-12-01 19:00 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-12-01 20:00 | 31.7159 | 0.01533% | 33.122 | 34.5904 | 36.124 | 37.7256 | 0 | 0 | 0 | 0.65303
2031-12-01 21:00 | 33.253 | 0.01607% | 34.7273 | 36.267 | 37.8749 | 39.554 | 0 | 0 | 0.78737 | 2.2986
2031-12-01 22:00 | 32.2939 | 0.01561% | 33.7257 | 35.2209 | 36.7825 | 38.4132 | 0 | 0 | 0 | 1.2719
2031-12-01 23:00 | 31.4531 | 0.0152% | 32.8476 | 34.3039 | 35.8247 | 37.413 | 0 | 0 | 0 | 0.37173
2031-12-02 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-12-02 01:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-12-02 02:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-12-02 03:00 | 24.8445 | 0.01201% | 25.946 | 27.0963 | 28.2977 | 29.5522 | 0 | 0 | 0 | 0
2031-12-02 04:00 | 22.5322 | 0.01089% | 23.5311 | 24.5744 | 25.6639 | 26.8017 | 0 | 0 | 0 | 0
2031-12-02 05:00 | 21.0738 | 0.01018% | 22.0081 | 22.9839 | 24.0029 | 25.067 | 0 | 0 | 0 | 0
2031-12-02 06:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-12-02 07:00 | 19.8126 | 0.009575% | 20.6909 | 21.6083 | 22.5663 | 23.5668 | 0 | 0 | 0 | 0
2031-12-02 08:00 | 19.7731 | 0.009556% | 20.6498 | 21.5653 | 22.5214 | 23.5199 | 0 | 0 | 0 | 0
2031-12-02 09:00 | 21.0344 | 0.01017% | 21.967 | 22.9409 | 23.958 | 25.0202 | 0 | 0 | 0 | 0
2031-12-02 10:00 | 24.0694 | 0.01163% | 25.1365 | 26.2509 | 27.4148 | 28.6302 | 0 | 0 | 0 | 0
2031-12-02 11:00 | 26.4474 | 0.01278% | 27.6199 | 28.8445 | 30.1233 | 31.4588 | 0 | 0 | 0 | 0
2031-12-02 12:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-12-02 13:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-12-02 14:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-12-02 15:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-12-02 16:00 | 26.5525 | 0.01283% | 27.7297 | 28.9591 | 30.243 | 31.5839 | 0 | 0 | 0 | 0
2031-12-02 17:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-12-02 18:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-12-02 19:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-12-02 20:00 | 30.875 | 0.01492% | 32.2438 | 33.6734 | 35.1663 | 36.7254 | 0 | 0 | 0 | 0
2031-12-02 21:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-12-02 22:00 | 31.8341 | 0.01538% | 33.2455 | 34.7194 | 36.2587 | 37.8662 | 0 | 0 | 0 | 0.77962
2031-12-02 23:00 | 31.3086 | 0.01513% | 32.6966 | 34.1462 | 35.6601 | 37.2411 | 0 | 0 | 0 | 0.21701
2031-12-03 | 30.7699 | 0.01487% | 32.1341 | 33.5588 | 35.0466 | 36.6004 | 0 | 0 | 0 | 0
2031-12-03 01:00 | 29.5086 | 0.01426% | 30.8169 | 32.1832 | 33.61 | 35.1001 | 0 | 0 | 0 | 0
2031-12-03 02:00 | 27.2357 | 0.01316% | 28.4432 | 29.7042 | 31.0212 | 32.3965 | 0 | 0 | 0 | 0
2031-12-03 03:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-12-03 04:00 | 22.8738 | 0.01105% | 23.8879 | 24.947 | 26.053 | 27.2081 | 0 | 0 | 0 | 0
2031-12-03 05:00 | 21.376 | 0.01033% | 22.3237 | 23.3134 | 24.3471 | 25.4265 | 0 | 0 | 0 | 0
2031-12-03 06:00 | 20.8636 | 0.01008% | 21.7886 | 22.7546 | 23.7634 | 24.817 | 0 | 0 | 0 | 0
2031-12-03 07:00 | 20.6665 | 0.009987% | 21.5828 | 22.5397 | 23.539 | 24.5826 | 0 | 0 | 0 | 0
2031-12-03 08:00 | 20.903 | 0.0101% | 21.8298 | 22.7976 | 23.8083 | 24.8639 | 0 | 0 | 0 | 0
2031-12-03 09:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-12-03 10:00 | 25.5934 | 0.01237% | 26.7281 | 27.9131 | 29.1506 | 30.443 | 0 | 0 | 0 | 0
2031-12-03 11:00 | 28.0765 | 0.01357% | 29.3213 | 30.6213 | 31.9789 | 33.3967 | 0 | 0 | 0 | 0
2031-12-03 12:00 | 28.4707 | 0.01376% | 29.7329 | 31.0512 | 32.4278 | 33.8655 | 0 | 0 | 0 | 0
2031-12-03 13:00 | 28.7072 | 0.01387% | 29.9799 | 31.3091 | 32.6972 | 34.1468 | 0 | 0 | 0 | 0
2031-12-03 14:00 | 28.6415 | 0.01384% | 29.9113 | 31.2374 | 32.6224 | 34.0687 | 0 | 0 | 0 | 0
2031-12-03 15:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-12-03 16:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-12-03 17:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-12-03 18:00 | 28.9305 | 0.01398% | 30.2132 | 31.5527 | 32.9516 | 34.4125 | 0 | 0 | 0 | 0
2031-12-03 19:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-12-03 20:00 | 32.2151 | 0.01557% | 33.6434 | 35.135 | 36.6927 | 38.3194 | 0 | 0 | 0 | 1.1875
2031-12-03 21:00 | 32.8589 | 0.01588% | 34.3157 | 35.8371 | 37.4259 | 39.0852 | 0 | 0 | 0.38333 | 1.8767
2031-12-03 22:00 | 32.2151 | 0.01557% | 33.6434 | 35.135 | 36.6927 | 38.3194 | 0 | 0 | 0 | 1.1875
2031-12-03 23:00 | 31.2297 | 0.01509% | 32.6143 | 34.0603 | 35.5703 | 37.1474 | 0 | 0 | 0 | 0.13262
2031-12-04 | 30.5465 | 0.01476% | 31.9008 | 33.3152 | 34.7922 | 36.3347 | 0 | 0 | 0 | 0
2031-12-04 01:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-12-04 02:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-12-04 03:00 | 24.9496 | 0.01206% | 26.0558 | 27.211 | 28.4174 | 29.6773 | 0 | 0 | 0 | 0
2031-12-04 04:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-12-04 05:00 | 20.9424 | 0.01012% | 21.8709 | 22.8406 | 23.8532 | 24.9108 | 0 | 0 | 0 | 0
2031-12-04 06:00 | 20.1147 | 0.009721% | 21.0065 | 21.9379 | 22.9105 | 23.9262 | 0 | 0 | 0 | 0
2031-12-04 07:00 | 19.7469 | 0.009543% | 20.6223 | 21.5366 | 22.4915 | 23.4886 | 0 | 0 | 0 | 0
2031-12-04 08:00 | 20.1541 | 0.00974% | 21.0477 | 21.9808 | 22.9554 | 23.9731 | 0 | 0 | 0 | 0
2031-12-04 09:00 | 21.6651 | 0.01047% | 22.6256 | 23.6287 | 24.6763 | 25.7703 | 0 | 0 | 0 | 0
2031-12-04 10:00 | 24.8971 | 0.01203% | 26.0009 | 27.1536 | 28.3575 | 29.6147 | 0 | 0 | 0 | 0
2031-12-04 11:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-12-04 12:00 | 27.7481 | 0.01341% | 28.9783 | 30.2631 | 31.6048 | 33.006 | 0 | 0 | 0 | 0
2031-12-04 13:00 | 27.9583 | 0.01351% | 29.1978 | 30.4923 | 31.8442 | 33.256 | 0 | 0 | 0 | 0
2031-12-04 14:00 | 28.116 | 0.01359% | 29.3625 | 30.6643 | 32.0238 | 33.4436 | 0 | 0 | 0 | 0
2031-12-04 15:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-12-04 16:00 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-12-04 17:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-12-04 18:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-12-04 19:00 | 30.5334 | 0.01476% | 31.8871 | 33.3008 | 34.7772 | 36.3191 | 0 | 0 | 0 | 0
2031-12-04 20:00 | 33.253 | 0.01607% | 34.7273 | 36.267 | 37.8749 | 39.554 | 0 | 0 | 0.78737 | 2.2986
2031-12-04 21:00 | 34.7377 | 0.01679% | 36.2778 | 37.8861 | 39.5658 | 41.32 | 0 | 0.79753 | 2.3092 | 3.888
2031-12-04 22:00 | 33.7654 | 0.01632% | 35.2624 | 36.8258 | 38.4585 | 40.1635 | 0 | 0 | 1.3126 | 2.8472
2031-12-04 23:00 | 33.253 | 0.01607% | 34.7273 | 36.267 | 37.8749 | 39.554 | 0 | 0 | 0.78737 | 2.2986
2031-12-05 | 32.8589 | 0.01588% | 34.3157 | 35.8371 | 37.4259 | 39.0852 | 0 | 0 | 0.38333 | 1.8767
2031-12-05 01:00 | 32.1757 | 0.01555% | 33.6022 | 35.092 | 36.6478 | 38.2726 | 0 | 0 | 0 | 1.1453
2031-12-05 02:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-12-05 03:00 | 27.0912 | 0.01309% | 28.2923 | 29.5466 | 30.8566 | 32.2246 | 0 | 0 | 0 | 0
2031-12-05 04:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-12-05 05:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-12-05 06:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-12-05 07:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-12-05 08:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-12-05 09:00 | 23.8723 | 0.01154% | 24.9307 | 26.036 | 27.1903 | 28.3958 | 0 | 0 | 0 | 0
2031-12-05 10:00 | 27.17 | 0.01313% | 28.3746 | 29.6326 | 30.9463 | 32.3184 | 0 | 0 | 0 | 0
2031-12-05 11:00 | 29.167 | 0.0141% | 30.4601 | 31.8106 | 33.2209 | 34.6938 | 0 | 0 | 0 | 0
2031-12-05 12:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-12-05 13:00 | 29.64 | 0.01432% | 30.9541 | 32.3265 | 33.7597 | 35.2564 | 0 | 0 | 0 | 0
2031-12-05 14:00 | 30.0736 | 0.01453% | 31.4069 | 32.7993 | 34.2535 | 35.7721 | 0 | 0 | 0 | 0
2031-12-05 15:00 | 30.2181 | 0.0146% | 31.5578 | 32.9569 | 34.4181 | 35.944 | 0 | 0 | 0 | 0
2031-12-05 16:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-12-05 17:00 | 29.4035 | 0.01421% | 30.7071 | 32.0685 | 33.4903 | 34.9751 | 0 | 0 | 0 | 0
2031-12-05 18:00 | 29.1407 | 0.01408% | 30.4327 | 31.7819 | 33.191 | 34.6625 | 0 | 0 | 0 | 0
2031-12-05 19:00 | 29.6663 | 0.01434% | 30.9815 | 32.3551 | 33.7896 | 35.2876 | 0 | 0 | 0 | 0
2031-12-05 20:00 | 31.7027 | 0.01532% | 33.1083 | 34.5761 | 36.1091 | 37.71 | 0 | 0 | 0 | 0.63897
2031-12-05 21:00 | 32.8852 | 0.01589% | 34.3431 | 35.8657 | 37.4559 | 39.1165 | 0 | 0 | 0.41027 | 1.9048
2031-12-05 22:00 | 31.7684 | 0.01535% | 33.1769 | 34.6478 | 36.1839 | 37.7881 | 0 | 0 | 0 | 0.70929
2031-12-05 23:00 | 30.9538 | 0.01496% | 32.3262 | 33.7594 | 35.2561 | 36.8192 | 0 | 0 | 0 | 0
2031-12-06 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-12-06 01:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-12-06 02:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-12-06 03:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-12-06 04:00 | 23.5176 | 0.01137% | 24.5602 | 25.6491 | 26.7862 | 27.9738 | 0 | 0 | 0 | 0
2031-12-06 05:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-12-06 06:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-12-06 07:00 | 19.9834 | 0.009657% | 20.8693 | 21.7946 | 22.7608 | 23.7699 | 0 | 0 | 0 | 0
2031-12-06 08:00 | 19.7206 | 0.00953% | 20.5949 | 21.508 | 22.4615 | 23.4574 | 0 | 0 | 0 | 0
2031-12-06 09:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-12-06 10:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-12-06 11:00 | 22.9395 | 0.01109% | 23.9565 | 25.0186 | 26.1278 | 27.2862 | 0 | 0 | 0 | 0
2031-12-06 12:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-12-06 13:00 | 26.7496 | 0.01293% | 27.9355 | 29.174 | 30.4675 | 31.8183 | 0 | 0 | 0 | 0
2031-12-06 14:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-12-06 15:00 | 28.4313 | 0.01374% | 29.6918 | 31.0082 | 32.3829 | 33.8186 | 0 | 0 | 0 | 0
2031-12-06 16:00 | 28.6021 | 0.01382% | 29.8702 | 31.1945 | 32.5775 | 34.0218 | 0 | 0 | 0 | 0
2031-12-06 17:00 | 28.7729 | 0.0139% | 30.0485 | 31.3807 | 32.772 | 34.225 | 0 | 0 | 0 | 0
2031-12-06 18:00 | 28.4576 | 0.01375% | 29.7192 | 31.0368 | 32.4129 | 33.8499 | 0 | 0 | 0 | 0
2031-12-06 19:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-12-06 20:00 | 30.5991 | 0.01479% | 31.9557 | 33.3725 | 34.8521 | 36.3972 | 0 | 0 | 0 | 0
2031-12-06 21:00 | 31.4662 | 0.01521% | 32.8613 | 34.3182 | 35.8397 | 37.4287 | 0 | 0 | 0 | 0.3858
2031-12-06 22:00 | 30.7699 | 0.01487% | 32.1341 | 33.5588 | 35.0466 | 36.6004 | 0 | 0 | 0 | 0
2031-12-06 23:00 | 29.732 | 0.01437% | 31.0501 | 32.4268 | 33.8644 | 35.3658 | 0 | 0 | 0 | 0
2031-12-07 | 28.5101 | 0.01378% | 29.7741 | 31.0941 | 32.4727 | 33.9124 | 0 | 0 | 0 | 0
2031-12-07 01:00 | 27.5247 | 0.0133% | 28.745 | 30.0195 | 31.3504 | 32.7403 | 0 | 0 | 0 | 0
2031-12-07 02:00 | 25.9219 | 0.01253% | 27.0711 | 28.2713 | 29.5247 | 30.8337 | 0 | 0 | 0 | 0
2031-12-07 03:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-12-07 04:00 | 22.1118 | 0.01069% | 23.0921 | 24.1159 | 25.1851 | 26.3016 | 0 | 0 | 0 | 0
2031-12-07 05:00 | 20.7191 | 0.01001% | 21.6377 | 22.597 | 23.5988 | 24.6451 | 0 | 0 | 0 | 0
2031-12-07 06:00 | 19.8914 | 0.009613% | 20.7733 | 21.6943 | 22.6561 | 23.6605 | 0 | 0 | 0 | 0
2031-12-07 07:00 | 19.3264 | 0.00934% | 20.1833 | 21.0781 | 22.0126 | 22.9885 | 0 | 0 | 0 | 0
2031-12-07 08:00 | 19.1556 | 0.009257% | 20.0049 | 20.8918 | 21.8181 | 22.7854 | 0 | 0 | 0 | 0
2031-12-07 09:00 | 19.3921 | 0.009372% | 20.2519 | 21.1498 | 22.0874 | 23.0667 | 0 | 0 | 0 | 0
2031-12-07 10:00 | 20.4169 | 0.009867% | 21.3221 | 22.2674 | 23.2547 | 24.2857 | 0 | 0 | 0 | 0
2031-12-07 11:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-12-07 12:00 | 23.8854 | 0.01154% | 24.9444 | 26.0503 | 27.2053 | 28.4114 | 0 | 0 | 0 | 0
2031-12-07 13:00 | 25.5803 | 0.01236% | 26.7144 | 27.8988 | 29.1357 | 30.4274 | 0 | 0 | 0 | 0
2031-12-07 14:00 | 26.6182 | 0.01286% | 27.7983 | 29.0308 | 30.3178 | 31.662 | 0 | 0 | 0 | 0
2031-12-07 15:00 | 28.0897 | 0.01357% | 29.335 | 30.6356 | 31.9939 | 33.4123 | 0 | 0 | 0 | 0
2031-12-07 16:00 | 28.2211 | 0.01364% | 29.4723 | 30.7789 | 32.1435 | 33.5686 | 0 | 0 | 0 | 0
2031-12-07 17:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-12-07 18:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-12-07 19:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-12-07 20:00 | 33.253 | 0.01607% | 34.7273 | 36.267 | 37.8749 | 39.554 | 0 | 0 | 0.78737 | 2.2986
2031-12-07 21:00 | 35.1975 | 0.01701% | 36.758 | 38.3877 | 40.0896 | 41.867 | 0 | 1.2489 | 2.7806 | 4.3803
2031-12-07 22:00 | 34.0545 | 0.01646% | 35.5643 | 37.141 | 38.7877 | 40.5073 | 0 | 0.12693 | 1.6089 | 3.1566
2031-12-07 23:00 | 32.6487 | 0.01578% | 34.0962 | 35.6078 | 37.1865 | 38.8352 | 0 | 0 | 0.16785 | 1.6516
2031-12-08 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-12-08 01:00 | 30.2838 | 0.01464% | 31.6264 | 33.0286 | 34.4929 | 36.0222 | 0 | 0 | 0 | 0
2031-12-08 02:00 | 27.7875 | 0.01343% | 29.0195 | 30.306 | 31.6497 | 33.0529 | 0 | 0 | 0 | 0
2031-12-08 03:00 | 25.2649 | 0.01221% | 26.3851 | 27.5549 | 28.7765 | 30.0523 | 0 | 0 | 0 | 0
2031-12-08 04:00 | 23.2416 | 0.01123% | 24.2721 | 25.3482 | 26.472 | 27.6456 | 0 | 0 | 0 | 0
2031-12-08 05:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-12-08 06:00 | 21.4548 | 0.01037% | 22.406 | 23.3994 | 24.4368 | 25.5203 | 0 | 0 | 0 | 0
2031-12-08 07:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-12-08 08:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-12-08 09:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-12-08 10:00 | 26.3817 | 0.01275% | 27.5513 | 28.7728 | 30.0485 | 31.3807 | 0 | 0 | 0 | 0
2031-12-08 11:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-12-08 12:00 | 29.4561 | 0.01424% | 30.762 | 32.1258 | 33.5502 | 35.0376 | 0 | 0 | 0 | 0
2031-12-08 13:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-12-08 14:00 | 29.259 | 0.01414% | 30.5562 | 31.9109 | 33.3257 | 34.8032 | 0 | 0 | 0 | 0
2031-12-08 15:00 | 29.2459 | 0.01413% | 30.5425 | 31.8966 | 33.3107 | 34.7876 | 0 | 0 | 0 | 0
2031-12-08 16:00 | 28.8254 | 0.01393% | 30.1034 | 31.438 | 32.8319 | 34.2875 | 0 | 0 | 0 | 0
2031-12-08 17:00 | 28.9831 | 0.01401% | 30.2681 | 31.61 | 33.0114 | 34.475 | 0 | 0 | 0 | 0
2031-12-08 18:00 | 28.786 | 0.01391% | 30.0622 | 31.3951 | 32.787 | 34.2406 | 0 | 0 | 0 | 0
2031-12-08 19:00 | 29.5612 | 0.01429% | 30.8718 | 32.2405 | 33.6699 | 35.1626 | 0 | 0 | 0 | 0
2031-12-08 20:00 | 33.5552 | 0.01622% | 35.0429 | 36.5965 | 38.219 | 39.9135 | 0 | 0 | 1.0971 | 2.6221
2031-12-08 21:00 | 35.2238 | 0.01702% | 36.7854 | 38.4163 | 40.1195 | 41.8982 | 0 | 1.2747 | 2.8076 | 4.4084
2031-12-08 22:00 | 34.4486 | 0.01665% | 35.9759 | 37.5709 | 39.2366 | 40.9762 | 0 | 0.51381 | 2.013 | 3.5786
2031-12-08 23:00 | 33.5027 | 0.01619% | 34.988 | 36.5392 | 38.1592 | 39.851 | 0 | 0 | 1.0433 | 2.5659
2031-12-09 | 32.9509 | 0.01592% | 34.4117 | 35.9374 | 37.5307 | 39.1946 | 0 | 0 | 0.47761 | 1.9751
2031-12-09 01:00 | 31.9392 | 0.01544% | 33.3552 | 34.834 | 36.3784 | 37.9913 | 0 | 0 | 0 | 0.89214
2031-12-09 02:00 | 29.9553 | 0.01448% | 31.2834 | 32.6704 | 34.1188 | 35.6315 | 0 | 0 | 0 | 0
2031-12-09 03:00 | 26.8284 | 0.01297% | 28.0178 | 29.26 | 30.5573 | 31.912 | 0 | 0 | 0 | 0
2031-12-09 04:00 | 24.7394 | 0.01196% | 25.8362 | 26.9817 | 28.1779 | 29.4272 | 0 | 0 | 0 | 0
2031-12-09 05:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-12-09 06:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-12-09 07:00 | 22.0592 | 0.01066% | 23.0372 | 24.0586 | 25.1252 | 26.2391 | 0 | 0 | 0 | 0
2031-12-09 08:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-12-09 09:00 | 23.3073 | 0.01126% | 24.3407 | 25.4198 | 26.5468 | 27.7238 | 0 | 0 | 0 | 0
2031-12-09 10:00 | 26.2766 | 0.0127% | 27.4416 | 28.6582 | 29.9288 | 31.2557 | 0 | 0 | 0 | 0
2031-12-09 11:00 | 28.0503 | 0.01356% | 29.2939 | 30.5926 | 31.949 | 33.3654 | 0 | 0 | 0 | 0
2031-12-09 12:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-12-09 13:00 | 29.4166 | 0.01422% | 30.7208 | 32.0829 | 33.5053 | 34.9907 | 0 | 0 | 0 | 0
2031-12-09 14:00 | 29.5743 | 0.01429% | 30.8855 | 32.2548 | 33.6848 | 35.1783 | 0 | 0 | 0 | 0
2031-12-09 15:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-12-09 16:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-12-09 17:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-12-09 18:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-12-09 19:00 | 30.7173 | 0.01484% | 32.0792 | 33.5014 | 34.9867 | 36.5379 | 0 | 0 | 0 | 0
2031-12-09 20:00 | 34.1333 | 0.0165% | 35.6466 | 37.227 | 38.8775 | 40.6011 | 0 | 0.2043 | 1.6897 | 3.241
2031-12-09 21:00 | 35.1449 | 0.01698% | 36.7031 | 38.3303 | 40.0297 | 41.8045 | 0 | 1.1973 | 2.7268 | 4.324
2031-12-09 22:00 | 33.726 | 0.0163% | 35.2213 | 36.7828 | 38.4136 | 40.1166 | 0 | 0 | 1.2722 | 2.805
2031-12-09 23:00 | 33.2399 | 0.01606% | 34.7136 | 36.2526 | 37.8599 | 39.5384 | 0 | 0 | 0.7739 | 2.2846
2031-12-10 | 31.7815 | 0.01536% | 33.1906 | 34.6621 | 36.1988 | 37.8037 | 0 | 0 | 0 | 0.72336
2031-12-10 01:00 | 30.2312 | 0.01461% | 31.5715 | 32.9713 | 34.433 | 35.9596 | 0 | 0 | 0 | 0
2031-12-10 02:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-12-10 03:00 | 24.792 | 0.01198% | 25.8911 | 27.039 | 28.2378 | 29.4897 | 0 | 0 | 0 | 0
2031-12-10 04:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-12-10 05:00 | 20.7848 | 0.01004% | 21.7063 | 22.6686 | 23.6737 | 24.7232 | 0 | 0 | 0 | 0
2031-12-10 06:00 | 20.1541 | 0.00974% | 21.0477 | 21.9808 | 22.9554 | 23.9731 | 0 | 0 | 0 | 0
2031-12-10 07:00 | 19.6286 | 0.009486% | 20.4989 | 21.4077 | 22.3568 | 23.348 | 0 | 0 | 0 | 0
2031-12-10 08:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-12-10 09:00 | 21.4154 | 0.01035% | 22.3649 | 23.3564 | 24.3919 | 25.4734 | 0 | 0 | 0 | 0
2031-12-10 10:00 | 24.3059 | 0.01175% | 25.3835 | 26.5088 | 27.6841 | 28.9115 | 0 | 0 | 0 | 0
2031-12-10 11:00 | 25.8693 | 0.0125% | 27.0162 | 28.214 | 29.4649 | 30.7712 | 0 | 0 | 0 | 0
2031-12-10 12:00 | 26.8021 | 0.01295% | 27.9904 | 29.2314 | 30.5273 | 31.8808 | 0 | 0 | 0 | 0
2031-12-10 13:00 | 27.551 | 0.01331% | 28.7725 | 30.0481 | 31.3803 | 32.7716 | 0 | 0 | 0 | 0
2031-12-10 14:00 | 28.6678 | 0.01385% | 29.9388 | 31.2661 | 32.6523 | 34.0999 | 0 | 0 | 0 | 0
2031-12-10 15:00 | 29.548 | 0.01428% | 30.858 | 32.2261 | 33.6549 | 35.147 | 0 | 0 | 0 | 0
2031-12-10 16:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-12-10 17:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-12-10 18:00 | 29.1145 | 0.01407% | 30.4053 | 31.7533 | 33.1611 | 34.6313 | 0 | 0 | 0 | 0
2031-12-10 19:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-12-10 20:00 | 31.9392 | 0.01544% | 33.3552 | 34.834 | 36.3784 | 37.9913 | 0 | 0 | 0 | 0.89214
2031-12-10 21:00 | 33.4238 | 0.01615% | 34.9057 | 36.4532 | 38.0694 | 39.7572 | 0 | 0 | 0.96245 | 2.4815
2031-12-10 22:00 | 32.5436 | 0.01573% | 33.9864 | 35.4932 | 37.0668 | 38.7101 | 0 | 0 | 0.060103 | 1.5391
2031-12-10 23:00 | 31.6896 | 0.01531% | 33.0945 | 34.5618 | 36.0941 | 37.6943 | 0 | 0 | 0 | 0.6249
2031-12-11 | 31.4531 | 0.0152% | 32.8476 | 34.3039 | 35.8247 | 37.413 | 0 | 0 | 0 | 0.37173
2031-12-11 01:00 | 30.2049 | 0.0146% | 31.5441 | 32.9426 | 34.4031 | 35.9284 | 0 | 0 | 0 | 0
2031-12-11 02:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-12-11 03:00 | 25.4095 | 0.01228% | 26.536 | 27.7125 | 28.9411 | 30.2242 | 0 | 0 | 0 | 0
2031-12-11 04:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-12-11 05:00 | 22.3482 | 0.0108% | 23.3391 | 24.3738 | 25.4544 | 26.5829 | 0 | 0 | 0 | 0
2031-12-11 06:00 | 21.3497 | 0.01032% | 22.2963 | 23.2848 | 24.3171 | 25.3952 | 0 | 0 | 0 | 0
2031-12-11 07:00 | 21.1395 | 0.01022% | 22.0767 | 23.0555 | 24.0777 | 25.1452 | 0 | 0 | 0 | 0
2031-12-11 08:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-12-11 09:00 | 23.2942 | 0.01126% | 24.327 | 25.4055 | 26.5319 | 27.7081 | 0 | 0 | 0 | 0
2031-12-11 10:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-12-11 11:00 | 28.6809 | 0.01386% | 29.9525 | 31.2804 | 32.6673 | 34.1156 | 0 | 0 | 0 | 0
2031-12-11 12:00 | 29.3772 | 0.0142% | 30.6797 | 32.0399 | 33.4604 | 34.9438 | 0 | 0 | 0 | 0
2031-12-11 13:00 | 29.3904 | 0.0142% | 30.6934 | 32.0542 | 33.4753 | 34.9595 | 0 | 0 | 0 | 0
2031-12-11 14:00 | 29.8634 | 0.01443% | 31.1873 | 32.57 | 34.014 | 35.5221 | 0 | 0 | 0 | 0
2031-12-11 15:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-12-11 16:00 | 29.4561 | 0.01424% | 30.762 | 32.1258 | 33.5502 | 35.0376 | 0 | 0 | 0 | 0
2031-12-11 17:00 | 30.0341 | 0.01451% | 31.3657 | 32.7563 | 34.2086 | 35.7252 | 0 | 0 | 0 | 0
2031-12-11 18:00 | 29.5874 | 0.0143% | 30.8992 | 32.2691 | 33.6998 | 35.1939 | 0 | 0 | 0 | 0
2031-12-11 19:00 | 30.5991 | 0.01479% | 31.9557 | 33.3725 | 34.8521 | 36.3972 | 0 | 0 | 0 | 0
2031-12-11 20:00 | 33.1085 | 0.016% | 34.5764 | 36.1093 | 37.7102 | 39.3821 | 0 | 0 | 0.63922 | 2.1439
2031-12-11 21:00 | 35.0924 | 0.01696% | 36.6482 | 38.273 | 39.9699 | 41.7419 | 0 | 1.1457 | 2.6729 | 4.2677
2031-12-11 22:00 | 34.3829 | 0.01662% | 35.9073 | 37.4993 | 39.1618 | 40.898 | 0 | 0.44933 | 1.9456 | 3.5082
2031-12-11 23:00 | 34.107 | 0.01648% | 35.6192 | 37.1983 | 38.8475 | 40.5699 | 0 | 0.17851 | 1.6628 | 3.2129
2031-12-12 | 33.4632 | 0.01617% | 34.9468 | 36.4962 | 38.1143 | 39.8041 | 0 | 0 | 1.0029 | 2.5237
2031-12-12 01:00 | 32.6487 | 0.01578% | 34.0962 | 35.6078 | 37.1865 | 38.8352 | 0 | 0 | 0.16785 | 1.6516
2031-12-12 02:00 | 30.2181 | 0.0146% | 31.5578 | 32.9569 | 34.4181 | 35.944 | 0 | 0 | 0 | 0
2031-12-12 03:00 | 27.7744 | 0.01342% | 29.0057 | 30.2917 | 31.6347 | 33.0372 | 0 | 0 | 0 | 0
2031-12-12 04:00 | 25.4883 | 0.01232% | 26.6183 | 27.7985 | 29.0309 | 30.318 | 0 | 0 | 0 | 0
2031-12-12 05:00 | 24.1219 | 0.01166% | 25.1914 | 26.3082 | 27.4746 | 28.6927 | 0 | 0 | 0 | 0
2031-12-12 06:00 | 23.176 | 0.0112% | 24.2035 | 25.2765 | 26.3972 | 27.5675 | 0 | 0 | 0 | 0
2031-12-12 07:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-12-12 08:00 | 22.6373 | 0.01094% | 23.6409 | 24.689 | 25.7836 | 26.9268 | 0 | 0 | 0 | 0
2031-12-12 09:00 | 23.8329 | 0.01152% | 24.8895 | 25.993 | 27.1454 | 28.3489 | 0 | 0 | 0 | 0
2031-12-12 10:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-12-12 11:00 | 29.1802 | 0.0141% | 30.4739 | 31.8249 | 33.2359 | 34.7094 | 0 | 0 | 0 | 0
2031-12-12 12:00 | 29.7057 | 0.01436% | 31.0227 | 32.3981 | 33.8345 | 35.3345 | 0 | 0 | 0 | 0
2031-12-12 13:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-12-12 14:00 | 30.0473 | 0.01452% | 31.3794 | 32.7707 | 34.2235 | 35.7409 | 0 | 0 | 0 | 0
2031-12-12 15:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-12-12 16:00 | 30.1655 | 0.01458% | 31.5029 | 32.8996 | 34.3582 | 35.8815 | 0 | 0 | 0 | 0
2031-12-12 17:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-12-12 18:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-12-12 19:00 | 30.113 | 0.01455% | 31.448 | 32.8423 | 34.2984 | 35.819 | 0 | 0 | 0 | 0
2031-12-12 20:00 | 32.0443 | 0.01549% | 33.465 | 34.9487 | 36.4981 | 38.1163 | 0 | 0 | 0 | 1.0047
2031-12-12 21:00 | 32.6881 | 0.0158% | 34.1373 | 35.6508 | 37.2314 | 38.8821 | 0 | 0 | 0.20825 | 1.6938
2031-12-12 22:00 | 32.2282 | 0.01557% | 33.6571 | 35.1493 | 36.7076 | 38.3351 | 0 | 0 | 0 | 1.2016
2031-12-12 23:00 | 31.256 | 0.0151% | 32.6418 | 34.0889 | 35.6003 | 37.1786 | 0 | 0 | 0 | 0.16075
2031-12-13 | 30.6648 | 0.01482% | 32.0243 | 33.4441 | 34.9269 | 36.4754 | 0 | 0 | 0 | 0
2031-12-13 01:00 | 30.0341 | 0.01451% | 31.3657 | 32.7563 | 34.2086 | 35.7252 | 0 | 0 | 0 | 0
2031-12-13 02:00 | 28.3393 | 0.0137% | 29.5957 | 30.9079 | 32.2782 | 33.7092 | 0 | 0 | 0 | 0
2031-12-13 03:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-12-13 04:00 | 23.754 | 0.01148% | 24.8072 | 25.907 | 27.0556 | 28.2551 | 0 | 0 | 0 | 0
2031-12-13 05:00 | 22.3877 | 0.01082% | 23.3802 | 24.4168 | 25.4993 | 26.6298 | 0 | 0 | 0 | 0
2031-12-13 06:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-12-13 07:00 | 20.4826 | 0.009899% | 21.3907 | 22.3391 | 23.3295 | 24.3638 | 0 | 0 | 0 | 0
2031-12-13 08:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-12-13 09:00 | 20.6271 | 0.009968% | 21.5416 | 22.4967 | 23.4941 | 24.5357 | 0 | 0 | 0 | 0
2031-12-13 10:00 | 21.7702 | 0.01052% | 22.7353 | 23.7433 | 24.796 | 25.8953 | 0 | 0 | 0 | 0
2031-12-13 11:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-12-13 12:00 | 25.1204 | 0.01214% | 26.2341 | 27.3972 | 28.6119 | 29.8804 | 0 | 0 | 0 | 0
2031-12-13 13:00 | 27.0255 | 0.01306% | 28.2237 | 29.475 | 30.7817 | 32.1465 | 0 | 0 | 0 | 0
2031-12-13 14:00 | 27.932 | 0.0135% | 29.1704 | 30.4637 | 31.8143 | 33.2248 | 0 | 0 | 0 | 0
2031-12-13 15:00 | 28.5364 | 0.01379% | 29.8015 | 31.1228 | 32.5026 | 33.9437 | 0 | 0 | 0 | 0
2031-12-13 16:00 | 29.0094 | 0.01402% | 30.2955 | 31.6387 | 33.0414 | 34.5063 | 0 | 0 | 0 | 0
2031-12-13 17:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-12-13 18:00 | 28.405 | 0.01373% | 29.6643 | 30.9795 | 32.353 | 33.7874 | 0 | 0 | 0 | 0
2031-12-13 19:00 | 29.3641 | 0.01419% | 30.666 | 32.0255 | 33.4454 | 34.9282 | 0 | 0 | 0 | 0
2031-12-13 20:00 | 31.8866 | 0.01541% | 33.3004 | 34.7767 | 36.3186 | 37.9288 | 0 | 0 | 0 | 0.83588
2031-12-13 21:00 | 32.8195 | 0.01586% | 34.2745 | 35.7941 | 37.381 | 39.0383 | 0 | 0 | 0.34293 | 1.8345
2031-12-13 22:00 | 32.3071 | 0.01561% | 33.7394 | 35.2353 | 36.7974 | 38.4288 | 0 | 0 | 0 | 1.286
2031-12-13 23:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-12-14 | 30.0867 | 0.01454% | 31.4206 | 32.8136 | 34.2684 | 35.7877 | 0 | 0 | 0 | 0
2031-12-14 01:00 | 29.1539 | 0.01409% | 30.4464 | 31.7963 | 33.206 | 34.6782 | 0 | 0 | 0 | 0
2031-12-14 02:00 | 27.7087 | 0.01339% | 28.9371 | 30.2201 | 31.5599 | 32.9591 | 0 | 0 | 0 | 0
2031-12-14 03:00 | 26.4211 | 0.01277% | 27.5925 | 28.8158 | 30.0934 | 31.4276 | 0 | 0 | 0 | 0
2031-12-14 04:00 | 24.6737 | 0.01192% | 25.7676 | 26.9101 | 28.1031 | 29.3491 | 0 | 0 | 0 | 0
2031-12-14 05:00 | 23.0052 | 0.01112% | 24.0251 | 25.0903 | 26.2026 | 27.3643 | 0 | 0 | 0 | 0
2031-12-14 06:00 | 22.0198 | 0.01064% | 22.996 | 24.0156 | 25.0803 | 26.1922 | 0 | 0 | 0 | 0
2031-12-14 07:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-12-14 08:00 | 21.4417 | 0.01036% | 22.3923 | 23.3851 | 24.4219 | 25.5046 | 0 | 0 | 0 | 0
2031-12-14 09:00 | 22.138 | 0.0107% | 23.1195 | 24.1445 | 25.215 | 26.3329 | 0 | 0 | 0 | 0
2031-12-14 10:00 | 22.7161 | 0.01098% | 23.7232 | 24.775 | 25.8734 | 27.0205 | 0 | 0 | 0 | 0
2031-12-14 11:00 | 24.6474 | 0.01191% | 25.7402 | 26.8814 | 28.0732 | 29.3178 | 0 | 0 | 0 | 0
2031-12-14 12:00 | 26.8153 | 0.01296% | 28.0041 | 29.2457 | 30.5423 | 31.8964 | 0 | 0 | 0 | 0
2031-12-14 13:00 | 27.8795 | 0.01347% | 29.1155 | 30.4064 | 31.7544 | 33.1623 | 0 | 0 | 0 | 0
2031-12-14 14:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-12-14 15:00 | 29.7582 | 0.01438% | 31.0776 | 32.4554 | 33.8943 | 35.397 | 0 | 0 | 0 | 0
2031-12-14 16:00 | 29.9947 | 0.0145% | 31.3246 | 32.7133 | 34.1637 | 35.6783 | 0 | 0 | 0 | 0
2031-12-14 17:00 | 30.3232 | 0.01465% | 31.6676 | 33.0716 | 34.5378 | 36.069 | 0 | 0 | 0 | 0
2031-12-14 18:00 | 30.1787 | 0.01458% | 31.5166 | 32.9139 | 34.3732 | 35.8971 | 0 | 0 | 0 | 0
2031-12-14 19:00 | 31.6239 | 0.01528% | 33.0259 | 34.4901 | 36.0193 | 37.6162 | 0 | 0 | 0 | 0.55458
2031-12-14 20:00 | 35.0004 | 0.01691% | 36.5522 | 38.1727 | 39.8651 | 41.6325 | 0 | 1.0555 | 2.5786 | 4.1693
2031-12-14 21:00 | 36.669 | 0.01772% | 38.2947 | 39.9925 | 41.7656 | 43.6173 | 1.1652 | 2.6933 | 4.289 | 5.9556
2031-12-14 22:00 | 36.3668 | 0.01757% | 37.9791 | 39.663 | 41.4214 | 43.2578 | 0.88122 | 2.3967 | 3.9793 | 5.6321
2031-12-14 23:00 | 35.0398 | 0.01693% | 36.5933 | 38.2157 | 39.91 | 41.6794 | 0 | 1.0941 | 2.619 | 4.2115
2031-12-15 | 34.0019 | 0.01643% | 35.5094 | 37.0837 | 38.7278 | 40.4448 | 0 | 0.075342 | 1.555 | 3.1004
2031-12-15 01:00 | 32.9509 | 0.01592% | 34.4117 | 35.9374 | 37.5307 | 39.1946 | 0 | 0 | 0.47761 | 1.9751
2031-12-15 02:00 | 29.7845 | 0.01439% | 31.105 | 32.4841 | 33.9243 | 35.4283 | 0 | 0 | 0 | 0
2031-12-15 03:00 | 27.2357 | 0.01316% | 28.4432 | 29.7042 | 31.0212 | 32.3965 | 0 | 0 | 0 | 0
2031-12-15 04:00 | 25.0153 | 0.01209% | 26.1244 | 27.2826 | 28.4922 | 29.7554 | 0 | 0 | 0 | 0
2031-12-15 05:00 | 23.2679 | 0.01124% | 24.2995 | 25.3768 | 26.5019 | 27.6769 | 0 | 0 | 0 | 0
2031-12-15 06:00 | 22.5979 | 0.01092% | 23.5998 | 24.6461 | 25.7387 | 26.8799 | 0 | 0 | 0 | 0
2031-12-15 07:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-12-15 08:00 | 22.3614 | 0.01081% | 23.3528 | 24.3881 | 25.4694 | 26.5986 | 0 | 0 | 0 | 0
2031-12-15 09:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-12-15 10:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-12-15 11:00 | 28.9043 | 0.01397% | 30.1857 | 31.524 | 32.9216 | 34.3812 | 0 | 0 | 0 | 0
2031-12-15 12:00 | 29.1933 | 0.01411% | 30.4876 | 31.8393 | 33.2509 | 34.725 | 0 | 0 | 0 | 0
2031-12-15 13:00 | 29.9159 | 0.01446% | 31.2422 | 32.6274 | 34.0739 | 35.5846 | 0 | 0 | 0 | 0
2031-12-15 14:00 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-12-15 15:00 | 30.8619 | 0.01491% | 32.2301 | 33.6591 | 35.1513 | 36.7098 | 0 | 0 | 0 | 0
2031-12-15 16:00 | 30.586 | 0.01478% | 31.942 | 33.3581 | 34.8371 | 36.3816 | 0 | 0 | 0 | 0
2031-12-15 17:00 | 30.8487 | 0.01491% | 32.2164 | 33.6447 | 35.1364 | 36.6942 | 0 | 0 | 0 | 0
2031-12-15 18:00 | 30.8356 | 0.0149% | 32.2027 | 33.6304 | 35.1214 | 36.6785 | 0 | 0 | 0 | 0
2031-12-15 19:00 | 31.4005 | 0.01517% | 32.7927 | 34.2466 | 35.7649 | 37.3505 | 0 | 0 | 0 | 0.31547
2031-12-15 20:00 | 34.0939 | 0.01648% | 35.6054 | 37.184 | 38.8326 | 40.5542 | 0 | 0.16562 | 1.6493 | 3.1988
2031-12-15 21:00 | 35.4865 | 0.01715% | 37.0598 | 38.7029 | 40.4188 | 42.2108 | 0.053861 | 1.5326 | 3.0769 | 4.6897
2031-12-15 22:00 | 35.1055 | 0.01697% | 36.6619 | 38.2874 | 39.9848 | 41.7576 | 0 | 1.1586 | 2.6864 | 4.2818
2031-12-15 23:00 | 34.2647 | 0.01656% | 35.7838 | 37.3703 | 39.0271 | 40.7574 | 0 | 0.33327 | 1.8244 | 3.3817
2031-12-16 | 33.0165 | 0.01596% | 34.4803 | 36.009 | 37.6055 | 39.2727 | 0 | 0 | 0.54495 | 2.0455
2031-12-16 01:00 | 32.202 | 0.01556% | 33.6296 | 35.1206 | 36.6777 | 38.3038 | 0 | 0 | 0 | 1.1734
2031-12-16 02:00 | 30.1787 | 0.01458% | 31.5166 | 32.9139 | 34.3732 | 35.8971 | 0 | 0 | 0 | 0
2031-12-16 03:00 | 26.224 | 0.01267% | 27.3867 | 28.6009 | 29.8689 | 31.1932 | 0 | 0 | 0 | 0
2031-12-16 04:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-12-16 05:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-12-16 06:00 | 21.849 | 0.01056% | 22.8177 | 23.8293 | 24.8858 | 25.9891 | 0 | 0 | 0 | 0
2031-12-16 07:00 | 21.4023 | 0.01034% | 22.3512 | 23.3421 | 24.377 | 25.4577 | 0 | 0 | 0 | 0
2031-12-16 08:00 | 21.5074 | 0.01039% | 22.4609 | 23.4567 | 24.4967 | 25.5828 | 0 | 0 | 0 | 0
2031-12-16 09:00 | 22.7555 | 0.011% | 23.7644 | 24.818 | 25.9183 | 27.0674 | 0 | 0 | 0 | 0
2031-12-16 10:00 | 25.646 | 0.01239% | 26.783 | 27.9704 | 29.2105 | 30.5055 | 0 | 0 | 0 | 0
2031-12-16 11:00 | 27.8663 | 0.01347% | 29.1018 | 30.392 | 31.7395 | 33.1466 | 0 | 0 | 0 | 0
2031-12-16 12:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-12-16 13:00 | 28.9699 | 0.014% | 30.2543 | 31.5957 | 32.9965 | 34.4594 | 0 | 0 | 0 | 0
2031-12-16 14:00 | 29.4692 | 0.01424% | 30.7757 | 32.1402 | 33.5651 | 35.0532 | 0 | 0 | 0 | 0
2031-12-16 15:00 | 29.9685 | 0.01448% | 31.2971 | 32.6847 | 34.1338 | 35.6471 | 0 | 0 | 0 | 0
2031-12-16 16:00 | 30.113 | 0.01455% | 31.448 | 32.8423 | 34.2984 | 35.819 | 0 | 0 | 0 | 0
2031-12-16 17:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-12-16 18:00 | 30.402 | 0.01469% | 31.7499 | 33.1575 | 34.6276 | 36.1628 | 0 | 0 | 0 | 0
2031-12-16 19:00 | 30.7568 | 0.01486% | 32.1204 | 33.5444 | 35.0316 | 36.5848 | 0 | 0 | 0 | 0
2031-12-16 20:00 | 33.2662 | 0.01608% | 34.741 | 36.2813 | 37.8898 | 39.5697 | 0 | 0 | 0.80084 | 2.3127
2031-12-16 21:00 | 34.4355 | 0.01664% | 35.9622 | 37.5566 | 39.2217 | 40.9606 | 0 | 0.50092 | 1.9995 | 3.5645
2031-12-16 22:00 | 33.6997 | 0.01629% | 35.1938 | 36.7541 | 38.3836 | 40.0854 | 0 | 0 | 1.2453 | 2.7769
2031-12-16 23:00 | 32.7669 | 0.01584% | 34.2196 | 35.7368 | 37.3212 | 38.9758 | 0 | 0 | 0.28906 | 1.7782
2031-12-17 | 31.8078 | 0.01537% | 33.218 | 34.6908 | 36.2288 | 37.835 | 0 | 0 | 0 | 0.75149
2031-12-17 01:00 | 30.6779 | 0.01483% | 32.038 | 33.4585 | 34.9418 | 36.491 | 0 | 0 | 0 | 0
2031-12-17 02:00 | 28.4181 | 0.01373% | 29.6781 | 30.9938 | 32.368 | 33.803 | 0 | 0 | 0 | 0
2031-12-17 03:00 | 25.5014 | 0.01232% | 26.632 | 27.8128 | 29.0459 | 30.3336 | 0 | 0 | 0 | 0
2031-12-17 04:00 | 22.7949 | 0.01102% | 23.8056 | 24.861 | 25.9632 | 27.1143 | 0 | 0 | 0 | 0
2031-12-17 05:00 | 21.4286 | 0.01036% | 22.3786 | 23.3708 | 24.4069 | 25.489 | 0 | 0 | 0 | 0
2031-12-17 06:00 | 20.7716 | 0.01004% | 21.6926 | 22.6543 | 23.6587 | 24.7076 | 0 | 0 | 0 | 0
2031-12-17 07:00 | 20.2987 | 0.00981% | 21.1986 | 22.1385 | 23.12 | 24.145 | 0 | 0 | 0 | 0
2031-12-17 08:00 | 20.2593 | 0.009791% | 21.1575 | 22.0955 | 23.0751 | 24.0981 | 0 | 0 | 0 | 0
2031-12-17 09:00 | 21.7833 | 0.01053% | 22.7491 | 23.7576 | 24.8109 | 25.9109 | 0 | 0 | 0 | 0
2031-12-17 10:00 | 24.5029 | 0.01184% | 25.5893 | 26.7238 | 27.9086 | 29.1459 | 0 | 0 | 0 | 0
2031-12-17 11:00 | 26.3948 | 0.01276% | 27.5651 | 28.7872 | 30.0634 | 31.3963 | 0 | 0 | 0 | 0
2031-12-17 12:00 | 26.697 | 0.0129% | 27.8806 | 29.1167 | 30.4076 | 31.7558 | 0 | 0 | 0 | 0
2031-12-17 13:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-12-17 14:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-12-17 15:00 | 27.7875 | 0.01343% | 29.0195 | 30.306 | 31.6497 | 33.0529 | 0 | 0 | 0 | 0
2031-12-17 16:00 | 28.313 | 0.01368% | 29.5683 | 30.8792 | 32.2482 | 33.678 | 0 | 0 | 0 | 0
2031-12-17 17:00 | 28.1948 | 0.01363% | 29.4448 | 30.7503 | 32.1136 | 33.5373 | 0 | 0 | 0 | 0
2031-12-17 18:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-12-17 19:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-12-17 20:00 | 31.1903 | 0.01507% | 32.5731 | 34.0173 | 35.5254 | 37.1005 | 0 | 0 | 0 | 0.090429
2031-12-17 21:00 | 32.3202 | 0.01562% | 33.7531 | 35.2496 | 36.8124 | 38.4445 | 0 | 0 | 0 | 1.3
2031-12-17 22:00 | 31.8735 | 0.0154% | 33.2866 | 34.7624 | 36.3036 | 37.9131 | 0 | 0 | 0 | 0.82181
2031-12-17 23:00 | 31.1903 | 0.01507% | 32.5731 | 34.0173 | 35.5254 | 37.1005 | 0 | 0 | 0 | 0.090429
2031-12-18 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-12-18 01:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-12-18 02:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-12-18 03:00 | 24.4241 | 0.0118% | 25.5069 | 26.6378 | 27.8188 | 29.0521 | 0 | 0 | 0 | 0
2031-12-18 04:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-12-18 05:00 | 21.087 | 0.01019% | 22.0219 | 22.9982 | 24.0178 | 25.0827 | 0 | 0 | 0 | 0
2031-12-18 06:00 | 20.1673 | 0.009746% | 21.0614 | 21.9952 | 22.9703 | 23.9887 | 0 | 0 | 0 | 0
2031-12-18 07:00 | 19.3659 | 0.009359% | 20.2244 | 21.1211 | 22.0575 | 23.0354 | 0 | 0 | 0 | 0
2031-12-18 08:00 | 19.6155 | 0.009479% | 20.4851 | 21.3933 | 22.3418 | 23.3324 | 0 | 0 | 0 | 0
2031-12-18 09:00 | 21.1789 | 0.01024% | 22.1179 | 23.0985 | 24.1226 | 25.1921 | 0 | 0 | 0 | 0
2031-12-18 10:00 | 23.6884 | 0.01145% | 24.7386 | 25.8354 | 26.9808 | 28.177 | 0 | 0 | 0 | 0
2031-12-18 11:00 | 25.9087 | 0.01252% | 27.0574 | 28.257 | 29.5098 | 30.8181 | 0 | 0 | 0 | 0
2031-12-18 12:00 | 26.3423 | 0.01273% | 27.5102 | 28.7298 | 30.0036 | 31.3338 | 0 | 0 | 0 | 0
2031-12-18 13:00 | 26.5394 | 0.01283% | 27.716 | 28.9448 | 30.2281 | 31.5682 | 0 | 0 | 0 | 0
2031-12-18 14:00 | 27.3145 | 0.0132% | 28.5255 | 29.7902 | 31.111 | 32.4903 | 0 | 0 | 0 | 0
2031-12-18 15:00 | 26.9861 | 0.01304% | 28.1825 | 29.432 | 30.7368 | 32.0996 | 0 | 0 | 0 | 0
2031-12-18 16:00 | 26.7102 | 0.01291% | 27.8944 | 29.1311 | 30.4226 | 31.7714 | 0 | 0 | 0 | 0
2031-12-18 17:00 | 26.5788 | 0.01284% | 27.7572 | 28.9878 | 30.2729 | 31.6151 | 0 | 0 | 0 | 0
2031-12-18 18:00 | 26.4868 | 0.0128% | 27.6611 | 28.8875 | 30.1682 | 31.5057 | 0 | 0 | 0 | 0
2031-12-18 19:00 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-12-18 20:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-12-18 21:00 | 31.0195 | 0.01499% | 32.3948 | 33.831 | 35.3309 | 36.8973 | 0 | 0 | 0 | 0
2031-12-18 22:00 | 30.3626 | 0.01467% | 31.7087 | 33.1146 | 34.5827 | 36.1159 | 0 | 0 | 0 | 0
2031-12-18 23:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-12-19 | 29.1013 | 0.01406% | 30.3915 | 31.739 | 33.1461 | 34.6157 | 0 | 0 | 0 | 0
2031-12-19 01:00 | 28.6546 | 0.01385% | 29.925 | 31.2518 | 32.6373 | 34.0843 | 0 | 0 | 0 | 0
2031-12-19 02:00 | 26.1715 | 0.01265% | 27.3318 | 28.5436 | 29.8091 | 31.1306 | 0 | 0 | 0 | 0
2031-12-19 03:00 | 23.2811 | 0.01125% | 24.3132 | 25.3912 | 26.5169 | 27.6925 | 0 | 0 | 0 | 0
2031-12-19 04:00 | 20.8505 | 0.01008% | 21.7749 | 22.7403 | 23.7485 | 24.8014 | 0 | 0 | 0 | 0
2031-12-19 05:00 | 19.287 | 0.009321% | 20.1421 | 21.0351 | 21.9677 | 22.9417 | 0 | 0 | 0 | 0
2031-12-19 06:00 | 18.3936 | 0.008889% | 19.2091 | 20.0607 | 20.9501 | 21.879 | 0 | 0 | 0 | 0
2031-12-19 07:00 | 17.7893 | 0.008597% | 18.5779 | 19.4016 | 20.2618 | 21.1601 | 0 | 0 | 0 | 0
2031-12-19 08:00 | 17.9469 | 0.008673% | 18.7426 | 19.5736 | 20.4413 | 21.3476 | 0 | 0 | 0 | 0
2031-12-19 09:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-12-19 10:00 | 21.8227 | 0.01055% | 22.7902 | 23.8006 | 24.8558 | 25.9578 | 0 | 0 | 0 | 0
2031-12-19 11:00 | 24.5686 | 0.01187% | 25.6579 | 26.7954 | 27.9834 | 29.224 | 0 | 0 | 0 | 0
2031-12-19 12:00 | 25.8956 | 0.01251% | 27.0437 | 28.2427 | 29.4948 | 30.8025 | 0 | 0 | 0 | 0
2031-12-19 13:00 | 26.3948 | 0.01276% | 27.5651 | 28.7872 | 30.0634 | 31.3963 | 0 | 0 | 0 | 0
2031-12-19 14:00 | 27.2488 | 0.01317% | 28.4569 | 29.7186 | 31.0361 | 32.4121 | 0 | 0 | 0 | 0
2031-12-19 15:00 | 28.2079 | 0.01363% | 29.4585 | 30.7646 | 32.1285 | 33.553 | 0 | 0 | 0 | 0
2031-12-19 16:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-12-19 17:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-12-19 18:00 | 28.9962 | 0.01401% | 30.2818 | 31.6243 | 33.0264 | 34.4906 | 0 | 0 | 0 | 0
2031-12-19 19:00 | 29.7845 | 0.01439% | 31.105 | 32.4841 | 33.9243 | 35.4283 | 0 | 0 | 0 | 0
2031-12-19 20:00 | 32.399 | 0.01566% | 33.8355 | 35.3356 | 36.9022 | 38.5382 | 0 | 0 | 0 | 1.3844
2031-12-19 21:00 | 33.2924 | 0.01609% | 34.7685 | 36.3099 | 37.9198 | 39.6009 | 0 | 0 | 0.82778 | 2.3408
2031-12-19 22:00 | 32.5961 | 0.01575% | 34.0413 | 35.5505 | 37.1266 | 38.7727 | 0 | 0 | 0.11397 | 1.5954
2031-12-19 23:00 | 31.6764 | 0.01531% | 33.0808 | 34.5475 | 36.0791 | 37.6787 | 0 | 0 | 0 | 0.61084
2031-12-20 | 31.0852 | 0.01502% | 32.4634 | 33.9027 | 35.4057 | 36.9755 | 0 | 0 | 0 | 0
2031-12-20 01:00 | 30.586 | 0.01478% | 31.942 | 33.3581 | 34.8371 | 36.3816 | 0 | 0 | 0 | 0
2031-12-20 02:00 | 28.8517 | 0.01394% | 30.1308 | 31.4667 | 32.8618 | 34.3187 | 0 | 0 | 0 | 0
2031-12-20 03:00 | 26.1452 | 0.01264% | 27.3044 | 28.5149 | 29.7791 | 31.0994 | 0 | 0 | 0 | 0
2031-12-20 04:00 | 24.3584 | 0.01177% | 25.4383 | 26.5662 | 27.744 | 28.974 | 0 | 0 | 0 | 0
2031-12-20 05:00 | 22.6767 | 0.01096% | 23.6821 | 24.732 | 25.8285 | 26.9736 | 0 | 0 | 0 | 0
2031-12-20 06:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-12-20 07:00 | 21.1658 | 0.01023% | 22.1042 | 23.0842 | 24.1076 | 25.1764 | 0 | 0 | 0 | 0
2031-12-20 08:00 | 20.4957 | 0.009905% | 21.4044 | 22.3534 | 23.3444 | 24.3794 | 0 | 0 | 0 | 0
2031-12-20 09:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-12-20 10:00 | 21.8621 | 0.01057% | 22.8314 | 23.8436 | 24.9007 | 26.0047 | 0 | 0 | 0 | 0
2031-12-20 11:00 | 23.3205 | 0.01127% | 24.3544 | 25.4342 | 26.5618 | 27.7394 | 0 | 0 | 0 | 0
2031-12-20 12:00 | 25.8299 | 0.01248% | 26.9751 | 28.171 | 29.42 | 30.7243 | 0 | 0 | 0 | 0
2031-12-20 13:00 | 28.1028 | 0.01358% | 29.3488 | 30.6499 | 32.0088 | 33.4279 | 0 | 0 | 0 | 0
2031-12-20 14:00 | 29.5612 | 0.01429% | 30.8718 | 32.2405 | 33.6699 | 35.1626 | 0 | 0 | 0 | 0
2031-12-20 15:00 | 29.9816 | 0.01449% | 31.3108 | 32.699 | 34.1487 | 35.6627 | 0 | 0 | 0 | 0
2031-12-20 16:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-12-20 17:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-12-20 18:00 | 29.6794 | 0.01434% | 30.9953 | 32.3694 | 33.8045 | 35.3033 | 0 | 0 | 0 | 0
2031-12-20 19:00 | 29.8371 | 0.01442% | 31.1599 | 32.5414 | 33.9841 | 35.4908 | 0 | 0 | 0 | 0
2031-12-20 20:00 | 31.5319 | 0.01524% | 32.9299 | 34.3898 | 35.9145 | 37.5068 | 0 | 0 | 0 | 0.45612
2031-12-20 21:00 | 32.0969 | 0.01551% | 33.5199 | 35.006 | 36.558 | 38.1788 | 0 | 0 | 0 | 1.0609
2031-12-20 22:00 | 30.967 | 0.01497% | 32.3399 | 33.7737 | 35.2711 | 36.8348 | 0 | 0 | 0 | 0
2031-12-20 23:00 | 29.9947 | 0.0145% | 31.3246 | 32.7133 | 34.1637 | 35.6783 | 0 | 0 | 0 | 0
2031-12-21 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-12-21 01:00 | 28.1685 | 0.01361% | 29.4174 | 30.7216 | 32.0836 | 33.5061 | 0 | 0 | 0 | 0
2031-12-21 02:00 | 26.5131 | 0.01281% | 27.6885 | 28.9161 | 30.1981 | 31.537 | 0 | 0 | 0 | 0
2031-12-21 03:00 | 24.6869 | 0.01193% | 25.7814 | 26.9244 | 28.1181 | 29.3647 | 0 | 0 | 0 | 0
2031-12-21 04:00 | 22.5453 | 0.0109% | 23.5449 | 24.5887 | 25.6789 | 26.8174 | 0 | 0 | 0 | 0
2031-12-21 05:00 | 21.1001 | 0.0102% | 22.0356 | 23.0125 | 24.0328 | 25.0983 | 0 | 0 | 0 | 0
2031-12-21 06:00 | 20.1147 | 0.009721% | 21.0065 | 21.9379 | 22.9105 | 23.9262 | 0 | 0 | 0 | 0
2031-12-21 07:00 | 19.8782 | 0.009606% | 20.7596 | 21.6799 | 22.6411 | 23.6449 | 0 | 0 | 0 | 0
2031-12-21 08:00 | 19.9439 | 0.009638% | 20.8282 | 21.7516 | 22.7159 | 23.7231 | 0 | 0 | 0 | 0
2031-12-21 09:00 | 20.5614 | 0.009937% | 21.473 | 22.425 | 23.4193 | 24.4576 | 0 | 0 | 0 | 0
2031-12-21 10:00 | 21.5337 | 0.01041% | 22.4884 | 23.4854 | 24.5266 | 25.614 | 0 | 0 | 0 | 0
2031-12-21 11:00 | 22.6636 | 0.01095% | 23.6684 | 24.7177 | 25.8136 | 26.958 | 0 | 0 | 0 | 0
2031-12-21 12:00 | 24.411 | 0.0118% | 25.4932 | 26.6235 | 27.8038 | 29.0365 | 0 | 0 | 0 | 0
2031-12-21 13:00 | 25.9744 | 0.01255% | 27.126 | 28.3286 | 29.5846 | 30.8962 | 0 | 0 | 0 | 0
2031-12-21 14:00 | 26.4999 | 0.01281% | 27.6748 | 28.9018 | 30.1832 | 31.5213 | 0 | 0 | 0 | 0
2031-12-21 15:00 | 27.9846 | 0.01352% | 29.2253 | 30.521 | 31.8741 | 33.2873 | 0 | 0 | 0 | 0
2031-12-21 16:00 | 29.0094 | 0.01402% | 30.2955 | 31.6387 | 33.0414 | 34.5063 | 0 | 0 | 0 | 0
2031-12-21 17:00 | 29.1276 | 0.01408% | 30.419 | 31.7676 | 33.176 | 34.6469 | 0 | 0 | 0 | 0
2031-12-21 18:00 | 29.351 | 0.01418% | 30.6522 | 32.0112 | 33.4304 | 34.9126 | 0 | 0 | 0 | 0
2031-12-21 19:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-12-21 20:00 | 32.7801 | 0.01584% | 34.2334 | 35.7511 | 37.3361 | 38.9914 | 0 | 0 | 0.30253 | 1.7923
2031-12-21 21:00 | 33.6735 | 0.01627% | 35.1664 | 36.7255 | 38.3537 | 40.0541 | 0 | 0 | 1.2183 | 2.7487
2031-12-21 22:00 | 32.872 | 0.01589% | 34.3294 | 35.8514 | 37.4409 | 39.1008 | 0 | 0 | 0.3968 | 1.8908
2031-12-21 23:00 | 32.1757 | 0.01555% | 33.6022 | 35.092 | 36.6478 | 38.2726 | 0 | 0 | 0 | 1.1453
2031-12-22 | 31.2035 | 0.01508% | 32.5869 | 34.0316 | 35.5404 | 37.1161 | 0 | 0 | 0 | 0.10449
2031-12-22 01:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-12-22 02:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-12-22 03:00 | 25.4357 | 0.01229% | 26.5634 | 27.7411 | 28.971 | 30.2555 | 0 | 0 | 0 | 0
2031-12-22 04:00 | 23.2022 | 0.01121% | 24.2309 | 25.3052 | 26.4271 | 27.5988 | 0 | 0 | 0 | 0
2031-12-22 05:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-12-22 06:00 | 20.8111 | 0.01006% | 21.7337 | 22.6973 | 23.7036 | 24.7545 | 0 | 0 | 0 | 0
2031-12-22 07:00 | 20.0622 | 0.009695% | 20.9516 | 21.8805 | 22.8506 | 23.8637 | 0 | 0 | 0 | 0
2031-12-22 08:00 | 20.1936 | 0.009759% | 21.0888 | 22.0238 | 23.0003 | 24.02 | 0 | 0 | 0 | 0
2031-12-22 09:00 | 21.284 | 0.01029% | 22.2277 | 23.2131 | 24.2423 | 25.3171 | 0 | 0 | 0 | 0
2031-12-22 10:00 | 23.6227 | 0.01142% | 24.67 | 25.7637 | 26.906 | 28.0988 | 0 | 0 | 0 | 0
2031-12-22 11:00 | 25.7379 | 0.01244% | 26.879 | 28.0707 | 29.3152 | 30.6149 | 0 | 0 | 0 | 0
2031-12-22 12:00 | 27.078 | 0.01309% | 28.2785 | 29.5323 | 30.8416 | 32.209 | 0 | 0 | 0 | 0
2031-12-22 13:00 | 27.4459 | 0.01326% | 28.6627 | 29.9335 | 31.2606 | 32.6465 | 0 | 0 | 0 | 0
2031-12-22 14:00 | 28.0634 | 0.01356% | 29.3076 | 30.607 | 31.9639 | 33.3811 | 0 | 0 | 0 | 0
2031-12-22 15:00 | 28.7203 | 0.01388% | 29.9936 | 31.3234 | 32.7121 | 34.1624 | 0 | 0 | 0 | 0
2031-12-22 16:00 | 28.3656 | 0.01371% | 29.6232 | 30.9365 | 32.3081 | 33.7405 | 0 | 0 | 0 | 0
2031-12-22 17:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-12-22 18:00 | 29.0882 | 0.01406% | 30.3778 | 31.7246 | 33.1311 | 34.6 | 0 | 0 | 0 | 0
2031-12-22 19:00 | 29.4561 | 0.01424% | 30.762 | 32.1258 | 33.5502 | 35.0376 | 0 | 0 | 0 | 0
2031-12-22 20:00 | 31.6107 | 0.01528% | 33.0122 | 34.4758 | 36.0043 | 37.6006 | 0 | 0 | 0 | 0.54051
2031-12-22 21:00 | 32.7538 | 0.01583% | 34.2059 | 35.7224 | 37.3062 | 38.9602 | 0 | 0 | 0.27559 | 1.7642
2031-12-22 22:00 | 32.1757 | 0.01555% | 33.6022 | 35.092 | 36.6478 | 38.2726 | 0 | 0 | 0 | 1.1453
2031-12-22 23:00 | 30.8224 | 0.0149% | 32.189 | 33.6161 | 35.1064 | 36.6629 | 0 | 0 | 0 | 0
2031-12-23 | 30.0998 | 0.01455% | 31.4343 | 32.828 | 34.2834 | 35.8034 | 0 | 0 | 0 | 0
2031-12-23 01:00 | 28.7466 | 0.01389% | 30.0211 | 31.3521 | 32.7421 | 34.1937 | 0 | 0 | 0 | 0
2031-12-23 02:00 | 27.0518 | 0.01307% | 28.2511 | 29.5036 | 30.8117 | 32.1777 | 0 | 0 | 0 | 0
2031-12-23 03:00 | 24.608 | 0.01189% | 25.699 | 26.8384 | 28.0283 | 29.2709 | 0 | 0 | 0 | 0
2031-12-23 04:00 | 22.4665 | 0.01086% | 23.4625 | 24.5028 | 25.5891 | 26.7236 | 0 | 0 | 0 | 0
2031-12-23 05:00 | 20.5352 | 0.009924% | 21.4456 | 22.3964 | 23.3893 | 24.4263 | 0 | 0 | 0 | 0
2031-12-23 06:00 | 19.7206 | 0.00953% | 20.5949 | 21.508 | 22.4615 | 23.4574 | 0 | 0 | 0 | 0
2031-12-23 07:00 | 18.998 | 0.009181% | 19.8403 | 20.7199 | 21.6385 | 22.5978 | 0 | 0 | 0 | 0
2031-12-23 08:00 | 19.0111 | 0.009187% | 19.854 | 20.7342 | 21.6535 | 22.6135 | 0 | 0 | 0 | 0
2031-12-23 09:00 | 20.2724 | 0.009797% | 21.1712 | 22.1098 | 23.09 | 24.1137 | 0 | 0 | 0 | 0
2031-12-23 10:00 | 22.3351 | 0.01079% | 23.3253 | 24.3595 | 25.4395 | 26.5673 | 0 | 0 | 0 | 0
2031-12-23 11:00 | 24.0299 | 0.01161% | 25.0953 | 26.2079 | 27.3699 | 28.5833 | 0 | 0 | 0 | 0
2031-12-23 12:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-12-23 13:00 | 26.6707 | 0.01289% | 27.8532 | 29.0881 | 30.3777 | 31.7245 | 0 | 0 | 0 | 0
2031-12-23 14:00 | 27.8532 | 0.01346% | 29.0881 | 30.3777 | 31.7245 | 33.131 | 0 | 0 | 0 | 0
2031-12-23 15:00 | 28.9437 | 0.01399% | 30.2269 | 31.567 | 32.9665 | 34.4281 | 0 | 0 | 0 | 0
2031-12-23 16:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-12-23 17:00 | 29.3378 | 0.01418% | 30.6385 | 31.9969 | 33.4155 | 34.897 | 0 | 0 | 0 | 0
2031-12-23 18:00 | 29.2853 | 0.01415% | 30.5836 | 31.9396 | 33.3556 | 34.8344 | 0 | 0 | 0 | 0
2031-12-23 19:00 | 29.5218 | 0.01427% | 30.8306 | 32.1975 | 33.625 | 35.1157 | 0 | 0 | 0 | 0
2031-12-23 20:00 | 30.967 | 0.01497% | 32.3399 | 33.7737 | 35.2711 | 36.8348 | 0 | 0 | 0 | 0
2031-12-23 21:00 | 31.7027 | 0.01532% | 33.1083 | 34.5761 | 36.1091 | 37.71 | 0 | 0 | 0 | 0.63897
2031-12-23 22:00 | 31.164 | 0.01506% | 32.5457 | 33.9886 | 35.4955 | 37.0692 | 0 | 0 | 0 | 0.062299
2031-12-23 23:00 | 30.0079 | 0.0145% | 31.3383 | 32.7277 | 34.1787 | 35.694 | 0 | 0 | 0 | 0
2031-12-24 | 29.7451 | 0.01437% | 31.0639 | 32.4411 | 33.8794 | 35.3814 | 0 | 0 | 0 | 0
2031-12-24 01:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-12-24 02:00 | 27.0123 | 0.01305% | 28.2099 | 29.4606 | 30.7668 | 32.1308 | 0 | 0 | 0 | 0
2031-12-24 03:00 | 24.7526 | 0.01196% | 25.85 | 26.996 | 28.1929 | 29.4428 | 0 | 0 | 0 | 0
2031-12-24 04:00 | 22.5716 | 0.01091% | 23.5723 | 24.6174 | 25.7088 | 26.8486 | 0 | 0 | 0 | 0
2031-12-24 05:00 | 20.7322 | 0.01002% | 21.6514 | 22.6113 | 23.6138 | 24.6607 | 0 | 0 | 0 | 0
2031-12-24 06:00 | 19.6943 | 0.009518% | 20.5675 | 21.4793 | 22.4316 | 23.4261 | 0 | 0 | 0 | 0
2031-12-24 07:00 | 19.2607 | 0.009308% | 20.1147 | 21.0065 | 21.9378 | 22.9104 | 0 | 0 | 0 | 0
2031-12-24 08:00 | 19.0637 | 0.009213% | 19.9089 | 20.7915 | 21.7133 | 22.676 | 0 | 0 | 0 | 0
2031-12-24 09:00 | 20.2461 | 0.009784% | 21.1437 | 22.0811 | 23.0601 | 24.0825 | 0 | 0 | 0 | 0
2031-12-24 10:00 | 22.1906 | 0.01072% | 23.1744 | 24.2019 | 25.2748 | 26.3954 | 0 | 0 | 0 | 0
2031-12-24 11:00 | 23.9643 | 0.01158% | 25.0267 | 26.1363 | 27.295 | 28.5052 | 0 | 0 | 0 | 0
2031-12-24 12:00 | 25.3832 | 0.01227% | 26.5086 | 27.6838 | 28.9112 | 30.193 | 0 | 0 | 0 | 0
2031-12-24 13:00 | 26.5656 | 0.01284% | 27.7434 | 28.9734 | 30.258 | 31.5995 | 0 | 0 | 0 | 0
2031-12-24 14:00 | 27.3539 | 0.01322% | 28.5667 | 29.8332 | 31.1558 | 32.5371 | 0 | 0 | 0 | 0
2031-12-24 15:00 | 28.1291 | 0.01359% | 29.3762 | 30.6786 | 32.0387 | 33.4592 | 0 | 0 | 0 | 0
2031-12-24 16:00 | 28.2079 | 0.01363% | 29.4585 | 30.7646 | 32.1285 | 33.553 | 0 | 0 | 0 | 0
2031-12-24 17:00 | 27.8401 | 0.01345% | 29.0743 | 30.3634 | 31.7095 | 33.1154 | 0 | 0 | 0 | 0
2031-12-24 18:00 | 27.4985 | 0.01329% | 28.7176 | 29.9908 | 31.3205 | 32.7091 | 0 | 0 | 0 | 0
2031-12-24 19:00 | 27.9977 | 0.01353% | 29.239 | 30.5353 | 31.8891 | 33.3029 | 0 | 0 | 0 | 0
2031-12-24 20:00 | 30.3101 | 0.01465% | 31.6539 | 33.0572 | 34.5228 | 36.0534 | 0 | 0 | 0 | 0
2031-12-24 21:00 | 30.6385 | 0.01481% | 31.9969 | 33.4155 | 34.8969 | 36.4441 | 0 | 0 | 0 | 0
2031-12-24 22:00 | 29.6269 | 0.01432% | 30.9404 | 32.3121 | 33.7447 | 35.2408 | 0 | 0 | 0 | 0
2031-12-24 23:00 | 28.6284 | 0.01384% | 29.8976 | 31.2231 | 32.6074 | 34.053 | 0 | 0 | 0 | 0
2031-12-25 | 27.8269 | 0.01345% | 29.0606 | 30.349 | 31.6946 | 33.0998 | 0 | 0 | 0 | 0
2031-12-25 01:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-12-25 02:00 | 26.0927 | 0.01261% | 27.2495 | 28.4576 | 29.7193 | 31.0369 | 0 | 0 | 0 | 0
2031-12-25 03:00 | 24.319 | 0.01175% | 25.3972 | 26.5232 | 27.6991 | 28.9271 | 0 | 0 | 0 | 0
2031-12-25 04:00 | 22.5847 | 0.01091% | 23.586 | 24.6317 | 25.7238 | 26.8642 | 0 | 0 | 0 | 0
2031-12-25 05:00 | 20.995 | 0.01015% | 21.9258 | 22.8979 | 23.9131 | 24.9733 | 0 | 0 | 0 | 0
2031-12-25 06:00 | 19.7074 | 0.009524% | 20.5812 | 21.4937 | 22.4466 | 23.4418 | 0 | 0 | 0 | 0
2031-12-25 07:00 | 18.9323 | 0.009149% | 19.7717 | 20.6482 | 21.5637 | 22.5197 | 0 | 0 | 0 | 0
2031-12-25 08:00 | 18.6958 | 0.009035% | 19.5247 | 20.3903 | 21.2943 | 22.2384 | 0 | 0 | 0 | 0
2031-12-25 09:00 | 18.9586 | 0.009162% | 19.7991 | 20.6769 | 21.5936 | 22.551 | 0 | 0 | 0 | 0
2031-12-25 10:00 | 20.2855 | 0.009803% | 21.1849 | 22.1241 | 23.105 | 24.1294 | 0 | 0 | 0 | 0
2031-12-25 11:00 | 21.9804 | 0.01062% | 22.9549 | 23.9726 | 25.0354 | 26.1454 | 0 | 0 | 0 | 0
2031-12-25 12:00 | 24.7657 | 0.01197% | 25.8637 | 27.0104 | 28.2079 | 29.4585 | 0 | 0 | 0 | 0
2031-12-25 13:00 | 26.3948 | 0.01276% | 27.5651 | 28.7872 | 30.0634 | 31.3963 | 0 | 0 | 0 | 0
2031-12-25 14:00 | 27.4722 | 0.01328% | 28.6902 | 29.9622 | 31.2905 | 32.6778 | 0 | 0 | 0 | 0
2031-12-25 15:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-12-25 16:00 | 27.3408 | 0.01321% | 28.553 | 29.8189 | 31.1409 | 32.5215 | 0 | 0 | 0 | 0
2031-12-25 17:00 | 27.5904 | 0.01333% | 28.8137 | 30.0911 | 31.4252 | 32.8185 | 0 | 0 | 0 | 0
2031-12-25 18:00 | 27.643 | 0.01336% | 28.8685 | 30.1484 | 31.4851 | 32.881 | 0 | 0 | 0 | 0
2031-12-25 19:00 | 28.0109 | 0.01354% | 29.2527 | 30.5496 | 31.9041 | 33.3185 | 0 | 0 | 0 | 0
2031-12-25 20:00 | 30.1524 | 0.01457% | 31.4892 | 32.8853 | 34.3433 | 35.8659 | 0 | 0 | 0 | 0
2031-12-25 21:00 | 30.3363 | 0.01466% | 31.6813 | 33.0859 | 34.5528 | 36.0847 | 0 | 0 | 0 | 0
2031-12-25 22:00 | 28.5495 | 0.0138% | 29.8153 | 31.1371 | 32.5176 | 33.9593 | 0 | 0 | 0 | 0
2031-12-25 23:00 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-12-26 | 27.1569 | 0.01312% | 28.3609 | 29.6183 | 30.9314 | 32.3027 | 0 | 0 | 0 | 0
2031-12-26 01:00 | 27.2094 | 0.01315% | 28.4157 | 29.6756 | 30.9912 | 32.3652 | 0 | 0 | 0 | 0
2031-12-26 02:00 | 26.8415 | 0.01297% | 28.0316 | 29.2744 | 30.5722 | 31.9277 | 0 | 0 | 0 | 0
2031-12-26 03:00 | 25.4489 | 0.0123% | 26.5772 | 27.7555 | 28.986 | 30.2711 | 0 | 0 | 0 | 0
2031-12-26 04:00 | 24.0168 | 0.01161% | 25.0816 | 26.1936 | 27.3549 | 28.5677 | 0 | 0 | 0 | 0
2031-12-26 05:00 | 22.4534 | 0.01085% | 23.4488 | 24.4884 | 25.5741 | 26.708 | 0 | 0 | 0 | 0
2031-12-26 06:00 | 21.6782 | 0.01048% | 22.6393 | 23.643 | 24.6912 | 25.7859 | 0 | 0 | 0 | 0
2031-12-26 07:00 | 21.3235 | 0.0103% | 22.2688 | 23.2561 | 24.2872 | 25.364 | 0 | 0 | 0 | 0
2031-12-26 08:00 | 21.2972 | 0.01029% | 22.2414 | 23.2275 | 24.2573 | 25.3327 | 0 | 0 | 0 | 0
2031-12-26 09:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-12-26 10:00 | 22.9001 | 0.01107% | 23.9153 | 24.9756 | 26.0829 | 27.2393 | 0 | 0 | 0 | 0
2031-12-26 11:00 | 24.1482 | 0.01167% | 25.2188 | 26.3369 | 27.5045 | 28.724 | 0 | 0 | 0 | 0
2031-12-26 12:00 | 25.7642 | 0.01245% | 26.9065 | 28.0994 | 29.3452 | 30.6462 | 0 | 0 | 0 | 0
2031-12-26 13:00 | 27.7349 | 0.0134% | 28.9646 | 30.2487 | 31.5898 | 32.9904 | 0 | 0 | 0 | 0
2031-12-26 14:00 | 30.3495 | 0.01467% | 31.695 | 33.1002 | 34.5677 | 36.1003 | 0 | 0 | 0 | 0
2031-12-26 15:00 | 32.0443 | 0.01549% | 33.465 | 34.9487 | 36.4981 | 38.1163 | 0 | 0 | 0 | 1.0047
2031-12-26 16:00 | 32.1888 | 0.01556% | 33.6159 | 35.1063 | 36.6627 | 38.2882 | 0 | 0 | 0 | 1.1594
2031-12-26 17:00 | 31.9261 | 0.01543% | 33.3415 | 34.8197 | 36.3635 | 37.9756 | 0 | 0 | 0 | 0.87807
2031-12-26 18:00 | 31.8472 | 0.01539% | 33.2592 | 34.7337 | 36.2737 | 37.8819 | 0 | 0 | 0 | 0.79368
2031-12-26 19:00 | 31.9918 | 0.01546% | 33.4101 | 34.8914 | 36.4383 | 38.0538 | 0 | 0 | 0 | 0.9484
2031-12-26 20:00 | 33.2136 | 0.01605% | 34.6861 | 36.224 | 37.83 | 39.5072 | 0 | 0 | 0.74697 | 2.2564
2031-12-26 21:00 | 34.0676 | 0.01646% | 35.578 | 37.1554 | 38.8026 | 40.523 | 0 | 0.13982 | 1.6224 | 3.1707
2031-12-26 22:00 | 33.1873 | 0.01604% | 34.6587 | 36.1953 | 37.8 | 39.4759 | 0 | 0 | 0.72003 | 2.2283
2031-12-26 23:00 | 32.3728 | 0.01564% | 33.808 | 35.3069 | 36.8722 | 38.507 | 0 | 0 | 0 | 1.3563
2031-12-27 | 31.2691 | 0.01511% | 32.6555 | 34.1033 | 35.6152 | 37.1942 | 0 | 0 | 0 | 0.17482
2031-12-27 01:00 | 30.783 | 0.01488% | 32.1478 | 33.5731 | 35.0616 | 36.616 | 0 | 0 | 0 | 0
2031-12-27 02:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-12-27 03:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-12-27 04:00 | 25.2387 | 0.0122% | 26.3576 | 27.5262 | 28.7466 | 30.0211 | 0 | 0 | 0 | 0
2031-12-27 05:00 | 23.2942 | 0.01126% | 24.327 | 25.4055 | 26.5319 | 27.7081 | 0 | 0 | 0 | 0
2031-12-27 06:00 | 22.3745 | 0.01081% | 23.3665 | 24.4025 | 25.4843 | 26.6142 | 0 | 0 | 0 | 0
2031-12-27 07:00 | 21.5731 | 0.01043% | 22.5295 | 23.5284 | 24.5715 | 25.6609 | 0 | 0 | 0 | 0
2031-12-27 08:00 | 21.3891 | 0.01034% | 22.3374 | 23.3278 | 24.362 | 25.4421 | 0 | 0 | 0 | 0
2031-12-27 09:00 | 22.0329 | 0.01065% | 23.0098 | 24.0299 | 25.0953 | 26.2079 | 0 | 0 | 0 | 0
2031-12-27 10:00 | 22.8869 | 0.01106% | 23.9016 | 24.9613 | 26.068 | 27.2237 | 0 | 0 | 0 | 0
2031-12-27 11:00 | 23.846 | 0.01152% | 24.9032 | 26.0073 | 27.1604 | 28.3645 | 0 | 0 | 0 | 0
2031-12-27 12:00 | 26.2109 | 0.01267% | 27.373 | 28.5866 | 29.8539 | 31.1775 | 0 | 0 | 0 | 0
2031-12-27 13:00 | 27.2882 | 0.01319% | 28.4981 | 29.7615 | 31.081 | 32.459 | 0 | 0 | 0 | 0
2031-12-27 14:00 | 28.9174 | 0.01397% | 30.1995 | 31.5384 | 32.9366 | 34.3969 | 0 | 0 | 0 | 0
2031-12-27 15:00 | 29.8765 | 0.01444% | 31.2011 | 32.5844 | 34.029 | 35.5377 | 0 | 0 | 0 | 0
2031-12-27 16:00 | 30.3757 | 0.01468% | 31.7225 | 33.1289 | 34.5977 | 36.1316 | 0 | 0 | 0 | 0
2031-12-27 17:00 | 29.929 | 0.01446% | 31.256 | 32.6417 | 34.0889 | 35.6002 | 0 | 0 | 0 | 0
2031-12-27 18:00 | 29.6926 | 0.01435% | 31.009 | 32.3838 | 33.8195 | 35.3189 | 0 | 0 | 0 | 0
2031-12-27 19:00 | 29.8896 | 0.01444% | 31.2148 | 32.5987 | 34.044 | 35.5533 | 0 | 0 | 0 | 0
2031-12-27 20:00 | 31.8998 | 0.01542% | 33.3141 | 34.7911 | 36.3335 | 37.9444 | 0 | 0 | 0 | 0.84994
2031-12-27 21:00 | 32.7406 | 0.01582% | 34.1922 | 35.7081 | 37.2912 | 38.9446 | 0 | 0 | 0.26212 | 1.7501
2031-12-27 22:00 | 32.4516 | 0.01568% | 33.8903 | 35.3929 | 36.962 | 38.6007 | 0 | 0 | 0 | 1.4407
2031-12-27 23:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-12-28 | 30.7962 | 0.01488% | 32.1615 | 33.5874 | 35.0765 | 36.6316 | 0 | 0 | 0 | 0
2031-12-28 01:00 | 29.6006 | 0.0143% | 30.9129 | 32.2835 | 33.7148 | 35.2095 | 0 | 0 | 0 | 0
2031-12-28 02:00 | 27.8006 | 0.01344% | 29.0332 | 30.3204 | 31.6646 | 33.0685 | 0 | 0 | 0 | 0
2031-12-28 03:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-12-28 04:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-12-28 05:00 | 22.8606 | 0.01105% | 23.8742 | 24.9326 | 26.038 | 27.1924 | 0 | 0 | 0 | 0
2031-12-28 06:00 | 21.8359 | 0.01055% | 22.8039 | 23.815 | 24.8708 | 25.9735 | 0 | 0 | 0 | 0
2031-12-28 07:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-12-28 08:00 | 20.706 | 0.01001% | 21.624 | 22.5827 | 23.5839 | 24.6295 | 0 | 0 | 0 | 0
2031-12-28 09:00 | 21.0213 | 0.01016% | 21.9533 | 22.9266 | 23.943 | 25.0045 | 0 | 0 | 0 | 0
2031-12-28 10:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-12-28 11:00 | 22.7161 | 0.01098% | 23.7232 | 24.775 | 25.8734 | 27.0205 | 0 | 0 | 0 | 0
2031-12-28 12:00 | 24.3321 | 0.01176% | 25.4109 | 26.5375 | 27.714 | 28.9427 | 0 | 0 | 0 | 0
2031-12-28 13:00 | 26.0795 | 0.0126% | 27.2358 | 28.4433 | 29.7043 | 31.0212 | 0 | 0 | 0 | 0
2031-12-28 14:00 | 27.0649 | 0.01308% | 28.2648 | 29.5179 | 30.8266 | 32.1933 | 0 | 0 | 0 | 0
2031-12-28 15:00 | 27.6298 | 0.01335% | 28.8548 | 30.1341 | 31.4701 | 32.8653 | 0 | 0 | 0 | 0
2031-12-28 16:00 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-12-28 17:00 | 29.1539 | 0.01409% | 30.4464 | 31.7963 | 33.206 | 34.6782 | 0 | 0 | 0 | 0
2031-12-28 18:00 | 29.8634 | 0.01443% | 31.1873 | 32.57 | 34.014 | 35.5221 | 0 | 0 | 0 | 0
2031-12-28 19:00 | 30.5991 | 0.01479% | 31.9557 | 33.3725 | 34.8521 | 36.3972 | 0 | 0 | 0 | 0
2031-12-28 20:00 | 33.1348 | 0.01601% | 34.6038 | 36.138 | 37.7402 | 39.4134 | 0 | 0 | 0.66616 | 2.1721
2031-12-28 21:00 | 34.0676 | 0.01646% | 35.578 | 37.1554 | 38.8026 | 40.523 | 0 | 0.13982 | 1.6224 | 3.1707
2031-12-28 22:00 | 32.491 | 0.0157% | 33.9315 | 35.4359 | 37.0069 | 38.6476 | 0 | 0 | 0.0062307 | 1.4829
2031-12-28 23:00 | 31.3348 | 0.01514% | 32.7241 | 34.1749 | 35.6901 | 37.2724 | 0 | 0 | 0 | 0.24514
2031-12-29 | 29.8239 | 0.01441% | 31.1462 | 32.5271 | 33.9692 | 35.4752 | 0 | 0 | 0 | 0
2031-12-29 01:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-12-29 02:00 | 26.6051 | 0.01286% | 27.7846 | 29.0164 | 30.3029 | 31.6464 | 0 | 0 | 0 | 0
2031-12-29 03:00 | 24.2664 | 0.01173% | 25.3423 | 26.4658 | 27.6392 | 28.8646 | 0 | 0 | 0 | 0
2031-12-29 04:00 | 22.23 | 0.01074% | 23.2156 | 24.2448 | 25.3197 | 26.4423 | 0 | 0 | 0 | 0
2031-12-29 05:00 | 20.5483 | 0.00993% | 21.4593 | 22.4107 | 23.4043 | 24.4419 | 0 | 0 | 0 | 0
2031-12-29 06:00 | 19.8126 | 0.009575% | 20.6909 | 21.6083 | 22.5663 | 23.5668 | 0 | 0 | 0 | 0
2031-12-29 07:00 | 19.2082 | 0.009283% | 20.0598 | 20.9491 | 21.8779 | 22.8479 | 0 | 0 | 0 | 0
2031-12-29 08:00 | 18.7352 | 0.009054% | 19.5658 | 20.4333 | 21.3392 | 22.2853 | 0 | 0 | 0 | 0
2031-12-29 09:00 | 19.4184 | 0.009384% | 20.2793 | 21.1784 | 22.1174 | 23.0979 | 0 | 0 | 0 | 0
2031-12-29 10:00 | 20.8242 | 0.01006% | 21.7474 | 22.7116 | 23.7185 | 24.7701 | 0 | 0 | 0 | 0
2031-12-29 11:00 | 22.2694 | 0.01076% | 23.2567 | 24.2878 | 25.3646 | 26.4892 | 0 | 0 | 0 | 0
2031-12-29 12:00 | 23.8197 | 0.01151% | 24.8758 | 25.9787 | 27.1304 | 28.3333 | 0 | 0 | 0 | 0
2031-12-29 13:00 | 26.1058 | 0.01262% | 27.2632 | 28.4719 | 29.7342 | 31.0525 | 0 | 0 | 0 | 0
2031-12-29 14:00 | 28.1422 | 0.0136% | 29.3899 | 30.6929 | 32.0537 | 33.4748 | 0 | 0 | 0 | 0
2031-12-29 15:00 | 28.5889 | 0.01382% | 29.8564 | 31.1801 | 32.5625 | 34.0062 | 0 | 0 | 0 | 0
2031-12-29 16:00 | 29.8108 | 0.01441% | 31.1325 | 32.5127 | 33.9542 | 35.4596 | 0 | 0 | 0 | 0
2031-12-29 17:00 | 29.8502 | 0.01443% | 31.1736 | 32.5557 | 33.9991 | 35.5064 | 0 | 0 | 0 | 0
2031-12-29 18:00 | 29.4298 | 0.01422% | 30.7346 | 32.0972 | 33.5202 | 35.0063 | 0 | 0 | 0 | 0
2031-12-29 19:00 | 29.7188 | 0.01436% | 31.0364 | 32.4124 | 33.8494 | 35.3502 | 0 | 0 | 0 | 0
2031-12-29 20:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-12-29 21:00 | 34.0676 | 0.01646% | 35.578 | 37.1554 | 38.8026 | 40.523 | 0 | 0.13982 | 1.6224 | 3.1707
2031-12-29 22:00 | 33.4895 | 0.01618% | 34.9743 | 36.5249 | 38.1442 | 39.8353 | 0 | 0 | 1.0298 | 2.5518
2031-12-29 23:00 | 32.3465 | 0.01563% | 33.7806 | 35.2782 | 36.8423 | 38.4757 | 0 | 0 | 0 | 1.3282
2031-12-30 | 31.9129 | 0.01542% | 33.3278 | 34.8054 | 36.3485 | 37.96 | 0 | 0 | 0 | 0.86401
2031-12-30 01:00 | 31.1115 | 0.01504% | 32.4908 | 33.9313 | 35.4357 | 37.0067 | 0 | 0 | 0 | 0.0060391
2031-12-30 02:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-12-30 03:00 | 26.4605 | 0.01279% | 27.6337 | 28.8588 | 30.1383 | 31.4745 | 0 | 0 | 0 | 0
2031-12-30 04:00 | 24.9628 | 0.01206% | 26.0695 | 27.2253 | 28.4323 | 29.6929 | 0 | 0 | 0 | 0
2031-12-30 05:00 | 23.5438 | 0.01138% | 24.5877 | 25.6777 | 26.8162 | 28.0051 | 0 | 0 | 0 | 0
2031-12-30 06:00 | 22.519 | 0.01088% | 23.5174 | 24.5601 | 25.649 | 26.7861 | 0 | 0 | 0 | 0
2031-12-30 07:00 | 21.8753 | 0.01057% | 22.8451 | 23.858 | 24.9157 | 26.0203 | 0 | 0 | 0 | 0
2031-12-30 08:00 | 21.5205 | 0.0104% | 22.4746 | 23.4711 | 24.5117 | 25.5984 | 0 | 0 | 0 | 0
2031-12-30 09:00 | 22.1906 | 0.01072% | 23.1744 | 24.2019 | 25.2748 | 26.3954 | 0 | 0 | 0 | 0
2031-12-30 10:00 | 23.6095 | 0.01141% | 24.6563 | 25.7494 | 26.891 | 28.0832 | 0 | 0 | 0 | 0
2031-12-30 11:00 | 25.3306 | 0.01224% | 26.4537 | 27.6265 | 28.8513 | 30.1305 | 0 | 0 | 0 | 0
2031-12-30 12:00 | 26.3686 | 0.01274% | 27.5376 | 28.7585 | 30.0335 | 31.3651 | 0 | 0 | 0 | 0
2031-12-30 13:00 | 27.3014 | 0.01319% | 28.5118 | 29.7759 | 31.096 | 32.4746 | 0 | 0 | 0 | 0
2031-12-30 14:00 | 28.5232 | 0.01378% | 29.7878 | 31.1085 | 32.4877 | 33.928 | 0 | 0 | 0 | 0
2031-12-30 15:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-12-30 16:00 | 29.0619 | 0.01404% | 30.3504 | 31.696 | 33.1012 | 34.5688 | 0 | 0 | 0 | 0
2031-12-30 17:00 | 28.7335 | 0.01389% | 30.0074 | 31.3377 | 32.7271 | 34.1781 | 0 | 0 | 0 | 0
2031-12-30 18:00 | 28.9568 | 0.01399% | 30.2406 | 31.5813 | 32.9815 | 34.4437 | 0 | 0 | 0 | 0
2031-12-30 19:00 | 29.7714 | 0.01439% | 31.0913 | 32.4697 | 33.9093 | 35.4127 | 0 | 0 | 0 | 0
2031-12-30 20:00 | 32.6881 | 0.0158% | 34.1373 | 35.6508 | 37.2314 | 38.8821 | 0 | 0 | 0.20825 | 1.6938
2031-12-30 21:00 | 34.3435 | 0.0166% | 35.8661 | 37.4563 | 39.1169 | 40.8512 | 0 | 0.41064 | 1.9052 | 3.466
2031-12-30 22:00 | 34.0807 | 0.01647% | 35.5917 | 37.1697 | 38.8176 | 40.5386 | 0 | 0.15272 | 1.6359 | 3.1847
2031-12-30 23:00 | 32.4385 | 0.01568% | 33.8766 | 35.3786 | 36.9471 | 38.5851 | 0 | 0 | 0 | 1.4266
2031-12-31 | 31.9918 | 0.01546% | 33.4101 | 34.8914 | 36.4383 | 38.0538 | 0 | 0 | 0 | 0.9484
2031-12-31 01:00 | 31.0852 | 0.01502% | 32.4634 | 33.9027 | 35.4057 | 36.9755 | 0 | 0 | 0 | 0
2031-12-31 02:00 | 29.4823 | 0.01425% | 30.7894 | 32.1545 | 33.5801 | 35.0689 | 0 | 0 | 0 | 0
2031-12-31 03:00 | 27.1831 | 0.01314% | 28.3883 | 29.6469 | 30.9613 | 32.334 | 0 | 0 | 0 | 0
2031-12-31 04:00 | 24.8577 | 0.01201% | 25.9597 | 27.1107 | 28.3126 | 29.5679 | 0 | 0 | 0 | 0
2031-12-31 05:00 | 23.3336 | 0.01128% | 24.3681 | 25.4485 | 26.5767 | 27.755 | 0 | 0 | 0 | 0
2031-12-31 06:00 | 22.4139 | 0.01083% | 23.4077 | 24.4454 | 25.5292 | 26.6611 | 0 | 0 | 0 | 0
2031-12-31 07:00 | 21.9672 | 0.01062% | 22.9412 | 23.9583 | 25.0205 | 26.1297 | 0 | 0 | 0 | 0
2031-12-31 08:00 | 21.9015 | 0.01058% | 22.8726 | 23.8866 | 24.9456 | 26.0516 | 0 | 0 | 0 | 0
2031-12-31 09:00 | 21.8096 | 0.01054% | 22.7765 | 23.7863 | 24.8409 | 25.9422 | 0 | 0 | 0 | 0
2031-12-31 10:00 | 23.1365 | 0.01118% | 24.1623 | 25.2335 | 26.3523 | 27.5206 | 0 | 0 | 0 | 0
2031-12-31 11:00 | 24.4766 | 0.01183% | 25.5618 | 26.6951 | 27.8786 | 29.1147 | 0 | 0 | 0 | 0
2031-12-31 12:00 | 26.0138 | 0.01257% | 27.1672 | 28.3716 | 29.6295 | 30.9431 | 0 | 0 | 0 | 0
2031-12-31 13:00 | 27.1963 | 0.01314% | 28.402 | 29.6612 | 30.9763 | 32.3496 | 0 | 0 | 0 | 0
2031-12-31 14:00 | 28.3524 | 0.0137% | 29.6095 | 30.9222 | 32.2931 | 33.7249 | 0 | 0 | 0 | 0
2031-12-31 15:00 | 28.3262 | 0.01369% | 29.582 | 30.8935 | 32.2632 | 33.6936 | 0 | 0 | 0 | 0
2031-12-31 16:00 | 29.2196 | 0.01412% | 30.515 | 31.8679 | 33.2808 | 34.7563 | 0 | 0 | 0 | 0
2031-12-31 17:00 | 29.3115 | 0.01417% | 30.6111 | 31.9682 | 33.3855 | 34.8657 | 0 | 0 | 0 | 0
2031-12-31 18:00 | 29.4955 | 0.01425% | 30.8032 | 32.1688 | 33.595 | 35.0845 | 0 | 0 | 0 | 0
2031-12-31 19:00 | 30.5203 | 0.01475% | 31.8734 | 33.2865 | 34.7623 | 36.3035 | 0 | 0 | 0 | 0
2031-12-31 20:00 | 32.3334 | 0.01563% | 33.7669 | 35.2639 | 36.8274 | 38.4601 | 0 | 0 | 0 | 1.3141
2031-12-31 21:00 | 33.2268 | 0.01606% | 34.6999 | 36.2383 | 37.8449 | 39.5228 | 0 | 0 | 0.76044 | 2.2705
2031-12-31 22:00 | 32.9246 | 0.01591% | 34.3843 | 35.9087 | 37.5007 | 39.1634 | 0 | 0 | 0.45067 | 1.947
2031-12-31 23:00
Formulas:
Date-Time = [Date-Time, row above] + TIME(1,0,0)

## Assumptions
Power factor | 0.9
Planning Capacity (MVA) | 37
1-in-10 planning criteria:
24 | hours in a day
10 | years
87600 | hours in 10 years
0.0274% | % of hours for 1-in-10 lole
2.4 | hours per year where event could occur

## 99 LookUps (hidden)
DST Benefit Types
Distribution Capacity (Deferral or Avoidance Benefit)
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Innovation & Market
Transformation
Planning Value
DST Cost Types
DER Acquisition Cost
DER Operations, Maintenance, and Administrative (OM&A) Costs
Distribution System Ancillary Services Costs
Risks (Distribution System)
EST Benefit Types
DST Benefits
Transmission Capacity
Avoided Energy Costs
Avoided Generation Capacity Costs
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Planning Value
Innovation & Market Transformation
EST Cost Types
DST Costs
DER Acquisition Cost
DER (OM&A) Costs
Energy System Ancillary Costs
Risks (Energy System)