## 00 Cover
Benefit-Cost Analysis Data Filing Submission Template
All electricity distributors must complete both the Summary tab and the Annual Values tab to accompany their filing submission. Values in the Summary tab should be linked to the Annual Values tab or other additional tabs included by the electricity distributor using formulas.
Electricity distributors are strongly encouraged to include additional tabs providing the upstream calculations that deliver the Annual Values tab and Summary tab outputs.
Ontario Energy Board

## 01 Summary
General Information
Electricity Distributor Name | Elexicon Energy Inc.
Project or Program Name | Bell F-2 BESS Deferal program
Description of NWS(s) (<150 words) | Elexicon proposes to administer three 2.2 MW (4-hour) distribution battery to defer the replacement of the BELL-F2 feeder by 1 years to 2032
Year for Net Present Value | 2026
Constant Dollar Year (i.e., nominal values deflated to this year) | 2026
Distribution Service Test
DST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV (Millions 2026 $)
Distribution Capacity Benefit | Distribution Capacity (Deferral or Avoidance Benefit) | 0.02006
Total DST Benefit |  | 0.02006
DST Costs
(Add more rows as required)
Cost | Cost Type | NPV (Millions 2026 $)
Capital Cost (Nominal $) | BESS Acquisition Cost | 8.7726
Fixed O&M (Nominal $) | BESS Operations, Maintenance, and Administrative (OM&A) Costs | 3.2779
Total DST Cost |  | 12.0505
NPV Net DST Benefit | -12.0305
Energy System Test (NOT APPLICABLE)
EST Benefits
(Add more rows as required)
Benefit | Benefit Type | NPV
Benefit 1 [replace name]
Benefit 2 [replace name]
Benefit 3 [replace name]
Benefit 4 [replace name]
Benefit 5 [replace name]
Benefit 6 [replace name]
Total EST Benefit
EST Costs
(Add more rows as required)
Cost | Cost Type | NPV
Cost 1 [replace name]
Cost 2 [replace name]
Cost 3 [replace name]
Cost 4 [replace name]
Cost 5 [replace name]
Cost 6 [replace name]
Total EST Cost
NPV Net EST Benefit

## 02 Annual Values
Use only such rows as are required. Insert additional columns as required.
| Distribution Service Benefits | Distribution Service Costs
Calendar Year | Distribution Capacity Benefit | Capital Cost (Nominal $) | Fixed O&M (Nominal $)
2026 | 0 | 0 | 0
2027 | 0 | 0 | 0
2028 | 0 | 0 | 0
2029 | 0 | 0 | 0
2030 | 0 | 0 | 0
2031 | 0.034614 | 1.083 | 0.40468
2032 | -0.00056672 | 1.0618 | 0.39674
2033 | -0.00055561 | 1.041 | 0.38896
2034 | -0.00054472 | 1.0206 | 0.38133
2035 | -0.00053404 | 1.0006 | 0.37386
2036 | -0.00052357 | 0.98094 | 0.36653
2037 | -0.0005133 | 0.96171 | 0.35934
2038 | -0.00050324 | 0.94285 | 0.35229
2039 | -0.00049337 | 0.92436 | 0.34539
2040 | -0.00048369 | 0.90624 | 0.33861
2041 | -0.00047421 | 0.88847 | 0.33198
2042 | -0.00046491 | 0.87105 | 0.32547
2043 | -0.0004558 | 0.85397 | 0.31908
2044 | -0.00044686 | 0.83723 | 0.31283
2045 | -0.0004381 | 0.82081 | 0.30669
2046 | -0.00042951 | 0 | 0
2047 | -0.00042108 | 0 | 0
2048 | -0.00041283 | 0 | 0
2049 | -0.00040473 | 0 | 0
2050 | -0.0003968 | 0 | 0
2051 | -0.00038902 | 0 | 0
2052 | -0.00038139 | 0 | 0
2053 | -0.00037391 | 0 | 0
2054 | -0.00036658 | 0 | 0
2055 | -0.00035939 | 0 | 0
2056 | -0.00035235 | 0 | 0
2057 | -0.00034544 | 0 | 0
2058 | -0.00033866 | 0 | 0
2059 | -0.00033202 | 0 | 0
2060 | -0.00032551 | 0 | 0
2061 | -0.00031913 | 0 | 0
2062 | -0.00031287 | 0 | 0
2063 | -0.00030674 | 0 | 0
2064 | -0.00030072 | 0 | 0
2065 | -0.00029483 | 0 | 0
2066 | -0.00028905 | 0 | 0
2067 | -0.00028338 | 0 | 0
2068 | -0.00027782 | 0 | 0
2069 | -0.00027237 | 0 | 0
2070 | -0.00026703 | 0 | 0
2071 | -0.0002618 | 0 | 0
2072 | -0.00025666 | 0 | 0
2073 | -0.00025163 | 0 | 0
2074 | -0.0002467 | 0 | 0
2075 | -0.00024186 | 0 | 0
NPV | 0.020402 | 8.7726 | 3.2779

## Inputs and Assumptions
Assumptions
Calculated Value
Economic Assumption | Value | Source |  | Manual Input
Debt % | 60% | Assumed
Equity % | 40%
Allowed Return on Equity (ROE) | 9.21% | Ontario Energy Board, 2024 Cost of Capital Parameters, October 2023
Deemed Long-Term Debt Rate | 4.88%
Federal Tax Rate | 15% | Government of Canada, Corporation Tax Rates, May 2022
Provincial Tax Rate | 11.5% | Government of Canada, Ontario – Provincial corporation tax, August 2023
Pre-tax Weighted Average Cost of Capital (WACC) | 7.94% | Calculated
O&M (percentage of capital expenditure) | 1.5% | Assumed
Inflation Rate | 2% | IESO Guide for NWAs
Social Discount Rate | 4%
Capital Recovery Factor | 11.11% | Calculated
LDC Calculations Inputs - Traditional Asset (Poles and Wires)
Inputs | Value | Source
Asset Life (years) | 60 | Assumed
Asset Cost (Millions $ - Nominal) | 0.34398 | From DSP Budget
Asset Depreciation | Straight-line 2% per year for 60 years | Assumed
Depreciation | 1.67% | Assumed
LDC Calculations Inputs - Non Wire Solution Costs and Benefits (Millions $)
Inputs | Value | Source
Battery Storage Cost (2026 $) | 19.4984 | Per LDC Calculations
Distribution Capacity Benefit (2026 $) | 0.02006 | Per LDC Calculations
Cost 1 Capital Cost Nominal ($) | 17.9365 | From previous experience (Support to be provided by LDC)
Cost 2 Fixed O&M (Nominal $) | 6.7019 | From previous experience (Support to be provided by LDC)
LDC Calculations Inputs - Traditional Solution Expenditure Timelines (Millions $)
Year | Cost ($M) | Source
2030 | 0.34398 | Elexicon DSP
2031 | 0 | Elexicon DSP
2032 |  | Elexicon DSP
Total | 0.34398 | Elexicon DSP
LDC Calculations Inputs - Non-Wire Solution Parameters
Inputs | Value | Source
Battery Specs
Number of Units | 3 | Calculated
Battery Unit Size (MW) | 2.2 | Per unit; Based on projected load growth; accounts for 10% efficiency loss
Hours | 4 | Based on number of consecutive hours in violation in 2031
Battery Discharge (MWh) | 8.8 | Calculated
Average Useful Life | 15 | Informed by Industry Research and EnergyAnalytics, 2025
Capital Cost ($/MW) - 2026 (4-hr battery) | 2717644.7873 | Calculated, including price reductions from 2024-2026 in NREL ATB
Fixed O&M ($/MW-year) - 2026 (4-hr battery) | 67696.1664 | Calculated, including price reductions from 2024-2026 in NREL ATB
Deferral Period (years) | 1 | Assumed
4-hour to 8-hour cost ratio
Capital Cost ($/kW)-2024 (4-hr battery) | 3051 | IESO, 2024
Fixed O&M ($/kW-year)-2024 (4-hr battery) | 76 | IESO, 2024
Capital Cost ($/kW) | 1.7424 | Calculated Using NREL ATB Baseline Capex ratio between 8-hr and 4-hr storage systems in 2026
Fixed O&M ($/kW-year) | 1.7919 | Calculated Using NREL ATB Baseline Fixed O&M ratio between 8-hr and 4-hr storage systems in 2026
Capital Cost ($/kW)-2024 (8-hr battery) | 5316.1403 | Calculated
Fixed O&M ($/kW-year)-2024 (8-hr battery) | 136.1837 | Calculated
2024-2026 Price Reduction | 14.38% | Calculated Using NREL ATB Baseline cost reduction in 4-hour battery storage in 2026 vs 2024 |  |  | Capital Cost ($/MW) - 2026 (4-hr battery)
Capital Cost ($/MW) - 2026 (4-hr battery) | 2717644.7873 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (4-hr battery) | 67696.1664 | Calculated Using IESO, 2024
Capital Cost ($/MW) - 2026 (8-hr battery) | 4735293.6262 | Calculated Using IESO, 2024
Fixed O&M ($/MW-year) - 2026 (8-hr battery) | 121304.1519 | Calculated Using IESO, 2024
Actual Asset Costs - Millions $ (Nominal)
Year | Inflation Index | Traditional Poles and Wires | Deferral via NWS
2026 | 100%
2027 | 102%
2028 | 104%
2029 | 106.1%
2030 | 108.2% | 0.34398
2031 | 110.4% | 0 | 0.34398
2032 | 112.6% | 0 | 0
2033 | 114.9% |  | 0
2034 | 117.2% |  | 0
2035 | 119.5% |  | 0
2036 | 121.9% |  | 0
2037 | 124.3% |  | 0
2038 | 126.8% |  | 0
2039 | 129.4% |  | 0
2040 | 131.9% |  | 0
2041 | 134.6% |  | 0
2042 | 137.3% |  | 0
2043 | 140% |  | 0
2044 | 142.8%
2045 | 145.7%
2046 | 148.6%
2047 | 151.6%
2048 | 154.6%
2049 | 157.7%
2050 | 160.8%
2051 | 164.1%
2052 | 167.3%
2053 | 170.7%
2054 | 174.1%
2055 | 177.6%
2056 | 181.1%
2057 | 184.8%
2058 | 188.5%
2059 | 192.2%
2060 | 196.1%
2061 | 200%
2062 | 204%
2063 | 208.1%
2064 | 212.2%
2065 | 216.5%
2066 | 220.8%
2067 | 225.2%
2068 | 229.7%
2069 | 234.3%
2070 | 239%
2071 | 243.8%
2072 | 248.7%
2073 | 253.6%
2074 | 258.7%
2075 | 263.9%
2076 | 269.2%
2077 | 274.5%
2078 | 280%
2079 | 285.6%
2080 | 291.3%
2081 | 297.2%
2082 | 303.1%
2083 | 309.2%
2084 | 315.4%
2085 | 321.7%
2086 | 328.1%
2087 | 334.7%
2088 | 341.4%
2089 | 348.2%
2090 | 355.1%
2091 | 362.3%
2092 | 369.5%
2093 | 376.9%
2094 | 384.4%
2095 | 392.1%
2096 | 400%
2097 | 408%
2098 | 416.1%
2099 | 424.4%
2100 | 432.9%
2101 | 441.6%
2102 | 450.4%
2103 | 459.4%
2104 | 468.6%
2105 | 478%
2106 | 487.5%
2107 | 497.3%
2108 | 507.2%

## Elexicon Calculations
Battery Storage |  |  |  |  | Alternative (Expansion) | [9 empty] | NPV Summary
|  |  | NPV | 12.0505 |  |  |  | NPV | 0.35002 |  |  |  | NPV | 0.32996
|  |  |  | Cost - Millions (2026 $) |  | Installed at Time of Need |  |  |  |  | Deferred Installation |  |  |  |  | Cost of NWA | 12.0505 | BESS Cost | -12.0505
[8 empty] | Nominal | 2026 $ |  |  |  | Nominal | 2026 $ |  | Total Benefit of NWA | 0.02006 | Deferral Benefit | 0.02006
| Calendar Year | Cost 1 Capital Cost Nominal ($) | Cost 2 Fixed O&M (Nominal $) | Battery Storage Cost | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements | Calendar Year | Opening Net Book Value | Dep'n | CRF / Revenue Requirements | CRF / Revenue Requirements |  | Net Benefit | -12.0305 | Net Benefit | -12.0305
| 2026 |  |  | 0 | 2026 | 0 |  | 0 | 0 | 2026 | 0 | 0 | 0 | 0
| 2027 |  |  | 0 | 2027 | 0 |  | 0 | 0 | 2027 | 0 | 0 | 0 | 0
| 2028 |  |  | 0 | 2028 | 0 |  | 0 | 0 | 2028 | 0 | 0 | 0 | 0
| 2029 |  |  | 0 | 2029 | 0 |  | 0 | 0 | 2029 | 0 | 0 | 0 | 0
| 2030 |  |  | 0 | 2030 | 0 |  | 0 | 0 | 2030 | 0 | 0 | 0 | 0
| 2031 | 1.083 | 0.40468 | 1.4877 | 2031 | 0.34398 | -0.0057445 | 0.038217 | 0.034614 | 2031 | 0 | 0 | 0 | 0
| 2032 | 1.0618 | 0.39674 | 1.4585 | 2032 | 0.33824 | -0.0057445 | 0.037579 | 0.033369 | 2032 | 0.34398 | -0.0057445 | 0.038217 | 0.033936
| 2033 | 1.041 | 0.38896 | 1.4299 | 2033 | 0.33249 | -0.0057445 | 0.036941 | 0.032159 | 2033 | 0.33824 | -0.0057445 | 0.037579 | 0.032715
| 2034 | 1.0206 | 0.38133 | 1.4019 | 2034 | 0.32675 | -0.0057445 | 0.036302 | 0.030984 | 2034 | 0.33249 | -0.0057445 | 0.036941 | 0.031528
| 2035 | 1.0006 | 0.37386 | 1.3744 | 2035 | 0.321 | -0.0057445 | 0.035664 | 0.029842 | 2035 | 0.32675 | -0.0057445 | 0.036302 | 0.030376
| 2036 | 0.98094 | 0.36653 | 1.3475 | 2036 | 0.31526 | -0.0057445 | 0.035026 | 0.028733 | 2036 | 0.321 | -0.0057445 | 0.035664 | 0.029257
| 2037 | 0.96171 | 0.35934 | 1.321 | 2037 | 0.30951 | -0.0057445 | 0.034388 | 0.027657 | 2037 | 0.31526 | -0.0057445 | 0.035026 | 0.02817
| 2038 | 0.94285 | 0.35229 | 1.2951 | 2038 | 0.30377 | -0.0057445 | 0.033749 | 0.026611 | 2038 | 0.30951 | -0.0057445 | 0.034388 | 0.027114
| 2039 | 0.92436 | 0.34539 | 1.2698 | 2039 | 0.29802 | -0.0057445 | 0.033111 | 0.025596 | 2039 | 0.30377 | -0.0057445 | 0.033749 | 0.026089
| 2040 | 0.90624 | 0.33861 | 1.2449 | 2040 | 0.29228 | -0.0057445 | 0.032473 | 0.02461 | 2040 | 0.29802 | -0.0057445 | 0.033111 | 0.025094
| 2041 | 0.88847 | 0.33198 | 1.2204 | 2041 | 0.28654 | -0.0057445 | 0.031835 | 0.023654 | 2041 | 0.29228 | -0.0057445 | 0.032473 | 0.024128
| 2042 | 0.87105 | 0.32547 | 1.1965 | 2042 | 0.28079 | -0.0057445 | 0.031197 | 0.022725 | 2042 | 0.28654 | -0.0057445 | 0.031835 | 0.02319
| 2043 | 0.85397 | 0.31908 | 1.1731 | 2043 | 0.27505 | -0.0057445 | 0.030558 | 0.021824 | 2043 | 0.28079 | -0.0057445 | 0.031197 | 0.022279
| 2044 | 0.83723 | 0.31283 | 1.1501 | 2044 | 0.2693 | -0.0057445 | 0.02992 | 0.020949 | 2044 | 0.27505 | -0.0057445 | 0.030558 | 0.021396
| 2045 | 0.82081 | 0.30669 | 1.1275 | 2045 | 0.26356 | -0.0057445 | 0.029282 | 0.0201 | 2045 | 0.2693 | -0.0057445 | 0.02992 | 0.020538
| 2046 |  |  |  | 2046 | 0.25781 | -0.0057445 | 0.028644 | 0.019276 | 2046 | 0.26356 | -0.0057445 | 0.029282 | 0.019706
| 2047 |  |  |  | 2047 | 0.25207 | -0.0057445 | 0.028005 | 0.018477 | 2047 | 0.25781 | -0.0057445 | 0.028644 | 0.018898
| 2048 |  |  |  | 2048 | 0.24632 | -0.0057445 | 0.027367 | 0.017702 | 2048 | 0.25207 | -0.0057445 | 0.028005 | 0.018115
| 2049 |  |  |  | 2049 | 0.24058 | -0.0057445 | 0.026729 | 0.01695 | 2049 | 0.24632 | -0.0057445 | 0.027367 | 0.017355
| 2050 |  |  |  | 2050 | 0.23484 | -0.0057445 | 0.026091 | 0.016221 | 2050 | 0.24058 | -0.0057445 | 0.026729 | 0.016618
| 2051 |  |  |  | 2051 | 0.22909 | -0.0057445 | 0.025453 | 0.015514 | 2051 | 0.23484 | -0.0057445 | 0.026091 | 0.015903
| 2052 |  |  |  | 2052 | 0.22335 | -0.0057445 | 0.024814 | 0.014829 | 2052 | 0.22909 | -0.0057445 | 0.025453 | 0.01521
| 2053 |  |  |  | 2053 | 0.2176 | -0.0057445 | 0.024176 | 0.014164 | 2053 | 0.22335 | -0.0057445 | 0.024814 | 0.014538
| 2054 |  |  |  | 2054 | 0.21186 | -0.0057445 | 0.023538 | 0.01352 | 2054 | 0.2176 | -0.0057445 | 0.024176 | 0.013886
| 2055 |  |  |  | 2055 | 0.20611 | -0.0057445 | 0.0229 | 0.012895 | 2055 | 0.21186 | -0.0057445 | 0.023538 | 0.013254
| 2056 |  |  |  | 2056 | 0.20037 | -0.0057445 | 0.022261 | 0.01229 | 2056 | 0.20611 | -0.0057445 | 0.0229 | 0.012642
| 2057 |  |  |  | 2057 | 0.19462 | -0.0057445 | 0.021623 | 0.011703 | 2057 | 0.20037 | -0.0057445 | 0.022261 | 0.012049
| 2058 |  |  |  | 2058 | 0.18888 | -0.0057445 | 0.020985 | 0.011135 | 2058 | 0.19462 | -0.0057445 | 0.021623 | 0.011474
| 2059 |  |  |  | 2059 | 0.18313 | -0.0057445 | 0.020347 | 0.010585 | 2059 | 0.18888 | -0.0057445 | 0.020985 | 0.010917
| 2060 |  |  |  | 2060 | 0.17739 | -0.0057445 | 0.019709 | 0.010052 | 2060 | 0.18313 | -0.0057445 | 0.020347 | 0.010377
| 2061 |  |  |  | 2061 | 0.17165 | -0.0057445 | 0.01907 | 0.0095357 | 2061 | 0.17739 | -0.0057445 | 0.019709 | 0.0098548
| 2062 |  |  |  | 2062 | 0.1659 | -0.0057445 | 0.018432 | 0.0090358 | 2062 | 0.17165 | -0.0057445 | 0.01907 | 0.0093487
| 2063 |  |  |  | 2063 | 0.16016 | -0.0057445 | 0.017794 | 0.0085519 | 2063 | 0.1659 | -0.0057445 | 0.018432 | 0.0088587
| 2064 |  |  |  | 2064 | 0.15441 | -0.0057445 | 0.017156 | 0.0080835 | 2064 | 0.16016 | -0.0057445 | 0.017794 | 0.0083842
| 2065 |  |  |  | 2065 | 0.14867 | -0.0057445 | 0.016517 | 0.0076302 | 2065 | 0.15441 | -0.0057445 | 0.017156 | 0.007925
| 2066 |  |  |  | 2066 | 0.14292 | -0.0057445 | 0.015879 | 0.0071915 | 2066 | 0.14867 | -0.0057445 | 0.016517 | 0.0074806
| 2067 |  |  |  | 2067 | 0.13718 | -0.0057445 | 0.015241 | 0.0067671 | 2067 | 0.14292 | -0.0057445 | 0.015879 | 0.0070505
| 2068 |  |  |  | 2068 | 0.13143 | -0.0057445 | 0.014603 | 0.0063566 | 2068 | 0.13718 | -0.0057445 | 0.015241 | 0.0066344
| 2069 |  |  |  | 2069 | 0.12569 | -0.0057445 | 0.013964 | 0.0059596 | 2069 | 0.13143 | -0.0057445 | 0.014603 | 0.006232
| 2070 |  |  |  | 2070 | 0.11995 | -0.0057445 | 0.013326 | 0.0055757 | 2070 | 0.12569 | -0.0057445 | 0.013964 | 0.0058428
| 2071 |  |  |  | 2071 | 0.1142 | -0.0057445 | 0.012688 | 0.0052046 | 2071 | 0.11995 | -0.0057445 | 0.013326 | 0.0054664
| 2072 |  |  |  | 2072 | 0.10846 | -0.0057445 | 0.01205 | 0.0048459 | 2072 | 0.1142 | -0.0057445 | 0.012688 | 0.0051025
| 2073 |  |  |  | 2073 | 0.10271 | -0.0057445 | 0.011412 | 0.0044992 | 2073 | 0.10846 | -0.0057445 | 0.01205 | 0.0047509
| 2074 |  |  |  | 2074 | 0.096968 | -0.0057445 | 0.010773 | 0.0041643 | 2074 | 0.10271 | -0.0057445 | 0.011412 | 0.004411
| 2075 |  |  |  | 2075 | 0.091223 | -0.0057445 | 0.010135 | 0.0038408 | 2075 | 0.096968 | -0.0057445 | 0.010773 | 0.0040827
| 2076 |  |  |  | 2076 | 0.085479 | -0.0057445 | 0.0094969 | 0.0035284 | 2076 | 0.091223 | -0.0057445 | 0.010135 | 0.0037655
[5 empty] | 2077 | 0.079735 | -0.0057445 | 0.0088587 | 0.0032267 | 2077 | 0.085479 | -0.0057445 | 0.0094969 | 0.0034592
[5 empty] | 2078 | 0.07399 | -0.0057445 | 0.0082205 | 0.0029355 | 2078 | 0.079735 | -0.0057445 | 0.0088587 | 0.0031635
[5 empty] | 2079 | 0.068246 | -0.0057445 | 0.0075823 | 0.0026545 | 2079 | 0.07399 | -0.0057445 | 0.0082205 | 0.002878
[5 empty] | 2080 | 0.062501 | -0.0057445 | 0.006944 | 0.0023834 | 2080 | 0.068246 | -0.0057445 | 0.0075823 | 0.0026025
[5 empty] | 2081 | 0.056757 | -0.0057445 | 0.0063058 | 0.0021219 | 2081 | 0.062501 | -0.0057445 | 0.006944 | 0.0023367
[5 empty] | 2082 | 0.051012 | -0.0057445 | 0.0056676 | 0.0018698 | 2082 | 0.056757 | -0.0057445 | 0.0063058 | 0.0020803
[5 empty] | 2083 | 0.045268 | -0.0057445 | 0.0050294 | 0.0016267 | 2083 | 0.051012 | -0.0057445 | 0.0056676 | 0.0018331
[5 empty] | 2084 | 0.039523 | -0.0057445 | 0.0043911 | 0.0013924 | 2084 | 0.045268 | -0.0057445 | 0.0050294 | 0.0015948
[5 empty] | 2085 | 0.033779 | -0.0057445 | 0.0037529 | 0.0011667 | 2085 | 0.039523 | -0.0057445 | 0.0043911 | 0.0013651
[5 empty] | 2086 | 0.028034 | -0.0057445 | 0.0031147 | 0.0009493 | 2086 | 0.033779 | -0.0057445 | 0.0037529 | 0.0011438
[5 empty] | 2087 | 0.02229 | -0.0057445 | 0.0024765 | 0.00073998 | 2087 | 0.028034 | -0.0057445 | 0.0031147 | 0.00093069
[5 empty] | 2088 | 0.016545 | -0.0057445 | 0.0018382 | 0.00053851 | 2088 | 0.02229 | -0.0057445 | 0.0024765 | 0.00072547
[5 empty] | 2089 | 0.010801 | -0.0057445 | 0.0012 | 0.00034465 | 2089 | 0.016545 | -0.0057445 | 0.0018382 | 0.00052795
[5 empty] | 2090 | 0.0050565 | -0.0057445 | 0.00056179 | 0.00015818 | 2090 | 0.010801 | -0.0057445 | 0.0012 | 0.00033789
[5 empty] | 2091 | -0.00068796 | -0.0057445 | -7.6434e-05 | -2.11e-05 | 2091 | 0.0050565 | -0.0057445 | 0.00056179 | 0.00015508
[10 empty] | 2092 | 0 | -0.0057445 | 0 | 0
[10 empty] | 2093 | 0 | -0.0057445 | 0 | 0

## BESS Inputs
Min MW BESS (total)
Deferral length | Year | Bell-F2
1 | 2032 | 6
2 | 2033 | 6.5
3 | 2034 | 7
4 | 2035 | 7.5
Battery Specs
Spec | Unit | Value
Duration | Hours | 4
Number of units | # | 3
CapEx for Deferred traditional solution - years of spend
Deferral length | Year1 | Year2
1 | 2031 | 2032
2 | 2032 | 2033
3 | 2033 | 2034
4 | 2034 | 2035
Traditional Solution Cost
Total Before 30% Contingency | 264600 | 0.2646
Total After 30% Contingency | 343980 | 0.34398
Traditional solution spend year
% spend per year
2030 | 1 | 0.34398
2031 | 0 | 0

## Input Calculation >>
The following tabs show how the battery solution was sized

## BELL-F2 hourly
[5 empty] | Hourly Load | [9 empty] | 2031 consectuive hours exceeding planning capacity
Total load |  |  | 28798.8183 |  | 42937.9603 | 44525.7367 | 46172.2265 | 47879.6009 | 49650.1112 | Exceeding Planning Capacity (MW)
Date-Time | Date | Hour | 2020 Load | Load Shape | 2031 | 2032 | 2033 | 2034 | 2035 | 2031 | 2032 | 2033 | 2034 | 2035 | 2031 consectuive hours | Total consecutive length
2020-01-01 | 2020-01-01 | 0 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0 |  |  | Duration Determination
2020-01-01 01:00 | 2020-01-01 | 1 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2031 |  | # of consecutive hours
2020-01-01 02:00 | 2020-01-01 | 2 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0 |  |  | # of hours exceeding | 1981 |  | avg | 11.0056
2020-01-01 03:00 | 2020-01-01 | 3 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0 |  |  | % of hours | 22.61% |  | max | 66
2020-01-01 04:00 | 2020-01-01 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0 | [5 empty] | median | 12
2020-01-01 05:00 | 2020-01-01 | 5 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-01-01 06:00 | 2020-01-01 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0 |  |  | Capacity Determination
2020-01-01 07:00 | 2020-01-01 | 7 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0 |  |  |  | MW Exceeding planning capacity
2020-01-01 08:00 | 2020-01-01 | 8 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2031 | 2032 | 2033 | 2034 | 2035
2020-01-01 09:00 | 2020-01-01 | 9 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0 |  |  | avg | 2.2193 | 2.1808 | 2.1063 | 2.0579 | 2.0231
2020-01-01 10:00 | 2020-01-01 | 10 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0 |  |  | max | 5.7919 | 6.2182 | 6.6603 | 7.1187 | 7.5941
2020-01-01 11:00 | 2020-01-01 | 11 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0 |  |  | median | 0.99848 | 1.0904 | 1.1316 | 1.1352 | 1.1298
2020-01-01 12:00 | 2020-01-01 | 12 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-01-01 13:00 | 2020-01-01 | 13 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0 |  |  | MW BESS Size | 2031 | 2032 | 2033 | 2034 | 2035
2020-01-01 14:00 | 2020-01-01 | 14 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0 |  |  | 0.5 | 1456 | 1681 | 1903 | 2157 | 2522
2020-01-01 15:00 | 2020-01-01 | 15 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 985 | 1204 | 1424 | 1636 | 1867
2020-01-01 16:00 | 2020-01-01 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0 |  |  | 1.5 | 614 | 797 | 999 | 1204 | 1433
2020-01-01 17:00 | 2020-01-01 | 17 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 301 | 472 | 636 | 812 | 1028
2020-01-01 18:00 | 2020-01-01 | 18 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0 |  |  | 2.5 | 159 | 242 | 343 | 509 | 680
2020-01-01 19:00 | 2020-01-01 | 19 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0 |  |  | 3 | 102 | 138 | 184 | 275 | 404
2020-01-01 20:00 | 2020-01-01 | 20 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0 |  |  | 3.5 | 66 | 87 | 116 | 151 | 223
2020-01-01 21:00 | 2020-01-01 | 21 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 48 | 62 | 77 | 103 | 138
2020-01-01 22:00 | 2020-01-01 | 22 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0 |  |  | 4.5 | 29 | 44 | 60 | 70 | 91
2020-01-01 23:00 | 2020-01-01 | 23 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0 |  |  | 5 | 12 | 23 | 37 | 53 | 65
2020-01-02 | 2020-01-01 | 0 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0 |  |  | 5.5 | 2 | 11 | 20 | 36 | 50
2020-01-02 01:00 | 2020-01-02 | 1 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0 |  |  | 6 | 0 | 2 | 6 | 18 | 34
2020-01-02 02:00 | 2020-01-02 | 2 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0 |  |  | 6.5 | 0 | 0 | 1 | 4 | 16
2020-01-02 03:00 | 2020-01-02 | 3 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0 |  |  | 7 | 0 | 0 | 0 | 1 | 3
2020-01-02 04:00 | 2020-01-02 | 4 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0 |  |  | 7.5 | 0 | 0 | 0 | 0 | 1
2020-01-02 05:00 | 2020-01-02 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0 |  |  | 8 | 0 | 0 | 0 | 0 | 0
2020-01-02 06:00 | 2020-01-02 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0 |  |  | 8.5 | 0 | 0 | 0 | 0 | 0
2020-01-02 07:00 | 2020-01-02 | 7 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0 |  |  | 9 | 0 | 0 | 0 | 0 | 0
2020-01-02 08:00 | 2020-01-02 | 8 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0 |  |  | 9.5 | 0 | 0 | 0 | 0 | 0
2020-01-02 09:00 | 2020-01-02 | 9 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0 |  |  | 10 | 0 | 0 | 0 | 0 | 0
2020-01-02 10:00 | 2020-01-02 | 10 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0 |  |  | 10.5 | 0 | 0 | 0 | 0 | 0
2020-01-02 11:00 | 2020-01-02 | 11 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0 |  |  | 11 | 0 | 0 | 0 | 0 | 0
2020-01-02 12:00 | 2020-01-02 | 12 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0 |  |  | 11.5 | 0 | 0 | 0 | 0 | 0
2020-01-02 13:00 | 2020-01-02 | 13 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0 |  |  | BESS MW needed | 5.5 | 6 | 6.5 | 7 | 7.5
2020-01-02 14:00 | 2020-01-02 | 14 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-01-02 15:00 | 2020-01-02 | 15 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0 |  |  | Year | Total BESS MW | Per-Unit MW
2020-01-02 16:00 | 2020-01-02 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0 |  |  | 2031 | 5.5 | 1.8333
2020-01-02 17:00 | 2020-01-02 | 17 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0 |  |  | 2032 | 6 | 2
2020-01-02 18:00 | 2020-01-02 | 18 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0 |  |  | 2033 | 6.5 | 2.1667
2020-01-02 19:00 | 2020-01-02 | 19 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0 |  |  | 2034 | 7 | 2.3333
2020-01-02 20:00 | 2020-01-02 | 20 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0 |  |  | 2035 | 7.5 | 2.5
2020-01-02 21:00 | 2020-01-02 | 21 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-01-02 22:00 | 2020-01-02 | 22 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-01-02 23:00 | 2020-01-02 | 23 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-03 | 2020-01-02 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-01-03 01:00 | 2020-01-03 | 1 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-01-03 02:00 | 2020-01-03 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-01-03 03:00 | 2020-01-03 | 3 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-01-03 04:00 | 2020-01-03 | 4 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-01-03 05:00 | 2020-01-03 | 5 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-01-03 06:00 | 2020-01-03 | 6 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-01-03 07:00 | 2020-01-03 | 7 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-01-03 08:00 | 2020-01-03 | 8 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-01-03 09:00 | 2020-01-03 | 9 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-03 10:00 | 2020-01-03 | 10 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-03 11:00 | 2020-01-03 | 11 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-01-03 12:00 | 2020-01-03 | 12 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-01-03 13:00 | 2020-01-03 | 13 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-01-03 14:00 | 2020-01-03 | 14 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-01-03 15:00 | 2020-01-03 | 15 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-01-03 16:00 | 2020-01-03 | 16 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-01-03 17:00 | 2020-01-03 | 17 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-01-03 18:00 | 2020-01-03 | 18 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-01-03 19:00 | 2020-01-03 | 19 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-01-03 20:00 | 2020-01-03 | 20 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-01-03 21:00 | 2020-01-03 | 21 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-01-03 22:00 | 2020-01-03 | 22 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-01-03 23:00 | 2020-01-03 | 23 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-01-04 | 2020-01-03 | 0 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-01-04 01:00 | 2020-01-04 | 1 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-01-04 02:00 | 2020-01-04 | 2 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-01-04 03:00 | 2020-01-04 | 3 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-01-04 04:00 | 2020-01-04 | 4 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-01-04 05:00 | 2020-01-04 | 5 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-01-04 06:00 | 2020-01-04 | 6 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-01-04 07:00 | 2020-01-04 | 7 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-01-04 08:00 | 2020-01-04 | 8 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-01-04 09:00 | 2020-01-04 | 9 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-01-04 10:00 | 2020-01-04 | 10 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-01-04 11:00 | 2020-01-04 | 11 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-01-04 12:00 | 2020-01-04 | 12 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-01-04 13:00 | 2020-01-04 | 13 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-01-04 14:00 | 2020-01-04 | 14 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-01-04 15:00 | 2020-01-04 | 15 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-04 16:00 | 2020-01-04 | 16 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-01-04 17:00 | 2020-01-04 | 17 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-01-04 18:00 | 2020-01-04 | 18 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-01-04 19:00 | 2020-01-04 | 19 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-01-04 20:00 | 2020-01-04 | 20 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-01-04 21:00 | 2020-01-04 | 21 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-04 22:00 | 2020-01-04 | 22 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-04 23:00 | 2020-01-04 | 23 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-01-05 | 2020-01-04 | 0 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-01-05 01:00 | 2020-01-05 | 1 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-01-05 02:00 | 2020-01-05 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-01-05 03:00 | 2020-01-05 | 3 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-01-05 04:00 | 2020-01-05 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-01-05 05:00 | 2020-01-05 | 5 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-01-05 06:00 | 2020-01-05 | 6 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-01-05 07:00 | 2020-01-05 | 7 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-01-05 08:00 | 2020-01-05 | 8 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-01-05 09:00 | 2020-01-05 | 9 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-01-05 10:00 | 2020-01-05 | 10 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-01-05 11:00 | 2020-01-05 | 11 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-01-05 12:00 | 2020-01-05 | 12 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-01-05 13:00 | 2020-01-05 | 13 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-01-05 14:00 | 2020-01-05 | 14 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-01-05 15:00 | 2020-01-05 | 15 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-05 16:00 | 2020-01-05 | 16 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-01-05 17:00 | 2020-01-05 | 17 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-01-05 18:00 | 2020-01-05 | 18 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-01-05 19:00 | 2020-01-05 | 19 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-01-05 20:00 | 2020-01-05 | 20 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-01-05 21:00 | 2020-01-05 | 21 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-01-05 22:00 | 2020-01-05 | 22 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-01-05 23:00 | 2020-01-05 | 23 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-01-06 | 2020-01-05 | 0 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-01-06 01:00 | 2020-01-06 | 1 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-01-06 02:00 | 2020-01-06 | 2 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-01-06 03:00 | 2020-01-06 | 3 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-01-06 04:00 | 2020-01-06 | 4 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-01-06 05:00 | 2020-01-06 | 5 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-01-06 06:00 | 2020-01-06 | 6 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-01-06 07:00 | 2020-01-06 | 7 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-01-06 08:00 | 2020-01-06 | 8 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-06 09:00 | 2020-01-06 | 9 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-06 10:00 | 2020-01-06 | 10 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-01-06 11:00 | 2020-01-06 | 11 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-01-06 12:00 | 2020-01-06 | 12 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-01-06 13:00 | 2020-01-06 | 13 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-01-06 14:00 | 2020-01-06 | 14 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-01-06 15:00 | 2020-01-06 | 15 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-01-06 16:00 | 2020-01-06 | 16 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-01-06 17:00 | 2020-01-06 | 17 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-01-06 18:00 | 2020-01-06 | 18 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-01-06 19:00 | 2020-01-06 | 19 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-06 20:00 | 2020-01-06 | 20 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-06 21:00 | 2020-01-06 | 21 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-01-06 22:00 | 2020-01-06 | 22 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-06 23:00 | 2020-01-06 | 23 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-01-07 | 2020-01-06 | 0 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-01-07 01:00 | 2020-01-07 | 1 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-01-07 02:00 | 2020-01-07 | 2 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-01-07 03:00 | 2020-01-07 | 3 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-01-07 04:00 | 2020-01-07 | 4 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-01-07 05:00 | 2020-01-07 | 5 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-01-07 06:00 | 2020-01-07 | 6 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-01-07 07:00 | 2020-01-07 | 7 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-01-07 08:00 | 2020-01-07 | 8 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-07 09:00 | 2020-01-07 | 9 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-01-07 10:00 | 2020-01-07 | 10 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-07 11:00 | 2020-01-07 | 11 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-07 12:00 | 2020-01-07 | 12 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-07 13:00 | 2020-01-07 | 13 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-07 14:00 | 2020-01-07 | 14 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-07 15:00 | 2020-01-07 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-01-07 16:00 | 2020-01-07 | 16 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-07 17:00 | 2020-01-07 | 17 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-01-07 18:00 | 2020-01-07 | 18 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-01-07 19:00 | 2020-01-07 | 19 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-07 20:00 | 2020-01-07 | 20 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-01-07 21:00 | 2020-01-07 | 21 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-01-07 22:00 | 2020-01-07 | 22 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-01-07 23:00 | 2020-01-07 | 23 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-01-08 | 2020-01-07 | 0 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-01-08 01:00 | 2020-01-08 | 1 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-01-08 02:00 | 2020-01-08 | 2 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-01-08 03:00 | 2020-01-08 | 3 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-01-08 04:00 | 2020-01-08 | 4 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-01-08 05:00 | 2020-01-08 | 5 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-01-08 06:00 | 2020-01-08 | 6 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-01-08 07:00 | 2020-01-08 | 7 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-01-08 08:00 | 2020-01-08 | 8 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-08 09:00 | 2020-01-08 | 9 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-08 10:00 | 2020-01-08 | 10 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-08 11:00 | 2020-01-08 | 11 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-01-08 12:00 | 2020-01-08 | 12 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-08 13:00 | 2020-01-08 | 13 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-08 14:00 | 2020-01-08 | 14 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-01-08 15:00 | 2020-01-08 | 15 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-08 16:00 | 2020-01-08 | 16 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-08 17:00 | 2020-01-08 | 17 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-01-08 18:00 | 2020-01-08 | 18 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 1
2020-01-08 19:00 | 2020-01-08 | 19 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 2
2020-01-08 20:00 | 2020-01-08 | 20 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 3
2020-01-08 21:00 | 2020-01-08 | 21 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 4 | 4
2020-01-08 22:00 | 2020-01-08 | 22 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-01-08 23:00 | 2020-01-08 | 23 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-09 | 2020-01-08 | 0 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-01-09 01:00 | 2020-01-09 | 1 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-01-09 02:00 | 2020-01-09 | 2 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-09 03:00 | 2020-01-09 | 3 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-09 04:00 | 2020-01-09 | 4 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-01-09 05:00 | 2020-01-09 | 5 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-09 06:00 | 2020-01-09 | 6 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-01-09 07:00 | 2020-01-09 | 7 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-01-09 08:00 | 2020-01-09 | 8 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-01-09 09:00 | 2020-01-09 | 9 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-01-09 10:00 | 2020-01-09 | 10 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-01-09 11:00 | 2020-01-09 | 11 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-01-09 12:00 | 2020-01-09 | 12 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-09 13:00 | 2020-01-09 | 13 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-01-09 14:00 | 2020-01-09 | 14 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-09 15:00 | 2020-01-09 | 15 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-01-09 16:00 | 2020-01-09 | 16 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-01-09 17:00 | 2020-01-09 | 17 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 1
2020-01-09 18:00 | 2020-01-09 | 18 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 2
2020-01-09 19:00 | 2020-01-09 | 19 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 3
2020-01-09 20:00 | 2020-01-09 | 20 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 4 | 4
2020-01-09 21:00 | 2020-01-09 | 21 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-01-09 22:00 | 2020-01-09 | 22 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-09 23:00 | 2020-01-09 | 23 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-01-10 | 2020-01-09 | 0 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-01-10 01:00 | 2020-01-10 | 1 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-10 02:00 | 2020-01-10 | 2 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-01-10 03:00 | 2020-01-10 | 3 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-10 04:00 | 2020-01-10 | 4 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-10 05:00 | 2020-01-10 | 5 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-10 06:00 | 2020-01-10 | 6 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-10 07:00 | 2020-01-10 | 7 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-01-10 08:00 | 2020-01-10 | 8 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-01-10 09:00 | 2020-01-10 | 9 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-10 10:00 | 2020-01-10 | 10 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-01-10 11:00 | 2020-01-10 | 11 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-10 12:00 | 2020-01-10 | 12 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-10 13:00 | 2020-01-10 | 13 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-10 14:00 | 2020-01-10 | 14 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-10 15:00 | 2020-01-10 | 15 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-10 16:00 | 2020-01-10 | 16 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-10 17:00 | 2020-01-10 | 17 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-01-10 18:00 | 2020-01-10 | 18 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-01-10 19:00 | 2020-01-10 | 19 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-10 20:00 | 2020-01-10 | 20 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-10 21:00 | 2020-01-10 | 21 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-10 22:00 | 2020-01-10 | 22 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-01-10 23:00 | 2020-01-10 | 23 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-01-11 | 2020-01-10 | 0 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-01-11 01:00 | 2020-01-11 | 1 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-01-11 02:00 | 2020-01-11 | 2 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-11 03:00 | 2020-01-11 | 3 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-01-11 04:00 | 2020-01-11 | 4 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-01-11 05:00 | 2020-01-11 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-01-11 06:00 | 2020-01-11 | 6 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-01-11 07:00 | 2020-01-11 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-01-11 08:00 | 2020-01-11 | 8 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-11 09:00 | 2020-01-11 | 9 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-01-11 10:00 | 2020-01-11 | 10 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-01-11 11:00 | 2020-01-11 | 11 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-11 12:00 | 2020-01-11 | 12 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-11 13:00 | 2020-01-11 | 13 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-01-11 14:00 | 2020-01-11 | 14 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-11 15:00 | 2020-01-11 | 15 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-11 16:00 | 2020-01-11 | 16 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-11 17:00 | 2020-01-11 | 17 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-11 18:00 | 2020-01-11 | 18 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-01-11 19:00 | 2020-01-11 | 19 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-11 20:00 | 2020-01-11 | 20 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-01-11 21:00 | 2020-01-11 | 21 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-11 22:00 | 2020-01-11 | 22 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-01-11 23:00 | 2020-01-11 | 23 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-01-12 | 2020-01-11 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-12 01:00 | 2020-01-12 | 1 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-01-12 02:00 | 2020-01-12 | 2 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-01-12 03:00 | 2020-01-12 | 3 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-01-12 04:00 | 2020-01-12 | 4 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-01-12 05:00 | 2020-01-12 | 5 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-01-12 06:00 | 2020-01-12 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-01-12 07:00 | 2020-01-12 | 7 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-01-12 08:00 | 2020-01-12 | 8 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-12 09:00 | 2020-01-12 | 9 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-01-12 10:00 | 2020-01-12 | 10 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-01-12 11:00 | 2020-01-12 | 11 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-01-12 12:00 | 2020-01-12 | 12 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-12 13:00 | 2020-01-12 | 13 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-01-12 14:00 | 2020-01-12 | 14 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-01-12 15:00 | 2020-01-12 | 15 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-01-12 16:00 | 2020-01-12 | 16 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-12 17:00 | 2020-01-12 | 17 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-01-12 18:00 | 2020-01-12 | 18 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-01-12 19:00 | 2020-01-12 | 19 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 2 | 2
2020-01-12 20:00 | 2020-01-12 | 20 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-01-12 21:00 | 2020-01-12 | 21 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-12 22:00 | 2020-01-12 | 22 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-01-12 23:00 | 2020-01-12 | 23 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-01-13 | 2020-01-12 | 0 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-01-13 01:00 | 2020-01-13 | 1 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-01-13 02:00 | 2020-01-13 | 2 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-01-13 03:00 | 2020-01-13 | 3 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-01-13 04:00 | 2020-01-13 | 4 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-01-13 05:00 | 2020-01-13 | 5 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-01-13 06:00 | 2020-01-13 | 6 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-01-13 07:00 | 2020-01-13 | 7 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-01-13 08:00 | 2020-01-13 | 8 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-01-13 09:00 | 2020-01-13 | 9 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-01-13 10:00 | 2020-01-13 | 10 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-13 11:00 | 2020-01-13 | 11 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-13 12:00 | 2020-01-13 | 12 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-01-13 13:00 | 2020-01-13 | 13 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-13 14:00 | 2020-01-13 | 14 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-13 15:00 | 2020-01-13 | 15 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-13 16:00 | 2020-01-13 | 16 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-01-13 17:00 | 2020-01-13 | 17 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 1
2020-01-13 18:00 | 2020-01-13 | 18 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 2
2020-01-13 19:00 | 2020-01-13 | 19 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 3 | 3
2020-01-13 20:00 | 2020-01-13 | 20 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-01-13 21:00 | 2020-01-13 | 21 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-13 22:00 | 2020-01-13 | 22 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-13 23:00 | 2020-01-13 | 23 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-01-14 | 2020-01-13 | 0 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-01-14 01:00 | 2020-01-14 | 1 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-14 02:00 | 2020-01-14 | 2 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-14 03:00 | 2020-01-14 | 3 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-01-14 04:00 | 2020-01-14 | 4 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-01-14 05:00 | 2020-01-14 | 5 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-01-14 06:00 | 2020-01-14 | 6 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-14 07:00 | 2020-01-14 | 7 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-01-14 08:00 | 2020-01-14 | 8 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-01-14 09:00 | 2020-01-14 | 9 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-14 10:00 | 2020-01-14 | 10 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-14 11:00 | 2020-01-14 | 11 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-01-14 12:00 | 2020-01-14 | 12 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-14 13:00 | 2020-01-14 | 13 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-14 14:00 | 2020-01-14 | 14 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-01-14 15:00 | 2020-01-14 | 15 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-01-14 16:00 | 2020-01-14 | 16 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-14 17:00 | 2020-01-14 | 17 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1
2020-01-14 18:00 | 2020-01-14 | 18 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 2
2020-01-14 19:00 | 2020-01-14 | 19 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 3 | 3
2020-01-14 20:00 | 2020-01-14 | 20 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-01-14 21:00 | 2020-01-14 | 21 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-14 22:00 | 2020-01-14 | 22 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-14 23:00 | 2020-01-14 | 23 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-15 | 2020-01-14 | 0 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-15 01:00 | 2020-01-15 | 1 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-15 02:00 | 2020-01-15 | 2 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-01-15 03:00 | 2020-01-15 | 3 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-01-15 04:00 | 2020-01-15 | 4 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-01-15 05:00 | 2020-01-15 | 5 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-15 06:00 | 2020-01-15 | 6 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-01-15 07:00 | 2020-01-15 | 7 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-01-15 08:00 | 2020-01-15 | 8 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-15 09:00 | 2020-01-15 | 9 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-15 10:00 | 2020-01-15 | 10 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-01-15 11:00 | 2020-01-15 | 11 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-15 12:00 | 2020-01-15 | 12 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-15 13:00 | 2020-01-15 | 13 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-15 14:00 | 2020-01-15 | 14 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-15 15:00 | 2020-01-15 | 15 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-01-15 16:00 | 2020-01-15 | 16 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-15 17:00 | 2020-01-15 | 17 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-15 18:00 | 2020-01-15 | 18 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-01-15 19:00 | 2020-01-15 | 19 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-01-15 20:00 | 2020-01-15 | 20 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-15 21:00 | 2020-01-15 | 21 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-15 22:00 | 2020-01-15 | 22 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-01-15 23:00 | 2020-01-15 | 23 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-01-16 | 2020-01-15 | 0 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-01-16 01:00 | 2020-01-16 | 1 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-01-16 02:00 | 2020-01-16 | 2 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-01-16 03:00 | 2020-01-16 | 3 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-01-16 04:00 | 2020-01-16 | 4 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-01-16 05:00 | 2020-01-16 | 5 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-16 06:00 | 2020-01-16 | 6 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-01-16 07:00 | 2020-01-16 | 7 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-01-16 08:00 | 2020-01-16 | 8 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-01-16 09:00 | 2020-01-16 | 9 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-16 10:00 | 2020-01-16 | 10 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-16 11:00 | 2020-01-16 | 11 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-01-16 12:00 | 2020-01-16 | 12 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-01-16 13:00 | 2020-01-16 | 13 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-16 14:00 | 2020-01-16 | 14 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-16 15:00 | 2020-01-16 | 15 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-16 16:00 | 2020-01-16 | 16 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-16 17:00 | 2020-01-16 | 17 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-16 18:00 | 2020-01-16 | 18 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-01-16 19:00 | 2020-01-16 | 19 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1
2020-01-16 20:00 | 2020-01-16 | 20 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 2
2020-01-16 21:00 | 2020-01-16 | 21 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 3 | 3
2020-01-16 22:00 | 2020-01-16 | 22 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-16 23:00 | 2020-01-16 | 23 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-01-17 | 2020-01-16 | 0 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-01-17 01:00 | 2020-01-17 | 1 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-01-17 02:00 | 2020-01-17 | 2 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-01-17 03:00 | 2020-01-17 | 3 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-01-17 04:00 | 2020-01-17 | 4 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-17 05:00 | 2020-01-17 | 5 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-17 06:00 | 2020-01-17 | 6 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-01-17 07:00 | 2020-01-17 | 7 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-17 08:00 | 2020-01-17 | 8 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-17 09:00 | 2020-01-17 | 9 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-17 10:00 | 2020-01-17 | 10 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-01-17 11:00 | 2020-01-17 | 11 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-01-17 12:00 | 2020-01-17 | 12 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-01-17 13:00 | 2020-01-17 | 13 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-01-17 14:00 | 2020-01-17 | 14 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-17 15:00 | 2020-01-17 | 15 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-17 16:00 | 2020-01-17 | 16 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-01-17 17:00 | 2020-01-17 | 17 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-01-17 18:00 | 2020-01-17 | 18 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-01-17 19:00 | 2020-01-17 | 19 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 2
2020-01-17 20:00 | 2020-01-17 | 20 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 3 | 3
2020-01-17 21:00 | 2020-01-17 | 21 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-01-17 22:00 | 2020-01-17 | 22 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-17 23:00 | 2020-01-17 | 23 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-01-18 | 2020-01-17 | 0 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-01-18 01:00 | 2020-01-18 | 1 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-01-18 02:00 | 2020-01-18 | 2 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-18 03:00 | 2020-01-18 | 3 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-18 04:00 | 2020-01-18 | 4 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-01-18 05:00 | 2020-01-18 | 5 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-01-18 06:00 | 2020-01-18 | 6 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-01-18 07:00 | 2020-01-18 | 7 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-01-18 08:00 | 2020-01-18 | 8 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-01-18 09:00 | 2020-01-18 | 9 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-01-18 10:00 | 2020-01-18 | 10 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-01-18 11:00 | 2020-01-18 | 11 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1
2020-01-18 12:00 | 2020-01-18 | 12 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 2
2020-01-18 13:00 | 2020-01-18 | 13 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 3
2020-01-18 14:00 | 2020-01-18 | 14 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 4
2020-01-18 15:00 | 2020-01-18 | 15 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 5
2020-01-18 16:00 | 2020-01-18 | 16 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 6
2020-01-18 17:00 | 2020-01-18 | 17 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 7
2020-01-18 18:00 | 2020-01-18 | 18 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 8
2020-01-18 19:00 | 2020-01-18 | 19 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 9
2020-01-18 20:00 | 2020-01-18 | 20 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 10 | 10
2020-01-18 21:00 | 2020-01-18 | 21 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-01-18 22:00 | 2020-01-18 | 22 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-01-18 23:00 | 2020-01-18 | 23 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-01-19 | 2020-01-18 | 0 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-01-19 01:00 | 2020-01-19 | 1 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-01-19 02:00 | 2020-01-19 | 2 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-01-19 03:00 | 2020-01-19 | 3 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-01-19 04:00 | 2020-01-19 | 4 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-01-19 05:00 | 2020-01-19 | 5 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-01-19 06:00 | 2020-01-19 | 6 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-01-19 07:00 | 2020-01-19 | 7 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-01-19 08:00 | 2020-01-19 | 8 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-01-19 09:00 | 2020-01-19 | 9 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-01-19 10:00 | 2020-01-19 | 10 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-19 11:00 | 2020-01-19 | 11 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-19 12:00 | 2020-01-19 | 12 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-19 13:00 | 2020-01-19 | 13 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-19 14:00 | 2020-01-19 | 14 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-01-19 15:00 | 2020-01-19 | 15 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-01-19 16:00 | 2020-01-19 | 16 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-19 17:00 | 2020-01-19 | 17 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-19 18:00 | 2020-01-19 | 18 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-01-19 19:00 | 2020-01-19 | 19 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 2 | 2
2020-01-19 20:00 | 2020-01-19 | 20 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-19 21:00 | 2020-01-19 | 21 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-19 22:00 | 2020-01-19 | 22 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-19 23:00 | 2020-01-19 | 23 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-01-20 | 2020-01-19 | 0 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-01-20 01:00 | 2020-01-20 | 1 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-20 02:00 | 2020-01-20 | 2 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-01-20 03:00 | 2020-01-20 | 3 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-01-20 04:00 | 2020-01-20 | 4 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-01-20 05:00 | 2020-01-20 | 5 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-20 06:00 | 2020-01-20 | 6 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-01-20 07:00 | 2020-01-20 | 7 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-20 08:00 | 2020-01-20 | 8 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-20 09:00 | 2020-01-20 | 9 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-20 10:00 | 2020-01-20 | 10 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-01-20 11:00 | 2020-01-20 | 11 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-01-20 12:00 | 2020-01-20 | 12 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-01-20 13:00 | 2020-01-20 | 13 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-01-20 14:00 | 2020-01-20 | 14 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-01-20 15:00 | 2020-01-20 | 15 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-01-20 16:00 | 2020-01-20 | 16 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-01-20 17:00 | 2020-01-20 | 17 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-01-20 18:00 | 2020-01-20 | 18 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 1
2020-01-20 19:00 | 2020-01-20 | 19 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 2
2020-01-20 20:00 | 2020-01-20 | 20 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 3
2020-01-20 21:00 | 2020-01-20 | 21 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 4 | 4
2020-01-20 22:00 | 2020-01-20 | 22 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-20 23:00 | 2020-01-20 | 23 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-01-21 | 2020-01-20 | 0 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-01-21 01:00 | 2020-01-21 | 1 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-01-21 02:00 | 2020-01-21 | 2 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-01-21 03:00 | 2020-01-21 | 3 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-01-21 04:00 | 2020-01-21 | 4 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-21 05:00 | 2020-01-21 | 5 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-21 06:00 | 2020-01-21 | 6 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-01-21 07:00 | 2020-01-21 | 7 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-21 08:00 | 2020-01-21 | 8 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-01-21 09:00 | 2020-01-21 | 9 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-21 10:00 | 2020-01-21 | 10 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1
2020-01-21 11:00 | 2020-01-21 | 11 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 2
2020-01-21 12:00 | 2020-01-21 | 12 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 3
2020-01-21 13:00 | 2020-01-21 | 13 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 4 | 4
2020-01-21 14:00 | 2020-01-21 | 14 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-01-21 15:00 | 2020-01-21 | 15 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1 | 1
2020-01-21 16:00 | 2020-01-21 | 16 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-01-21 17:00 | 2020-01-21 | 17 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-01-21 18:00 | 2020-01-21 | 18 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 1
2020-01-21 19:00 | 2020-01-21 | 19 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 2
2020-01-21 20:00 | 2020-01-21 | 20 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 3
2020-01-21 21:00 | 2020-01-21 | 21 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 4 | 4
2020-01-21 22:00 | 2020-01-21 | 22 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-21 23:00 | 2020-01-21 | 23 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-01-22 | 2020-01-21 | 0 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-01-22 01:00 | 2020-01-22 | 1 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-22 02:00 | 2020-01-22 | 2 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-01-22 03:00 | 2020-01-22 | 3 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-01-22 04:00 | 2020-01-22 | 4 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-01-22 05:00 | 2020-01-22 | 5 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-01-22 06:00 | 2020-01-22 | 6 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-22 07:00 | 2020-01-22 | 7 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-01-22 08:00 | 2020-01-22 | 8 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-22 09:00 | 2020-01-22 | 9 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-22 10:00 | 2020-01-22 | 10 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-01-22 11:00 | 2020-01-22 | 11 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-22 12:00 | 2020-01-22 | 12 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-01-22 13:00 | 2020-01-22 | 13 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-22 14:00 | 2020-01-22 | 14 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-01-22 15:00 | 2020-01-22 | 15 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-01-22 16:00 | 2020-01-22 | 16 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-01-22 17:00 | 2020-01-22 | 17 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-01-22 18:00 | 2020-01-22 | 18 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 1 | 1
2020-01-22 19:00 | 2020-01-22 | 19 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-01-22 20:00 | 2020-01-22 | 20 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-01-22 21:00 | 2020-01-22 | 21 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-22 22:00 | 2020-01-22 | 22 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-22 23:00 | 2020-01-22 | 23 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-01-23 | 2020-01-22 | 0 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-01-23 01:00 | 2020-01-23 | 1 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-01-23 02:00 | 2020-01-23 | 2 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-01-23 03:00 | 2020-01-23 | 3 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-01-23 04:00 | 2020-01-23 | 4 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-01-23 05:00 | 2020-01-23 | 5 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-01-23 06:00 | 2020-01-23 | 6 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-01-23 07:00 | 2020-01-23 | 7 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-01-23 08:00 | 2020-01-23 | 8 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-23 09:00 | 2020-01-23 | 9 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-23 10:00 | 2020-01-23 | 10 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-23 11:00 | 2020-01-23 | 11 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-01-23 12:00 | 2020-01-23 | 12 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-23 13:00 | 2020-01-23 | 13 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-23 14:00 | 2020-01-23 | 14 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-01-23 15:00 | 2020-01-23 | 15 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-23 16:00 | 2020-01-23 | 16 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-23 17:00 | 2020-01-23 | 17 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-23 18:00 | 2020-01-23 | 18 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-01-23 19:00 | 2020-01-23 | 19 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 1 | 1
2020-01-23 20:00 | 2020-01-23 | 20 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-23 21:00 | 2020-01-23 | 21 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-01-23 22:00 | 2020-01-23 | 22 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-23 23:00 | 2020-01-23 | 23 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-01-24 | 2020-01-23 | 0 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-24 01:00 | 2020-01-24 | 1 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-24 02:00 | 2020-01-24 | 2 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-01-24 03:00 | 2020-01-24 | 3 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-01-24 04:00 | 2020-01-24 | 4 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-01-24 05:00 | 2020-01-24 | 5 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-24 06:00 | 2020-01-24 | 6 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-24 07:00 | 2020-01-24 | 7 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-24 08:00 | 2020-01-24 | 8 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-01-24 09:00 | 2020-01-24 | 9 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-01-24 10:00 | 2020-01-24 | 10 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-24 11:00 | 2020-01-24 | 11 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-24 12:00 | 2020-01-24 | 12 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-01-24 13:00 | 2020-01-24 | 13 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-24 14:00 | 2020-01-24 | 14 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-24 15:00 | 2020-01-24 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-01-24 16:00 | 2020-01-24 | 16 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-01-24 17:00 | 2020-01-24 | 17 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-01-24 18:00 | 2020-01-24 | 18 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-24 19:00 | 2020-01-24 | 19 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-24 20:00 | 2020-01-24 | 20 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-01-24 21:00 | 2020-01-24 | 21 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-24 22:00 | 2020-01-24 | 22 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-24 23:00 | 2020-01-24 | 23 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-01-25 | 2020-01-24 | 0 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-01-25 01:00 | 2020-01-25 | 1 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-25 02:00 | 2020-01-25 | 2 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-01-25 03:00 | 2020-01-25 | 3 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-01-25 04:00 | 2020-01-25 | 4 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-01-25 05:00 | 2020-01-25 | 5 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-25 06:00 | 2020-01-25 | 6 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-01-25 07:00 | 2020-01-25 | 7 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-01-25 08:00 | 2020-01-25 | 8 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-01-25 09:00 | 2020-01-25 | 9 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-01-25 10:00 | 2020-01-25 | 10 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-01-25 11:00 | 2020-01-25 | 11 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-25 12:00 | 2020-01-25 | 12 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-25 13:00 | 2020-01-25 | 13 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-25 14:00 | 2020-01-25 | 14 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-01-25 15:00 | 2020-01-25 | 15 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-25 16:00 | 2020-01-25 | 16 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-25 17:00 | 2020-01-25 | 17 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-25 18:00 | 2020-01-25 | 18 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-25 19:00 | 2020-01-25 | 19 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-01-25 20:00 | 2020-01-25 | 20 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-01-25 21:00 | 2020-01-25 | 21 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-01-25 22:00 | 2020-01-25 | 22 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-01-25 23:00 | 2020-01-25 | 23 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-01-26 | 2020-01-25 | 0 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-01-26 01:00 | 2020-01-26 | 1 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-01-26 02:00 | 2020-01-26 | 2 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-01-26 03:00 | 2020-01-26 | 3 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-01-26 04:00 | 2020-01-26 | 4 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-01-26 05:00 | 2020-01-26 | 5 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-01-26 06:00 | 2020-01-26 | 6 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-01-26 07:00 | 2020-01-26 | 7 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-01-26 08:00 | 2020-01-26 | 8 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-26 09:00 | 2020-01-26 | 9 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-01-26 10:00 | 2020-01-26 | 10 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-01-26 11:00 | 2020-01-26 | 11 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-01-26 12:00 | 2020-01-26 | 12 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-26 13:00 | 2020-01-26 | 13 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-26 14:00 | 2020-01-26 | 14 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-01-26 15:00 | 2020-01-26 | 15 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-26 16:00 | 2020-01-26 | 16 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-26 17:00 | 2020-01-26 | 17 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-01-26 18:00 | 2020-01-26 | 18 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-26 19:00 | 2020-01-26 | 19 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-26 20:00 | 2020-01-26 | 20 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-01-26 21:00 | 2020-01-26 | 21 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-01-26 22:00 | 2020-01-26 | 22 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-01-26 23:00 | 2020-01-26 | 23 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-01-27 | 2020-01-26 | 0 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-01-27 01:00 | 2020-01-27 | 1 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-27 02:00 | 2020-01-27 | 2 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-27 03:00 | 2020-01-27 | 3 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-01-27 04:00 | 2020-01-27 | 4 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-01-27 05:00 | 2020-01-27 | 5 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-01-27 06:00 | 2020-01-27 | 6 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-01-27 07:00 | 2020-01-27 | 7 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-01-27 08:00 | 2020-01-27 | 8 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-01-27 09:00 | 2020-01-27 | 9 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-27 10:00 | 2020-01-27 | 10 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-01-27 11:00 | 2020-01-27 | 11 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-01-27 12:00 | 2020-01-27 | 12 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-27 13:00 | 2020-01-27 | 13 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-01-27 14:00 | 2020-01-27 | 14 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-01-27 15:00 | 2020-01-27 | 15 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-27 16:00 | 2020-01-27 | 16 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-01-27 17:00 | 2020-01-27 | 17 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-01-27 18:00 | 2020-01-27 | 18 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-01-27 19:00 | 2020-01-27 | 19 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-01-27 20:00 | 2020-01-27 | 20 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-01-27 21:00 | 2020-01-27 | 21 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-27 22:00 | 2020-01-27 | 22 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-27 23:00 | 2020-01-27 | 23 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-01-28 | 2020-01-27 | 0 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-01-28 01:00 | 2020-01-28 | 1 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-01-28 02:00 | 2020-01-28 | 2 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-01-28 03:00 | 2020-01-28 | 3 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-01-28 04:00 | 2020-01-28 | 4 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-01-28 05:00 | 2020-01-28 | 5 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-01-28 06:00 | 2020-01-28 | 6 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-01-28 07:00 | 2020-01-28 | 7 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-01-28 08:00 | 2020-01-28 | 8 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-01-28 09:00 | 2020-01-28 | 9 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-01-28 10:00 | 2020-01-28 | 10 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-01-28 11:00 | 2020-01-28 | 11 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-28 12:00 | 2020-01-28 | 12 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-28 13:00 | 2020-01-28 | 13 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-01-28 14:00 | 2020-01-28 | 14 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-01-28 15:00 | 2020-01-28 | 15 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-01-28 16:00 | 2020-01-28 | 16 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-01-28 17:00 | 2020-01-28 | 17 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-28 18:00 | 2020-01-28 | 18 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-01-28 19:00 | 2020-01-28 | 19 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-01-28 20:00 | 2020-01-28 | 20 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-28 21:00 | 2020-01-28 | 21 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-01-28 22:00 | 2020-01-28 | 22 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-28 23:00 | 2020-01-28 | 23 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-01-29 | 2020-01-28 | 0 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-01-29 01:00 | 2020-01-29 | 1 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-01-29 02:00 | 2020-01-29 | 2 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-01-29 03:00 | 2020-01-29 | 3 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-01-29 04:00 | 2020-01-29 | 4 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-01-29 05:00 | 2020-01-29 | 5 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-01-29 06:00 | 2020-01-29 | 6 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-01-29 07:00 | 2020-01-29 | 7 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-01-29 08:00 | 2020-01-29 | 8 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-01-29 09:00 | 2020-01-29 | 9 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-01-29 10:00 | 2020-01-29 | 10 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-29 11:00 | 2020-01-29 | 11 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-29 12:00 | 2020-01-29 | 12 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-01-29 13:00 | 2020-01-29 | 13 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-01-29 14:00 | 2020-01-29 | 14 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-01-29 15:00 | 2020-01-29 | 15 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-01-29 16:00 | 2020-01-29 | 16 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-01-29 17:00 | 2020-01-29 | 17 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-01-29 18:00 | 2020-01-29 | 18 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-01-29 19:00 | 2020-01-29 | 19 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-29 20:00 | 2020-01-29 | 20 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-01-29 21:00 | 2020-01-29 | 21 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-01-29 22:00 | 2020-01-29 | 22 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-01-29 23:00 | 2020-01-29 | 23 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-01-30 | 2020-01-29 | 0 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-01-30 01:00 | 2020-01-30 | 1 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-01-30 02:00 | 2020-01-30 | 2 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-01-30 03:00 | 2020-01-30 | 3 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-01-30 04:00 | 2020-01-30 | 4 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-01-30 05:00 | 2020-01-30 | 5 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-01-30 06:00 | 2020-01-30 | 6 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-01-30 07:00 | 2020-01-30 | 7 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-01-30 08:00 | 2020-01-30 | 8 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-30 09:00 | 2020-01-30 | 9 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-01-30 10:00 | 2020-01-30 | 10 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-01-30 11:00 | 2020-01-30 | 11 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-01-30 12:00 | 2020-01-30 | 12 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-01-30 13:00 | 2020-01-30 | 13 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-30 14:00 | 2020-01-30 | 14 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-01-30 15:00 | 2020-01-30 | 15 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-01-30 16:00 | 2020-01-30 | 16 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-01-30 17:00 | 2020-01-30 | 17 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-01-30 18:00 | 2020-01-30 | 18 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 1 | 1
2020-01-30 19:00 | 2020-01-30 | 19 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-01-30 20:00 | 2020-01-30 | 20 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 1 | 1
2020-01-30 21:00 | 2020-01-30 | 21 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-01-30 22:00 | 2020-01-30 | 22 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-01-30 23:00 | 2020-01-30 | 23 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-01-31 | 2020-01-30 | 0 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-01-31 01:00 | 2020-01-31 | 1 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-01-31 02:00 | 2020-01-31 | 2 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-01-31 03:00 | 2020-01-31 | 3 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-01-31 04:00 | 2020-01-31 | 4 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-01-31 05:00 | 2020-01-31 | 5 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-01-31 06:00 | 2020-01-31 | 6 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-01-31 07:00 | 2020-01-31 | 7 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-01-31 08:00 | 2020-01-31 | 8 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-01-31 09:00 | 2020-01-31 | 9 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-01-31 10:00 | 2020-01-31 | 10 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-01-31 11:00 | 2020-01-31 | 11 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1 | 1
2020-01-31 12:00 | 2020-01-31 | 12 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-01-31 13:00 | 2020-01-31 | 13 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-01-31 14:00 | 2020-01-31 | 14 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-31 15:00 | 2020-01-31 | 15 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-01-31 16:00 | 2020-01-31 | 16 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-01-31 17:00 | 2020-01-31 | 17 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-01-31 18:00 | 2020-01-31 | 18 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-01-31 19:00 | 2020-01-31 | 19 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-01-31 20:00 | 2020-01-31 | 20 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-01-31 21:00 | 2020-01-31 | 21 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-01-31 22:00 | 2020-01-31 | 22 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-01-31 23:00 | 2020-01-31 | 23 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-02-01 | 2020-01-31 | 0 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-02-01 01:00 | 2020-02-01 | 1 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-02-01 02:00 | 2020-02-01 | 2 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-02-01 03:00 | 2020-02-01 | 3 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-02-01 04:00 | 2020-02-01 | 4 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-02-01 05:00 | 2020-02-01 | 5 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-02-01 06:00 | 2020-02-01 | 6 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-02-01 07:00 | 2020-02-01 | 7 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-02-01 08:00 | 2020-02-01 | 8 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-02-01 09:00 | 2020-02-01 | 9 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-02-01 10:00 | 2020-02-01 | 10 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-02-01 11:00 | 2020-02-01 | 11 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-02-01 12:00 | 2020-02-01 | 12 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-02-01 13:00 | 2020-02-01 | 13 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-02-01 14:00 | 2020-02-01 | 14 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-02-01 15:00 | 2020-02-01 | 15 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-01 16:00 | 2020-02-01 | 16 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-02-01 17:00 | 2020-02-01 | 17 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-02-01 18:00 | 2020-02-01 | 18 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-02-01 19:00 | 2020-02-01 | 19 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-02-01 20:00 | 2020-02-01 | 20 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-02-01 21:00 | 2020-02-01 | 21 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-02-01 22:00 | 2020-02-01 | 22 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-02-01 23:00 | 2020-02-01 | 23 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-02-02 | 2020-02-01 | 0 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-02-02 01:00 | 2020-02-02 | 1 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-02-02 02:00 | 2020-02-02 | 2 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-02-02 03:00 | 2020-02-02 | 3 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-02-02 04:00 | 2020-02-02 | 4 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-02-02 05:00 | 2020-02-02 | 5 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-02-02 06:00 | 2020-02-02 | 6 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-02-02 07:00 | 2020-02-02 | 7 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-02-02 08:00 | 2020-02-02 | 8 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-02-02 09:00 | 2020-02-02 | 9 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-02-02 10:00 | 2020-02-02 | 10 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-02-02 11:00 | 2020-02-02 | 11 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-02-02 12:00 | 2020-02-02 | 12 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-02-02 13:00 | 2020-02-02 | 13 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-02-02 14:00 | 2020-02-02 | 14 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-02-02 15:00 | 2020-02-02 | 15 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-02-02 16:00 | 2020-02-02 | 16 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-02-02 17:00 | 2020-02-02 | 17 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-02-02 18:00 | 2020-02-02 | 18 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-02-02 19:00 | 2020-02-02 | 19 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-02-02 20:00 | 2020-02-02 | 20 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-02-02 21:00 | 2020-02-02 | 21 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-02-02 22:00 | 2020-02-02 | 22 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-02-02 23:00 | 2020-02-02 | 23 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-02-03 | 2020-02-02 | 0 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-02-03 01:00 | 2020-02-03 | 1 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-02-03 02:00 | 2020-02-03 | 2 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-02-03 03:00 | 2020-02-03 | 3 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-02-03 04:00 | 2020-02-03 | 4 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-02-03 05:00 | 2020-02-03 | 5 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-02-03 06:00 | 2020-02-03 | 6 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-02-03 07:00 | 2020-02-03 | 7 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-02-03 08:00 | 2020-02-03 | 8 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-02-03 09:00 | 2020-02-03 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-02-03 10:00 | 2020-02-03 | 10 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-02-03 11:00 | 2020-02-03 | 11 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-02-03 12:00 | 2020-02-03 | 12 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-02-03 13:00 | 2020-02-03 | 13 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-02-03 14:00 | 2020-02-03 | 14 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-02-03 15:00 | 2020-02-03 | 15 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-02-03 16:00 | 2020-02-03 | 16 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-02-03 17:00 | 2020-02-03 | 17 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-02-03 18:00 | 2020-02-03 | 18 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-02-03 19:00 | 2020-02-03 | 19 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-03 20:00 | 2020-02-03 | 20 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-02-03 21:00 | 2020-02-03 | 21 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-02-03 22:00 | 2020-02-03 | 22 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-02-03 23:00 | 2020-02-03 | 23 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-02-04 | 2020-02-03 | 0 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-02-04 01:00 | 2020-02-04 | 1 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-02-04 02:00 | 2020-02-04 | 2 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-02-04 03:00 | 2020-02-04 | 3 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-02-04 04:00 | 2020-02-04 | 4 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-02-04 05:00 | 2020-02-04 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-02-04 06:00 | 2020-02-04 | 6 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-02-04 07:00 | 2020-02-04 | 7 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-02-04 08:00 | 2020-02-04 | 8 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-02-04 09:00 | 2020-02-04 | 9 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-02-04 10:00 | 2020-02-04 | 10 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-02-04 11:00 | 2020-02-04 | 11 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-02-04 12:00 | 2020-02-04 | 12 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-02-04 13:00 | 2020-02-04 | 13 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-02-04 14:00 | 2020-02-04 | 14 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-02-04 15:00 | 2020-02-04 | 15 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-02-04 16:00 | 2020-02-04 | 16 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-02-04 17:00 | 2020-02-04 | 17 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-02-04 18:00 | 2020-02-04 | 18 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-02-04 19:00 | 2020-02-04 | 19 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-02-04 20:00 | 2020-02-04 | 20 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-04 21:00 | 2020-02-04 | 21 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-02-04 22:00 | 2020-02-04 | 22 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-02-04 23:00 | 2020-02-04 | 23 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-02-05 | 2020-02-04 | 0 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-02-05 01:00 | 2020-02-05 | 1 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-02-05 02:00 | 2020-02-05 | 2 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-02-05 03:00 | 2020-02-05 | 3 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-02-05 04:00 | 2020-02-05 | 4 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-02-05 05:00 | 2020-02-05 | 5 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-02-05 06:00 | 2020-02-05 | 6 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-02-05 07:00 | 2020-02-05 | 7 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-02-05 08:00 | 2020-02-05 | 8 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-02-05 09:00 | 2020-02-05 | 9 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-02-05 10:00 | 2020-02-05 | 10 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-02-05 11:00 | 2020-02-05 | 11 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-02-05 12:00 | 2020-02-05 | 12 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-02-05 13:00 | 2020-02-05 | 13 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-02-05 14:00 | 2020-02-05 | 14 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-02-05 15:00 | 2020-02-05 | 15 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-02-05 16:00 | 2020-02-05 | 16 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-02-05 17:00 | 2020-02-05 | 17 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-02-05 18:00 | 2020-02-05 | 18 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-02-05 19:00 | 2020-02-05 | 19 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-02-05 20:00 | 2020-02-05 | 20 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-02-05 21:00 | 2020-02-05 | 21 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-02-05 22:00 | 2020-02-05 | 22 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-02-05 23:00 | 2020-02-05 | 23 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-02-06 | 2020-02-05 | 0 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-02-06 01:00 | 2020-02-06 | 1 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-02-06 02:00 | 2020-02-06 | 2 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-02-06 03:00 | 2020-02-06 | 3 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-02-06 04:00 | 2020-02-06 | 4 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-02-06 05:00 | 2020-02-06 | 5 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-02-06 06:00 | 2020-02-06 | 6 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-02-06 07:00 | 2020-02-06 | 7 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-02-06 08:00 | 2020-02-06 | 8 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-02-06 09:00 | 2020-02-06 | 9 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-02-06 10:00 | 2020-02-06 | 10 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-06 11:00 | 2020-02-06 | 11 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-02-06 12:00 | 2020-02-06 | 12 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-02-06 13:00 | 2020-02-06 | 13 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-06 14:00 | 2020-02-06 | 14 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-02-06 15:00 | 2020-02-06 | 15 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-02-06 16:00 | 2020-02-06 | 16 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-02-06 17:00 | 2020-02-06 | 17 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-02-06 18:00 | 2020-02-06 | 18 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-02-06 19:00 | 2020-02-06 | 19 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-02-06 20:00 | 2020-02-06 | 20 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-02-06 21:00 | 2020-02-06 | 21 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-02-06 22:00 | 2020-02-06 | 22 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-02-06 23:00 | 2020-02-06 | 23 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-02-07 | 2020-02-06 | 0 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-02-07 01:00 | 2020-02-07 | 1 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-02-07 02:00 | 2020-02-07 | 2 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-02-07 03:00 | 2020-02-07 | 3 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-02-07 04:00 | 2020-02-07 | 4 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-02-07 05:00 | 2020-02-07 | 5 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-02-07 06:00 | 2020-02-07 | 6 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-02-07 07:00 | 2020-02-07 | 7 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-02-07 08:00 | 2020-02-07 | 8 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-02-07 09:00 | 2020-02-07 | 9 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-02-07 10:00 | 2020-02-07 | 10 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-07 11:00 | 2020-02-07 | 11 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-02-07 12:00 | 2020-02-07 | 12 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-02-07 13:00 | 2020-02-07 | 13 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-02-07 14:00 | 2020-02-07 | 14 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-02-07 15:00 | 2020-02-07 | 15 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-07 16:00 | 2020-02-07 | 16 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-07 17:00 | 2020-02-07 | 17 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-02-07 18:00 | 2020-02-07 | 18 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-02-07 19:00 | 2020-02-07 | 19 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 1 | 1
2020-02-07 20:00 | 2020-02-07 | 20 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-02-07 21:00 | 2020-02-07 | 21 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-02-07 22:00 | 2020-02-07 | 22 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-07 23:00 | 2020-02-07 | 23 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-02-08 | 2020-02-07 | 0 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-02-08 01:00 | 2020-02-08 | 1 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 1
2020-02-08 02:00 | 2020-02-08 | 2 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 2
2020-02-08 03:00 | 2020-02-08 | 3 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 3
2020-02-08 04:00 | 2020-02-08 | 4 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 4
2020-02-08 05:00 | 2020-02-08 | 5 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 5
2020-02-08 06:00 | 2020-02-08 | 6 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 6
2020-02-08 07:00 | 2020-02-08 | 7 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 7
2020-02-08 08:00 | 2020-02-08 | 8 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 8
2020-02-08 09:00 | 2020-02-08 | 9 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 9
2020-02-08 10:00 | 2020-02-08 | 10 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 10
2020-02-08 11:00 | 2020-02-08 | 11 | 5.2328 | 0.01817% | 7.8019 | 8.0904 | 8.3896 | 8.6998 | 9.0215 | 2.0649 | 2.3534 | 2.6526 | 2.9628 | 3.2845 | 11
2020-02-08 12:00 | 2020-02-08 | 12 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 12
2020-02-08 13:00 | 2020-02-08 | 13 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 13
2020-02-08 14:00 | 2020-02-08 | 14 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 14
2020-02-08 15:00 | 2020-02-08 | 15 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 15
2020-02-08 16:00 | 2020-02-08 | 16 | 4.9467 | 0.01718% | 7.3753 | 7.6481 | 7.9309 | 8.2242 | 8.5283 | 1.6383 | 1.9111 | 2.1939 | 2.4872 | 2.7913 | 16
2020-02-08 17:00 | 2020-02-08 | 17 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 17
2020-02-08 18:00 | 2020-02-08 | 18 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 18
2020-02-08 19:00 | 2020-02-08 | 19 | 5.5641 | 0.01932% | 8.2959 | 8.6026 | 8.9207 | 9.2506 | 9.5927 | 2.5589 | 2.8656 | 3.1837 | 3.5136 | 3.8557 | 19
2020-02-08 20:00 | 2020-02-08 | 20 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 20
2020-02-08 21:00 | 2020-02-08 | 21 | 5.3533 | 0.01859% | 7.9815 | 8.2767 | 8.5827 | 8.9001 | 9.2292 | 2.2445 | 2.5397 | 2.8457 | 3.1631 | 3.4922 | 21
2020-02-08 22:00 | 2020-02-08 | 22 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 22
2020-02-08 23:00 | 2020-02-08 | 23 | 4.9316 | 0.01712% | 7.3529 | 7.6248 | 7.9067 | 8.1991 | 8.5023 | 1.6159 | 1.8878 | 2.1697 | 2.4621 | 2.7653 | 23
2020-02-09 | 2020-02-08 | 0 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 24
2020-02-09 01:00 | 2020-02-09 | 1 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 25
2020-02-09 02:00 | 2020-02-09 | 2 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 26
2020-02-09 03:00 | 2020-02-09 | 3 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 27
2020-02-09 04:00 | 2020-02-09 | 4 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 28
2020-02-09 05:00 | 2020-02-09 | 5 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 29
2020-02-09 06:00 | 2020-02-09 | 6 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 30
2020-02-09 07:00 | 2020-02-09 | 7 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 31
2020-02-09 08:00 | 2020-02-09 | 8 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 32
2020-02-09 09:00 | 2020-02-09 | 9 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 33
2020-02-09 10:00 | 2020-02-09 | 10 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 34
2020-02-09 11:00 | 2020-02-09 | 11 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 35
2020-02-09 12:00 | 2020-02-09 | 12 | 5.3081 | 0.01843% | 7.9142 | 8.2068 | 8.5103 | 8.825 | 9.1513 | 2.1772 | 2.4698 | 2.7733 | 3.088 | 3.4143 | 36
2020-02-09 13:00 | 2020-02-09 | 13 | 5.4361 | 0.01888% | 8.105 | 8.4047 | 8.7155 | 9.0378 | 9.372 | 2.368 | 2.6677 | 2.9785 | 3.3008 | 3.635 | 37
2020-02-09 14:00 | 2020-02-09 | 14 | 5.2027 | 0.01807% | 7.757 | 8.0439 | 8.3413 | 8.6498 | 8.9696 | 2.02 | 2.3069 | 2.6043 | 2.9128 | 3.2326 | 38
2020-02-09 15:00 | 2020-02-09 | 15 | 5.1876 | 0.01801% | 7.7346 | 8.0206 | 8.3172 | 8.6247 | 8.9437 | 1.9976 | 2.2836 | 2.5802 | 2.8877 | 3.2067 | 39
2020-02-09 16:00 | 2020-02-09 | 16 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 40
2020-02-09 17:00 | 2020-02-09 | 17 | 5.406 | 0.01877% | 8.0601 | 8.3582 | 8.6672 | 8.9877 | 9.3201 | 2.3231 | 2.6212 | 2.9302 | 3.2507 | 3.5831 | 41
2020-02-09 18:00 | 2020-02-09 | 18 | 5.4963 | 0.01909% | 8.1948 | 8.4979 | 8.8121 | 9.138 | 9.4759 | 2.4578 | 2.7609 | 3.0751 | 3.401 | 3.7389 | 42
2020-02-09 19:00 | 2020-02-09 | 19 | 5.4361 | 0.01888% | 8.105 | 8.4047 | 8.7155 | 9.0378 | 9.372 | 2.368 | 2.6677 | 2.9785 | 3.3008 | 3.635 | 43
2020-02-09 20:00 | 2020-02-09 | 20 | 5.2253 | 0.01814% | 7.7907 | 8.0788 | 8.3775 | 8.6873 | 9.0086 | 2.0537 | 2.3418 | 2.6405 | 2.9503 | 3.2716 | 44
2020-02-09 21:00 | 2020-02-09 | 21 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 45
2020-02-09 22:00 | 2020-02-09 | 22 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 46
2020-02-09 23:00 | 2020-02-09 | 23 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 47
2020-02-10 | 2020-02-09 | 0 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 48 | 48
2020-02-10 01:00 | 2020-02-10 | 1 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-02-10 02:00 | 2020-02-10 | 2 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-02-10 03:00 | 2020-02-10 | 3 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-02-10 04:00 | 2020-02-10 | 4 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-02-10 05:00 | 2020-02-10 | 5 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-02-10 06:00 | 2020-02-10 | 6 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-02-10 07:00 | 2020-02-10 | 7 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 1
2020-02-10 08:00 | 2020-02-10 | 8 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 2
2020-02-10 09:00 | 2020-02-10 | 9 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 3
2020-02-10 10:00 | 2020-02-10 | 10 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 4
2020-02-10 11:00 | 2020-02-10 | 11 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 5
2020-02-10 12:00 | 2020-02-10 | 12 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 6
2020-02-10 13:00 | 2020-02-10 | 13 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 7
2020-02-10 14:00 | 2020-02-10 | 14 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 8
2020-02-10 15:00 | 2020-02-10 | 15 | 4.6229 | 0.01605% | 6.8926 | 7.1475 | 7.4118 | 7.6859 | 7.9701 | 1.1556 | 1.4105 | 1.6748 | 1.9489 | 2.2331 | 9
2020-02-10 16:00 | 2020-02-10 | 16 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 10
2020-02-10 17:00 | 2020-02-10 | 17 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 11
2020-02-10 18:00 | 2020-02-10 | 18 | 4.9919 | 0.01733% | 7.4427 | 7.7179 | 8.0033 | 8.2993 | 8.6062 | 1.7057 | 1.9809 | 2.2663 | 2.5623 | 2.8692 | 12
2020-02-10 19:00 | 2020-02-10 | 19 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 13
2020-02-10 20:00 | 2020-02-10 | 20 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 14
2020-02-10 21:00 | 2020-02-10 | 21 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 15
2020-02-10 22:00 | 2020-02-10 | 22 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 16
2020-02-10 23:00 | 2020-02-10 | 23 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 17
2020-02-11 | 2020-02-10 | 0 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 18 | 18
2020-02-11 01:00 | 2020-02-11 | 1 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-02-11 02:00 | 2020-02-11 | 2 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-02-11 03:00 | 2020-02-11 | 3 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-02-11 04:00 | 2020-02-11 | 4 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-02-11 05:00 | 2020-02-11 | 5 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-02-11 06:00 | 2020-02-11 | 6 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-02-11 07:00 | 2020-02-11 | 7 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 1
2020-02-11 08:00 | 2020-02-11 | 8 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 2
2020-02-11 09:00 | 2020-02-11 | 9 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 3
2020-02-11 10:00 | 2020-02-11 | 10 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 4
2020-02-11 11:00 | 2020-02-11 | 11 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 5
2020-02-11 12:00 | 2020-02-11 | 12 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 6
2020-02-11 13:00 | 2020-02-11 | 13 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 7
2020-02-11 14:00 | 2020-02-11 | 14 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 8
2020-02-11 15:00 | 2020-02-11 | 15 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 9
2020-02-11 16:00 | 2020-02-11 | 16 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 10
2020-02-11 17:00 | 2020-02-11 | 17 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 11
2020-02-11 18:00 | 2020-02-11 | 18 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 12
2020-02-11 19:00 | 2020-02-11 | 19 | 5.1199 | 0.01778% | 7.6335 | 7.9158 | 8.2085 | 8.5121 | 8.8268 | 1.8965 | 2.1788 | 2.4715 | 2.7751 | 3.0898 | 13
2020-02-11 20:00 | 2020-02-11 | 20 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 14
2020-02-11 21:00 | 2020-02-11 | 21 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 15
2020-02-11 22:00 | 2020-02-11 | 22 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 16
2020-02-11 23:00 | 2020-02-11 | 23 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 17 | 17
2020-02-12 | 2020-02-11 | 0 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-02-12 01:00 | 2020-02-12 | 1 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-02-12 02:00 | 2020-02-12 | 2 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-12 03:00 | 2020-02-12 | 3 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-02-12 04:00 | 2020-02-12 | 4 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-02-12 05:00 | 2020-02-12 | 5 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-02-12 06:00 | 2020-02-12 | 6 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-02-12 07:00 | 2020-02-12 | 7 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 1
2020-02-12 08:00 | 2020-02-12 | 8 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 2
2020-02-12 09:00 | 2020-02-12 | 9 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 3
2020-02-12 10:00 | 2020-02-12 | 10 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 4
2020-02-12 11:00 | 2020-02-12 | 11 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 5
2020-02-12 12:00 | 2020-02-12 | 12 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 6
2020-02-12 13:00 | 2020-02-12 | 13 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 7
2020-02-12 14:00 | 2020-02-12 | 14 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 8
2020-02-12 15:00 | 2020-02-12 | 15 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 9
2020-02-12 16:00 | 2020-02-12 | 16 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 10
2020-02-12 17:00 | 2020-02-12 | 17 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 11
2020-02-12 18:00 | 2020-02-12 | 18 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 12
2020-02-12 19:00 | 2020-02-12 | 19 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 13
2020-02-12 20:00 | 2020-02-12 | 20 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 14
2020-02-12 21:00 | 2020-02-12 | 21 | 5.2027 | 0.01807% | 7.757 | 8.0439 | 8.3413 | 8.6498 | 8.9696 | 2.02 | 2.3069 | 2.6043 | 2.9128 | 3.2326 | 15
2020-02-12 22:00 | 2020-02-12 | 22 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 16
2020-02-12 23:00 | 2020-02-12 | 23 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 17
2020-02-13 | 2020-02-12 | 0 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 18 | 18
2020-02-13 01:00 | 2020-02-13 | 1 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-02-13 02:00 | 2020-02-13 | 2 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-02-13 03:00 | 2020-02-13 | 3 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-02-13 04:00 | 2020-02-13 | 4 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-02-13 05:00 | 2020-02-13 | 5 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-02-13 06:00 | 2020-02-13 | 6 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-13 07:00 | 2020-02-13 | 7 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 1
2020-02-13 08:00 | 2020-02-13 | 8 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 2
2020-02-13 09:00 | 2020-02-13 | 9 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 3
2020-02-13 10:00 | 2020-02-13 | 10 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 4
2020-02-13 11:00 | 2020-02-13 | 11 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 5
2020-02-13 12:00 | 2020-02-13 | 12 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 6
2020-02-13 13:00 | 2020-02-13 | 13 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 7
2020-02-13 14:00 | 2020-02-13 | 14 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 8
2020-02-13 15:00 | 2020-02-13 | 15 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 9
2020-02-13 16:00 | 2020-02-13 | 16 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 10
2020-02-13 17:00 | 2020-02-13 | 17 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 11
2020-02-13 18:00 | 2020-02-13 | 18 | 5.2102 | 0.01809% | 7.7682 | 8.0555 | 8.3534 | 8.6623 | 8.9826 | 2.0312 | 2.3185 | 2.6164 | 2.9253 | 3.2456 | 12
2020-02-13 19:00 | 2020-02-13 | 19 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 13
2020-02-13 20:00 | 2020-02-13 | 20 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 14
2020-02-13 21:00 | 2020-02-13 | 21 | 5.3683 | 0.01864% | 8.004 | 8.3 | 8.6069 | 8.9252 | 9.2552 | 2.267 | 2.563 | 2.8699 | 3.1882 | 3.5182 | 15
2020-02-13 22:00 | 2020-02-13 | 22 | 5.2102 | 0.01809% | 7.7682 | 8.0555 | 8.3534 | 8.6623 | 8.9826 | 2.0312 | 2.3185 | 2.6164 | 2.9253 | 3.2456 | 16
2020-02-13 23:00 | 2020-02-13 | 23 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 17
2020-02-14 | 2020-02-13 | 0 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 18
2020-02-14 01:00 | 2020-02-14 | 1 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 19
2020-02-14 02:00 | 2020-02-14 | 2 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 20
2020-02-14 03:00 | 2020-02-14 | 3 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 21
2020-02-14 04:00 | 2020-02-14 | 4 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 22
2020-02-14 05:00 | 2020-02-14 | 5 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 23
2020-02-14 06:00 | 2020-02-14 | 6 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 24
2020-02-14 07:00 | 2020-02-14 | 7 | 4.9166 | 0.01707% | 7.3304 | 7.6015 | 7.8826 | 8.1741 | 8.4764 | 1.5934 | 1.8645 | 2.1456 | 2.4371 | 2.7394 | 25
2020-02-14 08:00 | 2020-02-14 | 8 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 26
2020-02-14 09:00 | 2020-02-14 | 9 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 27
2020-02-14 10:00 | 2020-02-14 | 10 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 28
2020-02-14 11:00 | 2020-02-14 | 11 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 29
2020-02-14 12:00 | 2020-02-14 | 12 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 30
2020-02-14 13:00 | 2020-02-14 | 13 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 31
2020-02-14 14:00 | 2020-02-14 | 14 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 32
2020-02-14 15:00 | 2020-02-14 | 15 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 33
2020-02-14 16:00 | 2020-02-14 | 16 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 34
2020-02-14 17:00 | 2020-02-14 | 17 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 35
2020-02-14 18:00 | 2020-02-14 | 18 | 5.406 | 0.01877% | 8.0601 | 8.3582 | 8.6672 | 8.9877 | 9.3201 | 2.3231 | 2.6212 | 2.9302 | 3.2507 | 3.5831 | 36
2020-02-14 19:00 | 2020-02-14 | 19 | 5.534 | 0.01922% | 8.251 | 8.5561 | 8.8725 | 9.2005 | 9.5408 | 2.514 | 2.8191 | 3.1355 | 3.4635 | 3.8038 | 37
2020-02-14 20:00 | 2020-02-14 | 20 | 5.549 | 0.01927% | 8.2734 | 8.5793 | 8.8966 | 9.2256 | 9.5667 | 2.5364 | 2.8423 | 3.1596 | 3.4886 | 3.8297 | 38
2020-02-14 21:00 | 2020-02-14 | 21 | 5.3156 | 0.01846% | 7.9254 | 8.2185 | 8.5224 | 8.8375 | 9.1643 | 2.1884 | 2.4815 | 2.7854 | 3.1005 | 3.4273 | 39
2020-02-14 22:00 | 2020-02-14 | 22 | 5.2479 | 0.01822% | 7.8244 | 8.1137 | 8.4137 | 8.7249 | 9.0475 | 2.0874 | 2.3767 | 2.6767 | 2.9879 | 3.3105 | 40
2020-02-14 23:00 | 2020-02-14 | 23 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 41
2020-02-15 | 2020-02-14 | 0 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 42
2020-02-15 01:00 | 2020-02-15 | 1 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 43
2020-02-15 02:00 | 2020-02-15 | 2 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 44
2020-02-15 03:00 | 2020-02-15 | 3 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 45
2020-02-15 04:00 | 2020-02-15 | 4 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 46
2020-02-15 05:00 | 2020-02-15 | 5 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 47
2020-02-15 06:00 | 2020-02-15 | 6 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 48
2020-02-15 07:00 | 2020-02-15 | 7 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 49
2020-02-15 08:00 | 2020-02-15 | 8 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 50
2020-02-15 09:00 | 2020-02-15 | 9 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 51
2020-02-15 10:00 | 2020-02-15 | 10 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 52
2020-02-15 11:00 | 2020-02-15 | 11 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 53
2020-02-15 12:00 | 2020-02-15 | 12 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 54
2020-02-15 13:00 | 2020-02-15 | 13 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 55
2020-02-15 14:00 | 2020-02-15 | 14 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 56
2020-02-15 15:00 | 2020-02-15 | 15 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 57
2020-02-15 16:00 | 2020-02-15 | 16 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 58
2020-02-15 17:00 | 2020-02-15 | 17 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 59
2020-02-15 18:00 | 2020-02-15 | 18 | 5.2629 | 0.01827% | 7.8468 | 8.137 | 8.4379 | 8.7499 | 9.0735 | 2.1098 | 2.4 | 2.7009 | 3.0129 | 3.3365 | 60
2020-02-15 19:00 | 2020-02-15 | 19 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 61
2020-02-15 20:00 | 2020-02-15 | 20 | 5.0822 | 0.01765% | 7.5774 | 7.8576 | 8.1482 | 8.4495 | 8.7619 | 1.8404 | 2.1206 | 2.4112 | 2.7125 | 3.0249 | 62
2020-02-15 21:00 | 2020-02-15 | 21 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 63
2020-02-15 22:00 | 2020-02-15 | 22 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 64
2020-02-15 23:00 | 2020-02-15 | 23 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 65
2020-02-16 | 2020-02-15 | 0 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 66 | 66
2020-02-16 01:00 | 2020-02-16 | 1 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-02-16 02:00 | 2020-02-16 | 2 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-02-16 03:00 | 2020-02-16 | 3 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-02-16 04:00 | 2020-02-16 | 4 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-02-16 05:00 | 2020-02-16 | 5 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-02-16 06:00 | 2020-02-16 | 6 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-02-16 07:00 | 2020-02-16 | 7 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-02-16 08:00 | 2020-02-16 | 8 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-02-16 09:00 | 2020-02-16 | 9 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 1
2020-02-16 10:00 | 2020-02-16 | 10 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 2
2020-02-16 11:00 | 2020-02-16 | 11 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 3
2020-02-16 12:00 | 2020-02-16 | 12 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 4
2020-02-16 13:00 | 2020-02-16 | 13 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 5
2020-02-16 14:00 | 2020-02-16 | 14 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 6
2020-02-16 15:00 | 2020-02-16 | 15 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 7
2020-02-16 16:00 | 2020-02-16 | 16 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 8
2020-02-16 17:00 | 2020-02-16 | 17 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 9
2020-02-16 18:00 | 2020-02-16 | 18 | 4.9316 | 0.01712% | 7.3529 | 7.6248 | 7.9067 | 8.1991 | 8.5023 | 1.6159 | 1.8878 | 2.1697 | 2.4621 | 2.7653 | 10
2020-02-16 19:00 | 2020-02-16 | 19 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 11
2020-02-16 20:00 | 2020-02-16 | 20 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 12
2020-02-16 21:00 | 2020-02-16 | 21 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 13
2020-02-16 22:00 | 2020-02-16 | 22 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 14
2020-02-16 23:00 | 2020-02-16 | 23 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 15
2020-02-17 | 2020-02-16 | 0 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 16 | 16
2020-02-17 01:00 | 2020-02-17 | 1 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-17 02:00 | 2020-02-17 | 2 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-02-17 03:00 | 2020-02-17 | 3 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-02-17 04:00 | 2020-02-17 | 4 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-02-17 05:00 | 2020-02-17 | 5 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-02-17 06:00 | 2020-02-17 | 6 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-02-17 07:00 | 2020-02-17 | 7 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-02-17 08:00 | 2020-02-17 | 8 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-02-17 09:00 | 2020-02-17 | 9 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-02-17 10:00 | 2020-02-17 | 10 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1
2020-02-17 11:00 | 2020-02-17 | 11 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 2
2020-02-17 12:00 | 2020-02-17 | 12 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 3
2020-02-17 13:00 | 2020-02-17 | 13 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 4
2020-02-17 14:00 | 2020-02-17 | 14 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 5
2020-02-17 15:00 | 2020-02-17 | 15 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 6
2020-02-17 16:00 | 2020-02-17 | 16 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 7
2020-02-17 17:00 | 2020-02-17 | 17 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 8
2020-02-17 18:00 | 2020-02-17 | 18 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 9
2020-02-17 19:00 | 2020-02-17 | 19 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 10
2020-02-17 20:00 | 2020-02-17 | 20 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 11
2020-02-17 21:00 | 2020-02-17 | 21 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 12
2020-02-17 22:00 | 2020-02-17 | 22 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 13
2020-02-17 23:00 | 2020-02-17 | 23 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 14 | 14
2020-02-18 | 2020-02-17 | 0 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-02-18 01:00 | 2020-02-18 | 1 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-02-18 02:00 | 2020-02-18 | 2 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-18 03:00 | 2020-02-18 | 3 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-02-18 04:00 | 2020-02-18 | 4 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-02-18 05:00 | 2020-02-18 | 5 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-02-18 06:00 | 2020-02-18 | 6 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 1
2020-02-18 07:00 | 2020-02-18 | 7 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 2
2020-02-18 08:00 | 2020-02-18 | 8 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 3
2020-02-18 09:00 | 2020-02-18 | 9 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 4
2020-02-18 10:00 | 2020-02-18 | 10 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 5
2020-02-18 11:00 | 2020-02-18 | 11 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 6
2020-02-18 12:00 | 2020-02-18 | 12 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 7
2020-02-18 13:00 | 2020-02-18 | 13 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 8
2020-02-18 14:00 | 2020-02-18 | 14 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 9
2020-02-18 15:00 | 2020-02-18 | 15 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 10
2020-02-18 16:00 | 2020-02-18 | 16 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 11
2020-02-18 17:00 | 2020-02-18 | 17 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 12
2020-02-18 18:00 | 2020-02-18 | 18 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 13
2020-02-18 19:00 | 2020-02-18 | 19 | 5.1801 | 0.01799% | 7.7233 | 8.0089 | 8.3051 | 8.6122 | 8.9307 | 1.9863 | 2.2719 | 2.5681 | 2.8752 | 3.1937 | 14
2020-02-18 20:00 | 2020-02-18 | 20 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 15
2020-02-18 21:00 | 2020-02-18 | 21 | 5.0672 | 0.0176% | 7.555 | 7.8343 | 8.124 | 8.4244 | 8.736 | 1.818 | 2.0973 | 2.387 | 2.6874 | 2.999 | 16
2020-02-18 22:00 | 2020-02-18 | 22 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 17
2020-02-18 23:00 | 2020-02-18 | 23 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 18
2020-02-19 | 2020-02-18 | 0 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 19 | 19
2020-02-19 01:00 | 2020-02-19 | 1 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-02-19 02:00 | 2020-02-19 | 2 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-02-19 03:00 | 2020-02-19 | 3 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-02-19 04:00 | 2020-02-19 | 4 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-02-19 05:00 | 2020-02-19 | 5 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-19 06:00 | 2020-02-19 | 6 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-02-19 07:00 | 2020-02-19 | 7 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 1
2020-02-19 08:00 | 2020-02-19 | 8 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 2
2020-02-19 09:00 | 2020-02-19 | 9 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 3
2020-02-19 10:00 | 2020-02-19 | 10 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 4
2020-02-19 11:00 | 2020-02-19 | 11 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 5
2020-02-19 12:00 | 2020-02-19 | 12 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 6
2020-02-19 13:00 | 2020-02-19 | 13 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 7
2020-02-19 14:00 | 2020-02-19 | 14 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 8
2020-02-19 15:00 | 2020-02-19 | 15 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 9
2020-02-19 16:00 | 2020-02-19 | 16 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 10
2020-02-19 17:00 | 2020-02-19 | 17 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 11
2020-02-19 18:00 | 2020-02-19 | 18 | 5.1801 | 0.01799% | 7.7233 | 8.0089 | 8.3051 | 8.6122 | 8.9307 | 1.9863 | 2.2719 | 2.5681 | 2.8752 | 3.1937 | 12
2020-02-19 19:00 | 2020-02-19 | 19 | 5.4512 | 0.01893% | 8.1275 | 8.428 | 8.7397 | 9.0628 | 9.398 | 2.3905 | 2.691 | 3.0027 | 3.3258 | 3.661 | 13
2020-02-19 20:00 | 2020-02-19 | 20 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 14
2020-02-19 21:00 | 2020-02-19 | 21 | 5.3081 | 0.01843% | 7.9142 | 8.2068 | 8.5103 | 8.825 | 9.1513 | 2.1772 | 2.4698 | 2.7733 | 3.088 | 3.4143 | 15
2020-02-19 22:00 | 2020-02-19 | 22 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 16
2020-02-19 23:00 | 2020-02-19 | 23 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 17
2020-02-20 | 2020-02-19 | 0 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 18
2020-02-20 01:00 | 2020-02-20 | 1 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 19 | 19
2020-02-20 02:00 | 2020-02-20 | 2 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-02-20 03:00 | 2020-02-20 | 3 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-02-20 04:00 | 2020-02-20 | 4 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-02-20 05:00 | 2020-02-20 | 5 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-02-20 06:00 | 2020-02-20 | 6 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 1
2020-02-20 07:00 | 2020-02-20 | 7 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 2
2020-02-20 08:00 | 2020-02-20 | 8 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 3
2020-02-20 09:00 | 2020-02-20 | 9 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 4
2020-02-20 10:00 | 2020-02-20 | 10 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 5
2020-02-20 11:00 | 2020-02-20 | 11 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 6
2020-02-20 12:00 | 2020-02-20 | 12 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 7
2020-02-20 13:00 | 2020-02-20 | 13 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 8
2020-02-20 14:00 | 2020-02-20 | 14 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 9
2020-02-20 15:00 | 2020-02-20 | 15 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 10
2020-02-20 16:00 | 2020-02-20 | 16 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 11
2020-02-20 17:00 | 2020-02-20 | 17 | 4.8187 | 0.01673% | 7.1845 | 7.4502 | 7.7257 | 8.0114 | 8.3076 | 1.4475 | 1.7132 | 1.9887 | 2.2744 | 2.5706 | 12
2020-02-20 18:00 | 2020-02-20 | 18 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 13
2020-02-20 19:00 | 2020-02-20 | 19 | 5.4135 | 0.0188% | 8.0713 | 8.3698 | 8.6793 | 9.0003 | 9.3331 | 2.3343 | 2.6328 | 2.9423 | 3.2633 | 3.5961 | 14
2020-02-20 20:00 | 2020-02-20 | 20 | 5.5114 | 0.01914% | 8.2173 | 8.5211 | 8.8362 | 9.163 | 9.5018 | 2.4803 | 2.7841 | 3.0992 | 3.426 | 3.7648 | 15
2020-02-20 21:00 | 2020-02-20 | 21 | 5.3759 | 0.01867% | 8.0152 | 8.3116 | 8.619 | 8.9377 | 9.2682 | 2.2782 | 2.5746 | 2.882 | 3.2007 | 3.5312 | 16
2020-02-20 22:00 | 2020-02-20 | 22 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 17
2020-02-20 23:00 | 2020-02-20 | 23 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 18
2020-02-21 | 2020-02-20 | 0 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 19
2020-02-21 01:00 | 2020-02-21 | 1 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 20
2020-02-21 02:00 | 2020-02-21 | 2 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 21
2020-02-21 03:00 | 2020-02-21 | 3 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 22
2020-02-21 04:00 | 2020-02-21 | 4 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 23
2020-02-21 05:00 | 2020-02-21 | 5 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 24
2020-02-21 06:00 | 2020-02-21 | 6 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 25
2020-02-21 07:00 | 2020-02-21 | 7 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 26
2020-02-21 08:00 | 2020-02-21 | 8 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 27
2020-02-21 09:00 | 2020-02-21 | 9 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 28
2020-02-21 10:00 | 2020-02-21 | 10 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 29
2020-02-21 11:00 | 2020-02-21 | 11 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 30
2020-02-21 12:00 | 2020-02-21 | 12 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 31
2020-02-21 13:00 | 2020-02-21 | 13 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 32
2020-02-21 14:00 | 2020-02-21 | 14 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 33
2020-02-21 15:00 | 2020-02-21 | 15 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 34
2020-02-21 16:00 | 2020-02-21 | 16 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 35
2020-02-21 17:00 | 2020-02-21 | 17 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 36
2020-02-21 18:00 | 2020-02-21 | 18 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 37
2020-02-21 19:00 | 2020-02-21 | 19 | 5.293 | 0.01838% | 7.8917 | 8.1836 | 8.4862 | 8.8 | 9.1254 | 2.1547 | 2.4466 | 2.7492 | 3.063 | 3.3884 | 38
2020-02-21 20:00 | 2020-02-21 | 20 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 39
2020-02-21 21:00 | 2020-02-21 | 21 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 40
2020-02-21 22:00 | 2020-02-21 | 22 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 41
2020-02-21 23:00 | 2020-02-21 | 23 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 42
2020-02-22 | 2020-02-21 | 0 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 43
2020-02-22 01:00 | 2020-02-22 | 1 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 44 | 44
2020-02-22 02:00 | 2020-02-22 | 2 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-02-22 03:00 | 2020-02-22 | 3 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-22 04:00 | 2020-02-22 | 4 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-02-22 05:00 | 2020-02-22 | 5 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-02-22 06:00 | 2020-02-22 | 6 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-02-22 07:00 | 2020-02-22 | 7 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 1
2020-02-22 08:00 | 2020-02-22 | 8 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 2
2020-02-22 09:00 | 2020-02-22 | 9 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 3
2020-02-22 10:00 | 2020-02-22 | 10 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 4
2020-02-22 11:00 | 2020-02-22 | 11 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 5
2020-02-22 12:00 | 2020-02-22 | 12 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 6
2020-02-22 13:00 | 2020-02-22 | 13 | 4.2314 | 0.01469% | 6.3089 | 6.5422 | 6.7841 | 7.035 | 7.2951 | 0.5719 | 0.80519 | 1.0471 | 1.298 | 1.5581 | 7
2020-02-22 14:00 | 2020-02-22 | 14 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 8
2020-02-22 15:00 | 2020-02-22 | 15 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 9
2020-02-22 16:00 | 2020-02-22 | 16 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 10
2020-02-22 17:00 | 2020-02-22 | 17 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 11
2020-02-22 18:00 | 2020-02-22 | 18 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 12
2020-02-22 19:00 | 2020-02-22 | 19 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 13
2020-02-22 20:00 | 2020-02-22 | 20 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 14
2020-02-22 21:00 | 2020-02-22 | 21 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 15
2020-02-22 22:00 | 2020-02-22 | 22 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 16
2020-02-22 23:00 | 2020-02-22 | 23 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 17
2020-02-23 | 2020-02-22 | 0 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 18 | 18
2020-02-23 01:00 | 2020-02-23 | 1 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-23 02:00 | 2020-02-23 | 2 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-02-23 03:00 | 2020-02-23 | 3 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-02-23 04:00 | 2020-02-23 | 4 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-02-23 05:00 | 2020-02-23 | 5 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-02-23 06:00 | 2020-02-23 | 6 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-02-23 07:00 | 2020-02-23 | 7 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-02-23 08:00 | 2020-02-23 | 8 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-02-23 09:00 | 2020-02-23 | 9 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-02-23 10:00 | 2020-02-23 | 10 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 2
2020-02-23 11:00 | 2020-02-23 | 11 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 3
2020-02-23 12:00 | 2020-02-23 | 12 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 4
2020-02-23 13:00 | 2020-02-23 | 13 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 5
2020-02-23 14:00 | 2020-02-23 | 14 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 6
2020-02-23 15:00 | 2020-02-23 | 15 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 7
2020-02-23 16:00 | 2020-02-23 | 16 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 8
2020-02-23 17:00 | 2020-02-23 | 17 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 9
2020-02-23 18:00 | 2020-02-23 | 18 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 10
2020-02-23 19:00 | 2020-02-23 | 19 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 11
2020-02-23 20:00 | 2020-02-23 | 20 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 12
2020-02-23 21:00 | 2020-02-23 | 21 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 13
2020-02-23 22:00 | 2020-02-23 | 22 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 14
2020-02-23 23:00 | 2020-02-23 | 23 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 15 | 15
2020-02-24 | 2020-02-23 | 0 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-02-24 01:00 | 2020-02-24 | 1 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-02-24 02:00 | 2020-02-24 | 2 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-02-24 03:00 | 2020-02-24 | 3 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-02-24 04:00 | 2020-02-24 | 4 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-02-24 05:00 | 2020-02-24 | 5 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-02-24 06:00 | 2020-02-24 | 6 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-02-24 07:00 | 2020-02-24 | 7 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 1
2020-02-24 08:00 | 2020-02-24 | 8 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 2
2020-02-24 09:00 | 2020-02-24 | 9 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 3
2020-02-24 10:00 | 2020-02-24 | 10 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 4
2020-02-24 11:00 | 2020-02-24 | 11 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 5
2020-02-24 12:00 | 2020-02-24 | 12 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 6
2020-02-24 13:00 | 2020-02-24 | 13 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 7
2020-02-24 14:00 | 2020-02-24 | 14 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 8
2020-02-24 15:00 | 2020-02-24 | 15 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 9
2020-02-24 16:00 | 2020-02-24 | 16 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 10
2020-02-24 17:00 | 2020-02-24 | 17 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 11
2020-02-24 18:00 | 2020-02-24 | 18 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 12
2020-02-24 19:00 | 2020-02-24 | 19 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 13
2020-02-24 20:00 | 2020-02-24 | 20 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 14
2020-02-24 21:00 | 2020-02-24 | 21 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 15
2020-02-24 22:00 | 2020-02-24 | 22 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 16
2020-02-24 23:00 | 2020-02-24 | 23 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 17 | 17
2020-02-25 | 2020-02-24 | 0 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-02-25 01:00 | 2020-02-25 | 1 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-02-25 02:00 | 2020-02-25 | 2 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-02-25 03:00 | 2020-02-25 | 3 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-02-25 04:00 | 2020-02-25 | 4 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-02-25 05:00 | 2020-02-25 | 5 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-02-25 06:00 | 2020-02-25 | 6 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-02-25 07:00 | 2020-02-25 | 7 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-02-25 08:00 | 2020-02-25 | 8 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 2
2020-02-25 09:00 | 2020-02-25 | 9 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 3
2020-02-25 10:00 | 2020-02-25 | 10 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 4
2020-02-25 11:00 | 2020-02-25 | 11 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 5
2020-02-25 12:00 | 2020-02-25 | 12 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 6
2020-02-25 13:00 | 2020-02-25 | 13 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 7
2020-02-25 14:00 | 2020-02-25 | 14 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 8
2020-02-25 15:00 | 2020-02-25 | 15 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 9
2020-02-25 16:00 | 2020-02-25 | 16 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 10
2020-02-25 17:00 | 2020-02-25 | 17 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 11
2020-02-25 18:00 | 2020-02-25 | 18 | 4.9618 | 0.01723% | 7.3978 | 7.6714 | 7.955 | 8.2492 | 8.5542 | 1.6608 | 1.9344 | 2.218 | 2.5122 | 2.8172 | 12
2020-02-25 19:00 | 2020-02-25 | 19 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 13
2020-02-25 20:00 | 2020-02-25 | 20 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 14
2020-02-25 21:00 | 2020-02-25 | 21 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 15
2020-02-25 22:00 | 2020-02-25 | 22 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 16
2020-02-25 23:00 | 2020-02-25 | 23 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 17 | 17
2020-02-26 | 2020-02-25 | 0 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-26 01:00 | 2020-02-26 | 1 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-02-26 02:00 | 2020-02-26 | 2 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-02-26 03:00 | 2020-02-26 | 3 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-02-26 04:00 | 2020-02-26 | 4 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-02-26 05:00 | 2020-02-26 | 5 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-02-26 06:00 | 2020-02-26 | 6 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-02-26 07:00 | 2020-02-26 | 7 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 1
2020-02-26 08:00 | 2020-02-26 | 8 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 2
2020-02-26 09:00 | 2020-02-26 | 9 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 3
2020-02-26 10:00 | 2020-02-26 | 10 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 4
2020-02-26 11:00 | 2020-02-26 | 11 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 5
2020-02-26 12:00 | 2020-02-26 | 12 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 6
2020-02-26 13:00 | 2020-02-26 | 13 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 7
2020-02-26 14:00 | 2020-02-26 | 14 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 8
2020-02-26 15:00 | 2020-02-26 | 15 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 9
2020-02-26 16:00 | 2020-02-26 | 16 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 10
2020-02-26 17:00 | 2020-02-26 | 17 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 11
2020-02-26 18:00 | 2020-02-26 | 18 | 5.278 | 0.01833% | 7.8693 | 8.1603 | 8.462 | 8.7749 | 9.0994 | 2.1323 | 2.4233 | 2.725 | 3.0379 | 3.3624 | 12
2020-02-26 19:00 | 2020-02-26 | 19 | 5.3382 | 0.01854% | 7.9591 | 8.2534 | 8.5586 | 8.8751 | 9.2033 | 2.2221 | 2.5164 | 2.8216 | 3.1381 | 3.4663 | 13
2020-02-26 20:00 | 2020-02-26 | 20 | 5.15 | 0.01788% | 7.6784 | 7.9624 | 8.2568 | 8.5621 | 8.8788 | 1.9414 | 2.2254 | 2.5198 | 2.8251 | 3.1418 | 14
2020-02-26 21:00 | 2020-02-26 | 21 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 15
2020-02-26 22:00 | 2020-02-26 | 22 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 16
2020-02-26 23:00 | 2020-02-26 | 23 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 17 | 17
2020-02-27 | 2020-02-26 | 0 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-02-27 01:00 | 2020-02-27 | 1 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-02-27 02:00 | 2020-02-27 | 2 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-02-27 03:00 | 2020-02-27 | 3 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-02-27 04:00 | 2020-02-27 | 4 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-02-27 05:00 | 2020-02-27 | 5 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-02-27 06:00 | 2020-02-27 | 6 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-02-27 07:00 | 2020-02-27 | 7 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 1
2020-02-27 08:00 | 2020-02-27 | 8 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 2
2020-02-27 09:00 | 2020-02-27 | 9 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 3
2020-02-27 10:00 | 2020-02-27 | 10 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 4
2020-02-27 11:00 | 2020-02-27 | 11 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 5
2020-02-27 12:00 | 2020-02-27 | 12 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 6
2020-02-27 13:00 | 2020-02-27 | 13 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 7
2020-02-27 14:00 | 2020-02-27 | 14 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 8
2020-02-27 15:00 | 2020-02-27 | 15 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 9
2020-02-27 16:00 | 2020-02-27 | 16 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 10
2020-02-27 17:00 | 2020-02-27 | 17 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 11
2020-02-27 18:00 | 2020-02-27 | 18 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 12
2020-02-27 19:00 | 2020-02-27 | 19 | 5.3608 | 0.01861% | 7.9928 | 8.2883 | 8.5948 | 8.9126 | 9.2422 | 2.2558 | 2.5513 | 2.8578 | 3.1756 | 3.5052 | 13
2020-02-27 20:00 | 2020-02-27 | 20 | 5.3985 | 0.01875% | 8.0489 | 8.3465 | 8.6552 | 8.9752 | 9.3071 | 2.3119 | 2.6095 | 2.9182 | 3.2382 | 3.5701 | 14
2020-02-27 21:00 | 2020-02-27 | 21 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 15
2020-02-27 22:00 | 2020-02-27 | 22 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 16
2020-02-27 23:00 | 2020-02-27 | 23 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 17
2020-02-28 | 2020-02-27 | 0 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 18
2020-02-28 01:00 | 2020-02-28 | 1 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 19 | 19
2020-02-28 02:00 | 2020-02-28 | 2 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-02-28 03:00 | 2020-02-28 | 3 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-02-28 04:00 | 2020-02-28 | 4 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-02-28 05:00 | 2020-02-28 | 5 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-02-28 06:00 | 2020-02-28 | 6 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-02-28 07:00 | 2020-02-28 | 7 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 2
2020-02-28 08:00 | 2020-02-28 | 8 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 3
2020-02-28 09:00 | 2020-02-28 | 9 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 4
2020-02-28 10:00 | 2020-02-28 | 10 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 5
2020-02-28 11:00 | 2020-02-28 | 11 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 6
2020-02-28 12:00 | 2020-02-28 | 12 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 7
2020-02-28 13:00 | 2020-02-28 | 13 | 4.6606 | 0.01618% | 6.9488 | 7.2057 | 7.4722 | 7.7485 | 8.035 | 1.2118 | 1.4687 | 1.7352 | 2.0115 | 2.298 | 8
2020-02-28 14:00 | 2020-02-28 | 14 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 9
2020-02-28 15:00 | 2020-02-28 | 15 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 10
2020-02-28 16:00 | 2020-02-28 | 16 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 11
2020-02-28 17:00 | 2020-02-28 | 17 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 12
2020-02-28 18:00 | 2020-02-28 | 18 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 13
2020-02-28 19:00 | 2020-02-28 | 19 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 14
2020-02-28 20:00 | 2020-02-28 | 20 | 5.1876 | 0.01801% | 7.7346 | 8.0206 | 8.3172 | 8.6247 | 8.9437 | 1.9976 | 2.2836 | 2.5802 | 2.8877 | 3.2067 | 15
2020-02-28 21:00 | 2020-02-28 | 21 | 5.1349 | 0.01783% | 7.656 | 7.9391 | 8.2327 | 8.5371 | 8.8528 | 1.919 | 2.2021 | 2.4957 | 2.8001 | 3.1158 | 16
2020-02-28 22:00 | 2020-02-28 | 22 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 17
2020-02-28 23:00 | 2020-02-28 | 23 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 18
2020-02-29 | 2020-02-28 | 0 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 19
2020-02-29 01:00 | 2020-02-29 | 1 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 20
2020-02-29 02:00 | 2020-02-29 | 2 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 21 | 21
2020-02-29 03:00 | 2020-02-29 | 3 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-02-29 04:00 | 2020-02-29 | 4 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-02-29 05:00 | 2020-02-29 | 5 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-02-29 06:00 | 2020-02-29 | 6 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-02-29 07:00 | 2020-02-29 | 7 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 1
2020-02-29 08:00 | 2020-02-29 | 8 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 2
2020-02-29 09:00 | 2020-02-29 | 9 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 3
2020-02-29 10:00 | 2020-02-29 | 10 | 4.8187 | 0.01673% | 7.1845 | 7.4502 | 7.7257 | 8.0114 | 8.3076 | 1.4475 | 1.7132 | 1.9887 | 2.2744 | 2.5706 | 4
2020-02-29 11:00 | 2020-02-29 | 11 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 5
2020-02-29 12:00 | 2020-02-29 | 12 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 6
2020-02-29 13:00 | 2020-02-29 | 13 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 7
2020-02-29 14:00 | 2020-02-29 | 14 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 8
2020-02-29 15:00 | 2020-02-29 | 15 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 9
2020-02-29 16:00 | 2020-02-29 | 16 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 10
2020-02-29 17:00 | 2020-02-29 | 17 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 11
2020-02-29 18:00 | 2020-02-29 | 18 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 12
2020-02-29 19:00 | 2020-02-29 | 19 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 13
2020-02-29 20:00 | 2020-02-29 | 20 | 5.3006 | 0.01841% | 7.903 | 8.1952 | 8.4982 | 8.8125 | 9.1384 | 2.166 | 2.4582 | 2.7612 | 3.0755 | 3.4014 | 14
2020-02-29 21:00 | 2020-02-29 | 21 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 15
2020-02-29 22:00 | 2020-02-29 | 22 | 4.9166 | 0.01707% | 7.3304 | 7.6015 | 7.8826 | 8.1741 | 8.4764 | 1.5934 | 1.8645 | 2.1456 | 2.4371 | 2.7394 | 16
2020-02-29 23:00 | 2020-02-29 | 23 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 17
2020-03-01 | 2020-02-29 | 0 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 18
2020-03-01 01:00 | 2020-03-01 | 1 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 19
2020-03-01 02:00 | 2020-03-01 | 2 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 20 | 20
2020-03-01 03:00 | 2020-03-01 | 3 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-03-01 04:00 | 2020-03-01 | 4 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-03-01 05:00 | 2020-03-01 | 5 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-03-01 06:00 | 2020-03-01 | 6 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1
2020-03-01 07:00 | 2020-03-01 | 7 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 2
2020-03-01 08:00 | 2020-03-01 | 8 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 3
2020-03-01 09:00 | 2020-03-01 | 9 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 4
2020-03-01 10:00 | 2020-03-01 | 10 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 5
2020-03-01 11:00 | 2020-03-01 | 11 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 6
2020-03-01 12:00 | 2020-03-01 | 12 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 7
2020-03-01 13:00 | 2020-03-01 | 13 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 8
2020-03-01 14:00 | 2020-03-01 | 14 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 9
2020-03-01 15:00 | 2020-03-01 | 15 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 10
2020-03-01 16:00 | 2020-03-01 | 16 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 11
2020-03-01 17:00 | 2020-03-01 | 17 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 12
2020-03-01 18:00 | 2020-03-01 | 18 | 5.1801 | 0.01799% | 7.7233 | 8.0089 | 8.3051 | 8.6122 | 8.9307 | 1.9863 | 2.2719 | 2.5681 | 2.8752 | 3.1937 | 13
2020-03-01 19:00 | 2020-03-01 | 19 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 14
2020-03-01 20:00 | 2020-03-01 | 20 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 15
2020-03-01 21:00 | 2020-03-01 | 21 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 16
2020-03-01 22:00 | 2020-03-01 | 22 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 17
2020-03-01 23:00 | 2020-03-01 | 23 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 18
2020-03-02 | 2020-03-01 | 0 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 19 | 19
2020-03-02 01:00 | 2020-03-02 | 1 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-03-02 02:00 | 2020-03-02 | 2 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-03-02 03:00 | 2020-03-02 | 3 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-03-02 04:00 | 2020-03-02 | 4 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-03-02 05:00 | 2020-03-02 | 5 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-03-02 06:00 | 2020-03-02 | 6 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-03-02 07:00 | 2020-03-02 | 7 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 1
2020-03-02 08:00 | 2020-03-02 | 8 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 2
2020-03-02 09:00 | 2020-03-02 | 9 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 3
2020-03-02 10:00 | 2020-03-02 | 10 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 4
2020-03-02 11:00 | 2020-03-02 | 11 | 4.5702 | 0.01587% | 6.8141 | 7.066 | 7.3273 | 7.5983 | 7.8792 | 1.0771 | 1.329 | 1.5903 | 1.8613 | 2.1422 | 5
2020-03-02 12:00 | 2020-03-02 | 12 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 6
2020-03-02 13:00 | 2020-03-02 | 13 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 7
2020-03-02 14:00 | 2020-03-02 | 14 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 8
2020-03-02 15:00 | 2020-03-02 | 15 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 9
2020-03-02 16:00 | 2020-03-02 | 16 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 10
2020-03-02 17:00 | 2020-03-02 | 17 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 11
2020-03-02 18:00 | 2020-03-02 | 18 | 5.0672 | 0.0176% | 7.555 | 7.8343 | 8.124 | 8.4244 | 8.736 | 1.818 | 2.0973 | 2.387 | 2.6874 | 2.999 | 12
2020-03-02 19:00 | 2020-03-02 | 19 | 5.0672 | 0.0176% | 7.555 | 7.8343 | 8.124 | 8.4244 | 8.736 | 1.818 | 2.0973 | 2.387 | 2.6874 | 2.999 | 13
2020-03-02 20:00 | 2020-03-02 | 20 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 14
2020-03-02 21:00 | 2020-03-02 | 21 | 4.9392 | 0.01715% | 7.3641 | 7.6364 | 7.9188 | 8.2116 | 8.5153 | 1.6271 | 1.8994 | 2.1818 | 2.4746 | 2.7783 | 15
2020-03-02 22:00 | 2020-03-02 | 22 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 16
2020-03-02 23:00 | 2020-03-02 | 23 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 17
2020-03-03 | 2020-03-02 | 0 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 18 | 18
2020-03-03 01:00 | 2020-03-03 | 1 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-03-03 02:00 | 2020-03-03 | 2 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-03 03:00 | 2020-03-03 | 3 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-03-03 04:00 | 2020-03-03 | 4 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-03-03 05:00 | 2020-03-03 | 5 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-03-03 06:00 | 2020-03-03 | 6 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-03-03 07:00 | 2020-03-03 | 7 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 1
2020-03-03 08:00 | 2020-03-03 | 8 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 2
2020-03-03 09:00 | 2020-03-03 | 9 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 3
2020-03-03 10:00 | 2020-03-03 | 10 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 4
2020-03-03 11:00 | 2020-03-03 | 11 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 5
2020-03-03 12:00 | 2020-03-03 | 12 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 6
2020-03-03 13:00 | 2020-03-03 | 13 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 7
2020-03-03 14:00 | 2020-03-03 | 14 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 8
2020-03-03 15:00 | 2020-03-03 | 15 | 4.6681 | 0.01621% | 6.96 | 7.2174 | 7.4842 | 7.761 | 8.048 | 1.223 | 1.4804 | 1.7472 | 2.024 | 2.311 | 9
2020-03-03 16:00 | 2020-03-03 | 16 | 4.6681 | 0.01621% | 6.96 | 7.2174 | 7.4842 | 7.761 | 8.048 | 1.223 | 1.4804 | 1.7472 | 2.024 | 2.311 | 10
2020-03-03 17:00 | 2020-03-03 | 17 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 11
2020-03-03 18:00 | 2020-03-03 | 18 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 12
2020-03-03 19:00 | 2020-03-03 | 19 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 13
2020-03-03 20:00 | 2020-03-03 | 20 | 4.9843 | 0.01731% | 7.4315 | 7.7063 | 7.9912 | 8.2867 | 8.5932 | 1.6945 | 1.9693 | 2.2542 | 2.5497 | 2.8562 | 14
2020-03-03 21:00 | 2020-03-03 | 21 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 15
2020-03-03 22:00 | 2020-03-03 | 22 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 16
2020-03-03 23:00 | 2020-03-03 | 23 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 17 | 17
2020-03-04 | 2020-03-03 | 0 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-03-04 01:00 | 2020-03-04 | 1 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-03-04 02:00 | 2020-03-04 | 2 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-03-04 03:00 | 2020-03-04 | 3 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-03-04 04:00 | 2020-03-04 | 4 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-03-04 05:00 | 2020-03-04 | 5 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-03-04 06:00 | 2020-03-04 | 6 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-03-04 07:00 | 2020-03-04 | 7 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 1
2020-03-04 08:00 | 2020-03-04 | 8 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 2
2020-03-04 09:00 | 2020-03-04 | 9 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 3
2020-03-04 10:00 | 2020-03-04 | 10 | 4.2314 | 0.01469% | 6.3089 | 6.5422 | 6.7841 | 7.035 | 7.2951 | 0.5719 | 0.80519 | 1.0471 | 1.298 | 1.5581 | 4
2020-03-04 11:00 | 2020-03-04 | 11 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 5
2020-03-04 12:00 | 2020-03-04 | 12 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 6
2020-03-04 13:00 | 2020-03-04 | 13 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 7
2020-03-04 14:00 | 2020-03-04 | 14 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 8
2020-03-04 15:00 | 2020-03-04 | 15 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 9
2020-03-04 16:00 | 2020-03-04 | 16 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 10
2020-03-04 17:00 | 2020-03-04 | 17 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 11
2020-03-04 18:00 | 2020-03-04 | 18 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 12
2020-03-04 19:00 | 2020-03-04 | 19 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 13
2020-03-04 20:00 | 2020-03-04 | 20 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 14
2020-03-04 21:00 | 2020-03-04 | 21 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 15
2020-03-04 22:00 | 2020-03-04 | 22 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 16
2020-03-04 23:00 | 2020-03-04 | 23 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 17 | 17
2020-03-05 | 2020-03-04 | 0 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-03-05 01:00 | 2020-03-05 | 1 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-03-05 02:00 | 2020-03-05 | 2 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-03-05 03:00 | 2020-03-05 | 3 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-03-05 04:00 | 2020-03-05 | 4 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-03-05 05:00 | 2020-03-05 | 5 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-03-05 06:00 | 2020-03-05 | 6 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-03-05 07:00 | 2020-03-05 | 7 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 1
2020-03-05 08:00 | 2020-03-05 | 8 | 4.2314 | 0.01469% | 6.3089 | 6.5422 | 6.7841 | 7.035 | 7.2951 | 0.5719 | 0.80519 | 1.0471 | 1.298 | 1.5581 | 2
2020-03-05 09:00 | 2020-03-05 | 9 | 4.2239 | 0.01467% | 6.2977 | 6.5305 | 6.772 | 7.0225 | 7.2821 | 0.56067 | 0.79355 | 1.035 | 1.2855 | 1.5451 | 3
2020-03-05 10:00 | 2020-03-05 | 10 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 4
2020-03-05 11:00 | 2020-03-05 | 11 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 5
2020-03-05 12:00 | 2020-03-05 | 12 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 6
2020-03-05 13:00 | 2020-03-05 | 13 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 7
2020-03-05 14:00 | 2020-03-05 | 14 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 8
2020-03-05 15:00 | 2020-03-05 | 15 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 9
2020-03-05 16:00 | 2020-03-05 | 16 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 10
2020-03-05 17:00 | 2020-03-05 | 17 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 11
2020-03-05 18:00 | 2020-03-05 | 18 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 12
2020-03-05 19:00 | 2020-03-05 | 19 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 13
2020-03-05 20:00 | 2020-03-05 | 20 | 4.9618 | 0.01723% | 7.3978 | 7.6714 | 7.955 | 8.2492 | 8.5542 | 1.6608 | 1.9344 | 2.218 | 2.5122 | 2.8172 | 14
2020-03-05 21:00 | 2020-03-05 | 21 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 15
2020-03-05 22:00 | 2020-03-05 | 22 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 16
2020-03-05 23:00 | 2020-03-05 | 23 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 17
2020-03-06 | 2020-03-05 | 0 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 18 | 18
2020-03-06 01:00 | 2020-03-06 | 1 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-03-06 02:00 | 2020-03-06 | 2 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-06 03:00 | 2020-03-06 | 3 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-06 04:00 | 2020-03-06 | 4 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-03-06 05:00 | 2020-03-06 | 5 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-06 06:00 | 2020-03-06 | 6 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-03-06 07:00 | 2020-03-06 | 7 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 1
2020-03-06 08:00 | 2020-03-06 | 8 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 2
2020-03-06 09:00 | 2020-03-06 | 9 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 3
2020-03-06 10:00 | 2020-03-06 | 10 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 4
2020-03-06 11:00 | 2020-03-06 | 11 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 5
2020-03-06 12:00 | 2020-03-06 | 12 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 6
2020-03-06 13:00 | 2020-03-06 | 13 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 7
2020-03-06 14:00 | 2020-03-06 | 14 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 8
2020-03-06 15:00 | 2020-03-06 | 15 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 9
2020-03-06 16:00 | 2020-03-06 | 16 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 10
2020-03-06 17:00 | 2020-03-06 | 17 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 11
2020-03-06 18:00 | 2020-03-06 | 18 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 12
2020-03-06 19:00 | 2020-03-06 | 19 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 13
2020-03-06 20:00 | 2020-03-06 | 20 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 14
2020-03-06 21:00 | 2020-03-06 | 21 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 15
2020-03-06 22:00 | 2020-03-06 | 22 | 4.7811 | 0.0166% | 7.1284 | 7.392 | 7.6653 | 7.9488 | 8.2427 | 1.3914 | 1.655 | 1.9283 | 2.2118 | 2.5057 | 16
2020-03-06 23:00 | 2020-03-06 | 23 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 17
2020-03-07 | 2020-03-06 | 0 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 18 | 18
2020-03-07 01:00 | 2020-03-07 | 1 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-03-07 02:00 | 2020-03-07 | 2 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-03-07 03:00 | 2020-03-07 | 3 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-03-07 04:00 | 2020-03-07 | 4 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-03-07 05:00 | 2020-03-07 | 5 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-03-07 06:00 | 2020-03-07 | 6 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-03-07 07:00 | 2020-03-07 | 7 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-03-07 08:00 | 2020-03-07 | 8 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 1
2020-03-07 09:00 | 2020-03-07 | 9 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 2
2020-03-07 10:00 | 2020-03-07 | 10 | 4.254 | 0.01477% | 6.3426 | 6.5771 | 6.8203 | 7.0725 | 7.3341 | 0.60557 | 0.84011 | 1.0833 | 1.3355 | 1.5971 | 3
2020-03-07 11:00 | 2020-03-07 | 11 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 4
2020-03-07 12:00 | 2020-03-07 | 12 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 5
2020-03-07 13:00 | 2020-03-07 | 13 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 6
2020-03-07 14:00 | 2020-03-07 | 14 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 7
2020-03-07 15:00 | 2020-03-07 | 15 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 8
2020-03-07 16:00 | 2020-03-07 | 16 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 9
2020-03-07 17:00 | 2020-03-07 | 17 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 10
2020-03-07 18:00 | 2020-03-07 | 18 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 11
2020-03-07 19:00 | 2020-03-07 | 19 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 12
2020-03-07 20:00 | 2020-03-07 | 20 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 13
2020-03-07 21:00 | 2020-03-07 | 21 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 14
2020-03-07 22:00 | 2020-03-07 | 22 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 15
2020-03-07 23:00 | 2020-03-07 | 23 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 16
2020-03-08 | 2020-03-07 | 0 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 17 | 17
2020-03-08 01:00 | 2020-03-08 | 1 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-03-08 02:00 | 2020-03-08 | 2 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-03-08 03:00 | 2020-03-08 | 3 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-03-08 04:00 | 2020-03-08 | 4 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-03-08 05:00 | 2020-03-08 | 5 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-03-08 06:00 | 2020-03-08 | 6 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-03-08 07:00 | 2020-03-08 | 7 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-03-08 08:00 | 2020-03-08 | 8 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 1
2020-03-08 09:00 | 2020-03-08 | 9 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 2
2020-03-08 10:00 | 2020-03-08 | 10 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 3
2020-03-08 11:00 | 2020-03-08 | 11 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 4
2020-03-08 12:00 | 2020-03-08 | 12 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 5
2020-03-08 13:00 | 2020-03-08 | 13 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 6
2020-03-08 14:00 | 2020-03-08 | 14 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 7
2020-03-08 15:00 | 2020-03-08 | 15 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 8
2020-03-08 16:00 | 2020-03-08 | 16 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 9
2020-03-08 17:00 | 2020-03-08 | 17 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 10
2020-03-08 18:00 | 2020-03-08 | 18 | 4.254 | 0.01477% | 6.3426 | 6.5771 | 6.8203 | 7.0725 | 7.3341 | 0.60557 | 0.84011 | 1.0833 | 1.3355 | 1.5971 | 11
2020-03-08 19:00 | 2020-03-08 | 19 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 12
2020-03-08 20:00 | 2020-03-08 | 20 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 13
2020-03-08 21:00 | 2020-03-08 | 21 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 14
2020-03-08 22:00 | 2020-03-08 | 22 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 15 | 15
2020-03-08 23:00 | 2020-03-08 | 23 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-03-09 | 2020-03-08 | 0 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-03-09 01:00 | 2020-03-09 | 1 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-03-09 02:00 | 2020-03-09 | 2 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-03-09 03:00 | 2020-03-09 | 3 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-03-09 04:00 | 2020-03-09 | 4 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-03-09 05:00 | 2020-03-09 | 5 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-03-09 06:00 | 2020-03-09 | 6 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 1
2020-03-09 07:00 | 2020-03-09 | 7 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 2
2020-03-09 08:00 | 2020-03-09 | 8 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 3
2020-03-09 09:00 | 2020-03-09 | 9 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 4
2020-03-09 10:00 | 2020-03-09 | 10 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 5
2020-03-09 11:00 | 2020-03-09 | 11 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 6 | 6
2020-03-09 12:00 | 2020-03-09 | 12 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-03-09 13:00 | 2020-03-09 | 13 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1
2020-03-09 14:00 | 2020-03-09 | 14 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 2
2020-03-09 15:00 | 2020-03-09 | 15 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 3
2020-03-09 16:00 | 2020-03-09 | 16 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 4
2020-03-09 17:00 | 2020-03-09 | 17 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 5
2020-03-09 18:00 | 2020-03-09 | 18 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 6
2020-03-09 19:00 | 2020-03-09 | 19 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 7
2020-03-09 20:00 | 2020-03-09 | 20 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 8
2020-03-09 21:00 | 2020-03-09 | 21 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 9
2020-03-09 22:00 | 2020-03-09 | 22 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 10 | 10
2020-03-09 23:00 | 2020-03-09 | 23 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-03-10 | 2020-03-09 | 0 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-10 01:00 | 2020-03-10 | 1 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-03-10 02:00 | 2020-03-10 | 2 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-03-10 03:00 | 2020-03-10 | 3 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-03-10 04:00 | 2020-03-10 | 4 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-03-10 05:00 | 2020-03-10 | 5 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-10 06:00 | 2020-03-10 | 6 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-03-10 07:00 | 2020-03-10 | 7 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 1
2020-03-10 08:00 | 2020-03-10 | 8 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 2
2020-03-10 09:00 | 2020-03-10 | 9 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 3
2020-03-10 10:00 | 2020-03-10 | 10 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 4
2020-03-10 11:00 | 2020-03-10 | 11 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 5
2020-03-10 12:00 | 2020-03-10 | 12 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 6
2020-03-10 13:00 | 2020-03-10 | 13 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 7
2020-03-10 14:00 | 2020-03-10 | 14 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 8
2020-03-10 15:00 | 2020-03-10 | 15 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 9
2020-03-10 16:00 | 2020-03-10 | 16 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 10
2020-03-10 17:00 | 2020-03-10 | 17 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 11
2020-03-10 18:00 | 2020-03-10 | 18 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 12
2020-03-10 19:00 | 2020-03-10 | 19 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 13
2020-03-10 20:00 | 2020-03-10 | 20 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 14
2020-03-10 21:00 | 2020-03-10 | 21 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 15
2020-03-10 22:00 | 2020-03-10 | 22 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 16
2020-03-10 23:00 | 2020-03-10 | 23 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 17 | 17
2020-03-11 | 2020-03-10 | 0 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-03-11 01:00 | 2020-03-11 | 1 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-03-11 02:00 | 2020-03-11 | 2 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-11 03:00 | 2020-03-11 | 3 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-03-11 04:00 | 2020-03-11 | 4 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-03-11 05:00 | 2020-03-11 | 5 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-03-11 06:00 | 2020-03-11 | 6 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 1
2020-03-11 07:00 | 2020-03-11 | 7 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 2
2020-03-11 08:00 | 2020-03-11 | 8 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 3
2020-03-11 09:00 | 2020-03-11 | 9 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 4
2020-03-11 10:00 | 2020-03-11 | 10 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 5
2020-03-11 11:00 | 2020-03-11 | 11 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 6
2020-03-11 12:00 | 2020-03-11 | 12 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 7
2020-03-11 13:00 | 2020-03-11 | 13 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 8
2020-03-11 14:00 | 2020-03-11 | 14 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 9
2020-03-11 15:00 | 2020-03-11 | 15 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 10
2020-03-11 16:00 | 2020-03-11 | 16 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 11
2020-03-11 17:00 | 2020-03-11 | 17 | 4.7811 | 0.0166% | 7.1284 | 7.392 | 7.6653 | 7.9488 | 8.2427 | 1.3914 | 1.655 | 1.9283 | 2.2118 | 2.5057 | 12
2020-03-11 18:00 | 2020-03-11 | 18 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 13
2020-03-11 19:00 | 2020-03-11 | 19 | 5.0672 | 0.0176% | 7.555 | 7.8343 | 8.124 | 8.4244 | 8.736 | 1.818 | 2.0973 | 2.387 | 2.6874 | 2.999 | 14
2020-03-11 20:00 | 2020-03-11 | 20 | 5.0822 | 0.01765% | 7.5774 | 7.8576 | 8.1482 | 8.4495 | 8.7619 | 1.8404 | 2.1206 | 2.4112 | 2.7125 | 3.0249 | 15
2020-03-11 21:00 | 2020-03-11 | 21 | 4.7811 | 0.0166% | 7.1284 | 7.392 | 7.6653 | 7.9488 | 8.2427 | 1.3914 | 1.655 | 1.9283 | 2.2118 | 2.5057 | 16
2020-03-11 22:00 | 2020-03-11 | 22 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 17
2020-03-11 23:00 | 2020-03-11 | 23 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 18 | 18
2020-03-12 | 2020-03-11 | 0 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-03-12 01:00 | 2020-03-12 | 1 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-03-12 02:00 | 2020-03-12 | 2 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-12 03:00 | 2020-03-12 | 3 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-03-12 04:00 | 2020-03-12 | 4 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-03-12 05:00 | 2020-03-12 | 5 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-03-12 06:00 | 2020-03-12 | 6 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 1
2020-03-12 07:00 | 2020-03-12 | 7 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 2
2020-03-12 08:00 | 2020-03-12 | 8 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 3
2020-03-12 09:00 | 2020-03-12 | 9 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 4
2020-03-12 10:00 | 2020-03-12 | 10 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 5
2020-03-12 11:00 | 2020-03-12 | 11 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 6
2020-03-12 12:00 | 2020-03-12 | 12 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 7
2020-03-12 13:00 | 2020-03-12 | 13 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 8
2020-03-12 14:00 | 2020-03-12 | 14 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 9
2020-03-12 15:00 | 2020-03-12 | 15 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 10
2020-03-12 16:00 | 2020-03-12 | 16 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 11
2020-03-12 17:00 | 2020-03-12 | 17 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 12
2020-03-12 18:00 | 2020-03-12 | 18 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 13
2020-03-12 19:00 | 2020-03-12 | 19 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 14
2020-03-12 20:00 | 2020-03-12 | 20 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 15
2020-03-12 21:00 | 2020-03-12 | 21 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 16
2020-03-12 22:00 | 2020-03-12 | 22 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 17 | 17
2020-03-12 23:00 | 2020-03-12 | 23 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-03-13 | 2020-03-12 | 0 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-03-13 01:00 | 2020-03-13 | 1 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-03-13 02:00 | 2020-03-13 | 2 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-03-13 03:00 | 2020-03-13 | 3 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-13 04:00 | 2020-03-13 | 4 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-03-13 05:00 | 2020-03-13 | 5 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-03-13 06:00 | 2020-03-13 | 6 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-03-13 07:00 | 2020-03-13 | 7 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 1
2020-03-13 08:00 | 2020-03-13 | 8 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 2
2020-03-13 09:00 | 2020-03-13 | 9 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 3
2020-03-13 10:00 | 2020-03-13 | 10 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 4
2020-03-13 11:00 | 2020-03-13 | 11 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 5
2020-03-13 12:00 | 2020-03-13 | 12 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 6
2020-03-13 13:00 | 2020-03-13 | 13 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 7
2020-03-13 14:00 | 2020-03-13 | 14 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 8
2020-03-13 15:00 | 2020-03-13 | 15 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 9
2020-03-13 16:00 | 2020-03-13 | 16 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 10
2020-03-13 17:00 | 2020-03-13 | 17 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 11
2020-03-13 18:00 | 2020-03-13 | 18 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 12
2020-03-13 19:00 | 2020-03-13 | 19 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 13
2020-03-13 20:00 | 2020-03-13 | 20 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 14
2020-03-13 21:00 | 2020-03-13 | 21 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 15
2020-03-13 22:00 | 2020-03-13 | 22 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 16
2020-03-13 23:00 | 2020-03-13 | 23 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 17 | 17
2020-03-14 | 2020-03-13 | 0 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-03-14 01:00 | 2020-03-14 | 1 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-03-14 02:00 | 2020-03-14 | 2 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-14 03:00 | 2020-03-14 | 3 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-03-14 04:00 | 2020-03-14 | 4 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-03-14 05:00 | 2020-03-14 | 5 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-14 06:00 | 2020-03-14 | 6 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-03-14 07:00 | 2020-03-14 | 7 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-03-14 08:00 | 2020-03-14 | 8 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-03-14 09:00 | 2020-03-14 | 9 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-03-14 10:00 | 2020-03-14 | 10 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 2
2020-03-14 11:00 | 2020-03-14 | 11 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 3
2020-03-14 12:00 | 2020-03-14 | 12 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 4
2020-03-14 13:00 | 2020-03-14 | 13 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 5
2020-03-14 14:00 | 2020-03-14 | 14 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 6
2020-03-14 15:00 | 2020-03-14 | 15 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 7
2020-03-14 16:00 | 2020-03-14 | 16 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 8
2020-03-14 17:00 | 2020-03-14 | 17 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 9
2020-03-14 18:00 | 2020-03-14 | 18 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 10
2020-03-14 19:00 | 2020-03-14 | 19 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 11
2020-03-14 20:00 | 2020-03-14 | 20 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 12
2020-03-14 21:00 | 2020-03-14 | 21 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 13
2020-03-14 22:00 | 2020-03-14 | 22 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 14 | 14
2020-03-14 23:00 | 2020-03-14 | 23 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-03-15 | 2020-03-14 | 0 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-03-15 01:00 | 2020-03-15 | 1 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-15 02:00 | 2020-03-15 | 2 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-03-15 03:00 | 2020-03-15 | 3 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-03-15 04:00 | 2020-03-15 | 4 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-03-15 05:00 | 2020-03-15 | 5 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-03-15 06:00 | 2020-03-15 | 6 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-03-15 07:00 | 2020-03-15 | 7 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-03-15 08:00 | 2020-03-15 | 8 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-03-15 09:00 | 2020-03-15 | 9 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 1
2020-03-15 10:00 | 2020-03-15 | 10 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 2
2020-03-15 11:00 | 2020-03-15 | 11 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 3
2020-03-15 12:00 | 2020-03-15 | 12 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 4
2020-03-15 13:00 | 2020-03-15 | 13 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 5
2020-03-15 14:00 | 2020-03-15 | 14 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 6
2020-03-15 15:00 | 2020-03-15 | 15 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 7
2020-03-15 16:00 | 2020-03-15 | 16 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 8
2020-03-15 17:00 | 2020-03-15 | 17 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 9
2020-03-15 18:00 | 2020-03-15 | 18 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 10
2020-03-15 19:00 | 2020-03-15 | 19 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 11
2020-03-15 20:00 | 2020-03-15 | 20 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 12
2020-03-15 21:00 | 2020-03-15 | 21 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 13
2020-03-15 22:00 | 2020-03-15 | 22 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 14
2020-03-15 23:00 | 2020-03-15 | 23 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 15 | 15
2020-03-16 | 2020-03-15 | 0 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-03-16 01:00 | 2020-03-16 | 1 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-03-16 02:00 | 2020-03-16 | 2 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-03-16 03:00 | 2020-03-16 | 3 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-03-16 04:00 | 2020-03-16 | 4 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-03-16 05:00 | 2020-03-16 | 5 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-03-16 06:00 | 2020-03-16 | 6 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 1
2020-03-16 07:00 | 2020-03-16 | 7 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 2
2020-03-16 08:00 | 2020-03-16 | 8 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 3
2020-03-16 09:00 | 2020-03-16 | 9 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 4
2020-03-16 10:00 | 2020-03-16 | 10 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 5
2020-03-16 11:00 | 2020-03-16 | 11 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 6
2020-03-16 12:00 | 2020-03-16 | 12 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 7
2020-03-16 13:00 | 2020-03-16 | 13 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 8
2020-03-16 14:00 | 2020-03-16 | 14 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 9
2020-03-16 15:00 | 2020-03-16 | 15 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 10
2020-03-16 16:00 | 2020-03-16 | 16 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 11
2020-03-16 17:00 | 2020-03-16 | 17 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 12
2020-03-16 18:00 | 2020-03-16 | 18 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 13
2020-03-16 19:00 | 2020-03-16 | 19 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 14
2020-03-16 20:00 | 2020-03-16 | 20 | 4.8187 | 0.01673% | 7.1845 | 7.4502 | 7.7257 | 8.0114 | 8.3076 | 1.4475 | 1.7132 | 1.9887 | 2.2744 | 2.5706 | 15
2020-03-16 21:00 | 2020-03-16 | 21 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 16
2020-03-16 22:00 | 2020-03-16 | 22 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 17 | 17
2020-03-16 23:00 | 2020-03-16 | 23 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-03-17 | 2020-03-16 | 0 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-03-17 01:00 | 2020-03-17 | 1 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-17 02:00 | 2020-03-17 | 2 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-03-17 03:00 | 2020-03-17 | 3 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-03-17 04:00 | 2020-03-17 | 4 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-03-17 05:00 | 2020-03-17 | 5 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-03-17 06:00 | 2020-03-17 | 6 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-03-17 07:00 | 2020-03-17 | 7 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 1
2020-03-17 08:00 | 2020-03-17 | 8 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 2
2020-03-17 09:00 | 2020-03-17 | 9 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 3
2020-03-17 10:00 | 2020-03-17 | 10 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 4
2020-03-17 11:00 | 2020-03-17 | 11 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 5
2020-03-17 12:00 | 2020-03-17 | 12 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 6
2020-03-17 13:00 | 2020-03-17 | 13 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 7
2020-03-17 14:00 | 2020-03-17 | 14 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 8
2020-03-17 15:00 | 2020-03-17 | 15 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 9
2020-03-17 16:00 | 2020-03-17 | 16 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 10
2020-03-17 17:00 | 2020-03-17 | 17 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 11
2020-03-17 18:00 | 2020-03-17 | 18 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 12
2020-03-17 19:00 | 2020-03-17 | 19 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 13
2020-03-17 20:00 | 2020-03-17 | 20 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 14
2020-03-17 21:00 | 2020-03-17 | 21 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 15
2020-03-17 22:00 | 2020-03-17 | 22 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 16 | 16
2020-03-17 23:00 | 2020-03-17 | 23 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-03-18 | 2020-03-17 | 0 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-03-18 01:00 | 2020-03-18 | 1 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-03-18 02:00 | 2020-03-18 | 2 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-03-18 03:00 | 2020-03-18 | 3 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-03-18 04:00 | 2020-03-18 | 4 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-03-18 05:00 | 2020-03-18 | 5 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-03-18 06:00 | 2020-03-18 | 6 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1
2020-03-18 07:00 | 2020-03-18 | 7 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 2
2020-03-18 08:00 | 2020-03-18 | 8 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 3
2020-03-18 09:00 | 2020-03-18 | 9 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 4
2020-03-18 10:00 | 2020-03-18 | 10 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 5
2020-03-18 11:00 | 2020-03-18 | 11 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 6
2020-03-18 12:00 | 2020-03-18 | 12 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 7
2020-03-18 13:00 | 2020-03-18 | 13 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 8
2020-03-18 14:00 | 2020-03-18 | 14 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 9
2020-03-18 15:00 | 2020-03-18 | 15 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 10
2020-03-18 16:00 | 2020-03-18 | 16 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 11
2020-03-18 17:00 | 2020-03-18 | 17 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 12
2020-03-18 18:00 | 2020-03-18 | 18 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 13
2020-03-18 19:00 | 2020-03-18 | 19 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 14
2020-03-18 20:00 | 2020-03-18 | 20 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 15
2020-03-18 21:00 | 2020-03-18 | 21 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 16
2020-03-18 22:00 | 2020-03-18 | 22 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 17 | 17
2020-03-18 23:00 | 2020-03-18 | 23 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-03-19 | 2020-03-18 | 0 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-03-19 01:00 | 2020-03-19 | 1 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-03-19 02:00 | 2020-03-19 | 2 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-03-19 03:00 | 2020-03-19 | 3 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-03-19 04:00 | 2020-03-19 | 4 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-03-19 05:00 | 2020-03-19 | 5 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-03-19 06:00 | 2020-03-19 | 6 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-03-19 07:00 | 2020-03-19 | 7 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 1
2020-03-19 08:00 | 2020-03-19 | 8 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 2
2020-03-19 09:00 | 2020-03-19 | 9 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 3
2020-03-19 10:00 | 2020-03-19 | 10 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 4
2020-03-19 11:00 | 2020-03-19 | 11 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 5
2020-03-19 12:00 | 2020-03-19 | 12 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 6
2020-03-19 13:00 | 2020-03-19 | 13 | 4.2314 | 0.01469% | 6.3089 | 6.5422 | 6.7841 | 7.035 | 7.2951 | 0.5719 | 0.80519 | 1.0471 | 1.298 | 1.5581 | 7
2020-03-19 14:00 | 2020-03-19 | 14 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 8
2020-03-19 15:00 | 2020-03-19 | 15 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 9
2020-03-19 16:00 | 2020-03-19 | 16 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 10
2020-03-19 17:00 | 2020-03-19 | 17 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 11
2020-03-19 18:00 | 2020-03-19 | 18 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 12
2020-03-19 19:00 | 2020-03-19 | 19 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 13
2020-03-19 20:00 | 2020-03-19 | 20 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 14
2020-03-19 21:00 | 2020-03-19 | 21 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 15
2020-03-19 22:00 | 2020-03-19 | 22 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 16 | 16
2020-03-19 23:00 | 2020-03-19 | 23 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-03-20 | 2020-03-19 | 0 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-03-20 01:00 | 2020-03-20 | 1 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-03-20 02:00 | 2020-03-20 | 2 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-03-20 03:00 | 2020-03-20 | 3 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-20 04:00 | 2020-03-20 | 4 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-20 05:00 | 2020-03-20 | 5 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-03-20 06:00 | 2020-03-20 | 6 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-03-20 07:00 | 2020-03-20 | 7 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-03-20 08:00 | 2020-03-20 | 8 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-03-20 09:00 | 2020-03-20 | 9 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 1
2020-03-20 10:00 | 2020-03-20 | 10 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 2
2020-03-20 11:00 | 2020-03-20 | 11 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 3 | 3
2020-03-20 12:00 | 2020-03-20 | 12 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-03-20 13:00 | 2020-03-20 | 13 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-03-20 14:00 | 2020-03-20 | 14 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-03-20 15:00 | 2020-03-20 | 15 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-03-20 16:00 | 2020-03-20 | 16 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-20 17:00 | 2020-03-20 | 17 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-03-20 18:00 | 2020-03-20 | 18 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-03-20 19:00 | 2020-03-20 | 19 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-03-20 20:00 | 2020-03-20 | 20 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-03-20 21:00 | 2020-03-20 | 21 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-03-20 22:00 | 2020-03-20 | 22 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-03-20 23:00 | 2020-03-20 | 23 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-03-21 | 2020-03-20 | 0 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-03-21 01:00 | 2020-03-21 | 1 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-03-21 02:00 | 2020-03-21 | 2 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-03-21 03:00 | 2020-03-21 | 3 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-03-21 04:00 | 2020-03-21 | 4 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-03-21 05:00 | 2020-03-21 | 5 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-03-21 06:00 | 2020-03-21 | 6 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-03-21 07:00 | 2020-03-21 | 7 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-03-21 08:00 | 2020-03-21 | 8 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-03-21 09:00 | 2020-03-21 | 9 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-03-21 10:00 | 2020-03-21 | 10 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-03-21 11:00 | 2020-03-21 | 11 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-03-21 12:00 | 2020-03-21 | 12 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-03-21 13:00 | 2020-03-21 | 13 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-03-21 14:00 | 2020-03-21 | 14 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-03-21 15:00 | 2020-03-21 | 15 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-03-21 16:00 | 2020-03-21 | 16 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-03-21 17:00 | 2020-03-21 | 17 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-03-21 18:00 | 2020-03-21 | 18 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-03-21 19:00 | 2020-03-21 | 19 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-03-21 20:00 | 2020-03-21 | 20 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-21 21:00 | 2020-03-21 | 21 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-03-21 22:00 | 2020-03-21 | 22 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-03-21 23:00 | 2020-03-21 | 23 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-03-22 | 2020-03-21 | 0 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-03-22 01:00 | 2020-03-22 | 1 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-03-22 02:00 | 2020-03-22 | 2 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-03-22 03:00 | 2020-03-22 | 3 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-03-22 04:00 | 2020-03-22 | 4 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-03-22 05:00 | 2020-03-22 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-03-22 06:00 | 2020-03-22 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-03-22 07:00 | 2020-03-22 | 7 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-03-22 08:00 | 2020-03-22 | 8 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-03-22 09:00 | 2020-03-22 | 9 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-03-22 10:00 | 2020-03-22 | 10 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-03-22 11:00 | 2020-03-22 | 11 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-03-22 12:00 | 2020-03-22 | 12 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-03-22 13:00 | 2020-03-22 | 13 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-03-22 14:00 | 2020-03-22 | 14 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-03-22 15:00 | 2020-03-22 | 15 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-03-22 16:00 | 2020-03-22 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-03-22 17:00 | 2020-03-22 | 17 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-03-22 18:00 | 2020-03-22 | 18 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-03-22 19:00 | 2020-03-22 | 19 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-22 20:00 | 2020-03-22 | 20 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-03-22 21:00 | 2020-03-22 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-22 22:00 | 2020-03-22 | 22 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-03-22 23:00 | 2020-03-22 | 23 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-03-23 | 2020-03-22 | 0 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-03-23 01:00 | 2020-03-23 | 1 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-03-23 02:00 | 2020-03-23 | 2 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-03-23 03:00 | 2020-03-23 | 3 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-03-23 04:00 | 2020-03-23 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-03-23 05:00 | 2020-03-23 | 5 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-03-23 06:00 | 2020-03-23 | 6 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-03-23 07:00 | 2020-03-23 | 7 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-03-23 08:00 | 2020-03-23 | 8 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-03-23 09:00 | 2020-03-23 | 9 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-03-23 10:00 | 2020-03-23 | 10 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-03-23 11:00 | 2020-03-23 | 11 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-03-23 12:00 | 2020-03-23 | 12 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-03-23 13:00 | 2020-03-23 | 13 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-03-23 14:00 | 2020-03-23 | 14 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-03-23 15:00 | 2020-03-23 | 15 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-03-23 16:00 | 2020-03-23 | 16 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-03-23 17:00 | 2020-03-23 | 17 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-03-23 18:00 | 2020-03-23 | 18 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-03-23 19:00 | 2020-03-23 | 19 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-03-23 20:00 | 2020-03-23 | 20 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-03-23 21:00 | 2020-03-23 | 21 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-03-23 22:00 | 2020-03-23 | 22 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-23 23:00 | 2020-03-23 | 23 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-03-24 | 2020-03-23 | 0 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-03-24 01:00 | 2020-03-24 | 1 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-03-24 02:00 | 2020-03-24 | 2 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-03-24 03:00 | 2020-03-24 | 3 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-03-24 04:00 | 2020-03-24 | 4 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-03-24 05:00 | 2020-03-24 | 5 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-03-24 06:00 | 2020-03-24 | 6 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-03-24 07:00 | 2020-03-24 | 7 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-03-24 08:00 | 2020-03-24 | 8 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-03-24 09:00 | 2020-03-24 | 9 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-03-24 10:00 | 2020-03-24 | 10 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-24 11:00 | 2020-03-24 | 11 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-03-24 12:00 | 2020-03-24 | 12 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-03-24 13:00 | 2020-03-24 | 13 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-03-24 14:00 | 2020-03-24 | 14 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-03-24 15:00 | 2020-03-24 | 15 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-03-24 16:00 | 2020-03-24 | 16 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-03-24 17:00 | 2020-03-24 | 17 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-03-24 18:00 | 2020-03-24 | 18 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-03-24 19:00 | 2020-03-24 | 19 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-03-24 20:00 | 2020-03-24 | 20 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-24 21:00 | 2020-03-24 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-24 22:00 | 2020-03-24 | 22 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-03-24 23:00 | 2020-03-24 | 23 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-03-25 | 2020-03-24 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-03-25 01:00 | 2020-03-25 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-03-25 02:00 | 2020-03-25 | 2 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-03-25 03:00 | 2020-03-25 | 3 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-03-25 04:00 | 2020-03-25 | 4 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-03-25 05:00 | 2020-03-25 | 5 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-03-25 06:00 | 2020-03-25 | 6 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-03-25 07:00 | 2020-03-25 | 7 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-25 08:00 | 2020-03-25 | 8 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-03-25 09:00 | 2020-03-25 | 9 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-25 10:00 | 2020-03-25 | 10 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-03-25 11:00 | 2020-03-25 | 11 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-03-25 12:00 | 2020-03-25 | 12 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-25 13:00 | 2020-03-25 | 13 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-03-25 14:00 | 2020-03-25 | 14 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-03-25 15:00 | 2020-03-25 | 15 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-25 16:00 | 2020-03-25 | 16 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-03-25 17:00 | 2020-03-25 | 17 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-03-25 18:00 | 2020-03-25 | 18 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-03-25 19:00 | 2020-03-25 | 19 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-03-25 20:00 | 2020-03-25 | 20 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-03-25 21:00 | 2020-03-25 | 21 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-03-25 22:00 | 2020-03-25 | 22 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-03-25 23:00 | 2020-03-25 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-03-26 | 2020-03-25 | 0 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-03-26 01:00 | 2020-03-26 | 1 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-03-26 02:00 | 2020-03-26 | 2 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-03-26 03:00 | 2020-03-26 | 3 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-03-26 04:00 | 2020-03-26 | 4 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-03-26 05:00 | 2020-03-26 | 5 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-03-26 06:00 | 2020-03-26 | 6 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-03-26 07:00 | 2020-03-26 | 7 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-03-26 08:00 | 2020-03-26 | 8 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-26 09:00 | 2020-03-26 | 9 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-03-26 10:00 | 2020-03-26 | 10 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-03-26 11:00 | 2020-03-26 | 11 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-26 12:00 | 2020-03-26 | 12 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-03-26 13:00 | 2020-03-26 | 13 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-26 14:00 | 2020-03-26 | 14 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-03-26 15:00 | 2020-03-26 | 15 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-03-26 16:00 | 2020-03-26 | 16 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-26 17:00 | 2020-03-26 | 17 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-03-26 18:00 | 2020-03-26 | 18 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-03-26 19:00 | 2020-03-26 | 19 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-03-26 20:00 | 2020-03-26 | 20 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-03-26 21:00 | 2020-03-26 | 21 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-26 22:00 | 2020-03-26 | 22 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-03-26 23:00 | 2020-03-26 | 23 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-03-27 | 2020-03-26 | 0 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-03-27 01:00 | 2020-03-27 | 1 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-03-27 02:00 | 2020-03-27 | 2 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-03-27 03:00 | 2020-03-27 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-03-27 04:00 | 2020-03-27 | 4 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-03-27 05:00 | 2020-03-27 | 5 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-03-27 06:00 | 2020-03-27 | 6 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-03-27 07:00 | 2020-03-27 | 7 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-03-27 08:00 | 2020-03-27 | 8 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-03-27 09:00 | 2020-03-27 | 9 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-03-27 10:00 | 2020-03-27 | 10 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-03-27 11:00 | 2020-03-27 | 11 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-03-27 12:00 | 2020-03-27 | 12 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-03-27 13:00 | 2020-03-27 | 13 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-03-27 14:00 | 2020-03-27 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-03-27 15:00 | 2020-03-27 | 15 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-03-27 16:00 | 2020-03-27 | 16 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-03-27 17:00 | 2020-03-27 | 17 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-03-27 18:00 | 2020-03-27 | 18 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-03-27 19:00 | 2020-03-27 | 19 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-03-27 20:00 | 2020-03-27 | 20 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-27 21:00 | 2020-03-27 | 21 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-03-27 22:00 | 2020-03-27 | 22 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-03-27 23:00 | 2020-03-27 | 23 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-03-28 | 2020-03-27 | 0 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-03-28 01:00 | 2020-03-28 | 1 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-03-28 02:00 | 2020-03-28 | 2 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-03-28 03:00 | 2020-03-28 | 3 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-03-28 04:00 | 2020-03-28 | 4 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-03-28 05:00 | 2020-03-28 | 5 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-03-28 06:00 | 2020-03-28 | 6 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-03-28 07:00 | 2020-03-28 | 7 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-03-28 08:00 | 2020-03-28 | 8 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-03-28 09:00 | 2020-03-28 | 9 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-03-28 10:00 | 2020-03-28 | 10 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-03-28 11:00 | 2020-03-28 | 11 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-03-28 12:00 | 2020-03-28 | 12 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-03-28 13:00 | 2020-03-28 | 13 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-03-28 14:00 | 2020-03-28 | 14 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-03-28 15:00 | 2020-03-28 | 15 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-03-28 16:00 | 2020-03-28 | 16 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-03-28 17:00 | 2020-03-28 | 17 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-03-28 18:00 | 2020-03-28 | 18 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-03-28 19:00 | 2020-03-28 | 19 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-03-28 20:00 | 2020-03-28 | 20 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-03-28 21:00 | 2020-03-28 | 21 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-03-28 22:00 | 2020-03-28 | 22 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-03-28 23:00 | 2020-03-28 | 23 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-03-29 | 2020-03-28 | 0 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-03-29 01:00 | 2020-03-29 | 1 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-03-29 02:00 | 2020-03-29 | 2 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-03-29 03:00 | 2020-03-29 | 3 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-03-29 04:00 | 2020-03-29 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-03-29 05:00 | 2020-03-29 | 5 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-03-29 06:00 | 2020-03-29 | 6 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-03-29 07:00 | 2020-03-29 | 7 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-03-29 08:00 | 2020-03-29 | 8 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-03-29 09:00 | 2020-03-29 | 9 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-03-29 10:00 | 2020-03-29 | 10 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-03-29 11:00 | 2020-03-29 | 11 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-29 12:00 | 2020-03-29 | 12 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-03-29 13:00 | 2020-03-29 | 13 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-03-29 14:00 | 2020-03-29 | 14 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-03-29 15:00 | 2020-03-29 | 15 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-03-29 16:00 | 2020-03-29 | 16 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-29 17:00 | 2020-03-29 | 17 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-03-29 18:00 | 2020-03-29 | 18 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-03-29 19:00 | 2020-03-29 | 19 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-03-29 20:00 | 2020-03-29 | 20 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-29 21:00 | 2020-03-29 | 21 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-03-29 22:00 | 2020-03-29 | 22 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-03-29 23:00 | 2020-03-29 | 23 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-03-30 | 2020-03-29 | 0 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-03-30 01:00 | 2020-03-30 | 1 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-03-30 02:00 | 2020-03-30 | 2 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-03-30 03:00 | 2020-03-30 | 3 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-03-30 04:00 | 2020-03-30 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-03-30 05:00 | 2020-03-30 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-03-30 06:00 | 2020-03-30 | 6 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-03-30 07:00 | 2020-03-30 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-03-30 08:00 | 2020-03-30 | 8 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-03-30 09:00 | 2020-03-30 | 9 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-30 10:00 | 2020-03-30 | 10 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-03-30 11:00 | 2020-03-30 | 11 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-03-30 12:00 | 2020-03-30 | 12 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-03-30 13:00 | 2020-03-30 | 13 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-03-30 14:00 | 2020-03-30 | 14 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-03-30 15:00 | 2020-03-30 | 15 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-03-30 16:00 | 2020-03-30 | 16 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-30 17:00 | 2020-03-30 | 17 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-03-30 18:00 | 2020-03-30 | 18 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-03-30 19:00 | 2020-03-30 | 19 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-03-30 20:00 | 2020-03-30 | 20 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-03-30 21:00 | 2020-03-30 | 21 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-03-30 22:00 | 2020-03-30 | 22 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-03-30 23:00 | 2020-03-30 | 23 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-03-31 | 2020-03-30 | 0 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-03-31 01:00 | 2020-03-31 | 1 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-03-31 02:00 | 2020-03-31 | 2 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-03-31 03:00 | 2020-03-31 | 3 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-03-31 04:00 | 2020-03-31 | 4 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-03-31 05:00 | 2020-03-31 | 5 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-03-31 06:00 | 2020-03-31 | 6 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-03-31 07:00 | 2020-03-31 | 7 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-03-31 08:00 | 2020-03-31 | 8 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-03-31 09:00 | 2020-03-31 | 9 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-03-31 10:00 | 2020-03-31 | 10 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-03-31 11:00 | 2020-03-31 | 11 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-03-31 12:00 | 2020-03-31 | 12 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-03-31 13:00 | 2020-03-31 | 13 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-03-31 14:00 | 2020-03-31 | 14 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-03-31 15:00 | 2020-03-31 | 15 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-03-31 16:00 | 2020-03-31 | 16 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-03-31 17:00 | 2020-03-31 | 17 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-03-31 18:00 | 2020-03-31 | 18 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-03-31 19:00 | 2020-03-31 | 19 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-03-31 20:00 | 2020-03-31 | 20 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-03-31 21:00 | 2020-03-31 | 21 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-03-31 22:00 | 2020-03-31 | 22 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-03-31 23:00 | 2020-03-31 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-01 | 2020-03-31 | 0 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-04-01 01:00 | 2020-04-01 | 1 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-01 02:00 | 2020-04-01 | 2 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-01 03:00 | 2020-04-01 | 3 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-01 04:00 | 2020-04-01 | 4 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-04-01 05:00 | 2020-04-01 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-01 06:00 | 2020-04-01 | 6 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-01 07:00 | 2020-04-01 | 7 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-04-01 08:00 | 2020-04-01 | 8 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-01 09:00 | 2020-04-01 | 9 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-01 10:00 | 2020-04-01 | 10 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-01 11:00 | 2020-04-01 | 11 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-01 12:00 | 2020-04-01 | 12 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-04-01 13:00 | 2020-04-01 | 13 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-01 14:00 | 2020-04-01 | 14 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-01 15:00 | 2020-04-01 | 15 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-01 16:00 | 2020-04-01 | 16 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-01 17:00 | 2020-04-01 | 17 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-04-01 18:00 | 2020-04-01 | 18 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-01 19:00 | 2020-04-01 | 19 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-04-01 20:00 | 2020-04-01 | 20 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-01 21:00 | 2020-04-01 | 21 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-01 22:00 | 2020-04-01 | 22 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-04-01 23:00 | 2020-04-01 | 23 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-04-02 | 2020-04-01 | 0 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-02 01:00 | 2020-04-02 | 1 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-02 02:00 | 2020-04-02 | 2 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-02 03:00 | 2020-04-02 | 3 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-02 04:00 | 2020-04-02 | 4 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-04-02 05:00 | 2020-04-02 | 5 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-04-02 06:00 | 2020-04-02 | 6 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-04-02 07:00 | 2020-04-02 | 7 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-04-02 08:00 | 2020-04-02 | 8 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-02 09:00 | 2020-04-02 | 9 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-02 10:00 | 2020-04-02 | 10 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-02 11:00 | 2020-04-02 | 11 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-04-02 12:00 | 2020-04-02 | 12 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-02 13:00 | 2020-04-02 | 13 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-02 14:00 | 2020-04-02 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-02 15:00 | 2020-04-02 | 15 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-04-02 16:00 | 2020-04-02 | 16 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-04-02 17:00 | 2020-04-02 | 17 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-02 18:00 | 2020-04-02 | 18 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-02 19:00 | 2020-04-02 | 19 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-02 20:00 | 2020-04-02 | 20 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-02 21:00 | 2020-04-02 | 21 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-02 22:00 | 2020-04-02 | 22 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-02 23:00 | 2020-04-02 | 23 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-03 | 2020-04-02 | 0 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-03 01:00 | 2020-04-03 | 1 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-04-03 02:00 | 2020-04-03 | 2 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-04-03 03:00 | 2020-04-03 | 3 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-04-03 04:00 | 2020-04-03 | 4 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-04-03 05:00 | 2020-04-03 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-03 06:00 | 2020-04-03 | 6 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-03 07:00 | 2020-04-03 | 7 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-03 08:00 | 2020-04-03 | 8 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-03 09:00 | 2020-04-03 | 9 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-03 10:00 | 2020-04-03 | 10 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-03 11:00 | 2020-04-03 | 11 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-04-03 12:00 | 2020-04-03 | 12 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-03 13:00 | 2020-04-03 | 13 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-03 14:00 | 2020-04-03 | 14 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-03 15:00 | 2020-04-03 | 15 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-03 16:00 | 2020-04-03 | 16 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-03 17:00 | 2020-04-03 | 17 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-04-03 18:00 | 2020-04-03 | 18 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-03 19:00 | 2020-04-03 | 19 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-04-03 20:00 | 2020-04-03 | 20 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-04-03 21:00 | 2020-04-03 | 21 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-03 22:00 | 2020-04-03 | 22 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-03 23:00 | 2020-04-03 | 23 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-04-04 | 2020-04-03 | 0 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-04 01:00 | 2020-04-04 | 1 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-04 02:00 | 2020-04-04 | 2 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-04-04 03:00 | 2020-04-04 | 3 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-04 04:00 | 2020-04-04 | 4 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-04-04 05:00 | 2020-04-04 | 5 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-04 06:00 | 2020-04-04 | 6 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-04 07:00 | 2020-04-04 | 7 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-04-04 08:00 | 2020-04-04 | 8 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-04 09:00 | 2020-04-04 | 9 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-04 10:00 | 2020-04-04 | 10 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-04 11:00 | 2020-04-04 | 11 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-04 12:00 | 2020-04-04 | 12 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-04 13:00 | 2020-04-04 | 13 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-04 14:00 | 2020-04-04 | 14 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-04-04 15:00 | 2020-04-04 | 15 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-04 16:00 | 2020-04-04 | 16 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-04-04 17:00 | 2020-04-04 | 17 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-04 18:00 | 2020-04-04 | 18 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-04 19:00 | 2020-04-04 | 19 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-04 20:00 | 2020-04-04 | 20 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-04 21:00 | 2020-04-04 | 21 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-04 22:00 | 2020-04-04 | 22 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-04-04 23:00 | 2020-04-04 | 23 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-04-05 | 2020-04-04 | 0 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-04-05 01:00 | 2020-04-05 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-04-05 02:00 | 2020-04-05 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-04-05 03:00 | 2020-04-05 | 3 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-04-05 04:00 | 2020-04-05 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-04-05 05:00 | 2020-04-05 | 5 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-04-05 06:00 | 2020-04-05 | 6 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-04-05 07:00 | 2020-04-05 | 7 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-05 08:00 | 2020-04-05 | 8 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-05 09:00 | 2020-04-05 | 9 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-05 10:00 | 2020-04-05 | 10 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-05 11:00 | 2020-04-05 | 11 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-05 12:00 | 2020-04-05 | 12 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-05 13:00 | 2020-04-05 | 13 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-04-05 14:00 | 2020-04-05 | 14 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-05 15:00 | 2020-04-05 | 15 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-05 16:00 | 2020-04-05 | 16 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-05 17:00 | 2020-04-05 | 17 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-05 18:00 | 2020-04-05 | 18 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-04-05 19:00 | 2020-04-05 | 19 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-04-05 20:00 | 2020-04-05 | 20 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-05 21:00 | 2020-04-05 | 21 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-05 22:00 | 2020-04-05 | 22 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-05 23:00 | 2020-04-05 | 23 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-06 | 2020-04-05 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-04-06 01:00 | 2020-04-06 | 1 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-04-06 02:00 | 2020-04-06 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-06 03:00 | 2020-04-06 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-06 04:00 | 2020-04-06 | 4 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-06 05:00 | 2020-04-06 | 5 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-04-06 06:00 | 2020-04-06 | 6 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-06 07:00 | 2020-04-06 | 7 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-04-06 08:00 | 2020-04-06 | 8 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-06 09:00 | 2020-04-06 | 9 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-06 10:00 | 2020-04-06 | 10 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-06 11:00 | 2020-04-06 | 11 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-06 12:00 | 2020-04-06 | 12 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-04-06 13:00 | 2020-04-06 | 13 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-04-06 14:00 | 2020-04-06 | 14 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-04-06 15:00 | 2020-04-06 | 15 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-04-06 16:00 | 2020-04-06 | 16 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-06 17:00 | 2020-04-06 | 17 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-04-06 18:00 | 2020-04-06 | 18 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-04-06 19:00 | 2020-04-06 | 19 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-04-06 20:00 | 2020-04-06 | 20 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-04-06 21:00 | 2020-04-06 | 21 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-06 22:00 | 2020-04-06 | 22 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-04-06 23:00 | 2020-04-06 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-07 | 2020-04-06 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-07 01:00 | 2020-04-07 | 1 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-07 02:00 | 2020-04-07 | 2 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-04-07 03:00 | 2020-04-07 | 3 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-04-07 04:00 | 2020-04-07 | 4 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-04-07 05:00 | 2020-04-07 | 5 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-04-07 06:00 | 2020-04-07 | 6 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-07 07:00 | 2020-04-07 | 7 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-07 08:00 | 2020-04-07 | 8 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-04-07 09:00 | 2020-04-07 | 9 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-07 10:00 | 2020-04-07 | 10 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-07 11:00 | 2020-04-07 | 11 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-07 12:00 | 2020-04-07 | 12 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-07 13:00 | 2020-04-07 | 13 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-07 14:00 | 2020-04-07 | 14 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-04-07 15:00 | 2020-04-07 | 15 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-07 16:00 | 2020-04-07 | 16 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-07 17:00 | 2020-04-07 | 17 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-07 18:00 | 2020-04-07 | 18 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-07 19:00 | 2020-04-07 | 19 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-07 20:00 | 2020-04-07 | 20 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-07 21:00 | 2020-04-07 | 21 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-07 22:00 | 2020-04-07 | 22 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-07 23:00 | 2020-04-07 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-08 | 2020-04-07 | 0 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-04-08 01:00 | 2020-04-08 | 1 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-08 02:00 | 2020-04-08 | 2 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-04-08 03:00 | 2020-04-08 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-08 04:00 | 2020-04-08 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-08 05:00 | 2020-04-08 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-08 06:00 | 2020-04-08 | 6 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-08 07:00 | 2020-04-08 | 7 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-08 08:00 | 2020-04-08 | 8 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-08 09:00 | 2020-04-08 | 9 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-08 10:00 | 2020-04-08 | 10 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-08 11:00 | 2020-04-08 | 11 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-04-08 12:00 | 2020-04-08 | 12 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-04-08 13:00 | 2020-04-08 | 13 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-04-08 14:00 | 2020-04-08 | 14 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-08 15:00 | 2020-04-08 | 15 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-08 16:00 | 2020-04-08 | 16 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-04-08 17:00 | 2020-04-08 | 17 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-08 18:00 | 2020-04-08 | 18 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-08 19:00 | 2020-04-08 | 19 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-08 20:00 | 2020-04-08 | 20 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-08 21:00 | 2020-04-08 | 21 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-08 22:00 | 2020-04-08 | 22 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-08 23:00 | 2020-04-08 | 23 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-09 | 2020-04-08 | 0 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-04-09 01:00 | 2020-04-09 | 1 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-09 02:00 | 2020-04-09 | 2 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-04-09 03:00 | 2020-04-09 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-09 04:00 | 2020-04-09 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-09 05:00 | 2020-04-09 | 5 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-09 06:00 | 2020-04-09 | 6 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-04-09 07:00 | 2020-04-09 | 7 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-09 08:00 | 2020-04-09 | 8 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-04-09 09:00 | 2020-04-09 | 9 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-04-09 10:00 | 2020-04-09 | 10 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-09 11:00 | 2020-04-09 | 11 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-09 12:00 | 2020-04-09 | 12 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-09 13:00 | 2020-04-09 | 13 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-09 14:00 | 2020-04-09 | 14 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-09 15:00 | 2020-04-09 | 15 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-09 16:00 | 2020-04-09 | 16 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-09 17:00 | 2020-04-09 | 17 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-09 18:00 | 2020-04-09 | 18 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-09 19:00 | 2020-04-09 | 19 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-09 20:00 | 2020-04-09 | 20 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-09 21:00 | 2020-04-09 | 21 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-09 22:00 | 2020-04-09 | 22 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-04-09 23:00 | 2020-04-09 | 23 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-10 | 2020-04-09 | 0 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-10 01:00 | 2020-04-10 | 1 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-04-10 02:00 | 2020-04-10 | 2 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-10 03:00 | 2020-04-10 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-10 04:00 | 2020-04-10 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-10 05:00 | 2020-04-10 | 5 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-10 06:00 | 2020-04-10 | 6 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-10 07:00 | 2020-04-10 | 7 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-10 08:00 | 2020-04-10 | 8 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-04-10 09:00 | 2020-04-10 | 9 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-10 10:00 | 2020-04-10 | 10 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-10 11:00 | 2020-04-10 | 11 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-10 12:00 | 2020-04-10 | 12 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-10 13:00 | 2020-04-10 | 13 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-04-10 14:00 | 2020-04-10 | 14 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-04-10 15:00 | 2020-04-10 | 15 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-10 16:00 | 2020-04-10 | 16 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-10 17:00 | 2020-04-10 | 17 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-10 18:00 | 2020-04-10 | 18 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-10 19:00 | 2020-04-10 | 19 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-10 20:00 | 2020-04-10 | 20 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-10 21:00 | 2020-04-10 | 21 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-10 22:00 | 2020-04-10 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-10 23:00 | 2020-04-10 | 23 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-11 | 2020-04-10 | 0 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-04-11 01:00 | 2020-04-11 | 1 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-04-11 02:00 | 2020-04-11 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-11 03:00 | 2020-04-11 | 3 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-11 04:00 | 2020-04-11 | 4 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-04-11 05:00 | 2020-04-11 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-11 06:00 | 2020-04-11 | 6 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-11 07:00 | 2020-04-11 | 7 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-11 08:00 | 2020-04-11 | 8 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-11 09:00 | 2020-04-11 | 9 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-04-11 10:00 | 2020-04-11 | 10 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-11 11:00 | 2020-04-11 | 11 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-11 12:00 | 2020-04-11 | 12 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-11 13:00 | 2020-04-11 | 13 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-11 14:00 | 2020-04-11 | 14 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-11 15:00 | 2020-04-11 | 15 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-04-11 16:00 | 2020-04-11 | 16 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-11 17:00 | 2020-04-11 | 17 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-11 18:00 | 2020-04-11 | 18 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-11 19:00 | 2020-04-11 | 19 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-11 20:00 | 2020-04-11 | 20 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-11 21:00 | 2020-04-11 | 21 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-04-11 22:00 | 2020-04-11 | 22 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-11 23:00 | 2020-04-11 | 23 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-12 | 2020-04-11 | 0 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-12 01:00 | 2020-04-12 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-12 02:00 | 2020-04-12 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-12 03:00 | 2020-04-12 | 3 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-04-12 04:00 | 2020-04-12 | 4 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-04-12 05:00 | 2020-04-12 | 5 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-04-12 06:00 | 2020-04-12 | 6 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-04-12 07:00 | 2020-04-12 | 7 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-12 08:00 | 2020-04-12 | 8 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-12 09:00 | 2020-04-12 | 9 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-12 10:00 | 2020-04-12 | 10 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-12 11:00 | 2020-04-12 | 11 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-12 12:00 | 2020-04-12 | 12 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-12 13:00 | 2020-04-12 | 13 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-04-12 14:00 | 2020-04-12 | 14 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-12 15:00 | 2020-04-12 | 15 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-12 16:00 | 2020-04-12 | 16 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-12 17:00 | 2020-04-12 | 17 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-12 18:00 | 2020-04-12 | 18 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-04-12 19:00 | 2020-04-12 | 19 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-12 20:00 | 2020-04-12 | 20 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-12 21:00 | 2020-04-12 | 21 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-12 22:00 | 2020-04-12 | 22 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-04-12 23:00 | 2020-04-12 | 23 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-04-13 | 2020-04-12 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-13 01:00 | 2020-04-13 | 1 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-04-13 02:00 | 2020-04-13 | 2 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-04-13 03:00 | 2020-04-13 | 3 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-04-13 04:00 | 2020-04-13 | 4 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-04-13 05:00 | 2020-04-13 | 5 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-04-13 06:00 | 2020-04-13 | 6 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-04-13 07:00 | 2020-04-13 | 7 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-04-13 08:00 | 2020-04-13 | 8 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-13 09:00 | 2020-04-13 | 9 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-13 10:00 | 2020-04-13 | 10 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-13 11:00 | 2020-04-13 | 11 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-13 12:00 | 2020-04-13 | 12 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-13 13:00 | 2020-04-13 | 13 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-04-13 14:00 | 2020-04-13 | 14 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-13 15:00 | 2020-04-13 | 15 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-13 16:00 | 2020-04-13 | 16 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-13 17:00 | 2020-04-13 | 17 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-13 18:00 | 2020-04-13 | 18 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-13 19:00 | 2020-04-13 | 19 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-13 20:00 | 2020-04-13 | 20 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-13 21:00 | 2020-04-13 | 21 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-13 22:00 | 2020-04-13 | 22 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-13 23:00 | 2020-04-13 | 23 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-14 | 2020-04-13 | 0 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-04-14 01:00 | 2020-04-14 | 1 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-04-14 02:00 | 2020-04-14 | 2 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-14 03:00 | 2020-04-14 | 3 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-14 04:00 | 2020-04-14 | 4 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-04-14 05:00 | 2020-04-14 | 5 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-04-14 06:00 | 2020-04-14 | 6 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-14 07:00 | 2020-04-14 | 7 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-04-14 08:00 | 2020-04-14 | 8 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-14 09:00 | 2020-04-14 | 9 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-14 10:00 | 2020-04-14 | 10 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-04-14 11:00 | 2020-04-14 | 11 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-14 12:00 | 2020-04-14 | 12 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-14 13:00 | 2020-04-14 | 13 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-14 14:00 | 2020-04-14 | 14 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-14 15:00 | 2020-04-14 | 15 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-14 16:00 | 2020-04-14 | 16 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-14 17:00 | 2020-04-14 | 17 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-14 18:00 | 2020-04-14 | 18 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-14 19:00 | 2020-04-14 | 19 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-14 20:00 | 2020-04-14 | 20 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-04-14 21:00 | 2020-04-14 | 21 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-04-14 22:00 | 2020-04-14 | 22 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-04-14 23:00 | 2020-04-14 | 23 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-15 | 2020-04-14 | 0 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-15 01:00 | 2020-04-15 | 1 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-15 02:00 | 2020-04-15 | 2 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-15 03:00 | 2020-04-15 | 3 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-04-15 04:00 | 2020-04-15 | 4 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-15 05:00 | 2020-04-15 | 5 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-15 06:00 | 2020-04-15 | 6 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-04-15 07:00 | 2020-04-15 | 7 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-15 08:00 | 2020-04-15 | 8 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-04-15 09:00 | 2020-04-15 | 9 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-15 10:00 | 2020-04-15 | 10 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-04-15 11:00 | 2020-04-15 | 11 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-04-15 12:00 | 2020-04-15 | 12 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-04-15 13:00 | 2020-04-15 | 13 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-04-15 14:00 | 2020-04-15 | 14 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-04-15 15:00 | 2020-04-15 | 15 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-04-15 16:00 | 2020-04-15 | 16 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-04-15 17:00 | 2020-04-15 | 17 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-04-15 18:00 | 2020-04-15 | 18 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-15 19:00 | 2020-04-15 | 19 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-04-15 20:00 | 2020-04-15 | 20 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-15 21:00 | 2020-04-15 | 21 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-04-15 22:00 | 2020-04-15 | 22 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-15 23:00 | 2020-04-15 | 23 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-16 | 2020-04-15 | 0 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-16 01:00 | 2020-04-16 | 1 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-16 02:00 | 2020-04-16 | 2 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-16 03:00 | 2020-04-16 | 3 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-04-16 04:00 | 2020-04-16 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-16 05:00 | 2020-04-16 | 5 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-04-16 06:00 | 2020-04-16 | 6 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-16 07:00 | 2020-04-16 | 7 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-16 08:00 | 2020-04-16 | 8 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-16 09:00 | 2020-04-16 | 9 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-16 10:00 | 2020-04-16 | 10 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-16 11:00 | 2020-04-16 | 11 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-16 12:00 | 2020-04-16 | 12 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-04-16 13:00 | 2020-04-16 | 13 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-04-16 14:00 | 2020-04-16 | 14 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-04-16 15:00 | 2020-04-16 | 15 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-16 16:00 | 2020-04-16 | 16 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-04-16 17:00 | 2020-04-16 | 17 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-04-16 18:00 | 2020-04-16 | 18 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-16 19:00 | 2020-04-16 | 19 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-04-16 20:00 | 2020-04-16 | 20 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-04-16 21:00 | 2020-04-16 | 21 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-04-16 22:00 | 2020-04-16 | 22 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-16 23:00 | 2020-04-16 | 23 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-17 | 2020-04-16 | 0 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-17 01:00 | 2020-04-17 | 1 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-04-17 02:00 | 2020-04-17 | 2 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-17 03:00 | 2020-04-17 | 3 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-17 04:00 | 2020-04-17 | 4 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-04-17 05:00 | 2020-04-17 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-17 06:00 | 2020-04-17 | 6 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-17 07:00 | 2020-04-17 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-17 08:00 | 2020-04-17 | 8 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-17 09:00 | 2020-04-17 | 9 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-17 10:00 | 2020-04-17 | 10 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-17 11:00 | 2020-04-17 | 11 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-17 12:00 | 2020-04-17 | 12 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-04-17 13:00 | 2020-04-17 | 13 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-04-17 14:00 | 2020-04-17 | 14 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-04-17 15:00 | 2020-04-17 | 15 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-17 16:00 | 2020-04-17 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-17 17:00 | 2020-04-17 | 17 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-04-17 18:00 | 2020-04-17 | 18 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-17 19:00 | 2020-04-17 | 19 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-04-17 20:00 | 2020-04-17 | 20 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-17 21:00 | 2020-04-17 | 21 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-17 22:00 | 2020-04-17 | 22 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-17 23:00 | 2020-04-17 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-18 | 2020-04-17 | 0 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-04-18 01:00 | 2020-04-18 | 1 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-18 02:00 | 2020-04-18 | 2 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-18 03:00 | 2020-04-18 | 3 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-04-18 04:00 | 2020-04-18 | 4 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-04-18 05:00 | 2020-04-18 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-18 06:00 | 2020-04-18 | 6 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-18 07:00 | 2020-04-18 | 7 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-04-18 08:00 | 2020-04-18 | 8 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-18 09:00 | 2020-04-18 | 9 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-04-18 10:00 | 2020-04-18 | 10 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-04-18 11:00 | 2020-04-18 | 11 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-18 12:00 | 2020-04-18 | 12 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-18 13:00 | 2020-04-18 | 13 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-18 14:00 | 2020-04-18 | 14 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-18 15:00 | 2020-04-18 | 15 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-18 16:00 | 2020-04-18 | 16 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-18 17:00 | 2020-04-18 | 17 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-18 18:00 | 2020-04-18 | 18 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-18 19:00 | 2020-04-18 | 19 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-18 20:00 | 2020-04-18 | 20 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-18 21:00 | 2020-04-18 | 21 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-18 22:00 | 2020-04-18 | 22 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-18 23:00 | 2020-04-18 | 23 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-19 | 2020-04-18 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-19 01:00 | 2020-04-19 | 1 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-04-19 02:00 | 2020-04-19 | 2 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-19 03:00 | 2020-04-19 | 3 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-04-19 04:00 | 2020-04-19 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-19 05:00 | 2020-04-19 | 5 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-04-19 06:00 | 2020-04-19 | 6 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-04-19 07:00 | 2020-04-19 | 7 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-04-19 08:00 | 2020-04-19 | 8 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-19 09:00 | 2020-04-19 | 9 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-19 10:00 | 2020-04-19 | 10 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-19 11:00 | 2020-04-19 | 11 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-19 12:00 | 2020-04-19 | 12 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-04-19 13:00 | 2020-04-19 | 13 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-19 14:00 | 2020-04-19 | 14 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-04-19 15:00 | 2020-04-19 | 15 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-04-19 16:00 | 2020-04-19 | 16 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-04-19 17:00 | 2020-04-19 | 17 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-19 18:00 | 2020-04-19 | 18 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-19 19:00 | 2020-04-19 | 19 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-19 20:00 | 2020-04-19 | 20 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-19 21:00 | 2020-04-19 | 21 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-19 22:00 | 2020-04-19 | 22 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-19 23:00 | 2020-04-19 | 23 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-20 | 2020-04-19 | 0 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-04-20 01:00 | 2020-04-20 | 1 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-20 02:00 | 2020-04-20 | 2 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-04-20 03:00 | 2020-04-20 | 3 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-04-20 04:00 | 2020-04-20 | 4 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-20 05:00 | 2020-04-20 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-04-20 06:00 | 2020-04-20 | 6 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-20 07:00 | 2020-04-20 | 7 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-20 08:00 | 2020-04-20 | 8 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-20 09:00 | 2020-04-20 | 9 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-04-20 10:00 | 2020-04-20 | 10 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-20 11:00 | 2020-04-20 | 11 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-20 12:00 | 2020-04-20 | 12 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-20 13:00 | 2020-04-20 | 13 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-04-20 14:00 | 2020-04-20 | 14 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-04-20 15:00 | 2020-04-20 | 15 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-20 16:00 | 2020-04-20 | 16 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-20 17:00 | 2020-04-20 | 17 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-04-20 18:00 | 2020-04-20 | 18 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-20 19:00 | 2020-04-20 | 19 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-20 20:00 | 2020-04-20 | 20 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-04-20 21:00 | 2020-04-20 | 21 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-20 22:00 | 2020-04-20 | 22 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-20 23:00 | 2020-04-20 | 23 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-04-21 | 2020-04-20 | 0 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-21 01:00 | 2020-04-21 | 1 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-04-21 02:00 | 2020-04-21 | 2 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-21 03:00 | 2020-04-21 | 3 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-04-21 04:00 | 2020-04-21 | 4 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-04-21 05:00 | 2020-04-21 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-21 06:00 | 2020-04-21 | 6 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-21 07:00 | 2020-04-21 | 7 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-21 08:00 | 2020-04-21 | 8 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-21 09:00 | 2020-04-21 | 9 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-21 10:00 | 2020-04-21 | 10 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-04-21 11:00 | 2020-04-21 | 11 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-21 12:00 | 2020-04-21 | 12 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-21 13:00 | 2020-04-21 | 13 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-21 14:00 | 2020-04-21 | 14 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-21 15:00 | 2020-04-21 | 15 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-21 16:00 | 2020-04-21 | 16 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-04-21 17:00 | 2020-04-21 | 17 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-04-21 18:00 | 2020-04-21 | 18 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-21 19:00 | 2020-04-21 | 19 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-21 20:00 | 2020-04-21 | 20 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-04-21 21:00 | 2020-04-21 | 21 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-21 22:00 | 2020-04-21 | 22 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-21 23:00 | 2020-04-21 | 23 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-22 | 2020-04-21 | 0 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-22 01:00 | 2020-04-22 | 1 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-22 02:00 | 2020-04-22 | 2 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-04-22 03:00 | 2020-04-22 | 3 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-04-22 04:00 | 2020-04-22 | 4 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-04-22 05:00 | 2020-04-22 | 5 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-22 06:00 | 2020-04-22 | 6 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-04-22 07:00 | 2020-04-22 | 7 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-22 08:00 | 2020-04-22 | 8 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-22 09:00 | 2020-04-22 | 9 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-22 10:00 | 2020-04-22 | 10 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-22 11:00 | 2020-04-22 | 11 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-22 12:00 | 2020-04-22 | 12 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-22 13:00 | 2020-04-22 | 13 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-22 14:00 | 2020-04-22 | 14 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-04-22 15:00 | 2020-04-22 | 15 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-22 16:00 | 2020-04-22 | 16 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-22 17:00 | 2020-04-22 | 17 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-22 18:00 | 2020-04-22 | 18 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-22 19:00 | 2020-04-22 | 19 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-22 20:00 | 2020-04-22 | 20 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-04-22 21:00 | 2020-04-22 | 21 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-04-22 22:00 | 2020-04-22 | 22 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-22 23:00 | 2020-04-22 | 23 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-23 | 2020-04-22 | 0 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-23 01:00 | 2020-04-23 | 1 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-23 02:00 | 2020-04-23 | 2 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-23 03:00 | 2020-04-23 | 3 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-04-23 04:00 | 2020-04-23 | 4 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-04-23 05:00 | 2020-04-23 | 5 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-23 06:00 | 2020-04-23 | 6 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-23 07:00 | 2020-04-23 | 7 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-23 08:00 | 2020-04-23 | 8 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-23 09:00 | 2020-04-23 | 9 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-23 10:00 | 2020-04-23 | 10 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-04-23 11:00 | 2020-04-23 | 11 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-23 12:00 | 2020-04-23 | 12 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-23 13:00 | 2020-04-23 | 13 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-23 14:00 | 2020-04-23 | 14 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-23 15:00 | 2020-04-23 | 15 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-23 16:00 | 2020-04-23 | 16 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-04-23 17:00 | 2020-04-23 | 17 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-23 18:00 | 2020-04-23 | 18 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-04-23 19:00 | 2020-04-23 | 19 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-04-23 20:00 | 2020-04-23 | 20 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-23 21:00 | 2020-04-23 | 21 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-23 22:00 | 2020-04-23 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-04-23 23:00 | 2020-04-23 | 23 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-04-24 | 2020-04-23 | 0 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-04-24 01:00 | 2020-04-24 | 1 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-24 02:00 | 2020-04-24 | 2 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-04-24 03:00 | 2020-04-24 | 3 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-04-24 04:00 | 2020-04-24 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-24 05:00 | 2020-04-24 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-24 06:00 | 2020-04-24 | 6 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-04-24 07:00 | 2020-04-24 | 7 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-04-24 08:00 | 2020-04-24 | 8 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-24 09:00 | 2020-04-24 | 9 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-24 10:00 | 2020-04-24 | 10 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-24 11:00 | 2020-04-24 | 11 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-04-24 12:00 | 2020-04-24 | 12 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-04-24 13:00 | 2020-04-24 | 13 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-04-24 14:00 | 2020-04-24 | 14 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-04-24 15:00 | 2020-04-24 | 15 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-04-24 16:00 | 2020-04-24 | 16 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-04-24 17:00 | 2020-04-24 | 17 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-04-24 18:00 | 2020-04-24 | 18 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-24 19:00 | 2020-04-24 | 19 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-24 20:00 | 2020-04-24 | 20 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-24 21:00 | 2020-04-24 | 21 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-24 22:00 | 2020-04-24 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-24 23:00 | 2020-04-24 | 23 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-04-25 | 2020-04-24 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-25 01:00 | 2020-04-25 | 1 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-04-25 02:00 | 2020-04-25 | 2 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-25 03:00 | 2020-04-25 | 3 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-25 04:00 | 2020-04-25 | 4 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-25 05:00 | 2020-04-25 | 5 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-25 06:00 | 2020-04-25 | 6 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-04-25 07:00 | 2020-04-25 | 7 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-04-25 08:00 | 2020-04-25 | 8 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-04-25 09:00 | 2020-04-25 | 9 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-04-25 10:00 | 2020-04-25 | 10 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-04-25 11:00 | 2020-04-25 | 11 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-25 12:00 | 2020-04-25 | 12 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-04-25 13:00 | 2020-04-25 | 13 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-25 14:00 | 2020-04-25 | 14 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-04-25 15:00 | 2020-04-25 | 15 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-04-25 16:00 | 2020-04-25 | 16 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-04-25 17:00 | 2020-04-25 | 17 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-25 18:00 | 2020-04-25 | 18 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-25 19:00 | 2020-04-25 | 19 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-25 20:00 | 2020-04-25 | 20 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-25 21:00 | 2020-04-25 | 21 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-04-25 22:00 | 2020-04-25 | 22 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-04-25 23:00 | 2020-04-25 | 23 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-04-26 | 2020-04-25 | 0 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-26 01:00 | 2020-04-26 | 1 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-04-26 02:00 | 2020-04-26 | 2 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-04-26 03:00 | 2020-04-26 | 3 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-04-26 04:00 | 2020-04-26 | 4 | 1.9501 | 0.006771% | 2.9075 | 3.015 | 3.1265 | 3.2421 | 3.362 | 0 | 0 | 0 | 0 | 0
2020-04-26 05:00 | 2020-04-26 | 5 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-04-26 06:00 | 2020-04-26 | 6 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-04-26 07:00 | 2020-04-26 | 7 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-04-26 08:00 | 2020-04-26 | 8 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-04-26 09:00 | 2020-04-26 | 9 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-04-26 10:00 | 2020-04-26 | 10 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-26 11:00 | 2020-04-26 | 11 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-26 12:00 | 2020-04-26 | 12 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-26 13:00 | 2020-04-26 | 13 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-04-26 14:00 | 2020-04-26 | 14 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-26 15:00 | 2020-04-26 | 15 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-26 16:00 | 2020-04-26 | 16 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-26 17:00 | 2020-04-26 | 17 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-26 18:00 | 2020-04-26 | 18 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-26 19:00 | 2020-04-26 | 19 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-04-26 20:00 | 2020-04-26 | 20 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-04-26 21:00 | 2020-04-26 | 21 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-04-26 22:00 | 2020-04-26 | 22 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-04-26 23:00 | 2020-04-26 | 23 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-04-27 | 2020-04-26 | 0 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-04-27 01:00 | 2020-04-27 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-04-27 02:00 | 2020-04-27 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-04-27 03:00 | 2020-04-27 | 3 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-04-27 04:00 | 2020-04-27 | 4 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-04-27 05:00 | 2020-04-27 | 5 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-04-27 06:00 | 2020-04-27 | 6 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-04-27 07:00 | 2020-04-27 | 7 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-04-27 08:00 | 2020-04-27 | 8 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-04-27 09:00 | 2020-04-27 | 9 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-27 10:00 | 2020-04-27 | 10 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-27 11:00 | 2020-04-27 | 11 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-27 12:00 | 2020-04-27 | 12 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-27 13:00 | 2020-04-27 | 13 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-27 14:00 | 2020-04-27 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-04-27 15:00 | 2020-04-27 | 15 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-04-27 16:00 | 2020-04-27 | 16 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-27 17:00 | 2020-04-27 | 17 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-04-27 18:00 | 2020-04-27 | 18 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-27 19:00 | 2020-04-27 | 19 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-04-27 20:00 | 2020-04-27 | 20 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-04-27 21:00 | 2020-04-27 | 21 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-04-27 22:00 | 2020-04-27 | 22 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-04-27 23:00 | 2020-04-27 | 23 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-28 | 2020-04-27 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-28 01:00 | 2020-04-28 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-28 02:00 | 2020-04-28 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-04-28 03:00 | 2020-04-28 | 3 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-28 04:00 | 2020-04-28 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-04-28 05:00 | 2020-04-28 | 5 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-04-28 06:00 | 2020-04-28 | 6 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-04-28 07:00 | 2020-04-28 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-04-28 08:00 | 2020-04-28 | 8 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-04-28 09:00 | 2020-04-28 | 9 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-04-28 10:00 | 2020-04-28 | 10 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-28 11:00 | 2020-04-28 | 11 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-04-28 12:00 | 2020-04-28 | 12 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-04-28 13:00 | 2020-04-28 | 13 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-28 14:00 | 2020-04-28 | 14 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-04-28 15:00 | 2020-04-28 | 15 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-28 16:00 | 2020-04-28 | 16 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-28 17:00 | 2020-04-28 | 17 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-04-28 18:00 | 2020-04-28 | 18 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-04-28 19:00 | 2020-04-28 | 19 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-04-28 20:00 | 2020-04-28 | 20 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-28 21:00 | 2020-04-28 | 21 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-28 22:00 | 2020-04-28 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-04-28 23:00 | 2020-04-28 | 23 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-04-29 | 2020-04-28 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-04-29 01:00 | 2020-04-29 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-04-29 02:00 | 2020-04-29 | 2 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-04-29 03:00 | 2020-04-29 | 3 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-04-29 04:00 | 2020-04-29 | 4 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-04-29 05:00 | 2020-04-29 | 5 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-04-29 06:00 | 2020-04-29 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-04-29 07:00 | 2020-04-29 | 7 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-04-29 08:00 | 2020-04-29 | 8 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-04-29 09:00 | 2020-04-29 | 9 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-29 10:00 | 2020-04-29 | 10 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-04-29 11:00 | 2020-04-29 | 11 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-29 12:00 | 2020-04-29 | 12 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-04-29 13:00 | 2020-04-29 | 13 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-29 14:00 | 2020-04-29 | 14 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-04-29 15:00 | 2020-04-29 | 15 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-04-29 16:00 | 2020-04-29 | 16 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-04-29 17:00 | 2020-04-29 | 17 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-04-29 18:00 | 2020-04-29 | 18 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-04-29 19:00 | 2020-04-29 | 19 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-04-29 20:00 | 2020-04-29 | 20 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-04-29 21:00 | 2020-04-29 | 21 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-29 22:00 | 2020-04-29 | 22 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-04-29 23:00 | 2020-04-29 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-04-30 | 2020-04-29 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-04-30 01:00 | 2020-04-30 | 1 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-04-30 02:00 | 2020-04-30 | 2 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-04-30 03:00 | 2020-04-30 | 3 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-04-30 04:00 | 2020-04-30 | 4 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-04-30 05:00 | 2020-04-30 | 5 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-04-30 06:00 | 2020-04-30 | 6 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-04-30 07:00 | 2020-04-30 | 7 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-04-30 08:00 | 2020-04-30 | 8 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-04-30 09:00 | 2020-04-30 | 9 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-30 10:00 | 2020-04-30 | 10 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-04-30 11:00 | 2020-04-30 | 11 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-04-30 12:00 | 2020-04-30 | 12 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-04-30 13:00 | 2020-04-30 | 13 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-04-30 14:00 | 2020-04-30 | 14 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-04-30 15:00 | 2020-04-30 | 15 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-30 16:00 | 2020-04-30 | 16 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-04-30 17:00 | 2020-04-30 | 17 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-04-30 18:00 | 2020-04-30 | 18 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-04-30 19:00 | 2020-04-30 | 19 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-04-30 20:00 | 2020-04-30 | 20 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-04-30 21:00 | 2020-04-30 | 21 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-04-30 22:00 | 2020-04-30 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-04-30 23:00 | 2020-04-30 | 23 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-05-01 | 2020-04-30 | 0 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-01 01:00 | 2020-05-01 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-05-01 02:00 | 2020-05-01 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-01 03:00 | 2020-05-01 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-01 04:00 | 2020-05-01 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-01 05:00 | 2020-05-01 | 5 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-05-01 06:00 | 2020-05-01 | 6 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-05-01 07:00 | 2020-05-01 | 7 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-05-01 08:00 | 2020-05-01 | 8 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-01 09:00 | 2020-05-01 | 9 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-01 10:00 | 2020-05-01 | 10 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-01 11:00 | 2020-05-01 | 11 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-01 12:00 | 2020-05-01 | 12 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-05-01 13:00 | 2020-05-01 | 13 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-01 14:00 | 2020-05-01 | 14 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-01 15:00 | 2020-05-01 | 15 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-01 16:00 | 2020-05-01 | 16 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-01 17:00 | 2020-05-01 | 17 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-01 18:00 | 2020-05-01 | 18 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-05-01 19:00 | 2020-05-01 | 19 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-01 20:00 | 2020-05-01 | 20 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-01 21:00 | 2020-05-01 | 21 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-01 22:00 | 2020-05-01 | 22 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-01 23:00 | 2020-05-01 | 23 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-05-02 | 2020-05-01 | 0 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-05-02 01:00 | 2020-05-02 | 1 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-02 02:00 | 2020-05-02 | 2 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-05-02 03:00 | 2020-05-02 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-05-02 04:00 | 2020-05-02 | 4 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-05-02 05:00 | 2020-05-02 | 5 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-05-02 06:00 | 2020-05-02 | 6 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-02 07:00 | 2020-05-02 | 7 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-02 08:00 | 2020-05-02 | 8 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-02 09:00 | 2020-05-02 | 9 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-02 10:00 | 2020-05-02 | 10 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-02 11:00 | 2020-05-02 | 11 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-05-02 12:00 | 2020-05-02 | 12 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-02 13:00 | 2020-05-02 | 13 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-05-02 14:00 | 2020-05-02 | 14 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-05-02 15:00 | 2020-05-02 | 15 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-02 16:00 | 2020-05-02 | 16 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-02 17:00 | 2020-05-02 | 17 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-02 18:00 | 2020-05-02 | 18 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-05-02 19:00 | 2020-05-02 | 19 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-02 20:00 | 2020-05-02 | 20 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-02 21:00 | 2020-05-02 | 21 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-02 22:00 | 2020-05-02 | 22 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-05-02 23:00 | 2020-05-02 | 23 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-05-03 | 2020-05-02 | 0 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-03 01:00 | 2020-05-03 | 1 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-05-03 02:00 | 2020-05-03 | 2 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-05-03 03:00 | 2020-05-03 | 3 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-03 04:00 | 2020-05-03 | 4 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-05-03 05:00 | 2020-05-03 | 5 | 1.9501 | 0.006771% | 2.9075 | 3.015 | 3.1265 | 3.2421 | 3.362 | 0 | 0 | 0 | 0 | 0
2020-05-03 06:00 | 2020-05-03 | 6 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-05-03 07:00 | 2020-05-03 | 7 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-05-03 08:00 | 2020-05-03 | 8 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-03 09:00 | 2020-05-03 | 9 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-05-03 10:00 | 2020-05-03 | 10 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-03 11:00 | 2020-05-03 | 11 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-03 12:00 | 2020-05-03 | 12 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-03 13:00 | 2020-05-03 | 13 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-03 14:00 | 2020-05-03 | 14 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-05-03 15:00 | 2020-05-03 | 15 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-03 16:00 | 2020-05-03 | 16 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-05-03 17:00 | 2020-05-03 | 17 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-03 18:00 | 2020-05-03 | 18 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-03 19:00 | 2020-05-03 | 19 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-05-03 20:00 | 2020-05-03 | 20 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-03 21:00 | 2020-05-03 | 21 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-03 22:00 | 2020-05-03 | 22 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-03 23:00 | 2020-05-03 | 23 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-04 | 2020-05-03 | 0 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-04 01:00 | 2020-05-04 | 1 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-05-04 02:00 | 2020-05-04 | 2 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-04 03:00 | 2020-05-04 | 3 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-05-04 04:00 | 2020-05-04 | 4 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-04 05:00 | 2020-05-04 | 5 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-05-04 06:00 | 2020-05-04 | 6 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-05-04 07:00 | 2020-05-04 | 7 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-05-04 08:00 | 2020-05-04 | 8 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-04 09:00 | 2020-05-04 | 9 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-04 10:00 | 2020-05-04 | 10 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-04 11:00 | 2020-05-04 | 11 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-05-04 12:00 | 2020-05-04 | 12 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-04 13:00 | 2020-05-04 | 13 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-05-04 14:00 | 2020-05-04 | 14 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-04 15:00 | 2020-05-04 | 15 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-04 16:00 | 2020-05-04 | 16 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-04 17:00 | 2020-05-04 | 17 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-04 18:00 | 2020-05-04 | 18 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-04 19:00 | 2020-05-04 | 19 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-04 20:00 | 2020-05-04 | 20 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-04 21:00 | 2020-05-04 | 21 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-04 22:00 | 2020-05-04 | 22 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-05-04 23:00 | 2020-05-04 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-05-05 | 2020-05-04 | 0 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-05 01:00 | 2020-05-05 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-05-05 02:00 | 2020-05-05 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-05 03:00 | 2020-05-05 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-05 04:00 | 2020-05-05 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-05-05 05:00 | 2020-05-05 | 5 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-05-05 06:00 | 2020-05-05 | 6 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-05-05 07:00 | 2020-05-05 | 7 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-05-05 08:00 | 2020-05-05 | 8 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-05-05 09:00 | 2020-05-05 | 9 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-05 10:00 | 2020-05-05 | 10 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-05 11:00 | 2020-05-05 | 11 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-05 12:00 | 2020-05-05 | 12 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-05 13:00 | 2020-05-05 | 13 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-05 14:00 | 2020-05-05 | 14 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-05 15:00 | 2020-05-05 | 15 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-05 16:00 | 2020-05-05 | 16 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-05-05 17:00 | 2020-05-05 | 17 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-05 18:00 | 2020-05-05 | 18 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-05 19:00 | 2020-05-05 | 19 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-05 20:00 | 2020-05-05 | 20 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-05 21:00 | 2020-05-05 | 21 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-05 22:00 | 2020-05-05 | 22 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-05 23:00 | 2020-05-05 | 23 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-06 | 2020-05-05 | 0 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-06 01:00 | 2020-05-06 | 1 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-06 02:00 | 2020-05-06 | 2 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-05-06 03:00 | 2020-05-06 | 3 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-05-06 04:00 | 2020-05-06 | 4 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-06 05:00 | 2020-05-06 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-06 06:00 | 2020-05-06 | 6 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-05-06 07:00 | 2020-05-06 | 7 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-06 08:00 | 2020-05-06 | 8 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-06 09:00 | 2020-05-06 | 9 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-06 10:00 | 2020-05-06 | 10 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-06 11:00 | 2020-05-06 | 11 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-06 12:00 | 2020-05-06 | 12 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-06 13:00 | 2020-05-06 | 13 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-06 14:00 | 2020-05-06 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-05-06 15:00 | 2020-05-06 | 15 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-06 16:00 | 2020-05-06 | 16 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-06 17:00 | 2020-05-06 | 17 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-06 18:00 | 2020-05-06 | 18 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-06 19:00 | 2020-05-06 | 19 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-05-06 20:00 | 2020-05-06 | 20 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-05-06 21:00 | 2020-05-06 | 21 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-05-06 22:00 | 2020-05-06 | 22 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-05-06 23:00 | 2020-05-06 | 23 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-05-07 | 2020-05-06 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-05-07 01:00 | 2020-05-07 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-05-07 02:00 | 2020-05-07 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-07 03:00 | 2020-05-07 | 3 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-05-07 04:00 | 2020-05-07 | 4 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-07 05:00 | 2020-05-07 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-07 06:00 | 2020-05-07 | 6 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-05-07 07:00 | 2020-05-07 | 7 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-07 08:00 | 2020-05-07 | 8 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-07 09:00 | 2020-05-07 | 9 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-07 10:00 | 2020-05-07 | 10 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-07 11:00 | 2020-05-07 | 11 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-05-07 12:00 | 2020-05-07 | 12 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-07 13:00 | 2020-05-07 | 13 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-07 14:00 | 2020-05-07 | 14 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-05-07 15:00 | 2020-05-07 | 15 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-05-07 16:00 | 2020-05-07 | 16 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-05-07 17:00 | 2020-05-07 | 17 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-05-07 18:00 | 2020-05-07 | 18 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-07 19:00 | 2020-05-07 | 19 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-07 20:00 | 2020-05-07 | 20 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-05-07 21:00 | 2020-05-07 | 21 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-07 22:00 | 2020-05-07 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-07 23:00 | 2020-05-07 | 23 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-05-08 | 2020-05-07 | 0 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-08 01:00 | 2020-05-08 | 1 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-08 02:00 | 2020-05-08 | 2 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-08 03:00 | 2020-05-08 | 3 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-08 04:00 | 2020-05-08 | 4 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-08 05:00 | 2020-05-08 | 5 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-05-08 06:00 | 2020-05-08 | 6 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-05-08 07:00 | 2020-05-08 | 7 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-08 08:00 | 2020-05-08 | 8 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-08 09:00 | 2020-05-08 | 9 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-05-08 10:00 | 2020-05-08 | 10 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-05-08 11:00 | 2020-05-08 | 11 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-08 12:00 | 2020-05-08 | 12 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-08 13:00 | 2020-05-08 | 13 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-08 14:00 | 2020-05-08 | 14 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-08 15:00 | 2020-05-08 | 15 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-08 16:00 | 2020-05-08 | 16 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-05-08 17:00 | 2020-05-08 | 17 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-05-08 18:00 | 2020-05-08 | 18 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-08 19:00 | 2020-05-08 | 19 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-08 20:00 | 2020-05-08 | 20 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-05-08 21:00 | 2020-05-08 | 21 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-05-08 22:00 | 2020-05-08 | 22 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-05-08 23:00 | 2020-05-08 | 23 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-05-09 | 2020-05-08 | 0 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-09 01:00 | 2020-05-09 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-09 02:00 | 2020-05-09 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-09 03:00 | 2020-05-09 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-09 04:00 | 2020-05-09 | 4 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-09 05:00 | 2020-05-09 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-09 06:00 | 2020-05-09 | 6 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-09 07:00 | 2020-05-09 | 7 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-05-09 08:00 | 2020-05-09 | 8 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-09 09:00 | 2020-05-09 | 9 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-05-09 10:00 | 2020-05-09 | 10 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-09 11:00 | 2020-05-09 | 11 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-09 12:00 | 2020-05-09 | 12 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-05-09 13:00 | 2020-05-09 | 13 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-09 14:00 | 2020-05-09 | 14 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-05-09 15:00 | 2020-05-09 | 15 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-09 16:00 | 2020-05-09 | 16 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-09 17:00 | 2020-05-09 | 17 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-09 18:00 | 2020-05-09 | 18 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-09 19:00 | 2020-05-09 | 19 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-05-09 20:00 | 2020-05-09 | 20 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-09 21:00 | 2020-05-09 | 21 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-09 22:00 | 2020-05-09 | 22 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-09 23:00 | 2020-05-09 | 23 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-05-10 | 2020-05-09 | 0 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-05-10 01:00 | 2020-05-10 | 1 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-10 02:00 | 2020-05-10 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-10 03:00 | 2020-05-10 | 3 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-10 04:00 | 2020-05-10 | 4 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-05-10 05:00 | 2020-05-10 | 5 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-10 06:00 | 2020-05-10 | 6 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-10 07:00 | 2020-05-10 | 7 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-10 08:00 | 2020-05-10 | 8 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-05-10 09:00 | 2020-05-10 | 9 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-05-10 10:00 | 2020-05-10 | 10 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-05-10 11:00 | 2020-05-10 | 11 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-10 12:00 | 2020-05-10 | 12 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-05-10 13:00 | 2020-05-10 | 13 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-10 14:00 | 2020-05-10 | 14 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-05-10 15:00 | 2020-05-10 | 15 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-05-10 16:00 | 2020-05-10 | 16 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-10 17:00 | 2020-05-10 | 17 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-10 18:00 | 2020-05-10 | 18 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-10 19:00 | 2020-05-10 | 19 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-10 20:00 | 2020-05-10 | 20 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-10 21:00 | 2020-05-10 | 21 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-10 22:00 | 2020-05-10 | 22 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-05-10 23:00 | 2020-05-10 | 23 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-05-11 | 2020-05-10 | 0 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-05-11 01:00 | 2020-05-11 | 1 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-11 02:00 | 2020-05-11 | 2 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-05-11 03:00 | 2020-05-11 | 3 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-05-11 04:00 | 2020-05-11 | 4 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-05-11 05:00 | 2020-05-11 | 5 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-11 06:00 | 2020-05-11 | 6 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-11 07:00 | 2020-05-11 | 7 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-11 08:00 | 2020-05-11 | 8 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-05-11 09:00 | 2020-05-11 | 9 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-05-11 10:00 | 2020-05-11 | 10 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-05-11 11:00 | 2020-05-11 | 11 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-05-11 12:00 | 2020-05-11 | 12 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-05-11 13:00 | 2020-05-11 | 13 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-05-11 14:00 | 2020-05-11 | 14 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-11 15:00 | 2020-05-11 | 15 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-11 16:00 | 2020-05-11 | 16 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-05-11 17:00 | 2020-05-11 | 17 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-05-11 18:00 | 2020-05-11 | 18 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-05-11 19:00 | 2020-05-11 | 19 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-11 20:00 | 2020-05-11 | 20 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-05-11 21:00 | 2020-05-11 | 21 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-11 22:00 | 2020-05-11 | 22 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-11 23:00 | 2020-05-11 | 23 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-05-12 | 2020-05-11 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-05-12 01:00 | 2020-05-12 | 1 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-05-12 02:00 | 2020-05-12 | 2 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-05-12 03:00 | 2020-05-12 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-12 04:00 | 2020-05-12 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-05-12 05:00 | 2020-05-12 | 5 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-05-12 06:00 | 2020-05-12 | 6 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-12 07:00 | 2020-05-12 | 7 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-12 08:00 | 2020-05-12 | 8 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-12 09:00 | 2020-05-12 | 9 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-12 10:00 | 2020-05-12 | 10 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-12 11:00 | 2020-05-12 | 11 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-12 12:00 | 2020-05-12 | 12 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-12 13:00 | 2020-05-12 | 13 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-05-12 14:00 | 2020-05-12 | 14 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-05-12 15:00 | 2020-05-12 | 15 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-12 16:00 | 2020-05-12 | 16 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-12 17:00 | 2020-05-12 | 17 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-12 18:00 | 2020-05-12 | 18 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-12 19:00 | 2020-05-12 | 19 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-12 20:00 | 2020-05-12 | 20 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-05-12 21:00 | 2020-05-12 | 21 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-12 22:00 | 2020-05-12 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-12 23:00 | 2020-05-12 | 23 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-13 | 2020-05-12 | 0 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-05-13 01:00 | 2020-05-13 | 1 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-13 02:00 | 2020-05-13 | 2 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-13 03:00 | 2020-05-13 | 3 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-05-13 04:00 | 2020-05-13 | 4 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-05-13 05:00 | 2020-05-13 | 5 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-13 06:00 | 2020-05-13 | 6 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-05-13 07:00 | 2020-05-13 | 7 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-13 08:00 | 2020-05-13 | 8 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-13 09:00 | 2020-05-13 | 9 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-13 10:00 | 2020-05-13 | 10 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-05-13 11:00 | 2020-05-13 | 11 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-13 12:00 | 2020-05-13 | 12 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-13 13:00 | 2020-05-13 | 13 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-05-13 14:00 | 2020-05-13 | 14 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-13 15:00 | 2020-05-13 | 15 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-13 16:00 | 2020-05-13 | 16 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-05-13 17:00 | 2020-05-13 | 17 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-13 18:00 | 2020-05-13 | 18 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-13 19:00 | 2020-05-13 | 19 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-13 20:00 | 2020-05-13 | 20 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-05-13 21:00 | 2020-05-13 | 21 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-13 22:00 | 2020-05-13 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-13 23:00 | 2020-05-13 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-05-14 | 2020-05-13 | 0 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-14 01:00 | 2020-05-14 | 1 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-14 02:00 | 2020-05-14 | 2 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-05-14 03:00 | 2020-05-14 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-05-14 04:00 | 2020-05-14 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-14 05:00 | 2020-05-14 | 5 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-05-14 06:00 | 2020-05-14 | 6 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-05-14 07:00 | 2020-05-14 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-14 08:00 | 2020-05-14 | 8 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-14 09:00 | 2020-05-14 | 9 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-14 10:00 | 2020-05-14 | 10 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-05-14 11:00 | 2020-05-14 | 11 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-14 12:00 | 2020-05-14 | 12 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-14 13:00 | 2020-05-14 | 13 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-05-14 14:00 | 2020-05-14 | 14 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-14 15:00 | 2020-05-14 | 15 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-14 16:00 | 2020-05-14 | 16 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-14 17:00 | 2020-05-14 | 17 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-05-14 18:00 | 2020-05-14 | 18 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-05-14 19:00 | 2020-05-14 | 19 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-05-14 20:00 | 2020-05-14 | 20 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-14 21:00 | 2020-05-14 | 21 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-14 22:00 | 2020-05-14 | 22 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-14 23:00 | 2020-05-14 | 23 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-05-15 | 2020-05-14 | 0 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-15 01:00 | 2020-05-15 | 1 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-05-15 02:00 | 2020-05-15 | 2 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-05-15 03:00 | 2020-05-15 | 3 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-05-15 04:00 | 2020-05-15 | 4 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-15 05:00 | 2020-05-15 | 5 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-05-15 06:00 | 2020-05-15 | 6 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-05-15 07:00 | 2020-05-15 | 7 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-05-15 08:00 | 2020-05-15 | 8 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-05-15 09:00 | 2020-05-15 | 9 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-05-15 10:00 | 2020-05-15 | 10 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-05-15 11:00 | 2020-05-15 | 11 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-15 12:00 | 2020-05-15 | 12 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-05-15 13:00 | 2020-05-15 | 13 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-05-15 14:00 | 2020-05-15 | 14 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-05-15 15:00 | 2020-05-15 | 15 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-15 16:00 | 2020-05-15 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-05-15 17:00 | 2020-05-15 | 17 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-15 18:00 | 2020-05-15 | 18 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-15 19:00 | 2020-05-15 | 19 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-15 20:00 | 2020-05-15 | 20 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-15 21:00 | 2020-05-15 | 21 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-15 22:00 | 2020-05-15 | 22 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-05-15 23:00 | 2020-05-15 | 23 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-05-16 | 2020-05-15 | 0 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-16 01:00 | 2020-05-16 | 1 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-05-16 02:00 | 2020-05-16 | 2 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-16 03:00 | 2020-05-16 | 3 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-05-16 04:00 | 2020-05-16 | 4 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-05-16 05:00 | 2020-05-16 | 5 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-16 06:00 | 2020-05-16 | 6 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-05-16 07:00 | 2020-05-16 | 7 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-16 08:00 | 2020-05-16 | 8 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-16 09:00 | 2020-05-16 | 9 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-16 10:00 | 2020-05-16 | 10 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-16 11:00 | 2020-05-16 | 11 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-05-16 12:00 | 2020-05-16 | 12 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-16 13:00 | 2020-05-16 | 13 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-16 14:00 | 2020-05-16 | 14 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-05-16 15:00 | 2020-05-16 | 15 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-05-16 16:00 | 2020-05-16 | 16 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-16 17:00 | 2020-05-16 | 17 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-16 18:00 | 2020-05-16 | 18 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-16 19:00 | 2020-05-16 | 19 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-16 20:00 | 2020-05-16 | 20 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-16 21:00 | 2020-05-16 | 21 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-16 22:00 | 2020-05-16 | 22 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-05-16 23:00 | 2020-05-16 | 23 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-05-17 | 2020-05-16 | 0 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-05-17 01:00 | 2020-05-17 | 1 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-05-17 02:00 | 2020-05-17 | 2 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-17 03:00 | 2020-05-17 | 3 | 1.92 | 0.006667% | 2.8626 | 2.9684 | 3.0782 | 3.192 | 3.3101 | 0 | 0 | 0 | 0 | 0
2020-05-17 04:00 | 2020-05-17 | 4 | 1.9124 | 0.006641% | 2.8514 | 2.9568 | 3.0661 | 3.1795 | 3.2971 | 0 | 0 | 0 | 0 | 0
2020-05-17 05:00 | 2020-05-17 | 5 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-05-17 06:00 | 2020-05-17 | 6 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-05-17 07:00 | 2020-05-17 | 7 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-05-17 08:00 | 2020-05-17 | 8 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-05-17 09:00 | 2020-05-17 | 9 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-17 10:00 | 2020-05-17 | 10 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-17 11:00 | 2020-05-17 | 11 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-05-17 12:00 | 2020-05-17 | 12 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-05-17 13:00 | 2020-05-17 | 13 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-05-17 14:00 | 2020-05-17 | 14 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-05-17 15:00 | 2020-05-17 | 15 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-05-17 16:00 | 2020-05-17 | 16 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-05-17 17:00 | 2020-05-17 | 17 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-17 18:00 | 2020-05-17 | 18 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-17 19:00 | 2020-05-17 | 19 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-17 20:00 | 2020-05-17 | 20 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-05-17 21:00 | 2020-05-17 | 21 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-17 22:00 | 2020-05-17 | 22 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-05-17 23:00 | 2020-05-17 | 23 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-05-18 | 2020-05-17 | 0 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-05-18 01:00 | 2020-05-18 | 1 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-18 02:00 | 2020-05-18 | 2 | 1.935 | 0.006719% | 2.885 | 2.9917 | 3.1023 | 3.2171 | 3.336 | 0 | 0 | 0 | 0 | 0
2020-05-18 03:00 | 2020-05-18 | 3 | 1.8672 | 0.006484% | 2.784 | 2.8869 | 2.9937 | 3.1044 | 3.2192 | 0 | 0 | 0 | 0 | 0
2020-05-18 04:00 | 2020-05-18 | 4 | 1.9049 | 0.006614% | 2.8401 | 2.9451 | 3.0541 | 3.167 | 3.2841 | 0 | 0 | 0 | 0 | 0
2020-05-18 05:00 | 2020-05-18 | 5 | 1.8748 | 0.00651% | 2.7952 | 2.8986 | 3.0058 | 3.1169 | 3.2322 | 0 | 0 | 0 | 0 | 0
2020-05-18 06:00 | 2020-05-18 | 6 | 1.9501 | 0.006771% | 2.9075 | 3.015 | 3.1265 | 3.2421 | 3.362 | 0 | 0 | 0 | 0 | 0
2020-05-18 07:00 | 2020-05-18 | 7 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-05-18 08:00 | 2020-05-18 | 8 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-18 09:00 | 2020-05-18 | 9 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-05-18 10:00 | 2020-05-18 | 10 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-05-18 11:00 | 2020-05-18 | 11 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-18 12:00 | 2020-05-18 | 12 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-05-18 13:00 | 2020-05-18 | 13 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-18 14:00 | 2020-05-18 | 14 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-05-18 15:00 | 2020-05-18 | 15 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-18 16:00 | 2020-05-18 | 16 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-18 17:00 | 2020-05-18 | 17 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-05-18 18:00 | 2020-05-18 | 18 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-05-18 19:00 | 2020-05-18 | 19 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-18 20:00 | 2020-05-18 | 20 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-05-18 21:00 | 2020-05-18 | 21 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-05-18 22:00 | 2020-05-18 | 22 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-05-18 23:00 | 2020-05-18 | 23 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-19 | 2020-05-18 | 0 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-05-19 01:00 | 2020-05-19 | 1 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-05-19 02:00 | 2020-05-19 | 2 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-05-19 03:00 | 2020-05-19 | 3 | 1.9049 | 0.006614% | 2.8401 | 2.9451 | 3.0541 | 3.167 | 3.2841 | 0 | 0 | 0 | 0 | 0
2020-05-19 04:00 | 2020-05-19 | 4 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-05-19 05:00 | 2020-05-19 | 5 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-05-19 06:00 | 2020-05-19 | 6 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-05-19 07:00 | 2020-05-19 | 7 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-05-19 08:00 | 2020-05-19 | 8 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-05-19 09:00 | 2020-05-19 | 9 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-19 10:00 | 2020-05-19 | 10 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-19 11:00 | 2020-05-19 | 11 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-19 12:00 | 2020-05-19 | 12 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-19 13:00 | 2020-05-19 | 13 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-19 14:00 | 2020-05-19 | 14 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-19 15:00 | 2020-05-19 | 15 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-05-19 16:00 | 2020-05-19 | 16 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-05-19 17:00 | 2020-05-19 | 17 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-05-19 18:00 | 2020-05-19 | 18 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-19 19:00 | 2020-05-19 | 19 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-05-19 20:00 | 2020-05-19 | 20 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-19 21:00 | 2020-05-19 | 21 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-19 22:00 | 2020-05-19 | 22 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-19 23:00 | 2020-05-19 | 23 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-20 | 2020-05-19 | 0 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-20 01:00 | 2020-05-20 | 1 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-20 02:00 | 2020-05-20 | 2 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-05-20 03:00 | 2020-05-20 | 3 | 1.935 | 0.006719% | 2.885 | 2.9917 | 3.1023 | 3.2171 | 3.336 | 0 | 0 | 0 | 0 | 0
2020-05-20 04:00 | 2020-05-20 | 4 | 1.9501 | 0.006771% | 2.9075 | 3.015 | 3.1265 | 3.2421 | 3.362 | 0 | 0 | 0 | 0 | 0
2020-05-20 05:00 | 2020-05-20 | 5 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-20 06:00 | 2020-05-20 | 6 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-20 07:00 | 2020-05-20 | 7 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-20 08:00 | 2020-05-20 | 8 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-05-20 09:00 | 2020-05-20 | 9 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-05-20 10:00 | 2020-05-20 | 10 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-05-20 11:00 | 2020-05-20 | 11 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-05-20 12:00 | 2020-05-20 | 12 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-05-20 13:00 | 2020-05-20 | 13 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-05-20 14:00 | 2020-05-20 | 14 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-05-20 15:00 | 2020-05-20 | 15 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-20 16:00 | 2020-05-20 | 16 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-05-20 17:00 | 2020-05-20 | 17 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-05-20 18:00 | 2020-05-20 | 18 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-05-20 19:00 | 2020-05-20 | 19 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-05-20 20:00 | 2020-05-20 | 20 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-20 21:00 | 2020-05-20 | 21 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-20 22:00 | 2020-05-20 | 22 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-05-20 23:00 | 2020-05-20 | 23 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-05-21 | 2020-05-20 | 0 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-05-21 01:00 | 2020-05-21 | 1 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-05-21 02:00 | 2020-05-21 | 2 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-21 03:00 | 2020-05-21 | 3 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-05-21 04:00 | 2020-05-21 | 4 | 1.9501 | 0.006771% | 2.9075 | 3.015 | 3.1265 | 3.2421 | 3.362 | 0 | 0 | 0 | 0 | 0
2020-05-21 05:00 | 2020-05-21 | 5 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-05-21 06:00 | 2020-05-21 | 6 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-05-21 07:00 | 2020-05-21 | 7 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-05-21 08:00 | 2020-05-21 | 8 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-21 09:00 | 2020-05-21 | 9 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-05-21 10:00 | 2020-05-21 | 10 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-21 11:00 | 2020-05-21 | 11 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-21 12:00 | 2020-05-21 | 12 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-05-21 13:00 | 2020-05-21 | 13 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-05-21 14:00 | 2020-05-21 | 14 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-21 15:00 | 2020-05-21 | 15 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-21 16:00 | 2020-05-21 | 16 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-05-21 17:00 | 2020-05-21 | 17 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-05-21 18:00 | 2020-05-21 | 18 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-05-21 19:00 | 2020-05-21 | 19 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-05-21 20:00 | 2020-05-21 | 20 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-05-21 21:00 | 2020-05-21 | 21 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-05-21 22:00 | 2020-05-21 | 22 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-05-21 23:00 | 2020-05-21 | 23 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-05-22 | 2020-05-21 | 0 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-05-22 01:00 | 2020-05-22 | 1 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-22 02:00 | 2020-05-22 | 2 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-05-22 03:00 | 2020-05-22 | 3 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-05-22 04:00 | 2020-05-22 | 4 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-05-22 05:00 | 2020-05-22 | 5 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-05-22 06:00 | 2020-05-22 | 6 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-05-22 07:00 | 2020-05-22 | 7 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-05-22 08:00 | 2020-05-22 | 8 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-22 09:00 | 2020-05-22 | 9 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-05-22 10:00 | 2020-05-22 | 10 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-05-22 11:00 | 2020-05-22 | 11 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-05-22 12:00 | 2020-05-22 | 12 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-05-22 13:00 | 2020-05-22 | 13 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-05-22 14:00 | 2020-05-22 | 14 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-05-22 15:00 | 2020-05-22 | 15 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-05-22 16:00 | 2020-05-22 | 16 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-05-22 17:00 | 2020-05-22 | 17 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-05-22 18:00 | 2020-05-22 | 18 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-05-22 19:00 | 2020-05-22 | 19 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-05-22 20:00 | 2020-05-22 | 20 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-05-22 21:00 | 2020-05-22 | 21 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-05-22 22:00 | 2020-05-22 | 22 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-22 23:00 | 2020-05-22 | 23 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-23 | 2020-05-22 | 0 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-23 01:00 | 2020-05-23 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-05-23 02:00 | 2020-05-23 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-23 03:00 | 2020-05-23 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-05-23 04:00 | 2020-05-23 | 4 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-05-23 05:00 | 2020-05-23 | 5 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-05-23 06:00 | 2020-05-23 | 6 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-05-23 07:00 | 2020-05-23 | 7 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-05-23 08:00 | 2020-05-23 | 8 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-05-23 09:00 | 2020-05-23 | 9 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-05-23 10:00 | 2020-05-23 | 10 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-05-23 11:00 | 2020-05-23 | 11 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-05-23 12:00 | 2020-05-23 | 12 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-05-23 13:00 | 2020-05-23 | 13 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-05-23 14:00 | 2020-05-23 | 14 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-05-23 15:00 | 2020-05-23 | 15 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-05-23 16:00 | 2020-05-23 | 16 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-05-23 17:00 | 2020-05-23 | 17 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-05-23 18:00 | 2020-05-23 | 18 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-05-23 19:00 | 2020-05-23 | 19 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-05-23 20:00 | 2020-05-23 | 20 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-05-23 21:00 | 2020-05-23 | 21 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-05-23 22:00 | 2020-05-23 | 22 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-05-23 23:00 | 2020-05-23 | 23 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-05-24 | 2020-05-23 | 0 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-05-24 01:00 | 2020-05-24 | 1 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-05-24 02:00 | 2020-05-24 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-24 03:00 | 2020-05-24 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-24 04:00 | 2020-05-24 | 4 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-05-24 05:00 | 2020-05-24 | 5 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-05-24 06:00 | 2020-05-24 | 6 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-05-24 07:00 | 2020-05-24 | 7 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-05-24 08:00 | 2020-05-24 | 8 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-05-24 09:00 | 2020-05-24 | 9 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-24 10:00 | 2020-05-24 | 10 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-05-24 11:00 | 2020-05-24 | 11 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-05-24 12:00 | 2020-05-24 | 12 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-05-24 13:00 | 2020-05-24 | 13 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-05-24 14:00 | 2020-05-24 | 14 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-05-24 15:00 | 2020-05-24 | 15 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-05-24 16:00 | 2020-05-24 | 16 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-05-24 17:00 | 2020-05-24 | 17 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-05-24 18:00 | 2020-05-24 | 18 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-05-24 19:00 | 2020-05-24 | 19 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-05-24 20:00 | 2020-05-24 | 20 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-05-24 21:00 | 2020-05-24 | 21 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-05-24 22:00 | 2020-05-24 | 22 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-05-24 23:00 | 2020-05-24 | 23 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-05-25 | 2020-05-24 | 0 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-05-25 01:00 | 2020-05-25 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-05-25 02:00 | 2020-05-25 | 2 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-05-25 03:00 | 2020-05-25 | 3 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-05-25 04:00 | 2020-05-25 | 4 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-05-25 05:00 | 2020-05-25 | 5 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-05-25 06:00 | 2020-05-25 | 6 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-05-25 07:00 | 2020-05-25 | 7 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-25 08:00 | 2020-05-25 | 8 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-05-25 09:00 | 2020-05-25 | 9 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-05-25 10:00 | 2020-05-25 | 10 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-05-25 11:00 | 2020-05-25 | 11 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-05-25 12:00 | 2020-05-25 | 12 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-05-25 13:00 | 2020-05-25 | 13 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-05-25 14:00 | 2020-05-25 | 14 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-05-25 15:00 | 2020-05-25 | 15 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 1
2020-05-25 16:00 | 2020-05-25 | 16 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 2
2020-05-25 17:00 | 2020-05-25 | 17 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 3
2020-05-25 18:00 | 2020-05-25 | 18 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 4
2020-05-25 19:00 | 2020-05-25 | 19 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 5
2020-05-25 20:00 | 2020-05-25 | 20 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 6 | 6
2020-05-25 21:00 | 2020-05-25 | 21 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-05-25 22:00 | 2020-05-25 | 22 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-05-25 23:00 | 2020-05-25 | 23 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-05-26 | 2020-05-25 | 0 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-05-26 01:00 | 2020-05-26 | 1 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-26 02:00 | 2020-05-26 | 2 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-05-26 03:00 | 2020-05-26 | 3 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-05-26 04:00 | 2020-05-26 | 4 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-05-26 05:00 | 2020-05-26 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-05-26 06:00 | 2020-05-26 | 6 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-26 07:00 | 2020-05-26 | 7 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-26 08:00 | 2020-05-26 | 8 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-05-26 09:00 | 2020-05-26 | 9 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-05-26 10:00 | 2020-05-26 | 10 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-05-26 11:00 | 2020-05-26 | 11 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 2
2020-05-26 12:00 | 2020-05-26 | 12 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 3
2020-05-26 13:00 | 2020-05-26 | 13 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 4
2020-05-26 14:00 | 2020-05-26 | 14 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 5
2020-05-26 15:00 | 2020-05-26 | 15 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 6
2020-05-26 16:00 | 2020-05-26 | 16 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 7
2020-05-26 17:00 | 2020-05-26 | 17 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 8
2020-05-26 18:00 | 2020-05-26 | 18 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 9
2020-05-26 19:00 | 2020-05-26 | 19 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 10
2020-05-26 20:00 | 2020-05-26 | 20 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 11
2020-05-26 21:00 | 2020-05-26 | 21 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 12
2020-05-26 22:00 | 2020-05-26 | 22 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 13 | 13
2020-05-26 23:00 | 2020-05-26 | 23 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-05-27 | 2020-05-26 | 0 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-05-27 01:00 | 2020-05-27 | 1 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-05-27 02:00 | 2020-05-27 | 2 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-27 03:00 | 2020-05-27 | 3 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-05-27 04:00 | 2020-05-27 | 4 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-27 05:00 | 2020-05-27 | 5 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-27 06:00 | 2020-05-27 | 6 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-05-27 07:00 | 2020-05-27 | 7 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-05-27 08:00 | 2020-05-27 | 8 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-05-27 09:00 | 2020-05-27 | 9 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1
2020-05-27 10:00 | 2020-05-27 | 10 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 2
2020-05-27 11:00 | 2020-05-27 | 11 | 4.5702 | 0.01587% | 6.8141 | 7.066 | 7.3273 | 7.5983 | 7.8792 | 1.0771 | 1.329 | 1.5903 | 1.8613 | 2.1422 | 3
2020-05-27 12:00 | 2020-05-27 | 12 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 4
2020-05-27 13:00 | 2020-05-27 | 13 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 5
2020-05-27 14:00 | 2020-05-27 | 14 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 6
2020-05-27 15:00 | 2020-05-27 | 15 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 7
2020-05-27 16:00 | 2020-05-27 | 16 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 8
2020-05-27 17:00 | 2020-05-27 | 17 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 9
2020-05-27 18:00 | 2020-05-27 | 18 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 10
2020-05-27 19:00 | 2020-05-27 | 19 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 11
2020-05-27 20:00 | 2020-05-27 | 20 | 4.382 | 0.01522% | 6.5334 | 6.775 | 7.0255 | 7.2853 | 7.5547 | 0.79641 | 1.038 | 1.2885 | 1.5483 | 1.8177 | 12
2020-05-27 21:00 | 2020-05-27 | 21 | 4.2239 | 0.01467% | 6.2977 | 6.5305 | 6.772 | 7.0225 | 7.2821 | 0.56067 | 0.79355 | 1.035 | 1.2855 | 1.5451 | 13 | 13
2020-05-27 22:00 | 2020-05-27 | 22 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-05-27 23:00 | 2020-05-27 | 23 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-05-28 | 2020-05-27 | 0 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-05-28 01:00 | 2020-05-28 | 1 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-05-28 02:00 | 2020-05-28 | 2 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-05-28 03:00 | 2020-05-28 | 3 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-05-28 04:00 | 2020-05-28 | 4 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-05-28 05:00 | 2020-05-28 | 5 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-28 06:00 | 2020-05-28 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-28 07:00 | 2020-05-28 | 7 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-05-28 08:00 | 2020-05-28 | 8 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-05-28 09:00 | 2020-05-28 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-05-28 10:00 | 2020-05-28 | 10 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-05-28 11:00 | 2020-05-28 | 11 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-05-28 12:00 | 2020-05-28 | 12 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 1
2020-05-28 13:00 | 2020-05-28 | 13 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 2
2020-05-28 14:00 | 2020-05-28 | 14 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 3
2020-05-28 15:00 | 2020-05-28 | 15 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 4
2020-05-28 16:00 | 2020-05-28 | 16 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 5
2020-05-28 17:00 | 2020-05-28 | 17 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 6 | 6
2020-05-28 18:00 | 2020-05-28 | 18 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-05-28 19:00 | 2020-05-28 | 19 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-05-28 20:00 | 2020-05-28 | 20 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-05-28 21:00 | 2020-05-28 | 21 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-05-28 22:00 | 2020-05-28 | 22 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-05-28 23:00 | 2020-05-28 | 23 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-05-29 | 2020-05-28 | 0 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-05-29 01:00 | 2020-05-29 | 1 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-29 02:00 | 2020-05-29 | 2 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-05-29 03:00 | 2020-05-29 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-05-29 04:00 | 2020-05-29 | 4 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-05-29 05:00 | 2020-05-29 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-05-29 06:00 | 2020-05-29 | 6 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-05-29 07:00 | 2020-05-29 | 7 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-05-29 08:00 | 2020-05-29 | 8 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-05-29 09:00 | 2020-05-29 | 9 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-05-29 10:00 | 2020-05-29 | 10 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-05-29 11:00 | 2020-05-29 | 11 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-05-29 12:00 | 2020-05-29 | 12 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-05-29 13:00 | 2020-05-29 | 13 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 1
2020-05-29 14:00 | 2020-05-29 | 14 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 2 | 2
2020-05-29 15:00 | 2020-05-29 | 15 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-05-29 16:00 | 2020-05-29 | 16 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-05-29 17:00 | 2020-05-29 | 17 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-05-29 18:00 | 2020-05-29 | 18 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-05-29 19:00 | 2020-05-29 | 19 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-05-29 20:00 | 2020-05-29 | 20 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-05-29 21:00 | 2020-05-29 | 21 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-05-29 22:00 | 2020-05-29 | 22 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-05-29 23:00 | 2020-05-29 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-05-30 | 2020-05-29 | 0 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-05-30 01:00 | 2020-05-30 | 1 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-05-30 02:00 | 2020-05-30 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-05-30 03:00 | 2020-05-30 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-05-30 04:00 | 2020-05-30 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-05-30 05:00 | 2020-05-30 | 5 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-05-30 06:00 | 2020-05-30 | 6 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-05-30 07:00 | 2020-05-30 | 7 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-05-30 08:00 | 2020-05-30 | 8 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-05-30 09:00 | 2020-05-30 | 9 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-05-30 10:00 | 2020-05-30 | 10 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-05-30 11:00 | 2020-05-30 | 11 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-05-30 12:00 | 2020-05-30 | 12 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-05-30 13:00 | 2020-05-30 | 13 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-05-30 14:00 | 2020-05-30 | 14 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-05-30 15:00 | 2020-05-30 | 15 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-05-30 16:00 | 2020-05-30 | 16 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-05-30 17:00 | 2020-05-30 | 17 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-05-30 18:00 | 2020-05-30 | 18 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-30 19:00 | 2020-05-30 | 19 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-05-30 20:00 | 2020-05-30 | 20 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-05-30 21:00 | 2020-05-30 | 21 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-05-30 22:00 | 2020-05-30 | 22 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-05-30 23:00 | 2020-05-30 | 23 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-05-31 | 2020-05-30 | 0 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-05-31 01:00 | 2020-05-31 | 1 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-05-31 02:00 | 2020-05-31 | 2 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-05-31 03:00 | 2020-05-31 | 3 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-05-31 04:00 | 2020-05-31 | 4 | 1.9275 | 0.006693% | 2.8738 | 2.9801 | 3.0903 | 3.2045 | 3.323 | 0 | 0 | 0 | 0 | 0
2020-05-31 05:00 | 2020-05-31 | 5 | 1.9275 | 0.006693% | 2.8738 | 2.9801 | 3.0903 | 3.2045 | 3.323 | 0 | 0 | 0 | 0 | 0
2020-05-31 06:00 | 2020-05-31 | 6 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-05-31 07:00 | 2020-05-31 | 7 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-05-31 08:00 | 2020-05-31 | 8 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-05-31 09:00 | 2020-05-31 | 9 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-05-31 10:00 | 2020-05-31 | 10 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-05-31 11:00 | 2020-05-31 | 11 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-05-31 12:00 | 2020-05-31 | 12 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-31 13:00 | 2020-05-31 | 13 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-05-31 14:00 | 2020-05-31 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-05-31 15:00 | 2020-05-31 | 15 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-05-31 16:00 | 2020-05-31 | 16 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-05-31 17:00 | 2020-05-31 | 17 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-05-31 18:00 | 2020-05-31 | 18 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-05-31 19:00 | 2020-05-31 | 19 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-05-31 20:00 | 2020-05-31 | 20 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-05-31 21:00 | 2020-05-31 | 21 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-05-31 22:00 | 2020-05-31 | 22 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-05-31 23:00 | 2020-05-31 | 23 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-06-01 | 2020-05-31 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-06-01 01:00 | 2020-06-01 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-06-01 02:00 | 2020-06-01 | 2 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-06-01 03:00 | 2020-06-01 | 3 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-06-01 04:00 | 2020-06-01 | 4 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-06-01 05:00 | 2020-06-01 | 5 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-06-01 06:00 | 2020-06-01 | 6 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-06-01 07:00 | 2020-06-01 | 7 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-06-01 08:00 | 2020-06-01 | 8 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-06-01 09:00 | 2020-06-01 | 9 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-06-01 10:00 | 2020-06-01 | 10 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-01 11:00 | 2020-06-01 | 11 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-06-01 12:00 | 2020-06-01 | 12 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-06-01 13:00 | 2020-06-01 | 13 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-06-01 14:00 | 2020-06-01 | 14 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-06-01 15:00 | 2020-06-01 | 15 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-06-01 16:00 | 2020-06-01 | 16 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-06-01 17:00 | 2020-06-01 | 17 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-06-01 18:00 | 2020-06-01 | 18 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-06-01 19:00 | 2020-06-01 | 19 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-06-01 20:00 | 2020-06-01 | 20 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-06-01 21:00 | 2020-06-01 | 21 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-06-01 22:00 | 2020-06-01 | 22 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-06-01 23:00 | 2020-06-01 | 23 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-06-02 | 2020-06-01 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-06-02 01:00 | 2020-06-02 | 1 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-06-02 02:00 | 2020-06-02 | 2 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-06-02 03:00 | 2020-06-02 | 3 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-06-02 04:00 | 2020-06-02 | 4 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-06-02 05:00 | 2020-06-02 | 5 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-06-02 06:00 | 2020-06-02 | 6 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-06-02 07:00 | 2020-06-02 | 7 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-06-02 08:00 | 2020-06-02 | 8 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-06-02 09:00 | 2020-06-02 | 9 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-06-02 10:00 | 2020-06-02 | 10 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-06-02 11:00 | 2020-06-02 | 11 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-06-02 12:00 | 2020-06-02 | 12 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-06-02 13:00 | 2020-06-02 | 13 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-06-02 14:00 | 2020-06-02 | 14 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-06-02 15:00 | 2020-06-02 | 15 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-06-02 16:00 | 2020-06-02 | 16 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-06-02 17:00 | 2020-06-02 | 17 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-06-02 18:00 | 2020-06-02 | 18 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-06-02 19:00 | 2020-06-02 | 19 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-06-02 20:00 | 2020-06-02 | 20 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-06-02 21:00 | 2020-06-02 | 21 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-06-02 22:00 | 2020-06-02 | 22 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-06-02 23:00 | 2020-06-02 | 23 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-06-03 | 2020-06-02 | 0 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-06-03 01:00 | 2020-06-03 | 1 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-06-03 02:00 | 2020-06-03 | 2 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-06-03 03:00 | 2020-06-03 | 3 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-06-03 04:00 | 2020-06-03 | 4 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-06-03 05:00 | 2020-06-03 | 5 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-06-03 06:00 | 2020-06-03 | 6 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-06-03 07:00 | 2020-06-03 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-06-03 08:00 | 2020-06-03 | 8 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-06-03 09:00 | 2020-06-03 | 9 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-06-03 10:00 | 2020-06-03 | 10 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-06-03 11:00 | 2020-06-03 | 11 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-06-03 12:00 | 2020-06-03 | 12 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-06-03 13:00 | 2020-06-03 | 13 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-06-03 14:00 | 2020-06-03 | 14 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-06-03 15:00 | 2020-06-03 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-06-03 16:00 | 2020-06-03 | 16 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-06-03 17:00 | 2020-06-03 | 17 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-06-03 18:00 | 2020-06-03 | 18 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-06-03 19:00 | 2020-06-03 | 19 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-06-03 20:00 | 2020-06-03 | 20 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-06-03 21:00 | 2020-06-03 | 21 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-03 22:00 | 2020-06-03 | 22 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-06-03 23:00 | 2020-06-03 | 23 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-06-04 | 2020-06-03 | 0 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-06-04 01:00 | 2020-06-04 | 1 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-06-04 02:00 | 2020-06-04 | 2 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-06-04 03:00 | 2020-06-04 | 3 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-06-04 04:00 | 2020-06-04 | 4 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-06-04 05:00 | 2020-06-04 | 5 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-06-04 06:00 | 2020-06-04 | 6 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-06-04 07:00 | 2020-06-04 | 7 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-04 08:00 | 2020-06-04 | 8 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-04 09:00 | 2020-06-04 | 9 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-06-04 10:00 | 2020-06-04 | 10 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-06-04 11:00 | 2020-06-04 | 11 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-06-04 12:00 | 2020-06-04 | 12 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-06-04 13:00 | 2020-06-04 | 13 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-06-04 14:00 | 2020-06-04 | 14 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-06-04 15:00 | 2020-06-04 | 15 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-06-04 16:00 | 2020-06-04 | 16 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 2
2020-06-04 17:00 | 2020-06-04 | 17 | 4.2314 | 0.01469% | 6.3089 | 6.5422 | 6.7841 | 7.035 | 7.2951 | 0.5719 | 0.80519 | 1.0471 | 1.298 | 1.5581 | 3
2020-06-04 18:00 | 2020-06-04 | 18 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 4
2020-06-04 19:00 | 2020-06-04 | 19 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 5 | 5
2020-06-04 20:00 | 2020-06-04 | 20 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-06-04 21:00 | 2020-06-04 | 21 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-06-04 22:00 | 2020-06-04 | 22 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-06-04 23:00 | 2020-06-04 | 23 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-06-05 | 2020-06-04 | 0 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-06-05 01:00 | 2020-06-05 | 1 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-06-05 02:00 | 2020-06-05 | 2 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-06-05 03:00 | 2020-06-05 | 3 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-06-05 04:00 | 2020-06-05 | 4 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-06-05 05:00 | 2020-06-05 | 5 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-05 06:00 | 2020-06-05 | 6 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-06-05 07:00 | 2020-06-05 | 7 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-06-05 08:00 | 2020-06-05 | 8 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-06-05 09:00 | 2020-06-05 | 9 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-06-05 10:00 | 2020-06-05 | 10 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-06-05 11:00 | 2020-06-05 | 11 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-06-05 12:00 | 2020-06-05 | 12 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 2
2020-06-05 13:00 | 2020-06-05 | 13 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 3
2020-06-05 14:00 | 2020-06-05 | 14 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 4
2020-06-05 15:00 | 2020-06-05 | 15 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 5
2020-06-05 16:00 | 2020-06-05 | 16 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 6
2020-06-05 17:00 | 2020-06-05 | 17 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 7
2020-06-05 18:00 | 2020-06-05 | 18 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 8
2020-06-05 19:00 | 2020-06-05 | 19 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 9 | 9
2020-06-05 20:00 | 2020-06-05 | 20 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-06-05 21:00 | 2020-06-05 | 21 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-06-05 22:00 | 2020-06-05 | 22 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-06-05 23:00 | 2020-06-05 | 23 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-06-06 | 2020-06-05 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-06-06 01:00 | 2020-06-06 | 1 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-06-06 02:00 | 2020-06-06 | 2 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-06-06 03:00 | 2020-06-06 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-06-06 04:00 | 2020-06-06 | 4 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-06-06 05:00 | 2020-06-06 | 5 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-06-06 06:00 | 2020-06-06 | 6 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-06-06 07:00 | 2020-06-06 | 7 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-06-06 08:00 | 2020-06-06 | 8 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-06-06 09:00 | 2020-06-06 | 9 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-06-06 10:00 | 2020-06-06 | 10 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-06-06 11:00 | 2020-06-06 | 11 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-06-06 12:00 | 2020-06-06 | 12 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-06-06 13:00 | 2020-06-06 | 13 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-06-06 14:00 | 2020-06-06 | 14 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-06-06 15:00 | 2020-06-06 | 15 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-06-06 16:00 | 2020-06-06 | 16 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-06-06 17:00 | 2020-06-06 | 17 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-06-06 18:00 | 2020-06-06 | 18 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-06-06 19:00 | 2020-06-06 | 19 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-06-06 20:00 | 2020-06-06 | 20 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-06 21:00 | 2020-06-06 | 21 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-06-06 22:00 | 2020-06-06 | 22 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-06-06 23:00 | 2020-06-06 | 23 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-06-07 | 2020-06-06 | 0 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-06-07 01:00 | 2020-06-07 | 1 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-06-07 02:00 | 2020-06-07 | 2 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-06-07 03:00 | 2020-06-07 | 3 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-06-07 04:00 | 2020-06-07 | 4 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-06-07 05:00 | 2020-06-07 | 5 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-06-07 06:00 | 2020-06-07 | 6 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-06-07 07:00 | 2020-06-07 | 7 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-06-07 08:00 | 2020-06-07 | 8 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-06-07 09:00 | 2020-06-07 | 9 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-06-07 10:00 | 2020-06-07 | 10 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-06-07 11:00 | 2020-06-07 | 11 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-06-07 12:00 | 2020-06-07 | 12 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-06-07 13:00 | 2020-06-07 | 13 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-06-07 14:00 | 2020-06-07 | 14 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-06-07 15:00 | 2020-06-07 | 15 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-06-07 16:00 | 2020-06-07 | 16 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-06-07 17:00 | 2020-06-07 | 17 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-07 18:00 | 2020-06-07 | 18 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-06-07 19:00 | 2020-06-07 | 19 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-06-07 20:00 | 2020-06-07 | 20 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-06-07 21:00 | 2020-06-07 | 21 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-06-07 22:00 | 2020-06-07 | 22 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-06-07 23:00 | 2020-06-07 | 23 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-06-08 | 2020-06-07 | 0 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-06-08 01:00 | 2020-06-08 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-06-08 02:00 | 2020-06-08 | 2 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-06-08 03:00 | 2020-06-08 | 3 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-06-08 04:00 | 2020-06-08 | 4 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-06-08 05:00 | 2020-06-08 | 5 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-06-08 06:00 | 2020-06-08 | 6 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-06-08 07:00 | 2020-06-08 | 7 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-06-08 08:00 | 2020-06-08 | 8 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-06-08 09:00 | 2020-06-08 | 9 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-06-08 10:00 | 2020-06-08 | 10 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-06-08 11:00 | 2020-06-08 | 11 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-06-08 12:00 | 2020-06-08 | 12 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-06-08 13:00 | 2020-06-08 | 13 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-06-08 14:00 | 2020-06-08 | 14 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-06-08 15:00 | 2020-06-08 | 15 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-06-08 16:00 | 2020-06-08 | 16 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-06-08 17:00 | 2020-06-08 | 17 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-06-08 18:00 | 2020-06-08 | 18 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-06-08 19:00 | 2020-06-08 | 19 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-06-08 20:00 | 2020-06-08 | 20 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-06-08 21:00 | 2020-06-08 | 21 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-06-08 22:00 | 2020-06-08 | 22 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-08 23:00 | 2020-06-08 | 23 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-06-09 | 2020-06-08 | 0 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-06-09 01:00 | 2020-06-09 | 1 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-06-09 02:00 | 2020-06-09 | 2 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-06-09 03:00 | 2020-06-09 | 3 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-06-09 04:00 | 2020-06-09 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-06-09 05:00 | 2020-06-09 | 5 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-06-09 06:00 | 2020-06-09 | 6 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-06-09 07:00 | 2020-06-09 | 7 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-06-09 08:00 | 2020-06-09 | 8 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-06-09 09:00 | 2020-06-09 | 9 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-06-09 10:00 | 2020-06-09 | 10 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-06-09 11:00 | 2020-06-09 | 11 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-06-09 12:00 | 2020-06-09 | 12 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-06-09 13:00 | 2020-06-09 | 13 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-06-09 14:00 | 2020-06-09 | 14 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 2
2020-06-09 15:00 | 2020-06-09 | 15 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 3
2020-06-09 16:00 | 2020-06-09 | 16 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 4
2020-06-09 17:00 | 2020-06-09 | 17 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 5
2020-06-09 18:00 | 2020-06-09 | 18 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 6
2020-06-09 19:00 | 2020-06-09 | 19 | 4.254 | 0.01477% | 6.3426 | 6.5771 | 6.8203 | 7.0725 | 7.3341 | 0.60557 | 0.84011 | 1.0833 | 1.3355 | 1.5971 | 7
2020-06-09 20:00 | 2020-06-09 | 20 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 8 | 8
2020-06-09 21:00 | 2020-06-09 | 21 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-06-09 22:00 | 2020-06-09 | 22 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-06-09 23:00 | 2020-06-09 | 23 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-06-10 | 2020-06-09 | 0 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-06-10 01:00 | 2020-06-10 | 1 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-06-10 02:00 | 2020-06-10 | 2 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-06-10 03:00 | 2020-06-10 | 3 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-06-10 04:00 | 2020-06-10 | 4 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-06-10 05:00 | 2020-06-10 | 5 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-06-10 06:00 | 2020-06-10 | 6 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-06-10 07:00 | 2020-06-10 | 7 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-06-10 08:00 | 2020-06-10 | 8 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-06-10 09:00 | 2020-06-10 | 9 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-06-10 10:00 | 2020-06-10 | 10 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-06-10 11:00 | 2020-06-10 | 11 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-06-10 12:00 | 2020-06-10 | 12 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 1
2020-06-10 13:00 | 2020-06-10 | 13 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 2
2020-06-10 14:00 | 2020-06-10 | 14 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 3
2020-06-10 15:00 | 2020-06-10 | 15 | 4.6681 | 0.01621% | 6.96 | 7.2174 | 7.4842 | 7.761 | 8.048 | 1.223 | 1.4804 | 1.7472 | 2.024 | 2.311 | 4
2020-06-10 16:00 | 2020-06-10 | 16 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 5
2020-06-10 17:00 | 2020-06-10 | 17 | 4.9166 | 0.01707% | 7.3304 | 7.6015 | 7.8826 | 8.1741 | 8.4764 | 1.5934 | 1.8645 | 2.1456 | 2.4371 | 2.7394 | 6
2020-06-10 18:00 | 2020-06-10 | 18 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 7
2020-06-10 19:00 | 2020-06-10 | 19 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 8
2020-06-10 20:00 | 2020-06-10 | 20 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 9
2020-06-10 21:00 | 2020-06-10 | 21 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 10
2020-06-10 22:00 | 2020-06-10 | 22 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 11 | 11
2020-06-10 23:00 | 2020-06-10 | 23 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-06-11 | 2020-06-10 | 0 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-06-11 01:00 | 2020-06-11 | 1 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-06-11 02:00 | 2020-06-11 | 2 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-06-11 03:00 | 2020-06-11 | 3 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-06-11 04:00 | 2020-06-11 | 4 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-06-11 05:00 | 2020-06-11 | 5 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-06-11 06:00 | 2020-06-11 | 6 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-06-11 07:00 | 2020-06-11 | 7 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-06-11 08:00 | 2020-06-11 | 8 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-06-11 09:00 | 2020-06-11 | 9 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-06-11 10:00 | 2020-06-11 | 10 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-06-11 11:00 | 2020-06-11 | 11 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-06-11 12:00 | 2020-06-11 | 12 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-06-11 13:00 | 2020-06-11 | 13 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-06-11 14:00 | 2020-06-11 | 14 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-06-11 15:00 | 2020-06-11 | 15 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-06-11 16:00 | 2020-06-11 | 16 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-06-11 17:00 | 2020-06-11 | 17 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-06-11 18:00 | 2020-06-11 | 18 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-06-11 19:00 | 2020-06-11 | 19 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-06-11 20:00 | 2020-06-11 | 20 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-06-11 21:00 | 2020-06-11 | 21 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-06-11 22:00 | 2020-06-11 | 22 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-06-11 23:00 | 2020-06-11 | 23 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-06-12 | 2020-06-11 | 0 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-06-12 01:00 | 2020-06-12 | 1 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-06-12 02:00 | 2020-06-12 | 2 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-12 03:00 | 2020-06-12 | 3 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-06-12 04:00 | 2020-06-12 | 4 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-06-12 05:00 | 2020-06-12 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-06-12 06:00 | 2020-06-12 | 6 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-06-12 07:00 | 2020-06-12 | 7 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-06-12 08:00 | 2020-06-12 | 8 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-06-12 09:00 | 2020-06-12 | 9 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-06-12 10:00 | 2020-06-12 | 10 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-06-12 11:00 | 2020-06-12 | 11 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-06-12 12:00 | 2020-06-12 | 12 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-06-12 13:00 | 2020-06-12 | 13 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-06-12 14:00 | 2020-06-12 | 14 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-06-12 15:00 | 2020-06-12 | 15 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-06-12 16:00 | 2020-06-12 | 16 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-06-12 17:00 | 2020-06-12 | 17 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-06-12 18:00 | 2020-06-12 | 18 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-06-12 19:00 | 2020-06-12 | 19 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-06-12 20:00 | 2020-06-12 | 20 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-12 21:00 | 2020-06-12 | 21 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-06-12 22:00 | 2020-06-12 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-06-12 23:00 | 2020-06-12 | 23 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-06-13 | 2020-06-12 | 0 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-06-13 01:00 | 2020-06-13 | 1 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-06-13 02:00 | 2020-06-13 | 2 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-06-13 03:00 | 2020-06-13 | 3 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-06-13 04:00 | 2020-06-13 | 4 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-06-13 05:00 | 2020-06-13 | 5 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-06-13 06:00 | 2020-06-13 | 6 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-06-13 07:00 | 2020-06-13 | 7 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-06-13 08:00 | 2020-06-13 | 8 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-06-13 09:00 | 2020-06-13 | 9 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-06-13 10:00 | 2020-06-13 | 10 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-06-13 11:00 | 2020-06-13 | 11 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-06-13 12:00 | 2020-06-13 | 12 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-06-13 13:00 | 2020-06-13 | 13 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-06-13 14:00 | 2020-06-13 | 14 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-06-13 15:00 | 2020-06-13 | 15 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-06-13 16:00 | 2020-06-13 | 16 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-06-13 17:00 | 2020-06-13 | 17 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-06-13 18:00 | 2020-06-13 | 18 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-06-13 19:00 | 2020-06-13 | 19 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-06-13 20:00 | 2020-06-13 | 20 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-13 21:00 | 2020-06-13 | 21 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-06-13 22:00 | 2020-06-13 | 22 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-06-13 23:00 | 2020-06-13 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-06-14 | 2020-06-13 | 0 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-06-14 01:00 | 2020-06-14 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-06-14 02:00 | 2020-06-14 | 2 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-06-14 03:00 | 2020-06-14 | 3 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-06-14 04:00 | 2020-06-14 | 4 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-06-14 05:00 | 2020-06-14 | 5 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-06-14 06:00 | 2020-06-14 | 6 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-06-14 07:00 | 2020-06-14 | 7 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-06-14 08:00 | 2020-06-14 | 8 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-06-14 09:00 | 2020-06-14 | 9 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-06-14 10:00 | 2020-06-14 | 10 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-06-14 11:00 | 2020-06-14 | 11 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-06-14 12:00 | 2020-06-14 | 12 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-06-14 13:00 | 2020-06-14 | 13 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-14 14:00 | 2020-06-14 | 14 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-06-14 15:00 | 2020-06-14 | 15 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-06-14 16:00 | 2020-06-14 | 16 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-06-14 17:00 | 2020-06-14 | 17 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-06-14 18:00 | 2020-06-14 | 18 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-06-14 19:00 | 2020-06-14 | 19 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-06-14 20:00 | 2020-06-14 | 20 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-06-14 21:00 | 2020-06-14 | 21 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-06-14 22:00 | 2020-06-14 | 22 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-06-14 23:00 | 2020-06-14 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-06-15 | 2020-06-14 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-06-15 01:00 | 2020-06-15 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-06-15 02:00 | 2020-06-15 | 2 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-06-15 03:00 | 2020-06-15 | 3 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-06-15 04:00 | 2020-06-15 | 4 | 1.9651 | 0.006824% | 2.9299 | 3.0383 | 3.1506 | 3.2671 | 3.3879 | 0 | 0 | 0 | 0 | 0
2020-06-15 05:00 | 2020-06-15 | 5 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-06-15 06:00 | 2020-06-15 | 6 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-06-15 07:00 | 2020-06-15 | 7 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-06-15 08:00 | 2020-06-15 | 8 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-06-15 09:00 | 2020-06-15 | 9 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-06-15 10:00 | 2020-06-15 | 10 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-06-15 11:00 | 2020-06-15 | 11 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-15 12:00 | 2020-06-15 | 12 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-06-15 13:00 | 2020-06-15 | 13 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-06-15 14:00 | 2020-06-15 | 14 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-06-15 15:00 | 2020-06-15 | 15 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-06-15 16:00 | 2020-06-15 | 16 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-06-15 17:00 | 2020-06-15 | 17 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-06-15 18:00 | 2020-06-15 | 18 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-06-15 19:00 | 2020-06-15 | 19 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-06-15 20:00 | 2020-06-15 | 20 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-06-15 21:00 | 2020-06-15 | 21 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-15 22:00 | 2020-06-15 | 22 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-06-15 23:00 | 2020-06-15 | 23 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-06-16 | 2020-06-15 | 0 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-06-16 01:00 | 2020-06-16 | 1 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-06-16 02:00 | 2020-06-16 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-06-16 03:00 | 2020-06-16 | 3 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-06-16 04:00 | 2020-06-16 | 4 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-06-16 05:00 | 2020-06-16 | 5 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-06-16 06:00 | 2020-06-16 | 6 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-06-16 07:00 | 2020-06-16 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-06-16 08:00 | 2020-06-16 | 8 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-06-16 09:00 | 2020-06-16 | 9 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-06-16 10:00 | 2020-06-16 | 10 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-16 11:00 | 2020-06-16 | 11 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-06-16 12:00 | 2020-06-16 | 12 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-06-16 13:00 | 2020-06-16 | 13 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-06-16 14:00 | 2020-06-16 | 14 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-06-16 15:00 | 2020-06-16 | 15 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-06-16 16:00 | 2020-06-16 | 16 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 2
2020-06-16 17:00 | 2020-06-16 | 17 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 3
2020-06-16 18:00 | 2020-06-16 | 18 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 4
2020-06-16 19:00 | 2020-06-16 | 19 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 5 | 5
2020-06-16 20:00 | 2020-06-16 | 20 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-06-16 21:00 | 2020-06-16 | 21 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-06-16 22:00 | 2020-06-16 | 22 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-06-16 23:00 | 2020-06-16 | 23 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-06-17 | 2020-06-16 | 0 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-06-17 01:00 | 2020-06-17 | 1 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-06-17 02:00 | 2020-06-17 | 2 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-17 03:00 | 2020-06-17 | 3 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-06-17 04:00 | 2020-06-17 | 4 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-06-17 05:00 | 2020-06-17 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-06-17 06:00 | 2020-06-17 | 6 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-06-17 07:00 | 2020-06-17 | 7 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-06-17 08:00 | 2020-06-17 | 8 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-06-17 09:00 | 2020-06-17 | 9 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-06-17 10:00 | 2020-06-17 | 10 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-06-17 11:00 | 2020-06-17 | 11 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-06-17 12:00 | 2020-06-17 | 12 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 1
2020-06-17 13:00 | 2020-06-17 | 13 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 2
2020-06-17 14:00 | 2020-06-17 | 14 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 3
2020-06-17 15:00 | 2020-06-17 | 15 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 4
2020-06-17 16:00 | 2020-06-17 | 16 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 5
2020-06-17 17:00 | 2020-06-17 | 17 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 6
2020-06-17 18:00 | 2020-06-17 | 18 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 7
2020-06-17 19:00 | 2020-06-17 | 19 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 8
2020-06-17 20:00 | 2020-06-17 | 20 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 9 | 9
2020-06-17 21:00 | 2020-06-17 | 21 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-06-17 22:00 | 2020-06-17 | 22 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-06-17 23:00 | 2020-06-17 | 23 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-06-18 | 2020-06-17 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-06-18 01:00 | 2020-06-18 | 1 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-06-18 02:00 | 2020-06-18 | 2 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-06-18 03:00 | 2020-06-18 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-06-18 04:00 | 2020-06-18 | 4 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-18 05:00 | 2020-06-18 | 5 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-06-18 06:00 | 2020-06-18 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-06-18 07:00 | 2020-06-18 | 7 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-06-18 08:00 | 2020-06-18 | 8 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-06-18 09:00 | 2020-06-18 | 9 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-06-18 10:00 | 2020-06-18 | 10 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 1
2020-06-18 11:00 | 2020-06-18 | 11 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 2
2020-06-18 12:00 | 2020-06-18 | 12 | 4.6681 | 0.01621% | 6.96 | 7.2174 | 7.4842 | 7.761 | 8.048 | 1.223 | 1.4804 | 1.7472 | 2.024 | 2.311 | 3
2020-06-18 13:00 | 2020-06-18 | 13 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 4
2020-06-18 14:00 | 2020-06-18 | 14 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 5
2020-06-18 15:00 | 2020-06-18 | 15 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 6
2020-06-18 16:00 | 2020-06-18 | 16 | 5.1274 | 0.0178% | 7.6448 | 7.9275 | 8.2206 | 8.5246 | 8.8398 | 1.9078 | 2.1905 | 2.4836 | 2.7876 | 3.1028 | 7
2020-06-18 17:00 | 2020-06-18 | 17 | 4.9467 | 0.01718% | 7.3753 | 7.6481 | 7.9309 | 8.2242 | 8.5283 | 1.6383 | 1.9111 | 2.1939 | 2.4872 | 2.7913 | 8
2020-06-18 18:00 | 2020-06-18 | 18 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 9
2020-06-18 19:00 | 2020-06-18 | 19 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 10
2020-06-18 20:00 | 2020-06-18 | 20 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 11
2020-06-18 21:00 | 2020-06-18 | 21 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 12 | 12
2020-06-18 22:00 | 2020-06-18 | 22 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-06-18 23:00 | 2020-06-18 | 23 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-06-19 | 2020-06-18 | 0 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-19 01:00 | 2020-06-19 | 1 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-06-19 02:00 | 2020-06-19 | 2 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-06-19 03:00 | 2020-06-19 | 3 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-06-19 04:00 | 2020-06-19 | 4 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-06-19 05:00 | 2020-06-19 | 5 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-06-19 06:00 | 2020-06-19 | 6 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-06-19 07:00 | 2020-06-19 | 7 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-06-19 08:00 | 2020-06-19 | 8 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-06-19 09:00 | 2020-06-19 | 9 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 1
2020-06-19 10:00 | 2020-06-19 | 10 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 2
2020-06-19 11:00 | 2020-06-19 | 11 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 3
2020-06-19 12:00 | 2020-06-19 | 12 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 4
2020-06-19 13:00 | 2020-06-19 | 13 | 4.9166 | 0.01707% | 7.3304 | 7.6015 | 7.8826 | 8.1741 | 8.4764 | 1.5934 | 1.8645 | 2.1456 | 2.4371 | 2.7394 | 5
2020-06-19 14:00 | 2020-06-19 | 14 | 4.9467 | 0.01718% | 7.3753 | 7.6481 | 7.9309 | 8.2242 | 8.5283 | 1.6383 | 1.9111 | 2.1939 | 2.4872 | 2.7913 | 6
2020-06-19 15:00 | 2020-06-19 | 15 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 7
2020-06-19 16:00 | 2020-06-19 | 16 | 5.1349 | 0.01783% | 7.656 | 7.9391 | 8.2327 | 8.5371 | 8.8528 | 1.919 | 2.2021 | 2.4957 | 2.8001 | 3.1158 | 8
2020-06-19 17:00 | 2020-06-19 | 17 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 9
2020-06-19 18:00 | 2020-06-19 | 18 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 10
2020-06-19 19:00 | 2020-06-19 | 19 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 11
2020-06-19 20:00 | 2020-06-19 | 20 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 12
2020-06-19 21:00 | 2020-06-19 | 21 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 13 | 13
2020-06-19 22:00 | 2020-06-19 | 22 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-06-19 23:00 | 2020-06-19 | 23 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-06-20 | 2020-06-19 | 0 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-06-20 01:00 | 2020-06-20 | 1 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-06-20 02:00 | 2020-06-20 | 2 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-06-20 03:00 | 2020-06-20 | 3 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-06-20 04:00 | 2020-06-20 | 4 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-06-20 05:00 | 2020-06-20 | 5 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-06-20 06:00 | 2020-06-20 | 6 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-06-20 07:00 | 2020-06-20 | 7 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-06-20 08:00 | 2020-06-20 | 8 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-06-20 09:00 | 2020-06-20 | 9 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-06-20 10:00 | 2020-06-20 | 10 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 1
2020-06-20 11:00 | 2020-06-20 | 11 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 2
2020-06-20 12:00 | 2020-06-20 | 12 | 4.6606 | 0.01618% | 6.9488 | 7.2057 | 7.4722 | 7.7485 | 8.035 | 1.2118 | 1.4687 | 1.7352 | 2.0115 | 2.298 | 3
2020-06-20 13:00 | 2020-06-20 | 13 | 4.7811 | 0.0166% | 7.1284 | 7.392 | 7.6653 | 7.9488 | 8.2427 | 1.3914 | 1.655 | 1.9283 | 2.2118 | 2.5057 | 4
2020-06-20 14:00 | 2020-06-20 | 14 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 5
2020-06-20 15:00 | 2020-06-20 | 15 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 6
2020-06-20 16:00 | 2020-06-20 | 16 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 7
2020-06-20 17:00 | 2020-06-20 | 17 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 8
2020-06-20 18:00 | 2020-06-20 | 18 | 4.9919 | 0.01733% | 7.4427 | 7.7179 | 8.0033 | 8.2993 | 8.6062 | 1.7057 | 1.9809 | 2.2663 | 2.5623 | 2.8692 | 9
2020-06-20 19:00 | 2020-06-20 | 19 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 10
2020-06-20 20:00 | 2020-06-20 | 20 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 11
2020-06-20 21:00 | 2020-06-20 | 21 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 12 | 12
2020-06-20 22:00 | 2020-06-20 | 22 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-06-20 23:00 | 2020-06-20 | 23 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-06-21 | 2020-06-20 | 0 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-06-21 01:00 | 2020-06-21 | 1 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-06-21 02:00 | 2020-06-21 | 2 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-06-21 03:00 | 2020-06-21 | 3 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-06-21 04:00 | 2020-06-21 | 4 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-06-21 05:00 | 2020-06-21 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-06-21 06:00 | 2020-06-21 | 6 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-06-21 07:00 | 2020-06-21 | 7 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-06-21 08:00 | 2020-06-21 | 8 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-06-21 09:00 | 2020-06-21 | 9 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-06-21 10:00 | 2020-06-21 | 10 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 1
2020-06-21 11:00 | 2020-06-21 | 11 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 2
2020-06-21 12:00 | 2020-06-21 | 12 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 3
2020-06-21 13:00 | 2020-06-21 | 13 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 4
2020-06-21 14:00 | 2020-06-21 | 14 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 5
2020-06-21 15:00 | 2020-06-21 | 15 | 5.0822 | 0.01765% | 7.5774 | 7.8576 | 8.1482 | 8.4495 | 8.7619 | 1.8404 | 2.1206 | 2.4112 | 2.7125 | 3.0249 | 6
2020-06-21 16:00 | 2020-06-21 | 16 | 5.1801 | 0.01799% | 7.7233 | 8.0089 | 8.3051 | 8.6122 | 8.9307 | 1.9863 | 2.2719 | 2.5681 | 2.8752 | 3.1937 | 7
2020-06-21 17:00 | 2020-06-21 | 17 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 8
2020-06-21 18:00 | 2020-06-21 | 18 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 9
2020-06-21 19:00 | 2020-06-21 | 19 | 4.9618 | 0.01723% | 7.3978 | 7.6714 | 7.955 | 8.2492 | 8.5542 | 1.6608 | 1.9344 | 2.218 | 2.5122 | 2.8172 | 10
2020-06-21 20:00 | 2020-06-21 | 20 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 11
2020-06-21 21:00 | 2020-06-21 | 21 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 12
2020-06-21 22:00 | 2020-06-21 | 22 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 13 | 13
2020-06-21 23:00 | 2020-06-21 | 23 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-06-22 | 2020-06-21 | 0 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-06-22 01:00 | 2020-06-22 | 1 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-06-22 02:00 | 2020-06-22 | 2 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-06-22 03:00 | 2020-06-22 | 3 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-06-22 04:00 | 2020-06-22 | 4 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-06-22 05:00 | 2020-06-22 | 5 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-06-22 06:00 | 2020-06-22 | 6 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-06-22 07:00 | 2020-06-22 | 7 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-06-22 08:00 | 2020-06-22 | 8 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1
2020-06-22 09:00 | 2020-06-22 | 9 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 2
2020-06-22 10:00 | 2020-06-22 | 10 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 3
2020-06-22 11:00 | 2020-06-22 | 11 | 4.9919 | 0.01733% | 7.4427 | 7.7179 | 8.0033 | 8.2993 | 8.6062 | 1.7057 | 1.9809 | 2.2663 | 2.5623 | 2.8692 | 4
2020-06-22 12:00 | 2020-06-22 | 12 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 5
2020-06-22 13:00 | 2020-06-22 | 13 | 5.3759 | 0.01867% | 8.0152 | 8.3116 | 8.619 | 8.9377 | 9.2682 | 2.2782 | 2.5746 | 2.882 | 3.2007 | 3.5312 | 6
2020-06-22 14:00 | 2020-06-22 | 14 | 5.4286 | 0.01885% | 8.0938 | 8.3931 | 8.7035 | 9.0253 | 9.359 | 2.3568 | 2.6561 | 2.9665 | 3.2883 | 3.622 | 7
2020-06-22 15:00 | 2020-06-22 | 15 | 5.534 | 0.01922% | 8.251 | 8.5561 | 8.8725 | 9.2005 | 9.5408 | 2.514 | 2.8191 | 3.1355 | 3.4635 | 3.8038 | 8
2020-06-22 16:00 | 2020-06-22 | 16 | 5.5189 | 0.01916% | 8.2285 | 8.5328 | 8.8483 | 9.1755 | 9.5148 | 2.4915 | 2.7958 | 3.1113 | 3.4385 | 3.7778 | 9
2020-06-22 17:00 | 2020-06-22 | 17 | 5.4286 | 0.01885% | 8.0938 | 8.3931 | 8.7035 | 9.0253 | 9.359 | 2.3568 | 2.6561 | 2.9665 | 3.2883 | 3.622 | 10
2020-06-22 18:00 | 2020-06-22 | 18 | 5.4662 | 0.01898% | 8.1499 | 8.4513 | 8.7638 | 9.0879 | 9.4239 | 2.4129 | 2.7143 | 3.0268 | 3.3509 | 3.6869 | 11
2020-06-22 19:00 | 2020-06-22 | 19 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 12
2020-06-22 20:00 | 2020-06-22 | 20 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 13
2020-06-22 21:00 | 2020-06-22 | 21 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 14
2020-06-22 22:00 | 2020-06-22 | 22 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 15 | 15
2020-06-22 23:00 | 2020-06-22 | 23 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-06-23 | 2020-06-22 | 0 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-06-23 01:00 | 2020-06-23 | 1 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-06-23 02:00 | 2020-06-23 | 2 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-06-23 03:00 | 2020-06-23 | 3 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-06-23 04:00 | 2020-06-23 | 4 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-06-23 05:00 | 2020-06-23 | 5 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-06-23 06:00 | 2020-06-23 | 6 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-06-23 07:00 | 2020-06-23 | 7 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-06-23 08:00 | 2020-06-23 | 8 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 1
2020-06-23 09:00 | 2020-06-23 | 9 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 2
2020-06-23 10:00 | 2020-06-23 | 10 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 3
2020-06-23 11:00 | 2020-06-23 | 11 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 4
2020-06-23 12:00 | 2020-06-23 | 12 | 4.9919 | 0.01733% | 7.4427 | 7.7179 | 8.0033 | 8.2993 | 8.6062 | 1.7057 | 1.9809 | 2.2663 | 2.5623 | 2.8692 | 5
2020-06-23 13:00 | 2020-06-23 | 13 | 5.1274 | 0.0178% | 7.6448 | 7.9275 | 8.2206 | 8.5246 | 8.8398 | 1.9078 | 2.1905 | 2.4836 | 2.7876 | 3.1028 | 6
2020-06-23 14:00 | 2020-06-23 | 14 | 5.2253 | 0.01814% | 7.7907 | 8.0788 | 8.3775 | 8.6873 | 9.0086 | 2.0537 | 2.3418 | 2.6405 | 2.9503 | 3.2716 | 7
2020-06-23 15:00 | 2020-06-23 | 15 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 8
2020-06-23 16:00 | 2020-06-23 | 16 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 9
2020-06-23 17:00 | 2020-06-23 | 17 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 10
2020-06-23 18:00 | 2020-06-23 | 18 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 11
2020-06-23 19:00 | 2020-06-23 | 19 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 12
2020-06-23 20:00 | 2020-06-23 | 20 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 13 | 13
2020-06-23 21:00 | 2020-06-23 | 21 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-06-23 22:00 | 2020-06-23 | 22 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-06-23 23:00 | 2020-06-23 | 23 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-06-24 | 2020-06-23 | 0 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-06-24 01:00 | 2020-06-24 | 1 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-06-24 02:00 | 2020-06-24 | 2 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-06-24 03:00 | 2020-06-24 | 3 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-06-24 04:00 | 2020-06-24 | 4 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-06-24 05:00 | 2020-06-24 | 5 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-06-24 06:00 | 2020-06-24 | 6 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-06-24 07:00 | 2020-06-24 | 7 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-06-24 08:00 | 2020-06-24 | 8 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-06-24 09:00 | 2020-06-24 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-06-24 10:00 | 2020-06-24 | 10 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-06-24 11:00 | 2020-06-24 | 11 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-06-24 12:00 | 2020-06-24 | 12 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-06-24 13:00 | 2020-06-24 | 13 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-06-24 14:00 | 2020-06-24 | 14 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-06-24 15:00 | 2020-06-24 | 15 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-06-24 16:00 | 2020-06-24 | 16 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-06-24 17:00 | 2020-06-24 | 17 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-06-24 18:00 | 2020-06-24 | 18 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-06-24 19:00 | 2020-06-24 | 19 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-06-24 20:00 | 2020-06-24 | 20 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-06-24 21:00 | 2020-06-24 | 21 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-06-24 22:00 | 2020-06-24 | 22 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-06-24 23:00 | 2020-06-24 | 23 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-06-25 | 2020-06-24 | 0 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-06-25 01:00 | 2020-06-25 | 1 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-06-25 02:00 | 2020-06-25 | 2 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-25 03:00 | 2020-06-25 | 3 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-06-25 04:00 | 2020-06-25 | 4 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-06-25 05:00 | 2020-06-25 | 5 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-06-25 06:00 | 2020-06-25 | 6 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-06-25 07:00 | 2020-06-25 | 7 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-06-25 08:00 | 2020-06-25 | 8 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-06-25 09:00 | 2020-06-25 | 9 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-06-25 10:00 | 2020-06-25 | 10 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-06-25 11:00 | 2020-06-25 | 11 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-06-25 12:00 | 2020-06-25 | 12 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-06-25 13:00 | 2020-06-25 | 13 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-06-25 14:00 | 2020-06-25 | 14 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-06-25 15:00 | 2020-06-25 | 15 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1
2020-06-25 16:00 | 2020-06-25 | 16 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 2
2020-06-25 17:00 | 2020-06-25 | 17 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 3
2020-06-25 18:00 | 2020-06-25 | 18 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 4
2020-06-25 19:00 | 2020-06-25 | 19 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 5 | 5
2020-06-25 20:00 | 2020-06-25 | 20 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-06-25 21:00 | 2020-06-25 | 21 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-06-25 22:00 | 2020-06-25 | 22 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-06-25 23:00 | 2020-06-25 | 23 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-06-26 | 2020-06-25 | 0 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-06-26 01:00 | 2020-06-26 | 1 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-06-26 02:00 | 2020-06-26 | 2 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-06-26 03:00 | 2020-06-26 | 3 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-06-26 04:00 | 2020-06-26 | 4 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-06-26 05:00 | 2020-06-26 | 5 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-06-26 06:00 | 2020-06-26 | 6 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-06-26 07:00 | 2020-06-26 | 7 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-26 08:00 | 2020-06-26 | 8 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-06-26 09:00 | 2020-06-26 | 9 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-06-26 10:00 | 2020-06-26 | 10 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-06-26 11:00 | 2020-06-26 | 11 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 1
2020-06-26 12:00 | 2020-06-26 | 12 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 2
2020-06-26 13:00 | 2020-06-26 | 13 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 3
2020-06-26 14:00 | 2020-06-26 | 14 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 4
2020-06-26 15:00 | 2020-06-26 | 15 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 5
2020-06-26 16:00 | 2020-06-26 | 16 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 6
2020-06-26 17:00 | 2020-06-26 | 17 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 7
2020-06-26 18:00 | 2020-06-26 | 18 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 8
2020-06-26 19:00 | 2020-06-26 | 19 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 9
2020-06-26 20:00 | 2020-06-26 | 20 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 10 | 10
2020-06-26 21:00 | 2020-06-26 | 21 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-06-26 22:00 | 2020-06-26 | 22 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-06-26 23:00 | 2020-06-26 | 23 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-06-27 | 2020-06-26 | 0 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-06-27 01:00 | 2020-06-27 | 1 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-06-27 02:00 | 2020-06-27 | 2 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-06-27 03:00 | 2020-06-27 | 3 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-06-27 04:00 | 2020-06-27 | 4 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-06-27 05:00 | 2020-06-27 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-06-27 06:00 | 2020-06-27 | 6 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-06-27 07:00 | 2020-06-27 | 7 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-06-27 08:00 | 2020-06-27 | 8 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-06-27 09:00 | 2020-06-27 | 9 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-06-27 10:00 | 2020-06-27 | 10 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-06-27 11:00 | 2020-06-27 | 11 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-06-27 12:00 | 2020-06-27 | 12 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-06-27 13:00 | 2020-06-27 | 13 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-06-27 14:00 | 2020-06-27 | 14 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-06-27 15:00 | 2020-06-27 | 15 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-06-27 16:00 | 2020-06-27 | 16 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 1
2020-06-27 17:00 | 2020-06-27 | 17 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 2
2020-06-27 18:00 | 2020-06-27 | 18 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 3
2020-06-27 19:00 | 2020-06-27 | 19 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 4 | 4
2020-06-27 20:00 | 2020-06-27 | 20 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-06-27 21:00 | 2020-06-27 | 21 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-06-27 22:00 | 2020-06-27 | 22 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-06-27 23:00 | 2020-06-27 | 23 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-06-28 | 2020-06-27 | 0 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-06-28 01:00 | 2020-06-28 | 1 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-06-28 02:00 | 2020-06-28 | 2 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-06-28 03:00 | 2020-06-28 | 3 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-06-28 04:00 | 2020-06-28 | 4 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-06-28 05:00 | 2020-06-28 | 5 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-06-28 06:00 | 2020-06-28 | 6 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-06-28 07:00 | 2020-06-28 | 7 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-06-28 08:00 | 2020-06-28 | 8 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-06-28 09:00 | 2020-06-28 | 9 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-06-28 10:00 | 2020-06-28 | 10 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-06-28 11:00 | 2020-06-28 | 11 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 1
2020-06-28 12:00 | 2020-06-28 | 12 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 2
2020-06-28 13:00 | 2020-06-28 | 13 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 3
2020-06-28 14:00 | 2020-06-28 | 14 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 4
2020-06-28 15:00 | 2020-06-28 | 15 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 5
2020-06-28 16:00 | 2020-06-28 | 16 | 4.5702 | 0.01587% | 6.8141 | 7.066 | 7.3273 | 7.5983 | 7.8792 | 1.0771 | 1.329 | 1.5903 | 1.8613 | 2.1422 | 6
2020-06-28 17:00 | 2020-06-28 | 17 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 7
2020-06-28 18:00 | 2020-06-28 | 18 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 8
2020-06-28 19:00 | 2020-06-28 | 19 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 9
2020-06-28 20:00 | 2020-06-28 | 20 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 10 | 10
2020-06-28 21:00 | 2020-06-28 | 21 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-06-28 22:00 | 2020-06-28 | 22 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-06-28 23:00 | 2020-06-28 | 23 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-06-29 | 2020-06-28 | 0 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-06-29 01:00 | 2020-06-29 | 1 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-06-29 02:00 | 2020-06-29 | 2 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-06-29 03:00 | 2020-06-29 | 3 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-06-29 04:00 | 2020-06-29 | 4 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-06-29 05:00 | 2020-06-29 | 5 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-06-29 06:00 | 2020-06-29 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-06-29 07:00 | 2020-06-29 | 7 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-06-29 08:00 | 2020-06-29 | 8 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-06-29 09:00 | 2020-06-29 | 9 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1
2020-06-29 10:00 | 2020-06-29 | 10 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 2
2020-06-29 11:00 | 2020-06-29 | 11 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 3
2020-06-29 12:00 | 2020-06-29 | 12 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 4
2020-06-29 13:00 | 2020-06-29 | 13 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 5
2020-06-29 14:00 | 2020-06-29 | 14 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 6
2020-06-29 15:00 | 2020-06-29 | 15 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 7
2020-06-29 16:00 | 2020-06-29 | 16 | 5.15 | 0.01788% | 7.6784 | 7.9624 | 8.2568 | 8.5621 | 8.8788 | 1.9414 | 2.2254 | 2.5198 | 2.8251 | 3.1418 | 8
2020-06-29 17:00 | 2020-06-29 | 17 | 4.9843 | 0.01731% | 7.4315 | 7.7063 | 7.9912 | 8.2867 | 8.5932 | 1.6945 | 1.9693 | 2.2542 | 2.5497 | 2.8562 | 9
2020-06-29 18:00 | 2020-06-29 | 18 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 10
2020-06-29 19:00 | 2020-06-29 | 19 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 11
2020-06-29 20:00 | 2020-06-29 | 20 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 12
2020-06-29 21:00 | 2020-06-29 | 21 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 13 | 13
2020-06-29 22:00 | 2020-06-29 | 22 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-06-29 23:00 | 2020-06-29 | 23 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-06-30 | 2020-06-29 | 0 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-06-30 01:00 | 2020-06-30 | 1 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-06-30 02:00 | 2020-06-30 | 2 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-06-30 03:00 | 2020-06-30 | 3 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-06-30 04:00 | 2020-06-30 | 4 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-06-30 05:00 | 2020-06-30 | 5 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-06-30 06:00 | 2020-06-30 | 6 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-06-30 07:00 | 2020-06-30 | 7 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-06-30 08:00 | 2020-06-30 | 8 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-06-30 09:00 | 2020-06-30 | 9 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 1
2020-06-30 10:00 | 2020-06-30 | 10 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 2
2020-06-30 11:00 | 2020-06-30 | 11 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 3
2020-06-30 12:00 | 2020-06-30 | 12 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 4
2020-06-30 13:00 | 2020-06-30 | 13 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 5
2020-06-30 14:00 | 2020-06-30 | 14 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 6
2020-06-30 15:00 | 2020-06-30 | 15 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 7
2020-06-30 16:00 | 2020-06-30 | 16 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 8
2020-06-30 17:00 | 2020-06-30 | 17 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 9
2020-06-30 18:00 | 2020-06-30 | 18 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 10
2020-06-30 19:00 | 2020-06-30 | 19 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 11 | 11
2020-06-30 20:00 | 2020-06-30 | 20 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-06-30 21:00 | 2020-06-30 | 21 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-06-30 22:00 | 2020-06-30 | 22 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-06-30 23:00 | 2020-06-30 | 23 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-07-01 | 2020-06-30 | 0 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-07-01 01:00 | 2020-07-01 | 1 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-07-01 02:00 | 2020-07-01 | 2 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-07-01 03:00 | 2020-07-01 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-07-01 04:00 | 2020-07-01 | 4 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-07-01 05:00 | 2020-07-01 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-07-01 06:00 | 2020-07-01 | 6 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-07-01 07:00 | 2020-07-01 | 7 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-07-01 08:00 | 2020-07-01 | 8 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-07-01 09:00 | 2020-07-01 | 9 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-07-01 10:00 | 2020-07-01 | 10 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-07-01 11:00 | 2020-07-01 | 11 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-07-01 12:00 | 2020-07-01 | 12 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 1
2020-07-01 13:00 | 2020-07-01 | 13 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 2
2020-07-01 14:00 | 2020-07-01 | 14 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 3
2020-07-01 15:00 | 2020-07-01 | 15 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 4
2020-07-01 16:00 | 2020-07-01 | 16 | 4.3971 | 0.01527% | 6.5559 | 6.7983 | 7.0497 | 7.3104 | 7.5807 | 0.81886 | 1.0613 | 1.3127 | 1.5734 | 1.8437 | 5
2020-07-01 17:00 | 2020-07-01 | 17 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 6
2020-07-01 18:00 | 2020-07-01 | 18 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 7
2020-07-01 19:00 | 2020-07-01 | 19 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 8
2020-07-01 20:00 | 2020-07-01 | 20 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 9 | 9
2020-07-01 21:00 | 2020-07-01 | 21 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-07-01 22:00 | 2020-07-01 | 22 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-07-01 23:00 | 2020-07-01 | 23 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-07-02 | 2020-07-01 | 0 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-07-02 01:00 | 2020-07-02 | 1 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-07-02 02:00 | 2020-07-02 | 2 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-07-02 03:00 | 2020-07-02 | 3 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-07-02 04:00 | 2020-07-02 | 4 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-07-02 05:00 | 2020-07-02 | 5 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-07-02 06:00 | 2020-07-02 | 6 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-07-02 07:00 | 2020-07-02 | 7 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-07-02 08:00 | 2020-07-02 | 8 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-07-02 09:00 | 2020-07-02 | 9 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 1
2020-07-02 10:00 | 2020-07-02 | 10 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 2
2020-07-02 11:00 | 2020-07-02 | 11 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 3
2020-07-02 12:00 | 2020-07-02 | 12 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 4
2020-07-02 13:00 | 2020-07-02 | 13 | 5.6544 | 0.01963% | 8.4306 | 8.7423 | 9.0656 | 9.4008 | 9.7485 | 2.6936 | 3.0053 | 3.3286 | 3.6638 | 4.0115 | 5
2020-07-02 14:00 | 2020-07-02 | 14 | 5.6243 | 0.01953% | 8.3857 | 8.6958 | 9.0173 | 9.3508 | 9.6965 | 2.6487 | 2.9588 | 3.2803 | 3.6138 | 3.9595 | 6
2020-07-02 15:00 | 2020-07-02 | 15 | 5.5114 | 0.01914% | 8.2173 | 8.5211 | 8.8362 | 9.163 | 9.5018 | 2.4803 | 2.7841 | 3.0992 | 3.426 | 3.7648 | 7
2020-07-02 16:00 | 2020-07-02 | 16 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 8
2020-07-02 17:00 | 2020-07-02 | 17 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 9
2020-07-02 18:00 | 2020-07-02 | 18 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 10
2020-07-02 19:00 | 2020-07-02 | 19 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 11
2020-07-02 20:00 | 2020-07-02 | 20 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 12
2020-07-02 21:00 | 2020-07-02 | 21 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 13
2020-07-02 22:00 | 2020-07-02 | 22 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 14 | 14
2020-07-02 23:00 | 2020-07-02 | 23 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-07-03 | 2020-07-02 | 0 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-07-03 01:00 | 2020-07-03 | 1 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-07-03 02:00 | 2020-07-03 | 2 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-07-03 03:00 | 2020-07-03 | 3 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-03 04:00 | 2020-07-03 | 4 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-03 05:00 | 2020-07-03 | 5 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-07-03 06:00 | 2020-07-03 | 6 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-07-03 07:00 | 2020-07-03 | 7 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-07-03 08:00 | 2020-07-03 | 8 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 1
2020-07-03 09:00 | 2020-07-03 | 9 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 2
2020-07-03 10:00 | 2020-07-03 | 10 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 3
2020-07-03 11:00 | 2020-07-03 | 11 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 4
2020-07-03 12:00 | 2020-07-03 | 12 | 5.3156 | 0.01846% | 7.9254 | 8.2185 | 8.5224 | 8.8375 | 9.1643 | 2.1884 | 2.4815 | 2.7854 | 3.1005 | 3.4273 | 5
2020-07-03 13:00 | 2020-07-03 | 13 | 5.4888 | 0.01906% | 8.1836 | 8.4862 | 8.8 | 9.1254 | 9.4629 | 2.4466 | 2.7492 | 3.063 | 3.3884 | 3.7259 | 6
2020-07-03 14:00 | 2020-07-03 | 14 | 5.5189 | 0.01916% | 8.2285 | 8.5328 | 8.8483 | 9.1755 | 9.5148 | 2.4915 | 2.7958 | 3.1113 | 3.4385 | 3.7778 | 7
2020-07-03 15:00 | 2020-07-03 | 15 | 5.3834 | 0.01869% | 8.0264 | 8.3232 | 8.631 | 8.9502 | 9.2812 | 2.2894 | 2.5862 | 2.894 | 3.2132 | 3.5442 | 8
2020-07-03 16:00 | 2020-07-03 | 16 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 9
2020-07-03 17:00 | 2020-07-03 | 17 | 5.3382 | 0.01854% | 7.9591 | 8.2534 | 8.5586 | 8.8751 | 9.2033 | 2.2221 | 2.5164 | 2.8216 | 3.1381 | 3.4663 | 10
2020-07-03 18:00 | 2020-07-03 | 18 | 5.15 | 0.01788% | 7.6784 | 7.9624 | 8.2568 | 8.5621 | 8.8788 | 1.9414 | 2.2254 | 2.5198 | 2.8251 | 3.1418 | 11
2020-07-03 19:00 | 2020-07-03 | 19 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 12
2020-07-03 20:00 | 2020-07-03 | 20 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 13
2020-07-03 21:00 | 2020-07-03 | 21 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 14
2020-07-03 22:00 | 2020-07-03 | 22 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 15 | 15
2020-07-03 23:00 | 2020-07-03 | 23 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-07-04 | 2020-07-03 | 0 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-07-04 01:00 | 2020-07-04 | 1 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-07-04 02:00 | 2020-07-04 | 2 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-07-04 03:00 | 2020-07-04 | 3 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-04 04:00 | 2020-07-04 | 4 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-04 05:00 | 2020-07-04 | 5 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-07-04 06:00 | 2020-07-04 | 6 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-07-04 07:00 | 2020-07-04 | 7 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-04 08:00 | 2020-07-04 | 8 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-07-04 09:00 | 2020-07-04 | 9 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-07-04 10:00 | 2020-07-04 | 10 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 1
2020-07-04 11:00 | 2020-07-04 | 11 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 2
2020-07-04 12:00 | 2020-07-04 | 12 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 3
2020-07-04 13:00 | 2020-07-04 | 13 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 4
2020-07-04 14:00 | 2020-07-04 | 14 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 5
2020-07-04 15:00 | 2020-07-04 | 15 | 4.9618 | 0.01723% | 7.3978 | 7.6714 | 7.955 | 8.2492 | 8.5542 | 1.6608 | 1.9344 | 2.218 | 2.5122 | 2.8172 | 6
2020-07-04 16:00 | 2020-07-04 | 16 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 7
2020-07-04 17:00 | 2020-07-04 | 17 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 8
2020-07-04 18:00 | 2020-07-04 | 18 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 9
2020-07-04 19:00 | 2020-07-04 | 19 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 10
2020-07-04 20:00 | 2020-07-04 | 20 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 11
2020-07-04 21:00 | 2020-07-04 | 21 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 12 | 12
2020-07-04 22:00 | 2020-07-04 | 22 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-07-04 23:00 | 2020-07-04 | 23 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-07-05 | 2020-07-04 | 0 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-07-05 01:00 | 2020-07-05 | 1 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-07-05 02:00 | 2020-07-05 | 2 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-07-05 03:00 | 2020-07-05 | 3 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-07-05 04:00 | 2020-07-05 | 4 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-07-05 05:00 | 2020-07-05 | 5 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-07-05 06:00 | 2020-07-05 | 6 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-07-05 07:00 | 2020-07-05 | 7 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-07-05 08:00 | 2020-07-05 | 8 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-07-05 09:00 | 2020-07-05 | 9 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-07-05 10:00 | 2020-07-05 | 10 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 1
2020-07-05 11:00 | 2020-07-05 | 11 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 2
2020-07-05 12:00 | 2020-07-05 | 12 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 3
2020-07-05 13:00 | 2020-07-05 | 13 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 4
2020-07-05 14:00 | 2020-07-05 | 14 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 5
2020-07-05 15:00 | 2020-07-05 | 15 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 6
2020-07-05 16:00 | 2020-07-05 | 16 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 7
2020-07-05 17:00 | 2020-07-05 | 17 | 5.0973 | 0.0177% | 7.5999 | 7.8809 | 8.1723 | 8.4745 | 8.7879 | 1.8629 | 2.1439 | 2.4353 | 2.7375 | 3.0509 | 8
2020-07-05 18:00 | 2020-07-05 | 18 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 9
2020-07-05 19:00 | 2020-07-05 | 19 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 10
2020-07-05 20:00 | 2020-07-05 | 20 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 11
2020-07-05 21:00 | 2020-07-05 | 21 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 12
2020-07-05 22:00 | 2020-07-05 | 22 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 13 | 13
2020-07-05 23:00 | 2020-07-05 | 23 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-07-06 | 2020-07-05 | 0 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-07-06 01:00 | 2020-07-06 | 1 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-07-06 02:00 | 2020-07-06 | 2 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-07-06 03:00 | 2020-07-06 | 3 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-07-06 04:00 | 2020-07-06 | 4 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-07-06 05:00 | 2020-07-06 | 5 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-07-06 06:00 | 2020-07-06 | 6 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-07-06 07:00 | 2020-07-06 | 7 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-07-06 08:00 | 2020-07-06 | 8 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-07-06 09:00 | 2020-07-06 | 9 | 4.2239 | 0.01467% | 6.2977 | 6.5305 | 6.772 | 7.0225 | 7.2821 | 0.56067 | 0.79355 | 1.035 | 1.2855 | 1.5451 | 2
2020-07-06 10:00 | 2020-07-06 | 10 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 3
2020-07-06 11:00 | 2020-07-06 | 11 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 4
2020-07-06 12:00 | 2020-07-06 | 12 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 5
2020-07-06 13:00 | 2020-07-06 | 13 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 6
2020-07-06 14:00 | 2020-07-06 | 14 | 5.1349 | 0.01783% | 7.656 | 7.9391 | 8.2327 | 8.5371 | 8.8528 | 1.919 | 2.2021 | 2.4957 | 2.8001 | 3.1158 | 7
2020-07-06 15:00 | 2020-07-06 | 15 | 5.293 | 0.01838% | 7.8917 | 8.1836 | 8.4862 | 8.8 | 9.1254 | 2.1547 | 2.4466 | 2.7492 | 3.063 | 3.3884 | 8
2020-07-06 16:00 | 2020-07-06 | 16 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 9
2020-07-06 17:00 | 2020-07-06 | 17 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 10
2020-07-06 18:00 | 2020-07-06 | 18 | 5.4361 | 0.01888% | 8.105 | 8.4047 | 8.7155 | 9.0378 | 9.372 | 2.368 | 2.6677 | 2.9785 | 3.3008 | 3.635 | 11
2020-07-06 19:00 | 2020-07-06 | 19 | 5.2253 | 0.01814% | 7.7907 | 8.0788 | 8.3775 | 8.6873 | 9.0086 | 2.0537 | 2.3418 | 2.6405 | 2.9503 | 3.2716 | 12
2020-07-06 20:00 | 2020-07-06 | 20 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 13
2020-07-06 21:00 | 2020-07-06 | 21 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 14
2020-07-06 22:00 | 2020-07-06 | 22 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 15 | 15
2020-07-06 23:00 | 2020-07-06 | 23 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-07-07 | 2020-07-06 | 0 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-07-07 01:00 | 2020-07-07 | 1 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-07-07 02:00 | 2020-07-07 | 2 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-07-07 03:00 | 2020-07-07 | 3 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-07-07 04:00 | 2020-07-07 | 4 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-07-07 05:00 | 2020-07-07 | 5 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-07-07 06:00 | 2020-07-07 | 6 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-07-07 07:00 | 2020-07-07 | 7 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-07-07 08:00 | 2020-07-07 | 8 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 1
2020-07-07 09:00 | 2020-07-07 | 9 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 2
2020-07-07 10:00 | 2020-07-07 | 10 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 3
2020-07-07 11:00 | 2020-07-07 | 11 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 4
2020-07-07 12:00 | 2020-07-07 | 12 | 5.3909 | 0.01872% | 8.0377 | 8.3349 | 8.6431 | 8.9627 | 9.2941 | 2.3007 | 2.5979 | 2.9061 | 3.2257 | 3.5571 | 5
2020-07-07 13:00 | 2020-07-07 | 13 | 5.3156 | 0.01846% | 7.9254 | 8.2185 | 8.5224 | 8.8375 | 9.1643 | 2.1884 | 2.4815 | 2.7854 | 3.1005 | 3.4273 | 6
2020-07-07 14:00 | 2020-07-07 | 14 | 5.4963 | 0.01909% | 8.1948 | 8.4979 | 8.8121 | 9.138 | 9.4759 | 2.4578 | 2.7609 | 3.0751 | 3.401 | 3.7389 | 7
2020-07-07 15:00 | 2020-07-07 | 15 | 5.6695 | 0.01969% | 8.453 | 8.7656 | 9.0897 | 9.4259 | 9.7744 | 2.716 | 3.0286 | 3.3527 | 3.6889 | 4.0374 | 8
2020-07-07 16:00 | 2020-07-07 | 16 | 5.7072 | 0.01982% | 8.5092 | 8.8238 | 9.1501 | 9.4885 | 9.8393 | 2.7722 | 3.0868 | 3.4131 | 3.7515 | 4.1023 | 9
2020-07-07 17:00 | 2020-07-07 | 17 | 5.7072 | 0.01982% | 8.5092 | 8.8238 | 9.1501 | 9.4885 | 9.8393 | 2.7722 | 3.0868 | 3.4131 | 3.7515 | 4.1023 | 10
2020-07-07 18:00 | 2020-07-07 | 18 | 5.549 | 0.01927% | 8.2734 | 8.5793 | 8.8966 | 9.2256 | 9.5667 | 2.5364 | 2.8423 | 3.1596 | 3.4886 | 3.8297 | 11
2020-07-07 19:00 | 2020-07-07 | 19 | 5.3307 | 0.01851% | 7.9479 | 8.2418 | 8.5465 | 8.8626 | 9.1903 | 2.2109 | 2.5048 | 2.8095 | 3.1256 | 3.4533 | 12
2020-07-07 20:00 | 2020-07-07 | 20 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 13
2020-07-07 21:00 | 2020-07-07 | 21 | 4.6606 | 0.01618% | 6.9488 | 7.2057 | 7.4722 | 7.7485 | 8.035 | 1.2118 | 1.4687 | 1.7352 | 2.0115 | 2.298 | 14
2020-07-07 22:00 | 2020-07-07 | 22 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 15
2020-07-07 23:00 | 2020-07-07 | 23 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 16 | 16
2020-07-08 | 2020-07-07 | 0 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-07-08 01:00 | 2020-07-08 | 1 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-07-08 02:00 | 2020-07-08 | 2 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-07-08 03:00 | 2020-07-08 | 3 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-07-08 04:00 | 2020-07-08 | 4 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-07-08 05:00 | 2020-07-08 | 5 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-07-08 06:00 | 2020-07-08 | 6 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-07-08 07:00 | 2020-07-08 | 7 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-07-08 08:00 | 2020-07-08 | 8 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 1
2020-07-08 09:00 | 2020-07-08 | 9 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 2
2020-07-08 10:00 | 2020-07-08 | 10 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 3
2020-07-08 11:00 | 2020-07-08 | 11 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 4
2020-07-08 12:00 | 2020-07-08 | 12 | 5.5039 | 0.01911% | 8.2061 | 8.5095 | 8.8242 | 9.1505 | 9.4888 | 2.4691 | 2.7725 | 3.0872 | 3.4135 | 3.7518 | 5
2020-07-08 13:00 | 2020-07-08 | 13 | 5.4436 | 0.0189% | 8.1162 | 8.4164 | 8.7276 | 9.0503 | 9.385 | 2.3792 | 2.6794 | 2.9906 | 3.3133 | 3.648 | 6
2020-07-08 14:00 | 2020-07-08 | 14 | 5.5415 | 0.01924% | 8.2622 | 8.5677 | 8.8845 | 9.2131 | 9.5537 | 2.5252 | 2.8307 | 3.1475 | 3.4761 | 3.8167 | 7
2020-07-08 15:00 | 2020-07-08 | 15 | 5.6319 | 0.01956% | 8.3969 | 8.7074 | 9.0294 | 9.3633 | 9.7095 | 2.6599 | 2.9704 | 3.2924 | 3.6263 | 3.9725 | 8
2020-07-08 16:00 | 2020-07-08 | 16 | 5.7599 | 0.02% | 8.5877 | 8.9053 | 9.2346 | 9.5761 | 9.9302 | 2.8507 | 3.1683 | 3.4976 | 3.8391 | 4.1932 | 9
2020-07-08 17:00 | 2020-07-08 | 17 | 5.534 | 0.01922% | 8.251 | 8.5561 | 8.8725 | 9.2005 | 9.5408 | 2.514 | 2.8191 | 3.1355 | 3.4635 | 3.8038 | 10
2020-07-08 18:00 | 2020-07-08 | 18 | 5.3081 | 0.01843% | 7.9142 | 8.2068 | 8.5103 | 8.825 | 9.1513 | 2.1772 | 2.4698 | 2.7733 | 3.088 | 3.4143 | 11
2020-07-08 19:00 | 2020-07-08 | 19 | 5.293 | 0.01838% | 7.8917 | 8.1836 | 8.4862 | 8.8 | 9.1254 | 2.1547 | 2.4466 | 2.7492 | 3.063 | 3.3884 | 12
2020-07-08 20:00 | 2020-07-08 | 20 | 4.8564 | 0.01686% | 7.2406 | 7.5084 | 7.786 | 8.0739 | 8.3725 | 1.5036 | 1.7714 | 2.049 | 2.3369 | 2.6355 | 13
2020-07-08 21:00 | 2020-07-08 | 21 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 14
2020-07-08 22:00 | 2020-07-08 | 22 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 15
2020-07-08 23:00 | 2020-07-08 | 23 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 16 | 16
2020-07-09 | 2020-07-08 | 0 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-09 01:00 | 2020-07-09 | 1 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-07-09 02:00 | 2020-07-09 | 2 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-07-09 03:00 | 2020-07-09 | 3 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-07-09 04:00 | 2020-07-09 | 4 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-07-09 05:00 | 2020-07-09 | 5 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-07-09 06:00 | 2020-07-09 | 6 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-07-09 07:00 | 2020-07-09 | 7 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-07-09 08:00 | 2020-07-09 | 8 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 1
2020-07-09 09:00 | 2020-07-09 | 9 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 2
2020-07-09 10:00 | 2020-07-09 | 10 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 3
2020-07-09 11:00 | 2020-07-09 | 11 | 5.3985 | 0.01875% | 8.0489 | 8.3465 | 8.6552 | 8.9752 | 9.3071 | 2.3119 | 2.6095 | 2.9182 | 3.2382 | 3.5701 | 4
2020-07-09 12:00 | 2020-07-09 | 12 | 5.6243 | 0.01953% | 8.3857 | 8.6958 | 9.0173 | 9.3508 | 9.6965 | 2.6487 | 2.9588 | 3.2803 | 3.6138 | 3.9595 | 5
2020-07-09 13:00 | 2020-07-09 | 13 | 5.6319 | 0.01956% | 8.3969 | 8.7074 | 9.0294 | 9.3633 | 9.7095 | 2.6599 | 2.9704 | 3.2924 | 3.6263 | 3.9725 | 6
2020-07-09 14:00 | 2020-07-09 | 14 | 5.805 | 0.02016% | 8.6551 | 8.9751 | 9.307 | 9.6512 | 10.0081 | 2.9181 | 3.2381 | 3.57 | 3.9142 | 4.2711 | 7
2020-07-09 15:00 | 2020-07-09 | 15 | 5.8803 | 0.02042% | 8.7673 | 9.0915 | 9.4277 | 9.7764 | 10.1379 | 3.0303 | 3.3545 | 3.6907 | 4.0394 | 4.4009 | 8
2020-07-09 16:00 | 2020-07-09 | 16 | 5.9782 | 0.02076% | 8.9133 | 9.2429 | 9.5847 | 9.9391 | 10.3066 | 3.1763 | 3.5059 | 3.8477 | 4.2021 | 4.5696 | 9
2020-07-09 17:00 | 2020-07-09 | 17 | 5.9255 | 0.02058% | 8.8347 | 9.1614 | 9.5002 | 9.8515 | 10.2158 | 3.0977 | 3.4244 | 3.7632 | 4.1145 | 4.4788 | 10
2020-07-09 18:00 | 2020-07-09 | 18 | 5.9255 | 0.02058% | 8.8347 | 9.1614 | 9.5002 | 9.8515 | 10.2158 | 3.0977 | 3.4244 | 3.7632 | 4.1145 | 4.4788 | 11
2020-07-09 19:00 | 2020-07-09 | 19 | 5.8201 | 0.02021% | 8.6775 | 8.9984 | 9.3312 | 9.6762 | 10.034 | 2.9405 | 3.2614 | 3.5942 | 3.9392 | 4.297 | 12
2020-07-09 20:00 | 2020-07-09 | 20 | 5.3759 | 0.01867% | 8.0152 | 8.3116 | 8.619 | 8.9377 | 9.2682 | 2.2782 | 2.5746 | 2.882 | 3.2007 | 3.5312 | 13
2020-07-09 21:00 | 2020-07-09 | 21 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 14
2020-07-09 22:00 | 2020-07-09 | 22 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 15
2020-07-09 23:00 | 2020-07-09 | 23 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 16 | 16
2020-07-10 | 2020-07-09 | 0 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-07-10 01:00 | 2020-07-10 | 1 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-07-10 02:00 | 2020-07-10 | 2 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-07-10 03:00 | 2020-07-10 | 3 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-07-10 04:00 | 2020-07-10 | 4 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-07-10 05:00 | 2020-07-10 | 5 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-07-10 06:00 | 2020-07-10 | 6 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-07-10 07:00 | 2020-07-10 | 7 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 1
2020-07-10 08:00 | 2020-07-10 | 8 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 2
2020-07-10 09:00 | 2020-07-10 | 9 | 5.0822 | 0.01765% | 7.5774 | 7.8576 | 8.1482 | 8.4495 | 8.7619 | 1.8404 | 2.1206 | 2.4112 | 2.7125 | 3.0249 | 3
2020-07-10 10:00 | 2020-07-10 | 10 | 5.3533 | 0.01859% | 7.9815 | 8.2767 | 8.5827 | 8.9001 | 9.2292 | 2.2445 | 2.5397 | 2.8457 | 3.1631 | 3.4922 | 4
2020-07-10 11:00 | 2020-07-10 | 11 | 5.6695 | 0.01969% | 8.453 | 8.7656 | 9.0897 | 9.4259 | 9.7744 | 2.716 | 3.0286 | 3.3527 | 3.6889 | 4.0374 | 5
2020-07-10 12:00 | 2020-07-10 | 12 | 5.7749 | 0.02005% | 8.6102 | 8.9286 | 9.2587 | 9.6011 | 9.9561 | 2.8732 | 3.1916 | 3.5217 | 3.8641 | 4.2191 | 6
2020-07-10 13:00 | 2020-07-10 | 13 | 5.9481 | 0.02065% | 8.8684 | 9.1963 | 9.5364 | 9.889 | 10.2547 | 3.1314 | 3.4593 | 3.7994 | 4.152 | 4.5177 | 7
2020-07-10 14:00 | 2020-07-10 | 14 | 6.0234 | 0.02092% | 8.9806 | 9.3127 | 9.6571 | 10.0142 | 10.3845 | 3.2436 | 3.5757 | 3.9201 | 4.2772 | 4.6475 | 8
2020-07-10 15:00 | 2020-07-10 | 15 | 5.9782 | 0.02076% | 8.9133 | 9.2429 | 9.5847 | 9.9391 | 10.3066 | 3.1763 | 3.5059 | 3.8477 | 4.2021 | 4.5696 | 9
2020-07-10 16:00 | 2020-07-10 | 16 | 6.046 | 0.02099% | 9.0143 | 9.3476 | 9.6933 | 10.0517 | 10.4234 | 3.2773 | 3.6106 | 3.9563 | 4.3147 | 4.6864 | 10
2020-07-10 17:00 | 2020-07-10 | 17 | 5.9029 | 0.0205% | 8.801 | 9.1265 | 9.464 | 9.8139 | 10.1768 | 3.064 | 3.3895 | 3.727 | 4.0769 | 4.4398 | 11
2020-07-10 18:00 | 2020-07-10 | 18 | 5.79 | 0.0201% | 8.6326 | 8.9519 | 9.2829 | 9.6261 | 9.9821 | 2.8956 | 3.2149 | 3.5459 | 3.8891 | 4.2451 | 12
2020-07-10 19:00 | 2020-07-10 | 19 | 5.6168 | 0.0195% | 8.3744 | 8.6841 | 9.0052 | 9.3382 | 9.6836 | 2.6374 | 2.9471 | 3.2682 | 3.6012 | 3.9466 | 13
2020-07-10 20:00 | 2020-07-10 | 20 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 14
2020-07-10 21:00 | 2020-07-10 | 21 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 15
2020-07-10 22:00 | 2020-07-10 | 22 | 4.6229 | 0.01605% | 6.8926 | 7.1475 | 7.4118 | 7.6859 | 7.9701 | 1.1556 | 1.4105 | 1.6748 | 1.9489 | 2.2331 | 16
2020-07-10 23:00 | 2020-07-10 | 23 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 17 | 17
2020-07-11 | 2020-07-10 | 0 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-07-11 01:00 | 2020-07-11 | 1 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-07-11 02:00 | 2020-07-11 | 2 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-07-11 03:00 | 2020-07-11 | 3 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-07-11 04:00 | 2020-07-11 | 4 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-07-11 05:00 | 2020-07-11 | 5 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-07-11 06:00 | 2020-07-11 | 6 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-07-11 07:00 | 2020-07-11 | 7 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-07-11 08:00 | 2020-07-11 | 8 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-07-11 09:00 | 2020-07-11 | 9 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 1
2020-07-11 10:00 | 2020-07-11 | 10 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 2
2020-07-11 11:00 | 2020-07-11 | 11 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 3
2020-07-11 12:00 | 2020-07-11 | 12 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 4
2020-07-11 13:00 | 2020-07-11 | 13 | 5.3382 | 0.01854% | 7.9591 | 8.2534 | 8.5586 | 8.8751 | 9.2033 | 2.2221 | 2.5164 | 2.8216 | 3.1381 | 3.4663 | 5
2020-07-11 14:00 | 2020-07-11 | 14 | 5.4662 | 0.01898% | 8.1499 | 8.4513 | 8.7638 | 9.0879 | 9.4239 | 2.4129 | 2.7143 | 3.0268 | 3.3509 | 3.6869 | 6
2020-07-11 15:00 | 2020-07-11 | 15 | 5.3683 | 0.01864% | 8.004 | 8.3 | 8.6069 | 8.9252 | 9.2552 | 2.267 | 2.563 | 2.8699 | 3.1882 | 3.5182 | 7
2020-07-11 16:00 | 2020-07-11 | 16 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 8
2020-07-11 17:00 | 2020-07-11 | 17 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 9
2020-07-11 18:00 | 2020-07-11 | 18 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 10
2020-07-11 19:00 | 2020-07-11 | 19 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 11
2020-07-11 20:00 | 2020-07-11 | 20 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 12
2020-07-11 21:00 | 2020-07-11 | 21 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 13
2020-07-11 22:00 | 2020-07-11 | 22 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 14 | 14
2020-07-11 23:00 | 2020-07-11 | 23 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-07-12 | 2020-07-11 | 0 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1 | 1
2020-07-12 01:00 | 2020-07-12 | 1 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-07-12 02:00 | 2020-07-12 | 2 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-07-12 03:00 | 2020-07-12 | 3 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-07-12 04:00 | 2020-07-12 | 4 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-07-12 05:00 | 2020-07-12 | 5 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-07-12 06:00 | 2020-07-12 | 6 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-07-12 07:00 | 2020-07-12 | 7 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-07-12 08:00 | 2020-07-12 | 8 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-07-12 09:00 | 2020-07-12 | 9 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1
2020-07-12 10:00 | 2020-07-12 | 10 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 2
2020-07-12 11:00 | 2020-07-12 | 11 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 3
2020-07-12 12:00 | 2020-07-12 | 12 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 4
2020-07-12 13:00 | 2020-07-12 | 13 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 5
2020-07-12 14:00 | 2020-07-12 | 14 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 6
2020-07-12 15:00 | 2020-07-12 | 15 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 7
2020-07-12 16:00 | 2020-07-12 | 16 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 8
2020-07-12 17:00 | 2020-07-12 | 17 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 9
2020-07-12 18:00 | 2020-07-12 | 18 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 10
2020-07-12 19:00 | 2020-07-12 | 19 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 11
2020-07-12 20:00 | 2020-07-12 | 20 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 12 | 12
2020-07-12 21:00 | 2020-07-12 | 21 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-07-12 22:00 | 2020-07-12 | 22 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-07-12 23:00 | 2020-07-12 | 23 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-07-13 | 2020-07-12 | 0 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-07-13 01:00 | 2020-07-13 | 1 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-07-13 02:00 | 2020-07-13 | 2 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-07-13 03:00 | 2020-07-13 | 3 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-07-13 04:00 | 2020-07-13 | 4 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-07-13 05:00 | 2020-07-13 | 5 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-07-13 06:00 | 2020-07-13 | 6 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-13 07:00 | 2020-07-13 | 7 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-07-13 08:00 | 2020-07-13 | 8 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-07-13 09:00 | 2020-07-13 | 9 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-07-13 10:00 | 2020-07-13 | 10 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 1
2020-07-13 11:00 | 2020-07-13 | 11 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 2
2020-07-13 12:00 | 2020-07-13 | 12 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 3
2020-07-13 13:00 | 2020-07-13 | 13 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 4
2020-07-13 14:00 | 2020-07-13 | 14 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 5
2020-07-13 15:00 | 2020-07-13 | 15 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 6
2020-07-13 16:00 | 2020-07-13 | 16 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 7
2020-07-13 17:00 | 2020-07-13 | 17 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 8
2020-07-13 18:00 | 2020-07-13 | 18 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 9
2020-07-13 19:00 | 2020-07-13 | 19 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 10
2020-07-13 20:00 | 2020-07-13 | 20 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 11 | 11
2020-07-13 21:00 | 2020-07-13 | 21 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-07-13 22:00 | 2020-07-13 | 22 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-07-13 23:00 | 2020-07-13 | 23 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-07-14 | 2020-07-13 | 0 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-07-14 01:00 | 2020-07-14 | 1 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-07-14 02:00 | 2020-07-14 | 2 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-07-14 03:00 | 2020-07-14 | 3 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-07-14 04:00 | 2020-07-14 | 4 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-07-14 05:00 | 2020-07-14 | 5 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-07-14 06:00 | 2020-07-14 | 6 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-07-14 07:00 | 2020-07-14 | 7 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-07-14 08:00 | 2020-07-14 | 8 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-07-14 09:00 | 2020-07-14 | 9 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-07-14 10:00 | 2020-07-14 | 10 | 4.254 | 0.01477% | 6.3426 | 6.5771 | 6.8203 | 7.0725 | 7.3341 | 0.60557 | 0.84011 | 1.0833 | 1.3355 | 1.5971 | 1
2020-07-14 11:00 | 2020-07-14 | 11 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 2
2020-07-14 12:00 | 2020-07-14 | 12 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 3
2020-07-14 13:00 | 2020-07-14 | 13 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 4
2020-07-14 14:00 | 2020-07-14 | 14 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 5
2020-07-14 15:00 | 2020-07-14 | 15 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 6
2020-07-14 16:00 | 2020-07-14 | 16 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 7
2020-07-14 17:00 | 2020-07-14 | 17 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 8
2020-07-14 18:00 | 2020-07-14 | 18 | 4.8338 | 0.01678% | 7.207 | 7.4735 | 7.7498 | 8.0364 | 8.3336 | 1.47 | 1.7365 | 2.0128 | 2.2994 | 2.5966 | 9
2020-07-14 19:00 | 2020-07-14 | 19 | 4.6606 | 0.01618% | 6.9488 | 7.2057 | 7.4722 | 7.7485 | 8.035 | 1.2118 | 1.4687 | 1.7352 | 2.0115 | 2.298 | 10
2020-07-14 20:00 | 2020-07-14 | 20 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 11
2020-07-14 21:00 | 2020-07-14 | 21 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 12 | 12
2020-07-14 22:00 | 2020-07-14 | 22 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-07-14 23:00 | 2020-07-14 | 23 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-07-15 | 2020-07-14 | 0 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-07-15 01:00 | 2020-07-15 | 1 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-07-15 02:00 | 2020-07-15 | 2 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-07-15 03:00 | 2020-07-15 | 3 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-07-15 04:00 | 2020-07-15 | 4 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-07-15 05:00 | 2020-07-15 | 5 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-07-15 06:00 | 2020-07-15 | 6 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-07-15 07:00 | 2020-07-15 | 7 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-07-15 08:00 | 2020-07-15 | 8 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-07-15 09:00 | 2020-07-15 | 9 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 1
2020-07-15 10:00 | 2020-07-15 | 10 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 2
2020-07-15 11:00 | 2020-07-15 | 11 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 3
2020-07-15 12:00 | 2020-07-15 | 12 | 4.9316 | 0.01712% | 7.3529 | 7.6248 | 7.9067 | 8.1991 | 8.5023 | 1.6159 | 1.8878 | 2.1697 | 2.4621 | 2.7653 | 4
2020-07-15 13:00 | 2020-07-15 | 13 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 5
2020-07-15 14:00 | 2020-07-15 | 14 | 5.1199 | 0.01778% | 7.6335 | 7.9158 | 8.2085 | 8.5121 | 8.8268 | 1.8965 | 2.1788 | 2.4715 | 2.7751 | 3.0898 | 6
2020-07-15 15:00 | 2020-07-15 | 15 | 5.1952 | 0.01804% | 7.7458 | 8.0322 | 8.3292 | 8.6372 | 8.9566 | 2.0088 | 2.2952 | 2.5922 | 2.9002 | 3.2196 | 7
2020-07-15 16:00 | 2020-07-15 | 16 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 8
2020-07-15 17:00 | 2020-07-15 | 17 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 9
2020-07-15 18:00 | 2020-07-15 | 18 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 10
2020-07-15 19:00 | 2020-07-15 | 19 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 11
2020-07-15 20:00 | 2020-07-15 | 20 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 12
2020-07-15 21:00 | 2020-07-15 | 21 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 13 | 13
2020-07-15 22:00 | 2020-07-15 | 22 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-07-15 23:00 | 2020-07-15 | 23 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-07-16 | 2020-07-15 | 0 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-07-16 01:00 | 2020-07-16 | 1 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-07-16 02:00 | 2020-07-16 | 2 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-07-16 03:00 | 2020-07-16 | 3 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-07-16 04:00 | 2020-07-16 | 4 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-07-16 05:00 | 2020-07-16 | 5 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-07-16 06:00 | 2020-07-16 | 6 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-07-16 07:00 | 2020-07-16 | 7 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-07-16 08:00 | 2020-07-16 | 8 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 1
2020-07-16 09:00 | 2020-07-16 | 9 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 2
2020-07-16 10:00 | 2020-07-16 | 10 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 3
2020-07-16 11:00 | 2020-07-16 | 11 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 4
2020-07-16 12:00 | 2020-07-16 | 12 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 5
2020-07-16 13:00 | 2020-07-16 | 13 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 6
2020-07-16 14:00 | 2020-07-16 | 14 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 7
2020-07-16 15:00 | 2020-07-16 | 15 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 8
2020-07-16 16:00 | 2020-07-16 | 16 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 9
2020-07-16 17:00 | 2020-07-16 | 17 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 10
2020-07-16 18:00 | 2020-07-16 | 18 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 11
2020-07-16 19:00 | 2020-07-16 | 19 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 12
2020-07-16 20:00 | 2020-07-16 | 20 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 13 | 13
2020-07-16 21:00 | 2020-07-16 | 21 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-07-16 22:00 | 2020-07-16 | 22 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-07-16 23:00 | 2020-07-16 | 23 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-07-17 | 2020-07-16 | 0 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-07-17 01:00 | 2020-07-17 | 1 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-07-17 02:00 | 2020-07-17 | 2 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-07-17 03:00 | 2020-07-17 | 3 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-07-17 04:00 | 2020-07-17 | 4 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-07-17 05:00 | 2020-07-17 | 5 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-07-17 06:00 | 2020-07-17 | 6 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-07-17 07:00 | 2020-07-17 | 7 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-07-17 08:00 | 2020-07-17 | 8 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 1
2020-07-17 09:00 | 2020-07-17 | 9 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 2
2020-07-17 10:00 | 2020-07-17 | 10 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 3
2020-07-17 11:00 | 2020-07-17 | 11 | 4.8036 | 0.01668% | 7.1621 | 7.4269 | 7.7015 | 7.9863 | 8.2816 | 1.4251 | 1.6899 | 1.9645 | 2.2493 | 2.5446 | 4
2020-07-17 12:00 | 2020-07-17 | 12 | 5.0069 | 0.01739% | 7.4652 | 7.7412 | 8.0275 | 8.3243 | 8.6321 | 1.7282 | 2.0042 | 2.2905 | 2.5873 | 2.8951 | 5
2020-07-17 13:00 | 2020-07-17 | 13 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 6
2020-07-17 14:00 | 2020-07-17 | 14 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 7
2020-07-17 15:00 | 2020-07-17 | 15 | 5.3307 | 0.01851% | 7.9479 | 8.2418 | 8.5465 | 8.8626 | 9.1903 | 2.2109 | 2.5048 | 2.8095 | 3.1256 | 3.4533 | 8
2020-07-17 16:00 | 2020-07-17 | 16 | 5.4587 | 0.01895% | 8.1387 | 8.4397 | 8.7517 | 9.0754 | 9.411 | 2.4017 | 2.7027 | 3.0147 | 3.3384 | 3.674 | 9
2020-07-17 17:00 | 2020-07-17 | 17 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 10
2020-07-17 18:00 | 2020-07-17 | 18 | 5.1876 | 0.01801% | 7.7346 | 8.0206 | 8.3172 | 8.6247 | 8.9437 | 1.9976 | 2.2836 | 2.5802 | 2.8877 | 3.2067 | 11
2020-07-17 19:00 | 2020-07-17 | 19 | 4.9467 | 0.01718% | 7.3753 | 7.6481 | 7.9309 | 8.2242 | 8.5283 | 1.6383 | 1.9111 | 2.1939 | 2.4872 | 2.7913 | 12
2020-07-17 20:00 | 2020-07-17 | 20 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 13
2020-07-17 21:00 | 2020-07-17 | 21 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 14
2020-07-17 22:00 | 2020-07-17 | 22 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 15 | 15
2020-07-17 23:00 | 2020-07-17 | 23 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-07-18 | 2020-07-17 | 0 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-18 01:00 | 2020-07-18 | 1 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-07-18 02:00 | 2020-07-18 | 2 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-07-18 03:00 | 2020-07-18 | 3 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-07-18 04:00 | 2020-07-18 | 4 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-07-18 05:00 | 2020-07-18 | 5 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-07-18 06:00 | 2020-07-18 | 6 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-07-18 07:00 | 2020-07-18 | 7 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-07-18 08:00 | 2020-07-18 | 8 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-07-18 09:00 | 2020-07-18 | 9 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 1
2020-07-18 10:00 | 2020-07-18 | 10 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 2
2020-07-18 11:00 | 2020-07-18 | 11 | 4.9091 | 0.01705% | 7.3192 | 7.5899 | 7.8705 | 8.1616 | 8.4634 | 1.5822 | 1.8529 | 2.1335 | 2.4246 | 2.7264 | 3
2020-07-18 12:00 | 2020-07-18 | 12 | 4.9919 | 0.01733% | 7.4427 | 7.7179 | 8.0033 | 8.2993 | 8.6062 | 1.7057 | 1.9809 | 2.2663 | 2.5623 | 2.8692 | 4
2020-07-18 13:00 | 2020-07-18 | 13 | 5.1349 | 0.01783% | 7.656 | 7.9391 | 8.2327 | 8.5371 | 8.8528 | 1.919 | 2.2021 | 2.4957 | 2.8001 | 3.1158 | 5
2020-07-18 14:00 | 2020-07-18 | 14 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 6
2020-07-18 15:00 | 2020-07-18 | 15 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 7
2020-07-18 16:00 | 2020-07-18 | 16 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 8
2020-07-18 17:00 | 2020-07-18 | 17 | 5.3909 | 0.01872% | 8.0377 | 8.3349 | 8.6431 | 8.9627 | 9.2941 | 2.3007 | 2.5979 | 2.9061 | 3.2257 | 3.5571 | 9
2020-07-18 18:00 | 2020-07-18 | 18 | 5.3533 | 0.01859% | 7.9815 | 8.2767 | 8.5827 | 8.9001 | 9.2292 | 2.2445 | 2.5397 | 2.8457 | 3.1631 | 3.4922 | 10
2020-07-18 19:00 | 2020-07-18 | 19 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 11
2020-07-18 20:00 | 2020-07-18 | 20 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 12
2020-07-18 21:00 | 2020-07-18 | 21 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 13
2020-07-18 22:00 | 2020-07-18 | 22 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 14 | 14
2020-07-18 23:00 | 2020-07-18 | 23 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-07-19 | 2020-07-18 | 0 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-07-19 01:00 | 2020-07-19 | 1 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-07-19 02:00 | 2020-07-19 | 2 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-07-19 03:00 | 2020-07-19 | 3 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-07-19 04:00 | 2020-07-19 | 4 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-07-19 05:00 | 2020-07-19 | 5 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-07-19 06:00 | 2020-07-19 | 6 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-19 07:00 | 2020-07-19 | 7 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-07-19 08:00 | 2020-07-19 | 8 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 1
2020-07-19 09:00 | 2020-07-19 | 9 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 2
2020-07-19 10:00 | 2020-07-19 | 10 | 4.9166 | 0.01707% | 7.3304 | 7.6015 | 7.8826 | 8.1741 | 8.4764 | 1.5934 | 1.8645 | 2.1456 | 2.4371 | 2.7394 | 3
2020-07-19 11:00 | 2020-07-19 | 11 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 4
2020-07-19 12:00 | 2020-07-19 | 12 | 5.293 | 0.01838% | 7.8917 | 8.1836 | 8.4862 | 8.8 | 9.1254 | 2.1547 | 2.4466 | 2.7492 | 3.063 | 3.3884 | 5
2020-07-19 13:00 | 2020-07-19 | 13 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 6
2020-07-19 14:00 | 2020-07-19 | 14 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 7
2020-07-19 15:00 | 2020-07-19 | 15 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 8
2020-07-19 16:00 | 2020-07-19 | 16 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 9
2020-07-19 17:00 | 2020-07-19 | 17 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 10
2020-07-19 18:00 | 2020-07-19 | 18 | 4.766 | 0.01655% | 7.1059 | 7.3687 | 7.6412 | 7.9237 | 8.2167 | 1.3689 | 1.6317 | 1.9042 | 2.1867 | 2.4797 | 11
2020-07-19 19:00 | 2020-07-19 | 19 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 12
2020-07-19 20:00 | 2020-07-19 | 20 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 13
2020-07-19 21:00 | 2020-07-19 | 21 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 14
2020-07-19 22:00 | 2020-07-19 | 22 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 15 | 15
2020-07-19 23:00 | 2020-07-19 | 23 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-07-20 | 2020-07-19 | 0 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-07-20 01:00 | 2020-07-20 | 1 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-07-20 02:00 | 2020-07-20 | 2 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-07-20 03:00 | 2020-07-20 | 3 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-07-20 04:00 | 2020-07-20 | 4 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-07-20 05:00 | 2020-07-20 | 5 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-20 06:00 | 2020-07-20 | 6 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-07-20 07:00 | 2020-07-20 | 7 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-07-20 08:00 | 2020-07-20 | 8 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 1
2020-07-20 09:00 | 2020-07-20 | 9 | 4.5326 | 0.01574% | 6.7579 | 7.0078 | 7.267 | 7.5357 | 7.8143 | 1.0209 | 1.2708 | 1.53 | 1.7987 | 2.0773 | 2
2020-07-20 10:00 | 2020-07-20 | 10 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 3
2020-07-20 11:00 | 2020-07-20 | 11 | 5.0672 | 0.0176% | 7.555 | 7.8343 | 8.124 | 8.4244 | 8.736 | 1.818 | 2.0973 | 2.387 | 2.6874 | 2.999 | 4
2020-07-20 12:00 | 2020-07-20 | 12 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 5
2020-07-20 13:00 | 2020-07-20 | 13 | 5.2328 | 0.01817% | 7.8019 | 8.0904 | 8.3896 | 8.6998 | 9.0215 | 2.0649 | 2.3534 | 2.6526 | 2.9628 | 3.2845 | 6
2020-07-20 14:00 | 2020-07-20 | 14 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 7
2020-07-20 15:00 | 2020-07-20 | 15 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 8
2020-07-20 16:00 | 2020-07-20 | 16 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 9
2020-07-20 17:00 | 2020-07-20 | 17 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 10
2020-07-20 18:00 | 2020-07-20 | 18 | 4.9542 | 0.0172% | 7.3866 | 7.6597 | 7.943 | 8.2367 | 8.5413 | 1.6496 | 1.9227 | 2.206 | 2.4997 | 2.8043 | 11
2020-07-20 19:00 | 2020-07-20 | 19 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 12
2020-07-20 20:00 | 2020-07-20 | 20 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 13
2020-07-20 21:00 | 2020-07-20 | 21 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 14 | 14
2020-07-20 22:00 | 2020-07-20 | 22 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-20 23:00 | 2020-07-20 | 23 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-07-21 | 2020-07-20 | 0 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-07-21 01:00 | 2020-07-21 | 1 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-07-21 02:00 | 2020-07-21 | 2 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-07-21 03:00 | 2020-07-21 | 3 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-07-21 04:00 | 2020-07-21 | 4 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-07-21 05:00 | 2020-07-21 | 5 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-07-21 06:00 | 2020-07-21 | 6 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-21 07:00 | 2020-07-21 | 7 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-07-21 08:00 | 2020-07-21 | 8 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-07-21 09:00 | 2020-07-21 | 9 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-07-21 10:00 | 2020-07-21 | 10 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 1
2020-07-21 11:00 | 2020-07-21 | 11 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 2
2020-07-21 12:00 | 2020-07-21 | 12 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 3
2020-07-21 13:00 | 2020-07-21 | 13 | 4.4498 | 0.01545% | 6.6344 | 6.8798 | 7.1342 | 7.398 | 7.6716 | 0.89744 | 1.1428 | 1.3972 | 1.661 | 1.9346 | 4
2020-07-21 14:00 | 2020-07-21 | 14 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 5
2020-07-21 15:00 | 2020-07-21 | 15 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 6
2020-07-21 16:00 | 2020-07-21 | 16 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 7
2020-07-21 17:00 | 2020-07-21 | 17 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 8
2020-07-21 18:00 | 2020-07-21 | 18 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 9
2020-07-21 19:00 | 2020-07-21 | 19 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 10
2020-07-21 20:00 | 2020-07-21 | 20 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 11
2020-07-21 21:00 | 2020-07-21 | 21 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 12 | 12
2020-07-21 22:00 | 2020-07-21 | 22 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-21 23:00 | 2020-07-21 | 23 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-07-22 | 2020-07-21 | 0 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-07-22 01:00 | 2020-07-22 | 1 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-07-22 02:00 | 2020-07-22 | 2 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-07-22 03:00 | 2020-07-22 | 3 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-07-22 04:00 | 2020-07-22 | 4 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-07-22 05:00 | 2020-07-22 | 5 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-07-22 06:00 | 2020-07-22 | 6 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-07-22 07:00 | 2020-07-22 | 7 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-07-22 08:00 | 2020-07-22 | 8 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-07-22 09:00 | 2020-07-22 | 9 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-07-22 10:00 | 2020-07-22 | 10 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1
2020-07-22 11:00 | 2020-07-22 | 11 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 2
2020-07-22 12:00 | 2020-07-22 | 12 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 3
2020-07-22 13:00 | 2020-07-22 | 13 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 4
2020-07-22 14:00 | 2020-07-22 | 14 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 5
2020-07-22 15:00 | 2020-07-22 | 15 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 6
2020-07-22 16:00 | 2020-07-22 | 16 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 7
2020-07-22 17:00 | 2020-07-22 | 17 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 8
2020-07-22 18:00 | 2020-07-22 | 18 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 9
2020-07-22 19:00 | 2020-07-22 | 19 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 10
2020-07-22 20:00 | 2020-07-22 | 20 | 4.126 | 0.01433% | 6.1517 | 6.3792 | 6.6151 | 6.8597 | 7.1134 | 0.41473 | 0.64222 | 0.87811 | 1.1227 | 1.3764 | 11
2020-07-22 21:00 | 2020-07-22 | 21 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 12 | 12
2020-07-22 22:00 | 2020-07-22 | 22 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-07-22 23:00 | 2020-07-22 | 23 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-07-23 | 2020-07-22 | 0 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-07-23 01:00 | 2020-07-23 | 1 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-07-23 02:00 | 2020-07-23 | 2 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-07-23 03:00 | 2020-07-23 | 3 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-07-23 04:00 | 2020-07-23 | 4 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-07-23 05:00 | 2020-07-23 | 5 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-07-23 06:00 | 2020-07-23 | 6 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-07-23 07:00 | 2020-07-23 | 7 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-07-23 08:00 | 2020-07-23 | 8 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-07-23 09:00 | 2020-07-23 | 9 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 1
2020-07-23 10:00 | 2020-07-23 | 10 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 2
2020-07-23 11:00 | 2020-07-23 | 11 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 3
2020-07-23 12:00 | 2020-07-23 | 12 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 4
2020-07-23 13:00 | 2020-07-23 | 13 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 5
2020-07-23 14:00 | 2020-07-23 | 14 | 5.2027 | 0.01807% | 7.757 | 8.0439 | 8.3413 | 8.6498 | 8.9696 | 2.02 | 2.3069 | 2.6043 | 2.9128 | 3.2326 | 6
2020-07-23 15:00 | 2020-07-23 | 15 | 5.3006 | 0.01841% | 7.903 | 8.1952 | 8.4982 | 8.8125 | 9.1384 | 2.166 | 2.4582 | 2.7612 | 3.0755 | 3.4014 | 7
2020-07-23 16:00 | 2020-07-23 | 16 | 5.4135 | 0.0188% | 8.0713 | 8.3698 | 8.6793 | 9.0003 | 9.3331 | 2.3343 | 2.6328 | 2.9423 | 3.2633 | 3.5961 | 8
2020-07-23 17:00 | 2020-07-23 | 17 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 9
2020-07-23 18:00 | 2020-07-23 | 18 | 5.2705 | 0.0183% | 7.8581 | 8.1486 | 8.45 | 8.7624 | 9.0864 | 2.1211 | 2.4116 | 2.713 | 3.0254 | 3.3494 | 10
2020-07-23 19:00 | 2020-07-23 | 19 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 11
2020-07-23 20:00 | 2020-07-23 | 20 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 12
2020-07-23 21:00 | 2020-07-23 | 21 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 13
2020-07-23 22:00 | 2020-07-23 | 22 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 14 | 14
2020-07-23 23:00 | 2020-07-23 | 23 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-24 | 2020-07-23 | 0 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-07-24 01:00 | 2020-07-24 | 1 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-07-24 02:00 | 2020-07-24 | 2 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-07-24 03:00 | 2020-07-24 | 3 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-07-24 04:00 | 2020-07-24 | 4 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-07-24 05:00 | 2020-07-24 | 5 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-07-24 06:00 | 2020-07-24 | 6 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-07-24 07:00 | 2020-07-24 | 7 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-07-24 08:00 | 2020-07-24 | 8 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-07-24 09:00 | 2020-07-24 | 9 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 1
2020-07-24 10:00 | 2020-07-24 | 10 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 2
2020-07-24 11:00 | 2020-07-24 | 11 | 4.6832 | 0.01626% | 6.9824 | 7.2406 | 7.5084 | 7.786 | 8.074 | 1.2454 | 1.5036 | 1.7714 | 2.049 | 2.337 | 3
2020-07-24 12:00 | 2020-07-24 | 12 | 4.9015 | 0.01702% | 7.308 | 7.5782 | 7.8585 | 8.1491 | 8.4504 | 1.571 | 1.8412 | 2.1215 | 2.4121 | 2.7134 | 4
2020-07-24 13:00 | 2020-07-24 | 13 | 4.9843 | 0.01731% | 7.4315 | 7.7063 | 7.9912 | 8.2867 | 8.5932 | 1.6945 | 1.9693 | 2.2542 | 2.5497 | 2.8562 | 5
2020-07-24 14:00 | 2020-07-24 | 14 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 6
2020-07-24 15:00 | 2020-07-24 | 15 | 5.2328 | 0.01817% | 7.8019 | 8.0904 | 8.3896 | 8.6998 | 9.0215 | 2.0649 | 2.3534 | 2.6526 | 2.9628 | 3.2845 | 7
2020-07-24 16:00 | 2020-07-24 | 16 | 5.406 | 0.01877% | 8.0601 | 8.3582 | 8.6672 | 8.9877 | 9.3201 | 2.3231 | 2.6212 | 2.9302 | 3.2507 | 3.5831 | 8
2020-07-24 17:00 | 2020-07-24 | 17 | 5.1801 | 0.01799% | 7.7233 | 8.0089 | 8.3051 | 8.6122 | 8.9307 | 1.9863 | 2.2719 | 2.5681 | 2.8752 | 3.1937 | 9
2020-07-24 18:00 | 2020-07-24 | 18 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 10
2020-07-24 19:00 | 2020-07-24 | 19 | 4.9618 | 0.01723% | 7.3978 | 7.6714 | 7.955 | 8.2492 | 8.5542 | 1.6608 | 1.9344 | 2.218 | 2.5122 | 2.8172 | 11
2020-07-24 20:00 | 2020-07-24 | 20 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 12
2020-07-24 21:00 | 2020-07-24 | 21 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 13
2020-07-24 22:00 | 2020-07-24 | 22 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 14 | 14
2020-07-24 23:00 | 2020-07-24 | 23 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-07-25 | 2020-07-24 | 0 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-07-25 01:00 | 2020-07-25 | 1 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-07-25 02:00 | 2020-07-25 | 2 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-07-25 03:00 | 2020-07-25 | 3 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-07-25 04:00 | 2020-07-25 | 4 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-07-25 05:00 | 2020-07-25 | 5 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-07-25 06:00 | 2020-07-25 | 6 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-07-25 07:00 | 2020-07-25 | 7 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-07-25 08:00 | 2020-07-25 | 8 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-07-25 09:00 | 2020-07-25 | 9 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-07-25 10:00 | 2020-07-25 | 10 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 1
2020-07-25 11:00 | 2020-07-25 | 11 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 2
2020-07-25 12:00 | 2020-07-25 | 12 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 3
2020-07-25 13:00 | 2020-07-25 | 13 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 4
2020-07-25 14:00 | 2020-07-25 | 14 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 5
2020-07-25 15:00 | 2020-07-25 | 15 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 6
2020-07-25 16:00 | 2020-07-25 | 16 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 7
2020-07-25 17:00 | 2020-07-25 | 17 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 8
2020-07-25 18:00 | 2020-07-25 | 18 | 4.9768 | 0.01728% | 7.4202 | 7.6946 | 7.9792 | 8.2742 | 8.5802 | 1.6832 | 1.9576 | 2.2422 | 2.5372 | 2.8432 | 9
2020-07-25 19:00 | 2020-07-25 | 19 | 4.8187 | 0.01673% | 7.1845 | 7.4502 | 7.7257 | 8.0114 | 8.3076 | 1.4475 | 1.7132 | 1.9887 | 2.2744 | 2.5706 | 10
2020-07-25 20:00 | 2020-07-25 | 20 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 11
2020-07-25 21:00 | 2020-07-25 | 21 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 12 | 12
2020-07-25 22:00 | 2020-07-25 | 22 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-07-25 23:00 | 2020-07-25 | 23 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-07-26 | 2020-07-25 | 0 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-07-26 01:00 | 2020-07-26 | 1 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-07-26 02:00 | 2020-07-26 | 2 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-07-26 03:00 | 2020-07-26 | 3 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-07-26 04:00 | 2020-07-26 | 4 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-07-26 05:00 | 2020-07-26 | 5 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-07-26 06:00 | 2020-07-26 | 6 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-07-26 07:00 | 2020-07-26 | 7 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-07-26 08:00 | 2020-07-26 | 8 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-07-26 09:00 | 2020-07-26 | 9 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 1
2020-07-26 10:00 | 2020-07-26 | 10 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 2
2020-07-26 11:00 | 2020-07-26 | 11 | 4.7058 | 0.01634% | 7.0161 | 7.2756 | 7.5446 | 7.8236 | 8.1129 | 1.2791 | 1.5386 | 1.8076 | 2.0866 | 2.3759 | 3
2020-07-26 12:00 | 2020-07-26 | 12 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 4
2020-07-26 13:00 | 2020-07-26 | 13 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 5
2020-07-26 14:00 | 2020-07-26 | 14 | 5.1199 | 0.01778% | 7.6335 | 7.9158 | 8.2085 | 8.5121 | 8.8268 | 1.8965 | 2.1788 | 2.4715 | 2.7751 | 3.0898 | 6
2020-07-26 15:00 | 2020-07-26 | 15 | 5.2403 | 0.0182% | 7.8132 | 8.1021 | 8.4017 | 8.7124 | 9.0345 | 2.0762 | 2.3651 | 2.6647 | 2.9754 | 3.2975 | 7
2020-07-26 16:00 | 2020-07-26 | 16 | 5.3533 | 0.01859% | 7.9815 | 8.2767 | 8.5827 | 8.9001 | 9.2292 | 2.2445 | 2.5397 | 2.8457 | 3.1631 | 3.4922 | 8
2020-07-26 17:00 | 2020-07-26 | 17 | 5.4963 | 0.01909% | 8.1948 | 8.4979 | 8.8121 | 9.138 | 9.4759 | 2.4578 | 2.7609 | 3.0751 | 3.401 | 3.7389 | 9
2020-07-26 18:00 | 2020-07-26 | 18 | 5.4436 | 0.0189% | 8.1162 | 8.4164 | 8.7276 | 9.0503 | 9.385 | 2.3792 | 2.6794 | 2.9906 | 3.3133 | 3.648 | 10
2020-07-26 19:00 | 2020-07-26 | 19 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 11
2020-07-26 20:00 | 2020-07-26 | 20 | 4.6907 | 0.01629% | 6.9937 | 7.2523 | 7.5205 | 7.7986 | 8.0869 | 1.2567 | 1.5153 | 1.7835 | 2.0616 | 2.3499 | 12
2020-07-26 21:00 | 2020-07-26 | 21 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 13
2020-07-26 22:00 | 2020-07-26 | 22 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 14
2020-07-26 23:00 | 2020-07-26 | 23 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 15 | 15
2020-07-27 | 2020-07-26 | 0 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-07-27 01:00 | 2020-07-27 | 1 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-07-27 02:00 | 2020-07-27 | 2 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-07-27 03:00 | 2020-07-27 | 3 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-07-27 04:00 | 2020-07-27 | 4 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-07-27 05:00 | 2020-07-27 | 5 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-07-27 06:00 | 2020-07-27 | 6 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-07-27 07:00 | 2020-07-27 | 7 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 1
2020-07-27 08:00 | 2020-07-27 | 8 | 4.5778 | 0.0159% | 6.8253 | 7.0777 | 7.3394 | 7.6108 | 7.8922 | 1.0883 | 1.3407 | 1.6024 | 1.8738 | 2.1552 | 2
2020-07-27 09:00 | 2020-07-27 | 9 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 3
2020-07-27 10:00 | 2020-07-27 | 10 | 5.2479 | 0.01822% | 7.8244 | 8.1137 | 8.4137 | 8.7249 | 9.0475 | 2.0874 | 2.3767 | 2.6767 | 2.9879 | 3.3105 | 4
2020-07-27 11:00 | 2020-07-27 | 11 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 5
2020-07-27 12:00 | 2020-07-27 | 12 | 5.6469 | 0.01961% | 8.4193 | 8.7307 | 9.0535 | 9.3883 | 9.7355 | 2.6823 | 2.9937 | 3.3165 | 3.6513 | 3.9985 | 6
2020-07-27 13:00 | 2020-07-27 | 13 | 5.7072 | 0.01982% | 8.5092 | 8.8238 | 9.1501 | 9.4885 | 9.8393 | 2.7722 | 3.0868 | 3.4131 | 3.7515 | 4.1023 | 7
2020-07-27 14:00 | 2020-07-27 | 14 | 5.6544 | 0.01963% | 8.4306 | 8.7423 | 9.0656 | 9.4008 | 9.7485 | 2.6936 | 3.0053 | 3.3286 | 3.6638 | 4.0115 | 8
2020-07-27 15:00 | 2020-07-27 | 15 | 5.6846 | 0.01974% | 8.4755 | 8.7889 | 9.1139 | 9.4509 | 9.8004 | 2.7385 | 3.0519 | 3.3769 | 3.7139 | 4.0634 | 9
2020-07-27 16:00 | 2020-07-27 | 16 | 5.4135 | 0.0188% | 8.0713 | 8.3698 | 8.6793 | 9.0003 | 9.3331 | 2.3343 | 2.6328 | 2.9423 | 3.2633 | 3.5961 | 10
2020-07-27 17:00 | 2020-07-27 | 17 | 5.7072 | 0.01982% | 8.5092 | 8.8238 | 9.1501 | 9.4885 | 9.8393 | 2.7722 | 3.0868 | 3.4131 | 3.7515 | 4.1023 | 11
2020-07-27 18:00 | 2020-07-27 | 18 | 5.5039 | 0.01911% | 8.2061 | 8.5095 | 8.8242 | 9.1505 | 9.4888 | 2.4691 | 2.7725 | 3.0872 | 3.4135 | 3.7518 | 12
2020-07-27 19:00 | 2020-07-27 | 19 | 5.2253 | 0.01814% | 7.7907 | 8.0788 | 8.3775 | 8.6873 | 9.0086 | 2.0537 | 2.3418 | 2.6405 | 2.9503 | 3.2716 | 13
2020-07-27 20:00 | 2020-07-27 | 20 | 4.9316 | 0.01712% | 7.3529 | 7.6248 | 7.9067 | 8.1991 | 8.5023 | 1.6159 | 1.8878 | 2.1697 | 2.4621 | 2.7653 | 14
2020-07-27 21:00 | 2020-07-27 | 21 | 4.6229 | 0.01605% | 6.8926 | 7.1475 | 7.4118 | 7.6859 | 7.9701 | 1.1556 | 1.4105 | 1.6748 | 1.9489 | 2.2331 | 15
2020-07-27 22:00 | 2020-07-27 | 22 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 16
2020-07-27 23:00 | 2020-07-27 | 23 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 17 | 17
2020-07-28 | 2020-07-27 | 0 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-07-28 01:00 | 2020-07-28 | 1 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-07-28 02:00 | 2020-07-28 | 2 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-07-28 03:00 | 2020-07-28 | 3 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-07-28 04:00 | 2020-07-28 | 4 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-07-28 05:00 | 2020-07-28 | 5 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-07-28 06:00 | 2020-07-28 | 6 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-07-28 07:00 | 2020-07-28 | 7 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-28 08:00 | 2020-07-28 | 8 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 1
2020-07-28 09:00 | 2020-07-28 | 9 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 2
2020-07-28 10:00 | 2020-07-28 | 10 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 3
2020-07-28 11:00 | 2020-07-28 | 11 | 4.7509 | 0.0165% | 7.0835 | 7.3454 | 7.617 | 7.8987 | 8.1908 | 1.3465 | 1.6084 | 1.88 | 2.1617 | 2.4538 | 4
2020-07-28 12:00 | 2020-07-28 | 12 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 5
2020-07-28 13:00 | 2020-07-28 | 13 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 6
2020-07-28 14:00 | 2020-07-28 | 14 | 5.1349 | 0.01783% | 7.656 | 7.9391 | 8.2327 | 8.5371 | 8.8528 | 1.919 | 2.2021 | 2.4957 | 2.8001 | 3.1158 | 7
2020-07-28 15:00 | 2020-07-28 | 15 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 8
2020-07-28 16:00 | 2020-07-28 | 16 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 9
2020-07-28 17:00 | 2020-07-28 | 17 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 10
2020-07-28 18:00 | 2020-07-28 | 18 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 11
2020-07-28 19:00 | 2020-07-28 | 19 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 12
2020-07-28 20:00 | 2020-07-28 | 20 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 13
2020-07-28 21:00 | 2020-07-28 | 21 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 14 | 14
2020-07-28 22:00 | 2020-07-28 | 22 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-07-28 23:00 | 2020-07-28 | 23 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-07-29 | 2020-07-28 | 0 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-07-29 01:00 | 2020-07-29 | 1 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-07-29 02:00 | 2020-07-29 | 2 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-07-29 03:00 | 2020-07-29 | 3 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-07-29 04:00 | 2020-07-29 | 4 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-07-29 05:00 | 2020-07-29 | 5 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-07-29 06:00 | 2020-07-29 | 6 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-07-29 07:00 | 2020-07-29 | 7 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-07-29 08:00 | 2020-07-29 | 8 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-07-29 09:00 | 2020-07-29 | 9 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 1
2020-07-29 10:00 | 2020-07-29 | 10 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 2
2020-07-29 11:00 | 2020-07-29 | 11 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 3
2020-07-29 12:00 | 2020-07-29 | 12 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 4
2020-07-29 13:00 | 2020-07-29 | 13 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 5
2020-07-29 14:00 | 2020-07-29 | 14 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 6
2020-07-29 15:00 | 2020-07-29 | 15 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 7
2020-07-29 16:00 | 2020-07-29 | 16 | 4.9693 | 0.01726% | 7.409 | 7.683 | 7.9671 | 8.2617 | 8.5672 | 1.672 | 1.946 | 2.2301 | 2.5247 | 2.8302 | 8
2020-07-29 17:00 | 2020-07-29 | 17 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 9
2020-07-29 18:00 | 2020-07-29 | 18 | 4.6229 | 0.01605% | 6.8926 | 7.1475 | 7.4118 | 7.6859 | 7.9701 | 1.1556 | 1.4105 | 1.6748 | 1.9489 | 2.2331 | 10
2020-07-29 19:00 | 2020-07-29 | 19 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 11
2020-07-29 20:00 | 2020-07-29 | 20 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 12 | 12
2020-07-29 21:00 | 2020-07-29 | 21 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-07-29 22:00 | 2020-07-29 | 22 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-07-29 23:00 | 2020-07-29 | 23 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-07-30 | 2020-07-29 | 0 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-07-30 01:00 | 2020-07-30 | 1 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-07-30 02:00 | 2020-07-30 | 2 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-07-30 03:00 | 2020-07-30 | 3 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-07-30 04:00 | 2020-07-30 | 4 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-07-30 05:00 | 2020-07-30 | 5 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-07-30 06:00 | 2020-07-30 | 6 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-07-30 07:00 | 2020-07-30 | 7 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-07-30 08:00 | 2020-07-30 | 8 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-07-30 09:00 | 2020-07-30 | 9 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 1
2020-07-30 10:00 | 2020-07-30 | 10 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 2
2020-07-30 11:00 | 2020-07-30 | 11 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 3
2020-07-30 12:00 | 2020-07-30 | 12 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 4
2020-07-30 13:00 | 2020-07-30 | 13 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 5
2020-07-30 14:00 | 2020-07-30 | 14 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 6
2020-07-30 15:00 | 2020-07-30 | 15 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 7
2020-07-30 16:00 | 2020-07-30 | 16 | 4.8488 | 0.01684% | 7.2294 | 7.4967 | 7.774 | 8.0614 | 8.3595 | 1.4924 | 1.7597 | 2.037 | 2.3244 | 2.6225 | 8
2020-07-30 17:00 | 2020-07-30 | 17 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 9
2020-07-30 18:00 | 2020-07-30 | 18 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 10
2020-07-30 19:00 | 2020-07-30 | 19 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 11
2020-07-30 20:00 | 2020-07-30 | 20 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 12
2020-07-30 21:00 | 2020-07-30 | 21 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 13 | 13
2020-07-30 22:00 | 2020-07-30 | 22 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-07-30 23:00 | 2020-07-30 | 23 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-07-31 | 2020-07-30 | 0 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-07-31 01:00 | 2020-07-31 | 1 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-07-31 02:00 | 2020-07-31 | 2 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-07-31 03:00 | 2020-07-31 | 3 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-07-31 04:00 | 2020-07-31 | 4 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-07-31 05:00 | 2020-07-31 | 5 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-07-31 06:00 | 2020-07-31 | 6 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-07-31 07:00 | 2020-07-31 | 7 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-07-31 08:00 | 2020-07-31 | 8 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-07-31 09:00 | 2020-07-31 | 9 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 1
2020-07-31 10:00 | 2020-07-31 | 10 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 2
2020-07-31 11:00 | 2020-07-31 | 11 | 4.6305 | 0.01608% | 6.9039 | 7.1592 | 7.4239 | 7.6984 | 7.9831 | 1.1669 | 1.4222 | 1.6869 | 1.9614 | 2.2461 | 3
2020-07-31 12:00 | 2020-07-31 | 12 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 4
2020-07-31 13:00 | 2020-07-31 | 13 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 5
2020-07-31 14:00 | 2020-07-31 | 14 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 6
2020-07-31 15:00 | 2020-07-31 | 15 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 7
2020-07-31 16:00 | 2020-07-31 | 16 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 8
2020-07-31 17:00 | 2020-07-31 | 17 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 9
2020-07-31 18:00 | 2020-07-31 | 18 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 10
2020-07-31 19:00 | 2020-07-31 | 19 | 4.8338 | 0.01678% | 7.207 | 7.4735 | 7.7498 | 8.0364 | 8.3336 | 1.47 | 1.7365 | 2.0128 | 2.2994 | 2.5966 | 11
2020-07-31 20:00 | 2020-07-31 | 20 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 12
2020-07-31 21:00 | 2020-07-31 | 21 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 13 | 13
2020-07-31 22:00 | 2020-07-31 | 22 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-07-31 23:00 | 2020-07-31 | 23 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-08-01 | 2020-07-31 | 0 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-08-01 01:00 | 2020-08-01 | 1 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-08-01 02:00 | 2020-08-01 | 2 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-08-01 03:00 | 2020-08-01 | 3 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-01 04:00 | 2020-08-01 | 4 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-08-01 05:00 | 2020-08-01 | 5 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-08-01 06:00 | 2020-08-01 | 6 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-08-01 07:00 | 2020-08-01 | 7 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-08-01 08:00 | 2020-08-01 | 8 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-08-01 09:00 | 2020-08-01 | 9 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-08-01 10:00 | 2020-08-01 | 10 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 1
2020-08-01 11:00 | 2020-08-01 | 11 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 2
2020-08-01 12:00 | 2020-08-01 | 12 | 4.8714 | 0.01692% | 7.2631 | 7.5317 | 7.8102 | 8.099 | 8.3985 | 1.5261 | 1.7947 | 2.0732 | 2.362 | 2.6615 | 3
2020-08-01 13:00 | 2020-08-01 | 13 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 4
2020-08-01 14:00 | 2020-08-01 | 14 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 5
2020-08-01 15:00 | 2020-08-01 | 15 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 6
2020-08-01 16:00 | 2020-08-01 | 16 | 5.1199 | 0.01778% | 7.6335 | 7.9158 | 8.2085 | 8.5121 | 8.8268 | 1.8965 | 2.1788 | 2.4715 | 2.7751 | 3.0898 | 7
2020-08-01 17:00 | 2020-08-01 | 17 | 5.1048 | 0.01773% | 7.6111 | 7.8925 | 8.1844 | 8.487 | 8.8009 | 1.8741 | 2.1555 | 2.4474 | 2.75 | 3.0639 | 8
2020-08-01 18:00 | 2020-08-01 | 18 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 9
2020-08-01 19:00 | 2020-08-01 | 19 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 10
2020-08-01 20:00 | 2020-08-01 | 20 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 11
2020-08-01 21:00 | 2020-08-01 | 21 | 4.1637 | 0.01446% | 6.2079 | 6.4374 | 6.6755 | 6.9223 | 7.1783 | 0.47086 | 0.70042 | 0.93847 | 1.1853 | 1.4413 | 12 | 12
2020-08-01 22:00 | 2020-08-01 | 22 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-08-01 23:00 | 2020-08-01 | 23 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-08-02 | 2020-08-01 | 0 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-08-02 01:00 | 2020-08-02 | 1 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-08-02 02:00 | 2020-08-02 | 2 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-08-02 03:00 | 2020-08-02 | 3 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-08-02 04:00 | 2020-08-02 | 4 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-08-02 05:00 | 2020-08-02 | 5 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-08-02 06:00 | 2020-08-02 | 6 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-08-02 07:00 | 2020-08-02 | 7 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-08-02 08:00 | 2020-08-02 | 8 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-08-02 09:00 | 2020-08-02 | 9 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-08-02 10:00 | 2020-08-02 | 10 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-08-02 11:00 | 2020-08-02 | 11 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-08-02 12:00 | 2020-08-02 | 12 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 1
2020-08-02 13:00 | 2020-08-02 | 13 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 2
2020-08-02 14:00 | 2020-08-02 | 14 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 3
2020-08-02 15:00 | 2020-08-02 | 15 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 4
2020-08-02 16:00 | 2020-08-02 | 16 | 4.3519 | 0.01511% | 6.4885 | 6.7284 | 6.9772 | 7.2353 | 7.5028 | 0.75151 | 0.99144 | 1.2402 | 1.4983 | 1.7658 | 5
2020-08-02 17:00 | 2020-08-02 | 17 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 6
2020-08-02 18:00 | 2020-08-02 | 18 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 7
2020-08-02 19:00 | 2020-08-02 | 19 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 8 | 8
2020-08-02 20:00 | 2020-08-02 | 20 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-08-02 21:00 | 2020-08-02 | 21 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-02 22:00 | 2020-08-02 | 22 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-08-02 23:00 | 2020-08-02 | 23 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-08-03 | 2020-08-02 | 0 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-08-03 01:00 | 2020-08-03 | 1 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-08-03 02:00 | 2020-08-03 | 2 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-08-03 03:00 | 2020-08-03 | 3 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-08-03 04:00 | 2020-08-03 | 4 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-08-03 05:00 | 2020-08-03 | 5 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-08-03 06:00 | 2020-08-03 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-08-03 07:00 | 2020-08-03 | 7 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-08-03 08:00 | 2020-08-03 | 8 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-03 09:00 | 2020-08-03 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-03 10:00 | 2020-08-03 | 10 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-08-03 11:00 | 2020-08-03 | 11 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 1
2020-08-03 12:00 | 2020-08-03 | 12 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 2
2020-08-03 13:00 | 2020-08-03 | 13 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 3
2020-08-03 14:00 | 2020-08-03 | 14 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 4
2020-08-03 15:00 | 2020-08-03 | 15 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 5
2020-08-03 16:00 | 2020-08-03 | 16 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 6
2020-08-03 17:00 | 2020-08-03 | 17 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 7
2020-08-03 18:00 | 2020-08-03 | 18 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 8
2020-08-03 19:00 | 2020-08-03 | 19 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 9
2020-08-03 20:00 | 2020-08-03 | 20 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 10
2020-08-03 21:00 | 2020-08-03 | 21 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 11 | 11
2020-08-03 22:00 | 2020-08-03 | 22 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-08-03 23:00 | 2020-08-03 | 23 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-08-04 | 2020-08-03 | 0 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-08-04 01:00 | 2020-08-04 | 1 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-08-04 02:00 | 2020-08-04 | 2 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-08-04 03:00 | 2020-08-04 | 3 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-04 04:00 | 2020-08-04 | 4 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-08-04 05:00 | 2020-08-04 | 5 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-08-04 06:00 | 2020-08-04 | 6 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-08-04 07:00 | 2020-08-04 | 7 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-08-04 08:00 | 2020-08-04 | 8 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-08-04 09:00 | 2020-08-04 | 9 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 1
2020-08-04 10:00 | 2020-08-04 | 10 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 2
2020-08-04 11:00 | 2020-08-04 | 11 | 5.4662 | 0.01898% | 8.1499 | 8.4513 | 8.7638 | 9.0879 | 9.4239 | 2.4129 | 2.7143 | 3.0268 | 3.3509 | 3.6869 | 3
2020-08-04 12:00 | 2020-08-04 | 12 | 5.7599 | 0.02% | 8.5877 | 8.9053 | 9.2346 | 9.5761 | 9.9302 | 2.8507 | 3.1683 | 3.4976 | 3.8391 | 4.1932 | 4
2020-08-04 13:00 | 2020-08-04 | 13 | 5.8427 | 0.02029% | 8.7112 | 9.0333 | 9.3674 | 9.7138 | 10.073 | 2.9742 | 3.2963 | 3.6304 | 3.9768 | 4.336 | 5
2020-08-04 14:00 | 2020-08-04 | 14 | 5.8577 | 0.02034% | 8.7337 | 9.0566 | 9.3915 | 9.7388 | 10.0989 | 2.9967 | 3.3196 | 3.6545 | 4.0018 | 4.3619 | 6
2020-08-04 15:00 | 2020-08-04 | 15 | 5.918 | 0.02055% | 8.8235 | 9.1498 | 9.4881 | 9.8389 | 10.2028 | 3.0865 | 3.4128 | 3.7511 | 4.1019 | 4.4658 | 7
2020-08-04 16:00 | 2020-08-04 | 16 | 5.8653 | 0.02037% | 8.7449 | 9.0683 | 9.4036 | 9.7513 | 10.1119 | 3.0079 | 3.3313 | 3.6666 | 4.0143 | 4.3749 | 8
2020-08-04 17:00 | 2020-08-04 | 17 | 6.0761 | 0.0211% | 9.0592 | 9.3942 | 9.7416 | 10.1018 | 10.4754 | 3.3222 | 3.6572 | 4.0046 | 4.3648 | 4.7384 | 9
2020-08-04 18:00 | 2020-08-04 | 18 | 6.0686 | 0.02107% | 9.048 | 9.3826 | 9.7295 | 10.0893 | 10.4624 | 3.311 | 3.6456 | 3.9925 | 4.3523 | 4.7254 | 10
2020-08-04 19:00 | 2020-08-04 | 19 | 5.7824 | 0.02008% | 8.6214 | 8.9402 | 9.2708 | 9.6136 | 9.9691 | 2.8844 | 3.2032 | 3.5338 | 3.8766 | 4.2321 | 11
2020-08-04 20:00 | 2020-08-04 | 20 | 5.3834 | 0.01869% | 8.0264 | 8.3232 | 8.631 | 8.9502 | 9.2812 | 2.2894 | 2.5862 | 2.894 | 3.2132 | 3.5442 | 12
2020-08-04 21:00 | 2020-08-04 | 21 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 13
2020-08-04 22:00 | 2020-08-04 | 22 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 14
2020-08-04 23:00 | 2020-08-04 | 23 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 15 | 15
2020-08-05 | 2020-08-04 | 0 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-08-05 01:00 | 2020-08-05 | 1 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-08-05 02:00 | 2020-08-05 | 2 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-08-05 03:00 | 2020-08-05 | 3 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-08-05 04:00 | 2020-08-05 | 4 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-08-05 05:00 | 2020-08-05 | 5 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-08-05 06:00 | 2020-08-05 | 6 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-08-05 07:00 | 2020-08-05 | 7 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 1
2020-08-05 08:00 | 2020-08-05 | 8 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 2
2020-08-05 09:00 | 2020-08-05 | 9 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 3
2020-08-05 10:00 | 2020-08-05 | 10 | 5.1876 | 0.01801% | 7.7346 | 8.0206 | 8.3172 | 8.6247 | 8.9437 | 1.9976 | 2.2836 | 2.5802 | 2.8877 | 3.2067 | 4
2020-08-05 11:00 | 2020-08-05 | 11 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 5
2020-08-05 12:00 | 2020-08-05 | 12 | 5.3232 | 0.01848% | 7.9366 | 8.2301 | 8.5345 | 8.85 | 9.1773 | 2.1996 | 2.4931 | 2.7975 | 3.113 | 3.4403 | 6
2020-08-05 13:00 | 2020-08-05 | 13 | 5.3307 | 0.01851% | 7.9479 | 8.2418 | 8.5465 | 8.8626 | 9.1903 | 2.2109 | 2.5048 | 2.8095 | 3.1256 | 3.4533 | 7
2020-08-05 14:00 | 2020-08-05 | 14 | 5.4361 | 0.01888% | 8.105 | 8.4047 | 8.7155 | 9.0378 | 9.372 | 2.368 | 2.6677 | 2.9785 | 3.3008 | 3.635 | 8
2020-08-05 15:00 | 2020-08-05 | 15 | 5.3382 | 0.01854% | 7.9591 | 8.2534 | 8.5586 | 8.8751 | 9.2033 | 2.2221 | 2.5164 | 2.8216 | 3.1381 | 3.4663 | 9
2020-08-05 16:00 | 2020-08-05 | 16 | 5.3909 | 0.01872% | 8.0377 | 8.3349 | 8.6431 | 8.9627 | 9.2941 | 2.3007 | 2.5979 | 2.9061 | 3.2257 | 3.5571 | 10
2020-08-05 17:00 | 2020-08-05 | 17 | 5.6469 | 0.01961% | 8.4193 | 8.7307 | 9.0535 | 9.3883 | 9.7355 | 2.6823 | 2.9937 | 3.3165 | 3.6513 | 3.9985 | 11
2020-08-05 18:00 | 2020-08-05 | 18 | 5.534 | 0.01922% | 8.251 | 8.5561 | 8.8725 | 9.2005 | 9.5408 | 2.514 | 2.8191 | 3.1355 | 3.4635 | 3.8038 | 12
2020-08-05 19:00 | 2020-08-05 | 19 | 5.278 | 0.01833% | 7.8693 | 8.1603 | 8.462 | 8.7749 | 9.0994 | 2.1323 | 2.4233 | 2.725 | 3.0379 | 3.3624 | 13
2020-08-05 20:00 | 2020-08-05 | 20 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 14
2020-08-05 21:00 | 2020-08-05 | 21 | 4.7359 | 0.01644% | 7.061 | 7.3221 | 7.5929 | 7.8737 | 8.1648 | 1.324 | 1.5851 | 1.8559 | 2.1367 | 2.4278 | 15
2020-08-05 22:00 | 2020-08-05 | 22 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 16
2020-08-05 23:00 | 2020-08-05 | 23 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 17
2020-08-06 | 2020-08-05 | 0 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 18 | 18
2020-08-06 01:00 | 2020-08-06 | 1 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-06 02:00 | 2020-08-06 | 2 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-08-06 03:00 | 2020-08-06 | 3 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-08-06 04:00 | 2020-08-06 | 4 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-08-06 05:00 | 2020-08-06 | 5 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-08-06 06:00 | 2020-08-06 | 6 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-08-06 07:00 | 2020-08-06 | 7 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-08-06 08:00 | 2020-08-06 | 8 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-08-06 09:00 | 2020-08-06 | 9 | 4.2917 | 0.0149% | 6.3987 | 6.6353 | 6.8807 | 7.1351 | 7.399 | 0.6617 | 0.89832 | 1.1437 | 1.3981 | 1.662 | 2
2020-08-06 10:00 | 2020-08-06 | 10 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 3
2020-08-06 11:00 | 2020-08-06 | 11 | 4.9467 | 0.01718% | 7.3753 | 7.6481 | 7.9309 | 8.2242 | 8.5283 | 1.6383 | 1.9111 | 2.1939 | 2.4872 | 2.7913 | 4
2020-08-06 12:00 | 2020-08-06 | 12 | 5.1274 | 0.0178% | 7.6448 | 7.9275 | 8.2206 | 8.5246 | 8.8398 | 1.9078 | 2.1905 | 2.4836 | 2.7876 | 3.1028 | 5
2020-08-06 13:00 | 2020-08-06 | 13 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 6
2020-08-06 14:00 | 2020-08-06 | 14 | 5.4135 | 0.0188% | 8.0713 | 8.3698 | 8.6793 | 9.0003 | 9.3331 | 2.3343 | 2.6328 | 2.9423 | 3.2633 | 3.5961 | 7
2020-08-06 15:00 | 2020-08-06 | 15 | 5.5415 | 0.01924% | 8.2622 | 8.5677 | 8.8845 | 9.2131 | 9.5537 | 2.5252 | 2.8307 | 3.1475 | 3.4761 | 3.8167 | 8
2020-08-06 16:00 | 2020-08-06 | 16 | 5.677 | 0.01971% | 8.4642 | 8.7772 | 9.1018 | 9.4384 | 9.7874 | 2.7272 | 3.0402 | 3.3648 | 3.7014 | 4.0504 | 9
2020-08-06 17:00 | 2020-08-06 | 17 | 5.7373 | 0.01992% | 8.5541 | 8.8704 | 9.1984 | 9.5385 | 9.8912 | 2.8171 | 3.1334 | 3.4614 | 3.8015 | 4.1542 | 10
2020-08-06 18:00 | 2020-08-06 | 18 | 5.7147 | 0.01984% | 8.5204 | 8.8354 | 9.1622 | 9.501 | 9.8523 | 2.7834 | 3.0984 | 3.4252 | 3.764 | 4.1153 | 11
2020-08-06 19:00 | 2020-08-06 | 19 | 5.5189 | 0.01916% | 8.2285 | 8.5328 | 8.8483 | 9.1755 | 9.5148 | 2.4915 | 2.7958 | 3.1113 | 3.4385 | 3.7778 | 12
2020-08-06 20:00 | 2020-08-06 | 20 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 13
2020-08-06 21:00 | 2020-08-06 | 21 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 14
2020-08-06 22:00 | 2020-08-06 | 22 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 15
2020-08-06 23:00 | 2020-08-06 | 23 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 16 | 16
2020-08-07 | 2020-08-06 | 0 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-08-07 01:00 | 2020-08-07 | 1 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-07 02:00 | 2020-08-07 | 2 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-08-07 03:00 | 2020-08-07 | 3 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-08-07 04:00 | 2020-08-07 | 4 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-08-07 05:00 | 2020-08-07 | 5 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-08-07 06:00 | 2020-08-07 | 6 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-08-07 07:00 | 2020-08-07 | 7 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-08-07 08:00 | 2020-08-07 | 8 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 1
2020-08-07 09:00 | 2020-08-07 | 9 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 2
2020-08-07 10:00 | 2020-08-07 | 10 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 3
2020-08-07 11:00 | 2020-08-07 | 11 | 5.0145 | 0.01741% | 7.4764 | 7.7528 | 8.0395 | 8.3368 | 8.6451 | 1.7394 | 2.0158 | 2.3025 | 2.5998 | 2.9081 | 4
2020-08-07 12:00 | 2020-08-07 | 12 | 5.3909 | 0.01872% | 8.0377 | 8.3349 | 8.6431 | 8.9627 | 9.2941 | 2.3007 | 2.5979 | 2.9061 | 3.2257 | 3.5571 | 5
2020-08-07 13:00 | 2020-08-07 | 13 | 5.4436 | 0.0189% | 8.1162 | 8.4164 | 8.7276 | 9.0503 | 9.385 | 2.3792 | 2.6794 | 2.9906 | 3.3133 | 3.648 | 6
2020-08-07 14:00 | 2020-08-07 | 14 | 5.7975 | 0.02013% | 8.6439 | 8.9635 | 9.295 | 9.6387 | 9.9951 | 2.9069 | 3.2265 | 3.558 | 3.9017 | 4.2581 | 7
2020-08-07 15:00 | 2020-08-07 | 15 | 5.8803 | 0.02042% | 8.7673 | 9.0915 | 9.4277 | 9.7764 | 10.1379 | 3.0303 | 3.3545 | 3.6907 | 4.0394 | 4.4009 | 8
2020-08-07 16:00 | 2020-08-07 | 16 | 6.0836 | 0.02112% | 9.0704 | 9.4059 | 9.7537 | 10.1143 | 10.4884 | 3.3334 | 3.6689 | 4.0167 | 4.3773 | 4.7514 | 9
2020-08-07 17:00 | 2020-08-07 | 17 | 6.0987 | 0.02118% | 9.0929 | 9.4291 | 9.7778 | 10.1394 | 10.5143 | 3.3559 | 3.6921 | 4.0408 | 4.4024 | 4.7773 | 10
2020-08-07 18:00 | 2020-08-07 | 18 | 6.1815 | 0.02146% | 9.2164 | 9.5572 | 9.9106 | 10.2771 | 10.6571 | 3.4794 | 3.8202 | 4.1736 | 4.5401 | 4.9201 | 11
2020-08-07 19:00 | 2020-08-07 | 19 | 6.0309 | 0.02094% | 8.9919 | 9.3244 | 9.6692 | 10.0267 | 10.3975 | 3.2549 | 3.5874 | 3.9322 | 4.2897 | 4.6605 | 12
2020-08-07 20:00 | 2020-08-07 | 20 | 5.6093 | 0.01948% | 8.3632 | 8.6725 | 8.9932 | 9.3257 | 9.6706 | 2.6262 | 2.9355 | 3.2562 | 3.5887 | 3.9336 | 13
2020-08-07 21:00 | 2020-08-07 | 21 | 5.3759 | 0.01867% | 8.0152 | 8.3116 | 8.619 | 8.9377 | 9.2682 | 2.2782 | 2.5746 | 2.882 | 3.2007 | 3.5312 | 14
2020-08-07 22:00 | 2020-08-07 | 22 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 15
2020-08-07 23:00 | 2020-08-07 | 23 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 16 | 16
2020-08-08 | 2020-08-07 | 0 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-08-08 01:00 | 2020-08-08 | 1 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-08-08 02:00 | 2020-08-08 | 2 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-08-08 03:00 | 2020-08-08 | 3 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-08-08 04:00 | 2020-08-08 | 4 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-08-08 05:00 | 2020-08-08 | 5 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-08-08 06:00 | 2020-08-08 | 6 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-08 07:00 | 2020-08-08 | 7 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-08-08 08:00 | 2020-08-08 | 8 | 4.239 | 0.01472% | 6.3201 | 6.5538 | 6.7962 | 7.0475 | 7.3081 | 0.58312 | 0.81683 | 1.0592 | 1.3105 | 1.5711 | 1
2020-08-08 09:00 | 2020-08-08 | 9 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 2
2020-08-08 10:00 | 2020-08-08 | 10 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 3
2020-08-08 11:00 | 2020-08-08 | 11 | 5.7975 | 0.02013% | 8.6439 | 8.9635 | 9.295 | 9.6387 | 9.9951 | 2.9069 | 3.2265 | 3.558 | 3.9017 | 4.2581 | 4
2020-08-08 12:00 | 2020-08-08 | 12 | 5.8427 | 0.02029% | 8.7112 | 9.0333 | 9.3674 | 9.7138 | 10.073 | 2.9742 | 3.2963 | 3.6304 | 3.9768 | 4.336 | 5
2020-08-08 13:00 | 2020-08-08 | 13 | 6.1815 | 0.02146% | 9.2164 | 9.5572 | 9.9106 | 10.2771 | 10.6571 | 3.4794 | 3.8202 | 4.1736 | 4.5401 | 4.9201 | 6
2020-08-08 14:00 | 2020-08-08 | 14 | 6.43 | 0.02233% | 9.5868 | 9.9413 | 10.3089 | 10.6902 | 11.0855 | 3.8498 | 4.2043 | 4.5719 | 4.9532 | 5.3485 | 7
2020-08-08 15:00 | 2020-08-08 | 15 | 6.5053 | 0.02259% | 9.6991 | 10.0577 | 10.4297 | 10.8153 | 11.2153 | 3.9621 | 4.3207 | 4.6927 | 5.0783 | 5.4783 | 8
2020-08-08 16:00 | 2020-08-08 | 16 | 6.6935 | 0.02324% | 9.9797 | 10.3488 | 10.7314 | 11.1283 | 11.5398 | 4.2427 | 4.6118 | 4.9944 | 5.3913 | 5.8028 | 9
2020-08-08 17:00 | 2020-08-08 | 17 | 6.829 | 0.02371% | 10.1818 | 10.5583 | 10.9487 | 11.3536 | 11.7734 | 4.4448 | 4.8213 | 5.2117 | 5.6166 | 6.0364 | 10
2020-08-08 18:00 | 2020-08-08 | 18 | 6.7612 | 0.02348% | 10.0808 | 10.4535 | 10.8401 | 11.2409 | 11.6566 | 4.3438 | 4.7165 | 5.1031 | 5.5039 | 5.9196 | 11
2020-08-08 19:00 | 2020-08-08 | 19 | 6.3923 | 0.0222% | 9.5307 | 9.8831 | 10.2486 | 10.6276 | 11.0206 | 3.7937 | 4.1461 | 4.5116 | 4.8906 | 5.2836 | 12
2020-08-08 20:00 | 2020-08-08 | 20 | 5.7222 | 0.01987% | 8.5316 | 8.8471 | 9.1742 | 9.5135 | 9.8653 | 2.7946 | 3.1101 | 3.4372 | 3.7765 | 4.1283 | 13
2020-08-08 21:00 | 2020-08-08 | 21 | 5.5566 | 0.01929% | 8.2846 | 8.591 | 8.9087 | 9.2381 | 9.5797 | 2.5476 | 2.854 | 3.1717 | 3.5011 | 3.8427 | 14
2020-08-08 22:00 | 2020-08-08 | 22 | 5.1274 | 0.0178% | 7.6448 | 7.9275 | 8.2206 | 8.5246 | 8.8398 | 1.9078 | 2.1905 | 2.4836 | 2.7876 | 3.1028 | 15
2020-08-08 23:00 | 2020-08-08 | 23 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 16
2020-08-09 | 2020-08-08 | 0 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 17
2020-08-09 01:00 | 2020-08-09 | 1 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 18 | 18
2020-08-09 02:00 | 2020-08-09 | 2 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-09 03:00 | 2020-08-09 | 3 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-08-09 04:00 | 2020-08-09 | 4 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-08-09 05:00 | 2020-08-09 | 5 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-08-09 06:00 | 2020-08-09 | 6 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-08-09 07:00 | 2020-08-09 | 7 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-08-09 08:00 | 2020-08-09 | 8 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 1
2020-08-09 09:00 | 2020-08-09 | 9 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 2
2020-08-09 10:00 | 2020-08-09 | 10 | 5.0898 | 0.01767% | 7.5886 | 7.8693 | 8.1602 | 8.462 | 8.7749 | 1.8516 | 2.1323 | 2.4232 | 2.725 | 3.0379 | 3
2020-08-09 11:00 | 2020-08-09 | 11 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 4
2020-08-09 12:00 | 2020-08-09 | 12 | 5.421 | 0.01882% | 8.0826 | 8.3815 | 8.6914 | 9.0128 | 9.3461 | 2.3456 | 2.6445 | 2.9544 | 3.2758 | 3.6091 | 5
2020-08-09 13:00 | 2020-08-09 | 13 | 5.8351 | 0.02026% | 8.7 | 9.0217 | 9.3553 | 9.7013 | 10.06 | 2.963 | 3.2847 | 3.6183 | 3.9643 | 4.323 | 6
2020-08-09 14:00 | 2020-08-09 | 14 | 5.8653 | 0.02037% | 8.7449 | 9.0683 | 9.4036 | 9.7513 | 10.1119 | 3.0079 | 3.3313 | 3.6666 | 4.0143 | 4.3749 | 7
2020-08-09 15:00 | 2020-08-09 | 15 | 6.2493 | 0.0217% | 9.3174 | 9.662 | 10.0192 | 10.3897 | 10.7739 | 3.5804 | 3.925 | 4.2822 | 4.6527 | 5.0369 | 8
2020-08-09 16:00 | 2020-08-09 | 16 | 6.4525 | 0.02241% | 9.6205 | 9.9763 | 10.3452 | 10.7277 | 11.1244 | 3.8835 | 4.2393 | 4.6082 | 4.9907 | 5.3874 | 9
2020-08-09 17:00 | 2020-08-09 | 17 | 6.6935 | 0.02324% | 9.9797 | 10.3488 | 10.7314 | 11.1283 | 11.5398 | 4.2427 | 4.6118 | 4.9944 | 5.3913 | 5.8028 | 10
2020-08-09 18:00 | 2020-08-09 | 18 | 6.6332 | 0.02303% | 9.8899 | 10.2556 | 10.6349 | 11.0281 | 11.4359 | 4.1529 | 4.5186 | 4.8979 | 5.2911 | 5.6989 | 11
2020-08-09 19:00 | 2020-08-09 | 19 | 6.2869 | 0.02183% | 9.3735 | 9.7202 | 10.0796 | 10.4523 | 10.8388 | 3.6365 | 3.9832 | 4.3426 | 4.7153 | 5.1018 | 12
2020-08-09 20:00 | 2020-08-09 | 20 | 5.8728 | 0.02039% | 8.7561 | 9.0799 | 9.4157 | 9.7638 | 10.1249 | 3.0191 | 3.3429 | 3.6787 | 4.0268 | 4.3879 | 13
2020-08-09 21:00 | 2020-08-09 | 21 | 5.8351 | 0.02026% | 8.7 | 9.0217 | 9.3553 | 9.7013 | 10.06 | 2.963 | 3.2847 | 3.6183 | 3.9643 | 4.323 | 14
2020-08-09 22:00 | 2020-08-09 | 22 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 15
2020-08-09 23:00 | 2020-08-09 | 23 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 16
2020-08-10 | 2020-08-09 | 0 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 17
2020-08-10 01:00 | 2020-08-10 | 1 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 18
2020-08-10 02:00 | 2020-08-10 | 2 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 19 | 19
2020-08-10 03:00 | 2020-08-10 | 3 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-08-10 04:00 | 2020-08-10 | 4 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-10 05:00 | 2020-08-10 | 5 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-08-10 06:00 | 2020-08-10 | 6 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 1
2020-08-10 07:00 | 2020-08-10 | 7 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 2
2020-08-10 08:00 | 2020-08-10 | 8 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 3 | 3
2020-08-10 09:00 | 2020-08-10 | 9 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020-08-10 10:00 | 2020-08-10 | 10 | 6.3095 | 0.02191% | 9.4072 | 9.7551 | 10.1158 | 10.4899 | 10.8778 | 3.6702 | 4.0181 | 4.3788 | 4.7529 | 5.1408 | 1
2020-08-10 11:00 | 2020-08-10 | 11 | 6.4525 | 0.02241% | 9.6205 | 9.9763 | 10.3452 | 10.7277 | 11.1244 | 3.8835 | 4.2393 | 4.6082 | 4.9907 | 5.3874 | 2
2020-08-10 12:00 | 2020-08-10 | 12 | 6.6558 | 0.02311% | 9.9236 | 10.2906 | 10.6711 | 11.0657 | 11.4749 | 4.1866 | 4.5536 | 4.9341 | 5.3287 | 5.7379 | 3
2020-08-10 13:00 | 2020-08-10 | 13 | 6.8516 | 0.02379% | 10.2155 | 10.5932 | 10.9849 | 11.3911 | 11.8124 | 4.4785 | 4.8562 | 5.2479 | 5.6541 | 6.0754 | 4
2020-08-10 14:00 | 2020-08-10 | 14 | 7.213 | 0.02505% | 10.7543 | 11.152 | 11.5644 | 11.992 | 12.4354 | 5.0173 | 5.415 | 5.8274 | 6.255 | 6.6984 | 5
2020-08-10 15:00 | 2020-08-10 | 15 | 7.3335 | 0.02546% | 10.9339 | 11.3382 | 11.7575 | 12.1923 | 12.6431 | 5.1969 | 5.6012 | 6.0205 | 6.4553 | 6.9061 | 6
2020-08-10 16:00 | 2020-08-10 | 16 | 7.612 | 0.02643% | 11.3493 | 11.769 | 12.2042 | 12.6554 | 13.1234 | 5.6123 | 6.032 | 6.4672 | 6.9184 | 7.3864 | 7
2020-08-10 17:00 | 2020-08-10 | 17 | 7.7325 | 0.02685% | 11.5289 | 11.9552 | 12.3973 | 12.8557 | 13.3311 | 5.7919 | 6.2182 | 6.6603 | 7.1187 | 7.5941 | 8
2020-08-10 18:00 | 2020-08-10 | 18 | 7.5217 | 0.02612% | 11.2146 | 11.6293 | 12.0593 | 12.5052 | 12.9677 | 5.4776 | 5.8923 | 6.3223 | 6.7682 | 7.2307 | 9
2020-08-10 19:00 | 2020-08-10 | 19 | 7.2808 | 0.02528% | 10.8553 | 11.2568 | 11.673 | 12.1047 | 12.5523 | 5.1183 | 5.5198 | 5.936 | 6.3677 | 6.8153 | 10
2020-08-10 20:00 | 2020-08-10 | 20 | 6.8667 | 0.02384% | 10.2379 | 10.6165 | 11.0091 | 11.4162 | 11.8383 | 4.5009 | 4.8795 | 5.2721 | 5.6792 | 6.1013 | 11
2020-08-10 21:00 | 2020-08-10 | 21 | 6.6709 | 0.02316% | 9.9461 | 10.3138 | 10.6952 | 11.0907 | 11.5008 | 4.2091 | 4.5768 | 4.9582 | 5.3537 | 5.7638 | 12
2020-08-10 22:00 | 2020-08-10 | 22 | 6.0911 | 0.02115% | 9.0817 | 9.4175 | 9.7657 | 10.1269 | 10.5013 | 3.3447 | 3.6805 | 4.0287 | 4.3899 | 4.7643 | 13
2020-08-10 23:00 | 2020-08-10 | 23 | 5.5792 | 0.01937% | 8.3183 | 8.6259 | 8.9449 | 9.2756 | 9.6186 | 2.5813 | 2.8889 | 3.2079 | 3.5386 | 3.8816 | 14
2020-08-11 | 2020-08-10 | 0 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 15
2020-08-11 01:00 | 2020-08-11 | 1 | 4.638 | 0.0161% | 6.9151 | 7.1708 | 7.436 | 7.7109 | 7.9961 | 1.1781 | 1.4338 | 1.699 | 1.9739 | 2.2591 | 16
2020-08-11 02:00 | 2020-08-11 | 2 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 17
2020-08-11 03:00 | 2020-08-11 | 3 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 18
2020-08-11 04:00 | 2020-08-11 | 4 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 19
2020-08-11 05:00 | 2020-08-11 | 5 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 20
2020-08-11 06:00 | 2020-08-11 | 6 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 21
2020-08-11 07:00 | 2020-08-11 | 7 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 22
2020-08-11 08:00 | 2020-08-11 | 8 | 5.7297 | 0.0199% | 8.5428 | 8.8587 | 9.1863 | 9.526 | 9.8783 | 2.8058 | 3.1217 | 3.4493 | 3.789 | 4.1413 | 23
2020-08-11 09:00 | 2020-08-11 | 9 | 6.061 | 0.02105% | 9.0368 | 9.3709 | 9.7174 | 10.0768 | 10.4494 | 3.2998 | 3.6339 | 3.9804 | 4.3398 | 4.7124 | 24
2020-08-11 10:00 | 2020-08-11 | 10 | 6.558 | 0.02277% | 9.7777 | 10.1392 | 10.5142 | 10.903 | 11.3061 | 4.0407 | 4.4022 | 4.7772 | 5.166 | 5.5691 | 25
2020-08-11 11:00 | 2020-08-11 | 11 | 7.0022 | 0.02431% | 10.44 | 10.826 | 11.2264 | 11.6415 | 12.072 | 4.703 | 5.089 | 5.4894 | 5.9045 | 6.335 | 26
2020-08-11 12:00 | 2020-08-11 | 12 | 6.9043 | 0.02397% | 10.2941 | 10.6747 | 11.0694 | 11.4788 | 11.9032 | 4.5571 | 4.9377 | 5.3324 | 5.7418 | 6.1662 | 27
2020-08-11 13:00 | 2020-08-11 | 13 | 7.1377 | 0.02478% | 10.6421 | 11.0356 | 11.4437 | 11.8668 | 12.3056 | 4.9051 | 5.2986 | 5.7067 | 6.1298 | 6.5686 | 28
2020-08-11 14:00 | 2020-08-11 | 14 | 7.1076 | 0.02468% | 10.5971 | 10.989 | 11.3954 | 11.8168 | 12.2537 | 4.8601 | 5.252 | 5.6584 | 6.0798 | 6.5167 | 29
2020-08-11 15:00 | 2020-08-11 | 15 | 7.3033 | 0.02536% | 10.889 | 11.2917 | 11.7092 | 12.1422 | 12.5912 | 5.152 | 5.5547 | 5.9722 | 6.4052 | 6.8542 | 30
2020-08-11 16:00 | 2020-08-11 | 16 | 7.3636 | 0.02557% | 10.9788 | 11.3848 | 11.8058 | 12.2424 | 12.6951 | 5.2418 | 5.6478 | 6.0688 | 6.5054 | 6.9581 | 31
2020-08-11 17:00 | 2020-08-11 | 17 | 7.0925 | 0.02463% | 10.5747 | 10.9657 | 11.3712 | 11.7917 | 12.2278 | 4.8377 | 5.2287 | 5.6342 | 6.0547 | 6.4908 | 32
2020-08-11 18:00 | 2020-08-11 | 18 | 7.0097 | 0.02434% | 10.4512 | 10.8377 | 11.2384 | 11.654 | 12.085 | 4.7142 | 5.1007 | 5.5014 | 5.917 | 6.348 | 33
2020-08-11 19:00 | 2020-08-11 | 19 | 6.8742 | 0.02387% | 10.2491 | 10.6281 | 11.0212 | 11.4287 | 11.8513 | 4.5121 | 4.8911 | 5.2842 | 5.6917 | 6.1143 | 34
2020-08-11 20:00 | 2020-08-11 | 20 | 6.3547 | 0.02207% | 9.4746 | 9.8249 | 10.1882 | 10.565 | 10.9557 | 3.7376 | 4.0879 | 4.4512 | 4.828 | 5.2187 | 35
2020-08-11 21:00 | 2020-08-11 | 21 | 6.0761 | 0.0211% | 9.0592 | 9.3942 | 9.7416 | 10.1018 | 10.4754 | 3.3222 | 3.6572 | 4.0046 | 4.3648 | 4.7384 | 36
2020-08-11 22:00 | 2020-08-11 | 22 | 5.5039 | 0.01911% | 8.2061 | 8.5095 | 8.8242 | 9.1505 | 9.4888 | 2.4691 | 2.7725 | 3.0872 | 3.4135 | 3.7518 | 37
2020-08-11 23:00 | 2020-08-11 | 23 | 4.8865 | 0.01697% | 7.2855 | 7.5549 | 7.8343 | 8.124 | 8.4244 | 1.5485 | 1.8179 | 2.0973 | 2.387 | 2.6874 | 38
2020-08-12 | 2020-08-11 | 0 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 39
2020-08-12 01:00 | 2020-08-12 | 1 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 40 | 40
2020-08-12 02:00 | 2020-08-12 | 2 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-08-12 03:00 | 2020-08-12 | 3 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-08-12 04:00 | 2020-08-12 | 4 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-08-12 05:00 | 2020-08-12 | 5 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-08-12 06:00 | 2020-08-12 | 6 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-08-12 07:00 | 2020-08-12 | 7 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 1
2020-08-12 08:00 | 2020-08-12 | 8 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 2
2020-08-12 09:00 | 2020-08-12 | 9 | 5.165 | 0.01793% | 7.7009 | 7.9857 | 8.281 | 8.5872 | 8.9047 | 1.9639 | 2.2487 | 2.544 | 2.8502 | 3.1677 | 3
2020-08-12 10:00 | 2020-08-12 | 10 | 5.5114 | 0.01914% | 8.2173 | 8.5211 | 8.8362 | 9.163 | 9.5018 | 2.4803 | 2.7841 | 3.0992 | 3.426 | 3.7648 | 4
2020-08-12 11:00 | 2020-08-12 | 11 | 5.9481 | 0.02065% | 8.8684 | 9.1963 | 9.5364 | 9.889 | 10.2547 | 3.1314 | 3.4593 | 3.7994 | 4.152 | 4.5177 | 5
2020-08-12 12:00 | 2020-08-12 | 12 | 6.2342 | 0.02165% | 9.295 | 9.6387 | 9.9951 | 10.3647 | 10.748 | 3.558 | 3.9017 | 4.2581 | 4.6277 | 5.011 | 6
2020-08-12 13:00 | 2020-08-12 | 13 | 6.4751 | 0.02248% | 9.6542 | 10.0112 | 10.3814 | 10.7653 | 11.1633 | 3.9172 | 4.2742 | 4.6444 | 5.0283 | 5.4263 | 7
2020-08-12 14:00 | 2020-08-12 | 14 | 6.6784 | 0.02319% | 9.9573 | 10.3255 | 10.7073 | 11.1032 | 11.5138 | 4.2203 | 4.5885 | 4.9703 | 5.3662 | 5.7768 | 8
2020-08-12 15:00 | 2020-08-12 | 15 | 6.8215 | 0.02369% | 10.1706 | 10.5467 | 10.9367 | 11.3411 | 11.7605 | 4.4336 | 4.8097 | 5.1997 | 5.6041 | 6.0235 | 9
2020-08-12 16:00 | 2020-08-12 | 16 | 7.1829 | 0.02494% | 10.7094 | 11.1054 | 11.5161 | 11.9419 | 12.3835 | 4.9724 | 5.3684 | 5.7791 | 6.2049 | 6.6465 | 10
2020-08-12 17:00 | 2020-08-12 | 17 | 7.0248 | 0.02439% | 10.4737 | 10.861 | 11.2626 | 11.6791 | 12.1109 | 4.7367 | 5.124 | 5.5256 | 5.9421 | 6.3739 | 11
2020-08-12 18:00 | 2020-08-12 | 18 | 7.0624 | 0.02452% | 10.5298 | 10.9192 | 11.3229 | 11.7416 | 12.1758 | 4.7928 | 5.1822 | 5.5859 | 6.0046 | 6.4388 | 12
2020-08-12 19:00 | 2020-08-12 | 19 | 6.686 | 0.02322% | 9.9685 | 10.3371 | 10.7194 | 11.1158 | 11.5268 | 4.2315 | 4.6001 | 4.9824 | 5.3788 | 5.7898 | 13
2020-08-12 20:00 | 2020-08-12 | 20 | 5.9857 | 0.02078% | 8.9245 | 9.2545 | 9.5967 | 9.9516 | 10.3196 | 3.1875 | 3.5175 | 3.8597 | 4.2146 | 4.5826 | 14
2020-08-12 21:00 | 2020-08-12 | 21 | 5.7222 | 0.01987% | 8.5316 | 8.8471 | 9.1742 | 9.5135 | 9.8653 | 2.7946 | 3.1101 | 3.4372 | 3.7765 | 4.1283 | 15
2020-08-12 22:00 | 2020-08-12 | 22 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 16
2020-08-12 23:00 | 2020-08-12 | 23 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 17
2020-08-13 | 2020-08-12 | 0 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 18
2020-08-13 01:00 | 2020-08-13 | 1 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 19 | 19
2020-08-13 02:00 | 2020-08-13 | 2 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-13 03:00 | 2020-08-13 | 3 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-08-13 04:00 | 2020-08-13 | 4 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-08-13 05:00 | 2020-08-13 | 5 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-08-13 06:00 | 2020-08-13 | 6 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-08-13 07:00 | 2020-08-13 | 7 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 1
2020-08-13 08:00 | 2020-08-13 | 8 | 4.7208 | 0.01639% | 7.0386 | 7.2988 | 7.5687 | 7.8486 | 8.1389 | 1.3016 | 1.5618 | 1.8317 | 2.1116 | 2.4019 | 2
2020-08-13 09:00 | 2020-08-13 | 9 | 5.2102 | 0.01809% | 7.7682 | 8.0555 | 8.3534 | 8.6623 | 8.9826 | 2.0312 | 2.3185 | 2.6164 | 2.9253 | 3.2456 | 3
2020-08-13 10:00 | 2020-08-13 | 10 | 5.7448 | 0.01995% | 8.5653 | 8.882 | 9.2105 | 9.551 | 9.9042 | 2.8283 | 3.145 | 3.4735 | 3.814 | 4.1672 | 4
2020-08-13 11:00 | 2020-08-13 | 11 | 6.174 | 0.02144% | 9.2051 | 9.5455 | 9.8985 | 10.2646 | 10.6441 | 3.4681 | 3.8085 | 4.1615 | 4.5276 | 4.9071 | 5
2020-08-13 12:00 | 2020-08-13 | 12 | 6.6107 | 0.02295% | 9.8562 | 10.2207 | 10.5987 | 10.9906 | 11.397 | 4.1192 | 4.4837 | 4.8617 | 5.2536 | 5.66 | 6
2020-08-13 13:00 | 2020-08-13 | 13 | 6.9946 | 0.02429% | 10.4288 | 10.8144 | 11.2143 | 11.629 | 12.059 | 4.6918 | 5.0774 | 5.4773 | 5.892 | 6.322 | 7
2020-08-13 14:00 | 2020-08-13 | 14 | 7.1151 | 0.02471% | 10.6084 | 11.0007 | 11.4074 | 11.8293 | 12.2667 | 4.8714 | 5.2637 | 5.6704 | 6.0923 | 6.5297 | 8
2020-08-13 15:00 | 2020-08-13 | 15 | 7.341 | 0.02549% | 10.9451 | 11.3499 | 11.7696 | 12.2048 | 12.6561 | 5.2081 | 5.6129 | 6.0326 | 6.4678 | 6.9191 | 9
2020-08-13 16:00 | 2020-08-13 | 16 | 7.2883 | 0.02531% | 10.8666 | 11.2684 | 11.6851 | 12.1172 | 12.5653 | 5.1296 | 5.5314 | 5.9481 | 6.3802 | 6.8283 | 10
2020-08-13 17:00 | 2020-08-13 | 17 | 7.3033 | 0.02536% | 10.889 | 11.2917 | 11.7092 | 12.1422 | 12.5912 | 5.152 | 5.5547 | 5.9722 | 6.4052 | 6.8542 | 11
2020-08-13 18:00 | 2020-08-13 | 18 | 7.2883 | 0.02531% | 10.8666 | 11.2684 | 11.6851 | 12.1172 | 12.5653 | 5.1296 | 5.5314 | 5.9481 | 6.3802 | 6.8283 | 12
2020-08-13 19:00 | 2020-08-13 | 19 | 6.7914 | 0.02358% | 10.1257 | 10.5001 | 10.8884 | 11.291 | 11.7085 | 4.3887 | 4.7631 | 5.1514 | 5.554 | 5.9715 | 13
2020-08-13 20:00 | 2020-08-13 | 20 | 6.4525 | 0.02241% | 9.6205 | 9.9763 | 10.3452 | 10.7277 | 11.1244 | 3.8835 | 4.2393 | 4.6082 | 4.9907 | 5.3874 | 14
2020-08-13 21:00 | 2020-08-13 | 21 | 6.2267 | 0.02162% | 9.2837 | 9.627 | 9.983 | 10.3522 | 10.735 | 3.5467 | 3.89 | 4.246 | 4.6152 | 4.998 | 15
2020-08-13 22:00 | 2020-08-13 | 22 | 5.6168 | 0.0195% | 8.3744 | 8.6841 | 9.0052 | 9.3382 | 9.6836 | 2.6374 | 2.9471 | 3.2682 | 3.6012 | 3.9466 | 16
2020-08-13 23:00 | 2020-08-13 | 23 | 5.0747 | 0.01762% | 7.5662 | 7.846 | 8.1361 | 8.437 | 8.7489 | 1.8292 | 2.109 | 2.3991 | 2.7 | 3.0119 | 17
2020-08-14 | 2020-08-13 | 0 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 18
2020-08-14 01:00 | 2020-08-14 | 1 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 19
2020-08-14 02:00 | 2020-08-14 | 2 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 20 | 20
2020-08-14 03:00 | 2020-08-14 | 3 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-14 04:00 | 2020-08-14 | 4 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-08-14 05:00 | 2020-08-14 | 5 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-08-14 06:00 | 2020-08-14 | 6 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 1
2020-08-14 07:00 | 2020-08-14 | 7 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 2
2020-08-14 08:00 | 2020-08-14 | 8 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 3
2020-08-14 09:00 | 2020-08-14 | 9 | 5.3457 | 0.01856% | 7.9703 | 8.265 | 8.5707 | 8.8876 | 9.2162 | 2.2333 | 2.528 | 2.8337 | 3.1506 | 3.4792 | 4
2020-08-14 10:00 | 2020-08-14 | 10 | 5.7599 | 0.02% | 8.5877 | 8.9053 | 9.2346 | 9.5761 | 9.9302 | 2.8507 | 3.1683 | 3.4976 | 3.8391 | 4.1932 | 5
2020-08-14 11:00 | 2020-08-14 | 11 | 6.1288 | 0.02128% | 9.1378 | 9.4757 | 9.8261 | 10.1894 | 10.5662 | 3.4008 | 3.7387 | 4.0891 | 4.4524 | 4.8292 | 6
2020-08-14 12:00 | 2020-08-14 | 12 | 6.43 | 0.02233% | 9.5868 | 9.9413 | 10.3089 | 10.6902 | 11.0855 | 3.8498 | 4.2043 | 4.5719 | 4.9532 | 5.3485 | 7
2020-08-14 13:00 | 2020-08-14 | 13 | 6.5203 | 0.02264% | 9.7215 | 10.081 | 10.4538 | 10.8404 | 11.2412 | 3.9845 | 4.344 | 4.7168 | 5.1034 | 5.5042 | 8
2020-08-14 14:00 | 2020-08-14 | 14 | 6.6107 | 0.02295% | 9.8562 | 10.2207 | 10.5987 | 10.9906 | 11.397 | 4.1192 | 4.4837 | 4.8617 | 5.2536 | 5.66 | 9
2020-08-14 15:00 | 2020-08-14 | 15 | 6.8742 | 0.02387% | 10.2491 | 10.6281 | 11.0212 | 11.4287 | 11.8513 | 4.5121 | 4.8911 | 5.2842 | 5.6917 | 6.1143 | 10
2020-08-14 16:00 | 2020-08-14 | 16 | 6.8742 | 0.02387% | 10.2491 | 10.6281 | 11.0212 | 11.4287 | 11.8513 | 4.5121 | 4.8911 | 5.2842 | 5.6917 | 6.1143 | 11
2020-08-14 17:00 | 2020-08-14 | 17 | 6.9495 | 0.02413% | 10.3614 | 10.7446 | 11.1419 | 11.5539 | 11.9811 | 4.6244 | 5.0076 | 5.4049 | 5.8169 | 6.2441 | 12
2020-08-14 18:00 | 2020-08-14 | 18 | 6.8365 | 0.02374% | 10.193 | 10.5699 | 10.9608 | 11.3661 | 11.7864 | 4.456 | 4.8329 | 5.2238 | 5.6291 | 6.0494 | 13
2020-08-14 19:00 | 2020-08-14 | 19 | 6.5278 | 0.02267% | 9.7328 | 10.0927 | 10.4659 | 10.8529 | 11.2542 | 3.9958 | 4.3557 | 4.7289 | 5.1159 | 5.5172 | 14
2020-08-14 20:00 | 2020-08-14 | 20 | 5.9481 | 0.02065% | 8.8684 | 9.1963 | 9.5364 | 9.889 | 10.2547 | 3.1314 | 3.4593 | 3.7994 | 4.152 | 4.5177 | 15
2020-08-14 21:00 | 2020-08-14 | 21 | 5.7523 | 0.01997% | 8.5765 | 8.8937 | 9.2225 | 9.5636 | 9.9172 | 2.8395 | 3.1567 | 3.4855 | 3.8266 | 4.1802 | 16
2020-08-14 22:00 | 2020-08-14 | 22 | 5.278 | 0.01833% | 7.8693 | 8.1603 | 8.462 | 8.7749 | 9.0994 | 2.1323 | 2.4233 | 2.725 | 3.0379 | 3.3624 | 17
2020-08-14 23:00 | 2020-08-14 | 23 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 18
2020-08-15 | 2020-08-14 | 0 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 19
2020-08-15 01:00 | 2020-08-15 | 1 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 20 | 20
2020-08-15 02:00 | 2020-08-15 | 2 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-08-15 03:00 | 2020-08-15 | 3 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-08-15 04:00 | 2020-08-15 | 4 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-08-15 05:00 | 2020-08-15 | 5 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-08-15 06:00 | 2020-08-15 | 6 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-08-15 07:00 | 2020-08-15 | 7 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-08-15 08:00 | 2020-08-15 | 8 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 1
2020-08-15 09:00 | 2020-08-15 | 9 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 2
2020-08-15 10:00 | 2020-08-15 | 10 | 5.3759 | 0.01867% | 8.0152 | 8.3116 | 8.619 | 8.9377 | 9.2682 | 2.2782 | 2.5746 | 2.882 | 3.2007 | 3.5312 | 3
2020-08-15 11:00 | 2020-08-15 | 11 | 5.5792 | 0.01937% | 8.3183 | 8.6259 | 8.9449 | 9.2756 | 9.6186 | 2.5813 | 2.8889 | 3.2079 | 3.5386 | 3.8816 | 4
2020-08-15 12:00 | 2020-08-15 | 12 | 5.9029 | 0.0205% | 8.801 | 9.1265 | 9.464 | 9.8139 | 10.1768 | 3.064 | 3.3895 | 3.727 | 4.0769 | 4.4398 | 5
2020-08-15 13:00 | 2020-08-15 | 13 | 6.174 | 0.02144% | 9.2051 | 9.5455 | 9.8985 | 10.2646 | 10.6441 | 3.4681 | 3.8085 | 4.1615 | 4.5276 | 4.9071 | 6
2020-08-15 14:00 | 2020-08-15 | 14 | 6.3923 | 0.0222% | 9.5307 | 9.8831 | 10.2486 | 10.6276 | 11.0206 | 3.7937 | 4.1461 | 4.5116 | 4.8906 | 5.2836 | 7
2020-08-15 15:00 | 2020-08-15 | 15 | 6.6107 | 0.02295% | 9.8562 | 10.2207 | 10.5987 | 10.9906 | 11.397 | 4.1192 | 4.4837 | 4.8617 | 5.2536 | 5.66 | 8
2020-08-15 16:00 | 2020-08-15 | 16 | 6.8215 | 0.02369% | 10.1706 | 10.5467 | 10.9367 | 11.3411 | 11.7605 | 4.4336 | 4.8097 | 5.1997 | 5.6041 | 6.0235 | 9
2020-08-15 17:00 | 2020-08-15 | 17 | 6.9118 | 0.024% | 10.3053 | 10.6864 | 11.0815 | 11.4913 | 11.9162 | 4.5683 | 4.9494 | 5.3445 | 5.7543 | 6.1792 | 10
2020-08-15 18:00 | 2020-08-15 | 18 | 6.7537 | 0.02345% | 10.0695 | 10.4419 | 10.828 | 11.2284 | 11.6436 | 4.3325 | 4.7049 | 5.091 | 5.4914 | 5.9066 | 11
2020-08-15 19:00 | 2020-08-15 | 19 | 6.5128 | 0.02261% | 9.7103 | 10.0694 | 10.4417 | 10.8278 | 11.2282 | 3.9733 | 4.3324 | 4.7047 | 5.0908 | 5.4912 | 12
2020-08-15 20:00 | 2020-08-15 | 20 | 6.1213 | 0.02126% | 9.1266 | 9.4641 | 9.814 | 10.1769 | 10.5533 | 3.3896 | 3.7271 | 4.077 | 4.4399 | 4.8163 | 13
2020-08-15 21:00 | 2020-08-15 | 21 | 6.0083 | 0.02086% | 8.9582 | 9.2894 | 9.633 | 9.9892 | 10.3585 | 3.2212 | 3.5524 | 3.896 | 4.2522 | 4.6215 | 14
2020-08-15 22:00 | 2020-08-15 | 22 | 5.5189 | 0.01916% | 8.2285 | 8.5328 | 8.8483 | 9.1755 | 9.5148 | 2.4915 | 2.7958 | 3.1113 | 3.4385 | 3.7778 | 15
2020-08-15 23:00 | 2020-08-15 | 23 | 4.9843 | 0.01731% | 7.4315 | 7.7063 | 7.9912 | 8.2867 | 8.5932 | 1.6945 | 1.9693 | 2.2542 | 2.5497 | 2.8562 | 16
2020-08-16 | 2020-08-15 | 0 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 17
2020-08-16 01:00 | 2020-08-16 | 1 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 18
2020-08-16 02:00 | 2020-08-16 | 2 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 19
2020-08-16 03:00 | 2020-08-16 | 3 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 20 | 20
2020-08-16 04:00 | 2020-08-16 | 4 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-08-16 05:00 | 2020-08-16 | 5 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-08-16 06:00 | 2020-08-16 | 6 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-08-16 07:00 | 2020-08-16 | 7 | 4.111 | 0.01427% | 6.1293 | 6.3559 | 6.591 | 6.8347 | 7.0874 | 0.39228 | 0.61893 | 0.85397 | 1.0977 | 1.3504 | 1
2020-08-16 08:00 | 2020-08-16 | 8 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 2
2020-08-16 09:00 | 2020-08-16 | 9 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 3
2020-08-16 10:00 | 2020-08-16 | 10 | 5.0371 | 0.01749% | 7.5101 | 7.7878 | 8.0757 | 8.3744 | 8.684 | 1.7731 | 2.0508 | 2.3387 | 2.6374 | 2.947 | 4
2020-08-16 11:00 | 2020-08-16 | 11 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 5
2020-08-16 12:00 | 2020-08-16 | 12 | 5.8653 | 0.02037% | 8.7449 | 9.0683 | 9.4036 | 9.7513 | 10.1119 | 3.0079 | 3.3313 | 3.6666 | 4.0143 | 4.3749 | 6
2020-08-16 13:00 | 2020-08-16 | 13 | 5.7749 | 0.02005% | 8.6102 | 8.9286 | 9.2587 | 9.6011 | 9.9561 | 2.8732 | 3.1916 | 3.5217 | 3.8641 | 4.2191 | 7
2020-08-16 14:00 | 2020-08-16 | 14 | 5.7222 | 0.01987% | 8.5316 | 8.8471 | 9.1742 | 9.5135 | 9.8653 | 2.7946 | 3.1101 | 3.4372 | 3.7765 | 4.1283 | 8
2020-08-16 15:00 | 2020-08-16 | 15 | 5.6846 | 0.01974% | 8.4755 | 8.7889 | 9.1139 | 9.4509 | 9.8004 | 2.7385 | 3.0519 | 3.3769 | 3.7139 | 4.0634 | 9
2020-08-16 16:00 | 2020-08-16 | 16 | 5.9556 | 0.02068% | 8.8796 | 9.208 | 9.5485 | 9.9015 | 10.2677 | 3.1426 | 3.471 | 3.8115 | 4.1645 | 4.5307 | 10
2020-08-16 17:00 | 2020-08-16 | 17 | 6.0384 | 0.02097% | 9.0031 | 9.336 | 9.6812 | 10.0392 | 10.4105 | 3.2661 | 3.599 | 3.9442 | 4.3022 | 4.6735 | 11
2020-08-16 18:00 | 2020-08-16 | 18 | 5.8351 | 0.02026% | 8.7 | 9.0217 | 9.3553 | 9.7013 | 10.06 | 2.963 | 3.2847 | 3.6183 | 3.9643 | 4.323 | 12
2020-08-16 19:00 | 2020-08-16 | 19 | 5.4813 | 0.01903% | 8.1724 | 8.4746 | 8.788 | 9.1129 | 9.4499 | 2.4354 | 2.7376 | 3.051 | 3.3759 | 3.7129 | 13
2020-08-16 20:00 | 2020-08-16 | 20 | 5.3533 | 0.01859% | 7.9815 | 8.2767 | 8.5827 | 8.9001 | 9.2292 | 2.2445 | 2.5397 | 2.8457 | 3.1631 | 3.4922 | 14
2020-08-16 21:00 | 2020-08-16 | 21 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 15
2020-08-16 22:00 | 2020-08-16 | 22 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 16
2020-08-16 23:00 | 2020-08-16 | 23 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 17
2020-08-17 | 2020-08-16 | 0 | 4.5627 | 0.01584% | 6.8028 | 7.0544 | 7.3152 | 7.5858 | 7.8663 | 1.0658 | 1.3174 | 1.5782 | 1.8488 | 2.1293 | 18 | 18
2020-08-17 01:00 | 2020-08-17 | 1 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-08-17 02:00 | 2020-08-17 | 2 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-08-17 03:00 | 2020-08-17 | 3 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-08-17 04:00 | 2020-08-17 | 4 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-08-17 05:00 | 2020-08-17 | 5 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-08-17 06:00 | 2020-08-17 | 6 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1
2020-08-17 07:00 | 2020-08-17 | 7 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 2
2020-08-17 08:00 | 2020-08-17 | 8 | 4.5552 | 0.01582% | 6.7916 | 7.0427 | 7.3032 | 7.5732 | 7.8533 | 1.0546 | 1.3057 | 1.5662 | 1.8362 | 2.1163 | 3 | 3
2020-08-17 09:00 | 2020-08-17 | 9 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-08-17 10:00 | 2020-08-17 | 10 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1
2020-08-17 11:00 | 2020-08-17 | 11 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 2
2020-08-17 12:00 | 2020-08-17 | 12 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 3
2020-08-17 13:00 | 2020-08-17 | 13 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 4
2020-08-17 14:00 | 2020-08-17 | 14 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 5
2020-08-17 15:00 | 2020-08-17 | 15 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 6
2020-08-17 16:00 | 2020-08-17 | 16 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 7 | 7
2020-08-17 17:00 | 2020-08-17 | 17 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-08-17 18:00 | 2020-08-17 | 18 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-08-17 19:00 | 2020-08-17 | 19 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-08-17 20:00 | 2020-08-17 | 20 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-08-17 21:00 | 2020-08-17 | 21 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-08-17 22:00 | 2020-08-17 | 22 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-08-17 23:00 | 2020-08-17 | 23 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-18 | 2020-08-17 | 0 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1 | 1
2020-08-18 01:00 | 2020-08-18 | 1 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-08-18 02:00 | 2020-08-18 | 2 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-08-18 03:00 | 2020-08-18 | 3 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-08-18 04:00 | 2020-08-18 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-08-18 05:00 | 2020-08-18 | 5 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-08-18 06:00 | 2020-08-18 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-08-18 07:00 | 2020-08-18 | 7 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-08-18 08:00 | 2020-08-18 | 8 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-08-18 09:00 | 2020-08-18 | 9 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-08-18 10:00 | 2020-08-18 | 10 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-18 11:00 | 2020-08-18 | 11 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-18 12:00 | 2020-08-18 | 12 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 1
2020-08-18 13:00 | 2020-08-18 | 13 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 2
2020-08-18 14:00 | 2020-08-18 | 14 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 3
2020-08-18 15:00 | 2020-08-18 | 15 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 4
2020-08-18 16:00 | 2020-08-18 | 16 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 5
2020-08-18 17:00 | 2020-08-18 | 17 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 6 | 6
2020-08-18 18:00 | 2020-08-18 | 18 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-18 19:00 | 2020-08-18 | 19 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-08-18 20:00 | 2020-08-18 | 20 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-08-18 21:00 | 2020-08-18 | 21 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-08-18 22:00 | 2020-08-18 | 22 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-08-18 23:00 | 2020-08-18 | 23 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-19 | 2020-08-18 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-08-19 01:00 | 2020-08-19 | 1 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-08-19 02:00 | 2020-08-19 | 2 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-08-19 03:00 | 2020-08-19 | 3 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-08-19 04:00 | 2020-08-19 | 4 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-08-19 05:00 | 2020-08-19 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-08-19 06:00 | 2020-08-19 | 6 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-08-19 07:00 | 2020-08-19 | 7 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-08-19 08:00 | 2020-08-19 | 8 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-08-19 09:00 | 2020-08-19 | 9 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-08-19 10:00 | 2020-08-19 | 10 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-08-19 11:00 | 2020-08-19 | 11 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-08-19 12:00 | 2020-08-19 | 12 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-08-19 13:00 | 2020-08-19 | 13 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-08-19 14:00 | 2020-08-19 | 14 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1
2020-08-19 15:00 | 2020-08-19 | 15 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 2 | 2
2020-08-19 16:00 | 2020-08-19 | 16 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-08-19 17:00 | 2020-08-19 | 17 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 1 | 1
2020-08-19 18:00 | 2020-08-19 | 18 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-08-19 19:00 | 2020-08-19 | 19 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-08-19 20:00 | 2020-08-19 | 20 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-08-19 21:00 | 2020-08-19 | 21 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-19 22:00 | 2020-08-19 | 22 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-08-19 23:00 | 2020-08-19 | 23 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-20 | 2020-08-19 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-08-20 01:00 | 2020-08-20 | 1 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-08-20 02:00 | 2020-08-20 | 2 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-08-20 03:00 | 2020-08-20 | 3 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-08-20 04:00 | 2020-08-20 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-08-20 05:00 | 2020-08-20 | 5 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-08-20 06:00 | 2020-08-20 | 6 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-08-20 07:00 | 2020-08-20 | 7 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-20 08:00 | 2020-08-20 | 8 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-08-20 09:00 | 2020-08-20 | 9 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-08-20 10:00 | 2020-08-20 | 10 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-08-20 11:00 | 2020-08-20 | 11 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-08-20 12:00 | 2020-08-20 | 12 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-08-20 13:00 | 2020-08-20 | 13 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 1
2020-08-20 14:00 | 2020-08-20 | 14 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 2
2020-08-20 15:00 | 2020-08-20 | 15 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 3
2020-08-20 16:00 | 2020-08-20 | 16 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 4
2020-08-20 17:00 | 2020-08-20 | 17 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 5
2020-08-20 18:00 | 2020-08-20 | 18 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 6 | 6
2020-08-20 19:00 | 2020-08-20 | 19 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-08-20 20:00 | 2020-08-20 | 20 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-08-20 21:00 | 2020-08-20 | 21 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-20 22:00 | 2020-08-20 | 22 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-08-20 23:00 | 2020-08-20 | 23 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-08-21 | 2020-08-20 | 0 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-08-21 01:00 | 2020-08-21 | 1 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-08-21 02:00 | 2020-08-21 | 2 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-08-21 03:00 | 2020-08-21 | 3 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-08-21 04:00 | 2020-08-21 | 4 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-08-21 05:00 | 2020-08-21 | 5 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-21 06:00 | 2020-08-21 | 6 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-08-21 07:00 | 2020-08-21 | 7 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-08-21 08:00 | 2020-08-21 | 8 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-08-21 09:00 | 2020-08-21 | 9 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-08-21 10:00 | 2020-08-21 | 10 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1
2020-08-21 11:00 | 2020-08-21 | 11 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 2
2020-08-21 12:00 | 2020-08-21 | 12 | 4.2088 | 0.01461% | 6.2752 | 6.5073 | 6.7479 | 6.9974 | 7.2562 | 0.53822 | 0.77027 | 1.0109 | 1.2604 | 1.5192 | 3
2020-08-21 13:00 | 2020-08-21 | 13 | 4.4197 | 0.01535% | 6.5895 | 6.8332 | 7.0859 | 7.3479 | 7.6196 | 0.85254 | 1.0962 | 1.3489 | 1.6109 | 1.8826 | 4
2020-08-21 14:00 | 2020-08-21 | 14 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 5
2020-08-21 15:00 | 2020-08-21 | 15 | 4.5401 | 0.01576% | 6.7692 | 7.0195 | 7.279 | 7.5482 | 7.8273 | 1.0322 | 1.2825 | 1.542 | 1.8112 | 2.0903 | 6
2020-08-21 16:00 | 2020-08-21 | 16 | 4.5477 | 0.01579% | 6.7804 | 7.0311 | 7.2911 | 7.5607 | 7.8403 | 1.0434 | 1.2941 | 1.5541 | 1.8237 | 2.1033 | 7
2020-08-21 17:00 | 2020-08-21 | 17 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 8
2020-08-21 18:00 | 2020-08-21 | 18 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 9
2020-08-21 19:00 | 2020-08-21 | 19 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 10
2020-08-21 20:00 | 2020-08-21 | 20 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 11 | 11
2020-08-21 21:00 | 2020-08-21 | 21 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-08-21 22:00 | 2020-08-21 | 22 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-08-21 23:00 | 2020-08-21 | 23 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-08-22 | 2020-08-21 | 0 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-08-22 01:00 | 2020-08-22 | 1 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-08-22 02:00 | 2020-08-22 | 2 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-08-22 03:00 | 2020-08-22 | 3 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-08-22 04:00 | 2020-08-22 | 4 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-08-22 05:00 | 2020-08-22 | 5 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-08-22 06:00 | 2020-08-22 | 6 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-08-22 07:00 | 2020-08-22 | 7 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-08-22 08:00 | 2020-08-22 | 8 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-08-22 09:00 | 2020-08-22 | 9 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-08-22 10:00 | 2020-08-22 | 10 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 1
2020-08-22 11:00 | 2020-08-22 | 11 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 2
2020-08-22 12:00 | 2020-08-22 | 12 | 4.4573 | 0.01548% | 6.6457 | 6.8914 | 7.1462 | 7.4105 | 7.6845 | 0.90867 | 1.1544 | 1.4092 | 1.6735 | 1.9475 | 3
2020-08-22 13:00 | 2020-08-22 | 13 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 4
2020-08-22 14:00 | 2020-08-22 | 14 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 5
2020-08-22 15:00 | 2020-08-22 | 15 | 4.7735 | 0.01658% | 7.1172 | 7.3803 | 7.6532 | 7.9363 | 8.2297 | 1.3802 | 1.6433 | 1.9162 | 2.1993 | 2.4927 | 6
2020-08-22 16:00 | 2020-08-22 | 16 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 7
2020-08-22 17:00 | 2020-08-22 | 17 | 4.8413 | 0.01681% | 7.2182 | 7.4851 | 7.7619 | 8.0489 | 8.3465 | 1.4812 | 1.7481 | 2.0249 | 2.3119 | 2.6095 | 8
2020-08-22 18:00 | 2020-08-22 | 18 | 4.894 | 0.01699% | 7.2968 | 7.5666 | 7.8464 | 8.1365 | 8.4374 | 1.5598 | 1.8296 | 2.1094 | 2.3995 | 2.7004 | 9
2020-08-22 19:00 | 2020-08-22 | 19 | 4.5853 | 0.01592% | 6.8365 | 7.0893 | 7.3515 | 7.6233 | 7.9052 | 1.0995 | 1.3523 | 1.6145 | 1.8863 | 2.1682 | 10
2020-08-22 20:00 | 2020-08-22 | 20 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 11
2020-08-22 21:00 | 2020-08-22 | 21 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 12 | 12
2020-08-22 22:00 | 2020-08-22 | 22 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-22 23:00 | 2020-08-22 | 23 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-08-23 | 2020-08-22 | 0 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-08-23 01:00 | 2020-08-23 | 1 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-08-23 02:00 | 2020-08-23 | 2 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-08-23 03:00 | 2020-08-23 | 3 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-08-23 04:00 | 2020-08-23 | 4 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-08-23 05:00 | 2020-08-23 | 5 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-08-23 06:00 | 2020-08-23 | 6 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-08-23 07:00 | 2020-08-23 | 7 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-08-23 08:00 | 2020-08-23 | 8 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-08-23 09:00 | 2020-08-23 | 9 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 1
2020-08-23 10:00 | 2020-08-23 | 10 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 2
2020-08-23 11:00 | 2020-08-23 | 11 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 3
2020-08-23 12:00 | 2020-08-23 | 12 | 4.9316 | 0.01712% | 7.3529 | 7.6248 | 7.9067 | 8.1991 | 8.5023 | 1.6159 | 1.8878 | 2.1697 | 2.4621 | 2.7653 | 4
2020-08-23 13:00 | 2020-08-23 | 13 | 5.0596 | 0.01757% | 7.5437 | 7.8227 | 8.112 | 8.4119 | 8.723 | 1.8067 | 2.0857 | 2.375 | 2.6749 | 2.986 | 5
2020-08-23 14:00 | 2020-08-23 | 14 | 4.9241 | 0.0171% | 7.3417 | 7.6132 | 7.8947 | 8.1866 | 8.4893 | 1.6047 | 1.8762 | 2.1577 | 2.4496 | 2.7523 | 6
2020-08-23 15:00 | 2020-08-23 | 15 | 5.1425 | 0.01786% | 7.6672 | 7.9507 | 8.2447 | 8.5496 | 8.8658 | 1.9302 | 2.2137 | 2.5077 | 2.8126 | 3.1288 | 7
2020-08-23 16:00 | 2020-08-23 | 16 | 5.2554 | 0.01825% | 7.8356 | 8.1254 | 8.4258 | 8.7374 | 9.0605 | 2.0986 | 2.3884 | 2.6888 | 3.0004 | 3.3235 | 8
2020-08-23 17:00 | 2020-08-23 | 17 | 5.3081 | 0.01843% | 7.9142 | 8.2068 | 8.5103 | 8.825 | 9.1513 | 2.1772 | 2.4698 | 2.7733 | 3.088 | 3.4143 | 9
2020-08-23 18:00 | 2020-08-23 | 18 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 10
2020-08-23 19:00 | 2020-08-23 | 19 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 11
2020-08-23 20:00 | 2020-08-23 | 20 | 4.2766 | 0.01485% | 6.3763 | 6.612 | 6.8565 | 7.1101 | 7.373 | 0.63925 | 0.87503 | 1.1195 | 1.3731 | 1.636 | 12
2020-08-23 21:00 | 2020-08-23 | 21 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 13 | 13
2020-08-23 22:00 | 2020-08-23 | 22 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-08-23 23:00 | 2020-08-23 | 23 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-08-24 | 2020-08-23 | 0 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-08-24 01:00 | 2020-08-24 | 1 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-08-24 02:00 | 2020-08-24 | 2 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-08-24 03:00 | 2020-08-24 | 3 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-08-24 04:00 | 2020-08-24 | 4 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-08-24 05:00 | 2020-08-24 | 5 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-08-24 06:00 | 2020-08-24 | 6 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-08-24 07:00 | 2020-08-24 | 7 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-08-24 08:00 | 2020-08-24 | 8 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 1
2020-08-24 09:00 | 2020-08-24 | 9 | 4.4422 | 0.01543% | 6.6232 | 6.8681 | 7.1221 | 7.3855 | 7.6586 | 0.88622 | 1.1311 | 1.3851 | 1.6485 | 1.9216 | 2
2020-08-24 10:00 | 2020-08-24 | 10 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 3
2020-08-24 11:00 | 2020-08-24 | 11 | 5.1123 | 0.01775% | 7.6223 | 7.9042 | 8.1965 | 8.4995 | 8.8138 | 1.8853 | 2.1672 | 2.4595 | 2.7625 | 3.0768 | 4
2020-08-24 12:00 | 2020-08-24 | 12 | 5.2178 | 0.01812% | 7.7795 | 8.0671 | 8.3655 | 8.6748 | 8.9956 | 2.0425 | 2.3301 | 2.6285 | 2.9378 | 3.2586 | 5
2020-08-24 13:00 | 2020-08-24 | 13 | 5.3985 | 0.01875% | 8.0489 | 8.3465 | 8.6552 | 8.9752 | 9.3071 | 2.3119 | 2.6095 | 2.9182 | 3.2382 | 3.5701 | 6
2020-08-24 14:00 | 2020-08-24 | 14 | 5.0295 | 0.01746% | 7.4988 | 7.7761 | 8.0637 | 8.3619 | 8.6711 | 1.7618 | 2.0391 | 2.3267 | 2.6249 | 2.9341 | 7
2020-08-24 15:00 | 2020-08-24 | 15 | 4.9994 | 0.01736% | 7.4539 | 7.7296 | 8.0154 | 8.3118 | 8.6191 | 1.7169 | 1.9926 | 2.2784 | 2.5748 | 2.8821 | 8
2020-08-24 16:00 | 2020-08-24 | 16 | 5.3382 | 0.01854% | 7.9591 | 8.2534 | 8.5586 | 8.8751 | 9.2033 | 2.2221 | 2.5164 | 2.8216 | 3.1381 | 3.4663 | 9
2020-08-24 17:00 | 2020-08-24 | 17 | 5.1726 | 0.01796% | 7.7121 | 7.9973 | 8.293 | 8.5997 | 8.9177 | 1.9751 | 2.2603 | 2.556 | 2.8627 | 3.1807 | 10
2020-08-24 18:00 | 2020-08-24 | 18 | 5.1199 | 0.01778% | 7.6335 | 7.9158 | 8.2085 | 8.5121 | 8.8268 | 1.8965 | 2.1788 | 2.4715 | 2.7751 | 3.0898 | 11
2020-08-24 19:00 | 2020-08-24 | 19 | 4.8187 | 0.01673% | 7.1845 | 7.4502 | 7.7257 | 8.0114 | 8.3076 | 1.4475 | 1.7132 | 1.9887 | 2.2744 | 2.5706 | 12
2020-08-24 20:00 | 2020-08-24 | 20 | 4.6531 | 0.01616% | 6.9375 | 7.1941 | 7.4601 | 7.736 | 8.022 | 1.2005 | 1.4571 | 1.7231 | 1.999 | 2.285 | 13
2020-08-24 21:00 | 2020-08-24 | 21 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 14
2020-08-24 22:00 | 2020-08-24 | 22 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 15 | 15
2020-08-24 23:00 | 2020-08-24 | 23 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-25 | 2020-08-24 | 0 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-25 01:00 | 2020-08-25 | 1 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-08-25 02:00 | 2020-08-25 | 2 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-08-25 03:00 | 2020-08-25 | 3 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-08-25 04:00 | 2020-08-25 | 4 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-08-25 05:00 | 2020-08-25 | 5 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-08-25 06:00 | 2020-08-25 | 6 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-25 07:00 | 2020-08-25 | 7 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-08-25 08:00 | 2020-08-25 | 8 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 1
2020-08-25 09:00 | 2020-08-25 | 9 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 2
2020-08-25 10:00 | 2020-08-25 | 10 | 4.4272 | 0.01537% | 6.6008 | 6.8449 | 7.098 | 7.3604 | 7.6326 | 0.86377 | 1.1079 | 1.361 | 1.6234 | 1.8956 | 3
2020-08-25 11:00 | 2020-08-25 | 11 | 4.7133 | 0.01637% | 7.0273 | 7.2872 | 7.5567 | 7.8361 | 8.1259 | 1.2903 | 1.5502 | 1.8197 | 2.0991 | 2.3889 | 4
2020-08-25 12:00 | 2020-08-25 | 12 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 5
2020-08-25 13:00 | 2020-08-25 | 13 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 6
2020-08-25 14:00 | 2020-08-25 | 14 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 7
2020-08-25 15:00 | 2020-08-25 | 15 | 4.8112 | 0.01671% | 7.1733 | 7.4385 | 7.7136 | 7.9988 | 8.2946 | 1.4363 | 1.7015 | 1.9766 | 2.2618 | 2.5576 | 8
2020-08-25 16:00 | 2020-08-25 | 16 | 4.7284 | 0.01642% | 7.0498 | 7.3105 | 7.5808 | 7.8611 | 8.1518 | 1.3128 | 1.5735 | 1.8438 | 2.1241 | 2.4148 | 9
2020-08-25 17:00 | 2020-08-25 | 17 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 10
2020-08-25 18:00 | 2020-08-25 | 18 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 11
2020-08-25 19:00 | 2020-08-25 | 19 | 4.1938 | 0.01456% | 6.2528 | 6.484 | 6.7238 | 6.9724 | 7.2302 | 0.51577 | 0.74698 | 0.98675 | 1.2354 | 1.4932 | 12 | 12
2020-08-25 20:00 | 2020-08-25 | 20 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-08-25 21:00 | 2020-08-25 | 21 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-08-25 22:00 | 2020-08-25 | 22 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-08-25 23:00 | 2020-08-25 | 23 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-08-26 | 2020-08-25 | 0 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-08-26 01:00 | 2020-08-26 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-08-26 02:00 | 2020-08-26 | 2 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-08-26 03:00 | 2020-08-26 | 3 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-08-26 04:00 | 2020-08-26 | 4 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-08-26 05:00 | 2020-08-26 | 5 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-08-26 06:00 | 2020-08-26 | 6 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-08-26 07:00 | 2020-08-26 | 7 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-08-26 08:00 | 2020-08-26 | 8 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-08-26 09:00 | 2020-08-26 | 9 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-08-26 10:00 | 2020-08-26 | 10 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-26 11:00 | 2020-08-26 | 11 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-08-26 12:00 | 2020-08-26 | 12 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-08-26 13:00 | 2020-08-26 | 13 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-08-26 14:00 | 2020-08-26 | 14 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-26 15:00 | 2020-08-26 | 15 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-08-26 16:00 | 2020-08-26 | 16 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-08-26 17:00 | 2020-08-26 | 17 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-26 18:00 | 2020-08-26 | 18 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-08-26 19:00 | 2020-08-26 | 19 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-08-26 20:00 | 2020-08-26 | 20 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-26 21:00 | 2020-08-26 | 21 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-26 22:00 | 2020-08-26 | 22 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-08-26 23:00 | 2020-08-26 | 23 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-27 | 2020-08-26 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-08-27 01:00 | 2020-08-27 | 1 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-08-27 02:00 | 2020-08-27 | 2 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-08-27 03:00 | 2020-08-27 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-08-27 04:00 | 2020-08-27 | 4 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-08-27 05:00 | 2020-08-27 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-08-27 06:00 | 2020-08-27 | 6 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-08-27 07:00 | 2020-08-27 | 7 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-08-27 08:00 | 2020-08-27 | 8 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-08-27 09:00 | 2020-08-27 | 9 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-08-27 10:00 | 2020-08-27 | 10 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-08-27 11:00 | 2020-08-27 | 11 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-08-27 12:00 | 2020-08-27 | 12 | 3.8324 | 0.01331% | 5.7139 | 5.9252 | 6.1443 | 6.3715 | 6.6071 | 0 | 0.18822 | 0.40733 | 0.63453 | 0.87014
2020-08-27 13:00 | 2020-08-27 | 13 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 1 | 1
2020-08-27 14:00 | 2020-08-27 | 14 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-08-27 15:00 | 2020-08-27 | 15 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1 | 1
2020-08-27 16:00 | 2020-08-27 | 16 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-08-27 17:00 | 2020-08-27 | 17 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-08-27 18:00 | 2020-08-27 | 18 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-08-27 19:00 | 2020-08-27 | 19 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-08-27 20:00 | 2020-08-27 | 20 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-08-27 21:00 | 2020-08-27 | 21 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-08-27 22:00 | 2020-08-27 | 22 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-08-27 23:00 | 2020-08-27 | 23 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-28 | 2020-08-27 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-08-28 01:00 | 2020-08-28 | 1 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-08-28 02:00 | 2020-08-28 | 2 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-08-28 03:00 | 2020-08-28 | 3 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-08-28 04:00 | 2020-08-28 | 4 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-08-28 05:00 | 2020-08-28 | 5 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-08-28 06:00 | 2020-08-28 | 6 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-08-28 07:00 | 2020-08-28 | 7 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-08-28 08:00 | 2020-08-28 | 8 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-08-28 09:00 | 2020-08-28 | 9 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-08-28 10:00 | 2020-08-28 | 10 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-28 11:00 | 2020-08-28 | 11 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-08-28 12:00 | 2020-08-28 | 12 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-08-28 13:00 | 2020-08-28 | 13 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-08-28 14:00 | 2020-08-28 | 14 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-08-28 15:00 | 2020-08-28 | 15 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-28 16:00 | 2020-08-28 | 16 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-28 17:00 | 2020-08-28 | 17 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-08-28 18:00 | 2020-08-28 | 18 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-08-28 19:00 | 2020-08-28 | 19 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-28 20:00 | 2020-08-28 | 20 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-08-28 21:00 | 2020-08-28 | 21 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-08-28 22:00 | 2020-08-28 | 22 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-08-28 23:00 | 2020-08-28 | 23 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-08-29 | 2020-08-28 | 0 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-08-29 01:00 | 2020-08-29 | 1 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-08-29 02:00 | 2020-08-29 | 2 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-08-29 03:00 | 2020-08-29 | 3 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-08-29 04:00 | 2020-08-29 | 4 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-08-29 05:00 | 2020-08-29 | 5 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-08-29 06:00 | 2020-08-29 | 6 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-08-29 07:00 | 2020-08-29 | 7 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-29 08:00 | 2020-08-29 | 8 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-08-29 09:00 | 2020-08-29 | 9 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-08-29 10:00 | 2020-08-29 | 10 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-29 11:00 | 2020-08-29 | 11 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-08-29 12:00 | 2020-08-29 | 12 | 4.0055 | 0.01391% | 5.9721 | 6.193 | 6.422 | 6.6594 | 6.9057 | 0.23512 | 0.45596 | 0.68497 | 0.92244 | 1.1687 | 1
2020-08-29 13:00 | 2020-08-29 | 13 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 2
2020-08-29 14:00 | 2020-08-29 | 14 | 4.2992 | 0.01493% | 6.4099 | 6.647 | 6.8927 | 7.1476 | 7.4119 | 0.67293 | 0.90996 | 1.1557 | 1.4106 | 1.6749 | 3
2020-08-29 15:00 | 2020-08-29 | 15 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 4
2020-08-29 16:00 | 2020-08-29 | 16 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 5
2020-08-29 17:00 | 2020-08-29 | 17 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 6 | 6
2020-08-29 18:00 | 2020-08-29 | 18 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-08-29 19:00 | 2020-08-29 | 19 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-08-29 20:00 | 2020-08-29 | 20 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-29 21:00 | 2020-08-29 | 21 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-08-29 22:00 | 2020-08-29 | 22 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-08-29 23:00 | 2020-08-29 | 23 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-08-30 | 2020-08-29 | 0 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-08-30 01:00 | 2020-08-30 | 1 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-08-30 02:00 | 2020-08-30 | 2 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-08-30 03:00 | 2020-08-30 | 3 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-08-30 04:00 | 2020-08-30 | 4 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-08-30 05:00 | 2020-08-30 | 5 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-08-30 06:00 | 2020-08-30 | 6 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-08-30 07:00 | 2020-08-30 | 7 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-08-30 08:00 | 2020-08-30 | 8 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-08-30 09:00 | 2020-08-30 | 9 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-08-30 10:00 | 2020-08-30 | 10 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-08-30 11:00 | 2020-08-30 | 11 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-08-30 12:00 | 2020-08-30 | 12 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-08-30 13:00 | 2020-08-30 | 13 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-08-30 14:00 | 2020-08-30 | 14 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-08-30 15:00 | 2020-08-30 | 15 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-08-30 16:00 | 2020-08-30 | 16 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-08-30 17:00 | 2020-08-30 | 17 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-08-30 18:00 | 2020-08-30 | 18 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-08-30 19:00 | 2020-08-30 | 19 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-08-30 20:00 | 2020-08-30 | 20 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-08-30 21:00 | 2020-08-30 | 21 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-08-30 22:00 | 2020-08-30 | 22 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-08-30 23:00 | 2020-08-30 | 23 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-08-31 | 2020-08-30 | 0 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-08-31 01:00 | 2020-08-31 | 1 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-08-31 02:00 | 2020-08-31 | 2 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-08-31 03:00 | 2020-08-31 | 3 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-08-31 04:00 | 2020-08-31 | 4 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-08-31 05:00 | 2020-08-31 | 5 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-08-31 06:00 | 2020-08-31 | 6 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-08-31 07:00 | 2020-08-31 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-08-31 08:00 | 2020-08-31 | 8 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-08-31 09:00 | 2020-08-31 | 9 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-08-31 10:00 | 2020-08-31 | 10 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-08-31 11:00 | 2020-08-31 | 11 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-08-31 12:00 | 2020-08-31 | 12 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-08-31 13:00 | 2020-08-31 | 13 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-08-31 14:00 | 2020-08-31 | 14 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-08-31 15:00 | 2020-08-31 | 15 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-08-31 16:00 | 2020-08-31 | 16 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-08-31 17:00 | 2020-08-31 | 17 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-08-31 18:00 | 2020-08-31 | 18 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-08-31 19:00 | 2020-08-31 | 19 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-08-31 20:00 | 2020-08-31 | 20 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-08-31 21:00 | 2020-08-31 | 21 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-08-31 22:00 | 2020-08-31 | 22 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-08-31 23:00 | 2020-08-31 | 23 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-09-01 | 2020-08-31 | 0 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-09-01 01:00 | 2020-09-01 | 1 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-09-01 02:00 | 2020-09-01 | 2 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-09-01 03:00 | 2020-09-01 | 3 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-09-01 04:00 | 2020-09-01 | 4 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-09-01 05:00 | 2020-09-01 | 5 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-09-01 06:00 | 2020-09-01 | 6 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-09-01 07:00 | 2020-09-01 | 7 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-09-01 08:00 | 2020-09-01 | 8 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-09-01 09:00 | 2020-09-01 | 9 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-09-01 10:00 | 2020-09-01 | 10 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-09-01 11:00 | 2020-09-01 | 11 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 1
2020-09-01 12:00 | 2020-09-01 | 12 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 2
2020-09-01 13:00 | 2020-09-01 | 13 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 3
2020-09-01 14:00 | 2020-09-01 | 14 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 4
2020-09-01 15:00 | 2020-09-01 | 15 | 4.1411 | 0.01438% | 6.1742 | 6.4025 | 6.6393 | 6.8848 | 7.1393 | 0.43719 | 0.6655 | 0.90225 | 1.1478 | 1.4023 | 5
2020-09-01 16:00 | 2020-09-01 | 16 | 4.3218 | 0.01501% | 6.4436 | 6.6819 | 6.929 | 7.1852 | 7.4509 | 0.7066 | 0.94488 | 1.192 | 1.4482 | 1.7139 | 6
2020-09-01 17:00 | 2020-09-01 | 17 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 7
2020-09-01 18:00 | 2020-09-01 | 18 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 8
2020-09-01 19:00 | 2020-09-01 | 19 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 9
2020-09-01 20:00 | 2020-09-01 | 20 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 10 | 10
2020-09-01 21:00 | 2020-09-01 | 21 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-09-01 22:00 | 2020-09-01 | 22 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-09-01 23:00 | 2020-09-01 | 23 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-09-02 | 2020-09-01 | 0 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-09-02 01:00 | 2020-09-02 | 1 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-09-02 02:00 | 2020-09-02 | 2 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-09-02 03:00 | 2020-09-02 | 3 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-09-02 04:00 | 2020-09-02 | 4 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-09-02 05:00 | 2020-09-02 | 5 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-09-02 06:00 | 2020-09-02 | 6 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-09-02 07:00 | 2020-09-02 | 7 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-09-02 08:00 | 2020-09-02 | 8 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-09-02 09:00 | 2020-09-02 | 9 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-09-02 10:00 | 2020-09-02 | 10 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-09-02 11:00 | 2020-09-02 | 11 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 2
2020-09-02 12:00 | 2020-09-02 | 12 | 4.2615 | 0.0148% | 6.3538 | 6.5888 | 6.8324 | 7.085 | 7.347 | 0.6168 | 0.85175 | 1.0954 | 1.348 | 1.61 | 3
2020-09-02 13:00 | 2020-09-02 | 13 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 4
2020-09-02 14:00 | 2020-09-02 | 14 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 5
2020-09-02 15:00 | 2020-09-02 | 15 | 4.6079 | 0.016% | 6.8702 | 7.1242 | 7.3877 | 7.6609 | 7.9441 | 1.1332 | 1.3872 | 1.6507 | 1.9239 | 2.2071 | 6
2020-09-02 16:00 | 2020-09-02 | 16 | 4.8639 | 0.01689% | 7.2519 | 7.52 | 7.7981 | 8.0865 | 8.3855 | 1.5149 | 1.783 | 2.0611 | 2.3495 | 2.6485 | 7
2020-09-02 17:00 | 2020-09-02 | 17 | 4.7886 | 0.01663% | 7.1396 | 7.4036 | 7.6774 | 7.9613 | 8.2557 | 1.4026 | 1.6666 | 1.9404 | 2.2243 | 2.5187 | 8
2020-09-02 18:00 | 2020-09-02 | 18 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 9
2020-09-02 19:00 | 2020-09-02 | 19 | 4.1862 | 0.01454% | 6.2415 | 6.4723 | 6.7117 | 6.9599 | 7.2172 | 0.50454 | 0.73534 | 0.97468 | 1.2229 | 1.4802 | 10
2020-09-02 20:00 | 2020-09-02 | 20 | 4.0583 | 0.01409% | 6.0507 | 6.2744 | 6.5065 | 6.7471 | 6.9966 | 0.3137 | 0.53745 | 0.76947 | 1.0101 | 1.2596 | 11 | 11
2020-09-02 21:00 | 2020-09-02 | 21 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-09-02 22:00 | 2020-09-02 | 22 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-09-02 23:00 | 2020-09-02 | 23 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-03 | 2020-09-02 | 0 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-09-03 01:00 | 2020-09-03 | 1 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-09-03 02:00 | 2020-09-03 | 2 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-09-03 03:00 | 2020-09-03 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-09-03 04:00 | 2020-09-03 | 4 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-09-03 05:00 | 2020-09-03 | 5 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-09-03 06:00 | 2020-09-03 | 6 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-09-03 07:00 | 2020-09-03 | 7 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-09-03 08:00 | 2020-09-03 | 8 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-09-03 09:00 | 2020-09-03 | 9 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-09-03 10:00 | 2020-09-03 | 10 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-09-03 11:00 | 2020-09-03 | 11 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1
2020-09-03 12:00 | 2020-09-03 | 12 | 4.1034 | 0.01425% | 6.1181 | 6.3443 | 6.5789 | 6.8222 | 7.0744 | 0.38106 | 0.60729 | 0.84189 | 1.0852 | 1.3374 | 2
2020-09-03 13:00 | 2020-09-03 | 13 | 4.2239 | 0.01467% | 6.2977 | 6.5305 | 6.772 | 7.0225 | 7.2821 | 0.56067 | 0.79355 | 1.035 | 1.2855 | 1.5451 | 3
2020-09-03 14:00 | 2020-09-03 | 14 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 4
2020-09-03 15:00 | 2020-09-03 | 15 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 5
2020-09-03 16:00 | 2020-09-03 | 16 | 4.3293 | 0.01503% | 6.4548 | 6.6935 | 6.941 | 7.1977 | 7.4639 | 0.71783 | 0.95652 | 1.204 | 1.4607 | 1.7269 | 6
2020-09-03 17:00 | 2020-09-03 | 17 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 7
2020-09-03 18:00 | 2020-09-03 | 18 | 4.3368 | 0.01506% | 6.4661 | 6.7052 | 6.9531 | 7.2102 | 7.4768 | 0.72906 | 0.96816 | 1.2161 | 1.4732 | 1.7398 | 8
2020-09-03 19:00 | 2020-09-03 | 19 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 9
2020-09-03 20:00 | 2020-09-03 | 20 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 10 | 10
2020-09-03 21:00 | 2020-09-03 | 21 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-09-03 22:00 | 2020-09-03 | 22 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-09-03 23:00 | 2020-09-03 | 23 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-09-04 | 2020-09-03 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-09-04 01:00 | 2020-09-04 | 1 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-09-04 02:00 | 2020-09-04 | 2 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-09-04 03:00 | 2020-09-04 | 3 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-04 04:00 | 2020-09-04 | 4 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-04 05:00 | 2020-09-04 | 5 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-09-04 06:00 | 2020-09-04 | 6 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-09-04 07:00 | 2020-09-04 | 7 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-09-04 08:00 | 2020-09-04 | 8 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-04 09:00 | 2020-09-04 | 9 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-09-04 10:00 | 2020-09-04 | 10 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-04 11:00 | 2020-09-04 | 11 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-09-04 12:00 | 2020-09-04 | 12 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-09-04 13:00 | 2020-09-04 | 13 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-09-04 14:00 | 2020-09-04 | 14 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-09-04 15:00 | 2020-09-04 | 15 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-09-04 16:00 | 2020-09-04 | 16 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-09-04 17:00 | 2020-09-04 | 17 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-09-04 18:00 | 2020-09-04 | 18 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-04 19:00 | 2020-09-04 | 19 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-09-04 20:00 | 2020-09-04 | 20 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-04 21:00 | 2020-09-04 | 21 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-04 22:00 | 2020-09-04 | 22 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-09-04 23:00 | 2020-09-04 | 23 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-09-05 | 2020-09-04 | 0 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-09-05 01:00 | 2020-09-05 | 1 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-05 02:00 | 2020-09-05 | 2 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-09-05 03:00 | 2020-09-05 | 3 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-05 04:00 | 2020-09-05 | 4 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-09-05 05:00 | 2020-09-05 | 5 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-05 06:00 | 2020-09-05 | 6 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-09-05 07:00 | 2020-09-05 | 7 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-09-05 08:00 | 2020-09-05 | 8 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-09-05 09:00 | 2020-09-05 | 9 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-09-05 10:00 | 2020-09-05 | 10 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-09-05 11:00 | 2020-09-05 | 11 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-09-05 12:00 | 2020-09-05 | 12 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-05 13:00 | 2020-09-05 | 13 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-09-05 14:00 | 2020-09-05 | 14 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-09-05 15:00 | 2020-09-05 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-09-05 16:00 | 2020-09-05 | 16 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-09-05 17:00 | 2020-09-05 | 17 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-09-05 18:00 | 2020-09-05 | 18 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-09-05 19:00 | 2020-09-05 | 19 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-09-05 20:00 | 2020-09-05 | 20 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-09-05 21:00 | 2020-09-05 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-05 22:00 | 2020-09-05 | 22 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-09-05 23:00 | 2020-09-05 | 23 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-09-06 | 2020-09-05 | 0 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-06 01:00 | 2020-09-06 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-06 02:00 | 2020-09-06 | 2 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-06 03:00 | 2020-09-06 | 3 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-09-06 04:00 | 2020-09-06 | 4 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-09-06 05:00 | 2020-09-06 | 5 | 1.9576 | 0.006797% | 2.9187 | 3.0266 | 3.1386 | 3.2546 | 3.375 | 0 | 0 | 0 | 0 | 0
2020-09-06 06:00 | 2020-09-06 | 6 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-09-06 07:00 | 2020-09-06 | 7 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-09-06 08:00 | 2020-09-06 | 8 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-09-06 09:00 | 2020-09-06 | 9 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-09-06 10:00 | 2020-09-06 | 10 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-09-06 11:00 | 2020-09-06 | 11 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-09-06 12:00 | 2020-09-06 | 12 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-09-06 13:00 | 2020-09-06 | 13 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-09-06 14:00 | 2020-09-06 | 14 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-09-06 15:00 | 2020-09-06 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-09-06 16:00 | 2020-09-06 | 16 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-09-06 17:00 | 2020-09-06 | 17 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-09-06 18:00 | 2020-09-06 | 18 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-06 19:00 | 2020-09-06 | 19 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-06 20:00 | 2020-09-06 | 20 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-09-06 21:00 | 2020-09-06 | 21 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-09-06 22:00 | 2020-09-06 | 22 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-09-06 23:00 | 2020-09-06 | 23 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-07 | 2020-09-06 | 0 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-07 01:00 | 2020-09-07 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-07 02:00 | 2020-09-07 | 2 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-09-07 03:00 | 2020-09-07 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-09-07 04:00 | 2020-09-07 | 4 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-09-07 05:00 | 2020-09-07 | 5 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-07 06:00 | 2020-09-07 | 6 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-07 07:00 | 2020-09-07 | 7 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-09-07 08:00 | 2020-09-07 | 8 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-09-07 09:00 | 2020-09-07 | 9 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-09-07 10:00 | 2020-09-07 | 10 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-09-07 11:00 | 2020-09-07 | 11 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-09-07 12:00 | 2020-09-07 | 12 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-09-07 13:00 | 2020-09-07 | 13 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-09-07 14:00 | 2020-09-07 | 14 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-09-07 15:00 | 2020-09-07 | 15 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-09-07 16:00 | 2020-09-07 | 16 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-09-07 17:00 | 2020-09-07 | 17 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-09-07 18:00 | 2020-09-07 | 18 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-09-07 19:00 | 2020-09-07 | 19 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-09-07 20:00 | 2020-09-07 | 20 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-09-07 21:00 | 2020-09-07 | 21 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-09-07 22:00 | 2020-09-07 | 22 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-09-07 23:00 | 2020-09-07 | 23 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-09-08 | 2020-09-07 | 0 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-08 01:00 | 2020-09-08 | 1 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-08 02:00 | 2020-09-08 | 2 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-08 03:00 | 2020-09-08 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-09-08 04:00 | 2020-09-08 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-08 05:00 | 2020-09-08 | 5 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-09-08 06:00 | 2020-09-08 | 6 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-09-08 07:00 | 2020-09-08 | 7 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-09-08 08:00 | 2020-09-08 | 8 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-09-08 09:00 | 2020-09-08 | 9 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-08 10:00 | 2020-09-08 | 10 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-09-08 11:00 | 2020-09-08 | 11 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-09-08 12:00 | 2020-09-08 | 12 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-08 13:00 | 2020-09-08 | 13 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-09-08 14:00 | 2020-09-08 | 14 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-09-08 15:00 | 2020-09-08 | 15 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-08 16:00 | 2020-09-08 | 16 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-09-08 17:00 | 2020-09-08 | 17 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-08 18:00 | 2020-09-08 | 18 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-09-08 19:00 | 2020-09-08 | 19 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-09-08 20:00 | 2020-09-08 | 20 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-09-08 21:00 | 2020-09-08 | 21 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-09-08 22:00 | 2020-09-08 | 22 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-08 23:00 | 2020-09-08 | 23 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-09-09 | 2020-09-08 | 0 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-09 01:00 | 2020-09-09 | 1 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-09 02:00 | 2020-09-09 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-09 03:00 | 2020-09-09 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-09 04:00 | 2020-09-09 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-09 05:00 | 2020-09-09 | 5 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-09-09 06:00 | 2020-09-09 | 6 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-09-09 07:00 | 2020-09-09 | 7 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-09-09 08:00 | 2020-09-09 | 8 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-09-09 09:00 | 2020-09-09 | 9 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-09-09 10:00 | 2020-09-09 | 10 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-09-09 11:00 | 2020-09-09 | 11 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-09 12:00 | 2020-09-09 | 12 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-09-09 13:00 | 2020-09-09 | 13 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-09 14:00 | 2020-09-09 | 14 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-09 15:00 | 2020-09-09 | 15 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-09-09 16:00 | 2020-09-09 | 16 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-09-09 17:00 | 2020-09-09 | 17 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-09-09 18:00 | 2020-09-09 | 18 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-09 19:00 | 2020-09-09 | 19 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-09-09 20:00 | 2020-09-09 | 20 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-09-09 21:00 | 2020-09-09 | 21 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-09-09 22:00 | 2020-09-09 | 22 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-09-09 23:00 | 2020-09-09 | 23 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-09-10 | 2020-09-09 | 0 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-09-10 01:00 | 2020-09-10 | 1 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-10 02:00 | 2020-09-10 | 2 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-09-10 03:00 | 2020-09-10 | 3 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-09-10 04:00 | 2020-09-10 | 4 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-09-10 05:00 | 2020-09-10 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-09-10 06:00 | 2020-09-10 | 6 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-09-10 07:00 | 2020-09-10 | 7 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-09-10 08:00 | 2020-09-10 | 8 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-09-10 09:00 | 2020-09-10 | 9 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-09-10 10:00 | 2020-09-10 | 10 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-09-10 11:00 | 2020-09-10 | 11 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-09-10 12:00 | 2020-09-10 | 12 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-09-10 13:00 | 2020-09-10 | 13 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-09-10 14:00 | 2020-09-10 | 14 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-09-10 15:00 | 2020-09-10 | 15 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-09-10 16:00 | 2020-09-10 | 16 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-09-10 17:00 | 2020-09-10 | 17 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-09-10 18:00 | 2020-09-10 | 18 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-10 19:00 | 2020-09-10 | 19 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-09-10 20:00 | 2020-09-10 | 20 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-10 21:00 | 2020-09-10 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-10 22:00 | 2020-09-10 | 22 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-09-10 23:00 | 2020-09-10 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-09-11 | 2020-09-10 | 0 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-09-11 01:00 | 2020-09-11 | 1 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-09-11 02:00 | 2020-09-11 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-11 03:00 | 2020-09-11 | 3 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-09-11 04:00 | 2020-09-11 | 4 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-09-11 05:00 | 2020-09-11 | 5 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-11 06:00 | 2020-09-11 | 6 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-09-11 07:00 | 2020-09-11 | 7 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-09-11 08:00 | 2020-09-11 | 8 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-09-11 09:00 | 2020-09-11 | 9 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-09-11 10:00 | 2020-09-11 | 10 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-11 11:00 | 2020-09-11 | 11 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-09-11 12:00 | 2020-09-11 | 12 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-09-11 13:00 | 2020-09-11 | 13 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-09-11 14:00 | 2020-09-11 | 14 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-11 15:00 | 2020-09-11 | 15 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-11 16:00 | 2020-09-11 | 16 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-11 17:00 | 2020-09-11 | 17 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-11 18:00 | 2020-09-11 | 18 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-11 19:00 | 2020-09-11 | 19 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-11 20:00 | 2020-09-11 | 20 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-09-11 21:00 | 2020-09-11 | 21 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-09-11 22:00 | 2020-09-11 | 22 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-09-11 23:00 | 2020-09-11 | 23 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-09-12 | 2020-09-11 | 0 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-09-12 01:00 | 2020-09-12 | 1 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-12 02:00 | 2020-09-12 | 2 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-09-12 03:00 | 2020-09-12 | 3 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-09-12 04:00 | 2020-09-12 | 4 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-09-12 05:00 | 2020-09-12 | 5 | 1.9877 | 0.006902% | 2.9636 | 3.0732 | 3.1868 | 3.3047 | 3.4269 | 0 | 0 | 0 | 0 | 0
2020-09-12 06:00 | 2020-09-12 | 6 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-12 07:00 | 2020-09-12 | 7 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-09-12 08:00 | 2020-09-12 | 8 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-09-12 09:00 | 2020-09-12 | 9 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-09-12 10:00 | 2020-09-12 | 10 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-09-12 11:00 | 2020-09-12 | 11 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-09-12 12:00 | 2020-09-12 | 12 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-09-12 13:00 | 2020-09-12 | 13 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-09-12 14:00 | 2020-09-12 | 14 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-12 15:00 | 2020-09-12 | 15 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-09-12 16:00 | 2020-09-12 | 16 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-12 17:00 | 2020-09-12 | 17 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-12 18:00 | 2020-09-12 | 18 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-09-12 19:00 | 2020-09-12 | 19 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-09-12 20:00 | 2020-09-12 | 20 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-09-12 21:00 | 2020-09-12 | 21 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-09-12 22:00 | 2020-09-12 | 22 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-09-12 23:00 | 2020-09-12 | 23 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-09-13 | 2020-09-12 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-09-13 01:00 | 2020-09-13 | 1 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-09-13 02:00 | 2020-09-13 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-09-13 03:00 | 2020-09-13 | 3 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-13 04:00 | 2020-09-13 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-13 05:00 | 2020-09-13 | 5 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-13 06:00 | 2020-09-13 | 6 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-09-13 07:00 | 2020-09-13 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-09-13 08:00 | 2020-09-13 | 8 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-09-13 09:00 | 2020-09-13 | 9 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-13 10:00 | 2020-09-13 | 10 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-09-13 11:00 | 2020-09-13 | 11 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-09-13 12:00 | 2020-09-13 | 12 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-09-13 13:00 | 2020-09-13 | 13 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-09-13 14:00 | 2020-09-13 | 14 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-09-13 15:00 | 2020-09-13 | 15 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-09-13 16:00 | 2020-09-13 | 16 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-09-13 17:00 | 2020-09-13 | 17 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-09-13 18:00 | 2020-09-13 | 18 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-09-13 19:00 | 2020-09-13 | 19 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-09-13 20:00 | 2020-09-13 | 20 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-09-13 21:00 | 2020-09-13 | 21 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-09-13 22:00 | 2020-09-13 | 22 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-09-13 23:00 | 2020-09-13 | 23 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-14 | 2020-09-13 | 0 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-09-14 01:00 | 2020-09-14 | 1 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-09-14 02:00 | 2020-09-14 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-14 03:00 | 2020-09-14 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-14 04:00 | 2020-09-14 | 4 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-09-14 05:00 | 2020-09-14 | 5 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-09-14 06:00 | 2020-09-14 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-09-14 07:00 | 2020-09-14 | 7 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-09-14 08:00 | 2020-09-14 | 8 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-09-14 09:00 | 2020-09-14 | 9 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-14 10:00 | 2020-09-14 | 10 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-14 11:00 | 2020-09-14 | 11 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-09-14 12:00 | 2020-09-14 | 12 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-09-14 13:00 | 2020-09-14 | 13 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-09-14 14:00 | 2020-09-14 | 14 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-09-14 15:00 | 2020-09-14 | 15 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-09-14 16:00 | 2020-09-14 | 16 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-14 17:00 | 2020-09-14 | 17 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-09-14 18:00 | 2020-09-14 | 18 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-14 19:00 | 2020-09-14 | 19 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-09-14 20:00 | 2020-09-14 | 20 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-09-14 21:00 | 2020-09-14 | 21 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-09-14 22:00 | 2020-09-14 | 22 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-09-14 23:00 | 2020-09-14 | 23 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-09-15 | 2020-09-14 | 0 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-15 01:00 | 2020-09-15 | 1 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-15 02:00 | 2020-09-15 | 2 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-09-15 03:00 | 2020-09-15 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-09-15 04:00 | 2020-09-15 | 4 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-09-15 05:00 | 2020-09-15 | 5 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-09-15 06:00 | 2020-09-15 | 6 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-09-15 07:00 | 2020-09-15 | 7 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-15 08:00 | 2020-09-15 | 8 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-09-15 09:00 | 2020-09-15 | 9 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-09-15 10:00 | 2020-09-15 | 10 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-09-15 11:00 | 2020-09-15 | 11 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-09-15 12:00 | 2020-09-15 | 12 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-09-15 13:00 | 2020-09-15 | 13 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-09-15 14:00 | 2020-09-15 | 14 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-15 15:00 | 2020-09-15 | 15 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-09-15 16:00 | 2020-09-15 | 16 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-09-15 17:00 | 2020-09-15 | 17 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-15 18:00 | 2020-09-15 | 18 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-09-15 19:00 | 2020-09-15 | 19 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-09-15 20:00 | 2020-09-15 | 20 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-09-15 21:00 | 2020-09-15 | 21 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-09-15 22:00 | 2020-09-15 | 22 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-09-15 23:00 | 2020-09-15 | 23 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-16 | 2020-09-15 | 0 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-16 01:00 | 2020-09-16 | 1 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-09-16 02:00 | 2020-09-16 | 2 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-09-16 03:00 | 2020-09-16 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-16 04:00 | 2020-09-16 | 4 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-16 05:00 | 2020-09-16 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-09-16 06:00 | 2020-09-16 | 6 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-09-16 07:00 | 2020-09-16 | 7 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-09-16 08:00 | 2020-09-16 | 8 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-16 09:00 | 2020-09-16 | 9 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-09-16 10:00 | 2020-09-16 | 10 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-09-16 11:00 | 2020-09-16 | 11 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-09-16 12:00 | 2020-09-16 | 12 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-09-16 13:00 | 2020-09-16 | 13 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-09-16 14:00 | 2020-09-16 | 14 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-09-16 15:00 | 2020-09-16 | 15 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-09-16 16:00 | 2020-09-16 | 16 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-09-16 17:00 | 2020-09-16 | 17 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-09-16 18:00 | 2020-09-16 | 18 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-09-16 19:00 | 2020-09-16 | 19 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-09-16 20:00 | 2020-09-16 | 20 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-09-16 21:00 | 2020-09-16 | 21 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-09-16 22:00 | 2020-09-16 | 22 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-09-16 23:00 | 2020-09-16 | 23 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-09-17 | 2020-09-16 | 0 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-17 01:00 | 2020-09-17 | 1 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-09-17 02:00 | 2020-09-17 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-09-17 03:00 | 2020-09-17 | 3 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-17 04:00 | 2020-09-17 | 4 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-09-17 05:00 | 2020-09-17 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-09-17 06:00 | 2020-09-17 | 6 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-09-17 07:00 | 2020-09-17 | 7 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-09-17 08:00 | 2020-09-17 | 8 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-17 09:00 | 2020-09-17 | 9 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-09-17 10:00 | 2020-09-17 | 10 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-09-17 11:00 | 2020-09-17 | 11 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-09-17 12:00 | 2020-09-17 | 12 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-09-17 13:00 | 2020-09-17 | 13 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-09-17 14:00 | 2020-09-17 | 14 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-09-17 15:00 | 2020-09-17 | 15 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-09-17 16:00 | 2020-09-17 | 16 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-17 17:00 | 2020-09-17 | 17 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-09-17 18:00 | 2020-09-17 | 18 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-09-17 19:00 | 2020-09-17 | 19 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-17 20:00 | 2020-09-17 | 20 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-09-17 21:00 | 2020-09-17 | 21 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-09-17 22:00 | 2020-09-17 | 22 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-09-17 23:00 | 2020-09-17 | 23 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-09-18 | 2020-09-17 | 0 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-09-18 01:00 | 2020-09-18 | 1 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-09-18 02:00 | 2020-09-18 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-18 03:00 | 2020-09-18 | 3 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-18 04:00 | 2020-09-18 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-18 05:00 | 2020-09-18 | 5 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-09-18 06:00 | 2020-09-18 | 6 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-09-18 07:00 | 2020-09-18 | 7 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-09-18 08:00 | 2020-09-18 | 8 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-09-18 09:00 | 2020-09-18 | 9 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-09-18 10:00 | 2020-09-18 | 10 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-09-18 11:00 | 2020-09-18 | 11 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-09-18 12:00 | 2020-09-18 | 12 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-09-18 13:00 | 2020-09-18 | 13 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-18 14:00 | 2020-09-18 | 14 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-09-18 15:00 | 2020-09-18 | 15 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-18 16:00 | 2020-09-18 | 16 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-09-18 17:00 | 2020-09-18 | 17 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-09-18 18:00 | 2020-09-18 | 18 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-09-18 19:00 | 2020-09-18 | 19 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-18 20:00 | 2020-09-18 | 20 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-18 21:00 | 2020-09-18 | 21 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-09-18 22:00 | 2020-09-18 | 22 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-09-18 23:00 | 2020-09-18 | 23 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-19 | 2020-09-18 | 0 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-09-19 01:00 | 2020-09-19 | 1 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-09-19 02:00 | 2020-09-19 | 2 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-09-19 03:00 | 2020-09-19 | 3 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-09-19 04:00 | 2020-09-19 | 4 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-09-19 05:00 | 2020-09-19 | 5 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-19 06:00 | 2020-09-19 | 6 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-09-19 07:00 | 2020-09-19 | 7 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-19 08:00 | 2020-09-19 | 8 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-09-19 09:00 | 2020-09-19 | 9 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-09-19 10:00 | 2020-09-19 | 10 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-09-19 11:00 | 2020-09-19 | 11 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-09-19 12:00 | 2020-09-19 | 12 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-09-19 13:00 | 2020-09-19 | 13 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-09-19 14:00 | 2020-09-19 | 14 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-09-19 15:00 | 2020-09-19 | 15 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-09-19 16:00 | 2020-09-19 | 16 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-09-19 17:00 | 2020-09-19 | 17 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-09-19 18:00 | 2020-09-19 | 18 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-09-19 19:00 | 2020-09-19 | 19 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-09-19 20:00 | 2020-09-19 | 20 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-19 21:00 | 2020-09-19 | 21 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-09-19 22:00 | 2020-09-19 | 22 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-09-19 23:00 | 2020-09-19 | 23 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-09-20 | 2020-09-19 | 0 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-20 01:00 | 2020-09-20 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-20 02:00 | 2020-09-20 | 2 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-09-20 03:00 | 2020-09-20 | 3 | 2.0103 | 0.006981% | 2.9973 | 3.1081 | 3.2231 | 3.3422 | 3.4658 | 0 | 0 | 0 | 0 | 0
2020-09-20 04:00 | 2020-09-20 | 4 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-09-20 05:00 | 2020-09-20 | 5 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-09-20 06:00 | 2020-09-20 | 6 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-20 07:00 | 2020-09-20 | 7 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-09-20 08:00 | 2020-09-20 | 8 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-20 09:00 | 2020-09-20 | 9 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-09-20 10:00 | 2020-09-20 | 10 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-09-20 11:00 | 2020-09-20 | 11 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-09-20 12:00 | 2020-09-20 | 12 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-09-20 13:00 | 2020-09-20 | 13 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-09-20 14:00 | 2020-09-20 | 14 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-09-20 15:00 | 2020-09-20 | 15 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-09-20 16:00 | 2020-09-20 | 16 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-09-20 17:00 | 2020-09-20 | 17 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-09-20 18:00 | 2020-09-20 | 18 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-09-20 19:00 | 2020-09-20 | 19 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-09-20 20:00 | 2020-09-20 | 20 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-09-20 21:00 | 2020-09-20 | 21 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-09-20 22:00 | 2020-09-20 | 22 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-09-20 23:00 | 2020-09-20 | 23 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-21 | 2020-09-20 | 0 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-21 01:00 | 2020-09-21 | 1 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-09-21 02:00 | 2020-09-21 | 2 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-21 03:00 | 2020-09-21 | 3 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-09-21 04:00 | 2020-09-21 | 4 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-21 05:00 | 2020-09-21 | 5 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-09-21 06:00 | 2020-09-21 | 6 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-09-21 07:00 | 2020-09-21 | 7 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-09-21 08:00 | 2020-09-21 | 8 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-09-21 09:00 | 2020-09-21 | 9 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-21 10:00 | 2020-09-21 | 10 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-09-21 11:00 | 2020-09-21 | 11 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-09-21 12:00 | 2020-09-21 | 12 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-09-21 13:00 | 2020-09-21 | 13 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-09-21 14:00 | 2020-09-21 | 14 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-09-21 15:00 | 2020-09-21 | 15 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-09-21 16:00 | 2020-09-21 | 16 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-09-21 17:00 | 2020-09-21 | 17 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-09-21 18:00 | 2020-09-21 | 18 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-09-21 19:00 | 2020-09-21 | 19 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-09-21 20:00 | 2020-09-21 | 20 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-09-21 21:00 | 2020-09-21 | 21 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-09-21 22:00 | 2020-09-21 | 22 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-09-21 23:00 | 2020-09-21 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-09-22 | 2020-09-21 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-09-22 01:00 | 2020-09-22 | 1 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-22 02:00 | 2020-09-22 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-22 03:00 | 2020-09-22 | 3 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-09-22 04:00 | 2020-09-22 | 4 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-22 05:00 | 2020-09-22 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-09-22 06:00 | 2020-09-22 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-09-22 07:00 | 2020-09-22 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-09-22 08:00 | 2020-09-22 | 8 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-22 09:00 | 2020-09-22 | 9 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-09-22 10:00 | 2020-09-22 | 10 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-09-22 11:00 | 2020-09-22 | 11 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-22 12:00 | 2020-09-22 | 12 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-09-22 13:00 | 2020-09-22 | 13 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-09-22 14:00 | 2020-09-22 | 14 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-09-22 15:00 | 2020-09-22 | 15 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-09-22 16:00 | 2020-09-22 | 16 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-22 17:00 | 2020-09-22 | 17 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-22 18:00 | 2020-09-22 | 18 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-22 19:00 | 2020-09-22 | 19 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-09-22 20:00 | 2020-09-22 | 20 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-22 21:00 | 2020-09-22 | 21 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-09-22 22:00 | 2020-09-22 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-09-22 23:00 | 2020-09-22 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-09-23 | 2020-09-22 | 0 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-09-23 01:00 | 2020-09-23 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-09-23 02:00 | 2020-09-23 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-09-23 03:00 | 2020-09-23 | 3 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-09-23 04:00 | 2020-09-23 | 4 | 2.063 | 0.007164% | 3.0759 | 3.1896 | 3.3076 | 3.4299 | 3.5567 | 0 | 0 | 0 | 0 | 0
2020-09-23 05:00 | 2020-09-23 | 5 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-09-23 06:00 | 2020-09-23 | 6 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-09-23 07:00 | 2020-09-23 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-09-23 08:00 | 2020-09-23 | 8 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-23 09:00 | 2020-09-23 | 9 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-09-23 10:00 | 2020-09-23 | 10 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-09-23 11:00 | 2020-09-23 | 11 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-09-23 12:00 | 2020-09-23 | 12 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-09-23 13:00 | 2020-09-23 | 13 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-09-23 14:00 | 2020-09-23 | 14 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-09-23 15:00 | 2020-09-23 | 15 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-09-23 16:00 | 2020-09-23 | 16 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-09-23 17:00 | 2020-09-23 | 17 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-09-23 18:00 | 2020-09-23 | 18 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-23 19:00 | 2020-09-23 | 19 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-09-23 20:00 | 2020-09-23 | 20 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-09-23 21:00 | 2020-09-23 | 21 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-09-23 22:00 | 2020-09-23 | 22 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-09-23 23:00 | 2020-09-23 | 23 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-09-24 | 2020-09-23 | 0 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-09-24 01:00 | 2020-09-24 | 1 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-09-24 02:00 | 2020-09-24 | 2 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-24 03:00 | 2020-09-24 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-24 04:00 | 2020-09-24 | 4 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-24 05:00 | 2020-09-24 | 5 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-09-24 06:00 | 2020-09-24 | 6 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-24 07:00 | 2020-09-24 | 7 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-09-24 08:00 | 2020-09-24 | 8 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-09-24 09:00 | 2020-09-24 | 9 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-09-24 10:00 | 2020-09-24 | 10 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-24 11:00 | 2020-09-24 | 11 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-09-24 12:00 | 2020-09-24 | 12 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-09-24 13:00 | 2020-09-24 | 13 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-09-24 14:00 | 2020-09-24 | 14 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-09-24 15:00 | 2020-09-24 | 15 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-09-24 16:00 | 2020-09-24 | 16 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-09-24 17:00 | 2020-09-24 | 17 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-09-24 18:00 | 2020-09-24 | 18 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-09-24 19:00 | 2020-09-24 | 19 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-24 20:00 | 2020-09-24 | 20 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-09-24 21:00 | 2020-09-24 | 21 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-24 22:00 | 2020-09-24 | 22 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-09-24 23:00 | 2020-09-24 | 23 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-09-25 | 2020-09-24 | 0 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-09-25 01:00 | 2020-09-25 | 1 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-09-25 02:00 | 2020-09-25 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-09-25 03:00 | 2020-09-25 | 3 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-25 04:00 | 2020-09-25 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-09-25 05:00 | 2020-09-25 | 5 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-09-25 06:00 | 2020-09-25 | 6 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-09-25 07:00 | 2020-09-25 | 7 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-09-25 08:00 | 2020-09-25 | 8 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-09-25 09:00 | 2020-09-25 | 9 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-09-25 10:00 | 2020-09-25 | 10 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-09-25 11:00 | 2020-09-25 | 11 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-09-25 12:00 | 2020-09-25 | 12 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-09-25 13:00 | 2020-09-25 | 13 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-09-25 14:00 | 2020-09-25 | 14 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-09-25 15:00 | 2020-09-25 | 15 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-09-25 16:00 | 2020-09-25 | 16 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-09-25 17:00 | 2020-09-25 | 17 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-09-25 18:00 | 2020-09-25 | 18 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-09-25 19:00 | 2020-09-25 | 19 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-25 20:00 | 2020-09-25 | 20 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-09-25 21:00 | 2020-09-25 | 21 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-25 22:00 | 2020-09-25 | 22 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-09-25 23:00 | 2020-09-25 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-09-26 | 2020-09-25 | 0 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-09-26 01:00 | 2020-09-26 | 1 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-09-26 02:00 | 2020-09-26 | 2 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-09-26 03:00 | 2020-09-26 | 3 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-09-26 04:00 | 2020-09-26 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-26 05:00 | 2020-09-26 | 5 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-26 06:00 | 2020-09-26 | 6 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-09-26 07:00 | 2020-09-26 | 7 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-09-26 08:00 | 2020-09-26 | 8 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-09-26 09:00 | 2020-09-26 | 9 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-09-26 10:00 | 2020-09-26 | 10 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-09-26 11:00 | 2020-09-26 | 11 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-26 12:00 | 2020-09-26 | 12 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-09-26 13:00 | 2020-09-26 | 13 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-09-26 14:00 | 2020-09-26 | 14 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-09-26 15:00 | 2020-09-26 | 15 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-26 16:00 | 2020-09-26 | 16 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-09-26 17:00 | 2020-09-26 | 17 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-09-26 18:00 | 2020-09-26 | 18 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-09-26 19:00 | 2020-09-26 | 19 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-09-26 20:00 | 2020-09-26 | 20 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-09-26 21:00 | 2020-09-26 | 21 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-09-26 22:00 | 2020-09-26 | 22 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-09-26 23:00 | 2020-09-26 | 23 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-09-27 | 2020-09-26 | 0 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-09-27 01:00 | 2020-09-27 | 1 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-09-27 02:00 | 2020-09-27 | 2 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-09-27 03:00 | 2020-09-27 | 3 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-27 04:00 | 2020-09-27 | 4 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-09-27 05:00 | 2020-09-27 | 5 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-09-27 06:00 | 2020-09-27 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-09-27 07:00 | 2020-09-27 | 7 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-09-27 08:00 | 2020-09-27 | 8 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-09-27 09:00 | 2020-09-27 | 9 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-09-27 10:00 | 2020-09-27 | 10 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-27 11:00 | 2020-09-27 | 11 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-09-27 12:00 | 2020-09-27 | 12 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-09-27 13:00 | 2020-09-27 | 13 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-09-27 14:00 | 2020-09-27 | 14 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-09-27 15:00 | 2020-09-27 | 15 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-09-27 16:00 | 2020-09-27 | 16 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 1
2020-09-27 17:00 | 2020-09-27 | 17 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 2
2020-09-27 18:00 | 2020-09-27 | 18 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 3 | 3
2020-09-27 19:00 | 2020-09-27 | 19 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-09-27 20:00 | 2020-09-27 | 20 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-09-27 21:00 | 2020-09-27 | 21 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-09-27 22:00 | 2020-09-27 | 22 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-09-27 23:00 | 2020-09-27 | 23 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-09-28 | 2020-09-27 | 0 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-09-28 01:00 | 2020-09-28 | 1 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-09-28 02:00 | 2020-09-28 | 2 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-09-28 03:00 | 2020-09-28 | 3 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-09-28 04:00 | 2020-09-28 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-09-28 05:00 | 2020-09-28 | 5 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-09-28 06:00 | 2020-09-28 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-09-28 07:00 | 2020-09-28 | 7 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-28 08:00 | 2020-09-28 | 8 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-09-28 09:00 | 2020-09-28 | 9 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-09-28 10:00 | 2020-09-28 | 10 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-09-28 11:00 | 2020-09-28 | 11 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-09-28 12:00 | 2020-09-28 | 12 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-09-28 13:00 | 2020-09-28 | 13 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 1
2020-09-28 14:00 | 2020-09-28 | 14 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 2
2020-09-28 15:00 | 2020-09-28 | 15 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 3
2020-09-28 16:00 | 2020-09-28 | 16 | 4.2239 | 0.01467% | 6.2977 | 6.5305 | 6.772 | 7.0225 | 7.2821 | 0.56067 | 0.79355 | 1.035 | 1.2855 | 1.5451 | 4
2020-09-28 17:00 | 2020-09-28 | 17 | 4.0884 | 0.0142% | 6.0956 | 6.321 | 6.5548 | 6.7971 | 7.0485 | 0.35861 | 0.58401 | 0.81775 | 1.0601 | 1.3115 | 5
2020-09-28 18:00 | 2020-09-28 | 18 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 6
2020-09-28 19:00 | 2020-09-28 | 19 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 7
2020-09-28 20:00 | 2020-09-28 | 20 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 8 | 8
2020-09-28 21:00 | 2020-09-28 | 21 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-09-28 22:00 | 2020-09-28 | 22 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-09-28 23:00 | 2020-09-28 | 23 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-09-29 | 2020-09-28 | 0 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-09-29 01:00 | 2020-09-29 | 1 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-09-29 02:00 | 2020-09-29 | 2 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-09-29 03:00 | 2020-09-29 | 3 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-09-29 04:00 | 2020-09-29 | 4 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-09-29 05:00 | 2020-09-29 | 5 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-09-29 06:00 | 2020-09-29 | 6 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-09-29 07:00 | 2020-09-29 | 7 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-09-29 08:00 | 2020-09-29 | 8 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-09-29 09:00 | 2020-09-29 | 9 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-09-29 10:00 | 2020-09-29 | 10 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-29 11:00 | 2020-09-29 | 11 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-09-29 12:00 | 2020-09-29 | 12 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-09-29 13:00 | 2020-09-29 | 13 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-09-29 14:00 | 2020-09-29 | 14 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-09-29 15:00 | 2020-09-29 | 15 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-09-29 16:00 | 2020-09-29 | 16 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-29 17:00 | 2020-09-29 | 17 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-09-29 18:00 | 2020-09-29 | 18 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-09-29 19:00 | 2020-09-29 | 19 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-09-29 20:00 | 2020-09-29 | 20 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-09-29 21:00 | 2020-09-29 | 21 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-09-29 22:00 | 2020-09-29 | 22 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-09-29 23:00 | 2020-09-29 | 23 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-09-30 | 2020-09-29 | 0 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-09-30 01:00 | 2020-09-30 | 1 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-09-30 02:00 | 2020-09-30 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-09-30 03:00 | 2020-09-30 | 3 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-09-30 04:00 | 2020-09-30 | 4 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-09-30 05:00 | 2020-09-30 | 5 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-09-30 06:00 | 2020-09-30 | 6 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-30 07:00 | 2020-09-30 | 7 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-30 08:00 | 2020-09-30 | 8 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-09-30 09:00 | 2020-09-30 | 9 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-09-30 10:00 | 2020-09-30 | 10 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-09-30 11:00 | 2020-09-30 | 11 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-09-30 12:00 | 2020-09-30 | 12 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-09-30 13:00 | 2020-09-30 | 13 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-09-30 14:00 | 2020-09-30 | 14 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-09-30 15:00 | 2020-09-30 | 15 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-09-30 16:00 | 2020-09-30 | 16 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-09-30 17:00 | 2020-09-30 | 17 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-09-30 18:00 | 2020-09-30 | 18 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-09-30 19:00 | 2020-09-30 | 19 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-09-30 20:00 | 2020-09-30 | 20 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-09-30 21:00 | 2020-09-30 | 21 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-09-30 22:00 | 2020-09-30 | 22 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-09-30 23:00 | 2020-09-30 | 23 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-01 | 2020-09-30 | 0 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-01 01:00 | 2020-10-01 | 1 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-10-01 02:00 | 2020-10-01 | 2 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-01 03:00 | 2020-10-01 | 3 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-01 04:00 | 2020-10-01 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-01 05:00 | 2020-10-01 | 5 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-01 06:00 | 2020-10-01 | 6 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-10-01 07:00 | 2020-10-01 | 7 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-10-01 08:00 | 2020-10-01 | 8 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-10-01 09:00 | 2020-10-01 | 9 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-01 10:00 | 2020-10-01 | 10 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-01 11:00 | 2020-10-01 | 11 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-01 12:00 | 2020-10-01 | 12 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-01 13:00 | 2020-10-01 | 13 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-01 14:00 | 2020-10-01 | 14 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-01 15:00 | 2020-10-01 | 15 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-01 16:00 | 2020-10-01 | 16 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-01 17:00 | 2020-10-01 | 17 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-01 18:00 | 2020-10-01 | 18 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-01 19:00 | 2020-10-01 | 19 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-01 20:00 | 2020-10-01 | 20 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-01 21:00 | 2020-10-01 | 21 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-10-01 22:00 | 2020-10-01 | 22 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-10-01 23:00 | 2020-10-01 | 23 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-10-02 | 2020-10-01 | 0 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-02 01:00 | 2020-10-02 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-02 02:00 | 2020-10-02 | 2 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-02 03:00 | 2020-10-02 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-02 04:00 | 2020-10-02 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-02 05:00 | 2020-10-02 | 5 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-02 06:00 | 2020-10-02 | 6 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-10-02 07:00 | 2020-10-02 | 7 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-10-02 08:00 | 2020-10-02 | 8 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-10-02 09:00 | 2020-10-02 | 9 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-02 10:00 | 2020-10-02 | 10 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-02 11:00 | 2020-10-02 | 11 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-10-02 12:00 | 2020-10-02 | 12 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-02 13:00 | 2020-10-02 | 13 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-02 14:00 | 2020-10-02 | 14 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-10-02 15:00 | 2020-10-02 | 15 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-10-02 16:00 | 2020-10-02 | 16 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-10-02 17:00 | 2020-10-02 | 17 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-10-02 18:00 | 2020-10-02 | 18 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-02 19:00 | 2020-10-02 | 19 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-02 20:00 | 2020-10-02 | 20 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-02 21:00 | 2020-10-02 | 21 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-02 22:00 | 2020-10-02 | 22 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-10-02 23:00 | 2020-10-02 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-03 | 2020-10-02 | 0 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-10-03 01:00 | 2020-10-03 | 1 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-10-03 02:00 | 2020-10-03 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-10-03 03:00 | 2020-10-03 | 3 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-10-03 04:00 | 2020-10-03 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-03 05:00 | 2020-10-03 | 5 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-03 06:00 | 2020-10-03 | 6 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-10-03 07:00 | 2020-10-03 | 7 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-10-03 08:00 | 2020-10-03 | 8 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-10-03 09:00 | 2020-10-03 | 9 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-10-03 10:00 | 2020-10-03 | 10 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-03 11:00 | 2020-10-03 | 11 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-10-03 12:00 | 2020-10-03 | 12 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-03 13:00 | 2020-10-03 | 13 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-10-03 14:00 | 2020-10-03 | 14 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-10-03 15:00 | 2020-10-03 | 15 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-03 16:00 | 2020-10-03 | 16 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-03 17:00 | 2020-10-03 | 17 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-03 18:00 | 2020-10-03 | 18 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-03 19:00 | 2020-10-03 | 19 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-03 20:00 | 2020-10-03 | 20 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-10-03 21:00 | 2020-10-03 | 21 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-10-03 22:00 | 2020-10-03 | 22 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-10-03 23:00 | 2020-10-03 | 23 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-10-04 | 2020-10-03 | 0 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-10-04 01:00 | 2020-10-04 | 1 | 2.0555 | 0.007137% | 3.0646 | 3.178 | 3.2955 | 3.4173 | 3.5437 | 0 | 0 | 0 | 0 | 0
2020-10-04 02:00 | 2020-10-04 | 2 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-10-04 03:00 | 2020-10-04 | 3 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-10-04 04:00 | 2020-10-04 | 4 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-10-04 05:00 | 2020-10-04 | 5 | 2.0178 | 0.007007% | 3.0085 | 3.1198 | 3.2351 | 3.3548 | 3.4788 | 0 | 0 | 0 | 0 | 0
2020-10-04 06:00 | 2020-10-04 | 6 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-10-04 07:00 | 2020-10-04 | 7 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-04 08:00 | 2020-10-04 | 8 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-10-04 09:00 | 2020-10-04 | 9 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-10-04 10:00 | 2020-10-04 | 10 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-10-04 11:00 | 2020-10-04 | 11 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-10-04 12:00 | 2020-10-04 | 12 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-10-04 13:00 | 2020-10-04 | 13 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-04 14:00 | 2020-10-04 | 14 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-04 15:00 | 2020-10-04 | 15 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-04 16:00 | 2020-10-04 | 16 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-04 17:00 | 2020-10-04 | 17 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-10-04 18:00 | 2020-10-04 | 18 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-04 19:00 | 2020-10-04 | 19 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-04 20:00 | 2020-10-04 | 20 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-04 21:00 | 2020-10-04 | 21 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-10-04 22:00 | 2020-10-04 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-10-04 23:00 | 2020-10-04 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-05 | 2020-10-04 | 0 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-05 01:00 | 2020-10-05 | 1 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-10-05 02:00 | 2020-10-05 | 2 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-10-05 03:00 | 2020-10-05 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-10-05 04:00 | 2020-10-05 | 4 | 2.0479 | 0.007111% | 3.0534 | 3.1663 | 3.2834 | 3.4048 | 3.5307 | 0 | 0 | 0 | 0 | 0
2020-10-05 05:00 | 2020-10-05 | 5 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-10-05 06:00 | 2020-10-05 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-10-05 07:00 | 2020-10-05 | 7 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-10-05 08:00 | 2020-10-05 | 8 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-10-05 09:00 | 2020-10-05 | 9 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-05 10:00 | 2020-10-05 | 10 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-05 11:00 | 2020-10-05 | 11 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-05 12:00 | 2020-10-05 | 12 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-05 13:00 | 2020-10-05 | 13 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-05 14:00 | 2020-10-05 | 14 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-05 15:00 | 2020-10-05 | 15 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-10-05 16:00 | 2020-10-05 | 16 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-05 17:00 | 2020-10-05 | 17 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-05 18:00 | 2020-10-05 | 18 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-05 19:00 | 2020-10-05 | 19 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-05 20:00 | 2020-10-05 | 20 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-05 21:00 | 2020-10-05 | 21 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-05 22:00 | 2020-10-05 | 22 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-10-05 23:00 | 2020-10-05 | 23 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-06 | 2020-10-05 | 0 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-10-06 01:00 | 2020-10-06 | 1 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-10-06 02:00 | 2020-10-06 | 2 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-06 03:00 | 2020-10-06 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-06 04:00 | 2020-10-06 | 4 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-06 05:00 | 2020-10-06 | 5 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-10-06 06:00 | 2020-10-06 | 6 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-10-06 07:00 | 2020-10-06 | 7 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-06 08:00 | 2020-10-06 | 8 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-06 09:00 | 2020-10-06 | 9 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-06 10:00 | 2020-10-06 | 10 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-10-06 11:00 | 2020-10-06 | 11 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-10-06 12:00 | 2020-10-06 | 12 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-06 13:00 | 2020-10-06 | 13 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-06 14:00 | 2020-10-06 | 14 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-06 15:00 | 2020-10-06 | 15 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-06 16:00 | 2020-10-06 | 16 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-10-06 17:00 | 2020-10-06 | 17 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-06 18:00 | 2020-10-06 | 18 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-06 19:00 | 2020-10-06 | 19 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-10-06 20:00 | 2020-10-06 | 20 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-06 21:00 | 2020-10-06 | 21 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-06 22:00 | 2020-10-06 | 22 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-10-06 23:00 | 2020-10-06 | 23 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-10-07 | 2020-10-06 | 0 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-10-07 01:00 | 2020-10-07 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-07 02:00 | 2020-10-07 | 2 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-07 03:00 | 2020-10-07 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-07 04:00 | 2020-10-07 | 4 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-07 05:00 | 2020-10-07 | 5 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-10-07 06:00 | 2020-10-07 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-07 07:00 | 2020-10-07 | 7 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-07 08:00 | 2020-10-07 | 8 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-10-07 09:00 | 2020-10-07 | 9 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-07 10:00 | 2020-10-07 | 10 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-07 11:00 | 2020-10-07 | 11 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-07 12:00 | 2020-10-07 | 12 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-07 13:00 | 2020-10-07 | 13 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-07 14:00 | 2020-10-07 | 14 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-07 15:00 | 2020-10-07 | 15 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-07 16:00 | 2020-10-07 | 16 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-10-07 17:00 | 2020-10-07 | 17 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-07 18:00 | 2020-10-07 | 18 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-10-07 19:00 | 2020-10-07 | 19 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-10-07 20:00 | 2020-10-07 | 20 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-07 21:00 | 2020-10-07 | 21 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-10-07 22:00 | 2020-10-07 | 22 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-10-07 23:00 | 2020-10-07 | 23 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-08 | 2020-10-07 | 0 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-10-08 01:00 | 2020-10-08 | 1 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-08 02:00 | 2020-10-08 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-10-08 03:00 | 2020-10-08 | 3 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-08 04:00 | 2020-10-08 | 4 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-08 05:00 | 2020-10-08 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-08 06:00 | 2020-10-08 | 6 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-08 07:00 | 2020-10-08 | 7 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-10-08 08:00 | 2020-10-08 | 8 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-08 09:00 | 2020-10-08 | 9 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-10-08 10:00 | 2020-10-08 | 10 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-08 11:00 | 2020-10-08 | 11 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-10-08 12:00 | 2020-10-08 | 12 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-08 13:00 | 2020-10-08 | 13 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-08 14:00 | 2020-10-08 | 14 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-08 15:00 | 2020-10-08 | 15 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-08 16:00 | 2020-10-08 | 16 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-08 17:00 | 2020-10-08 | 17 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-08 18:00 | 2020-10-08 | 18 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-08 19:00 | 2020-10-08 | 19 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-08 20:00 | 2020-10-08 | 20 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-08 21:00 | 2020-10-08 | 21 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-08 22:00 | 2020-10-08 | 22 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-08 23:00 | 2020-10-08 | 23 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-10-09 | 2020-10-08 | 0 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-09 01:00 | 2020-10-09 | 1 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-09 02:00 | 2020-10-09 | 2 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-09 03:00 | 2020-10-09 | 3 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-10-09 04:00 | 2020-10-09 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-09 05:00 | 2020-10-09 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-09 06:00 | 2020-10-09 | 6 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-10-09 07:00 | 2020-10-09 | 7 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-10-09 08:00 | 2020-10-09 | 8 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-10-09 09:00 | 2020-10-09 | 9 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-09 10:00 | 2020-10-09 | 10 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-09 11:00 | 2020-10-09 | 11 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-09 12:00 | 2020-10-09 | 12 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-10-09 13:00 | 2020-10-09 | 13 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-10-09 14:00 | 2020-10-09 | 14 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-09 15:00 | 2020-10-09 | 15 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-09 16:00 | 2020-10-09 | 16 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-10-09 17:00 | 2020-10-09 | 17 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-09 18:00 | 2020-10-09 | 18 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-09 19:00 | 2020-10-09 | 19 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-09 20:00 | 2020-10-09 | 20 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-10-09 21:00 | 2020-10-09 | 21 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-09 22:00 | 2020-10-09 | 22 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-10-09 23:00 | 2020-10-09 | 23 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-10-10 | 2020-10-09 | 0 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-10-10 01:00 | 2020-10-10 | 1 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-10-10 02:00 | 2020-10-10 | 2 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-10-10 03:00 | 2020-10-10 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-10 04:00 | 2020-10-10 | 4 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-10 05:00 | 2020-10-10 | 5 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-10-10 06:00 | 2020-10-10 | 6 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-10-10 07:00 | 2020-10-10 | 7 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-10 08:00 | 2020-10-10 | 8 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-10-10 09:00 | 2020-10-10 | 9 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-10 10:00 | 2020-10-10 | 10 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-10 11:00 | 2020-10-10 | 11 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-10 12:00 | 2020-10-10 | 12 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-10-10 13:00 | 2020-10-10 | 13 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-10 14:00 | 2020-10-10 | 14 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-10 15:00 | 2020-10-10 | 15 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-10-10 16:00 | 2020-10-10 | 16 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-10-10 17:00 | 2020-10-10 | 17 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-10 18:00 | 2020-10-10 | 18 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-10 19:00 | 2020-10-10 | 19 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-10-10 20:00 | 2020-10-10 | 20 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-10-10 21:00 | 2020-10-10 | 21 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-10-10 22:00 | 2020-10-10 | 22 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-10-10 23:00 | 2020-10-10 | 23 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-11 | 2020-10-10 | 0 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-10-11 01:00 | 2020-10-11 | 1 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-10-11 02:00 | 2020-10-11 | 2 | 2.0028 | 0.006954% | 2.9861 | 3.0965 | 3.211 | 3.3297 | 3.4528 | 0 | 0 | 0 | 0 | 0
2020-10-11 03:00 | 2020-10-11 | 3 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-10-11 04:00 | 2020-10-11 | 4 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-10-11 05:00 | 2020-10-11 | 5 | 2.0254 | 0.007033% | 3.0197 | 3.1314 | 3.2472 | 3.3673 | 3.4918 | 0 | 0 | 0 | 0 | 0
2020-10-11 06:00 | 2020-10-11 | 6 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-10-11 07:00 | 2020-10-11 | 7 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-11 08:00 | 2020-10-11 | 8 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-10-11 09:00 | 2020-10-11 | 9 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-10-11 10:00 | 2020-10-11 | 10 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-10-11 11:00 | 2020-10-11 | 11 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-10-11 12:00 | 2020-10-11 | 12 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-10-11 13:00 | 2020-10-11 | 13 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-10-11 14:00 | 2020-10-11 | 14 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-10-11 15:00 | 2020-10-11 | 15 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-10-11 16:00 | 2020-10-11 | 16 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-10-11 17:00 | 2020-10-11 | 17 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-10-11 18:00 | 2020-10-11 | 18 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-10-11 19:00 | 2020-10-11 | 19 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-11 20:00 | 2020-10-11 | 20 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-10-11 21:00 | 2020-10-11 | 21 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-10-11 22:00 | 2020-10-11 | 22 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-10-11 23:00 | 2020-10-11 | 23 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-10-12 | 2020-10-11 | 0 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-12 01:00 | 2020-10-12 | 1 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-10-12 02:00 | 2020-10-12 | 2 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-10-12 03:00 | 2020-10-12 | 3 | 1.9952 | 0.006928% | 2.9748 | 3.0848 | 3.1989 | 3.3172 | 3.4399 | 0 | 0 | 0 | 0 | 0
2020-10-12 04:00 | 2020-10-12 | 4 | 1.9802 | 0.006876% | 2.9524 | 3.0616 | 3.1748 | 3.2922 | 3.4139 | 0 | 0 | 0 | 0 | 0
2020-10-12 05:00 | 2020-10-12 | 5 | 2.0705 | 0.00719% | 3.0871 | 3.2012 | 3.3196 | 3.4424 | 3.5697 | 0 | 0 | 0 | 0 | 0
2020-10-12 06:00 | 2020-10-12 | 6 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-12 07:00 | 2020-10-12 | 7 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-12 08:00 | 2020-10-12 | 8 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-10-12 09:00 | 2020-10-12 | 9 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-10-12 10:00 | 2020-10-12 | 10 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-10-12 11:00 | 2020-10-12 | 11 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-10-12 12:00 | 2020-10-12 | 12 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-10-12 13:00 | 2020-10-12 | 13 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-10-12 14:00 | 2020-10-12 | 14 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-10-12 15:00 | 2020-10-12 | 15 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-10-12 16:00 | 2020-10-12 | 16 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-10-12 17:00 | 2020-10-12 | 17 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-12 18:00 | 2020-10-12 | 18 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-10-12 19:00 | 2020-10-12 | 19 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-12 20:00 | 2020-10-12 | 20 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-12 21:00 | 2020-10-12 | 21 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-10-12 22:00 | 2020-10-12 | 22 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-10-12 23:00 | 2020-10-12 | 23 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-10-13 | 2020-10-12 | 0 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-13 01:00 | 2020-10-13 | 1 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-10-13 02:00 | 2020-10-13 | 2 | 1.9727 | 0.00685% | 2.9412 | 3.0499 | 3.1627 | 3.2796 | 3.4009 | 0 | 0 | 0 | 0 | 0
2020-10-13 03:00 | 2020-10-13 | 3 | 1.9425 | 0.006745% | 2.8963 | 3.0034 | 3.1144 | 3.2296 | 3.349 | 0 | 0 | 0 | 0 | 0
2020-10-13 04:00 | 2020-10-13 | 4 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-10-13 05:00 | 2020-10-13 | 5 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-10-13 06:00 | 2020-10-13 | 6 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-10-13 07:00 | 2020-10-13 | 7 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-10-13 08:00 | 2020-10-13 | 8 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-13 09:00 | 2020-10-13 | 9 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-13 10:00 | 2020-10-13 | 10 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-10-13 11:00 | 2020-10-13 | 11 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-13 12:00 | 2020-10-13 | 12 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-13 13:00 | 2020-10-13 | 13 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-13 14:00 | 2020-10-13 | 14 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-13 15:00 | 2020-10-13 | 15 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-13 16:00 | 2020-10-13 | 16 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-13 17:00 | 2020-10-13 | 17 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-13 18:00 | 2020-10-13 | 18 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-13 19:00 | 2020-10-13 | 19 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-13 20:00 | 2020-10-13 | 20 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-10-13 21:00 | 2020-10-13 | 21 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-10-13 22:00 | 2020-10-13 | 22 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-10-13 23:00 | 2020-10-13 | 23 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-10-14 | 2020-10-13 | 0 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-14 01:00 | 2020-10-14 | 1 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-14 02:00 | 2020-10-14 | 2 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-14 03:00 | 2020-10-14 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-14 04:00 | 2020-10-14 | 4 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-14 05:00 | 2020-10-14 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-14 06:00 | 2020-10-14 | 6 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-10-14 07:00 | 2020-10-14 | 7 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-10-14 08:00 | 2020-10-14 | 8 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-10-14 09:00 | 2020-10-14 | 9 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-14 10:00 | 2020-10-14 | 10 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-10-14 11:00 | 2020-10-14 | 11 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-14 12:00 | 2020-10-14 | 12 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-10-14 13:00 | 2020-10-14 | 13 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-14 14:00 | 2020-10-14 | 14 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-14 15:00 | 2020-10-14 | 15 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-14 16:00 | 2020-10-14 | 16 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-14 17:00 | 2020-10-14 | 17 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-14 18:00 | 2020-10-14 | 18 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-14 19:00 | 2020-10-14 | 19 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-10-14 20:00 | 2020-10-14 | 20 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-14 21:00 | 2020-10-14 | 21 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-14 22:00 | 2020-10-14 | 22 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-10-14 23:00 | 2020-10-14 | 23 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-15 | 2020-10-14 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-10-15 01:00 | 2020-10-15 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-15 02:00 | 2020-10-15 | 2 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-15 03:00 | 2020-10-15 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-15 04:00 | 2020-10-15 | 4 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-15 05:00 | 2020-10-15 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-15 06:00 | 2020-10-15 | 6 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-10-15 07:00 | 2020-10-15 | 7 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-15 08:00 | 2020-10-15 | 8 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-10-15 09:00 | 2020-10-15 | 9 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-15 10:00 | 2020-10-15 | 10 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-15 11:00 | 2020-10-15 | 11 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-10-15 12:00 | 2020-10-15 | 12 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-10-15 13:00 | 2020-10-15 | 13 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-10-15 14:00 | 2020-10-15 | 14 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-10-15 15:00 | 2020-10-15 | 15 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-10-15 16:00 | 2020-10-15 | 16 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-10-15 17:00 | 2020-10-15 | 17 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-15 18:00 | 2020-10-15 | 18 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-10-15 19:00 | 2020-10-15 | 19 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-15 20:00 | 2020-10-15 | 20 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-15 21:00 | 2020-10-15 | 21 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-15 22:00 | 2020-10-15 | 22 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-10-15 23:00 | 2020-10-15 | 23 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-10-16 | 2020-10-15 | 0 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-16 01:00 | 2020-10-16 | 1 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-10-16 02:00 | 2020-10-16 | 2 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-10-16 03:00 | 2020-10-16 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-16 04:00 | 2020-10-16 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-16 05:00 | 2020-10-16 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-16 06:00 | 2020-10-16 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-16 07:00 | 2020-10-16 | 7 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-16 08:00 | 2020-10-16 | 8 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-16 09:00 | 2020-10-16 | 9 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-16 10:00 | 2020-10-16 | 10 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-16 11:00 | 2020-10-16 | 11 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-16 12:00 | 2020-10-16 | 12 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-16 13:00 | 2020-10-16 | 13 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-10-16 14:00 | 2020-10-16 | 14 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-16 15:00 | 2020-10-16 | 15 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-10-16 16:00 | 2020-10-16 | 16 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-16 17:00 | 2020-10-16 | 17 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-10-16 18:00 | 2020-10-16 | 18 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-16 19:00 | 2020-10-16 | 19 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-10-16 20:00 | 2020-10-16 | 20 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-16 21:00 | 2020-10-16 | 21 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-10-16 22:00 | 2020-10-16 | 22 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-10-16 23:00 | 2020-10-16 | 23 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-10-17 | 2020-10-16 | 0 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-10-17 01:00 | 2020-10-17 | 1 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-10-17 02:00 | 2020-10-17 | 2 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-10-17 03:00 | 2020-10-17 | 3 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-17 04:00 | 2020-10-17 | 4 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-10-17 05:00 | 2020-10-17 | 5 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-10-17 06:00 | 2020-10-17 | 6 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-10-17 07:00 | 2020-10-17 | 7 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-10-17 08:00 | 2020-10-17 | 8 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-10-17 09:00 | 2020-10-17 | 9 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-10-17 10:00 | 2020-10-17 | 10 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-17 11:00 | 2020-10-17 | 11 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-17 12:00 | 2020-10-17 | 12 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-17 13:00 | 2020-10-17 | 13 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-10-17 14:00 | 2020-10-17 | 14 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-10-17 15:00 | 2020-10-17 | 15 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-10-17 16:00 | 2020-10-17 | 16 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-10-17 17:00 | 2020-10-17 | 17 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-17 18:00 | 2020-10-17 | 18 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-10-17 19:00 | 2020-10-17 | 19 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-17 20:00 | 2020-10-17 | 20 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-17 21:00 | 2020-10-17 | 21 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-10-17 22:00 | 2020-10-17 | 22 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-10-17 23:00 | 2020-10-17 | 23 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-10-18 | 2020-10-17 | 0 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-18 01:00 | 2020-10-18 | 1 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-10-18 02:00 | 2020-10-18 | 2 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-10-18 03:00 | 2020-10-18 | 3 | 2.0329 | 0.007059% | 3.031 | 3.143 | 3.2593 | 3.3798 | 3.5048 | 0 | 0 | 0 | 0 | 0
2020-10-18 04:00 | 2020-10-18 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-10-18 05:00 | 2020-10-18 | 5 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-18 06:00 | 2020-10-18 | 6 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-10-18 07:00 | 2020-10-18 | 7 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-18 08:00 | 2020-10-18 | 8 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-10-18 09:00 | 2020-10-18 | 9 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-10-18 10:00 | 2020-10-18 | 10 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-10-18 11:00 | 2020-10-18 | 11 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-10-18 12:00 | 2020-10-18 | 12 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-10-18 13:00 | 2020-10-18 | 13 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-10-18 14:00 | 2020-10-18 | 14 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-18 15:00 | 2020-10-18 | 15 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-18 16:00 | 2020-10-18 | 16 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-10-18 17:00 | 2020-10-18 | 17 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-10-18 18:00 | 2020-10-18 | 18 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-18 19:00 | 2020-10-18 | 19 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-18 20:00 | 2020-10-18 | 20 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-18 21:00 | 2020-10-18 | 21 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-10-18 22:00 | 2020-10-18 | 22 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-10-18 23:00 | 2020-10-18 | 23 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-10-19 | 2020-10-18 | 0 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-10-19 01:00 | 2020-10-19 | 1 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-19 02:00 | 2020-10-19 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-10-19 03:00 | 2020-10-19 | 3 | 2.0404 | 0.007085% | 3.0422 | 3.1547 | 3.2713 | 3.3923 | 3.5178 | 0 | 0 | 0 | 0 | 0
2020-10-19 04:00 | 2020-10-19 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-10-19 05:00 | 2020-10-19 | 5 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-19 06:00 | 2020-10-19 | 6 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-10-19 07:00 | 2020-10-19 | 7 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-19 08:00 | 2020-10-19 | 8 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-19 09:00 | 2020-10-19 | 9 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-19 10:00 | 2020-10-19 | 10 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-10-19 11:00 | 2020-10-19 | 11 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-10-19 12:00 | 2020-10-19 | 12 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-10-19 13:00 | 2020-10-19 | 13 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-19 14:00 | 2020-10-19 | 14 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-19 15:00 | 2020-10-19 | 15 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-10-19 16:00 | 2020-10-19 | 16 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-10-19 17:00 | 2020-10-19 | 17 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-10-19 18:00 | 2020-10-19 | 18 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-10-19 19:00 | 2020-10-19 | 19 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-10-19 20:00 | 2020-10-19 | 20 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-19 21:00 | 2020-10-19 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-19 22:00 | 2020-10-19 | 22 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-10-19 23:00 | 2020-10-19 | 23 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-10-20 | 2020-10-19 | 0 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-10-20 01:00 | 2020-10-20 | 1 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-10-20 02:00 | 2020-10-20 | 2 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-10-20 03:00 | 2020-10-20 | 3 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-10-20 04:00 | 2020-10-20 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-20 05:00 | 2020-10-20 | 5 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-10-20 06:00 | 2020-10-20 | 6 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-10-20 07:00 | 2020-10-20 | 7 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-10-20 08:00 | 2020-10-20 | 8 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-10-20 09:00 | 2020-10-20 | 9 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-20 10:00 | 2020-10-20 | 10 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-20 11:00 | 2020-10-20 | 11 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-20 12:00 | 2020-10-20 | 12 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-10-20 13:00 | 2020-10-20 | 13 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-20 14:00 | 2020-10-20 | 14 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-20 15:00 | 2020-10-20 | 15 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-10-20 16:00 | 2020-10-20 | 16 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-20 17:00 | 2020-10-20 | 17 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-10-20 18:00 | 2020-10-20 | 18 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-20 19:00 | 2020-10-20 | 19 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-20 20:00 | 2020-10-20 | 20 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-10-20 21:00 | 2020-10-20 | 21 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-10-20 22:00 | 2020-10-20 | 22 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-10-20 23:00 | 2020-10-20 | 23 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-21 | 2020-10-20 | 0 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-10-21 01:00 | 2020-10-21 | 1 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-10-21 02:00 | 2020-10-21 | 2 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-21 03:00 | 2020-10-21 | 3 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-21 04:00 | 2020-10-21 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-10-21 05:00 | 2020-10-21 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-10-21 06:00 | 2020-10-21 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-21 07:00 | 2020-10-21 | 7 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-21 08:00 | 2020-10-21 | 8 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-21 09:00 | 2020-10-21 | 9 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-21 10:00 | 2020-10-21 | 10 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-10-21 11:00 | 2020-10-21 | 11 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-10-21 12:00 | 2020-10-21 | 12 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-10-21 13:00 | 2020-10-21 | 13 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-10-21 14:00 | 2020-10-21 | 14 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-10-21 15:00 | 2020-10-21 | 15 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-21 16:00 | 2020-10-21 | 16 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-10-21 17:00 | 2020-10-21 | 17 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-10-21 18:00 | 2020-10-21 | 18 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-10-21 19:00 | 2020-10-21 | 19 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-10-21 20:00 | 2020-10-21 | 20 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-10-21 21:00 | 2020-10-21 | 21 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-10-21 22:00 | 2020-10-21 | 22 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-10-21 23:00 | 2020-10-21 | 23 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-10-22 | 2020-10-21 | 0 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-10-22 01:00 | 2020-10-22 | 1 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-22 02:00 | 2020-10-22 | 2 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-10-22 03:00 | 2020-10-22 | 3 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-10-22 04:00 | 2020-10-22 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-10-22 05:00 | 2020-10-22 | 5 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-10-22 06:00 | 2020-10-22 | 6 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-10-22 07:00 | 2020-10-22 | 7 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-10-22 08:00 | 2020-10-22 | 8 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-10-22 09:00 | 2020-10-22 | 9 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-10-22 10:00 | 2020-10-22 | 10 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-22 11:00 | 2020-10-22 | 11 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-22 12:00 | 2020-10-22 | 12 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-22 13:00 | 2020-10-22 | 13 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-10-22 14:00 | 2020-10-22 | 14 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-22 15:00 | 2020-10-22 | 15 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-22 16:00 | 2020-10-22 | 16 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-10-22 17:00 | 2020-10-22 | 17 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-22 18:00 | 2020-10-22 | 18 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-10-22 19:00 | 2020-10-22 | 19 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-10-22 20:00 | 2020-10-22 | 20 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-22 21:00 | 2020-10-22 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-22 22:00 | 2020-10-22 | 22 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-10-22 23:00 | 2020-10-22 | 23 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-10-23 | 2020-10-22 | 0 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-23 01:00 | 2020-10-23 | 1 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-10-23 02:00 | 2020-10-23 | 2 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-23 03:00 | 2020-10-23 | 3 | 2.1157 | 0.007347% | 3.1544 | 3.2711 | 3.3921 | 3.5175 | 3.6476 | 0 | 0 | 0 | 0 | 0
2020-10-23 04:00 | 2020-10-23 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-10-23 05:00 | 2020-10-23 | 5 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-10-23 06:00 | 2020-10-23 | 6 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-10-23 07:00 | 2020-10-23 | 7 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-23 08:00 | 2020-10-23 | 8 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-23 09:00 | 2020-10-23 | 9 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-10-23 10:00 | 2020-10-23 | 10 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-10-23 11:00 | 2020-10-23 | 11 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-10-23 12:00 | 2020-10-23 | 12 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-23 13:00 | 2020-10-23 | 13 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-23 14:00 | 2020-10-23 | 14 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-10-23 15:00 | 2020-10-23 | 15 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-23 16:00 | 2020-10-23 | 16 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-10-23 17:00 | 2020-10-23 | 17 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-23 18:00 | 2020-10-23 | 18 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-10-23 19:00 | 2020-10-23 | 19 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-10-23 20:00 | 2020-10-23 | 20 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-23 21:00 | 2020-10-23 | 21 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-23 22:00 | 2020-10-23 | 22 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-10-23 23:00 | 2020-10-23 | 23 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-10-24 | 2020-10-23 | 0 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-10-24 01:00 | 2020-10-24 | 1 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-10-24 02:00 | 2020-10-24 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-10-24 03:00 | 2020-10-24 | 3 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-10-24 04:00 | 2020-10-24 | 4 | 2.0931 | 0.007268% | 3.1208 | 3.2362 | 3.3558 | 3.4799 | 3.6086 | 0 | 0 | 0 | 0 | 0
2020-10-24 05:00 | 2020-10-24 | 5 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-10-24 06:00 | 2020-10-24 | 6 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-10-24 07:00 | 2020-10-24 | 7 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-10-24 08:00 | 2020-10-24 | 8 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-10-24 09:00 | 2020-10-24 | 9 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-24 10:00 | 2020-10-24 | 10 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-10-24 11:00 | 2020-10-24 | 11 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-24 12:00 | 2020-10-24 | 12 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-24 13:00 | 2020-10-24 | 13 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-10-24 14:00 | 2020-10-24 | 14 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-24 15:00 | 2020-10-24 | 15 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-10-24 16:00 | 2020-10-24 | 16 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-10-24 17:00 | 2020-10-24 | 17 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-24 18:00 | 2020-10-24 | 18 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-10-24 19:00 | 2020-10-24 | 19 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-10-24 20:00 | 2020-10-24 | 20 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-24 21:00 | 2020-10-24 | 21 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-10-24 22:00 | 2020-10-24 | 22 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-10-24 23:00 | 2020-10-24 | 23 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-10-25 | 2020-10-24 | 0 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-25 01:00 | 2020-10-25 | 1 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-25 02:00 | 2020-10-25 | 2 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-10-25 03:00 | 2020-10-25 | 3 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-25 04:00 | 2020-10-25 | 4 | 2.0781 | 0.007216% | 3.0983 | 3.2129 | 3.3317 | 3.4549 | 3.5827 | 0 | 0 | 0 | 0 | 0
2020-10-25 05:00 | 2020-10-25 | 5 | 2.1082 | 0.00732% | 3.1432 | 3.2595 | 3.38 | 3.505 | 3.6346 | 0 | 0 | 0 | 0 | 0
2020-10-25 06:00 | 2020-10-25 | 6 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-10-25 07:00 | 2020-10-25 | 7 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-10-25 08:00 | 2020-10-25 | 8 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-10-25 09:00 | 2020-10-25 | 9 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-10-25 10:00 | 2020-10-25 | 10 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-10-25 11:00 | 2020-10-25 | 11 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-10-25 12:00 | 2020-10-25 | 12 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-10-25 13:00 | 2020-10-25 | 13 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-10-25 14:00 | 2020-10-25 | 14 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-10-25 15:00 | 2020-10-25 | 15 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-10-25 16:00 | 2020-10-25 | 16 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-25 17:00 | 2020-10-25 | 17 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-10-25 18:00 | 2020-10-25 | 18 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-25 19:00 | 2020-10-25 | 19 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-25 20:00 | 2020-10-25 | 20 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-25 21:00 | 2020-10-25 | 21 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-10-25 22:00 | 2020-10-25 | 22 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-10-25 23:00 | 2020-10-25 | 23 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-10-26 | 2020-10-25 | 0 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-26 01:00 | 2020-10-26 | 1 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-10-26 02:00 | 2020-10-26 | 2 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-10-26 03:00 | 2020-10-26 | 3 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-26 04:00 | 2020-10-26 | 4 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-10-26 05:00 | 2020-10-26 | 5 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-10-26 06:00 | 2020-10-26 | 6 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-10-26 07:00 | 2020-10-26 | 7 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-26 08:00 | 2020-10-26 | 8 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-10-26 09:00 | 2020-10-26 | 9 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-26 10:00 | 2020-10-26 | 10 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-10-26 11:00 | 2020-10-26 | 11 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-10-26 12:00 | 2020-10-26 | 12 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-10-26 13:00 | 2020-10-26 | 13 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-10-26 14:00 | 2020-10-26 | 14 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-10-26 15:00 | 2020-10-26 | 15 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-10-26 16:00 | 2020-10-26 | 16 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-10-26 17:00 | 2020-10-26 | 17 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-10-26 18:00 | 2020-10-26 | 18 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-10-26 19:00 | 2020-10-26 | 19 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-26 20:00 | 2020-10-26 | 20 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-10-26 21:00 | 2020-10-26 | 21 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-10-26 22:00 | 2020-10-26 | 22 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-10-26 23:00 | 2020-10-26 | 23 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-10-27 | 2020-10-26 | 0 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-27 01:00 | 2020-10-27 | 1 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-27 02:00 | 2020-10-27 | 2 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-10-27 03:00 | 2020-10-27 | 3 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-10-27 04:00 | 2020-10-27 | 4 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-27 05:00 | 2020-10-27 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-10-27 06:00 | 2020-10-27 | 6 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-10-27 07:00 | 2020-10-27 | 7 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-10-27 08:00 | 2020-10-27 | 8 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-10-27 09:00 | 2020-10-27 | 9 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-27 10:00 | 2020-10-27 | 10 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-10-27 11:00 | 2020-10-27 | 11 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-10-27 12:00 | 2020-10-27 | 12 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-10-27 13:00 | 2020-10-27 | 13 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-27 14:00 | 2020-10-27 | 14 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-27 15:00 | 2020-10-27 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-10-27 16:00 | 2020-10-27 | 16 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-10-27 17:00 | 2020-10-27 | 17 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-10-27 18:00 | 2020-10-27 | 18 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-10-27 19:00 | 2020-10-27 | 19 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-10-27 20:00 | 2020-10-27 | 20 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-10-27 21:00 | 2020-10-27 | 21 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-27 22:00 | 2020-10-27 | 22 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-27 23:00 | 2020-10-27 | 23 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-10-28 | 2020-10-27 | 0 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-10-28 01:00 | 2020-10-28 | 1 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-10-28 02:00 | 2020-10-28 | 2 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-10-28 03:00 | 2020-10-28 | 3 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-10-28 04:00 | 2020-10-28 | 4 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-10-28 05:00 | 2020-10-28 | 5 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-10-28 06:00 | 2020-10-28 | 6 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-10-28 07:00 | 2020-10-28 | 7 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-10-28 08:00 | 2020-10-28 | 8 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-28 09:00 | 2020-10-28 | 9 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-10-28 10:00 | 2020-10-28 | 10 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-10-28 11:00 | 2020-10-28 | 11 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-28 12:00 | 2020-10-28 | 12 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-10-28 13:00 | 2020-10-28 | 13 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-28 14:00 | 2020-10-28 | 14 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-28 15:00 | 2020-10-28 | 15 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-28 16:00 | 2020-10-28 | 16 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-10-28 17:00 | 2020-10-28 | 17 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-10-28 18:00 | 2020-10-28 | 18 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-10-28 19:00 | 2020-10-28 | 19 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-10-28 20:00 | 2020-10-28 | 20 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-10-28 21:00 | 2020-10-28 | 21 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-28 22:00 | 2020-10-28 | 22 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-10-28 23:00 | 2020-10-28 | 23 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-10-29 | 2020-10-28 | 0 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-10-29 01:00 | 2020-10-29 | 1 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-10-29 02:00 | 2020-10-29 | 2 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-10-29 03:00 | 2020-10-29 | 3 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-10-29 04:00 | 2020-10-29 | 4 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-10-29 05:00 | 2020-10-29 | 5 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-10-29 06:00 | 2020-10-29 | 6 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-10-29 07:00 | 2020-10-29 | 7 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-10-29 08:00 | 2020-10-29 | 8 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-10-29 09:00 | 2020-10-29 | 9 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-10-29 10:00 | 2020-10-29 | 10 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-10-29 11:00 | 2020-10-29 | 11 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-10-29 12:00 | 2020-10-29 | 12 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-10-29 13:00 | 2020-10-29 | 13 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-10-29 14:00 | 2020-10-29 | 14 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-10-29 15:00 | 2020-10-29 | 15 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-10-29 16:00 | 2020-10-29 | 16 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-10-29 17:00 | 2020-10-29 | 17 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-10-29 18:00 | 2020-10-29 | 18 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-10-29 19:00 | 2020-10-29 | 19 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-10-29 20:00 | 2020-10-29 | 20 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-10-29 21:00 | 2020-10-29 | 21 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-29 22:00 | 2020-10-29 | 22 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-10-29 23:00 | 2020-10-29 | 23 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-10-30 | 2020-10-29 | 0 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-10-30 01:00 | 2020-10-30 | 1 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-10-30 02:00 | 2020-10-30 | 2 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-10-30 03:00 | 2020-10-30 | 3 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-10-30 04:00 | 2020-10-30 | 4 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-30 05:00 | 2020-10-30 | 5 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-10-30 06:00 | 2020-10-30 | 6 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-30 07:00 | 2020-10-30 | 7 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-10-30 08:00 | 2020-10-30 | 8 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-30 09:00 | 2020-10-30 | 9 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-10-30 10:00 | 2020-10-30 | 10 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-30 11:00 | 2020-10-30 | 11 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-10-30 12:00 | 2020-10-30 | 12 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-10-30 13:00 | 2020-10-30 | 13 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-10-30 14:00 | 2020-10-30 | 14 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-30 15:00 | 2020-10-30 | 15 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-10-30 16:00 | 2020-10-30 | 16 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-10-30 17:00 | 2020-10-30 | 17 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-10-30 18:00 | 2020-10-30 | 18 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-10-30 19:00 | 2020-10-30 | 19 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-10-30 20:00 | 2020-10-30 | 20 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-10-30 21:00 | 2020-10-30 | 21 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-10-30 22:00 | 2020-10-30 | 22 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-10-30 23:00 | 2020-10-30 | 23 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-10-31 | 2020-10-30 | 0 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-31 01:00 | 2020-10-31 | 1 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-10-31 02:00 | 2020-10-31 | 2 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-10-31 03:00 | 2020-10-31 | 3 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-10-31 04:00 | 2020-10-31 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-10-31 05:00 | 2020-10-31 | 5 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-10-31 06:00 | 2020-10-31 | 6 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-10-31 07:00 | 2020-10-31 | 7 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-10-31 08:00 | 2020-10-31 | 8 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-10-31 09:00 | 2020-10-31 | 9 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-10-31 10:00 | 2020-10-31 | 10 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-10-31 11:00 | 2020-10-31 | 11 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-10-31 12:00 | 2020-10-31 | 12 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-10-31 13:00 | 2020-10-31 | 13 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-10-31 14:00 | 2020-10-31 | 14 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-31 15:00 | 2020-10-31 | 15 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-10-31 16:00 | 2020-10-31 | 16 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-10-31 17:00 | 2020-10-31 | 17 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-10-31 18:00 | 2020-10-31 | 18 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-10-31 19:00 | 2020-10-31 | 19 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-10-31 20:00 | 2020-10-31 | 20 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-10-31 21:00 | 2020-10-31 | 21 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-10-31 22:00 | 2020-10-31 | 22 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-10-31 23:00 | 2020-10-31 | 23 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-11-01 | 2020-10-31 | 0 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-11-01 01:00 | 2020-11-01 | 1 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-11-01 02:00 | 2020-11-01 | 2 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-11-01 03:00 | 2020-11-01 | 3 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-11-01 04:00 | 2020-11-01 | 4 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-11-01 05:00 | 2020-11-01 | 5 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-01 06:00 | 2020-11-01 | 6 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-11-01 07:00 | 2020-11-01 | 7 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-11-01 08:00 | 2020-11-01 | 8 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-11-01 09:00 | 2020-11-01 | 9 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-11-01 10:00 | 2020-11-01 | 10 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-11-01 11:00 | 2020-11-01 | 11 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-01 12:00 | 2020-11-01 | 12 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-01 13:00 | 2020-11-01 | 13 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-11-01 14:00 | 2020-11-01 | 14 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-11-01 15:00 | 2020-11-01 | 15 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-01 16:00 | 2020-11-01 | 16 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-01 17:00 | 2020-11-01 | 17 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-11-01 18:00 | 2020-11-01 | 18 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-11-01 19:00 | 2020-11-01 | 19 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-11-01 20:00 | 2020-11-01 | 20 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-11-01 21:00 | 2020-11-01 | 21 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-11-01 22:00 | 2020-11-01 | 22 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-01 23:00 | 2020-11-01 | 23 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-11-02 | 2020-11-01 | 0 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-11-02 01:00 | 2020-11-02 | 1 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-11-02 02:00 | 2020-11-02 | 2 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-11-02 03:00 | 2020-11-02 | 3 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-11-02 04:00 | 2020-11-02 | 4 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-11-02 05:00 | 2020-11-02 | 5 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-02 06:00 | 2020-11-02 | 6 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-11-02 07:00 | 2020-11-02 | 7 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-11-02 08:00 | 2020-11-02 | 8 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-02 09:00 | 2020-11-02 | 9 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-11-02 10:00 | 2020-11-02 | 10 | 4.2013 | 0.01459% | 6.264 | 6.4956 | 6.7358 | 6.9849 | 7.2432 | 0.52699 | 0.75862 | 0.99882 | 1.2479 | 1.5062 | 1
2020-11-02 11:00 | 2020-11-02 | 11 | 4.2164 | 0.01464% | 6.2864 | 6.5189 | 6.76 | 7.0099 | 7.2692 | 0.54944 | 0.78191 | 1.023 | 1.2729 | 1.5322 | 2
2020-11-02 12:00 | 2020-11-02 | 12 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 3
2020-11-02 13:00 | 2020-11-02 | 13 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 4
2020-11-02 14:00 | 2020-11-02 | 14 | 4.5175 | 0.01569% | 6.7355 | 6.9845 | 7.2428 | 7.5106 | 7.7884 | 0.99848 | 1.2475 | 1.5058 | 1.7736 | 2.0514 | 5
2020-11-02 15:00 | 2020-11-02 | 15 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 6
2020-11-02 16:00 | 2020-11-02 | 16 | 4.7434 | 0.01647% | 7.0722 | 7.3338 | 7.605 | 7.8862 | 8.1778 | 1.3352 | 1.5968 | 1.868 | 2.1492 | 2.4408 | 7
2020-11-02 17:00 | 2020-11-02 | 17 | 5.1274 | 0.0178% | 7.6448 | 7.9275 | 8.2206 | 8.5246 | 8.8398 | 1.9078 | 2.1905 | 2.4836 | 2.7876 | 3.1028 | 8
2020-11-02 18:00 | 2020-11-02 | 18 | 5.1952 | 0.01804% | 7.7458 | 8.0322 | 8.3292 | 8.6372 | 8.9566 | 2.0088 | 2.2952 | 2.5922 | 2.9002 | 3.2196 | 9
2020-11-02 19:00 | 2020-11-02 | 19 | 5.0521 | 0.01754% | 7.5325 | 7.811 | 8.0999 | 8.3994 | 8.71 | 1.7955 | 2.074 | 2.3629 | 2.6624 | 2.973 | 10
2020-11-02 20:00 | 2020-11-02 | 20 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 11
2020-11-02 21:00 | 2020-11-02 | 21 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 12
2020-11-02 22:00 | 2020-11-02 | 22 | 4.5025 | 0.01563% | 6.713 | 6.9613 | 7.2187 | 7.4856 | 7.7624 | 0.97602 | 1.2243 | 1.4817 | 1.7486 | 2.0254 | 13
2020-11-02 23:00 | 2020-11-02 | 23 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 14 | 14
2020-11-03 | 2020-11-02 | 0 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-11-03 01:00 | 2020-11-03 | 1 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-11-03 02:00 | 2020-11-03 | 2 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-11-03 03:00 | 2020-11-03 | 3 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-03 04:00 | 2020-11-03 | 4 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-11-03 05:00 | 2020-11-03 | 5 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-03 06:00 | 2020-11-03 | 6 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-11-03 07:00 | 2020-11-03 | 7 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 1
2020-11-03 08:00 | 2020-11-03 | 8 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 2
2020-11-03 09:00 | 2020-11-03 | 9 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 3
2020-11-03 10:00 | 2020-11-03 | 10 | 4.3594 | 0.01514% | 6.4997 | 6.7401 | 6.9893 | 7.2478 | 7.5158 | 0.76273 | 1.0031 | 1.2523 | 1.5108 | 1.7788 | 4
2020-11-03 11:00 | 2020-11-03 | 11 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 5
2020-11-03 12:00 | 2020-11-03 | 12 | 4.4347 | 0.0154% | 6.612 | 6.8565 | 7.11 | 7.373 | 7.6456 | 0.87499 | 1.1195 | 1.373 | 1.636 | 1.9086 | 6
2020-11-03 13:00 | 2020-11-03 | 13 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 7
2020-11-03 14:00 | 2020-11-03 | 14 | 4.4874 | 0.01558% | 6.6906 | 6.938 | 7.1945 | 7.4606 | 7.7365 | 0.95357 | 1.201 | 1.4575 | 1.7236 | 1.9995 | 8
2020-11-03 15:00 | 2020-11-03 | 15 | 4.4799 | 0.01556% | 6.6793 | 6.9263 | 7.1825 | 7.4481 | 7.7235 | 0.94235 | 1.1893 | 1.4455 | 1.7111 | 1.9865 | 9
2020-11-03 16:00 | 2020-11-03 | 16 | 4.51 | 0.01566% | 6.7242 | 6.9729 | 7.2307 | 7.4981 | 7.7754 | 0.98725 | 1.2359 | 1.4937 | 1.7611 | 2.0384 | 10
2020-11-03 17:00 | 2020-11-03 | 17 | 4.8789 | 0.01694% | 7.2743 | 7.5433 | 7.8222 | 8.1115 | 8.4114 | 1.5373 | 1.8063 | 2.0852 | 2.3745 | 2.6744 | 11
2020-11-03 18:00 | 2020-11-03 | 18 | 5.1575 | 0.01791% | 7.6897 | 7.974 | 8.2689 | 8.5747 | 8.8917 | 1.9527 | 2.237 | 2.5319 | 2.8377 | 3.1547 | 12
2020-11-03 19:00 | 2020-11-03 | 19 | 5.0446 | 0.01752% | 7.5213 | 7.7994 | 8.0878 | 8.3869 | 8.697 | 1.7843 | 2.0624 | 2.3508 | 2.6499 | 2.96 | 13
2020-11-03 20:00 | 2020-11-03 | 20 | 4.8262 | 0.01676% | 7.1957 | 7.4618 | 7.7377 | 8.0239 | 8.3206 | 1.4587 | 1.7248 | 2.0007 | 2.2869 | 2.5836 | 14
2020-11-03 21:00 | 2020-11-03 | 21 | 4.7585 | 0.01652% | 7.0947 | 7.3571 | 7.6291 | 7.9112 | 8.2038 | 1.3577 | 1.6201 | 1.8921 | 2.1742 | 2.4668 | 15
2020-11-03 22:00 | 2020-11-03 | 22 | 4.5251 | 0.01571% | 6.7467 | 6.9962 | 7.2549 | 7.5232 | 7.8014 | 1.0097 | 1.2592 | 1.5179 | 1.7862 | 2.0644 | 16
2020-11-03 23:00 | 2020-11-03 | 23 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 17 | 17
2020-11-04 | 2020-11-03 | 0 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-11-04 01:00 | 2020-11-04 | 1 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-11-04 02:00 | 2020-11-04 | 2 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-04 03:00 | 2020-11-04 | 3 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-04 04:00 | 2020-11-04 | 4 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-11-04 05:00 | 2020-11-04 | 5 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-04 06:00 | 2020-11-04 | 6 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-11-04 07:00 | 2020-11-04 | 7 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1
2020-11-04 08:00 | 2020-11-04 | 8 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 2
2020-11-04 09:00 | 2020-11-04 | 9 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 3
2020-11-04 10:00 | 2020-11-04 | 10 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 4
2020-11-04 11:00 | 2020-11-04 | 11 | 4.0959 | 0.01422% | 6.1068 | 6.3327 | 6.5668 | 6.8097 | 7.0615 | 0.36983 | 0.59565 | 0.82982 | 1.0727 | 1.3245 | 5
2020-11-04 12:00 | 2020-11-04 | 12 | 4.0733 | 0.01414% | 6.0732 | 6.2977 | 6.5306 | 6.7721 | 7.0225 | 0.33615 | 0.56073 | 0.79361 | 1.0351 | 1.2855 | 6
2020-11-04 13:00 | 2020-11-04 | 13 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 7
2020-11-04 14:00 | 2020-11-04 | 14 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 8
2020-11-04 15:00 | 2020-11-04 | 15 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 9
2020-11-04 16:00 | 2020-11-04 | 16 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 10
2020-11-04 17:00 | 2020-11-04 | 17 | 4.367 | 0.01516% | 6.511 | 6.7517 | 7.0014 | 7.2603 | 7.5288 | 0.77396 | 1.0147 | 1.2644 | 1.5233 | 1.7918 | 11
2020-11-04 18:00 | 2020-11-04 | 18 | 4.6982 | 0.01631% | 7.0049 | 7.2639 | 7.5325 | 7.8111 | 8.0999 | 1.2679 | 1.5269 | 1.7955 | 2.0741 | 2.3629 | 12
2020-11-04 19:00 | 2020-11-04 | 19 | 4.6756 | 0.01624% | 6.9712 | 7.229 | 7.4963 | 7.7735 | 8.061 | 1.2342 | 1.492 | 1.7593 | 2.0365 | 2.324 | 13
2020-11-04 20:00 | 2020-11-04 | 20 | 4.4724 | 0.01553% | 6.6681 | 6.9147 | 7.1704 | 7.4355 | 7.7105 | 0.93112 | 1.1777 | 1.4334 | 1.6985 | 1.9735 | 14
2020-11-04 21:00 | 2020-11-04 | 21 | 4.3444 | 0.01509% | 6.4773 | 6.7168 | 6.9652 | 7.2227 | 7.4898 | 0.74028 | 0.9798 | 1.2282 | 1.4857 | 1.7528 | 15
2020-11-04 22:00 | 2020-11-04 | 22 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 16 | 16
2020-11-04 23:00 | 2020-11-04 | 23 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-11-05 | 2020-11-04 | 0 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-11-05 01:00 | 2020-11-05 | 1 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-05 02:00 | 2020-11-05 | 2 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-05 03:00 | 2020-11-05 | 3 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-11-05 04:00 | 2020-11-05 | 4 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-11-05 05:00 | 2020-11-05 | 5 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-05 06:00 | 2020-11-05 | 6 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-05 07:00 | 2020-11-05 | 7 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-11-05 08:00 | 2020-11-05 | 8 | 3.8851 | 0.01349% | 5.7925 | 6.0067 | 6.2288 | 6.4592 | 6.698 | 0.055509 | 0.26971 | 0.49182 | 0.72216 | 0.96101 | 1 | 1
2020-11-05 09:00 | 2020-11-05 | 9 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-11-05 10:00 | 2020-11-05 | 10 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 1
2020-11-05 11:00 | 2020-11-05 | 11 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 2
2020-11-05 12:00 | 2020-11-05 | 12 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 3
2020-11-05 13:00 | 2020-11-05 | 13 | 4.0432 | 0.01404% | 6.0283 | 6.2512 | 6.4823 | 6.722 | 6.9706 | 0.29125 | 0.51417 | 0.74532 | 0.98503 | 1.2336 | 4
2020-11-05 14:00 | 2020-11-05 | 14 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 5
2020-11-05 15:00 | 2020-11-05 | 15 | 4.0131 | 0.01393% | 5.9833 | 6.2046 | 6.434 | 6.672 | 6.9187 | 0.24635 | 0.4676 | 0.69704 | 0.93496 | 1.1817 | 6
2020-11-05 16:00 | 2020-11-05 | 16 | 4.0281 | 0.01399% | 6.0058 | 6.2279 | 6.4582 | 6.697 | 6.9446 | 0.2688 | 0.49088 | 0.72118 | 0.95999 | 1.2076 | 7
2020-11-05 17:00 | 2020-11-05 | 17 | 4.3142 | 0.01498% | 6.4324 | 6.6702 | 6.9169 | 7.1727 | 7.4379 | 0.69538 | 0.93324 | 1.1799 | 1.4357 | 1.7009 | 8
2020-11-05 18:00 | 2020-11-05 | 18 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 9
2020-11-05 19:00 | 2020-11-05 | 19 | 4.4949 | 0.01561% | 6.7018 | 6.9496 | 7.2066 | 7.4731 | 7.7494 | 0.9648 | 1.2126 | 1.4696 | 1.7361 | 2.0124 | 10
2020-11-05 20:00 | 2020-11-05 | 20 | 4.3745 | 0.01519% | 6.5222 | 6.7634 | 7.0135 | 7.2728 | 7.5417 | 0.78519 | 1.0264 | 1.2765 | 1.5358 | 1.8047 | 11
2020-11-05 21:00 | 2020-11-05 | 21 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 12
2020-11-05 22:00 | 2020-11-05 | 22 | 4.0808 | 0.01417% | 6.0844 | 6.3094 | 6.5427 | 6.7846 | 7.0355 | 0.34738 | 0.57237 | 0.80568 | 1.0476 | 1.2985 | 13 | 13
2020-11-05 23:00 | 2020-11-05 | 23 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-11-06 | 2020-11-05 | 0 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-06 01:00 | 2020-11-06 | 1 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-06 02:00 | 2020-11-06 | 2 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-11-06 03:00 | 2020-11-06 | 3 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-11-06 04:00 | 2020-11-06 | 4 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-11-06 05:00 | 2020-11-06 | 5 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-06 06:00 | 2020-11-06 | 6 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-06 07:00 | 2020-11-06 | 7 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-11-06 08:00 | 2020-11-06 | 8 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-11-06 09:00 | 2020-11-06 | 9 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-11-06 10:00 | 2020-11-06 | 10 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-11-06 11:00 | 2020-11-06 | 11 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-11-06 12:00 | 2020-11-06 | 12 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 1
2020-11-06 13:00 | 2020-11-06 | 13 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 2
2020-11-06 14:00 | 2020-11-06 | 14 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 3
2020-11-06 15:00 | 2020-11-06 | 15 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 4
2020-11-06 16:00 | 2020-11-06 | 16 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 5
2020-11-06 17:00 | 2020-11-06 | 17 | 4.3067 | 0.01495% | 6.4212 | 6.6586 | 6.9048 | 7.1602 | 7.4249 | 0.68415 | 0.9216 | 1.1678 | 1.4232 | 1.6879 | 6
2020-11-06 18:00 | 2020-11-06 | 18 | 4.6154 | 0.01603% | 6.8814 | 7.1359 | 7.3997 | 7.6734 | 7.9571 | 1.1444 | 1.3989 | 1.6627 | 1.9364 | 2.2201 | 7
2020-11-06 19:00 | 2020-11-06 | 19 | 4.4648 | 0.0155% | 6.6569 | 6.9031 | 7.1583 | 7.423 | 7.6975 | 0.91989 | 1.1661 | 1.4213 | 1.686 | 1.9605 | 8
2020-11-06 20:00 | 2020-11-06 | 20 | 4.254 | 0.01477% | 6.3426 | 6.5771 | 6.8203 | 7.0725 | 7.3341 | 0.60557 | 0.84011 | 1.0833 | 1.3355 | 1.5971 | 9
2020-11-06 21:00 | 2020-11-06 | 21 | 4.1712 | 0.01448% | 6.2191 | 6.4491 | 6.6875 | 6.9348 | 7.1913 | 0.48209 | 0.71206 | 0.95054 | 1.1978 | 1.4543 | 10
2020-11-06 22:00 | 2020-11-06 | 22 | 3.9303 | 0.01365% | 5.8599 | 6.0766 | 6.3013 | 6.5343 | 6.7759 | 0.12286 | 0.33955 | 0.56425 | 0.79726 | 1.0389 | 11 | 11
2020-11-06 23:00 | 2020-11-06 | 23 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-11-07 | 2020-11-06 | 0 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-07 01:00 | 2020-11-07 | 1 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-11-07 02:00 | 2020-11-07 | 2 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-07 03:00 | 2020-11-07 | 3 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-11-07 04:00 | 2020-11-07 | 4 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-11-07 05:00 | 2020-11-07 | 5 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-11-07 06:00 | 2020-11-07 | 6 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-11-07 07:00 | 2020-11-07 | 7 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-07 08:00 | 2020-11-07 | 8 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-11-07 09:00 | 2020-11-07 | 9 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-11-07 10:00 | 2020-11-07 | 10 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-11-07 11:00 | 2020-11-07 | 11 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-11-07 12:00 | 2020-11-07 | 12 | 3.9378 | 0.01367% | 5.8711 | 6.0882 | 6.3133 | 6.5468 | 6.7889 | 0.13409 | 0.35119 | 0.57632 | 0.80978 | 1.0519 | 1
2020-11-07 13:00 | 2020-11-07 | 13 | 3.9227 | 0.01362% | 5.8486 | 6.0649 | 6.2892 | 6.5217 | 6.7629 | 0.11164 | 0.32791 | 0.55218 | 0.78475 | 1.0259 | 2
2020-11-07 14:00 | 2020-11-07 | 14 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 3
2020-11-07 15:00 | 2020-11-07 | 15 | 3.9528 | 0.01373% | 5.8935 | 6.1115 | 6.3375 | 6.5718 | 6.8148 | 0.15654 | 0.37447 | 0.60047 | 0.83482 | 1.0778 | 4
2020-11-07 16:00 | 2020-11-07 | 16 | 3.9905 | 0.01386% | 5.9497 | 6.1697 | 6.3978 | 6.6344 | 6.8797 | 0.21267 | 0.43268 | 0.66082 | 0.89741 | 1.1427 | 5
2020-11-07 17:00 | 2020-11-07 | 17 | 4.3895 | 0.01524% | 6.5446 | 6.7866 | 7.0376 | 7.2978 | 7.5677 | 0.80764 | 1.0496 | 1.3006 | 1.5608 | 1.8307 | 6
2020-11-07 18:00 | 2020-11-07 | 18 | 4.6004 | 0.01597% | 6.859 | 7.1126 | 7.3756 | 7.6483 | 7.9312 | 1.122 | 1.3756 | 1.6386 | 1.9113 | 2.1942 | 7
2020-11-07 19:00 | 2020-11-07 | 19 | 4.5928 | 0.01595% | 6.8477 | 7.101 | 7.3635 | 7.6358 | 7.9182 | 1.1107 | 1.364 | 1.6265 | 1.8988 | 2.1812 | 8
2020-11-07 20:00 | 2020-11-07 | 20 | 4.4121 | 0.01532% | 6.5783 | 6.8216 | 7.0738 | 7.3354 | 7.6067 | 0.84131 | 1.0846 | 1.3368 | 1.5984 | 1.8697 | 9
2020-11-07 21:00 | 2020-11-07 | 21 | 4.1486 | 0.01441% | 6.1854 | 6.4141 | 6.6513 | 6.8973 | 7.1523 | 0.44841 | 0.67714 | 0.91432 | 1.1603 | 1.4153 | 10 | 10
2020-11-07 22:00 | 2020-11-07 | 22 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-11-07 23:00 | 2020-11-07 | 23 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-11-08 | 2020-11-07 | 0 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-08 01:00 | 2020-11-08 | 1 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-11-08 02:00 | 2020-11-08 | 2 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-11-08 03:00 | 2020-11-08 | 3 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-11-08 04:00 | 2020-11-08 | 4 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-11-08 05:00 | 2020-11-08 | 5 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-11-08 06:00 | 2020-11-08 | 6 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-08 07:00 | 2020-11-08 | 7 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-11-08 08:00 | 2020-11-08 | 8 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-11-08 09:00 | 2020-11-08 | 9 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-11-08 10:00 | 2020-11-08 | 10 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-11-08 11:00 | 2020-11-08 | 11 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-11-08 12:00 | 2020-11-08 | 12 | 3.8776 | 0.01346% | 5.7813 | 5.9951 | 6.2168 | 6.4466 | 6.685 | 0.044283 | 0.25807 | 0.47975 | 0.70964 | 0.94803 | 1
2020-11-08 13:00 | 2020-11-08 | 13 | 4.0507 | 0.01407% | 6.0395 | 6.2628 | 6.4944 | 6.7345 | 6.9836 | 0.30248 | 0.52581 | 0.75739 | 0.99755 | 1.2466 | 2
2020-11-08 14:00 | 2020-11-08 | 14 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 3
2020-11-08 15:00 | 2020-11-08 | 15 | 3.9754 | 0.0138% | 5.9272 | 6.1464 | 6.3737 | 6.6094 | 6.8538 | 0.19022 | 0.4094 | 0.63668 | 0.87237 | 1.1168 | 4
2020-11-08 16:00 | 2020-11-08 | 16 | 4.1335 | 0.01435% | 6.163 | 6.3909 | 6.6272 | 6.8722 | 7.1264 | 0.42596 | 0.65386 | 0.89018 | 1.1352 | 1.3894 | 5
2020-11-08 17:00 | 2020-11-08 | 17 | 4.4046 | 0.01529% | 6.5671 | 6.8099 | 7.0617 | 7.3229 | 7.5937 | 0.83009 | 1.0729 | 1.3247 | 1.5859 | 1.8567 | 6
2020-11-08 18:00 | 2020-11-08 | 18 | 4.7961 | 0.01665% | 7.1508 | 7.4153 | 7.6895 | 7.9738 | 8.2687 | 1.4138 | 1.6783 | 1.9525 | 2.2368 | 2.5317 | 7
2020-11-08 19:00 | 2020-11-08 | 19 | 4.6455 | 0.01613% | 6.9263 | 7.1824 | 7.448 | 7.7234 | 8.009 | 1.1893 | 1.4454 | 1.711 | 1.9864 | 2.272 | 8
2020-11-08 20:00 | 2020-11-08 | 20 | 4.2841 | 0.01488% | 6.3875 | 6.6237 | 6.8686 | 7.1226 | 7.386 | 0.65048 | 0.88667 | 1.1316 | 1.3856 | 1.649 | 9
2020-11-08 21:00 | 2020-11-08 | 21 | 4.0206 | 0.01396% | 5.9946 | 6.2162 | 6.4461 | 6.6845 | 6.9317 | 0.25757 | 0.47924 | 0.70911 | 0.94748 | 1.1947 | 10 | 10
2020-11-08 22:00 | 2020-11-08 | 22 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-11-08 23:00 | 2020-11-08 | 23 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-11-09 | 2020-11-08 | 0 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-11-09 01:00 | 2020-11-09 | 1 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-11-09 02:00 | 2020-11-09 | 2 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-11-09 03:00 | 2020-11-09 | 3 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-11-09 04:00 | 2020-11-09 | 4 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-11-09 05:00 | 2020-11-09 | 5 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-11-09 06:00 | 2020-11-09 | 6 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-11-09 07:00 | 2020-11-09 | 7 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-11-09 08:00 | 2020-11-09 | 8 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-11-09 09:00 | 2020-11-09 | 9 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-11-09 10:00 | 2020-11-09 | 10 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-11-09 11:00 | 2020-11-09 | 11 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-11-09 12:00 | 2020-11-09 | 12 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-11-09 13:00 | 2020-11-09 | 13 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-09 14:00 | 2020-11-09 | 14 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-11-09 15:00 | 2020-11-09 | 15 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-11-09 16:00 | 2020-11-09 | 16 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-09 17:00 | 2020-11-09 | 17 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-09 18:00 | 2020-11-09 | 18 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-09 19:00 | 2020-11-09 | 19 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-09 20:00 | 2020-11-09 | 20 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-11-09 21:00 | 2020-11-09 | 21 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-11-09 22:00 | 2020-11-09 | 22 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-09 23:00 | 2020-11-09 | 23 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-11-10 | 2020-11-09 | 0 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-11-10 01:00 | 2020-11-10 | 1 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-11-10 02:00 | 2020-11-10 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-10 03:00 | 2020-11-10 | 3 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-11-10 04:00 | 2020-11-10 | 4 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-10 05:00 | 2020-11-10 | 5 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-11-10 06:00 | 2020-11-10 | 6 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-11-10 07:00 | 2020-11-10 | 7 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-11-10 08:00 | 2020-11-10 | 8 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-11-10 09:00 | 2020-11-10 | 9 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-11-10 10:00 | 2020-11-10 | 10 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-11-10 11:00 | 2020-11-10 | 11 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-10 12:00 | 2020-11-10 | 12 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-11-10 13:00 | 2020-11-10 | 13 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-11-10 14:00 | 2020-11-10 | 14 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-11-10 15:00 | 2020-11-10 | 15 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-11-10 16:00 | 2020-11-10 | 16 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-10 17:00 | 2020-11-10 | 17 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-11-10 18:00 | 2020-11-10 | 18 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-11-10 19:00 | 2020-11-10 | 19 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-10 20:00 | 2020-11-10 | 20 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-11-10 21:00 | 2020-11-10 | 21 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-11-10 22:00 | 2020-11-10 | 22 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-10 23:00 | 2020-11-10 | 23 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-11-11 | 2020-11-10 | 0 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-11-11 01:00 | 2020-11-11 | 1 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-11-11 02:00 | 2020-11-11 | 2 | 2.1007 | 0.007294% | 3.132 | 3.2478 | 3.3679 | 3.4925 | 3.6216 | 0 | 0 | 0 | 0 | 0
2020-11-11 03:00 | 2020-11-11 | 3 | 2.1232 | 0.007373% | 3.1657 | 3.2827 | 3.4041 | 3.53 | 3.6605 | 0 | 0 | 0 | 0 | 0
2020-11-11 04:00 | 2020-11-11 | 4 | 2.0856 | 0.007242% | 3.1095 | 3.2245 | 3.3438 | 3.4674 | 3.5956 | 0 | 0 | 0 | 0 | 0
2020-11-11 05:00 | 2020-11-11 | 5 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-11-11 06:00 | 2020-11-11 | 6 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-11-11 07:00 | 2020-11-11 | 7 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-11-11 08:00 | 2020-11-11 | 8 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-11-11 09:00 | 2020-11-11 | 9 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-11 10:00 | 2020-11-11 | 10 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-11-11 11:00 | 2020-11-11 | 11 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-11-11 12:00 | 2020-11-11 | 12 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-11-11 13:00 | 2020-11-11 | 13 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-11-11 14:00 | 2020-11-11 | 14 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-11-11 15:00 | 2020-11-11 | 15 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-11 16:00 | 2020-11-11 | 16 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-11 17:00 | 2020-11-11 | 17 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-11-11 18:00 | 2020-11-11 | 18 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-11-11 19:00 | 2020-11-11 | 19 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-11 20:00 | 2020-11-11 | 20 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-11 21:00 | 2020-11-11 | 21 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-11-11 22:00 | 2020-11-11 | 22 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-11-11 23:00 | 2020-11-11 | 23 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-11-12 | 2020-11-11 | 0 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-11-12 01:00 | 2020-11-12 | 1 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-12 02:00 | 2020-11-12 | 2 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-12 03:00 | 2020-11-12 | 3 | 2.2512 | 0.007817% | 3.3565 | 3.4806 | 3.6093 | 3.7428 | 3.8812 | 0 | 0 | 0 | 0 | 0
2020-11-12 04:00 | 2020-11-12 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-11-12 05:00 | 2020-11-12 | 5 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-11-12 06:00 | 2020-11-12 | 6 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-11-12 07:00 | 2020-11-12 | 7 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-11-12 08:00 | 2020-11-12 | 8 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-11-12 09:00 | 2020-11-12 | 9 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-11-12 10:00 | 2020-11-12 | 10 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-12 11:00 | 2020-11-12 | 11 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-11-12 12:00 | 2020-11-12 | 12 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-11-12 13:00 | 2020-11-12 | 13 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-12 14:00 | 2020-11-12 | 14 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-11-12 15:00 | 2020-11-12 | 15 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-11-12 16:00 | 2020-11-12 | 16 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-11-12 17:00 | 2020-11-12 | 17 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-12 18:00 | 2020-11-12 | 18 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-11-12 19:00 | 2020-11-12 | 19 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-11-12 20:00 | 2020-11-12 | 20 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-11-12 21:00 | 2020-11-12 | 21 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-11-12 22:00 | 2020-11-12 | 22 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-11-12 23:00 | 2020-11-12 | 23 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-11-13 | 2020-11-12 | 0 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-11-13 01:00 | 2020-11-13 | 1 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-11-13 02:00 | 2020-11-13 | 2 | 2.1835 | 0.007582% | 3.2555 | 3.3759 | 3.5007 | 3.6301 | 3.7644 | 0 | 0 | 0 | 0 | 0
2020-11-13 03:00 | 2020-11-13 | 3 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-11-13 04:00 | 2020-11-13 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-11-13 05:00 | 2020-11-13 | 5 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-11-13 06:00 | 2020-11-13 | 6 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-11-13 07:00 | 2020-11-13 | 7 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-11-13 08:00 | 2020-11-13 | 8 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-11-13 09:00 | 2020-11-13 | 9 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-13 10:00 | 2020-11-13 | 10 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-13 11:00 | 2020-11-13 | 11 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-11-13 12:00 | 2020-11-13 | 12 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-11-13 13:00 | 2020-11-13 | 13 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-13 14:00 | 2020-11-13 | 14 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-11-13 15:00 | 2020-11-13 | 15 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-11-13 16:00 | 2020-11-13 | 16 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-13 17:00 | 2020-11-13 | 17 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-13 18:00 | 2020-11-13 | 18 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-11-13 19:00 | 2020-11-13 | 19 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-11-13 20:00 | 2020-11-13 | 20 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-11-13 21:00 | 2020-11-13 | 21 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-11-13 22:00 | 2020-11-13 | 22 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-11-13 23:00 | 2020-11-13 | 23 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-11-14 | 2020-11-13 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-14 01:00 | 2020-11-14 | 1 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-11-14 02:00 | 2020-11-14 | 2 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-11-14 03:00 | 2020-11-14 | 3 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-11-14 04:00 | 2020-11-14 | 4 | 2.1458 | 0.007451% | 3.1994 | 3.3177 | 3.4403 | 3.5676 | 3.6995 | 0 | 0 | 0 | 0 | 0
2020-11-14 05:00 | 2020-11-14 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-11-14 06:00 | 2020-11-14 | 6 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-14 07:00 | 2020-11-14 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-11-14 08:00 | 2020-11-14 | 8 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-11-14 09:00 | 2020-11-14 | 9 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-11-14 10:00 | 2020-11-14 | 10 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-11-14 11:00 | 2020-11-14 | 11 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-11-14 12:00 | 2020-11-14 | 12 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-11-14 13:00 | 2020-11-14 | 13 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-14 14:00 | 2020-11-14 | 14 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-11-14 15:00 | 2020-11-14 | 15 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-11-14 16:00 | 2020-11-14 | 16 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-14 17:00 | 2020-11-14 | 17 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-11-14 18:00 | 2020-11-14 | 18 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-11-14 19:00 | 2020-11-14 | 19 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-11-14 20:00 | 2020-11-14 | 20 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-11-14 21:00 | 2020-11-14 | 21 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-11-14 22:00 | 2020-11-14 | 22 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-11-14 23:00 | 2020-11-14 | 23 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-11-15 | 2020-11-14 | 0 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-11-15 01:00 | 2020-11-15 | 1 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-11-15 02:00 | 2020-11-15 | 2 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-15 03:00 | 2020-11-15 | 3 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-11-15 04:00 | 2020-11-15 | 4 | 2.1684 | 0.00753% | 3.233 | 3.3526 | 3.4766 | 3.6051 | 3.7384 | 0 | 0 | 0 | 0 | 0
2020-11-15 05:00 | 2020-11-15 | 5 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-11-15 06:00 | 2020-11-15 | 6 | 2.1759 | 0.007556% | 3.2443 | 3.3642 | 3.4886 | 3.6176 | 3.7514 | 0 | 0 | 0 | 0 | 0
2020-11-15 07:00 | 2020-11-15 | 7 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-11-15 08:00 | 2020-11-15 | 8 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-11-15 09:00 | 2020-11-15 | 9 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-11-15 10:00 | 2020-11-15 | 10 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-15 11:00 | 2020-11-15 | 11 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-15 12:00 | 2020-11-15 | 12 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-15 13:00 | 2020-11-15 | 13 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-15 14:00 | 2020-11-15 | 14 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-11-15 15:00 | 2020-11-15 | 15 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-11-15 16:00 | 2020-11-15 | 16 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-11-15 17:00 | 2020-11-15 | 17 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-11-15 18:00 | 2020-11-15 | 18 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-11-15 19:00 | 2020-11-15 | 19 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-11-15 20:00 | 2020-11-15 | 20 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-11-15 21:00 | 2020-11-15 | 21 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-11-15 22:00 | 2020-11-15 | 22 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-11-15 23:00 | 2020-11-15 | 23 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-11-16 | 2020-11-15 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-16 01:00 | 2020-11-16 | 1 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-11-16 02:00 | 2020-11-16 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-16 03:00 | 2020-11-16 | 3 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-16 04:00 | 2020-11-16 | 4 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-16 05:00 | 2020-11-16 | 5 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-11-16 06:00 | 2020-11-16 | 6 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-11-16 07:00 | 2020-11-16 | 7 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-11-16 08:00 | 2020-11-16 | 8 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-11-16 09:00 | 2020-11-16 | 9 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-11-16 10:00 | 2020-11-16 | 10 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-11-16 11:00 | 2020-11-16 | 11 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-16 12:00 | 2020-11-16 | 12 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-16 13:00 | 2020-11-16 | 13 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-11-16 14:00 | 2020-11-16 | 14 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-11-16 15:00 | 2020-11-16 | 15 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-16 16:00 | 2020-11-16 | 16 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-16 17:00 | 2020-11-16 | 17 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-11-16 18:00 | 2020-11-16 | 18 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-11-16 19:00 | 2020-11-16 | 19 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-11-16 20:00 | 2020-11-16 | 20 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-16 21:00 | 2020-11-16 | 21 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-11-16 22:00 | 2020-11-16 | 22 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-11-16 23:00 | 2020-11-16 | 23 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-11-17 | 2020-11-16 | 0 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-11-17 01:00 | 2020-11-17 | 1 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-11-17 02:00 | 2020-11-17 | 2 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-11-17 03:00 | 2020-11-17 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-11-17 04:00 | 2020-11-17 | 4 | 2.3039 | 0.008% | 3.4351 | 3.5621 | 3.6938 | 3.8304 | 3.9721 | 0 | 0 | 0 | 0 | 0
2020-11-17 05:00 | 2020-11-17 | 5 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-11-17 06:00 | 2020-11-17 | 6 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-11-17 07:00 | 2020-11-17 | 7 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-11-17 08:00 | 2020-11-17 | 8 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-11-17 09:00 | 2020-11-17 | 9 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-11-17 10:00 | 2020-11-17 | 10 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-17 11:00 | 2020-11-17 | 11 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-11-17 12:00 | 2020-11-17 | 12 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-11-17 13:00 | 2020-11-17 | 13 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-17 14:00 | 2020-11-17 | 14 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-11-17 15:00 | 2020-11-17 | 15 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-17 16:00 | 2020-11-17 | 16 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-17 17:00 | 2020-11-17 | 17 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-11-17 18:00 | 2020-11-17 | 18 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-11-17 19:00 | 2020-11-17 | 19 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-11-17 20:00 | 2020-11-17 | 20 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-11-17 21:00 | 2020-11-17 | 21 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-11-17 22:00 | 2020-11-17 | 22 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-17 23:00 | 2020-11-17 | 23 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-11-18 | 2020-11-17 | 0 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-11-18 01:00 | 2020-11-18 | 1 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-11-18 02:00 | 2020-11-18 | 2 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-11-18 03:00 | 2020-11-18 | 3 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-11-18 04:00 | 2020-11-18 | 4 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-11-18 05:00 | 2020-11-18 | 5 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-11-18 06:00 | 2020-11-18 | 6 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-11-18 07:00 | 2020-11-18 | 7 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-11-18 08:00 | 2020-11-18 | 8 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-11-18 09:00 | 2020-11-18 | 9 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-18 10:00 | 2020-11-18 | 10 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-11-18 11:00 | 2020-11-18 | 11 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-18 12:00 | 2020-11-18 | 12 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 13:00 | 2020-11-18 | 13 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 14:00 | 2020-11-18 | 14 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 15:00 | 2020-11-18 | 15 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 16:00 | 2020-11-18 | 16 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 17:00 | 2020-11-18 | 17 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 18:00 | 2020-11-18 | 18 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 19:00 | 2020-11-18 | 19 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-18 20:00 | 2020-11-18 | 20 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-11-18 21:00 | 2020-11-18 | 21 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-11-18 22:00 | 2020-11-18 | 22 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-18 23:00 | 2020-11-18 | 23 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-11-19 | 2020-11-18 | 0 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-11-19 01:00 | 2020-11-19 | 1 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-11-19 02:00 | 2020-11-19 | 2 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-11-19 03:00 | 2020-11-19 | 3 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-11-19 04:00 | 2020-11-19 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-11-19 05:00 | 2020-11-19 | 5 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-19 06:00 | 2020-11-19 | 6 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-11-19 07:00 | 2020-11-19 | 7 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-11-19 08:00 | 2020-11-19 | 8 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-19 09:00 | 2020-11-19 | 9 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-11-19 10:00 | 2020-11-19 | 10 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-19 11:00 | 2020-11-19 | 11 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-19 12:00 | 2020-11-19 | 12 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-11-19 13:00 | 2020-11-19 | 13 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-19 14:00 | 2020-11-19 | 14 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-19 15:00 | 2020-11-19 | 15 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-19 16:00 | 2020-11-19 | 16 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-19 17:00 | 2020-11-19 | 17 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-11-19 18:00 | 2020-11-19 | 18 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-11-19 19:00 | 2020-11-19 | 19 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-11-19 20:00 | 2020-11-19 | 20 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-19 21:00 | 2020-11-19 | 21 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-11-19 22:00 | 2020-11-19 | 22 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-11-19 23:00 | 2020-11-19 | 23 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-11-20 | 2020-11-19 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-11-20 01:00 | 2020-11-20 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-11-20 02:00 | 2020-11-20 | 2 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-20 03:00 | 2020-11-20 | 3 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-20 04:00 | 2020-11-20 | 4 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-11-20 05:00 | 2020-11-20 | 5 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-11-20 06:00 | 2020-11-20 | 6 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-11-20 07:00 | 2020-11-20 | 7 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-11-20 08:00 | 2020-11-20 | 8 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-11-20 09:00 | 2020-11-20 | 9 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-11-20 10:00 | 2020-11-20 | 10 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-11-20 11:00 | 2020-11-20 | 11 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-11-20 12:00 | 2020-11-20 | 12 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-11-20 13:00 | 2020-11-20 | 13 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-20 14:00 | 2020-11-20 | 14 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-11-20 15:00 | 2020-11-20 | 15 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-11-20 16:00 | 2020-11-20 | 16 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-20 17:00 | 2020-11-20 | 17 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-11-20 18:00 | 2020-11-20 | 18 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-11-20 19:00 | 2020-11-20 | 19 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-20 20:00 | 2020-11-20 | 20 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-20 21:00 | 2020-11-20 | 21 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-20 22:00 | 2020-11-20 | 22 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-20 23:00 | 2020-11-20 | 23 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-11-21 | 2020-11-20 | 0 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-11-21 01:00 | 2020-11-21 | 1 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-11-21 02:00 | 2020-11-21 | 2 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-11-21 03:00 | 2020-11-21 | 3 | 2.1609 | 0.007503% | 3.2218 | 3.3409 | 3.4645 | 3.5926 | 3.7254 | 0 | 0 | 0 | 0 | 0
2020-11-21 04:00 | 2020-11-21 | 4 | 2.1534 | 0.007477% | 3.2106 | 3.3293 | 3.4524 | 3.5801 | 3.7125 | 0 | 0 | 0 | 0 | 0
2020-11-21 05:00 | 2020-11-21 | 5 | 2.191 | 0.007608% | 3.2667 | 3.3875 | 3.5128 | 3.6427 | 3.7774 | 0 | 0 | 0 | 0 | 0
2020-11-21 06:00 | 2020-11-21 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-11-21 07:00 | 2020-11-21 | 7 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-11-21 08:00 | 2020-11-21 | 8 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-11-21 09:00 | 2020-11-21 | 9 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-11-21 10:00 | 2020-11-21 | 10 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-11-21 11:00 | 2020-11-21 | 11 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-11-21 12:00 | 2020-11-21 | 12 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-21 13:00 | 2020-11-21 | 13 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-11-21 14:00 | 2020-11-21 | 14 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-21 15:00 | 2020-11-21 | 15 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-21 16:00 | 2020-11-21 | 16 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-21 17:00 | 2020-11-21 | 17 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-11-21 18:00 | 2020-11-21 | 18 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-11-21 19:00 | 2020-11-21 | 19 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-11-21 20:00 | 2020-11-21 | 20 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-21 21:00 | 2020-11-21 | 21 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-21 22:00 | 2020-11-21 | 22 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-11-21 23:00 | 2020-11-21 | 23 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-11-22 | 2020-11-21 | 0 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-11-22 01:00 | 2020-11-22 | 1 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-11-22 02:00 | 2020-11-22 | 2 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-22 03:00 | 2020-11-22 | 3 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-22 04:00 | 2020-11-22 | 4 | 2.2211 | 0.007713% | 3.3116 | 3.4341 | 3.5611 | 3.6927 | 3.8293 | 0 | 0 | 0 | 0 | 0
2020-11-22 05:00 | 2020-11-22 | 5 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-22 06:00 | 2020-11-22 | 6 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-22 07:00 | 2020-11-22 | 7 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-11-22 08:00 | 2020-11-22 | 8 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-11-22 09:00 | 2020-11-22 | 9 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-11-22 10:00 | 2020-11-22 | 10 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-11-22 11:00 | 2020-11-22 | 11 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-11-22 12:00 | 2020-11-22 | 12 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-11-22 13:00 | 2020-11-22 | 13 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-11-22 14:00 | 2020-11-22 | 14 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-11-22 15:00 | 2020-11-22 | 15 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-11-22 16:00 | 2020-11-22 | 16 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-11-22 17:00 | 2020-11-22 | 17 | 3.7496 | 0.01302% | 5.5904 | 5.7972 | 6.0115 | 6.2338 | 6.4644 | 0 | 0.06017 | 0.27454 | 0.49684 | 0.72735
2020-11-22 18:00 | 2020-11-22 | 18 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-11-22 19:00 | 2020-11-22 | 19 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-11-22 20:00 | 2020-11-22 | 20 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-22 21:00 | 2020-11-22 | 21 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-22 22:00 | 2020-11-22 | 22 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-11-22 23:00 | 2020-11-22 | 23 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-11-23 | 2020-11-22 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-23 01:00 | 2020-11-23 | 1 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-11-23 02:00 | 2020-11-23 | 2 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-11-23 03:00 | 2020-11-23 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-11-23 04:00 | 2020-11-23 | 4 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-11-23 05:00 | 2020-11-23 | 5 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-11-23 06:00 | 2020-11-23 | 6 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-11-23 07:00 | 2020-11-23 | 7 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-11-23 08:00 | 2020-11-23 | 8 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-11-23 09:00 | 2020-11-23 | 9 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-11-23 10:00 | 2020-11-23 | 10 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-23 11:00 | 2020-11-23 | 11 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-11-23 12:00 | 2020-11-23 | 12 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-11-23 13:00 | 2020-11-23 | 13 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-11-23 14:00 | 2020-11-23 | 14 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-11-23 15:00 | 2020-11-23 | 15 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-23 16:00 | 2020-11-23 | 16 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-11-23 17:00 | 2020-11-23 | 17 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-11-23 18:00 | 2020-11-23 | 18 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-11-23 19:00 | 2020-11-23 | 19 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-11-23 20:00 | 2020-11-23 | 20 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-11-23 21:00 | 2020-11-23 | 21 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-11-23 22:00 | 2020-11-23 | 22 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-23 23:00 | 2020-11-23 | 23 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-11-24 | 2020-11-23 | 0 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-11-24 01:00 | 2020-11-24 | 1 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-11-24 02:00 | 2020-11-24 | 2 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-11-24 03:00 | 2020-11-24 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-11-24 04:00 | 2020-11-24 | 4 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-11-24 05:00 | 2020-11-24 | 5 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-11-24 06:00 | 2020-11-24 | 6 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-11-24 07:00 | 2020-11-24 | 7 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-11-24 08:00 | 2020-11-24 | 8 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-11-24 09:00 | 2020-11-24 | 9 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-24 10:00 | 2020-11-24 | 10 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-11-24 11:00 | 2020-11-24 | 11 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-11-24 12:00 | 2020-11-24 | 12 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-11-24 13:00 | 2020-11-24 | 13 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-11-24 14:00 | 2020-11-24 | 14 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-24 15:00 | 2020-11-24 | 15 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-24 16:00 | 2020-11-24 | 16 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-11-24 17:00 | 2020-11-24 | 17 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-11-24 18:00 | 2020-11-24 | 18 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-11-24 19:00 | 2020-11-24 | 19 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-11-24 20:00 | 2020-11-24 | 20 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-11-24 21:00 | 2020-11-24 | 21 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-11-24 22:00 | 2020-11-24 | 22 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-11-24 23:00 | 2020-11-24 | 23 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-11-25 | 2020-11-24 | 0 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-11-25 01:00 | 2020-11-25 | 1 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-11-25 02:00 | 2020-11-25 | 2 | 2.5373 | 0.008811% | 3.7831 | 3.923 | 4.0681 | 4.2185 | 4.3745 | 0 | 0 | 0 | 0 | 0
2020-11-25 03:00 | 2020-11-25 | 3 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-11-25 04:00 | 2020-11-25 | 4 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-11-25 05:00 | 2020-11-25 | 5 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-11-25 06:00 | 2020-11-25 | 6 | 2.6804 | 0.009307% | 3.9964 | 4.1442 | 4.2974 | 4.4563 | 4.6211 | 0 | 0 | 0 | 0 | 0
2020-11-25 07:00 | 2020-11-25 | 7 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-11-25 08:00 | 2020-11-25 | 8 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-25 09:00 | 2020-11-25 | 9 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-11-25 10:00 | 2020-11-25 | 10 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-25 11:00 | 2020-11-25 | 11 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-11-25 12:00 | 2020-11-25 | 12 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-11-25 13:00 | 2020-11-25 | 13 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-25 14:00 | 2020-11-25 | 14 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-25 15:00 | 2020-11-25 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-25 16:00 | 2020-11-25 | 16 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-25 17:00 | 2020-11-25 | 17 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-11-25 18:00 | 2020-11-25 | 18 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-11-25 19:00 | 2020-11-25 | 19 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-11-25 20:00 | 2020-11-25 | 20 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-11-25 21:00 | 2020-11-25 | 21 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-11-25 22:00 | 2020-11-25 | 22 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-25 23:00 | 2020-11-25 | 23 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-11-26 | 2020-11-25 | 0 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-11-26 01:00 | 2020-11-26 | 1 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-11-26 02:00 | 2020-11-26 | 2 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-11-26 03:00 | 2020-11-26 | 3 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-26 04:00 | 2020-11-26 | 4 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-11-26 05:00 | 2020-11-26 | 5 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-11-26 06:00 | 2020-11-26 | 6 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-11-26 07:00 | 2020-11-26 | 7 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-11-26 08:00 | 2020-11-26 | 8 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-11-26 09:00 | 2020-11-26 | 9 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-11-26 10:00 | 2020-11-26 | 10 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-11-26 11:00 | 2020-11-26 | 11 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-11-26 12:00 | 2020-11-26 | 12 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-26 13:00 | 2020-11-26 | 13 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-11-26 14:00 | 2020-11-26 | 14 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-26 15:00 | 2020-11-26 | 15 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-11-26 16:00 | 2020-11-26 | 16 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-11-26 17:00 | 2020-11-26 | 17 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-11-26 18:00 | 2020-11-26 | 18 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-11-26 19:00 | 2020-11-26 | 19 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-11-26 20:00 | 2020-11-26 | 20 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-11-26 21:00 | 2020-11-26 | 21 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-26 22:00 | 2020-11-26 | 22 | 3.0945 | 0.01075% | 4.6138 | 4.7844 | 4.9613 | 5.1448 | 5.335 | 0 | 0 | 0 | 0 | 0
2020-11-26 23:00 | 2020-11-26 | 23 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-11-27 | 2020-11-26 | 0 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-11-27 01:00 | 2020-11-27 | 1 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-11-27 02:00 | 2020-11-27 | 2 | 2.2287 | 0.007739% | 3.3228 | 3.4457 | 3.5731 | 3.7053 | 3.8423 | 0 | 0 | 0 | 0 | 0
2020-11-27 03:00 | 2020-11-27 | 3 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-11-27 04:00 | 2020-11-27 | 4 | 2.1985 | 0.007634% | 3.2779 | 3.3991 | 3.5248 | 3.6552 | 3.7903 | 0 | 0 | 0 | 0 | 0
2020-11-27 05:00 | 2020-11-27 | 5 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-11-27 06:00 | 2020-11-27 | 6 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-11-27 07:00 | 2020-11-27 | 7 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-11-27 08:00 | 2020-11-27 | 8 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-11-27 09:00 | 2020-11-27 | 9 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-27 10:00 | 2020-11-27 | 10 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-27 11:00 | 2020-11-27 | 11 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-11-27 12:00 | 2020-11-27 | 12 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-11-27 13:00 | 2020-11-27 | 13 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-11-27 14:00 | 2020-11-27 | 14 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-11-27 15:00 | 2020-11-27 | 15 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-11-27 16:00 | 2020-11-27 | 16 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-11-27 17:00 | 2020-11-27 | 17 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-11-27 18:00 | 2020-11-27 | 18 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-11-27 19:00 | 2020-11-27 | 19 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-11-27 20:00 | 2020-11-27 | 20 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-11-27 21:00 | 2020-11-27 | 21 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-11-27 22:00 | 2020-11-27 | 22 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-11-27 23:00 | 2020-11-27 | 23 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-11-28 | 2020-11-27 | 0 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-11-28 01:00 | 2020-11-28 | 1 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-11-28 02:00 | 2020-11-28 | 2 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-28 03:00 | 2020-11-28 | 3 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-28 04:00 | 2020-11-28 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-11-28 05:00 | 2020-11-28 | 5 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-28 06:00 | 2020-11-28 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-11-28 07:00 | 2020-11-28 | 7 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-11-28 08:00 | 2020-11-28 | 8 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-11-28 09:00 | 2020-11-28 | 9 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-11-28 10:00 | 2020-11-28 | 10 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-11-28 11:00 | 2020-11-28 | 11 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-11-28 12:00 | 2020-11-28 | 12 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-28 13:00 | 2020-11-28 | 13 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-28 14:00 | 2020-11-28 | 14 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-11-28 15:00 | 2020-11-28 | 15 | 3.0493 | 0.01059% | 4.5464 | 4.7146 | 4.8889 | 5.0697 | 5.2572 | 0 | 0 | 0 | 0 | 0
2020-11-28 16:00 | 2020-11-28 | 16 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-11-28 17:00 | 2020-11-28 | 17 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-11-28 18:00 | 2020-11-28 | 18 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-11-28 19:00 | 2020-11-28 | 19 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-11-28 20:00 | 2020-11-28 | 20 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-11-28 21:00 | 2020-11-28 | 21 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-11-28 22:00 | 2020-11-28 | 22 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-11-28 23:00 | 2020-11-28 | 23 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-11-29 | 2020-11-28 | 0 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-11-29 01:00 | 2020-11-29 | 1 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-11-29 02:00 | 2020-11-29 | 2 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-11-29 03:00 | 2020-11-29 | 3 | 2.2061 | 0.00766% | 3.2892 | 3.4108 | 3.5369 | 3.6677 | 3.8033 | 0 | 0 | 0 | 0 | 0
2020-11-29 04:00 | 2020-11-29 | 4 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-11-29 05:00 | 2020-11-29 | 5 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-29 06:00 | 2020-11-29 | 6 | 2.2889 | 0.007948% | 3.4126 | 3.5388 | 3.6697 | 3.8054 | 3.9461 | 0 | 0 | 0 | 0 | 0
2020-11-29 07:00 | 2020-11-29 | 7 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-11-29 08:00 | 2020-11-29 | 8 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-11-29 09:00 | 2020-11-29 | 9 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-11-29 10:00 | 2020-11-29 | 10 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-11-29 11:00 | 2020-11-29 | 11 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-11-29 12:00 | 2020-11-29 | 12 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-29 13:00 | 2020-11-29 | 13 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-11-29 14:00 | 2020-11-29 | 14 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-11-29 15:00 | 2020-11-29 | 15 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-11-29 16:00 | 2020-11-29 | 16 | 3.1472 | 0.01093% | 4.6924 | 4.8659 | 5.0458 | 5.2324 | 5.4259 | 0 | 0 | 0 | 0 | 0
2020-11-29 17:00 | 2020-11-29 | 17 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-11-29 18:00 | 2020-11-29 | 18 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-11-29 19:00 | 2020-11-29 | 19 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-11-29 20:00 | 2020-11-29 | 20 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-11-29 21:00 | 2020-11-29 | 21 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-11-29 22:00 | 2020-11-29 | 22 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-11-29 23:00 | 2020-11-29 | 23 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-11-30 | 2020-11-29 | 0 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-11-30 01:00 | 2020-11-30 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-11-30 02:00 | 2020-11-30 | 2 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-11-30 03:00 | 2020-11-30 | 3 | 2.2738 | 0.007896% | 3.3902 | 3.5156 | 3.6456 | 3.7804 | 3.9202 | 0 | 0 | 0 | 0 | 0
2020-11-30 04:00 | 2020-11-30 | 4 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-11-30 05:00 | 2020-11-30 | 5 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-11-30 06:00 | 2020-11-30 | 6 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-11-30 07:00 | 2020-11-30 | 7 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-11-30 08:00 | 2020-11-30 | 8 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-11-30 09:00 | 2020-11-30 | 9 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-11-30 10:00 | 2020-11-30 | 10 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-11-30 11:00 | 2020-11-30 | 11 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-11-30 12:00 | 2020-11-30 | 12 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-11-30 13:00 | 2020-11-30 | 13 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-11-30 14:00 | 2020-11-30 | 14 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-11-30 15:00 | 2020-11-30 | 15 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-11-30 16:00 | 2020-11-30 | 16 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-11-30 17:00 | 2020-11-30 | 17 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-11-30 18:00 | 2020-11-30 | 18 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-11-30 19:00 | 2020-11-30 | 19 | 3.5689 | 0.01239% | 5.321 | 5.5178 | 5.7218 | 5.9334 | 6.1528 | 0 | 0 | 0 | 0.19641 | 0.41582
2020-11-30 20:00 | 2020-11-30 | 20 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-11-30 21:00 | 2020-11-30 | 21 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-11-30 22:00 | 2020-11-30 | 22 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-11-30 23:00 | 2020-11-30 | 23 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-12-01 | 2020-11-30 | 0 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-12-01 01:00 | 2020-12-01 | 1 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-12-01 02:00 | 2020-12-01 | 2 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-12-01 03:00 | 2020-12-01 | 3 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-12-01 04:00 | 2020-12-01 | 4 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-12-01 05:00 | 2020-12-01 | 5 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-01 06:00 | 2020-12-01 | 6 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-12-01 07:00 | 2020-12-01 | 7 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-12-01 08:00 | 2020-12-01 | 8 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-12-01 09:00 | 2020-12-01 | 9 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-12-01 10:00 | 2020-12-01 | 10 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-12-01 11:00 | 2020-12-01 | 11 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-01 12:00 | 2020-12-01 | 12 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-01 13:00 | 2020-12-01 | 13 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-12-01 14:00 | 2020-12-01 | 14 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-01 15:00 | 2020-12-01 | 15 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-12-01 16:00 | 2020-12-01 | 16 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-01 17:00 | 2020-12-01 | 17 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-12-01 18:00 | 2020-12-01 | 18 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-12-01 19:00 | 2020-12-01 | 19 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-01 20:00 | 2020-12-01 | 20 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-12-01 21:00 | 2020-12-01 | 21 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-12-01 22:00 | 2020-12-01 | 22 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-01 23:00 | 2020-12-01 | 23 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-12-02 | 2020-12-01 | 0 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-02 01:00 | 2020-12-02 | 1 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-12-02 02:00 | 2020-12-02 | 2 | 2.3943 | 0.008314% | 3.5698 | 3.7018 | 3.8387 | 3.9806 | 4.1278 | 0 | 0 | 0 | 0 | 0
2020-12-02 03:00 | 2020-12-02 | 3 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-02 04:00 | 2020-12-02 | 4 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-02 05:00 | 2020-12-02 | 5 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-12-02 06:00 | 2020-12-02 | 6 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-12-02 07:00 | 2020-12-02 | 7 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-12-02 08:00 | 2020-12-02 | 8 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-02 09:00 | 2020-12-02 | 9 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-02 10:00 | 2020-12-02 | 10 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-12-02 11:00 | 2020-12-02 | 11 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-02 12:00 | 2020-12-02 | 12 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-02 13:00 | 2020-12-02 | 13 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-02 14:00 | 2020-12-02 | 14 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-02 15:00 | 2020-12-02 | 15 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-02 16:00 | 2020-12-02 | 16 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-12-02 17:00 | 2020-12-02 | 17 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-12-02 18:00 | 2020-12-02 | 18 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-12-02 19:00 | 2020-12-02 | 19 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-12-02 20:00 | 2020-12-02 | 20 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-12-02 21:00 | 2020-12-02 | 21 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-12-02 22:00 | 2020-12-02 | 22 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-12-02 23:00 | 2020-12-02 | 23 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-12-03 | 2020-12-02 | 0 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-12-03 01:00 | 2020-12-03 | 1 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-12-03 02:00 | 2020-12-03 | 2 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-12-03 03:00 | 2020-12-03 | 3 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-12-03 04:00 | 2020-12-03 | 4 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-12-03 05:00 | 2020-12-03 | 5 | 2.5298 | 0.008784% | 3.7719 | 3.9113 | 4.056 | 4.206 | 4.3615 | 0 | 0 | 0 | 0 | 0
2020-12-03 06:00 | 2020-12-03 | 6 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-12-03 07:00 | 2020-12-03 | 7 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-12-03 08:00 | 2020-12-03 | 8 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-03 09:00 | 2020-12-03 | 9 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-12-03 10:00 | 2020-12-03 | 10 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-03 11:00 | 2020-12-03 | 11 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-12-03 12:00 | 2020-12-03 | 12 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-12-03 13:00 | 2020-12-03 | 13 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-12-03 14:00 | 2020-12-03 | 14 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-03 15:00 | 2020-12-03 | 15 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-03 16:00 | 2020-12-03 | 16 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-03 17:00 | 2020-12-03 | 17 | 3.8248 | 0.01328% | 5.7027 | 5.9136 | 6.1323 | 6.359 | 6.5942 | 0 | 0.17658 | 0.39525 | 0.62201 | 0.85716
2020-12-03 18:00 | 2020-12-03 | 18 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-12-03 19:00 | 2020-12-03 | 19 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-12-03 20:00 | 2020-12-03 | 20 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-03 21:00 | 2020-12-03 | 21 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-12-03 22:00 | 2020-12-03 | 22 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-03 23:00 | 2020-12-03 | 23 | 2.9665 | 0.0103% | 4.423 | 4.5865 | 4.7561 | 4.932 | 5.1144 | 0 | 0 | 0 | 0 | 0
2020-12-04 | 2020-12-03 | 0 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-12-04 01:00 | 2020-12-04 | 1 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-12-04 02:00 | 2020-12-04 | 2 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-12-04 03:00 | 2020-12-04 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-04 04:00 | 2020-12-04 | 4 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-12-04 05:00 | 2020-12-04 | 5 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-12-04 06:00 | 2020-12-04 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-04 07:00 | 2020-12-04 | 7 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-12-04 08:00 | 2020-12-04 | 8 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-04 09:00 | 2020-12-04 | 9 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-04 10:00 | 2020-12-04 | 10 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-04 11:00 | 2020-12-04 | 11 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-04 12:00 | 2020-12-04 | 12 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-12-04 13:00 | 2020-12-04 | 13 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-12-04 14:00 | 2020-12-04 | 14 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-12-04 15:00 | 2020-12-04 | 15 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-12-04 16:00 | 2020-12-04 | 16 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-04 17:00 | 2020-12-04 | 17 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-12-04 18:00 | 2020-12-04 | 18 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-04 19:00 | 2020-12-04 | 19 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-04 20:00 | 2020-12-04 | 20 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-04 21:00 | 2020-12-04 | 21 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-12-04 22:00 | 2020-12-04 | 22 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-04 23:00 | 2020-12-04 | 23 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-12-05 | 2020-12-04 | 0 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-12-05 01:00 | 2020-12-05 | 1 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-05 02:00 | 2020-12-05 | 2 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-12-05 03:00 | 2020-12-05 | 3 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-05 04:00 | 2020-12-05 | 4 | 2.3341 | 0.008105% | 3.48 | 3.6087 | 3.7421 | 3.8805 | 4.024 | 0 | 0 | 0 | 0 | 0
2020-12-05 05:00 | 2020-12-05 | 5 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-12-05 06:00 | 2020-12-05 | 6 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-05 07:00 | 2020-12-05 | 7 | 2.6126 | 0.009072% | 3.8953 | 4.0394 | 4.1888 | 4.3437 | 4.5043 | 0 | 0 | 0 | 0 | 0
2020-12-05 08:00 | 2020-12-05 | 8 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-12-05 09:00 | 2020-12-05 | 9 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-12-05 10:00 | 2020-12-05 | 10 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-12-05 11:00 | 2020-12-05 | 11 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-05 12:00 | 2020-12-05 | 12 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-05 13:00 | 2020-12-05 | 13 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-05 14:00 | 2020-12-05 | 14 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-12-05 15:00 | 2020-12-05 | 15 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-05 16:00 | 2020-12-05 | 16 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-12-05 17:00 | 2020-12-05 | 17 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-12-05 18:00 | 2020-12-05 | 18 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-12-05 19:00 | 2020-12-05 | 19 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-05 20:00 | 2020-12-05 | 20 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-12-05 21:00 | 2020-12-05 | 21 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-12-05 22:00 | 2020-12-05 | 22 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-12-05 23:00 | 2020-12-05 | 23 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-12-06 | 2020-12-05 | 0 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-12-06 01:00 | 2020-12-06 | 1 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-12-06 02:00 | 2020-12-06 | 2 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-12-06 03:00 | 2020-12-06 | 3 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-12-06 04:00 | 2020-12-06 | 4 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-06 05:00 | 2020-12-06 | 5 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-12-06 06:00 | 2020-12-06 | 6 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-12-06 07:00 | 2020-12-06 | 7 | 2.7406 | 0.009516% | 4.0862 | 4.2373 | 4.394 | 4.5565 | 4.7249 | 0 | 0 | 0 | 0 | 0
2020-12-06 08:00 | 2020-12-06 | 8 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-12-06 09:00 | 2020-12-06 | 9 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-12-06 10:00 | 2020-12-06 | 10 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-06 11:00 | 2020-12-06 | 11 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-12-06 12:00 | 2020-12-06 | 12 | 3.1849 | 0.01106% | 4.7485 | 4.9241 | 5.1062 | 5.295 | 5.4908 | 0 | 0 | 0 | 0 | 0
2020-12-06 13:00 | 2020-12-06 | 13 | 3.1096 | 0.0108% | 4.6363 | 4.8077 | 4.9855 | 5.1698 | 5.361 | 0 | 0 | 0 | 0 | 0
2020-12-06 14:00 | 2020-12-06 | 14 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-12-06 15:00 | 2020-12-06 | 15 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-06 16:00 | 2020-12-06 | 16 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-06 17:00 | 2020-12-06 | 17 | 3.727 | 0.01294% | 5.5568 | 5.7622 | 5.9753 | 6.1963 | 6.4254 | 0 | 0.025248 | 0.23833 | 0.45928 | 0.68841
2020-12-06 18:00 | 2020-12-06 | 18 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-12-06 19:00 | 2020-12-06 | 19 | 3.6893 | 0.01281% | 5.5006 | 5.704 | 5.915 | 6.1337 | 6.3605 | 0 | 0 | 0.17797 | 0.3967 | 0.62351
2020-12-06 20:00 | 2020-12-06 | 20 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-12-06 21:00 | 2020-12-06 | 21 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-06 22:00 | 2020-12-06 | 22 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-06 23:00 | 2020-12-06 | 23 | 2.974 | 0.01033% | 4.4342 | 4.5982 | 4.7682 | 4.9445 | 5.1273 | 0 | 0 | 0 | 0 | 0
2020-12-07 | 2020-12-06 | 0 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-12-07 01:00 | 2020-12-07 | 1 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-07 02:00 | 2020-12-07 | 2 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-12-07 03:00 | 2020-12-07 | 3 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-12-07 04:00 | 2020-12-07 | 4 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-12-07 05:00 | 2020-12-07 | 5 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-12-07 06:00 | 2020-12-07 | 6 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-12-07 07:00 | 2020-12-07 | 7 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-12-07 08:00 | 2020-12-07 | 8 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-12-07 09:00 | 2020-12-07 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-07 10:00 | 2020-12-07 | 10 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-12-07 11:00 | 2020-12-07 | 11 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-07 12:00 | 2020-12-07 | 12 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-12-07 13:00 | 2020-12-07 | 13 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-07 14:00 | 2020-12-07 | 14 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-07 15:00 | 2020-12-07 | 15 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-07 16:00 | 2020-12-07 | 16 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-12-07 17:00 | 2020-12-07 | 17 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-12-07 18:00 | 2020-12-07 | 18 | 3.8625 | 0.01341% | 5.7588 | 5.9718 | 6.1926 | 6.4216 | 6.6591 | 0.021832 | 0.23478 | 0.45561 | 0.6846 | 0.92206 | 1 | 1
2020-12-07 19:00 | 2020-12-07 | 19 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-12-07 20:00 | 2020-12-07 | 20 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-12-07 21:00 | 2020-12-07 | 21 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-07 22:00 | 2020-12-07 | 22 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-12-07 23:00 | 2020-12-07 | 23 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-12-08 | 2020-12-07 | 0 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-12-08 01:00 | 2020-12-08 | 1 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-08 02:00 | 2020-12-08 | 2 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-12-08 03:00 | 2020-12-08 | 3 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-12-08 04:00 | 2020-12-08 | 4 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-12-08 05:00 | 2020-12-08 | 5 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-12-08 06:00 | 2020-12-08 | 6 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-12-08 07:00 | 2020-12-08 | 7 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-12-08 08:00 | 2020-12-08 | 8 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-08 09:00 | 2020-12-08 | 9 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-08 10:00 | 2020-12-08 | 10 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-12-08 11:00 | 2020-12-08 | 11 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-08 12:00 | 2020-12-08 | 12 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-08 13:00 | 2020-12-08 | 13 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-08 14:00 | 2020-12-08 | 14 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-08 15:00 | 2020-12-08 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-12-08 16:00 | 2020-12-08 | 16 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-08 17:00 | 2020-12-08 | 17 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-12-08 18:00 | 2020-12-08 | 18 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-12-08 19:00 | 2020-12-08 | 19 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-12-08 20:00 | 2020-12-08 | 20 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-08 21:00 | 2020-12-08 | 21 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-12-08 22:00 | 2020-12-08 | 22 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-08 23:00 | 2020-12-08 | 23 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-12-09 | 2020-12-08 | 0 | 2.7783 | 0.009647% | 4.1423 | 4.2955 | 4.4543 | 4.619 | 4.7899 | 0 | 0 | 0 | 0 | 0
2020-12-09 01:00 | 2020-12-09 | 1 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-12-09 02:00 | 2020-12-09 | 2 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-09 03:00 | 2020-12-09 | 3 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-12-09 04:00 | 2020-12-09 | 4 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-12-09 05:00 | 2020-12-09 | 5 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-12-09 06:00 | 2020-12-09 | 6 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-09 07:00 | 2020-12-09 | 7 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-12-09 08:00 | 2020-12-09 | 8 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-12-09 09:00 | 2020-12-09 | 9 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-09 10:00 | 2020-12-09 | 10 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-12-09 11:00 | 2020-12-09 | 11 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-09 12:00 | 2020-12-09 | 12 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-09 13:00 | 2020-12-09 | 13 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-09 14:00 | 2020-12-09 | 14 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-12-09 15:00 | 2020-12-09 | 15 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-09 16:00 | 2020-12-09 | 16 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-12-09 17:00 | 2020-12-09 | 17 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-12-09 18:00 | 2020-12-09 | 18 | 3.8098 | 0.01323% | 5.6803 | 5.8903 | 6.1081 | 6.334 | 6.5682 | 0 | 0.1533 | 0.37111 | 0.59698 | 0.8312
2020-12-09 19:00 | 2020-12-09 | 19 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-09 20:00 | 2020-12-09 | 20 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-09 21:00 | 2020-12-09 | 21 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-12-09 22:00 | 2020-12-09 | 22 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-09 23:00 | 2020-12-09 | 23 | 3.0042 | 0.01043% | 4.4791 | 4.6447 | 4.8165 | 4.9946 | 5.1793 | 0 | 0 | 0 | 0 | 0
2020-12-10 | 2020-12-09 | 0 | 2.703 | 0.009386% | 4.0301 | 4.1791 | 4.3336 | 4.4939 | 4.66 | 0 | 0 | 0 | 0 | 0
2020-12-10 01:00 | 2020-12-10 | 1 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-12-10 02:00 | 2020-12-10 | 2 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-10 03:00 | 2020-12-10 | 3 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-12-10 04:00 | 2020-12-10 | 4 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-12-10 05:00 | 2020-12-10 | 5 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-12-10 06:00 | 2020-12-10 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-10 07:00 | 2020-12-10 | 7 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-12-10 08:00 | 2020-12-10 | 8 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-12-10 09:00 | 2020-12-10 | 9 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-10 10:00 | 2020-12-10 | 10 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-12-10 11:00 | 2020-12-10 | 11 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-12-10 12:00 | 2020-12-10 | 12 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-10 13:00 | 2020-12-10 | 13 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-12-10 14:00 | 2020-12-10 | 14 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-12-10 15:00 | 2020-12-10 | 15 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-10 16:00 | 2020-12-10 | 16 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-10 17:00 | 2020-12-10 | 17 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-12-10 18:00 | 2020-12-10 | 18 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-12-10 19:00 | 2020-12-10 | 19 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-12-10 20:00 | 2020-12-10 | 20 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-12-10 21:00 | 2020-12-10 | 21 | 4.2691 | 0.01482% | 6.365 | 6.6004 | 6.8445 | 7.0976 | 7.36 | 0.62802 | 0.86339 | 1.1075 | 1.3606 | 1.623 | 1
2020-12-10 22:00 | 2020-12-10 | 22 | 4.1787 | 0.01451% | 6.2303 | 6.4607 | 6.6996 | 6.9473 | 7.2043 | 0.49331 | 0.7237 | 0.96261 | 1.2103 | 1.4673 | 2 | 2
2020-12-10 23:00 | 2020-12-10 | 23 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-12-11 | 2020-12-10 | 0 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-12-11 01:00 | 2020-12-11 | 1 | 2.5524 | 0.008863% | 3.8055 | 3.9463 | 4.0922 | 4.2435 | 4.4004 | 0 | 0 | 0 | 0 | 0
2020-12-11 02:00 | 2020-12-11 | 2 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-12-11 03:00 | 2020-12-11 | 3 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-12-11 04:00 | 2020-12-11 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-12-11 05:00 | 2020-12-11 | 5 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-12-11 06:00 | 2020-12-11 | 6 | 2.6955 | 0.00936% | 4.0188 | 4.1674 | 4.3215 | 4.4814 | 4.6471 | 0 | 0 | 0 | 0 | 0
2020-12-11 07:00 | 2020-12-11 | 7 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-12-11 08:00 | 2020-12-11 | 8 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-12-11 09:00 | 2020-12-11 | 9 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-11 10:00 | 2020-12-11 | 10 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-12-11 11:00 | 2020-12-11 | 11 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-12-11 12:00 | 2020-12-11 | 12 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-11 13:00 | 2020-12-11 | 13 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-12-11 14:00 | 2020-12-11 | 14 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-11 15:00 | 2020-12-11 | 15 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-11 16:00 | 2020-12-11 | 16 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-11 17:00 | 2020-12-11 | 17 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-12-11 18:00 | 2020-12-11 | 18 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-11 19:00 | 2020-12-11 | 19 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-12-11 20:00 | 2020-12-11 | 20 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-12-11 21:00 | 2020-12-11 | 21 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-11 22:00 | 2020-12-11 | 22 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-12-11 23:00 | 2020-12-11 | 23 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-12-12 | 2020-12-11 | 0 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-12-12 01:00 | 2020-12-12 | 1 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-12-12 02:00 | 2020-12-12 | 2 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-12 03:00 | 2020-12-12 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-12-12 04:00 | 2020-12-12 | 4 | 2.2814 | 0.007922% | 3.4014 | 3.5272 | 3.6576 | 3.7929 | 3.9331 | 0 | 0 | 0 | 0 | 0
2020-12-12 05:00 | 2020-12-12 | 5 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-12 06:00 | 2020-12-12 | 6 | 2.4771 | 0.008601% | 3.6933 | 3.8299 | 3.9715 | 4.1183 | 4.2706 | 0 | 0 | 0 | 0 | 0
2020-12-12 07:00 | 2020-12-12 | 7 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-12-12 08:00 | 2020-12-12 | 8 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-12-12 09:00 | 2020-12-12 | 9 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-12-12 10:00 | 2020-12-12 | 10 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-12-12 11:00 | 2020-12-12 | 11 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-12-12 12:00 | 2020-12-12 | 12 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-12-12 13:00 | 2020-12-12 | 13 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-12 14:00 | 2020-12-12 | 14 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-12-12 15:00 | 2020-12-12 | 15 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-12 16:00 | 2020-12-12 | 16 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-12-12 17:00 | 2020-12-12 | 17 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-12-12 18:00 | 2020-12-12 | 18 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-12-12 19:00 | 2020-12-12 | 19 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-12 20:00 | 2020-12-12 | 20 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-12 21:00 | 2020-12-12 | 21 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-12 22:00 | 2020-12-12 | 22 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-12-12 23:00 | 2020-12-12 | 23 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-12-13 | 2020-12-12 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-13 01:00 | 2020-12-13 | 1 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-13 02:00 | 2020-12-13 | 2 | 2.2588 | 0.007843% | 3.3677 | 3.4923 | 3.6214 | 3.7553 | 3.8942 | 0 | 0 | 0 | 0 | 0
2020-12-13 03:00 | 2020-12-13 | 3 | 2.2663 | 0.007869% | 3.379 | 3.5039 | 3.6335 | 3.7678 | 3.9072 | 0 | 0 | 0 | 0 | 0
2020-12-13 04:00 | 2020-12-13 | 4 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-12-13 05:00 | 2020-12-13 | 5 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-12-13 06:00 | 2020-12-13 | 6 | 2.3416 | 0.008131% | 3.4912 | 3.6203 | 3.7542 | 3.893 | 4.037 | 0 | 0 | 0 | 0 | 0
2020-12-13 07:00 | 2020-12-13 | 7 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-12-13 08:00 | 2020-12-13 | 8 | 2.7181 | 0.009438% | 4.0525 | 4.2024 | 4.3578 | 4.5189 | 4.686 | 0 | 0 | 0 | 0 | 0
2020-12-13 09:00 | 2020-12-13 | 9 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-12-13 10:00 | 2020-12-13 | 10 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-13 11:00 | 2020-12-13 | 11 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-13 12:00 | 2020-12-13 | 12 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-13 13:00 | 2020-12-13 | 13 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-12-13 14:00 | 2020-12-13 | 14 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-12-13 15:00 | 2020-12-13 | 15 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-12-13 16:00 | 2020-12-13 | 16 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-12-13 17:00 | 2020-12-13 | 17 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-12-13 18:00 | 2020-12-13 | 18 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-12-13 19:00 | 2020-12-13 | 19 | 3.7345 | 0.01297% | 5.568 | 5.7739 | 5.9874 | 6.2088 | 6.4384 | 0 | 0.036888 | 0.2504 | 0.4718 | 0.70139
2020-12-13 20:00 | 2020-12-13 | 20 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-13 21:00 | 2020-12-13 | 21 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-13 22:00 | 2020-12-13 | 22 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-12-13 23:00 | 2020-12-13 | 23 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-12-14 | 2020-12-13 | 0 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-12-14 01:00 | 2020-12-14 | 1 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-12-14 02:00 | 2020-12-14 | 2 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-12-14 03:00 | 2020-12-14 | 3 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-12-14 04:00 | 2020-12-14 | 4 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-12-14 05:00 | 2020-12-14 | 5 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-14 06:00 | 2020-12-14 | 6 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-12-14 07:00 | 2020-12-14 | 7 | 2.9364 | 0.0102% | 4.3781 | 4.54 | 4.7078 | 4.8819 | 5.0624 | 0 | 0 | 0 | 0 | 0
2020-12-14 08:00 | 2020-12-14 | 8 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-12-14 09:00 | 2020-12-14 | 9 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-12-14 10:00 | 2020-12-14 | 10 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-12-14 11:00 | 2020-12-14 | 11 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-12-14 12:00 | 2020-12-14 | 12 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-14 13:00 | 2020-12-14 | 13 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-14 14:00 | 2020-12-14 | 14 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-14 15:00 | 2020-12-14 | 15 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-12-14 16:00 | 2020-12-14 | 16 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-12-14 17:00 | 2020-12-14 | 17 | 3.7721 | 0.0131% | 5.6241 | 5.8321 | 6.0478 | 6.2714 | 6.5033 | 0 | 0.095093 | 0.31075 | 0.53439 | 0.7663
2020-12-14 18:00 | 2020-12-14 | 18 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-12-14 19:00 | 2020-12-14 | 19 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-12-14 20:00 | 2020-12-14 | 20 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-14 21:00 | 2020-12-14 | 21 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-14 22:00 | 2020-12-14 | 22 | 3.2903 | 0.01143% | 4.9057 | 5.0871 | 5.2752 | 5.4703 | 5.6725 | 0 | 0 | 0 | 0 | 0
2020-12-14 23:00 | 2020-12-14 | 23 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-12-15 | 2020-12-14 | 0 | 2.6202 | 0.009098% | 3.9066 | 4.051 | 4.2008 | 4.3562 | 4.5173 | 0 | 0 | 0 | 0 | 0
2020-12-15 01:00 | 2020-12-15 | 1 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-15 02:00 | 2020-12-15 | 2 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-12-15 03:00 | 2020-12-15 | 3 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-12-15 04:00 | 2020-12-15 | 4 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-12-15 05:00 | 2020-12-15 | 5 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-12-15 06:00 | 2020-12-15 | 6 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-12-15 07:00 | 2020-12-15 | 7 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-15 08:00 | 2020-12-15 | 8 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-12-15 09:00 | 2020-12-15 | 9 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-12-15 10:00 | 2020-12-15 | 10 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-15 11:00 | 2020-12-15 | 11 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-12-15 12:00 | 2020-12-15 | 12 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-15 13:00 | 2020-12-15 | 13 | 3.3806 | 0.01174% | 5.0404 | 5.2268 | 5.42 | 5.6205 | 5.8283 | 0 | 0 | 0 | 0 | 0.091304
2020-12-15 14:00 | 2020-12-15 | 14 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-12-15 15:00 | 2020-12-15 | 15 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-15 16:00 | 2020-12-15 | 16 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-15 17:00 | 2020-12-15 | 17 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-12-15 18:00 | 2020-12-15 | 18 | 4.0357 | 0.01401% | 6.017 | 6.2395 | 6.4703 | 6.7095 | 6.9576 | 0.28002 | 0.50252 | 0.73325 | 0.97251 | 1.2206 | 2 | 2
2020-12-15 19:00 | 2020-12-15 | 19 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-12-15 20:00 | 2020-12-15 | 20 | 3.7947 | 0.01318% | 5.6578 | 5.867 | 6.084 | 6.3089 | 6.5422 | 0 | 0.13002 | 0.34697 | 0.57194 | 0.80524
2020-12-15 21:00 | 2020-12-15 | 21 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-12-15 22:00 | 2020-12-15 | 22 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-15 23:00 | 2020-12-15 | 23 | 3.2376 | 0.01124% | 4.8271 | 5.0056 | 5.1907 | 5.3826 | 5.5817 | 0 | 0 | 0 | 0 | 0
2020-12-16 | 2020-12-15 | 0 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-12-16 01:00 | 2020-12-16 | 1 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-12-16 02:00 | 2020-12-16 | 2 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-16 03:00 | 2020-12-16 | 3 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-16 04:00 | 2020-12-16 | 4 | 2.7632 | 0.009595% | 4.1199 | 4.2722 | 4.4302 | 4.594 | 4.7639 | 0 | 0 | 0 | 0 | 0
2020-12-16 05:00 | 2020-12-16 | 5 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-12-16 06:00 | 2020-12-16 | 6 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-12-16 07:00 | 2020-12-16 | 7 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-16 08:00 | 2020-12-16 | 8 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-16 09:00 | 2020-12-16 | 9 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-12-16 10:00 | 2020-12-16 | 10 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-12-16 11:00 | 2020-12-16 | 11 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 1
2020-12-16 12:00 | 2020-12-16 | 12 | 3.9604 | 0.01375% | 5.9048 | 6.1231 | 6.3495 | 6.5843 | 6.8278 | 0.16777 | 0.38612 | 0.61254 | 0.84733 | 1.0908 | 2 | 2
2020-12-16 13:00 | 2020-12-16 | 13 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-12-16 14:00 | 2020-12-16 | 14 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-12-16 15:00 | 2020-12-16 | 15 | 3.9152 | 0.01359% | 5.8374 | 6.0533 | 6.2771 | 6.5092 | 6.7499 | 0.10041 | 0.31627 | 0.54011 | 0.77223 | 1.0129 | 2
2020-12-16 16:00 | 2020-12-16 | 16 | 3.998 | 0.01388% | 5.9609 | 6.1813 | 6.4099 | 6.6469 | 6.8927 | 0.2239 | 0.44432 | 0.6729 | 0.90992 | 1.1557 | 3
2020-12-16 17:00 | 2020-12-16 | 17 | 4.2465 | 0.01475% | 6.3313 | 6.5655 | 6.8083 | 7.06 | 7.3211 | 0.59435 | 0.82847 | 1.0713 | 1.323 | 1.5841 | 4
2020-12-16 18:00 | 2020-12-16 | 18 | 4.1561 | 0.01443% | 6.1966 | 6.4258 | 6.6634 | 6.9098 | 7.1653 | 0.45964 | 0.68878 | 0.92639 | 1.1728 | 1.4283 | 5
2020-12-16 19:00 | 2020-12-16 | 19 | 4.1185 | 0.0143% | 6.1405 | 6.3676 | 6.603 | 6.8472 | 7.1004 | 0.40351 | 0.63057 | 0.86604 | 1.1102 | 1.3634 | 6
2020-12-16 20:00 | 2020-12-16 | 20 | 3.9679 | 0.01378% | 5.916 | 6.1348 | 6.3616 | 6.5969 | 6.8408 | 0.17899 | 0.39776 | 0.62461 | 0.85985 | 1.1038 | 7
2020-12-16 21:00 | 2020-12-16 | 21 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 8 | 8
2020-12-16 22:00 | 2020-12-16 | 22 | 3.7044 | 0.01286% | 5.5231 | 5.7273 | 5.9391 | 6.1587 | 6.3865 | 0 | 0 | 0.20211 | 0.42173 | 0.64947
2020-12-16 23:00 | 2020-12-16 | 23 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-17 | 2020-12-16 | 0 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-12-17 01:00 | 2020-12-17 | 1 | 2.8837 | 0.01001% | 4.2995 | 4.4585 | 4.6233 | 4.7943 | 4.9716 | 0 | 0 | 0 | 0 | 0
2020-12-17 02:00 | 2020-12-17 | 2 | 2.7708 | 0.009621% | 4.1311 | 4.2839 | 4.4423 | 4.6065 | 4.7769 | 0 | 0 | 0 | 0 | 0
2020-12-17 03:00 | 2020-12-17 | 3 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-12-17 04:00 | 2020-12-17 | 4 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-12-17 05:00 | 2020-12-17 | 5 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-12-17 06:00 | 2020-12-17 | 6 | 3.0192 | 0.01048% | 4.5015 | 4.668 | 4.8406 | 5.0196 | 5.2052 | 0 | 0 | 0 | 0 | 0
2020-12-17 07:00 | 2020-12-17 | 7 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-12-17 08:00 | 2020-12-17 | 8 | 3.6968 | 0.01284% | 5.5119 | 5.7157 | 5.927 | 6.1462 | 6.3735 | 0 | 0 | 0.19004 | 0.40921 | 0.63649
2020-12-17 09:00 | 2020-12-17 | 9 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-12-17 10:00 | 2020-12-17 | 10 | 3.8023 | 0.0132% | 5.669 | 5.8787 | 6.096 | 6.3215 | 6.5552 | 0 | 0.14166 | 0.35904 | 0.58446 | 0.81822
2020-12-17 11:00 | 2020-12-17 | 11 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-12-17 12:00 | 2020-12-17 | 12 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-17 13:00 | 2020-12-17 | 13 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-12-17 14:00 | 2020-12-17 | 14 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-12-17 15:00 | 2020-12-17 | 15 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-12-17 16:00 | 2020-12-17 | 16 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-17 17:00 | 2020-12-17 | 17 | 3.983 | 0.01383% | 5.9384 | 6.158 | 6.3858 | 6.6219 | 6.8668 | 0.20144 | 0.42104 | 0.64875 | 0.88489 | 1.1298 | 1
2020-12-17 18:00 | 2020-12-17 | 18 | 4.0658 | 0.01412% | 6.0619 | 6.2861 | 6.5185 | 6.7596 | 7.0095 | 0.32493 | 0.54909 | 0.78154 | 1.0226 | 1.2725 | 2
2020-12-17 19:00 | 2020-12-17 | 19 | 3.9077 | 0.01357% | 5.8262 | 6.0416 | 6.265 | 6.4967 | 6.7369 | 0.089186 | 0.30463 | 0.52804 | 0.75971 | 0.99995 | 3 | 3
2020-12-17 20:00 | 2020-12-17 | 20 | 3.8474 | 0.01336% | 5.7364 | 5.9485 | 6.1685 | 6.3966 | 6.6331 | 0 | 0.2115 | 0.43147 | 0.65957 | 0.8961
2020-12-17 21:00 | 2020-12-17 | 21 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-12-17 22:00 | 2020-12-17 | 22 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-17 23:00 | 2020-12-17 | 23 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-12-18 | 2020-12-17 | 0 | 3.0569 | 0.01061% | 4.5577 | 4.7262 | 4.901 | 5.0822 | 5.2701 | 0 | 0 | 0 | 0 | 0
2020-12-18 01:00 | 2020-12-18 | 1 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-12-18 02:00 | 2020-12-18 | 2 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-12-18 03:00 | 2020-12-18 | 3 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-12-18 04:00 | 2020-12-18 | 4 | 2.7256 | 0.009464% | 4.0637 | 4.214 | 4.3698 | 4.5314 | 4.699 | 0 | 0 | 0 | 0 | 0
2020-12-18 05:00 | 2020-12-18 | 5 | 2.846 | 0.009883% | 4.2433 | 4.4003 | 4.563 | 4.7317 | 4.9067 | 0 | 0 | 0 | 0 | 0
2020-12-18 06:00 | 2020-12-18 | 6 | 3.0719 | 0.01067% | 4.5801 | 4.7495 | 4.9251 | 5.1072 | 5.2961 | 0 | 0 | 0 | 0 | 0
2020-12-18 07:00 | 2020-12-18 | 7 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-18 08:00 | 2020-12-18 | 8 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-18 09:00 | 2020-12-18 | 9 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-12-18 10:00 | 2020-12-18 | 10 | 3.6441 | 0.01265% | 5.4333 | 5.6342 | 5.8425 | 6.0586 | 6.2826 | 0 | 0 | 0.10554 | 0.32159 | 0.54563
2020-12-18 11:00 | 2020-12-18 | 11 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-18 12:00 | 2020-12-18 | 12 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-18 13:00 | 2020-12-18 | 13 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-18 14:00 | 2020-12-18 | 14 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-12-18 15:00 | 2020-12-18 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-18 16:00 | 2020-12-18 | 16 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-12-18 17:00 | 2020-12-18 | 17 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-12-18 18:00 | 2020-12-18 | 18 | 3.9453 | 0.0137% | 5.8823 | 6.0998 | 6.3254 | 6.5593 | 6.8019 | 0.14532 | 0.36283 | 0.5884 | 0.8223 | 1.0649 | 1
2020-12-18 19:00 | 2020-12-18 | 19 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 2 | 2
2020-12-18 20:00 | 2020-12-18 | 20 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-12-18 21:00 | 2020-12-18 | 21 | 3.6743 | 0.01276% | 5.4782 | 5.6808 | 5.8908 | 6.1087 | 6.3345 | 0 | 0 | 0.15383 | 0.37166 | 0.59755
2020-12-18 22:00 | 2020-12-18 | 22 | 3.4785 | 0.01208% | 5.1863 | 5.3781 | 5.577 | 5.7832 | 5.9971 | 0 | 0 | 0 | 0.046198 | 0.26005
2020-12-18 23:00 | 2020-12-18 | 23 | 3.1999 | 0.01111% | 4.771 | 4.9474 | 5.1303 | 5.32 | 5.5168 | 0 | 0 | 0 | 0 | 0
2020-12-19 | 2020-12-18 | 0 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-12-19 01:00 | 2020-12-19 | 1 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-12-19 02:00 | 2020-12-19 | 2 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-19 03:00 | 2020-12-19 | 3 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-19 04:00 | 2020-12-19 | 4 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-19 05:00 | 2020-12-19 | 5 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-12-19 06:00 | 2020-12-19 | 6 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-12-19 07:00 | 2020-12-19 | 7 | 2.8762 | 0.009987% | 4.2883 | 4.4468 | 4.6113 | 4.7818 | 4.9586 | 0 | 0 | 0 | 0 | 0
2020-12-19 08:00 | 2020-12-19 | 8 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-12-19 09:00 | 2020-12-19 | 9 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-19 10:00 | 2020-12-19 | 10 | 3.5237 | 0.01224% | 5.2537 | 5.4479 | 5.6494 | 5.8583 | 6.0749 | 0 | 0 | 0 | 0.1213 | 0.33794
2020-12-19 11:00 | 2020-12-19 | 11 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-19 12:00 | 2020-12-19 | 12 | 3.6517 | 0.01268% | 5.4445 | 5.6458 | 5.8546 | 6.0711 | 6.2956 | 0 | 0 | 0.11761 | 0.33411 | 0.55861
2020-12-19 13:00 | 2020-12-19 | 13 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-19 14:00 | 2020-12-19 | 14 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-12-19 15:00 | 2020-12-19 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-19 16:00 | 2020-12-19 | 16 | 3.5312 | 0.01226% | 5.2649 | 5.4596 | 5.6615 | 5.8708 | 6.0879 | 0 | 0 | 0 | 0.13382 | 0.35092
2020-12-19 17:00 | 2020-12-19 | 17 | 3.7646 | 0.01307% | 5.6129 | 5.8205 | 6.0357 | 6.2589 | 6.4903 | 0 | 0.083452 | 0.29868 | 0.52187 | 0.75332
2020-12-19 18:00 | 2020-12-19 | 18 | 3.8926 | 0.01352% | 5.8037 | 6.0183 | 6.2409 | 6.4717 | 6.711 | 0.066735 | 0.28135 | 0.5039 | 0.73467 | 0.97399 | 1 | 1
2020-12-19 19:00 | 2020-12-19 | 19 | 3.8173 | 0.01326% | 5.6915 | 5.9019 | 6.1202 | 6.3465 | 6.5812 | 0 | 0.16494 | 0.38318 | 0.6095 | 0.84418
2020-12-19 20:00 | 2020-12-19 | 20 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-19 21:00 | 2020-12-19 | 21 | 3.5086 | 0.01218% | 5.2312 | 5.4247 | 5.6253 | 5.8333 | 6.049 | 0 | 0 | 0 | 0.096269 | 0.31197
2020-12-19 22:00 | 2020-12-19 | 22 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-12-19 23:00 | 2020-12-19 | 23 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-12-20 | 2020-12-19 | 0 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-12-20 01:00 | 2020-12-20 | 1 | 2.4922 | 0.008654% | 3.7157 | 3.8531 | 3.9956 | 4.1434 | 4.2966 | 0 | 0 | 0 | 0 | 0
2020-12-20 02:00 | 2020-12-20 | 2 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-12-20 03:00 | 2020-12-20 | 3 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-20 04:00 | 2020-12-20 | 4 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-12-20 05:00 | 2020-12-20 | 5 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-12-20 06:00 | 2020-12-20 | 6 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-12-20 07:00 | 2020-12-20 | 7 | 2.7557 | 0.009569% | 4.1086 | 4.2606 | 4.4181 | 4.5815 | 4.7509 | 0 | 0 | 0 | 0 | 0
2020-12-20 08:00 | 2020-12-20 | 8 | 2.9439 | 0.01022% | 4.3893 | 4.5516 | 4.7199 | 4.8944 | 5.0754 | 0 | 0 | 0 | 0 | 0
2020-12-20 09:00 | 2020-12-20 | 9 | 3.1623 | 0.01098% | 4.7148 | 4.8892 | 5.07 | 5.2575 | 5.4519 | 0 | 0 | 0 | 0 | 0
2020-12-20 10:00 | 2020-12-20 | 10 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-20 11:00 | 2020-12-20 | 11 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-20 12:00 | 2020-12-20 | 12 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-20 13:00 | 2020-12-20 | 13 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-20 14:00 | 2020-12-20 | 14 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-12-20 15:00 | 2020-12-20 | 15 | 3.4484 | 0.01197% | 5.1414 | 5.3315 | 5.5287 | 5.7331 | 5.9451 | 0 | 0 | 0 | 0 | 0.20813
2020-12-20 16:00 | 2020-12-20 | 16 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-20 17:00 | 2020-12-20 | 17 | 3.7797 | 0.01312% | 5.6353 | 5.8437 | 6.0598 | 6.2839 | 6.5163 | 0 | 0.10673 | 0.32283 | 0.54691 | 0.77928
2020-12-20 18:00 | 2020-12-20 | 18 | 3.742 | 0.01299% | 5.5792 | 5.7855 | 5.9995 | 6.2213 | 6.4514 | 0 | 0.048529 | 0.26247 | 0.48432 | 0.71437
2020-12-20 19:00 | 2020-12-20 | 19 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-20 20:00 | 2020-12-20 | 20 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-12-20 21:00 | 2020-12-20 | 21 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-20 22:00 | 2020-12-20 | 22 | 3.1397 | 0.0109% | 4.6812 | 4.8543 | 5.0338 | 5.2199 | 5.4129 | 0 | 0 | 0 | 0 | 0
2020-12-20 23:00 | 2020-12-20 | 23 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-12-21 | 2020-12-20 | 0 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-12-21 01:00 | 2020-12-21 | 1 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-12-21 02:00 | 2020-12-21 | 2 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-12-21 03:00 | 2020-12-21 | 3 | 2.3642 | 0.008209% | 3.5249 | 3.6552 | 3.7904 | 3.9306 | 4.0759 | 0 | 0 | 0 | 0 | 0
2020-12-21 04:00 | 2020-12-21 | 4 | 2.4244 | 0.008418% | 3.6147 | 3.7484 | 3.887 | 4.0307 | 4.1798 | 0 | 0 | 0 | 0 | 0
2020-12-21 05:00 | 2020-12-21 | 5 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-21 06:00 | 2020-12-21 | 6 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-12-21 07:00 | 2020-12-21 | 7 | 2.9289 | 0.01017% | 4.3668 | 4.5283 | 4.6958 | 4.8694 | 5.0495 | 0 | 0 | 0 | 0 | 0
2020-12-21 08:00 | 2020-12-21 | 8 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-12-21 09:00 | 2020-12-21 | 9 | 3.1924 | 0.01109% | 4.7597 | 4.9357 | 5.1183 | 5.3075 | 5.5038 | 0 | 0 | 0 | 0 | 0
2020-12-21 10:00 | 2020-12-21 | 10 | 3.3882 | 0.01176% | 5.0516 | 5.2384 | 5.4321 | 5.633 | 5.8413 | 0 | 0 | 0 | 0 | 0.10428
2020-12-21 11:00 | 2020-12-21 | 11 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-12-21 12:00 | 2020-12-21 | 12 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-21 13:00 | 2020-12-21 | 13 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-12-21 14:00 | 2020-12-21 | 14 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-21 15:00 | 2020-12-21 | 15 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-21 16:00 | 2020-12-21 | 16 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-12-21 17:00 | 2020-12-21 | 17 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-12-21 18:00 | 2020-12-21 | 18 | 3.9001 | 0.01354% | 5.815 | 6.03 | 6.253 | 6.4842 | 6.724 | 0.077961 | 0.29299 | 0.51597 | 0.74719 | 0.98697 | 1 | 1
2020-12-21 19:00 | 2020-12-21 | 19 | 3.6667 | 0.01273% | 5.467 | 5.6691 | 5.8788 | 6.0961 | 6.3216 | 0 | 0 | 0.14176 | 0.35914 | 0.58457
2020-12-21 20:00 | 2020-12-21 | 20 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-21 21:00 | 2020-12-21 | 21 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-12-21 22:00 | 2020-12-21 | 22 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-12-21 23:00 | 2020-12-21 | 23 | 3.0117 | 0.01046% | 4.4903 | 4.6564 | 4.8285 | 5.0071 | 5.1923 | 0 | 0 | 0 | 0 | 0
2020-12-22 | 2020-12-21 | 0 | 2.5976 | 0.00902% | 3.8729 | 4.0161 | 4.1646 | 4.3186 | 4.4783 | 0 | 0 | 0 | 0 | 0
2020-12-22 01:00 | 2020-12-22 | 1 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-12-22 02:00 | 2020-12-22 | 2 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-12-22 03:00 | 2020-12-22 | 3 | 2.4545 | 0.008523% | 3.6596 | 3.7949 | 3.9353 | 4.0808 | 4.2317 | 0 | 0 | 0 | 0 | 0
2020-12-22 04:00 | 2020-12-22 | 4 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-22 05:00 | 2020-12-22 | 5 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-12-22 06:00 | 2020-12-22 | 6 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-12-22 07:00 | 2020-12-22 | 7 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-12-22 08:00 | 2020-12-22 | 8 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-22 09:00 | 2020-12-22 | 9 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-12-22 10:00 | 2020-12-22 | 10 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-22 11:00 | 2020-12-22 | 11 | 3.3656 | 0.01169% | 5.0179 | 5.2035 | 5.3959 | 5.5954 | 5.8023 | 0 | 0 | 0 | 0 | 0.065342
2020-12-22 12:00 | 2020-12-22 | 12 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-22 13:00 | 2020-12-22 | 13 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-22 14:00 | 2020-12-22 | 14 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-22 15:00 | 2020-12-22 | 15 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-12-22 16:00 | 2020-12-22 | 16 | 3.4032 | 0.01182% | 5.0741 | 5.2617 | 5.4563 | 5.658 | 5.8672 | 0 | 0 | 0 | 0 | 0.13025
2020-12-22 17:00 | 2020-12-22 | 17 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-22 18:00 | 2020-12-22 | 18 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-12-22 19:00 | 2020-12-22 | 19 | 3.7119 | 0.01289% | 5.5343 | 5.739 | 5.9512 | 6.1712 | 6.3995 | 0 | 0.0019658 | 0.21418 | 0.43425 | 0.66245
2020-12-22 20:00 | 2020-12-22 | 20 | 3.5764 | 0.01242% | 5.3323 | 5.5294 | 5.7339 | 5.9459 | 6.1658 | 0 | 0 | 0 | 0.20893 | 0.4288
2020-12-22 21:00 | 2020-12-22 | 21 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-12-22 22:00 | 2020-12-22 | 22 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-12-22 23:00 | 2020-12-22 | 23 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-12-23 | 2020-12-22 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-23 01:00 | 2020-12-23 | 1 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-12-23 02:00 | 2020-12-23 | 2 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-12-23 03:00 | 2020-12-23 | 3 | 2.575 | 0.008941% | 3.8392 | 3.9812 | 4.1284 | 4.2811 | 4.4394 | 0 | 0 | 0 | 0 | 0
2020-12-23 04:00 | 2020-12-23 | 4 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-12-23 05:00 | 2020-12-23 | 5 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-12-23 06:00 | 2020-12-23 | 6 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-23 07:00 | 2020-12-23 | 7 | 3.0795 | 0.01069% | 4.5913 | 4.7611 | 4.9372 | 5.1198 | 5.3091 | 0 | 0 | 0 | 0 | 0
2020-12-23 08:00 | 2020-12-23 | 8 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-23 09:00 | 2020-12-23 | 9 | 3.4107 | 0.01184% | 5.0853 | 5.2733 | 5.4683 | 5.6705 | 5.8802 | 0 | 0 | 0 | 0 | 0.14323
2020-12-23 10:00 | 2020-12-23 | 10 | 3.5387 | 0.01229% | 5.2761 | 5.4712 | 5.6735 | 5.8833 | 6.1009 | 0 | 0 | 0 | 0.14634 | 0.3639
2020-12-23 11:00 | 2020-12-23 | 11 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-23 12:00 | 2020-12-23 | 12 | 3.6592 | 0.01271% | 5.4557 | 5.6575 | 5.8667 | 6.0836 | 6.3086 | 0 | 0 | 0.12968 | 0.34662 | 0.57159
2020-12-23 13:00 | 2020-12-23 | 13 | 3.5839 | 0.01244% | 5.3435 | 5.5411 | 5.746 | 5.9584 | 6.1788 | 0 | 0 | 0.0089702 | 0.22145 | 0.44178
2020-12-23 14:00 | 2020-12-23 | 14 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-12-23 15:00 | 2020-12-23 | 15 | 3.6818 | 0.01278% | 5.4894 | 5.6924 | 5.9029 | 6.1212 | 6.3475 | 0 | 0 | 0.1659 | 0.38418 | 0.61053
2020-12-23 16:00 | 2020-12-23 | 16 | 3.5613 | 0.01237% | 5.3098 | 5.5061 | 5.7098 | 5.9209 | 6.1398 | 0 | 0 | 0 | 0.18389 | 0.40284
2020-12-23 17:00 | 2020-12-23 | 17 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-12-23 18:00 | 2020-12-23 | 18 | 3.87 | 0.01344% | 5.7701 | 5.9834 | 6.2047 | 6.4341 | 6.672 | 0.033057 | 0.24642 | 0.46768 | 0.69712 | 0.93504 | 1 | 1
2020-12-23 19:00 | 2020-12-23 | 19 | 3.614 | 0.01255% | 5.3884 | 5.5876 | 5.7943 | 6.0085 | 6.2307 | 0 | 0 | 0.057256 | 0.27152 | 0.4937
2020-12-23 20:00 | 2020-12-23 | 20 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-23 21:00 | 2020-12-23 | 21 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-12-23 22:00 | 2020-12-23 | 22 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-23 23:00 | 2020-12-23 | 23 | 3.0267 | 0.01051% | 4.5128 | 4.6796 | 4.8527 | 5.0321 | 5.2182 | 0 | 0 | 0 | 0 | 0
2020-12-24 | 2020-12-23 | 0 | 2.7331 | 0.00949% | 4.075 | 4.2256 | 4.3819 | 4.5439 | 4.712 | 0 | 0 | 0 | 0 | 0
2020-12-24 01:00 | 2020-12-24 | 1 | 2.5901 | 0.008994% | 3.8617 | 4.0045 | 4.1525 | 4.3061 | 4.4653 | 0 | 0 | 0 | 0 | 0
2020-12-24 02:00 | 2020-12-24 | 2 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-24 03:00 | 2020-12-24 | 3 | 2.4018 | 0.00834% | 3.581 | 3.7134 | 3.8508 | 3.9932 | 4.1408 | 0 | 0 | 0 | 0 | 0
2020-12-24 04:00 | 2020-12-24 | 4 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-24 05:00 | 2020-12-24 | 5 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-24 06:00 | 2020-12-24 | 6 | 2.5223 | 0.008758% | 3.7606 | 3.8997 | 4.0439 | 4.1934 | 4.3485 | 0 | 0 | 0 | 0 | 0
2020-12-24 07:00 | 2020-12-24 | 7 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-12-24 08:00 | 2020-12-24 | 8 | 3.0343 | 0.01054% | 4.524 | 4.6913 | 4.8648 | 5.0447 | 5.2312 | 0 | 0 | 0 | 0 | 0
2020-12-24 09:00 | 2020-12-24 | 9 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-12-24 10:00 | 2020-12-24 | 10 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-12-24 11:00 | 2020-12-24 | 11 | 3.471 | 0.01205% | 5.1751 | 5.3665 | 5.5649 | 5.7707 | 5.9841 | 0 | 0 | 0 | 0.033681 | 0.24707
2020-12-24 12:00 | 2020-12-24 | 12 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-24 13:00 | 2020-12-24 | 13 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-12-24 14:00 | 2020-12-24 | 14 | 3.4634 | 0.01203% | 5.1639 | 5.3548 | 5.5528 | 5.7582 | 5.9711 | 0 | 0 | 0 | 0.021163 | 0.23409
2020-12-24 15:00 | 2020-12-24 | 15 | 3.3279 | 0.01156% | 4.9618 | 5.1453 | 5.3355 | 5.5328 | 5.7374 | 0 | 0 | 0 | 0 | 0.00043918
2020-12-24 16:00 | 2020-12-24 | 16 | 3.2451 | 0.01127% | 4.8383 | 5.0172 | 5.2028 | 5.3951 | 5.5947 | 0 | 0 | 0 | 0 | 0
2020-12-24 17:00 | 2020-12-24 | 17 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-24 18:00 | 2020-12-24 | 18 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-24 19:00 | 2020-12-24 | 19 | 3.1246 | 0.01085% | 4.6587 | 4.831 | 5.0096 | 5.1949 | 5.387 | 0 | 0 | 0 | 0 | 0
2020-12-24 20:00 | 2020-12-24 | 20 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-12-24 21:00 | 2020-12-24 | 21 | 2.9063 | 0.01009% | 4.3332 | 4.4934 | 4.6595 | 4.8318 | 5.0105 | 0 | 0 | 0 | 0 | 0
2020-12-24 22:00 | 2020-12-24 | 22 | 2.831 | 0.00983% | 4.2209 | 4.377 | 4.5388 | 4.7067 | 4.8807 | 0 | 0 | 0 | 0 | 0
2020-12-24 23:00 | 2020-12-24 | 23 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-25 | 2020-12-24 | 0 | 2.6879 | 0.009333% | 4.0076 | 4.1558 | 4.3095 | 4.4688 | 4.6341 | 0 | 0 | 0 | 0 | 0
2020-12-25 01:00 | 2020-12-25 | 1 | 2.3265 | 0.008079% | 3.4688 | 3.597 | 3.7301 | 3.868 | 4.011 | 0 | 0 | 0 | 0 | 0
2020-12-25 02:00 | 2020-12-25 | 2 | 2.2437 | 0.007791% | 3.3453 | 3.469 | 3.5973 | 3.7303 | 3.8682 | 0 | 0 | 0 | 0 | 0
2020-12-25 03:00 | 2020-12-25 | 3 | 2.2136 | 0.007686% | 3.3004 | 3.4224 | 3.549 | 3.6802 | 3.8163 | 0 | 0 | 0 | 0 | 0
2020-12-25 04:00 | 2020-12-25 | 4 | 2.1383 | 0.007425% | 3.1881 | 3.306 | 3.4283 | 3.555 | 3.6865 | 0 | 0 | 0 | 0 | 0
2020-12-25 05:00 | 2020-12-25 | 5 | 2.1308 | 0.007399% | 3.1769 | 3.2944 | 3.4162 | 3.5425 | 3.6735 | 0 | 0 | 0 | 0 | 0
2020-12-25 06:00 | 2020-12-25 | 6 | 2.2362 | 0.007765% | 3.3341 | 3.4573 | 3.5852 | 3.7178 | 3.8552 | 0 | 0 | 0 | 0 | 0
2020-12-25 07:00 | 2020-12-25 | 7 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-25 08:00 | 2020-12-25 | 8 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-25 09:00 | 2020-12-25 | 9 | 2.4846 | 0.008628% | 3.7045 | 3.8415 | 3.9836 | 4.1309 | 4.2836 | 0 | 0 | 0 | 0 | 0
2020-12-25 10:00 | 2020-12-25 | 10 | 2.6277 | 0.009124% | 3.9178 | 4.0627 | 4.2129 | 4.3687 | 4.5302 | 0 | 0 | 0 | 0 | 0
2020-12-25 11:00 | 2020-12-25 | 11 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-12-25 12:00 | 2020-12-25 | 12 | 2.8536 | 0.009909% | 4.2546 | 4.4119 | 4.575 | 4.7442 | 4.9197 | 0 | 0 | 0 | 0 | 0
2020-12-25 13:00 | 2020-12-25 | 13 | 2.7482 | 0.009543% | 4.0974 | 4.2489 | 4.406 | 4.569 | 4.7379 | 0 | 0 | 0 | 0 | 0
2020-12-25 14:00 | 2020-12-25 | 14 | 2.8084 | 0.009752% | 4.1872 | 4.3421 | 4.5026 | 4.6691 | 4.8418 | 0 | 0 | 0 | 0 | 0
2020-12-25 15:00 | 2020-12-25 | 15 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-12-25 16:00 | 2020-12-25 | 16 | 2.7858 | 0.009673% | 4.1535 | 4.3071 | 4.4664 | 4.6316 | 4.8028 | 0 | 0 | 0 | 0 | 0
2020-12-25 17:00 | 2020-12-25 | 17 | 3.0644 | 0.01064% | 4.5689 | 4.7378 | 4.913 | 5.0947 | 5.2831 | 0 | 0 | 0 | 0 | 0
2020-12-25 18:00 | 2020-12-25 | 18 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-12-25 19:00 | 2020-12-25 | 19 | 2.9966 | 0.01041% | 4.4679 | 4.6331 | 4.8044 | 4.9821 | 5.1663 | 0 | 0 | 0 | 0 | 0
2020-12-25 20:00 | 2020-12-25 | 20 | 2.9213 | 0.01014% | 4.3556 | 4.5167 | 4.6837 | 4.8569 | 5.0365 | 0 | 0 | 0 | 0 | 0
2020-12-25 21:00 | 2020-12-25 | 21 | 2.9138 | 0.01012% | 4.3444 | 4.505 | 4.6716 | 4.8444 | 5.0235 | 0 | 0 | 0 | 0 | 0
2020-12-25 22:00 | 2020-12-25 | 22 | 2.8009 | 0.009726% | 4.176 | 4.3304 | 4.4905 | 4.6566 | 4.8288 | 0 | 0 | 0 | 0 | 0
2020-12-25 23:00 | 2020-12-25 | 23 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-12-26 | 2020-12-25 | 0 | 2.4094 | 0.008366% | 3.5923 | 3.7251 | 3.8628 | 4.0057 | 4.1538 | 0 | 0 | 0 | 0 | 0
2020-12-26 01:00 | 2020-12-26 | 1 | 2.4696 | 0.008575% | 3.6821 | 3.8182 | 3.9594 | 4.1058 | 4.2576 | 0 | 0 | 0 | 0 | 0
2020-12-26 02:00 | 2020-12-26 | 2 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-12-26 03:00 | 2020-12-26 | 3 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-26 04:00 | 2020-12-26 | 4 | 2.3792 | 0.008262% | 3.5474 | 3.6785 | 3.8146 | 3.9556 | 4.1019 | 0 | 0 | 0 | 0 | 0
2020-12-26 05:00 | 2020-12-26 | 5 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-12-26 06:00 | 2020-12-26 | 6 | 2.4319 | 0.008445% | 3.6259 | 3.76 | 3.8991 | 4.0432 | 4.1927 | 0 | 0 | 0 | 0 | 0
2020-12-26 07:00 | 2020-12-26 | 7 | 2.6352 | 0.00915% | 3.929 | 4.0743 | 4.225 | 4.3812 | 4.5432 | 0 | 0 | 0 | 0 | 0
2020-12-26 08:00 | 2020-12-26 | 8 | 2.8235 | 0.009804% | 4.2097 | 4.3653 | 4.5268 | 4.6942 | 4.8677 | 0 | 0 | 0 | 0 | 0
2020-12-26 09:00 | 2020-12-26 | 9 | 2.8912 | 0.01004% | 4.3107 | 4.4701 | 4.6354 | 4.8068 | 4.9846 | 0 | 0 | 0 | 0 | 0
2020-12-26 10:00 | 2020-12-26 | 10 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-12-26 11:00 | 2020-12-26 | 11 | 3.102 | 0.01077% | 4.625 | 4.7961 | 4.9734 | 5.1573 | 5.348 | 0 | 0 | 0 | 0 | 0
2020-12-26 12:00 | 2020-12-26 | 12 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-26 13:00 | 2020-12-26 | 13 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-26 14:00 | 2020-12-26 | 14 | 3.2602 | 0.01132% | 4.8608 | 5.0405 | 5.2269 | 5.4202 | 5.6206 | 0 | 0 | 0 | 0 | 0
2020-12-26 15:00 | 2020-12-26 | 15 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-26 16:00 | 2020-12-26 | 16 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-12-26 17:00 | 2020-12-26 | 17 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-26 18:00 | 2020-12-26 | 18 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-26 19:00 | 2020-12-26 | 19 | 3.4409 | 0.01195% | 5.1302 | 5.3199 | 5.5166 | 5.7206 | 5.9321 | 0 | 0 | 0 | 0 | 0.19515
2020-12-26 20:00 | 2020-12-26 | 20 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-26 21:00 | 2020-12-26 | 21 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-12-26 22:00 | 2020-12-26 | 22 | 2.9816 | 0.01035% | 4.4454 | 4.6098 | 4.7803 | 4.957 | 5.1403 | 0 | 0 | 0 | 0 | 0
2020-12-26 23:00 | 2020-12-26 | 23 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-12-27 | 2020-12-26 | 0 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-12-27 01:00 | 2020-12-27 | 1 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-12-27 02:00 | 2020-12-27 | 2 | 2.3868 | 0.008288% | 3.5586 | 3.6902 | 3.8266 | 3.9681 | 4.1149 | 0 | 0 | 0 | 0 | 0
2020-12-27 03:00 | 2020-12-27 | 3 | 2.3115 | 0.008026% | 3.4463 | 3.5738 | 3.7059 | 3.8429 | 3.9851 | 0 | 0 | 0 | 0 | 0
2020-12-27 04:00 | 2020-12-27 | 4 | 2.2964 | 0.007974% | 3.4239 | 3.5505 | 3.6818 | 3.8179 | 3.9591 | 0 | 0 | 0 | 0 | 0
2020-12-27 05:00 | 2020-12-27 | 5 | 2.319 | 0.008052% | 3.4575 | 3.5854 | 3.718 | 3.8555 | 3.998 | 0 | 0 | 0 | 0 | 0
2020-12-27 06:00 | 2020-12-27 | 6 | 2.3491 | 0.008157% | 3.5024 | 3.632 | 3.7663 | 3.9055 | 4.05 | 0 | 0 | 0 | 0 | 0
2020-12-27 07:00 | 2020-12-27 | 7 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-27 08:00 | 2020-12-27 | 8 | 2.6729 | 0.009281% | 3.9852 | 4.1325 | 4.2853 | 4.4438 | 4.6081 | 0 | 0 | 0 | 0 | 0
2020-12-27 09:00 | 2020-12-27 | 9 | 2.8159 | 0.009778% | 4.1984 | 4.3537 | 4.5147 | 4.6816 | 4.8548 | 0 | 0 | 0 | 0 | 0
2020-12-27 10:00 | 2020-12-27 | 10 | 2.959 | 0.01027% | 4.4117 | 4.5749 | 4.744 | 4.9195 | 5.1014 | 0 | 0 | 0 | 0 | 0
2020-12-27 11:00 | 2020-12-27 | 11 | 3.1322 | 0.01088% | 4.6699 | 4.8426 | 5.0217 | 5.2074 | 5.3999 | 0 | 0 | 0 | 0 | 0
2020-12-27 12:00 | 2020-12-27 | 12 | 3.1547 | 0.01095% | 4.7036 | 4.8775 | 5.0579 | 5.2449 | 5.4389 | 0 | 0 | 0 | 0 | 0
2020-12-27 13:00 | 2020-12-27 | 13 | 3.2526 | 0.01129% | 4.8495 | 5.0289 | 5.2148 | 5.4077 | 5.6076 | 0 | 0 | 0 | 0 | 0
2020-12-27 14:00 | 2020-12-27 | 14 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-12-27 15:00 | 2020-12-27 | 15 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-27 16:00 | 2020-12-27 | 16 | 3.3129 | 0.0115% | 4.9393 | 5.122 | 5.3114 | 5.5078 | 5.7115 | 0 | 0 | 0 | 0 | 0
2020-12-27 17:00 | 2020-12-27 | 17 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-27 18:00 | 2020-12-27 | 18 | 3.6366 | 0.01263% | 5.4221 | 5.6226 | 5.8305 | 6.0461 | 6.2696 | 0 | 0 | 0.09347 | 0.30907 | 0.53265
2020-12-27 19:00 | 2020-12-27 | 19 | 3.5161 | 0.01221% | 5.2424 | 5.4363 | 5.6373 | 5.8458 | 6.062 | 0 | 0 | 0 | 0.10879 | 0.32495
2020-12-27 20:00 | 2020-12-27 | 20 | 3.3731 | 0.01171% | 5.0292 | 5.2151 | 5.408 | 5.608 | 5.8153 | 0 | 0 | 0 | 0 | 0.078323
2020-12-27 21:00 | 2020-12-27 | 21 | 3.1698 | 0.01101% | 4.7261 | 4.9008 | 5.082 | 5.27 | 5.4648 | 0 | 0 | 0 | 0 | 0
2020-12-27 22:00 | 2020-12-27 | 22 | 2.9515 | 0.01025% | 4.4005 | 4.5632 | 4.732 | 4.907 | 5.0884 | 0 | 0 | 0 | 0 | 0
2020-12-27 23:00 | 2020-12-27 | 23 | 2.7933 | 0.0097% | 4.1648 | 4.3188 | 4.4785 | 4.6441 | 4.8158 | 0 | 0 | 0 | 0 | 0
2020-12-28 | 2020-12-27 | 0 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-28 01:00 | 2020-12-28 | 1 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-28 02:00 | 2020-12-28 | 2 | 2.5072 | 0.008706% | 3.7382 | 3.8764 | 4.0198 | 4.1684 | 4.3226 | 0 | 0 | 0 | 0 | 0
2020-12-28 03:00 | 2020-12-28 | 3 | 2.4621 | 0.008549% | 3.6708 | 3.8066 | 3.9473 | 4.0933 | 4.2447 | 0 | 0 | 0 | 0 | 0
2020-12-28 04:00 | 2020-12-28 | 4 | 2.3566 | 0.008183% | 3.5137 | 3.6436 | 3.7783 | 3.9181 | 4.0629 | 0 | 0 | 0 | 0 | 0
2020-12-28 05:00 | 2020-12-28 | 5 | 2.4395 | 0.008471% | 3.6372 | 3.7717 | 3.9111 | 4.0557 | 4.2057 | 0 | 0 | 0 | 0 | 0
2020-12-28 06:00 | 2020-12-28 | 6 | 2.5449 | 0.008837% | 3.7943 | 3.9346 | 4.0801 | 4.231 | 4.3875 | 0 | 0 | 0 | 0 | 0
2020-12-28 07:00 | 2020-12-28 | 7 | 2.6428 | 0.009177% | 3.9403 | 4.086 | 4.237 | 4.3937 | 4.5562 | 0 | 0 | 0 | 0 | 0
2020-12-28 08:00 | 2020-12-28 | 8 | 2.8686 | 0.009961% | 4.277 | 4.4352 | 4.5992 | 4.7693 | 4.9456 | 0 | 0 | 0 | 0 | 0
2020-12-28 09:00 | 2020-12-28 | 9 | 2.9891 | 0.01038% | 4.4566 | 4.6214 | 4.7923 | 4.9695 | 5.1533 | 0 | 0 | 0 | 0 | 0
2020-12-28 10:00 | 2020-12-28 | 10 | 3.1171 | 0.01082% | 4.6475 | 4.8193 | 4.9975 | 5.1823 | 5.374 | 0 | 0 | 0 | 0 | 0
2020-12-28 11:00 | 2020-12-28 | 11 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-12-28 12:00 | 2020-12-28 | 12 | 3.3957 | 0.01179% | 5.0628 | 5.25 | 5.4442 | 5.6455 | 5.8543 | 0 | 0 | 0 | 0 | 0.11726
2020-12-28 13:00 | 2020-12-28 | 13 | 3.3204 | 0.01153% | 4.9506 | 5.1336 | 5.3235 | 5.5203 | 5.7245 | 0 | 0 | 0 | 0 | 0
2020-12-28 14:00 | 2020-12-28 | 14 | 3.2978 | 0.01145% | 4.9169 | 5.0987 | 5.2873 | 5.4828 | 5.6855 | 0 | 0 | 0 | 0 | 0
2020-12-28 15:00 | 2020-12-28 | 15 | 3.343 | 0.01161% | 4.9843 | 5.1686 | 5.3597 | 5.5579 | 5.7634 | 0 | 0 | 0 | 0 | 0.0264
2020-12-28 16:00 | 2020-12-28 | 16 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-28 17:00 | 2020-12-28 | 17 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-12-28 18:00 | 2020-12-28 | 18 | 3.599 | 0.0125% | 5.3659 | 5.5644 | 5.7701 | 5.9835 | 6.2047 | 0 | 0 | 0.033113 | 0.24648 | 0.46774
2020-12-28 19:00 | 2020-12-28 | 19 | 3.5463 | 0.01231% | 5.2873 | 5.4829 | 5.6856 | 5.8959 | 6.1139 | 0 | 0 | 0 | 0.15886 | 0.37688
2020-12-28 20:00 | 2020-12-28 | 20 | 3.358 | 0.01166% | 5.0067 | 5.1918 | 5.3838 | 5.5829 | 5.7894 | 0 | 0 | 0 | 0 | 0.052362
2020-12-28 21:00 | 2020-12-28 | 21 | 3.23 | 0.01122% | 4.8159 | 4.9939 | 5.1786 | 5.3701 | 5.5687 | 0 | 0 | 0 | 0 | 0
2020-12-28 22:00 | 2020-12-28 | 22 | 3.2074 | 0.01114% | 4.7822 | 4.959 | 5.1424 | 5.3326 | 5.5297 | 0 | 0 | 0 | 0 | 0
2020-12-28 23:00 | 2020-12-28 | 23 | 2.8988 | 0.01007% | 4.3219 | 4.4817 | 4.6475 | 4.8193 | 4.9975 | 0 | 0 | 0 | 0 | 0
2020-12-29 | 2020-12-28 | 0 | 2.6578 | 0.009229% | 3.9627 | 4.1092 | 4.2612 | 4.4188 | 4.5822 | 0 | 0 | 0 | 0 | 0
2020-12-29 01:00 | 2020-12-29 | 1 | 2.5148 | 0.008732% | 3.7494 | 3.8881 | 4.0318 | 4.1809 | 4.3355 | 0 | 0 | 0 | 0 | 0
2020-12-29 02:00 | 2020-12-29 | 2 | 2.4997 | 0.00868% | 3.727 | 3.8648 | 4.0077 | 4.1559 | 4.3096 | 0 | 0 | 0 | 0 | 0
2020-12-29 03:00 | 2020-12-29 | 3 | 2.4169 | 0.008392% | 3.6035 | 3.7367 | 3.8749 | 4.0182 | 4.1668 | 0 | 0 | 0 | 0 | 0
2020-12-29 04:00 | 2020-12-29 | 4 | 2.3717 | 0.008235% | 3.5361 | 3.6669 | 3.8025 | 3.9431 | 4.0889 | 0 | 0 | 0 | 0 | 0
2020-12-29 05:00 | 2020-12-29 | 5 | 2.447 | 0.008497% | 3.6484 | 3.7833 | 3.9232 | 4.0683 | 4.2187 | 0 | 0 | 0 | 0 | 0
2020-12-29 06:00 | 2020-12-29 | 6 | 2.6051 | 0.009046% | 3.8841 | 4.0278 | 4.1767 | 4.3311 | 4.4913 | 0 | 0 | 0 | 0 | 0
2020-12-29 07:00 | 2020-12-29 | 7 | 2.8385 | 0.009856% | 4.2321 | 4.3886 | 4.5509 | 4.7192 | 4.8937 | 0 | 0 | 0 | 0 | 0
2020-12-29 08:00 | 2020-12-29 | 8 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-12-29 09:00 | 2020-12-29 | 9 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-12-29 10:00 | 2020-12-29 | 10 | 3.2752 | 0.01137% | 4.8832 | 5.0638 | 5.251 | 5.4452 | 5.6466 | 0 | 0 | 0 | 0 | 0
2020-12-29 11:00 | 2020-12-29 | 11 | 3.2677 | 0.01135% | 4.872 | 5.0522 | 5.239 | 5.4327 | 5.6336 | 0 | 0 | 0 | 0 | 0
2020-12-29 12:00 | 2020-12-29 | 12 | 3.2827 | 0.0114% | 4.8944 | 5.0754 | 5.2631 | 5.4577 | 5.6596 | 0 | 0 | 0 | 0 | 0
2020-12-29 13:00 | 2020-12-29 | 13 | 3.4559 | 0.012% | 5.1526 | 5.3432 | 5.5408 | 5.7456 | 5.9581 | 0 | 0 | 0 | 0.0086452 | 0.22111
2020-12-29 14:00 | 2020-12-29 | 14 | 3.3505 | 0.01163% | 4.9955 | 5.1802 | 5.3718 | 5.5704 | 5.7764 | 0 | 0 | 0 | 0 | 0.039381
2020-12-29 15:00 | 2020-12-29 | 15 | 3.215 | 0.01116% | 4.7934 | 4.9707 | 5.1545 | 5.3451 | 5.5427 | 0 | 0 | 0 | 0 | 0
2020-12-29 16:00 | 2020-12-29 | 16 | 3.486 | 0.0121% | 5.1975 | 5.3897 | 5.589 | 5.7957 | 6.01 | 0 | 0 | 0 | 0.058716 | 0.27303
2020-12-29 17:00 | 2020-12-29 | 17 | 3.7194 | 0.01292% | 5.5455 | 5.7506 | 5.9633 | 6.1838 | 6.4124 | 0 | 0.013607 | 0.22625 | 0.44677 | 0.67543
2020-12-29 18:00 | 2020-12-29 | 18 | 3.855 | 0.01339% | 5.7476 | 5.9601 | 6.1805 | 6.4091 | 6.6461 | 0.010606 | 0.22314 | 0.44354 | 0.67209 | 0.90908 | 1 | 1
2020-12-29 19:00 | 2020-12-29 | 19 | 3.8399 | 0.01333% | 5.7252 | 5.9369 | 6.1564 | 6.3841 | 6.6201 | 0 | 0.19986 | 0.4194 | 0.64705 | 0.88312
2020-12-29 20:00 | 2020-12-29 | 20 | 3.6216 | 0.01258% | 5.3996 | 5.5993 | 5.8063 | 6.021 | 6.2437 | 0 | 0 | 0.069327 | 0.28404 | 0.50668
2020-12-29 21:00 | 2020-12-29 | 21 | 3.4258 | 0.0119% | 5.1077 | 5.2966 | 5.4925 | 5.6956 | 5.9062 | 0 | 0 | 0 | 0 | 0.16919
2020-12-29 22:00 | 2020-12-29 | 22 | 3.2225 | 0.01119% | 4.8046 | 4.9823 | 5.1665 | 5.3576 | 5.5557 | 0 | 0 | 0 | 0 | 0
2020-12-29 23:00 | 2020-12-29 | 23 | 3.0418 | 0.01056% | 4.5352 | 4.7029 | 4.8768 | 5.0572 | 5.2442 | 0 | 0 | 0 | 0 | 0
2020-12-30 | 2020-12-29 | 0 | 2.6503 | 0.009203% | 3.9515 | 4.0976 | 4.2491 | 4.4062 | 4.5692 | 0 | 0 | 0 | 0 | 0
2020-12-30 01:00 | 2020-12-30 | 1 | 2.6653 | 0.009255% | 3.9739 | 4.1209 | 4.2733 | 4.4313 | 4.5951 | 0 | 0 | 0 | 0 | 0
2020-12-30 02:00 | 2020-12-30 | 2 | 2.5675 | 0.008915% | 3.828 | 3.9695 | 4.1163 | 4.2686 | 4.4264 | 0 | 0 | 0 | 0 | 0
2020-12-30 03:00 | 2020-12-30 | 3 | 2.5599 | 0.008889% | 3.8168 | 3.9579 | 4.1043 | 4.256 | 4.4134 | 0 | 0 | 0 | 0 | 0
2020-12-30 04:00 | 2020-12-30 | 4 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-12-30 05:00 | 2020-12-30 | 5 | 2.5825 | 0.008967% | 3.8504 | 3.9928 | 4.1405 | 4.2936 | 4.4524 | 0 | 0 | 0 | 0 | 0
2020-12-30 06:00 | 2020-12-30 | 6 | 2.7105 | 0.009412% | 4.0413 | 4.1907 | 4.3457 | 4.5064 | 4.673 | 0 | 0 | 0 | 0 | 0
2020-12-30 07:00 | 2020-12-30 | 7 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
2020-12-30 08:00 | 2020-12-30 | 8 | 3.087 | 0.01072% | 4.6026 | 4.7728 | 4.9493 | 5.1323 | 5.3221 | 0 | 0 | 0 | 0 | 0
2020-12-30 09:00 | 2020-12-30 | 9 | 3.3053 | 0.01148% | 4.9281 | 5.1104 | 5.2993 | 5.4953 | 5.6985 | 0 | 0 | 0 | 0 | 0
2020-12-30 10:00 | 2020-12-30 | 10 | 3.4183 | 0.01187% | 5.0965 | 5.285 | 5.4804 | 5.6831 | 5.8932 | 0 | 0 | 0 | 0 | 0.15621
2020-12-30 11:00 | 2020-12-30 | 11 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-30 12:00 | 2020-12-30 | 12 | 3.4936 | 0.01213% | 5.2088 | 5.4014 | 5.6011 | 5.8082 | 6.023 | 0 | 0 | 0 | 0.071234 | 0.28601
2020-12-30 13:00 | 2020-12-30 | 13 | 3.5538 | 0.01234% | 5.2986 | 5.4945 | 5.6977 | 5.9084 | 6.1269 | 0 | 0 | 0 | 0.17138 | 0.38986
2020-12-30 14:00 | 2020-12-30 | 14 | 3.5011 | 0.01216% | 5.22 | 5.413 | 5.6132 | 5.8208 | 6.036 | 0 | 0 | 0 | 0.083752 | 0.29899
2020-12-30 15:00 | 2020-12-30 | 15 | 3.5914 | 0.01247% | 5.3547 | 5.5527 | 5.758 | 5.971 | 6.1918 | 0 | 0 | 0.021042 | 0.23396 | 0.45476
2020-12-30 16:00 | 2020-12-30 | 16 | 3.6065 | 0.01252% | 5.3772 | 5.576 | 5.7822 | 5.996 | 6.2177 | 0 | 0 | 0.045184 | 0.259 | 0.48072
2020-12-30 17:00 | 2020-12-30 | 17 | 3.7872 | 0.01315% | 5.6466 | 5.8554 | 6.0719 | 6.2964 | 6.5293 | 0 | 0.11837 | 0.3349 | 0.55943 | 0.79226
2020-12-30 18:00 | 2020-12-30 | 18 | 3.7571 | 0.01305% | 5.6017 | 5.8088 | 6.0236 | 6.2464 | 6.4773 | 0 | 0.071811 | 0.28661 | 0.50936 | 0.74034
2020-12-30 19:00 | 2020-12-30 | 19 | 3.6291 | 0.0126% | 5.4108 | 5.6109 | 5.8184 | 6.0336 | 6.2567 | 0 | 0 | 0.081398 | 0.29655 | 0.51966
2020-12-30 20:00 | 2020-12-30 | 20 | 3.4333 | 0.01192% | 5.119 | 5.3083 | 5.5045 | 5.7081 | 5.9192 | 0 | 0 | 0 | 0 | 0.18217
2020-12-30 21:00 | 2020-12-30 | 21 | 3.3354 | 0.01158% | 4.973 | 5.1569 | 5.3476 | 5.5454 | 5.7504 | 0 | 0 | 0 | 0 | 0.01342
2020-12-30 22:00 | 2020-12-30 | 22 | 3.1773 | 0.01103% | 4.7373 | 4.9125 | 5.0941 | 5.2825 | 5.4778 | 0 | 0 | 0 | 0 | 0
2020-12-30 23:00 | 2020-12-30 | 23 | 2.8611 | 0.009935% | 4.2658 | 4.4235 | 4.5871 | 4.7567 | 4.9326 | 0 | 0 | 0 | 0 | 0
Formulas:
Date = INT([Date-Time])
Date-Time = [Date-Time, row above] + TIME(1,0,0)

## 2031 forecast
Feeder | Feeder Capacity (kVA) | Peak Load (kVA) | Peak Load Forecasted (kVA) - 2031 | 2031 KW
8M1 | 7171 | 7781 | 10376 | 11528.8889
2020 peak (KW) | 7732.5139
CAGR 2020-2031 | 3.698%
Panning Capacity (kW) | 5737
MW | 5.737

## Assumptions
Power factor | 0.9
1-in-10 planning criteria:
24 | hours in a day
10 | years
87600 | hours in 10 years
0.0274% | % of hours for 1-in-10 lole
2.4 | hours per year where event could occur

## 99 LookUps (hidden)
DST Benefit Types
Distribution Capacity (Deferral or Avoidance Benefit)
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Innovation & Market
Transformation
Planning Value
DST Cost Types
DER Acquisition Cost
DER Operations, Maintenance, and Administrative (OM&A) Costs
Distribution System Ancillary Services Costs
Risks (Distribution System)
EST Benefit Types
DST Benefits
Transmission Capacity
Avoided Energy Costs
Avoided Generation Capacity Costs
Reliability (Net Avoided Outage Costs)
Resilience (Critical Load Benefits)
Planning Value
Innovation & Market Transformation
EST Cost Types
DST Costs
DER Acquisition Cost
DER (OM&A) Costs
Energy System Ancillary Costs
Risks (Energy System)