## 2025 Scorecard
Performance Measures | 2025 | 2024 | 2023 | 2022 | Trend | Target
OHSA recordable injuries | 0 | 0 | 0 | 0 | n/a | 0
Return on equity | 10.22% | 8.5% | 9.31% | 9.42% | n/a | 8.34% based on 2020 OEB cost of capital
Violations of NERC FAC-003-4 vegetation compliance standard | 0 | 0 | 0 | 0 | n/a | 0
OM&A cost per linear km | 15882 | 21733.33 | 13651.63 | 8180.74 | n/a | $10,977/km based on application revenue requirement
Average system availability | 99.9% | 99.9% | 99.9% | 99.3% | n/a | 99%

## 2024 Scorecard
Performance Measures | 2024 | 2023 | 2022 | Trend | Target
OHSA recordable injuries | 0 | 0 | 0 | n/a | 0
Return on equity |  | 9.31% | 9.42% | n/a | 8.34% based on 2020 OEB cost of capital
Violations of NERC FAC-003-4 vegetation compliance standard | 0 | 0 | 0 | n/a | 0
OM&A cost per circuit km | 21733.33 | 13651.63 | 8180.74 | n/a | $10,977/km based on application revenue requirement
Average system availability | 99.9% | 99.9% | 99.3% | n/a | 99%

## 2023 Scorecard
Performance Measures | 2023 | 2022 | Trend | Target
OHSA recordable injuries | 0 | 0 | n/a | 0
Return on equity | 9.31% | 9.42% | n/a | 8.34% based on 2020 OEB cost of capital
Violations of NERC FAC-003-4 vegetation compliance standard | 0 | 0 | n/a | 0
OM&A cost per circuit km | 13651.63 | 8180.74 | n/a | $10,977/km based on application revenue requirement
Average system availability | 99.9% | 99.3% | n/a | 99%

## 2025 Outage Report
Ontario East-West Tie Line Outage Report 2024
Date | Circuit | Event Type | Root Cause | Action | Event Duration | Status | Comments
2025-07-01 | M38L | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | 15:38 EST, 230kV circuit M38L (Marathon x Lakehead) was automatically removed from service by 'A' & 'B' Line Protections and auto reclosed
2025-07-27 | M38L | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | at 11:25 EST, 230kV circuit M38L (Marathon x Lakehead) was automatically removed from service by 'A' & 'B' Line Protections and auto reclosed

## 2024 Outage Report
Ontario East-West Tie Line Outage Report 2024
Date | Circuit | Event Type | Root Cause | Action | Event Duration | Status | Comments
2024-08-27 | W36M | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | At 2:22 EST W36M (Wawa-Marathon) tripped and reclosed. Lightning in the area B phase to ground fault

## 2023 Outage Report
Ontario East-West Tie Line Outage Report 2023
Date | Circuit | Event Type | Root Cause | Action | Event Duration | Status | Comments
2023-07-22 | M38L | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | At 12:57 The East West Tie, Lakehead - Marathon 230kV Line M38L tripped and reclosed. Hydro 1 reports lightning in the area ABGT two phase to ground fault
2023-07-25 | M38L | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | At 20:20 The East West Tie, Lakehead - Marathon 230kV Line M38L tripped and reclosed. Hydro 1 reports lightning in the area ABC three phase fault
2023-08-02 | W36M | Line Trip | Lightning | Line Patrol | 0h0m | Closed - No further action required | At 20:25, W36M (Wawa x Marathon) 230kV circuit auto-reclosed initiated by line protection. Thunderstorm in the area AG fault
2023-10-01 | W36M | Line Trip | Lightning | Line Patrol | 0h0m | Closed - No further action required | At 21:06 EST, 230 kV circuit W36M (Wawa x Marathon) Transmission was automatically removed from service and re-closed. Electrical storm activity in the area. AG fault
2023-10-01 | M38L | Line Trip | Lightning | Line Patrol | 0h0m | Closed - No further action required | At 22:17 EST, 230 kV circuit M38L (Marathon x Lakehead) was automatically removed from service reclosed. Electrical storm activity in the area.BCG fault

## 2022 Outage Report
Ontario East-West Tie Line Outage Report 2022
Date | Circuit | Event Type | Root Cause | Action | Event Duration | Status | Comments
3/29/2022 | WM + ML | Energization | N/A | Line Energized | N/A | N/A | No Fault Event Successful energization of W35M, W36M, M37L, M38L circuits
5/14/2022 | W35M | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | Lightning strike near structure E082 (White River Region) Event caused OCR to cycle once - tripped and reclosed on second cycle Lightning confirmed on Sala software
5/31/2022 | W36M | Line Trip | Faulty NGLA Assembly | Removal of F233 NGLA | 0h 0m | Closed - No further action required | High winds caused NGLA ground lead to encroach on conductor clearance limits Event caused OCR to cycle once - tripped and reclosed on second cycle
6/24/2022 | W36M | Line Trip | Faulty NGLA Assembly | Removal of F233 NGLA | 0h 0m | Closed - No further action required | High winds caused NGLA ground lead to encroach on conductor clearance limits Event caused OCR to cycle once - tripped and reclosed on second cycle
8/18/2022 | M38L | Line Trip | Lightning | Line Patrol | 0h 0m | Closed - No further action required | Lightning strike near structure C022 (Pays Plat Region) Event caused OCR to cycle once - tripped and reclosed on second cycle Lightning confirmed on Sala software
10/18/2022 | M37L | Line Outage | Faulty NGLA Assembly | Removal of A002 NGLA | 55h 46m | Closed - No further action required | High winds allowed a blown NGLA ground lead to encroach on conductor clearance limits Lead made contact with the live phase and became attached to the conductor Breaker tripped and held in the open position Relay data confirmed a ground fault on the M37L circuit
11/6/2022 | W36M | Line Trip | Faulty NGLA Assembly | Removal of F236 NGLA | 0h 0m | Closed - No further action required | High winds caused NGLA ground lead to encroach on conductor clearance limits Event caused OCR to cycle once - tripped and reclosed on second cycle
11/30/2022 | W36M | Line Trip | Faulty NGLA Assembly | Removal of F235 NGLA | 0h 0m | Closed - No further action required | High winds caused NGLA ground lead to encroach on conductor clearance limits Event caused OCR to cycle once - tripped and reclosed on second cycle
12/17/2022 | W36M | Planned Outage | Planned Maintenance | N/A | 1h 15m | Closed - No further action required | Planned outage for the removal of the faulty NGLA assembly at F233
12/17/2022 | W35M | Planned Outage | Planned Maintenance | N/A | 2h 30m | Closed - No further action required | Planned outage for the removal of the faulty NGLA assemblies at F234 & F235
2/7/2023 | M37L | Planned Outage | Planned Maintenance / Tests | N/A | 1h 0m | Closed - No further action required | Planned outage requested by HONI for testing purposes to support NOMS 22-23005 HONI P&C to place Lakehead SC21 in service to allow for readings