## 2027-FULL
Dry Core Transformer Losses Effective Jun 1, 2027
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 7.7472 | 0.1363 |  | 8.1174
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.0435 | 31.755 | 0.013013 | 2.3644 | 0.056513 | 34.1194 | 0.43781 | 4.6505 | 5.0883 | 0.45873 | 5.547
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.2449 | 12.3872 | 13.6321 | 1.3044 | 14.9366
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.6599 | 16.5163 | 18.1762 | 1.7392 | 19.9154
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 2.1164 | 20.778 | 22.8943 | 2.2175 | 25.1118
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.8219 | 28.6382 | 31.4601 | 2.9567 | 34.4168
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 3.4028 | 33.2978 | 36.7006 | 3.5654 | 40.266 |  | 2027 Proposed Rates
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.8153 | 37.2507 | 41.066 | 3.9976 | 45.0636 |  | LV | Network | Line & Transmission | Variable
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 4.5025 | 43.8194 | 48.3218 | 4.7176 | 53.0394 | GS 50 to 1,499 kW | 0.02393 | 4.6857 | 2.6522 | 8.123
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 5.6021 | 54.341 | 59.9431 | 5.8698 | 65.8129 | GS 1,500 to 4,999 kW | 0.02374 | 4.6486 | 2.6311 | 7.7968
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 5.7291 | 55.5876 | 61.3168 | 6.0029 | 67.3196 | Large Use | 0.02787 | 5.4587 | 3.0897 | 8.4323
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.9939 | 58.1715 | 64.1654 | 6.2803 | 70.4457
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 6.4412 | 62.5162 | 68.9574 | 6.749 | 75.7064
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 6.8886 | 66.8608 | 73.7493 | 7.2177 | 80.9671 | Tier 1 | 0.12 | November 1, 2025 Rate
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 0.69 | 503.7 | 0.32789 | 59.576 | 1.0179 | 563.276 | 7.8858 | 76.7745 | 84.6603 | 8.2626 | 92.9228
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 8.5485 | 83.3771 | 91.9255 | 8.9569 | 100.8825
[14 empty] | Tier 2 | 0.142 | November 1, 2025 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.64821 | 6.7243 | 7.3725 | 0.67918 | 8.0517
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.99596 | 10.19 | 11.186 | 1.0435 | 12.2296 | WMSR | 0.0041 | Jan 1, 2026 Rate
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.9919 | 20.3801 | 22.372 | 2.0871 | 24.4591 | CBR | 0.0006 | Jan 1, 2026 Rate
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.4899 | 24.7744 | 27.2643 | 2.6088 | 29.8731 | RRRP | 0.0006 | Jan 1, 2026 Rate
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 3.3198 | 33.0325 | 36.3524 | 3.4785 | 39.8308
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 0.36 | 262.8 | 0.14994 | 27.2436 | 0.50994 | 290.0436 | 3.9506 | 39.5329 | 43.4835 | 4.1394 | 47.6229
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.8968 | 49.2836 | 54.1803 | 5.1307 | 59.3111
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 0.47475 | 346.5675 | 0.20171 | 36.6492 | 0.67646 | 383.2167 | 5.2406 | 52.2324 | 57.4731 | 5.491 | 62.9641
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.9341 | 58.2048 | 64.1389 | 6.2177 | 70.3566
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 6.4284 | 63.4841 | 69.9125 | 6.7356 | 76.6481
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 6.928 | 68.8367 | 75.7647 | 7.2591 | 83.0238
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 7.4281 | 74.1906 | 81.6187 | 7.7831 | 89.4018
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 0.72525 | 529.4325 | 0.30165 | 54.8084 | 1.0269 | 584.2409 | 7.9556 | 79.632 | 87.5876 | 8.3357 | 95.9233
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 9.0051 | 90.4416 | 99.4467 | 9.4353 | 108.882
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 1.3125 | 958.125 | 0.37217 | 67.6226 | 1.6847 | 1025.7476 | 13.0515 | 139.8094 | 152.8609 | 13.6751 | 166.536
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 15.0747 | 164.4933 | 179.568 | 15.795 | 195.3629
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 17.0979 | 189.1772 | 206.2751 | 17.9149 | 224.1899
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 22.4095 | 239.7869 | 262.1964 | 23.4803 | 285.6767
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 25.1485 | 270.9628 | 296.1113 | 26.3502 | 322.4615
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 33.6142 | 359.6804 | 393.2946 | 35.2204 | 428.5151
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 40.0882 | 430.8208 | 470.9089 | 42.0037 | 512.9127
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 48.139 | 518.2122 | 566.3512 | 50.4393 | 616.7905
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 56.7709 | 613.066 | 669.8369 | 59.4837 | 729.3206
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 69.7188 | 755.3467 | 825.0656 | 73.0502 | 898.1158
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 80.0938 | 872.5878 | 952.6817 | 83.921 | 1036.6027
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2025 RPP Tiered Pricing, WMSR Pricing to be effective January 1, 2026
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2027 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date June 1, 2027
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2026-0051
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 7.7472 | 0.1363 |  | 8.1174
1.5 KVA 1PH, 1.2kV BIL | 58 | 243 | 0.43781 | 4.6505 | 5.0883 | 0.45873 | 5.547
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.2449 | 12.3872 | 13.6321 | 1.3044 | 14.9366
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.6599 | 16.5163 | 18.1762 | 1.7392 | 19.9154
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 2.1164 | 20.778 | 22.8943 | 2.2175 | 25.1118
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.8219 | 28.6382 | 31.4601 | 2.9567 | 34.4168
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 3.4028 | 33.2978 | 36.7006 | 3.5654 | 40.266
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.8153 | 37.2507 | 41.066 | 3.9976 | 45.0636
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 4.5025 | 43.8194 | 48.3218 | 4.7176 | 53.0394
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 5.6021 | 54.341 | 59.9431 | 5.8698 | 65.8129
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 5.7291 | 55.5876 | 61.3168 | 6.0029 | 67.3196
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.9939 | 58.1715 | 64.1654 | 6.2803 | 70.4457
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 6.4412 | 62.5162 | 68.9574 | 6.749 | 75.7064
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 6.8886 | 66.8608 | 73.7493 | 7.2177 | 80.9671
300 KVA 1 PH, 1.2kV BIL | 920 | 6123 | 7.8858 | 76.7745 | 84.6603 | 8.2626 | 92.9228
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 8.5485 | 83.3771 | 91.9255 | 8.9569 | 100.8825
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.64821 | 6.7243 | 7.3725 | 0.67918 | 8.0517
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.99596 | 10.19 | 11.186 | 1.0435 | 12.2296
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.9919 | 20.3801 | 22.372 | 2.0871 | 24.4591
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.4899 | 24.7744 | 27.2643 | 2.6088 | 29.8731
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 3.3198 | 33.0325 | 36.3524 | 3.4785 | 39.8308
*90 KVA 3 PH, 1.2kV BIL | 480 | 2800 | 3.9506 | 39.5329 | 43.4835 | 4.1394 | 47.6229
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.8968 | 49.2836 | 54.1803 | 5.1307 | 59.3111
125 KVA 3PH, 1.2kV BIL | 633 | 3766.67 | 5.2406 | 52.2324 | 57.4731 | 5.491 | 62.9641
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.9341 | 58.2048 | 64.1389 | 6.2177 | 70.3566
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 6.4284 | 63.4841 | 69.9125 | 6.7356 | 76.6481
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 6.928 | 68.8367 | 75.7647 | 7.2591 | 83.0238
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 7.4281 | 74.1906 | 81.6187 | 7.7831 | 89.4018
*250 KVA 3 PH, 1.2kV BIL | 967 | 5633 | 7.9556 | 79.632 | 87.5876 | 8.3357 | 95.9233
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 9.0051 | 90.4416 | 99.4467 | 9.4353 | 108.882
400 KVA 3 PH, 1.2kV BIL | 1750 | 6950 | 13.0515 | 139.8094 | 152.8609 | 13.6751 | 166.536
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 15.0747 | 164.4933 | 179.568 | 15.795 | 195.3629
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 17.0979 | 189.1772 | 206.2751 | 17.9149 | 224.1899
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 22.4095 | 239.7869 | 262.1964 | 23.4803 | 285.6767
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 25.1485 | 270.9628 | 296.1113 | 26.3502 | 322.4615
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 33.6142 | 359.6804 | 393.2946 | 35.2204 | 428.5151
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 40.0882 | 430.8208 | 470.9089 | 42.0037 | 512.9127
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 48.139 | 518.2122 | 566.3512 | 50.4393 | 616.7905
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 56.7709 | 613.066 | 669.8369 | 59.4837 | 729.3206
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 69.7188 | 755.3467 | 825.0656 | 73.0502 | 898.1158
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 80.0938 | 872.5878 | 952.6817 | 83.921 | 1036.6027
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard